## Dashboard
Timestamp
Month | 2025-06-01
Date | 2025-06-12
Operation Year | 2026
Year Start Date | 2025-04-01
Year End Date | 2026-03-31
Sr. No. | Particular | Target | Measured | Deviation | Remarks
1 | E_Grid Daily (MWh) | 1787.1885 | 1990.334 | 11.37%
| E_Grid MTD(MWh) | 21446.2624 | 23517.935 | 9.66%
| E_Grid YTD (MWh) | 139476.2476 | 138222.344 | -0.899%
2 | CUF Daily(%) | 22.22% | 24.75% | 11.37%
| CUF MTD(%) | 22.22% | 24.37% | 9.66%
| CUF YTD(%) | 23.76% | 23.54% | -0.899%
3 | PR_Daily (%) | 82.99% | 78.17% | -5.803%
| PR_MTD (%) | 82.99% | 79.8% | -3.837%
| PR_YTD (%) | 81.47% | 78.51% | -3.627%
4 | POA Daily (KWh/m2) | 6.4267 | 7.5981 | 18.23% | WMS-02,09 POA_UP VALUE EXCLUDED DUE TO PYRANOMETER REMOVED FOR CALIBRATION & WMS-4 Data Excluded Due to data error.
| POA MTD(KWh/m2) | 77.12 | 87.9441 | 14.04%
| POA YTD(KWh/m2) | 510.92 | 525.3799 | 2.83%
5 | PA Daily | 99.75% | 100% | 0.2501%
| PA MTD | 99.75% | 99.9% | 0.1503%
| PA YTD | 99.75% | 99.67% | -0.07578%
6 | GA Daily | 99.75% | 95.13% | -4.636% | Load Curtailment @ 30% of Active Power Due to 400KV Akal Line Trip.
| GA MTD | 99.75% | 97.75% | -2.005%
| GA YTD | 99.75% | 98.01% | -1.747%
7 | WPR_Daily | 82.99% | 83.5% | 0.6197%
| WPR_MTD | 82.99% | 82% | -1.194%
| WPR_YTD | 81.47% | 81.46% | -0.01363%

## Annual_KPI
Till Date | 2025-06-12 | 2025-06-01
Clean Solar Power (Bhainsada) Private Limited Performance Summary-YTD
Year | Days | Estimated POA(KWh/m2) | Measured POA (KWh/m2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Targt PR (%) | Measured PR(%) | Target DC CUF (%) | Measured DC CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | WPR_Eac | WPR_Edc
2026 | 73 | 510.92 | 525.3799 | 139476.2476 | 138222.344 | 81.47% | 78.51% | 23.76% | 23.54% | 99.75% | 98.01% | 99.75% | 99.67% | 136499.4248 | 167573.5393
Clean Solar Power (Bhainsada) Private Limited Performance Summary-Monthwise
Year | Days | Estimated POA(KWh/m2) | Measured POA (KWh/m2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Targt PR (%) | Measured PR(%) | Target DC CUF (%) | Measured DC CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | WPR_Eac | WPR_Edc
2023-04-01 | 30 | 215.9 | 209.757 | 58630 | 56357.027 | 81.04% | 80.18% | 24.3% | 23.36% | 99.5% | 100% | 99.5% | 100% | 56472.21 | 69868.2422
2023-05-01 | 31 | 217.9 | 219.3794 | 61780 | 59365.339 | 84.61% | 80.76% | 24.78% | 23.81% | 99.5% | 100% | 99.5% | 99.4% | 59471.674 | 73429.2808
2023-06-01 | 30 | 192.8 | 195.6695 | 53700 | 51693.87 | 83.12% | 78.84% | 22.26% | 21.43% | 99.5% | 100% | 99.5% | 99.9% | 43888.604 | 52861.6404
2023-07-01 | 31 | 168.9 | 183.7896 | 49210 | 51842.389 | 86.95% | 84.18% | 19.74% | 20.79% | 99.5% | 100% | 99.5% | 99.78% | 50252.473 | 59478.2021
2023-08-01 | 31 | 174.2 | 178.5686 | 50100 | 50784.686 | 85.83% | 84.87% | 20.1% | 20.37% | 99.5% | 100% | 99.5% | 99.94% | 50847.866 | 60536.8676
2023-09-01 | 30 | 192.1 | 180.6934 | 52760 | 50322.204 | 81.96% | 83.11% | 21.87% | 20.86% | 99.5% | 100% | 99.5% | 99.89% | 50414.205 | 60399.04
2023-10-01 | 31 | 202.3 | 186.0129 | 57190 | 51919.071 | 84.36% | 83.3% | 22.94% | 20.83% | 99.5% | 100% | 99.5% | 99.96% | 51978.47 | 61679.6024
2023-11-01 | 30 | 162.9 | 138.9341 | 46900 | 39756.536 | 85.92% | 85.4% | 19.44% | 16.48% | 99.5% | 100% | 99.5% | 99.85% | 39899.011 | 46001.2406
2023-12-01 | 31 | 158.6 | 158.5562 | 48280 | 46671.27 | 90.85% | 87.84% | 19.37% | 18.72% | 99.5% | 100% | 99.5% | 99.91% | 46788.007 | 51956.5069
2024-01-01 | 31 | 169.0285 | 161.5271 | 51260 | 48383.138 | 90.5% | 89.39% | 20.56% | 19.41% | 99.5% | 100% | 99.5% | 99.9% | 48497.272 | 53260.2852
2024-02-01 | 29 | 172.5591 | 170.0986 | 47290 | 48336.603 | 81.78% | 84.8% | 20.28% | 20.73% | 99.5% | 100% | 99.5% | 99.83% | 48163.971 | 55819.1611
2024-03-01 | 31 | 215.7458 | 210.3972 | 60510 | 58114.871 | 83.7% | 82.43% | 24.27% | 23.31% | 99.5% | 100% | 99.5% | 99.97% | 58210.471 | 69565.8168
2024-04-01 | 30 | 215.9 | 189.0023 | 59074 | 52092.671 | 81.65% | 82.25% | 24.49% | 21.59% | 99.5% | 100% | 99.5% | 99.69% | 49364.537 | 58686.3604
2024-05-01 | 31 | 217.9 | 216.4405 | 60423.7 | 59441.338 | 82.75% | 81.96% | 24.24% | 23.84% | 99.5% | 100% | 99.5% | 99.99% | 59539.538 | 71492.3842
2024-06-01 | 30 | 192.8 | 197.8582 | 54283.7 | 55234.538 | 84.02% | 83.31% | 22.5% | 22.89% | 99.5% | 100% | 99.5% | 99.99% | 55322.101 | 66180.9806
2024-07-01 | 31 | 168.9 | 188.419 | 48128.2 | 51733.071 | 85.04% | 81.94% | 19.3% | 20.75% | 99.5% | 100% | 99.5% | 98.85% | 51747.334 | 62706.3114
2024-08-01 | 31 | 174.2 | 136.2012 | 48997.8 | 37134.229 | 83.94% | 81.36% | 19.65% | 14.89% | 99.5% | 100% | 99.5% | 99.24% | 32555.659 | 39121.4038
2024-09-01 | 30 | 192.1 | 185.3687 | 53326.7 | 49369.644 | 82.84% | 79.48% | 22.1% | 20.46% | 99.5% | 100% | 99.5% | 99.93% | 41868.327 | 50565.8377
2024-10-01 | 31 | 202.3 | 184.023 | 55941.2 | 50682.27 | 82.52% | 82.19% | 22.44% | 20.33% | 99.5% | 100% | 99.5% | 99.99% | 50799.337 | 60612.753
2024-11-01 | 30 | 162.9 | 167.8896 | 47411.9 | 47069.604 | 86.86% | 83.67% | 19.65% | 19.51% | 99.5% | 100% | 99.5% | 99.74% | 47058.0886 | 54279.9904
2024-12-01 | 31 | 158.6 | 157.6097 | 47221.3 | 44800.271 | 88.85% | 84.83% | 18.94% | 17.97% | 99.5% | 98.2% | 99.5% | 99.89% | 44441.774 | 50467.4308
2025-01-01 | 31 | 169.0285 | 171.7465 | 50133.1 | 49936.937 | 88.51% | 86.77% | 20.11% | 20.03% | 99.5% | 100% | 99.5% | 99.99% | 49676.6572 | 55596.3792
2025-02-01 | 28 | 172.5591 | 161.3875 | 49142.5 | 45482.803 | 84.99% | 84.1% | 21.82% | 20.2% | 99.5% | 99.5% | 99.5% | 99.99% | 45348.9353 | 52003.2965
2025-03-01 | 31 | 215.7458 | 222.7635 | 59189.3 | 59425.205 | 81.87% | 79.61% | 23.74% | 23.84% | 99.5% | 99.99% | 99.5% | 99.06% | 59065.796 | 72230.7289
2025-04-01 | 30 | 215.9 | 224.5394 | 58341.8915 | 57802.737 | 80.64% | 76.82% | 24.18% | 23.96% | 99.5% | 97.81% | 99.5% | 99.68% | 57206.7945 | 70400.0947
Formulas:
Days = DAY(EOMONTH([Year],0))

## Monthly_KPI
Till Date | 2025-06-12
Clean Solar Power (Bhainsada) Private Limited Performance Summary
Year | Days | Estimated POA(KWh/m2) | Measured POA (KWh/m2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Targt PR (%) | Measured PR(%) | Target DC CUF (%) | Measured DC CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | WPR_Eac | WPR_Edc
2025-06-01 | 12 | 77.12 | 87.9441 | 21446.2624 | 23517.935 | 82.99% | 79.8% | 22.22% | 24.37% | 99.75% | 97.75% | 99.75% | 99.9% | 23018.0131 | 28071.4431
Start Date | 2025-06-05
End Date | 2025-06-12
Clean Solar Power (Bhainsada) Private Limited Performance Summary
Year | Days | Estimated POA(KWh/m2) | Measured POA (KWh/m2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Targt PR (%) | Measured PR(%) | Target DC CUF (%) | Measured DC CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | WPR_Eac | WPR_Edc
2025-06-01 | 8 | 51.4133 | 60.2306 | 14297.5082 | 16300.601 | 82.99% | 80.77% | 22.22% | 25.34% | 99.75% | 99.21% | 99.75% | 99.85% | 15583242.3555 | 18950567.0816
Formulas:
Days = [Days, row below]-7

## Daily KPI
Date | Financial Year | Calendar Year | Month Year | Days | Operating Hours | GHI-UP (KWh/m2) | GHI-Down(KWh/m2) | POA-UP(KWh/m2) | POA-Down(KWh/m2) | Amb_Temp(°C) | Mod_Temp(°C) | WS_Avg(m/s) | WS_Max(m/s) | PA(%) | MA (%) | IGA (%) | EGA(%) | EMA (%) | TA (%) | PR(%) | WPR(%) | CUF(%) | Gen_Exp (kWh) | Mtr_Export (kWh) | Mtr_Import (kWh) | Mtr_Net_Exp (KWh) | Operational Capacity (MW) | Bugt_Resource | Bugt_Energy | Bugt PR | Bugt CUF | Bugt_PA | Bugt_EGA | Expected Energy | Actual Energy WPR | RA (%) | Mod Clean Dry (Num) | Mod Clean Wet (Num) | Line Loss(%) | Reactive Power (%) | Bugt Line loss (%) (Wind) | Bugt Reactive Power (%) (Wind) | Bugt Capacity | CC*Bugt
2022-04-04 | 2023 | 2022 | 2022-04-01 | 30 | 12.7667 | 7.33 | 2.13 | 7.71 | 2.06 | 36.82 | 39.13 | 5.66 | 7.1 | 100% |  |  | 100% |  |  | 79.06% | 86.21% | 1.592% | 131256.1 | 133000 | 5000 | 128000 | 21 | 7.1967 | 1987920 | 82.43% | 24.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-04-05 | 2023 | 2022 | 2022-04-01 | 30 | 12.9667 | 7.8 | 2.18 | 7.69 | 2.09 | 36.42 | 42.99 | 5.1 | 6.23 | 100% |  |  | 100% |  |  | 95.98% |  | 1.927% | 145490 | 160000 | 5000 | 155000 | 21 | 7.1967 | 1987920 | 82.43% | 24.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-04-06 | 2023 | 2022 | 2022-04-01 | 30 | 12.95 | 7.77 | 2.17 | 7.82 | 2.11 | 38 | 34.2768 | 2.56 | 7.15 | 100% |  |  | 100% |  |  | 81.84% |  | 2.164% | 177941.8 | 177000 | 3000 | 174000 | 27.189 | 7.1967 | 1987920 | 82.43% | 24.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-04-07 | 2023 | 2022 | 2022-04-01 | 30 | 12.9333 | 7.2285 | 2.2836 | 7.6673 | 2.2039 | 34.6152 | 34.6152 | 2.74 | 6.49 | 100% |  |  | 100% |  |  | 80.75% |  | 2.474% | 88289.3 | 202000 | 3000 | 199000 | 32.142 | 7.1967 | 1987920 | 82.43% | 24.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-04-08 | 2023 | 2022 | 2022-04-01 | 30 | 12.7333 | 7.0062 | 2.2242 | 7.4199 | 2.1504 | 34.8657 | 34.8657 | 4.88 | 9.78 | 100% |  |  | 100% |  |  | 82.27% |  | 2.86% | 224774.4 | 233000 | 3000 | 230000 | 37.68 | 7.1967 | 1987920 | 82.43% | 24.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-04-09 | 2023 | 2022 | 2022-04-01 | 30 | 12.7167 | 7.3634 | 2.3211 | 7.808 | 2.2463 | 33.4074 | 33.4074 | 3.28 | 7.03 | 100% |  |  | 100% |  |  | 77.03% |  | 3.519% | 287832.2 | 286000 | 3000 | 283000 | 47.05 | 7.1967 | 1987920 | 82.43% | 24.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-04-10 | 2023 | 2022 | 2022-04-01 | 30 | 12.7167 | 7.08 | 2.2 | 7.4 | 2.13 | 36.71 | 34.73 | 2.66 | 3.57 | 100% |  |  | 100% |  |  | 79.06% |  | 4.19% | 380061 | 340000 | 3000 | 337000 | 57.6 | 7.1967 | 1987920 | 82.43% | 24.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-04-11 | 2023 | 2022 | 2022-04-01 | 30 | 12.7167 | 7.28 | 2.27 | 7.68 | 2.2 | 40 | 38.03 | 4.5 | 9.1 | 100% |  |  | 100% |  |  | 78.2% |  | 5.272% | 430354 | 427000 | 3000 | 424000 | 70.6 | 7.1967 | 1987920 | 82.43% | 24.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-04-12 | 2023 | 2022 | 2022-04-01 | 30 | 12.7167 | 7.12 | 2.19 | 7.52 | 2.13 | 36.85 | 34.07 | 6 | 11.22 | 100% |  |  | 100% |  |  | 63.5% |  | 4.75% | 389870.7 | 385000 | 3000 | 382000 | 80 | 7.1967 | 1987920 | 82.43% | 24.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-04-13 | 2023 | 2022 | 2022-04-01 | 30 | 12.7167 | 6.9 | 2.12 | 7.24 | 2.04 | 38.21 | 35.08 | 3.08 | 7.67 | 100% |  |  | 100% |  |  | 82.05% |  | 6.205% | 505732 | 502000 | 3000 | 499000 | 84 | 7.1967 | 1987920 | 82.43% | 24.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-04-14 | 2023 | 2022 | 2022-04-01 | 30 | 12.6833 | 6.68 | 2.08 | 7.02 | 2.02 | 40 | 37.81 | 5.07 | 9.4 | 100% |  |  | 100% |  |  | 79.77% |  | 6.267% | 513924.4 | 507000 | 3000 | 504000 | 90 | 7.1967 | 1987920 | 82.43% | 24.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-04-15 | 2023 | 2022 | 2022-04-01 | 30 | 12.65 | 7.18 | 2.24 | 7.55 | 2.17 | 40.81 | 37.48 | 3.6 | 8.65 | 100% |  |  | 100% |  |  | 82.35% |  | 7.112% | 575500.9 | 575000 | 3000 | 572000 | 92 | 7.1967 | 1987920 | 82.43% | 24.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-04-16 | 2023 | 2022 | 2022-04-01 | 30 | 12.6833 | 7.1 | 2.23 | 7.46 | 2.16 | 40.29 | 37.54 | 4.2 | 7.8 | 100% |  |  | 100% |  |  | 81.69% |  | 7.274% | 593733.6 | 589000 | 4000 | 585000 | 96 | 7.1967 | 1987920 | 82.43% | 24.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-04-17 | 2023 | 2022 | 2022-04-01 | 30 | 12.65 | 6.92 | 2.17 | 7.27 | 2.1 | 35.64 | 37.08 | 5.08 | 8.51 | 100% |  |  | 100% |  |  | 83.61% |  | 7.709% | 627798.9 | 623000 | 3000 | 620000 | 102 | 7.1967 | 1987920 | 82.43% | 24.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-04-18 | 2023 | 2022 | 2022-04-01 | 30 | 12.6667 | 6.95 | 2.16 | 7.24 | 2.09 | 38.83 | 36.1 | 5.6 | 9.7 | 100% |  |  | 100% |  |  | 82.18% |  | 8.064% | 656982.2 | 652290 | 3770 | 648520 | 109 | 7.1967 | 1987920 | 82.43% | 24.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-04-19 | 2023 | 2022 | 2022-04-01 | 30 | 12.6667 | 6.97 | 2.2 | 7.27 | 2.13 | 36.59 | 38.21 | 3.78 | 6.94 | 100% |  |  | 100% |  |  | 80.98% |  | 8.126% | 662271 | 656710 | 3230 | 653480 | 111 | 7.1967 | 1987920 | 82.43% | 24.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-04-20 | 2023 | 2022 | 2022-04-01 | 30 | 12.6667 | 6.515 | 1.77 | 6.85 | 1.76 | 36.28 | 37.74 | 3.77 | 9.485 | 100% |  |  | 100% |  |  | 76.76% |  | 7.846% | 639508.7 | 634000 | 3000 | 631000 | 120 | 7.1967 | 1987920 | 82.43% | 24.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-04-21 | 2023 | 2022 | 2022-04-01 | 30 | 12.6667 | 7.12 | 2.0025 | 7.6225 | 1.9925 | 36.395 | 41.33 | 5.1175 | 11.4025 | 100% |  |  | 100% |  |  | 72.1% |  | 8.542% | 696284.8 | 691000 | 4000 | 687000 | 125 | 7.1967 | 1987920 | 82.43% | 24.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-04-22 | 2023 | 2022 | 2022-04-01 | 30 | 12.6667 | 7.6975 | 2.1625 | 8.2025 | 2.1425 | 37.6125 | 37.37 | 2.8975 | 7.8575 | 100% |  |  | 100% |  |  | 71.05% |  | 9.276% | 754982.5 | 749000 | 3000 | 746000 | 128 | 7.1967 | 1987920 | 82.43% | 24.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-04-23 | 2023 | 2022 | 2022-04-01 | 30 | 12.7833 | 7.5575 | 2.14 | 8.075 | 2.1275 | 36.5125 | 38.44 | 2.31 | 5.865 | 100% |  |  | 100% |  |  | 70.94% |  | 9.189% | 749540.9 | 743000 | 4000 | 739000 | 129 | 7.1967 | 1987920 | 82.43% | 24.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-04-24 | 2023 | 2022 | 2022-04-01 | 30 | 12.8 | 7.2725 | 2.005 | 7.7248 | 2.008 | 37.225 | 38.36 | 2.575 | 8.0175 | 100% |  |  | 100% |  |  | 70.51% |  | 8.94% | 728063.9 | 722000 | 3000 | 719000 | 132 | 7.1967 | 1987920 | 82.43% | 24.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-04-25 | 2023 | 2022 | 2022-04-01 | 30 | 12.9167 | 7.17 | 2.0125 | 7.58 | 2.0025 | 37.9425 | 39.25 | 4.165 | 8.005 | 100% |  |  | 100% |  |  | 69.61% |  | 8.791% | 715481.9 | 710000 | 3000 | 707000 | 134 | 7.1967 | 1987920 | 82.43% | 24.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-04-26 | 2023 | 2022 | 2022-04-01 | 30 | 12.85 | 7.73 | 2.045 | 8.175 | 2.095 | 37.5675 | 39.49 | 3.44 | 7.8475 | 100% |  |  | 100% |  |  | 70.59% |  | 9.686% | 788840.9 | 782000 | 3000 | 779000 | 135 | 7.1967 | 1987920 | 82.43% | 24.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-04-27 | 2023 | 2022 | 2022-04-01 | 30 | 12.9667 | 7.71 | 2.1225 | 8.1375 | 2.125 | 38.5675 | 39.94 | 4.7525 | 9.0375 | 100% |  |  | 100% |  |  | 70.73% |  | 9.948% | 808339.8 | 803000 | 3000 | 800000 | 139 | 7.1967 | 1987920 | 82.43% | 24.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-04-28 | 2023 | 2022 | 2022-04-01 | 30 | 12.9667 | 7.9375 | 2.105 | 8.365 | 2.1075 | 38.755 | 46.4 | 6.0775 | 12.0575 | 100% |  |  | 100% |  |  | 69.59% |  | 10.13% | 825332.6 | 819000 | 4000 | 815000 | 140 | 7.1967 | 1987920 | 82.43% | 24.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-04-29 | 2023 | 2022 | 2022-04-01 | 30 | 13 | 7.895 | 2.065 | 8.2925 | 2.055 | 35.935 | 37.72 | 4.1625 | 8.51 | 100% |  |  | 100% |  |  | 71.59% |  | 10.48% | 851722.1 | 846000 | 3000 | 843000 | 142 | 7.1967 | 1987920 | 82.43% | 24.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-04-30 | 2023 | 2022 | 2022-04-01 | 30 | 13.0833 | 7.095 | 1.855 | 7.435 | 1.845 | 38.775 | 40.6 | 3.125 | 6.665 | 100% |  |  | 100% |  |  | 70.85% |  | 9.301% | 758525.6 | 752000 | 4000 | 748000 | 142 | 7.1967 | 1987920 | 82.43% | 24.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-05-01 | 2023 | 2022 | 2022-05-01 | 31 | 13.05 | 7.65 | 2.0025 | 8.0225 | 1.9725 | 39.2525 | 41.04 | 4.535 | 8.97 | 100% |  |  | 100% |  |  | 70.84% |  | 10.03% | 816969.3 | 810000 | 3000 | 807000 | 142 | 7.029 | 1968183.871 | 83.56% | 24.47% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-05-02 | 2023 | 2022 | 2022-05-01 | 31 | 13.05 | 6.8175 | 1.86 | 7.0925 | 1.86 | 37.0225 | 37.81 | 9.2225 | 13.815 | 100% |  |  | 100% |  |  | 71.57% |  | 9.09% | 739476.5 | 734000 | 3000 | 731000 | 144 | 7.029 | 1968183.871 | 83.56% | 24.47% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-05-03 | 2023 | 2022 | 2022-05-01 | 31 | 13.0333 | 6.7 | 1.7925 | 6.99 | 1.79 | 34.245 | 35.58 | 8.2225 | 13.435 | 100% |  |  | 100% |  |  | 76.4% |  | 9.562% | 779667 | 772000 | 3000 | 769000 | 144 | 7.029 | 1968183.871 | 83.56% | 24.47% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-05-04 | 2023 | 2022 | 2022-05-01 | 31 | 13.1333 | 7.5425 | 1.97 | 7.9175 | 1.9625 | 33.5275 | 35.44 | 3.89 | 8.8075 | 100% |  |  | 100% |  |  | 77.55% |  | 11.45% | 933355.9 | 925000 | 4000 | 921000 | 150 | 7.029 | 1968183.871 | 83.56% | 24.47% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-05-05 | 2023 | 2022 | 2022-05-01 | 31 | 12.5167 | 5.795 | 1.525 | 6.035 | 1.5225 | 36.375 | 37.65 | 4.055 | 20.86 | 100% |  |  | 100% |  |  | 84.18% |  | 9.475% | 771844.6 | 766000 | 4000 | 762000 | 150 | 7.029 | 1968183.871 | 83.56% | 24.47% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-05-06 | 2023 | 2022 | 2022-05-01 | 31 | 13.1167 | 7.1425 | 1.7075 | 7.475 | 1.695 | 35.7375 | 44.35 | 3.585 | 5.975 | 100% |  |  | 100% |  |  | 67.27% |  | 10.94% | 892671.4 | 885000 | 5000 | 880000 | 175 | 7.029 | 1968183.871 | 83.56% | 24.47% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-05-07 | 2023 | 2022 | 2022-05-01 | 31 | 13.1 | 7.48 | 1.8925 | 7.81 | 1.855 | 38.9475 | 40.32 | 4.08 | 7.775 | 100% |  |  | 100% |  |  | 75% |  | 12.75% | 1033279 | 1028000 | 3000 | 1025000 | 175 | 7.029 | 1968183.871 | 83.56% | 24.47% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-05-08 | 2023 | 2022 | 2022-05-01 | 31 | 13.2333 | 7.7225 | 1.98 | 7.9175 | 1.9625 | 39.8075 | 41.09 | 5.76 | 10.07 | 100% |  |  | 100% |  |  | 72.31% |  | 13.74% | 1117571.6 | 1109470 | 4570 | 1104900 | 193 | 7.029 | 1968183.871 | 83.56% | 24.47% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-05-09 | 2023 | 2022 | 2022-05-01 | 31 | 13.2667 | 8.03 | 2.0875 | 8.3375 | 2.06 | 39.8125 | 41.1 | 6.5125 | 11.9225 | 100% |  |  | 100% |  |  | 74.21% |  | 14.85% | 1207217.8 | 1197530 | 3430 | 1194100 | 193 | 7.029 | 1968183.871 | 83.56% | 24.47% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-05-10 | 2023 | 2022 | 2022-05-01 | 31 | 13.2833 | 7.825 | 2.035 | 8.105 | 2 | 39.21 | 40.66 | 4.0075 | 7.8175 | 100% |  |  | 100% |  |  | 69.01% |  | 14.88% | 1209572.4 | 1201000 | 4000 | 1197000 | 214 | 7.029 | 1968183.871 | 83.56% | 24.47% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-05-11 | 2023 | 2022 | 2022-05-01 | 31 | 13.3 | 7.62 | 1.9725 | 7.885 | 1.955 | 39.575 | 41.04 | 3.4825 | 7.92 | 100% |  |  | 100% |  |  | 70.7% |  | 14.83% | 1205543.9 | 1196000 | 3000 | 1193000 | 214 | 7.029 | 1968183.871 | 83.56% | 24.47% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-05-12 | 2023 | 2022 | 2022-05-01 | 31 | 13.3167 | 7.8425 | 2.0625 | 8.12 | 2.0425 | 41.255 | 42.64 | 5.0325 | 9.6975 | 100% |  |  | 100% |  |  | 70.1% |  | 15.64% | 1270627.6 | 1262000 | 4000 | 1258000 | 221 | 7.029 | 1968183.871 | 83.56% | 24.47% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-05-13 | 2023 | 2022 | 2022-05-01 | 31 | 13.2667 | 7.98 | 2.0825 | 8.245 | 2.07 | 41.69 | 43.1 | 4.905 | 9.4725 | 100% |  |  | 100% |  |  | 65.15% |  | 15.1% | 1226942.9 | 1217000 | 3000 | 1214000 | 226 | 7.029 | 1968183.871 | 83.56% | 24.47% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-05-14 | 2023 | 2022 | 2022-05-01 | 31 | 13.3667 | 7.895 | 2.0525 | 8.155 | 2.0425 | 40.5 | 42.26 | 5.2375 | 9.16 | 100% |  |  | 100% |  |  | 68.85% |  | 16.13% | 1310134 | 1300000 | 3000 | 1297000 | 231 | 7.029 | 1968183.871 | 83.56% | 24.47% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-05-15 | 2023 | 2022 | 2022-05-01 | 31 | 13.4 | 7.4375 | 1.83 | 7.645 | 1.825 | 38.5375 | 39.48 | 8.6775 | 12.175 | 100% |  |  | 100% |  |  | 70.94% |  | 15.92% | 1293853.9 | 1284000 | 4000 | 1280000 | 236 | 7.029 | 1968183.871 | 83.56% | 24.47% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-05-16 | 2023 | 2022 | 2022-05-01 | 31 | 13.4 | 7.194 | 1.8114 | 7.4979 | 1.8062 | 36.1534 | 37.8718 | 8.2781 | 12.7975 | 100% |  |  | 100% |  |  | 69.3% |  | 16.15% | 1312365.337 | 1302000 | 3000 | 1299000 | 250 | 7.029 | 1968183.871 | 83.56% | 24.47% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-05-17 | 2023 | 2022 | 2022-05-01 | 31 | 13.4333 | 7.6607 | 1.8794 | 7.9219 | 1.8763 | 34.5728 | 37.0325 | 3.8736 | 7.5687 | 100% |  |  | 100% |  |  | 69.07% |  | 17.01% | 1383546.3 | 1372000 | 4000 | 1368000 | 250 | 7.029 | 1968183.871 | 83.56% | 24.47% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-05-18 | 2023 | 2022 | 2022-05-01 | 31 | 13.3167 | 7.4854 | 1.7293 | 7.7416 | 1.7436 | 37.7846 | 41.2256 | 3.0465 | 6.9992 | 100% |  |  | 100% |  |  | 69.24% |  | 16.66% | 1352762.907 | 1343000 | 3000 | 1340000 | 250 | 7.029 | 1968183.871 | 83.56% | 24.47% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-05-19 | 2023 | 2022 | 2022-05-01 | 31 | 13.3833 | 7.6313 | 1.7549 | 7.8659 | 1.7722 | 40.3962 | 42.4423 | 4.6614 | 7.8987 | 100% |  |  | 100% |  |  | 69.55% |  | 17.1% | 1390681.043 | 1379000 | 4000 | 1375000 | 251.332 | 7.029 | 1968183.871 | 83.56% | 24.47% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-05-20 | 2023 | 2022 | 2022-05-01 | 31 | 13.7667 | 7.1505 | 1.6868 | 7.3536 | 1.7064 | 40.0276 | 41.3914 | 8.7497 | 13.8962 | 100% |  |  | 100% |  |  | 73.12% |  | 17.02% | 1383190.5 | 1373000 | 4000 | 1369000 | 254.608 | 7.029 | 1968183.871 | 83.56% | 24.47% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-05-21 | 2023 | 2022 | 2022-05-01 | 31 | 13.4167 | 7.3762 | 1.7228 | 7.6456 | 1.7423 | 37.2334 | 38.6634 | 8.1279 | 12.3488 | 100% |  |  | 100% |  |  | 74.04% |  | 18.19% | 1478228.383 | 1466000 | 3000 | 1463000 | 258.435 | 7.029 | 1968183.871 | 83.56% | 24.47% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-05-22 | 2023 | 2022 | 2022-05-01 | 31 | 13.5 | 7.3557 | 1.6736 | 7.6684 | 1.6912 | 36.3008 | 38.2913 | 6.4134 | 9.9375 | 100% |  |  | 100% |  |  | 75.28% |  | 18.95% | 1539664.159 | 1527000 | 3000 | 1524000 | 264.005 | 7.029 | 1968183.871 | 83.56% | 24.47% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-05-23 | 2023 | 2022 | 2022-05-01 | 31 | 13.2667 | 5.6004 | 1.3401 | 5.8431 | 1.3661 | 35.6247 | 35.3077 | 8.0718 | 12.5346 | 100% |  |  | 100% |  |  | 77.77% |  | 15.18% | 1240884.5 | 1225000 | 4000 | 1221000 | 268.6957 | 7.029 | 1968183.871 | 83.56% | 24.47% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-05-24 | 2023 | 2022 | 2022-05-01 | 31 | 13.4667 | 7.3517 | 1.6864 | 7.588 | 1.7044 | 35.2706 | 52.9407 | 4.7613 | 8.0487 | 100% |  |  | 100% |  |  | 73.44% |  | 18.81% | 1529421.076 | 1517000 | 4000 | 1513000 | 271.513 | 7.029 | 1968183.871 | 83.56% | 24.47% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-05-25 | 2023 | 2022 | 2022-05-01 | 31 | 13.35 | 7.2805 | 1.6725 | 7.5105 | 1.6887 | 37.0145 | 54.5307 | 4.6867 | 8.2779 | 100% |  |  | 100% |  |  | 73.17% |  | 18.61% | 1512851.67 | 1500000 | 3000 | 1497000 | 272.394 | 7.029 | 1968183.871 | 83.56% | 24.47% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-05-26 | 2023 | 2022 | 2022-05-01 | 31 | 13.4833 | 7.5034 | 1.7216 | 7.7343 | 1.75 | 35.1602 |  | 6.6516 | 9.7129 | 100% |  |  | 100% |  |  | 74.9% |  | 19.73% | 1604299.8 | 1591000 | 4000 | 1587000 | 273.9636 | 7.029 | 1968183.871 | 83.56% | 24.47% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-05-27 | 2023 | 2022 | 2022-05-01 | 31 | 13.5833 | 7.2956 | 1.6899 | 7.5153 | 1.7183 | 34.7724 |  | 7.6817 | 11.6808 | 100% |  |  | 100% |  |  | 75.85% |  | 19.45% | 1568412.9 | 1567000 | 3000 | 1564000 | 274.367 | 7.029 | 1968183.871 | 83.56% | 24.47% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-05-28 | 2023 | 2022 | 2022-05-01 | 31 | 13.4833 | 6.697 | 1.6028 | 6.6958 | 1.5945 | 35.0523 |  | 7.5287 | 12.3529 | 100% |  |  | 100% |  |  | 78.71% |  | 18.2% | 1521017.97 | 1469000 | 5000 | 1464000 | 277.773 | 7.029 | 1968183.871 | 83.56% | 24.47% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-05-29 | 2023 | 2022 | 2022-05-01 | 31 | 13.6 | 7.2461 | 1.6656 | 7.4627 | 1.7021 | 35.5759 |  | 7.8281 | 11.0883 | 100% |  |  | 100% |  |  | 72.09% |  | 18.71% | 1508256.36 | 1506000 | 1000 | 1505000 | 279.763 | 7.029 | 1968183.871 | 83.56% | 24.47% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-05-30 | 2023 | 2022 | 2022-05-01 | 31 | 13.5 | 7.4899 | 1.7245 | 7.5602 | 1.7768 | 35.1967 |  | 6.7661 | 11.2362 | 100% |  |  | 100% |  |  | 72.32% |  | 19.4% | 1556453.84 | 1562000 | 2000 | 1560000 | 285.338 | 7.029 | 1968183.871 | 83.56% | 24.47% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-05-31 | 2023 | 2022 | 2022-05-01 | 31 | 13.5167 | 7.36 | 1.6775 | 7.555 | 1.7525 | 35.845 |  | 6.62 | 10.8767 | 100% |  |  | 100% |  |  | 72.23% |  | 19.77% | 1607865.92 | 1594000 | 4000 | 1590000 | 291.37 | 7.029 | 1968183.871 | 83.56% | 24.47% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-06-01 | 2023 | 2022 | 2022-06-01 | 30 | 13.5333 | 7.7131 | 1.8758 | 7.7682 | 1.8628 | 36.6324 |  | 4.7411 | 9.1108 | 100% |  |  | 100% |  |  | 74.78% |  | 21.03% | 1607707.78 | 1694000 | 3000 | 1691000 | 291.0982 | 6.4267 | 1826880 | 84.83% | 22.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-06-02 | 2023 | 2022 | 2022-06-01 | 30 | 13.5333 | 7.3528 | 1.7246 | 7.5149 | 1.7415 | 37.6776 | 55.4925 | 3.7801 | 7.5312 | 100% |  |  | 100% |  |  | 72.65% |  | 19.81% | 1514777.81 | 1596000 | 3000 | 1593000 | 291.7687 | 6.4267 | 1826880 | 84.83% | 22.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-06-03 | 2023 | 2022 | 2022-06-01 | 30 | 13.5333 | 7.6909 | 1.794 | 7.8838 | 1.8014 | 38.1839 | 54.4274 | 4.7835 | 9.3804 | 100% |  |  | 100% |  |  | 72.72% |  | 20.84% | 1593918.76 | 1680000 | 4000 | 1676000 | 292.351 | 6.4267 | 1826880 | 84.83% | 22.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-06-04 | 2023 | 2022 | 2022-06-01 | 30 | 13.5333 | 7.4416 | 1.7384 | 7.5892 | 1.7361 | 36.1468 | 50.817 | 6.6103 | 12.1104 | 100% |  |  | 100% |  |  | 74.82% |  | 20.53% | 1570766.83 | 1655000 | 4000 | 1651000 | 290.7589 | 6.4267 | 1826880 | 84.83% | 22.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-06-05 | 2023 | 2022 | 2022-06-01 | 30 | 13.5833 | 7.5966 | 1.7483 | 7.771 | 1.7391 | 35.6618 | 51.5734 | 5.7389 | 9.2758 | 100% |  |  | 100% |  |  | 75.44% |  | 21.29% | 1648963.42 | 1715000 | 3000 | 1712000 | 292.0207 | 6.4267 | 1826880 | 84.83% | 22.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-06-06 | 2023 | 2022 | 2022-06-01 | 30 | 13.7167 | 7.6925 | 1.7175 | 7.8575 | 1.705 | 35.6618 | 51.5734 | 5.7389 | 9.2758 | 100% |  |  | 100% |  |  | 75.09% |  | 21.62% | 1572207.66 | 1743000 | 4000 | 1739000 | 294.718 | 6.4267 | 1826880 | 84.83% | 22.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-06-07 | 2023 | 2022 | 2022-06-01 | 30 | 13.7 | 7.068 | 1.584 | 7.302 | 1.594 | 36.5775 | 45.725 | 9.13 | 13.608 | 100% |  |  | 100% |  |  | 77.65% |  | 20.84% | 1517370.53 | 1679000 | 3000 | 1676000 | 295.6 | 6.4267 | 1826880 | 84.83% | 22.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-06-08 | 2023 | 2022 | 2022-06-01 | 30 | 13.7333 | 7.1084 | 1.5908 | 7.3606 | 1.6079 | 35.7545 | 44.6783 | 8.3164 | 12.355 | 100% |  |  | 100% |  |  | 78.59% |  | 21.42% | 1706014.6 | 1727000 | 4000 | 1723000 | 297.8473 | 6.4267 | 1826880 | 84.83% | 22.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-06-09 | 2023 | 2022 | 2022-06-01 | 30 | 13.7333 | 7.3077 | 1.6431 | 7.6958 | 1.677 | 35.2078 | 45.8932 | 8.249 | 12.0933 | 100% |  |  | 100% |  |  | 77.99% |  | 22.27% | 1708809.66 | 1794000 | 3000 | 1791000 | 298.415 | 6.4267 | 1826880 | 84.83% | 22.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-06-10 | 2023 | 2022 | 2022-06-01 | 30 | 13.7333 | 7.4289 | 1.6529 | 7.8258 | 1.6922 | 35.8509 | 46.8664 | 7.6342 | 11.4175 | 100% |  |  | 100% |  |  | 74.44% |  | 21.74% | 1658200.04 | 1752000 | 4000 | 1748000 | 300.061 | 6.4267 | 1826880 | 84.83% | 22.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-06-11 | 2023 | 2022 | 2022-06-01 | 30 | 13.7333 | 7.7934 | 1.7398 | 7.9512 | 1.7371 | 36.2293 | 45.5307 | 7.5301 | 11.8992 | 100% |  |  | 100% |  |  | 77.55% |  | 23.15% | 1750849.49 | 1866000 | 4000 | 1862000 | 301.9782 | 6.4267 | 1826880 | 84.83% | 22.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-06-12 | 2023 | 2022 | 2022-06-01 | 30 | 13.8167 | 7.5518 | 1.6504 | 7.8328 | 1.677 | 35.3399 | 48.1682 | 5.9425 | 9.7137 | 100% |  |  | 100% |  |  | 77.89% |  | 23% | 1749449.98 | 1853000 | 3000 | 1850000 | 303.217 | 6.4267 | 1826880 | 84.83% | 22.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-06-13 | 2023 | 2022 | 2022-06-01 | 30 | 13.25 | 6.8537 | 1.4373 | 7.0767 | 1.4393 | 35.3431 | 50.3041 | 3.7049 | 14.4371 | 100% |  |  | 100% |  |  | 76.24% |  | 20.5% | 1580381.15 | 1653000 | 4000 | 1649000 | 305.624 | 6.4267 | 1826880 | 84.83% | 22.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-06-14 | 2023 | 2022 | 2022-06-01 | 30 | 13.55 | 6.0417 | 1.1177 | 6.0997 | 1.1294 | 31.4545 | 43.834 | 3.8043 | 7.1513 | 100% |  |  | 100% |  |  | 80.26% |  | 19.24% | 1480572.39 | 1551000 | 4000 | 1547000 | 315.998 | 6.4267 | 1826880 | 84.83% | 22.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-06-15 | 2023 | 2022 | 2022-06-01 | 30 | 13.85 | 7.4198 | 1.4888 | 7.5434 | 1.5168 | 35.4527 | 47.0176 | 6.523 | 10.6747 | 100% |  |  | 100% |  |  | 80.06% |  | 23.75% | 1829784.2 | 1914000 | 4000 | 1910000 | 316.249 | 6.4267 | 1826880 | 84.83% | 22.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-06-16 | 2023 | 2022 | 2022-06-01 | 30 | 13.8333 | 7.2197 | 1.58 | 7.4758 | 1.5787 | 34.8665 | 45.7255 | 8.0735 | 13.2338 | 100% |  |  | 100% |  |  | 80.88% |  | 23.85% | 1813830.72 | 1922000 | 4000 | 1918000 | 317.1975 | 6.4267 | 1826880 | 84.83% | 22.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-06-17 | 2023 | 2022 | 2022-06-01 | 30 | 13.85 | 7.3436 | 1.5175 | 7.2591 | 1.6282 | 34.7534 | 45.7731 | 7.9315 | 12.4908 | 100% |  |  | 100% |  |  | 82.28% |  | 23.9% | 1841157.11 | 1925000 | 3000 | 1922000 | 321.8088 | 6.4267 | 1826880 | 84.83% | 22.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-06-18 | 2023 | 2022 | 2022-06-01 | 30 | 13.5667 | 4.7786 | 1.0462 | 4.8105 | 1.093 | 33.9086 | 42.0143 | 6.5073 | 11.1196 | 100% |  |  | 100% |  |  | 84.34% |  | 16.4% | 1262809.22 | 1323000 | 4000 | 1319000 | 325.1087 | 6.4267 | 1826880 | 84.83% | 22.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-06-19 | 2023 | 2022 | 2022-06-01 | 30 | 13.0333 | 6.3411 | 1.3601 | 6.3433 | 1.4037 | 34.7378 | 46.2382 | 5.4524 | 10.2692 | 100% |  |  | 100% |  |  | 78.9% |  | 20.24% | 1571256.25 | 1628000 | 0 | 1628000 | 325.2653 | 6.4267 | 1826880 | 84.83% | 22.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-06-20 | 2023 | 2022 | 2022-06-01 | 30 | 13.4 | 4.973 | 1.0931 | 4.9591 | 1.115 | 34.0981 | 42.7143 | 6.2488 | 9.7438 | 100% |  |  | 100% |  |  | 81.67% |  | 16.43% | 1259987.57 | 1322000 | 1000 | 1321000 | 326.152 | 6.4267 | 1826880 | 84.83% | 22.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-06-21 | 2023 | 2022 | 2022-06-01 | 30 | 13.6667 | 3.6102 | 0.79689 | 3.6208 | 0.81447 | 32.3757 | 38.9826 | 6.1863 | 10.905 | 100% |  |  | 100% |  |  | 83.97% |  | 12.4% | 950272.42 | 997000 | 0 | 997000 | 327.9034 | 6.4267 | 1826880 | 84.83% | 22.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-06-22 | 2023 | 2022 | 2022-06-01 | 30 | 13.4667 | 5.5084 | 1.1383 | 5.5759 | 1.1951 | 32.7843 | 45.8253 | 3.0317 | 7.905 | 100% |  |  | 100% |  |  | 77.43% |  | 17.62% | 1348179.17 | 1420000 | 3000 | 1417000 | 328.2137 | 6.4267 | 1826880 | 84.83% | 22.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-06-23 | 2023 | 2022 | 2022-06-01 | 30 | 13.4667 | 6.5871 | 1.3577 | 6.5578 | 1.4355 | 34.9135 | 44.6558 | 4.299 | 7.4029 | 100% |  |  | 100% |  |  | 76.24% |  | 20.4% | 1570136.2 | 1645000 | 4000 | 1641000 | 328.2137 | 6.4267 | 1826880 | 84.83% | 22.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-06-24 | 2023 | 2022 | 2022-06-01 | 30 | 13.7333 | 7.4179 | 1.6782 | 7.398 | 1.6273 | 37.8025 | 51.5395 | 2.1935 | 6.6633 | 100% |  |  | 100% |  |  | 73.51% |  | 22.2% | 1820942.69 | 1785000 | 0 | 1785000 | 328.2137 | 6.4267 | 1826880 | 84.83% | 22.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-06-25 | 2023 | 2022 | 2022-06-01 | 30 | 13.75 | 7.5143 | 1.5852 | 7.4728 | 1.645 | 39.7588 | 52.5173 | 3.145 | 7.22 | 100% |  |  | 100% |  |  | 72.74% | 74.19% | 22.18% | 1825356.22 | 1784000 | 0 | 1784000 | 328.2137 | 6.4267 | 1826880 | 84.83% | 22.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-06-26 | 2023 | 2022 | 2022-06-01 | 30 | 13.7167 | 7.7113 | 1.5105 | 7.6469 | 1.7033 | 41.1339 | 51.5535 | 4.225 | 8.3317 | 100% |  |  | 100% |  |  | 73.15% | 76.16% | 22.83% | 1851708.12 | 1836000 | 0 | 1836000 | 328.2137 | 6.4267 | 1826880 | 84.83% | 22.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-06-27 | 2023 | 2022 | 2022-06-01 | 30 | 14.0167 | 7.3752 | 1.4803 | 7.3372 | 1.6303 | 39.0266 | 51.6613 | 4.5413 | 8.4725 | 100% |  |  | 100% |  |  | 73% | 75.74% | 21.86% | 1776066.04 | 1762000 | 4000 | 1758000 | 328.2137 | 6.4267 | 1826880 | 84.83% | 22.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-06-28 | 2023 | 2022 | 2022-06-01 | 30 | 13.9167 | 7.0373 | 1.4451 | 6.9862 | 1.5452 | 37.4411 | 48.572 | 6.363 | 9.3758 | 100% |  |  | 100% |  |  | 75.01% | 74.96% | 21.39% | 1735517.27 | 1723000 | 3000 | 1720000 | 328.2137 | 6.4267 | 1826880 | 84.83% | 22.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-06-29 | 2023 | 2022 | 2022-06-01 | 30 | 13.8333 | 7.0195 | 1.4692 | 6.9883 | 1.5687 | 36.1543 | 46.2628 | 8.6705 | 12.6608 | 100% |  |  | 100% |  |  | 77.75% | 80.84% | 22.18% | 1708727.52 | 1788000 | 4000 | 1784000 | 328.339 | 6.4267 | 1826880 | 84.83% | 22.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-06-30 | 2023 | 2022 | 2022-06-01 | 30 | 13.7 | 5.8904 | 1.2026 | 5.8382 | 1.3011 | 34.8045 | 45.2466 | 8.0079 | 12.723 | 100% |  |  | 100% |  |  | 79.37% | 84.29% | 18.97% | 1521482.93 | 1530000 | 4000 | 1526000 | 329.3357 | 6.4267 | 1826880 | 84.83% | 22.72% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-07-01 | 2023 | 2022 | 2022-07-01 | 31 | 13.4833 | 3.743 | 0.72863 | 3.7071 | 0.79283 | 33.5489 | 41.455 | 4.5777 | 7.9843 | 100% |  |  | 100% |  |  | 84.45% | 82.96% | 12.82% | 1040845.1 | 1034000 | 3000 | 1031000 | 329.3357 | 5.4484 | 1567680.9677 | 85.87% | 19.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-07-02 | 2023 | 2022 | 2022-07-01 | 31 | 13.6 | 2.8637 | 0.45606 | 2.803 | 0.49117 | 30.2596 | 36.2986 | 3.0372 | 7.6296 | 100% |  |  | 100% |  |  | 88.85% | 83.83% | 10.21% | 822848.37 | 825000 | 4000 | 821000 | 329.6481 | 5.4484 | 1567680.9677 | 85.87% | 19.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-07-03 | 2023 | 2022 | 2022-07-01 | 31 | 13.4167 | 3.9375 | 0.67158 | 4.0181 | 0.73688 | 30.7968 | 40.1138 | 3.4149 | 10.8423 | 100% |  |  | 100% |  |  | 83.2% | 82.1% | 13.7% | 1114705.88 | 1106000 | 4000 | 1102000 | 329.6481 | 5.4484 | 1567680.9677 | 85.87% | 19.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-07-04 | 2023 | 2022 | 2022-07-01 | 31 | 13.55 | 5.1388 | 0.79939 | 5.185 | 0.8664 | 30.7799 | 43.1425 | 3.4233 | 14.3507 | 100% |  |  | 100% |  |  | 78.98% | 79.83% | 16.79% | 1351862.27 | 1354000 | 4000 | 1350000 | 329.6481 | 5.4484 | 1567680.9677 | 85.87% | 19.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-07-05 | 2023 | 2022 | 2022-07-01 | 31 | 13.7167 | 6.2079 | 1.0433 | 6.3097 | 1.1425 | 33.3929 | 64.1589 | 2.6837 | 8.8857 | 100% |  |  | 100% |  |  | 77.84% | 79.06% | 20.13% | 1636273.5 | 1622000 | 3000 | 1619000 | 329.6481 | 5.4484 | 1567680.9677 | 85.87% | 19.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-07-06 | 2023 | 2022 | 2022-07-01 | 31 | 13.6333 | 6.9768 | 1.3369 | 6.3556 | 1.4125 | 35.1677 | 51.9932 | 5.1791 | 10.9479 | 100% |  |  | 100% |  |  | 82.72% | 80.16% | 21.55% | 1752306.4 | 1738000 | 5000 | 1733000 | 329.6481 | 5.4484 | 1567680.9677 | 85.87% | 19.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-07-07 | 2023 | 2022 | 2022-07-01 | 31 | 13.3 | 5.3985 | 0.90838 | 5.2068 | 1.0114 | 31.8581 | 42.5054 | 3.2768 | 11.1063 | 100% |  |  | 100% |  |  | 75.51% | 78.73% | 16.12% | 1309431.7 | 1299000 | 3000 | 1296000 | 329.6481 | 5.4484 | 1567680.9677 | 85.87% | 19.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-07-08 | 2023 | 2022 | 2022-07-01 | 31 | 13.2667 | 5.6065 | 0.99486 | 5.6447 | 1.0438 | 31.4742 | 45.5844 | 2.7875 | 13.061 | 100% |  |  | 100% |  |  | 75.4% | 77.35% | 17.45% | 1428586.63 | 1407000 | 4000 | 1403000 | 329.6481 | 5.4484 | 1567680.9677 | 85.87% | 19.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-07-09 | 2023 | 2022 | 2022-07-01 | 31 | 13.5 | 6.7822 | 1.1982 | 6.5152 | 1.2953 | 32.6457 | 44.8092 | 3.635 | 7.66 | 100% |  |  | 100% |  |  | 81.29% | 78.37% | 21.71% | 1766240.09 | 1751000 | 5000 | 1746000 | 329.6481 | 5.4484 | 1567680.9677 | 85.87% | 19.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-07-10 | 2023 | 2022 | 2022-07-01 | 31 | 13.3833 | 6.3255 | 1.3523 | 6.4445 | 1.3848 | 32.238 | 45.8618 | 3.6815 | 7.5103 | 100% |  |  | 100% |  |  | 74.93% | 79.87% | 19.81% | 1610948.61 | 1596000 | 3000 | 1593000 | 329.8989 | 5.4484 | 1567680.9677 | 85.87% | 19.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-07-11 | 2023 | 2022 | 2022-07-01 | 31 | 13.3833 | 6.7337 | 1.3422 | 6.5042 | 1.4095 | 33.092 | 48.4165 | 3.5865 | 8.8747 | 100% |  |  | 100% |  |  | 79.88% | 78.77% | 21.31% | 1733033.3 | 1717000 | 3000 | 1714000 | 329.8989 | 5.4484 | 1567680.9677 | 85.87% | 19.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-07-12 | 2023 | 2022 | 2022-07-01 | 31 | 13.6833 | 7.2326 | 1.5413 | 7.3172 | 1.5958 | 32.8105 | 47.8242 | 3.5924 | 6.921 | 100% |  |  | 100% |  |  | 77.23% | 78.41% | 23.2% | 1887730.6 | 1871000 | 5000 | 1866000 | 330.1986 | 5.4484 | 1567680.9677 | 85.87% | 19.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-07-13 | 2023 | 2022 | 2022-07-01 | 31 | 13.65 | 6.8949 | 1.517 | 6.991 | 1.5739 | 32.8167 | 47.1328 | 3.9437 | 6.988 | 100% |  |  | 100% |  |  | 78.32% | 79.24% | 22.48% | 1827614.27 | 1812000 | 4000 | 1808000 | 330.1986 | 5.4484 | 1567680.9677 | 85.87% | 19.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-07-14 | 2023 | 2022 | 2022-07-01 | 31 | 13.5 | 5.3582 | 1.1458 | 5.3944 | 1.1932 | 33.6826 | 42.7604 | 4.54 | 13.417 | 100% |  |  | 100% |  |  | 80.33% | 81.28% | 17.79% | 1448752.48 | 1435000 | 4000 | 1431000 | 330.2299 | 5.4484 | 1567680.9677 | 85.87% | 19.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-07-15 | 2023 | 2022 | 2022-07-01 | 31 | 12.8667 | 3.3301 | 0.62787 | 3.3916 | 0.69886 | 30.6932 | 36.3307 | 4.4231 | 12.95 | 100% |  |  | 100% |  |  | 85.29% | 83.9% | 11.9% | 969880.7 | 961000 | 4000 | 957000 | 330.8342 | 5.4484 | 1567680.9677 | 85.87% | 19.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-07-16 | 2023 | 2022 | 2022-07-01 | 31 | 13.2667 | 6.5966 | 1.1155 | 6.6481 | 1.2183 | 31.9742 | 43.5805 | 4.5136 | 10.6933 | 100% |  |  | 100% |  |  | 78.79% | 78.39% | 21.55% | 1752205.4 | 1738000 | 5000 | 1733000 | 330.8342 | 5.4484 | 1567680.9677 | 85.87% | 19.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-07-17 | 2023 | 2022 | 2022-07-01 | 31 | 13.45 | 5.5403 | 0.85654 | 5.2065 | 1.0218 | 31.2021 | 41.7142 | 3.5276 | 7.839 | 100% |  |  | 100% |  |  | 80.41% | 84% | 17.22% | 1399813.56 | 1389000 | 4000 | 1385000 | 330.8342 | 5.4484 | 1567680.9677 | 85.87% | 19.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-07-18 | 2023 | 2022 | 2022-07-01 | 31 | 13.4667 | 5.5069 | 0.71206 | 5.3116 | 0.88701 | 31.1171 | 40.8884 | 2.9599 | 7.4107 | 100% |  |  | 100% |  |  | 75.16% | 76.81% | 16.45% | 1337092.54 | 1327000 | 4000 | 1323000 | 331.3942 | 5.4484 | 1567680.9677 | 85.87% | 19.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-07-19 | 2023 | 2022 | 2022-07-01 | 31 | 13.5 | 5.2246 | 0.99756 | 5.2193 | 1.0474 | 31.9459 | 42.7604 | 3.9356 | 9.5297 | 100% |  |  | 100% |  |  | 65.62% | 79.75% | 14.11% | 1147505.29 | 1136000 | 1000 | 1135000 | 331.3942 | 5.4484 | 1567680.9677 | 85.87% | 19.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-07-20 | 2023 | 2022 | 2022-07-01 | 31 | 13.4833 | 7.0112 | 1.0654 | 6.728 | 1.3903 | 32.5418 | 42.8243 | 6.5105 | 10.9203 | 100% |  |  | 100% |  |  | 85.53% | 81.48% | 23.71% | 1928915.61 | 1910000 | 3000 | 1907000 | 331.3942 | 5.4484 | 1567680.9677 | 85.87% | 19.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-07-21 | 2023 | 2022 | 2022-07-01 | 31 | 13.4833 | 5.6368 | 1.0188 | 5.4427 | 1.1852 | 32.2032 | 40.287 | 6.6356 | 11.072 | 100% |  |  | 100% |  |  | 83.66% | 82.71% | 18.76% | 1525792.4 | 1513000 | 4000 | 1509000 | 331.3942 | 5.4484 | 1567680.9677 | 85.87% | 19.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-07-22 | 2023 | 2022 | 2022-07-01 | 31 | 13.4833 | 5.0788 | 0.99108 | 5.1112 | 1.1593 | 32.1535 | 41.5999 | 5.5112 | 9.1867 | 100% |  |  | 100% |  |  | 84.37% | 83.55% | 17.77% | 1438188.69 | 1433000 | 4000 | 1429000 | 331.3942 | 5.4484 | 1567680.9677 | 85.87% | 19.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-07-23 | 2023 | 2022 | 2022-07-01 | 31 | 12.75 | 3.1078 | 0.40369 | 3.1359 | 0.47085 | 28.2367 | 35.8596 | 3.02 | 5.5073 | 100% |  |  | 100% |  |  | 89.49% | 87.69% | 11.56% | 942566.42 | 935000 | 5000 | 930000 | 331.3942 | 5.4484 | 1567680.9677 | 85.87% | 19.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-07-24 | 2023 | 2022 | 2022-07-01 | 31 | 13.3167 | 5.9022 | 0.95435 | 5.948 | 1.1061 | 30.5733 | 42.9694 | 3.6485 | 7.198 | 100% |  |  | 100% |  |  | 82.64% | 82.31% | 20.26% | 1646496.58 | 1633000 | 4000 | 1629000 | 331.3942 | 5.4484 | 1567680.9677 | 85.87% | 19.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-07-25 | 2023 | 2022 | 2022-07-01 | 31 | 13.3333 | 5.2118 | 1.06 | 5.3034 | 1.1123 | 29.189 | 40.1075 | 4.105 | 7.756 | 100% |  |  | 100% |  |  | 83.58% | 82.48% | 18.27% | 1486249.08 | 1474000 | 5000 | 1469000 | 331.3942 | 5.4484 | 1567680.9677 | 85.87% | 19.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-07-26 | 2023 | 2022 | 2022-07-01 | 31 | 12.75 | 1.2827 | 0.21809 | 1.2846 | 0.2321 | 27.3817 | 29.2241 | 4.2082 | 6.8583 | 100% |  |  | 100% |  |  | 94.67% | 90.82% | 5.011% | 411419.2 | 407000 | 4000 | 403000 | 331.3942 | 5.4484 | 1567680.9677 | 85.87% | 19.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-07-27 | 2023 | 2022 | 2022-07-01 | 31 | 12.3833 | 1.4253 | 0.20381 | 1.4295 | 0.21716 | 27.2776 | 29.8021 | 4.1207 | 6.972 | 100% |  |  | 100% |  |  | 91.61% | 87.56% | 5.397% | 443229.3 | 439000 | 5000 | 434000 | 331.3942 | 5.4484 | 1567680.9677 | 85.87% | 19.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-07-28 | 2023 | 2022 | 2022-07-01 | 31 | 13.35 | 4.0265 | 0.7075 | 4.0294 | 0.76566 | 28.8298 | 35.7288 | 5.958 | 9.1003 | 100% |  |  | 100% |  |  | 87.92% | 85.29% | 14.6% | 1187733.97 | 1178000 | 4000 | 1174000 | 331.3942 | 5.4484 | 1567680.9677 | 85.87% | 19.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-07-29 | 2023 | 2022 | 2022-07-01 | 31 | 13.3 | 5.7975 | 1.2072 | 5.8879 | 1.2796 | 30.2708 | 40.9715 | 6.4003 | 9.9837 | 100% |  |  | 100% |  |  | 82.72% | 81.55% | 20.07% | 1631586.5 | 1618000 | 4000 | 1614000 | 331.3942 | 5.4484 | 1567680.9677 | 85.87% | 19.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-07-30 | 2023 | 2022 | 2022-07-01 | 31 | 13.1833 | 5.3082 | 1.1291 | 5.4225 | 1.1965 | 30.2035 | 40.4587 | 6.3645 | 9.812 | 100% |  |  | 100% |  |  | 82.81% | 81.71% | 18.5% | 1505036.63 | 1492000 | 4000 | 1488000 | 331.3942 | 5.4484 | 1567680.9677 | 85.87% | 19.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-07-31 | 2023 | 2022 | 2022-07-01 | 31 | 13.25 | 5.9147 | 1.3242 | 6.0224 | 1.3938 | 30.3554 | 41.5605 | 6.9071 | 10.0073 | 100% |  |  | 100% |  |  | 82.67% | 81.52% | 20.52% | 1668552.5 | 1654000 | 4000 | 1650000 | 331.3942 | 5.4484 | 1567680.9677 | 85.87% | 19.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-08-01 | 2023 | 2022 | 2022-08-01 | 31 | 13.1833 | 3.9299 | 0.87199 | 4.0082 | 0.92338 | 30.2462 | 38.4987 | 5.6079 | 9.27 | 100% |  |  | 100% |  |  | 88.61% | 86.55% | 14.66% | 1190069.6 | 1183000 | 4000 | 1179000 | 331.968 | 5.6194 | 1596007.7419 | 84.76% | 19.85% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-08-02 | 2023 | 2022 | 2022-08-01 | 31 | 13.1667 | 6.3942 | 1.4105 | 6.5213 | 1.4741 | 32.2964 | 46.1116 | 4.4014 | 7.6504 | 100% |  |  | 100% |  |  | 82.59% | 83.24% | 22.23% | 1808463.2 | 1792000 | 4000 | 1788000 | 331.968 | 5.6194 | 1596007.7419 | 84.76% | 19.85% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-08-03 | 2023 | 2022 | 2022-08-01 | 31 | 13.4167 | 6.8564 | 1.5094 | 6.9756 | 1.5892 | 32.862 | 48.8292 | 3.0746 | 6.203 | 100% |  |  | 100% |  |  | 81.91% | 83.47% | 23.61% | 1920923.76 | 1904000 | 5000 | 1899000 | 332.3782 | 5.6194 | 1596007.7419 | 84.76% | 19.85% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-08-04 | 2023 | 2022 | 2022-08-01 | 31 | 12.9167 | 5.4556 | 1.2193 | 5.5662 | 1.2859 | 32.6904 | 46.644 | 3.2421 | 12.8787 | 100% |  |  | 100% |  |  | 83.69% | 85.79% | 19.26% | 1567286.1 | 1553000 | 4000 | 1549000 | 332.533 | 5.6194 | 1596007.7419 | 84.76% | 19.85% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-08-05 | 2023 | 2022 | 2022-08-01 | 31 | 13.0667 | 5.1332 | 1.075 | 5.2351 | 1.1304 | 33.0382 | 44.4892 | 2.3328 | 5.7123 | 100% |  |  | 100% |  |  | 87.18% | 87.72% | 18.88% | 1533638 | 1522000 | 4000 | 1518000 | 332.6016 | 5.6194 | 1596007.7419 | 84.76% | 19.85% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-08-06 | 2023 | 2022 | 2022-08-01 | 31 | 13.2167 | 5.7105 | 0.97508 | 5.8343 | 1.0638 | 30.71 | 43.6095 | 2.3987 | 6.3297 | 100% |  |  | 100% |  |  | 78.38% | 79.11% | 18.91% | 1539931.8 | 1526000 | 5000 | 1521000 | 332.6016 | 5.6194 | 1596007.7419 | 84.76% | 19.85% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-08-07 | 2023 | 2022 | 2022-08-01 | 31 | 12.0333 | 6.2333 | 1.2357 | 6.3652 | 1.3252 | 33.0206 | 49.5671 | 2.3417 | 5.4433 | 100% |  |  | 100% |  |  | 83.23% | 85.04% | 21.91% | 1780790.06 | 1766000 | 4000 | 1762000 | 332.6016 | 5.6194 | 1596007.7419 | 84.76% | 19.85% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-08-08 | 2023 | 2022 | 2022-08-01 | 31 | 10.3333 | 2.6245 | 0.36866 | 2.6474 | 0.39302 | 29.487 | 36.8469 | 3.4088 | 10.6628 | 100% |  |  | 100% |  |  | 89.15% | 88.16% | 9.761% | 797828.91 | 790000 | 5000 | 785000 | 332.6016 | 5.6194 | 1596007.7419 | 84.76% | 19.85% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-08-09 | 2023 | 2022 | 2022-08-01 | 31 | 13.1667 | 6.3292 | 1.0353 | 6.4514 | 1.0827 | 31.8335 | 43.4614 | 3.1453 | 8.3606 | 100% |  |  | 100% |  |  | 81.93% | 83.02% | 21.86% | 1777947 | 1762000 | 4000 | 1758000 | 332.6016 | 5.6194 | 1596007.7419 | 84.76% | 19.85% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-08-10 | 2023 | 2022 | 2022-08-01 | 31 | 13.1 | 6.8982 | 1.1557 | 7.0214 | 1.2432 | 33.5558 | 45.0205 | 4.4859 | 8.4786 | 100% |  |  | 100% |  |  | 81.58% | 82.81% | 23.74% | 1930821.46 | 1913000 | 4000 | 1909000 | 333.2747 | 5.6194 | 1596007.7419 | 84.76% | 19.85% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-08-11 | 2023 | 2022 | 2022-08-01 | 31 | 13.1833 | 6.1574 | 1.2088 | 6.2798 | 1.2889 | 32.7924 | 41.9064 | 6.4224 | 10.312 | 100% |  |  | 100% |  |  | 83.66% | 81.17% | 21.77% | 1771380.79 | 1756000 | 5000 | 1751000 | 333.2747 | 5.6194 | 1596007.7419 | 84.76% | 19.85% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-08-12 | 2023 | 2022 | 2022-08-01 | 31 | 13 | 3.632 | 0.704 | 3.712 | 0.738 | 30.592 | 36.61 | 4.768 | 10.234 | 100% |  |  | 100% |  |  | 88.35% | 86.5% | 13.59% | 1104538.43 | 1097000 | 4000 | 1093000 | 333.2747 | 5.6194 | 1596007.7419 | 84.76% | 19.85% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-08-13 | 2023 | 2022 | 2022-08-01 | 31 | 12.8667 | 1.7144 | 0.21565 | 1.7367 | 0.2366 | 26.6193 | 30.4335 | 4.686 | 9.6728 | 100% |  |  | 100% |  |  | 97.42% | 92.14% | 7.013% | 572347.23 | 568000 | 4000 | 564000 | 333.367 | 5.6194 | 1596007.7419 | 84.76% | 19.85% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-08-14 | 2023 | 2022 | 2022-08-01 | 31 | 13.1333 | 4.524 | 0.82678 | 4.6014 | 0.88085 | 27.5608 | 36.715 | 4.7184 | 8.7982 | 100% |  |  | 100% |  |  | 88.99% | 86.53% | 16.97% | 1379742.74 | 1370000 | 5000 | 1365000 | 333.367 | 5.6194 | 1596007.7419 | 84.76% | 19.85% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-08-15 | 2023 | 2022 | 2022-08-01 | 31 | 13.0167 | 5.0029 | 0.99842 | 5.1216 | 1.0518 | 29.6457 | 42.4622 | 2.0798 | 5.3363 | 100% |  |  | 100% |  |  | 87.83% | 87.51% | 18.65% | 1516239.99 | 1504000 | 4000 | 1500000 | 333.4468 | 5.6194 | 1596007.7419 | 84.76% | 19.85% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-08-16 | 2023 | 2022 | 2022-08-01 | 31 | 12.95 | 4.5272 | 0.94251 | 4.6129 | 0.9865 | 31.5307 | 38.8171 | 5.3835 | 9.6648 | 100% |  |  | 100% |  |  | 87.25% | 86.21% | 16.69% | 1355607.83 | 1346000 | 4000 | 1342000 | 333.4468 | 5.6194 | 1596007.7419 | 84.76% | 19.85% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-08-17 | 2023 | 2022 | 2022-08-01 | 31 | 12.3833 | 1.571 | 0.15312 | 1.5916 | 0.16824 | 25.8207 | 29.5322 | 3.1068 | 7.9146 | 100% |  |  | 100% |  |  | 92.89% | 88.35% | 6.13% | 503879.38 | 499000 | 6000 | 493000 | 333.4468 | 5.6194 | 1596007.7419 | 84.76% | 19.85% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-08-18 | 2023 | 2022 | 2022-08-01 | 31 | 12.7833 | 2.1627 | 0.26231 | 2.1962 | 0.29033 | 25.5116 | 28.8409 | 7.7076 | 13.5166 | 100% |  |  | 100% |  |  | 79.88% | 74.8% | 7.274% | 593370.5 | 588000 | 3000 | 585000 | 333.4468 | 5.6194 | 1596007.7419 | 84.76% | 19.85% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-08-19 | 2023 | 2022 | 2022-08-01 | 31 | 12.7167 | 4.9691 | 0.78636 | 4.8825 | 0.85292 | 29.1253 | 37.0677 | 4.8217 | 9.2693 | 100% |  |  | 100% |  |  | 82.43% | 85.46% | 16.69% | 1357118.6 | 1347000 | 5000 | 1342000 | 333.4468 | 5.6194 | 1596007.7419 | 84.76% | 19.85% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-08-20 | 2023 | 2022 | 2022-08-01 | 31 | 12.8 | 4.5743 | 0.79994 | 4.4558 | 0.86549 | 29.2052 | 36.0024 | 4.6951 | 8.776 | 100% |  |  | 100% |  |  | 82.99% | 87.76% | 15.33% | 1245788.3 | 1238000 | 5000 | 1233000 | 333.4468 | 5.6194 | 1596007.7419 | 84.76% | 19.85% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-08-21 | 2023 | 2022 | 2022-08-01 | 31 | 12.7833 | 5.3823 | 1.0138 | 5.2873 | 1.0737 | 29.7332 | 39.7774 | 4.1363 | 7.807 | 100% |  |  | 100% |  |  | 85.54% | 86.52% | 18.78% | 1526128.8 | 1514000 | 4000 | 1510000 | 333.8458 | 5.6194 | 1596007.7419 | 84.76% | 19.85% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-08-22 | 2023 | 2022 | 2022-08-01 | 31 | 12.7833 | 4.111 | 0.66342 | 4.1956 | 0.714 | 27.3637 | 36.2777 | 4.1919 | 8.932 | 100% |  |  | 100% |  |  | 87.03% | 84.78% | 15.16% | 1233767.6 | 1224000 | 5000 | 1219000 | 333.8458 | 5.6194 | 1596007.7419 | 84.76% | 19.85% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-08-23 | 2023 | 2022 | 2022-08-01 | 31 | 12.15 | 5.3185 | 0.95546 | 5.2753 | 1.0184 | 30.8367 | 39.4018 | 4.2872 | 8.936 | 100% |  |  | 100% |  |  | 82.9% | 85.75% | 18.15% | 1477333.2 | 1465000 | 5000 | 1460000 | 333.8458 | 5.6194 | 1596007.7419 | 84.76% | 19.85% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-08-24 | 2023 | 2022 | 2022-08-01 | 31 | 12.5333 | 4.177 | 0.65423 | 4.0892 | 0.70953 | 28.5208 | 34.7889 | 4.4728 | 8.8893 | 100% |  |  | 100% |  |  | 77.82% | 85.33% | 13.22% | 1075676.8 | 1067000 | 4000 | 1063000 | 334.0397 | 5.6194 | 1596007.7419 | 84.76% | 19.85% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-08-25 | 2023 | 2022 | 2022-08-01 | 31 | 12.6 | 4.4628 | 0.71824 | 4.5667 | 0.7743 | 27.3107 | 36.9499 | 5.3176 | 8.9442 | 100% |  |  | 100% |  |  | 85.65% | 83.31% | 16.25% | 1320005.2 | 1310000 | 3000 | 1307000 | 334.1698 | 5.6194 | 1596007.7419 | 84.76% | 19.85% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-08-26 | 2023 | 2022 | 2022-08-01 | 31 | 12.8 | 5.8636 | 1.1877 | 6.0746 | 1.2483 | 28.8295 | 41.7605 | 4.3336 | 8.1487 | 100% |  |  | 100% |  |  | 81.68% | 81.2% | 20.62% | 1678865.38 | 1663000 | 5000 | 1658000 | 334.1698 | 5.6194 | 1596007.7419 | 84.76% | 19.85% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-08-27 | 2023 | 2022 | 2022-08-01 | 31 | 12.85 | 6.1607 | 1.334 | 6.3853 | 1.3874 | 29.3223 | 41.5276 | 4.6159 | 7.6227 | 100% |  |  | 100% |  |  | 82.01% | 81.6% | 21.76% | 1768985.4 | 1754000 | 4000 | 1750000 | 334.1698 | 5.6194 | 1596007.7419 | 84.76% | 19.85% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-08-28 | 2023 | 2022 | 2022-08-01 | 31 | 12.75 | 6.5424 | 1.3725 | 6.5598 | 1.4089 | 30.3175 | 44.0298 | 4.0527 | 7.93 | 100% |  |  | 100% |  |  | 83.39% | 82.22% | 22.73% | 1842054.48 | 1832000 | 4000 | 1828000 | 334.1907 | 5.6194 | 1596007.7419 | 84.76% | 19.85% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-08-29 | 2023 | 2022 | 2022-08-01 | 31 | 12.6 | 5.5683 | 1.2315 | 5.7558 | 1.2787 | 29.966 | 43.5557 | 3.1589 | 5.7063 | 100% |  |  | 100% |  |  | 82.82% | 83.25% | 19.81% | 1619150.3 | 1599000 | 6000 | 1593000 | 334.1907 | 5.6194 | 1596007.7419 | 84.76% | 19.85% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-08-30 | 2023 | 2022 | 2022-08-01 | 31 | 12.7167 | 6.4833 | 1.3984 | 6.7352 | 1.4483 | 31.8702 | 48.1006 | 2.3521 | 5.0233 | 100% |  |  | 100% |  |  | 83.12% | 84.58% | 23.26% | 1890106.7 | 1874000 | 3000 | 1871000 | 334.2011 | 5.6194 | 1596007.7419 | 84.76% | 19.85% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-08-31 | 2023 | 2022 | 2022-08-01 | 31 | 12.75 | 6.6225 | 1.4618 | 6.8848 | 1.5073 | 32.0551 | 46.5346 | 4.0182 | 6.6817 | 100% |  |  | 100% |  |  | 83.14% | 84.19% | 23.79% | 1933758.61 | 1916910 | 4000 | 1912910 | 334.2011 | 5.6194 | 1596007.7419 | 84.76% | 19.85% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-09-01 | 2023 | 2022 | 2022-09-01 | 30 | 12.6667 | 6.9268 | 1.5205 | 7.2224 | 1.5651 | 31.6465 | 45.7474 | 4.986 | 8.564 | 100% |  |  | 100% |  |  | 82.49% | 82.93% | 24.76% | 2011903.65 | 1996090 | 5000 | 1991090 | 334.2011 | 6.4033 | 1794672 | 83.64% | 22.32% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-09-02 | 2023 | 2022 | 2022-09-01 | 30 | 12.7167 | 6.774 | 1.4922 | 7.0376 | 1.5375 | 31.5219 | 47.3741 | 3.8653 | 6.597 | 100% |  |  | 100% |  |  | 80.74% | 81.3% | 23.61% | 1920505.7 | 1902000 | 3000 | 1899000 | 334.2011 | 6.4033 | 1794672 | 83.64% | 22.32% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-09-03 | 2023 | 2022 | 2022-09-01 | 30 | 12.7 | 7.0534 | 1.5544 | 7.3589 | 1.5987 | 31.9619 | 45.2976 | 6.1963 | 9.8943 | 100% |  |  | 100% |  |  | 81.57% | 81.49% | 24.94% | 2027201.54 | 2008000 | 2000 | 2006000 | 334.2011 | 6.4033 | 1794672 | 83.64% | 22.32% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-09-04 | 2023 | 2022 | 2022-09-01 | 30 | 12.3833 | 5.4621 | 1.2515 | 5.6673 | 1.3023 | 29.6107 | 40.2791 | 7.3081 | 10.8713 | 100% |  |  | 100% |  |  | 80.83% | 79.43% | 19.04% | 1548250.39 | 1535000 | 4000 | 1531000 | 334.2011 | 6.4033 | 1794672 | 83.64% | 22.32% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-09-05 | 2023 | 2022 | 2022-09-01 | 30 | 12.6167 | 6.1621 | 1.3874 | 6.4124 | 1.4374 | 29.6715 | 43.338 | 5.3067 | 8.6893 | 100% |  |  | 100% |  |  | 68.32% | 67.53% | 18.2% | 1474409.1 | 1467000 | 3000 | 1464000 | 334.1957 | 6.4033 | 1794672 | 83.64% | 22.32% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-09-06 | 2023 | 2022 | 2022-09-01 | 30 | 12.6167 | 6.2858 | 1.4603 | 6.6731 | 1.447 | 30.5107 | 46.2083 | 3.1603 | 6.6077 | 100% |  |  | 100% |  |  | 78.61% | 79.29% | 21.8% | 1771556.2 | 1757000 | 4000 | 1753000 | 334.1957 | 6.4033 | 1794672 | 83.64% | 22.32% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-09-07 | 2023 | 2022 | 2022-09-01 | 30 | 12.5333 | 6.7215 | 1.4648 | 7.052 | 1.5299 | 32.3554 | 49.4793 | 1.9819 | 4.9977 | 100% |  |  | 100% |  |  | 80.79% | 82.36% | 23.68% | 1921575.17 | 1908000 | 4000 | 1904000 | 334.1957 | 6.4033 | 1794672 | 83.64% | 22.32% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-09-08 | 2023 | 2022 | 2022-09-01 | 30 | 12.5 | 6.7582 | 1.4372 | 7.0699 | 1.506 | 34.4271 | 48.9951 | 2.8297 | 5.813 | 100% |  |  | 100% |  |  | 80.92% | 82.48% | 23.77% | 1931242.7 | 1914000 | 2000 | 1912000 | 334.1957 | 6.4033 | 1794672 | 83.64% | 22.32% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-09-09 | 2023 | 2022 | 2022-09-01 | 30 | 12.4333 | 6.5957 | 1.4134 | 6.8942 | 1.4812 | 35.4719 | 51.3347 | 2.1688 | 5.3763 | 100% |  |  | 100% |  |  | 80.82% | 81.06% | 23.15% | 1883529.22 | 1866000 | 4000 | 1862000 | 334.1957 | 6.4033 | 1794672 | 83.64% | 22.32% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-09-10 | 2023 | 2022 | 2022-09-01 | 30 | 12.5167 | 5.8355 | 1.2551 | 6.0843 | 1.3174 | 35.4137 | 49.8033 | 1.8396 | 6.6727 | 100% |  |  | 100% |  |  | 81.64% | 83.43% | 20.64% | 1678457.53 | 1664000 | 4000 | 1660000 | 334.1957 | 6.4033 | 1794672 | 83.64% | 22.32% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-09-11 | 2023 | 2022 | 2022-09-01 | 30 | 12.6333 | 5.4656 | 1.1844 | 5.7231 | 1.2444 | 33.0179 | 46.2523 | 2.9533 | 10.732 | 100% |  |  | 100% |  |  | 83.24% | 84.67% | 19.8% | 1608678.7 | 1597000 | 5000 | 1592000 | 334.1957 | 6.4033 | 1794672 | 83.64% | 22.32% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-09-12 | 2023 | 2022 | 2022-09-01 | 30 | 12.4833 | 6.0725 | 1.285 | 6.3759 | 1.3472 | 32.7521 | 47.3763 | 3.4371 | 12.5813 | 100% |  |  | 100% |  |  | 81.47% | 82.32% | 21.59% | 1752214.2 | 1740000 | 4000 | 1736000 | 334.1957 | 6.4033 | 1794672 | 83.64% | 22.32% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-09-13 | 2023 | 2022 | 2022-09-01 | 30 | 12.3333 | 5.8453 | 1.1961 | 6.1184 | 1.2539 | 33.4836 | 45.8394 | 3.8497 | 7.9633 | 100% |  |  | 100% |  |  | 81.53% | 82.24% | 20.73% | 1686677.32 | 1670000 | 3000 | 1667000 | 334.1957 | 6.4033 | 1794672 | 83.64% | 22.32% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-09-14 | 2023 | 2022 | 2022-09-01 | 30 | 12.2167 | 6.1657 | 1.2557 | 6.454 | 1.316 | 33.5768 | 46.8522 | 3.6541 | 7.3152 | 100% |  |  | 100% |  |  | 81.78% | 82.48% | 21.93% | 1780868.7 | 1769000 | 5000 | 1764000 | 334.1957 | 6.4033 | 1794672 | 83.64% | 22.32% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-09-15 | 2023 | 2022 | 2022-09-01 | 30 | 12.3667 | 6.1556 | 1.2759 | 6.4656 | 1.3386 | 33.7346 | 49.1497 | 2.2689 | 5.5148 | 100% |  |  | 100% |  |  | 82.24% | 83.57% | 22.1% | 1798019.2 | 1781000 | 4000 | 1777000 | 334.1957 | 6.4033 | 1794672 | 83.64% | 22.32% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-09-16 | 2023 | 2022 | 2022-09-01 | 30 | 12.35 | 6.6263 | 1.4001 | 6.9712 | 1.4661 | 31.2993 | 45.9141 | 4.9897 | 8.2092 | 100% |  |  | 100% |  |  | 81.9% | 82.18% | 23.72% | 1930491.11 | 1912000 | 4000 | 1908000 | 334.1957 | 6.4033 | 1794672 | 83.64% | 22.32% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-09-17 | 2023 | 2022 | 2022-09-01 | 30 | 12.3167 | 6.6024 | 1.4051 | 6.9425 | 1.4689 | 30.5221 | 44.1932 | 6.2569 | 10.4296 | 100% |  |  | 100% |  |  | 82.06% | 81.8% | 23.68% | 1927509.47 | 1908000 | 4000 | 1904000 | 334.1957 | 6.4033 | 1794672 | 83.64% | 22.32% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-09-18 | 2023 | 2022 | 2022-09-01 | 30 | 12.2667 | 6.6897 | 1.3986 | 7.051 | 1.4657 | 30.9008 | 47.1561 | 2.6936 | 5.804 | 100% |  |  | 100% |  |  | 81.73% | 82.6% | 23.95% | 1948542.3 | 1930000 | 4000 | 1926000 | 334.1957 | 6.4033 | 1794672 | 83.64% | 22.32% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-09-19 | 2023 | 2022 | 2022-09-01 | 30 | 12.3 | 6.7879 | 1.4287 | 7.1588 | 1.4937 | 31.9488 | 46.2171 | 4.2113 | 7.4002 | 100% |  |  | 100% |  |  | 81.72% | 82.48% | 24.31% | 1978975.5 | 1960000 | 5000 | 1955000 | 334.1957 | 6.4033 | 1794672 | 83.64% | 22.32% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-09-20 | 2023 | 2022 | 2022-09-01 | 30 | 12.2833 | 6.5568 | 1.3758 | 6.9384 | 1.4312 | 31.4559 | 45.9223 | 4.6689 | 8.1908 | 100% |  |  | 100% |  |  | 83.32% | 82.27% | 24.02% | 1954745.7 | 1936000 | 4000 | 1932000 | 334.1957 | 6.4033 | 1794672 | 83.64% | 22.32% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-09-21 | 2023 | 2022 | 2022-09-01 | 30 | 12.2667 | 6.6171 | 1.3833 | 7.0432 | 1.4462 | 31.938 | 46.8789 | 3.7419 | 6.3412 | 100% |  |  | 100% |  |  | 81.99% | 82.9% | 24% | 1952150.61 | 1934000 | 4000 | 1930000 | 334.1957 | 6.4033 | 1794672 | 83.64% | 22.32% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-09-22 | 2023 | 2022 | 2022-09-01 | 30 | 12.3333 | 6.4315 | 1.3476 | 6.8098 | 1.4136 | 32.5573 | 45.7922 | 3.9704 | 6.2808 | 100% |  |  | 100% |  |  | 82.74% | 83.63% | 23.41% | 1904289 | 1887000 | 4000 | 1883000 | 334.1957 | 6.4033 | 1794672 | 83.64% | 22.32% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-09-23 | 2023 | 2022 | 2022-09-01 | 30 | 12.2 | 6.4 | 1.3302 | 6.7839 | 1.395 | 32.9459 | 46.9902 | 3.8927 | 7.1582 | 100% |  |  | 100% |  |  | 82.35% | 83.39% | 23.22% | 1887345.6 | 1871000 | 4000 | 1867000 | 334.1957 | 6.4033 | 1794672 | 83.64% | 22.32% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-09-24 | 2023 | 2022 | 2022-09-01 | 30 | 12.15 | 6.4701 | 1.3523 | 6.8668 | 1.4124 | 30.6034 | 42.6627 | 5.0814 | 7.9976 | 100% |  |  | 100% |  |  | 83.32% | 82.22% | 23.77% | 1933815.5 | 1916000 | 4000 | 1912000 | 334.1957 | 6.4033 | 1794672 | 83.64% | 22.32% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-09-25 | 2023 | 2022 | 2022-09-01 | 30 | 12.15 | 5.8366 | 1.2516 | 6.1676 | 1.3102 | 29.47 | 41.9244 | 5.7538 | 9.3188 | 100% |  |  | 100% |  |  | 80.59% | 80.02% | 20.65% | 1681711.5 | 1666000 | 5000 | 1661000 | 334.1957 | 6.4033 | 1794672 | 83.64% | 22.32% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-09-26 | 2023 | 2022 | 2022-09-01 | 30 | 12.1333 | 5.7991 | 1.2214 | 6.1397 | 1.276 | 29.9208 | 44.5646 | 2.4037 | 6.0527 | 100% |  |  | 100% |  |  | 82.51% | 82.37% | 21.05% | 1711826.31 | 1697000 | 4000 | 1693000 | 334.1957 | 6.4033 | 1794672 | 83.64% | 22.32% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-09-27 | 2023 | 2022 | 2022-09-01 | 30 | 12.0833 | 6.1286 | 1.2816 | 6.5176 | 1.3341 | 31.4207 | 45.6235 | 3.619 | 6.6467 | 100% |  |  | 100% |  |  | 82.82% | 83.23% | 22.43% | 1824409.41 | 1808000 | 4000 | 1804000 | 334.1957 | 6.4033 | 1794672 | 83.64% | 22.32% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-09-28 | 2023 | 2022 | 2022-09-01 | 30 | 12.0833 | 6.2903 | 1.3056 | 6.7039 | 1.3637 | 31.4825 | 46.0274 | 3.9643 | 7.648 | 100% |  |  | 100% |  |  | 82.44% | 82.9% | 22.97% | 1869691.1 | 1852000 | 5000 | 1847000 | 334.1957 | 6.4033 | 1794672 | 83.64% | 22.32% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-09-29 | 2023 | 2022 | 2022-09-01 | 30 | 12.05 | 6.6288 | 1.3627 | 6.9292 | 1.4119 | 32.046 | 47.7704 | 3.4045 | 6.4993 | 100% |  |  | 100% |  |  | 82.31% | 83.3% | 23.7% | 1927909.82 | 1910000 | 4000 | 1906000 | 334.1957 | 6.4033 | 1794672 | 83.64% | 22.32% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-09-30 | 2023 | 2022 | 2022-09-01 | 30 | 12.0167 | 6.6377 | 1.365 | 6.812 | 1.5318 | 32.4481 | 46.6005 | 3.7046 | 6.8507 | 100% |  |  | 100% |  |  | 80.74% | 82.13% | 22.85% | 1859641 | 1843000 | 5000 | 1838000 | 334.1957 | 6.4033 | 1794672 | 83.64% | 22.32% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-10-01 | 2023 | 2022 | 2022-10-01 | 31 | 12 | 6.5695 | 1.3773 | 7.0561 | 1.4443 | 32.6737 | 46.2393 | 4.9484 | 8.3536 | 100% |  |  | 100% |  |  | -828.5% | 82.91% | -242.9% | 1944478.2 | -19655916 | -118933 | -19536983 | 334.1957 | 6.5258 | 1822174.8387 | 83.33% | 22.66% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-10-02 | 2023 | 2022 | 2022-10-01 | 31 | 11.9833 | 6.5794 | 1.3664 | 7.0726 | 1.4393 | 30.6678 | 45.0281 | 5.0867 | 8.4472 | 100% |  |  | 100% |  |  | 81.42% | 82.08% | 23.93% | 1945852.2 | 1928934 | 4400 | 1924534 | 334.1957 | 6.5258 | 1822174.8387 | 83.33% | 22.66% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-10-03 | 2023 | 2022 | 2022-10-01 | 31 | 11.9833 | 6.2683 | 1.3081 | 6.7578 | 1.3665 | 31.113 | 45.9212 | 3.302 | 6.2028 | 100% |  |  | 100% |  |  | 82.62% | 83.78% | 23.2% | 1886679.5 | 1870400 | 4466 | 1865934 | 334.1957 | 6.5258 | 1822174.8387 | 83.33% | 22.66% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-10-04 | 2023 | 2022 | 2022-10-01 | 31 | 11.9 | 6.3964 | 1.3512 | 7.0076 | 1.4092 | 32.3634 | 48.2526 | 2.3123 | 5.1128 | 100% |  |  | 100% |  |  | 80.69% | 82.92% | 23.5% | 1910465.9 | 1894067 | 4467 | 1889600 | 334.1957 | 6.5258 | 1822174.8387 | 83.33% | 22.66% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-10-05 | 2023 | 2022 | 2022-10-01 | 31 | 11.9333 | 6.4733 | 1.3796 | 7.1067 | 1.4434 | 32.8437 | 46.4043 | 3.0958 | 5.8936 | 100% |  |  | 100% |  |  | 81.4% | 83.5% | 24.04% | 1953988.6 | 1937600 | 4333 | 1933267 | 334.1957 | 6.5258 | 1822174.8387 | 83.33% | 22.66% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-10-06 | 2023 | 2022 | 2022-10-01 | 31 | 11.8833 | 6.3129 | 1.3188 | 6.9484 | 1.4074 | 33.3076 | 47.621 | 2.4771 | 5.2482 | 100% |  |  | 100% |  |  | 81.24% | 83.73% | 23.46% | 1906833 | 1890667 | 4134 | 1886533 | 334.1957 | 6.5258 | 1822174.8387 | 83.33% | 22.66% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-10-07 | 2023 | 2022 | 2022-10-01 | 31 | 11.65 | 5.7866 | 1.2077 | 6.153 | 1.299 | 33.4284 | 45.4015 | 4.0217 | 8.1686 | 100% |  |  | 100% |  |  | 82.75% | 84.52% | 21.16% | 1720488 | 1706200 | 4533 | 1701667 | 334.1957 | 6.5258 | 1822174.8387 | 83.33% | 22.66% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-10-08 | 2023 | 2022 | 2022-10-01 | 31 | 11.7333 | 4.9187 | 1.0499 | 5.228 | 1.0918 | 30.7913 | 40.3878 | 4.4904 | 8.7514 | 100% |  |  | 100% |  |  | 84.4% | 84.09% | 18.33% | 1490888.3 | 1479067 | 4533 | 1474534 | 334.1957 | 6.5258 | 1822174.8387 | 83.33% | 22.66% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-10-09 | 2023 | 2022 | 2022-10-01 | 31 | 11.8167 | 6.0915 | 1.2553 | 6.5169 | 1.3282 | 29.8485 | 42.6016 | 3.6702 | 6.9348 | 100% |  |  | 100% |  |  | 84.55% | 85.01% | 22.9% | 1861983.9 | 1846000 | 4667 | 1841333 | 334.1957 | 6.5258 | 1822174.8387 | 83.33% | 22.66% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-10-10 | 2023 | 2022 | 2022-10-01 | 31 | 11.8 | 5.9209 | 1.2416 | 6.3193 | 1.3178 | 31.548 | 45.7071 | 2.3404 | 5.6022 | 100% |  |  | 100% |  |  | 85.2% | 86.7% | 22.37% | 1819215.2 | 1803933 | 4533 | 1799400 | 334.1957 | 6.5258 | 1822174.8387 | 83.33% | 22.66% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-10-11 | 2023 | 2022 | 2022-10-01 | 31 | 11.7667 | 6.1181 | 1.0588 | 6.5549 | 1.3906 | 32.3354 | 46.9405 | 1.7989 | 4.9538 | 100% |  |  | 100% |  |  | 84.36% | 86.5% | 22.98% | 1866293.2 | 1850867 | 2800 | 1848067 | 334.1957 | 6.5258 | 1822174.8387 | 83.33% | 22.66% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-10-12 | 2023 | 2022 | 2022-10-01 | 31 | 11.75 | 5.1401 | 0.82649 | 5.5133 | 1.1466 | 29.7227 | 44.1284 | 2.041 | 5.3444 | 100% |  |  | 100% |  |  | 86.78% | 87.79% | 19.88% | 1616750.9 | 1603467 | 4467 | 1599000 | 334.1957 | 6.5258 | 1822174.8387 | 83.33% | 22.66% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-10-13 | 2023 | 2022 | 2022-10-01 | 31 | 11.75 | 5.9556 | 1.2352 | 6.7353 | 1.3837 | 32.5202 | 47.8615 | 1.9322 | 5.6339 | 100% |  |  | 100% |  |  | 81.96% | 84.43% | 22.94% | 1866743.7 | 1851200 | 6333 | 1844867 | 334.1957 | 6.5258 | 1822174.8387 | 83.33% | 22.66% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-10-14 | 2023 | 2022 | 2022-10-01 | 31 | 11.7333 | 5.9818 | 1.3283 | 6.7917 | 1.3946 | 32.0652 | 46.7183 | 2.0861 | 5.91 | 100% |  |  | 100% |  |  | 81.43% | 83.7% | 22.98% | 1866242.1 | 1850800 | 2534 | 1848266 | 334.1957 | 6.5258 | 1822174.8387 | 83.33% | 22.66% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-10-15 | 2023 | 2022 | 2022-10-01 | 31 | 11.7 | 6.0617 | 1.126 | 6.892 | 1.4164 | 32.1143 | 47.1942 | 1.9018 | 5.8014 | 100% |  |  | 100% |  |  | 80.98% | 83.52% | 23.19% | 1887665.4 | 1871734 | 6533 | 1865201 | 334.1957 | 6.5258 | 1822174.8387 | 83.33% | 22.66% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-10-16 | 2023 | 2022 | 2022-10-01 | 31 | 11.6667 | 5.9375 | 1.331 | 6.7528 | 1.3953 | 32.0566 | 46.2863 | 2.5252 | 6.105 | 100% |  |  | 100% |  |  | 81.89% | 83.78% | 22.98% | 1866037.2 | 1850600 | 2600 | 1848000 | 334.1957 | 6.5258 | 1822174.8387 | 83.33% | 22.66% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-10-17 | 2023 | 2022 | 2022-10-01 | 31 | 11.65 | 5.9135 | 1.3307 | 6.7371 | 1.397 | 31.6383 | 46.7793 | 1.9386 | 5.3272 | 100% |  |  | 100% |  |  | 81.77% | 83.96% | 22.89% | 1860813.3 | 1845667 | 4667 | 1841000 | 334.1957 | 6.5258 | 1822174.8387 | 83.33% | 22.66% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-10-18 | 2023 | 2022 | 2022-10-01 | 31 | 11.6333 | 5.8381 | 1.3142 | 6.6584 | 1.3781 | 31.9985 | 46.7127 | 2.349 | 5.5804 | 100% |  |  | 100% |  |  | 81.96% | 84.05% | 22.68% | 1843260.5 | 1828466 | 4666 | 1823800 | 334.1957 | 6.5258 | 1822174.8387 | 83.33% | 22.66% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-10-19 | 2023 | 2022 | 2022-10-01 | 31 | 11.65 | 5.833 | 1.3172 | 6.671 | 1.3832 | 32.2337 | 46.33 | 3.1584 | 6.006 | 100% |  |  | 100% |  |  | 82.1% | 83.96% | 22.76% | 1850110.4 | 1834867 | 4600 | 1830267 | 334.1957 | 6.5258 | 1822174.8387 | 83.33% | 22.66% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-10-20 | 2023 | 2022 | 2022-10-01 | 31 | 11.55 | 5.5861 | 1.2677 | 6.3747 | 1.3302 | 30.9542 | 44.4322 | 3.7358 | 8.2424 | 100% |  |  | 100% |  |  | 83.11% | 84.1% | 22.02% | 1792362.2 | 1777467 | 6800 | 1770667 | 334.1957 | 6.5258 | 1822174.8387 | 83.33% | 22.66% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-10-21 | 2023 | 2022 | 2022-10-01 | 31 | 11.4833 | 5.3727 | 1.2105 | 6.1292 | 1.2707 | 31.0585 | 43.9719 | 2.5199 | 4.8384 | 100% |  |  | 100% |  |  | 84.34% | 85.55% | 21.48% | 1744170.1 | 1730067 | 2534 | 1727533 | 334.1957 | 6.5258 | 1822174.8387 | 83.33% | 22.66% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-10-22 | 2023 | 2022 | 2022-10-01 | 31 | 11.4833 | 5.482 | 1.2626 | 6.2787 | 1.3226 | 31.4974 | 45.6346 | 2.3096 | 5.4652 | 100% |  |  | 100% |  |  | 83.25% | 85% | 21.72% | 1768330.7 | 1753733 | 6866 | 1746867 | 334.1957 | 6.5258 | 1822174.8387 | 83.33% | 22.66% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-10-23 | 2023 | 2022 | 2022-10-01 | 31 | 11.4833 | 5.5956 | 1.2729 | 6.4355 | 1.335 | 31.1935 | 45.5335 | 1.9425 | 5.071 | 100% |  |  | 100% |  |  | 82.64% | 84.46% | 22.1% | 1799556.4 | 1782267 | 4934 | 1777333 | 334.1957 | 6.5258 | 1822174.8387 | 83.33% | 22.66% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-10-24 | 2023 | 2022 | 2022-10-01 | 31 | 11.4667 | 5.5561 | 1.2617 | 6.3969 | 1.3236 | 30.9482 | 44.9883 | 2.0361 | 5.3688 | 100% |  |  | 100% |  |  | 82.68% | 84.38% | 21.98% | 1789639 | 1772334 | 4800 | 1767534 | 334.1957 | 6.5258 | 1822174.8387 | 83.33% | 22.66% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-10-25 | 2023 | 2022 | 2022-10-01 | 31 | 11.4167 | 5.4744 | 1.2486 | 6.3007 | 1.3097 | 31.1883 | 43.6441 | 4.4443 | 8.3682 | 100% |  |  | 100% |  |  | 83.06% | 83.94% | 21.75% | 1771270.5 | 1753733 | 4866 | 1748867 | 334.1957 | 6.5258 | 1822174.8387 | 83.33% | 22.66% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-10-26 | 2023 | 2022 | 2022-10-01 | 31 | 11.3833 | 5.4411 | 1.2476 | 6.2823 | 1.2965 | 30.7593 | 44.6656 | 4.1688 | 7.4554 | 100% |  |  | 100% |  |  | 83.05% | 83.88% | 21.68% | 1766429.4 | 1748467 | 4867 | 1743600 | 334.1957 | 6.5258 | 1822174.8387 | 83.33% | 22.66% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-10-27 | 2023 | 2022 | 2022-10-01 | 31 | 11.3333 | 5.4101 | 1.2328 | 6.2633 | 1.2848 | 30.5046 | 44.4323 | 3.6329 | 7.7132 | 100% |  |  | 100% |  |  | 83.27% | 84.11% | 21.67% | 1763357.7 | 1747933 | 4867 | 1743066 | 334.1957 | 6.5258 | 1822174.8387 | 83.33% | 22.66% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-10-28 | 2023 | 2022 | 2022-10-01 | 31 | 11.3833 | 5.2673 | 1.1858 | 6.0825 | 1.2433 | 30.9804 | 43.8678 | 2.8556 | 5.3548 | 100% |  |  | 100% |  |  | 83.99% | 85.11% | 21.23% | 1728106.3 | 1712067 | 4866 | 1707201 | 334.1957 | 6.5258 | 1822174.8387 | 83.33% | 22.66% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-10-29 | 2023 | 2022 | 2022-10-01 | 31 | 11.3833 | 5.0905 | 1.1513 | 5.8907 | 1.2099 | 30.5 | 44.0158 | 2.1759 | 4.547 | 100% |  |  | 100% |  |  | 84.46% | 85.65% | 20.67% | 1683677.9 | 1667467 | 4800 | 1662667 | 334.1957 | 6.5258 | 1822174.8387 | 83.33% | 22.66% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-10-30 | 2023 | 2022 | 2022-10-01 | 31 | 11.2333 | 5.322 | 1.1974 | 6.2089 | 1.2567 | 30.7661 | 45.0896 | 1.9384 | 4.6844 | 100% |  |  | 100% |  |  | 83.67% | 85.3% | 21.59% | 1757408.9 | 1741133 | 4934 | 1736199 | 334.1957 | 6.5258 | 1822174.8387 | 83.33% | 22.66% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-10-31 | 2023 | 2022 | 2022-10-01 | 31 | 11.2833 | 5.3177 | 1.217 | 6.2116 | 1.2779 | 31.5639 | 45.5741 | 2.3128 | 5.4514 | 100% |  |  | 100% |  |  | 83.71% | 85.4% | 21.61% | 1758467.6 | 1742667 | 5000 | 1737667 | 334.1957 | 6.5258 | 1822174.8387 | 83.33% | 22.66% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-11-01 | 2023 | 2022 | 2022-11-01 | 30 | 11.1833 | 5.3041 | 1.2149 | 6.1642 | 1.2723 | 31.8631 | 45.0654 | 3.0924 | 5.6066 | 100% |  |  | 100% |  |  | 84.04% | 87.9% | 21.53% | 1752112.1 | 1736267 | 5000 | 1731267 | 334.1957 | 5.43 | 1595616 | 87.69% | 19.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-11-02 | 2023 | 2022 | 2022-11-01 | 30 | 11.1167 | 5.2129 | 1.1825 | 5.9782 | 1.2377 | 31.3504 | 45.259 | 2.6414 | 5.4044 | 100% |  |  | 100% |  |  | 85.34% | 89.15% | 21.2% | 1725584.4 | 1709933 | 4866 | 1705067 | 334.1957 | 5.43 | 1595616 | 87.69% | 19.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-11-03 | 2023 | 2022 | 2022-11-01 | 30 | 11.2667 | 5.2844 | 1.2028 | 5.9408 | 1.2538 | 33.1231 | 45.4922 | 4.2374 | 7.0593 | 100% |  |  | 100% |  |  | 87.75% | 91.47% | 21.66% | 1763079.4 | 1747067 | 4867 | 1742200 | 334.1957 | 5.43 | 1595616 | 87.69% | 19.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-11-04 | 2023 | 2022 | 2022-11-01 | 30 | 11.3 | 5.5118 | 1.247 | 6.4749 | 1.3054 | 32.5112 | 45.672 | 3.8687 | 8.6847 | 100% |  |  | 100% |  |  | 82.8% | 86.83% | 22.28% | 1812786.3 | 1796667 | 5000 | 1791667 | 334.1957 | 5.43 | 1595616 | 87.69% | 19.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-11-05 | 2023 | 2022 | 2022-11-01 | 30 | 11.2167 | 5.4956 | 1.2727 | 6.5468 | 1.3323 | 32.636 | 44.0999 | 5.5562 | 10.5196 | 100% |  |  | 100% |  |  | 80.11% | 83.3% | 21.79% | 1770942.1 | 1755267 | 2600 | 1752667 | 334.1957 | 5.43 | 1595616 | 87.69% | 19.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-11-06 | 2023 | 2022 | 2022-11-01 | 30 | 11.0833 | 4.113 | 0.95434 | 4.6339 | 1.0027 | 30.783 | 39.8721 | 3.4151 | 7.7247 | 100% |  |  | 100% |  |  | 86.27% | 88.76% | 16.61% | 1354520.8 | 1343067 | 7067 | 1336000 | 334.1957 | 5.43 | 1595616 | 87.69% | 19.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-11-07 | 2023 | 2022 | 2022-11-01 | 30 | 10.9 | 4.304 | 1.0034 | 4.9862 | 1.0551 | 28.2383 | 41.1888 | 2.4599 | 6.1185 | 100% |  |  | 100% |  |  | 85.06% | 87.22% | 17.62% | 1432715.7 | 1420200 | 2800 | 1417400 | 334.1957 | 5.43 | 1595616 | 87.69% | 19.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-11-08 | 2023 | 2022 | 2022-11-01 | 30 | 10.9833 | 4.5437 | 1.0621 | 5.2916 | 1.1141 | 28.6215 | 41.1667 | 2.9302 | 7.0612 | 100% |  |  | 100% |  |  | 84.88% | 87.26% | 18.66% | 1519971 | 1506067 | 5000 | 1501067 | 334.1957 | 5.43 | 1595616 | 87.69% | 19.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-11-09 | 2023 | 2022 | 2022-11-01 | 30 | 10.9833 | 4.4596 | 1.0422 | 5.2247 | 1.0931 | 27.8011 | 51.7908 | 2.8162 | 6.1568 | 100% |  |  | 100% |  |  | 85.46% | 87.26% | 18.55% | 1510287.2 | 1496933 | 4733 | 1492200 | 334.1957 | 5.43 | 1595616 | 87.69% | 19.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-11-10 | 2023 | 2022 | 2022-11-01 | 30 | 11.0833 | 4.6075 | 1.0831 | 5.428 | 1.201 | 27.3865 | 38.396 | 2.9717 | 5.6475 | 100% |  |  | 100% |  |  | 86.42% | 88.44% | 19.49% | 1588351 | 1574600 | 7000 | 1567600 | 334.1957 | 5.43 | 1595616 | 87.69% | 19.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-11-11 | 2023 | 2022 | 2022-11-01 | 30 | 10.9167 | 4.2428 | 1.021 | 4.9483 | 1.1352 | 26.6233 | 38.3746 | 1.958 | 4.2419 | 100% |  |  | 100% |  |  | 85.62% | 87.28% | 17.61% | 1433158.4 | 1420734 | 4800 | 1415934 | 334.1957 | 5.43 | 1595616 | 87.69% | 19.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-11-12 | 2023 | 2022 | 2022-11-01 | 30 | 10.95 | 4.6594 | 1.1086 | 5.5253 | 1.1974 | 26.926 | 40.4953 | 1.7081 | 4.4136 | 100% |  |  | 100% |  |  | 85.55% | 87.8% | 19.64% | 1598252.7 | 1584600 | 4800 | 1579800 | 334.1957 | 5.43 | 1595616 | 87.69% | 19.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-11-13 | 2023 | 2022 | 2022-11-01 | 30 | 10.9167 | 4.8162 | 1.1218 | 5.757 | 1.1765 | 27.9698 | 41.984 | 2.3655 | 5.3047 | 100% |  |  | 100% |  |  | 85.11% | 87.66% | 20.36% | 1657660.6 | 1642333 | 4800 | 1637533 | 334.1957 | 5.43 | 1595616 | 87.69% | 19.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-11-14 | 2023 | 2022 | 2022-11-01 | 30 | 11.0167 | 4.6628 | 1.1072 | 5.5548 | 1.184 | 27.6212 | 39.664 | 4.1938 | 8.3133 | 100% |  |  | 100% |  |  | 85.98% | 87.64% | 19.85% | 1616206.9 | 1601000 | 4933 | 1596067 | 334.1957 | 5.43 | 1595616 | 87.69% | 19.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-11-15 | 2023 | 2022 | 2022-11-01 | 30 | 10.9833 | 4.1341 | 0.99442 | 4.8346 | 1.555 | 22.8012 | 31.9495 | 3.7154 | 5.7481 | 100% |  |  | 100% |  |  | 88.37% | 88.1% | 17.75% | 1445347.1 | 1432534 | 4800 | 1427734 | 334.1957 | 5.43 | 1595616 | 87.69% | 19.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-11-16 | 2023 | 2022 | 2022-11-01 | 30 | 10.9833 | 4.5159 | 1.0469 | 5.3823 | 1.2532 | 24.6563 | 38.5386 | 1.7054 | 4.0131 | 100% |  |  | 100% |  |  | 86.64% | 88.12% | 19.38% | 1577419 | 1563266 | 4800 | 1558466 | 334.1957 | 5.43 | 1595616 | 87.69% | 19.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-11-17 | 2023 | 2022 | 2022-11-01 | 30 | 11 | 4.8593 | 1.1311 | 5.8557 | 1.2375 | 26.0142 | 41.1316 | 1.8181 | 4.4633 | 100% |  |  | 100% |  |  | 85.89% | 88.25% | 20.9% | 1700960.9 | 1685601 | 4867 | 1680734 | 334.1957 | 5.43 | 1595616 | 87.69% | 19.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-11-18 | 2023 | 2022 | 2022-11-01 | 30 | 10.9167 | 4.8363 | 1.129 | 5.8449 | 1.2351 | 26.8066 | 41.1177 | 2.1412 | 5.5114 | 100% |  |  | 100% |  |  | 85.81% | 88.11% | 20.84% | 1695764.9 | 1680933 | 4800 | 1676133 | 334.1957 | 5.43 | 1595616 | 87.69% | 19.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-11-19 | 2023 | 2022 | 2022-11-01 | 30 | 11.0667 | 4.68 | 1.087 | 5.6474 | 1.229 | 26.5072 | 40.173 | 2.1128 | 5.2197 | 100% |  |  | 100% |  |  | 86.16% | 88.35% | 20.22% | 1645659.3 | 1631000 | 4800 | 1626200 | 334.1957 | 5.43 | 1595616 | 87.69% | 19.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-11-20 | 2023 | 2022 | 2022-11-01 | 30 | 10.9333 | 4.6518 | 1.0834 | 5.6236 | 1.1358 | 26.2775 | 39.662 | 2.2978 | 4.6742 | 100% |  |  | 100% |  |  | 86.46% | 88.51% | 20.21% | 1644296.5 | 1629867 | 4933 | 1624934 | 334.1957 | 5.43 | 1595616 | 87.69% | 19.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-11-21 | 2023 | 2022 | 2022-11-01 | 30 | 10.9333 | 4.6695 | 1.0998 | 5.6596 | 1.1524 | 24.7058 | 37.5075 | 2.3019 | 4.9367 | 100% |  |  | 100% |  |  | 87.06% | 88.54% | 20.48% | 1666895.8 | 1651667 | 4934 | 1646733 | 334.1957 | 5.43 | 1595616 | 87.69% | 19.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-11-22 | 2023 | 2022 | 2022-11-01 | 30 | 10.7833 | 4.6232 | 1.0844 | 5.5829 | 1.137 | 24.7567 | 39.3588 | 1.7913 | 4.3236 | 100% |  |  | 100% |  |  | 87.35% | 88.94% | 20.26% | 1649265.2 | 1634667 | 4933 | 1629734 | 334.1957 | 5.43 | 1595616 | 87.69% | 19.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-11-23 | 2023 | 2022 | 2022-11-01 | 30 | 10.9167 | 4.9028 | 1.1263 | 5.8041 | 1.1846 | 25.3843 | 40.2047 | 1.7405 | 3.5733 | 100% |  |  | 100% |  |  | 86.8% | 88.79% | 20.93% | 1704246.8 | 1688600 | 5000 | 1683600 | 334.1957 | 5.43 | 1595616 | 87.69% | 19.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-11-24 | 2023 | 2022 | 2022-11-01 | 30 | 10.95 | 4.96 | 1.1588 | 6.1096 | 1.2161 | 25.0823 | 40.4335 | 1.6629 | 4.1547 | 100% |  |  | 100% |  |  | 84.31% | 86.57% | 21.41% | 1742552.7 | 1726400 | 4867 | 1721533 | 334.1957 | 5.43 | 1595616 | 87.69% | 19.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-11-25 | 2023 | 2022 | 2022-11-01 | 30 | 10.9 | 4.9592 | 1.1615 | 6.1184 | 1.1815 | 25.0956 | 39.8738 | 1.961 | 4.8614 | 100% |  |  | 100% |  |  | 84.54% | 86.55% | 21.5% | 1749582.8 | 1733600 | 4866 | 1728734 | 334.1957 | 5.43 | 1595616 | 87.69% | 19.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-11-26 | 2023 | 2022 | 2022-11-01 | 30 | 10.8833 | 4.9189 | 1.1701 | 6.0925 | 1.223 | 25.4863 | 40.6689 | 1.5795 | 4.2731 | 100% |  |  | 100% |  |  | 84.2% | 86.59% | 21.32% | 1735235.6 | 1719375 | 4934 | 1714441 | 334.1957 | 5.43 | 1595616 | 87.69% | 19.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-11-27 | 2023 | 2022 | 2022-11-01 | 30 | 10.85 | 4.8338 | 1.1534 | 5.988 | 1.1904 | 25.2871 | 39.9013 | 1.811 | 4.1156 | 100% |  |  | 100% |  |  | 84.68% | 86.78% | 21.07% | 1715033.4 | 1699425 | 4866 | 1694559 | 334.1957 | 5.43 | 1595616 | 87.69% | 19.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-11-28 | 2023 | 2022 | 2022-11-01 | 30 | 10.8333 | 4.8286 | 1.1421 | 6.0287 | 1.1646 | 25.3546 | 39.0972 | 2.0199 | 4.2028 | 100% |  |  | 100% |  |  | 84.54% | 87.26% | 21.18% | 1723786.7 | 1708067 | 4867 | 1703200 | 334.1957 | 5.43 | 1595616 | 87.69% | 19.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-11-29 | 2023 | 2022 | 2022-11-01 | 30 | 10.8833 | 4.6189 | 1.0569 | 5.4634 | 1.0668 | 25.2502 | 36.6769 | 2.8814 | 5.7672 | 100% |  |  | 100% |  |  | 88.43% | 89.78% | 20.08% | 1634352.4 | 1619467 | 4933 | 1614534 | 334.1957 | 5.43 | 1595616 | 87.69% | 19.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-11-30 | 2023 | 2022 | 2022-11-01 | 30 | 10.7833 | 4.7386 | 1.0925 | 5.6994 | 1.0986 | 25.0591 | 36.6423 | 3.1736 | 5.86 | 100% |  |  | 100% |  |  | 88.12% | 89.64% | 20.87% | 1699821.2 | 1683400 | 4934 | 1678466 | 334.1957 | 5.43 | 1595616 | 87.69% | 19.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-12-01 | 2023 | 2022 | 2022-12-01 | 31 | 10.8333 | 4.6004 | 1.0509 | 5.524 | 1.0607 | 23.8654 | 37.935 | 2.0683 | 4.7869 | 100% |  |  | 100% |  |  | 88.34% | 91.64% | 20.28% | 1650897.5 | 1635800 | 5000 | 1630800 | 334.1957 | 5.1161 | 1538140.6452 | 89.72% | 19.13% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-12-02 | 2023 | 2022 | 2022-12-01 | 31 | 10.6333 | 4.49 | 1.0453 | 5.3826 | 1.0541 | 23.7626 | 37.5114 | 2.0185 | 5.4172 | 100% |  |  | 100% |  |  | 88.09% | 91.25% | 19.7% | 1604469 | 1589600 | 5000 | 1584600 | 334.1957 | 5.1161 | 1538140.6452 | 89.72% | 19.13% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-12-03 | 2023 | 2022 | 2022-12-01 | 31 | 10.6333 | 4.3096 | 1.02 | 5.1506 | 1.0255 | 23.7214 | 35.7465 | 2.1093 | 5.0806 | 100% |  |  | 100% |  |  | 88.67% | 91.73% | 18.98% | 1545186.2 | 1531334 | 5000 | 1526334 | 334.1957 | 5.1161 | 1538140.6452 | 89.72% | 19.13% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-12-04 | 2023 | 2022 | 2022-12-01 | 31 | 10.6167 | 4.2517 | 1.0235 | 5.0764 | 1.0185 | 23.4878 | 35.0989 | 2.3629 | 5.0486 | 100% |  |  | 100% |  |  | 88.9% | 91.69% | 18.75% | 1526384.8 | 1513266 | 5000 | 1508266 | 334.1957 | 5.1161 | 1538140.6452 | 89.72% | 19.13% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-12-05 | 2023 | 2022 | 2022-12-01 | 31 | 10.6167 | 4.4541 | 1.0687 | 5.3449 | 1.062 | 23.1439 | 34.8309 | 2.5904 | 5.4933 | 100% |  |  | 100% |  |  | 89.19% | 92.03% | 19.81% | 1612543.3 | 1598001 | 4866 | 1593135 | 334.1957 | 5.1161 | 1538140.6452 | 89.72% | 19.13% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-12-06 | 2023 | 2022 | 2022-12-01 | 31 | 10.6333 | 4.5038 | 1.081 | 5.42 | 1.0742 | 22.9302 | 34.1651 | 2.9056 | 6.2 | 100% |  |  | 100% |  |  | 88.9% | 91.5% | 20.02% | 1629892.4 | 1615266 | 4934 | 1610332 | 334.1957 | 5.1161 | 1538140.6452 | 89.72% | 19.13% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-12-07 | 2023 | 2022 | 2022-12-01 | 31 | 10.65 | 4.5469 | 1.082 | 5.4845 | 1.0685 | 23.4394 | 36.4701 | 1.9585 | 4.8361 | 100% |  |  | 100% |  |  | 88.53% | 91.8% | 20.18% | 1643653.7 | 1627534 | 4933 | 1622601 | 334.1957 | 5.1161 | 1538140.6452 | 89.72% | 19.13% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-12-08 | 2023 | 2022 | 2022-12-01 | 31 | 10.6 | 4.566 | 1.0737 | 5.5234 | 1.0528 | 24.7756 | 38.9844 | 1.2453 | 3.6283 | 100% |  |  | 100% |  |  | 88.1% | 91.98% | 20.22% | 1646910.6 | 1631200 | 4933 | 1626267 | 334.1957 | 5.1161 | 1538140.6452 | 89.72% | 19.13% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-12-09 | 2023 | 2022 | 2022-12-01 | 31 | 10.7167 | 4.5416 | 1.073 | 5.4907 | 1.053 | 25.0288 | 38.7331 | 1.8918 | 4.7108 | 100% |  |  | 100% |  |  | 88.24% | 91.96% | 20.13% | 1638848.6 | 1624067 | 4934 | 1619133 | 334.1957 | 5.1161 | 1538140.6452 | 89.72% | 19.13% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-12-10 | 2023 | 2022 | 2022-12-01 | 31 | 10.6167 | 4.5083 | 1.076 | 5.4483 | 1.0617 | 24.37 | 36.85 | 2.6267 | 5.2583 | 100% |  |  | 100% |  |  | 89% | 92.26% | 20.15% | 1640532.6 | 1625467 | 5000 | 1620467 | 334.1957 | 5.1161 | 1538140.6452 | 89.72% | 19.13% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-12-11 | 2023 | 2022 | 2022-12-01 | 31 | 10.5833 | 4.4267 | 1.058 | 5.335 | 1.0733 | 24.224 | 34.39 | 4.3017 | 7.5617 | 100% |  |  | 100% |  |  | 89.09% | 91.61% | 19.75% | 1608388.9 | 1593306 | 5133 | 1588173 | 334.1435 | 5.1161 | 1538140.6452 | 89.72% | 19.13% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-12-12 | 2023 | 2022 | 2022-12-01 | 31 | 10.7167 | 4.36 | 1.04 | 5.2483 | 1.07 | 24.302 | 34.74 | 4.1017 | 6.695 | 100% |  |  | 100% |  |  | 90.23% | 92.72% | 19.68% | 1602630.1 | 1587360 | 5000 | 1582360 | 334.1435 | 5.1161 | 1538140.6452 | 89.72% | 19.13% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-12-13 | 2023 | 2022 | 2022-12-01 | 31 | 10.7167 | 4.3883 | 1.046 | 5.2917 | 1.05 | 24.146 | 33.36 | 5.0417 | 7.8233 | 100% |  |  | 100% |  |  | 90.7% | 92.85% | 19.94% | 1623080 | 1608667 | 5000 | 1603667 | 334.1435 | 5.1161 | 1538140.6452 | 89.72% | 19.13% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-12-14 | 2023 | 2022 | 2022-12-01 | 31 | 10.7 | 4.4867 | 1.074 | 5.4317 | 1.0817 | 22.872 | 34.9 | 2.9333 | 5.0167 | 100% |  |  | 100% |  |  | 90.4% | 93.02% | 20.42% | 1662936.6 | 1647267 | 5000 | 1642267 | 334.4583 | 5.1161 | 1538140.6452 | 89.72% | 19.13% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-12-15 | 2023 | 2022 | 2022-12-01 | 31 | 10.7167 | 4.64 | 1.116 | 5.6417 | 1.1067 | 22.274 | 35.99 | 2.0417 | 4.25 | 100% |  |  | 100% |  |  | 88.88% | 91.84% | 20.85% | 1698916.9 | 1681934 | 4933 | 1677001 | 334.4583 | 5.1161 | 1538140.6452 | 89.72% | 19.13% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-12-16 | 2023 | 2022 | 2022-12-01 | 31 | 10.7167 | 4.7243 | 1.1192 | 5.7579 | 1.1283 | 23.1641 | 38.8033 | 1.5822 | 3.4002 | 100% |  |  | 100% |  |  | 88.35% | 91.8% | 21.16% | 1723917.4 | 1706333 | 4934 | 1701399 | 334.4583 | 5.1161 | 1538140.6452 | 89.72% | 19.13% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-12-17 | 2023 | 2022 | 2022-12-01 | 31 | 10.6833 | 4.7746 | 1.1352 | 5.8273 | 1.1445 | 23.5948 | 39.2299 | 1.4523 | 3.4605 | 100% |  |  | 100% |  |  | 82.67% | 86.1% | 20.04% | 1632233.2 | 1616333 | 4933 | 1611400 | 334.4841 | 5.1161 | 1538140.6452 | 89.72% | 19.13% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-12-18 | 2023 | 2022 | 2022-12-01 | 31 | 10.6667 | 4.5696 | 1.0724 | 5.5644 | 1.0825 | 24.2261 | 38.633 | 1.9204 | 4.3403 | 100% |  |  | 100% |  |  | 89.53% | 92.71% | 20.72% | 1687730.7 | 1671267 | 4933 | 1666334 | 334.4841 | 5.1161 | 1538140.6452 | 89.72% | 19.13% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-12-19 | 2023 | 2022 | 2022-12-01 | 31 | 10.7167 | 4.0648 | 0.94756 | 4.8333 | 0.96171 | 23.6099 | 36.4669 | 1.491 | 3.3755 | 100% |  |  | 100% |  |  | 89.11% | 91.77% | 17.91% | 1457712 | 1445534 | 4934 | 1440600 | 334.4841 | 5.1161 | 1538140.6452 | 89.72% | 19.13% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-12-20 | 2023 | 2022 | 2022-12-01 | 31 | 10.7333 | 4.1636 | 1.0065 | 4.914 | 1.0271 | 23.1538 | 35.248 | 2.0174 | 4.8547 | 100% |  |  | 100% |  |  | 88.16% | 90.86% | 18.02% | 1467157.7 | 1453866 | 4866 | 1449000 | 334.4841 | 5.1161 | 1538140.6452 | 89.72% | 19.13% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-12-21 | 2023 | 2022 | 2022-12-01 | 31 | 10.5667 | 4.5132 | 1.0986 | 5.458 | 1.1065 | 21.6702 | 32.6432 | 3.2904 | 6.5497 | 100% |  |  | 100% |  |  | 90.8% | 92.94% | 20.61% | 1678637.5 | 1662734 | 5000 | 1657734 | 334.4841 | 5.1161 | 1538140.6452 | 89.72% | 19.13% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-12-22 | 2023 | 2022 | 2022-12-01 | 31 | 10.6833 | 4.6198 | 1.1228 | 5.6099 | 1.1332 | 19.9599 | 31.5343 | 3.0841 | 5.9108 | 100% |  |  | 100% |  |  | 91.18% | 92.04% | 21.28% | 1732654.6 | 1715867 | 4867 | 1711000 | 334.4841 | 5.1161 | 1538140.6452 | 89.72% | 19.13% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-12-23 | 2023 | 2022 | 2022-12-01 | 31 | 10.7 | 4.6248 | 1.1282 | 5.609 | 1.1398 | 19.217 | 31.3356 | 2.916 | 5.6812 | 100% |  |  | 100% |  |  | 90.62% | 92.24% | 21.14% | 1722584 | 1705200 | 5000 | 1700200 | 334.4841 | 5.1161 | 1538140.6452 | 89.72% | 19.13% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-12-24 | 2023 | 2022 | 2022-12-01 | 31 | 10.7167 | 4.5983 | 1.1149 | 5.5745 | 1.1253 | 19.2564 | 30.4309 | 3.5322 | 6.6985 | 100% |  |  | 100% |  |  | 91.14% | 92.46% | 21.13% | 1721417.1 | 1704333 | 4933 | 1699400 | 334.4841 | 5.1161 | 1538140.6452 | 89.72% | 19.13% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-12-25 | 2023 | 2022 | 2022-12-01 | 31 | 10.6667 | 4.4464 | 1.0941 | 5.2931 | 1.1108 | 18.4379 | 31.7143 | 2.5029 | 4.955 | 100% |  |  | 100% |  |  | 89.25% | 90.96% | 19.65% | 1601599.8 | 1585267 | 5067 | 1580200 | 334.4841 | 5.1161 | 1538140.6452 | 89.72% | 19.13% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-12-26 | 2023 | 2022 | 2022-12-01 | 31 | 10.7 | 4.6188 | 1.1161 | 5.6009 | 1.1279 | 18.9459 | 30.7068 | 3.382 | 5.9583 | 100% |  |  | 100% |  |  | 91.3% | 92.5% | 21.27% | 1731877.3 | 1715334 | 5000 | 1710334 | 334.4841 | 5.1161 | 1538140.6452 | 89.72% | 19.13% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-12-27 | 2023 | 2022 | 2022-12-01 | 31 | 10.7167 | 4.5523 | 1.0923 | 5.5164 | 1.1032 | 19.1094 | 31.0324 | 3.2896 | 5.5122 | 100% |  |  | 100% |  |  | 91.8% | 93% | 21.06% | 1715757.3 | 1698666 | 5000 | 1693666 | 334.458 | 5.1161 | 1538140.6452 | 89.72% | 19.13% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-12-28 | 2023 | 2022 | 2022-12-01 | 31 | 10.7 | 4.3757 | 1.0412 | 5.2915 | 1.0525 | 21.3885 | 36.0725 | 1.9093 | 4.0262 | 100% |  |  | 100% |  |  | 91.12% | 93.42% | 20.05% | 1632067.7 | 1617601 | 5000 | 1612601 | 334.458 | 5.1161 | 1538140.6452 | 89.72% | 19.13% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-12-29 | 2023 | 2022 | 2022-12-01 | 31 | 10.7 | 3.7133 | 0.87797 | 4.3882 | 0.89388 | 24.1081 | 34.0269 | 4.9068 | 9.4458 | 100% |  |  | 100% |  |  | 91.72% | 93.4% | 16.74% | 1364175.1 | 1351200 | 5000 | 1346200 | 334.458 | 5.1161 | 1538140.6452 | 89.72% | 19.13% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-12-30 | 2023 | 2022 | 2022-12-01 | 31 | 10.7 | 4.1702 | 1.0214 | 4.9838 | 1.0396 | 17.4453 | 27.0674 | 3.8976 | 6.4392 | 100% |  |  | 100% |  |  | 93.04% | 93.24% | 19.28% | 1571488.6 | 1555933 | 5067 | 1550866 | 334.458 | 5.1161 | 1538140.6452 | 89.72% | 19.13% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2022-12-31 | 2023 | 2022 | 2022-12-01 | 31 | 10.75 | 4.5868 | 1.1104 | 5.5633 | 1.1215 | 16.9255 | 29.3279 | 3.047 | 5.547 | 100% |  |  | 100% |  |  | 91.69% | 92.27% | 21.21% | 1728235.7 | 1711000 | 5000 | 1706000 | 334.458 | 5.1161 | 1538140.6452 | 89.72% | 19.13% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-01-01 | 2023 | 2023 | 2023-01-01 | 31 | 10.75 | 4.6561 | 1.119 | 5.6657 | 1.1265 | 18.9304 | 34.5765 | 2.1669 | 5.7815 | 100% |  |  | 100% |  |  | 89.06% | 90.96% | 20.99% | 1710192.7 | 1692934 | 4933 | 1688001 | 334.5355 | 5.4525 | 1632989.0323 | 89.38% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-01-02 | 2023 | 2023 | 2023-01-01 | 31 | 10.65 | 4.6542 | 1.12 | 5.6506 | 1.1294 | 20.4603 | 34.0317 | 2.5832 | 5.1868 | 100% |  |  | 100% |  |  | 90.88% | 93.33% | 21.36% | 1739563.8 | 1722867 | 4933 | 1717934 | 334.5355 | 5.4525 | 1632989.0323 | 89.38% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-01-03 | 2023 | 2023 | 2023-01-01 | 31 | 10.7333 | 4.4067 | 1.0694 | 5.3071 | 1.0827 | 19.3509 | 31.4176 | 3.0994 | 6.0765 | 100% |  |  | 100% |  |  | 92.03% | 93.8% | 20.32% | 1654570.4 | 1638800 | 4934 | 1633866 | 334.5355 | 5.4525 | 1632989.0323 | 89.38% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-01-04 | 2023 | 2023 | 2023-01-01 | 31 | 10.7333 | 4.7702 | 1.1774 | 5.7685 | 1.189 | 17.0577 | 27.983 | 4.3936 | 7.8687 | 100% |  |  | 100% |  |  | 90.38% | 91.21% | 21.69% | 1766259.4 | 1749133 | 4933 | 1744200 | 334.5355 | 5.4525 | 1632989.0323 | 89.38% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-01-05 | 2023 | 2023 | 2023-01-01 | 31 | 10.65 | 4.7031 | 1.1561 | 5.688 | 1.1653 | 17.1479 | 28.1197 | 4.6531 | 8.569 | 100% |  |  | 100% |  |  | 90.21% | 90.81% | 21.35% | 1739896.4 | 1722267 | 5000 | 1717267 | 334.6619 | 5.4525 | 1632989.0323 | 89.38% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-01-06 | 2023 | 2023 | 2023-01-01 | 31 | 10.7833 | 4.8205 | 1.1678 | 5.8341 | 1.1776 | 19.1967 | 31.1814 | 3.9668 | 7.3715 | 100% |  |  | 100% |  |  | 89.79% | 91.5% | 21.8% | 1776107.3 | 1758000 | 4933 | 1753067 | 334.6619 | 5.4525 | 1632989.0323 | 89.38% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-01-07 | 2023 | 2023 | 2023-01-01 | 31 | 10.7833 | 4.2852 | 1.0412 | 5.0892 | 1.062 | 20.3877 | 32.4353 | 2.6484 | 4.8875 | 100% |  |  | 100% |  |  | 91.74% | 93.81% | 19.44% | 1582514.7 | 1568000 | 4867 | 1563133 | 334.7939 | 5.4525 | 1632989.0323 | 89.38% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-01-08 | 2023 | 2023 | 2023-01-01 | 31 | 10.6333 | 4.3506 | 1.0551 | 5.2138 | 1.0836 | 21.8315 | 36.076 | 2.0813 | 5.0325 | 100% |  |  | 100% |  |  | 90.9% | 93.86% | 19.73% | 1605849.7 | 1591467 | 4800 | 1586667 | 334.7678 | 5.4525 | 1632989.0323 | 89.38% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-01-09 | 2023 | 2023 | 2023-01-01 | 31 | 10.6333 | 3.6846 | 0.8737 | 4.2409 | 0.89689 | 22.1372 | 33.8729 | 1.8102 | 5.5577 | 100% |  |  | 100% |  |  | 91.38% | 93.42% | 16.13% | 1314271.5 | 1302200 | 4800 | 1297400 | 334.7678 | 5.4525 | 1632989.0323 | 89.38% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-01-10 | 2023 | 2023 | 2023-01-01 | 31 | 10.7833 | 4.5559 | 1.0973 | 5.4824 | 1.1111 | 21.2915 | 35.0697 | 2.1247 | 4.464 | 100% |  |  | 100% |  |  | 91.15% | 93.86% | 20.8% | 1694337.1 | 1677734 | 4800 | 1672934 | 334.7678 | 5.4525 | 1632989.0323 | 89.38% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-01-11 | 2023 | 2023 | 2023-01-01 | 31 | 10.7333 | 4.3904 | 1.0558 | 5.2504 | 1.0711 | 22.6701 | 34.1752 | 5.0917 | 10.0758 | 100% |  |  | 100% |  |  | 91.74% | 93.77% | 20.05% | 1632773.1 | 1617266 | 4800 | 1612466 | 334.7678 | 5.4525 | 1632989.0323 | 89.38% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-01-12 | 2023 | 2023 | 2023-01-01 | 31 | 10.7833 | 4.4096 | 1.0541 | 5.2538 | 1.0707 | 20.1812 | 33.5161 | 2.9542 | 6.7132 | 100% |  |  | 100% |  |  | 91.45% | 93.72% | 20% | 1629554.6 | 1613200 | 4867 | 1608333 | 334.7678 | 5.4525 | 1632989.0323 | 89.38% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-01-13 | 2023 | 2023 | 2023-01-01 | 31 | 10.65 | 4.5482 | 1.0909 | 5.412 | 1.1103 | 16.326 | 28.3868 | 2.7353 | 6.201 | 100% |  |  | 100% |  |  | 90.14% | 91.28% | 20.31% | 1655567.2 | 1638067 | 4866 | 1633201 | 334.7678 | 5.4525 | 1632989.0323 | 89.38% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-01-14 | 2023 | 2023 | 2023-01-01 | 31 | 10.7667 | 4.9464 | 1.1912 | 5.9441 | 1.2058 | 15.1783 | 27.6455 | 3.5431 | 6.596 | 100% |  |  | 100% |  |  | 90.4% | 90.9% | 22.37% | 1823261.3 | 1803734 | 4867 | 1798867 | 334.7678 | 5.4525 | 1632989.0323 | 89.38% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-01-15 | 2023 | 2023 | 2023-01-01 | 31 | 10.8 | 5.0499 | 1.2098 | 6.081 | 1.2208 | 15.0514 | 30.2144 | 2.3878 | 4.9235 | 100% |  |  | 100% |  |  | 89.55% | 90.55% | 22.67% | 1846811.4 | 1827667 | 4733 | 1822934 | 334.7678 | 5.4525 | 1632989.0323 | 89.38% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-01-16 | 2023 | 2023 | 2023-01-01 | 31 | 10.8167 | 5.0684 | 1.1984 | 6.1132 | 1.2122 | 17.1151 | 30.7627 | 3.0532 | 5.7318 | 100% |  |  | 100% |  |  | 88.22% | 89.76% | 22.45% | 1828207.4 | 1810133 | 4800 | 1805333 | 334.7678 | 5.4525 | 1632989.0323 | 89.38% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-01-17 | 2023 | 2023 | 2023-01-01 | 31 | 10.7833 | 4.9347 | 1.1636 | 5.9325 | 1.1789 | 17.8896 | 31.762 | 2.6103 | 4.9967 | 100% |  |  | 100% |  |  | 88.95% | 90.78% | 21.97% | 1789937.3 | 1771400 | 4867 | 1766533 | 334.7678 | 5.4525 | 1632989.0323 | 89.38% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-01-18 | 2023 | 2023 | 2023-01-01 | 31 | 10.85 | 4.8582 | 1.1402 | 5.8234 | 1.1548 | 19.4674 | 32.0251 | 3.4767 | 6.4115 | 100% |  |  | 100% |  |  | 89.66% | 91.55% | 21.73% | 1768771 | 1752934 | 5000 | 1747934 | 334.7678 | 5.4525 | 1632989.0323 | 89.38% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-01-19 | 2023 | 2023 | 2023-01-01 | 31 | 10.8667 | 4.004 | 0.93273 | 4.6091 | 0.95842 | 20.2311 | 30.8767 | 3.2442 | 6.3792 | 100% |  |  | 100% |  |  | 90.3% | 91.69% | 17.32% | 1410435.3 | 1398200 | 4933 | 1393267 | 334.7678 | 5.4525 | 1632989.0323 | 89.38% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-01-20 | 2023 | 2023 | 2023-01-01 | 31 | 10.8833 | 4.3506 | 1.0551 | 5.2138 | 1.0836 | 21.8315 | 36.076 | 2.0813 | 5.0325 | 100% |  |  | 100% |  |  | 88.16% | 92.01% | 19.13% | 1557467 | 1543666 | 4867 | 1538799 | 334.7678 | 5.4525 | 1632989.0323 | 89.38% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-01-21 | 2023 | 2023 | 2023-01-01 | 31 | 10.7833 | 4.0806 | 0.9947 | 4.7307 | 1.0183 | 16.3677 | 25.1739 | 3.7764 | 6.6653 | 100% |  |  | 100% |  |  | 91.86% | 91.66% | 18.09% | 1473105.5 | 1459801 | 5067 | 1454734 | 334.7678 | 5.4525 | 1632989.0323 | 89.38% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-01-22 | 2023 | 2023 | 2023-01-01 | 31 | 10.3833 | 4.4347 | 1.0676 | 5.1896 | 1.0897 | 16.5402 | 28.916 | 4.5231 | 7.2973 | 100% |  |  | 100% |  |  | 35.94% | 35.99% | 7.763% | 632699.8 | 626533 | 2200 | 624333 | 334.7678 | 5.4525 | 1632989.0323 | 89.38% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-01-23 | 2023 | 2023 | 2023-01-01 | 31 | 10.65 | 3.3915 | 0.84179 | 3.7786 | 0.87163 | 16.3907 | 22.6515 | 4.7402 | 7.7753 | 100% |  |  | 100% |  |  | 90.43% | 89% | 14.22% | 1158027.7 | 1148933 | 5000 | 1143933 | 334.7678 | 5.4525 | 1632989.0323 | 89.38% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-01-24 | 2023 | 2023 | 2023-01-01 | 31 | 10.85 | 4.5282 | 1.0969 | 5.2949 | 1.1203 | 16.2389 | 25.9425 | 4.1478 | 6.7825 | 100% |  |  | 100% |  |  | 91.51% | 91.79% | 20.17% | 1641228 | 1627001 | 4866 | 1622135 | 334.7678 | 5.4525 | 1632989.0323 | 89.38% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-01-25 | 2023 | 2023 | 2023-01-01 | 31 | 11.0167 | 5.3182 | 1.2754 | 6.3277 | 1.2922 | 16.5498 | 32.0433 | 2.4517 | 4.6873 | 100% |  |  | 100% |  |  | 86.96% | 88.8% | 22.9% | 1865753 | 1846866 | 4867 | 1841999 | 334.7678 | 5.4525 | 1632989.0323 | 89.38% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-01-26 | 2023 | 2023 | 2023-01-01 | 31 | 11.0667 | 5.1461 | 1.2366 | 6.0811 | 1.2548 | 16.4863 | 27.4399 | 4.4787 | 7.6103 | 100% |  |  | 100% |  |  | 89.11% | 89.84% | 22.56% | 1836304.3 | 1818867 | 4867 | 1814000 | 334.7678 | 5.4525 | 1632989.0323 | 89.38% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-01-27 | 2023 | 2023 | 2023-01-01 | 31 | 11.05 | 5.2448 | 1.258 | 6.2036 | 1.2758 | 16.7418 | 28.0801 | 4.8856 | 8.3452 | 100% |  |  | 100% |  |  | 87.92% | 88.59% | 22.7% | 1849872.1 | 1830667 | 4733 | 1825934 | 334.7678 | 5.4525 | 1632989.0323 | 89.38% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-01-28 | 2023 | 2023 | 2023-01-01 | 31 | 11.0333 | 5.3049 | 1.2644 | 6.276 | 1.2817 | 18.7256 | 32.3742 | 3.1908 | 5.2007 | 100% |  |  | 100% |  |  | 87.62% | 89.77% | 22.89% | 1863944.2 | 1845800 | 4867 | 1840933 | 334.7678 | 5.4525 | 1632989.0323 | 89.38% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-01-29 | 2023 | 2023 | 2023-01-01 | 31 | 10.8833 | 4.227 | 1.0081 | 4.8781 | 1.0358 | 20.8155 | 33.3269 | 2.4544 | 5.0173 | 100% |  |  | 100% |  |  | 89.77% | 92.13% | 18.23% | 1483878.4 | 1470934 | 5000 | 1465934 | 334.7678 | 5.4525 | 1632989.0323 | 89.38% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-01-30 | 2023 | 2023 | 2023-01-01 | 31 | 11.0667 | 5.1406 | 1.1474 | 6.0236 | 1.1694 | 19.3084 | 34.3182 | 2.273 | 5.0207 | 100% |  |  | 100% |  |  | 88.26% | 90.68% | 22.13% | 1801214.3 | 1784466 | 4733 | 1779733 | 334.7678 | 5.4525 | 1632989.0323 | 89.38% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-01-31 | 2023 | 2023 | 2023-01-01 | 31 | 10.8667 | 4.9051 | 1.1433 | 5.7216 | 1.1683 | 17.9213 | 28.8043 | 4.2564 | 7.2627 | 100% |  |  | 100% |  |  | 87.55% | 89.13% | 20.85% | 1698561.5 | 1681667 | 4733 | 1676934 | 334.7678 | 5.4525 | 1632989.0323 | 89.38% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-02-01 | 2023 | 2023 | 2023-02-01 | 28 | 11.1333 | 5.3698 | 1.2346 | 6.3094 | 1.255 | 20.3591 | 33.8521 | 3.435 | 6.2818 | 100% |  |  | 100% |  |  | 87.88% | 88.78% | 23.08% | 1879216.1 | 1861000 | 4734 | 1856266 | 334.7678 | 6.1628 | 1783060.7143 | 86.34% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-02-02 | 2023 | 2023 | 2023-02-01 | 28 | 11.15 | 5.4171 | 1.2312 | 6.3657 | 1.2498 | 22.5211 | 37.7327 | 2.5376 | 4.8858 | 100% |  |  | 100% |  |  | 86.98% | 88.96% | 23.05% | 1874859.5 | 1858400 | 4866 | 1853534 | 334.7678 | 6.1628 | 1783060.7143 | 86.34% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-02-03 | 2023 | 2023 | 2023-02-01 | 28 | 11.1667 | 5.4128 | 1.2414 | 6.3442 | 1.2631 | 24.6743 | 40.6451 | 2.4181 | 5.2188 | 100% |  |  | 100% |  |  | 86.11% | 88.75% | 22.74% | 1850679.3 | 1833601 | 4800 | 1828801 | 334.7678 | 6.1628 | 1783060.7143 | 86.34% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-02-04 | 2023 | 2023 | 2023-02-01 | 28 | 11.2167 | 5.2307 | 1.1842 | 6.1064 | 1.208 | 25.9188 | 41.5132 | 2.095 | 4.4683 | 100% |  |  | 100% |  |  | 87.29% | 90.4% | 22.19% | 1805008.5 | 1789133 | 4800 | 1784333 | 334.7678 | 6.1628 | 1783060.7143 | 86.34% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-02-05 | 2023 | 2023 | 2023-02-01 | 28 | 11.2 | 5.2223 | 1.2122 | 6.0769 | 1.2419 | 26.5242 | 39.7897 | 4.1365 | 8.452 | 100% |  |  | 100% |  |  | 87.17% | 89.64% | 22.05% | 1793912.5 | 1778200 | 4867 | 1773333 | 334.7678 | 6.1628 | 1783060.7143 | 86.34% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-02-06 | 2023 | 2023 | 2023-02-01 | 28 | 11.2167 | 4.9837 | 1.163 | 5.7455 | 1.1982 | 23.7883 | 35.5609 | 3.5385 | 6.6997 | 100% |  |  | 100% |  |  | 89.33% | 90.86% | 21.36% | 1738949.5 | 1723000 | 4800 | 1718200 | 334.7678 | 6.1628 | 1783060.7143 | 86.34% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-02-07 | 2023 | 2023 | 2023-02-01 | 28 | 11.2667 | 5.3136 | 1.2396 | 6.1625 | 1.272 | 23.3663 | 38.6655 | 1.8856 | 4.0027 | 100% |  |  | 100% |  |  | 87.19% | 89.48% | 22.37% | 1820092.3 | 1803534 | 4733 | 1798801 | 334.7678 | 6.1628 | 1783060.7143 | 86.34% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-02-08 | 2023 | 2023 | 2023-02-01 | 28 | 11.25 | 5.3745 | 1.2664 | 6.2227 | 1.3006 | 25.8678 | 39.5755 | 3.9661 | 7.8323 | 100% |  |  | 100% |  |  | 86.64% | 88.99% | 22.44% | 1826183.9 | 1809733 | 4800 | 1804933 | 334.7678 | 6.1628 | 1783060.7143 | 86.34% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-02-09 | 2023 | 2023 | 2023-02-01 | 28 | 11.35 | 5.4 | 1.28 | 6.0696 | 1.3235 | 23.098 | 37.94 | 4.7933 | 10.5383 | 100% |  |  | 100% |  |  | 89.42% | 88.8% | 22.59% | 1838359.4 | 1821600 | 4734 | 1816866 | 334.7678 | 6.1628 | 1783060.7143 | 86.34% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-02-10 | 2023 | 2023 | 2023-02-01 | 28 | 11.4333 | 5.2303 | 1.2406 | 6.0282 | 1.2764 | 22.238 | 36.83 | 4.2617 | 8.1283 | 100% |  |  | 100% |  |  | 87.43% | 89.2% | 21.94% | 1786175.1 | 1769201 | 4733 | 1764468 | 334.7678 | 6.1628 | 1783060.7143 | 86.34% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-02-11 | 2023 | 2023 | 2023-02-01 | 28 | 11.3667 | 5.1363 | 1.2229 | 5.8907 | 1.2622 | 24.909 | 36.6094 | 2.9934 | 6.4163 | 100% |  |  | 100% |  |  | 87.31% | 89.34% | 21.41% | 1743073.8 | 1726533 | 4800 | 1721733 | 334.7678 | 6.1628 | 1783060.7143 | 86.34% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-02-12 | 2023 | 2023 | 2023-02-01 | 28 | 11.4333 | 5.8596 | 1.4214 | 6.7625 | 1.4585 | 18.586 | 32.9 | 3.5467 | 7.9095 | 100% |  |  | 100% |  |  | 84.01% | 85.52% | 23.65% | 1925780.5 | 1906600 | 4733 | 1901867 | 334.7678 | 6.1628 | 1783060.7143 | 86.34% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-02-13 | 2023 | 2023 | 2023-02-01 | 28 | 11.55 | 5.9761 | 1.3547 | 6.6761 | 1.4145 | 17.25 | 36.87 | 2.1483 | 4.49 | 100% |  |  | 100% |  |  | 83.89% | 85.92% | 23.31% | 1898020.8 | 1879534 | 4667 | 1874867 | 334.7678 | 6.1628 | 1783060.7143 | 86.34% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-02-14 | 2023 | 2023 | 2023-02-01 | 28 | 11.5333 | 5.8702 | 1.3942 | 6.7483 | 1.4335 | 20.468 | 41.44 | 2.174 | 4.6983 | 100% |  |  | 100% |  |  | 83.67% | 87.14% | 23.5% | 1912268.3 | 1894933 | 4733 | 1890200 | 334.7678 | 6.1628 | 1783060.7143 | 86.34% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-02-15 | 2023 | 2023 | 2023-02-01 | 28 | 11.4333 | 5.8627 | 1.3614 | 6.7359 | 1.4002 | 29.5501 | 45.6786 | 2.4569 | 4.8842 | 100% |  |  | 100% |  |  | 83.43% | 87.92% | 23.39% | 1898529.7 | 1885934 | 4667 | 1881267 | 334.7678 | 6.1628 | 1783060.7143 | 86.34% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-02-16 | 2023 | 2023 | 2023-02-01 | 28 | 11.65 | 5.5288 | 1.3165 | 6.2342 | 1.3634 | 29.8903 | 43.9025 | 2.7979 | 6.6027 | 100% |  |  | 100% |  |  | 83.06% | 87.54% | 21.55% | 1754974.2 | 1738133 | 4667 | 1733466 | 334.7678 | 6.1628 | 1783060.7143 | 86.34% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-02-17 | 2023 | 2023 | 2023-02-01 | 28 | 11.4833 | 5.9924 | 1.4053 | 6.869 | 1.4435 | 31.4945 | 47.0481 | 1.9687 | 4.1582 | 100% |  |  | 100% |  |  | 82.75% | 88.14% | 23.66% | 1926155.6 | 1907600 | 4733 | 1902867 | 334.7678 | 6.1628 | 1783060.7143 | 86.34% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-02-18 | 2023 | 2023 | 2023-02-01 | 28 | 11.5167 | 6.0691 | 1.4501 | 6.9446 | 1.4898 | 24.874 | 45.46 | 2.0583 | 4.34 | 100% |  |  | 100% |  |  | 82.18% | 87.45% | 23.76% | 1932951.1 | 1915400 | 4800 | 1910600 | 334.7678 | 6.1628 | 1783060.7143 | 86.34% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-02-19 | 2023 | 2023 | 2023-02-01 | 28 | 11.6167 | 6.1569 | 1.4903 | 7.0427 | 1.5214 | 25.776 | 43.7 | 3.825 | 7.9733 | 100% |  |  | 100% |  |  | 81.72% | 86.2% | 23.96% | 1948262.7 | 1931401 | 4733 | 1926668 | 334.7678 | 6.1628 | 1783060.7143 | 86.34% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-02-20 | 2023 | 2023 | 2023-02-01 | 28 | 11.6167 | 6.2363 | 1.4814 | 7.1046 | 1.5136 | 29.389 | 43.5479 | 4.8901 | 8.3132 | 100% |  |  | 100% |  |  | 81.72% | 85.43% | 24.17% | 1967600.8 | 1948133 | 4600 | 1943533 | 334.7678 | 6.1628 | 1783060.7143 | 86.34% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-02-21 | 2023 | 2023 | 2023-02-01 | 28 | 11.5333 | 5.1698 | 1.227 | 5.8332 | 1.2609 | 27.9786 | 42.2026 | 1.9781 | 4.8767 | 100% |  |  | 100% |  |  | 86.45% | 89.85% | 20.99% | 1707716.9 | 1693000 | 4800 | 1688200 | 334.7678 | 6.1628 | 1783060.7143 | 86.34% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-02-22 | 2023 | 2023 | 2023-02-01 | 28 | 11.6 | 5.4298 | 1.3004 | 6.0925 | 1.3393 | 28.6895 | 42.8837 | 3.1669 | 7.3125 | 100% |  |  | 100% |  |  | 83.9% | 87.42% | 21.28% | 1730910.2 | 1716000 | 4800 | 1711200 | 334.7678 | 6.1628 | 1783060.7143 | 86.34% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-02-23 | 2023 | 2023 | 2023-02-01 | 28 | 11.6 | 5.2483 | 1.2222 | 5.9148 | 1.253 | 27.733 | 42.2943 | 2.7612 | 5.5778 | 100% |  |  | 100% |  |  | 84.44% | 87.22% | 20.79% | 1690779.4 | 1675934 | 3934 | 1672000 | 334.7678 | 6.1628 | 1783060.7143 | 86.34% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-02-24 | 2023 | 2023 | 2023-02-01 | 28 | 11.7667 | 5.3532 | 1.284 | 6.0056 | 1.3241 | 27.5949 | 42.7263 | 2.4655 | 5.9043 | 100% |  |  | 100% |  |  | 83.29% | 86.53% | 20.82% | 1694581.5 | 1679200 | 4600 | 1674600 | 334.7678 | 6.1628 | 1783060.7143 | 86.34% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-02-25 | 2023 | 2023 | 2023-02-01 | 28 | 11.65 | 5.4488 | 1.2918 | 6.1014 | 1.3293 | 28.4794 | 43.1499 | 2.2952 | 5.7962 | 100% |  |  | 100% |  |  | 85.68% | 89.2% | 21.78% | 1772777.5 | 1756533 | 4800 | 1751733 | 335.0909 | 6.1628 | 1783060.7143 | 86.34% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-02-26 | 2023 | 2023 | 2023-02-01 | 28 | 11.7333 | 5.3118 | 1.2666 | 5.8952 | 1.3116 | 29.0265 | 41.3956 | 2.5642 | 5.95 | 100% |  |  | 100% |  |  | 85.37% | 88.99% | 20.97% | 1706834.5 | 1691001 | 4600 | 1686401 | 335.0909 | 6.1628 | 1783060.7143 | 86.34% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-02-27 | 2023 | 2023 | 2023-02-01 | 28 | 11.6333 | 5.7571 | 1.3653 | 6.4352 | 1.4074 | 30.3656 | 44.9333 | 2.2891 | 5.4305 | 100% |  |  | 100% |  |  | 83.73% | 88.19% | 22.45% | 1826508.8 | 1810066 | 4533 | 1805533 | 335.0909 | 6.1628 | 1783060.7143 | 86.34% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-02-28 | 2023 | 2023 | 2023-02-01 | 28 | 11.6667 | 5.8189 | 1.3794 | 6.5076 | 1.423 | 31.5372 | 44.775 | 3.5265 | 7.4085 | 100% |  |  | 100% |  |  | 82.73% | 87.08% | 22.43% | 1825862.2 | 1808800 | 4733 | 1804067 | 335.0909 | 6.1628 | 1783060.7143 | 86.34% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-03-01 | 2023 | 2023 | 2023-03-01 | 31 | 11.6833 | 5.6369 | 1.3393 | 6.2927 | 1.3831 | 28.5493 | 42.0647 | 2.8275 | 5.1647 | 100% |  |  | 100% |  |  | 85.35% | 86.8% | 22.38% | 1821472.3 | 1804401 | 4734 | 1799667 | 335.0909 | 6.9595 | 1927977.0968 | 82.67% | 23.97% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-03-02 | 2023 | 2023 | 2023-03-01 | 31 | 11.7167 | 5.4234 | 1.2883 | 6.0282 | 1.3307 | 27.0573 | 39.2158 | 3.0513 | 6.1792 | 100% |  |  | 100% |  |  | 86.62% | 87.02% | 21.76% | 1770028.5 | 1754333 | 4666 | 1749667 | 335.0909 | 6.9595 | 1927977.0968 | 82.67% | 23.97% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-03-03 | 2023 | 2023 | 2023-03-01 | 31 | 11.7333 | 5.6706 | 1.3414 | 6.3063 | 1.385 | 29.0174 | 22.2249 | 4.0565 | 7.9142 | 100% |  |  | 100% |  |  | 84.95% | 86.02% | 22.32% | 1816842.4 | 1799667 | 4467 | 1795200 | 335.0909 | 6.9595 | 1927977.0968 | 82.67% | 23.97% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-03-04 | 2023 | 2023 | 2023-03-01 | 31 | 11.7333 | 5.2913 | 1.2647 | 5.8408 | 1.3113 | 29.02 | 19.8669 | 4.5112 | 7.7942 | 100% |  |  | 100% |  |  | 86.49% | 87.08% | 21.05% | 1712897.8 | 1697467 | 4733 | 1692734 | 335.0909 | 6.9595 | 1927977.0968 | 82.67% | 23.97% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-03-05 | 2023 | 2023 | 2023-03-01 | 31 | 11.8167 | 6.2943 | 1.4729 | 7.0195 | 1.5224 | 29.2174 | 25.2208 | 2.3987 | 6.1187 | 100% |  |  | 100% |  |  | 82.13% | 84.31% | 24.02% | 1954884.4 | 1936400 | 4467 | 1931933 | 335.0909 | 6.9595 | 1927977.0968 | 82.67% | 23.97% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-03-06 | 2023 | 2023 | 2023-03-01 | 31 | 11.8167 | 6.2707 | 1.4823 | 6.961 | 1.5363 | 29.9279 | 44.9304 | 2.802 | 5.9133 | 100% |  |  | 100% |  |  | 82.26% | 84.55% | 23.86% | 1942455.9 | 1923467 | 4667 | 1918800 | 335.0909 | 6.9595 | 1927977.0968 | 82.67% | 23.97% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-03-07 | 2023 | 2023 | 2023-03-01 | 31 | 11.6833 | 5.2429 | 1.1995 | 5.7237 | 1.2406 | 29.4303 | 27.1666 | 4.4405 | 11.2877 | 100% |  |  | 100% |  |  | 83.07% | 84.44% | 19.81% | 1614851.3 | 1597866 | 4600 | 1593266 | 335.0909 | 6.9595 | 1927977.0968 | 82.67% | 23.97% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-03-08 | 2023 | 2023 | 2023-03-01 | 31 | 11.9 | 6.509 | 1.3348 | 7.2207 | 1.3863 | 27.1372 | 24.5184 | 2.6965 | 6.0005 | 100% |  |  | 100% |  |  | 81.38% | 83% | 24.48% | 1994085.7 | 1973867 | 4800 | 1969067 | 335.0909 | 6.9595 | 1927977.0968 | 82.67% | 23.97% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-03-09 | 2023 | 2023 | 2023-03-01 | 31 | 11.9333 | 6.4408 | 1.3526 | 7.1218 | 1.4053 | 29.3953 | 29.1335 | 2.785 | 7.5235 | 100% |  |  | 100% |  |  | 81.53% | 83.62% | 24.19% | 1968833.9 | 1950095 | 4533 | 1945562 | 335.0909 | 6.9595 | 1927977.0968 | 82.67% | 23.97% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-03-10 | 2023 | 2023 | 2023-03-01 | 31 | 11.9667 | 6.6287 | 1.4182 | 7.328 | 1.4764 | 30.0162 | 32.6754 | 2.379 | 5.6297 | 100% |  |  | 100% |  |  | 80.82% | 83.46% | 24.68% | 2008375.1 | 1989039 | 4467 | 1984572 | 335.0909 | 6.9595 | 1927977.0968 | 82.67% | 23.97% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-03-11 | 2023 | 2023 | 2023-03-01 | 31 | 11.9333 | 6.5972 | 1.4164 | 7.2739 | 1.4758 | 31.0714 | 43.1256 | 2.5547 | 6.5432 | 100% |  |  | 100% |  |  | 80.55% | 83.36% | 24.41% | 1986493.4 | 1967867 | 4466 | 1963401 | 335.0909 | 6.9595 | 1927977.0968 | 82.67% | 23.97% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-03-12 | 2023 | 2023 | 2023-03-01 | 31 | 11.95 | 5.6277 | 1.2136 | 6.0776 | 1.2747 | 31.0019 | 36.0582 | 2.2964 | 6.2135 | 100% |  |  | 100% |  |  | 82.05% | 84.63% | 20.78% | 1693246.2 | 1675667 | 4600 | 1671067 | 335.0909 | 6.9595 | 1927977.0968 | 82.67% | 23.97% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-03-13 | 2023 | 2023 | 2023-03-01 | 31 | 11.9667 | 6.3882 | 1.3943 | 6.9725 | 1.4602 | 31.6918 | 45.4868 | 2.3973 | 5.5437 | 100% |  |  | 100% |  |  | 79.69% | 82.85% | 23.15% | 1883552 | 1864733 | 2867 | 1861866 | 335.0909 | 6.9595 | 1927977.0968 | 82.67% | 23.97% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-03-14 | 2023 | 2023 | 2023-03-01 | 31 | 11.95 | 6.2305 | 1.3721 | 6.8224 | 1.434 | 32.0235 | 45.4758 | 2.7205 | 6.7115 | 100% |  |  | 100% |  |  | 81.03% | 83.92% | 23.04% | 1874514.8 | 1856333 | 3800 | 1852533 | 335.0909 | 6.9595 | 1927977.0968 | 82.67% | 23.97% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-03-15 | 2023 | 2023 | 2023-03-01 | 31 | 11.85 | 3.3513 | 0.75124 | 3.4618 | 0.79737 | 30.1058 | 54.1522 | 3.2785 | 10.7255 | 100% |  |  | 100% |  |  | 91.4% | 90.44% | 13.18% | 1073397 | 1064867 | 4667 | 1060200 | 335.0909 | 6.9595 | 1927977.0968 | 82.67% | 23.97% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-03-16 | 2023 | 2023 | 2023-03-01 | 31 | 11.95 | 5.4307 | 1.222 | 5.8683 | 1.2826 | 29.177 | 60.0472 | 3.3088 | 6.939 | 100% |  |  | 100% |  |  | 82.78% | 84.38% | 20.24% | 1648951.4 | 1632467 | 4600 | 1627867 | 335.0909 | 6.9595 | 1927977.0968 | 82.67% | 23.97% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-03-17 | 2023 | 2023 | 2023-03-01 | 31 | 11.9333 | 5.8521 | 1.1354 | 6.3428 | 1.1853 | 25.7395 | 34.5187 | 3.2755 | 6.1677 | 100% |  |  | 100% |  |  | 82.77% | 83.3% | 21.87% | 1784846.3 | 1764000 | 4800 | 1759200 | 335.0909 | 6.9595 | 1927977.0968 | 82.67% | 23.97% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-03-18 | 2023 | 2023 | 2023-03-01 | 31 | 12 | 6.5504 | 1.412 | 7.1012 | 1.4683 | 24.6722 | 33.2329 | 3.6453 | 6.4688 | 100% |  |  | 100% |  |  | 82.99% | 83.09% | 24.55% | 2001362.2 | 1979400 | 4733 | 1974667 | 335.0909 | 6.9595 | 1927977.0968 | 82.67% | 23.97% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-03-19 | 2023 | 2023 | 2023-03-01 | 31 | 11.9667 | 4.102 | 0.84952 | 4.3396 | 0.88549 | 22.592 | 41.4901 | 3.6 | 11.5362 | 100% |  |  | 100% |  |  | 86.31% | 85.64% | 15.61% | 1273607.5 | 1259800 | 4667 | 1255133 | 335.0909 | 6.9595 | 1927977.0968 | 82.67% | 23.97% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-03-20 | 2023 | 2023 | 2023-03-01 | 31 | 11.85 | 6.6118 | 1.3308 | 7.1803 | 1.3896 | 25.0627 | 28.0455 | 2.8452 | 5.5877 | 100% |  |  | 100% |  |  | 81.37% | 82.14% | 24.34% | 1985440.5 | 1962534 | 4733 | 1957801 | 335.0909 | 6.9595 | 1927977.0968 | 82.67% | 23.97% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-03-21 | 2023 | 2023 | 2023-03-01 | 31 | 11.85 | 6.4637 | 1.3178 | 6.9861 | 1.3741 | 27.8239 | 27.15 | 1.9688 | 4.7385 | 100% |  |  | 100% |  |  | 80.09% | 82.25% | 23.31% | 1901098.2 | 1879600 | 4600 | 1875000 | 335.0909 | 6.9595 | 1927977.0968 | 82.67% | 23.97% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-03-22 | 2023 | 2023 | 2023-03-01 | 31 | 11.8667 | 6.4338 | 1.3764 | 6.9237 | 1.438 | 27.1297 | 46.0007 | 3.6843 | 7.0373 | 100% |  |  | 100% |  |  | 81.69% | 82.59% | 23.57% | 1922148.4 | 1900134 | 4800 | 1895334 | 335.0909 | 6.9595 | 1927977.0968 | 82.67% | 23.97% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-03-23 | 2023 | 2023 | 2023-03-01 | 31 | 11.8333 | 6.1338 | 1.3091 | 6.574 | 1.3698 | 28.6931 | 28.0041 | 2.8271 | 7.2815 | 100% |  |  | 100% |  |  | 81.69% | 83.11% | 22.38% | 1822930 | 1804266 | 4667 | 1799599 | 335.0909 | 6.9595 | 1927977.0968 | 82.67% | 23.97% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-03-24 | 2023 | 2023 | 2023-03-01 | 31 | 12.2833 | 6.7606 | 1.4972 | 7.2752 | 1.566 | 26.7252 | 37.171 | 6.4847 | 11.158 | 100% |  |  | 100% |  |  | 80.64% | 80.61% | 24.44% | 1988718.8 | 1970400 | 4600 | 1965800 | 335.0909 | 6.9595 | 1927977.0968 | 82.67% | 23.97% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-03-25 | 2023 | 2023 | 2023-03-01 | 31 | 12.3 | 6.3525 | 1.4344 | 6.8036 | 1.5069 | 27.004 | 47.9193 | 2.6533 | 7.013 | 100% |  |  | 100% |  |  | 82.69% | 83.73% | 23.44% | 1906180.6 | 1889667 | 4533 | 1885134 | 335.0909 | 6.9595 | 1927977.0968 | 82.67% | 23.97% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-03-26 | 2023 | 2023 | 2023-03-01 | 31 | 12.35 | 6.7849 | 1.5338 | 7.2715 | 1.6072 | 27.1648 | 49.0025 | 3.8495 | 7.4153 | 100% |  |  | 100% |  |  | 81.61% | 82.75% | 24.73% | 2010609 | 1993000 | 4533 | 1988467 | 335.0909 | 6.9595 | 1927977.0968 | 82.67% | 23.97% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-03-27 | 2023 | 2023 | 2023-03-01 | 31 | 12.4167 | 6.8357 | 1.5397 | 7.3272 | 1.6102 | 27.7729 | 52.4522 | 2.7351 | 6.3728 | 100% |  |  | 100% |  |  | 80.88% | 82.6% | 24.69% | 2008129.4 | 1990201 | 4467 | 1985734 | 335.0909 | 6.9595 | 1927977.0968 | 82.67% | 23.97% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-03-28 | 2023 | 2023 | 2023-03-01 | 31 | 12.35 | 7.0216 | 1.5916 | 7.5317 | 1.6659 | 30.6566 | 56.3747 | 3.3094 | 7.6085 | 100% |  |  | 100% |  |  | 80.01% | 82.39% | 25.11% | 2041541.8 | 2023866 | 4467 | 2019399 | 335.0909 | 6.9595 | 1927977.0968 | 82.67% | 23.97% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-03-29 | 2023 | 2023 | 2023-03-01 | 31 | 12.35 | 5.9222 | 1.3542 | 6.2918 | 1.4237 | 30.3974 | 55.1714 | 4.7433 | 9.7942 | 100% |  |  | 100% |  |  | 80.34% | 81.85% | 21.06% | 1713204.7 | 1698067 | 4266 | 1693801 | 335.0909 | 6.9595 | 1927977.0968 | 82.67% | 23.97% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-03-30 | 2023 | 2023 | 2023-03-01 | 31 | 12.35 | 5.2263 | 1.1237 | 5.5495 | 1.187 | 26.6956 | 55.0537 | 4.2495 | 9.8762 | 100% |  |  | 100% |  |  | 78.99% | 79.79% | 18.27% | 1486695 | 1473400 | 4467 | 1468933 | 335.0909 | 6.9595 | 1927977.0968 | 82.67% | 23.97% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-03-31 | 2023 | 2023 | 2023-03-01 | 31 | 12.4167 | 6.2561 | 1.3514 | 6.6342 | 1.4156 | 27.3002 | 58.689 | 3.3907 | 7.1455 | 100% |  |  | 100% |  |  | 80.66% | 81.33% | 22.3% | 1813782.3 | 1797600 | 4533 | 1793067 | 335.0909 | 6.9595 | 1927977.0968 | 82.67% | 23.97% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-04-01 | 2024 | 2023 | 2023-04-01 | 30 | 12.3833 | 6.5866 | 1.4269 | 6.9819 | 1.4927 | 29.608 | 41.6955 | 3.0154 | 13.4183 | 100% |  |  | 100% |  |  | 78.73% | 79.71% | 22.9% | 1863880 | 1846334 | 4467 | 1841867 | 335.0909 | 7.1967 | 1954333.3333 | 81.04% | 24.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-04-02 | 2024 | 2023 | 2023-04-01 | 30 | 12.45 | 7.3319 | 1.6116 | 7.8002 | 1.6808 | 30.4803 | 56.147 | 6.2777 | 10.7233 | 100% |  |  | 100% |  |  | 78.93% | 78.89% | 25.65% | 2089277.8 | 2067333 | 4267 | 2063066 | 335.0909 | 7.1967 | 1954333.3333 | 81.04% | 24.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-04-03 | 2024 | 2023 | 2023-04-01 | 30 | 12.45 | 6.2606 | 1.3809 | 6.6322 | 1.4467 | 29.8248 | 57.7772 | 7.0802 | 12.7253 | 100% |  |  | 100% |  |  | 82.43% | 81.39% | 22.78% | 1854610.5 | 1836201 | 4333 | 1831868 | 335.0909 | 7.1967 | 1954333.3333 | 81.04% | 24.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-04-04 | 2024 | 2023 | 2023-04-01 | 30 | 12.3833 | 7.2647 | 1.6283 | 7.7095 | 1.7053 | 29.0764 | 42.0231 | 2.6324 | 6.804 | 100% |  |  | 100% |  |  | 79.03% | 79.63% | 25.39% | 2067315.9 | 2045933 | 4400 | 2041533 | 335.0909 | 7.1967 | 1954333.3333 | 81.04% | 24.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-04-05 | 2024 | 2023 | 2023-04-01 | 30 | 12.4 | 6.9886 | 1.5609 | 7.3969 | 1.6195 | 29.2 | 41.3048 | 2.741 | 7.5642 | 100% |  |  | 100% |  |  | 81.9% | 80.56% | 25.24% | 2056135.5 | 2034334 | 4267 | 2030067 | 335.0909 | 7.1967 | 1954333.3333 | 81.04% | 24.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-04-06 | 2024 | 2023 | 2023-04-01 | 30 | 12.45 | 6.6858 | 1.5328 | 7.0501 | 1.6088 | 30.48 | 57.3354 | 4.6466 | 9.2783 | 100% |  |  | 100% |  |  | 81.15% | 81.41% | 23.84% | 1941015.9 | 1921466 | 4266 | 1917200 | 335.0909 | 7.1967 | 1954333.3333 | 81.04% | 24.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-04-07 | 2024 | 2023 | 2023-04-01 | 30 | 12.4833 | 6.7695 | 1.5648 | 7.145 | 1.6433 | 32.2477 | 54.3131 | 5.7679 | 10.2028 | 100% |  |  | 100% |  |  | 81.26% | 81.52% | 24.19% | 1968791 | 1949801 | 4267 | 1945534 | 335.0909 | 7.1967 | 1954333.3333 | 81.04% | 24.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-04-08 | 2024 | 2023 | 2023-04-01 | 30 | 12.4667 | 6.5184 | 1.4846 | 6.8536 | 1.563 | 33.1194 | 57.0753 | 4.0353 | 10.2967 | 99.94% |  |  | 100% |  |  | 80.52% | 81.48% | 22.99% | 1871323.7 | 1853666 | 4400 | 1849266 | 335.0909 | 7.1967 | 1954333.3333 | 81.04% | 24.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-04-09 | 2024 | 2023 | 2023-04-01 | 30 | 12.3333 | 7.2474 | 1.635 | 7.6312 | 1.7221 | 33.667 | 67.4074 | 2.7913 | 6.7942 | 100% |  |  | 100% |  |  | 76.8% | 78.93% | 24.42% | 1987166.2 | 1968067 | 4267 | 1963800 | 335.0909 | 7.1967 | 1954333.3333 | 81.04% | 24.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-04-10 | 2024 | 2023 | 2023-04-01 | 30 | 12.5 | 5.3517 | 1.1878 | 5.5852 | 1.2492 | 33.6065 | 63.5784 | 3.7734 | 15.3645 | 100% |  |  | 100% |  |  | 79.82% | 81.16% | 18.58% | 1511836.8 | 1498134 | 4266 | 1493868 | 335.0909 | 7.1967 | 1954333.3333 | 81.04% | 24.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-04-11 | 2024 | 2023 | 2023-04-01 | 30 | 12.6667 | 4.3488 | 0.94898 | 4.4925 | 1.0002 | 33.5565 | 46.1694 | 2.568 | 6.1302 | 100% |  |  | 100% |  |  | 85.04% | 84.75% | 15.92% | 1293489.8 | 1284266 | 4134 | 1280132 | 335.0909 | 7.1967 | 1954333.3333 | 81.04% | 24.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-04-12 | 2024 | 2023 | 2023-04-01 | 30 | 12.6667 | 7.1026 | 1.5602 | 7.459 | 1.6406 | 32.9849 | 43.3789 | 3.1003 | 7.1165 | 100% |  |  | 100% |  |  | 80.67% | 81.01% | 25.07% | 2039145.3 | 2020334 | 4066 | 2016268 | 335.0909 | 7.1967 | 1954333.3333 | 81.04% | 24.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-04-13 | 2024 | 2023 | 2023-04-01 | 30 | 12.6667 | 7.014 | 1.5651 | 7.3524 | 1.644 | 34.2919 | 52.7 | 2.2077 | 6.0987 | 100% |  |  | 100% |  |  | 79.79% | 82.08% | 24.44% | 1986424.1 | 1969733 | 4000 | 1965733 | 335.0909 | 7.1967 | 1954333.3333 | 81.04% | 24.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-04-14 | 2024 | 2023 | 2023-04-01 | 30 | 12.6667 | 6.8374 | 1.5756 | 7.1563 | 1.658 | 36.1187 | 49.595 | 2.7163 | 5.594 | 100% |  |  | 100% |  |  | 79.93% | 82.38% | 23.83% | 1937713.2 | 1920801 | 4067 | 1916734 | 335.0909 | 7.1967 | 1954333.3333 | 81.04% | 24.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-04-15 | 2024 | 2023 | 2023-04-01 | 30 | 12.6667 | 6.8833 | 1.5182 | 7.15 | 1.612 | 35.5 | 49.05 | 3.6167 | 8.25 | 100% |  |  | 100% |  |  | 79.92% | 81.68% | 23.81% | 1933449 | 1916889 | 2200 | 1914689 | 335.0909 | 7.1967 | 1954333.3333 | 81.04% | 24.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-04-16 | 2024 | 2023 | 2023-04-01 | 30 | 12.5 | 7.5 | 1.682 | 7.8267 | 1.772 | 34.544 | 49.565 | 3.8117 | 9.0767 | 100% |  |  | 100% |  |  | 78.28% | 79.88% | 25.53% | 2073568.7 | 2055000 | 2000 | 2053000 | 335.0909 | 7.1967 | 1954333.3333 | 81.04% | 24.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-04-17 | 2024 | 2023 | 2023-04-01 | 30 | 12.8167 | 7.3665 | 1.6459 | 7.682 | 1.7367 | 34.3654 | 49.1288 | 4.6868 | 9.623 | 100% |  |  | 100% |  |  | 78.9% | 80.34% | 25.25% | 2051248.7 | 2033400 | 2400 | 2031000 | 335.0909 | 7.1967 | 1954333.3333 | 81.04% | 24.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-04-18 | 2024 | 2023 | 2023-04-01 | 30 | 12.7333 | 7.1999 | 1.6181 | 7.4859 | 1.7097 | 34.2985 | 48.845 | 4.2957 | 10.2477 | 100% |  |  | 100% |  |  | 78.79% | 80.34% | 24.58% | 1995963.5 | 1979667 | 3267 | 1976400 | 335.0909 | 7.1967 | 1954333.3333 | 81.04% | 24.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-04-19 | 2024 | 2023 | 2023-04-01 | 30 | 12.7 | 6.1856 | 1.418 | 6.3597 | 1.5056 | 31.6436 | 43.45 | 4.646 | 8.4665 | 100% |  |  | 100% |  |  | 81.82% | 81.51% | 21.68% | 1761802.4 | 1747867 | 4266 | 1743601 | 335.0909 | 7.1967 | 1954333.3333 | 81.04% | 24.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-04-20 | 2024 | 2023 | 2023-04-01 | 30 | 12.9167 | 6.9286 | 1.6188 | 7.18 | 1.7147 | 32.5544 | 45.6 | 3.9854 | 9.4023 | 100% |  |  | 100% |  |  | 80.85% | 81.7% | 24.19% | 1966417.3 | 1949467 | 4267 | 1945200 | 335.0909 | 7.1967 | 1954333.3333 | 81.04% | 24.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-04-21 | 2024 | 2023 | 2023-04-01 | 30 | 12.85 | 7.712 | 1.7726 | 7.987 | 1.8607 | 32.8156 | 47.3 | 3.6139 | 9.2818 | 100% |  |  | 100% |  |  | 77.62% | 79.08% | 25.83% | 2099866.2 | 2081533 | 4200 | 2077333 | 335.0909 | 7.1967 | 1954333.3333 | 81.04% | 24.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-04-22 | 2024 | 2023 | 2023-04-01 | 30 | 12.8167 | 7.7878 | 1.8127 | 8.0665 | 1.9059 | 33.5934 | 48.1 | 2.6599 | 6.5075 | 100% |  |  | 100% |  |  | 77.67% | 79.95% | 26.11% | 2122759.8 | 2103734 | 4267 | 2099467 | 335.0909 | 7.1967 | 1954333.3333 | 81.04% | 24.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-04-23 | 2024 | 2023 | 2023-04-01 | 30 | 12.8667 | 7.7928 | 1.8142 | 8.029 | 1.9079 | 32.339 | 44.75 | 3.9315 | 8.4002 | 100% |  |  | 100% |  |  | 78.43% | 79.79% | 26.24% | 2133696.7 | 2114467 | 4333 | 2110134 | 335.0909 | 7.1967 | 1954333.3333 | 81.04% | 24.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-04-24 | 2024 | 2023 | 2023-04-01 | 30 | 13.0333 | 7.5254 | 1.747 | 7.7453 | 1.8378 | 32.0663 | 43.85 | 3.6871 | 8.1227 | 100% |  |  | 100% |  |  | 80.49% | 81.39% | 25.98% | 2111855 | 2093266 | 4267 | 2088999 | 335.0909 | 7.1967 | 1954333.3333 | 81.04% | 24.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-04-25 | 2024 | 2023 | 2023-04-01 | 30 | 12.9 | 7.3143 | 1.7001 | 7.5462 | 1.7847 | 33.519 | 46.65 | 3.784 | 8.0458 | 100% |  |  | 100% |  |  | 80.36% | 81.81% | 25.27% | 2054971.3 | 2036334 | 4200 | 2032134 | 335.0909 | 7.1967 | 1954333.3333 | 81.04% | 24.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-04-26 | 2024 | 2023 | 2023-04-01 | 30 | 12.9333 | 5.8007 | 1.3573 | 5.9565 | 1.4251 | 34.1709 | 45.15 | 5.5026 | 16.821 | 100% |  |  | 100% |  |  | 81.37% | 82.32% | 20.2% | 1642542.4 | 1628400 | 4200 | 1624200 | 335.0909 | 7.1967 | 1954333.3333 | 81.04% | 24.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-04-27 | 2024 | 2023 | 2023-04-01 | 30 | 13.0833 | 5.0232 | 1.1401 | 5.1663 | 1.2007 | 32.0129 | 42.95 | 3.4375 | 11.3645 | 100% |  |  | 100% |  |  | 83.93% | 84.16% | 18.07% | 1469405.6 | 1457267 | 4333 | 1452934 | 335.0909 | 7.1967 | 1954333.3333 | 81.04% | 24.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-04-28 | 2024 | 2023 | 2023-04-01 | 30 | 12.9 | 4.6665 | 0.94455 | 4.7817 | 0.99322 | 28.6314 | 38.9 | 3.6626 | 12.6978 | 100% |  |  | 100% |  |  | 79.7% | 79.1% | 15.88% | 1292215.2 | 1281400 | 4333 | 1277067 | 335.0909 | 7.1967 | 1954333.3333 | 81.04% | 24.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-04-29 | 2024 | 2023 | 2023-04-01 | 30 | 13.1167 | 7.2488 | 1.3421 | 7.4701 | 1.4118 | 26.7541 | 43.35 | 3.2266 | 7.2538 | 100% |  |  | 100% |  |  | 79.95% | 78.94% | 24.89% | 2023067.9 | 2004867 | 3467 | 2001400 | 335.0909 | 7.1967 | 1954333.3333 | 81.04% | 24.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-04-30 | 2024 | 2023 | 2023-04-01 | 30 | 13.1333 | 5.9235 | 1.1733 | 6.0782 | 1.2506 | 25.8763 | 40.05 | 3.8627 | 8.5422 | 100% |  |  | 100% |  |  | 87.03% | 81.14% | 22.04% | 1792091.6 | 1776533 | 4000 | 1772533 | 335.0909 | 7.1967 | 1954333.3333 | 81.04% | 24.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-05-01 | 2024 | 2023 | 2023-05-01 | 31 | 13.1833 | 6.2141 | 1.1866 | 6.4061 | 1.251 | 26.9838 | 40.65 | 2.8221 | 9.5077 | 99.32% |  |  | 100% |  |  | 79.72% | 79.02% | 21.28% | 1731562.9 | 1715467 | 4267 | 1711200 | 335.0909 | 7.029 | 1992903.2258 | 84.61% | 24.78% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-05-02 | 2024 | 2023 | 2023-05-01 | 31 | 13.0833 | 6.9783 | 1.3571 | 7.1945 | 1.4289 | 30.6236 | 47.05 | 1.8906 | 5.9573 | 99.98% |  |  | 100% |  |  | 79.75% | 79.93% | 23.91% | 1944100.2 | 1926733 | 4200 | 1922533 | 335.0909 | 7.029 | 1992903.2258 | 84.61% | 24.78% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-05-03 | 2024 | 2023 | 2023-05-01 | 31 | 13.0833 | 7.2335 | 1.4126 | 7.475 | 1.4919 | 30.4961 | 45.8197 | 2.2056 | 5.755 | 99.28% |  |  | 100% |  |  | 79.89% | 80.77% | 24.88% | 2022803.9 | 2005267 | 4200 | 2001067 | 335.0909 | 7.029 | 1992903.2258 | 84.61% | 24.78% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-05-04 | 2024 | 2023 | 2023-05-01 | 31 | 13.1833 | 6.7678 | 1.3699 | 6.98 | 1.4514 | 33.655 | 48.5 | 2.1105 | 7.6563 | 99.98% |  |  | 100% |  |  | 79.57% | 80.83% | 23.14% | 1882312 | 1865067 | 4066 | 1861001 | 335.0909 | 7.029 | 1992903.2258 | 84.61% | 24.78% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-05-05 | 2024 | 2023 | 2023-05-01 | 31 | 12.9167 | 6.7236 | 1.3882 | 6.9104 | 1.4741 | 33.1723 | 46.9 | 2.5627 | 9.3857 | 99.98% |  |  | 100% |  |  | 80.81% | 81.54% | 23.27% | 1892395.6 | 1875334 | 4134 | 1871200 | 335.0909 | 7.029 | 1992903.2258 | 84.61% | 24.78% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-05-06 | 2024 | 2023 | 2023-05-01 | 31 | 13.1167 | 6.9931 | 1.4725 | 7.1714 | 1.565 | 35.5393 | 48.8 | 3.6663 | 8.5048 | 99.98% |  |  | 100% |  |  | 81.7% | 82.25% | 24.41% | 1983854.1 | 1967333 | 4133 | 1963200 | 335.0909 | 7.029 | 1992903.2258 | 84.61% | 24.78% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-05-07 | 2024 | 2023 | 2023-05-01 | 31 | 13.1833 | 7.2994 | 1.5625 | 7.4891 | 1.6625 | 37.1246 | 48.25 | 6.0864 | 11.0278 | 99.98% |  |  | 100% |  |  | 79.71% | 80.36% | 24.87% | 2021783.6 | 2004334 | 4067 | 2000267 | 335.0909 | 7.029 | 1992903.2258 | 84.61% | 24.78% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-05-08 | 2024 | 2023 | 2023-05-01 | 31 | 13.1833 | 7.9576 | 1.7253 | 8.1313 | 1.8363 | 36.0958 | 48.3 | 5.2447 | 9.9357 | 99.72% |  |  | 100% |  |  | 78.28% | 79.26% | 26.52% | 2155815.1 | 2136933 | 4133 | 2132800 | 335.0909 | 7.029 | 1992903.2258 | 84.61% | 24.78% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-05-09 | 2024 | 2023 | 2023-05-01 | 31 | 13.1667 | 7.8903 | 1.7387 | 8.0024 | 1.852 | 36.3392 | 33.8437 | 2.8287 | 6.765 | 99.98% |  |  | 100% |  |  | 78.94% | 80.74% | 26.32% | 2139473.4 | 2120800 | 4067 | 2116733 | 335.0909 | 7.029 | 1992903.2258 | 84.61% | 24.78% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-05-10 | 2024 | 2023 | 2023-05-01 | 31 | 13.2 | 7.6729 | 1.7393 | 7.5202 | 1.8504 | 37.226 | 50.85 | 3.2954 | 7.2883 | 99.6% |  |  | 100% |  |  | 83.94% | 85.35% | 26.3% | 2137900.3 | 2119200 | 4000 | 2115200 | 335.0909 | 7.029 | 1992903.2258 | 84.61% | 24.78% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-05-11 | 2024 | 2023 | 2023-05-01 | 31 | 13.1833 | 7.6902 | 1.7447 | 6.7694 | 1.8617 | 39.1237 | 53.25 | 2.7201 | 7.1918 | 98.83% |  |  | 100% |  |  | 92.27% | 93.71% | 26.03% | 2115647.8 | 2097134 | 4066 | 2093068 | 335.0909 | 7.029 | 1992903.2258 | 84.61% | 24.78% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-05-12 | 2024 | 2023 | 2023-05-01 | 31 | 13.1833 | 7.5859 | 1.7123 | 7.2543 | 1.8261 | 40.5017 | 53.3 | 4.1174 | 8.3428 | 99.37% |  |  | 100% |  |  | 85.58% | 82.69% | 25.87% | 2101894.4 | 2084333 | 3934 | 2080399 | 335.0909 | 7.029 | 1992903.2258 | 84.61% | 24.78% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-05-13 | 2024 | 2023 | 2023-05-01 | 31 | 13.1333 | 7.7844 | 1.6898 | 7.9157 | 1.8041 | 40.7402 | 51.7 | 6.0612 | 11.1865 | 99.97% |  |  | 100% |  |  | 77.85% | 79.68% | 25.68% | 2086371 | 2069067 | 4200 | 2064867 | 335.0909 | 7.029 | 1992903.2258 | 84.61% | 24.78% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-05-14 | 2024 | 2023 | 2023-05-01 | 31 | 13.25 | 6.9685 | 1.4917 | 7.1166 | 1.5897 | 37.2934 | 49.6 | 4.4433 | 9.5297 | 99.98% |  |  | 100% |  |  | 79.9% | 81.14% | 23.69% | 1926660.4 | 1909467 | 4000 | 1905467 | 335.0909 | 7.029 | 1992903.2258 | 84.61% | 24.78% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-05-15 | 2024 | 2023 | 2023-05-01 | 31 | 13.1 | 6.924 | 1.6237 | 7.0534 | 1.7365 | 35.5114 | 47.05 | 8.7433 | 13.0015 | 89.01% |  |  | 100% |  |  | 76.91% | 76.24% | 22.6% | 1838944.7 | 1821800 | 4000 | 1817800 | 335.0909 | 7.029 | 1992903.2258 | 84.61% | 24.78% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-05-16 | 2024 | 2023 | 2023-05-01 | 31 | 13.05 | 7.3836 | 1.6091 | 7.538 | 1.7204 | 35.4778 | 47.2 | 6.9039 | 11.2022 | 99.98% |  |  | 100% |  |  | 79.1% | 78.97% | 24.84% | 2020860.9 | 2002200 | 4200 | 1998000 | 335.0909 | 7.029 | 1992903.2258 | 84.61% | 24.78% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-05-17 | 2024 | 2023 | 2023-05-01 | 31 | 13.0833 | 7.2962 | 1.5901 | 7.4324 | 1.7009 | 35.0579 | 47.95 | 6.3726 | 10.1755 | 99.98% |  |  | 100% |  |  | 80.57% | 80.48% | 24.95% | 2027803.5 | 2010667 | 4133 | 2006534 | 335.0909 | 7.029 | 1992903.2258 | 84.61% | 24.78% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-05-18 | 2024 | 2023 | 2023-05-01 | 31 | 13.1333 | 7.1241 | 1.5356 | 7.238 | 1.6435 | 33.481 | 48.9 | 3.1187 | 6.5923 | 99.98% |  |  | 100% |  |  | 78.79% | 79.06% | 23.76% | 1930898.3 | 1914867 | 4000 | 1910867 | 335.0909 | 7.029 | 1992903.2258 | 84.61% | 24.78% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-05-19 | 2024 | 2023 | 2023-05-01 | 31 | 13.2333 | 7.2094 | 1.6191 | 7.4573 | 1.7314 | 37.5634 | 51.85 | 2.9074 | 7.7492 | 99.98% |  |  | 100% |  |  | 79.78% | 81.53% | 24.79% | 2014710.8 | 1996867 | 3200 | 1993667 | 335.0909 | 7.029 | 1992903.2258 | 84.61% | 24.78% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-05-20 | 2024 | 2023 | 2023-05-01 | 31 | 13.2167 | 7.5777 | 1.435 | 7.7573 | 1.5624 | 38.1385 | 49.5309 | 5.8282 | 9.2666 | 99.98% |  |  | 100% |  |  | 78.7% | 81.9% | 25.44% | 2063690.3 | 2049200 | 3467 | 2045733 | 335.0909 | 7.029 | 1992903.2258 | 84.61% | 24.78% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-05-21 | 2024 | 2023 | 2023-05-01 | 31 | 13.2 | 7.7561 | 1.7124 | 7.8183 | 1.8325 | 27.8548 | 36.1924 | 5.41 | 11.379 | 99.98% |  |  | 100% |  |  | 78.39% | 78.69% | 25.54% | 2081229 | 2058000 | 4200 | 2053800 | 335.0909 | 7.029 | 1992903.2258 | 84.61% | 24.78% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-05-22 | 2024 | 2023 | 2023-05-01 | 31 | 13.1167 | 7.8469 | 1.7324 | 7.8852 | 1.8542 | 36.0948 | 48.6608 | 6.5267 | 11.1339 | 99.98% |  |  | 100% |  |  | 78.82% | 79.1% | 25.9% | 2104292.1 | 2086534 | 3933 | 2082601 | 335.0909 | 7.029 | 1992903.2258 | 84.61% | 24.78% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-05-23 | 2024 | 2023 | 2023-05-01 | 31 | 13.0833 | 7.2357 | 1.5993 | 7.3059 | 1.7076 | 34.9083 | 47.7228 | 5.9768 | 10.9592 | 99.98% |  |  | 100% |  |  | 79.18% | 79.17% | 24.1% | 1959531.6 | 1942600 | 4200 | 1938400 | 335.0909 | 7.029 | 1992903.2258 | 84.61% | 24.78% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-05-24 | 2024 | 2023 | 2023-05-01 | 31 | 13.2167 | 7.4454 | 1.6062 | 7.4795 | 1.7224 | 36.0381 | 49.2488 | 6.426 | 11.0047 | 99.98% |  |  | 100% |  |  | 80.31% | 80.61% | 25.03% | 2034435.2 | 2016867 | 4000 | 2012867 | 335.0909 | 7.029 | 1992903.2258 | 84.61% | 24.78% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-05-25 | 2024 | 2023 | 2023-05-01 | 31 | 12.6333 | 6.6956 | 1.484 | 6.7604 | 1.5921 | 34.693 | 46.3379 | 7.5373 | 12.43 | 99.38% |  |  | 100% |  |  | 82.25% | 81.42% | 23.17% | 1882897.4 | 1867466 | 4133 | 1863333 | 335.0909 | 7.029 | 1992903.2258 | 84.61% | 24.78% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-05-26 | 2024 | 2023 | 2023-05-01 | 31 | 13.2 | 6.8835 | 1.4926 | 6.9221 | 1.5803 | 35.0867 | 45.3018 | 8.2122 | 12.9517 | 99.51% |  |  | 100% |  |  | 82.35% | 80.97% | 23.75% | 1930247.1 | 1914134 | 4067 | 1910067 | 335.0909 | 7.029 | 1992903.2258 | 84.61% | 24.78% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-05-27 | 2024 | 2023 | 2023-05-01 | 31 | 13.2333 | 6.1203 | 1.2858 | 6.1753 | 1.3934 | 33.8477 | 46.3607 | 5.3223 | 10.3006 | 99.53% |  |  | 100% |  |  | 80.86% | 79.92% | 20.81% | 1690630.7 | 1677400 | 4133 | 1673267 | 335.0909 | 7.029 | 1992903.2258 | 84.61% | 24.78% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-05-28 | 2024 | 2023 | 2023-05-01 | 31 | 13.0167 | 4.8034 | 1.0113 | 4.8447 | 1.0838 | 33.5218 | 45.8867 | 5.4761 | 11.3436 | 99.91% |  |  | 100% |  |  | 82% | 81.36% | 16.55% | 1347483.5 | 1336067 | 4867 | 1331200 | 335.0909 | 7.029 | 1992903.2258 | 84.61% | 24.78% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-05-29 | 2024 | 2023 | 2023-05-01 | 31 | 13.3167 | 6.7012 | 1.1884 | 6.7302 | 1.2893 | 28.2219 | 42.2017 | 3.0826 | 9.4575 | 99.91% |  |  | 100% |  |  | 82.64% | 81.39% | 23.17% | 1883715.4 | 1867733 | 4067 | 1863666 | 335.0909 | 7.029 | 1992903.2258 | 84.61% | 24.78% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-05-30 | 2024 | 2023 | 2023-05-01 | 31 | 13.0833 | 3.2589 | 0.47375 | 3.2584 | 0.51489 | 23.9893 | 29.275 | 3.3152 | 10.0647 | 98.53% |  |  | 100% |  |  | 90.43% | 84.74% | 12.28% | 998000.2 | 991467 | 4133 | 987334 | 335.0909 | 7.029 | 1992903.2258 | 84.61% | 24.78% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-05-31 | 2024 | 2023 | 2023-05-01 | 31 | 13.6 | 7.4477 | 1.4043 | 7.3865 | 1.5039 | 29.81 | 43.695 | 3.6882 | 7.4756 | 99.84% |  |  | 100% |  |  | 82.31% | 81.23% | 25.33% | 2059028.3 | 2041334 | 4133 | 2037201 | 335.0909 | 7.029 | 1992903.2258 | 84.61% | 24.78% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-06-01 | 2024 | 2023 | 2023-06-01 | 30 | 13.3 | 4.4114 | 0.90901 | 4.4174 | 0.97759 | 30.1928 | 40.4151 | 4.555 | 7.6308 | 99.91% |  |  | 100% |  |  | 84.53% | 82.14% | 15.56% | 1263691.4 | 1255400 | 4134 | 1251266 | 335.0909 | 6.4267 | 1790000 | 83.12% | 22.26% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-06-02 | 2024 | 2023 | 2023-06-01 | 30 | 13.35 | 6.7544 | 1.4408 | 6.7634 | 1.5411 | 33.2591 | 47.7268 | 3.411 | 6.7962 | 99.98% |  |  | 100% |  |  | 80.57% | 80.33% | 22.71% | 1845315 | 1830266 | 4200 | 1826066 | 335.0909 | 6.4267 | 1790000 | 83.12% | 22.26% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-06-03 | 2024 | 2023 | 2023-06-01 | 30 | 13.35 | 6.8931 | 1.4949 | 6.8515 | 1.6073 | 35.1911 | 48.6011 | 3.7479 | 7.6247 | 99.98% |  |  | 100% |  |  | 81.08% | 81.3% | 23.15% | 1880086.6 | 1865601 | 4066 | 1861535 | 335.0909 | 6.4267 | 1790000 | 83.12% | 22.26% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-06-04 | 2024 | 2023 | 2023-06-01 | 30 | 13.2333 | 7.1319 | 1.3152 | 7.1296 | 1.4114 | 29.8531 | 41.7172 | 4.2762 | 7.8972 | 99.98% |  |  | 100% |  |  | 82.58% | 81.4% | 24.53% | 1993857 | 1976800 | 4000 | 1972800 | 335.0909 | 6.4267 | 1790000 | 83.12% | 22.26% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-06-05 | 2024 | 2023 | 2023-06-01 | 30 | 12.9167 | 6.7246 | 1.3445 | 6.5861 | 1.4365 | 33.9329 | 48.384 | 2.6121 | 6.8122 | 99.98% |  |  | 100% |  |  | 83.49% | 83.7% | 22.91% | 1863080.5 | 1846800 | 4134 | 1842666 | 335.0909 | 6.4267 | 1790000 | 83.12% | 22.26% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-06-06 | 2024 | 2023 | 2023-06-01 | 30 | 13.4667 | 7.3544 | 1.5385 | 7.145 | 1.6526 | 32.8816 | 47.2963 | 4.3264 | 11.409 | 99.35% |  |  | 100% |  |  | 82.58% | 82.85% | 24.59% | 1998134.1 | 1981200 | 4000 | 1977200 | 335.0909 | 6.4267 | 1790000 | 83.12% | 22.26% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-06-07 | 2024 | 2023 | 2023-06-01 | 30 | 13.45 | 7.3367 | 1.4002 | 7.289 | 1.4933 | 33.8578 | 48.4035 | 3.3604 | 6.6217 | 99.93% |  |  | 100% |  |  | 81.12% | 81.68% | 24.64% | 2001844.1 | 1985267 | 3933 | 1981334 | 335.0909 | 6.4267 | 1790000 | 83.12% | 22.26% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-06-08 | 2024 | 2023 | 2023-06-01 | 30 | 13.4 | 7.5828 | 1.5878 | 7.4933 | 1.7043 | 35.4016 | 47.8852 | 5.4693 | 9.4655 | 99.83% |  |  | 100% |  |  | 77.9% | 81.33% | 24.32% | 1975834.1 | 1960133 | 4000 | 1956133 | 335.0909 | 6.4267 | 1790000 | 83.12% | 22.26% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-06-09 | 2024 | 2023 | 2023-06-01 | 30 | 13.3667 | 7.6565 | 1.5376 | 7.0702 | 1.6411 | 32.986 | 45.4901 | 7.363 | 11.2887 | 99.78% |  |  | 100% |  |  | 67.37% | 84.14% | 19.85% | 1609927.9 | 1600067 | 3933 | 1596134 | 335.0909 | 6.4267 | 1790000 | 83.12% | 22.26% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-06-10 | 2024 | 2023 | 2023-06-01 | 30 | 13.3333 | 7.5381 | 1.6428 | 7.1785 | 1.7703 | 35.228 | 46.0838 | 8.5649 | 13.4425 | 99.97% |  |  | 100% |  |  | 65.15% | 85.13% | 19.49% | 1580581.5 | 1571000 | 3934 | 1567066 | 335.0909 | 6.4267 | 1790000 | 83.12% | 22.26% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-06-11 | 2024 | 2023 | 2023-06-01 | 30 | 13.3333 | 7.6843 | 1.6237 | 7.7247 | 1.7365 | 35.5114 | 47.0607 | 8.7433 | 13.0015 | 99.98% |  |  | 100% |  |  | 65.43% | 79.96% | 21.06% | 1708489.3 | 1697667 | 4000 | 1693667 | 335.0909 | 6.4267 | 1790000 | 83.12% | 22.26% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-06-12 | 2024 | 2023 | 2023-06-01 | 30 | 13.4 | 7.5694 | 1.6404 | 7.2519 | 1.7687 | 35.563 | 49.1166 | 5.5333 | 9.8138 | 99.98% |  |  | 100% |  |  | 67.89% | 85.14% | 20.51% | 1664221.5 | 1653667 | 3933 | 1649734 | 335.0909 | 6.4267 | 1790000 | 83.12% | 22.26% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-06-13 | 2024 | 2023 | 2023-06-01 | 30 | 13.0667 | 7.4842 | 1.6117 | 7.2036 | 1.7419 | 34.2065 | 48.19 | 6.0202 | 10.9893 | 99.98% |  |  | 100% |  |  | 67.43% | 82.88% | 20.24% | 1640369.7 | 1630067 | 2467 | 1627600 | 335.0909 | 6.4267 | 1790000 | 83.12% | 22.26% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-06-14 | 2024 | 2023 | 2023-06-01 | 30 | 12.9833 | 6.954 | 1.4974 | 6.7454 | 1.6161 | 34.0052 | 46.3396 | 6.8853 | 12.3502 | 99.99% |  |  | 100% |  |  | 77.38% | 83.33% | 21.75% | 1764692.4 | 1752800 | 3866 | 1748934 | 335.0909 | 6.4267 | 1790000 | 83.12% | 22.26% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-06-15 | 2024 | 2023 | 2023-06-01 | 30 | 13.1833 | 4.9731 | 1.0012 | 4.9039 | 1.0741 | 30.5947 | 39.5696 | 5.6629 | 15.8393 | 99.46% |  |  | 100% |  |  | 83.12% | 81.14% | 16.98% | 1380546.7 | 1369800 | 3867 | 1365933 | 335.0909 | 6.4267 | 1790000 | 83.12% | 22.26% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-06-16 | 2024 | 2023 | 2023-06-01 | 30 | 12.9333 | 3.7525 | 0.71632 | 3.7195 | 0.77092 | 28.2362 | 35.5391 | 6.1535 | 11.9665 | 99.88% |  |  | 100% |  |  | 89.77% | 86.13% | 13.91% | 1131669 | 1122933 | 4067 | 1118866 | 335.0909 | 6.4267 | 1790000 | 83.12% | 22.26% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-06-17 | 2024 | 2023 | 2023-06-01 | 30 | 12.8333 | 1.6801 | 0.13966 | 1.6837 | 0.15586 | 26.4184 | 27.9802 | 7.8439 | 12.8225 | 99.98% |  |  | 100% |  |  | 94.47% | 88.3% | 6.628% | 543403 | 539067 | 6066 | 533001 | 335.0909 | 6.4267 | 1790000 | 83.12% | 22.26% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-06-18 | 2024 | 2023 | 2023-06-01 | 30 | 13.2667 | 5.2864 | 0.81807 | 5.2053 | 0.89227 | 31.2253 | 39.5132 | 4.2496 | 7.7333 | 99.98% |  |  | 100% |  |  | 88.34% | 85.74% | 19.16% | 1552792.5 | 1544933 | 4067 | 1540866 | 335.0909 | 6.4267 | 1790000 | 83.12% | 22.26% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-06-19 | 2024 | 2023 | 2023-06-01 | 30 | 13.2667 | 7.0873 | 1.2911 | 6.9491 | 1.3948 | 32.4899 | 45.5546 | 5.4941 | 8.7677 | 99.98% |  |  | 100% |  |  | 83.68% | 82.77% | 24.23% | 1966084.4 | 1952267 | 3733 | 1948534 | 335.0909 | 6.4267 | 1790000 | 83.12% | 22.26% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-06-20 | 2024 | 2023 | 2023-06-01 | 30 | 13.3 | 7.3502 | 1.4455 | 7.1882 | 1.5665 | 32.6637 | 45.3627 | 6.781 | 9.8315 | 99.98% |  |  | 100% |  |  | 76.09% | 84.1% | 22.79% | 1846569.6 | 1836600 | 3934 | 1832666 | 335.0909 | 6.4267 | 1790000 | 83.12% | 22.26% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-06-21 | 2024 | 2023 | 2023-06-01 | 30 | 13.1167 | 7.5827 | 1.5296 | 7.3872 | 1.6596 | 33.348 | 37.0526 | 5.9393 | 10.1697 | 99.98% |  |  | 100% |  |  | 82.87% | 82.51% | 25.51% | 2071161.1 | 2055334 | 3866 | 2051468 | 335.0909 | 6.4267 | 1790000 | 83.12% | 22.26% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-06-22 | 2024 | 2023 | 2023-06-01 | 30 | 13.2333 | 7.1588 | 1.4728 | 7.0625 | 1.6026 | 33.1215 | 45.6407 | 6.1923 | 9.6827 | 99.98% |  |  | 100% |  |  | 71.45% | 82.36% | 21.03% | 1703365.2 | 1694867 | 3934 | 1690933 | 335.0909 | 6.4267 | 1790000 | 83.12% | 22.26% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-06-23 | 2024 | 2023 | 2023-06-01 | 30 | 13.6667 | 7.5176 | 1.5338 | 7.3362 | 1.6632 | 33.647 | 46.3 | 6.1589 | 10.0878 | 99.98% |  |  | 100% |  |  | 72.19% | 83.48% | 22.07% | 1788173.3 | 1778533 | 3933 | 1774600 | 335.0909 | 6.4267 | 1790000 | 83.12% | 22.26% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-06-24 | 2024 | 2023 | 2023-06-01 | 30 | 13.6667 | 7.3143 | 1.4892 | 7.1284 | 1.6156 | 33.5777 | 46.6 | 5.4981 | 9.0747 | 99.98% |  |  | 100% |  |  | 82.07% | 83.45% | 24.38% | 1978391.5 | 1964400 | 3933 | 1960467 | 335.0909 | 6.4267 | 1790000 | 83.12% | 22.26% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-06-25 | 2024 | 2023 | 2023-06-01 | 30 | 13.6667 | 7.2599 | 1.4598 | 7.1144 | 1.5802 | 34.0951 | 47.8 | 4.7459 | 9.321 | 99.98% |  |  | 100% |  |  | 83.39% | 82.87% | 24.72% | 2007470.8 | 1992067 | 4000 | 1988067 | 335.0909 | 6.4267 | 1790000 | 83.12% | 22.26% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-06-26 | 2024 | 2023 | 2023-06-01 | 30 | 13.6667 | 6.6326 | 1.3409 | 6.4775 | 1.4532 | 33.8974 | 48 | 3.5922 | 6.7903 | 99.98% |  |  | 100% |  |  | 84.81% | 84.42% | 22.89% | 1857152.1 | 1845000 | 4134 | 1840866 | 335.0909 | 6.4267 | 1790000 | 83.12% | 22.26% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-06-27 | 2024 | 2023 | 2023-06-01 | 30 | 13.3333 | 5.8519 | 0.95036 | 5.7939 | 1.0276 | 30.9163 | 44.98 | 3.4041 | 9.4405 | 99.98% |  |  | 100% |  |  | 84.76% | 84.36% | 20.46% | 1661797.7 | 1649934 | 4266 | 1645668 | 335.0909 | 6.4267 | 1790000 | 83.12% | 22.26% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-06-28 | 2024 | 2023 | 2023-06-01 | 30 | 13.6667 | 7.4861 | 1.4094 | 7.3053 | 1.5302 | 33.2122 | 49.79 | 2.5482 | 5.69 | 99.27% |  |  | 100% |  |  | 82.95% | 83.46% | 25.25% | 2049897.5 | 2034733 | 4067 | 2030666 | 335.0909 | 6.4267 | 1790000 | 83.12% | 22.26% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-06-29 | 2024 | 2023 | 2023-06-01 | 30 | 12.3333 | 6.5306 | 1.2523 | 6.43 | 1.3513 | 33.1338 | 39.0451 | 4.2197 | 13.0042 | 99.95% |  |  | 100% |  |  | 84.15% | 84.2% | 22.55% | 1831759.1 | 1817534 | 4400 | 1813134 | 335.0909 | 6.4267 | 1790000 | 83.12% | 22.26% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-06-30 | 2024 | 2023 | 2023-06-01 | 30 | 13.6667 | 7.2983 | 1.3959 | 7.1348 | 1.5098 | 32.5739 | 46.5851 | 4.9138 | 7.714 | 99.98% |  |  | 100% |  |  | 83.91% | 83.23% | 24.94% | 2024481.1 | 2009933 | 3933 | 2006000 | 335.0909 | 6.4267 | 1790000 | 83.12% | 22.26% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-07-01 | 2024 | 2023 | 2023-07-01 | 31 | 13.2667 | 7.423 | 1.2096 | 7.2197 | 1.3144 | 32.8997 | 47.3324 | 4.0743 | 7.0913 | 99.98% |  |  | 100% |  |  | 81.12% | 84.52% | 24.4% | 1980784.7 | 1966600 | 4000 | 1962600 | 335.0909 | 5.4484 | 1587419.3548 | 86.95% | 19.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-07-02 | 2024 | 2023 | 2023-07-01 | 31 | 13.45 | 7.4826 | 1.381 | 7.2842 | 1.4918 | 33.7154 | 47.4854 | 4.4633 | 7.1223 | 95.1% |  |  | 100% |  |  | 79.69% | 80.45% | 24.19% | 1961908.5 | 1949067 | 3867 | 1945200 | 335.0909 | 5.4484 | 1587419.3548 | 86.95% | 19.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-07-03 | 2024 | 2023 | 2023-07-01 | 31 | 13.4 | 7.6014 | 1.4502 | 7.3727 | 1.5643 | 34.9213 | 48.161 | 4.3834 | 7.863 | 99.98% |  |  | 100% |  |  | 83.09% | 84.32% | 25.53% | 2072326.1 | 2056734 | 3933 | 2052801 | 335.0909 | 5.4484 | 1587419.3548 | 86.95% | 19.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-07-04 | 2024 | 2023 | 2023-07-01 | 31 | 13.35 | 7.4816 | 1.4525 | 7.2858 | 1.5722 | 35.249 | 47.4439 | 5.5977 | 9.014 | 99.98% |  |  | 100% |  |  | 83.18% | 84.23% | 25.25% | 2049422.3 | 2034733 | 3867 | 2030866 | 335.0909 | 5.4484 | 1587419.3548 | 86.95% | 19.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-07-05 | 2024 | 2023 | 2023-07-01 | 31 | 13.3833 | 6.8308 | 1.3443 | 6.7019 | 1.4507 | 33.1734 | 45.3814 | 4.9946 | 9.3977 | 99.98% |  |  | 100% |  |  | 85.42% | 85.37% | 23.85% | 1935327.6 | 1922200 | 3933 | 1918267 | 335.0909 | 5.4484 | 1587419.3548 | 86.95% | 19.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-07-06 | 2024 | 2023 | 2023-07-01 | 31 | 13.1667 | 6.2153 | 1.1854 | 6.1339 | 1.2845 | 32.7806 | 46.8509 | 2.6746 | 10.6018 | 99.98% |  |  | 100% |  |  | 85.18% | 85.85% | 21.77% | 1765152.8 | 1754867 | 4134 | 1750733 | 335.0909 | 5.4484 | 1587419.3548 | 86.95% | 19.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-07-07 | 2024 | 2023 | 2023-07-01 | 31 | 13.25 | 4.5303 | 0.72613 | 4.6633 | 0.78442 | 27.4412 | 39.0473 | 2.7618 | 8.2528 | 99.75% |  |  | 100% |  |  | 84.89% | 84.43% | 16.5% | 1340585.1 | 1330800 | 4200 | 1326600 | 335.0909 | 5.4484 | 1587419.3548 | 86.95% | 19.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-07-08 | 2024 | 2023 | 2023-07-01 | 31 | 13.2833 | 4.0592 | 0.6491 | 3.9871 | 0.71194 | 28.3642 | 36.8007 | 2.262 | 5.2212 | 99.98% |  |  | 100% |  |  | 88.32% | 86.34% | 14.67% | 1191040.2 | 1184067 | 4066 | 1180001 | 335.0909 | 5.4484 | 1587419.3548 | 86.95% | 19.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-07-09 | 2024 | 2023 | 2023-07-01 | 31 | 13.1333 | 6.6128 | 0.96152 | 6.4291 | 1.0287 | 31.0181 | 44.5227 | 2.6136 | 4.8017 | 99.62% |  |  | 100% |  |  | 83.31% | 83.77% | 22.32% | 1812423.2 | 1798933 | 4067 | 1794866 | 335.0909 | 5.4484 | 1587419.3548 | 86.95% | 19.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-07-10 | 2024 | 2023 | 2023-07-01 | 31 | 13.4333 | 5.0096 | 0.79398 | 4.8944 | 0.86205 | 31.9626 | 42.1463 | 2.6392 | 5.3595 | 99.98% |  |  | 100% |  |  | 88.91% | 87.19% | 18.13% | 1468813.8 | 1462201 | 4067 | 1458134 | 335.0909 | 5.4484 | 1587419.3548 | 86.95% | 19.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-07-11 | 2024 | 2023 | 2023-07-01 | 31 | 13.3833 | 6.875 | 1.1954 | 6.6701 | 1.2872 | 34.1252 | 46.5493 | 4.5372 | 7.1207 | 99.98% |  |  | 100% |  |  | 84.44% | 85.41% | 23.47% | 1905484.8 | 1891266 | 4000 | 1887266 | 335.0909 | 5.4484 | 1587419.3548 | 86.95% | 19.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-07-12 | 2024 | 2023 | 2023-07-01 | 31 | 13.2667 | 7.4367 | 1.2893 | 7.2377 | 1.3891 | 32.8221 | 46.1141 | 4.9985 | 7.8033 | 99.98% |  |  | 100% |  |  | 83.28% | 83.71% | 25.12% | 2038549.1 | 2023267 | 3466 | 2019801 | 335.0909 | 5.4484 | 1587419.3548 | 86.95% | 19.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-07-13 | 2024 | 2023 | 2023-07-01 | 31 | 13.5 | 7.4712 | 1.3518 | 7.2828 | 1.457 | 33.2143 | 45.8 | 5.5611 | 8.6715 | 99.98% |  |  | 100% |  |  | 82.34% | 83.86% | 24.99% | 2028245.1 | 2013200 | 3734 | 2009466 | 335.0909 | 5.4484 | 1587419.3548 | 86.95% | 19.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-07-14 | 2024 | 2023 | 2023-07-01 | 31 | 13.5 | 7.2719 | 1.3188 | 7.0864 | 1.4239 | 32.8799 | 46.2 | 4.932 | 7.9858 | 99.98% |  |  | 100% |  |  | 83.44% | 83.79% | 24.64% | 2000593 | 1985201 | 3866 | 1981335 | 335.0909 | 5.4484 | 1587419.3548 | 86.95% | 19.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-07-15 | 2024 | 2023 | 2023-07-01 | 31 | 13.3167 | 7.3465 | 1.3909 | 7.1646 | 1.4818 | 32.682 | 44.6306 | 7.0798 | 11.2265 | 99.98% |  |  | 100% |  |  | 73.36% | 84.74% | 21.9% | 1774928.2 | 1765000 | 3800 | 1761200 | 335.0909 | 5.4484 | 1587419.3548 | 86.95% | 19.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-07-16 | 2024 | 2023 | 2023-07-01 | 31 | 13.2 | 6.8213 | 1.3133 | 6.7403 | 1.4004 | 31.6487 | 44.4608 | 5.6484 | 9.4363 | 99.98% |  |  | 100% |  |  | 83.83% | 83.3% | 23.54% | 1910216.6 | 1897400 | 3934 | 1893466 | 335.0909 | 5.4484 | 1587419.3548 | 86.95% | 19.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-07-17 | 2024 | 2023 | 2023-07-01 | 31 | 13.6667 | 6.7835 | 1.2992 | 6.6879 | 1.3856 | 33.2654 | 46.2 | 4.5368 | 7.4507 | 99.35% |  |  | 100% |  |  | 84.41% | 84.72% | 23.52% | 1909019.3 | 1895733 | 4000 | 1891733 | 335.0909 | 5.4484 | 1587419.3548 | 86.95% | 19.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-07-18 | 2024 | 2023 | 2023-07-01 | 31 | 13.5 | 6.7095 | 1.2749 | 6.6044 | 1.3624 | 34.0014 | 46.6 | 4.7808 | 8.0917 | 99.98% |  |  | 100% |  |  | 84.71% | 84.99% | 23.31% | 1891475.3 | 1878734 | 3933 | 1874801 | 335.0909 | 5.4484 | 1587419.3548 | 86.95% | 19.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-07-19 | 2024 | 2023 | 2023-07-01 | 31 | 13 | 5.5371 | 1.0349 | 5.5463 | 1.1006 | 32.4326 | 46.5 | 3.6756 | 11.1217 | 99.98% |  |  | 100% |  |  | 84.09% | 84.91% | 19.43% | 1578120.6 | 1566467 | 3733 | 1562734 | 335.0909 | 5.4484 | 1587419.3548 | 86.95% | 19.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-07-20 | 2024 | 2023 | 2023-07-01 | 31 | 13.5 | 5.0684 | 0.92053 | 4.9393 | 0.98658 | 31.6862 | 42.4 | 2.9208 | 6.3147 | 99.98% |  |  | 100% |  |  | 86.09% | 85.18% | 17.72% | 1435258.1 | 1427466 | 2534 | 1424932 | 335.0909 | 5.4484 | 1587419.3548 | 86.95% | 19.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-07-21 | 2024 | 2023 | 2023-07-01 | 31 | 13.4667 | 6.2893 | 1.1475 | 6.2189 | 1.2138 | 33.6975 | 48.3 | 2.5983 | 6.0707 | 99.98% |  |  | 100% |  |  | 83.35% | 84.55% | 21.6% | 1753861.1 | 1740520 | 3600 | 1736920 | 335.0909 | 5.4484 | 1587419.3548 | 86.95% | 19.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-07-22 | 2024 | 2023 | 2023-07-01 | 31 | 13.3833 | 5.1802 | 0.77973 | 5.0941 | 0.83093 | 29.51 | 43.15 | 2.6666 | 8.752 | 99.98% |  |  | 100% |  |  | 84.97% | 84.22% | 18.04% | 1463854.3 | 1454500 | 4066 | 1450434 | 335.0909 | 5.4484 | 1587419.3548 | 86.95% | 19.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-07-23 | 2024 | 2023 | 2023-07-01 | 31 | 13.3833 | 5.6336 | 0.83808 | 5.3985 | 0.86801 | 31.3269 | 40.85 | 4.6036 | 9.981 | 99.98% |  |  | 100% |  |  | 86.68% | 85.57% | 19.5% | 1582130.5 | 1572047 | 3934 | 1568113 | 335.0909 | 5.4484 | 1587419.3548 | 86.95% | 19.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-07-24 | 2024 | 2023 | 2023-07-01 | 31 | 13.5167 | 5.4524 | 0.86171 | 5.3168 | 0.89327 | 30.5789 | 44.3 | 3.3341 | 6.8982 | 99.98% |  |  | 100% |  |  | 87.17% | 85.63% | 19.31% | 1565579.2 | 1556953 | 3933 | 1553020 | 335.0909 | 5.4484 | 1587419.3548 | 86.95% | 19.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-07-25 | 2024 | 2023 | 2023-07-01 | 31 | 13.1833 | 5.3802 | 0.86738 | 5.3215 | 0.89579 | 30.5086 | 44.8 | 3.3651 | 8.5238 | 99.98% |  |  | 100% |  |  | 84.84% | 83.32% | 18.81% | 1525844.1 | 1516981 | 4067 | 1512914 | 335.0909 | 5.4484 | 1587419.3548 | 86.95% | 19.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-07-26 | 2024 | 2023 | 2023-07-01 | 31 | 13.25 | 4.7159 | 0.65704 | 4.5786 | 0.68301 | 29.5989 | 41.25 | 3.2387 | 6.8142 | 99.98% |  |  | 100% |  |  | 86.78% | 84.76% | 16.56% | 1342848 | 1335400 | 4000 | 1331400 | 335.0909 | 5.4484 | 1587419.3548 | 86.95% | 19.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-07-27 | 2024 | 2023 | 2023-07-01 | 31 | 13.2167 | 3.4265 | 0.47197 | 3.3438 | 0.49062 | 27.3223 | 37.7 | 3.3887 | 6.9525 | 99.91% |  |  | 100% |  |  | 91.44% | 88.37% | 12.74% | 1034442.3 | 1028600 | 4000 | 1024600 | 335.0909 | 5.4484 | 1587419.3548 | 86.95% | 19.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-07-28 | 2024 | 2023 | 2023-07-01 | 31 | 13.25 | 3.7284 | 0.56008 | 3.6462 | 0.58608 | 28.8363 | 36.95 | 5.2974 | 7.7072 | 99.99% |  |  | 100% |  |  | 91.6% | 87.78% | 13.92% | 1127516.8 | 1123334 | 4133 | 1119201 | 335.0909 | 5.4484 | 1587419.3548 | 86.95% | 19.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-07-29 | 2024 | 2023 | 2023-07-01 | 31 | 13.5333 | 4.7453 | 0.78132 | 4.6245 | 0.81287 | 28.493 | 38.9 | 6.188 | 9.4458 | 99.96% |  |  | 100% |  |  | 88.05% | 84.9% | 16.97% | 1374604.7 | 1367685 | 3200 | 1364485 | 335.0909 | 5.4484 | 1587419.3548 | 86.95% | 19.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-07-30 | 2024 | 2023 | 2023-07-01 | 31 | 13.4 | 5.779 | 0.98233 | 5.6806 | 1.0195 | 29.7241 | 41.95 | 4.831 | 7.7402 | 99.98% |  |  | 100% |  |  | 85.49% | 83.38% | 20.24% | 1639188.7 | 1629800 | 2400 | 1627400 | 335.0909 | 5.4484 | 1587419.3548 | 86.95% | 19.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-07-31 | 2024 | 2023 | 2023-07-01 | 31 | 13.4 | 6.7433 | 1.155 | 6.634 | 1.19 | 30.745 | 44.175 | 5.0617 | 7.775 | 99.98% |  |  | 100% |  |  | 82.19% | 81.33% | 22.72% | 1843251.7 | 1829900 | 2800 | 1827100 | 335.0909 | 5.4484 | 1587419.3548 | 86.95% | 19.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-08-01 | 2024 | 2023 | 2023-08-01 | 31 | 13.4 | 6.2865 | 1.1042 | 6.2259 | 1.1403 | 30.445 | 43.3 | 5.596 | 8.2622 | 99.99% |  |  | 100% |  |  | 82.09% | 82.03% | 21.3% | 1728566.8 | 1716682 | 4000 | 1712682 | 335.0909 | 5.6194 | 1616129.0323 | 85.83% | 20.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-08-02 | 2024 | 2023 | 2023-08-01 | 31 | 13.4 | 5.9463 | 1.0816 | 5.8041 | 1.1175 | 29.295 | 40.0871 | 7.0341 | 10.4683 | 99.99% |  |  | 100% |  |  | 84.78% | 83.43% | 20.5% | 1662907.1 | 1653018 | 4133 | 1648885 | 335.0909 | 5.6194 | 1616129.0323 | 85.83% | 20.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-08-03 | 2024 | 2023 | 2023-08-01 | 31 | 13.4 | 4.9883 | 0.905 | 4.934 | 0.93833 | 29.0317 | 39.75 | 5.3717 | 8.4767 | 99.94% |  |  | 100% |  |  | 85.92% | 83.86% | 17.66% | 1432094.9 | 1424649 | 4134 | 1420515 | 335.0909 | 5.6194 | 1616129.0323 | 85.83% | 20.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-08-04 | 2024 | 2023 | 2023-08-01 | 31 | 13.2333 | 5.4691 | 0.9984 | 5.4146 | 1.0367 | 29.4364 | 40.6 | 4.6741 | 8.1568 | 99.99% |  |  | 100% |  |  | 85.68% | 84.5% | 19.33% | 1566751.8 | 1558666 | 4133 | 1554533 | 335.0909 | 5.6194 | 1616129.0323 | 85.83% | 20.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-08-05 | 2024 | 2023 | 2023-08-01 | 31 | 13.25 | 6.2054 | 1.132 | 6.1676 | 1.1737 | 29.661 | 42.5857 | 5.3845 | 9.207 | 99.94% |  |  | 100% |  |  | 83.33% | 82.83% | 21.41% | 1737074.7 | 1726285 | 4133 | 1722152 | 335.0909 | 5.6194 | 1616129.0323 | 85.83% | 20.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-08-06 | 2024 | 2023 | 2023-08-01 | 31 | 13.2 | 6.4354 | 1.1957 | 6.4216 | 1.2342 | 29.0847 | 40.2434 | 7.9202 | 11.7558 | 99.99% |  |  | 100% |  |  | 82.64% | 81.14% | 22.11% | 1795559 | 1782249 | 3934 | 1778315 | 335.0909 | 5.6194 | 1616129.0323 | 85.83% | 20.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-08-07 | 2024 | 2023 | 2023-08-01 | 31 | 13.2167 | 5.899 | 1.0965 | 5.9216 | 1.1368 | 27.9839 | 39.0534 | 8.7907 | 12.7665 | 99.99% |  |  | 100% |  |  | 83.9% | 82.4% | 20.7% | 1681882.7 | 1668734 | 4000 | 1664734 | 335.0909 | 5.6194 | 1616129.0323 | 85.83% | 20.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-08-08 | 2024 | 2023 | 2023-08-01 | 31 | 13.35 | 6.1059 | 1.1548 | 6.1218 | 1.1933 | 28.9907 | 40.1889 | 7.4493 | 10.8038 | 99.99% |  |  | 100% |  |  | 85.09% | 83.96% | 21.7% | 1762301.6 | 1749466 | 4000 | 1745466 | 335.0909 | 5.6194 | 1616129.0323 | 85.83% | 20.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-08-09 | 2024 | 2023 | 2023-08-01 | 31 | 13.3333 | 5.5633 | 1.0417 | 5.586 | 1.0783 | 28.595 | 40.155 | 6.7783 | 10.065 | 99.99% |  |  | 100% |  |  | 85.76% | 84.91% | 19.96% | 1621202.3 | 1609467 | 4133 | 1605334 | 335.0909 | 5.6194 | 1616129.0323 | 85.83% | 20.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-08-10 | 2024 | 2023 | 2023-08-01 | 31 | 13.25 | 5.8639 | 1.1454 | 5.8878 | 1.1859 | 28.4844 | 40.9076 | 6.3447 | 10.1578 | 99.92% |  |  | 100% |  |  | 87.02% | 85.62% | 21.35% | 1732491.9 | 1721000 | 4067 | 1716933 | 335.0909 | 5.6194 | 1616129.0323 | 85.83% | 20.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-08-11 | 2024 | 2023 | 2023-08-01 | 31 | 13.1833 | 5.4992 | 1.0561 | 5.5167 | 1.0976 | 29.0804 | 40.0582 | 5.701 | 9.2367 | 99.99% |  |  | 100% |  |  | 85.44% | 83.7% | 19.64% | 1592970.4 | 1583467 | 4066 | 1579401 | 335.0909 | 5.6194 | 1616129.0323 | 85.83% | 20.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-08-12 | 2024 | 2023 | 2023-08-01 | 31 | 13.2 | 5.7406 | 1.0989 | 5.8033 | 1.1383 | 28.1779 | 40.7585 | 6.6076 | 9.874 | 99.99% |  |  | 100% |  |  | 84.73% | 83.57% | 20.49% | 1662071 | 1651800 | 4067 | 1647733 | 335.0909 | 5.6194 | 1616129.0323 | 85.83% | 20.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-08-13 | 2024 | 2023 | 2023-08-01 | 31 | 13.1667 | 5.0435 | 0.98882 | 5.1218 | 1.0263 | 27.6276 | 38.7343 | 7.2452 | 10.8607 | 99.99% |  |  | 100% |  |  | 87.76% | 85.73% | 18.73% | 1519989.6 | 1510267 | 4133 | 1506134 | 335.0909 | 5.6194 | 1616129.0323 | 85.83% | 20.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-08-14 | 2024 | 2023 | 2023-08-01 | 31 | 13.0333 | 5.4633 | 1.085 | 5.55 | 1.1183 | 28.7017 | 40.7 | 6.1867 | 9.7633 | 99.99% |  |  | 100% |  |  | 86.76% | 85.61% | 20.06% | 1627725 | 1617933 | 4334 | 1613599 | 335.0909 | 5.6194 | 1616129.0323 | 85.83% | 20.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-08-15 | 2024 | 2023 | 2023-08-01 | 31 | 12.9833 | 4.1542 | 0.81111 | 4.1255 | 0.84428 | 28.2666 | 39 | 3.8772 | 6.6877 | 99.99% |  |  | 100% |  |  | 89.89% | 87.76% | 15.45% | 1252558.6 | 1246934 | 4266 | 1242668 | 335.0909 | 5.6194 | 1616129.0323 | 85.83% | 20.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-08-16 | 2024 | 2023 | 2023-08-01 | 31 | 13.1 | 5.583 | 1.0858 | 5.6444 | 1.1283 | 29.5553 | 41.6789 | 4.8475 | 8.2032 | 99.99% |  |  | 100% |  |  | 85.71% | 84.84% | 20.16% | 1635167.8 | 1625467 | 4267 | 1621200 | 335.0909 | 5.6194 | 1616129.0323 | 85.83% | 20.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-08-17 | 2024 | 2023 | 2023-08-01 | 31 | 12.9167 | 5.207 | 1.0264 | 5.3236 | 1.0656 | 28.1266 | 40.7431 | 6.1139 | 9.3673 | 99.51% |  |  | 100% |  |  | 86.07% | 85.02% | 19.09% | 1548122.3 | 1538200 | 2800 | 1535400 | 335.0909 | 5.6194 | 1616129.0323 | 85.83% | 20.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-08-18 | 2024 | 2023 | 2023-08-01 | 31 | 13.2 | 6.5356 | 1.2736 | 6.595 | 1.3208 | 28.7156 | 45 | 3.9566 | 6.9837 | 99.85% |  |  | 100% |  |  | 83.85% | 84% | 23.04% | 1870158.5 | 1857133 | 4000 | 1853133 | 335.0909 | 5.6194 | 1616129.0323 | 85.83% | 20.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-08-19 | 2024 | 2023 | 2023-08-01 | 31 | 13.05 | 6.7075 | 1.2741 | 6.7741 | 1.3148 | 30.33 | 47.95 | 3.001 | 6.0822 | 99.99% |  |  | 100% |  |  | 81.93% | 82.88% | 23.12% | 1876936.7 | 1863867 | 4200 | 1859667 | 335.0909 | 5.6194 | 1616129.0323 | 85.83% | 20.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-08-20 | 2024 | 2023 | 2023-08-01 | 31 | 12.9167 | 4.2612 | 0.80003 | 4.2169 | 0.83278 | 30.4042 | 43 | 2.4404 | 6.608 | 99.99% |  |  | 100% |  |  | 87.26% | 86.64% | 15.33% | 1242341.1 | 1237216 | 4267 | 1232949 | 335.0909 | 5.6194 | 1616129.0323 | 85.83% | 20.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-08-21 | 2024 | 2023 | 2023-08-01 | 31 | 13.1 | 6.3627 | 1.1333 | 6.4104 | 1.1695 | 32.4063 | 48.65 | 2.6688 | 5.1925 | 99.65% |  |  | 100% |  |  | 80.2% | 80.35% | 21.42% | 1737975.1 | 1727118 | 4266 | 1722852 | 335.0909 | 5.6194 | 1616129.0323 | 85.83% | 20.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-08-22 | 2024 | 2023 | 2023-08-01 | 31 | 13.15 | 7.1036 | 1.2985 | 7.2214 | 1.3403 | 33.149 | 47.3159 | 5.6804 | 9.2778 | 99.85% |  |  | 100% |  |  | 80.88% | 81.56% | 24.34% | 1975109.1 | 1961282 | 4134 | 1957148 | 335.0909 | 5.6194 | 1616129.0323 | 85.83% | 20.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-08-23 | 2024 | 2023 | 2023-08-01 | 31 | 12.9333 | 5.2981 | 1.0116 | 5.3009 | 1.0538 | 29.3921 | 38.7289 | 8.9335 | 12.9375 | 99.86% |  |  | 100% |  |  | 87.15% | 84.2% | 19.25% | 1561380.8 | 1552300 | 4266 | 1548034 | 335.0909 | 5.6194 | 1616129.0323 | 85.83% | 20.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-08-24 | 2024 | 2023 | 2023-08-01 | 31 | 12.8333 | 5.6939 | 1.096 | 5.7869 | 1.1379 | 30.5033 | 40.8 | 7.4632 | 11.1695 | 99.92% |  |  | 100% |  |  | 82.87% | 81.55% | 19.98% | 1621765.2 | 1611285 | 4334 | 1606951 | 335.0909 | 5.6194 | 1616129.0323 | 85.83% | 20.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-08-25 | 2024 | 2023 | 2023-08-01 | 31 | 12.85 | 5.5828 | 1.0809 | 5.6976 | 1.1214 | 30.4222 | 40.8 | 7.1405 | 11.0318 | 99.99% |  |  | 100% |  |  | 84.03% | 81.75% | 19.95% | 1619359.4 | 1608666 | 4266 | 1604400 | 335.0909 | 5.6194 | 1616129.0323 | 85.83% | 20.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-08-26 | 2024 | 2023 | 2023-08-01 | 31 | 12.85 | 4.5521 | 1.0102 | 4.6972 | 1.0509 | 30.3879 | 40.4273 | 6.0537 | 9.6815 | 99.99% |  |  | 100% |  |  | 93.06% | 91.11% | 18.21% | 1476714.2 | 1469001 | 4267 | 1464734 | 335.0909 | 5.6194 | 1616129.0323 | 85.83% | 20.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-08-27 | 2024 | 2023 | 2023-08-01 | 31 | 12.8167 | 5.0417 | 1.0517 | 5.0483 | 1.0967 | 30.91 | 41.5333 | 6.1683 | 9.5617 | 99.99% |  |  | 100% |  |  | 89.91% | 88.54% | 18.91% | 1534142.5 | 1525248 | 4267 | 1520981 | 335.0909 | 5.6194 | 1616129.0323 | 85.83% | 20.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-08-28 | 2024 | 2023 | 2023-08-01 | 31 | 12.7833 | 5.6925 | 1.1498 | 5.7621 | 1.1961 | 30.7967 | 41.8 | 7.3745 | 11.5868 | 99.99% |  |  | 100% |  |  | 87.54% | 86.24% | 21.02% | 1708260.2 | 1694485 | 4200 | 1690285 | 335.0909 | 5.6194 | 1616129.0323 | 85.83% | 20.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-08-29 | 2024 | 2023 | 2023-08-01 | 31 | 12.7833 | 5.3323 | 1.0113 | 5.4735 | 1.0542 | 30.2203 | 42.5902 | 4.3632 | 8.2968 | 99.89% |  |  | 100% |  |  | 84.08% | 84.08% | 19.17% | 1558095.1 | 1546467 | 4400 | 1542067 | 335.0909 | 5.6194 | 1616129.0323 | 85.83% | 20.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-08-30 | 2024 | 2023 | 2023-08-01 | 31 | 12.7833 | 6.7474 | 1.3075 | 6.9635 | 1.3555 | 31.1564 | 46.5333 | 4.206 | 7.5843 | 99.99% |  |  | 100% |  |  | 82.29% | 82.97% | 23.88% | 1938926.9 | 1924648 | 4466 | 1920182 | 335.0909 | 5.6194 | 1616129.0323 | 85.83% | 20.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-08-31 | 2024 | 2023 | 2023-08-01 | 31 | 12.7833 | 6.8073 | 1.3324 | 7.0503 | 1.3784 | 31.8355 | 47.1667 | 4.214 | 7.9748 | 99.99% |  |  | 100% |  |  | 82.36% | 83.02% | 24.19% | 1965306.3 | 1950086 | 4467 | 1945619 | 335.0909 | 5.6194 | 1616129.0323 | 85.83% | 20.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-09-01 | 2024 | 2023 | 2023-09-01 | 30 | 12.7667 | 6.8641 | 1.3384 | 7.1172 | 1.3854 | 32.2224 | 46.6667 | 4.7059 | 8.9617 | 99.91% |  |  | 100% |  |  | 82.42% | 82.78% | 24.44% | 1985752.3 | 1970000 | 4400 | 1965600 | 335.0909 | 6.4033 | 1758666.6667 | 81.96% | 21.87% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-09-02 | 2024 | 2023 | 2023-09-01 | 30 | 12.7333 | 7.122 | 1.4128 | 7.3885 | 1.4589 | 32.7452 | 45.9667 | 6.1485 | 10.101 | 100% |  |  | 100% |  |  | 80.98% | 81.11% | 24.93% | 2028549.4 | 2009067 | 4267 | 2004800 | 335.0909 | 6.4033 | 1758666.6667 | 81.96% | 21.87% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-09-03 | 2024 | 2023 | 2023-09-01 | 30 | 12.7333 | 7.3767 | 1.412 | 7.2436 | 1.4565 | 32.2359 | 45.6667 | 6.4529 | 10.5107 | 100% |  |  | 100% |  |  | 82.66% | 82.46% | 24.95% | 2030104.3 | 2010600 | 4266 | 2006334 | 335.0909 | 6.4033 | 1758666.6667 | 81.96% | 21.87% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-09-04 | 2024 | 2023 | 2023-09-01 | 30 | 12.3833 | 7.195 | 1.3783 | 7.18 | 1.425 | 31.49 | 46.6 | 4.6417 | 8.665 | 100% |  |  | 100% |  |  | 83.03% | 82.75% | 24.84% | 2018849.3 | 2002067 | 4400 | 1997667 | 335.0909 | 6.4033 | 1758666.6667 | 81.96% | 21.87% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-09-05 | 2024 | 2023 | 2023-09-01 | 30 | 12.3167 | 6.7028 | 1.3534 | 7.0507 | 1.3954 | 32.6532 | 49.1333 | 3.0333 | 6.4468 | 100% |  |  | 100% |  |  | 83.31% | 83.98% | 24.48% | 1988461.2 | 1972866 | 4467 | 1968399 | 335.0909 | 6.4033 | 1758666.6667 | 81.96% | 21.87% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-09-06 | 2024 | 2023 | 2023-09-01 | 30 | 12.6167 | 6.4624 | 1.3028 | 6.7917 | 1.3436 | 34.4297 | 47.3883 | 3.3282 | 5.993 | 99.56% |  |  | 100% |  |  | 83.73% | 85% | 23.69% | 1923742.8 | 1909867 | 4333 | 1905534 | 335.0909 | 6.4033 | 1758666.6667 | 81.96% | 21.87% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-09-07 | 2024 | 2023 | 2023-09-01 | 30 | 12.5667 | 6.2633 | 1.255 | 6.495 | 1.29 | 35.85 | 49.39 | 2.6717 | 6.325 | 100% |  |  | 100% |  |  | 82.96% | 84.51% | 22.45% | 1822638.5 | 1810047 | 4400 | 1805647 | 335.0909 | 6.4033 | 1758666.6667 | 81.96% | 21.87% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-09-08 | 2024 | 2023 | 2023-09-01 | 30 | 12.5167 | 6.2384 | 1.2635 | 6.5077 | 1.3003 | 37.6584 | 50.5667 | 2.718 | 6.7465 | 99.6% |  |  | 100% |  |  | 82.63% | 84.7% | 22.41% | 1818283.1 | 1806153 | 4267 | 1801886 | 335.0909 | 6.4033 | 1758666.6667 | 81.96% | 21.87% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-09-09 | 2024 | 2023 | 2023-09-01 | 30 | 12.5 | 6.5249 | 1.3245 | 6.8496 | 1.3651 | 36.2628 | 51.7554 | 2.2861 | 5.5772 | 99.85% |  |  | 100% |  |  | 82.43% | 84.3% | 23.53% | 1908805 | 1895667 | 3667 | 1892000 | 335.0909 | 6.4033 | 1758666.6667 | 81.96% | 21.87% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-09-10 | 2024 | 2023 | 2023-09-01 | 30 | 12.45 | 6.2712 | 1.2848 | 6.6025 | 1.3238 | 35.5937 | 50.9333 | 3.0954 | 5.853 | 100% |  |  | 100% |  |  | 83.07% | 84.64% | 22.85% | 1855828.3 | 1842334 | 4400 | 1837934 | 335.0909 | 6.4033 | 1758666.6667 | 81.96% | 21.87% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-09-11 | 2024 | 2023 | 2023-09-01 | 30 | 12.5167 | 6.3021 | 1.2959 | 6.6626 | 1.3352 | 33.2438 | 47.8892 | 4.672 | 7.6515 | 99.86% |  |  | 100% |  |  | 83.61% | 84.05% | 23.21% | 1883685 | 1870946 | 4266 | 1866680 | 335.0909 | 6.4033 | 1758666.6667 | 81.96% | 21.87% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-09-12 | 2024 | 2023 | 2023-09-01 | 30 | 12.3 | 6.4538 | 1.3302 | 6.8574 | 1.3679 | 32.4424 | 47.7187 | 4.7144 | 7.5317 | 99.85% |  |  | 100% |  |  | 82.76% | 83.23% | 23.65% | 1918070.4 | 1904854 | 3200 | 1901654 | 335.0909 | 6.4033 | 1758666.6667 | 81.96% | 21.87% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-09-13 | 2024 | 2023 | 2023-09-01 | 30 | 12.4167 | 6.0282 | 1.2592 | 6.4263 | 1.2968 | 31.8845 | 46.4961 | 4.7278 | 7.9482 | 100% |  |  | 100% |  |  | 83.47% | 83.62% | 22.35% | 1814357.6 | 1801667 | 4200 | 1797467 | 335.0909 | 6.4033 | 1758666.6667 | 81.96% | 21.87% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-09-14 | 2024 | 2023 | 2023-09-01 | 30 | 12.0667 | 4.0363 | 0.83219 | 4.2003 | 0.86538 | 30.0251 | 39.9909 | 4.09 | 7.8153 | 99.76% |  |  | 100% |  |  | 88.11% | 86.19% | 15.42% | 1251127.2 | 1244600 | 4467 | 1240133 | 335.0909 | 6.4033 | 1758666.6667 | 81.96% | 21.87% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-09-15 | 2024 | 2023 | 2023-09-01 | 30 | 12.1833 | 4.8732 | 0.96497 | 5.1144 | 0.9979 | 32.2395 | 43.3726 | 4.2771 | 7.8433 | 100% |  |  | 100% |  |  | 84.79% | 83.7% | 18.07% | 1464253.8 | 1457600 | 4467 | 1453133 | 335.0909 | 6.4033 | 1758666.6667 | 81.96% | 21.87% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-09-16 | 2024 | 2023 | 2023-09-01 | 30 | 12.2167 | 4.9534 | 0.97493 | 5.2067 | 1.0045 | 33.8383 | 44.3667 | 3.0389 | 6.4807 | 100% |  |  | 100% |  |  | 85.82% | 85.52% | 18.62% | 1509464.6 | 1501800 | 4533 | 1497267 | 335.0909 | 6.4033 | 1758666.6667 | 81.96% | 21.87% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-09-17 | 2024 | 2023 | 2023-09-01 | 30 | 12.3333 | 5.1538 | 1.0257 | 5.4595 | 1.0569 | 31.7687 | 40.4 | 5.0239 | 10.0683 | 99.97% |  |  | 100% |  |  | 82.63% | 82.01% | 18.8% | 1525051.4 | 1515934 | 4333 | 1511601 | 335.0909 | 6.4033 | 1758666.6667 | 81.96% | 21.87% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-09-18 | 2024 | 2023 | 2023-09-01 | 30 | 12.2167 | 2.6871 | 0.49116 | 2.7204 | 0.50743 | 29.175 | 33.6 | 4.038 | 8.6812 | 99.87% |  |  | 100% |  |  | 87.73% | 84.48% | 9.944% | 807821.4 | 804200 | 4467 | 799733 | 335.0909 | 6.4033 | 1758666.6667 | 81.96% | 21.87% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-09-19 | 2024 | 2023 | 2023-09-01 | 30 | 11.9333 | 3.0243 | 0.46302 | 3.1427 | 0.48101 | 28.8067 | 36.3667 | 3.0218 | 6.5367 | 99.98% |  |  | 100% |  |  | 87.64% | 85.37% | 11.48% | 932856.6 | 927645 | 4733 | 922912 | 335.0909 | 6.4033 | 1758666.6667 | 81.96% | 21.87% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-09-20 | 2024 | 2023 | 2023-09-01 | 30 | 11.9167 | 4.486 | 0.7271 | 4.7008 | 0.74926 | 30.815 | 42.2667 | 3.0542 | 6.2282 | 100% |  |  | 100% |  |  | 84.61% | 83.45% | 16.57% | 1344365.1 | 1337400 | 4600 | 1332800 | 335.0909 | 6.4033 | 1758666.6667 | 81.96% | 21.87% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-09-21 | 2024 | 2023 | 2023-09-01 | 30 | 12.2667 | 5.7684 | 0.99991 | 6.2034 | 1.0231 | 31.1269 | 45.9667 | 3.7572 | 7.4675 | 100% |  |  | 100% |  |  | 81.73% | 81.43% | 21.12% | 1714291.2 | 1703288 | 4467 | 1698821 | 335.0909 | 6.4033 | 1758666.6667 | 81.96% | 21.87% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-09-22 | 2024 | 2023 | 2023-09-01 | 30 | 12.1667 | 6.1595 | 1.0813 | 6.7348 | 1.1054 | 32.1466 | 47.7315 | 3.8507 | 7.1397 | 99.96% |  |  | 100% |  |  | 82.75% | 83.06% | 23.22% | 1884966 | 1872134 | 4600 | 1867534 | 335.0909 | 6.4033 | 1758666.6667 | 81.96% | 21.87% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-09-23 | 2024 | 2023 | 2023-09-01 | 30 | 12.2 | 6.1331 | 1.0845 | 6.734 | 1.1084 | 33.1398 | 48.6294 | 3.798 | 6.93 | 99.98% |  |  | 100% |  |  | 82.66% | 83.27% | 23.19% | 1882984.7 | 1869933 | 4667 | 1865266 | 335.0909 | 6.4033 | 1758666.6667 | 81.96% | 21.87% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-09-24 | 2024 | 2023 | 2023-09-01 | 30 | 12.1 | 5.2958 | 0.93991 | 5.7914 | 0.96543 | 33.2526 | 46.1836 | 4.1216 | 7.8088 | 100% |  |  | 100% |  |  | 81.18% | 81.14% | 19.59% | 1590662.9 | 1580045 | 4666 | 1575379 | 335.0909 | 6.4033 | 1758666.6667 | 81.96% | 21.87% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-09-25 | 2024 | 2023 | 2023-09-01 | 30 | 12.1333 | 6.1652 | 1.1297 | 6.7951 | 1.155 | 32.6209 | 48.1564 | 3.7563 | 7.4215 | 100% |  |  | 100% |  |  | 82.74% | 83.35% | 23.43% | 1902344.1 | 1888700 | 4734 | 1883966 | 335.0909 | 6.4033 | 1758666.6667 | 81.96% | 21.87% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-09-26 | 2024 | 2023 | 2023-09-01 | 30 | 12.05 | 5.1039 | 0.92561 | 5.651 | 0.95128 | 34.1682 | 47.4602 | 2.7191 | 6.4868 | 99.99% |  |  | 100% |  |  | 81.33% | 81.91% | 19.15% | 1553216.9 | 1544800 | 4733 | 1540067 | 335.0909 | 6.4033 | 1758666.6667 | 81.96% | 21.87% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-09-27 | 2024 | 2023 | 2023-09-01 | 30 | 11.9667 | 4.4524 | 0.77544 | 4.8494 | 0.79172 | 32.8323 | 43.2 | 2.8375 | 11.1607 | 100% |  |  | 100% |  |  | 83.11% | 83.6% | 16.79% | 1363683.6 | 1355389 | 4800 | 1350589 | 335.0909 | 6.4033 | 1758666.6667 | 81.96% | 21.87% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-09-28 | 2024 | 2023 | 2023-09-01 | 30 | 12.1 | 5.0882 | 0.92658 | 5.66 | 0.94538 | 34.5969 | 47.3494 | 2.0537 | 6.5463 | 99.41% |  |  | 100% |  |  | 82.63% | 83.37% | 19.49% | 1580537.1 | 1571711 | 4467 | 1567244 | 335.0909 | 6.4033 | 1758666.6667 | 81.96% | 21.87% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-09-29 | 2024 | 2023 | 2023-09-01 | 30 | 12.0333 | 5.9976 | 1.1259 | 6.7231 | 1.1461 | 35.4131 | 50.4842 | 2.3732 | 5.806 | 99.13% |  |  | 100% |  |  | 81.05% | 83.17% | 22.7% | 1843422.2 | 1830356 | 4466 | 1825890 | 335.0909 | 6.4033 | 1758666.6667 | 81.96% | 21.87% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-09-30 | 2024 | 2023 | 2023-09-01 | 30 | 11.95 | 5.2363 | 1.001 | 5.8335 | 1.0164 | 34.0421 | 45.9 | 2.819 | 5.4318 | 100% |  |  | 100% |  |  | 83.81% | 84.72% | 20.37% | 1653467.2 | 1642867 | 4600 | 1638267 | 335.0909 | 6.4033 | 1758666.6667 | 81.96% | 21.87% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-10-01 | 2024 | 2023 | 2023-10-01 | 31 | 11.9833 | 5.5325 | 1.0715 | 6.1995 | 1.0938 | 34.3484 | 47.4122 | 2.6301 | 6.4342 | 100% |  |  | 100% |  |  | 82.21% | 84.56% | 21.24% | 1724176.7 | 1712477 | 4600 | 1707877 | 335.0909 | 6.5258 | 1844838.7097 | 84.36% | 22.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-10-02 | 2024 | 2023 | 2023-10-01 | 31 | 11.9667 | 6.0958 | 1.1837 | 6.8711 | 1.2133 | 34.1968 | 48.4339 | 2.7154 | 6.0452 | 99.99% |  |  | 100% |  |  | 81.26% | 83.89% | 23.27% | 1889202.8 | 1875400 | 4334 | 1871066 | 335.0909 | 6.5258 | 1844838.7097 | 84.36% | 22.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-10-03 | 2024 | 2023 | 2023-10-01 | 31 | 11.9667 | 6.1692 | 1.2068 | 6.9864 | 1.237 | 34.6339 | 47.7892 | 3.4125 | 6.8427 | 99.99% |  |  | 100% |  |  | 80.98% | 83.57% | 23.57% | 1913676.4 | 1900300 | 4533 | 1895767 | 335.0909 | 6.5258 | 1844838.7097 | 84.36% | 22.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-10-04 | 2024 | 2023 | 2023-10-01 | 31 | 11.95 | 6.1377 | 1.2108 | 6.924 | 1.2431 | 34.7432 | 48.1 | 4.0277 | 6.902 | 99.98% |  |  | 100% |  |  | 82.62% | 84.91% | 23.84% | 1934817.4 | 1921290 | 4400 | 1916890 | 335.0909 | 6.5258 | 1844838.7097 | 84.36% | 22.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-10-05 | 2024 | 2023 | 2023-10-01 | 31 | 11.9333 | 6.085 | 1.21 | 6.865 | 1.2417 | 33.4883 | 46.42 | 5.1917 | 8.9833 | 99.96% |  |  | 100% |  |  | 83.34% | 84.66% | 23.84% | 1935378.1 | 1921734 | 4533 | 1917201 | 335.0909 | 6.5258 | 1844838.7097 | 84.36% | 22.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-10-06 | 2024 | 2023 | 2023-10-01 | 31 | 11.9 | 5.9646 | 1.1906 | 6.7443 | 1.2185 | 31.9536 | 45 | 6.0256 | 9.5132 | 99.94% |  |  | 100% |  |  | 84.11% | 84.67% | 23.64% | 1919031.1 | 1905476 | 4667 | 1900809 | 335.0909 | 6.5258 | 1844838.7097 | 84.36% | 22.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-10-07 | 2024 | 2023 | 2023-10-01 | 31 | 11.7833 | 5.8605 | 1.1576 | 6.7073 | 1.1776 | 32.3175 | 45.4176 | 6.3807 | 9.5637 | 100% |  |  | 100% |  |  | 82.4% | 83.16% | 23.03% | 1869900.3 | 1856657 | 4667 | 1851990 | 335.0909 | 6.5258 | 1844838.7097 | 84.36% | 22.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-10-08 | 2024 | 2023 | 2023-10-01 | 31 | 11.8167 | 5.8456 | 1.1694 | 6.7067 | 1.1865 | 32.7535 | 45.1707 | 6.2304 | 10.1455 | 99.99% |  |  | 100% |  |  | 82.89% | 83.73% | 23.16% | 1880439.9 | 1867334 | 4600 | 1862734 | 335.0909 | 6.5258 | 1844838.7097 | 84.36% | 22.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-10-09 | 2024 | 2023 | 2023-10-01 | 31 | 11.8 | 5.7949 | 1.1509 | 6.6177 | 1.1698 | 32.4294 | 44.8633 | 6.378 | 10.1172 | 99.99% |  |  | 100% |  |  | 82.72% | 83.33% | 22.81% | 1852353.2 | 1839067 | 4666 | 1834401 | 335.0909 | 6.5258 | 1844838.7097 | 84.36% | 22.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-10-10 | 2024 | 2023 | 2023-10-01 | 31 | 11.7667 | 5.7808 | 1.1464 | 6.6348 | 1.1675 | 31.3727 | 46.3 | 4.0267 | 8.2258 | 100% |  |  | 100% |  |  | 82.61% | 83.72% | 22.84% | 1854243 | 1841242 | 4600 | 1836642 | 335.0909 | 6.5258 | 1844838.7097 | 84.36% | 22.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-10-11 | 2024 | 2023 | 2023-10-01 | 31 | 11.7667 | 5.0079 | 0.98195 | 5.6837 | 1.0011 | 32.9944 | 47.3 | 2.8614 | 5.6998 | 100% |  |  | 100% |  |  | 83% | 83.97% | 19.66% | 1594959 | 1585491 | 4667 | 1580824 | 335.0909 | 6.5258 | 1844838.7097 | 84.36% | 22.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-10-12 | 2024 | 2023 | 2023-10-01 | 31 | 11.75 | 5.5231 | 1.0945 | 6.3278 | 1.1368 | 33.0848 | 47.6341 | 3.3549 | 6.589 | 100% |  |  | 100% |  |  | 82.18% | 83.66% | 21.67% | 1758873.3 | 1747267 | 4733 | 1742534 | 335.0909 | 6.5258 | 1844838.7097 | 84.36% | 22.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-10-13 | 2024 | 2023 | 2023-10-01 | 31 | 11.7167 | 5.7614 | 1.1533 | 6.6696 | 1.1951 | 32.9992 | 47.1 | 4.0817 | 7.7363 | 100% |  |  | 100% |  |  | 82.2% | 83.82% | 22.84% | 1855049.6 | 1841642 | 4600 | 1837042 | 335.0909 | 6.5258 | 1844838.7097 | 84.36% | 22.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-10-14 | 2024 | 2023 | 2023-10-01 | 31 | 11.6833 | 5.5028 | 1.1217 | 6.3587 | 1.1601 | 32.9145 | 44.5667 | 5.5722 | 10.5253 | 100% |  |  | 100% |  |  | 83.8% | 84.55% | 22.2% | 1802471.9 | 1790225 | 4667 | 1785558 | 335.0909 | 6.5258 | 1844838.7097 | 84.36% | 22.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-10-15 | 2024 | 2023 | 2023-10-01 | 31 | 11.6167 | 5.6071 | 1.146 | 6.4926 | 1.1844 | 30.7371 | 43.7 | 4.8048 | 8.4555 | 99.9% |  |  | 100% |  |  | 83.57% | 84.19% | 22.61% | 1836415.2 | 1822975 | 4733 | 1818242 | 335.0909 | 6.5258 | 1844838.7097 | 84.36% | 22.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-10-16 | 2024 | 2023 | 2023-10-01 | 31 | 11.0167 | 3.5388 | 0.70236 | 3.8403 | 0.73115 | 26.3928 | 36.1667 | 5.2855 | 11.5837 | 99.96% |  |  | 100% |  |  | 88.5% | 86.62% | 14.16% | 1151038 | 1143758 | 4867 | 1138891 | 335.0909 | 6.5258 | 1844838.7097 | 84.36% | 22.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-10-17 | 2024 | 2023 | 2023-10-01 | 31 | 11.6 | 4.6732 | 0.5982 | 4.6216 | 0.62624 | 25.2931 | 36.2667 | 3.4819 | 6.8323 | 100% |  |  | 100% |  |  | 86.61% | 85.44% | 16.68% | 1356294.5 | 1346042 | 4800 | 1341242 | 335.0909 | 6.5258 | 1844838.7097 | 84.36% | 22.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-10-18 | 2024 | 2023 | 2023-10-01 | 31 | 11.75 | 8.2901 | 0.86686 | 6.2711 | 0.89519 | 26.4546 | 38.1333 | 3.0972 | 5.5708 | 100% |  |  | 100% |  |  | 84.61% | 83.88% | 22.11% | 1795318.7 | 1782692 | 4733 | 1777959 | 335.0909 | 6.5258 | 1844838.7097 | 84.36% | 22.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-10-19 | 2024 | 2023 | 2023-10-01 | 31 | 11.7333 | 5.5512 | 0.81558 | 6.0719 | 0.83766 | 28.6418 | 42.2333 | 2.0025 | 4.0958 | 100% |  |  | 100% |  |  | 84.17% | 84.66% | 21.3% | 1729052.4 | 1717333 | 4734 | 1712599 | 335.0909 | 6.5258 | 1844838.7097 | 84.36% | 22.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-10-20 | 2024 | 2023 | 2023-10-01 | 31 | 11.15 | 5.39 | 0.82185 | 6.1382 | 0.84331 | 30.4986 | 44.6333 | 1.8978 | 4.4108 | 100% |  |  | 100% |  |  | 83.55% | 84.26% | 21.37% | 1734578.6 | 1723001 | 4600 | 1718401 | 335.0909 | 6.5258 | 1844838.7097 | 84.36% | 22.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-10-21 | 2024 | 2023 | 2023-10-01 | 31 | 10.9833 | 4.4 | 0.646 | 4.806 | 0.634 | 30.2 | 40.1667 | 2.48 | 11.86 | 100% |  |  | 100% |  |  | 85.29% | 86.03% | 17.08% | 1387360 | 1378174 | 4633 | 1373541 | 335.0909 | 6.5258 | 1844838.7097 | 84.36% | 22.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-10-22 | 2024 | 2023 | 2023-10-01 | 31 | 11.4 | 5.066 | 0.768 | 5.768 | 0.752 | 29.632 | 40.7467 | 2.814 | 5.246 | 99.35% |  |  | 100% |  |  | 84.21% | 84.48% | 20.24% | 1642139 | 1631693 | 4033 | 1627660 | 335.0909 | 6.5258 | 1844838.7097 | 84.36% | 22.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-10-23 | 2024 | 2023 | 2023-10-01 | 31 | 11.0333 | 4.905 | 0.84667 | 6.005 | 0.87667 | 30.7417 | 43.3333 | 2.61 | 4.9933 | 99.99% |  |  | 100% |  |  | 83.78% | 84.18% | 20.96% | 1702285.9 | 1690733 | 4800 | 1685933 | 335.0909 | 6.5258 | 1844838.7097 | 84.36% | 22.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-10-24 | 2024 | 2023 | 2023-10-01 | 31 | 11.3667 | 5.1694 | 1.1906 | 5.9794 | 0.93255 | 30.3996 | 42.5667 | 2.5258 | 5.9463 | 99.95% |  |  | 100% |  |  | 83.52% | 84.56% | 20.81% | 1689228 | 1678200 | 4800 | 1673400 | 335.0909 | 6.5258 | 1844838.7097 | 84.36% | 22.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-10-25 | 2024 | 2023 | 2023-10-01 | 31 | 11.2167 | 5.4883 | 0.895 | 6.196 | 0.95167 | 30.74 | 42.1667 | 2.2483 | 5.405 | 100% |  |  | 100% |  |  | 81.92% | 83.44% | 21.15% | 1717261.4 | 1705600 | 4734 | 1700866 | 335.0909 | 6.5258 | 1844838.7097 | 84.36% | 22.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-10-26 | 2024 | 2023 | 2023-10-01 | 31 | 11.2333 | 5.7107 | 0.94764 | 6.3358 | 0.98304 | 31.5743 | 44.7 | 2.393 | 5.3905 | 99.99% |  |  | 100% |  |  | 82.57% | 84.21% | 21.8% | 1770155.2 | 1757734 | 4666 | 1753068 | 335.0909 | 6.5258 | 1844838.7097 | 84.36% | 22.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-10-27 | 2024 | 2023 | 2023-10-01 | 31 | 11.3167 | 5.3083 | 0.89333 | 5.9067 | 0.97333 | 31.6283 | 44.7667 | 2.7983 | 6.365 | 99.99% |  |  | 100% |  |  | 83.03% | 84.29% | 20.43% | 1659990.1 | 1648200 | 4800 | 1643400 | 335.0909 | 6.5258 | 1844838.7097 | 84.36% | 22.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-10-28 | 2024 | 2023 | 2023-10-01 | 31 | 11.3333 | 3.8153 | 0.67164 | 4.3364 | 0.73316 | 31.6793 | 40.9 | 2.7633 | 6.8102 | 99.99% |  |  | 100% |  |  | 83.55% | 84.05% | 15.1% | 1226242.6 | 1218733 | 4667 | 1214066 | 335.0909 | 6.5258 | 1844838.7097 | 84.36% | 22.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-10-29 | 2024 | 2023 | 2023-10-01 | 31 | 11.2167 | 4.9516 | 0.88446 | 5.9452 | 0.96143 | 31.9061 | 44.2667 | 2.4215 | 5.1487 | 99.99% |  |  | 100% |  |  | 83.09% | 84.57% | 20.58% | 1670757.6 | 1659907 | 4700 | 1655207 | 335.0909 | 6.5258 | 1844838.7097 | 84.36% | 22.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-10-30 | 2024 | 2023 | 2023-10-01 | 31 | 11.2167 | 4.5017 | 0.79994 | 5.272 | 0.86714 | 31.9353 | 42.3333 | 2.4456 | 5.5253 | 99.99% |  |  | 100% |  |  | 82.34% | 83.27% | 18.09% | 1468172 | 1459494 | 4833 | 1454661 | 335.0909 | 6.5258 | 1844838.7097 | 84.36% | 22.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-10-31 | 2024 | 2023 | 2023-10-01 | 31 | 11.05 | 3.2517 | 0.58 | 3.73 | 0.63167 | 30.83 | 37.07 | 4.84 | 11.1317 | 99.96% |  |  | 100% |  |  | 87.1% | 86.54% | 13.54% | 1099506.7 | 1093400 | 4800 | 1088600 | 335.0909 | 6.5258 | 1844838.7097 | 84.36% | 22.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-11-01 | 2024 | 2023 | 2023-11-01 | 30 | 11.05 | 4.2122 | 0.94315 | 4.6188 | 0.7768 | 30.5561 | 40.1333 | 3.3738 | 10.4957 | 100% |  |  | 100% |  |  | 84.06% | 86.97% | 16.18% | 1313783.6 | 1305800 | 4800 | 1301000 | 335.0909 | 5.43 | 1563333.3333 | 85.92% | 19.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-11-02 | 2024 | 2023 | 2023-11-01 | 30 | 11.1 | 4.1115 | 0.63921 | 4.8644 | 0.81938 | 30.6347 | 40.1 | 2.2715 | 5.5265 | 100% |  |  | 100% |  |  | 83.62% | 86.28% | 16.95% | 1375369.3 | 1367600 | 4667 | 1362933 | 335.0909 | 5.43 | 1563333.3333 | 85.92% | 19.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-11-03 | 2024 | 2023 | 2023-11-01 | 30 | 11.1667 | 4.4268 | 0.70011 | 5.2719 | 0.88998 | 30.7021 | 42.8667 | 2.2626 | 5.384 | 100% |  |  | 100% |  |  | 83.26% | 86.1% | 18.29% | 1483970.6 | 1475606 | 4733 | 1470873 | 335.0909 | 5.43 | 1563333.3333 | 85.92% | 19.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-11-04 | 2024 | 2023 | 2023-11-01 | 30 | 11.2 | 4.3117 | 0.815 | 5.14 | 0.87167 | 30.3133 | 41.7333 | 2.7133 | 7.06 | 100% |  |  | 100% |  |  | 83.97% | 86.79% | 17.98% | 1459323.8 | 1451061 | 4734 | 1446327 | 335.0909 | 5.43 | 1563333.3333 | 85.92% | 19.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-11-05 | 2024 | 2023 | 2023-11-01 | 30 | 11.15 | 4.3947 | 0.84073 | 5.2996 | 0.90097 | 31.1995 | 41.7333 | 3.4616 | 7.5853 | 100% |  |  | 100% |  |  | 83.98% | 86.69% | 18.54% | 1504639.3 | 1496067 | 4733 | 1491334 | 335.0909 | 5.43 | 1563333.3333 | 85.92% | 19.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-11-06 | 2024 | 2023 | 2023-11-01 | 30 | 11.2 | 4.3152 | 0.83155 | 5.1989 | 0.891 | 30.6048 | 41.0824 | 2.8521 | 5.8827 | 100% |  |  | 100% |  |  | 83.95% | 86.75% | 18.19% | 1475652.6 | 1467333 | 4800 | 1462533 | 335.0909 | 5.43 | 1563333.3333 | 85.92% | 19.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-11-07 | 2024 | 2023 | 2023-11-01 | 30 | 11.0833 | 3.6018 | 0.69508 | 4.1823 | 0.75098 | 30.0862 | 39.1061 | 2.2466 | 4.1912 | 100% |  |  | 100% |  |  | 85.09% | 87.1% | 14.83% | 1202725.7 | 1197400 | 4867 | 1192533 | 335.0909 | 5.43 | 1563333.3333 | 85.92% | 19.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-11-08 | 2024 | 2023 | 2023-11-01 | 30 | 11.15 | 3.382 | 0.65759 | 3.9097 | 0.71083 | 28.8202 | 37.4003 | 1.746 | 3.7515 | 99.99% |  |  | 100% |  |  | 84.88% | 86.27% | 13.83% | 1121191.1 | 1116867 | 4866 | 1112001 | 335.0909 | 5.43 | 1563333.3333 | 85.92% | 19.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-11-09 | 2024 | 2023 | 2023-11-01 | 30 | 11.1833 | 3.6133 | 0.705 | 4.175 | 0.76333 | 28.8783 | 36.6083 | 2.77 | 5.65 | 99.96% |  |  | 100% |  |  | 85% | 86.23% | 14.79% | 1198733.4 | 1193972 | 4767 | 1189205 | 335.0909 | 5.43 | 1563333.3333 | 85.92% | 19.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-11-10 | 2024 | 2023 | 2023-11-01 | 30 | 11.0833 | 4.4743 | 0.7232 | 5.5081 | 0.78508 | 28.6383 | 35.2057 | 4.2069 | 8.1158 | 99.98% |  |  | 100% |  |  | 85.18% | 87.11% | 19.55% | 1586799.5 | 1576961 | 4767 | 1572194 | 335.0909 | 5.43 | 1563333.3333 | 85.92% | 19.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-11-11 | 2024 | 2023 | 2023-11-01 | 30 | 11.1833 | 4.8925 | 0.86692 | 6.1624 | 0.93521 | 25.0997 | 32.7814 | 3.18 | 5.8925 | 100% |  |  | 100% |  |  | 84.49% | 86.24% | 21.69% | 1762103 | 1749334 | 4666 | 1744668 | 335.0909 | 5.43 | 1563333.3333 | 85.92% | 19.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-11-12 | 2024 | 2023 | 2023-11-01 | 30 | 11.1833 | 4.8515 | 0.85708 | 6.1202 | 0.92541 | 24.8627 | 37.561 | 2.2636 | 4.7228 | 99.99% |  |  | 100% |  |  | 85% | 86.9% | 21.68% | 1760742.8 | 1748000 | 4800 | 1743200 | 335.0909 | 5.43 | 1563333.3333 | 85.92% | 19.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-11-13 | 2024 | 2023 | 2023-11-01 | 30 | 10.9833 | 3.9208 | 0.68751 | 4.6577 | 0.7455 | 24.8232 | 35.1984 | 2.1784 | 4.4707 | 99.98% |  |  | 100% |  |  | 87.95% | 88.77% | 17.07% | 1384783.5 | 1377400 | 4667 | 1372733 | 335.0909 | 5.43 | 1563333.3333 | 85.92% | 19.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-11-14 | 2024 | 2023 | 2023-11-01 | 30 | 10.7833 | 3.9418 | 0.67414 | 4.7967 | 0.69665 | 25.8732 | 35 | 3.2249 | 6.232 | 100% |  |  | 100% |  |  | 86.25% | 87.02% | 17.24% | 1399130.1 | 1391005 | 4733 | 1386272 | 335.0909 | 5.43 | 1563333.3333 | 85.92% | 19.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-11-15 | 2024 | 2023 | 2023-11-01 | 30 | 11 | 4.2496 | 0.79154 | 5.2257 | 0.81361 | 21.177 | 24.5052 | 2.7258 | 5.5227 | 99.3% |  |  | 100% |  |  | 84.76% | 86.46% | 18.46% | 1497876.1 | 1489000 | 4734 | 1484266 | 335.0909 | 5.43 | 1563333.3333 | 85.92% | 19.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-11-16 | 2024 | 2023 | 2023-11-01 | 30 | 10.9667 | 4.3105 | 0.81129 | 5.348 | 0.80347 | 19.8896 | 21.6531 | 2.8158 | 5.495 | 100% |  |  | 100% |  |  | 85.28% | 86.18% | 19% | 1543035 | 1533195 | 4933 | 1528262 | 335.0909 | 5.43 | 1563333.3333 | 85.92% | 19.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-11-17 | 2024 | 2023 | 2023-11-01 | 30 | 10.9333 | 3.7134 | 0.70254 | 4.449 | 0.72996 | 20.1966 | 22.3 | 2.7746 | 5.5818 | 100% |  |  | 100% |  |  | 86.26% | 86.64% | 15.99% | 1297829.5 | 1290905 | 4933 | 1285972 | 335.0909 | 5.43 | 1563333.3333 | 85.92% | 19.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-11-18 | 2024 | 2023 | 2023-11-01 | 30 | 10.9 | 3.6579 | 0.6932 | 4.4135 | 0.71575 | 20.3259 | 22.6333 | 2.282 | 4.4468 | 100% |  |  | 100% |  |  | 85.34% | 85.73% | 15.69% | 1272782.3 | 1267000 | 4867 | 1262133 | 335.0909 | 5.43 | 1563333.3333 | 85.92% | 19.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-11-19 | 2024 | 2023 | 2023-11-01 | 30 | 10.9 | 3.8167 | 0.7214 | 4.682 | 0.74078 | 21.0822 | 23.5 | 2.349 | 4.1707 | 99.49% |  |  | 100% |  |  | 85.1% | 86.5% | 16.6% | 1346594.9 | 1339962 | 4867 | 1335095 | 335.0909 | 5.43 | 1563333.3333 | 85.92% | 19.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-11-20 | 2024 | 2023 | 2023-11-01 | 30 | 10.9167 | 3.9529 | 0.74492 | 4.9166 | 0.76689 | 21.9301 | 24.1333 | 2.9711 | 6.2902 | 100% |  |  | 100% |  |  | 86% | 86.82% | 17.62% | 1429484.4 | 1421734 | 4800 | 1416934 | 335.0909 | 5.43 | 1563333.3333 | 85.92% | 19.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-11-21 | 2024 | 2023 | 2023-11-01 | 30 | 10.9333 | 3.9581 | 0.75251 | 4.931 | 0.7728 | 21.2803 | 23.9 | 2.8554 | 5.1773 | 99.99% |  |  | 100% |  |  | 85.37% | 86.26% | 17.54% | 1423559.6 | 1415404 | 4866 | 1410538 | 335.0909 | 5.43 | 1563333.3333 | 85.92% | 19.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-11-22 | 2024 | 2023 | 2023-11-01 | 30 | 10.9167 | 4.0906 | 0.79531 | 5.145 | 0.80743 | 19.5657 | 22.95 | 2.0367 | 5.2492 | 99.98% |  |  | 100% |  |  | 85.05% | 86.13% | 18.23% | 1479683.6 | 1471063 | 4800 | 1466263 | 335.0909 | 5.43 | 1563333.3333 | 85.92% | 19.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-11-23 | 2024 | 2023 | 2023-11-01 | 30 | 10.8833 | 4.0093 | 0.77604 | 5.0455 | 0.79357 | 19.9641 | 23.0875 | 1.7638 | 5.7072 | 100% |  |  | 100% |  |  | 85.47% | 86.54% | 17.97% | 1457911.7 | 1449837 | 4867 | 1444970 | 335.0909 | 5.43 | 1563333.3333 | 85.92% | 19.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-11-24 | 2024 | 2023 | 2023-11-01 | 30 | 10.8833 | 4.0066 | 0.77632 | 5.0399 | 0.79395 | 21.1776 | 23.0667 | 2.4596 | 6.2467 | 100% |  |  | 100% |  |  | 85.62% | 86.98% | 17.98% | 1459513.9 | 1450900 | 4933 | 1445967 | 335.0909 | 5.43 | 1563333.3333 | 85.92% | 19.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-11-25 | 2024 | 2023 | 2023-11-01 | 30 | 10.7667 | 3.1201 | 0.61604 | 3.6529 | 0.64046 | 21.1593 | 22.2667 | 2.5234 | 5.5218 | 100% |  |  | 100% |  |  | 89.29% | 89.41% | 13.59% | 1104209.3 | 1097996 | 5000 | 1092996 | 335.0909 | 5.43 | 1563333.3333 | 85.92% | 19.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-11-26 | 2024 | 2023 | 2023-11-01 | 30 | 10.0333 | 0.40928 | 0.06572 | 0.39675 | 0.069501 | 17.2987 | 15.9451 | 2.3782 | 9.2403 | 99.89% |  |  | 100% |  |  | 91.84% | 89.49% | 1.518% | 130525.2 | 127504 | 5400 | 122104 | 335.0909 | 5.43 | 1563333.3333 | 85.92% | 19.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-11-27 | 2024 | 2023 | 2023-11-01 | 30 | 10.6333 | 2.9728 | 0.44531 | 3.4204 | 0.46847 | 18.1297 | 20.7 | 2.6847 | 5.6578 | 100% |  |  | 100% |  |  | 88.58% | 86.64% | 12.62% | 1025538.9 | 1020400 | 5134 | 1015266 | 335.0909 | 5.43 | 1563333.3333 | 85.92% | 19.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-11-28 | 2024 | 2023 | 2023-11-01 | 30 | 10.7333 | 2.7933 | 0.47333 | 3.87 | 0.57333 | 17.1317 | 17.9333 | 2.7117 | 5.8717 | 97.07% |  |  | 100% |  |  | 84.66% | 85.51% | 13.65% | 1107452.6 | 1102800 | 4933 | 1097867 | 335.0909 | 5.43 | 1563333.3333 | 85.92% | 19.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-11-29 | 2024 | 2023 | 2023-11-01 | 30 | 10.7 | 3.2483 | 0.55012 | 3.9073 | 0.5708 | 17.4562 | 18.5 | 2.464 | 4.8113 | 100% |  |  | 100% |  |  | 86.65% | 85.48% | 14.11% | 1144891.1 | 1139630 | 5067 | 1134563 | 335.0909 | 5.43 | 1563333.3333 | 85.92% | 19.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-11-30 | 2024 | 2023 | 2023-11-01 | 30 | 10.7333 | 3.5833 | 0.62418 | 4.5851 | 0.64655 | 18.7677 | 20.4333 | 2.6455 | 5.9218 | 100% |  |  | 100% |  |  | 88.88% | 88.96% | 16.98% | 1378981.2 | 1370600 | 5066 | 1365534 | 335.0909 | 5.43 | 1563333.3333 | 85.92% | 19.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-12-01 | 2024 | 2023 | 2023-12-01 | 31 | 10.7333 | 3.6013 | 0.62753 | 4.5453 | 0.65171 | 19.7613 | 20.8667 | 3.6098 | 8.6618 | 100% |  |  | 100% |  |  | 88.09% | 89.21% | 16.68% | 1354130 | 1346670 | 5000 | 1341670 | 335.0909 | 5.1161 | 1557419.3548 | 90.85% | 19.37% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-12-02 | 2024 | 2023 | 2023-12-01 | 31 | 10.75 | 3.779 | 0.65695 | 4.8646 | 0.68264 | 20.996 | 23.9667 | 3.8101 | 7.2203 | 99.71% |  |  | 100% |  |  | 86.59% | 88.12% | 17.55% | 1424741.7 | 1416400 | 4934 | 1411466 | 335.0909 | 5.1161 | 1557419.3548 | 90.85% | 19.37% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-12-03 | 2024 | 2023 | 2023-12-01 | 31 | 10.8167 | 3.95 | 0.68333 | 5.1933 | 0.71333 | 19.69 | 21.6333 | 3.2 | 6.7667 | 99.49% |  |  | 100% |  |  | 85.49% | 87.6% | 18.5% | 1501786.5 | 1492664 | 4933 | 1487731 | 335.0909 | 5.1161 | 1557419.3548 | 90.85% | 19.37% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-12-04 | 2024 | 2023 | 2023-12-01 | 31 | 10.7667 | 4.07 | 0.71667 | 5.44 | 0.74333 | 18.54 | 20.3333 | 3.1383 | 6.7483 | 99.8% |  |  | 100% |  |  | 87.32% | 89.61% | 19.79% | 1607306.4 | 1596736 | 5067 | 1591669 | 335.0909 | 5.1161 | 1557419.3548 | 90.85% | 19.37% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-12-05 | 2024 | 2023 | 2023-12-01 | 31 | 10.7167 | 4.0607 | 0.72523 | 5.4391 | 0.75065 | 18.4227 | 20.7333 | 3.2211 | 7.2937 | 99.93% |  |  | 100% |  |  | 87.05% | 89.1% | 19.73% | 1601850.4 | 1591531 | 5000 | 1586531 | 335.0909 | 5.1161 | 1557419.3548 | 90.85% | 19.37% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-12-06 | 2024 | 2023 | 2023-12-01 | 31 | 10.7333 | 4.0082 | 0.72262 | 5.3421 | 0.74929 | 18.569 | 21.0333 | 3.2483 | 6.7622 | 98.47% |  |  | 100% |  |  | 85.4% | 87.41% | 19.01% | 1543428.9 | 1533600 | 4933 | 1528667 | 335.0909 | 5.1161 | 1557419.3548 | 90.85% | 19.37% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-12-07 | 2024 | 2023 | 2023-12-01 | 31 | 10.75 | 3.986 | 0.73162 | 5.3172 | 0.75073 | 18.6827 | 21.535 | 3.0535 | 6.0045 | 100% |  |  | 100% |  |  | 86.82% | 89.13% | 19.24% | 1561731 | 1551969 | 5000 | 1546969 | 335.0909 | 5.1161 | 1557419.3548 | 90.85% | 19.37% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-12-08 | 2024 | 2023 | 2023-12-01 | 31 | 10.7333 | 4.0244 | 0.72788 | 5.4012 | 0.81538 | 20.7058 | 29.5667 | 2.0103 | 5.213 | 100% |  |  | 100% |  |  | 86.33% | 89.12% | 19.43% | 1577076.7 | 1567498 | 5000 | 1562498 | 335.0909 | 5.1161 | 1557419.3548 | 90.85% | 19.37% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-12-09 | 2024 | 2023 | 2023-12-01 | 31 | 10.7667 | 4.1879 | 0.81331 | 5.394 | 0.82424 | 23.6884 | 36.8 | 1.9809 | 4.4723 | 100% |  |  | 100% |  |  | 86.5% | 89.54% | 19.44% | 1578184.8 | 1568466 | 5000 | 1563466 | 335.0909 | 5.1161 | 1557419.3548 | 90.85% | 19.37% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-12-10 | 2024 | 2023 | 2023-12-01 | 31 | 10.75 | 4.1991 | 0.82499 | 5.423 | 0.83638 | 22.7778 | 35.3333 | 2.1312 | 4.9242 | 100% |  |  | 100% |  |  | 86.68% | 89.49% | 19.59% | 1590227.4 | 1580267 | 5067 | 1575200 | 335.0909 | 5.1161 | 1557419.3548 | 90.85% | 19.37% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-12-11 | 2024 | 2023 | 2023-12-01 | 31 | 10.75 | 4.2158 | 0.84712 | 5.5192 | 0.85695 | 23.5974 | 36.4667 | 2.2433 | 5.3975 | 99.99% |  |  | 100% |  |  | 86.31% | 89.25% | 19.85% | 1611795.9 | 1601267 | 4933 | 1596334 | 335.0909 | 5.1161 | 1557419.3548 | 90.85% | 19.37% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-12-12 | 2024 | 2023 | 2023-12-01 | 31 | 10.95 | 3.6927 | 0.73566 | 4.6778 | 0.75075 | 22.9926 | 32.7433 | 2.7858 | 5.2275 | 100% |  |  | 100% |  |  | 87.71% | 89.66% | 17.09% | 1387087.4 | 1379600 | 4800 | 1374800 | 335.0909 | 5.1161 | 1557419.3548 | 90.85% | 19.37% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-12-13 | 2024 | 2023 | 2023-12-01 | 31 | 10.8333 | 4.0422 | 0.83467 | 5.2883 | 0.82461 | 22.8578 | 35.5667 | 1.8989 | 3.6317 | 100% |  |  | 100% |  |  | 86.44% | 89.18% | 19.05% | 1546345.4 | 1536702 | 4933 | 1531769 | 335.0909 | 5.1161 | 1557419.3548 | 90.85% | 19.37% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-12-14 | 2024 | 2023 | 2023-12-01 | 31 | 10.7333 | 4.1483 | 0.86 | 5.4817 | 0.88667 | 23.6183 | 37 | 1.9083 | 4.39 | 100% |  |  | 100% |  |  | 86.1% | 89.31% | 19.67% | 1596889.2 | 1586600 | 5067 | 1581533 | 335.0909 | 5.1161 | 1557419.3548 | 90.85% | 19.37% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-12-15 | 2024 | 2023 | 2023-12-01 | 31 | 10.8 | 4.141 | 0.9581 | 5.29 | 0.9953 | 22.8822 | 36.0333 | 1.9889 | 4.7627 | 100% |  |  | 100% |  |  | 87.58% | 90.35% | 19.3% | 1568021.2 | 1557400 | 5000 | 1552400 | 335.0909 | 5.1161 | 1557419.3548 | 90.85% | 19.37% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-12-16 | 2024 | 2023 | 2023-12-01 | 31 | 10.7 | 3.8455 | 0.89522 | 5.1925 | 0.92877 | 23.2688 | 34.8333 | 2.4453 | 5.725 | 99.99% |  |  | 100% |  |  | 87.61% | 90.3% | 18.96% | 1539293.4 | 1529365 | 4933 | 1524432 | 335.0909 | 5.1161 | 1557419.3548 | 90.85% | 19.37% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-12-17 | 2024 | 2023 | 2023-12-01 | 31 | 10.7 | 4.1694 | 0.97239 | 5.3372 | 0.96964 | 22.2037 | 34.3 | 2.3306 | 5.555 | 100% |  |  | 100% |  |  | 88.36% | 90.91% | 19.65% | 1595891.5 | 1585135 | 4934 | 1580201 | 335.0909 | 5.1161 | 1557419.3548 | 90.85% | 19.37% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-12-18 | 2024 | 2023 | 2023-12-01 | 31 | 10.6333 | 4.0902 | 0.9813 | 5.2077 | 1.0202 | 21.4436 | 31.0667 | 3.4714 | 6.4797 | 100% |  |  | 100% |  |  | 88.89% | 90.65% | 19.29% | 1566876.3 | 1556399 | 5200 | 1551199 | 335.0909 | 5.1161 | 1557419.3548 | 90.85% | 19.37% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-12-19 | 2024 | 2023 | 2023-12-01 | 31 | 10.65 | 3.9133 | 0.94002 | 4.8502 | 0.97752 | 20.2824 | 31.0667 | 2.8353 | 5.127 | 100% |  |  | 100% |  |  | 88.23% | 89.75% | 17.83% | 1448581.7 | 1439000 | 5000 | 1434000 | 335.0909 | 5.1161 | 1557419.3548 | 90.85% | 19.37% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-12-20 | 2024 | 2023 | 2023-12-01 | 31 | 10.5167 | 3.6069 | 0.85023 | 4.4502 | 0.89081 | 20.7831 | 28.6939 | 3.3366 | 6.4673 | 100% |  |  | 100% |  |  | 90.59% | 91.53% | 16.8% | 1364666.3 | 1356000 | 5066 | 1350934 | 335.0909 | 5.1161 | 1557419.3548 | 90.85% | 19.37% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-12-21 | 2024 | 2023 | 2023-12-01 | 31 | 10.65 | 4.121 | 0.97415 | 5.2744 | 1.0168 | 22.9554 | 32.8 | 3.3946 | 5.7367 | 99.95% |  |  | 100% |  |  | 88.49% | 90.76% | 19.45% | 1580113.2 | 1569000 | 4934 | 1564066 | 335.0909 | 5.1161 | 1557419.3548 | 90.85% | 19.37% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-12-22 | 2024 | 2023 | 2023-12-01 | 31 | 10.55 | 3.8281 | 0.90019 | 4.6838 | 0.94448 | 24.7079 | 34.8667 | 3.3219 | 6.2656 | 99.99% |  |  | 100% |  |  | 88.61% | 91.35% | 17.29% | 1405651.2 | 1395801 | 5133 | 1390668 | 335.0909 | 5.1161 | 1557419.3548 | 90.85% | 19.37% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-12-23 | 2024 | 2023 | 2023-12-01 | 31 | 10.6667 | 4.1132 | 0.97403 | 5.3044 | 1.0164 | 23.3905 | 35.2333 | 2.5315 | 5.5408 | 100% |  |  | 100% |  |  | 88.05% | 90.91% | 19.46% | 1580419.2 | 1570000 | 5000 | 1565000 | 335.0909 | 5.1161 | 1557419.3548 | 90.85% | 19.37% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-12-24 | 2024 | 2023 | 2023-12-01 | 31 | 10.7 | 3.8112 | 0.9173 | 4.799 | 0.95938 | 22.6895 | 32.4 | 2.6847 | 4.8097 | 99.95% |  |  | 100% |  |  | 89.06% | 91.09% | 17.81% | 1445783.3 | 1437200 | 5000 | 1432200 | 335.0909 | 5.1161 | 1557419.3548 | 90.85% | 19.37% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-12-25 | 2024 | 2023 | 2023-12-01 | 31 | 10.65 | 3.5893 | 0.89669 | 4.6298 | 0.93698 | 22.4037 | 32.2667 | 2.4981 | 4.8607 | 99.91% |  |  | 100% |  |  | 89.04% | 90.91% | 17.18% | 1394573.1 | 1386600 | 5200 | 1381400 | 335.0909 | 5.1161 | 1557419.3548 | 90.85% | 19.37% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-12-26 | 2024 | 2023 | 2023-12-01 | 31 | 10.6667 | 3.7432 | 0.93361 | 4.8654 | 0.97707 | 23.7737 | 35.8667 | 1.7362 | 4.1752 | 100% |  |  | 100% |  |  | 88.15% | 91.01% | 17.87% | 1450718 | 1442333 | 5200 | 1437133 | 335.0909 | 5.1161 | 1557419.3548 | 90.85% | 19.37% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-12-27 | 2024 | 2023 | 2023-12-01 | 31 | 10.6167 | 3.5652 | 0.89444 | 4.6259 | 0.93593 | 24.0605 | 33 | 3.0897 | 5.6375 | 100% |  |  | 100% |  |  | 89.62% | 91.78% | 17.27% | 1402193.8 | 1394267 | 5000 | 1389267 | 335.0909 | 5.1161 | 1557419.3548 | 90.85% | 19.37% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-12-28 | 2024 | 2023 | 2023-12-01 | 31 | 10.7333 | 4.117 | 1.0258 | 5.4751 | 1.072 | 23.1085 | 34.1667 | 3.2075 | 5.6803 | 100% |  |  | 100% |  |  | 88.85% | 91.34% | 20.27% | 1646956.1 | 1635300 | 5133 | 1630167 | 335.0909 | 5.1161 | 1557419.3548 | 90.85% | 19.37% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-12-29 | 2024 | 2023 | 2023-12-01 | 31 | 10.7167 | 3.8887 | 0.97144 | 5.0978 | 1.0179 | 22.9336 | 33.0333 | 3.1967 | 5.6975 | 100% |  |  | 100% |  |  | 88.66% | 90.84% | 18.83% | 1529402.6 | 1519600 | 5067 | 1514533 | 335.0909 | 5.1161 | 1557419.3548 | 90.85% | 19.37% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-12-30 | 2024 | 2023 | 2023-12-01 | 31 | 10.75 | 3.7719 | 0.96672 | 4.9087 | 1.0096 | 17.7171 | 26.9667 | 3.6439 | 5.6648 | 100% |  |  | 100% |  |  | 90.35% | 90.43% | 18.48% | 1500772.7 | 1491167 | 5067 | 1486100 | 335.0909 | 5.1161 | 1557419.3548 | 90.85% | 19.37% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2023-12-31 | 2024 | 2023 | 2023-12-01 | 31 | 10.7167 | 4.0056 | 1.0207 | 5.2372 | 1.0652 | 19.9123 | 29.0333 | 3.9152 | 7.1212 | 100% |  |  | 100% |  |  | 91.59% | 92.64% | 19.99% | 1623522 | 1612400 | 5133 | 1607267 | 335.0909 | 5.1161 | 1557419.3548 | 90.85% | 19.37% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-01-01 | 2024 | 2024 | 2024-01-01 | 31 | 10.7 | 4.0654 | 1.0317 | 5.389 | 1.0733 | 17.6622 | 27.7667 | 3.3654 | 5.6442 | 99.76% |  |  | 100% |  |  | 90.96% | 91.95% | 20.42% | 1659606 | 1647667 | 5133 | 1642534 | 335.0909 | 5.4525 | 1653548.3871 | 90.5% | 20.56% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-01-02 | 2024 | 2024 | 2024-01-01 | 31 | 10.7167 | 4.0834 | 1.0215 | 5.34 | 1.0649 | 18.6109 | 28.6667 | 3.5262 | 5.63 | 99.86% |  |  | 100% |  |  | 91.12% | 92.33% | 20.28% | 1648127.3 | 1635566 | 5000 | 1630566 | 335.0909 | 5.4525 | 1653548.3871 | 90.5% | 20.56% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-01-03 | 2024 | 2024 | 2024-01-01 | 31 | 10.7167 | 4.1125 | 1.032 | 5.3945 | 1.0773 | 18.3059 | 28.6667 | 3.4854 | 5.807 | 98.92% |  |  | 100% |  |  | 90.91% | 92.03% | 20.43% | 1660667.5 | 1648367 | 5067 | 1643300 | 335.0909 | 5.4525 | 1653548.3871 | 90.5% | 20.56% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-01-04 | 2024 | 2024 | 2024-01-01 | 31 | 10.65 | 4.1114 | 0.97392 | 5.2006 | 1.0207 | 15.5199 | 26.2333 | 3.377 | 5.477 | 99.36% |  |  | 100% |  |  | 88.7% | 89.37% | 19.22% | 1563002.5 | 1550833 | 5000 | 1545833 | 335.0909 | 5.4525 | 1653548.3871 | 90.5% | 20.56% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-01-05 | 2024 | 2024 | 2024-01-01 | 31 | 10.7167 | 4.1611 | 0.98535 | 5.314 | 1.0321 | 18.5289 | 29.6667 | 2.7668 | 5.2053 | 99.97% |  |  | 100% |  |  | 88.48% | 90.14% | 19.59% | 1592124.7 | 1580568 | 5000 | 1575568 | 335.0909 | 5.4525 | 1653548.3871 | 90.5% | 20.56% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-01-06 | 2024 | 2024 | 2024-01-01 | 31 | 10.75 | 4.1959 | 0.99991 | 5.3676 | 1.0437 | 18.264 | 28.8333 | 3.2887 | 5.692 | 100% |  |  | 100% |  |  | 89.26% | 90.48% | 19.96% | 1622228.9 | 1610466 | 4933 | 1605533 | 335.0909 | 5.4525 | 1653548.3871 | 90.5% | 20.56% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-01-07 | 2024 | 2024 | 2024-01-01 | 31 | 10.75 | 4.2968 | 1.028 | 5.495 | 1.0719 | 16.1758 | 27.1333 | 3.4036 | 6.2 | 100% |  |  | 100% |  |  | 89.66% | 90.27% | 20.53% | 1668649.8 | 1656001 | 5000 | 1651001 | 335.0909 | 5.4525 | 1653548.3871 | 90.5% | 20.56% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-01-08 | 2024 | 2024 | 2024-01-01 | 31 | 10.55 | 3.8515 | 0.88904 | 4.6902 | 0.92538 | 14.0314 | 24.4333 | 3.1988 | 5.062 | 100% |  |  | 100% |  |  | 89.55% | 89.85% | 17.5% | 1423994.2 | 1412665 | 5200 | 1407465 | 335.0909 | 5.4525 | 1653548.3871 | 90.5% | 20.56% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-01-09 | 2024 | 2024 | 2024-01-01 | 31 | 10.55 | 4.1614 | 0.97205 | 5.1357 | 1.0109 | 13.9723 | 23.7667 | 4.167 | 7.3481 | 100% |  |  | 100% |  |  | 90.36% | 90.27% | 19.34% | 1573410.2 | 1560135 | 5067 | 1555068 | 335.0909 | 5.4525 | 1653548.3871 | 90.5% | 20.56% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-01-10 | 2024 | 2024 | 2024-01-01 | 31 | 10.8 | 4.2902 | 1.028 | 5.3034 | 1.0644 | 17.2383 | 26.9 | 3.3849 | 6.0073 | 100% |  |  | 100% |  |  | 92.77% | 93.48% | 20.5% | 1666307.7 | 1653667 | 5000 | 1648667 | 335.0909 | 5.4525 | 1653548.3871 | 90.5% | 20.56% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-01-11 | 2024 | 2024 | 2024-01-01 | 31 | 10.8333 | 4.6618 | 1.109 | 5.7751 | 0.23613 | 19.42 | 31.7667 | 2.6321 | 5.3208 | 100% |  |  | 100% |  |  | 90.9% | 93.04% | 21.87% | 1777997.8 | 1764098 | 5000 | 1759098 | 335.0909 | 5.4525 | 1653548.3871 | 90.5% | 20.56% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-01-12 | 2024 | 2024 | 2024-01-01 | 31 | 10.9333 | 4.5179 | 1.1089 | 5.9154 | 0.2388 | 21.8123 | 34.8 | 2.2016 | 4.5108 | 100% |  |  | 100% |  |  | 86.88% | 90.05% | 21.41% | 1740475.3 | 1727200 | 5000 | 1722200 | 335.0909 | 5.4525 | 1653548.3871 | 90.5% | 20.56% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-01-13 | 2024 | 2024 | 2024-01-01 | 31 | 10.9333 | 4.1824 | 1.0408 | 5.2689 | 0.28942 | 16.2322 | 18.2733 | 2.5229 | 5.5781 | 99.93% |  |  | 100% |  |  | 87.82% | 90.15% | 19.28% | 1564807.3 | 1555435 | 4867 | 1550568 | 335.0909 | 5.4525 | 1653548.3871 | 90.5% | 20.56% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-01-14 | 2024 | 2024 | 2024-01-01 | 31 | 11.0167 | 4.2776 | 1.0557 | 5.4627 | 0.23887 | 20.1884 | 31.0667 | 2.6104 | 5.027 | 100% |  |  | 100% |  |  | 88.43% | 90.69% | 20.13% | 1635054.2 | 1623734 | 5000 | 1618734 | 335.0909 | 5.4525 | 1653548.3871 | 90.5% | 20.56% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-01-15 | 2024 | 2024 | 2024-01-01 | 31 | 10.8333 | 4.5581 | 1.1187 | 5.885 | 0.24335 | 20.2214 | 34.7667 | 1.9345 | 3.927 | 100% |  |  | 100% |  |  | 87.27% | 90% | 21.4% | 1739069.7 | 1726067 | 5066 | 1721001 | 335.0909 | 5.4525 | 1653548.3871 | 90.5% | 20.56% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-01-16 | 2024 | 2024 | 2024-01-01 | 31 | 11 | 4.4219 | 1.0905 | 5.6512 | 0.24592 | 21.822 | 36.0667 | 1.8372 | 4.7173 | 99.99% |  |  | 100% |  |  | 87.41% | 90.51% | 20.58% | 1672182.3 | 1660266 | 5000 | 1655266 | 335.0909 | 5.4525 | 1653548.3871 | 90.5% | 20.56% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-01-17 | 2024 | 2024 | 2024-01-01 | 31 | 10.6667 | 4.1623 | 1.0309 | 5.2836 | 0.23549 | 18.9094 | 30.6333 | 2.8108 | 5.1982 | 100% |  |  | 100% |  |  | 89.02% | 90.78% | 19.6% | 1592324.2 | 1581201 | 5134 | 1576067 | 335.0909 | 5.4525 | 1653548.3871 | 90.5% | 20.56% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-01-18 | 2024 | 2024 | 2024-01-01 | 31 | 10.8333 | 4.3146 | 1.0749 | 5.4723 | 0.24393 | 18.7336 | 29.3333 | 3.1529 | 5.4033 | 99.91% |  |  | 100% |  |  | 89.37% | 90.95% | 20.38% | 1656092.9 | 1643800 | 5066 | 1638734 | 335.0909 | 5.4525 | 1653548.3871 | 90.5% | 20.56% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-01-19 | 2024 | 2024 | 2024-01-01 | 31 | 10.6667 | 4.5606 | 1.1375 | 5.8368 | 0.25376 | 19.8873 | 32.1667 | 2.5382 | 4.8858 | 100% |  |  | 100% |  |  | 87.59% | 90.11% | 21.3% | 1731568.2 | 1718266 | 5134 | 1713132 | 335.0909 | 5.4525 | 1653548.3871 | 90.5% | 20.56% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-01-20 | 2024 | 2024 | 2024-01-01 | 31 | 10.6667 | 4.473 | 1.1172 | 5.7106 | 0.24788 | 21.2553 | 32.9 | 2.5229 | 4.8067 | 99.99% |  |  | 100% |  |  | 88.44% | 91.21% | 21.04% | 1709848.4 | 1697467 | 5066 | 1692401 | 335.0909 | 5.4525 | 1653548.3871 | 90.5% | 20.56% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-01-21 | 2024 | 2024 | 2024-01-01 | 31 | 10.8333 | 4.4721 | 1.1122 | 5.6575 | 0.25312 | 19.7542 | 32.1667 | 2.5349 | 4.9885 | 100% |  |  | 100% |  |  | 88.38% | 90.82% | 20.83% | 1693328.95 | 1680534 | 5067 | 1675467 | 335.0909 | 5.4525 | 1653548.3871 | 90.5% | 20.56% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-01-22 | 2024 | 2024 | 2024-01-01 | 31 | 10.6667 | 4.1123 | 1.0288 | 5.1039 | 0.22124 | 21.9054 | 33.9 | 2.9086 | 6.2795 | 99.96% |  |  | 100% |  |  | 88.35% | 90.89% | 18.79% | 1526897.4 | 1516200 | 5133 | 1511067 | 335.0909 | 5.4525 | 1653548.3871 | 90.5% | 20.56% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-01-23 | 2024 | 2024 | 2024-01-01 | 31 | 10.6667 | 4.3511 | 1.0838 | 5.3907 | 0.25422 | 14.7387 | 26.2667 | 3.0975 | 5.097 | 100% |  |  | 100% |  |  | 90.1% | 90.52% | 20.24% | 1645744.8 | 1632667 | 5134 | 1627533 | 335.0909 | 5.4525 | 1653548.3871 | 90.5% | 20.56% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-01-24 | 2024 | 2024 | 2024-01-01 | 31 | 10.6667 | 4.5144 | 1.1171 | 5.6866 | 0.25465 | 17.4556 | 30.7667 | 2.1038 | 4.0233 | 100% |  |  | 100% |  |  | 88.44% | 90.11% | 20.95% | 1703150.5 | 1690400 | 5200 | 1685200 | 335.0909 | 5.4525 | 1653548.3871 | 90.5% | 20.56% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-01-25 | 2024 | 2024 | 2024-01-01 | 31 | 10.6667 | 4.38 | 1.0833 | 5.3167 | 0.26667 | 21.2733 | 34.1 | 2.4833 | 5.9817 | 100% |  |  | 100% |  |  | 87.91% | 90.46% | 19.47% | 1581713.1 | 1571200 | 5000 | 1566200 | 335.0909 | 5.4525 | 1653548.3871 | 90.5% | 20.56% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-01-26 | 2024 | 2024 | 2024-01-01 | 31 | 10.6667 | 4.2564 | 1.0552 | 5.1842 | 0.26964 | 16.0859 | 27.4333 | 2.7612 | 4.737 | 100% |  |  | 100% |  |  | 90.26% | 90.91% | 19.5% | 1584714.1 | 1573000 | 5066 | 1567934 | 335.0909 | 5.4525 | 1653548.3871 | 90.5% | 20.56% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-01-27 | 2024 | 2024 | 2024-01-01 | 31 | 10.8333 | 3.2526 | 0.80387 | 3.6876 | 0.22674 | 18.4147 | 27.1667 | 2.244 | 4.0047 | 99.32% |  |  | 100% |  |  | 91.91% | 92.03% | 14.12% | 1145786.9 | 1140733 | 5000 | 1135733 | 335.0909 | 5.4525 | 1653548.3871 | 90.5% | 20.56% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-01-28 | 2024 | 2024 | 2024-01-01 | 31 | 10.8333 | 3.7757 | 0.93467 | 4.276 | 0.25535 | 21.3951 | 31.7333 | 3.2589 | 7.5418 | 100% |  |  | 100% |  |  | 91.59% | 92.75% | 16.32% | 1323720.2 | 1317467 | 5134 | 1312333 | 335.0909 | 5.4525 | 1653548.3871 | 90.5% | 20.56% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-01-29 | 2024 | 2024 | 2024-01-01 | 31 | 10.6667 | 3.8804 | 0.94531 | 4.4883 | 0.23084 | 22.7089 | 34.1333 | 1.6568 | 3.7793 | 100% |  |  | 100% |  |  | 90.64% | 93.17% | 16.95% | 1375359.2 | 1367934 | 4800 | 1363134 | 335.0909 | 5.4525 | 1653548.3871 | 90.5% | 20.56% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-01-30 | 2024 | 2024 | 2024-01-01 | 31 | 10.5 | 2.3746 | 0.5782 | 2.4641 | 0.16937 | 22.0329 | 28.7 | 2.5396 | 5.2352 | 100% |  |  | 100% |  |  | 96.45% | 95.74% | 9.903% | 802776.7 | 800600 | 4200 | 796400 | 335.0909 | 5.4525 | 1653548.3871 | 90.5% | 20.56% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-01-31 | 2024 | 2024 | 2024-01-01 | 31 | 10.8333 | 4.5005 | 1.1009 | 5.3798 | 0.24694 | 24.2808 | 37.0333 | 3.3518 | 6.9093 | 100% |  |  | 100% |  |  | 88.17% | 91.13% | 19.76% | 1604626.8 | 1593267 | 3866 | 1589401 | 335.0909 | 5.4525 | 1653548.3871 | 90.5% | 20.56% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-02-01 | 2024 | 2024 | 2024-02-01 | 29 | 10.6667 | 4.4338 | 1.1119 | 5.2885 | 0.25973 | 23.5376 | 35.4 | 2.3371 | 4.8707 | 100% |  |  | 100% |  |  | 89.09% | 90.55% | 19.63% | 1594349.2 | 1583600 | 4867 | 1578733 | 335.0909 | 5.9503 | 1630689.6552 | 81.78% | 20.28% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-02-02 | 2024 | 2024 | 2024-02-01 | 29 | 10.8667 | 4.6212 | 1.0896 | 5.4912 | 0.24193 | 24.0576 | 36.9333 | 2.9607 | 6.2277 | 100% |  |  | 100% |  |  | 88.21% | 89.86% | 20.18% | 1639675.1 | 1628162 | 5000 | 1623162 | 335.0909 | 5.9503 | 1630689.6552 | 81.78% | 20.28% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-02-03 | 2024 | 2024 | 2024-02-01 | 29 | 10.7667 | 2.2433 | 0.41509 | 2.362 | 0.089091 | 20.5917 | 25.205 | 3.4854 | 7.2503 | 100% |  |  | 100% |  |  | 94.04% | 91.55% | 9.255% | 752474.5 | 749505 | 5200 | 744305 | 335.0909 | 5.9503 | 1630689.6552 | 81.78% | 20.28% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-02-04 | 2024 | 2024 | 2024-02-01 | 29 | 10.5 | 1.3447 | 0.18047 | 1.3425 | 0.034045 | 16.7944 | 20.7 | 2.4389 | 5.3833 | 100% |  |  | 100% |  |  | 94.83% | 89.65% | 5.305% | 434723.3 | 432000 | 5400 | 426600 | 335.0909 | 5.9503 | 1630689.6552 | 81.78% | 20.28% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-02-05 | 2024 | 2024 | 2024-02-01 | 29 | 10.9833 | 4.7629 | 0.9148 | 5.8184 | 0.20115 | 19.2636 | 32.2 | 2.2907 | 4.7963 | 99.99% |  |  | 100% |  |  | 87.69% | 88.11% | 21.26% | 1727094.7 | 1714866 | 5133 | 1709733 | 335.0909 | 5.9503 | 1630689.6552 | 81.78% | 20.28% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-02-06 | 2024 | 2024 | 2024-02-01 | 29 | 11.0167 | 4.6191 | 0.9193 | 5.4936 | 0.22016 | 20.882 | 32.9667 | 2.7919 | 5.6977 | 99.99% |  |  | 100% |  |  | 87.55% | 87.91% | 20.04% | 1627747.4 | 1616534 | 4934 | 1611600 | 335.0909 | 5.9503 | 1630689.6552 | 81.78% | 20.28% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-02-07 | 2024 | 2024 | 2024-02-01 | 29 | 10.8667 | 4.5404 | 1.2047 | 5.3582 | 0.22746 | 20.7371 | 30.3255 | 3.5611 | 6.6958 | 100% |  |  | 100% |  |  | 88.2% | 85.85% | 19.69% | 1599423.8 | 1588533 | 4933 | 1583600 | 335.0909 | 5.9503 | 1630689.6552 | 81.78% | 20.28% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-02-08 | 2024 | 2024 | 2024-02-01 | 29 | 11.1833 | 5.5075 | 1.175 | 6.7417 | 0.26733 | 20.7466 | 33.0333 | 3.1948 | 6.7532 | 100% |  |  | 100% |  |  | 83.41% | 84.62% | 23.43% | 1904310.4 | 1889200 | 4867 | 1884333 | 335.0909 | 5.9503 | 1630689.6552 | 81.78% | 20.28% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-02-09 | 2024 | 2024 | 2024-02-01 | 29 | 11.25 | 5.6022 | 1.2029 | 6.9038 | 0.24373 | 21.3704 | 38 | 1.9928 | 5.2855 | 100% |  |  | 100% |  |  | 82.4% | 84.4% | 23.7% | 1927106.8 | 1911162 | 4933 | 1906229 | 335.0909 | 5.9503 | 1630689.6552 | 81.78% | 20.28% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-02-10 | 2024 | 2024 | 2024-02-01 | 29 | 11.25 | 5.5581 | 1.2083 | 6.8154 | 0.25466 | 22.5794 | 34.5333 | 3.7804 | 7.6693 | 100% |  |  | 100% |  |  | 83.06% | 84.68% | 23.59% | 1917794.2 | 1901772 | 4933 | 1896839 | 335.0909 | 5.9503 | 1630689.6552 | 81.78% | 20.28% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-02-11 | 2024 | 2024 | 2024-02-01 | 29 | 11.25 | 5.5558 | 1.2115 | 6.7857 | 0.25762 | 22.2426 | 35.5333 | 2.9314 | 6.2647 | 100% |  |  | 100% |  |  | 83.33% | 85.22% | 23.56% | 1915399.9 | 1899667 | 4867 | 1894800 | 335.0909 | 5.9503 | 1630689.6552 | 81.78% | 20.28% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-02-12 | 2024 | 2024 | 2024-02-01 | 29 | 11.15 | 4.6893 | 1.0107 | 5.452 | 0.25417 | 21.2177 | 32.2 | 2.5802 | 5.5043 | 100% |  |  | 100% |  |  | 85.3% | 86.15% | 19.38% | 1573366.9 | 1563267 | 4933 | 1558334 | 335.0909 | 5.9503 | 1630689.6552 | 81.78% | 20.28% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-02-13 | 2024 | 2024 | 2024-02-01 | 29 | 11.1667 | 4.5562 | 0.99223 | 5.2813 | 0.25947 | 20.1492 | 29.3 | 3.5021 | 6.5208 | 100% |  |  | 100% |  |  | 87.89% | 86.56% | 19.34% | 1570744.6 | 1560400 | 5000 | 1555400 | 335.0909 | 5.9503 | 1630689.6552 | 81.78% | 20.28% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-02-14 | 2024 | 2024 | 2024-02-01 | 29 | 11.2833 | 5.311 | 1.2024 | 6.3927 | 0.26733 | 21.2026 | 31 | 4.0555 | 7.789 | 100% |  |  | 100% |  |  | 85.07% | 85.8% | 22.66% | 1841818.6 | 1827200 | 4867 | 1822333 | 335.0909 | 5.9503 | 1630689.6552 | 81.78% | 20.28% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-02-15 | 2024 | 2024 | 2024-02-01 | 29 | 11.3333 | 5.5317 | 1.2383 | 6.6767 | 0.26667 | 23.4317 | 36.9333 | 2.7217 | 5.9183 | 100% |  |  | 100% |  |  | 83.18% | 85.48% | 23.14% | 1880460.6 | 1865667 | 4800 | 1860867 | 335.0909 | 5.9503 | 1630689.6552 | 81.78% | 20.28% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-02-16 | 2024 | 2024 | 2024-02-01 | 29 | 11.2667 | 5.2613 | 1.1723 | 6.2989 | 0.2614 | 25.2209 | 38.1333 | 2.749 | 6.1127 | 100% |  |  | 100% |  |  | 84.14% | 86.63% | 22.08% | 1794064.4 | 1780600 | 4733 | 1775867 | 335.0909 | 5.9503 | 1630689.6552 | 81.78% | 20.28% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-02-17 | 2024 | 2024 | 2024-02-01 | 29 | 11.3833 | 5.5489 | 1.2318 | 6.6748 | 0.25797 | 26.3087 | 41.1667 | 2.0704 | 4.7628 | 100% |  |  | 100% |  |  | 82.41% | 85.72% | 22.92% | 1862568.5 | 1847933 | 4600 | 1843333 | 335.0909 | 5.9503 | 1630689.6552 | 81.78% | 20.28% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-02-18 | 2024 | 2024 | 2024-02-01 | 29 | 11.5667 | 5.3696 | 1.2224 | 6.3099 | 0.28515 | 26.5451 | 37.1667 | 7.3156 | 13.6442 | 96.15% |  |  | 100% |  |  | 81.91% | 83.23% | 21.53% | 1751313 | 1736267 | 4467 | 1731800 | 335.0909 | 5.9503 | 1630689.6552 | 81.78% | 20.28% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-02-19 | 2024 | 2024 | 2024-02-01 | 29 | 11.2667 | 4.9297 | 1.1222 | 5.718 | 0.25809 | 27.0832 | 36.6333 | 9.1253 | 13.2645 | 98.93% |  |  | 100% |  |  | 82.27% | 85.05% | 19.6% | 1592645.9 | 1580934 | 4667 | 1576267 | 335.0909 | 5.9503 | 1630689.6552 | 81.78% | 20.28% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-02-20 | 2024 | 2024 | 2024-02-01 | 29 | 11.2833 | 4.9893 | 1.1407 | 5.7841 | 0.2825 | 25.2006 | 38.3425 | 2.7976 | 5.67 | 100% |  |  | 100% |  |  | 85.9% | 88.03% | 20.7% | 1681415.4 | 1669666 | 4733 | 1664933 | 335.0909 | 5.9503 | 1630689.6552 | 81.78% | 20.28% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-02-21 | 2024 | 2024 | 2024-02-01 | 29 | 11.3667 | 5.3247 | 1.2245 | 6.2096 | 0.29266 | 25.2942 | 38.8905 | 3.0602 | 7.6092 | 100% |  |  | 100% |  |  | 84.53% | 87.06% | 21.87% | 1776739.7 | 1763401 | 4600 | 1758801 | 335.0909 | 5.9503 | 1630689.6552 | 81.78% | 20.28% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-02-22 | 2024 | 2024 | 2024-02-01 | 29 | 11.35 | 5.4092 | 1.2466 | 6.3425 | 0.28426 | 23.3379 | 36.9667 | 2.4736 | 5.866 | 99.99% |  |  | 100% |  |  | 83.97% | 85.95% | 22.19% | 1803555.4 | 1789133 | 4600 | 1784533 | 335.0909 | 5.9503 | 1630689.6552 | 81.78% | 20.28% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-02-23 | 2024 | 2024 | 2024-02-01 | 29 | 11.5167 | 5.8801 | 1.3543 | 6.9276 | 0.28969 | 23.0075 | 38.8333 | 2.5233 | 5.8722 | 100% |  |  | 100% |  |  | 82.52% | 84.88% | 23.82% | 1935733.8 | 1920133 | 4600 | 1915533 | 335.0909 | 5.9503 | 1630689.6552 | 81.78% | 20.28% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-02-24 | 2024 | 2024 | 2024-02-01 | 29 | 11.55 | 6.0069 | 1.3952 | 7.0851 | 0.29919 | 23.3914 | 37.5333 | 3.059 | 7.199 | 99.99% |  |  | 100% |  |  | 81.8% | 84.17% | 24.15% | 1962896.2 | 1946667 | 4600 | 1942067 | 335.0909 | 5.9503 | 1630689.6552 | 81.78% | 20.28% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-02-25 | 2024 | 2024 | 2024-02-01 | 29 | 11.4333 | 5.3128 | 1.225 | 6.1032 | 0.30418 | 23.7022 | 35.2 | 3.3706 | 7.3893 | 99.99% |  |  | 100% |  |  | 85.05% | 86.62% | 21.63% | 1757211.8 | 1744267 | 4800 | 1739467 | 335.0909 | 5.9503 | 1630689.6552 | 81.78% | 20.28% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-02-26 | 2024 | 2024 | 2024-02-01 | 29 | 11.3667 | 4.1587 | 0.88039 | 4.7087 | 0.22102 | 23.2822 | 33.5 | 3.4877 | 7.495 | 100% |  |  | 100% |  |  | 83.97% | 85.55% | 16.47% | 1339448.4 | 1329667 | 4733 | 1324934 | 335.0909 | 5.9503 | 1630689.6552 | 81.78% | 20.28% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-02-27 | 2024 | 2024 | 2024-02-01 | 29 | 11.45 | 5.4731 | 1.2824 | 6.3725 | 0.29558 | 22.5531 | 31.9 | 5.6531 | 9.8425 | 100% |  |  | 100% |  |  | 86.35% | 86.91% | 22.93% | 1861240.3 | 1848867 | 5000 | 1843867 | 335.0909 | 5.9503 | 1630689.6552 | 81.78% | 20.28% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-02-28 | 2024 | 2024 | 2024-02-01 | 29 | 11.5833 | 5.7528 | 1.3224 | 6.7195 | 0.28517 | 23.7094 | 36.9333 | 3.1313 | 6.0695 | 99.99% |  |  | 100% |  |  | 84.6% | 86.58% | 23.69% | 1924723.9 | 1909733 | 4867 | 1904866 | 335.0909 | 5.9503 | 1630689.6552 | 81.78% | 20.28% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-02-29 | 2024 | 2024 | 2024-02-01 | 29 | 11.5667 | 5.7136 | 1.3136 | 6.6404 | 0.2822 | 26.9808 | 41.5333 | 3.0716 | 6.4392 | 100% |  |  | 100% |  |  | 84.2% | 87.26% | 23.3% | 1892115.6 | 1878267 | 4800 | 1873467 | 335.0909 | 5.9503 | 1630689.6552 | 81.78% | 20.28% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-03-01 | 2024 | 2024 | 2024-03-01 | 31 | 11.3833 | 4.1794 | 0.97235 | 4.5554 | 0.2495 | 27.1221 | 36.3044 | 5.6959 | 12.3413 | 100% |  |  | 100% |  |  | 88.26% | 87.62% | 16.75% | 1360182.7 | 1352067 | 4800 | 1347267 | 335.0909 | 6.9595 | 1951935.4839 | 83.7% | 24.27% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-03-02 | 2024 | 2024 | 2024-03-01 | 31 | 11.55 | 5.2426 | 1.1002 | 5.8977 | 0.28883 | 23.0163 | 32.3667 | 8.9576 | 14.0028 | 100% |  |  | 100% |  |  | 83.95% | 81.47% | 20.63% | 1675922.9 | 1664000 | 4933 | 1659067 | 335.0909 | 6.9595 | 1951935.4839 | 83.7% | 24.27% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-03-03 | 2024 | 2024 | 2024-03-01 | 31 | 11.7667 | 6.5117 | 1.43 | 7.5067 | 0.31667 | 18.51 | 34.78 | 2.8683 | 7.1433 | 99.94% |  |  | 100% |  |  | 80.63% | 79.79% | 25.22% | 2050313.3 | 2032933 | 4734 | 2028199 | 335.0909 | 6.9595 | 1951935.4839 | 83.7% | 24.27% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-03-04 | 2024 | 2024 | 2024-03-01 | 31 | 11.7667 | 6.3352 | 1.399 | 7.5015 | 0.32819 | 19.2357 | 32.8 | 3.2854 | 6.4353 | 100% |  |  | 100% |  |  | 80.85% | 80.06% | 25.27% | 2055448.2 | 2037067 | 4666 | 2032401 | 335.0909 | 6.9595 | 1951935.4839 | 83.7% | 24.27% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-03-05 | 2024 | 2024 | 2024-03-01 | 31 | 11.75 | 6.1712 | 1.3689 | 6.9349 | 0.33428 | 20.4621 | 32.6 | 4.0049 | 7.4765 | 100% |  |  | 100% |  |  | 82.28% | 81.36% | 23.78% | 1934126.3 | 1916667 | 4600 | 1912067 | 335.0909 | 6.9595 | 1951935.4839 | 83.7% | 24.27% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-03-06 | 2024 | 2024 | 2024-03-01 | 31 | 11.6833 | 5.568 | 1.2137 | 6.2264 | 0.30005 | 22.744 | 37.6667 | 2.4238 | 5.4922 | 100% |  |  | 100% |  |  | 82.97% | 82.65% | 21.52% | 1748425.6 | 1735867 | 4800 | 1731067 | 335.0909 | 6.9595 | 1951935.4839 | 83.7% | 24.27% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-03-07 | 2024 | 2024 | 2024-03-01 | 31 | 11.8 | 6.1709 | 1.3655 | 7.0277 | 0.3098 | 24.0448 | 37.5 | 3.4436 | 6.9962 | 99.99% |  |  | 100% |  |  | 83.3% | 83.56% | 24.39% | 1981683.9 | 1966267 | 4734 | 1961533 | 335.0909 | 6.9595 | 1951935.4839 | 83.7% | 24.27% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-03-08 | 2024 | 2024 | 2024-03-01 | 31 | 11.85 | 6.508 | 1.4668 | 7.4024 | 0.3579 | 23.3058 | 36.8333 | 3.1717 | 6.6963 | 100% |  |  | 100% |  |  | 81.04% | 81.43% | 24.99% | 2031645.4 | 2014866 | 4733 | 2010133 | 335.0909 | 6.9595 | 1951935.4839 | 83.7% | 24.27% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-03-09 | 2024 | 2024 | 2024-03-01 | 31 | 11.8333 | 6.1947 | 1.3993 | 7.008 | 0.31178 | 24.8017 | 36.9333 | 3.565 | 7.4285 | 100% |  |  | 100% |  |  | 81.75% | 82.06% | 23.87% | 1939933.3 | 1924201 | 4467 | 1919734 | 335.0909 | 6.9595 | 1951935.4839 | 83.7% | 24.27% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-03-10 | 2024 | 2024 | 2024-03-01 | 31 | 11.85 | 5.8521 | 1.3201 | 6.4598 | 0.32384 | 26.8281 | 40.3 | 3.2017 | 7.0768 | 100% |  |  | 100% |  |  | 82.16% | 83.16% | 22.11% | 1796205.5 | 1783066 | 4600 | 1778466 | 335.0909 | 6.9595 | 1951935.4839 | 83.7% | 24.27% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-03-11 | 2024 | 2024 | 2024-03-01 | 31 | 11.8833 | 6.3341 | 1.4101 | 7.1156 | 0.30637 | 28.4693 | 44 | 3.1601 | 7.2415 | 100% |  |  | 100% |  |  | 81.98% | 83.54% | 24.3% | 1974379.3 | 1959267 | 4666 | 1954601 | 335.0909 | 6.9595 | 1951935.4839 | 83.7% | 24.27% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-03-12 | 2024 | 2024 | 2024-03-01 | 31 | 11.8833 | 6.347 | 1.427 | 7.1372 | 0.32141 | 27.4678 | 42.0667 | 2.6309 | 6.5532 | 99.99% |  |  | 100% |  |  | 81.96% | 83.53% | 24.37% | 1979566.3 | 1964867 | 4800 | 1960067 | 335.0909 | 6.9595 | 1951935.4839 | 83.7% | 24.27% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-03-13 | 2024 | 2024 | 2024-03-01 | 31 | 11.9 | 6.1888 | 1.3987 | 6.8936 | 0.34175 | 26.9712 | 39.4333 | 4.2581 | 8.5365 | 100% |  |  | 100% |  |  | 83.06% | 83.54% | 23.86% | 1937792.4 | 1923267 | 4667 | 1918600 | 335.0909 | 6.9595 | 1951935.4839 | 83.7% | 24.27% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-03-14 | 2024 | 2024 | 2024-03-01 | 31 | 11.95 | 6.5367 | 1.4983 | 7.2783 | 0.36167 | 26.8733 | 42.4 | 2.31 | 5.2833 | 99.49% |  |  | 100% |  |  | 80.59% | 82.16% | 24.44% | 1985400.9 | 1970333 | 4733 | 1965600 | 335.0909 | 6.9595 | 1951935.4839 | 83.7% | 24.27% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-03-15 | 2024 | 2024 | 2024-03-01 | 31 | 11.8833 | 6.4047 | 1.468 | 7.1128 | 0.35273 | 27.4399 | 41.2 | 3.2735 | 6.7442 | 100% |  |  | 100% |  |  | 82.38% | 83.65% | 24.42% | 1983602 | 1968267 | 4734 | 1963533 | 335.0909 | 6.9595 | 1951935.4839 | 83.7% | 24.27% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-03-16 | 2024 | 2024 | 2024-03-01 | 31 | 11.8833 | 6.5201 | 1.4996 | 7.2157 | 0.35182 | 28.5204 | 42.9667 | 3.1449 | 6.9852 | 100% |  |  | 100% |  |  | 81.62% | 83.35% | 24.54% | 1993656.2 | 1978200 | 4800 | 1973400 | 335.0909 | 6.9595 | 1951935.4839 | 83.7% | 24.27% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-03-17 | 2024 | 2024 | 2024-03-01 | 31 | 12.0333 | 5.2093 | 1.1967 | 5.535 | 0.3521 | 28.1708 | 37 | 3.5337 | 7.3185 | 100% |  |  | 100% |  |  | 88.28% | 88.02% | 20.36% | 1650535 | 1641934 | 4600 | 1637334 | 335.0909 | 6.9595 | 1951935.4839 | 83.7% | 24.27% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-03-18 | 2024 | 2024 | 2024-03-01 | 31 | 12.0667 | 6.7145 | 1.5468 | 7.4147 | 0.35172 | 29.2419 | 44.0667 | 2.5874 | 6.4878 | 99.99% |  |  | 100% |  |  | 80.55% | 82.51% | 24.89% | 2021782 | 2006067 | 4733 | 2001334 | 335.0909 | 6.9595 | 1951935.4839 | 83.7% | 24.27% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-03-19 | 2024 | 2024 | 2024-03-01 | 31 | 12 | 6.4733 | 1.4936 | 7.1197 | 0.34767 | 32.1423 | 44.3667 | 3.6367 | 8.0738 | 99.83% |  |  | 100% |  |  | 81.5% | 84.06% | 24.18% | 1963915.8 | 1949133 | 4800 | 1944333 | 335.0909 | 6.9595 | 1951935.4839 | 83.7% | 24.27% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-03-20 | 2024 | 2024 | 2024-03-01 | 31 | 12 | 6.7031 | 1.571 | 7.2093 | 0.3649 | 31.114 | 43.4333 | 3.6438 | 6.7252 | 100% |  |  | 100% |  |  | 82.34% | 84.56% | 24.73% | 2007359.8 | 1992534 | 3467 | 1989067 | 335.0909 | 6.9595 | 1951935.4839 | 83.7% | 24.27% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-03-21 | 2024 | 2024 | 2024-03-01 | 31 | 11.9833 | 6.2516 | 1.4636 | 6.7275 | 0.33271 | 32.6403 | 47.1667 | 2.9882 | 7.1638 | 99.88% |  |  | 100% |  |  | 81.98% | 84.82% | 22.98% | 1866561.1 | 1852933 | 4733 | 1848200 | 335.0909 | 6.9595 | 1951935.4839 | 83.7% | 24.27% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-03-22 | 2024 | 2024 | 2024-03-01 | 31 | 12.1 | 6.7117 | 1.5537 | 7.2426 | 0.35469 | 32.3522 | 49 | 2.1554 | 5.451 | 100% |  |  | 100% |  |  | 81.9% | 84.88% | 24.71% | 2006609.4 | 1992267 | 4733 | 1987534 | 335.0909 | 6.9595 | 1951935.4839 | 83.7% | 24.27% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-03-23 | 2024 | 2024 | 2024-03-01 | 31 | 12 | 6.1627 | 1.438 | 6.5419 | 0.36697 | 33.3821 | 48.0786 | 3.0429 | 7.202 | 100% |  |  | 100% |  |  | 82.95% | 85.85% | 22.61% | 1835720.5 | 1822933 | 4667 | 1818266 | 335.0909 | 6.9595 | 1951935.4839 | 83.7% | 24.27% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-03-24 | 2024 | 2024 | 2024-03-01 | 31 | 12 | 6.5113 | 1.5017 | 6.9948 | 0.3487 | 32.5605 | 48.6 | 3.0076 | 6.3005 | 100% |  |  | 100% |  |  | 82.79% | 85.56% | 24.13% | 1959095.3 | 1945067 | 4600 | 1940467 | 335.0909 | 6.9595 | 1951935.4839 | 83.7% | 24.27% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-03-25 | 2024 | 2024 | 2024-03-01 | 31 | 12.15 | 5.4611 | 1.2585 | 5.7397 | 0.34203 | 32.7593 | 46.3667 | 2.0419 | 4.7788 | 100% |  |  | 100% |  |  | 85.36% | 87.41% | 20.41% | 1655616 | 1645734 | 4000 | 1641734 | 335.0909 | 6.9595 | 1951935.4839 | 83.7% | 24.27% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-03-26 | 2024 | 2024 | 2024-03-01 | 31 | 12.2 | 6.2273 | 1.4347 | 6.6283 | 0.36444 | 35.2688 | 49.3445 | 2.962 | 7.8658 | 100% |  |  | 100% |  |  | 82.67% | 85.95% | 22.83% | 1853765.6 | 1840533 | 4467 | 1836066 | 335.0909 | 6.9595 | 1951935.4839 | 83.7% | 24.27% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-03-27 | 2024 | 2024 | 2024-03-01 | 31 | 12.1 | 6.2168 | 1.4596 | 6.5876 | 0.36172 | 36.043 | 49.2073 | 4.628 | 9.9043 | 100% |  |  | 100% |  |  | 81.91% | 84.81% | 22.48% | 1824726.2 | 1812755 | 4666 | 1808089 | 335.0909 | 6.9595 | 1951935.4839 | 83.7% | 24.27% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-03-28 | 2024 | 2024 | 2024-03-01 | 31 | 12.1167 | 6.4066 | 1.5075 | 6.786 | 0.39309 | 33.5756 | 47.2333 | 3.5832 | 7.96 | 100% |  |  | 100% |  |  | 82.04% | 84.63% | 23.2% | 1882860.6 | 1870245 | 4600 | 1865645 | 335.0909 | 6.9595 | 1951935.4839 | 83.7% | 24.27% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-03-29 | 2024 | 2024 | 2024-03-01 | 31 | 12.15 | 5.8765 | 1.3738 | 6.2105 | 0.34915 | 32.5483 | 46.4831 | 3.5043 | 8.131 | 100% |  |  | 100% |  |  | 82.05% | 84.13% | 21.23% | 1723642.8 | 1712267 | 4667 | 1707600 | 335.0909 | 6.9595 | 1951935.4839 | 83.7% | 24.27% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-03-30 | 2024 | 2024 | 2024-03-01 | 31 | 12.3 | 7.081 | 1.6987 | 7.4897 | 0.41871 | 31.1205 | 42.8333 | 7.1439 | 13.074 | 100% |  |  | 100% |  |  | 81.3% | 82.27% | 25.37% | 2061302.3 | 2045067 | 4533 | 2040534 | 335.0909 | 6.9595 | 1951935.4839 | 83.7% | 24.27% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-03-31 | 2024 | 2024 | 2024-03-01 | 31 | 12.2333 | 6.5474 | 1.57 | 6.8963 | 0.40581 | 31.2078 | 45 | 2.8899 | 6.1703 | 100% |  |  | 100% |  |  | 83.64% | 85.9% | 24.03% | 1951710.2 | 1937467 | 4534 | 1932933 | 335.0909 | 6.9595 | 1951935.4839 | 83.7% | 24.27% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-04-01 | 2025 | 2024 | 2024-04-01 | 30 | 12.25 | 6.5411 | 1.5668 | 6.826 | 0.41456 | 30.8374 | 44.7667 | 3.1289 | 7.2525 | 100% |  |  | 100% |  |  | 83.14% | 83.69% | 23.65% | 1920526.1 | 1906467 | 4666 | 1901801 | 335.0909 | 7.1967 | 1969133.3333 | 81.65% | 24.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-04-02 | 2025 | 2024 | 2024-04-01 | 30 | 12.2 | 6.2612 | 1.5044 | 6.5243 | 0.39335 | 32.8013 | 47.7 | 2.466 | 6.7933 | 100% |  |  | 100% |  |  | 83.87% | 84.9% | 22.8% | 1850680.3 | 1838133 | 4600 | 1833533 | 335.0909 | 7.1967 | 1969133.3333 | 81.65% | 24.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-04-03 | 2025 | 2024 | 2024-04-01 | 30 | 12.3 | 5.8444 | 1.3952 | 5.9496 | 0.39836 | 30.9317 | 44.6333 | 3.3633 | 6.6835 | 100% |  |  | 100% |  |  | 87.57% | 87.17% | 21.71% | 1762119.8 | 1750534 | 4667 | 1745867 | 335.0909 | 7.1967 | 1969133.3333 | 81.65% | 24.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-04-04 | 2025 | 2024 | 2024-04-01 | 30 | 12.2667 | 5.2997 | 1.2797 | 5.4078 | 0.36701 | 33.265 | 44.7667 | 3.0643 | 6.661 | 100% |  |  | 100% |  |  | 85.95% | 86.31% | 19.37% | 1571072 | 1562133 | 4667 | 1557466 | 335.0909 | 7.1967 | 1969133.3333 | 81.65% | 24.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-04-05 | 2025 | 2024 | 2024-04-01 | 30 | 12.3167 | 4.2762 | 1.0204 | 4.3936 | 0.29272 | 30.9596 | 41.1 | 3.2958 | 9.0237 | 100% |  |  | 100% |  |  | 87.06% | 86.4% | 15.94% | 1293931.1 | 1286400 | 4666 | 1281734 | 335.0909 | 7.1967 | 1969133.3333 | 81.65% | 24.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-04-06 | 2025 | 2024 | 2024-04-01 | 30 | 12.4 | 6.3663 | 1.5114 | 6.4678 | 0.39705 | 32.538 | 45.5 | 2.6226 | 6.4307 | 100% |  |  | 100% |  |  | 84.32% | 85.11% | 22.72% | 1844942.3 | 1832067 | 4534 | 1827533 | 335.0909 | 7.1967 | 1969133.3333 | 81.65% | 24.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-04-07 | 2025 | 2024 | 2024-04-01 | 30 | 12.4833 | 6.9558 | 1.6818 | 7.1181 | 0.41641 | 34.1646 | 49.3333 | 2.5864 | 6.6273 | 100% |  |  | 100% |  |  | 74.62% | 84.5% | 22.13% | 1794042.2 | 1784333 | 4533 | 1779800 | 335.0909 | 7.1967 | 1969133.3333 | 81.65% | 24.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-04-08 | 2025 | 2024 | 2024-04-01 | 30 | 12.45 | 7.0444 | 1.7126 | 7.4486 | 0.43164 | 35.1635 | 50.5667 | 2.3532 | 6.5117 | 100% |  |  | 100% |  |  | 72.05% | 84.92% | 22.36% | 1812330 | 1802867 | 4533 | 1798334 | 335.0909 | 7.1967 | 1969133.3333 | 81.65% | 24.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-04-09 | 2025 | 2024 | 2024-04-01 | 30 | 12.3167 | 5.7657 | 1.4044 | 6.0135 | 0.37844 | 36.3279 | 47.6 | 3.4845 | 7.2108 | 100% |  |  | 100% |  |  | 83.27% | 84.98% | 20.86% | 1693106.4 | 1682400 | 4400 | 1678000 | 335.0909 | 7.1967 | 1969133.3333 | 81.65% | 24.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-04-10 | 2025 | 2024 | 2024-04-01 | 30 | 12.1333 | 5.0567 | 1.2295 | 5.3078 | 0.32897 | 37.0229 | 47.0667 | 3.2945 | 12.6117 | 99.99% |  |  | 100% |  |  | 82.35% | 84.42% | 18.21% | 1478704.6 | 1469201 | 4534 | 1464667 | 335.0909 | 7.1967 | 1969133.3333 | 81.65% | 24.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-04-11 | 2025 | 2024 | 2024-04-01 | 30 | 12.4833 | 5.4726 | 1.3505 | 5.7102 | 0.35439 | 35.5998 | 45.6667 | 3.4569 | 9.6637 | 100% |  |  | 100% |  |  | 82.62% | 84.26% | 19.66% | 1596368.8 | 1585333 | 4400 | 1580933 | 335.0909 | 7.1967 | 1969133.3333 | 81.65% | 24.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-04-12 | 2025 | 2024 | 2024-04-01 | 30 | 12.5167 | 5.5967 | 1.3961 | 5.8708 | 0.34478 | 34.1946 | 45.4173 | 5.1882 | 10.429 | 100% |  |  | 100% |  |  | 84.3% | 84.91% | 20.62% | 1674836.6 | 1662800 | 4400 | 1658400 | 335.0909 | 7.1967 | 1969133.3333 | 81.65% | 24.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-04-13 | 2025 | 2024 | 2024-04-01 | 30 | 12.5167 | 5.6619 | 1.3343 | 5.8931 | 0.38825 | 34.2785 | 47.2333 | 4.4865 | 10.2165 | 90.79% |  |  | 100% |  |  | 76.42% | 76.73% | 18.76% | 1522689.3 | 1513200 | 4200 | 1509000 | 335.0909 | 7.1967 | 1969133.3333 | 81.65% | 24.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-04-14 | 2025 | 2024 | 2024-04-01 | 30 | 12.3833 | 5.4689 | 1.0835 | 5.5489 | 0.32887 | 28.4744 | 40.4667 | 3.3475 | 7.5527 | 99.98% |  |  | 100% |  |  | 87.4% | 86.16% | 20.21% | 1638537.9 | 1628534 | 3400 | 1625134 | 335.0909 | 7.1967 | 1969133.3333 | 81.65% | 24.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-04-15 | 2025 | 2024 | 2024-04-01 | 30 | 12.4833 | 4.2452 | 0.87067 | 4.242 | 0.28384 | 29.8147 | 38.0667 | 4.4334 | 8.538 | 99.99% |  |  | 100% |  |  | 90.73% | 88.48% | 16.04% | 1300542.7 | 1294133 | 4466 | 1289667 | 335.0909 | 7.1967 | 1969133.3333 | 81.65% | 24.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-04-16 | 2025 | 2024 | 2024-04-01 | 30 | 12.55 | 6.8524 | 1.4772 | 7.0345 | 0.41236 | 33.0141 | 45.6667 | 3.3688 | 6.3942 | 100% |  |  | 100% |  |  | 82.11% | 83.37% | 24.07% | 1954284.3 | 1939867 | 4467 | 1935400 | 335.0909 | 7.1967 | 1969133.3333 | 81.65% | 24.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-04-17 | 2025 | 2024 | 2024-04-01 | 30 | 12.5333 | 4.9791 | 1.071 | 4.9696 | 0.35907 | 33.0631 | 44.3 | 2.2758 | 4.882 | 100% |  |  | 100% |  |  | 89.26% | 88.59% | 18.48% | 1496937.1 | 1491000 | 4533 | 1486467 | 335.0909 | 7.1967 | 1969133.3333 | 81.65% | 24.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-04-18 | 2025 | 2024 | 2024-04-01 | 30 | 12.5667 | 3.1967 | 0.6703 | 3.1568 | 0.21517 | 31.1901 | 36.0333 | 5.3479 | 12.4315 | 99.95% |  |  | 100% |  |  | 90.96% | 88.05% | 11.96% | 970201.4 | 966533 | 4400 | 962133 | 335.0909 | 7.1967 | 1969133.3333 | 81.65% | 24.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-04-19 | 2025 | 2024 | 2024-04-01 | 30 | 12.65 | 7.1314 | 1.5997 | 7.2866 | 0.45519 | 31.8663 | 43.1333 | 8.4607 | 13.6583 | 100% |  |  | 100% |  |  | 74.11% | 84.45% | 22.5% | 1825946.4 | 1813734 | 4267 | 1809467 | 335.0909 | 7.1967 | 1969133.3333 | 81.65% | 24.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-04-20 | 2025 | 2024 | 2024-04-01 | 30 | 12.7167 | 6.386 | 1.4237 | 6.4545 | 0.4273 | 30.3577 | 45.2667 | 2.7103 | 6.4568 | 100% |  |  | 100% |  |  | 83.3% | 83.25% | 22.4% | 1818059.8 | 1806067 | 4467 | 1801600 | 335.0909 | 7.1967 | 1969133.3333 | 81.65% | 24.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-04-21 | 2025 | 2024 | 2024-04-01 | 30 | 12.8333 | 6.6326 | 1.4842 | 6.7292 | 0.42406 | 32.5094 | 46.8333 | 2.4534 | 6.187 | 100% |  |  | 100% |  |  | 80.55% | 81.46% | 22.58% | 1833244 | 1820667 | 4466 | 1816201 | 335.0909 | 7.1967 | 1969133.3333 | 81.65% | 24.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-04-22 | 2025 | 2024 | 2024-04-01 | 30 | 12.8333 | 7.0306 | 1.6102 | 7.0631 | 0.46445 | 34.1816 | 47.5333 | 2.7463 | 6.5318 | 100% |  |  | 100% |  |  | 82.33% | 83.74% | 24.23% | 1967036.5 | 1953066 | 4467 | 1948599 | 335.0909 | 7.1967 | 1969133.3333 | 81.65% | 24.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-04-23 | 2025 | 2024 | 2024-04-01 | 30 | 12.8333 | 7.4395 | 1.7199 | 7.4951 | 0.4734 | 34.1741 | 49.0667 | 2.8043 | 7.3572 | 100% |  |  | 100% |  |  | 81.42% | 83.26% | 25.43% | 2064560.5 | 2049201 | 4333 | 2044868 | 335.0909 | 7.1967 | 1969133.3333 | 81.65% | 24.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-04-24 | 2025 | 2024 | 2024-04-01 | 30 | 12.7833 | 7.3685 | 1.6092 | 6.7201 | 0.47238 | 34.9386 | 49.1333 | 2.4885 | 7.2203 | 100% |  |  | 100% |  |  | 81.28% | 82.96% | 22.76% | 1837808.1 | 1834666 | 4400 | 1830266 | 335.0909 | 7.1967 | 1969133.3333 | 81.65% | 24.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-04-25 | 2025 | 2024 | 2024-04-01 | 30 | 12.45 | 7.0767 | 1.6337 | 7.3907 | 0.45121 | 36.265 | 51.7667 | 3.3238 | 7.9402 | 100% |  |  | 100% |  |  | 80.95% | 83.26% | 24.93% | 2024073 | 2009200 | 4400 | 2004800 | 335.0909 | 7.1967 | 1969133.3333 | 81.65% | 24.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-04-26 | 2025 | 2024 | 2024-04-01 | 30 | 12.8333 | 7.1683 | 1.6717 | 7.19 | 0.48167 | 33.37 | 45.8333 | 6.7 | 11.31 | 100% |  |  | 100% |  |  | 81.99% | 82.11% | 24.56% | 1994275.8 | 1979818 | 4400 | 1975418 | 335.0909 | 7.1967 | 1969133.3333 | 81.65% | 24.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-04-27 | 2025 | 2024 | 2024-04-01 | 30 | 12.8833 | 6.6283 | 1.5867 | 6.6667 | 0.49333 | 32.1533 | 45.4333 | 4.12 | 8.6467 | 100% |  |  | 100% |  |  | 84.44% | 84.73% | 23.45% | 1903291.6 | 1890649 | 4400 | 1886249 | 335.0909 | 7.1967 | 1969133.3333 | 81.65% | 24.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-04-28 | 2025 | 2024 | 2024-04-01 | 30 | 12.85 | 6.9833 | 1.63 | 6.9417 | 0.49833 | 34.8033 | 49.9333 | 2.6433 | 6.745 | 100% |  |  | 100% |  |  | 81.67% | 83.16% | 23.62% | 1917504.6 | 1904201 | 4400 | 1899801 | 335.0909 | 7.1967 | 1969133.3333 | 81.65% | 24.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-04-29 | 2025 | 2024 | 2024-04-01 | 30 | 12.8833 | 7.344 | 1.7607 | 7.4102 | 0.5359 | 33.5412 | 44.4333 | 5.7036 | 10.904 | 100% |  |  | 100% |  |  | 82.82% | 83.4% | 25.57% | 2076590.8 | 2061000 | 4467 | 2056533 | 335.0909 | 7.1967 | 1969133.3333 | 81.65% | 24.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-04-30 | 2025 | 2024 | 2024-04-01 | 30 | 13.0833 | 7.78 | 1.895 | 7.7717 | 0.56167 | 33.23 | 47.3333 | 3.8067 | 9.4083 | 100% |  |  | 100% |  |  | 80.75% | 82.19% | 26.15% | 2123396.9 | 2107267 | 4267 | 2103000 | 335.0909 | 7.1967 | 1969133.3333 | 81.65% | 24.49% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-05-01 | 2025 | 2024 | 2024-05-01 | 31 | 13.0833 | 7.9461 | 1.8976 | 7.9237 | 0.56605 | 31.3322 | 45.4477 | 2.95 | 8.0205 | 100% |  |  | 100% |  |  | 79.33% | 79.63% | 26.19% | 2126920 | 2110783 | 4333 | 2106450 | 335.0909 | 7.029 | 1949151.6129 | 82.75% | 24.24% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-05-02 | 2025 | 2024 | 2024-05-01 | 31 | 13.05 | 7.9376 | 1.8943 | 7.8498 | 0.57398 | 32.9495 | 47.4881 | 2.6697 | 6.5973 | 100% |  |  | 100% |  |  | 79.65% | 80.54% | 26.05% | 2115905.1 | 2099417 | 4333 | 2095084 | 335.0909 | 7.029 | 1949151.6129 | 82.75% | 24.24% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-05-03 | 2025 | 2024 | 2024-05-01 | 31 | 12.9667 | 6.3333 | 1.505 | 6.29 | 0.465 | 35.695 | 47.9667 | 3.4917 | 8.6917 | 100% |  |  | 100% |  |  | 82.08% | 82.55% | 21.51% | 1745718.1 | 1734333 | 4400 | 1729933 | 335.0909 | 7.029 | 1949151.6129 | 82.75% | 24.24% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-05-04 | 2025 | 2024 | 2024-05-01 | 31 | 12.95 | 6.3671 | 1.4958 | 6.3529 | 0.46792 | 34.7848 | 45.3333 | 6.1741 | 10.6958 | 100% |  |  | 100% |  |  | 83.64% | 82.96% | 22.14% | 1795947.8 | 1784734 | 4267 | 1780467 | 335.0909 | 7.029 | 1949151.6129 | 82.75% | 24.24% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-05-05 | 2025 | 2024 | 2024-05-01 | 31 | 12.8833 | 7.104 | 1.7063 | 7.035 | 0.5094 | 36.0913 | 49.3333 | 3.2272 | 6.5918 | 100% |  |  | 100% |  |  | 82.75% | 83.67% | 24.25% | 1968679.4 | 1954933 | 4333 | 1950600 | 335.0909 | 7.029 | 1949151.6129 | 82.75% | 24.24% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-05-06 | 2025 | 2024 | 2024-05-01 | 31 | 12.9833 | 6.2726 | 1.5027 | 6.186 | 0.47 | 37.5756 | 50.0333 | 2.7455 | 6.1215 | 100% |  |  | 100% |  |  | 83.12% | 83.85% | 21.42% | 1737928.8 | 1727267 | 4334 | 1722933 | 335.0909 | 7.029 | 1949151.6129 | 82.75% | 24.24% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-05-07 | 2025 | 2024 | 2024-05-01 | 31 | 12.9167 | 6.1183 | 1.4733 | 6.0783 | 0.44667 | 38.785 | 50.3667 | 3.465 | 6.6383 | 99.74% |  |  | 100% |  |  | 82.6% | 83.93% | 20.92% | 1697237.1 | 1686734 | 4266 | 1682468 | 335.0909 | 7.029 | 1949151.6129 | 82.75% | 24.24% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-05-08 | 2025 | 2024 | 2024-05-01 | 31 | 13.0333 | 7.6207 | 1.8386 | 7.507 | 0.55252 | 40.8039 | 53.5667 | 3.7047 | 7.7302 | 99.89% |  |  | 100% |  |  | 81.02% | 83.52% | 25.34% | 2056376 | 2042333 | 4267 | 2038066 | 335.0909 | 7.029 | 1949151.6129 | 82.75% | 24.24% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-05-09 | 2025 | 2024 | 2024-05-01 | 31 | 13.05 | 7.2789 | 1.7644 | 7.1567 | 0.52335 | 40.1249 | 53.1667 | 4.2866 | 7.7842 | 100% |  |  | 100% |  |  | 80.4% | 82.57% | 23.98% | 1946438.1 | 1932449 | 4267 | 1928182 | 335.0909 | 7.029 | 1949151.6129 | 82.75% | 24.24% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-05-10 | 2025 | 2024 | 2024-05-01 | 31 | 13.05 | 7.2164 | 1.729 | 7.0598 | 0.53399 | 38.0705 | 49.4333 | 4.9326 | 8.6732 | 100% |  |  | 100% |  |  | 82.62% | 83.45% | 24.3% | 1972724.1 | 1958751 | 4200 | 1954551 | 335.0909 | 7.029 | 1949151.6129 | 82.75% | 24.24% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-05-11 | 2025 | 2024 | 2024-05-01 | 31 | 12.9833 | 6.1333 | 1.515 | 6.02 | 0.44833 | 34.33 | 39.8633 | 4.9117 | 9.9783 | 100% |  |  | 100% |  |  | 89.23% | 83.5% | 22.38% | 1816072.5 | 1804249 | 4200 | 1800049 | 335.0909 | 7.029 | 1949151.6129 | 82.75% | 24.24% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-05-12 | 2025 | 2024 | 2024-05-01 | 31 | 13.1833 | 7.6417 | 1.835 | 7.4356 | 0.55758 | 36.8844 | 51.8667 | 3.399 | 9.1873 | 99.98% |  |  | 100% |  |  | 81.53% | 82.63% | 25.26% | 2050404.8 | 2035752 | 4266 | 2031486 | 335.0909 | 7.029 | 1949151.6129 | 82.75% | 24.24% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-05-13 | 2025 | 2024 | 2024-05-01 | 31 | 13.1 | 7.33 | 1.7717 | 7.1433 | 0.53667 | 38.2367 | 52.4867 | 3.4317 | 6.7833 | 100% |  |  | 100% |  |  | 82.28% | 83.98% | 24.49% | 1987922.8 | 1973748 | 4334 | 1969414 | 335.0909 | 7.029 | 1949151.6129 | 82.75% | 24.24% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-05-14 | 2025 | 2024 | 2024-05-01 | 31 | 13.2 | 6.2561 | 1.475 | 6.1278 | 0.45127 | 34.6303 | 45.6333 | 4.7626 | 13.6405 | 99.99% |  |  | 100% |  |  | 83.21% | 83.98% | 21.25% | 1725284.6 | 1712852 | 4266 | 1708586 | 335.0909 | 7.029 | 1949151.6129 | 82.75% | 24.24% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-05-15 | 2025 | 2024 | 2024-05-01 | 31 | 13.1333 | 7.3388 | 1.6553 | 7.1517 | 0.54498 | 38.0424 | 52.4 | 3.7559 | 7.9977 | 100% |  |  | 100% |  |  | 82.01% | 83.52% | 24.44% | 1983219.6 | 1969734 | 4400 | 1965334 | 335.0909 | 7.029 | 1949151.6129 | 82.75% | 24.24% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-05-16 | 2025 | 2024 | 2024-05-01 | 31 | 13.1333 | 7.3665 | 1.6893 | 7.1667 | 0.558 | 40.7895 | 54.2 | 3.084 | 7.8452 | 99.99% |  |  | 100% |  |  | 80.5% | 82.9% | 24.04% | 1950276.1 | 1937400 | 4267 | 1933133 | 335.0909 | 7.029 | 1949151.6129 | 82.75% | 24.24% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-05-17 | 2025 | 2024 | 2024-05-01 | 31 | 13.0833 | 7.3327 | 1.6975 | 7.1678 | 0.55276 | 40.9312 | 52.3 | 3.7435 | 7.4092 | 100% |  |  | 100% |  |  | 81.24% | 83.69% | 24.26% | 1969175.5 | 1955514 | 4333 | 1951181 | 335.0909 | 7.029 | 1949151.6129 | 82.75% | 24.24% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-05-18 | 2025 | 2024 | 2024-05-01 | 31 | 13.15 | 7.375 | 1.72 | 7.1717 | 0.56333 | 41.66 | 53.5 | 3.8233 | 7.6733 | 100% |  |  | 100% |  |  | 81.35% | 83.76% | 24.31% | 1971055.1 | 1957300 | 2400 | 1954900 | 335.0909 | 7.029 | 1949151.6129 | 82.75% | 24.24% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-05-19 | 2025 | 2024 | 2024-05-01 | 31 | 13.2167 | 6.8573 | 1.6196 | 6.6713 | 0.55314 | 41.1528 | 52.6905 | 3.7798 | 9.2285 | 100% |  |  | 100% |  |  | 81.81% | 83.93% | 22.74% | 1844519.7 | 1832986 | 4134 | 1828852 | 335.0909 | 7.029 | 1949151.6129 | 82.75% | 24.24% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-05-20 | 2025 | 2024 | 2024-05-01 | 31 | 13.2333 | 7.3183 | 1.7317 | 7.0717 | 0.55833 | 39.365 | 51.6467 | 5.5633 | 10.83 | 100% |  |  | 100% |  |  | 82.74% | 83.95% | 24.38% | 1978802 | 1964814 | 4233 | 1960581 | 335.0909 | 7.029 | 1949151.6129 | 82.75% | 24.24% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-05-21 | 2025 | 2024 | 2024-05-01 | 31 | 13.2833 | 7.7444 | 1.8207 | 7.4178 | 0.57952 | 39.1075 | 55.2333 | 2.2074 | 6.532 | 100% |  |  | 100% |  |  | 81.28% | 83.43% | 25.12% | 2038619.3 | 2024386 | 4167 | 2020219 | 335.0909 | 7.029 | 1949151.6129 | 82.75% | 24.24% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-05-22 | 2025 | 2024 | 2024-05-01 | 31 | 13.2167 | 6.4858 | 1.558 | 6.2307 | 0.5316 | 42.1479 | 51.4667 | 3.3591 | 7.2422 | 100% |  |  | 100% |  |  | 81.78% | 83.75% | 21.23% | 1722803.4 | 1711801 | 4333 | 1707468 | 335.0909 | 7.029 | 1949151.6129 | 82.75% | 24.24% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-05-23 | 2025 | 2024 | 2024-05-01 | 31 | 13.2833 | 7.5509 | 1.8195 | 7.2547 | 0.59465 | 42.7496 | 56.1 | 2.1103 | 7.1392 | 100% |  |  | 100% |  |  | 80.9% | 84.21% | 24.45% | 1984271.6 | 1970800 | 4200 | 1966600 | 335.0909 | 7.029 | 1949151.6129 | 82.75% | 24.24% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-05-24 | 2025 | 2024 | 2024-05-01 | 31 | 13.25 | 7.3014 | 1.7904 | 7.0386 | 0.58851 | 42.7659 | 56.0867 | 2.3038 | 7.1672 | 100% |  |  | 100% |  |  | 81.76% | 84.85% | 23.98% | 1945315.4 | 1932467 | 4133 | 1928334 | 335.0909 | 7.029 | 1949151.6129 | 82.75% | 24.24% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-05-25 | 2025 | 2024 | 2024-05-01 | 31 | 13.2167 | 6.5229 | 1.5967 | 6.286 | 0.53043 | 42.4342 | 53.9323 | 2.7653 | 6.9102 | 100% |  |  | 100% |  |  | 83.45% | 85.89% | 21.86% | 1772458.8 | 1761866 | 4200 | 1757666 | 335.0909 | 7.029 | 1949151.6129 | 82.75% | 24.24% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-05-26 | 2025 | 2024 | 2024-05-01 | 31 | 13.0667 | 6.8814 | 1.6935 | 6.6562 | 0.57037 | 43.4683 | 53.6333 | 5.072 | 8.5525 | 100% |  |  | 100% |  |  | 82.08% | 84.47% | 22.76% | 1847109.9 | 1834867 | 4200 | 1830667 | 335.0909 | 7.029 | 1949151.6129 | 82.75% | 24.24% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-05-27 | 2025 | 2024 | 2024-05-01 | 31 | 13.3 | 7.8373 | 1.9473 | 7.5506 | 0.64792 | 42.8213 | 52.6919 | 6.0912 | 11.6745 | 100% |  |  | 100% |  |  | 78.98% | 81.3% | 24.85% | 2016494.1 | 2002334 | 4134 | 1998200 | 335.0909 | 7.029 | 1949151.6129 | 82.75% | 24.24% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-05-28 | 2025 | 2024 | 2024-05-01 | 31 | 13.3333 | 7.4717 | 1.8533 | 7.2117 | 0.61333 | 40.8067 | 52.2667 | 6.73 | 10.74 | 100% |  |  | 100% |  |  | 82.49% | 83.92% | 24.79% | 2011157 | 1997379 | 3933 | 1993446 | 335.0909 | 7.029 | 1949151.6129 | 82.75% | 24.24% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-05-29 | 2025 | 2024 | 2024-05-01 | 31 | 13.4167 | 7.5967 | 1.8833 | 7.29 | 0.625 | 37.5917 | 50.7 | 6.9983 | 10.9917 | 100% |  |  | 100% |  |  | 82.91% | 83.2% | 25.18% | 2043095 | 2029200 | 3900 | 2025300 | 335.0909 | 7.029 | 1949151.6129 | 82.75% | 24.24% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-05-30 | 2025 | 2024 | 2024-05-01 | 31 | 13.3833 | 7.771 | 1.9444 | 7.4557 | 0.63491 | 38.5603 | 51.6333 | 6.277 | 9.9778 | 100% |  |  | 100% |  |  | 82.25% | 83.09% | 25.55% | 2073737.7 | 2058888 | 4100 | 2054788 | 335.0909 | 7.029 | 1949151.6129 | 82.75% | 24.24% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-05-31 | 2025 | 2024 | 2024-05-01 | 31 | 13.4 | 7.826 | 1.9629 | 7.4817 | 0.65317 | 37.6669 | 50.6763 | 7.001 | 11.2653 | 100% |  |  | 100% |  |  | 82.42% | 82.75% | 25.69% | 2086899.9 | 2070600 | 4200 | 2066400 | 335.0909 | 7.029 | 1949151.6129 | 82.75% | 24.24% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-06-01 | 2025 | 2024 | 2024-06-01 | 30 | 13.4333 | 7.7339 | 1.9352 | 7.3991 | 0.63868 | 36.4647 | 50.3667 | 5.8335 | 10.1455 | 100% |  |  | 100% |  |  | 82.55% | 83.01% | 25.45% | 2066341 | 2050867 | 4133 | 2046734 | 335.0909 | 6.4267 | 1809456.6667 | 84.02% | 22.5% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-06-02 | 2025 | 2024 | 2024-06-01 | 30 | 13.4 | 7.6017 | 1.9054 | 7.2975 | 0.62568 | 36.8259 | 50.6 | 5.5135 | 10.1692 | 99.99% |  |  | 100% |  |  | 83.29% | 83.82% | 25.33% | 2055463.8 | 2041000 | 4200 | 2036800 | 335.0909 | 6.4267 | 1809456.6667 | 84.02% | 22.5% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-06-03 | 2025 | 2024 | 2024-06-01 | 30 | 13.3667 | 7.4171 | 1.8651 | 7.1461 | 0.62746 | 38.1491 | 50.7667 | 6.0069 | 10.4697 | 99.99% |  |  | 100% |  |  | 83.21% | 84.02% | 24.78% | 2010937.3 | 1996600 | 4134 | 1992466 | 335.0909 | 6.4267 | 1809456.6667 | 84.02% | 22.5% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-06-04 | 2025 | 2024 | 2024-06-01 | 30 | 13.4333 | 7.6317 | 1.9367 | 7.3367 | 0.65333 | 37.375 | 49.1333 | 7.7933 | 12.2533 | 99.99% |  |  | 100% |  |  | 82.49% | 82.66% | 25.22% | 2047212 | 2031845 | 3933 | 2027912 | 335.0909 | 6.4267 | 1809456.6667 | 84.02% | 22.5% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-06-05 | 2025 | 2024 | 2024-06-01 | 30 | 13.3667 | 7.4305 | 1.8905 | 7.1506 | 0.63998 | 34.9062 | 46.8 | 8.0602 | 12.2332 | 99.97% |  |  | 100% |  |  | 84.49% | 83.74% | 25.17% | 2043302.3 | 2028422 | 4067 | 2024355 | 335.0909 | 6.4267 | 1809456.6667 | 84.02% | 22.5% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-06-06 | 2025 | 2024 | 2024-06-01 | 30 | 13.3667 | 7.1254 | 1.7912 | 6.8602 | 0.60975 | 34.4281 | 48.6 | 4.966 | 8.7122 | 99.99% |  |  | 100% |  |  | 83.23% | 82.99% | 23.79% | 1930076.4 | 1917534 | 4266 | 1913268 | 335.0909 | 6.4267 | 1809456.6667 | 84.02% | 22.5% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-06-07 | 2025 | 2024 | 2024-06-01 | 30 | 13.3167 | 6.8779 | 1.7574 | 6.6368 | 0.59131 | 37.3292 | 51.2333 | 3.8695 | 8.4048 | 100% |  |  | 100% |  |  | 83.63% | 84.49% | 23.13% | 1875020 | 1864000 | 4200 | 1859800 | 335.0909 | 6.4267 | 1809456.6667 | 84.02% | 22.5% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-06-08 | 2025 | 2024 | 2024-06-01 | 30 | 13.4167 | 6.7544 | 1.6473 | 6.5053 | 0.59343 | 34.0831 | 47.3667 | 4.2604 | 8.3602 | 99.94% |  |  | 100% |  |  | 84.41% | 83.85% | 22.88% | 1854136.5 | 1844000 | 4067 | 1839933 | 335.0909 | 6.4267 | 1809456.6667 | 84.02% | 22.5% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-06-09 | 2025 | 2024 | 2024-06-01 | 30 | 13.4167 | 7.5517 | 1.6983 | 7.2033 | 0.55667 | 36.135 | 50.7333 | 2.755 | 6.0367 | 100% |  |  | 100% |  |  | 80.86% | 81.96% | 24.27% | 1970731 | 1955644 | 3900 | 1951744 | 335.0909 | 6.4267 | 1809456.6667 | 84.02% | 22.5% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-06-10 | 2025 | 2024 | 2024-06-01 | 30 | 13.4167 | 7.7048 | 1.7185 | 7.347 | 0.55997 | 36.8631 | 51.5 | 3.1587 | 6.3923 | 100% |  |  | 100% |  |  | 81.96% | 83.48% | 25.09% | 2036258.8 | 2021956 | 4167 | 2017789 | 335.0909 | 6.4267 | 1809456.6667 | 84.02% | 22.5% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-06-11 | 2025 | 2024 | 2024-06-01 | 30 | 13.4167 | 7.6841 | 1.7965 | 7.3186 | 0.58768 | 37.7129 | 51.7333 | 4.1277 | 7.7702 | 100% |  |  | 100% |  |  | 81.7% | 83.11% | 24.92% | 2021855.2 | 2007867 | 4133 | 2003734 | 335.0909 | 6.4267 | 1809456.6667 | 84.02% | 22.5% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-06-12 | 2025 | 2024 | 2024-06-01 | 30 | 13.4667 | 7.6567 | 1.825 | 7.2917 | 0.60333 | 36.375 | 49.8667 | 5.31 | 8.96 | 100% |  |  | 100% |  |  | 82.73% | 83.23% | 25.13% | 2039232 | 2025477 | 4100 | 2021377 | 335.0909 | 6.4267 | 1809456.6667 | 84.02% | 22.5% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-06-13 | 2025 | 2024 | 2024-06-01 | 30 | 13.3167 | 6.9383 | 1.685 | 6.65 | 0.55667 | 34.9917 | 47 | 6.6083 | 10.8683 | 100% |  |  | 100% |  |  | 83.43% | 83.14% | 23.12% | 1875734.5 | 1863200 | 4033 | 1859167 | 335.0909 | 6.4267 | 1809456.6667 | 84.02% | 22.5% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-06-14 | 2025 | 2024 | 2024-06-01 | 30 | 13.3333 | 7.6059 | 1.8587 | 7.2409 | 0.60769 | 34.9924 | 48.2 | 6.3684 | 11.0882 | 100% |  |  | 100% |  |  | 83.13% | 82.81% | 25.08% | 2035659.1 | 2021123 | 4200 | 2016923 | 335.0909 | 6.4267 | 1809456.6667 | 84.02% | 22.5% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-06-15 | 2025 | 2024 | 2024-06-01 | 30 | 13.3 | 7.7383 | 1.9033 | 7.3467 | 0.625 | 35.6033 | 50.7 | 4.8767 | 8.7817 | 99.97% |  |  | 100% |  |  | 82.32% | 82.82% | 25.2% | 2044925.8 | 2030677 | 4134 | 2026543 | 335.0909 | 6.4267 | 1809456.6667 | 84.02% | 22.5% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-06-16 | 2025 | 2024 | 2024-06-01 | 30 | 13.3 | 7.6778 | 1.8906 | 7.3034 | 0.61943 | 37.0111 | 52.1 | 4.9459 | 8.3733 | 100% |  |  | 100% |  |  | 82.47% | 83.42% | 25.1% | 2035815.2 | 2022390 | 4200 | 2018190 | 335.0909 | 6.4267 | 1809456.6667 | 84.02% | 22.5% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-06-17 | 2025 | 2024 | 2024-06-01 | 30 | 13.3833 | 7.6053 | 1.8777 | 7.1519 | 0.60723 | 37.5152 | 51.5667 | 5.8044 | 9.6312 | 100% |  |  | 100% |  |  | 83.83% | 84.43% | 24.98% | 2027039 | 2013334 | 4266 | 2009068 | 335.0909 | 6.4267 | 1809456.6667 | 84.02% | 22.5% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-06-18 | 2025 | 2024 | 2024-06-01 | 30 | 13.3333 | 7.6051 | 1.895 | 7.1747 | 0.6211 | 36.6769 | 49.2333 | 7.5721 | 11.5655 | 100% |  |  | 100% |  |  | 84.03% | 83.88% | 25.12% | 2039399.4 | 2024200 | 3934 | 2020266 | 335.0909 | 6.4267 | 1809456.6667 | 84.02% | 22.5% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-06-19 | 2025 | 2024 | 2024-06-01 | 30 | 13.35 | 7.3799 | 1.8704 | 7.0096 | 0.61445 | 35.5415 | 48.9667 | 7.3391 | 11.6175 | 100% |  |  | 100% |  |  | 84.14% | 83.8% | 24.58% | 1993896.2 | 1980334 | 3933 | 1976401 | 335.0909 | 6.4267 | 1809456.6667 | 84.02% | 22.5% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-06-20 | 2025 | 2024 | 2024-06-01 | 30 | 13.3333 | 7.2768 | 1.8613 | 6.9257 | 0.61881 | 35.6631 | 49.5 | 6.3265 | 10.88 | 100% |  |  | 100% |  |  | 84.81% | 84.66% | 24.47% | 1985261.6 | 1972200 | 4067 | 1968133 | 335.0909 | 6.4267 | 1809456.6667 | 84.02% | 22.5% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-06-21 | 2025 | 2024 | 2024-06-01 | 30 | 13.2833 | 6.7999 | 1.7436 | 6.5183 | 0.57518 | 35.9532 | 50.4333 | 3.7393 | 8.784 | 100% |  |  | 100% |  |  | 84.42% | 85% | 22.93% | 1859979.6 | 1848000 | 4133 | 1843867 | 335.0909 | 6.4267 | 1809456.6667 | 84.02% | 22.5% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-06-22 | 2025 | 2024 | 2024-06-01 | 30 | 13.3333 | 4.3972 | 0.97991 | 4.2028 | 0.29962 | 31.2183 | 39.4333 | 3.8644 | 15.3845 | 99.93% |  |  | 100% |  |  | 85.76% | 84.66% | 15.02% | 1219184.6 | 1211933 | 4200 | 1207733 | 335.0909 | 6.4267 | 1809456.6667 | 84.02% | 22.5% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-06-23 | 2025 | 2024 | 2024-06-01 | 30 | 13.2833 | 7.125 | 1.7017 | 6.8117 | 0.56 | 36.8683 | 48.4667 | 2.7133 | 6.5617 | 99.98% |  |  | 100% |  |  | 83.43% | 84.67% | 23.68% | 1921099 | 1908309 | 4100 | 1904209 | 335.0909 | 6.4267 | 1809456.6667 | 84.02% | 22.5% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-06-24 | 2025 | 2024 | 2024-06-01 | 30 | 13.3 | 5.9028 | 1.4186 | 5.6163 | 0.48698 | 39.2764 | 50.5667 | 2.1399 | 6.7198 | 99.99% |  |  | 100% |  |  | 82.18% | 83.28% | 19.23% | 1558465.3 | 1550825 | 4167 | 1546658 | 335.0909 | 6.4267 | 1809456.6667 | 84.02% | 22.5% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-06-25 | 2025 | 2024 | 2024-06-01 | 30 | 13.5333 | 6.1906 | 1.489 | 5.9696 | 0.48616 | 36.9112 | 49.4333 | 3.9117 | 16.352 | 100% |  |  | 100% |  |  | 82.49% | 83.71% | 20.52% | 1663576.9 | 1654133 | 4066 | 1650067 | 335.0909 | 6.4267 | 1809456.6667 | 84.02% | 22.5% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-06-26 | 2025 | 2024 | 2024-06-01 | 30 | 13.2833 | 5.1615 | 1.1974 | 4.9982 | 0.40978 | 36.1556 | 46.0333 | 2.6535 | 8.097 | 100% |  |  | 100% |  |  | 85.09% | 84.84% | 17.72% | 1435590.9 | 1429334 | 4200 | 1425134 | 335.0909 | 6.4267 | 1809456.6667 | 84.02% | 22.5% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-06-27 | 2025 | 2024 | 2024-06-01 | 30 | 13.0833 | 6.5767 | 1.5805 | 6.3235 | 0.54816 | 34.359 | 47.599 | 3.9485 | 13.4357 | 100% |  |  | 100% |  |  | 82.52% | 82.81% | 21.74% | 1763715.1 | 1752667 | 4067 | 1748600 | 335.0909 | 6.4267 | 1809456.6667 | 84.02% | 22.5% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-06-28 | 2025 | 2024 | 2024-06-01 | 30 | 13.2333 | 4.0909 | 0.94689 | 3.9973 | 0.31028 | 31.0065 | 43.9 | 3.6304 | 9.0197 | 100% |  |  | 100% |  |  | 85.33% | 84.83% | 14.21% | 1154724.2 | 1147200 | 4267 | 1142933 | 335.0909 | 6.4267 | 1809456.6667 | 84.02% | 22.5% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-06-29 | 2025 | 2024 | 2024-06-01 | 30 | 13.0167 | 5.5165 | 1.1741 | 5.3243 | 0.37706 | 32.5225 | 44.8667 | 3.7742 | 7.2775 | 99.98% |  |  | 100% |  |  | 85.69% | 84.08% | 19.01% | 1541827.8 | 1533333 | 4466 | 1528867 | 335.0909 | 6.4267 | 1809456.6667 | 84.02% | 22.5% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-06-30 | 2025 | 2024 | 2024-06-01 | 30 | 13.3333 | 6.0318 | 1.3743 | 5.8006 | 0.44066 | 34.5067 | 47.9 | 3.686 | 6.6615 | 100% |  |  | 100% |  |  | 82.62% | 81.95% | 19.97% | 1617629 | 1608334 | 2467 | 1605867 | 335.0909 | 6.4267 | 1809456.6667 | 84.02% | 22.5% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-07-01 | 2025 | 2024 | 2024-07-01 | 31 | 13.3667 | 6.6393 | 1.5503 | 6.4167 | 0.48135 | 34.1562 | 48.4333 | 5.1507 | 8.5255 | 76.09% |  |  | 100% |  |  | 63.78% | 64.08% | 17.05% | 1398058.9 | 1371666 | 333 | 1371333 | 335.0909 | 5.4484 | 1552522.5806 | 85.04% | 19.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-07-02 | 2025 | 2024 | 2024-07-01 | 31 | 13.45 | 6.97 | 1.6502 | 6.6815 | 0.55122 | 34.5892 | 48.4933 | 5.0287 | 9.1233 | 100% |  |  | 100% |  |  | 81.95% | 83.55% | 22.81% | 1872310.6 | 1837134 | 2400 | 1834734 | 335.0909 | 5.4484 | 1552522.5806 | 85.04% | 19.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-07-03 | 2025 | 2024 | 2024-07-01 | 31 | 13.1667 | 7.335 | 1.7583 | 7.0217 | 0.57833 | 35.115 | 49.8 | 5.475 | 9.2917 | 94.89% |  |  | 100% |  |  | 79.01% | 79.81% | 23.12% | 1874187.8 | 1862600 | 3600 | 1859000 | 335.0909 | 5.4484 | 1552522.5806 | 85.04% | 19.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-07-04 | 2025 | 2024 | 2024-07-01 | 31 | 13.15 | 6.2751 | 1.5013 | 6.1228 | 0.46208 | 35.0746 | 48.2 | 4.9178 | 9.0612 | 100% |  |  | 100% |  |  | 83.83% | 84.56% | 21.39% | 1734907.9 | 1724401 | 4467 | 1719934 | 335.0909 | 5.4484 | 1552522.5806 | 85.04% | 19.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-07-05 | 2025 | 2024 | 2024-07-01 | 31 | 13.3333 | 6.585 | 1.595 | 6.3617 | 0.53833 | 36.0817 | 48.1667 | 5.91 | 9.7917 | 99.74% |  |  | 100% |  |  | 84.08% | 84.75% | 22.29% | 1805639.8 | 1795266 | 2867 | 1792399 | 335.0909 | 5.4484 | 1552522.5806 | 85.04% | 19.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-07-06 | 2025 | 2024 | 2024-07-01 | 31 | 13.35 | 6.7132 | 1.6504 | 6.6048 | 0.5433 | 35.2714 | 47 | 8.0946 | 12.3677 | 99.74% |  |  | 100% |  |  | 83.82% | 83.84% | 23.07% | 1871103.4 | 1858134 | 2933 | 1855201 | 335.0909 | 5.4484 | 1552522.5806 | 85.04% | 19.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-07-07 | 2025 | 2024 | 2024-07-01 | 31 | 13.1833 | 3.9317 | 0.96195 | 3.8667 | 0.32975 | 31.9989 | 42.1667 | 3.9958 | 8.6038 | 96.53% |  |  | 100% |  |  | 83.47% | 82.39% | 13.45% | 1089957.7 | 1085869 | 4333 | 1081536 | 335.0909 | 5.4484 | 1552522.5806 | 85.04% | 19.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-07-08 | 2025 | 2024 | 2024-07-01 | 31 | 12.7333 | 4.4903 | 1.0776 | 4.433 | 0.34478 | 32.6238 | 43.4933 | 2.8191 | 10.933 | 99.96% |  |  | 100% |  |  | 84.02% | 84.47% | 15.52% | 1259656.4 | 1252531 | 4400 | 1248131 | 335.0909 | 5.4484 | 1552522.5806 | 85.04% | 19.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-07-09 | 2025 | 2024 | 2024-07-01 | 31 | 13.2333 | 5.7009 | 1.1846 | 5.5854 | 0.3412 | 33.6972 | 45.4333 | 2.5348 | 8.4912 | 97.59% |  |  | 100% |  |  | 81.56% | 82.82% | 18.98% | 1539150.2 | 1530733 | 4267 | 1526466 | 335.0909 | 5.4484 | 1552522.5806 | 85.04% | 19.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-07-10 | 2025 | 2024 | 2024-07-01 | 31 | 13.4333 | 6.62 | 1.5583 | 6.425 | 0.46167 | 35.7367 | 50.5667 | 2.2867 | 7.715 | 100% |  |  | 100% |  |  | 82.36% | 83.95% | 22.05% | 1788209.8 | 1777466 | 4200 | 1773266 | 335.0909 | 5.4484 | 1552522.5806 | 85.04% | 19.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-07-11 | 2025 | 2024 | 2024-07-01 | 31 | 13.25 | 7.2479 | 1.7567 | 6.9642 | 0.55145 | 36.3851 | 49.6 | 5.6265 | 9.1556 | 100% |  |  | 100% |  |  | 82.93% | 84.14% | 24.06% | 1952190.3 | 1939470 | 4133 | 1935337 | 335.0909 | 5.4484 | 1552522.5806 | 85.04% | 19.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-07-12 | 2025 | 2024 | 2024-07-01 | 31 | 12.9833 | 6.3336 | 1.5715 | 6.1215 | 0.53175 | 34.4418 | 45.4667 | 8.5198 | 12.7781 | 100% |  |  | 100% |  |  | 83.15% | 82.49% | 21.21% | 1719120.2 | 1709600 | 4067 | 1705533 | 335.0909 | 5.4484 | 1552522.5806 | 85.04% | 19.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-07-13 | 2025 | 2024 | 2024-07-01 | 31 | 13.1667 | 5.8704 | 1.4702 | 5.709 | 0.48097 | 34.1608 | 46.3667 | 5.2653 | 8.4203 | 100% |  |  | 100% |  |  | 83.02% | 82.91% | 19.75% | 1601058.6 | 1592398 | 4267 | 1588131 | 335.0909 | 5.4484 | 1552522.5806 | 85.04% | 19.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-07-14 | 2025 | 2024 | 2024-07-01 | 31 | 13.0667 | 6.6904 | 1.677 | 6.4849 | 0.54209 | 35.5827 | 50.8 | 3.7699 | 7.8475 | 100% |  |  | 100% |  |  | 82.93% | 84.24% | 22.41% | 1816860.3 | 1806334 | 4333 | 1802001 | 335.0909 | 5.4484 | 1552522.5806 | 85.04% | 19.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-07-15 | 2025 | 2024 | 2024-07-01 | 31 | 13.1667 | 6.3219 | 1.5072 | 6.1447 | 0.49095 | 35.7031 | 47.1667 | 3.8812 | 8.7656 | 99.99% |  |  | 100% |  |  | 81.48% | 79.82% | 20.86% | 1691771.4 | 1682067 | 4400 | 1677667 | 335.0909 | 5.4484 | 1552522.5806 | 85.04% | 19.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-07-16 | 2025 | 2024 | 2024-07-01 | 31 | 13.3333 | 6.4637 | 1.5853 | 6.2838 | 0.50424 | 37.393 | 48.2141 | 4.1474 | 10.2125 | 99.99% |  |  | 100% |  |  | 82.39% | 83.83% | 21.57% | 1748941.7 | 1739071 | 4267 | 1734804 | 335.0909 | 5.4484 | 1552522.5806 | 85.04% | 19.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-07-17 | 2025 | 2024 | 2024-07-01 | 31 | 12.0167 | 5.6514 | 1.3841 | 5.5281 | 0.43303 | 35.6858 | 47.0491 | 4.7271 | 11.4907 | 100% |  |  | 100% |  |  | 83.17% | 81.32% | 19.16% | 1553386 | 1545062 | 4333 | 1540729 | 335.0909 | 5.4484 | 1552522.5806 | 85.04% | 19.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-07-18 | 2025 | 2024 | 2024-07-01 | 31 | 12.85 | 6.7747 | 1.4873 | 6.5731 | 0.44835 | 34.6365 | 48.4 | 3.4875 | 10.7527 | 99.99% |  |  | 100% |  |  | 82.34% | 83.67% | 22.55% | 1829035.2 | 1817867 | 4333 | 1813534 | 335.0909 | 5.4484 | 1552522.5806 | 85.04% | 19.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-07-19 | 2025 | 2024 | 2024-07-01 | 31 | 13.1167 | 7.135 | 1.6917 | 6.9604 | 0.47667 | 34.1033 | 48 | 3.2917 | 8.5517 | 99.99% |  |  | 100% |  |  | 81.83% | 83.28% | 23.73% | 1925329 | 1913067 | 4467 | 1908600 | 335.0909 | 5.4484 | 1552522.5806 | 85.04% | 19.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-07-20 | 2025 | 2024 | 2024-07-01 | 31 | 12.1 | 5.3435 | 1.2709 | 5.212 | 0.40035 | 33.9085 | 46.3 | 3.5294 | 16.2052 | 100% |  |  | 100% |  |  | 83.91% | 84.81% | 18.22% | 1478243.3 | 1469800 | 4400 | 1465400 | 335.0909 | 5.4484 | 1552522.5806 | 85.04% | 19.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-07-21 | 2025 | 2024 | 2024-07-01 | 31 | 12.5833 | 6.73 | 1.4883 | 6.5853 | 0.43333 | 35.6433 | 49.9333 | 2.515 | 7.985 | 100% |  |  | 100% |  |  | 82.43% | 84.29% | 22.62% | 1833830.8 | 1823204 | 4267 | 1818937 | 335.0909 | 5.4484 | 1552522.5806 | 85.04% | 19.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-07-22 | 2025 | 2024 | 2024-07-01 | 31 | 12.3833 | 5.4003 | 1.2862 | 5.2833 | 0.35782 | 34.1518 | 46.7333 | 3.9906 | 9.7031 | 100% |  |  | 100% |  |  | 82.31% | 84.13% | 18.12% | 1472125.8 | 1461796 | 4533 | 1457263 | 335.0909 | 5.4484 | 1552522.5806 | 85.04% | 19.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-07-23 | 2025 | 2024 | 2024-07-01 | 31 | 13.15 | 6.9191 | 1.4506 | 6.7301 | 0.45047 | 32.8709 | 47.6667 | 3.786 | 6.6633 | 100% |  |  | 100% |  |  | 82.47% | 82.76% | 23.13% | 1875690.2 | 1864204 | 4267 | 1859937 | 335.0909 | 5.4484 | 1552522.5806 | 85.04% | 19.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-07-24 | 2025 | 2024 | 2024-07-01 | 31 | 12.9167 | 7.0211 | 1.627 | 6.8661 | 0.46612 | 34.1036 | 49.5333 | 4.0877 | 7.5358 | 100% |  |  | 100% |  |  | 82.07% | 83.13% | 23.48% | 1905020.2 | 1892596 | 4466 | 1888130 | 335.0909 | 5.4484 | 1552522.5806 | 85.04% | 19.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-07-25 | 2025 | 2024 | 2024-07-01 | 31 | 13 | 6.685 | 1.5783 | 6.58 | 0.46167 | 33.2483 | 47.5667 | 4.9017 | 8.4433 | 100% |  |  | 100% |  |  | 82.58% | 82.96% | 22.64% | 1837445.6 | 1825201 | 4400 | 1820801 | 335.0909 | 5.4484 | 1552522.5806 | 85.04% | 19.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-07-26 | 2025 | 2024 | 2024-07-01 | 31 | 12.9167 | 5.5483 | 1.3017 | 5.4533 | 0.40167 | 33.12 | 45.2 | 4.83 | 7.8583 | 100% |  |  | 100% |  |  | 85.06% | 84.86% | 19.33% | 1567193.2 | 1558866 | 4467 | 1554399 | 335.0909 | 5.4484 | 1552522.5806 | 85.04% | 19.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-07-27 | 2025 | 2024 | 2024-07-01 | 31 | 12.3167 | 6.6117 | 1.5883 | 6.56 | 0.44333 | 33.81 | 47.9333 | 5.6817 | 9.1517 | 100% |  |  | 100% |  |  | 83.13% | 83.65% | 22.72% | 1844654.9 | 1832067 | 4600 | 1827467 | 335.0909 | 5.4484 | 1552522.5806 | 85.04% | 19.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-07-28 | 2025 | 2024 | 2024-07-01 | 31 | 12.7333 | 5.4783 | 1.2917 | 5.4233 | 0.38167 | 33.765 | 47.5333 | 3.15 | 8.8367 | 100% |  |  | 100% |  |  | 83.04% | 84.11% | 18.77% | 1522829.9 | 1513600 | 4467 | 1509133 | 335.0909 | 5.4484 | 1552522.5806 | 85.04% | 19.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-07-29 | 2025 | 2024 | 2024-07-01 | 31 | 12.3333 | 5.7696 | 1.3244 | 5.6556 | 0.43183 | 35.0141 | 45.7338 | 4.1237 | 13.1933 | 100% |  |  | 100% |  |  | 82.14% | 82.58% | 19.36% | 1569774.8 | 1561267 | 4533 | 1556734 | 335.0909 | 5.4484 | 1552522.5806 | 85.04% | 19.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-07-30 | 2025 | 2024 | 2024-07-01 | 31 | 12.9 | 5.4868 | 1.2719 | 5.3908 | 0.39665 | 33.4757 | 43.9345 | 4.499 | 13.7017 | 100% |  |  | 100% |  |  | 81.65% | 81.89% | 18.34% | 1487330.7 | 1479400 | 4467 | 1474933 | 335.0909 | 5.4484 | 1552522.5806 | 85.04% | 19.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-07-31 | 2025 | 2024 | 2024-07-01 | 31 | 12.8333 | 6.525 | 1.52 | 6.39 | 0.47833 | 32.345 | 47.8333 | 4.435 | 8.2067 | 100% |  |  | 100% |  |  | 80.87% | 80.72% | 21.53% | 1745376 | 1735334 | 3733 | 1731601 | 335.0909 | 5.4484 | 1552522.5806 | 85.04% | 19.3% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-08-01 | 2025 | 2024 | 2024-08-01 | 31 | 12.3833 | 3.4333 | 0.79167 | 3.3783 | 0.24 | 30.41 | 38.2333 | 6.42 | 10.4133 | 100% |  |  | 100% |  |  | 92.19% | 89.15% | 12.98% | 1050643.1 | 1047266 | 3667 | 1043599 | 335.0909 | 5.6194 | 1580574.1935 | 83.94% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-08-02 | 2025 | 2024 | 2024-08-01 | 31 | 12.4167 | 1.4183 | 0.24167 | 1.38 | 0.026667 | 28.665 | 31.64 | 5.1533 | 7.545 | 99.69% |  |  | 100% |  |  | 94.21% | 89.59% | 5.417% | 442550.7 | 439667 | 4000 | 435667 | 335.0909 | 5.6194 | 1580574.1935 | 83.94% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-08-03 | 2025 | 2024 | 2024-08-01 | 31 | 12.2333 | 1.7467 | 0.21833 | 1.665 | 0.035 | 26.5933 | 29.6633 | 3.9467 | 7.9067 | 99.96% |  |  | 100% |  |  | 93.07% | 87.83% | 6.457% | 526828 | 523896 | 4633 | 519263 | 335.0909 | 5.6194 | 1580574.1935 | 83.94% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-08-04 | 2025 | 2024 | 2024-08-01 | 31 | 12.65 | 4.955 | 0.815 | 4.865 | 0.255 | 29.265 | 39.78 | 4.015 | 7.3433 | 100% |  |  | 100% |  |  | 85.15% | 84.06% | 17.26% | 1400402.8 | 1392504 | 4433 | 1388071 | 335.0909 | 5.6194 | 1580574.1935 | 83.94% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-08-05 | 2025 | 2024 | 2024-08-01 | 31 | 9.0667 | 1.15 | 0.16167 | 1.095 | 0.028333 | 26.4033 | 29.9733 | 5.84 | 9.07 | 97.64% |  |  | 100% |  |  | 90.66% | 85.44% | 4.137% | 340837.7 | 338000 | 5334 | 332666 | 335.0909 | 5.6194 | 1580574.1935 | 83.94% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-08-06 | 2025 | 2024 | 2024-08-01 | 31 | 12.3333 | 0.92837 | 0.016365 | 0.87122 | 0 | 25.4488 | 26.0203 | 5.5106 | 9.9789 | 97.67% |  |  | 100% |  |  | 88.7% | 82.75% | 3.22% | 266528.1 | 263334 | 4400 | 258934 | 335.0909 | 5.6194 | 1580574.1935 | 83.94% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-08-07 | 2025 | 2024 | 2024-08-01 | 31 | 12.5167 | 2.88 | 0.43333 | 2.8267 | 0.11333 | 28.7133 | 34.2 | 6.3533 | 9.57 | 99.4% |  |  | 100% |  |  | 90.21% | 86.32% | 10.62% | 860840.4 | 858862 | 4400 | 854462 | 335.0909 | 5.6194 | 1580574.1935 | 83.94% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-08-08 | 2025 | 2024 | 2024-08-01 | 31 | 12.8 | 5.4883 | 1.0083 | 5.42 | 0.305 | 29.6383 | 41.02 | 5.165 | 8.0533 | 99.84% |  |  | 100% |  |  | 84.14% | 83.69% | 19% | 1540321.6 | 1532340 | 4266 | 1528074 | 335.0909 | 5.6194 | 1580574.1935 | 83.94% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-08-09 | 2025 | 2024 | 2024-08-01 | 31 | 12.6167 | 6.2704 | 1.2355 | 6.197 | 0.36824 | 32.2506 | 44.7505 | 4.513 | 7.2481 | 99.93% |  |  | 100% |  |  | 83.63% | 83.75% | 21.59% | 1751010.5 | 1740998 | 4467 | 1736531 | 335.0909 | 5.6194 | 1580574.1935 | 83.94% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-08-10 | 2025 | 2024 | 2024-08-01 | 31 | 12.2 | 5.358 | 1.1 | 5.342 | 0.326 | 31.318 | 41.4667 | 6.362 | 9.65 | 100% |  |  | 100% |  |  | 84.41% | 86.14% | 18.79% | 1523516 | 1515562 | 4500 | 1511062 | 335.0909 | 5.6194 | 1580574.1935 | 83.94% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-08-11 | 2025 | 2024 | 2024-08-01 | 31 | 12.6167 | 5.5794 | 1.2511 | 5.5353 | 0.3696 | 31.226 | 41.9667 | 6.8686 | 10.4683 | 99.33% |  |  | 100% |  |  | 63.83% | 85.17% | 14.72% | 1191653.8 | 1188238 | 4367 | 1183871 | 335.0909 | 5.6194 | 1580574.1935 | 83.94% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-08-12 | 2025 | 2024 | 2024-08-01 | 31 | 12.7333 | 5.9385 | 1.353 | 5.9252 | 0.38514 | 32.7143 | 44.6333 | 3.8188 | 7.1303 | 99.35% |  |  | 100% |  |  | 81.66% | 81.82% | 20.16% | 1634387.4 | 1625734 | 4400 | 1621334 | 335.0909 | 5.6194 | 1580574.1935 | 83.94% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-08-13 | 2025 | 2024 | 2024-08-01 | 31 | 12 | 5.7033 | 1.3133 | 5.6983 | 0.365 | 34.03 | 46.7667 | 3.8367 | 8.29 | 100% |  |  | 100% |  |  | 83.49% | 84.37% | 19.82% | 1607983.6 | 1598800 | 4666 | 1594134 | 335.0909 | 5.6194 | 1580574.1935 | 83.94% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-08-14 | 2025 | 2024 | 2024-08-01 | 31 | 12.1667 | 2.4067 | 0.32667 | 2.3417 | 0.08 | 29.7983 | 35 | 2.7233 | 5.9583 | 100% |  |  | 100% |  |  | 86.99% | 85.27% | 8.488% | 691530.3 | 687267 | 4667 | 682600 | 335.0909 | 5.6194 | 1580574.1935 | 83.94% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-08-15 | 2025 | 2024 | 2024-08-01 | 31 | 12.2 | 3.4211 | 0.53251 | 3.4257 | 0.12622 | 29.8826 | 37.144 | 3.8788 | 6.4111 | 99.95% |  |  | 100% |  |  | 87.64% | 88.67% | 12.51% | 1014754.8 | 1010600 | 4600 | 1006000 | 335.0909 | 5.6194 | 1580574.1935 | 83.94% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-08-16 | 2025 | 2024 | 2024-08-01 | 31 | 11.5833 | 1.7757 | 0.18194 | 1.6791 | 0.027555 | 26.8785 | 29.3765 | 3.9971 | 6.9896 | 94.82% |  |  | 100% |  |  | 91.09% | 86.57% | 6.373% | 518815.85 | 517400 | 4867 | 512533 | 335.0909 | 5.6194 | 1580574.1935 | 83.94% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-08-17 | 2025 | 2024 | 2024-08-01 | 31 | 12.25 | 2.9365 | 0.40963 | 2.8745 | 0.10885 | 27.0209 | 32.1666 | 5.4649 | 9.455 | 98.74% |  |  | 100% |  |  | 87.82% | 84.51% | 10.52% | 853368.4 | 850471 | 4600 | 845871 | 335.0909 | 5.6194 | 1580574.1935 | 83.94% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-08-18 | 2025 | 2024 | 2024-08-01 | 31 | 12.0333 | 5.4072 | 0.91358 | 5.4524 | 0.24976 | 30.4915 | 41.4 | 4.4248 | 8.1053 | 100% |  |  | 100% |  |  | 82.9% | 82.22% | 18.83% | 1528024.5 | 1519329 | 4733 | 1514596 | 335.0909 | 5.6194 | 1580574.1935 | 83.94% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-08-19 | 2025 | 2024 | 2024-08-01 | 31 | 12.3833 | 6.4213 | 1.2128 | 6.4859 | 0.3268 | 31.7094 | 45.4822 | 3.7116 | 7.2058 | 100% |  |  | 100% |  |  | 80.7% | 81.16% | 21.81% | 1768013.2 | 1756671 | 2867 | 1753804 | 335.0909 | 5.6194 | 1580574.1935 | 83.94% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-08-20 | 2025 | 2024 | 2024-08-01 | 31 | 12.4333 | 6.8998 | 1.4211 | 6.9586 | 0.36252 | 32.2483 | 45.2667 | 5.0467 | 8.2292 | 100% |  |  | 100% |  |  | 81.77% | 82.18% | 23.71% | 1921828.8 | 1908529 | 1800 | 1906729 | 335.0909 | 5.6194 | 1580574.1935 | 83.94% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-08-21 | 2025 | 2024 | 2024-08-01 | 31 | 12.55 | 7.0267 | 1.5117 | 7.1333 | 0.37667 | 32.9767 | 47.1333 | 4.0083 | 7.875 | 100% |  |  | 100% |  |  | 81.73% | 83.01% | 24.29% | 1970865 | 1957361 | 3833 | 1953528 | 335.0909 | 5.6194 | 1580574.1935 | 83.94% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-08-22 | 2025 | 2024 | 2024-08-01 | 31 | 12.3833 | 6.926 | 1.5075 | 7.03 | 0.3627 | 34.2445 | 48.8 | 3.0796 | 6.9875 | 100% |  |  | 100% |  |  | 80.93% | 82.69% | 23.71% | 1923657.3 | 1910839 | 4300 | 1906539 | 335.0909 | 5.6194 | 1580574.1935 | 83.94% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-08-23 | 2025 | 2024 | 2024-08-01 | 31 | 12.35 | 6.9765 | 1.5522 | 7.12 | 0.39084 | 34.3331 | 47.9333 | 4.1686 | 9.349 | 90.18% |  |  | 100% |  |  | 73.72% | 75.33% | 21.87% | 1775508.4 | 1763334 | 4533 | 1758801 | 335.0909 | 5.6194 | 1580574.1935 | 83.94% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-08-24 | 2025 | 2024 | 2024-08-01 | 31 | 12.25 | 3.5982 | 0.7231 | 3.6031 | 0.17025 | 29.0514 | 37.7045 | 2.7707 | 10.7506 | 100% |  |  | 100% |  |  | 85.02% | 84.67% | 12.76% | 1037194.6 | 1031000 | 4467 | 1026533 | 335.0909 | 5.6194 | 1580574.1935 | 83.94% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-08-25 | 2025 | 2024 | 2024-08-01 | 31 | 12.2667 | 4.5735 | 0.99122 | 4.6338 | 0.2637 | 32.1009 | 39.8245 | 3.4048 | 7.0053 | 100% |  |  | 100% |  |  | 83.69% | 83.74% | 16.16% | 1311481.7 | 1304200 | 4733 | 1299467 | 335.0909 | 5.6194 | 1580574.1935 | 83.94% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-08-26 | 2025 | 2024 | 2024-08-01 | 31 | 12.1667 | 4.9233 | 1.06 | 5.0117 | 0.28667 | 31.7083 | 39.1067 | 6.0567 | 12.5917 | 100% |  |  | 100% |  |  | 82.43% | 86.06% | 17.21% | 1396199.3 | 1388934 | 4600 | 1384334 | 335.0909 | 5.6194 | 1580574.1935 | 83.94% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-08-27 | 2025 | 2024 | 2024-08-01 | 31 | 11.9667 | 2.5423 | 0.53226 | 2.4997 | 0.13556 | 27.9474 | 31.9333 | 8.1607 | 12.6356 | 100% |  |  | 100% |  |  | 93.74% | 85.45% | 9.764% | 792194.2 | 789800 | 4600 | 785200 | 335.0909 | 5.6194 | 1580574.1935 | 83.94% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-08-28 | 2025 | 2024 | 2024-08-01 | 31 | 12.3833 | 4.5467 | 0.895 | 4.5583 | 0.26 | 29.3183 | 38.57 | 5.9933 | 11.6883 | 100% |  |  | 100% |  |  | 44.03% | 85.06% | 8.363% | 679379 | 677133 | 4534 | 672599 | 335.0909 | 5.6194 | 1580574.1935 | 83.94% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-08-29 | 2025 | 2024 | 2024-08-01 | 31 | 12.2667 | 4.8671 | 1.0272 | 4.9263 | 0.268 | 29.9541 | 39.9 | 5.7977 | 9.1222 | 100% |  |  | 100% |  |  | 80.32% | 83.48% | 16.49% | 1336627.5 | 1330200 | 4333 | 1325867 | 335.0909 | 5.6194 | 1580574.1935 | 83.94% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-08-30 | 2025 | 2024 | 2024-08-01 | 31 | 12.4167 | 5.345 | 1.1583 | 5.4867 | 0.31 | 29.8133 | 41.8367 | 4.775 | 8.9283 | 100% |  |  | 100% |  |  | 81.73% | 81.43% | 18.68% | 1519707 | 1513460 | 10900 | 1502560 | 335.0909 | 5.6194 | 1580574.1935 | 83.94% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-08-31 | 2025 | 2024 | 2024-08-01 | 31 | 12.4333 | 4.6733 | 0.985 | 4.7817 | 0.27833 | 29.2717 | 43.1967 | 1.915 | 9.305 | 100% |  |  | 100% |  |  | 80.45% | 80.23% | 16.03% | 1335908 | 1289000 | 0 | 1289000 | 335.0909 | 5.6194 | 1580574.1935 | 83.94% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-09-01 | 2025 | 2024 | 2024-09-01 | 30 | 12.4167 | 4.5067 | 0.8 | 4.6367 | 0.17333 | 29.46 | 39 | 2.93 | 7.5317 | 100% |  |  | 100% |  |  | 85.23% | 81.17% | 16.47% | 1294204 | 1325740 | 1500 | 1324240 | 335.0909 | 6.4033 | 1777556.6667 | 82.84% | 22.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-09-02 | 2025 | 2024 | 2024-09-01 | 30 | 12.1 | 5.1883 | 0.98667 | 5.3783 | 0.26333 | 31.4183 | 44.5667 | 1.585 | 6.0217 | 100% |  |  | 100% |  |  | 85.15% | 83.51% | 19.08% | 1547133.5 | 1539400 | 4733 | 1534667 | 335.0909 | 6.4033 | 1777556.6667 | 82.84% | 22.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-09-03 | 2025 | 2024 | 2024-09-01 | 30 | 10.0167 | 4.4833 | 0.88667 | 4.6667 | 0.22167 | 30.7133 | 45.6967 | 2.165 | 10.7067 | 100% |  |  | 100% |  |  | 82.89% | 83.27% | 16.12% | 1310519.4 | 1301201 | 5000 | 1296201 | 335.0909 | 6.4033 | 1777556.6667 | 82.84% | 22.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-09-04 | 2025 | 2024 | 2024-09-01 | 30 | 11.1667 | 3.2671 | 0.494 | 3.2515 | 0.11916 | 27.6477 | 36.7128 | 1.6668 | 3.9033 | 99.97% |  |  | 100% |  |  | 90.16% | 86.69% | 12.22% | 990639.6 | 987129 | 4734 | 982395 | 335.0909 | 6.4033 | 1777556.6667 | 82.84% | 22.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-09-05 | 2025 | 2024 | 2024-09-01 | 30 | 12.2167 | 5.1833 | 0.89833 | 5.4067 | 0.21333 | 30.5 | 45.3667 | 1.9267 | 4.5633 | 100% |  |  | 100% |  |  | 75.28% | 84.33% | 16.96% | 1375744 | 1368430 | 4633 | 1363797 | 335.0909 | 6.4033 | 1777556.6667 | 82.84% | 22.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-09-06 | 2025 | 2024 | 2024-09-01 | 30 | 11.8667 | 6.2568 | 1.2018 | 6.5801 | 0.26481 | 31.4182 | 47.5333 | 3.0421 | 5.5767 | 100% |  |  | 100% |  |  | 81.05% | 81.83% | 22.22% | 1804676.7 | 1791908 | 4700 | 1787208 | 335.0909 | 6.4033 | 1777556.6667 | 82.84% | 22.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-09-07 | 2025 | 2024 | 2024-09-01 | 30 | 12.1167 | 6.62 | 1.227 | 6.9736 | 0.29679 | 31.6408 | 47.4395 | 2.6802 | 5.6764 | 99.97% |  |  | 100% |  |  | 81.76% | 82.49% | 23.76% | 1928194.5 | 1915133 | 4667 | 1910466 | 335.0909 | 6.4033 | 1777556.6667 | 82.84% | 22.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-09-08 | 2025 | 2024 | 2024-09-01 | 30 | 12.05 | 6.3199 | 1.25 | 6.7105 | 0.2919 | 32.619 | 46.727 | 2.5725 | 5.4419 | 99.44% |  |  | 100% |  |  | 68.29% | 81.63% | 19.1% | 1547678.8 | 1540200 | 4533 | 1535667 | 335.0909 | 6.4033 | 1777556.6667 | 82.84% | 22.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-09-09 | 2025 | 2024 | 2024-09-01 | 30 | 11.9667 | 6.5398 | 1.3169 | 6.9615 | 0.30512 | 33.3897 | 48.2 | 2.2207 | 5.4239 | 100% |  |  | 100% |  |  | 81.18% | 82.64% | 23.55% | 1911070.7 | 1898400 | 4667 | 1893733 | 335.0909 | 6.4033 | 1777556.6667 | 82.84% | 22.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-09-10 | 2025 | 2024 | 2024-09-01 | 30 | 11.9833 | 6.2083 | 1.2467 | 6.6383 | 0.29167 | 33.02 | 48.9333 | 1.9567 | 5.2417 | 100% |  |  | 100% |  |  | 80.44% | 81.72% | 22.25% | 1806087 | 1793959 | 4633 | 1789326 | 335.0909 | 6.4033 | 1777556.6667 | 82.84% | 22.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-09-11 | 2025 | 2024 | 2024-09-01 | 30 | 11.9 | 5.5617 | 1.1233 | 5.9183 | 0.26667 | 31.53 | 43.1367 | 3.12 | 9.4367 | 99.99% |  |  | 100% |  |  | 80.55% | 84.03% | 19.86% | 1612614.9 | 1601975 | 4500 | 1597475 | 335.0909 | 6.4033 | 1777556.6667 | 82.84% | 22.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-09-12 | 2025 | 2024 | 2024-09-01 | 30 | 12.0667 | 6.2216 | 1.2235 | 6.6533 | 0.27936 | 32.7782 | 45.2 | 5.1352 | 7.7214 | 100% |  |  | 100% |  |  | 82.71% | 83.13% | 22.93% | 1861076.7 | 1848467 | 4467 | 1844000 | 335.0909 | 6.4033 | 1777556.6667 | 82.84% | 22.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-09-13 | 2025 | 2024 | 2024-09-01 | 30 | 11.9667 | 6.1367 | 1.2183 | 6.5283 | 0.31833 | 30.5883 | 42.5 | 7.2783 | 10.9217 | 100% |  |  | 100% |  |  | 77.62% | 83.07% | 21.11% | 1712814.3 | 1701867 | 3933 | 1697934 | 335.0909 | 6.4033 | 1777556.6667 | 82.84% | 22.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-09-14 | 2025 | 2024 | 2024-09-01 | 30 | 11.85 | 6.0367 | 1.285 | 6.4383 | 0.31833 | 30.005 | 42.0633 | 6.3417 | 10.4883 | 100% |  |  | 100% |  |  | 77.93% | 81.67% | 20.9% | 1698923 | 1685691 | 4500 | 1681191 | 335.0909 | 6.4033 | 1777556.6667 | 82.84% | 22.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-09-15 | 2025 | 2024 | 2024-09-01 | 30 | 11.95 | 6.1267 | 1.31 | 6.5467 | 0.32667 | 29.945 | 43.9667 | 3.935 | 7.0733 | 100% |  |  | 100% |  |  | 77.36% | 83.92% | 21.1% | 1722457.6 | 1701042 | 3967 | 1697075 | 335.0909 | 6.4033 | 1777556.6667 | 82.84% | 22.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-09-16 | 2025 | 2024 | 2024-09-01 | 30 | 11.8833 | 6.3983 | 1.3767 | 6.905 | 0.31833 | 30.0217 | 44.7167 | 3.72 | 7.0783 | 99.29% |  |  | 100% |  |  | 76.94% | 79.35% | 22.13% | 1796455 | 1784358 | 4233 | 1780125 | 335.0909 | 6.4033 | 1777556.6667 | 82.84% | 22.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-09-17 | 2025 | 2024 | 2024-09-01 | 30 | 11.9167 | 6.515 | 1.3967 | 7.065 | 0.30667 | 31.3417 | 46.6033 | 2.7867 | 6.99 | 99.34% |  |  | 100% |  |  | 76.22% | 82.63% | 22.44% | 1822966.3 | 1808200 | 3767 | 1804433 | 335.0909 | 6.4033 | 1777556.6667 | 82.84% | 22.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-09-18 | 2025 | 2024 | 2024-09-01 | 30 | 11.85 | 6.1261 | 1.2837 | 6.6622 | 0.28865 | 32.2645 | 46.5333 | 1.4641 | 4.3992 | 100% |  |  | 100% |  |  | 82.06% | 83.2% | 22.78% | 1848776.5 | 1836709 | 4866 | 1831843 | 335.0909 | 6.4033 | 1777556.6667 | 82.84% | 22.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-09-19 | 2025 | 2024 | 2024-09-01 | 30 | 11.7 | 5.9433 | 1.2767 | 6.4583 | 0.29167 | 32.195 | 43.59 | 4.3717 | 7.4467 | 100% |  |  | 100% |  |  | 76.7% | 82.9% | 20.64% | 1676268.3 | 1664591 | 4667 | 1659924 | 335.0909 | 6.4033 | 1777556.6667 | 82.84% | 22.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-09-20 | 2025 | 2024 | 2024-09-01 | 30 | 11.7333 | 5.5457 | 1.1694 | 5.9819 | 0.25846 | 32.5867 | 46.2746 | 1.5038 | 4.4508 | 100% |  |  | 100% |  |  | 58.65% | 84.36% | 14.62% | 1184536.4 | 1177809 | 2200 | 1175609 | 335.0909 | 6.4033 | 1777556.6667 | 82.84% | 22.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-09-21 | 2025 | 2024 | 2024-09-01 | 30 | 11.8 | 5.2184 | 1.1108 | 5.6612 | 0.23988 | 33.3567 | 47.1 | 2.0986 | 5.0631 | 100% |  |  | 100% |  |  | 81.42% | 82.83% | 19.21% | 1557515.9 | 1546667 | 2067 | 1544600 | 335.0909 | 6.4033 | 1777556.6667 | 82.84% | 22.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-09-22 | 2025 | 2024 | 2024-09-01 | 30 | 11.6833 | 5.9933 | 1.2717 | 6.5617 | 0.26 | 33.7817 | 49.5667 | 1.9333 | 5.0217 | 100% |  |  | 100% |  |  | 81.82% | 83.32% | 22.37% | 1815538.6 | 1803800 | 4800 | 1799000 | 335.0909 | 6.4033 | 1777556.6667 | 82.84% | 22.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-09-23 | 2025 | 2024 | 2024-09-01 | 30 | 11.7167 | 5.6917 | 1.1933 | 6.2483 | 0.25667 | 34.13 | 48.9933 | 1.9717 | 4.5533 | 99.99% |  |  | 100% |  |  | 80.52% | 81.9% | 20.96% | 1700788.8 | 1690624 | 4666 | 1685958 | 335.0909 | 6.4033 | 1777556.6667 | 82.84% | 22.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-09-24 | 2025 | 2024 | 2024-09-01 | 30 | 11.6833 | 5.8275 | 1.2273 | 6.4516 | 0.23443 | 34.5189 | 48.6 | 2.1609 | 5.4389 | 100% |  |  | 100% |  |  | 79.84% | 81.46% | 21.46% | 1742535.8 | 1730577 | 4534 | 1726043 | 335.0909 | 6.4033 | 1777556.6667 | 82.84% | 22.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-09-25 | 2025 | 2024 | 2024-09-01 | 30 | 11.65 | 5.8154 | 1.2188 | 6.3925 | 0.27787 | 34.5157 | 47.5846 | 2.3043 | 5.8219 | 100% |  |  | 100% |  |  | 81.79% | 83.3% | 21.79% | 1767599.1 | 1756400 | 4400 | 1752000 | 335.0909 | 6.4033 | 1777556.6667 | 82.84% | 22.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-09-26 | 2025 | 2024 | 2024-09-01 | 30 | 11.5667 | 5.8383 | 1.2633 | 6.4583 | 0.28667 | 35.1317 | 46.7667 | 3.4217 | 6.4867 | 100% |  |  | 100% |  |  | 81.83% | 83.02% | 22.02% | 1786697.3 | 1775333 | 4533 | 1770800 | 335.0909 | 6.4033 | 1777556.6667 | 82.84% | 22.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-09-27 | 2025 | 2024 | 2024-09-01 | 30 | 11.6667 | 5.4667 | 1.18 | 6.0383 | 0.26 | 33.825 | 49.3667 | 1.9967 | 6.905 | 100% |  |  | 100% |  |  | 80.96% | 82.18% | 20.37% | 1652345.5 | 1642934 | 4733 | 1638201 | 335.0909 | 6.4033 | 1777556.6667 | 82.84% | 22.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-09-28 | 2025 | 2024 | 2024-09-01 | 30 | 11.55 | 5.6793 | 1.2436 | 6.2799 | 0.2542 | 33.2144 | 49.4612 | 2.3557 | 5.4894 | 100% |  |  | 100% |  |  | 81.38% | 82.5% | 21.3% | 1727807.6 | 1717333 | 4734 | 1712599 | 335.0909 | 6.4033 | 1777556.6667 | 82.84% | 22.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-09-29 | 2025 | 2024 | 2024-09-01 | 30 | 11.65 | 5.9366 | 1.1429 | 6.6306 | 0.22439 | 31.9451 | 47.1717 | 1.5578 | 4.0669 | 99.99% |  |  | 100% |  |  | 82.23% | 83.3% | 22.72% | 1844652.6 | 1831800 | 4800 | 1827000 | 335.0909 | 6.4033 | 1777556.6667 | 82.84% | 22.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-09-30 | 2025 | 2024 | 2024-09-01 | 30 | 11.4667 | 5.6595 | 1.134 | 6.2851 | 0.24893 | 33.4601 | 46.9333 | 2.4514 | 5.5458 | 100% |  |  | 100% |  |  | 81.96% | 82.97% | 21.46% | 1742467.2 | 1730800 | 4666 | 1726134 | 335.0909 | 6.4033 | 1777556.6667 | 82.84% | 22.1% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-10-01 | 2025 | 2024 | 2024-10-01 | 31 | 11.55 | 5.8508 | 1.1999 | 6.5533 | 0.25472 | 33.8781 | 46.8972 | 4.2724 | 6.8933 | 99.99% |  |  | 100% |  |  | 82.2% | 83.76% | 22.45% | 1822541.7 | 1809801 | 4667 | 1805134 | 335.0909 | 6.5258 | 1804554.8387 | 82.52% | 22.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-10-02 | 2025 | 2024 | 2024-10-01 | 31 | 11.5833 | 6.0797 | 1.2689 | 6.8512 | 0.26617 | 34.0238 | 46.6333 | 4.8917 | 8.0406 | 100% |  |  | 100% |  |  | 81.33% | 82.9% | 23.22% | 1884267.1 | 1872000 | 4800 | 1867200 | 335.0909 | 6.5258 | 1804554.8387 | 82.52% | 22.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-10-03 | 2025 | 2024 | 2024-10-01 | 31 | 11.5833 | 6.1151 | 1.2829 | 6.9177 | 0.25848 | 32.5531 | 46.2603 | 5.4825 | 9.1492 | 100% |  |  | 100% |  |  | 81.24% | 82.43% | 23.42% | 1900645.3 | 1888067 | 4800 | 1883267 | 335.0909 | 6.5258 | 1804554.8387 | 82.52% | 22.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-10-04 | 2025 | 2024 | 2024-10-01 | 31 | 11.3667 | 5.835 | 1.2317 | 6.5883 | 0.255 | 30.9533 | 44.45 | 5.9733 | 9.5517 | 100% |  |  | 100% |  |  | 80.99% | 81.56% | 22.23% | 1805745.1 | 1792755 | 4733 | 1788022 | 335.0909 | 6.5258 | 1804554.8387 | 82.52% | 22.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-10-05 | 2025 | 2024 | 2024-10-01 | 31 | 11.4667 | 5.1238 | 1.0763 | 5.6946 | 0.23886 | 30.1817 | 43.3345 | 3.5043 | 6.4881 | 100% |  |  | 100% |  |  | 80.48% | 80.93% | 19.09% | 1550691.8 | 1540512 | 4867 | 1535645 | 335.0909 | 6.5258 | 1804554.8387 | 82.52% | 22.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-10-06 | 2025 | 2024 | 2024-10-01 | 31 | 11.4 | 5.365 | 1.1233 | 6.065 | 0.23833 | 31.645 | 46.29 | 1.495 | 4.9417 | 100% |  |  | 100% |  |  | 82.57% | 83.7% | 20.87% | 1692797 | 1682933 | 4867 | 1678066 | 335.0909 | 6.5258 | 1804554.8387 | 82.52% | 22.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-10-07 | 2025 | 2024 | 2024-10-01 | 31 | 11.4667 | 5.57 | 1.17 | 6.3317 | 0.245 | 33.09 | 47.1833 | 1.86 | 5.31 | 100% |  |  | 100% |  |  | 81.71% | 83.63% | 21.56% | 1749549.3 | 1738555 | 4866 | 1733689 | 335.0909 | 6.5258 | 1804554.8387 | 82.52% | 22.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-10-08 | 2025 | 2024 | 2024-10-01 | 31 | 11.3167 | 4.8683 | 1.0383 | 5.4717 | 0.215 | 32.9033 | 46.2733 | 2.4267 | 8.6217 | 100% |  |  | 100% |  |  | 83.55% | 85.14% | 19.05% | 1546507 | 1536600 | 4767 | 1531833 | 335.0909 | 6.5258 | 1804554.8387 | 82.52% | 22.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-10-09 | 2025 | 2024 | 2024-10-01 | 31 | 11.25 | 4.9481 | 1.0501 | 5.6195 | 0.22044 | 32.8567 | 45.5734 | 1.3695 | 4.0139 | 100% |  |  | 100% |  |  | 82.52% | 84.18% | 19.32% | 1568361.6 | 1558779 | 4900 | 1553879 | 335.0909 | 6.5258 | 1804554.8387 | 82.52% | 22.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-10-10 | 2025 | 2024 | 2024-10-01 | 31 | 11.35 | 5.57 | 1.1933 | 6.3967 | 0.25167 | 32.7517 | 46.0667 | 1.6133 | 5.4917 | 100% |  |  | 100% |  |  | 81.89% | 83.95% | 21.83% | 1771636.4 | 1760121 | 4733 | 1755388 | 335.0909 | 6.5258 | 1804554.8387 | 82.52% | 22.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-10-11 | 2025 | 2024 | 2024-10-01 | 31 | 11.45 | 5.9947 | 1.3105 | 6.9797 | 0.26534 | 32.7555 | 45.6667 | 2.2004 | 7.1967 | 100% |  |  | 100% |  |  | 80.49% | 82.73% | 23.41% | 1900329.5 | 1887346 | 4734 | 1882612 | 335.0909 | 6.5258 | 1804554.8387 | 82.52% | 22.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-10-12 | 2025 | 2024 | 2024-10-01 | 31 | 11.3667 | 5.6651 | 1.2307 | 6.5805 | 0.23653 | 32.3593 | 46.967 | 1.4152 | 4.8264 | 100% |  |  | 100% |  |  | 81.38% | 83.55% | 22.31% | 1811213.3 | 1799133 | 4733 | 1794400 | 335.0909 | 6.5258 | 1804554.8387 | 82.52% | 22.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-10-13 | 2025 | 2024 | 2024-10-01 | 31 | 11.0167 | 3.3433 | 0.68833 | 3.524 | 0.19 | 31.185 | 40.0267 | 0.99833 | 3.3683 | 100% |  |  | 100% |  |  | 88.21% | 86.98% | 12.95% | 1049785.6 | 1046400 | 4800 | 1041600 | 335.0909 | 6.5258 | 1804554.8387 | 82.52% | 22.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-10-14 | 2025 | 2024 | 2024-10-01 | 31 | 11.3833 | 3.3865 | 0.72847 | 3.6584 | 0.18401 | 30.545 | 37.9723 | 1.7022 | 5.6469 | 100% |  |  | 100% |  |  | 85.98% | 85.22% | 13.11% | 1065865 | 1059021 | 5000 | 1054021 | 335.0909 | 6.5258 | 1804554.8387 | 82.52% | 22.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-10-15 | 2025 | 2024 | 2024-10-01 | 31 | 11.3333 | 5.3389 | 1.1676 | 6.192 | 0.23845 | 32.3763 | 44.16 | 1.616 | 5.3142 | 100% |  |  | 100% |  |  | 82.08% | 84.21% | 21.18% | 1720381 | 1708000 | 5000 | 1703000 | 335.0909 | 6.5258 | 1804554.8387 | 82.52% | 22.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-10-16 | 2025 | 2024 | 2024-10-01 | 31 | 11.4333 | 5.5054 | 1.2289 | 6.3229 | 0.25775 | 33.4553 | 48.0281 | 1.738 | 5.6547 | 99.94% |  |  | 100% |  |  | 81.09% | 83.4% | 21.36% | 1736824.2 | 1723000 | 5000 | 1718000 | 335.0909 | 6.5258 | 1804554.8387 | 82.52% | 22.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-10-17 | 2025 | 2024 | 2024-10-01 | 31 | 11.4 | 4.9073 | 1.097 | 5.635 | 0.22566 | 33.3186 | 47.478 | 1.8597 | 5.3275 | 99.92% |  |  | 100% |  |  | 82.15% | 83.64% | 19.29% | 1561043.7 | 1555600 | 4333 | 1551267 | 335.0909 | 6.5258 | 1804554.8387 | 82.52% | 22.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-10-18 | 2025 | 2024 | 2024-10-01 | 31 | 11.2 | 4.6834 | 1.0463 | 5.4272 | 0.20394 | 33.1474 | 45.3 | 1.0712 | 4.4156 | 99.93% |  |  | 100% |  |  | 83.49% | 84.83% | 18.88% | 1532502 | 1523200 | 4767 | 1518433 | 335.0909 | 6.5258 | 1804554.8387 | 82.52% | 22.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-10-19 | 2025 | 2024 | 2024-10-01 | 31 | 11.1833 | 4.7828 | 1.0829 | 5.6077 | 0.20813 | 33.7995 | 46.4034 | 1.0107 | 4.6069 | 100% |  |  | 100% |  |  | 81.64% | 83.45% | 19.07% | 1547155.1 | 1538780 | 4767 | 1534013 | 335.0909 | 6.5258 | 1804554.8387 | 82.52% | 22.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-10-20 | 2025 | 2024 | 2024-10-01 | 31 | 11.2167 | 4.1386 | 0.93044 | 4.7457 | 0.19358 | 32.0129 | 40.8604 | 3.1604 | 8.5122 | 99.98% |  |  | 100% |  |  | 82.69% | 83.55% | 16.35% | 1327685.8 | 1319733 | 4800 | 1314933 | 335.0909 | 6.5258 | 1804554.8387 | 82.52% | 22.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-10-21 | 2025 | 2024 | 2024-10-01 | 31 | 10.95 | 4.4417 | 1.0583 | 5.1417 | 0.21833 | 30.1 | 41.7467 | 3.18 | 12.505 | 100% |  |  | 100% |  |  | 83.46% | 84.13% | 17.88% | 1451259.5 | 1443000 | 5000 | 1438000 | 335.0909 | 6.5258 | 1804554.8387 | 82.52% | 22.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-10-22 | 2025 | 2024 | 2024-10-01 | 31 | 11.0667 | 5.0215 | 1.148 | 5.9361 | 0.23085 | 31.0978 | 43.9304 | 1.3973 | 5.2719 | 100% |  |  | 100% |  |  | 82.98% | 84.3% | 20.53% | 1666040.9 | 1655601 | 4933 | 1650668 | 335.0909 | 6.5258 | 1804554.8387 | 82.52% | 22.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-10-23 | 2025 | 2024 | 2024-10-01 | 31 | 11.0667 | 5.1434 | 1.1793 | 6.0919 | 0.23678 | 32.3046 | 44.4687 | 1.5385 | 5.1506 | 100% |  |  | 100% |  |  | 82.66% | 84.4% | 20.98% | 1701580.2 | 1690866 | 3533 | 1687333 | 335.0909 | 6.5258 | 1804554.8387 | 82.52% | 22.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-10-24 | 2025 | 2024 | 2024-10-01 | 31 | 11.1667 | 5.1778 | 1.1992 | 6.1845 | 0.2446 | 32.6182 | 43.9799 | 2.017 | 6.2203 | 99.89% |  |  | 100% |  |  | 82.78% | 84.5% | 21.33% | 1728412.1 | 1717401 | 1934 | 1715467 | 335.0909 | 6.5258 | 1804554.8387 | 82.52% | 22.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-10-25 | 2025 | 2024 | 2024-10-01 | 31 | 11.15 | 5.1127 | 1.1815 | 6.0731 | 0.24006 | 33.0747 | 45.2667 | 1.4952 | 4.9756 | 100% |  |  | 100% |  |  | 82.47% | 84.53% | 20.87% | 1693949.1 | 1683133 | 4933 | 1678200 | 335.0909 | 6.5258 | 1804554.8387 | 82.52% | 22.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-10-26 | 2025 | 2024 | 2024-10-01 | 31 | 11.0333 | 5.1817 | 1.2133 | 6.2267 | 0.24 | 34.3967 | 46.7967 | 1.8633 | 5.2733 | 100% |  |  | 100% |  |  | 81.83% | 84.3% | 21.23% | 1723210.6 | 1712486 | 5067 | 1707419 | 335.0909 | 6.5258 | 1804554.8387 | 82.52% | 22.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-10-27 | 2025 | 2024 | 2024-10-01 | 31 | 11.0333 | 5.0583 | 1.19 | 6.0833 | 0.23833 | 35.3333 | 46.4333 | 2.935 | 5.9 | 100% |  |  | 100% |  |  | 82.03% | 84.3% | 20.79% | 1687064.1 | 1677048 | 4933 | 1672115 | 335.0909 | 6.5258 | 1804554.8387 | 82.52% | 22.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-10-28 | 2025 | 2024 | 2024-10-01 | 31 | 11.0167 | 5.2032 | 1.2226 | 6.3093 | 0.2274 | 35.3687 | 48.4 | 2.0685 | 5.3781 | 100% |  |  | 100% |  |  | 81.34% | 84.04% | 21.38% | 1734778.2 | 1724533 | 4933 | 1719600 | 335.0909 | 6.5258 | 1804554.8387 | 82.52% | 22.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-10-29 | 2025 | 2024 | 2024-10-01 | 31 | 11.05 | 5.1026 | 1.22 | 6.1625 | 0.24488 | 34.3286 | 45.822 | 2.8905 | 6.4756 | 100% |  |  | 100% |  |  | 82.14% | 84.15% | 21.09% | 1711923.5 | 1701267 | 5067 | 1696200 | 335.0909 | 6.5258 | 1804554.8387 | 82.52% | 22.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-10-30 | 2025 | 2024 | 2024-10-01 | 31 | 11.0167 | 5.2869 | 1.2748 | 6.4553 | 0.237 | 33.7077 | 47.4994 | 2.584 | 6.7958 | 100% |  |  | 100% |  |  | 81.64% | 83.8% | 21.96% | 1782570.8 | 1771133 | 5067 | 1766066 | 335.0909 | 6.5258 | 1804554.8387 | 82.52% | 22.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-10-31 | 2025 | 2024 | 2024-10-01 | 31 | 11.05 | 5.116 | 1.2178 | 6.196 | 0.23299 | 33.2162 | 46.9 | 1.4248 | 4.8161 | 100% |  |  | 100% |  |  | 82.21% | 84.47% | 21.22% | 1722569.8 | 1711800 | 5000 | 1706800 | 335.0909 | 6.5258 | 1804554.8387 | 82.52% | 22.44% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-11-01 | 2025 | 2024 | 2024-11-01 | 30 | 10.8833 | 4.9133 | 1.1733 | 5.95 | 0.23333 | 33.1683 | 45.9 | 1.6317 | 5.2517 | 100% |  |  | 100% |  |  | 82.61% | 86.92% | 20.48% | 1662130.5 | 1652067 | 5000 | 1647067 | 335.0909 | 5.43 | 1580396.6667 | 86.86% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-11-02 | 2025 | 2024 | 2024-11-01 | 30 | 10.9167 | 4.9116 | 1.1827 | 5.9717 | 0.23183 | 32.9121 | 45.63 | 2.2497 | 6.2479 | 100% |  |  | 100% |  |  | 82.79% | 86.8% | 20.6% | 1671960.1 | 1661734 | 5000 | 1656734 | 335.0909 | 5.43 | 1580396.6667 | 86.86% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-11-03 | 2025 | 2024 | 2024-11-01 | 30 | 10.8667 | 4.8733 | 1.1667 | 5.94 | 0.225 | 32.4883 | 45.9 | 1.705 | 5.6767 | 100% |  |  | 100% |  |  | 82.8% | 86.78% | 20.49% | 1663081.5 | 1653200 | 5133 | 1648067 | 335.0909 | 5.43 | 1580396.6667 | 86.86% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-11-04 | 2025 | 2024 | 2024-11-01 | 30 | 10.8833 | 4.8595 | 1.1628 | 5.9433 | 0.22645 | 32.4458 | 45.028 | 1.5924 | 4.6898 | 100% |  |  | 100% |  |  | 82.97% | 87.08% | 20.55% | 1667475.4 | 1657400 | 5067 | 1652333 | 335.0909 | 5.43 | 1580396.6667 | 86.86% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-11-05 | 2025 | 2024 | 2024-11-01 | 30 | 10.8667 | 4.7783 | 1.145 | 5.855 | 0.22167 | 32.0683 | 45.9133 | 1.34 | 4.1833 | 100% |  |  | 100% |  |  | 82.6% | 86.64% | 20.15% | 1635201.1 | 1625533 | 4933 | 1620600 | 335.0909 | 5.43 | 1580396.6667 | 86.86% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-11-06 | 2025 | 2024 | 2024-11-01 | 30 | 10.8667 | 4.7583 | 1.1483 | 5.8467 | 0.225 | 32.4333 | 44.6 | 1.59 | 4.8317 | 100% |  |  | 100% |  |  | 82.67% | 86.68% | 20.14% | 1633977.3 | 1624485 | 4933 | 1619552 | 335.0909 | 5.43 | 1580396.6667 | 86.86% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-11-07 | 2025 | 2024 | 2024-11-01 | 30 | 10.9167 | 4.855 | 1.1767 | 6.005 | 0.22167 | 32.1767 | 46.1 | 1.6483 | 5.5883 | 100% |  |  | 100% |  |  | 82.69% | 86.81% | 20.69% | 1678893.5 | 1669000 | 5000 | 1664000 | 335.0909 | 5.43 | 1580396.6667 | 86.86% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-11-08 | 2025 | 2024 | 2024-11-01 | 30 | 10.85 | 4.9012 | 1.191 | 6.0808 | 0.22772 | 31.9417 | 44.5333 | 1.802 | 5.7437 | 100% |  |  | 100% |  |  | 83.09% | 87.09% | 21.05% | 1708455.3 | 1698116 | 5067 | 1693049 | 335.0909 | 5.43 | 1580396.6667 | 86.86% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-11-09 | 2025 | 2024 | 2024-11-01 | 30 | 10.85 | 4.8952 | 1.192 | 6.0887 | 0.22853 | 31.4229 | 43.5705 | 2.1667 | 5.9709 | 99.62% |  |  | 100% |  |  | 83.34% | 87.03% | 21.14% | 1715752.4 | 1705267 | 5000 | 1700267 | 335.0909 | 5.43 | 1580396.6667 | 86.86% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-11-10 | 2025 | 2024 | 2024-11-01 | 30 | 10.9167 | 4.8783 | 1.19 | 6.0883 | 0.22833 | 31.0567 | 43.5 | 1.6283 | 5.2617 | 100% |  |  | 100% |  |  | 83.54% | 87.36% | 21.19% | 1720045.1 | 1709333 | 4933 | 1704400 | 335.0909 | 5.43 | 1580396.6667 | 86.86% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-11-11 | 2025 | 2024 | 2024-11-01 | 30 | 10.8167 | 4.7438 | 1.1622 | 5.9002 | 0.22253 | 30.7964 | 42.9069 | 1.8099 | 6.0637 | 100% |  |  | 100% |  |  | 83.4% | 86.84% | 20.5% | 1662574.5 | 1652467 | 3534 | 1648933 | 335.0909 | 5.43 | 1580396.6667 | 86.86% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-11-12 | 2025 | 2024 | 2024-11-01 | 30 | 10.8 | 4.6265 | 1.1332 | 5.7387 | 0.21717 | 29.9541 | 42.4574 | 1.3512 | 5.0732 | 100% |  |  | 100% |  |  | 83.38% | 87.24% | 19.94% | 1617721.8 | 1607800 | 4466 | 1603334 | 335.0909 | 5.43 | 1580396.6667 | 86.86% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-11-13 | 2025 | 2024 | 2024-11-01 | 30 | 10.7167 | 4.4649 | 1.1025 | 5.5039 | 0.21387 | 29.5448 | 42.3095 | 1.4771 | 4.5354 | 100% |  |  | 100% |  |  | 82.75% | 86.71% | 18.98% | 1539537.2 | 1531133 | 5000 | 1526133 | 335.0909 | 5.43 | 1580396.6667 | 86.86% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-11-14 | 2025 | 2024 | 2024-11-01 | 30 | 10.7 | 4.4649 | 1.1025 | 5.4344 | 0.21387 | 28.8004 | 42.234 | 1.4821 | 4.5354 | 100% |  |  | 100% |  |  | 85.13% | 86.91% | 19.28% | 1563982.9 | 1555334 | 5000 | 1550334 | 335.0909 | 5.43 | 1580396.6667 | 86.86% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-11-15 | 2025 | 2024 | 2024-11-01 | 30 | 10.7 | 4.145 | 1.03 | 4.875 | 0.21333 | 28.295 | 40.2933 | 1.3583 | 5.0783 | 100% |  |  | 100% |  |  | 83.91% | 85.9% | 17.05% | 1381984.2 | 1375800 | 5000 | 1370800 | 335.0909 | 5.43 | 1580396.6667 | 86.86% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-11-16 | 2025 | 2024 | 2024-11-01 | 30 | 10.6667 | 4.1507 | 1.0606 | 5.1426 | 0.21322 | 27.9884 | 40.5168 | 1.3186 | 5.3392 | 94.48% |  |  | 100% |  |  | 79.39% | 81.48% | 17.01% | 1380449.1 | 1373000 | 5000 | 1368000 | 335.0909 | 5.43 | 1580396.6667 | 86.86% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-11-17 | 2025 | 2024 | 2024-11-01 | 30 | 10.65 | 4.2167 | 1.0867 | 5.2433 | 0.225 | 26.2867 | 37.66 | 1.6017 | 4.255 | 100% |  |  | 100% |  |  | 84.78% | 86.58% | 18.52% | 1503240.5 | 1494750 | 5200 | 1489550 | 335.0909 | 5.43 | 1580396.6667 | 86.86% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-11-18 | 2025 | 2024 | 2024-11-01 | 30 | 10.65 | 4.4417 | 1.141 | 5.6265 | 0.22443 | 25.1915 | 38.3985 | 1.2045 | 4.2342 | 100% |  |  | 100% |  |  | 84.48% | 86.48% | 19.81% | 1607694.9 | 1597900 | 5134 | 1592766 | 335.0909 | 5.43 | 1580396.6667 | 86.86% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-11-19 | 2025 | 2024 | 2024-11-01 | 30 | 10.6667 | 4.4318 | 1.1409 | 5.6418 | 0.22221 | 25.5904 | 39.0969 | 0.99899 | 3.6033 | 100% |  |  | 100% |  |  | 84.46% | 86.51% | 19.85% | 1611410.5 | 1601817 | 5133 | 1596684 | 335.0909 | 5.43 | 1580396.6667 | 86.86% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-11-20 | 2025 | 2024 | 2024-11-01 | 30 | 10.6833 | 4.3867 | 1.1467 | 5.6383 | 0.22167 | 25.185 | 39.3067 | 0.96833 | 3.665 | 100% |  |  | 100% |  |  | 84.57% | 86.72% | 19.87% | 1612684 | 1602983 | 5100 | 1597883 | 335.0909 | 5.43 | 1580396.6667 | 86.86% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-11-21 | 2025 | 2024 | 2024-11-01 | 30 | 10.6667 | 4.342 | 1.1466 | 5.6503 | 0.21783 | 25.5602 | 39.8727 | 0.89453 | 3.8564 | 100% |  |  | 100% |  |  | 84.43% | 86.62% | 19.88% | 1613339.7 | 1603417 | 4900 | 1598517 | 335.0909 | 5.43 | 1580396.6667 | 86.86% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-11-22 | 2025 | 2024 | 2024-11-01 | 30 | 10.6333 | 4.3667 | 1.1367 | 5.575 | 0.21833 | 25.68 | 39.3667 | 1.1783 | 3.9817 | 100% |  |  | 100% |  |  | 84.18% | 86.35% | 19.56% | 1586818 | 1577583 | 4900 | 1572683 | 335.0909 | 5.43 | 1580396.6667 | 86.86% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-11-23 | 2025 | 2024 | 2024-11-01 | 30 | 10.5667 | 4.19 | 1.1017 | 5.3267 | 0.21333 | 25.65 | 39.01 | 1.02 | 3.7667 | 100% |  |  | 100% |  |  | 84.51% | 86.48% | 18.76% | 1521607 | 1513600 | 5200 | 1508400 | 335.0909 | 5.43 | 1580396.6667 | 86.86% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-11-24 | 2025 | 2024 | 2024-11-01 | 30 | 10.6167 | 4.0517 | 1.0617 | 5.1417 | 0.21167 | 25.05 | 37.81 | 0.67667 | 2.6933 | 100% |  |  | 100% |  |  | 85.1% | 89.71% | 18.23% | 1479136.5 | 1471284 | 5033 | 1466251 | 335.0909 | 5.43 | 1580396.6667 | 86.86% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-11-25 | 2025 | 2024 | 2024-11-01 | 30 | 10.5 | 3.9283 | 1.0267 | 4.9567 | 0.20667 | 25.495 | 37.6367 | 1.0117 | 3.6067 | 100% |  |  | 100% |  |  | 85.09% | 89.28% | 17.57% | 1425831 | 1418467 | 5134 | 1413333 | 335.0909 | 5.43 | 1580396.6667 | 86.86% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-11-26 | 2025 | 2024 | 2024-11-01 | 30 | 10.5167 | 4.0239 | 1.0533 | 5.1111 | 0.2063 | 26.4078 | 39.0704 | 1.5125 | 5.7264 | 98.06% |  |  | 100% |  |  | 83.23% | 84.98% | 17.73% | 1437988.4 | 1430667 | 5133 | 1425534 | 335.0909 | 5.43 | 1580396.6667 | 86.86% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-11-27 | 2025 | 2024 | 2024-11-01 | 30 | 10.5333 | 4.2151 | 1.1011 | 5.4371 | 0.21226 | 26.7994 | 40.3383 | 1.0552 | 4.3317 | 100% |  |  | 100% |  |  | 84.36% | 86.61% | 19.11% | 1551275.7 | 1542200 | 5200 | 1537000 | 335.0909 | 5.43 | 1580396.6667 | 86.86% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-11-28 | 2025 | 2024 | 2024-11-01 | 30 | 10.5667 | 4.2537 | 1.1199 | 5.509 | 0.21733 | 26.7019 | 39.8879 | 1.2908 | 4.5489 | 100% |  |  | 100% |  |  | 84.43% | 86.82% | 19.38% | 1572815.7 | 1563800 | 5133 | 1558667 | 335.0909 | 5.43 | 1580396.6667 | 86.86% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-11-29 | 2025 | 2024 | 2024-11-01 | 30 | 10.55 | 4.2788 | 1.1284 | 5.5677 | 0.21539 | 25.3958 | 38.434 | 1.5365 | 4.9858 | 100% |  |  | 100% |  |  | 84.56% | 86.39% | 19.62% | 1591872.2 | 1582600 | 4934 | 1577666 | 335.0909 | 5.43 | 1580396.6667 | 86.86% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-11-30 | 2025 | 2024 | 2024-11-01 | 30 | 10.4833 | 3.9367 | 1.0833 | 5.1 | 0.21333 | 25.05 | 36.3367 | 1.58 | 5.095 | 100% |  |  | 100% |  |  | 85.49% | 86.78% | 18.17% | 1473955.3 | 1466200 | 5133 | 1461067 | 335.0909 | 5.43 | 1580396.6667 | 86.86% | 19.65% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-12-01 | 2025 | 2024 | 2024-12-01 | 31 | 10.5 | 3.9133 | 1.0783 | 4.9667 | 0.20833 | 25.0267 | 36.34 | 1.635 | 4.5117 | 100% |  |  | 100% |  |  | 85.34% | 88.39% | 17.66% | 1432831.6 | 1425467 | 5133 | 1420334 | 335.0909 | 5.1161 | 1523267.7419 | 88.85% | 18.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-12-02 | 2025 | 2024 | 2024-12-01 | 31 | 10.4667 | 3.9672 | 1.0463 | 5.1162 | 0.21129 | 25.0885 | 35.7667 | 2.3834 | 6.7192 | 100% |  |  | 100% |  |  | 85.62% | 88.66% | 18.25% | 1480778.3 | 1472867 | 5000 | 1467867 | 335.0909 | 5.1161 | 1523267.7419 | 88.85% | 18.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-12-03 | 2025 | 2024 | 2024-12-01 | 31 | 10.45 | 4.0697 | 1.0826 | 5.2785 | 0.22249 | 25.4682 | 35.4223 | 2.999 | 6.8939 | 100% |  |  | 100% |  |  | 86.13% | 89.29% | 18.94% | 1537271.7 | 1528467 | 5067 | 1523400 | 335.0909 | 5.1161 | 1523267.7419 | 88.85% | 18.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-12-04 | 2025 | 2024 | 2024-12-01 | 31 | 10.45 | 3.8841 | 1.0407 | 4.9886 | 0.21702 | 24.0391 | 33.6035 | 2.3739 | 5.6736 | 100% |  |  | 100% |  |  | 86.21% | 88.95% | 17.92% | 1454035.6 | 1446467 | 5267 | 1441200 | 335.0909 | 5.1161 | 1523267.7419 | 88.85% | 18.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-12-05 | 2025 | 2024 | 2024-12-01 | 31 | 10.5167 | 4.1195 | 1.0968 | 5.3822 | 0.21582 | 23.621 | 37.6435 | 1.3422 | 4.7253 | 100% |  |  | 100% |  |  | 85.35% | 88.24% | 19.14% | 1552481.3 | 1543933 | 4666 | 1539267 | 335.0909 | 5.1161 | 1523267.7419 | 88.85% | 18.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-12-06 | 2025 | 2024 | 2024-12-01 | 31 | 10.45 | 4.0493 | 1.0765 | 5.2875 | 0.21444 | 23.9206 | 36.9988 | 0.96645 | 4.1506 | 100% |  |  | 100% |  |  | 85.24% | 88.57% | 18.78% | 1524107.1 | 1515000 | 4800 | 1510200 | 335.0909 | 5.1161 | 1523267.7419 | 88.85% | 18.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-12-07 | 2025 | 2024 | 2024-12-01 | 31 | 10.5833 | 4.502 | 1.2191 | 5.9842 | 0.24763 | 23.3814 | 35.4695 | 2.2508 | 5.8464 | 100% |  |  | 100% |  |  | 85.06% | 88.27% | 21.21% | 1722559.5 | 1710267 | 4667 | 1705600 | 335.0909 | 5.1161 | 1523267.7419 | 88.85% | 18.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-12-08 | 2025 | 2024 | 2024-12-01 | 31 | 10.5667 | 4.1562 | 1.156 | 5.3458 | 0.2689 | 21.6591 | 29.0191 | 5.8547 | 11.4775 | 100% |  |  | 100% |  |  | 84.8% | 87.48% | 18.89% | 1533268.5 | 1523733 | 4733 | 1519000 | 335.0909 | 5.1161 | 1523267.7419 | 88.85% | 18.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-12-09 | 2025 | 2024 | 2024-12-01 | 31 | 10.5333 | 4.0717 | 1.12 | 5.29 | 0.24833 | 18.82 | 29.4367 | 2.1567 | 5.395 | 100% |  |  | 100% |  |  | 86.63% | 87.72% | 19.1% | 1548825.9 | 1538934 | 3267 | 1535667 | 335.0909 | 5.1161 | 1523267.7419 | 88.85% | 18.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-12-10 | 2025 | 2024 | 2024-12-01 | 31 | 10.4833 | 4.1117 | 1.125 | 5.3783 | 0.23833 | 19.4383 | 30.4567 | 2.4183 | 6.5383 | 100% |  |  | 100% |  |  | 86.44% | 87.99% | 19.37% | 1573915.1 | 1562467 | 4600 | 1557867 | 335.0909 | 5.1161 | 1523267.7419 | 88.85% | 18.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-12-11 | 2025 | 2024 | 2024-12-01 | 31 | 10.4667 | 4.21 | 1.1517 | 5.5483 | 0.24333 | 19.8217 | 34.2133 | 1.7983 | 4.8983 | 100% |  |  | 44.1% |  |  | 39.12% | 88.89% | 9.043% | 740302 | 734200 | 6933 | 727267 | 335.0909 | 5.1161 | 1523267.7419 | 88.85% | 18.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-12-12 | 2025 | 2024 | 2024-12-01 | 31 | 10.4833 | 4.2683 | 1.1667 | 5.6567 | 0.25 | 20.0967 | 32.0333 | 1.7317 | 5.1883 | 100% |  |  | 100% |  |  | 85.98% | 88.24% | 20.26% | 1645449.6 | 1634733 | 5000 | 1629733 | 335.0909 | 5.1161 | 1523267.7419 | 88.85% | 18.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-12-13 | 2025 | 2024 | 2024-12-01 | 31 | 10.4667 | 4.2769 | 1.1873 | 5.6612 | 0.25579 | 18.8874 | 28.8161 | 3.59 | 7.3194 | 100% |  |  | 100% |  |  | 87.2% | 88.38% | 20.57% | 1670758.6 | 1659334 | 5067 | 1654267 | 335.0909 | 5.1161 | 1523267.7419 | 88.85% | 18.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-12-14 | 2025 | 2024 | 2024-12-01 | 31 | 10.5 | 4.4489 | 1.2395 | 5.9412 | 0.25782 | 19.8304 | 31.6026 | 2.4109 | 5.7425 | 100% |  |  | 100% |  |  | 85.83% | 87.95% | 21.25% | 1725779.7 | 1713866 | 5133 | 1708733 | 335.0909 | 5.1161 | 1523267.7419 | 88.85% | 18.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-12-15 | 2025 | 2024 | 2024-12-01 | 31 | 10.4833 | 4.4808 | 1.2415 | 6.008 | 0.25449 | 20.9932 | 33.8371 | 1.4211 | 4.3275 | 100% |  |  | 100% |  |  | 84.98% | 87.74% | 21.27% | 1727978 | 1716001 | 5134 | 1710867 | 335.0909 | 5.1161 | 1523267.7419 | 88.85% | 18.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-12-16 | 2025 | 2024 | 2024-12-01 | 31 | 10.4667 | 4.0351 | 1.2122 | 5.8105 | 0.25419 | 20.2211 | 31.7938 | 2.2997 | 5.5128 | 99.99% |  |  | 100% |  |  | 86.1% | 88.19% | 20.85% | 1692830.8 | 1681600 | 5200 | 1676400 | 335.0909 | 5.1161 | 1523267.7419 | 88.85% | 18.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-12-17 | 2025 | 2024 | 2024-12-01 | 31 | 10.45 | 4.275 | 1.2283 | 5.7633 | 0.26667 | 19.53 | 29.6 | 3.28 | 7.1667 | 100% |  |  | 100% |  |  | 86.2% | 87.63% | 20.7% | 1681335 | 1669933 | 5266 | 1664667 | 335.0909 | 5.1161 | 1523267.7419 | 88.85% | 18.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-12-18 | 2025 | 2024 | 2024-12-01 | 31 | 10.5167 | 4.1517 | 1.2183 | 5.7067 | 0.26333 | 18.8533 | 29.4433 | 3.4033 | 6.1567 | 100% |  |  | 100% |  |  | 85.75% | 87.22% | 20.39% | 1656260.3 | 1644867 | 5067 | 1639800 | 335.0909 | 5.1161 | 1523267.7419 | 88.85% | 18.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-12-19 | 2025 | 2024 | 2024-12-01 | 31 | 10.45 | 4.2733 | 1.2133 | 5.67 | 0.26 | 19.1017 | 28.6 | 3.355 | 7.15 | 100% |  |  | 100% |  |  | 87.01% | 88.04% | 20.56% | 1669897.6 | 1658333 | 5200 | 1653133 | 335.0909 | 5.1161 | 1523267.7419 | 88.85% | 18.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-12-20 | 2025 | 2024 | 2024-12-01 | 31 | 10.3667 | 3.741 | 1.0769 | 4.7826 | 0.24459 | 17.7245 | 24.7229 | 5.1086 | 8.9494 | 100% |  |  | 100% |  |  | 88.42% | 87.95% | 17.62% | 1430247.2 | 1422267 | 5200 | 1417067 | 335.0909 | 5.1161 | 1523267.7419 | 88.85% | 18.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-12-21 | 2025 | 2024 | 2024-12-01 | 31 | 10.3333 | 3.3541 | 0.96615 | 4.1426 | 0.22308 | 18.5492 | 26.7517 | 2.3197 | 5.3561 | 100% |  |  | 100% |  |  | 87.63% | 87.63% | 15.13% | 1226073.9 | 1220400 | 4000 | 1216400 | 335.0909 | 5.1161 | 1523267.7419 | 88.85% | 18.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-12-22 | 2025 | 2024 | 2024-12-01 | 31 | 10.1167 | 2.8183 | 0.8 | 3.29 | 0.195 | 20.3767 | 29.5767 | 1.285 | 5.185 | 100% |  |  | 100% |  |  | 86.8% | 86.99% | 11.9% | 965795.7 | 962267 | 5333 | 956934 | 335.0909 | 5.1161 | 1523267.7419 | 88.85% | 18.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-12-23 | 2025 | 2024 | 2024-12-01 | 31 | 10.3 | 3.115 | 0.89833 | 3.75 | 0.21833 | 17.51 | 24.3933 | 3.4583 | 6.2633 | 100% |  |  | 100% |  |  | 87.72% | 86.95% | 13.71% | 1112280.8 | 1107533 | 5200 | 1102333 | 335.0909 | 5.1161 | 1523267.7419 | 88.85% | 18.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-12-24 | 2025 | 2024 | 2024-12-01 | 31 | 10.2667 | 3.225 | 0.91333 | 3.9317 | 0.22 | 16.0333 | 21.9967 | 4.5667 | 7.8467 | 99.93% |  |  | 100% |  |  | 88.42% | 86.96% | 14.48% | 1175347.4 | 1170001 | 5134 | 1164867 | 335.0909 | 5.1161 | 1523267.7419 | 88.85% | 18.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-12-25 | 2025 | 2024 | 2024-12-01 | 31 | 10.3667 | 3.685 | 1.0383 | 4.6883 | 0.23667 | 17.5267 | 25.4033 | 4.405 | 7.4317 | 100% |  |  | 100% |  |  | 88.4% | 88.1% | 17.27% | 1401927.9 | 1393800 | 5066 | 1388734 | 335.0909 | 5.1161 | 1523267.7419 | 88.85% | 18.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-12-26 | 2025 | 2024 | 2024-12-01 | 31 | 10.2167 | 2.4041 | 0.66843 | 2.6861 | 0.15935 | 17.9873 | 23.1684 | 3.3555 | 6.3383 | 100% |  |  | 100% |  |  | 88.81% | 87.74% | 9.94% | 807689.5 | 804600 | 5200 | 799400 | 335.0909 | 5.1161 | 1523267.7419 | 88.85% | 18.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-12-27 | 2025 | 2024 | 2024-12-01 | 31 | 10.2667 | 2.8547 | 0.79561 | 3.3415 | 0.21273 | 18.6833 | 23.6681 | 4.2935 | 8.3083 | 100% |  |  | 100% |  |  | 88.32% | 87% | 12.3% | 997238.7 | 994000 | 5067 | 988933 | 335.0909 | 5.1161 | 1523267.7419 | 88.85% | 18.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-12-28 | 2025 | 2024 | 2024-12-01 | 31 | 10.5667 | 4.05 | 1.1383 | 5.2983 | 0.24667 | 18.4183 | 29.7333 | 1.9333 | 4.725 | 100% |  |  | 100% |  |  | 87.44% | 88.79% | 19.3% | 1567247.2 | 1557545 | 5133 | 1552412 | 335.0909 | 5.1161 | 1523267.7419 | 88.85% | 18.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-12-29 | 2025 | 2024 | 2024-12-01 | 31 | 10.5667 | 4.1283 | 1.1583 | 5.4167 | 0.24833 | 18.4633 | 28.2333 | 3.11 | 7.175 | 96.52% |  |  | 100% |  |  | 85.08% | 86.01% | 19.2% | 1559515.4 | 1549455 | 5267 | 1544188 | 335.0909 | 5.1161 | 1523267.7419 | 88.85% | 18.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-12-30 | 2025 | 2024 | 2024-12-01 | 31 | 10.5167 | 4.4133 | 1.2183 | 5.8617 | 0.25667 | 16.2133 | 29.3233 | 2.12 | 4.7433 | 100% |  |  | 100% |  |  | 87.75% | 89.05% | 21.43% | 1740464.7 | 1727800 | 4133 | 1723667 | 335.0909 | 5.1161 | 1523267.7419 | 88.85% | 18.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2024-12-31 | 2025 | 2024 | 2024-12-01 | 31 | 10.4833 | 4.3014 | 1.1833 | 5.6363 | 0.25761 | 19.5695 | 32.3022 | 1.9181 | 5.2908 | 100% |  |  | 100% |  |  | 87.9% | 89.82% | 20.64% | 1676649.8 | 1665267 | 5200 | 1660067 | 335.0909 | 5.1161 | 1523267.7419 | 88.85% | 18.94% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-01-01 | 2025 | 2025 | 2025-01-01 | 31 | 10.5333 | 4.2133 | 1.1517 | 5.565 | 0.235 | 20.3733 | 32.0867 | 1.8783 | 4.8667 | 99.7% |  |  | 100% |  |  | 87.27% | 89.64% | 20.24% | 1643387.1 | 1632533 | 5067 | 1627466 | 335.0909 | 5.4525 | 1617196.7742 | 88.51% | 20.11% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-01-02 | 2025 | 2025 | 2025-01-01 | 31 | 10.6 | 4.0433 | 1.115 | 5.0717 | 0.25333 | 21.9383 | 34.6433 | 1.25 | 3.6367 | 99.98% |  |  | 100% |  |  | 87.36% | 90.05% | 18.46% | 1498511 | 1489645 | 5000 | 1484645 | 335.0909 | 5.4525 | 1617196.7742 | 88.51% | 20.11% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-01-03 | 2025 | 2025 | 2025-01-01 | 31 | 10.5333 | 4.1533 | 1.145 | 5.4617 | 0.22833 | 23.6183 | 37.9833 | 1.2467 | 4.61 | 100% |  |  | 100% |  |  | 86% | 89.86% | 19.57% | 1588215.3 | 1579022 | 5067 | 1573955 | 335.0909 | 5.4525 | 1617196.7742 | 88.51% | 20.11% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-01-04 | 2025 | 2025 | 2025-01-01 | 31 | 10.4167 | 3.99 | 1.11 | 5.105 | 0.22833 | 23.18 | 34.6233 | 2.3633 | 5.8583 | 100% |  |  | 100% |  |  | 86.82% | 89.76% | 18.47% | 1498881.2 | 1490400 | 5200 | 1485200 | 335.0909 | 5.4525 | 1617196.7742 | 88.51% | 20.11% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-01-05 | 2025 | 2025 | 2025-01-01 | 31 | 10.4167 | 3.7267 | 1.08 | 4.7483 | 0.24 | 19.005 | 28.4867 | 2.5467 | 5.6317 | 100% |  |  | 100% |  |  | 88.37% | 89.53% | 17.48% | 1419574.4 | 1411267 | 5133 | 1406134 | 335.0909 | 5.4525 | 1617196.7742 | 88.51% | 20.11% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-01-06 | 2025 | 2025 | 2025-01-01 | 31 | 10.5333 | 4.3917 | 1.2517 | 5.7683 | 0.26 | 18.0667 | 29.1033 | 2.9233 | 5.9333 | 100% |  |  | 100% |  |  | 88.06% | 89.65% | 21.16% | 1719515.7 | 1707267 | 5200 | 1702067 | 335.0909 | 5.4525 | 1617196.7742 | 88.51% | 20.11% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-01-07 | 2025 | 2025 | 2025-01-01 | 31 | 10.6 | 4.4527 | 1.2787 | 5.8594 | 0.26432 | 18.0345 | 28.1806 | 2.8882 | 6.4775 | 100% |  |  | 100% |  |  | 87.47% | 89.11% | 21.35% | 1734934.6 | 1722534 | 5133 | 1717401 | 335.0909 | 5.4525 | 1617196.7742 | 88.51% | 20.11% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-01-08 | 2025 | 2025 | 2025-01-01 | 31 | 10.5667 | 4.4836 | 1.264 | 5.92 | 0.24305 | 20.2208 | 36.666 | 1.0339 | 3.0828 | 100% |  |  | 100% |  |  | 86.19% | 89.24% | 21.26% | 1725641.1 | 1713733 | 3867 | 1709866 | 335.0909 | 5.4525 | 1617196.7742 | 88.51% | 20.11% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-01-09 | 2025 | 2025 | 2025-01-01 | 31 | 10.6167 | 4.4818 | 1.2651 | 5.8723 | 0.25806 | 22.2917 | 35.6828 | 1.7525 | 4.2361 | 100% |  |  | 100% |  |  | 86.53% | 89.75% | 21.17% | 1719002.5 | 1707800 | 5133 | 1702667 | 335.0909 | 5.4525 | 1617196.7742 | 88.51% | 20.11% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-01-10 | 2025 | 2025 | 2025-01-01 | 31 | 10.5167 | 4.1144 | 1.1741 | 5.2996 | 0.23142 | 20.9105 | 35.099 | 1.2934 | 3.8236 | 100% |  |  | 100% |  |  | 85.38% | 91.92% | 18.85% | 1530157 | 1521200 | 5000 | 1516200 | 335.0909 | 5.4525 | 1617196.7742 | 88.51% | 20.11% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-01-11 | 2025 | 2025 | 2025-01-01 | 31 | 10.3 | 3.8217 | 0.97972 | 4.7982 | 0.21313 | 20.2442 | 32.5306 | 2.2449 | 5.4725 | 99.99% |  |  | 100% |  |  | 87.74% | 89.64% | 17.54% | 1423936.7 | 1416067 | 5400 | 1410667 | 335.0909 | 5.4525 | 1617196.7742 | 88.51% | 20.11% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-01-12 | 2025 | 2025 | 2025-01-01 | 31 | 10.1833 | 3.295 | 0.85667 | 4.0317 | 0.18333 | 14.6283 | 23.34 | 3.4983 | 6.2533 | 100% |  |  | 100% |  |  | 89.46% | 89.39% | 15.03% | 1222833.9 | 1213910 | 5334 | 1208576 | 335.0909 | 5.4525 | 1617196.7742 | 88.51% | 20.11% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-01-13 | 2025 | 2025 | 2025-01-01 | 31 | 10.3 | 3.2868 | 0.85292 | 4.0188 | 0.18485 | 13.5716 | 22.7319 | 3.2703 | 6.0403 | 100% |  |  | 100% |  |  | 89.49% | 89.37% | 14.98% | 1219355.8 | 1210357 | 5266 | 1205091 | 335.0909 | 5.4525 | 1617196.7742 | 88.51% | 20.11% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-01-14 | 2025 | 2025 | 2025-01-01 | 31 | 10.5167 | 4.2 | 1.09 | 5.35 | 0.23833 | 17.2033 | 27.6667 | 3.3367 | 7.0333 | 100% |  |  | 100% |  |  | 88.76% | 89.77% | 19.79% | 1607186.7 | 1596400 | 5200 | 1591200 | 335.0909 | 5.4525 | 1617196.7742 | 88.51% | 20.11% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-01-15 | 2025 | 2025 | 2025-01-01 | 31 | 10.5167 | 4.155 | 1.1033 | 5.2633 | 0.24167 | 18.155 | 27.11 | 3.705 | 7.6067 | 100% |  |  | 100% |  |  | 89.05% | 89.9% | 19.53% | 1585557.2 | 1575643 | 5067 | 1570576 | 335.0909 | 5.4525 | 1617196.7742 | 88.51% | 20.11% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-01-16 | 2025 | 2025 | 2025-01-01 | 31 | 10.6167 | 4.3161 | 1.1496 | 5.5457 | 0.24552 | 18.7937 | 31.0761 | 2.0296 | 5.6592 | 100% |  |  | 100% |  |  | 87.91% | 89.83% | 20.31% | 1648920.1 | 1638824 | 5133 | 1633691 | 335.0909 | 5.4525 | 1617196.7742 | 88.51% | 20.11% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-01-17 | 2025 | 2025 | 2025-01-01 | 31 | 10.6333 | 4.571 | 1.2231 | 5.8911 | 0.2587 | 17.8921 | 27.6208 | 4.5264 | 8.8314 | 100% |  |  | 100% |  |  | 87.11% | 88.03% | 21.38% | 1737068.1 | 1724667 | 5134 | 1719533 | 335.0909 | 5.4525 | 1617196.7742 | 88.51% | 20.11% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-01-18 | 2025 | 2025 | 2025-01-01 | 31 | 10.5667 | 4.1787 | 1.1011 | 5.291 | 0.23511 | 19.242 | 31.1858 | 2.1607 | 4.7842 | 100% |  |  | 100% |  |  | 87.89% | 89.69% | 19.38% | 1573141 | 1563533 | 5266 | 1558267 | 335.0909 | 5.4525 | 1617196.7742 | 88.51% | 20.11% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-01-19 | 2025 | 2025 | 2025-01-01 | 31 | 10.6167 | 4.3832 | 1.1613 | 5.5704 | 0.24118 | 20.9227 | 34.1143 | 2.0234 | 4.7264 | 100% |  |  | 100% |  |  | 86.85% | 89.71% | 20.16% | 1636957.7 | 1626467 | 5267 | 1621200 | 335.0909 | 5.4525 | 1617196.7742 | 88.51% | 20.11% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-01-20 | 2025 | 2025 | 2025-01-01 | 31 | 10.6 | 4.2467 | 1.1267 | 5.3567 | 0.23833 | 20.6633 | 32.3633 | 2.2183 | 4.4567 | 99.99% |  |  | 100% |  |  | 87.68% | 90.08% | 19.57% | 1589088.3 | 1579133 | 5267 | 1573866 | 335.0909 | 5.4525 | 1617196.7742 | 88.51% | 20.11% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-01-21 | 2025 | 2025 | 2025-01-01 | 31 | 10.5667 | 4.1183 | 1.1067 | 5.1483 | 0.235 | 21.7733 | 32.9567 | 2.3417 | 4.8933 | 100% |  |  | 100% |  |  | 87.36% | 89.88% | 18.74% | 1520799.1 | 1512201 | 5133 | 1507068 | 335.0909 | 5.4525 | 1617196.7742 | 88.51% | 20.11% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-01-22 | 2025 | 2025 | 2025-01-01 | 31 | 10.55 | 4.215 | 1.1267 | 5.2683 | 0.24 | 22.0383 | 34.1967 | 2.1667 | 5.205 | 100% |  |  | 100% |  |  | 87.2% | 89.99% | 19.14% | 1553571.7 | 1544466 | 5133 | 1539333 | 335.0909 | 5.4525 | 1617196.7742 | 88.51% | 20.11% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-01-23 | 2025 | 2025 | 2025-01-01 | 31 | 10.7 | 4.7667 | 1.2883 | 6.0817 | 0.26 | 19.805 | 30.44 | 3.685 | 7.0583 | 100% |  |  | 100% |  |  | 86.71% | 88.68% | 21.97% | 1784121.9 | 1772134 | 5067 | 1767067 | 335.0909 | 5.4525 | 1617196.7742 | 88.51% | 20.11% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-01-24 | 2025 | 2025 | 2025-01-01 | 31 | 10.8333 | 4.8683 | 1.315 | 6.2233 | 0.26833 | 20.9483 | 32.5767 | 3.355 | 6.805 | 100% |  |  | 100% |  |  | 86.15% | 88.75% | 22.34% | 1813782.6 | 1801467 | 5000 | 1796467 | 335.0909 | 5.4525 | 1617196.7742 | 88.51% | 20.11% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-01-25 | 2025 | 2025 | 2025-01-01 | 31 | 10.8833 | 5.0218 | 1.3592 | 6.4458 | 0.27102 | 21.0994 | 35.8119 | 1.6648 | 4.5975 | 100% |  |  | 100% |  |  | 84.74% | 88.09% | 22.76% | 1847772.6 | 1835266 | 5000 | 1830266 | 335.0909 | 5.4525 | 1617196.7742 | 88.51% | 20.11% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-01-26 | 2025 | 2025 | 2025-01-01 | 31 | 10.8667 | 5.1247 | 1.3854 | 6.5703 | 0.27741 | 21.7867 | 36.0101 | 1.8973 | 4.3928 | 100% |  |  | 100% |  |  | 84.26% | 87.93% | 23.07% | 1873160 | 1860267 | 5067 | 1855200 | 335.0909 | 5.4525 | 1617196.7742 | 88.51% | 20.11% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-01-27 | 2025 | 2025 | 2025-01-01 | 31 | 10.8833 | 5.1517 | 1.3917 | 6.5867 | 0.28 | 22.855 | 36.79 | 1.895 | 4.6883 | 100% |  |  | 100% |  |  | 83.9% | 87.91% | 23.03% | 1870268.3 | 1856800 | 4933 | 1851867 | 335.0909 | 5.4525 | 1617196.7742 | 88.51% | 20.11% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-01-28 | 2025 | 2025 | 2025-01-01 | 31 | 10.8833 | 5.1067 | 1.37 | 6.5 | 0.26167 | 24.05 | 40.1867 | 1.16 | 3.72 | 100% |  |  | 100% |  |  | 83.74% | 88.33% | 22.68% | 1840732.7 | 1828775 | 4933 | 1823842 | 335.0909 | 5.4525 | 1617196.7742 | 88.51% | 20.11% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-01-29 | 2025 | 2025 | 2025-01-01 | 31 | 10.9167 | 5.0715 | 1.3716 | 6.3893 | 0.26758 | 25.9041 | 39.1208 | 3.8003 | 8.0608 | 100% |  |  | 100% |  |  | 84.34% | 88.34% | 22.45% | 1822747.9 | 1810692 | 5067 | 1805625 | 335.0909 | 5.4525 | 1617196.7742 | 88.51% | 20.11% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-01-30 | 2025 | 2025 | 2025-01-01 | 31 | 10.8167 | 4.6785 | 1.2809 | 5.8094 | 0.26469 | 22.1148 | 34.0243 | 2.5493 | 5.3136 | 100% |  |  | 100% |  |  | 87.27% | 90.17% | 21.12% | 1714872.6 | 1704067 | 5200 | 1698867 | 335.0909 | 5.4525 | 1617196.7742 | 88.51% | 20.11% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-01-31 | 2025 | 2025 | 2025-01-01 | 31 | 10.8 | 4.0983 | 1.135 | 4.935 | 0.24833 | 21.4033 | 33.61 | 1.345 | 4.8467 | 100% |  |  | 100% |  |  | 87.26% | 89.55% | 17.94% | 1455663.6 | 1448267 | 5200 | 1443067 | 335.0909 | 5.4525 | 1617196.7742 | 88.51% | 20.11% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-02-01 | 2025 | 2025 | 2025-02-01 | 28 | 10.7667 | 4.1736 | 1.1508 | 5.0209 | 0.26055 | 21.7971 | 31.7547 | 3.0061 | 6.2186 | 100% |  |  | 100% |  |  | 87.36% | 87.73% | 18.28% | 1482885.7 | 1474933 | 5067 | 1469866 | 335.0909 | 6.1628 | 1755089.2857 | 84.99% | 21.82% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-02-02 | 2025 | 2025 | 2025-02-01 | 28 | 10.85 | 4.915 | 1.3583 | 6.095 | 0.28333 | 21.085 | 31.9833 | 3.575 | 7.205 | 100% |  |  | 100% |  |  | 85.89% | 86.47% | 21.81% | 1771055.4 | 1759267 | 5000 | 1754267 | 335.0909 | 6.1628 | 1755089.2857 | 84.99% | 21.82% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-02-03 | 2025 | 2025 | 2025-02-01 | 28 | 10.7833 | 4.5784 | 1.2613 | 5.5907 | 0.26925 | 21.089 | 33.1534 | 2.1023 | 5.1686 | 100% |  |  | 100% |  |  | 87.24% | 88.17% | 20.32% | 1649355.3 | 1639334 | 5000 | 1634334 | 335.0909 | 6.1628 | 1755089.2857 | 84.99% | 21.82% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-02-04 | 2025 | 2025 | 2025-02-01 | 28 | 10.8833 | 5.05 | 1.3867 | 6.25 | 0.28333 | 21.4117 | 35.0233 | 1.68 | 5.055 | 99.99% |  |  | 100% |  |  | 85.39% | 87.05% | 22.24% | 1805384.3 | 1793333 | 5066 | 1788267 | 335.0909 | 6.1628 | 1755089.2857 | 84.99% | 21.82% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-02-05 | 2025 | 2025 | 2025-02-01 | 28 | 10.9833 | 5.0717 | 1.3883 | 6.265 | 0.28167 | 21.9933 | 36.62 | 1.5417 | 4.985 | 100% |  |  | 100% |  |  | 84.92% | 86.7% | 22.17% | 1798265.7 | 1786400 | 3667 | 1782733 | 335.0909 | 6.1628 | 1755089.2857 | 84.99% | 21.82% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-02-06 | 2025 | 2025 | 2025-02-01 | 28 | 11 | 5.4583 | 1.4733 | 6.6167 | 0.3 | 22.3817 | 35.3967 | 3.27 | 7.1883 | 100% |  |  | 86.1% |  |  | 73.22% | 85.86% | 20.19% | 1639348 | 1628400 | 5000 | 1623400 | 335.0909 | 6.1628 | 1755089.2857 | 84.99% | 21.82% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-02-07 | 2025 | 2025 | 2025-02-01 | 28 | 11.0167 | 5.0982 | 1.3979 | 6.1819 | 0.29012 | 21.5115 | 33.9536 | 3.085 | 6.0939 | 100% |  |  | 100% |  |  | 85.12% | 86.26% | 21.92% | 1780066.4 | 1768134 | 4933 | 1763201 | 335.0909 | 6.1628 | 1755089.2857 | 84.99% | 21.82% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-02-08 | 2025 | 2025 | 2025-02-01 | 28 | 10.9833 | 5.2217 | 1.39 | 6.1833 | 0.285 | 23.6283 | 37.86 | 2.1733 | 4.995 | 100% |  |  | 100% |  |  | 83.59% | 85.49% | 21.54% | 1747671.7 | 1737067 | 5000 | 1732067 | 335.0909 | 6.1628 | 1755089.2857 | 84.99% | 21.82% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-02-09 | 2025 | 2025 | 2025-02-01 | 28 | 11.0167 | 5.1767 | 1.4083 | 6.225 | 0.27667 | 25.2683 | 40.43 | 1.1533 | 3.6633 | 100% |  |  | 100% |  |  | 83.96% | 87.08% | 21.78% | 1768081.5 | 1756333 | 4934 | 1751399 | 335.0909 | 6.1628 | 1755089.2857 | 84.99% | 21.82% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-02-10 | 2025 | 2025 | 2025-02-01 | 28 | 10.9833 | 5.0098 | 1.3764 | 5.993 | 0.29619 | 26.5257 | 39.3163 | 2.7783 | 6.4511 | 99.8% |  |  | 100% |  |  | 84.44% | 86.9% | 21.08% | 1710116.3 | 1699600 | 3933 | 1695667 | 335.0909 | 6.1628 | 1755089.2857 | 84.99% | 21.82% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-02-11 | 2025 | 2025 | 2025-02-01 | 28 | 11 | 5.1579 | 1.407 | 6.2496 | 0.27631 | 25.823 | 41.4471 | 1.509 | 5.3775 | 100% |  |  | 100% |  |  | 71.22% | 87.74% | 18.54% | 1777969 | 1493467 | 2067 | 1491400 | 335.0909 | 6.1628 | 1755089.2857 | 84.99% | 21.82% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-02-12 | 2025 | 2025 | 2025-02-01 | 28 | 11.0333 | 5.1132 | 1.4139 | 6.1684 | 0.29313 | 24.6719 | 38.315 | 1.8644 | 5.1369 | 100% |  |  | 100% |  |  | 85.3% | 87.9% | 21.92% | 1780240.1 | 1768067 | 5000 | 1763067 | 335.0909 | 6.1628 | 1755089.2857 | 84.99% | 21.82% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-02-13 | 2025 | 2025 | 2025-02-01 | 28 | 11.1 | 5.1417 | 1.415 | 6.1883 | 0.285 | 25.15 | 40.09 | 2.01 | 5.13 | 100% |  |  | 100% |  |  | 85.09% | 87.62% | 21.94% | 1780151 | 1768733 | 4333 | 1764400 | 335.0909 | 6.1628 | 1755089.2857 | 84.99% | 21.82% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-02-14 | 2025 | 2025 | 2025-02-01 | 28 | 11.05 | 5.0659 | 1.431 | 6.0421 | 0.29613 | 27.3165 | 40.571 | 3.3635 | 7.903 | 100% |  |  | 100% |  |  | 84.56% | 87.3% | 21.29% | 1727755.9 | 1716934 | 4933 | 1712001 | 335.0909 | 6.1628 | 1755089.2857 | 84.99% | 21.82% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-02-15 | 2025 | 2025 | 2025-02-01 | 28 | 11.05 | 5.352 | 1.514 | 6.464 | 0.304 | 27.36 | 39.98 | 3.446 | 6.574 | 100% |  |  | 100% |  |  | 84.1% | 87.2% | 22.65% | 1838618.6 | 1826400 | 4800 | 1821600 | 335.0909 | 6.1628 | 1755089.2857 | 84.99% | 21.82% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-02-16 | 2025 | 2025 | 2025-02-01 | 28 | 11.0833 | 4.9208 | 1.3479 | 5.7986 | 0.28827 | 27.3954 | 41.1065 | 2.749 | 6.9686 | 100% |  |  | 100% |  |  | 84.8% | 87.83% | 20.49% | 1662465.3 | 1652599 | 4934 | 1647665 | 335.0909 | 6.1628 | 1755089.2857 | 84.99% | 21.82% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-02-17 | 2025 | 2025 | 2025-02-01 | 28 | 11.0667 | 5.2833 | 1.4417 | 6.315 | 0.295 | 28.1 | 40.02 | 2.6317 | 6.5067 | 100% |  |  | 100% |  |  | 84.19% | 87.43% | 22.15% | 1798313.9 | 1786468 | 5000 | 1781468 | 335.0909 | 6.1628 | 1755089.2857 | 84.99% | 21.82% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-02-18 | 2025 | 2025 | 2025-02-01 | 28 | 11.0833 | 5.1783 | 1.42 | 6.1433 | 0.28667 | 27.3483 | 40.6933 | 2.0583 | 5.1867 | 100% |  |  | 100% |  |  | 84.86% | 87.93% | 21.72% | 1762665.7 | 1751733 | 4866 | 1746867 | 335.0909 | 6.1628 | 1755089.2857 | 84.99% | 21.82% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-02-19 | 2025 | 2025 | 2025-02-01 | 28 | 11.2 | 3.738 | 1.0139 | 4.2003 | 0.23643 | 27.5972 | 36.219 | 4.0665 | 10.4892 | 100% |  |  | 100% |  |  | 87.1% | 88.27% | 15.24% | 1236073.2 | 1230667 | 4800 | 1225867 | 335.0909 | 6.1628 | 1755089.2857 | 84.99% | 21.82% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-02-20 | 2025 | 2025 | 2025-02-01 | 28 | 11.2167 | 5.365 | 1.4767 | 6.2833 | 0.33167 | 25.575 | 38.17 | 2.4033 | 6.4833 | 100% |  |  | 100% |  |  | 84.27% | 86.89% | 22.06% | 1790491.6 | 1779000 | 4734 | 1774266 | 335.0909 | 6.1628 | 1755089.2857 | 84.99% | 21.82% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-02-21 | 2025 | 2025 | 2025-02-01 | 28 | 11.3 | 5.215 | 1.415 | 6.1017 | 0.31167 | 24.34 | 37.2367 | 2.14 | 6.3217 | 100% |  |  | 100% |  |  | 84.44% | 86.1% | 21.47% | 1741856.4 | 1731200 | 4666 | 1726534 | 335.0909 | 6.1628 | 1755089.2857 | 84.99% | 21.82% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-02-22 | 2025 | 2025 | 2025-02-01 | 28 | 11.2833 | 5.5567 | 1.5067 | 6.5467 | 0.30667 | 24.5333 | 38.9 | 2.165 | 5.9217 | 100% |  |  | 100% |  |  | 83.66% | 86.05% | 22.82% | 1851950 | 1840032 | 4767 | 1835265 | 335.0909 | 6.1628 | 1755089.2857 | 84.99% | 21.82% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-02-23 | 2025 | 2025 | 2025-02-01 | 28 | 11.3333 | 5.7274 | 1.5533 | 6.7522 | 0.30874 | 27.0292 | 41.5037 | 2.0543 | 6.3022 | 100% |  |  | 100% |  |  | 82.03% | 85.54% | 23.08% | 1873311.9 | 1860902 | 4833 | 1856069 | 335.0909 | 6.1628 | 1755089.2857 | 84.99% | 21.82% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-02-24 | 2025 | 2025 | 2025-02-01 | 28 | 11.2833 | 4.715 | 1.2783 | 5.495 | 0.25667 | 28.0467 | 40.3767 | 1.68 | 5.8833 | 100% |  |  | 100% |  |  | 84.25% | 86.88% | 19.29% | 1564152.5 | 1556067 | 4800 | 1551267 | 335.0909 | 6.1628 | 1755089.2857 | 84.99% | 21.82% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-02-25 | 2025 | 2025 | 2025-02-01 | 28 | 11.0833 | 3.5374 | 0.96939 | 3.7013 | 0.2744 | 27.6 | 34.8462 | 2.9457 | 7.3803 | 100% |  |  | 100% |  |  | 90.81% | 91.04% | 14.01% | 1132416 | 1129266 | 2934 | 1126332 | 335.0909 | 6.1628 | 1755089.2857 | 84.99% | 21.82% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-02-26 | 2025 | 2025 | 2025-02-01 | 28 | 11.35 | 4.75 | 1.305 | 5.345 | 0.305 | 29.5917 | 41.0467 | 2.78 | 7.725 | 100% |  |  | 100% |  |  | 85.05% | 87.55% | 18.94% | 1534450 | 1526734 | 3400 | 1523334 | 335.0909 | 6.1628 | 1755089.2857 | 84.99% | 21.82% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-02-27 | 2025 | 2025 | 2025-02-01 | 28 | 11.1333 | 3.1194 | 0.84758 | 3.186 | 0.2462 | 27.3188 | 34.2805 | 2.5921 | 8.1781 | 100% |  |  | 100% |  |  | 92.15% | 92.12% | 12.23% | 992057.6 | 988866 | 5066 | 983800 | 335.0909 | 6.1628 | 1755089.2857 | 84.99% | 21.82% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-02-28 | 2025 | 2025 | 2025-02-01 | 28 | 11.0167 | 3.625 | 0.96833 | 3.985 | 0.22333 | 26.365 | 34.2367 | 5.1467 | 9.0417 | 100% |  |  | 100% |  |  | 86.6% | 87.27% | 14.38% | 1167240.5 | 1161534 | 5134 | 1156400 | 335.0909 | 6.1628 | 1755089.2857 | 84.99% | 21.82% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-03-01 | 2025 | 2025 | 2025-03-01 | 31 | 11.3167 | 5.035 | 1.3683 | 5.7033 | 0.305 | 26.125 | 40.58 | 1.375 | 5.4917 | 100% |  |  | 100% |  |  | 84.52% | 84.76% | 20.08% | 1630250.5 | 1620200 | 4933 | 1615267 | 335.0909 | 6.9595 | 1909332.2581 | 81.87% | 23.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-03-02 | 2025 | 2025 | 2025-03-01 | 31 | 11.45 | 5.9533 | 1.6283 | 6.8967 | 0.33667 | 26.5 | 39.8933 | 2.805 | 6.6133 | 100% |  |  | 100% |  |  | 81.83% | 82.64% | 23.52% | 1908602 | 1895934 | 4800 | 1891134 | 335.0909 | 6.9595 | 1909332.2581 | 81.87% | 23.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-03-03 | 2025 | 2025 | 2025-03-01 | 31 | 11.5333 | 5.9883 | 1.6383 | 6.8633 | 0.35667 | 27.8833 | 38.52 | 6.2983 | 10.6383 | 100% |  |  | 100% |  |  | 82.21% | 82.3% | 23.51% | 1906184.6 | 1893466 | 2867 | 1890599 | 335.0909 | 6.9595 | 1909332.2581 | 81.87% | 23.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-03-04 | 2025 | 2025 | 2025-03-01 | 31 | 11.5667 | 6.7299 | 1.8952 | 7.744 | 0.41778 | 22.5729 | 33.8231 | 5.3376 | 9.5417 | 77.44% |  |  | 100% |  |  | 64.02% | 63.39% | 20.66% | 1676855.5 | 1663467 | 2133 | 1661334 | 335.0909 | 6.9595 | 1909332.2581 | 81.87% | 23.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-03-05 | 2025 | 2025 | 2025-03-01 | 31 | 11.7 | 6.5767 | 1.83 | 7.6067 | 0.37833 | 23.4233 | 38.43 | 1.9783 | 5.405 | 100% |  |  | 100% |  |  | 79.74% | 80.49% | 25.27% | 2049165.1 | 2034667 | 2200 | 2032467 | 335.0909 | 6.9595 | 1909332.2581 | 81.87% | 23.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-03-06 | 2025 | 2025 | 2025-03-01 | 31 | 11.7 | 6.4517 | 1.7583 | 7.3983 | 0.35167 | 28.7417 | 42.5667 | 3.06 | 6.25 | 100% |  |  | 100% |  |  | 80.35% | 82.12% | 24.77% | 2009831 | 1996533 | 4533 | 1992000 | 335.0909 | 6.9595 | 1909332.2581 | 81.87% | 23.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-03-07 | 2025 | 2025 | 2025-03-01 | 31 | 11.65 | 6.2733 | 1.705 | 7.16 | 0.35 | 30.9083 | 43.7767 | 3.1367 | 8.2317 | 100% |  |  | 100% |  |  | 80.99% | 83.29% | 24.16% | 1958916.8 | 1946334 | 3067 | 1943267 | 335.0909 | 6.9595 | 1909332.2581 | 81.87% | 23.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-03-08 | 2025 | 2025 | 2025-03-01 | 31 | 11.6833 | 6.3534 | 1.7211 | 7.2379 | 0.34701 | 31.2431 | 45.8638 | 2.3555 | 7.3681 | 99.94% |  |  | 100% |  |  | 80.56% | 83.35% | 24.3% | 1971776.8 | 1957667 | 3733 | 1953934 | 335.0909 | 6.9595 | 1909332.2581 | 81.87% | 23.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-03-09 | 2025 | 2025 | 2025-03-01 | 31 | 11.6833 | 6.205 | 1.7067 | 7.0433 | 0.34333 | 32.1317 | 46.13 | 1.7333 | 5.785 | 99.83% |  |  | 100% |  |  | 80.22% | 83.54% | 23.54% | 1909753.5 | 1896800 | 3467 | 1893333 | 335.0909 | 6.9595 | 1909332.2581 | 81.87% | 23.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-03-10 | 2025 | 2025 | 2025-03-01 | 31 | 11.55 | 6.1367 | 1.665 | 6.8417 | 0.35167 | 33.2317 | 48.62 | 1.7367 | 4.8717 | 99.9% |  |  | 100% |  |  | 79.44% | 82.74% | 22.65% | 1837765.5 | 1825733 | 4533 | 1821200 | 335.0909 | 6.9595 | 1909332.2581 | 81.87% | 23.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-03-11 | 2025 | 2025 | 2025-03-01 | 31 | 11.6167 | 6.1 | 1.6783 | 6.7783 | 0.37167 | 31.8333 | 45.9 | 2.2883 | 6.96 | 99.93% |  |  | 100% |  |  | 80.95% | 83.72% | 22.86% | 1855873.4 | 1843201 | 4534 | 1838667 | 335.0909 | 6.9595 | 1909332.2581 | 81.87% | 23.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-03-12 | 2025 | 2025 | 2025-03-01 | 31 | 11.6 | 5.9367 | 1.6283 | 6.6417 | 0.34167 | 32.15 | 46.5933 | 2.2167 | 6.455 | 99.85% |  |  | 100% |  |  | 81.95% | 84.65% | 22.68% | 1839622.2 | 1828400 | 4600 | 1823800 | 335.0909 | 6.9595 | 1909332.2581 | 81.87% | 23.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-03-13 | 2025 | 2025 | 2025-03-01 | 31 | 11.65 | 5.705 | 1.5717 | 6.3367 | 0.33167 | 31.6467 | 45.12 | 1.685 | 5.885 | 100% |  |  | 100% |  |  | 82.85% | 85.64% | 21.87% | 1775174.3 | 1763866 | 4733 | 1759133 | 335.0909 | 6.9595 | 1909332.2581 | 81.87% | 23.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-03-14 | 2025 | 2025 | 2025-03-01 | 31 | 11.7167 | 5.7319 | 1.5767 | 6.3201 | 0.35274 | 30.8881 | 43.8694 | 4.0422 | 11.1775 | 100% |  |  | 100% |  |  | 82.43% | 84.11% | 21.71% | 1761709.4 | 1750467 | 4733 | 1745734 | 335.0909 | 6.9595 | 1909332.2581 | 81.87% | 23.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-03-15 | 2025 | 2025 | 2025-03-01 | 31 | 11.8 | 6.185 | 1.7017 | 6.8583 | 0.37 | 27.7017 | 40.6633 | 3.11 | 7.815 | 99.97% |  |  | 100% |  |  | 81.74% | 83.12% | 23.36% | 1896217.8 | 1883267 | 4667 | 1878600 | 335.0909 | 6.9595 | 1909332.2581 | 81.87% | 23.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-03-16 | 2025 | 2025 | 2025-03-01 | 31 | 11.7833 | 6.045 | 1.665 | 6.6533 | 0.37 | 27.275 | 41.4 | 1.9817 | 5.87 | 99.99% |  |  | 100% |  |  | 82.2% | 83.51% | 22.79% | 1850114.7 | 1837267 | 4600 | 1832667 | 335.0909 | 6.9595 | 1909332.2581 | 81.87% | 23.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-03-17 | 2025 | 2025 | 2025-03-01 | 31 | 11.8833 | 6.8017 | 1.8667 | 7.5483 | 0.38667 | 28.1067 | 43.3767 | 1.515 | 5.8933 | 100% |  |  | 100% |  |  | 79.5% | 81.82% | 25% | 2029747.5 | 2015400 | 4533 | 2010867 | 335.0909 | 6.9595 | 1909332.2581 | 81.87% | 23.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-03-18 | 2025 | 2025 | 2025-03-01 | 31 | 11.8833 | 6.8233 | 1.8617 | 7.56 | 0.38167 | 29.45 | 45.5867 | 1.7783 | 6.025 | 100% |  |  | 100% |  |  | 79.46% | 82.07% | 25.03% | 2031633.2 | 2017472 | 4534 | 2012938 | 335.0909 | 6.9595 | 1909332.2581 | 81.87% | 23.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-03-19 | 2025 | 2025 | 2025-03-01 | 31 | 11.9167 | 6.7683 | 1.8583 | 7.47 | 0.385 | 30.495 | 45.7467 | 2.3183 | 7.22 | 100% |  |  | 100% |  |  | 79.86% | 82.4% | 24.86% | 2017475.1 | 2003595 | 4533 | 1999062 | 335.0909 | 6.9595 | 1909332.2581 | 81.87% | 23.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-03-20 | 2025 | 2025 | 2025-03-01 | 31 | 11.8833 | 6.3433 | 1.755 | 6.9 | 0.39667 | 30.275 | 46.0567 | 1.8683 | 6.3667 | 100% |  |  | 100% |  |  | 81.23% | 83.67% | 23.35% | 1894989.3 | 1881933 | 3733 | 1878200 | 335.0909 | 6.9595 | 1909332.2581 | 81.87% | 23.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-03-21 | 2025 | 2025 | 2025-03-01 | 31 | 11.9167 | 6.3532 | 1.7223 | 6.9509 | 0.37871 | 31.3201 | 45.422 | 1.7257 | 5.4975 | 95.27% |  |  | 100% |  |  | 77.74% | 80.22% | 22.51% | 1825175.5 | 1813734 | 3134 | 1810600 | 335.0909 | 6.9595 | 1909332.2581 | 81.87% | 23.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-03-22 | 2025 | 2025 | 2025-03-01 | 31 | 12.0167 | 7.068 | 1.8983 | 7.728 | 0.39667 | 33.1733 | 48.48 | 1.8467 | 6.5683 | 100% |  |  | 100% |  |  | 77.68% | 81.3% | 25.01% | 2027271.1 | 2014000 | 2466 | 2011534 | 335.0909 | 6.9595 | 1909332.2581 | 81.87% | 23.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-03-23 | 2025 | 2025 | 2025-03-01 | 31 | 11.9667 | 6.8883 | 1.8717 | 7.525 | 0.39333 | 33.0933 | 48.6767 | 1.645 | 6.2317 | 99.33% |  |  | 100% |  |  | 78.43% | 82.14% | 24.59% | 1995168 | 1982228 | 4567 | 1977661 | 335.0909 | 6.9595 | 1909332.2581 | 81.87% | 23.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-03-24 | 2025 | 2025 | 2025-03-01 | 31 | 11.9833 | 6.95 | 1.9 | 7.5833 | 0.40667 | 35.1683 | 49.0433 | 2.9183 | 7.3733 | 99.34% |  |  | 100% |  |  | 78.44% | 82.31% | 24.78% | 2010734 | 1997800 | 4600 | 1993200 | 335.0909 | 6.9595 | 1909332.2581 | 81.87% | 23.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-03-25 | 2025 | 2025 | 2025-03-01 | 31 | 12.0667 | 6.8133 | 1.8883 | 7.3833 | 0.41333 | 33.935 | 46.6433 | 4.9617 | 10.335 | 100% |  |  | 100% |  |  | 79.89% | 82.65% | 24.58% | 1994164 | 1981000 | 4500 | 1976500 | 335.0909 | 6.9595 | 1909332.2581 | 81.87% | 23.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-03-26 | 2025 | 2025 | 2025-03-01 | 31 | 12.1 | 6.8117 | 1.885 | 7.365 | 0.41667 | 32.3367 | 44.2633 | 7.1917 | 12.9217 | 100% |  |  | 100% |  |  | 80.28% | 81.67% | 24.64% | 1998789 | 1985600 | 4400 | 1981200 | 335.0909 | 6.9595 | 1909332.2581 | 81.87% | 23.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-03-27 | 2025 | 2025 | 2025-03-01 | 31 | 12.1167 | 7.2524 | 2.0264 | 7.8224 | 0.4688 | 29.2034 | 41.5555 | 5.2708 | 9.2433 | 100% |  |  | 100% |  |  | 78.48% | 80.02% | 25.58% | 2075996.9 | 2061640 | 4467 | 2057173 | 335.0909 | 6.9595 | 1909332.2581 | 81.87% | 23.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-03-28 | 2025 | 2025 | 2025-03-01 | 31 | 12.2167 | 7.5717 | 2.125 | 8.1633 | 0.49 | 26.7067 | 40.4133 | 2.3833 | 6.7033 | 100% |  |  | 100% |  |  | 77.28% | 79.19% | 26.29% | 2134476.1 | 2118733 | 4733 | 2114000 | 335.0909 | 6.9595 | 1909332.2581 | 81.87% | 23.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-03-29 | 2025 | 2025 | 2025-03-01 | 31 | 12.2 | 6.2681 | 1.7423 | 6.6469 | 0.45407 | 27.4226 | 37.8394 | 3.154 | 7.7831 | 100% |  |  | 100% |  |  | 83.39% | 84.22% | 23.1% | 1874005.5 | 1861267 | 3800 | 1857467 | 335.0909 | 6.9595 | 1909332.2581 | 81.87% | 23.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-03-30 | 2025 | 2025 | 2025-03-01 | 31 | 12.2833 | 7.505 | 2.08 | 8.055 | 0.45667 | 30.5467 | 46.51 | 1.2 | 4.505 | 100% |  |  | 100% |  |  | 77.6% | 80.85% | 26.05% | 2110656.8 | 2095667 | 1000 | 2094667 | 335.0909 | 6.9595 | 1909332.2581 | 81.87% | 23.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-03-31 | 2025 | 2025 | 2025-03-01 | 31 | 12.2833 | 7.4567 | 2.065 | 7.9783 | 0.44833 | 32.1133 | 48.1167 | 1.36 | 5.1917 | 100% |  |  | 99.67% |  |  | 77.69% | 82.05% | 25.83% | 2092910.7 | 2079000 | 2000 | 2077000 | 335.0909 | 6.9595 | 1909332.2581 | 81.87% | 23.74% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-04-01 | 2026 | 2025 | 2025-04-01 | 30 | 12.3167 | 7.3682 | 2.0415 | 7.86 | 0.44914 | 32.9295 | 48.2996 | 1.6888 | 5.8067 | 100% |  |  | 100% |  |  | 78.32% | 80.78% | 25.65% | 2110276.8 | 2067333 | 4467 | 2062866 | 335.0909 | 7.1967 | 1944729.7155 | 80.64% | 24.18% | 99.75% | 99.75% |  |  | 96.7% | 519917.22 | [5 empty] | 335.091
2025-04-02 | 2026 | 2025 | 2025-04-01 | 30 | 12.3 | 7.355 | 2.05 | 7.8217 | 0.46167 | 33.8683 | 48.02 | 2.2883 | 7.355 | 100% |  |  | 100% |  |  | 78.3% | 80.49% | 25.52% | 2070371.8 | 2056801 | 4466 | 2052335 | 335.0909 | 7.1967 | 1944729.7155 | 80.64% | 24.18% | 99.75% | 99.75% |  |  | 97.5% | 524218.5 | [5 empty] | 335.091
2025-04-03 | 2026 | 2025 | 2025-04-01 | 30 | 12.3 | 7.3208 | 2.0405 | 7.7725 | 0.46544 | 35.0972 | 49.2723 | 2.3305 | 7.7775 | 100% |  |  | 100% |  |  | 78.23% | 80.89% | 25.34% | 2055280 | 2041133 | 3600 | 2037533 | 335.0909 | 7.1967 | 1944729.7155 | 80.64% | 24.18% | 99.75% | 99.75% |  |  | 97.5% | 524218.5 | [5 empty] | 335.091
2025-04-04 | 2026 | 2025 | 2025-04-01 | 30 | 12.3333 | 7.0883 | 1.975 | 7.5167 | 0.47 | 32.895 | 44.97 | 3.1267 | 6.5433 | 100% |  |  | 100% |  |  | 80.14% | 81.58% | 25.1% | 2035769.3 | 2021667 | 3067 | 2018600 | 335.0909 | 7.1967 | 1944729.7155 | 80.64% | 24.18% | 99.75% | 99.75% |  |  | 97.8% | 525831.48 | [5 empty] | 335.091
2025-04-05 | 2026 | 2025 | 2025-04-01 | 30 | 12.35 | 6.9853 | 1.9424 | 7.3667 | 0.45993 | 35.1975 | 49.0118 | 2.9069 | 7.6481 | 100% |  |  | 100% |  |  | 79.84% | 81.85% | 24.51% | 1987718.7 | 1974400 | 3467 | 1970933 | 335.0909 | 7.1967 | 1944729.7155 | 80.64% | 24.18% | 99.75% | 99.75% |  |  | 97.5% | 524218.5 | [5 empty] | 335.091
2025-04-06 | 2026 | 2025 | 2025-04-01 | 30 | 12.35 | 7.3183 | 2.0333 | 7.7083 | 0.475 | 38.44 | 50.7933 | 3.5783 | 8.555 | 100% |  |  | 100% |  |  | 76.35% | 81.34% | 24.52% | 1989573.1 | 1976600 | 4466 | 1972134 | 335.0909 | 7.1967 | 1944729.7155 | 80.64% | 24.18% | 99.75% | 99.75% |  |  | 98% | 526906.8 | [5 empty] | 335.091
2025-04-07 | 2026 | 2025 | 2025-04-01 | 30 | 12.3167 | 7.1678 | 1.98 | 7.5302 | 0.45341 | 37.7475 | 53.2827 | 1.9382 | 6.5564 | 100% |  |  | 100% |  |  | 72.64% | 81.93% | 22.79% | 1847572.8 | 1837334 | 4534 | 1832800 | 335.0909 | 7.1967 | 1944729.7155 | 80.64% | 24.18% | 99.75% | 99.75% |  |  | 97.5% | 524218.5 | [5 empty] | 335.091
2025-04-08 | 2026 | 2025 | 2025-04-01 | 30 | 12.2833 | 7.1617 | 1.995 | 7.5033 | 0.475 | 39.2533 | 51.39 | 5.085 | 9.6033 | 100% |  |  | 100% |  |  | 78.94% | 81.59% | 24.68% | 2002346.7 | 1989266 | 4466 | 1984800 | 335.0909 | 7.1967 | 1944729.7155 | 80.64% | 24.18% | 99.75% | 99.75% |  |  | 97.8% | 525831.48 | [5 empty] | 335.091
2025-04-09 | 2026 | 2025 | 2025-04-01 | 30 | 12.35 | 7.1667 | 2.0033 | 7.4967 | 0.46833 | 37.935 | 50.6567 | 3.6633 | 9.0817 | 100% |  |  | 100% |  |  | 78.9% | 81.59% | 24.64% | 1998756.5 | 1985667 | 3734 | 1981933 | 335.0909 | 7.1967 | 1944729.7155 | 80.64% | 24.18% | 99.75% | 99.75% |  |  | 97.7% | 525293.82 | [5 empty] | 335.091
2025-04-10 | 2026 | 2025 | 2025-04-01 | 30 | 12.4667 | 7.1041 | 1.9679 | 7.404 | 0.48304 | 34.7988 | 47.9001 | 4.9062 | 11.2667 | 100% |  |  | 100% |  |  | 80.23% | 81.58% | 24.75% | 2008891.9 | 1995134 | 4533 | 1990601 | 335.0909 | 7.1967 | 1944729.7155 | 80.64% | 24.18% | 99.75% | 99.75% |  |  | 44.9% | 241409.34 | [5 empty] | 335.091
2025-04-11 | 2026 | 2025 | 2025-04-01 | 30 | 12.3333 | 6.1038 | 1.6961 | 6.3049 | 0.43847 | 33.909 | 45.2003 | 6.0412 | 11.3425 | 100% |  |  | 100% |  |  | 81.17% | 81.34% | 21.32% | 1730096.6 | 1719467 | 4600 | 1714867 | 335.0909 | 7.1967 | 1944729.7155 | 80.64% | 24.18% | 99.75% | 99.75% |  |  | 98.8% | 531208.08 | [5 empty] | 335.091
2025-04-12 | 2026 | 2025 | 2025-04-01 | 30 | 12.3667 | 7.1405 | 1.9711 | 7.4054 | 0.49011 | 34.0926 | 47.9667 | 4.9075 | 9.0358 | 100% |  |  | 100% |  |  | 77.13% | 79.94% | 23.8% | 1931231.1 | 1918533 | 4533 | 1914000 | 335.0909 | 7.1967 | 1944729.7155 | 80.64% | 24.18% | 99.75% | 99.75% |  |  | 98.2% | 527982.12 | [5 empty] | 335.091
2025-04-13 | 2026 | 2025 | 2025-04-01 | 30 | 12.4333 | 7.345 | 2.0217 | 7.6083 | 0.485 | 36.43 | 51.1767 | 3.3533 | 7.9483 | 100% |  |  | 100% |  |  | 78.58% | 81.28% | 24.91% | 2021702.5 | 2007800 | 4467 | 2003333 | 335.0909 | 7.1967 | 1944729.7155 | 80.64% | 24.18% | 99.75% | 99.75% |  |  | 97.8% | 525831.48 | [5 empty] | 335.091
2025-04-14 | 2026 | 2025 | 2025-04-01 | 30 | 12.4667 | 7.0833 | 1.96 | 7.3183 | 0.485 | 37.7967 | 54.6233 | 2.1967 | 6.8167 | 100% |  |  | 34.3% |  |  | 28.05% | 82.05% | 8.553% | 695047 | 692000 | 4133 | 687867 | 335.0909 | 7.1967 | 1944729.7155 | 80.64% | 24.18% | 99.75% | 99.75% |  |  | 98.5% | 529595.1 | [5 empty] | 335.091
2025-04-15 | 2026 | 2025 | 2025-04-01 | 30 | 12.5 | 7.0472 | 1.9566 | 7.2749 | 0.48994 | 38.9799 | 52.0633 | 2.4263 | 6.7928 | 93.17% |  |  | 100% |  |  | 74.57% | 77.64% | 22.6% | 1831071.4 | 1819867 | 1934 | 1817933 | 335.0909 | 7.1967 | 1944729.7155 | 80.64% | 24.18% | 99.75% | 99.75% |  |  | 98.7% | 530670.42 | [5 empty] | 335.091
2025-04-16 | 2026 | 2025 | 2025-04-01 | 30 | 12.55 | 6.8866 | 1.8899 | 7.0809 | 0.47331 | 38.0627 | 53.0765 | 2.2987 | 7.2506 | 99.97% |  |  | 100% |  |  | 79.96% | 82.97% | 23.59% | 1912076.8 | 1899867 | 2600 | 1897267 | 335.0909 | 7.1967 | 1944729.7155 | 80.64% | 24.18% | 99.75% | 99.75% |  |  | 98.2% | 527982.12 | [5 empty] | 335.091
2025-04-17 | 2026 | 2025 | 2025-04-01 | 30 | 12.5 | 7.2383 | 1.9883 | 7.4267 | 0.505 | 36.2883 | 50.6933 | 4.41 | 8.2017 | 100% |  |  | 100% |  |  | 79.94% | 81.54% | 24.74% | 2006709 | 1993800 | 4400 | 1989400 | 335.0909 | 7.1967 | 1944729.7155 | 80.64% | 24.18% | 99.75% | 99.75% |  |  | 97.2% | 522605.52 | [5 empty] | 335.091
2025-04-18 | 2026 | 2025 | 2025-04-01 | 30 | 12.4833 | 6.59 | 1.8583 | 6.7083 | 0.53167 | 37.5517 | 46.84 | 8.5433 | 15.2317 | 100% |  |  | 100% |  |  | 80.93% | 82.16% | 22.62% | 1833798.2 | 1823467 | 4266 | 1819201 | 335.0909 | 7.1967 | 1944729.7155 | 80.64% | 24.18% | 99.75% | 99.75% |  |  | 97.3% | 523143.18 | [5 empty] | 335.091
2025-04-19 | 2026 | 2025 | 2025-04-01 | 30 | 12.5667 | 6.9733 | 1.935 | 7.0833 | 0.56 | 34.0783 | 46.0333 | 6.3417 | 10.615 | 100% |  |  | 100% |  |  | 77.17% | 80.74% | 22.78% | 1847122.9 | 1836067 | 4334 | 1831733 | 335.0909 | 7.1967 | 1944729.7155 | 80.64% | 24.18% | 99.75% | 99.75% |  |  | 96.8% | 520454.88 | [5 empty] | 335.091
2025-04-20 | 2026 | 2025 | 2025-04-01 | 30 | 12.5 | 7.5817 | 2.115 | 7.755 | 0.57 | 35.0567 | 47.84 | 4.935 | 10.18 | 100% |  |  | 100% |  |  | 78.28% | 79.92% | 25.29% | 2052833.9 | 2038533 | 4400 | 2034133 | 335.0909 | 7.1967 | 1944729.7155 | 80.64% | 24.18% | 99.75% | 99.75% |  |  | 96.5% | 518841.9 | [5 empty] | 335.091
2025-04-21 | 2026 | 2025 | 2025-04-01 | 30 | 12.6667 | 7.7682 | 2.1558 | 7.9112 | 0.57441 | 35.2737 | 49.4692 | 3.0515 | 8.8894 | 100% |  |  | 100% |  |  | 78.19% | 80.7% | 25.77% | 2091974.5 | 2077267 | 4400 | 2072867 | 335.0909 | 7.1967 | 1944729.7155 | 80.64% | 24.18% | 99.75% | 99.75% |  |  | 97.2% | 522605.52 | [5 empty] | 335.091
2025-04-22 | 2026 | 2025 | 2025-04-01 | 30 | 12.8 | 8.1966 | 2.2812 | 8.318 | 0.59697 | 35.8228 | 47.6131 | 3.9243 | 8.2603 | 100% |  |  | 100% |  |  | 77.11% | 79.57% | 26.73% | 2169534.1 | 2153467 | 4133 | 2149334 | 335.0909 | 7.1967 | 1944729.7155 | 80.64% | 24.18% | 99.75% | 99.75% |  |  | 96% | 516153.6 | [5 empty] | 335.091
2025-04-23 | 2026 | 2025 | 2025-04-01 | 30 | 12.8667 | 7.9358 | 2.2098 | 8.0445 | 0.5771 | 37.1326 | 50.5966 | 3.0921 | 7.6717 | 100% |  |  | 100% |  |  | 77.95% | 80.84% | 26.13% | 2119554.2 | 2104533 | 3267 | 2101266 | 335.0909 | 7.1967 | 1944729.7155 | 80.64% | 24.18% | 99.75% | 99.75% |  |  | 96.8% | 520454.88 | [5 empty] | 335.091
2025-04-24 | 2026 | 2025 | 2025-04-01 | 30 | 12.7667 | 7.7888 | 2.1643 | 7.886 | 0.56618 | 37.955 | 50.9598 | 4.003 | 9.0506 | 100% |  |  | 100% |  |  | 78.67% | 81.54% | 25.85% | 2097488.8 | 2083267 | 4266 | 2079001 | 335.0909 | 7.1967 | 1944729.7155 | 80.64% | 24.18% | 99.75% | 99.75% |  |  | 97% | 521530.2 | [5 empty] | 335.091
2025-04-25 | 2026 | 2025 | 2025-04-01 | 30 | 12.7167 | 7.4628 | 2.0919 | 7.5451 | 0.56116 | 37.9196 | 50.2998 | 5.6082 | 10.5117 | 100% |  |  | 100% |  |  | 78.92% | 80.92% | 24.81% | 2012458.2 | 1998334 | 2934 | 1995400 | 335.0909 | 7.1967 | 1944729.7155 | 80.64% | 24.18% | 99.75% | 99.75% |  |  | 97.8% | 525831.48 | [5 empty] | 335.091
2025-04-26 | 2026 | 2025 | 2025-04-01 | 30 | 12.85 | 7.3283 | 2.0753 | 7.4105 | 0.57387 | 37.8814 | 51.3949 | 3.3847 | 7.0267 | 97.24% |  |  | 100% |  |  | 78.53% | 81.1% | 24.25% | 1966464.5 | 1953200 | 3266 | 1949934 | 335.0909 | 7.1967 | 1944729.7155 | 80.64% | 24.18% | 99.75% | 99.75% |  |  | 98.3% | 528519.78 | [5 empty] | 335.091
2025-04-27 | 2026 | 2025 | 2025-04-01 | 30 | 12.8 | 7.4802 | 2.1075 | 7.5411 | 0.56504 | 39.7153 | 53.0892 | 2.172 | 7.0489 | 100% |  |  | 100% |  |  | 79.47% | 83.33% | 24.97% | 2025932.1 | 2012600 | 4334 | 2008266 | 335.0909 | 7.1967 | 1944729.7155 | 80.64% | 24.18% | 99.75% | 99.75% |  |  | 97.8% | 525831.48 | [5 empty] | 335.091
2025-04-28 | 2026 | 2025 | 2025-04-01 | 30 | 12.85 | 7.4686 | 2.0594 | 7.5059 | 0.54854 | 39.3931 | 53.7486 | 2.6149 | 8.3669 | 100% |  |  | 100% |  |  | 79.2% | 82.66% | 24.77% | 2009060.2 | 1995867 | 3733 | 1992134 | 335.0909 | 7.1967 | 1944729.7155 | 80.64% | 24.18% | 99.75% | 99.75% |  |  | 97.3% | 523143.18 | [5 empty] | 335.091
2025-04-29 | 2026 | 2025 | 2025-04-01 | 30 | 12.8667 | 7.0138 | 1.9403 | 7.0088 | 0.53399 | 39.84 | 53.3667 | 2.1896 | 7.4592 | 99.98% |  |  | 100% |  |  | 79.69% | 83.07% | 23.27% | 1887754.9 | 1876000 | 4400 | 1871600 | 335.0909 | 7.1967 | 1944729.7155 | 80.64% | 24.18% | 99.75% | 99.75% |  |  | 99% | 532283.4 | [5 empty] | 335.091
2025-04-30 | 2026 | 2025 | 2025-04-01 | 30 | 12.7167 | 7.4099 | 2.0073 | 7.4222 | 0.55052 | 37.8181 | 52.7363 | 3.1875 | 7.1864 | 100% |  |  | 100% |  |  | 79.16% | 81.99% | 24.48% | 1986574.7 | 1973133 | 4467 | 1968666 | 335.0909 | 7.1967 | 1944729.7155 | 80.64% | 24.18% | 99.75% | 99.75% |  |  | 99.3% | 533896.38 | [5 empty] | 335.091
2025-05-01 | 2026 | 2025 | 2025-05-01 | 31 | 10.7833 | 6.4268 | 1.7973 | 6.461 | 0.4886 | 37.3699 | 52.6376 | 3.9696 | 8.5042 | 100% |  |  | 100% |  |  | 80.28% | 81.76% | 21.61% | 1755655.6 | 1743267 | 5133 | 1738134 | 335.0909 | 7.029 | 1925422.3809 | 81.75% | 23.94% | 99.75% | 99.75% |  |  | 97.2% | 522605.52 | [5 empty] | 335.091
2025-05-02 | 2026 | 2025 | 2025-05-01 | 31 | 12.7333 | 6.4696 | 1.6139 | 6.4665 | 0.49321 | 36.7571 | 49.6333 | 2.7713 | 7.1906 | 99.91% |  |  | 100% |  |  | 76.82% | 77.72% | 20.7% | 1677908.8 | 1668934 | 4267 | 1664667 | 335.0909 | 7.029 | 1925422.3809 | 81.75% | 23.94% | 99.75% | 99.75% |  |  | 98.8% | 531208.08 | [5 empty] | 335.091
2025-05-03 | 2026 | 2025 | 2025-05-01 | 31 | 12.75 | 6.9499 | 1.7395 | 6.9392 | 0.54524 | 37.6659 | 51.1521 | 4.0705 | 9.8011 | 99.48% |  |  | 100% |  |  | 76.86% | 77.79% | 22.22% | 1800994.4 | 1791600 | 4333 | 1787267 | 335.0909 | 7.029 | 1925422.3809 | 81.75% | 23.94% | 99.75% | 99.75% |  |  | 98.2% | 527982.12 | [5 empty] | 335.091
2025-05-04 | 2026 | 2025 | 2025-05-01 | 31 | 12.7667 | 6.8953 | 1.5199 | 6.8662 | 0.42237 | 30.5882 | 43.5307 | 4.0959 | 7.835 | 99.98% |  |  | 100% |  |  | 82.84% | 81.95% | 23.7% | 1923381.7 | 1910467 | 4400 | 1906067 | 335.0909 | 7.029 | 1925422.3809 | 81.75% | 23.94% | 99.75% | 99.75% |  |  | 97.8% | 525831.48 | [5 empty] | 335.091
2025-05-05 | 2026 | 2025 | 2025-05-01 | 31 | 11.75 | 5.3612 | 1.0657 | 5.3148 | 0.35699 | 28.0147 | 41.8399 | 3.4096 | 7.7889 | 90.06% |  |  | 63.62% |  |  | 51.65% | 76.76% | 11.44% | 929392.9 | 924466 | 4533 | 919933 | 335.0909 | 7.029 | 1925422.3809 | 81.75% | 23.94% | 99.75% | 99.75% |  |  | 0% | 0 | [5 empty] | 335.091
2025-05-06 | 2026 | 2025 | 2025-05-01 | 31 | 12.8667 | 5.0157 | 1.1329 | 4.9428 | 0.33104 | 28.6376 | 37.1307 | 3.9348 | 9.4236 | 100% |  |  | 100% |  |  | 85.33% | 82.82% | 17.57% | 1427314.3 | 1417934 | 4600 | 1413334 | 335.0909 | 7.029 | 1925422.3809 | 81.75% | 23.94% | 99.75% | 99.75% |  |  | 97.2% | 522605.52 | [5 empty] | 335.091
2025-05-07 | 2026 | 2025 | 2025-05-01 | 31 | 12.9333 | 7.2198 | 1.679 | 7.177 | 0.48925 | 30.4753 | 46.1028 | 1.7831 | 5.3122 | 99.88% |  |  | 100% |  |  | 82.58% | 82.39% | 24.69% | 2004778.5 | 1990533 | 4534 | 1985999 | 335.0909 | 7.029 | 1925422.3809 | 81.75% | 23.94% | 99.75% | 99.75% |  |  | 97.3% | 523143.18 | [5 empty] | 335.091
2025-05-08 | 2026 | 2025 | 2025-05-01 | 31 | 12.8167 | 6.8692 | 1.6573 | 6.7823 | 0.48944 | 33.4444 | 48.9806 | 2.5852 | 6.1244 | 99.96% |  |  | 100% |  |  | 82.13% | 82.5% | 23.21% | 1883342.1 | 1870867 | 4400 | 1866467 | 335.0909 | 7.029 | 1925422.3809 | 81.75% | 23.94% | 99.75% | 99.75% |  |  | 96.7% | 519917.22 | [5 empty] | 335.091
2025-05-09 | 2026 | 2025 | 2025-05-01 | 31 | 12.55 | 6.5408 | 1.4165 | 6.491 | 0.43747 | 30.2177 | 41.2974 | 3.5894 | 6.8692 | 99.98% |  |  | 100% |  |  | 85.09% | 83.85% | 23.01% | 1867148.5 | 1855267 | 4400 | 1850867 | 335.0909 | 7.029 | 1925422.3809 | 81.75% | 23.94% | 99.75% | 99.75% |  |  | 0% | 0 | [5 empty] | 335.091
2025-05-10 | 2026 | 2025 | 2025-05-01 | 31 | 12.9333 | 7.3742 | 1.707 | 7.2589 | 0.50724 | 33.9058 | 48.3724 | 1.6492 | 4.605 | 100% |  |  | 100% |  |  | 82.13% | 82.89% | 24.84% | 2015493.1 | 2002067 | 4266 | 1997801 | 335.0909 | 7.029 | 1925422.3809 | 81.75% | 23.94% | 99.75% | 99.75% |  |  | 97.5% | 524218.5 | [5 empty] | 335.091
2025-05-11 | 2026 | 2025 | 2025-05-01 | 31 | 12.9833 | 7.3227 | 1.7251 | 7.1937 | 0.51803 | 36.3631 | 50.9 | 2.5087 | 6.6117 | 100% |  |  | 100% |  |  | 81.75% | 83.09% | 24.5% | 1987766.4 | 1975000 | 4400 | 1970600 | 335.0909 | 7.029 | 1925422.3809 | 81.75% | 23.94% | 99.75% | 99.75% |  |  | 92.2% | 495722.52 | [5 empty] | 335.091
2025-05-12 | 2026 | 2025 | 2025-05-01 | 31 | 12.9333 | 7.5711 | 1.8065 | 7.4236 | 0.56016 | 35.9432 | 49.0333 | 5.1807 | 9.6958 | 100% |  |  | 95.89% |  |  | 77.65% | 81.32% | 24.02% | 1947041 | 1935867 | 4200 | 1931667 | 335.0909 | 7.029 | 1925422.3809 | 81.75% | 23.94% | 99.75% | 99.75% |  |  | 97% | 521530.2 | [5 empty] | 335.091
2025-05-13 | 2026 | 2025 | 2025-05-01 | 31 | 13.0333 | 7.55 | 1.825 | 7.3767 | 0.575 | 36.56 | 49 | 5.4167 | 9.9483 | 100% |  |  | 98.21% |  |  | 80.29% | 82.1% | 24.68% | 2002101.2 | 1989000 | 4267 | 1984733 | 335.0909 | 7.029 | 1925422.3809 | 81.75% | 23.94% | 99.75% | 99.75% |  |  | 98.2% | 527982.12 | [5 empty] | 335.091
2025-05-14 | 2026 | 2025 | 2025-05-01 | 31 | 13.0167 | 7.7465 | 1.8772 | 7.5534 | 0.57924 | 36.4541 | 49.7172 | 4.7974 | 8.575 | 99.67% |  |  | 100% |  |  | 81.11% | 81.83% | 25.53% | 2071281.2 | 2057133 | 4267 | 2052866 | 335.0909 | 7.029 | 1925422.3809 | 81.75% | 23.94% | 99.75% | 99.75% |  |  | 98.3% | 528519.78 | [5 empty] | 335.091
2025-05-15 | 2026 | 2025 | 2025-05-01 | 31 | 13.0167 | 7.7404 | 1.8814 | 7.5316 | 0.58079 | 37.942 | 51.8333 | 3.4626 | 7.7442 | 100% |  |  | 100% |  |  | 80.97% | 82.47% | 25.41% | 2061967.6 | 2048001 | 4466 | 2043535 | 335.0909 | 7.029 | 1925422.3809 | 81.75% | 23.94% | 99.75% | 99.75% |  |  | 97.7% | 525293.82 | [5 empty] | 335.091
2025-05-16 | 2026 | 2025 | 2025-05-01 | 31 | 12.9833 | 7.6801 | 1.8775 | 7.4746 | 0.58758 | 38.5255 | 50.8667 | 5.6426 | 9.7214 | 100% |  |  | 100% |  |  | 81.25% | 82.17% | 25.3% | 2054238.2 | 2039466 | 4467 | 2034999 | 335.0909 | 7.029 | 1925422.3809 | 81.75% | 23.94% | 99.75% | 99.75% |  |  | 97.3% | 523143.18 | [5 empty] | 335.091
2025-05-17 | 2026 | 2025 | 2025-05-01 | 31 | 13.0667 | 7.7788 | 1.9086 | 7.5421 | 0.60485 | 36.5468 | 49.3539 | 5.5106 | 10.2397 | 100% |  |  | 100% |  |  | 81.7% | 81.92% | 25.67% | 2083076.1 | 2069001 | 4200 | 2064801 | 335.0909 | 7.029 | 1925422.3809 | 81.75% | 23.94% | 99.75% | 99.75% |  |  | 97.3% | 523143.18 | [5 empty] | 335.091
2025-05-18 | 2026 | 2025 | 2025-05-01 | 31 | 13.05 | 7.6475 | 1.881 | 7.4243 | 0.60221 | 36.9627 | 48.9667 | 6.9162 | 11.3542 | 99.94% |  |  | 97.95% |  |  | 80.05% | 81.74% | 24.76% | 2008375.2 | 1995600 | 4200 | 1991400 | 335.0909 | 7.029 | 1925422.3809 | 81.75% | 23.94% | 99.75% | 99.75% |  |  | 97% | 521530.2 | [5 empty] | 335.091
2025-05-19 | 2026 | 2025 | 2025-05-01 | 31 | 13.1 | 7.7156 | 1.9198 | 7.486 | 0.61425 | 38.3833 | 49.9333 | 7.1013 | 11.17 | 99.93% |  |  | 95.74% |  |  | 78.14% | 82.09% | 24.37% | 1976817.1 | 1964266 | 4133 | 1960133 | 335.0909 | 7.029 | 1925422.3809 | 81.75% | 23.94% | 99.75% | 99.75% |  |  | 96.5% | 518841.9 | [5 empty] | 335.091
2025-05-20 | 2026 | 2025 | 2025-05-01 | 31 | 13.1 | 7.6206 | 1.9095 | 7.4144 | 0.61975 | 38.4285 | 50.2667 | 5.3515 | 9.1192 | 99.87% |  |  | 100% |  |  | 81.61% | 82.65% | 25.21% | 2045266.7 | 2031734 | 4067 | 2027667 | 335.0909 | 7.029 | 1925422.3809 | 81.75% | 23.94% | 99.75% | 99.75% |  |  | 98.3% | 528519.78 | [5 empty] | 335.091
2025-05-21 | 2026 | 2025 | 2025-05-01 | 31 | 13.1 | 7.886 | 1.9616 | 7.6853 | 0.62506 | 38.3847 | 50.7993 | 5.8698 | 9.7883 | 99.87% |  |  | 100% |  |  | 80.01% | 80.87% | 25.62% | 2078810 | 2064333 | 3933 | 2060400 | 335.0909 | 7.029 | 1925422.3809 | 81.75% | 23.94% | 99.75% | 99.75% |  |  | 96.3% | 517766.58 | [5 empty] | 335.091
2025-05-22 | 2026 | 2025 | 2025-05-01 | 31 | 13.1 | 7.7806 | 1.9502 | 7.5802 | 0.62713 | 39.0723 | 51.4761 | 5.3906 | 9.2803 | 99.03% |  |  | 100% |  |  | 79.69% | 80.81% | 25.17% | 2042430.3 | 2028201 | 4067 | 2024134 | 335.0909 | 7.029 | 1925422.3809 | 81.75% | 23.94% | 99.75% | 99.75% |  |  | 97.2% | 522605.52 | [5 empty] | 335.091
2025-05-23 | 2026 | 2025 | 2025-05-01 | 31 | 13.1333 | 7.8035 | 2.0035 | 7.5878 | 0.63625 | 40.6811 | 51.3 | 5.8927 | 10.8447 | 99.86% |  |  | 97.84% |  |  | 78.19% | 81.34% | 24.72% | 2004758.4 | 1992266 | 4200 | 1988066 | 335.0909 | 7.029 | 1925422.3809 | 81.75% | 23.94% | 99.75% | 99.75% |  |  | 97% | 521530.2 | [5 empty] | 335.091
2025-05-24 | 2026 | 2025 | 2025-05-01 | 31 | 13.1 | 7.4694 | 1.9135 | 7.2808 | 0.58669 | 39.0592 | 51.5 | 3.8841 | 13.663 | 99.9% |  |  | 100% |  |  | 80.63% | 82.91% | 24.46% | 1984633.2 | 1971467 | 4333 | 1967134 | 335.0909 | 7.029 | 1925422.3809 | 81.75% | 23.94% | 99.75% | 99.75% |  |  | 99% | 532283.4 | [5 empty] | 335.091
2025-05-25 | 2026 | 2025 | 2025-05-01 | 31 | 12.4333 | 5.014 | 1.3226 | 5.002 | 0.48303 | 38.6377 | 48.588 | 2.5415 | 5.7883 | 99.9% |  |  | 100% |  |  | 72.35% | 73.02% | 15.08% | 1220637.4 | 1216934 | 4334 | 1212600 | 335.0909 | 7.029 | 1925422.3809 | 81.75% | 23.94% | 99.75% | 99.75% |  |  | 99% | 532283.4 | [5 empty] | 335.091
2025-05-26 | 2026 | 2025 | 2025-05-01 | 31 | 12.9 | 6.2862 | 1.6196 | 6.1647 | 0.57746 | 37.9836 | 48.0169 | 3.3665 | 7.0992 | 100% |  |  | 100% |  |  | 78.76% | 79.37% | 20.23% | 1639580.9 | 1631000 | 4066 | 1626934 | 335.0909 | 7.029 | 1925422.3809 | 81.75% | 23.94% | 99.75% | 99.75% |  |  | 97.8% | 525831.48 | [5 empty] | 335.091
2025-05-27 | 2026 | 2025 | 2025-05-01 | 31 | 13.0667 | 6.6237 | 1.6955 | 6.4502 | 0.57575 | 39.8314 | 51.5089 | 2.0373 | 5.9403 | 100% |  |  | 100% |  |  | 80.51% | 82.25% | 21.64% | 1754549.5 | 1744400 | 4267 | 1740133 | 335.0909 | 7.029 | 1925422.3809 | 81.75% | 23.94% | 99.75% | 99.75% |  |  | 97.3% | 523143.18 | [5 empty] | 335.091
2025-05-28 | 2026 | 2025 | 2025-05-01 | 31 | 13.1667 | 6.1294 | 1.4289 | 5.9413 | 0.4854 | 37.2974 | 49.8333 | 2.6743 | 6.4825 | 99.94% |  |  | 100% |  |  | 81.43% | 81.96% | 20.16% | 1634051.2 | 1625533 | 4267 | 1621266 | 335.0909 | 7.029 | 1925422.3809 | 81.75% | 23.94% | 99.75% | 99.75% |  |  | 98% | 526906.8 | [5 empty] | 335.091
2025-05-29 | 2026 | 2025 | 2025-05-01 | 31 | 13.0333 | 6.2537 | 1.4974 | 6.1086 | 0.48814 | 34.0235 | 45.2784 | 4.5282 | 11.1658 | 99.97% |  |  | 100% |  |  | 81.27% | 80.9% | 20.69% | 1678762.3 | 1667934 | 4333 | 1663601 | 335.0909 | 7.029 | 1925422.3809 | 81.75% | 23.94% | 99.75% | 99.75% |  |  | 98.2% | 527982.12 | [5 empty] | 335.091
2025-05-30 | 2026 | 2025 | 2025-05-01 | 31 | 13.1167 | 7.3909 | 1.7842 | 7.1232 | 0.5794 | 35.8824 | 48.8486 | 4.3586 | 8.5197 | 99.97% |  |  | 100% |  |  | 81.6% | 82.09% | 24.22% | 1964991.7 | 1951933 | 4267 | 1947666 | 335.0909 | 7.029 | 1925422.3809 | 81.75% | 23.94% | 99.75% | 99.75% |  |  | 97.3% | 523143.18 | [5 empty] | 335.091
2025-05-31 | 2026 | 2025 | 2025-05-01 | 31 | 13.1333 | 7.07 | 1.7518 | 6.8522 | 0.58985 | 35.6025 | 46.5667 | 6.7605 | 11.2175 | 99.99% |  |  | 97.98% |  |  | 80.87% | 81.97% | 23.09% | 1871744.9 | 1861067 | 4266 | 1856801 | 335.0909 | 7.029 | 1925422.3809 | 81.75% | 23.94% | 99.75% | 99.75% |  |  | 97.3% | 523143.18 | [5 empty] | 335.091
2025-06-01 | 2026 | 2025 | 2025-06-01 | 30 | 12.9 | 6.8304 | 1.6837 | 6.6376 | 0.56648 | 34.1991 | 47.0323 | 5.0827 | 10.0053 | 100% |  |  | 88.92% |  |  | 70.74% | 79.18% | 19.56% | 1584800.6 | 1576734 | 3400 | 1573334 | 335.0909 | 6.4267 | 1787188.53 | 82.99% | 22.22% | 99.75% | 99.75% |  |  | 97.7% | 525293.82 | [5 empty] | 335.091
2025-06-02 | 2026 | 2025 | 2025-06-01 | 30 | 13.15 | 7.3711 | 1.8092 | 7.1023 | 0.60623 | 34.7139 | 47.4076 | 5.5028 | 10.11 | 100% |  |  | 97.8% |  |  | 80.54% | 81.83% | 23.83% | 1931233.6 | 1919800 | 3067 | 1916733 | 335.0909 | 6.4267 | 1787188.53 | 82.99% | 22.22% | 99.75% | 99.75% |  |  | 96.7% | 519917.22 | [5 empty] | 335.091
2025-06-03 | 2026 | 2025 | 2025-06-01 | 30 | 13.1667 | 7.0838 | 1.792 | 6.859 | 0.62038 | 34.7738 | 46.1612 | 5.9517 | 10.8147 | 100% |  |  | 98.45% |  |  | 82.36% | 83.2% | 23.54% | 1907785.6 | 1897200 | 4133 | 1893067 | 335.0909 | 6.4267 | 1787188.53 | 82.99% | 22.22% | 99.75% | 99.75% |  |  | 98% | 526906.8 | [5 empty] | 335.091
2025-06-04 | 2026 | 2025 | 2025-06-01 | 30 | 13.1333 | 7.3755 | 1.8698 | 7.1147 | 0.63905 | 34.9 | 48.0729 | 4.734 | 8.9947 | 100% |  |  | 94.13% |  |  | 76.94% | 81.76% | 22.81% | 1847400.8 | 1838467 | 4267 | 1834200 | 335.0909 | 6.4267 | 1787188.53 | 82.99% | 22.22% | 99.75% | 99.75% |  |  | 97.2% | 522605.52 | [5 empty] | 335.091
2025-06-05 | 2026 | 2025 | 2025-06-01 | 30 | 13.1833 | 7.534 | 1.8883 | 7.2576 | 0.62868 | 35.3935 | 48.3452 | 4.5916 | 9.3128 | 100% |  |  | 100% |  |  | 82.09% | 81.92% | 24.82% | 2012506.2 | 2000533 | 4200 | 1996333 | 335.0909 | 6.4267 | 1787188.53 | 82.99% | 22.22% | 99.75% | 99.75% |  |  | 97.5% | 524218.5 | [5 empty] | 335.091
2025-06-06 | 2026 | 2025 | 2025-06-01 | 30 | 13.2 | 7.7514 | 1.9621 | 7.4528 | 0.65701 | 37.0938 | 48.4667 | 6.1669 | 10.2025 | 99.29% |  |  | 100% |  |  | 81.09% | 81.52% | 25.18% | 2042243.5 | 2029200 | 4000 | 2025200 | 335.0909 | 6.4267 | 1787188.53 | 82.99% | 22.22% | 99.75% | 99.75% |  |  | 97.2% | 522605.52 | [5 empty] | 335.091
2025-06-07 | 2026 | 2025 | 2025-06-01 | 30 | 13.2833 | 7.8456 | 1.9813 | 7.5082 | 0.66022 | 37.3718 | 50.5794 | 4.7304 | 7.9256 | 99.98% |  |  | 100% |  |  | 80.92% | 81.99% | 25.32% | 2052991 | 2040001 | 4067 | 2035934 | 335.0909 | 6.4267 | 1787188.53 | 82.99% | 22.22% | 99.75% | 99.75% |  |  | 97.8% | 525831.48 | [5 empty] | 335.091
2025-06-08 | 2026 | 2025 | 2025-06-01 | 30 | 13.25 | 7.9717 | 2.0471 | 7.6321 | 0.68568 | 38.6367 | 50.1 | 5.6953 | 11.0475 | 100% |  |  | 98.59% |  |  | 80.27% | 82.79% | 25.53% | 2070280 | 2057000 | 4133 | 2052867 | 335.0909 | 6.4267 | 1787188.53 | 82.99% | 22.22% | 99.75% | 99.75% |  |  | 98.7% | 530670.42 | [5 empty] | 335.091
2025-06-09 | 2026 | 2025 | 2025-06-01 | 30 | 13.2667 | 7.9095 | 2.0288 | 7.5627 | 0.68315 | 38.0497 | 49.9153 | 5.9233 | 9.2714 | 100% |  |  | 100% |  |  | 81.35% | 82.24% | 25.63% | 2078951.4 | 2065867 | 4333 | 2061534 | 335.0909 | 6.4267 | 1787188.53 | 82.99% | 22.22% | 99.75% | 99.75% |  |  | 97.7% | 525293.82 | [5 empty] | 335.091
2025-06-10 | 2026 | 2025 | 2025-06-01 | 30 | 13.2667 | 6.6372 | 2.0114 | 7.5232 | 0.67425 | 37.284 | 49.5 | 5.6889 | 9.3992 | 100% |  |  | 100% |  |  | 81.37% | 82.27% | 25.51% | 2068251.7 | 2055466 | 4200 | 2051266 | 335.0909 | 6.4267 | 1787188.53 | 82.99% | 22.22% | 99.75% | 99.75% |  |  | 97.7% | 525293.82 | [5 empty] | 335.091
2025-06-11 | 2026 | 2025 | 2025-06-01 | 30 | 13.3167 | 8.1249 | 2.0945 | 7.6959 | 0.67526 | 36.8171 | 50.0677 | 5.3507 | 8.8633 | 99.54% |  |  | 100% |  |  | 80.93% | 81.64% | 25.95% | 2105370.2 | 2091267 | 4134 | 2087133 | 335.0909 | 6.4267 | 1787188.53 | 82.99% | 22.22% | 99.75% | 99.75% |  |  | 98.5% | 529595.1 | [5 empty] | 335.091
2025-06-12 | 2026 | 2025 | 2025-06-01 | 30 | 13.2833 | 8.0232 | 2.0797 | 7.5981 | 0.6603 | 37.0591 | 52.412 | 3.6317 | 6.8662 | 100% |  |  | 95.13% |  |  | 78.17% | 83.5% | 24.75% | 2005872.4 | 1994467 | 4133 | 1990334 | 335.0909 | 6.4267 | 1787188.53 | 82.99% | 22.22% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-06-13 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 6.4267 | 1787188.53 | 82.99% | 22.22% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-06-14 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 6.4267 | 1787188.53 | 82.99% | 22.22% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-06-15 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 6.4267 | 1787188.53 | 82.99% | 22.22% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-06-16 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 6.4267 | 1787188.53 | 82.99% | 22.22% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-06-17 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 6.4267 | 1787188.53 | 82.99% | 22.22% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-06-18 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 6.4267 | 1787188.53 | 82.99% | 22.22% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-06-19 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 6.4267 | 1787188.53 | 82.99% | 22.22% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-06-20 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 6.4267 | 1787188.53 | 82.99% | 22.22% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-06-21 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 6.4267 | 1787188.53 | 82.99% | 22.22% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-06-22 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 6.4267 | 1787188.53 | 82.99% | 22.22% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-06-23 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 6.4267 | 1787188.53 | 82.99% | 22.22% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-06-24 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 6.4267 | 1787188.53 | 82.99% | 22.22% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-06-25 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 6.4267 | 1787188.53 | 82.99% | 22.22% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-06-26 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 6.4267 | 1787188.53 | 82.99% | 22.22% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-06-27 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 6.4267 | 1787188.53 | 82.99% | 22.22% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-06-28 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 6.4267 | 1787188.53 | 82.99% | 22.22% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-06-29 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 6.4267 | 1787188.53 | 82.99% | 22.22% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-06-30 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 6.4267 | 1787188.53 | 82.99% | 22.22% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-07-01 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 5.4484 | 1533620.9517 | 84% | 19.07% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-07-02 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 5.4484 | 1533620.9517 | 84% | 19.07% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-07-03 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 5.4484 | 1533620.9517 | 84% | 19.07% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-07-04 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 5.4484 | 1533620.9517 | 84% | 19.07% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-07-05 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 5.4484 | 1533620.9517 | 84% | 19.07% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-07-06 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 5.4484 | 1533620.9517 | 84% | 19.07% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-07-07 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 5.4484 | 1533620.9517 | 84% | 19.07% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-07-08 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 5.4484 | 1533620.9517 | 84% | 19.07% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-07-09 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 5.4484 | 1533620.9517 | 84% | 19.07% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-07-10 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 5.4484 | 1533620.9517 | 84% | 19.07% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-07-11 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 5.4484 | 1533620.9517 | 84% | 19.07% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-07-12 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 5.4484 | 1533620.9517 | 84% | 19.07% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-07-13 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 5.4484 | 1533620.9517 | 84% | 19.07% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-07-14 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 5.4484 | 1533620.9517 | 84% | 19.07% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-07-15 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 5.4484 | 1533620.9517 | 84% | 19.07% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-07-16 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 5.4484 | 1533620.9517 | 84% | 19.07% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-07-17 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 5.4484 | 1533620.9517 | 84% | 19.07% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-07-18 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 5.4484 | 1533620.9517 | 84% | 19.07% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-07-19 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 5.4484 | 1533620.9517 | 84% | 19.07% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-07-20 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 5.4484 | 1533620.9517 | 84% | 19.07% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-07-21 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 5.4484 | 1533620.9517 | 84% | 19.07% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-07-22 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 5.4484 | 1533620.9517 | 84% | 19.07% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-07-23 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 5.4484 | 1533620.9517 | 84% | 19.07% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-07-24 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 5.4484 | 1533620.9517 | 84% | 19.07% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-07-25 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 5.4484 | 1533620.9517 | 84% | 19.07% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-07-26 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 5.4484 | 1533620.9517 | 84% | 19.07% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-07-27 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 5.4484 | 1533620.9517 | 84% | 19.07% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-07-28 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 5.4484 | 1533620.9517 | 84% | 19.07% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-07-29 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 5.4484 | 1533620.9517 | 84% | 19.07% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-07-30 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 5.4484 | 1533620.9517 | 84% | 19.07% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-07-31 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 5.4484 | 1533620.9517 | 84% | 19.07% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-08-01 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 5.6194 | 1561332.288 | 82.92% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-08-02 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 5.6194 | 1561332.288 | 82.92% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-08-03 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 5.6194 | 1561332.288 | 82.92% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-08-04 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 5.6194 | 1561332.288 | 82.92% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-08-05 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 5.6194 | 1561332.288 | 82.92% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-08-06 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 5.6194 | 1561332.288 | 82.92% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-08-07 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 5.6194 | 1561332.288 | 82.92% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-08-08 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 5.6194 | 1561332.288 | 82.92% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-08-09 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 5.6194 | 1561332.288 | 82.92% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-08-10 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 5.6194 | 1561332.288 | 82.92% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-08-11 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 5.6194 | 1561332.288 | 82.92% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-08-12 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 5.6194 | 1561332.288 | 82.92% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-08-13 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 5.6194 | 1561332.288 | 82.92% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-08-14 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 5.6194 | 1561332.288 | 82.92% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-08-15 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 5.6194 | 1561332.288 | 82.92% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-08-16 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 5.6194 | 1561332.288 | 82.92% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-08-17 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 5.6194 | 1561332.288 | 82.92% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-08-18 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 5.6194 | 1561332.288 | 82.92% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-08-19 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 5.6194 | 1561332.288 | 82.92% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-08-20 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 5.6194 | 1561332.288 | 82.92% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-08-21 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 5.6194 | 1561332.288 | 82.92% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-08-22 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 5.6194 | 1561332.288 | 82.92% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-08-23 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 5.6194 | 1561332.288 | 82.92% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-08-24 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 5.6194 | 1561332.288 | 82.92% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-08-25 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 5.6194 | 1561332.288 | 82.92% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-08-26 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 5.6194 | 1561332.288 | 82.92% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-08-27 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 5.6194 | 1561332.288 | 82.92% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-08-28 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 5.6194 | 1561332.288 | 82.92% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-08-29 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 5.6194 | 1561332.288 | 82.92% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-08-30 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 5.6194 | 1561332.288 | 82.92% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-08-31 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 5.6194 | 1561332.288 | 82.92% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-09-01 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 6.4033 | 1755680.2929 | 81.82% | 21.83% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-09-02 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 6.4033 | 1755680.2929 | 81.82% | 21.83% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-09-03 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 6.4033 | 1755680.2929 | 81.82% | 21.83% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-09-04 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 6.4033 | 1755680.2929 | 81.82% | 21.83% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-09-05 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 6.4033 | 1755680.2929 | 81.82% | 21.83% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-09-06 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 6.4033 | 1755680.2929 | 81.82% | 21.83% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-09-07 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 6.4033 | 1755680.2929 | 81.82% | 21.83% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-09-08 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 6.4033 | 1755680.2929 | 81.82% | 21.83% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-09-09 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 6.4033 | 1755680.2929 | 81.82% | 21.83% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-09-10 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 6.4033 | 1755680.2929 | 81.82% | 21.83% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-09-11 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 6.4033 | 1755680.2929 | 81.82% | 21.83% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-09-12 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 6.4033 | 1755680.2929 | 81.82% | 21.83% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-09-13 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 6.4033 | 1755680.2929 | 81.82% | 21.83% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-09-14 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 6.4033 | 1755680.2929 | 81.82% | 21.83% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-09-15 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 6.4033 | 1755680.2929 | 81.82% | 21.83% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-09-16 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 6.4033 | 1755680.2929 | 81.82% | 21.83% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-09-17 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 6.4033 | 1755680.2929 | 81.82% | 21.83% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-09-18 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 6.4033 | 1755680.2929 | 81.82% | 21.83% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-09-19 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 6.4033 | 1755680.2929 | 81.82% | 21.83% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-09-20 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 6.4033 | 1755680.2929 | 81.82% | 21.83% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-09-21 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 6.4033 | 1755680.2929 | 81.82% | 21.83% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-09-22 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 6.4033 | 1755680.2929 | 81.82% | 21.83% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-09-23 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 6.4033 | 1755680.2929 | 81.82% | 21.83% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-09-24 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 6.4033 | 1755680.2929 | 81.82% | 21.83% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-09-25 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 6.4033 | 1755680.2929 | 81.82% | 21.83% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-09-26 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 6.4033 | 1755680.2929 | 81.82% | 21.83% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-09-27 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 6.4033 | 1755680.2929 | 81.82% | 21.83% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-09-28 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 6.4033 | 1755680.2929 | 81.82% | 21.83% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-09-29 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 6.4033 | 1755680.2929 | 81.82% | 21.83% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-09-30 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 6.4033 | 1755680.2929 | 81.82% | 21.83% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-10-01 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.5258 | 1782585.5948 | 81.52% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-10-02 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.5258 | 1782585.5948 | 81.52% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-10-03 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.5258 | 1782585.5948 | 81.52% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-10-04 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.5258 | 1782585.5948 | 81.52% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-10-05 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.5258 | 1782585.5948 | 81.52% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-10-06 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.5258 | 1782585.5948 | 81.52% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-10-07 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.5258 | 1782585.5948 | 81.52% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-10-08 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.5258 | 1782585.5948 | 81.52% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-10-09 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.5258 | 1782585.5948 | 81.52% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-10-10 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.5258 | 1782585.5948 | 81.52% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-10-11 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.5258 | 1782585.5948 | 81.52% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-10-12 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.5258 | 1782585.5948 | 81.52% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-10-13 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.5258 | 1782585.5948 | 81.52% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-10-14 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.5258 | 1782585.5948 | 81.52% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-10-15 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.5258 | 1782585.5948 | 81.52% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-10-16 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.5258 | 1782585.5948 | 81.52% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-10-17 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.5258 | 1782585.5948 | 81.52% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-10-18 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.5258 | 1782585.5948 | 81.52% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-10-19 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.5258 | 1782585.5948 | 81.52% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-10-20 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.5258 | 1782585.5948 | 81.52% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-10-21 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.5258 | 1782585.5948 | 81.52% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-10-22 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.5258 | 1782585.5948 | 81.52% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-10-23 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.5258 | 1782585.5948 | 81.52% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-10-24 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.5258 | 1782585.5948 | 81.52% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-10-25 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.5258 | 1782585.5948 | 81.52% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-10-26 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.5258 | 1782585.5948 | 81.52% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-10-27 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.5258 | 1782585.5948 | 81.52% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-10-28 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.5258 | 1782585.5948 | 81.52% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-10-29 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.5258 | 1782585.5948 | 81.52% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-10-30 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.5258 | 1782585.5948 | 81.52% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-10-31 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.5258 | 1782585.5948 | 81.52% | 22.17% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-11-01 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.43 | 1560949.0571 | 85.79% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-11-02 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.43 | 1560949.0571 | 85.79% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-11-03 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.43 | 1560949.0571 | 85.79% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-11-04 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.43 | 1560949.0571 | 85.79% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-11-05 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.43 | 1560949.0571 | 85.79% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-11-06 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.43 | 1560949.0571 | 85.79% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-11-07 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.43 | 1560949.0571 | 85.79% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-11-08 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.43 | 1560949.0571 | 85.79% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-11-09 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.43 | 1560949.0571 | 85.79% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-11-10 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.43 | 1560949.0571 | 85.79% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-11-11 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.43 | 1560949.0571 | 85.79% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-11-12 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.43 | 1560949.0571 | 85.79% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-11-13 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.43 | 1560949.0571 | 85.79% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-11-14 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.43 | 1560949.0571 | 85.79% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-11-15 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.43 | 1560949.0571 | 85.79% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-11-16 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.43 | 1560949.0571 | 85.79% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-11-17 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.43 | 1560949.0571 | 85.79% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-11-18 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.43 | 1560949.0571 | 85.79% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-11-19 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.43 | 1560949.0571 | 85.79% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-11-20 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.43 | 1560949.0571 | 85.79% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-11-21 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.43 | 1560949.0571 | 85.79% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-11-22 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.43 | 1560949.0571 | 85.79% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-11-23 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.43 | 1560949.0571 | 85.79% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-11-24 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.43 | 1560949.0571 | 85.79% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-11-25 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.43 | 1560949.0571 | 85.79% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-11-26 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.43 | 1560949.0571 | 85.79% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-11-27 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.43 | 1560949.0571 | 85.79% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-11-28 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.43 | 1560949.0571 | 85.79% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-11-29 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.43 | 1560949.0571 | 85.79% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-11-30 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.43 | 1560949.0571 | 85.79% | 19.41% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-12-01 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.1161 | 1504722.4331 | 87.77% | 18.71% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-12-02 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.1161 | 1504722.4331 | 87.77% | 18.71% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-12-03 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.1161 | 1504722.4331 | 87.77% | 18.71% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-12-04 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.1161 | 1504722.4331 | 87.77% | 18.71% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-12-05 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.1161 | 1504722.4331 | 87.77% | 18.71% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-12-06 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.1161 | 1504722.4331 | 87.77% | 18.71% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-12-07 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.1161 | 1504722.4331 | 87.77% | 18.71% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-12-08 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.1161 | 1504722.4331 | 87.77% | 18.71% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-12-09 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.1161 | 1504722.4331 | 87.77% | 18.71% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-12-10 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.1161 | 1504722.4331 | 87.77% | 18.71% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-12-11 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.1161 | 1504722.4331 | 87.77% | 18.71% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-12-12 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.1161 | 1504722.4331 | 87.77% | 18.71% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-12-13 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.1161 | 1504722.4331 | 87.77% | 18.71% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-12-14 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.1161 | 1504722.4331 | 87.77% | 18.71% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-12-15 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.1161 | 1504722.4331 | 87.77% | 18.71% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-12-16 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.1161 | 1504722.4331 | 87.77% | 18.71% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-12-17 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.1161 | 1504722.4331 | 87.77% | 18.71% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-12-18 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.1161 | 1504722.4331 | 87.77% | 18.71% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-12-19 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.1161 | 1504722.4331 | 87.77% | 18.71% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-12-20 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.1161 | 1504722.4331 | 87.77% | 18.71% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-12-21 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.1161 | 1504722.4331 | 87.77% | 18.71% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-12-22 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.1161 | 1504722.4331 | 87.77% | 18.71% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-12-23 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.1161 | 1504722.4331 | 87.77% | 18.71% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-12-24 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.1161 | 1504722.4331 | 87.77% | 18.71% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-12-25 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.1161 | 1504722.4331 | 87.77% | 18.71% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-12-26 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.1161 | 1504722.4331 | 87.77% | 18.71% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-12-27 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.1161 | 1504722.4331 | 87.77% | 18.71% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-12-28 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.1161 | 1504722.4331 | 87.77% | 18.71% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-12-29 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.1161 | 1504722.4331 | 87.77% | 18.71% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-12-30 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.1161 | 1504722.4331 | 87.77% | 18.71% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2025-12-31 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.1161 | 1504722.4331 | 87.77% | 18.71% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-01-01 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.4525 | 1597510.1091 | 87.43% | 19.86% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-01-02 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.4525 | 1597510.1091 | 87.43% | 19.86% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-01-03 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.4525 | 1597510.1091 | 87.43% | 19.86% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-01-04 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.4525 | 1597510.1091 | 87.43% | 19.86% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-01-05 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.4525 | 1597510.1091 | 87.43% | 19.86% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-01-06 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.4525 | 1597510.1091 | 87.43% | 19.86% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-01-07 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.4525 | 1597510.1091 | 87.43% | 19.86% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-01-08 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.4525 | 1597510.1091 | 87.43% | 19.86% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-01-09 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.4525 | 1597510.1091 | 87.43% | 19.86% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-01-10 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.4525 | 1597510.1091 | 87.43% | 19.86% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-01-11 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.4525 | 1597510.1091 | 87.43% | 19.86% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-01-12 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.4525 | 1597510.1091 | 87.43% | 19.86% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-01-13 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.4525 | 1597510.1091 | 87.43% | 19.86% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-01-14 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.4525 | 1597510.1091 | 87.43% | 19.86% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-01-15 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.4525 | 1597510.1091 | 87.43% | 19.86% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-01-16 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.4525 | 1597510.1091 | 87.43% | 19.86% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-01-17 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.4525 | 1597510.1091 | 87.43% | 19.86% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-01-18 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.4525 | 1597510.1091 | 87.43% | 19.86% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-01-19 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.4525 | 1597510.1091 | 87.43% | 19.86% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-01-20 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.4525 | 1597510.1091 | 87.43% | 19.86% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-01-21 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.4525 | 1597510.1091 | 87.43% | 19.86% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-01-22 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.4525 | 1597510.1091 | 87.43% | 19.86% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-01-23 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.4525 | 1597510.1091 | 87.43% | 19.86% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-01-24 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.4525 | 1597510.1091 | 87.43% | 19.86% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-01-25 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.4525 | 1597510.1091 | 87.43% | 19.86% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-01-26 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.4525 | 1597510.1091 | 87.43% | 19.86% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-01-27 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.4525 | 1597510.1091 | 87.43% | 19.86% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-01-28 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.4525 | 1597510.1091 | 87.43% | 19.86% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-01-29 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.4525 | 1597510.1091 | 87.43% | 19.86% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-01-30 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.4525 | 1597510.1091 | 87.43% | 19.86% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-01-31 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.4525 | 1597510.1091 | 87.43% | 19.86% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-02-01 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.1628 | 1744321.2783 | 84.47% | 21.69% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-02-02 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.1628 | 1744321.2783 | 84.47% | 21.69% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-02-03 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.1628 | 1744321.2783 | 84.47% | 21.69% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-02-04 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.1628 | 1744321.2783 | 84.47% | 21.69% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-02-05 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.1628 | 1744321.2783 | 84.47% | 21.69% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-02-06 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.1628 | 1744321.2783 | 84.47% | 21.69% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-02-07 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.1628 | 1744321.2783 | 84.47% | 21.69% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-02-08 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.1628 | 1744321.2783 | 84.47% | 21.69% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-02-09 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.1628 | 1744321.2783 | 84.47% | 21.69% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-02-10 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.1628 | 1744321.2783 | 84.47% | 21.69% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-02-11 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.1628 | 1744321.2783 | 84.47% | 21.69% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-02-12 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.1628 | 1744321.2783 | 84.47% | 21.69% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-02-13 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.1628 | 1744321.2783 | 84.47% | 21.69% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-02-14 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.1628 | 1744321.2783 | 84.47% | 21.69% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-02-15 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.1628 | 1744321.2783 | 84.47% | 21.69% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-02-16 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.1628 | 1744321.2783 | 84.47% | 21.69% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-02-17 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.1628 | 1744321.2783 | 84.47% | 21.69% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-02-18 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.1628 | 1744321.2783 | 84.47% | 21.69% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-02-19 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.1628 | 1744321.2783 | 84.47% | 21.69% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-02-20 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.1628 | 1744321.2783 | 84.47% | 21.69% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-02-21 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.1628 | 1744321.2783 | 84.47% | 21.69% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-02-22 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.1628 | 1744321.2783 | 84.47% | 21.69% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-02-23 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.1628 | 1744321.2783 | 84.47% | 21.69% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-02-24 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.1628 | 1744321.2783 | 84.47% | 21.69% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-02-25 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.1628 | 1744321.2783 | 84.47% | 21.69% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-02-26 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.1628 | 1744321.2783 | 84.47% | 21.69% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-02-27 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.1628 | 1744321.2783 | 84.47% | 21.69% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-02-28 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.1628 | 1744321.2783 | 84.47% | 21.69% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-03-01 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9595 | 1886089.1539 | 80.88% | 23.45% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-03-02 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9595 | 1886089.1539 | 80.88% | 23.45% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-03-03 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9595 | 1886089.1539 | 80.88% | 23.45% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-03-04 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9595 | 1886089.1539 | 80.88% | 23.45% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-03-05 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9595 | 1886089.1539 | 80.88% | 23.45% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-03-06 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9595 | 1886089.1539 | 80.88% | 23.45% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-03-07 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9595 | 1886089.1539 | 80.88% | 23.45% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-03-08 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9595 | 1886089.1539 | 80.88% | 23.45% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-03-09 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9595 | 1886089.1539 | 80.88% | 23.45% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-03-10 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9595 | 1886089.1539 | 80.88% | 23.45% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-03-11 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9595 | 1886089.1539 | 80.88% | 23.45% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-03-12 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9595 | 1886089.1539 | 80.88% | 23.45% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-03-13 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9595 | 1886089.1539 | 80.88% | 23.45% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-03-14 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9595 | 1886089.1539 | 80.88% | 23.45% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-03-15 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9595 | 1886089.1539 | 80.88% | 23.45% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-03-16 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9595 | 1886089.1539 | 80.88% | 23.45% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-03-17 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9595 | 1886089.1539 | 80.88% | 23.45% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-03-18 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9595 | 1886089.1539 | 80.88% | 23.45% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-03-19 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9595 | 1886089.1539 | 80.88% | 23.45% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-03-20 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9595 | 1886089.1539 | 80.88% | 23.45% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-03-21 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9595 | 1886089.1539 | 80.88% | 23.45% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-03-22 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9595 | 1886089.1539 | 80.88% | 23.45% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-03-23 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9595 | 1886089.1539 | 80.88% | 23.45% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-03-24 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9595 | 1886089.1539 | 80.88% | 23.45% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-03-25 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9595 | 1886089.1539 | 80.88% | 23.45% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-03-26 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9595 | 1886089.1539 | 80.88% | 23.45% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-03-27 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9595 | 1886089.1539 | 80.88% | 23.45% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-03-28 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9595 | 1886089.1539 | 80.88% | 23.45% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-03-29 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9595 | 1886089.1539 | 80.88% | 23.45% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-03-30 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9595 | 1886089.1539 | 80.88% | 23.45% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
2026-03-31 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9595 | 1886089.1539 | 80.88% | 23.45% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 335.091
Formulas:
Month Year = Table13[[#This Row],[Date]]-DAY(Table13[[#This Row],[Date]])+1
Days = DAY(EOMONTH([Date],0))
Date = [Date, row above]+1
Note on AK1104: GOVIND GUPTA: SB robots not operate, cause to change its cleaning time, so from tomorrow these run in morning.

## Raw_Data
[230 empty] | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 | 120 | 121 | 122 | 123 | 124 | 125 | 126 | 127 | 128 | 129 | 130 | 131 | 132 | 133 | 134 | 135 | 136 | 137 | 138 | 139 | 140 | 141 | 142 | 143 | 144 | 145 | 146 | 147 | 148 | 149 | 150 | 151 | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181 | 182 | 183 | 184 | 185 | 186 | 187 | 188 | 189 | 190 | 191 | 192 | 193 | 194 | 195 | 196 | 197 | 198 | 199 | 200 | 201 | 202 | 203 | 204 | 205 | 206 | 207 | 208 | 209 | 210 | 211 | 212 | 213 | 214 | 215 | 216 | 217 | 218 | 219 | 220 | 221 | 222 | 223 | 224 | 225 | 226 | 227 | 228 | 229 | 230 | 231 | 232 | 233 | 234 | 235 | 236 | 237 | 238 | 239 | 240 | 241 | 242 | 243 | 244 | 245 | 246 | 247 | 248 | 249 | 250 | 251 | 252 | 253 | 254 | 255 | 256 | 257 | 258 | 259 | 260 | 261 | 262 | 263 | 264 | 265 | 266 | 267 | 268 | 269 | 270 | 271
Date | Finacial Year | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Plant DC Capcity (MW) | Sunrise Time (POA>20 W/m2) | Sunset Time (POA<20 W/m2) | IS1_INV1_M1 | IS1_INV1_M2 | IS1_INV2_M1 | IS1_INV2_M2 | IS1_INV3_M1 | IS1_INV3_M2 | IS1_INV4_M1 | IS1_INV4_M2 | IS2_INV1_M1 | IS2_INV1_M2 | IS2_INV2_M1 | IS2_INV2_M2 | IS2_INV3_M1 | IS2_INV3_M2 | IS2_INV4_M1 | IS2_INV4_M2 | IS3_INV1_M1 | IS3_INV1_M2 | IS3_INV2_M1 | IS3_INV2_M2 | IS3_INV3_M1 | IS3_INV3_M2 | IS3_INV4_M1 | IS3_INV4_M2 | IS4_INV1_M1 | IS4_INV1_M2 | IS4_INV2_M1 | IS4_INV2_M2 | IS4_INV3_M1 | IS4_INV3_M2 | IS4_INV4_M1 | IS4_INV4_M2 | IS5_INV1_M1 | IS5_INV1_M2 | IS5_INV2_M1 | IS5_INV2_M2 | IS5_INV3_M1 | IS5_INV3_M2 | IS5_INV4_M1 | IS5_INV4_M2 | IS6_INV1_M1 | IS6_INV1_M2 | IS6_INV2_M1 | IS6_INV2_M2 | IS6_INV3_M1 | IS6_INV3_M2 | IS6_INV4_M1 | IS6_INV4_M2 | IS7_INV1_M1 | IS7_INV1_M2 | IS7_INV2_M1 | IS7_INV2_M2 | IS7_INV3_M1 | IS7_INV3_M2 | IS7_INV4_M1 | IS7_INV4_M2 | IS8_INV1_M1 | IS8_INV1_M2 | IS8_INV2_M1 | IS8_INV2_M2 | IS8_INV3_M1 | IS8_INV3_M2 | IS8_INV4_M1 | IS8_INV4_M2 | IS9_INV1_M1 | IS9_INV1_M2 | IS9_INV2_M1 | IS9_INV2_M2 | IS9_INV3_M1 | IS9_INV3_M2 | IS9_INV4_M1 | IS9_INV4_M2 | IS10_INV1_M1 | IS10_INV1_M2 | IS10_INV2_M1 | IS10_INV2_M2 | IS10_INV3_M1 | IS10_INV3_M2 | IS10_INV4_M1 | IS10_INV4_M2 | IS11_INV1_M1 | IS11_INV1_M2 | IS11_INV2_M1 | IS11_INV2_M2 | IS11_INV3_M1 | IS11_INV3_M2 | IS11_INV4_M1 | IS11_INV4_M2 | IS12_INV1_M1 | IS12_INV1_M2 | IS12_INV2_M1 | IS12_INV2_M2 | IS12_INV3_M1 | IS12_INV3_M2 | IS12_INV4_M1 | IS12_INV4_M2 | IS13_INV1_M1 | IS13_INV1_M2 | IS13_INV2_M1 | IS13_INV2_M2 | IS13_INV3_M1 | IS13_INV3_M2 | IS13_INV4_M1 | IS13_INV4_M2 | IS14_INV1_M1 | IS14_INV1_M2 | IS14_INV2_M1 | IS14_INV2_M2 | IS14_INV3_M1 | IS14_INV3_M2 | IS14_INV4_M1 | IS14_INV4_M2 | IS15_INV1_M1 | IS15_INV1_M2 | IS15_INV2_M1 | IS15_INV2_M2 | IS15_INV3_M1 | IS15_INV3_M2 | IS15_INV4_M1 | IS15_INV4_M2 | IS16_INV1_M1 | IS16_INV1_M2 | IS16_INV2_M1 | IS16_INV2_M2 | IS16_INV3_M1 | IS16_INV3_M2 | IS16_INV4_M1 | IS16_INV4_M2 | IS17_INV1_M1 | IS17_INV1_M2 | IS17_INV2_M1 | IS17_INV2_M2 | IS17_INV3_M1 | IS17_INV3_M2 | IS17_INV4_M1 | IS17_INV4_M2 | IS18_INV1_M1 | IS18_INV1_M2 | IS18_INV2_M1 | IS18_INV2_M2 | IS18_INV3_M1 | IS18_INV3_M2 | IS18_INV4_M1 | IS18_INV4_M2 | IS19_INV1_M1 | IS19_INV1_M2 | IS19_INV2_M1 | IS19_INV2_M2 | IS19_INV3_M1 | IS19_INV3_M2 | IS19_INV4_M1 | IS19_INV4_M2 | IS20_INV1_M1 | IS20_INV1_M2 | IS20_INV2_M1 | IS20_INV2_M2 | IS20_INV3_M1 | IS20_INV3_M2 | IS20_INV4_M1 | IS20_INV4_M2 | Amb_Temp_IS2_W1 | Amb_Temp_IS4_W2 | Amb_Temp_IS6_W3 | Amb_Temp_IS9_W4 | Amb_Temp_IS15_W5 | Amb_Temp_IS19_W6 | MT_Temp_IS2_W1 | MT_Temp_IS4_W2 | MT_Temp_IS6_W3 | MT_Temp_IS9_W4 | MT_Temp_IS15_W5 | MT_Temp_IS19_W6 | WS_Avg_IS2_W1 | WS_Avg_IS4_W2 | WS_Avg_IS6_W3 | WS_Avg_IS9_W4 | WS_Avg_IS15_W5 | WS_Avg_IS19_W6 | WS_Max_IS2_W1 | WS_Max_IS4_W2 | WS_Max_IS6_W3 | WS_Max_IS9_W4 | WS_Max_IS15_W5 | WS_Max_IS19_W6 | GHI_Up_IS2_W1 | GHI_Up_IS4_W2 | GHI_Up_IS6_W3 | GHI_Up_IS9_W4 | GHI_Up_IS15_W5 | GHI_Up_IS19_W6 | GHI_Down_IS2_W1 | GHI_Down_IS4_W2 | GHI_Down_IS6_W3 | GHI_Down_IS9_W4 | GHI_Down_IS15_W5 | GHI_Down_IS19_W6 | POA_Up_IS2_W1 | POA_Up_IS4_W2 | POA_Up_IS6_W3 | POA_Up_IS9_W4 | POA_Up_IS15_W5 | POA_Up_IS19_W6 | POA_Down_IS2_W1 | POA_Down_IS4_W2 | POA_Down_IS6_W3 | POA_Down_IS9_W4 | POA_Down_IS15_W5 | POA_Down_IS19_W6 | GHI_UP_Lost_IS2_W1 | GHI_UP_Lost_IS4_W2 | GHI_UP_Lost_IS6_W3 | GHI_UP_Lost_IS9_W4 | GHI_UP_Lost_IS15_W5 | GHI_UP_Lost_IS19_W6 | POA_UP_Lost_IS2_W1 | POA_UP_Lost_IS4_W2 | POA_UP_Lost_IS6_W3 | POA_UP_Lost_IS9_W4 | POA_UP_Lost_IS15_W5 | POA_UP_Lost_IS19_W6 | 33kV_OG2_Ex | 33kV_OG2_Im | 33kV_OG1_Ex | 33kV_OG1_Im | 220kV_PQM_Ex | 220kV_PQM_Im | GHI_UP_Net_IS2_W1 | GHI_UP_Net_IS4_W2 | GHI_UP_Net_IS6_W3 | GHI_UP_Net_IS9_W4 | GHI_UP_Net_IS15_W5 | GHI_UP_Net_IS19_W6 | POA_UP_Net_IS2_W1 | POA_UP_Net_IS4_W2 | POA_UP_Net_IS6_W3 | POA_UP_Net_IS9_W4 | POA_UP_Net_IS15_W5 | POA_UP_Net_IS19_W6 | 33kV_OG2_EX (KWh) | 33kV_OG2_Im (KWh) | 33kV_OG1_Ex(KWh) | 33kV_OG1_Im(KWh) | 220kV_PQM_Ex(KWh) | 220kV_PQM_Im(KWh) | 33kV_Net_Ex (kWh) | 220kV_Net_Ex (kWh) | Operating Hours | GHI-UP (KWh/m2) | GHI-Down(KWh/m2) | POA-UP(KWh/m2) | POA-Down(KWh/m2) | Albedo GHI (%) | Albedo POA (%) | Amm_Temp(°C) | Mod_Temp(°C) | WS_Avg(m/s) | WS_Max(m/s) | Inv_Exp(KWh) | WPR_Eac | WPR_Edc | WPR | Forecasting Data count received on Forecasting Portal | Forecasting Penalties (INR)
2022-04-04 | 2023 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 21000 | 6:13 | 18:59 | 1487.8 | 1487.8 | 688.2 | 688.2 | 1394 | 1394 | 1279.1 | 1279.1 | 789.75 | 789.75 | 982.75 | 982.75 | 796.75 | 796.75 | 5514.95 | 5514.95 | 372.3 | 372.3 | 447.9 | 447.9 | 1046.95 | 1046.95 | 939.15 | 939.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2412.25 | 2412.25 | 3401.7 | 3401.7 | 1752.55 | 1752.55 | 2540.65 | 2540.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 819.4 | 819.4 | 1548.75 | 1548.75 | 1577.55 | 1577.55 | 1453.8 | 1453.8 | 3330.2 | 3330.2 | 3203.4 | 3203.4 | 2499.35 | 2499.35 | 1553.5 | 1553.5 | 1164.9 | 1164.9 | 642.15 | 642.15 | 1680.9 | 1680.9 | 897.45 | 897.45 | 909.5 | 909.5 | 1348.65 | 1348.65 | 965.55 | 965.55 | 1026.1 | 1026.1 | 940.65 | 940.65 | 2968.75 | 2968.75 | 2237.8 | 2237.8 | 2371.85 | 2371.85 | 1071.2 | 1071.2 | 890 | 890 | 649.65 | 649.65 | 518.3 | 518.3 | 860.1 | 860.1 | 675.75 | 675.75 | 371.85 | 371.85 | 207.55 | 207.55 | 349.25 | 349.25 | 301.25 | 301.25 | 304.4 | 304.4 | 441.8 | 441.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.82 | 0 | 0 | 0 | 0 | 0 | 39.13 | 0 | 0 | 0 | 0 | 0 | 5.66 | 0 | 0 | 0 | 0 | 0 | 7.1 | 0 | 0 | 0 | 0 | 0 | 7.33 | 0 | 0 | 0 | 0 | 0 | 2.13 | 0 | 0 | 0 | 0 | 0 | 7.71 | 0 | 0 | 0 | 0 | 0 | 2.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 1 | 35 | 1 | 133 | 5 | 0 | 7.33 | 0 | 0 | 0 | 0 | 0 | 7.71 | 0 | 0 | 0 | 0 | 90000 | 1000 | 35000 | 1000 | 133000 | 5000 | 123000 | 128000 | 12.7667 | 7.33 | 2.13 | 7.71 | 2.06 | 29.06% | 26.72% | 36.82 | 39.13 | 5.66 | 7.1 | 131256.1 | 125000 | 145000 | 86.21%
2022-04-05 | 2023 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 21000 | 6:12 | 19:10 | 1483.05 | 1483.05 | 1022.6 | 1022.6 | 1409.1 | 1409.1 | 1310.6 | 1310.6 | 805.85 | 805.85 | 1047.4 | 1047.4 | 809.3 | 809.3 | 5980.85 | 5980.85 | 372.75 | 372.75 | 442.45 | 442.45 | 1098.65 | 1098.65 | 925 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2093.9 | 2093.9 | 3083.05 | 3083.05 | 1652.6 | 1652.6 | 1914.85 | 1914.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1079.75 | 1079.75 | 1658.1 | 1658.1 | 1560.35 | 1560.35 | 1602.05 | 1602.05 | 3347.25 | 3347.25 | 3183.75 | 3183.75 | 2513.2 | 2513.2 | 1590.2 | 1590.2 | 1409.4 | 1409.4 | 1140.2 | 1140.2 | 2733.8 | 2733.8 | 1203.75 | 1203.75 | 947.1 | 947.1 | 1436.4 | 1436.4 | 1014.9 | 1014.9 | 1123.2 | 1123.2 | 1138.45 | 1138.45 | 3822.05 | 3822.05 | 2640.85 | 2640.85 | 2801.5 | 2801.5 | 1237.5 | 1237.5 | 1360.6 | 1360.6 | 786.4 | 786.4 | 623.1 | 623.1 | 932.25 | 932.25 | 741.6 | 741.6 | 625 | 625 | 391.3 | 391.3 | 659.8 | 659.8 | 561.85 | 561.85 | 575.6 | 575.6 | 851.75 | 851.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.42 | 0 | 0 | 0 | 0 | 0 | 42.99 | 0 | 0 | 0 | 0 | 0 | 5.1 | 0 | 0 | 0 | 0 | 0 | 6.23 | 0 | 0 | 0 | 0 | 0 | 7.8 | 0 | 0 | 0 | 0 | 0 | 2.18 | 0 | 0 | 0 | 0 | 0 | 7.69 | 0 | 0 | 0 | 0 | 0 | 2.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 2 | 70 | 1 | 293 | 10 | 0 | 7.8 | 0 | 0 | 0 | 0 | 0 | 7.69 | 0 | 0 | 0 | 0 | 108000 | 1000 | 35000 | 0 | 160000 | 5000 | 142000 | 155000 | 12.9667 | 7.8 | 2.18 | 7.69 | 2.09 | 27.95% | 27.18% | 36.42 | 42.99 | 5.1 | 6.23 | 145490
2022-04-06 | 2023 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 27189 | 6:13 | 19:10 | 1525.3 | 1525.3 | 324.8 | 324.8 | 1471.75 | 1471.75 | 1353.85 | 1353.85 | 826.7 | 826.7 | 1396.1 | 1396.1 | 2185.1 | 2185.1 | 7730.25 | 7730.25 | 469.8 | 469.8 | 450.85 | 450.85 | 1407.6 | 1407.6 | 1064.85 | 1064.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2816.9 | 2816.9 | 4932.75 | 4932.75 | 4756.6 | 4756.6 | 2585.2 | 2585.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1518.3 | 1518.3 | 1706.25 | 1706.25 | 1600.55 | 1600.55 | 1588.9 | 1588.9 | 3426.65 | 3426.65 | 3447.85 | 3447.85 | 2666.3 | 2666.3 | 1610.95 | 1610.95 | 1440.25 | 1440.25 | 1215.1 | 1215.1 | 2835.9 | 2835.9 | 1229.35 | 1229.35 | 969.05 | 969.05 | 1853.2 | 1853.2 | 1067.5 | 1067.5 | 1872.05 | 1872.05 | 1167.35 | 1167.35 | 7360.55 | 7360.55 | 2697.7 | 2697.7 | 2819.95 | 2819.95 | 1266.1 | 1266.1 | 1399.6 | 1399.6 | 804.8 | 804.8 | 621.7 | 621.7 | 951.55 | 951.55 | 755.45 | 755.45 | 638.7 | 638.7 | 432.1 | 432.1 | 671.6 | 671.6 | 576.1 | 576.1 | 588.45 | 588.45 | 872.65 | 872.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 34.2768 | 0 | 0 | 0 | 0 | 0 | 2.56 | 0 | 0 | 0 | 0 | 0 | 7.15 | 0 | 0 | 0 | 0 | 0 | 7.77 | 0 | 0 | 0 | 0 | 0 | 2.17 | 0 | 0 | 0 | 0 | 0 | 7.82 | 0 | 0 | 0 | 0 | 0 | 2.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 3 | 90 | 2 | 470 | 13 | 0 | 7.77 | 0 | 0 | 0 | 0 | 0 | 7.82 | 0 | 0 | 0 | 0 | 137000 | 1000 | 20000 | 1000 | 177000 | 3000 | 155000 | 174000 | 12.95 | 7.77 | 2.17 | 7.82 | 2.11 | 27.93% | 26.98% | 38 | 34.2768 | 2.56 | 7.15 | 177941.8
2022-04-07 | 2023 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 32142 | 6:13 | 19:09 | 388.55 | 388.55 | 340.85 | 340.85 | 367.8 | 367.8 | 337.4 | 337.4 | 211.3 | 211.3 | 789.85 | 789.85 | 678.3 | 678.3 | 2195.3 | 2195.3 | 281.5 | 281.5 | 112.4 | 112.4 | 409.15 | 409.15 | 288.4 | 288.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1692.35 | 1692.35 | 1393.25 | 1393.25 | 1474.4 | 1474.4 | 664.7 | 664.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1470.75 | 1470.75 | 2823.6 | 2823.6 | 1945.6 | 1945.6 | 1191.9 | 1191.9 | 3365.1 | 3365.1 | 5714.8 | 5714.8 | 3618.65 | 3618.65 | 1582.5 | 1582.5 | 368.95 | 368.95 | 443.4 | 443.4 | 827.15 | 827.15 | 312.25 | 312.25 | 246.35 | 246.35 | 1810.95 | 1810.95 | 271.75 | 271.75 | 475.9 | 475.9 | 294.35 | 294.35 | 1866.85 | 1866.85 | 680.75 | 680.75 | 714.45 | 714.45 | 323.75 | 323.75 | 358.45 | 358.45 | 204.45 | 204.45 | 155.25 | 155.25 | 233.8 | 233.8 | 190.05 | 190.05 | 161 | 161 | 192.95 | 192.95 | 167.45 | 167.45 | 144.4 | 144.4 | 147.95 | 147.95 | 213.65 | 213.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.6152 | 0 | 0 | 0 | 0 | 0 | 34.6152 | 0 | 0 | 0 | 0 | 0 | 2.74 | 0 | 0 | 0 | 0 | 0 | 6.49 | 0 | 0 | 0 | 0 | 0 | 7.2285 | 0 | 0 | 0 | 0 | 0 | 2.2836 | 0 | 0 | 0 | 0 | 0 | 7.6673 | 0 | 0 | 0 | 0 | 0 | 2.2039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 430 | 4 | 160 | 3 | 672 | 16 | 0 | 7.2285 | 0 | 0 | 0 | 0 | 0 | 7.6673 | 0 | 0 | 0 | 0 | 95000 | 1000 | 70000 | 1000 | 202000 | 3000 | 163000 | 199000 | 12.9333 | 7.2285 | 2.2836 | 7.6673 | 2.2039 | 31.59% | 28.74% | 34.6152 | 34.6152 | 2.74 | 6.49 | 88289.3
2022-04-08 | 2023 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 37680 | 6:14 | 18:58 | 1419.15 | 1419.15 | 1261.2 | 1261.2 | 1697.75 | 1697.75 | 2729.55 | 2729.55 | 1888.05 | 1888.05 | 6662.35 | 6662.35 | 2499.15 | 2499.15 | 8018.4 | 8018.4 | 1440.9 | 1440.9 | 429.55 | 429.55 | 2629.6 | 2629.6 | 1025.65 | 1025.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6159.15 | 6159.15 | 5108.7 | 5108.7 | 5392.8 | 5392.8 | 2417.25 | 2417.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1442.55 | 1442.55 | 2798.35 | 2798.35 | 2004.85 | 2004.85 | 1189.1 | 1189.1 | 3329.4 | 3329.4 | 5770.95 | 5770.95 | 3581.2 | 3581.2 | 1929 | 1929 | 1352.9 | 1352.9 | 1622.7 | 1622.7 | 3040.85 | 3040.85 | 1151.5 | 1151.5 | 905.9 | 905.9 | 1753.55 | 1753.55 | 961.2 | 961.2 | 1745.3 | 1745.3 | 1085.75 | 1085.75 | 6858.35 | 6858.35 | 2394.65 | 2394.65 | 7138.75 | 7138.75 | 1187.6 | 1187.6 | 1316.05 | 1316.05 | 726.35 | 726.35 | 553.9 | 553.9 | 889.8 | 889.8 | 701.2 | 701.2 | 960.1 | 960.1 | 709.45 | 709.45 | 629.2 | 629.2 | 534.7 | 534.7 | 533.85 | 533.85 | 809 | 809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.8657 | 0 | 0 | 0 | 0 | 0 | 34.8657 | 0 | 0 | 0 | 0 | 0 | 4.88 | 0 | 0 | 0 | 0 | 0 | 9.78 | 0 | 0 | 0 | 0 | 0 | 7.0062 | 0 | 0 | 0 | 0 | 0 | 2.2242 | 0 | 0 | 0 | 0 | 0 | 7.4199 | 0 | 0 | 0 | 0 | 0 | 2.1504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 630 | 5 | 390 | 3 | 905 | 19 | 0 | 7.0062 | 0 | 0 | 0 | 0 | 0 | 7.4199 | 0 | 0 | 0 | 0 | 200000 | 1000 | 230000 | 0 | 233000 | 3000 | 429000 | 230000 | 12.7333 | 7.0062 | 2.2242 | 7.4199 | 2.1504 | 31.75% | 28.98% | 34.8657 | 34.8657 | 4.88 | 9.78 | 224774.4
2022-04-09 | 2023 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 47050 | 6:14 | 18:57 | 1486.35 | 1486.35 | 1797.85 | 1797.85 | 1945.4 | 1945.4 | 2912 | 2912 | 2758.6 | 2758.6 | 7859.75 | 7859.75 | 2653.15 | 2653.15 | 8516.8 | 8516.8 | 3693.45 | 3693.45 | 455.05 | 455.05 | 2792.6 | 2792.6 | 1089.45 | 1089.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6099.35 | 6099.35 | 5073.7 | 5073.7 | 5449.55 | 5449.55 | 2432.5 | 2432.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2592.95 | 2592.95 | 3518.25 | 3518.25 | 6447.35 | 6447.35 | 1938.25 | 1938.25 | 3454.45 | 3454.45 | 5965.5 | 5965.5 | 3756.75 | 3756.75 | 2029.8 | 2029.8 | 1433.85 | 1433.85 | 5181.45 | 5181.45 | 3234.25 | 3234.25 | 1736.7 | 1736.7 | 963.5 | 963.5 | 1850.5 | 1850.5 | 5829.95 | 5829.95 | 1868.2 | 1868.2 | 1154.3 | 1154.3 | 7266.35 | 7266.35 | 2707.5 | 2707.5 | 10623.05 | 10623.05 | 1258.05 | 1258.05 | 1387.1 | 1387.1 | 1560.6 | 1560.6 | 1362.85 | 1362.85 | 1223.5 | 1223.5 | 745.25 | 745.25 | 1362 | 1362 | 1735 | 1735 | 689.15 | 689.15 | 567.55 | 567.55 | 597.2 | 597.2 | 859.4 | 859.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.4074 | 0 | 0 | 0 | 0 | 0 | 33.4074 | 0 | 0 | 0 | 0 | 0 | 3.28 | 0 | 0 | 0 | 0 | 0 | 7.03 | 0 | 0 | 0 | 0 | 0 | 7.3634 | 0 | 0 | 0 | 0 | 0 | 2.3211 | 0 | 0 | 0 | 0 | 0 | 7.808 | 0 | 0 | 0 | 0 | 0 | 2.2463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 870 | 6 | 447 | 4 | 1191 | 22 | 0 | 7.3634 | 0 | 0 | 0 | 0 | 0 | 7.808 | 0 | 0 | 0 | 0 | 240000 | 1000 | 57000 | 1000 | 286000 | 3000 | 295000 | 283000 | 12.7167 | 7.3634 | 2.3211 | 7.808 | 2.2463 | 31.52% | 28.77% | 33.4074 | 33.4074 | 3.28 | 7.03 | 287832.2
2022-04-10 | 2023 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 57600 | 6:14 | 18:57 | 1412.15 | 1412.15 | 3257.1 | 3257.1 | 3527.35 | 3527.35 | 2936.9 | 2936.9 | 3445.3 | 3445.3 | 9138.8 | 9138.8 | 3412.95 | 3412.95 | 9622.15 | 9622.15 | 4911.3 | 4911.3 | 433.4 | 433.4 | 2669.55 | 2669.55 | 1037.95 | 1037.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7675.95 | 7675.95 | 6973.95 | 6973.95 | 10248.95 | 10248.95 | 2457.1 | 2457.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7675.95 | 7675.95 | 6973.95 | 6973.95 | 10248.95 | 10248.95 | 2457.1 | 2457.1 | 4143.55 | 4143.55 | 3502.25 | 3502.25 | 7936.8 | 7936.8 | 1854.7 | 1854.7 | 4987.25 | 4987.25 | 6163.3 | 6163.3 | 4135.6 | 4135.6 | 2111.35 | 2111.35 | 1107.55 | 1107.55 | 2672.5 | 2672.5 | 4214.5 | 4214.5 | 10296.45 | 10296.45 | 1107.55 | 1107.55 | 7023.25 | 7023.25 | 4214.5 | 4214.5 | 10296.45 | 10296.45 | 1146.5 | 1146.5 | 1333.3 | 1333.3 | 1495.4 | 1495.4 | 1297.4 | 1297.4 | 1157.55 | 1157.55 | 714.25 | 714.25 | 1133.35 | 1133.35 | 2442.15 | 2442.15 | 752.7 | 752.7 | 542.05 | 542.05 | 902.8 | 902.8 | 828.7 | 828.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.71 | 0 | 0 | 0 | 0 | 0 | 34.73 | 0 | 0 | 0 | 0 | 0 | 2.66 | 0 | 0 | 0 | 0 | 0 | 3.57 | 0 | 0 | 0 | 0 | 0 | 7.08 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 | 0 | 0 | 7.4 | 0 | 0 | 0 | 0 | 0 | 2.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1091 | 7 | 574 | 4 | 1531 | 25 | 0 | 7.08 | 0 | 0 | 0 | 0 | 0 | 7.4 | 0 | 0 | 0 | 0 | 221000 | 1000 | 127000 | 0 | 340000 | 3000 | 347000 | 337000 | 12.7167 | 7.08 | 2.2 | 7.4 | 2.13 | 31.07% | 28.78% | 36.71 | 34.73 | 2.66 | 3.57 | 380061
2022-04-11 | 2023 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 70600 | 6:14 | 18:57 | 1748.9 | 1748.9 | 4413.65 | 4413.65 | 7601.35 | 7601.35 | 3178.45 | 3178.45 | 3698.4 | 3698.4 | 9699.4 | 9699.4 | 4646.45 | 4646.45 | 10211.15 | 10211.15 | 6017.3 | 6017.3 | 443.5 | 443.5 | 2725.1 | 2725.1 | 1059.25 | 1059.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9723.9 | 9723.9 | 10595.45 | 10595.45 | 11243.75 | 11243.75 | 4477.35 | 4477.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6258.45 | 6258.45 | 5860.3 | 5860.3 | 8522.2 | 8522.2 | 1891.1 | 1891.1 | 6178.7 | 6178.7 | 8078.65 | 8078.65 | 7860.35 | 7860.35 | 3278.4 | 3278.4 | 1399.35 | 1399.35 | 8665.65 | 8665.65 | 3158.65 | 3158.65 | 2068.95 | 2068.95 | 936.1 | 936.1 | 3907 | 3907 | 8360.55 | 8360.55 | 5191.4 | 5191.4 | 1127.25 | 1127.25 | 7150.7 | 7150.7 | 6321.45 | 6321.45 | 10475.35 | 10475.35 | 3630.75 | 3630.75 | 1360.2 | 1360.2 | 1516.6 | 1516.6 | 1317.7 | 1317.7 | 1175.8 | 1175.8 | 726.8 | 726.8 | 1820.85 | 1820.85 | 2478.7 | 2478.7 | 770.15 | 770.15 | 440.35 | 440.35 | 915.85 | 915.85 | 849.35 | 849.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 38.03 | 0 | 0 | 0 | 0 | 0 | 4.5 | 0 | 0 | 0 | 0 | 0 | 9.1 | 0 | 0 | 0 | 0 | 0 | 7.28 | 0 | 0 | 0 | 0 | 0 | 2.27 | 0 | 0 | 0 | 0 | 0 | 7.68 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1359 | 8 | 719 | 5 | 1958 | 28 | 0 | 7.28 | 0 | 0 | 0 | 0 | 0 | 7.68 | 0 | 0 | 0 | 0 | 268000 | 1000 | 145000 | 1000 | 427000 | 3000 | 411000 | 424000 | 12.7167 | 7.28 | 2.27 | 7.68 | 2.2 | 31.18% | 28.65% | 40 | 38.03 | 4.5 | 9.1 | 430354
2022-04-12 | 2023 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 80000 | 6:15 | 18:58 | 1761.35 | 1761.35 | 4354 | 4354 | 7578.65 | 7578.65 | 4492.25 | 4492.25 | 3688.55 | 3688.55 | 9668.35 | 9668.35 | 4629.3 | 4629.3 | 10185.9 | 10185.9 | 7056.05 | 7056.05 | 449.45 | 449.45 | 2740.9 | 2740.9 | 1057.05 | 1057.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 522.8 | 522.8 | 611.8 | 611.8 | 603.1 | 603.1 | 573 | 573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6965.9 | 6965.9 | 5840.55 | 5840.55 | 8499.55 | 8499.55 | 1890.25 | 1890.25 | 7832.5 | 7832.5 | 9264.3 | 9264.3 | 8061.95 | 8061.95 | 3769.1 | 3769.1 | 1407.05 | 1407.05 | 8939.3 | 8939.3 | 3116.85 | 3116.85 | 2605.75 | 2605.75 | 929.3 | 929.3 | 5116.65 | 5116.65 | 8604.15 | 8604.15 | 5157.05 | 5157.05 | 1127.6 | 1127.6 | 7116.6 | 7116.6 | 6293.3 | 6293.3 | 10406.7 | 10406.7 | 7287.5 | 7287.5 | 2973.2 | 2973.2 | 1556.35 | 1556.35 | 1359.3 | 1359.3 | 1095.15 | 1095.15 | 331.85 | 331.85 | 1635.35 | 1635.35 | 2300.3 | 2300.3 | 768.2 | 768.2 | 932.95 | 932.95 | 929.15 | 929.15 | 849.15 | 849.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.85 | 0 | 0 | 0 | 0 | 0 | 34.07 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 11.22 | 0 | 0 | 0 | 0 | 0 | 7.12 | 0 | 0 | 0 | 0 | 0 | 2.19 | 0 | 0 | 0 | 0 | 0 | 7.52 | 0 | 0 | 0 | 0 | 0 | 2.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1590 | 9 | 889 | 5 | 2343 | 31 | 0 | 7.12 | 0 | 0 | 0 | 0 | 0 | 7.52 | 0 | 0 | 0 | 0 | 231000 | 1000 | 170000 | 0 | 385000 | 3000 | 400000 | 382000 | 12.7167 | 7.12 | 2.19 | 7.52 | 2.13 | 30.76% | 28.32% | 36.85 | 34.07 | 6 | 11.22 | 389870.7
2022-04-13 | 2023 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 84000 | 6:15 | 18:58 | 1690.55 | 1690.55 | 4661.2 | 4661.2 | 7963.6 | 7963.6 | 5766.95 | 5766.95 | 3578.3 | 3578.3 | 9319.45 | 9319.45 | 4452.2 | 4452.2 | 9859.7 | 9859.7 | 7635.4 | 7635.4 | 2223.15 | 2223.15 | 2630.85 | 2630.85 | 1017.55 | 1017.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10374.65 | 10374.65 | 11626.3 | 11626.3 | 11219.25 | 11219.25 | 12068.55 | 12068.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6769.85 | 6769.85 | 5680.7 | 5680.7 | 8257.55 | 8257.55 | 1835.55 | 1835.55 | 7609.15 | 7609.15 | 9581.7 | 9581.7 | 8521.7 | 8521.7 | 3886.95 | 3886.95 | 1363.2 | 1363.2 | 8684.35 | 8684.35 | 5883.2 | 5883.2 | 2723.2 | 2723.2 | 992.35 | 992.35 | 6224.5 | 6224.5 | 10685.8 | 10685.8 | 5464.35 | 5464.35 | 1937.45 | 1937.45 | 7315.9 | 7315.9 | 7905.2 | 7905.2 | 10232.25 | 10232.25 | 7079.9 | 7079.9 | 3650.2 | 3650.2 | 1523.4 | 1523.4 | 1347.7 | 1347.7 | 1480 | 1480 | 345.55 | 345.55 | 3895 | 3895 | 2404.35 | 2404.35 | 755.35 | 755.35 | 999.15 | 999.15 | 912.85 | 912.85 | 830 | 830 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.21 | 0 | 0 | 0 | 0 | 0 | 35.08 | 0 | 0 | 0 | 0 | 0 | 3.08 | 0 | 0 | 0 | 0 | 0 | 7.67 | 0 | 0 | 0 | 0 | 0 | 6.9 | 0 | 0 | 0 | 0 | 0 | 2.12 | 0 | 0 | 0 | 0 | 0 | 7.24 | 0 | 0 | 0 | 0 | 0 | 2.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1905 | 10 | 1077 | 6 | 2845 | 34 | 0 | 6.9 | 0 | 0 | 0 | 0 | 0 | 7.24 | 0 | 0 | 0 | 0 | 315000 | 1000 | 188000 | 1000 | 502000 | 3000 | 501000 | 499000 | 12.7167 | 6.9 | 2.12 | 7.24 | 2.04 | 30.72% | 28.18% | 38.21 | 35.08 | 3.08 | 7.67 | 505732
2022-04-14 | 2023 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 90000 | 6:19 | 19:00 | 1655.1 | 1655.1 | 4609.4 | 4609.4 | 7901.95 | 7901.95 | 5674.45 | 5674.45 | 4263.45 | 4263.45 | 9161.55 | 9161.55 | 4418 | 4418 | 9710.25 | 9710.25 | 7547.3 | 7547.3 | 3336.7 | 3336.7 | 2675.1 | 2675.1 | 999.85 | 999.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10752.45 | 10752.45 | 11432.35 | 11432.35 | 11366 | 11366 | 11904.35 | 11904.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7111.3 | 7111.3 | 5944.55 | 5944.55 | 8789.55 | 8789.55 | 1765.75 | 1765.75 | 7550.75 | 7550.75 | 9518.25 | 9518.25 | 7995.7 | 7995.7 | 4393.95 | 4393.95 | 1309.6 | 1309.6 | 9047.6 | 9047.6 | 5671.5 | 5671.5 | 2625.4 | 2625.4 | 945.7 | 945.7 | 6022.3 | 6022.3 | 10097.95 | 10097.95 | 5678.2 | 5678.2 | 2001.4 | 2001.4 | 7357.8 | 7357.8 | 8270.2 | 8270.2 | 9886.6 | 9886.6 | 9194.6 | 9194.6 | 3480.65 | 3480.65 | 1461.6 | 1461.6 | 1282.9 | 1282.9 | 1809.55 | 1809.55 | 329.55 | 329.55 | 3751.25 | 3751.25 | 2277.9 | 2277.9 | 724.95 | 724.95 | 765.1 | 765.1 | 866.05 | 866.05 | 1625.8 | 1625.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 37.81 | 0 | 0 | 0 | 0 | 0 | 5.07 | 0 | 0 | 0 | 0 | 0 | 9.4 | 0 | 0 | 0 | 0 | 0 | 6.68 | 0 | 0 | 0 | 0 | 0 | 2.08 | 0 | 0 | 0 | 0 | 0 | 7.02 | 0 | 0 | 0 | 0 | 0 | 2.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2224 | 12 | 1268.1 | 6.9 | 3352 | 37 | 0 | 6.68 | 0 | 0 | 0 | 0 | 0 | 7.02 | 0 | 0 | 0 | 0 | 319000 | 2000 | 191100 | 900 | 507000 | 3000 | 507200 | 504000 | 12.6833 | 6.68 | 2.08 | 7.02 | 2.02 | 31.14% | 28.77% | 40 | 37.81 | 5.07 | 9.4 | 513924.4
2022-04-15 | 2023 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 92000 | 6:21 | 19:00 | 1741.8 | 1741.8 | 4830.3 | 4830.3 | 8265.15 | 8265.15 | 5954.5 | 5954.5 | 4487.6 | 4487.6 | 9647.75 | 9647.75 | 4654.9 | 4654.9 | 10174.9 | 10174.9 | 8380.5 | 8380.5 | 4857.3 | 4857.3 | 3729.9 | 3729.9 | 1059.35 | 1059.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11376.95 | 11376.95 | 12033.3 | 12033.3 | 11913.3 | 11913.3 | 12515.45 | 12515.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7752.2 | 7752.2 | 6475.1 | 6475.1 | 9534.45 | 9534.45 | 1896.65 | 1896.65 | 9833.95 | 9833.95 | 10106.45 | 10106.45 | 8810.65 | 8810.65 | 5491.1 | 5491.1 | 2383.4 | 2383.4 | 9794.45 | 9794.45 | 6028.05 | 6028.05 | 5798.1 | 5798.1 | 1022.9 | 1022.9 | 6615.25 | 6615.25 | 10822.25 | 10822.25 | 6368.65 | 6368.65 | 2156.1 | 2156.1 | 7922.55 | 7922.55 | 10820.75 | 10820.75 | 11200.25 | 11200.25 | 9977.6 | 9977.6 | 4728.35 | 4728.35 | 1575.95 | 1575.95 | 1379.25 | 1379.25 | 2203.55 | 2203.55 | 353.55 | 353.55 | 4039.95 | 4039.95 | 2426.45 | 2426.45 | 780.05 | 780.05 | 2042.4 | 2042.4 | 925.3 | 925.3 | 861.85 | 861.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.81 | 0 | 0 | 0 | 0 | 0 | 37.48 | 0 | 0 | 0 | 0 | 0 | 3.6 | 0 | 0 | 0 | 0 | 0 | 8.65 | 0 | 0 | 0 | 0 | 0 | 7.18 | 0 | 0 | 0 | 0 | 0 | 2.24 | 0 | 0 | 0 | 0 | 0 | 7.55 | 0 | 0 | 0 | 0 | 0 | 2.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2575 | 13 | 1492 | 7 | 3927 | 40 | 0 | 7.18 | 0 | 0 | 0 | 0 | 0 | 7.55 | 0 | 0 | 0 | 0 | 351000 | 1000 | 223900 | 100 | 575000 | 3000 | 573800 | 572000 | 12.65 | 7.18 | 2.24 | 7.55 | 2.17 | 31.2% | 28.74% | 40.81 | 37.48 | 3.6 | 8.65 | 575500.9
2022-04-16 | 2023 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 96000 | 6:21 | 19:02 | 2012.75 | 2012.75 | 4972.15 | 4972.15 | 8889.6 | 8889.6 | 5945.2 | 5945.2 | 4869.15 | 4869.15 | 9679.05 | 9679.05 | 4687.1 | 4687.1 | 10218.35 | 10218.35 | 11445.35 | 11445.35 | 4996.8 | 4996.8 | 4549.35 | 4549.35 | 1060.45 | 1060.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11408 | 11408 | 12044.2 | 12044.2 | 11924.65 | 11924.65 | 12534.15 | 12534.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7984.45 | 7984.45 | 6541.7 | 6541.7 | 9616.9 | 9616.9 | 1822.1 | 1822.1 | 9960.3 | 9960.3 | 10157.55 | 10157.55 | 9009.05 | 9009.05 | 5882.95 | 5882.95 | 2407.75 | 2407.75 | 9864.25 | 9864.25 | 6051.1 | 6051.1 | 7635.15 | 7635.15 | 1026.35 | 1026.35 | 6653.5 | 6653.5 | 10829.65 | 10829.65 | 6339.65 | 6339.65 | 2182.9 | 2182.9 | 7980.2 | 7980.2 | 10849 | 10849 | 11235.25 | 11235.25 | 9943.45 | 9943.45 | 5077.3 | 5077.3 | 1574.4 | 1574.4 | 1374.5 | 1374.5 | 2223.45 | 2223.45 | 352.1 | 352.1 | 4051 | 4051 | 2462.45 | 2462.45 | 782.65 | 782.65 | 1966.75 | 1966.75 | 924.35 | 924.35 | 868.35 | 868.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.29 | 0 | 0 | 0 | 0 | 0 | 37.54 | 0 | 0 | 0 | 0 | 0 | 4.2 | 0 | 0 | 0 | 0 | 0 | 7.8 | 0 | 0 | 0 | 0 | 0 | 7.1 | 0 | 0 | 0 | 0 | 0 | 2.23 | 0 | 0 | 0 | 0 | 0 | 7.46 | 0 | 0 | 0 | 0 | 0 | 2.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2922 | 14 | 1712 | 8 | 4516 | 44 | 0 | 7.1 | 0 | 0 | 0 | 0 | 0 | 7.46 | 0 | 0 | 0 | 0 | 347000 | 1000 | 220000 | 1000 | 589000 | 4000 | 565000 | 585000 | 12.6833 | 7.1 | 2.23 | 7.46 | 2.16 | 31.41% | 28.95% | 40.29 | 37.54 | 4.2 | 7.8 | 593733.6
2022-04-17 | 2023 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 102000 | 6:22 | 19:01 | 3475.05 | 3475.05 | 4988.05 | 4988.05 | 9302.75 | 9302.75 | 5824.75 | 5824.75 | 11350.7 | 11350.7 | 9735.15 | 9735.15 | 8448.75 | 8448.75 | 9984.1 | 9984.1 | 11218.6 | 11218.6 | 6034.05 | 6034.05 | 5023.2 | 5023.2 | 1039.35 | 1039.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11579.15 | 11579.15 | 11838 | 11838 | 11732.7 | 11732.7 | 12368.35 | 12368.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7824.35 | 7824.35 | 6405.4 | 6405.4 | 9423.7 | 9423.7 | 1770.95 | 1770.95 | 9879.65 | 9879.65 | 10512.75 | 10512.75 | 9570.6 | 9570.6 | 5698.3 | 5698.3 | 2458.65 | 2458.65 | 10373.8 | 10373.8 | 5979.5 | 5979.5 | 8207.6 | 8207.6 | 1001.8 | 1001.8 | 6509.7 | 6509.7 | 10567.85 | 10567.85 | 6185.35 | 6185.35 | 2133.65 | 2133.65 | 7820.85 | 7820.85 | 10638.55 | 10638.55 | 11012.6 | 11012.6 | 9810.55 | 9810.55 | 4995.7 | 4995.7 | 1552.25 | 1552.25 | 1348.4 | 1348.4 | 2166.75 | 2166.75 | 853.1 | 853.1 | 4291.15 | 4291.15 | 3929.1 | 3929.1 | 768.5 | 768.5 | 4505.6 | 4505.6 | 909.6 | 909.6 | 850.45 | 850.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.64 | 0 | 0 | 0 | 0 | 0 | 37.08 | 0 | 0 | 0 | 0 | 0 | 5.08 | 0 | 0 | 0 | 0 | 0 | 8.51 | 0 | 0 | 0 | 0 | 0 | 6.92 | 0 | 0 | 0 | 0 | 0 | 2.17 | 0 | 0 | 0 | 0 | 0 | 7.27 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3325 | 15 | 1948 | 9 | 5139 | 47 | 0 | 6.92 | 0 | 0 | 0 | 0 | 0 | 7.27 | 0 | 0 | 0 | 0 | 403000 | 1000 | 236000 | 1000 | 623000 | 3000 | 637000 | 620000 | 12.65 | 6.92 | 2.17 | 7.27 | 2.1 | 31.36% | 28.89% | 35.64 | 37.08 | 5.08 | 8.51 | 627798.9
2022-04-18 | 2023 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 109000 | 6:22 | 19:02 | 4092.8 | 4092.8 | 5454.85 | 5454.85 | 9512.15 | 9512.15 | 6856.7 | 6856.7 | 11555.3 | 11555.3 | 9953.35 | 9953.35 | 8605.7 | 8605.7 | 10214.85 | 10214.85 | 11225.9 | 11225.9 | 5786.85 | 5786.85 | 4917.45 | 4917.45 | 1042.15 | 1042.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11828.15 | 11828.15 | 11970 | 11970 | 11919.35 | 11919.35 | 12534.35 | 12534.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8008.05 | 8008.05 | 6538.1 | 6538.1 | 9617.6 | 9617.6 | 2489.15 | 2489.15 | 10032.45 | 10032.45 | 10647.35 | 10647.35 | 9809.1 | 9809.1 | 5864.7 | 5864.7 | 2502.95 | 2502.95 | 10549.35 | 10549.35 | 7223.65 | 7223.65 | 8700.95 | 8700.95 | 1025.85 | 1025.85 | 6678.55 | 6678.55 | 10821.1 | 10821.1 | 6391.1 | 6391.1 | 2174.25 | 2174.25 | 7978.35 | 7978.35 | 10833.85 | 10833.85 | 11228.05 | 11228.05 | 10543.7 | 10543.7 | 5149.85 | 5149.85 | 1576.7 | 1576.7 | 1446.4 | 1446.4 | 2200.65 | 2200.65 | 1299.5 | 1299.5 | 4735.2 | 4735.2 | 4389.25 | 4389.25 | 786.05 | 786.05 | 7767.4 | 7767.4 | 1141.3 | 1141.3 | 870.7 | 870.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.83 | 0 | 0 | 0 | 0 | 0 | 36.1 | 0 | 0 | 0 | 0 | 0 | 5.6 | 0 | 0 | 0 | 0 | 0 | 9.7 | 0 | 0 | 0 | 0 | 0 | 6.95 | 0 | 0 | 0 | 0 | 0 | 2.16 | 0 | 0 | 0 | 0 | 0 | 7.24 | 0 | 0 | 0 | 0 | 0 | 2.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3723 | 16 | 2212 | 10 | 5791.29 | 50.77 | 0 | 6.95 | 0 | 0 | 0 | 0 | 0 | 7.24 | 0 | 0 | 0 | 0 | 398000 | 1000 | 264000 | 1000 | 652290 | 3770 | 660000 | 648520 | 12.6667 | 6.95 | 2.16 | 7.24 | 2.09 | 31.08% | 28.87% | 38.83 | 36.1 | 5.6 | 9.7 | 656982.2
2022-04-19 | 2023 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 111000 | 6:22 | 19:02 | 4867.3 | 4867.3 | 5328.65 | 5328.65 | 9260.3 | 9260.3 | 6995.75 | 6995.75 | 11307.05 | 11307.05 | 10015.65 | 10015.65 | 10548.1 | 10548.1 | 10851.5 | 10851.5 | 11259.85 | 11259.85 | 6347.3 | 6347.3 | 5030.35 | 5030.35 | 1038.25 | 1038.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11675 | 11675 | 11796.35 | 11796.35 | 11753.1 | 11753.1 | 12388.2 | 12388.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7756.65 | 7756.65 | 6349.15 | 6349.15 | 9357.55 | 9357.55 | 2847.45 | 2847.45 | 9835.25 | 9835.25 | 10527.85 | 10527.85 | 9509.45 | 9509.45 | 5706.15 | 5706.15 | 2826.1 | 2826.1 | 10253.7 | 10253.7 | 8573.25 | 8573.25 | 9389 | 9389 | 992.8 | 992.8 | 6523.2 | 6523.2 | 10475.2 | 10475.2 | 6173 | 6173 | 2121.9 | 2121.9 | 7779.1 | 7779.1 | 10555.4 | 10555.4 | 10936.5 | 10936.5 | 11306.35 | 11306.35 | 5040.55 | 5040.55 | 1526.45 | 1526.45 | 1447.6 | 1447.6 | 2156.75 | 2156.75 | 1400 | 1400 | 4787.4 | 4787.4 | 4276.35 | 4276.35 | 766.45 | 766.45 | 7515.7 | 7515.7 | 1113.2 | 1113.2 | 847.35 | 847.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.59 | 0 | 0 | 0 | 0 | 0 | 38.21 | 0 | 0 | 0 | 0 | 0 | 3.78 | 0 | 0 | 0 | 0 | 0 | 6.94 | 0 | 0 | 0 | 0 | 0 | 6.97 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 | 0 | 0 | 7.27 | 0 | 0 | 0 | 0 | 0 | 2.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4125 | 17 | 2469 | 11 | 6448 | 54 | 0 | 6.97 | 0 | 0 | 0 | 0 | 0 | 7.27 | 0 | 0 | 0 | 0 | 402000 | 1000 | 257000 | 1000 | 656710 | 3230 | 657000 | 653480 | 12.6667 | 6.97 | 2.2 | 7.27 | 2.13 | 31.56% | 29.3% | 36.59 | 38.21 | 3.78 | 6.94 | 662271
2022-04-20 | 2023 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 120000 | 6:23 | 19:03 | 5566.7 | 5566.7 | 5819.8 | 5819.8 | 8766.5 | 8766.5 | 6609.05 | 6609.05 | 10829.6 | 10829.6 | 9978.9 | 9978.9 | 10215.1 | 10215.1 | 10372.35 | 10372.35 | 10578.75 | 10578.75 | 6957.55 | 6957.55 | 4755.05 | 4755.05 | 982.25 | 982.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10999.85 | 10999.85 | 11029.5 | 11029.5 | 10939 | 10939 | 11671.85 | 11671.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7294.05 | 7294.05 | 5933.5 | 5933.5 | 9432.75 | 9432.75 | 2661.9 | 2661.9 | 9149.1 | 9149.1 | 8896.65 | 8896.65 | 9900.3 | 9900.3 | 5318.8 | 5318.8 | 2638.75 | 2638.75 | 9540.7 | 9540.7 | 8405.15 | 8405.15 | 8918.15 | 8918.15 | 932.8 | 932.8 | 6130.35 | 6130.35 | 9844.75 | 9844.75 | 5784.65 | 5784.65 | 1976.45 | 1976.45 | 7260.85 | 7260.85 | 9883.7 | 9883.7 | 10126.45 | 10126.45 | 10594.95 | 10594.95 | 4691.8 | 4691.8 | 1395.2 | 1395.2 | 1350.4 | 1350.4 | 1993.9 | 1993.9 | 3003.45 | 3003.45 | 5027.4 | 5027.4 | 4022.55 | 4022.55 | 707.9 | 707.9 | 8950.3 | 8950.3 | 1123.8 | 1123.8 | 791.1 | 791.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.43 | 36.13 | 0 | 0 | 0 | 0 | 0 | 37.74 | 0 | 0 | 0 | 0 | 3.79 | 3.75 | 0 | 0 | 0 | 0 | 9.26 | 9.71 | 0 | 0 | 0 | 0 | 6.74 | 6.29 | 0 | 0 | 0 | 0 | 1.47 | 2.07 | 0 | 0 | 0 | 0 | 6.61 | 7.09 | 0 | 0 | 0 | 0 | 1.51 | 2.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4512 | 18 | 2718 | 12 | 7082 | 57 | 6.74 | 6.29 | 0 | 0 | 0 | 0 | 6.61 | 7.09 | 0 | 0 | 0 | 0 | 387000 | 1000 | 249000 | 1000 | 634000 | 3000 | 634000 | 631000 | 12.6667 | 6.515 | 1.77 | 6.85 | 1.76 | 27.17% | 25.69% | 36.28 | 37.74 | 3.77 | 9.485 | 639508.7
2022-04-21 | 2023 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 125000 | 6:25 | 19:05 | 6429.05 | 6429.05 | 5233.1 | 5233.1 | 9804.45 | 9804.45 | 7718.5 | 7718.5 | 11473.2 | 11473.2 | 11347.55 | 11347.55 | 11035.15 | 11035.15 | 11594.9 | 11594.9 | 11574.6 | 11574.6 | 7748.85 | 7748.85 | 5211.75 | 5211.75 | 1124.6 | 1124.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11303.15 | 11303.15 | 11711.7 | 11711.7 | 11563.25 | 11563.25 | 12072.35 | 12072.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7619.6 | 7619.6 | 6302 | 6302 | 9889.45 | 9889.45 | 2851.25 | 2851.25 | 9561.65 | 9561.65 | 10209.7 | 10209.7 | 9363.95 | 9363.95 | 5578.55 | 5578.55 | 3598.9 | 3598.9 | 9907.35 | 9907.35 | 8855.85 | 8855.85 | 9331.15 | 9331.15 | 1011.3 | 1011.3 | 6577 | 6577 | 10991.35 | 10991.35 | 6840.1 | 6840.1 | 2174.8 | 2174.8 | 8027.5 | 8027.5 | 10561.3 | 10561.3 | 11086.1 | 11086.1 | 11188.4 | 11188.4 | 4958.5 | 4958.5 | 1508.85 | 1508.85 | 1545.85 | 1545.85 | 2217.7 | 2217.7 | 4056.1 | 4056.1 | 6489.95 | 6489.95 | 4404.65 | 4404.65 | 776 | 776 | 10793.4 | 10793.4 | 2076 | 2076 | 842 | 842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.98 | 35.84 | 0 | 33.96 | 34.8 | 0 | 0 | 41.33 | 0 | 0 | 0 | 0 | 4.99 | 5.14 | 0 | 5.1 | 5.24 | 0 | 11.15 | 10.73 | 0 | 11.4 | 12.33 | 0 | 7.08 | 7.17 | 0 | 6.98 | 7.25 | 0 | 1.52 | 2.16 | 0 | 2.23 | 2.1 | 0 | 6.99 | 7.39 | 0 | 7.79 | 8.32 | 0 | 1.55 | 2.08 | 0 | 2.15 | 2.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4926 | 20 | 2996 | 13 | 7773 | 61 | 7.08 | 7.17 | 0 | 6.98 | 7.25 | 0 | 6.99 | 7.39 | 0 | 7.79 | 8.32 | 0 | 414000 | 2000 | 278000 | 1000 | 691000 | 4000 | 689000 | 687000 | 12.6667 | 7.12 | 2.0025 | 7.6225 | 1.9925 | 28.12% | 26.14% | 36.395 | 41.33 | 5.1175 | 11.4025 | 696284.8
2022-04-22 | 2023 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 128000 | 6:26 | 19:06 | 7001.35 | 7001.35 | 5654.1 | 5654.1 | 10563.6 | 10563.6 | 8292.2 | 8292.2 | 12555.45 | 12555.45 | 12083.55 | 12083.55 | 11838.75 | 11838.75 | 12429.45 | 12429.45 | 12225.45 | 12225.45 | 8204.9 | 8204.9 | 5864.65 | 5864.65 | 3351.85 | 3351.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11996.25 | 11996.25 | 12371.75 | 12371.75 | 12303.7 | 12303.7 | 12717.9 | 12717.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8669.65 | 8669.65 | 6907.95 | 6907.95 | 10610.5 | 10610.5 | 3104.95 | 3104.95 | 10144.95 | 10144.95 | 10782.85 | 10782.85 | 10028.1 | 10028.1 | 5993.65 | 5993.65 | 5461.6 | 5461.6 | 10640.95 | 10640.95 | 10978.6 | 10978.6 | 10000.45 | 10000.45 | 1110.45 | 1110.45 | 7091.45 | 7091.45 | 11651.1 | 11651.1 | 7232.3 | 7232.3 | 2315.65 | 2315.65 | 8526.25 | 8526.25 | 11233.95 | 11233.95 | 11692.1 | 11692.1 | 11709.25 | 11709.25 | 5205.15 | 5205.15 | 1556.05 | 1556.05 | 1641.85 | 1641.85 | 2351.05 | 2351.05 | 4343.35 | 4343.35 | 7018.55 | 7018.55 | 4694.45 | 4694.45 | 818.05 | 818.05 | 11430.1 | 11430.1 | 2196.65 | 2196.65 | 894.4 | 894.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.59 | 35.47 | 0 | 39.51 | 39.88 | 0 | 0 | 37.37 | 0 | 0 | 0 | 0 | 2.86 | 2.9 | 0 | 2.9 | 2.93 | 0 | 8.55 | 8.45 | 0 | 7.3 | 7.13 | 0 | 7.74 | 7.74 | 0 | 7.76 | 7.55 | 0 | 1.65 | 2.32 | 0 | 2.43 | 2.25 | 0 | 7.58 | 7.96 | 0 | 8.42 | 8.85 | 0 | 1.68 | 2.23 | 0 | 2.33 | 2.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5375 | 21 | 3298 | 13 | 8522 | 64 | 7.74 | 7.74 | 0 | 7.76 | 7.55 | 0 | 7.58 | 7.96 | 0 | 8.42 | 8.85 | 0 | 449000 | 1000 | 302000 | 0 | 749000 | 3000 | 750000 | 746000 | 12.6667 | 7.6975 | 2.1625 | 8.2025 | 2.1425 | 28.09% | 26.12% | 37.6125 | 37.37 | 2.8975 | 7.8575 | 754982.5
2022-04-23 | 2023 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 129000 | 6:21 | 19:08 | 6855.9 | 6855.9 | 5570.3 | 5570.3 | 10399.95 | 10399.95 | 8221.2 | 8221.2 | 12488.85 | 12488.85 | 11963.45 | 11963.45 | 11722.1 | 11722.1 | 12321.4 | 12321.4 | 12099.55 | 12099.55 | 8067.5 | 8067.5 | 5761.45 | 5761.45 | 5513.1 | 5513.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11860.2 | 11860.2 | 12249.5 | 12249.5 | 12146.65 | 12146.65 | 12601.55 | 12601.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8517.45 | 8517.45 | 6833.6 | 6833.6 | 10438.3 | 10438.3 | 4503.35 | 4503.35 | 10037.35 | 10037.35 | 10700.75 | 10700.75 | 9855.15 | 9855.15 | 5889.55 | 5889.55 | 5751.35 | 5751.35 | 10709.15 | 10709.15 | 10856.35 | 10856.35 | 9848.7 | 9848.7 | 1091.75 | 1091.75 | 6991 | 6991 | 11504.7 | 11504.7 | 7083.6 | 7083.6 | 2275.6 | 2275.6 | 8383.9 | 8383.9 | 11096.45 | 11096.45 | 11507.15 | 11507.15 | 11495.25 | 11495.25 | 5118 | 5118 | 1530.05 | 1530.05 | 1615.55 | 1615.55 | 2319.8 | 2319.8 | 5077.25 | 5077.25 | 3998.3 | 3998.3 | 4813.95 | 4813.95 | 800.85 | 800.85 | 11237.55 | 11237.55 | 2167 | 2167 | 879.05 | 879.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.84 | 36.37 | 0 | 36.4 | 36.44 | 0 | 0 | 38.44 | 0 | 0 | 0 | 0 | 2.38 | 2.28 | 0 | 2.31 | 2.27 | 0 | 6.54 | 5.37 | 0 | 5.38 | 6.17 | 0 | 7.5 | 7.62 | 0 | 7.46 | 7.65 | 0 | 1.63 | 2.28 | 0 | 2.42 | 2.23 | 0 | 7.47 | 7.83 | 0 | 8.29 | 8.71 | 0 | 1.67 | 2.2 | 0 | 2.32 | 2.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5825 | 22 | 3593 | 14 | 9265 | 68 | 7.5 | 7.62 | 0 | 7.46 | 7.65 | 0 | 7.47 | 7.83 | 0 | 8.29 | 8.71 | 0 | 450000 | 1000 | 295000 | 1000 | 743000 | 4000 | 743000 | 739000 | 12.7833 | 7.5575 | 2.14 | 8.075 | 2.1275 | 28.32% | 26.35% | 36.5125 | 38.44 | 2.31 | 5.865 | 749540.9
2022-04-24 | 2023 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 132000 | 6:19 | 19:07 | 6401.35 | 6401.35 | 5277.65 | 5277.65 | 9758.05 | 9758.05 | 7768.9 | 7768.9 | 11884.75 | 11884.75 | 11357.95 | 11357.95 | 11189.35 | 11189.35 | 11714.65 | 11714.65 | 11417.1 | 11417.1 | 7520.1 | 7520.1 | 5470.25 | 5470.25 | 5343 | 5343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11336.8 | 11336.8 | 11735.05 | 11735.05 | 11581.45 | 11581.45 | 12131.65 | 12131.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8170.4 | 8170.4 | 6561.55 | 6561.55 | 10017.45 | 10017.45 | 4311.45 | 4311.45 | 9632.65 | 9632.65 | 10304.65 | 10304.65 | 9432.35 | 9432.35 | 5629.55 | 5629.55 | 5734.75 | 5734.75 | 10608.95 | 10608.95 | 10776.25 | 10776.25 | 9614.35 | 9614.35 | 1053.65 | 1053.65 | 6766.4 | 6766.4 | 11132.25 | 11132.25 | 7744.3 | 7744.3 | 2213.2 | 2213.2 | 8113.95 | 8113.95 | 10743.7 | 10743.7 | 11137.7 | 11137.7 | 11182 | 11182 | 4950.15 | 4950.15 | 1480.55 | 1480.55 | 1559.05 | 1559.05 | 2235.5 | 2235.5 | 5935.3 | 5935.3 | 4290.9 | 4290.9 | 4714 | 4714 | 2171.8 | 2171.8 | 10980.95 | 10980.95 | 2098.35 | 2098.35 | 845.85 | 845.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.4 | 37.09 | 0 | 37.25 | 37.16 | 0 | 0 | 38.36 | 0 | 0 | 0 | 0 | 2.55 | 2.51 | 0 | 2.65 | 2.59 | 0 | 7.15 | 6.11 | 0 | 8.15 | 10.66 | 0 | 7.2 | 7.2 | 0 | 7.29 | 7.4 | 0 | 1.54 | 2.17 | 0 | 2.17 | 2.14 | 0 | 7.03 | 7.486 | 0 | 7.983 | 8.4 | 0 | 1.58 | 2.1 | 0 | 2.212 | 2.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6254 | 24 | 3887 | 15 | 9987 | 71 | 7.2 | 7.2 | 0 | 7.29 | 7.4 | 0 | 7.03 | 7.486 | 0 | 7.983 | 8.4 | 0 | 429000 | 2000 | 294000 | 1000 | 722000 | 3000 | 720000 | 719000 | 12.8 | 7.2725 | 2.005 | 7.7248 | 2.008 | 27.57% | 25.99% | 37.225 | 38.36 | 2.575 | 8.0175 | 728063.9
2022-04-25 | 2023 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 134000 | 6:14 | 19:09 | 6329.8 | 6329.8 | 5194.35 | 5194.35 | 9546.85 | 9546.85 | 7579.2 | 7579.2 | 11855.75 | 11855.75 | 11180.95 | 11180.95 | 10960.85 | 10960.85 | 11417.75 | 11417.75 | 11136.9 | 11136.9 | 7920.85 | 7920.85 | 5359.45 | 5359.45 | 5406.35 | 5406.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11124.7 | 11124.7 | 11464.45 | 11464.45 | 11389.4 | 11389.4 | 11844.95 | 11844.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8306.05 | 8306.05 | 6664.65 | 6664.65 | 10211.35 | 10211.35 | 4386.5 | 4386.5 | 9800.95 | 9800.95 | 10376.5 | 10376.5 | 9592.9 | 9592.9 | 5731.3 | 5731.3 | 1652.5 | 1652.5 | 10767.7 | 10767.7 | 10610.5 | 10610.5 | 9461.7 | 9461.7 | 1040 | 1040 | 6679.15 | 6679.15 | 10994.75 | 10994.75 | 7780.9 | 7780.9 | 2138.2 | 2138.2 | 7894.75 | 7894.75 | 10462.45 | 10462.45 | 10865.15 | 10865.15 | 10754.6 | 10754.6 | 5462.45 | 5462.45 | 1431.15 | 1431.15 | 1497.7 | 1497.7 | 2173.6 | 2173.6 | 6555.05 | 6555.05 | 4213.7 | 4213.7 | 4883.65 | 4883.65 | 2112.9 | 2112.9 | 10680.25 | 10680.25 | 2028.65 | 2028.65 | 816.75 | 816.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.1 | 37.87 | 0 | 37.82 | 37.98 | 0 | 0 | 39.25 | 0 | 0 | 0 | 0 | 4.13 | 4.1 | 0 | 4.17 | 4.26 | 0 | 8.65 | 7.97 | 0 | 7.91 | 7.49 | 0 | 7.14 | 7.1 | 0 | 7.26 | 7.18 | 0 | 1.54 | 2.1 | 0 | 2.35 | 2.06 | 0 | 6.91 | 7.27 | 0 | 8.04 | 8.1 | 0 | 1.58 | 2.04 | 0 | 2.24 | 2.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6681 | 24 | 4172 | 16 | 10697 | 74 | 7.14 | 7.1 | 0 | 7.26 | 7.18 | 0 | 6.91 | 7.27 | 0 | 8.04 | 8.1 | 0 | 427000 | 0 | 285000 | 1000 | 710000 | 3000 | 711000 | 707000 | 12.9167 | 7.17 | 2.0125 | 7.58 | 2.0025 | 28.07% | 26.42% | 37.9425 | 39.25 | 4.165 | 8.005 | 715481.9
2022-04-26 | 2023 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 135000 | 6:18 | 19:09 | 6855.8 | 6855.8 | 5603.85 | 5603.85 | 10357.5 | 10357.5 | 9363.5 | 9363.5 | 12635.85 | 12635.85 | 12000.4 | 12000.4 | 11748.45 | 11748.45 | 12289.15 | 12289.15 | 11884.4 | 11884.4 | 9618.9 | 9618.9 | 5764.95 | 5764.95 | 5895.1 | 5895.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11943.7 | 11943.7 | 12331.75 | 12331.75 | 12200.6 | 12200.6 | 12674.1 | 12674.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9008.5 | 9008.5 | 6987.7 | 6987.7 | 10614.35 | 10614.35 | 4528.25 | 4528.25 | 10183.85 | 10183.85 | 10793.75 | 10793.75 | 9930.95 | 9930.95 | 5944.7 | 5944.7 | 7248.75 | 7248.75 | 11384.85 | 11384.85 | 11227.75 | 11227.75 | 10020.2 | 10020.2 | 1098 | 1098 | 7073.8 | 7073.8 | 12022.7 | 12022.7 | 9244.6 | 9244.6 | 2294.05 | 2294.05 | 8443.25 | 8443.25 | 11214.7 | 11214.7 | 11632.1 | 11632.1 | 11514.35 | 11514.35 | 6198.95 | 6198.95 | 1527.7 | 1527.7 | 1586.3 | 1586.3 | 2317.3 | 2317.3 | 6999.2 | 6999.2 | 4929.15 | 4929.15 | 5575.75 | 5575.75 | 4941.25 | 4941.25 | 11730.3 | 11730.3 | 2173.7 | 2173.7 | 861.7 | 861.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.54 | 37.54 | 0 | 37.59 | 37.6 | 0 | 0 | 39.49 | 0 | 0 | 0 | 0 | 3.38 | 3.41 | 0 | 3.42 | 3.55 | 0 | 7.62 | 8.19 | 0 | 7.95 | 7.63 | 0 | 7.76 | 7.77 | 0 | 7.59 | 7.8 | 0 | 1.63 | 2.23 | 0 | 2.24 | 2.08 | 0 | 7.54 | 7.94 | 0 | 8.4 | 8.82 | 0 | 1.67 | 2.25 | 0 | 2.23 | 2.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7140 | 26 | 4497 | 17 | 11479 | 77 | 7.76 | 7.77 | 0 | 7.59 | 7.8 | 0 | 7.54 | 7.94 | 0 | 8.4 | 8.82 | 0 | 459000 | 2000 | 325000 | 1000 | 782000 | 3000 | 781000 | 779000 | 12.85 | 7.73 | 2.045 | 8.175 | 2.095 | 26.46% | 25.63% | 37.5675 | 39.49 | 3.44 | 7.8475 | 788840.9
2022-04-27 | 2023 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 139000 | 6:14 | 19:12 | 7201.95 | 7201.95 | 5810.05 | 5810.05 | 11341.35 | 11341.35 | 9741.7 | 9741.7 | 12648.25 | 12648.25 | 12022.75 | 12022.75 | 11768.8 | 11768.8 | 12309.8 | 12309.8 | 11929 | 11929 | 10144.45 | 10144.45 | 6169.05 | 6169.05 | 5917.15 | 5917.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11973.55 | 11973.55 | 12355.5 | 12355.5 | 12218.4 | 12218.4 | 12692.15 | 12692.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9084.3 | 9084.3 | 7116.8 | 7116.8 | 10675.5 | 10675.5 | 5032.45 | 5032.45 | 10180.15 | 10180.15 | 10840.6 | 10840.6 | 10002.9 | 10002.9 | 6028.9 | 6028.9 | 8224.1 | 8224.1 | 11436.8 | 11436.8 | 11439.75 | 11439.75 | 10148 | 10148 | 1106.45 | 1106.45 | 7154.2 | 7154.2 | 12351.85 | 12351.85 | 9760.5 | 9760.5 | 2310.95 | 2310.95 | 8456.5 | 8456.5 | 11284 | 11284 | 11691.6 | 11691.6 | 11724.85 | 11724.85 | 7591.05 | 7591.05 | 1542.95 | 1542.95 | 1563.45 | 1563.45 | 2410.1 | 2410.1 | 7777.2 | 7777.2 | 5145.6 | 5145.6 | 5826.4 | 5826.4 | 4968.4 | 4968.4 | 11994.4 | 11994.4 | 2178.7 | 2178.7 | 876.6 | 876.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.86 | 38.59 | 0 | 38.41 | 38.41 | 0 | 0 | 39.94 | 0 | 0 | 0 | 0 | 4.83 | 4.72 | 0 | 4.84 | 4.62 | 0 | 9.23 | 8.86 | 0 | 8.8 | 9.26 | 0 | 7.74 | 7.72 | 0 | 7.6 | 7.78 | 0 | 1.64 | 2.15 | 0 | 2.46 | 2.24 | 0 | 7.5 | 7.87 | 0 | 8.39 | 8.79 | 0 | 1.67 | 2.16 | 0 | 2.34 | 2.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7608 | 27 | 4833 | 18 | 12282 | 80 | 7.74 | 7.72 | 0 | 7.6 | 7.78 | 0 | 7.5 | 7.87 | 0 | 8.39 | 8.79 | 0 | 468000 | 1000 | 336000 | 1000 | 803000 | 3000 | 802000 | 800000 | 12.9667 | 7.71 | 2.1225 | 8.1375 | 2.125 | 27.53% | 26.11% | 38.5675 | 39.94 | 4.7525 | 9.0375 | 808339.8
2022-04-28 | 2023 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 140000 | 6:14 | 19:12 | 7234.55 | 7234.55 | 6669.1 | 6669.1 | 11381.5 | 11381.5 | 9920.3 | 9920.3 | 12568.75 | 12568.75 | 12006.8 | 12006.8 | 11790.05 | 11790.05 | 12288.25 | 12288.25 | 11951.7 | 11951.7 | 11129.95 | 11129.95 | 6745.05 | 6745.05 | 5967.85 | 5967.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11923.85 | 11923.85 | 12294.5 | 12294.5 | 12175.2 | 12175.2 | 12844.15 | 12844.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11003.25 | 11003.25 | 7804.05 | 7804.05 | 10688.95 | 10688.95 | 5306.05 | 5306.05 | 10211.4 | 10211.4 | 10784.2 | 10784.2 | 10098.15 | 10098.15 | 7236.85 | 7236.85 | 8188.5 | 8188.5 | 11432.45 | 11432.45 | 11426.4 | 11426.4 | 10202.05 | 10202.05 | 1108.6 | 1108.6 | 7161.55 | 7161.55 | 12267.5 | 12267.5 | 9756.85 | 9756.85 | 2315.25 | 2315.25 | 8468.6 | 8468.6 | 11302.55 | 11302.55 | 11682.7 | 11682.7 | 11657.15 | 11657.15 | 7472.4 | 7472.4 | 1553 | 1553 | 1567.9 | 1567.9 | 2694.6 | 2694.6 | 8691.25 | 8691.25 | 5168.55 | 5168.55 | 5999.3 | 5999.3 | 5473.85 | 5473.85 | 11964.45 | 11964.45 | 2193.15 | 2193.15 | 893.25 | 893.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.99 | 38.75 | 0 | 38.58 | 38.7 | 0 | 0 | 46.4 | 0 | 0 | 0 | 0 | 5.92 | 6.12 | 0 | 6.18 | 6.09 | 0 | 11.92 | 12.43 | 0 | 12.05 | 11.83 | 0 | 7.96 | 7.97 | 0 | 7.81 | 8.01 | 0 | 1.71 | 1.84 | 0 | 2.55 | 2.32 | 0 | 7.7 | 8.12 | 0 | 8.6 | 9.04 | 0 | 1.75 | 1.81 | 0 | 2.55 | 2.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8089 | 28 | 5173 | 18 | 13101 | 84 | 7.96 | 7.97 | 0 | 7.81 | 8.01 | 0 | 7.7 | 8.12 | 0 | 8.6 | 9.04 | 0 | 481000 | 1000 | 340000 | 0 | 819000 | 4000 | 820000 | 815000 | 12.9667 | 7.9375 | 2.105 | 8.365 | 2.1075 | 26.52% | 25.19% | 38.755 | 46.4 | 6.0775 | 12.0575 | 825332.6
2022-04-29 | 2023 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 142000 | 6:13 | 19:13 | 7367.15 | 7367.15 | 6911.85 | 6911.85 | 11566.2 | 11566.2 | 10143.5 | 10143.5 | 12857.1 | 12857.1 | 12240.5 | 12240.5 | 12056.65 | 12056.65 | 12586.95 | 12586.95 | 12204.1 | 12204.1 | 11895.1 | 11895.1 | 7241.4 | 7241.4 | 6024.65 | 6024.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12152.85 | 12152.85 | 12573.15 | 12573.15 | 12421.8 | 12421.8 | 12872.85 | 12872.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11118.7 | 11118.7 | 8825.8 | 8825.8 | 10840.1 | 10840.1 | 5373.05 | 5373.05 | 10372.15 | 10372.15 | 11004.45 | 11004.45 | 10248.5 | 10248.5 | 7337.2 | 7337.2 | 9270.3 | 9270.3 | 11600.6 | 11600.6 | 11609.85 | 11609.85 | 10323.6 | 10323.6 | 1126.2 | 1126.2 | 7285.55 | 7285.55 | 12535.25 | 12535.25 | 9932.6 | 9932.6 | 2370.05 | 2370.05 | 8631.65 | 8631.65 | 11512.8 | 11512.8 | 11899.3 | 11899.3 | 11918.7 | 11918.7 | 7680.1 | 7680.1 | 1570.95 | 1570.95 | 1609.5 | 1609.5 | 2684.65 | 2684.65 | 9388.85 | 9388.85 | 5259.9 | 5259.9 | 6088.8 | 6088.8 | 7972.5 | 7972.5 | 12221.55 | 12221.55 | 2231.85 | 2231.85 | 900.2 | 900.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.06 | 35.99 | 0 | 35.73 | 35.96 | 0 | 0 | 37.72 | 0 | 0 | 0 | 0 | 3.89 | 4.25 | 0 | 4.35 | 4.16 | 0 | 8.43 | 8.75 | 0 | 8.46 | 8.4 | 0 | 7.93 | 7.91 | 0 | 7.78 | 7.96 | 0 | 1.66 | 1.81 | 0 | 2.51 | 2.28 | 0 | 7.65 | 8.05 | 0 | 8.54 | 8.93 | 0 | 1.69 | 1.78 | 0 | 2.38 | 2.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8583 | 29 | 5527 | 19 | 13947 | 87 | 7.93 | 7.91 | 0 | 7.78 | 7.96 | 0 | 7.65 | 8.05 | 0 | 8.54 | 8.93 | 0 | 494000 | 1000 | 354000 | 1000 | 846000 | 3000 | 846000 | 843000 | 13 | 7.895 | 2.065 | 8.2925 | 2.055 | 26.16% | 24.78% | 35.935 | 37.72 | 4.1625 | 8.51 | 851722.1
2022-04-30 | 2023 | 2022 | Year_1 | Year_1 | 2022-05-01 | 30 | 142000 | 6:08 | 19:13 | 6962.05 | 6962.05 | 6286.85 | 6286.85 | 10515.45 | 10515.45 | 9174.9 | 9174.9 | 11929.3 | 11929.3 | 11170.8 | 11170.8 | 10968.8 | 10968.8 | 11570.95 | 11570.95 | 10756.4 | 10756.4 | 10768.3 | 10768.3 | 6527.15 | 6527.15 | 3153.5 | 3153.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11110 | 11110 | 11474.8 | 11474.8 | 11327.3 | 11327.3 | 11698.4 | 11698.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9937.9 | 9937.9 | 7965.45 | 7965.45 | 9699.8 | 9699.8 | 4798.2 | 4798.2 | 9389.55 | 9389.55 | 10108.8 | 10108.8 | 9173.75 | 9173.75 | 6566.6 | 6566.6 | 8566.35 | 8566.35 | 8468.45 | 8468.45 | 7869.25 | 7869.25 | 9213.3 | 9213.3 | 1004.05 | 1004.05 | 6511 | 6511 | 11332.1 | 11332.1 | 8878.55 | 8878.55 | 2101.95 | 2101.95 | 7675.2 | 7675.2 | 10170.55 | 10170.55 | 10600.65 | 10600.65 | 10794.95 | 10794.95 | 7778.6 | 7778.6 | 1392.55 | 1392.55 | 1426.5 | 1426.5 | 2835.1 | 2835.1 | 8562 | 8562 | 4540.55 | 4540.55 | 5420.05 | 5420.05 | 7341.85 | 7341.85 | 10963.8 | 10963.8 | 1985.3 | 1985.3 | 795.15 | 795.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.1 | 38.38 | 0 | 38.71 | 38.91 | 0 | 0 | 40.6 | 0 | 0 | 0 | 0 | 3.08 | 3.22 | 0 | 3.08 | 3.12 | 0 | 6.7 | 6.13 | 0 | 7.13 | 6.7 | 0 | 7.21 | 7.12 | 0 | 6.97 | 7.08 | 0 | 1.54 | 1.59 | 0 | 2.27 | 2.02 | 0 | 6.93 | 7.24 | 0 | 7.65 | 7.92 | 0 | 1.57 | 1.56 | 0 | 2.15 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9026.3 | 30 | 5838 | 20 | 14699 | 91 | 7.21 | 7.12 | 0 | 6.97 | 7.08 | 0 | 6.93 | 7.24 | 0 | 7.65 | 7.92 | 0 | 443300 | 1000 | 311000 | 1000 | 752000 | 4000 | 752300 | 748000 | 13.0833 | 7.095 | 1.855 | 7.435 | 1.845 | 26.15% | 24.82% | 38.775 | 40.6 | 3.125 | 6.665 | 758525.6
2022-05-01 | 2023 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 142000 | 6:07 | 19:10 | 7599.85 | 7599.85 | 6597.5 | 6597.5 | 11020.5 | 11020.5 | 9657.1 | 9657.1 | 12454.3 | 12454.3 | 11790.1 | 11790.1 | 11604 | 11604 | 12224 | 12224 | 11945.65 | 11945.65 | 11599.85 | 11599.85 | 7468.35 | 7468.35 | 6006.9 | 6006.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11732.5 | 11732.5 | 12154.3 | 12154.3 | 11985.15 | 11985.15 | 12515.8 | 12515.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10644.65 | 10644.65 | 8509 | 8509 | 10367.5 | 10367.5 | 2753 | 2753 | 9977.05 | 9977.05 | 10678.6 | 10678.6 | 9796.4 | 9796.4 | 7006.65 | 7006.65 | 9174.35 | 9174.35 | 9051.85 | 9051.85 | 8377.1 | 8377.1 | 9873.8 | 9873.8 | 1076 | 1076 | 6974.55 | 6974.55 | 12110.25 | 12110.25 | 9534.4 | 9534.4 | 2257.95 | 2257.95 | 8207.3 | 8207.3 | 10901.75 | 10901.75 | 11380.8 | 11380.8 | 11653.2 | 11653.2 | 8368 | 8368 | 1521.65 | 1521.65 | 1533 | 1533 | 3375.45 | 3375.45 | 9138.85 | 9138.85 | 4797.8 | 4797.8 | 5848.75 | 5848.75 | 10372 | 10372 | 11863 | 11863 | 2144.2 | 2144.2 | 859.95 | 859.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.46 | 39.3 | 0 | 39.05 | 39.2 | 0 | 0 | 41.04 | 0 | 0 | 0 | 0 | 4.54 | 4.37 | 0 | 4.69 | 4.54 | 0 | 9.64 | 8.99 | 0 | 9.59 | 7.66 | 0 | 7.66 | 7.7 | 0 | 7.51 | 7.73 | 0 | 1.6 | 1.77 | 0 | 2.42 | 2.22 | 0 | 7.4 | 7.82 | 0 | 8.27 | 8.6 | 0 | 1.63 | 1.74 | 0 | 2.29 | 2.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9499 | 32 | 6177 | 21 | 15509 | 94 | 7.66 | 7.7 | 0 | 7.51 | 7.73 | 0 | 7.4 | 7.82 | 0 | 8.27 | 8.6 | 0 | 472700 | 2000 | 339000 | 1000 | 810000 | 3000 | 808700 | 807000 | 13.05 | 7.65 | 2.0025 | 8.0225 | 1.9725 | 26.18% | 24.59% | 39.2525 | 41.04 | 4.535 | 8.97 | 816969.3
2022-05-02 | 2023 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 144000 | 6:07 | 19:10 | 7159.95 | 7159.95 | 5093.75 | 5093.75 | 9927.05 | 9927.05 | 8799.5 | 8799.5 | 11279.6 | 11279.6 | 10647.75 | 10647.75 | 10485.85 | 10485.85 | 11043 | 11043 | 10927.1 | 10927.1 | 10493.2 | 10493.2 | 6757.65 | 6757.65 | 6002.75 | 6002.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10831.25 | 10831.25 | 10950.15 | 10950.15 | 10850.4 | 10850.4 | 11396.75 | 11396.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9610.75 | 9610.75 | 7647.7 | 7647.7 | 9336.6 | 9336.6 | 2469.35 | 2469.35 | 8987.85 | 8987.85 | 9719.55 | 9719.55 | 8810.2 | 8810.2 | 6317.65 | 6317.65 | 8240.2 | 8240.2 | 8155.75 | 8155.75 | 7581.3 | 7581.3 | 8902.25 | 8902.25 | 966.95 | 966.95 | 6273.5 | 6273.5 | 10945.05 | 10945.05 | 8712 | 8712 | 2036 | 2036 | 7402 | 7402 | 9811.85 | 9811.85 | 10264.35 | 10264.35 | 10745.65 | 10745.65 | 7614.1 | 7614.1 | 1404.15 | 1404.15 | 1423.65 | 1423.65 | 3576.1 | 3576.1 | 8194.4 | 8194.4 | 4315.5 | 4315.5 | 4820 | 4820 | 9323.3 | 9323.3 | 10744.35 | 10744.35 | 1960.85 | 1960.85 | 779.65 | 779.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.29 | 36.91 | 0 | 36.89 | 37 | 0 | 0 | 37.81 | 0 | 0 | 0 | 0 | 9.35 | 9.24 | 0 | 9.47 | 8.83 | 0 | 14.18 | 13.7 | 0 | 14.16 | 13.22 | 0 | 6.85 | 6.85 | 0 | 6.72 | 6.85 | 0 | 1.6 | 1.54 | 0 | 2.29 | 2.01 | 0 | 6.5 | 6.93 | 0 | 7.35 | 7.59 | 0 | 1.64 | 1.53 | 0 | 2.18 | 2.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9927 | 33 | 6484 | 22 | 16243 | 97 | 6.85 | 6.85 | 0 | 6.72 | 6.85 | 0 | 6.5 | 6.93 | 0 | 7.35 | 7.59 | 0 | 428000 | 1000 | 307000 | 1000 | 734000 | 3000 | 733000 | 731000 | 13.05 | 6.8175 | 1.86 | 7.0925 | 1.86 | 27.28% | 26.22% | 37.0225 | 37.81 | 9.2225 | 13.815 | 739476.5
2022-05-03 | 2023 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 144000 | 6:10 | 19:12 | 7645.15 | 7645.15 | 5199.55 | 5199.55 | 10381.8 | 10381.8 | 9772.45 | 9772.45 | 11692.8 | 11692.8 | 11041 | 11041 | 10902.45 | 10902.45 | 11482.05 | 11482.05 | 10848.05 | 10848.05 | 11357.05 | 11357.05 | 7608.7 | 7608.7 | 7039.55 | 7039.55 | 279.35 | 279.35 | 327.85 | 327.85 | 268.35 | 268.35 | 227.65 | 227.65 | 89.3 | 89.3 | 22.1 | 22.1 | 50.3 | 50.3 | 99.3 | 99.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11006.6 | 11006.6 | 11356.45 | 11356.45 | 11241.1 | 11241.1 | 11961.85 | 11961.85 | 356.25 | 356.25 | 213.8 | 213.8 | 315.1 | 315.1 | 593.1 | 593.1 | 9945.95 | 9945.95 | 7936.4 | 7936.4 | 9648.8 | 9648.8 | 2552.45 | 2552.45 | 9267.75 | 9267.75 | 10032.1 | 10032.1 | 9080.3 | 9080.3 | 6527.35 | 6527.35 | 8489.5 | 8489.5 | 8370.75 | 8370.75 | 7816.75 | 7816.75 | 9146.55 | 9146.55 | 996.35 | 996.35 | 6475.8 | 6475.8 | 11343.8 | 11343.8 | 9069.5 | 9069.5 | 2094.85 | 2094.85 | 7620.2 | 7620.2 | 10095.3 | 10095.3 | 10586.35 | 10586.35 | 11539.9 | 11539.9 | 8410.3 | 8410.3 | 1443.15 | 1443.15 | 1478.4 | 1478.4 | 4921.45 | 4921.45 | 8321.5 | 8321.5 | 4443.75 | 4443.75 | 5186.8 | 5186.8 | 9647.45 | 9647.45 | 11133.25 | 11133.25 | 2030.65 | 2030.65 | 801.05 | 801.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.37 | 34.38 | 0 | 34.03 | 34.2 | 0 | 0 | 35.58 | 0 | 0 | 0 | 0 | 7.96 | 8.21 | 0 | 8.57 | 8.15 | 0 | 12.89 | 13.89 | 0 | 13.58 | 13.38 | 0 | 6.74 | 6.72 | 0 | 6.6 | 6.74 | 0 | 1.52 | 1.52 | 0 | 2.19 | 1.94 | 0 | 6.43 | 6.81 | 0 | 7.22 | 7.5 | 0 | 1.56 | 1.5 | 0 | 2.08 | 2.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10381 | 34 | 6805 | 23 | 17015 | 100 | 6.74 | 6.72 | 0 | 6.6 | 6.74 | 0 | 6.43 | 6.81 | 0 | 7.22 | 7.5 | 0 | 454000 | 1000 | 321000 | 1000 | 772000 | 3000 | 773000 | 769000 | 13.0333 | 6.7 | 1.7925 | 6.99 | 1.79 | 26.75% | 25.61% | 34.245 | 35.58 | 8.2225 | 13.435 | 779667
2022-05-04 | 2023 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 150000 | 6:06 | 19:14 | 8373.6 | 8373.6 | 5936.95 | 5936.95 | 11676.95 | 11676.95 | 10670.7 | 10670.7 | 12589.7 | 12589.7 | 12015.25 | 12015.25 | 11884.3 | 11884.3 | 12426.6 | 12426.6 | 12336.75 | 12336.75 | 11818.65 | 11818.65 | 7873.6 | 7873.6 | 9025.2 | 9025.2 | 665 | 665 | 828.2 | 828.2 | 702.5 | 702.5 | 616.65 | 616.65 | 555.75 | 555.75 | 159.3 | 159.3 | 351 | 351 | 681.2 | 681.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11925.7 | 11925.7 | 12325 | 12325 | 12191.4 | 12191.4 | 13034.15 | 13034.15 | 1527.7 | 1527.7 | 7848.25 | 7848.25 | 5681.15 | 5681.15 | 11382.9 | 11382.9 | 10880.8 | 10880.8 | 8643.35 | 8643.35 | 10570.15 | 10570.15 | 2802.9 | 2802.9 | 10186.1 | 10186.1 | 10793.65 | 10793.65 | 9964.25 | 9964.25 | 7149.7 | 7149.7 | 9340.5 | 9340.5 | 9176.9 | 9176.9 | 8465.4 | 8465.4 | 10010.5 | 10010.5 | 1094 | 1094 | 7109.2 | 7109.2 | 12318.75 | 12318.75 | 9949.25 | 9949.25 | 2299.95 | 2299.95 | 8354.6 | 8354.6 | 11077.15 | 11077.15 | 11603.9 | 11603.9 | 12472.15 | 12472.15 | 9214.2 | 9214.2 | 1579.45 | 1579.45 | 1618.25 | 1618.25 | 5366.1 | 5366.1 | 9104.75 | 9104.75 | 4872.85 | 4872.85 | 5076.15 | 5076.15 | 10518.65 | 10518.65 | 12098.9 | 12098.9 | 2220.45 | 2220.45 | 877.8 | 877.8 | 2356.45 | 2356.45 | 1238.4 | 1238.4 | 2473.6 | 2473.6 | 415.4 | 415.4 | 566.8 | 566.8 | 205.45 | 205.45 | 1053.4 | 1053.4 | 1145.7 | 1145.7 | 162.7 | 162.7 | 329.65 | 329.65 | 1190.2 | 1190.2 | 85.25 | 85.25 | 647.1 | 647.1 | 297.4 | 297.4 | 173.65 | 173.65 | 422 | 422 | 33.71 | 33.53 | 0 | 33.4 | 33.47 | 0 | 0 | 35.44 | 0 | 0 | 0 | 0 | 3.86 | 3.86 | 0 | 3.93 | 3.91 | 0 | 8.37 | 9.77 | 0 | 8.75 | 8.34 | 0 | 7.51 | 7.59 | 0 | 7.44 | 7.63 | 0 | 1.59 | 1.74 | 0 | 2.38 | 2.17 | 0 | 7.29 | 7.69 | 0 | 8.14 | 8.55 | 0 | 1.63 | 1.7 | 0 | 2.25 | 2.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10934 | 35 | 7180 | 25 | 17940 | 104 | 7.51 | 7.59 | 0 | 7.44 | 7.63 | 0 | 7.29 | 7.69 | 0 | 8.14 | 8.55 | 0 | 553000 | 1000 | 375000 | 2000 | 925000 | 4000 | 925000 | 921000 | 13.1333 | 7.5425 | 1.97 | 7.9175 | 1.9625 | 26.12% | 24.79% | 33.5275 | 35.44 | 3.89 | 8.8075 | 933355.9
2022-05-05 | 2023 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 150000 | 6:05 | 18:36 | 6396.5 | 6396.5 | 4625.3 | 4625.3 | 9121.75 | 9121.75 | 8229.6 | 8229.6 | 9789.1 | 9789.1 | 9225.05 | 9225.05 | 9112.1 | 9112.1 | 9720.55 | 9720.55 | 9001.65 | 9001.65 | 9550.65 | 9550.65 | 6838.4 | 6838.4 | 6012.5 | 6012.5 | 507.4 | 507.4 | 613.15 | 613.15 | 525.4 | 525.4 | 658.1 | 658.1 | 4581.35 | 4581.35 | 118.75 | 118.75 | 5055.05 | 5055.05 | 4009.7 | 4009.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9133.55 | 9133.55 | 9405.5 | 9405.5 | 9380.25 | 9380.25 | 9755.15 | 9755.15 | 5974.55 | 5974.55 | 7069.1 | 7069.1 | 6247.1 | 6247.1 | 8566.75 | 8566.75 | 8276.1 | 8276.1 | 6643.35 | 6643.35 | 8099.05 | 8099.05 | 2145.6 | 2145.6 | 7724.85 | 7724.85 | 8412.3 | 8412.3 | 7611.8 | 7611.8 | 5449.15 | 5449.15 | 7157.1 | 7157.1 | 7012.15 | 7012.15 | 6592.3 | 6592.3 | 7657.45 | 7657.45 | 838.65 | 838.65 | 5466.8 | 5466.8 | 9564.35 | 9564.35 | 7638.65 | 7638.65 | 1784.25 | 1784.25 | 6479.8 | 6479.8 | 8565.05 | 8565.05 | 8973.75 | 8973.75 | 9796.45 | 9796.45 | 7770.1 | 7770.1 | 1216.1 | 1216.1 | 1251.55 | 1251.55 | 3738.45 | 3738.45 | 6669.05 | 6669.05 | 3790.85 | 3790.85 | 4310 | 4310 | 8212.2 | 8212.2 | 9503.35 | 9503.35 | 1723.95 | 1723.95 | 677.6 | 677.6 | 2679.3 | 2679.3 | 1219.75 | 1219.75 | 2517.55 | 2517.55 | 438.35 | 438.35 | 680.05 | 680.05 | 239.1 | 239.1 | 1246.35 | 1246.35 | 1325.3 | 1325.3 | 283.8 | 283.8 | 559.45 | 559.45 | 2005.9 | 2005.9 | 157.55 | 157.55 | 869.85 | 869.85 | 399.75 | 399.75 | 246.3 | 246.3 | 1077.8 | 1077.8 | 36.59 | 36.34 | 0 | 36.19 | 36.38 | 0 | 0 | 37.65 | 0 | 0 | 0 | 0 | 4.07 | 4.08 | 0 | 4.18 | 3.89 | 0 | 21.2 | 21.93 | 0 | 20.79 | 19.52 | 0 | 5.85 | 5.7 | 0 | 5.7 | 5.93 | 0 | 1.32 | 1.22 | 0 | 1.88 | 1.68 | 0 | 5.56 | 5.78 | 0 | 6.22 | 6.58 | 0 | 1.35 | 1.2 | 0 | 1.78 | 1.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11398 | 37 | 7482 | 26 | 18706 | 108 | 5.85 | 5.7 | 0 | 5.7 | 5.93 | 0 | 5.56 | 5.78 | 0 | 6.22 | 6.58 | 0 | 464000 | 2000 | 302000 | 1000 | 766000 | 4000 | 763000 | 762000 | 12.5167 | 5.795 | 1.525 | 6.035 | 1.5225 | 26.32% | 25.23% | 36.375 | 37.65 | 4.055 | 20.86 | 771844.6
2022-05-06 | 2023 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 175000 | 6:07 | 19:14 | 7724.9 | 7724.9 | 5461.8 | 5461.8 | 10834 | 10834 | 9890.5 | 9890.5 | 11900.8 | 11900.8 | 11171.85 | 11171.85 | 11047.45 | 11047.45 | 11656.65 | 11656.65 | 10683.95 | 10683.95 | 11581.4 | 11581.4 | 8337.85 | 8337.85 | 9191.05 | 9191.05 | 3361.85 | 3361.85 | 643.7 | 643.7 | 738.5 | 738.5 | 5847.95 | 5847.95 | 8010.55 | 8010.55 | 145.65 | 145.65 | 6379.6 | 6379.6 | 6882.65 | 6882.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11140.15 | 11140.15 | 11507.65 | 11507.65 | 11395.65 | 11395.65 | 11750.8 | 11750.8 | 8927.95 | 8927.95 | 8969.8 | 8969.8 | 8709.45 | 8709.45 | 10422.05 | 10422.05 | 9978.65 | 9978.65 | 8110.95 | 8110.95 | 9862.4 | 9862.4 | 2188.55 | 2188.55 | 9368.75 | 9368.75 | 10228.6 | 10228.6 | 9167.6 | 9167.6 | 6580.1 | 6580.1 | 8508.45 | 8508.45 | 5711.8 | 5711.8 | 5818.55 | 5818.55 | 4278.2 | 4278.2 | 1009.1 | 1009.1 | 6493.4 | 6493.4 | 11548.8 | 11548.8 | 9247.5 | 9247.5 | 923.3 | 923.3 | 3312.05 | 3312.05 | 4468.5 | 4468.5 | 4596.4 | 4596.4 | 5005.55 | 5005.55 | 4026.05 | 4026.05 | 597.25 | 597.25 | 620.45 | 620.45 | 4295.15 | 4295.15 | 8118.75 | 8118.75 | 4510.7 | 4510.7 | 4803.05 | 4803.05 | 8190.65 | 8190.65 | 9421.4 | 9421.4 | 1654.5 | 1654.5 | 734.3 | 734.3 | 3593.8 | 3593.8 | 1397.15 | 1397.15 | 3292.85 | 3292.85 | 527.3 | 527.3 | 796.5 | 796.5 | 277 | 277 | 1632.4 | 1632.4 | 7032.45 | 7032.45 | 334.15 | 334.15 | 644.3 | 644.3 | 2300.6 | 2300.6 | 697.25 | 697.25 | 1692.5 | 1692.5 | 1288.95 | 1288.95 | 717.45 | 717.45 | 2415.45 | 2415.45 | 36.24 | 35.82 | 0 | 35 | 35.89 | 0 | 0 | 44.35 | 0 | 0 | 0 | 0 | 3.73 | 3.62 | 0 | 3.45 | 3.54 | 0 | 5.96 | 6.04 | 0 | 5.76 | 6.14 | 0 | 7.15 | 7.18 | 0 | 7.02 | 7.22 | 0 | 1.28 | 1.64 | 0 | 2.04 | 1.87 | 0 | 6.88 | 7.26 | 0 | 7.68 | 8.08 | 0 | 1.31 | 1.6 | 0 | 1.92 | 1.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11995 | 38 | 7774 | 27 | 19591 | 113 | 7.15 | 7.18 | 0 | 7.02 | 7.22 | 0 | 6.88 | 7.26 | 0 | 7.68 | 8.08 | 0 | 597000 | 1000 | 292000 | 1000 | 885000 | 5000 | 887000 | 880000 | 13.1167 | 7.1425 | 1.7075 | 7.475 | 1.695 | 23.91% | 22.68% | 35.7375 | 44.35 | 3.585 | 5.975 | 892671.4
2022-05-07 | 2023 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 175000 | 6:09 | 19:15 | 8090.75 | 8090.75 | 5699.95 | 5699.95 | 11203.25 | 11203.25 | 10227.75 | 10227.75 | 11893.5 | 11893.5 | 11251.95 | 11251.95 | 11129.45 | 11129.45 | 8502.35 | 8502.35 | 11908.4 | 11908.4 | 11004.35 | 11004.35 | 9690.45 | 9690.45 | 9022.25 | 9022.25 | 3647.45 | 3647.45 | 3909.85 | 3909.85 | 4430.05 | 4430.05 | 6595.45 | 6595.45 | 8332.85 | 8332.85 | 152.15 | 152.15 | 10263.4 | 10263.4 | 8135.6 | 8135.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11443.25 | 11443.25 | 11887.85 | 11887.85 | 11720.5 | 11720.5 | 12049.7 | 12049.7 | 9256.3 | 9256.3 | 9303.2 | 9303.2 | 9775.2 | 9775.2 | 10638.7 | 10638.7 | 10370.75 | 10370.75 | 8396.35 | 8396.35 | 10219.2 | 10219.2 | 2061.75 | 2061.75 | 9755.1 | 9755.1 | 10424.65 | 10424.65 | 9504.85 | 9504.85 | 7122.05 | 7122.05 | 8802.1 | 8802.1 | 8728.15 | 8728.15 | 6004 | 6004 | 4457.6 | 4457.6 | 1047.45 | 1047.45 | 6735.9 | 6735.9 | 11910.35 | 11910.35 | 9588.85 | 9588.85 | 2196.4 | 2196.4 | 7796.15 | 7796.15 | 10559.6 | 10559.6 | 10799.9 | 10799.9 | 11852.65 | 11852.65 | 5859.65 | 5859.65 | 1450.5 | 1450.5 | 1505 | 1505 | 4538.05 | 4538.05 | 8233.8 | 8233.8 | 4665.75 | 4665.75 | 5213.95 | 5213.95 | 9546.6 | 9546.6 | 11046.35 | 11046.35 | 1933.5 | 1933.5 | 857.65 | 857.65 | 3468.75 | 3468.75 | 1445.7 | 1445.7 | 4404.95 | 4404.95 | 2670.9 | 2670.9 | 1115.6 | 1115.6 | 318.05 | 318.05 | 4506.8 | 4506.8 | 7283.45 | 7283.45 | 3429.25 | 3429.25 | 1503.9 | 1503.9 | 3089.95 | 3089.95 | 2673.2 | 2673.2 | 1747.85 | 1747.85 | 1396.25 | 1396.25 | 731.95 | 731.95 | 2502.45 | 2502.45 | 39.37 | 38.93 | 0 | 38.63 | 38.86 | 0 | 0 | 40.32 | 0 | 0 | 0 | 0 | 4.09 | 4.01 | 0 | 4.04 | 4.18 | 0 | 7.6 | 7.72 | 0 | 7.8 | 7.98 | 0 | 7.51 | 7.52 | 0 | 7.35 | 7.54 | 0 | 1.41 | 1.75 | 0 | 2.34 | 2.07 | 0 | 7.21 | 7.59 | 0 | 8.05 | 8.39 | 0 | 1.43 | 1.7 | 0 | 2.14 | 2.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12632 | 39 | 8167 | 29 | 20619 | 116 | 7.51 | 7.52 | 0 | 7.35 | 7.54 | 0 | 7.21 | 7.59 | 0 | 8.05 | 8.39 | 0 | 637000 | 1000 | 393000 | 2000 | 1028000 | 3000 | 1027000 | 1025000 | 13.1 | 7.48 | 1.8925 | 7.81 | 1.855 | 25.3% | 23.75% | 38.9475 | 40.32 | 4.08 | 7.775 | 1033279
2022-05-08 | 2023 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 193000 | 6:02 | 19:16 | 8627.4 | 8627.4 | 5807.35 | 5807.35 | 11616.25 | 11616.25 | 10519.55 | 10519.55 | 6887.15 | 6887.15 | 11898.35 | 11898.35 | 11764.85 | 11764.85 | 8943.7 | 8943.7 | 12143.75 | 12143.75 | 11292.1 | 11292.1 | 10497.6 | 10497.6 | 9688.35 | 9688.35 | 3723.4 | 3723.4 | 4026.1 | 4026.1 | 2573.95 | 2573.95 | 6892.25 | 6892.25 | 8562.3 | 8562.3 | 156.4 | 156.4 | 11055 | 11055 | 8421.6 | 8421.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11767.3 | 11767.3 | 12198.4 | 12198.4 | 12064.35 | 12064.35 | 12387.85 | 12387.85 | 9420.3 | 9420.3 | 11324.6 | 11324.6 | 10367 | 10367 | 10906.5 | 10906.5 | 10686.35 | 10686.35 | 8660.05 | 8660.05 | 10529.7 | 10529.7 | 2123 | 2123 | 10042 | 10042 | 10680.15 | 10680.15 | 9779.95 | 9779.95 | 7406.3 | 7406.3 | 9078.85 | 9078.85 | 9000 | 9000 | 8283.4 | 8283.4 | 4612.9 | 4612.9 | 1079.5 | 1079.5 | 6931.95 | 6931.95 | 12233.2 | 12233.2 | 9919.95 | 9919.95 | 2265.45 | 2265.45 | 8013.35 | 8013.35 | 10871.85 | 10871.85 | 11119.8 | 11119.8 | 12171.25 | 12171.25 | 12143.6 | 12143.6 | 1490.4 | 1490.4 | 1545.25 | 1545.25 | 5829.7 | 5829.7 | 8458.1 | 8458.1 | 4809.95 | 4809.95 | 5380.3 | 5380.3 | 11005.75 | 11005.75 | 11434.95 | 11434.95 | 2012.75 | 2012.75 | 3195.35 | 3195.35 | 4099.3 | 4099.3 | 1489.35 | 1489.35 | 4926.9 | 4926.9 | 3092.8 | 3092.8 | 5638 | 5638 | 4526.65 | 4526.65 | 4655.2 | 4655.2 | 9032.85 | 9032.85 | 4360.55 | 4360.55 | 3524.7 | 3524.7 | 4596.55 | 4596.55 | 2769.25 | 2769.25 | 1811.1 | 1811.1 | 2190.75 | 2190.75 | 1152.1 | 1152.1 | 2591 | 2591 | 40.13 | 39.82 | 0 | 39.59 | 39.69 | 0 | 0 | 41.09 | 0 | 0 | 0 | 0 | 5.57 | 5.79 | 0 | 5.89 | 5.79 | 0 | 9.92 | 10.23 | 0 | 10.36 | 9.77 | 0 | 7.75 | 7.75 | 0 | 7.6 | 7.79 | 0 | 1.47 | 1.82 | 0 | 2.42 | 2.21 | 0 | 7.04 | 7.8 | 0 | 8.2 | 8.63 | 0 | 1.59 | 1.77 | 0 | 2.25 | 2.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13280.08 | 40.78 | 8631.92 | 30.56 | 21728.47 | 120.57 | 7.75 | 7.75 | 0 | 7.6 | 7.79 | 0 | 7.04 | 7.8 | 0 | 8.2 | 8.63 | 0 | 648080 | 1780 | 464920 | 1560 | 1109470 | 4570 | 1109660 | 1104900 | 13.2333 | 7.7225 | 1.98 | 7.9175 | 1.9625 | 25.64% | 24.79% | 39.8075 | 41.09 | 5.76 | 10.07 | 1117571.6
2022-05-09 | 2023 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 193000 | 6:02 | 19:18 | 9578.05 | 9578.05 | 6092.05 | 6092.05 | 12010.8 | 12010.8 | 10837.1 | 10837.1 | 7151.35 | 7151.35 | 12265.75 | 12265.75 | 12100.15 | 12100.15 | 9275.7 | 9275.7 | 10114.95 | 10114.95 | 10934.35 | 10934.35 | 11538.75 | 11538.75 | 12485.4 | 12485.4 | 4369.3 | 4369.3 | 6250.35 | 6250.35 | 7614.55 | 7614.55 | 9623.55 | 9623.55 | 8850.15 | 8850.15 | 349.55 | 349.55 | 12064.8 | 12064.8 | 8721.4 | 8721.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12099.7 | 12099.7 | 12497.6 | 12497.6 | 12400.45 | 12400.45 | 12703.3 | 12703.3 | 10667.25 | 10667.25 | 12454.55 | 12454.55 | 10927.15 | 10927.15 | 11178.6 | 11178.6 | 11039.4 | 11039.4 | 8891.4 | 8891.4 | 10912.4 | 10912.4 | 2205.6 | 2205.6 | 10346 | 10346 | 10942.05 | 10942.05 | 10141.65 | 10141.65 | 7729.15 | 7729.15 | 9398.55 | 9398.55 | 9316.5 | 9316.5 | 8510.75 | 8510.75 | 4785.4 | 4785.4 | 1116.65 | 1116.65 | 7175 | 7175 | 12574.55 | 12574.55 | 10218.75 | 10218.75 | 2342.6 | 2342.6 | 8287.15 | 8287.15 | 11237.6 | 11237.6 | 11495.7 | 11495.7 | 12479.55 | 12479.55 | 12522.15 | 12522.15 | 1538.1 | 1538.1 | 1599.4 | 1599.4 | 6272.4 | 6272.4 | 8630.3 | 8630.3 | 4743.05 | 4743.05 | 5408.15 | 5408.15 | 11443.65 | 11443.65 | 12049.2 | 12049.2 | 2112.65 | 2112.65 | 3310.6 | 3310.6 | 6171.1 | 6171.1 | 2045.445 | 2045.445 | 5458.8 | 5458.8 | 3583.2 | 3583.2 | 6241.35 | 6241.35 | 6143 | 6143 | 5284.9 | 5284.9 | 10130.805 | 10130.805 | 7492.45 | 7492.45 | 5758.25 | 5758.25 | 5566.4 | 5566.4 | 2874.3 | 2874.3 | 1879.2 | 1879.2 | 2276.25 | 2276.25 | 2088.35 | 2088.35 | 2682.4 | 2682.4 | 40.07 | 39.87 | 0 | 39.62 | 39.69 | 0 | 0 | 41.1 | 0 | 0 | 0 | 0 | 6.43 | 6.4 | 0 | 6.69 | 6.53 | 0 | 13.23 | 10.91 | 0 | 11.98 | 11.57 | 0 | 8.09 | 8.05 | 0 | 7.89 | 8.09 | 0 | 1.55 | 1.91 | 0 | 2.55 | 2.34 | 0 | 7.72 | 8.08 | 0 | 8.6 | 8.95 | 0 | 1.57 | 1.86 | 0 | 2.37 | 2.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13975 | 41 | 9138 | 31 | 22926 | 124 | 8.09 | 8.05 | 0 | 7.89 | 8.09 | 0 | 7.72 | 8.08 | 0 | 8.6 | 8.95 | 0 | 694920 | 220 | 506080 | 440 | 1197530 | 3430 | 1200340 | 1194100 | 13.2667 | 8.03 | 2.0875 | 8.3375 | 2.06 | 26% | 24.71% | 39.8125 | 41.1 | 6.5125 | 11.9225 | 1207217.8
2022-05-10 | 2023 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 214000 | 6:01 | 19:18 | 9707 | 9707 | 6139.85 | 6139.85 | 11664.4 | 11664.4 | 10902.85 | 10902.85 | 6915.65 | 6915.65 | 11976 | 11976 | 11802.4 | 11802.4 | 8942.9 | 8942.9 | 9417.4 | 9417.4 | 10609.7 | 10609.7 | 11263.4 | 11263.4 | 12202.25 | 12202.25 | 5775.5 | 5775.5 | 8679.1 | 8679.1 | 7944 | 7944 | 9894.8 | 9894.8 | 8569.55 | 8569.55 | 398.5 | 398.5 | 11862.7 | 11862.7 | 8406.2 | 8406.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11820.3 | 11820.3 | 12230.9 | 12230.9 | 12118.65 | 12118.65 | 12401.9 | 12401.9 | 10421.55 | 10421.55 | 12339.3 | 12339.3 | 10665.3 | 10665.3 | 11715.2 | 11715.2 | 10652.45 | 10652.45 | 8670.35 | 8670.35 | 10560.2 | 10560.2 | 2128.6 | 2128.6 | 10085.1 | 10085.1 | 10732 | 10732 | 9800.65 | 9800.65 | 7507.95 | 7507.95 | 9170.2 | 9170.2 | 10566.5 | 10566.5 | 9271.55 | 9271.55 | 4629.8 | 4629.8 | 1079.7 | 1079.7 | 6937.8 | 6937.8 | 12268.55 | 12268.55 | 9867.35 | 9867.35 | 2266.1 | 2266.1 | 8022.85 | 8022.85 | 10881.4 | 10881.4 | 11122.65 | 11122.65 | 12176.15 | 12176.15 | 12205.55 | 12205.55 | 2428.3 | 2428.3 | 1544.95 | 1544.95 | 6067.3 | 6067.3 | 8472 | 8472 | 4220.25 | 4220.25 | 4976.9 | 4976.9 | 11125.45 | 11125.45 | 11687.85 | 11687.85 | 2038.3 | 2038.3 | 864.65 | 864.65 | 6494.35 | 6494.35 | 2402.15 | 2402.15 | 6169.65 | 6169.65 | 5422.15 | 5422.15 | 5975.15 | 5975.15 | 6312.45 | 6312.45 | 5586.95 | 5586.95 | 10184.75 | 10184.75 | 8229.35 | 8229.35 | 7261.9 | 7261.9 | 8480.9 | 8480.9 | 2755.5 | 2755.5 | 1819.75 | 1819.75 | 2194.3 | 2194.3 | 2082.2 | 2082.2 | 2598.05 | 2598.05 | 39.46 | 39.15 | 0 | 39.04 | 39.19 | 0 | 0 | 40.66 | 0 | 0 | 0 | 0 | 4.01 | 4.09 | 0 | 3.84 | 4.09 | 0 | 7.73 | 8.47 | 0 | 7.32 | 7.75 | 0 | 7.88 | 7.92 | 0 | 7.66 | 7.84 | 0 | 1.5 | 1.86 | 0 | 2.5 | 2.28 | 0 | 7.47 | 7.92 | 0 | 8.36 | 8.67 | 0 | 1.53 | 1.81 | 0 | 2.33 | 2.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14665 | 43 | 9651 | 33 | 24127 | 128 | 7.88 | 7.92 | 0 | 7.66 | 7.84 | 0 | 7.47 | 7.92 | 0 | 8.36 | 8.67 | 0 | 690000 | 2000 | 513000 | 2000 | 1201000 | 4000 | 1199000 | 1197000 | 13.2833 | 7.825 | 2.035 | 8.105 | 2 | 26.01% | 24.68% | 39.21 | 40.66 | 4.0075 | 7.8175 | 1209572.4
2022-05-11 | 2023 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 214000 | 6:00 | 19:18 | 9768.45 | 9768.45 | 6332.25 | 6332.25 | 10338.55 | 10338.55 | 11029.25 | 11029.25 | 6743.2 | 6743.2 | 11662.2 | 11662.2 | 11506.35 | 11506.35 | 7408.6 | 7408.6 | 9504.95 | 9504.95 | 10349.25 | 10349.25 | 11010.85 | 11010.85 | 10456.8 | 10456.8 | 7268.55 | 7268.55 | 9974.15 | 9974.15 | 4228.05 | 4228.05 | 9628 | 9628 | 10062.25 | 10062.25 | 388 | 388 | 11815.7 | 11815.7 | 8557.3 | 8557.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11577.9 | 11577.9 | 11944.05 | 11944.05 | 11872.75 | 11872.75 | 12121.75 | 12121.75 | 10232.7 | 10232.7 | 12053.35 | 12053.35 | 10387.45 | 10387.45 | 11872.05 | 11872.05 | 10373.2 | 10373.2 | 8451.2 | 8451.2 | 10297.95 | 10297.95 | 2074.2 | 2074.2 | 9836.9 | 9836.9 | 10547.9 | 10547.9 | 9579.25 | 9579.25 | 7343.35 | 7343.35 | 11333.25 | 11333.25 | 11053.3 | 11053.3 | 9782.85 | 9782.85 | 6832.6 | 6832.6 | 1049.95 | 1049.95 | 6747 | 6747 | 11968.4 | 11968.4 | 9590.55 | 9590.55 | 2209.15 | 2209.15 | 7816.25 | 7816.25 | 10592.75 | 10592.75 | 10828.9 | 10828.9 | 11929.7 | 11929.7 | 11904.25 | 11904.25 | 4115.85 | 4115.85 | 1504.95 | 1504.95 | 5916.9 | 5916.9 | 8252.85 | 8252.85 | 7184.2 | 7184.2 | 3866.15 | 3866.15 | 10847.05 | 10847.05 | 11392 | 11392 | 1987.3 | 1987.3 | 1927.6 | 1927.6 | 6339.05 | 6339.05 | 2345.55 | 2345.55 | 6181.5 | 6181.5 | 6017.85 | 6017.85 | 5835.25 | 5835.25 | 6370.15 | 6370.15 | 5452.35 | 5452.35 | 9987.05 | 9987.05 | 8076.55 | 8076.55 | 7489.1 | 7489.1 | 8279.55 | 8279.55 | 2656 | 2656 | 1783.3 | 1783.3 | 2146 | 2146 | 2039.3 | 2039.3 | 2541 | 2541 | 39.79 | 39.47 | 0 | 39.39 | 39.65 | 0 | 0 | 41.04 | 0 | 0 | 0 | 0 | 3.42 | 3.46 | 0 | 3.53 | 3.52 | 0 | 7.76 | 8 | 0 | 8.11 | 7.81 | 0 | 7.68 | 7.72 | 0 | 7.45 | 7.63 | 0 | 1.45 | 1.81 | 0 | 2.41 | 2.22 | 0 | 7.29 | 7.7 | 0 | 8.11 | 8.44 | 0 | 1.48 | 1.77 | 0 | 2.25 | 2.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15339 | 44 | 10177 | 34 | 25323 | 131 | 7.68 | 7.72 | 0 | 7.45 | 7.63 | 0 | 7.29 | 7.7 | 0 | 8.11 | 8.44 | 0 | 674000 | 1000 | 526000 | 1000 | 1196000 | 3000 | 1198000 | 1193000 | 13.3 | 7.62 | 1.9725 | 7.885 | 1.955 | 25.89% | 24.79% | 39.575 | 41.04 | 3.4825 | 7.92 | 1205543.9
2022-05-12 | 2023 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 221000 | 6:00 | 19:19 | 9955.3 | 9955.3 | 6446.45 | 6446.45 | 10944.8 | 10944.8 | 11254.3 | 11254.3 | 6898.85 | 6898.85 | 11889.5 | 11889.5 | 11759.3 | 11759.3 | 7511.7 | 7511.7 | 9613.05 | 9613.05 | 10519.55 | 10519.55 | 11201.7 | 11201.7 | 10488.25 | 10488.25 | 7408.2 | 7408.2 | 10211.75 | 10211.75 | 12066.85 | 12066.85 | 9849.1 | 9849.1 | 10922.85 | 10922.85 | 396.7 | 396.7 | 12140.15 | 12140.15 | 8940.6 | 8940.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11794.2 | 11794.2 | 12172.35 | 12172.35 | 12074.65 | 12074.65 | 12349.15 | 12349.15 | 10494.9 | 10494.9 | 12293.2 | 12293.2 | 10641.85 | 10641.85 | 12049.95 | 12049.95 | 10649.1 | 10649.1 | 8642.35 | 8642.35 | 10555.8 | 10555.8 | 2128.4 | 2128.4 | 10109.05 | 10109.05 | 10727.15 | 10727.15 | 9821.5 | 9821.5 | 7523.7 | 7523.7 | 11867.65 | 11867.65 | 11581.3 | 11581.3 | 10059.4 | 10059.4 | 7073.2 | 7073.2 | 1076 | 1076 | 6911.65 | 6911.65 | 12208.95 | 12208.95 | 9835.2 | 9835.2 | 2256.2 | 2256.2 | 7992.9 | 7992.9 | 10848.95 | 10848.95 | 11084.5 | 11084.5 | 12139.6 | 12139.6 | 12148.55 | 12148.55 | 5096.5 | 5096.5 | 1543.9 | 1543.9 | 6438.1 | 6438.1 | 8446.05 | 8446.05 | 7678.4 | 7678.4 | 4082.6 | 4082.6 | 11172.7 | 11172.7 | 11658.7 | 11658.7 | 2531.15 | 2531.15 | 6580.5 | 6580.5 | 7210.3 | 7210.3 | 2347.9 | 2347.9 | 7510.55 | 7510.55 | 6158.85 | 6158.85 | 5976.55 | 5976.55 | 6454 | 6454 | 5582.25 | 5582.25 | 10178.1 | 10178.1 | 8224.65 | 8224.65 | 8376.55 | 8376.55 | 8475.3 | 8475.3 | 2683.2 | 2683.2 | 2497.1 | 2497.1 | 2197.15 | 2197.15 | 2085.3 | 2085.3 | 2597.15 | 2597.15 | 41.52 | 41.23 | 0 | 41.09 | 41.18 | 0 | 0 | 42.64 | 0 | 0 | 0 | 0 | 4.93 | 4.96 | 0 | 5.15 | 5.09 | 0 | 10.01 | 8.81 | 0 | 9.7 | 10.27 | 0 | 7.91 | 7.95 | 0 | 7.69 | 7.82 | 0 | 1.54 | 1.89 | 0 | 2.52 | 2.3 | 0 | 7.52 | 7.94 | 0 | 8.37 | 8.65 | 0 | 1.57 | 1.85 | 0 | 2.35 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16044 | 45 | 10736 | 35 | 26585 | 135 | 7.91 | 7.95 | 0 | 7.69 | 7.82 | 0 | 7.52 | 7.94 | 0 | 8.37 | 8.65 | 0 | 705000 | 1000 | 559000 | 1000 | 1262000 | 4000 | 1262000 | 1258000 | 13.3167 | 7.8425 | 2.0625 | 8.12 | 2.0425 | 26.3% | 25.15% | 41.255 | 42.64 | 5.0325 | 9.6975 | 1270627.6
2022-05-13 | 2023 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 226000 | 6:04 | 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6942.65 | 6942.65 | 11941.25 | 11941.25 | 11825.3 | 11825.3 | 7564.35 | 7564.35 | 9588.65 | 9588.65 | 10549.4 | 10549.4 | 11266.05 | 11266.05 | 10479.25 | 10479.25 | 7436.7 | 7436.7 | 10262.4 | 10262.4 | 12094.2 | 12094.2 | 9900.9 | 9900.9 | 10965.7 | 10965.7 | 399.5 | 399.5 | 12203.35 | 12203.35 | 9009.85 | 9009.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11843.2 | 11843.2 | 12276.1 | 12276.1 | 12147.5 | 12147.5 | 12418.85 | 12418.85 | 10574 | 10574 | 12343.7 | 12343.7 | 10699.45 | 10699.45 | 12089.8 | 12089.8 | 10707.95 | 10707.95 | 8680.65 | 8680.65 | 10603.2 | 10603.2 | 2137.5 | 2137.5 | 10142.3 | 10142.3 | 10765.15 | 10765.15 | 9864 | 9864 | 7557.1 | 7557.1 | 11926.75 | 11926.75 | 11641.8 | 11641.8 | 10322.1 | 10322.1 | 10633.9 | 10633.9 | 1081.5 | 1081.5 | 6952.45 | 6952.45 | 12278.55 | 12278.55 | 9890.95 | 9890.95 | 2272.2 | 2272.2 | 8042.95 | 8042.95 | 10915.7 | 10915.7 | 11154.7 | 11154.7 | 12180.55 | 12180.55 | 12229.75 | 12229.75 | 5556 | 5556 | 1555.7 | 1555.7 | 7310.15 | 7310.15 | 8494.9 | 8494.9 | 8111.4 | 8111.4 | 5403.95 | 5403.95 | 11242.3 | 11242.3 | 11717 | 11717 | 2545.4 | 2545.4 | 6840.7 | 6840.7 | 9971.05 | 9971.05 | 2709.75 | 2709.75 | 7745.95 | 7745.95 | 6196.65 | 6196.65 | 6165.55 | 6165.55 | 6548.85 | 6548.85 | 6558.2 | 6558.2 | 10244.1 | 10244.1 | 8892.9 | 8892.9 | 9570.4 | 9570.4 | 8481.6 | 8481.6 | 3196.05 | 3196.05 | 2734.25 | 2734.25 | 2171.5 | 2171.5 | 2095.7 | 2095.7 | 2607.65 | 2607.65 | 42.02 | 41.64 | 0 | 41.52 | 41.58 | 0 | 0 | 43.1 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 4.89 | 4.73 | 0 | 8.71 | 10.64 | 0 | 8.98 | 9.56 | 0 | 8.01 | 8.06 | 0 | 7.79 | 8.06 | 0 | 1.57 | 1.91 | 0 | 2.55 | 2.3 | 0 | 7.6 | 8.03 | 0 | 8.46 | 8.89 | 0 | 1.6 | 1.87 | 0 | 2.38 | 2.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16675 | 46 | 11326 | 36 | 27802 | 138 | 8.01 | 8.06 | 0 | 7.79 | 8.06 | 0 | 7.6 | 8.03 | 0 | 8.46 | 8.89 | 0 | 631000 | 1000 | 590000 | 1000 | 1217000 | 3000 | 1219000 | 1214000 | 13.2667 | 7.98 | 2.0825 | 8.245 | 2.07 | 26.1% | 25.11% | 41.69 | 43.1 | 4.905 | 9.4725 | 1226942.9
2022-05-14 | 2023 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 231000 | 5:59 | 19:21 | 9947.15 | 9947.15 | 7266.05 | 7266.05 | 10345.05 | 10345.05 | 11287.6 | 11287.6 | 6900.8 | 6900.8 | 11852.6 | 11852.6 | 11765.1 | 11765.1 | 7489.55 | 7489.55 | 9521.7 | 9521.7 | 10474.55 | 10474.55 | 11169.6 | 11169.6 | 10395.25 | 10395.25 | 7382.75 | 7382.75 | 9730.45 | 9730.45 | 12189.7 | 12189.7 | 9792.8 | 9792.8 | 10894.75 | 10894.75 | 394 | 394 | 12076.85 | 12076.85 | 8926.6 | 8926.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11762.85 | 11762.85 | 12209.4 | 12209.4 | 12049.35 | 12049.35 | 12325.4 | 12325.4 | 10466.1 | 10466.1 | 12250.1 | 12250.1 | 10631.85 | 10631.85 | 12046.7 | 12046.7 | 10593.7 | 10593.7 | 8605.9 | 8605.9 | 10500.25 | 10500.25 | 2116.45 | 2116.45 | 10066.8 | 10066.8 | 10687.85 | 10687.85 | 9773 | 9773 | 7444.25 | 7444.25 | 12233.05 | 12233.05 | 11611.75 | 11611.75 | 10466.8 | 10466.8 | 10657.9 | 10657.9 | 1069.55 | 1069.55 | 6875.95 | 6875.95 | 12160.9 | 12160.9 | 9774.6 | 9774.6 | 2246.35 | 2246.35 | 7949 | 7949 | 10803.25 | 10803.25 | 11052.2 | 11052.2 | 12112 | 12112 | 12132.25 | 12132.25 | 6329.65 | 6329.65 | 1546.5 | 1546.5 | 7423.45 | 7423.45 | 8407.6 | 8407.6 | 8031.8 | 8031.8 | 5354.8 | 5354.8 | 11160.95 | 11160.95 | 11612.3 | 11612.3 | 2514.35 | 2514.35 | 6773.45 | 6773.45 | 10800.5 | 10800.5 | 2976.65 | 2976.65 | 7907.3 | 7907.3 | 6165.4 | 6165.4 | 6295 | 6295 | 6697.2 | 6697.2 | 6846.55 | 6846.55 | 10251.35 | 10251.35 | 8857.75 | 8857.75 | 10334.75 | 10334.75 | 10790.65 | 10790.65 | 3185.95 | 3185.95 | 2867.4 | 2867.4 | 2303.95 | 2303.95 | 2331.5 | 2331.5 | 2821.85 | 2821.85 | 40.67 | 40.69 | 0 | 40.31 | 40.33 | 0 | 0 | 42.26 | 0 | 0 | 0 | 0 | 5.06 | 5.2 | 0 | 5.38 | 5.31 | 0 | 8.86 | 9.18 | 0 | 9.22 | 9.38 | 0 | 7.93 | 7.98 | 0 | 7.7 | 7.97 | 0 | 1.56 | 1.9 | 0 | 2.52 | 2.23 | 0 | 7.53 | 7.95 | 0 | 8.36 | 8.78 | 0 | 1.6 | 1.86 | 0 | 2.35 | 2.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17378 | 47 | 11927 | 37 | 29102 | 141 | 7.93 | 7.98 | 0 | 7.7 | 7.97 | 0 | 7.53 | 7.95 | 0 | 8.36 | 8.78 | 0 | 703000 | 1000 | 601000 | 1000 | 1300000 | 3000 | 1302000 | 1297000 | 13.3667 | 7.895 | 2.0525 | 8.155 | 2.0425 | 26% | 25.05% | 40.5 | 42.26 | 5.2375 | 9.16 | 1310134
2022-05-15 | 2023 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 236000 | 5:57 | 19:21 | 9646.55 | 9646.55 | 8235.5 | 8235.5 | 10059.9 | 10059.9 | 10984.85 | 10984.85 | 6678.3 | 6678.3 | 11485.6 | 11485.6 | 11433.6 | 11433.6 | 7290.35 | 7290.35 | 9330.9 | 9330.9 | 10205.75 | 10205.75 | 10836.25 | 10836.25 | 10220.05 | 10220.05 | 7481.75 | 7481.75 | 9461.75 | 9461.75 | 11816.2 | 11816.2 | 9781.15 | 9781.15 | 10610.15 | 10610.15 | 382.9 | 382.9 | 11730.85 | 11730.85 | 8690.2 | 8690.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11401.15 | 11401.15 | 11808.45 | 11808.45 | 11679.3 | 11679.3 | 11989.45 | 11989.45 | 10132.2 | 10132.2 | 11855.4 | 11855.4 | 10331.45 | 10331.45 | 11678.85 | 11678.85 | 10261.9 | 10261.9 | 8317.65 | 8317.65 | 10126.8 | 10126.8 | 2039.95 | 2039.95 | 9712.9 | 9712.9 | 10352.6 | 10352.6 | 9413.7 | 9413.7 | 7169.15 | 7169.15 | 11804.5 | 11804.5 | 11211.75 | 11211.75 | 10133.45 | 10133.45 | 10268.85 | 10268.85 | 1035.05 | 1035.05 | 6656.25 | 6656.25 | 11806.05 | 11806.05 | 9504.95 | 9504.95 | 2166.9 | 2166.9 | 7670.3 | 7670.3 | 10436.2 | 10436.2 | 10683.85 | 10683.85 | 11757.3 | 11757.3 | 11743.35 | 11743.35 | 6577.95 | 6577.95 | 4388.4 | 4388.4 | 7168.25 | 7168.25 | 8130.3 | 8130.3 | 7865.5 | 7865.5 | 5191.65 | 5191.65 | 10789.55 | 10789.55 | 11260.1 | 11260.1 | 2449.9 | 2449.9 | 7037.65 | 7037.65 | 10789.9 | 10789.9 | 3165.6 | 3165.6 | 7639.65 | 7639.65 | 5953.3 | 5953.3 | 6094.4 | 6094.4 | 6541.45 | 6541.45 | 8013.9 | 8013.9 | 9883.15 | 9883.15 | 8594.4 | 8594.4 | 9964.9 | 9964.9 | 10221.2 | 10221.2 | 6826.85 | 6826.85 | 2769.1 | 2769.1 | 3032.95 | 3032.95 | 2268.2 | 2268.2 | 2796.55 | 2796.55 | 38.92 | 38.47 | 0 | 38.4 | 38.36 | 0 | 0 | 39.48 | 0 | 0 | 0 | 0 | 8.71 | 8.79 | 0 | 8.7 | 8.51 | 0 | 12.28 | 12.51 | 0 | 12.3 | 11.61 | 0 | 7.47 | 7.49 | 0 | 7.32 | 7.47 | 0 | 1.58 | 1.72 | 0 | 2.45 | 1.57 | 0 | 7.05 | 7.46 | 0 | 7.92 | 8.15 | 0 | 1.61 | 1.7 | 0 | 2.29 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18064 | 48 | 12528 | 39 | 30386 | 145 | 7.47 | 7.49 | 0 | 7.32 | 7.47 | 0 | 7.05 | 7.46 | 0 | 7.92 | 8.15 | 0 | 686000 | 1000 | 601000 | 2000 | 1284000 | 4000 | 1284000 | 1280000 | 13.4 | 7.4375 | 1.83 | 7.645 | 1.825 | 24.61% | 23.87% | 38.5375 | 39.48 | 8.6775 | 12.175 | 1293853.9
2022-05-16 | 2023 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 250000 | 5:57 | 19:21 | 9539.95 | 9539.95 | 9362.6 | 9362.6 | 9955.05 | 9955.05 | 10885.7585 | 10885.7585 | 6583.3835 | 6583.3835 | 11334.15 | 11334.15 | 11251.179 | 11251.179 | 7219.846 | 7219.846 | 9290.8 | 9290.8 | 10104.65 | 10104.65 | 10685.2 | 10685.2 | 10154.546 | 10154.546 | 8748.6165 | 8748.6165 | 10325.2 | 10325.2 | 11662.4085 | 11662.4085 | 10031.5585 | 10031.5585 | 10428.3 | 10428.3 | 375.95 | 375.95 | 11557.1875 | 11557.1875 | 8568.65 | 8568.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11231.125 | 11231.125 | 11594.375 | 11594.375 | 11499.3665 | 11499.3665 | 11808.621 | 11808.621 | 10668.8625 | 10668.8625 | 11667.0625 | 11667.0625 | 10180.529 | 10180.529 | 11584.879 | 11584.879 | 10189.9085 | 10189.9085 | 8244.546 | 8244.546 | 10061.6415 | 10061.6415 | 2028.1 | 2028.1 | 9618.5915 | 9618.5915 | 10255.8335 | 10255.8335 | 9382.229 | 9382.229 | 7111.2 | 7111.2 | 11721.4335 | 11721.4335 | 11129.2415 | 11129.2415 | 10056.6 | 10056.6 | 10389.3 | 10389.3 | 1026 | 1026 | 6594.95 | 6594.95 | 11638.479 | 11638.479 | 9392.8915 | 9392.8915 | 2149.9 | 2149.9 | 7565.2125 | 7565.2125 | 10312.45 | 10312.45 | 10562.671 | 10562.671 | 11623.1665 | 11623.1665 | 11595.3585 | 11595.3585 | 7971.946 | 7971.946 | 5266.096 | 5266.096 | 8585.5625 | 8585.5625 | 7760.571 | 7760.571 | 8040.5 | 8040.5 | 5600.0085 | 5600.0085 | 10765.1085 | 10765.1085 | 11154.15 | 11154.15 | 2611.4 | 2611.4 | 7839.7 | 7839.7 | 10872.896 | 10872.896 | 3151.25 | 3151.25 | 9225.325 | 9225.325 | 5965.15 | 5965.15 | 6045.3 | 6045.3 | 6472.1835 | 6472.1835 | 9944.1 | 9944.1 | 9825.1335 | 9825.1335 | 8542.121 | 8542.121 | 9923.246 | 9923.246 | 10183.6625 | 10183.6625 | 6836.6 | 6836.6 | 2778.65 | 2778.65 | 4514.15 | 4514.15 | 2262.95 | 2262.95 | 3095.4 | 3095.4 | 36.5041 | 36.1447 | 0 | 35.9865 | 35.9785 | 0 | 0 | 37.8718 | 0 | 0 | 0 | 0 | 8.1883 | 8.3168 | 0 | 8.3982 | 8.2091 | 0 | 12.41 | 12.4933 | 0 | 12.9317 | 13.355 | 0 | 7.2085 | 7.2673 | 0 | 7.0841 | 7.2159 | 0 | 1.4731 | 1.8171 | 0 | 2.3215 | 1.6337 | 0 | 6.8895 | 7.2875 | 0 | 7.7244 | 8.0904 | 0 | 1.5163 | 1.7724 | 0 | 2.1806 | 1.7557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18751 | 49 | 13147 | 40 | 31688 | 148 | 7.2085 | 7.2673 | 0 | 7.0841 | 7.2159 | 0 | 6.8895 | 7.2875 | 0 | 7.7244 | 8.0904 | 0 | 687000 | 1000 | 619000 | 1000 | 1302000 | 3000 | 1304000 | 1299000 | 13.4 | 7.194 | 1.8114 | 7.4979 | 1.8062 | 25.18% | 24.09% | 36.1534 | 37.8718 | 8.2781 | 12.7975 | 1312365.337
2022-05-17 | 2023 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 250000 | 5:56 | 19:22 | 9920.8 | 9920.8 | 9720.25 | 9720.25 | 10300.85 | 10300.85 | 11294.25 | 11294.25 | 6848.15 | 6848.15 | 11813.65 | 11813.65 | 11694.45 | 11694.45 | 7519.8 | 7519.8 | 9686.5 | 9686.5 | 10512 | 10512 | 11118.1 | 11118.1 | 10554.85 | 10554.85 | 9194.8 | 9194.8 | 10761.35 | 10761.35 | 12161.1 | 12161.1 | 11263.75 | 11263.75 | 10893.6 | 10893.6 | 1535 | 1535 | 12099.7 | 12099.7 | 8927.6 | 8927.6 | 190 | 190 | 94 | 94 | 191.5 | 191.5 | 192 | 192 | 11690.75 | 11690.75 | 12078.95 | 12078.95 | 11924.95 | 11924.95 | 12270.05 | 12270.05 | 11234.15 | 11234.15 | 12093.5 | 12093.5 | 10540.9 | 10540.9 | 12000.25 | 12000.25 | 10527.85 | 10527.85 | 8551.5 | 8551.5 | 10421.45 | 10421.45 | 2300.3 | 2300.3 | 9883.6 | 9883.6 | 10615.55 | 10615.55 | 9730.3 | 9730.3 | 9948.8 | 9948.8 | 12153.2 | 12153.2 | 11526.25 | 11526.25 | 10394.8 | 10394.8 | 10898.75 | 10898.75 | 1065.4 | 1065.4 | 6841.05 | 6841.05 | 12082.35 | 12082.35 | 9714.6 | 9714.6 | 2233.2 | 2233.2 | 7854.4 | 7854.4 | 10714.85 | 10714.85 | 10968.55 | 10968.55 | 12059.1 | 12059.1 | 12059 | 12059 | 8280.25 | 8280.25 | 6728.8 | 6728.8 | 9131.7 | 9131.7 | 7683.15 | 7683.15 | 8172.45 | 8172.45 | 5806.45 | 5806.45 | 11175.75 | 11175.75 | 11574.15 | 11574.15 | 4806.85 | 4806.85 | 9462.9 | 9462.9 | 11460.65 | 11460.65 | 3222.85 | 3222.85 | 10413.55 | 10413.55 | 6132.2 | 6132.2 | 6549.55 | 6549.55 | 6695 | 6695 | 10731.3 | 10731.3 | 10160.1 | 10160.1 | 8842.1 | 8842.1 | 10297.55 | 10297.55 | 10467.85 | 10467.85 | 7042.8 | 7042.8 | 4036.55 | 4036.55 | 4872.5 | 4872.5 | 2337.75 | 2337.75 | 822 | 822 | 34.8103 | 34.657 | 0 | 34.3434 | 34.4803 | 0 | 0 | 37.0325 | 0 | 0 | 0 | 0 | 3.7846 | 3.9331 | 0 | 4.0046 | 3.7721 | 0 | 7.9783 | 7.5 | 0 | 7.5133 | 7.2833 | 0 | 7.6311 | 7.6824 | 0 | 7.5744 | 7.7547 | 0 | 1.5625 | 1.8608 | 0 | 2.4513 | 1.6433 | 0 | 7.2514 | 7.6633 | 0 | 8.2044 | 8.5683 | 0 | 1.6113 | 1.8227 | 0 | 2.2921 | 1.779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19475 | 50 | 13799 | 41 | 33060 | 152 | 7.6311 | 7.6824 | 0 | 7.5744 | 7.7547 | 0 | 7.2514 | 7.6633 | 0 | 8.2044 | 8.5683 | 0 | 724000 | 1000 | 652000 | 1000 | 1372000 | 4000 | 1374000 | 1368000 | 13.4333 | 7.6607 | 1.8794 | 7.9219 | 1.8763 | 24.53% | 23.69% | 34.5728 | 37.0325 | 3.8736 | 7.5687 | 1383546.3
2022-05-18 | 2023 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 250000 | 6:01 | 19:20 | 9532.3625 | 9532.3625 | 10207.8875 | 10207.8875 | 10280.2085 | 10280.2085 | 10918.2665 | 10918.2665 | 6542.154 | 6542.154 | 11295.246 | 11295.246 | 11223.579 | 11223.579 | 7205.171 | 7205.171 | 9093.5 | 9093.5 | 9891 | 9891 | 10533.5 | 10533.5 | 9869.5 | 9869.5 | 9154.3125 | 9154.3125 | 10276.7585 | 10276.7585 | 11592.304 | 11592.304 | 11263.7915 | 11263.7915 | 10443.7665 | 10443.7665 | 4446.8625 | 4446.8625 | 11615.771 | 11615.771 | 8468.05 | 8468.05 | 179.15 | 179.15 | 88.85 | 88.85 | 154.5 | 154.5 | 179.55 | 179.55 | 10669.4665 | 10669.4665 | 11396.8585 | 11396.8585 | 11433.546 | 11433.546 | 11232.196 | 11232.196 | 10706.0915 | 10706.0915 | 11623.479 | 11623.479 | 10045.646 | 10045.646 | 11615.3375 | 11615.3375 | 10063.529 | 10063.529 | 8176.971 | 8176.971 | 9938.446 | 9938.446 | 2198.7 | 2198.7 | 9299.1835 | 9299.1835 | 10254.429 | 10254.429 | 9281.746 | 9281.746 | 10588.196 | 10588.196 | 11447.496 | 11447.496 | 11123.8085 | 11123.8085 | 10036.0915 | 10036.0915 | 10420.854 | 10420.854 | 1015.95 | 1015.95 | 6525.25 | 6525.25 | 11582.5585 | 11582.5585 | 9223.204 | 9223.204 | 2127.95 | 2127.95 | 7483.604 | 7483.604 | 10208.4625 | 10208.4625 | 10440.979 | 10440.979 | 11586.729 | 11586.729 | 11545.3335 | 11545.3335 | 7829.7415 | 7829.7415 | 8913.1585 | 8913.1585 | 9131.629 | 9131.629 | 7130.1915 | 7130.1915 | 7695 | 7695 | 5305.621 | 5305.621 | 10690.9375 | 10690.9375 | 10975.971 | 10975.971 | 4546.85 | 4546.85 | 11210.979 | 11210.979 | 11143.0415 | 11143.0415 | 3617.5335 | 3617.5335 | 9908.4625 | 9908.4625 | 5841.1665 | 5841.1665 | 6357.904 | 6357.904 | 6521.6665 | 6521.6665 | 10233.071 | 10233.071 | 9760.8875 | 9760.8875 | 8957.704 | 8957.704 | 10988.2415 | 10988.2415 | 10067.05 | 10067.05 | 6829.4 | 6829.4 | 4789.85 | 4789.85 | 4734.85 | 4734.85 | 2551.55 | 2551.55 | 2900.8625 | 2900.8625 | 34.8103 | 38.9081 | 0 | 38.6138 | 38.8062 | 0 | 0 | 41.2256 | 0 | 0 | 0 | 0 | 3.7846 | 2.7492 | 0 | 2.8374 | 2.8151 | 0 | 7.9783 | 6.2183 | 0 | 6.6233 | 7.1767 | 0 | 7.6311 | 7.4446 | 0 | 7.3629 | 7.5031 | 0 | 1.5625 | 1.8244 | 0 | 1.9373 | 1.5932 | 0 | 7.2514 | 7.42 | 0 | 8.0022 | 8.2927 | 0 | 1.6113 | 1.7852 | 0 | 1.8492 | 1.7286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20177 | 51 | 14443 | 42 | 34403 | 155 | 7.6311 | 7.4446 | 0 | 7.3629 | 7.5031 | 0 | 7.2514 | 7.42 | 0 | 8.0022 | 8.2927 | 0 | 702000 | 1000 | 644000 | 1000 | 1343000 | 3000 | 1344000 | 1340000 | 13.3167 | 7.4854 | 1.7293 | 7.7416 | 1.7436 | 23.1% | 22.52% | 37.7846 | 41.2256 | 3.0465 | 6.9992 | 1352762.907
2022-05-19 | 2023 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 251332 | 6:00 | 19:23 | 9781.78 | 9781.78 | 10553.37 | 10553.37 | 10504.085 | 10504.085 | 11089.195 | 11089.195 | 6658.655 | 6658.655 | 11516.21 | 11516.21 | 11376.63 | 11376.63 | 7326.345 | 7326.345 | 9404.7415 | 9404.7415 | 10274.421 | 10274.421 | 10882.3915 | 10882.3915 | 10139.4625 | 10139.4625 | 9405.875 | 9405.875 | 10476.545 | 10476.545 | 11821.02 | 11821.02 | 11488.59 | 11488.59 | 10629.1835 | 10629.1835 | 6305.6 | 6305.6 | 11821.1335 | 11821.1335 | 8928.0375 | 8928.0375 | 185.05 | 185.05 | 90.35 | 90.35 | 184.5 | 184.5 | 184.1 | 184.1 | 11012.8665 | 11012.8665 | 11743.0625 | 11743.0625 | 11762.629 | 11762.629 | 11565.771 | 11565.771 | 10514.1915 | 10514.1915 | 11500.029 | 11500.029 | 9933.446 | 9933.446 | 11426.8875 | 11426.8875 | 9884.475 | 9884.475 | 8462.835 | 8462.835 | 9944.96 | 9944.96 | 2161.1 | 2161.1 | 9490.575 | 9490.575 | 10424.2835 | 10424.2835 | 9477.725 | 9477.725 | 10812.221 | 10812.221 | 11782.379 | 11782.379 | 11324.0085 | 11324.0085 | 10217.596 | 10217.596 | 10655.0085 | 10655.0085 | 1036.2 | 1036.2 | 6740.079 | 6740.079 | 11837.521 | 11837.521 | 9441.954 | 9441.954 | 2169.6 | 2169.6 | 7647.7 | 7647.7 | 10438.121 | 10438.121 | 10684.4835 | 10684.4835 | 11819.8415 | 11819.8415 | 11778.904 | 11778.904 | 8349.121 | 8349.121 | 10751.5835 | 10751.5835 | 10185.85 | 10185.85 | 8774.8625 | 8774.8625 | 8427.321 | 8427.321 | 5146.746 | 5146.746 | 11047.721 | 11047.721 | 11177.5125 | 11177.5125 | 4706.8335 | 4706.8335 | 11461.1665 | 11461.1665 | 11372.325 | 11372.325 | 3701.821 | 3701.821 | 10072.575 | 10072.575 | 5990.9085 | 5990.9085 | 6451.0335 | 6451.0335 | 6610.85 | 6610.85 | 10462.4585 | 10462.4585 | 9965.275 | 9965.275 | 9134.529 | 9134.529 | 11231.1415 | 11231.1415 | 9746.775 | 9746.775 | 6977.821 | 6977.821 | 5260.529 | 5260.529 | 6232.7375 | 6232.7375 | 2589.7 | 2589.7 | 793.6 | 793.6 | 40.6433 | 40.3415 | 0 | 40.2412 | 40.3589 | 0 | 0 | 42.4423 | 0 | 0 | 0 | 0 | 4.6425 | 4.6888 | 0 | 4.5636 | 4.7505 | 0 | 7.655 | 7.6417 | 0 | 8.1967 | 8.1017 | 0 | 7.5917 | 7.7594 | 0 | 7.4973 | 7.6769 | 0 | 1.5801 | 1.8639 | 0 | 1.9263 | 1.6492 | 0 | 7.1856 | 7.7162 | 0 | 8.1068 | 8.4548 | 0 | 1.6299 | 1.8296 | 0 | 1.8499 | 1.7793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20896 | 53 | 15108 | 44 | 35782 | 159 | 7.5917 | 7.7594 | 0 | 7.4973 | 7.6769 | 0 | 7.1856 | 7.7162 | 0 | 8.1068 | 8.4548 | 0 | 719000 | 2000 | 665000 | 2000 | 1379000 | 4000 | 1380000 | 1375000 | 13.3833 | 7.6313 | 1.7549 | 7.8659 | 1.7722 | 23% | 22.53% | 40.3962 | 42.4423 | 4.6614 | 7.8987 | 1390681.043
2022-05-20 | 2023 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 254608 | 5:57 | 19:43 | 9467.05 | 9467.05 | 10589.9 | 10589.9 | 10159.5 | 10159.5 | 10745.45 | 10745.45 | 6443.05 | 6443.05 | 11134.45 | 11134.45 | 10985.55 | 10985.55 | 7070.75 | 7070.75 | 9104.3 | 9104.3 | 10186.95 | 10186.95 | 10499.4 | 10499.4 | 9810.25 | 9810.25 | 10321.15 | 10321.15 | 11044.95 | 11044.95 | 11415.95 | 11415.95 | 11094 | 11094 | 9796.65 | 9796.65 | 6112.75 | 6112.75 | 10897.3 | 10897.3 | 8376.45 | 8376.45 | 178.35 | 178.35 | 86.25 | 86.25 | 172.5 | 172.5 | 176.5 | 176.5 | 11061.2 | 11061.2 | 11790.5 | 11790.5 | 11842.75 | 11842.75 | 11649.1 | 11649.1 | 10464.5 | 10464.5 | 11478.75 | 11478.75 | 9845.7 | 9845.7 | 11421.8 | 11421.8 | 9979.9 | 9979.9 | 8772.3 | 8772.3 | 10217.35 | 10217.35 | 2949.35 | 2949.35 | 9250.35 | 9250.35 | 10082 | 10082 | 9143.35 | 9143.35 | 10424.3 | 10424.3 | 11330.25 | 11330.25 | 10922.6 | 10922.6 | 9880.9 | 9880.9 | 10299.1 | 10299.1 | 1002.35 | 1002.35 | 6543.95 | 6543.95 | 11445.85 | 11445.85 | 9197.5 | 9197.5 | 2096 | 2096 | 7390.5 | 7390.5 | 10088.8 | 10088.8 | 10330.1 | 10330.1 | 11440.7 | 11440.7 | 11408.05 | 11408.05 | 10308.55 | 10308.55 | 10477.3 | 10477.3 | 10487.85 | 10487.85 | 10249.75 | 10249.75 | 8486.2 | 8486.2 | 5196.1 | 5196.1 | 10684.25 | 10684.25 | 10906.5 | 10906.5 | 6085.55 | 6085.55 | 11112.35 | 11112.35 | 11023.45 | 11023.45 | 3590.5 | 3590.5 | 10108.3 | 10108.3 | 5782.7 | 5782.7 | 7380 | 7380 | 8720.5 | 8720.5 | 9953.35 | 9953.35 | 9612.75 | 9612.75 | 8854 | 8854 | 10493.4 | 10493.4 | 8526.6 | 8526.6 | 6690.6 | 6690.6 | 6369.1 | 6369.1 | 5931.75 | 5931.75 | 2586.15 | 2586.15 | 2358.45 | 2358.45 | 40.4251 | 39.9143 | 0 | 39.9032 | 39.8679 | 0 | 0 | 41.3914 | 0 | 0 | 0 | 0 | 8.7556 | 8.9285 | 0 | 8.7389 | 8.5759 | 0 | 13.2 | 14.665 | 0 | 14.14 | 13.58 | 0 | 7.1197 | 7.2372 | 0 | 7.0312 | 7.2141 | 0 | 1.5667 | 1.7256 | 0 | 1.9209 | 1.5341 | 0 | 6.7227 | 7.2103 | 0 | 7.5748 | 7.9067 | 0 | 1.6176 | 1.6986 | 0 | 1.8426 | 1.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21604 | 54 | 15776 | 45 | 37155 | 163 | 7.1197 | 7.2372 | 0 | 7.0312 | 7.2141 | 0 | 6.7227 | 7.2103 | 0 | 7.5748 | 7.9067 | 0 | 708000 | 1000 | 668000 | 1000 | 1373000 | 4000 | 1374000 | 1369000 | 13.7667 | 7.1505 | 1.6868 | 7.3536 | 1.7064 | 23.59% | 23.2% | 40.0276 | 41.3914 | 8.7497 | 13.8962 | 1383190.5
2022-05-21 | 2023 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 258435 | 6:00 | 19:25 | 9946.35 | 9946.35 | 11271.35 | 11271.35 | 10632.3 | 10632.3 | 11209.3 | 11209.3 | 6705.5 | 6705.5 | 11588.1 | 11588.1 | 11449.8 | 11449.8 | 9041.25 | 9041.25 | 10702.95 | 10702.95 | 10869.5 | 10869.5 | 10914.5 | 10914.5 | 10262.65 | 10262.65 | 10777 | 10777 | 11525.2 | 11525.2 | 11938.55 | 11938.55 | 10883.6 | 10883.6 | 10740.5 | 10740.5 | 6735.45 | 6735.45 | 11963.35 | 11963.35 | 9204.8 | 9204.8 | 183.8 | 183.8 | 90.9 | 90.9 | 184.5 | 184.5 | 150 | 150 | 11495.8 | 11495.8 | 12269.4 | 12269.4 | 12311.55 | 12311.55 | 12094.85 | 12094.85 | 10896 | 10896 | 11946.05 | 11946.05 | 10266.7 | 10266.7 | 11820 | 11820 | 10424.05 | 10424.05 | 10241.5 | 10241.5 | 10727.95 | 10727.95 | 4410.85 | 4410.85 | 9714.75 | 9714.75 | 10450.45 | 10450.45 | 9544.2 | 9544.2 | 10886.75 | 10886.75 | 11816 | 11816 | 11429 | 11429 | 10255.5 | 10255.5 | 10766 | 10766 | 1045.55 | 1045.55 | 6830.75 | 6830.75 | 11915.1 | 11915.1 | 9604 | 9604 | 2177.055 | 2177.055 | 7632.67 | 7632.67 | 10464.13 | 10464.13 | 10727.315 | 10727.315 | 11833 | 11833 | 11836.871 | 11836.871 | 10715.175 | 10715.175 | 11070.3665 | 11070.3665 | 10938.6665 | 10938.6665 | 10636.5915 | 10636.5915 | 9118.975 | 9118.975 | 9068.6665 | 9068.6665 | 8043.2375 | 8043.2375 | 8351.7585 | 8351.7585 | 6030.025 | 6030.025 | 8397.8915 | 8397.8915 | 11730.679 | 11730.679 | 3740.854 | 3740.854 | 10596.4835 | 10596.4835 | 6030.0125 | 6030.0125 | 11423.775 | 11423.775 | 12709.7085 | 12709.7085 | 10468.5835 | 10468.5835 | 10766.146 | 10766.146 | 10696 | 10696 | 10875.8 | 10875.8 | 12712.7 | 12712.7 | 6960.75 | 6960.75 | 7509.58 | 7509.58 | 6287.855 | 6287.855 | 2965.01 | 2965.01 | 4463.91 | 4463.91 | 37.5481 | 37.0819 | 0 | 37.0751 | 37.2283 | 0 | 0 | 38.6634 | 0 | 0 | 0 | 0 | 8.2266 | 8.285 | 0 | 8.1245 | 7.8756 | 0 | 12.795 | 12.5367 | 0 | 11.465 | 12.5983 | 0 | 7.3159 | 7.4665 | 0 | 7.2569 | 7.4654 | 0 | 1.5156 | 1.889 | 0 | 1.8147 | 1.672 | 0 | 6.9676 | 7.4387 | 0 | 7.8778 | 8.2985 | 0 | 1.571 | 1.8435 | 0 | 1.7584 | 1.7962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22357 | 55 | 16495 | 46 | 38621 | 166 | 7.3159 | 7.4665 | 0 | 7.2569 | 7.4654 | 0 | 6.9676 | 7.4387 | 0 | 7.8778 | 8.2985 | 0 | 753000 | 1000 | 719000 | 1000 | 1466000 | 3000 | 1470000 | 1463000 | 13.4167 | 7.3762 | 1.7228 | 7.6456 | 1.7423 | 23.36% | 22.79% | 37.2334 | 38.6634 | 8.1279 | 12.3488 | 1478228.383
2022-05-22 | 2023 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 264005 | 5:55 | 19:25 | 10043.7 | 10043.7 | 11371.11 | 11371.11 | 10720 | 10720 | 11259.925 | 11259.925 | 8363.205 | 8363.205 | 11664.025 | 11664.025 | 11559.18 | 11559.18 | 9791.38 | 9791.38 | 11795.15 | 11795.15 | 11404.45 | 11404.45 | 11063.65 | 11063.65 | 9676.92 | 9676.92 | 10919.7 | 10919.7 | 11668.8 | 11668.8 | 12057.54 | 12057.54 | 11043.35 | 11043.35 | 10870.15 | 10870.15 | 6851.25 | 6851.25 | 12102.285 | 12102.285 | 9377 | 9377 | 183.55 | 183.55 | 89 | 89 | 191 | 191 | 1697.7 | 1697.7 | 11039 | 11039 | 11762.53 | 11762.53 | 11919.085 | 11919.085 | 11645.235 | 11645.235 | 10941.4 | 10941.4 | 11968.65 | 11968.65 | 10320.565 | 10320.565 | 11723.87 | 11723.87 | 10529.48 | 10529.48 | 9802.7 | 9802.7 | 10796.85 | 10796.85 | 4410.15 | 4410.15 | 9663.595 | 9663.595 | 10335.735 | 10335.735 | 9534.6 | 9534.6 | 10829.95 | 10829.95 | 11741.15 | 11741.15 | 11340.445 | 11340.445 | 10167.505 | 10167.505 | 10766.61 | 10766.61 | 1054.5 | 1054.5 | 6887.8 | 6887.8 | 11948.45 | 11948.45 | 9698.6 | 9698.6 | 2195.55 | 2195.55 | 7697.255 | 7697.255 | 10595.75 | 10595.75 | 10877.425 | 10877.425 | 11921.9625 | 11921.9625 | 12068.546 | 12068.546 | 10963.1 | 10963.1 | 11434.5 | 11434.5 | 10948.2835 | 10948.2835 | 10664.2 | 10664.2 | 9278.3335 | 9278.3335 | 9195.75 | 9195.75 | 11254 | 11254 | 12025.3 | 12025.3 | 9041.5 | 9041.5 | 11786.3415 | 11786.3415 | 11766.4 | 11766.4 | 3776.9 | 3776.9 | 10665.7335 | 10665.7335 | 6084.65 | 6084.65 | 12555.9165 | 12555.9165 | 12830.4875 | 12830.4875 | 11233.45 | 11233.45 | 11605.45 | 11605.45 | 12146.15 | 12146.15 | 11397.66 | 11397.66 | 12242.41 | 12242.41 | 10553.25 | 10553.25 | 8501.35 | 8501.35 | 6357.7 | 6357.7 | 3469.5 | 3469.5 | 6104.8 | 6104.8 | 36.5918 | 36.3147 | 0 | 36.1323 | 36.1645 | 0 | 0 | 38.2913 | 0 | 0 | 0 | 0 | 6.4285 | 6.4286 | 0 | 6.4862 | 6.3104 | 0 | 9.8667 | 9.5567 | 0 | 10.0083 | 10.3183 | 0 | 7.4275 | 7.156 | 0 | 7.3059 | 7.5331 | 0 | 1.5169 | 1.718 | 0 | 1.7836 | 1.6758 | 0 | 7.0892 | 7.1738 | 0 | 7.9345 | 8.476 | 0 | 1.5693 | 1.6791 | 0 | 1.7125 | 1.8038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23119 | 56 | 17264 | 47 | 40148 | 169 | 7.4275 | 7.156 | 0 | 7.3059 | 7.5331 | 0 | 7.0892 | 7.1738 | 0 | 7.9345 | 8.476 | 0 | 762000 | 1000 | 769000 | 1000 | 1527000 | 3000 | 1529000 | 1524000 | 13.5 | 7.3557 | 1.6736 | 7.6684 | 1.6912 | 22.75% | 22.05% | 36.3008 | 38.2913 | 6.4134 | 9.9375 | 1539664.159
2022-05-23 | 2023 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 268695.73 | 6:06 | 19:22 | 8330.4 | 8330.4 | 9387.8 | 9387.8 | 4973.7 | 4973.7 | 9165.4 | 9165.4 | 9798.35 | 9798.35 | 9369.75 | 9369.75 | 4945.8 | 4945.8 | 7755.65 | 7755.65 | 9459.95 | 9459.95 | 9022.55 | 9022.55 | 8870.9 | 8870.9 | 7694.1 | 7694.1 | 8730.95 | 8730.95 | 9341.7 | 9341.7 | 9644.7 | 9644.7 | 8773.55 | 8773.55 | 8720 | 8720 | 5427.3 | 5427.3 | 9699.2 | 9699.2 | 7432.4 | 7432.4 | 148.2 | 148.2 | 71.25 | 71.25 | 150 | 150 | 1359.15 | 1359.15 | 9373.9 | 9373.9 | 9972.45 | 9972.45 | 10136.15 | 10136.15 | 9875.4 | 9875.4 | 8792.95 | 8792.95 | 9696.4 | 9696.4 | 8302.45 | 8302.45 | 9903.95 | 9903.95 | 8562.4 | 8562.4 | 8031.25 | 8031.25 | 8722.9 | 8722.9 | 3561.65 | 3561.65 | 7837.2 | 7837.2 | 8704.95 | 8704.95 | 7698.45 | 7698.45 | 8752.9 | 8752.9 | 9536.45 | 9536.45 | 9350.65 | 9350.65 | 8495.35 | 8495.35 | 8721.3 | 8721.3 | 842.5 | 842.5 | 5515.55 | 5515.55 | 9604.4 | 9604.4 | 7746.45 | 7746.45 | 1756.75 | 1756.75 | 6154.1 | 6154.1 | 8366.45 | 8366.45 | 8667.6 | 8667.6 | 9657.9 | 9657.9 | 9632.15 | 9632.15 | 8779.5 | 8779.5 | 9745.7 | 9745.7 | 8373.2 | 8373.2 | 8660.05 | 8660.05 | 7330.15 | 7330.15 | 7343.15 | 7343.15 | 9217.1 | 9217.1 | 9762.35 | 9762.35 | 7778.4 | 7778.4 | 9860.25 | 9860.25 | 9439.5 | 9439.5 | 3026 | 3026 | 8581.7 | 8581.7 | 4561 | 4561 | 10231.5 | 10231.5 | 10607.85 | 10607.85 | 8984.7 | 8984.7 | 8647.8 | 8647.8 | 9953.75 | 9953.75 | 9200.95 | 9200.95 | 10205.45 | 10205.45 | 8360 | 8360 | 7867.15 | 7867.15 | 5093.5 | 5093.5 | 3594.2 | 3594.2 | 4991.65 | 4991.65 | 35.9787 | 35.4981 | 0 | 35.4822 | 35.5397 | 0 | 0 | 35.3077 | 0 | 0 | 0 | 0 | 8.1764 | 8.139 | 0 | 8.1916 | 7.7802 | 0 | 12.2767 | 12.6767 | 0 | 12.6133 | 12.5717 | 0 | 5.708 | 5.2142 | 0 | 5.628 | 5.8514 | 0 | 1.2278 | 1.2969 | 0 | 1.4489 | 1.387 | 0 | 5.4646 | 5.2094 | 0 | 6.1251 | 6.5731 | 0 | 1.2847 | 1.281 | 0 | 1.4027 | 1.496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23729 | 58 | 17883 | 48 | 41373 | 173 | 5.708 | 5.2142 | 0 | 5.628 | 5.8514 | 0 | 5.4646 | 5.2094 | 0 | 6.1251 | 6.5731 | 0 | 610000 | 2000 | 619000 | 1000 | 1225000 | 4000 | 1226000 | 1221000 | 13.2667 | 5.6004 | 1.3401 | 5.8431 | 1.3661 | 23.93% | 23.38% | 35.6247 | 35.3077 | 8.0718 | 12.5346 | 1240884.5
2022-05-24 | 2023 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 271513 | 5:53 | 19:21 | 7791.635 | 7791.635 | 11502.04 | 11502.04 | 11085.985 | 11085.985 | 11122.075 | 11122.075 | 12051.04 | 12051.04 | 12131.67 | 12131.67 | 11943.75 | 11943.75 | 9549.97 | 9549.97 | 11301.18 | 11301.18 | 10847.425 | 10847.425 | 10805.55 | 10805.55 | 9223.19 | 9223.19 | 10517.55 | 10517.55 | 11258.185 | 11258.185 | 11559.34 | 11559.34 | 10517.585 | 10517.585 | 10450.9 | 10450.9 | 8395.865 | 8395.865 | 11804.69 | 11804.69 | 8888.69 | 8888.69 | 178.5 | 178.5 | 88.5 | 88.5 | 153.5 | 153.5 | 1637.7 | 1637.7 | 11246.1 | 11246.1 | 11972.915 | 11972.915 | 12030.13 | 12030.13 | 11792.015 | 11792.015 | 10604.325 | 10604.325 | 11676.445 | 11676.445 | 10068.665 | 10068.665 | 11668.185 | 11668.185 | 10431.73 | 10431.73 | 10363.855 | 10363.855 | 10528.29 | 10528.29 | 4317.67 | 4317.67 | 9475.595 | 9475.595 | 10276.875 | 10276.875 | 9302.41 | 9302.41 | 10592.375 | 10592.375 | 11490.08 | 11490.08 | 11200.705 | 11200.705 | 10078.155 | 10078.155 | 10495.85 | 10495.85 | 1019.045 | 1019.045 | 6648.06 | 6648.06 | 11535.75 | 11535.75 | 9256.25 | 9256.25 | 2128.13 | 2128.13 | 7447.27 | 7447.27 | 10096.345 | 10096.345 | 10483.46 | 10483.46 | 11538.17 | 11538.17 | 11710.47 | 11710.47 | 10542.13 | 10542.13 | 11737.07 | 11737.07 | 10566.885 | 10566.885 | 10531.855 | 10531.855 | 9796.97 | 9796.97 | 8886.405 | 8886.405 | 11134.8 | 11134.8 | 11760.665 | 11760.665 | 9340.7 | 9340.7 | 11840.69 | 11840.69 | 11391.171 | 11391.171 | 3649.054 | 3649.054 | 10387.25 | 10387.25 | 6703.729 | 6703.729 | 12210.679 | 12210.679 | 12593.2665 | 12593.2665 | 10856.621 | 10856.621 | 9960.4875 | 9960.4875 | 11958.795 | 11958.795 | 11040.69 | 11040.69 | 11958.125 | 11958.125 | 10138.72 | 10138.72 | 10644.83 | 10644.83 | 7202.935 | 7202.935 | 4688.815 | 4688.815 | 6905.365 | 6905.365 | 35.4874 | 35.318 | 0 | 35.1358 | 35.1414 | 0 | 0 | 52.9407 | 0 | 0 | 0 | 0 | 4.7338 | 4.7488 | 0 | 4.8825 | 4.6801 | 0 | 9.135 | 7.76 | 0 | 7.6267 | 7.6733 | 0 | 7.4213 | 7.4685 | 0 | 7.0786 | 7.4384 | 0 | 1.5314 | 1.7751 | 0 | 1.8445 | 1.5944 | 0 | 7.0261 | 7.4291 | 0 | 7.6413 | 8.2556 | 0 | 1.5946 | 1.7257 | 0 | 1.7674 | 1.7301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24488 | 59 | 18647 | 49 | 42890 | 177 | 7.4213 | 7.4685 | 0 | 7.0786 | 7.4384 | 0 | 7.0261 | 7.4291 | 0 | 7.6413 | 8.2556 | 0 | 759000 | 1000 | 764000 | 1000 | 1517000 | 4000 | 1521000 | 1513000 | 13.4667 | 7.3517 | 1.6864 | 7.588 | 1.7044 | 22.94% | 22.46% | 35.2706 | 52.9407 | 4.7613 | 8.0487 | 1529421.076
2022-05-25 | 2023 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 272394 | 5:57 | 19:18 | 9627.7 | 9627.7 | 11597.11 | 11597.11 | 11023.105 | 11023.105 | 10955.62 | 10955.62 | 12130.25 | 12130.25 | 12197.405 | 12197.405 | 12166.845 | 12166.845 | 9991.36 | 9991.36 | 11118.38 | 11118.38 | 10737.14 | 10737.14 | 8768.125 | 8768.125 | 6407.61 | 6407.61 | 10371.965 | 10371.965 | 11422.3 | 11422.3 | 11673.345 | 11673.345 | 10422.845 | 10422.845 | 10315.845 | 10315.845 | 8292.54 | 8292.54 | 11619.535 | 11619.535 | 8713.935 | 8713.935 | 250.45 | 250.45 | 87 | 87 | 181.4 | 181.4 | 1614.85 | 1614.85 | 11117.465 | 11117.465 | 11816.925 | 11816.925 | 11871.495 | 11871.495 | 11603.095 | 11603.095 | 10617.355 | 10617.355 | 11585.945 | 11585.945 | 10088.045 | 10088.045 | 11738.56 | 11738.56 | 10263.865 | 10263.865 | 10329.445 | 10329.445 | 10234.19 | 10234.19 | 4247.315 | 4247.315 | 9337.97 | 9337.97 | 10117.75 | 10117.75 | 9151.79 | 9151.79 | 10432.55 | 10432.55 | 10616.905 | 10616.905 | 11004.11 | 11004.11 | 9929.67 | 9929.67 | 10107.66 | 10107.66 | 1004.25 | 1004.25 | 6549.655 | 6549.655 | 11344.98 | 11344.98 | 9082.96 | 9082.96 | 2091.8 | 2091.8 | 7321.9 | 7321.9 | 9848.605 | 9848.605 | 10290.295 | 10290.295 | 11336.185 | 11336.185 | 11568.89 | 11568.89 | 10384.075 | 10384.075 | 11540.89 | 11540.89 | 10483.56 | 10483.56 | 10449.035 | 10449.035 | 9926.385 | 9926.385 | 9467.12 | 9467.12 | 10991.74 | 10991.74 | 11585.18 | 11585.18 | 9128.48 | 9128.48 | 11591.07 | 11591.07 | 11197.7 | 11197.7 | 3583.75 | 3583.75 | 10206.535 | 10206.535 | 6597.735 | 6597.735 | 12047.235 | 12047.235 | 12392.76 | 12392.76 | 10666.365 | 10666.365 | 9803.02 | 9803.02 | 11801.935 | 11801.935 | 10893.285 | 10893.285 | 11780.465 | 11780.465 | 10013.305 | 10013.305 | 10816.12 | 10816.12 | 7137.155 | 7137.155 | 6787.66 | 6787.66 | 6814.99 | 6814.99 | 37.2836 | 36.9408 | 0 | 36.9327 | 36.9008 | 0 | 0 | 54.5307 | 0 | 0 | 0 | 0 | 4.7901 | 4.7273 | 0 | 4.6643 | 4.5652 | 0 | 8.5017 | 7.8133 | 0 | 8.345 | 8.4517 | 0 | 7.3654 | 7.4125 | 0 | 7.0085 | 7.3357 | 0 | 1.5211 | 1.7695 | 0 | 1.8266 | 1.5726 | 0 | 6.9643 | 7.3662 | 0 | 7.5651 | 8.1463 | 0 | 1.6 | 1.7189 | 0 | 1.7469 | 1.6891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25236 | 60 | 19403 | 50 | 44390 | 180 | 7.3654 | 7.4125 | 0 | 7.0085 | 7.3357 | 0 | 6.9643 | 7.3662 | 0 | 7.5651 | 8.1463 | 0 | 748000 | 1000 | 756000 | 1000 | 1500000 | 3000 | 1502000 | 1497000 | 13.35 | 7.2805 | 1.6725 | 7.5105 | 1.6887 | 22.97% | 22.49% | 37.0145 | 54.5307 | 4.6867 | 8.2779 | 1512851.67
2022-05-26 | 2023 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 273963.58 | 5:56 | 19:25 | 10851.25 | 10851.25 | 12102.55 | 12102.55 | 11495.25 | 11495.25 | 11405 | 11405 | 12700.55 | 12700.55 | 12666.5 | 12666.5 | 12594.25 | 12594.25 | 12500.3 | 12500.3 | 11793.9 | 11793.9 | 11594.25 | 11594.25 | 10050.65 | 10050.65 | 6977 | 6977 | 10788.75 | 10788.75 | 12013.35 | 12013.35 | 12195.9 | 12195.9 | 11297.3 | 11297.3 | 10764.4 | 10764.4 | 8696.25 | 8696.25 | 12140.95 | 12140.95 | 9135.85 | 9135.85 | 1668.5 | 1668.5 | 69.9 | 69.9 | 194.1 | 194.1 | 1703.05 | 1703.05 | 11628.45 | 11628.45 | 12312.15 | 12312.15 | 12353.85 | 12353.85 | 12102.55 | 12102.55 | 11274.85 | 11274.85 | 12141.7 | 12141.7 | 10849.15 | 10849.15 | 12223.8 | 12223.8 | 10974.05 | 10974.05 | 10988.4 | 10988.4 | 11072.8 | 11072.8 | 4461.7 | 4461.7 | 9786.8 | 9786.8 | 10508.9 | 10508.9 | 9607.95 | 9607.95 | 10954.3 | 10954.3 | 11443.6 | 11443.6 | 11389.5 | 11389.5 | 10329.1 | 10329.1 | 10564.35 | 10564.35 | 1052.7 | 1052.7 | 6866.05 | 6866.05 | 11867.65 | 11867.65 | 9536.3 | 9536.3 | 2196.35 | 2196.35 | 7690.95 | 7690.95 | 10243.05 | 10243.05 | 10674.3 | 10674.3 | 11856.3 | 11856.3 | 12123.7 | 12123.7 | 10890.5 | 10890.5 | 12493.7 | 12493.7 | 11958.7 | 11958.7 | 11025.95 | 11025.95 | 10835.3 | 10835.3 | 10286.5 | 10286.5 | 11473.1 | 11473.1 | 12138.1 | 12138.1 | 9622.25 | 9622.25 | 12128.4 | 12128.4 | 11799.4 | 11799.4 | 3788.3 | 3788.3 | 10765.35 | 10765.35 | 6807.75 | 6807.75 | 12519.65 | 12519.65 | 12858.2 | 12858.2 | 11167.85 | 11167.85 | 10236.35 | 10236.35 | 12272.95 | 12272.95 | 11423.45 | 11423.45 | 12264.75 | 12264.75 | 10440.8 | 10440.8 | 12056.85 | 12056.85 | 7479.15 | 7479.15 | 7566.45 | 7566.45 | 7375.1 | 7375.1 | 35.4004 | 35.2812 | 0 | 34.9742 | 34.9851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4046 | 6.8049 | 0 | 6.8227 | 6.5742 | 0 | 10.18 | 9.6817 | 0 | 9.9233 | 9.0667 | 0 | 7.6632 | 7.6973 | 0 | 7.3097 | 7.3433 | 0 | 1.5745 | 1.8348 | 0 | 1.8899 | 1.5872 | 0 | 7.2482 | 7.6252 | 0 | 7.8743 | 8.1895 | 0 | 1.6659 | 1.7879 | 0 | 1.8163 | 1.7299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26033 | 62 | 20202 | 51 | 45981 | 184 | 7.6632 | 7.6973 | 0 | 7.3097 | 7.3433 | 0 | 7.2482 | 7.6252 | 0 | 7.8743 | 8.1895 | 0 | 797000 | 2000 | 799000 | 1000 | 1591000 | 4000 | 1593000 | 1587000 | 13.4833 | 7.5034 | 1.7216 | 7.7343 | 1.75 | 22.94% | 22.63% | 35.1602 | #DIV/0! | 6.6516 | 9.7129 | 1604299.8
2022-05-27 | 2023 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 274366.97 | 5:53 | 19:28 | 10658.05 | 10658.05 | 11877.75 | 11877.75 | 11298.65 | 11298.65 | 11218 | 11218 | 12489.85 | 12489.85 | 12444.85 | 12444.85 | 12374.05 | 12374.05 | 12341.4 | 12341.4 | 11595.7 | 11595.7 | 11359.65 | 11359.65 | 9844.85 | 9844.85 | 6972.8 | 6972.8 | 10567 | 10567 | 12010.6 | 12010.6 | 12076.15 | 12076.15 | 11760.6 | 11760.6 | 10545.85 | 10545.85 | 8483.2 | 8483.2 | 11897.85 | 11897.85 | 8946.75 | 8946.75 | 2904.15 | 2904.15 | 33.3 | 33.3 | 185.75 | 185.75 | 1656.6 | 1656.6 | 11421.2 | 11421.2 | 12132.75 | 12132.75 | 12080.05 | 12080.05 | 11867.9 | 11867.9 | 11055.5 | 11055.5 | 11881.85 | 11881.85 | 10589.6 | 10589.6 | 11990.1 | 11990.1 | 10669.95 | 10669.95 | 10541.5 | 10541.5 | 11015.8 | 11015.8 | 4429.8 | 4429.8 | 9588.65 | 9588.65 | 10320.05 | 10320.05 | 9398.75 | 9398.75 | 10720.7 | 10720.7 | 10913.55 | 10913.55 | 11064.95 | 11064.95 | 10084.15 | 10084.15 | 10330.2 | 10330.2 | 1028 | 1028 | 6730.2 | 6730.2 | 11641.15 | 11641.15 | 9369.4 | 9369.4 | 2141.2 | 2141.2 | 7505.45 | 7505.45 | 10098.45 | 10098.45 | 10485.8 | 10485.8 | 11540.8 | 11540.8 | 11713.2 | 11713.2 | 10544.45 | 10544.45 | 11739.8 | 11739.8 | 10569.4 | 10569.4 | 10534.3 | 10534.3 | 9799.45 | 9799.45 | 8888.25 | 8888.25 | 11137.4 | 11137.4 | 11763.3 | 11763.3 | 9342.75 | 9342.75 | 11843.45 | 11843.45 | 11799.25 | 11799.25 | 3650.3 | 3650.3 | 10391 | 10391 | 6705.95 | 6705.95 | 12213.45 | 12213.45 | 12596.25 | 12596.25 | 10858.95 | 10858.95 | 9962.7 | 9962.7 | 11998.55 | 11998.55 | 11142.5 | 11142.5 | 11960.95 | 11960.95 | 10141 | 10141 | 12096.3 | 12096.3 | 7402.75 | 7402.75 | 7777.7 | 7777.7 | 7452.25 | 7452.25 | 34.8253 | 34.8243 | 0 | 34.4549 | 34.9851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9531 | 7.9099 | 0 | 8.2896 | 6.5742 | 0 | 11.9583 | 11.355 | 0 | 11.87 | 11.54 | 0 | 7.3841 | 7.4457 | 0 | 7.0094 | 7.3433 | 0 | 1.5574 | 1.7306 | 0 | 1.8843 | 1.5872 | 0 | 6.9591 | 7.3807 | 0 | 7.5318 | 8.1895 | 0 | 1.6478 | 1.6948 | 0 | 1.8005 | 1.7299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26820 | 63 | 20988 | 52 | 47548 | 187 | 7.3841 | 7.4457 | 0 | 7.0094 | 7.3433 | 0 | 6.9591 | 7.3807 | 0 | 7.5318 | 8.1895 | 0 | 787000 | 1000 | 786000 | 1000 | 1567000 | 3000 | 1571000 | 1564000 | 13.5833 | 7.2956 | 1.6899 | 7.5153 | 1.7183 | 23.16% | 22.86% | 34.7724 | #DIV/0! | 7.6817 | 11.6808 | 1568412.9
2022-05-28 | 2023 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 277773.02 | 5:55 | 19:24 | 10000.08 | 10000.08 | 11120.375 | 11120.375 | 10615.105 | 10615.105 | 10607.375 | 10607.375 | 11830.305 | 11830.305 | 11800.82 | 11800.82 | 11785.76 | 11785.76 | 11708.495 | 11708.495 | 10931.85 | 10931.85 | 10602.205 | 10602.205 | 9242.875 | 9242.875 | 6565.48 | 6565.48 | 9542.76 | 9542.76 | 11324.86 | 11324.86 | 11505.8 | 11505.8 | 11116.615 | 11116.615 | 9958.52 | 9958.52 | 8929.765 | 8929.765 | 11138.805 | 11138.805 | 8784.055 | 8784.055 | 3056.4 | 3056.4 | 30 | 30 | 173.55 | 173.55 | 1549.35 | 1549.35 | 10680.375 | 10680.375 | 11345.095 | 11345.095 | 11349.325 | 11349.325 | 11168.5 | 11168.5 | 10574.21 | 10574.21 | 11185.415 | 11185.415 | 9035.675 | 9035.675 | 11313.405 | 11313.405 | 10179.2 | 10179.2 | 10270.685 | 10270.685 | 11009.25 | 11009.25 | 4469.65 | 4469.65 | 8821.395 | 8821.395 | 9646.69 | 9646.69 | 8616.035 | 8616.035 | 9833.54 | 9833.54 | 9708.465 | 9708.465 | 10075.41 | 10075.41 | 9257.17 | 9257.17 | 9396.385 | 9396.385 | 942.15 | 942.15 | 6179.3 | 6179.3 | 10742.475 | 10742.475 | 8659.15 | 8659.15 | 2141.2 | 2141.2 | 7505.45 | 7505.45 | 9986.75 | 9986.75 | 10345.65 | 10345.65 | 11647 | 11647 | 11849.25 | 11849.25 | 10632.2 | 10632.2 | 12221.55 | 12221.55 | 11686.9 | 11686.9 | 10753.1 | 10753.1 | 10594.45 | 10594.45 | 10097.25 | 10097.25 | 11237.75 | 11237.75 | 11879.55 | 11879.55 | 9415.1 | 9415.1 | 11830.5 | 11830.5 | 11513.05 | 11513.05 | 3706.25 | 3706.25 | 10522.35 | 10522.35 | 7765.35 | 7765.35 | 12347.8 | 12347.8 | 12618.6 | 12618.6 | 11557 | 11557 | 10055.4 | 10055.4 | 11998.55 | 11998.55 | 11142.5 | 11142.5 | 12012.7 | 12012.7 | 10163.85 | 10163.85 | 11480.5 | 11480.5 | 7071.185 | 7071.185 | 7203.45 | 7203.45 | 7146.645 | 7146.645 | 35.2798 | 35.0852 | 0 | 34.859 | 34.9851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5591 | 7.4207 | 0 | 7.675 | 7.46 | 0 | 12.8083 | 11.8917 | 0 | 12.9517 | 11.76 | 0 | 6.8088 | 6.8457 | 0 | 6.3735 | 6.76 | 0 | 1.4404 | 1.622 | 0 | 1.7089 | 1.64 | 0 | 6.3992 | 6.7909 | 0 | 6.8329 | 6.76 | 0 | 1.5319 | 1.5932 | 0 | 1.6428 | 1.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27563 | 64 | 21718 | 54 | 49017 | 192 | 6.8088 | 6.8457 | 0 | 6.3735 | 6.76 | 0 | 6.3992 | 6.7909 | 0 | 6.8329 | 6.76 | 0 | 743000 | 1000 | 730000 | 2000 | 1469000 | 5000 | 1470000 | 1464000 | 13.4833 | 6.697 | 1.6028 | 6.6958 | 1.5945 | 23.93% | 23.81% | 35.0523 | #DIV/0! | 7.5287 | 12.3529 | 1521017.97
2022-05-29 | 2023 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 279763 | 5:53 | 19:29 | 7688.55 | 7688.55 | 8486.35 | 8486.35 | 8087.64 | 8087.64 | 8081.63 | 8081.63 | 12465.545 | 12465.545 | 12435.27 | 12435.27 | 12402.14 | 12402.14 | 12383.4 | 12383.4 | 11522.555 | 11522.555 | 11168.955 | 11168.955 | 9777.85 | 9777.85 | 6968.53 | 6968.53 | 10517.3 | 10517.3 | 12008.895 | 12008.895 | 12155.895 | 12155.895 | 11829.115 | 11829.115 | 10626.345 | 10626.345 | 9708.45 | 9708.45 | 11884.835 | 11884.835 | 9489.57 | 9489.57 | 3337.58 | 3337.58 | 2487.3 | 2487.3 | 184 | 184 | 1647.5 | 1647.5 | 11307.15 | 11307.15 | 12044.3 | 12044.3 | 11993.12 | 11993.12 | 11889.725 | 11889.725 | 11760.5 | 11760.5 | 11930 | 11930 | 11792 | 11792 | 11958.5 | 11958.5 | 11070.095 | 11070.095 | 11294.325 | 11294.325 | 11974.875 | 11974.875 | 5021.45 | 5021.45 | 9545.41 | 9545.41 | 10313.975 | 10313.975 | 9350.34 | 9350.34 | 10666.145 | 10666.145 | 10607.805 | 10607.805 | 10924.65 | 10924.65 | 10012.33 | 10012.33 | 10235.28 | 10235.28 | 1021.1 | 1021.1 | 6694.95 | 6694.95 | 11606.14 | 11606.14 | 9363.335 | 9363.335 | 1926.35 | 1926.35 | 6851.75 | 6851.75 | 9120.2 | 9120.2 | 9442.15 | 9442.15 | 11797.95 | 11797.95 | 10956.15 | 10956.15 | 9856.95 | 9856.95 | 11414.595 | 11414.595 | 10766.45 | 10766.45 | 4283.95 | 4283.95 | 9827.2 | 9827.2 | 9728.45 | 9728.45 | 10426.095 | 10426.095 | 11003.95 | 11003.95 | 8692.9 | 8692.9 | 10972.4 | 10972.4 | 10558.45 | 10558.45 | 3412.2 | 3412.2 | 9646.3 | 9646.3 | 7742.65 | 7742.65 | 11568.5 | 11568.5 | 11968.7 | 11968.7 | 826.25 | 826.25 | 9375.75 | 9375.75 | 11172.45 | 11172.45 | 10287.25 | 10287.25 | 11211.95 | 11211.95 | 9380.25 | 9380.25 | 12291.895 | 12291.895 | 8928.57 | 8928.57 | 8380.885 | 8380.885 | 8585.94 | 8585.94 | 36.0438 | 35.7036 | 0 | 35.5709 | 34.9851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1435 | 8.3866 | 0 | 8.2083 | 6.5742 | 0 | 12.1 | 11.6017 | 0 | 11.585 | 9.0667 | 0 | 7.3263 | 7.3871 | 0 | 6.9278 | 7.3433 | 0 | 1.5178 | 1.7644 | 0 | 1.7928 | 1.5872 | 0 | 6.9124 | 7.3162 | 0 | 7.4328 | 8.1895 | 0 | 1.6104 | 1.7264 | 0 | 1.7416 | 1.7299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28342 | 65 | 22451 | 54 | 50523 | 193 | 7.3263 | 7.3871 | 0 | 6.9278 | 7.3433 | 0 | 6.9124 | 7.3162 | 0 | 7.4328 | 8.1895 | 0 | 779000 | 1000 | 733000 | 0 | 1506000 | 1000 | 1511000 | 1505000 | 13.6 | 7.2461 | 1.6656 | 7.4627 | 1.7021 | 22.99% | 22.81% | 35.5759 | #DIV/0! | 7.8281 | 11.0883 | 1508256.36
2022-05-30 | 2023 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 285337.96 | 5:58 | 19:28 | 10727.92 | 10727.92 | 12184.86 | 12184.86 | 11479.42 | 11479.42 | 11413.67 | 11413.67 | 11135.385 | 11135.385 | 12651.17 | 12651.17 | 12616.47 | 12616.47 | 12617.41 | 12617.41 | 11709.955 | 11709.955 | 11283.8 | 11283.8 | 10020.51 | 10020.51 | 7100.87 | 7100.87 | 10731.575 | 10731.575 | 12265.2 | 12265.2 | 12338.09 | 12338.09 | 12010.095 | 12010.095 | 10825.575 | 10825.575 | 9901.935 | 9901.935 | 12103.685 | 12103.685 | 9659.225 | 9659.225 | 4509.72 | 4509.72 | 2559.4 | 2559.4 | 185.5 | 185.5 | 1679.65 | 1679.65 | 11526.905 | 11526.905 | 12293.69 | 12293.69 | 12225.305 | 12225.305 | 12161.745 | 12161.745 | 12279.25 | 12279.25 | 12507.05 | 12507.05 | 12163.05 | 12163.05 | 12131.25 | 12131.25 | 9692.05 | 9692.05 | 9965.2 | 9965.2 | 10450.05 | 10450.05 | 4400.05 | 4400.05 | 3235.445 | 3235.445 | 3580.78 | 3580.78 | 3161.045 | 3161.045 | 3605.24 | 3605.24 | 10802.06 | 10802.06 | 10980.09 | 10980.09 | 10158.81 | 10158.81 | 10299.225 | 10299.225 | 1039.4 | 1039.4 | 6812.88 | 6812.88 | 11820.08 | 11820.08 | 9489.8 | 9489.8 | 2090.65 | 2090.65 | 7397.95 | 7397.95 | 9884.35 | 9884.35 | 10230.5 | 10230.5 | 11578.95 | 11578.95 | 11742.35 | 11742.35 | 10547.7 | 10547.7 | 12266.25 | 12266.25 | 11644.2 | 11644.2 | 4432.05 | 4432.05 | 11830.3 | 11830.3 | 10742.7 | 10742.7 | 11229.1 | 11229.1 | 11847.2 | 11847.2 | 9403.3 | 9403.3 | 11817.8 | 11817.8 | 11431 | 11431 | 3693.9 | 3693.9 | 10472.05 | 10472.05 | 8368.35 | 8368.35 | 12830.55 | 12830.55 | 12676 | 12676 | 12367.95 | 12367.95 | 10531.1 | 10531.1 | 12249 | 12249 | 11090.55 | 11090.55 | 12196.25 | 12196.25 | 10303.9 | 10303.9 | 12680.6 | 12680.6 | 9070.265 | 9070.265 | 8794.94 | 8794.94 | 10293.625 | 10293.625 | 35.2798 | 35.8743 | 34.9851 | 34.859 | 34.9851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4285 | 6.5788 | 0 | 7.675 | 6.5742 | 6.5742 | 12.8083 | 10.1183 | 0 | 12.9517 | 9.0667 | 0 | 7.42 | 7.6064 | 7.3433 | 0 | 7.59 | 0 | 1.71 | 1.778 | 1.68 | 0 | 1.73 | 0 | 7.48 | 7.5206 | 7.61 | 0 | 7.63 | 0 | 1.76 | 1.7473 | 1.79 | 0 | 1.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29096 | 66 | 23263 | 55 | 52085 | 195 | 7.42 | 7.6064 | 7.3433 | 0 | 7.59 | 0 | 7.48 | 7.5206 | 7.61 | 0 | 7.63 | 0 | 754000 | 1000 | 812000 | 1000 | 1562000 | 2000 | 1564000 | 1560000 | 13.5 | 7.4899 | 1.7245 | 7.5602 | 1.7768 | 23.02% | 23.5% | 35.1967 | #DIV/0! | 6.7661 | 11.2362 | 1556453.84
2022-05-31 | 2023 | 2022 | Year_1 | Year_1 | 2022-06-01 | 31 | 291369.96 | 5:56 | 19:27 | 10703.785 | 10703.785 | 12129.74 | 12129.74 | 11369.765 | 11369.765 | 11338.535 | 11338.535 | 11042.93 | 11042.93 | 12613.265 | 12613.265 | 12583.09 | 12583.09 | 12658.185 | 12658.185 | 11553.4 | 11553.4 | 11185.865 | 11185.865 | 9924.07 | 9924.07 | 8657.24 | 8657.24 | 10560.81 | 10560.81 | 12120.665 | 12120.665 | 12274.3 | 12274.3 | 11877.355 | 11877.355 | 10681.76 | 10681.76 | 10272.98 | 10272.98 | 11956.01 | 11956.01 | 9473.91 | 9473.91 | 7799.12 | 7799.12 | 3939.525 | 3939.525 | 182.8 | 182.8 | 1648.4 | 1648.4 | 11443.065 | 11443.065 | 12147.355 | 12147.355 | 12060.865 | 12060.865 | 12042.145 | 12042.145 | 12196.55 | 12196.55 | 12318.7 | 12318.7 | 11985.3 | 11985.3 | 8227.45 | 8227.45 | 10488.75 | 10488.75 | 10765.9 | 10765.9 | 11366 | 11366 | 4777.5 | 4777.5 | 8737.55 | 8737.55 | 7705.85 | 7705.85 | 8469.2 | 8469.2 | 7876.6 | 7876.6 | 10629.75 | 10629.75 | 10810.475 | 10810.475 | 10033.975 | 10033.975 | 10225.775 | 10225.775 | 1021.65 | 1021.65 | 6699.665 | 6699.665 | 11630.55 | 11630.55 | 9370.32 | 9370.32 | 2095.35 | 2095.35 | 7421.9 | 7421.9 | 9889.05 | 9889.05 | 10232.7 | 10232.7 | 11583.25 | 11583.25 | 11611.75 | 11611.75 | 10554.15 | 10554.15 | 12338.1 | 12338.1 | 11687.05 | 11687.05 | 9569.3 | 9569.3 | 11997.55 | 11997.55 | 10589.25 | 10589.25 | 11237.45 | 11237.45 | 11853.95 | 11853.95 | 9404.3 | 9404.3 | 11750.05 | 11750.05 | 11450.9 | 11450.9 | 3698.9 | 3698.9 | 10374.15 | 10374.15 | 8375.15 | 8375.15 | 12638.95 | 12638.95 | 13034.95 | 13034.95 | 12197.65 | 12197.65 | 10394.8 | 10394.8 | 12093.6 | 12093.6 | 10939.7 | 10939.7 | 12014.1 | 12014.1 | 10113.45 | 10113.45 | 12742.75 | 12742.75 | 9402.48 | 9402.48 | 8660.1 | 8660.1 | 10407.735 | 10407.735 | 36.39 | 37.06 | 35.21 | 0 | 34.9851 | 35.58 | 0 | 0 | 0 | 0 | 0 | 0 | 6.73 | 6.76 | 0 | 0 | 6.24 | 6.75 | 11.87 | 11.23 | 0 | 11.34 | 9.0667 | 0 | 7.32 | 7.39 | 7.33 | 0 | 7.4 | 0 | 1.68 | 1.71 | 1.67 | 0 | 1.65 | 0 | 7.51 | 7.5 | 7.67 | 0 | 7.54 | 0 | 1.75 | 1.73 | 1.77 | 0 | 1.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29895 | 67 | 24064 | 56 | 53679 | 199 | 7.32 | 7.39 | 7.33 | 0 | 7.4 | 0 | 7.51 | 7.5 | 7.67 | 0 | 7.54 | 0 | 799000 | 1000 | 801000 | 1000 | 1594000 | 4000 | 1598000 | 1590000 | 13.5167 | 7.36 | 1.6775 | 7.555 | 1.7525 | 22.79% | 23.2% | 35.845 | #DIV/0! | 6.62 | 10.8767 | 1607865.92
2022-06-01 | 2023 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 291098.23 | 5:58 | 19:30 | 9366.8 | 12800.62 | 12629.58 | 12533.21 | 12671.67 | 10859.79 | 13006.8 | 10341.3 | 12853.01 | 10003.02 | 12846.6 | 13010.01 | 12850.05 | 12949.93 | 12893.21 | 12988.16 | 11484.42 | 12550.13 | 12106.15 | 11300.38 | 12534.3 | 7330.3 | 5865.5 | 12182.3 | 12606.5 | 9447.3 | 12459.28 | 12668.12 | 12707.16 | 12586.67 | 12175.1 | 12547.55 | 12634.65 | 9625.8 | 12646.84 | 9685.9 | 12622.14 | 12163.74 | 8237.38 | 11658.05 | 11837 | 12758.04 | 3131.8 | 6808.6 | 0 | 233.2 | 3472 | 0 | 12985.68 | 10652.08 | 12749.94 | 12436.28 | 13154.59 | 11870.92 | 13063.68 | 12014.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11831.52 | 11424.02 | 13079.12 | 10596.38 | 12881.88 | 12079.67 | 6597.38 | 4018.1 | 12298.23 | 7794.3 | 8015.7 | 13479.76 | 10617.13 | 9038.2 | 10644.94 | 11617.48 | 10379.56 | 11819.71 | 10454.74 | 12129.19 | 13045.41 | 7803.9 | 12004.96 | 9494 | 0 | 2152.8 | 6170.17 | 7919.71 | 12473.42 | 11864.56 | 11497.17 | 8171.6 | 0 | 4417.7 | 5605.4 | 10026.24 | 9965.3 | 10786.24 | 10056.25 | 11420.75 | 12748.71 | 11331.05 | 11959.2 | 10862.02 | 12600.21 | 9382.9 | 12866.84 | 12722.89 | 11693.17 | 12760.63 | 7735.8 | 12353.23 | 12375.36 | 12519.5 | 13463.64 | 7911.7 | 12797.89 | 10677.98 | 12650.91 | 12106.81 | 11318.3 | 8420.78 | 12475.35 | 12116.28 | 12430.22 | 10557.9 | 0 | 7760.82 | 11007.14 | 10787.29 | 6171.6 | 11417.19 | 13309.02 | 12530.88 | 13579.81 | 12796.65 | 12754.94 | 12583.19 | 13444.04 | 7690.3 | 12148.9 | 13069.85 | 10589.1 | 12286.35 | 11795.7 | 13246.08 | 10079.53 | 11175.74 | 13194.67 | 13437.67 | 13148.55 | 6485 | 8746.67 | 9581.3 | 10661.34 | 12119.18 | 36.6297 | 0 | 36.6351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7451 | 0 | 4.7371 | 0 | 0 | 0 | 9.2183 | 0 | 9.0033 | 0 | 0 | 0 | 7.974 | 0 | 7.4521 | 0 | 0 | 0 | 1.6266 | 0 | 2.125 | 0 | 0 | 0 | 7.507 | 0 | 8.0293 | 0 | 0 | 0 | 1.7275 | 0 | 1.9981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30761 | 68 | 24898 | 57 | 55373 | 202 | 7.974 | 0 | 7.4521 | 0 | 0 | 0 | 7.507 | 0 | 8.0293 | 0 | 0 | 0 | 866000 | 1000 | 834000 | 1000 | 1694000 | 3000 | 1698000 | 1691000 | 13.5333 | 7.7131 | 1.8758 | 7.7682 | 1.8628 | 24.32% | 23.98% | 36.6324 | #DIV/0! | 4.7411 | 9.1108 | 1607707.78
2022-06-02 | 2023 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 291768.71 | 5:58 | 19:30 | 8732.8 | 12182.52 | 12501.97 | 11893.76 | 12236.3 | 10285.3 | 12540.03 | 9610.95 | 12301.14 | 9319.6 | 12298 | 12542.33 | 12313.47 | 12471.32 | 12366.58 | 12486.17 | 10693.1 | 11863.85 | 11302.24 | 10556.41 | 11816.8 | 6626.1 | 5489.8 | 11299.63 | 11887.63 | 8779.04 | 11707.18 | 11996 | 6413.55 | 11093.65 | 11308.99 | 11784.6 | 11831.35 | 8899.8 | 11897.63 | 8992.44 | 11886.4 | 11277.8 | 7594.8 | 10716.16 | 11049.49 | 12060.31 | 2722.2 | 4829.9 | 0 | 467.6 | 4695.5 | 10166.76 | 12667.99 | 10031.3 | 12418.36 | 11844.37 | 12943.25 | 11170.06 | 12961.4 | 11259.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10963.52 | 10623.6 | 12580.13 | 9775.97 | 12249.04 | 11215.53 | 6107.1 | 3762.3 | 11375.5 | 7355.4 | 7418.4 | 13228.44 | 9831.38 | 8374.3 | 9863.7 | 10765.1 | 9628.8 | 10978.9 | 9679.7 | 11187.08 | 12515.46 | 7215.34 | 11130.9 | 8746.2 | 0 | 1984.2 | 5701.4 | 7291.9 | 11585.36 | 10929.34 | 10553.98 | 7489 | 0 | 3976.6 | 5218.2 | 9178.57 | 9013.8 | 9856.25 | 9065.91 | 10419.57 | 11759.3 | 10260.15 | 10977.47 | 11328.13 | 11502.28 | 8550.4 | 11976.89 | 11763.64 | 10712.74 | 11929.02 | 7107.45 | 11337.1 | 11363.14 | 11735.77 | 13057.27 | 7257.5 | 11950.46 | 9757.3 | 11697.86 | 11022.69 | 10277 | 7666.61 | 11471.69 | 11075.2 | 11453.22 | 10235.96 | 0 | 7095.78 | 10062.68 | 9879.59 | 6824.5 | 10513.9 | 12869.93 | 11672.59 | 13307.81 | 12055.11 | 11982.26 | 11734.76 | 13077.61 | 7089.6 | 11280.91 | 12542.28 | 9789.5 | 11412.04 | 10916.1 | 12781.09 | 9337.95 | 10353.09 | 12681.17 | 13281.22 | 12722.99 | 7038.3 | 9129.03 | 8891 | 9900 | 11408.13 | 37.8397 | 37.5167 | 37.8843 | 0 | 37.4697 | 0 | 0 | 55.4925 | 0 | 0 | 0 | 0 | 3.7909 | 3.7875 | 3.6902 | 0 | 3.8516 | 0 | 7.1283 | 7.5883 | 7.205 | 0 | 8.2033 | 0 | 7.4997 | 7.5302 | 7.0148 | 0 | 7.3666 | 0 | 1.5354 | 1.7694 | 1.9941 | 0 | 1.5995 | 0 | 7.0598 | 7.4158 | 7.4945 | 0 | 8.0896 | 0 | 1.6267 | 1.7365 | 1.8751 | 0 | 1.7276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31582 | 69 | 25678 | 58 | 56969 | 205 | 7.4997 | 7.5302 | 7.0148 | 0 | 7.3666 | 0 | 7.0598 | 7.4158 | 7.4945 | 0 | 8.0896 | 0 | 821000 | 1000 | 780000 | 1000 | 1596000 | 3000 | 1599000 | 1593000 | 13.5333 | 7.3528 | 1.7246 | 7.5149 | 1.7415 | 23.45% | 23.17% | 37.6776 | 55.4925 | 3.7801 | 7.5312 | 1514777.81
2022-06-03 | 2023 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 292351.03 | 5:58 | 19:30 | 7997.52 | 12719.65 | 13100.74 | 12484.85 | 12826.39 | 10783.46 | 13078.65 | 10021.45 | 12819.15 | 9710.06 | 12821.63 | 13079.35 | 12810.87 | 12996.34 | 12856.28 | 12954.24 | 11108.19 | 12333.97 | 11745.75 | 10988.14 | 12320.94 | 6954.53 | 5766.38 | 11683.05 | 11503.08 | 8468.17 | 11300.96 | 11509.09 | 6910.5 | 11380.43 | 10926.07 | 11399.35 | 12470.49 | 9362.13 | 12457.72 | 9409.2 | 12433.88 | 11803.66 | 7970.22 | 11308.27 | 11408.08 | 12577.06 | 3129.4 | 6411.77 | 0 | 2246.1 | 4877.6 | 10562.17 | 13245.87 | 10485.9 | 12889.05 | 12349.51 | 13558.42 | 11622.43 | 13639.22 | 11972.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11500.51 | 11055.77 | 13190.03 | 10232.78 | 12834.78 | 11763.63 | 6411.9 | 3938.9 | 11965.83 | 9189.46 | 7765.05 | 13846.45 | 10317.74 | 8801.61 | 10325.59 | 11294.72 | 10072.5 | 11476.98 | 9597.13 | 11255.12 | 13112.05 | 7573.1 | 11584.64 | 9171.8 | 0 | 2044.3 | 5447.26 | 7673.27 | 12164.94 | 11510.63 | 11126.47 | 7887.45 | 0 | 4203.99 | 5545.4 | 9732.44 | 9543.58 | 10373.43 | 9626.87 | 10997.47 | 12299.17 | 10819.05 | 11662.02 | 12051.14 | 12440.57 | 9127.77 | 12824.13 | 12551.76 | 11351.93 | 12721.09 | 8989.62 | 12159.55 | 12121.56 | 12521.25 | 13825.92 | 7697 | 12712.55 | 10391.56 | 12467.25 | 11776.63 | 10992.54 | 8194.6 | 12229.86 | 11797.02 | 12143.35 | 11271.61 | 0 | 7532.52 | 10729.22 | 10689.23 | 8908.42 | 11101.78 | 13563.71 | 12309.7 | 13966.05 | 12687.19 | 12618.01 | 12368.15 | 13744.46 | 7481.1 | 11834.18 | 13160.07 | 10278.66 | 11994.8 | 11482.23 | 13467.8 | 9827.81 | 10885.67 | 13522.53 | 13815.91 | 13258.04 | 8404.53 | 9906.16 | 9266.91 | 10345.99 | 11921.94 | 38.3403 | 38.0052 | 38.5314 | 0 | 37.8588 | 0 | 0 | 54.4274 | 0 | 0 | 0 | 0 | 4.7433 | 4.7996 | 4.6996 | 0 | 4.8913 | 0 | 9.5783 | 9.1533 | 9.6317 | 0 | 9.1583 | 0 | 7.8062 | 7.8714 | 7.2797 | 0 | 7.8064 | 0 | 1.6082 | 1.9034 | 1.9128 | 0 | 1.7515 | 0 | 7.3514 | 7.7288 | 7.8149 | 0 | 8.6401 | 0 | 1.7025 | 1.8663 | 1.7477 | 0 | 1.8891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32439 | 70 | 26505 | 59 | 58649 | 209 | 7.8062 | 7.8714 | 7.2797 | 0 | 7.8064 | 0 | 7.3514 | 7.7288 | 7.8149 | 0 | 8.6401 | 0 | 857000 | 1000 | 827000 | 1000 | 1680000 | 4000 | 1682000 | 1676000 | 13.5333 | 7.6909 | 1.794 | 7.8838 | 1.8014 | 23.33% | 22.85% | 38.1839 | 54.4274 | 4.7835 | 9.3804 | 1593918.76
2022-06-04 | 2023 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 290758.93 | 5:58 | 19:30 | 7785.5 | 12366.7 | 12821.7 | 12343.6 | 12681 | 10663.9 | 12895 | 10272.08 | 12687 | 9613.9 | 12668.1 | 12950.4 | 12644.1 | 12827.3 | 12682.73 | 12700.27 | 11006.7 | 12222.4 | 11749.19 | 11165.5 | 12268.1 | 8291.4 | 12537.07 | 12066.25 | 12237.7 | 8991.5 | 11988 | 12205.1 | 0 | 12208.7 | 11665.96 | 12131.3 | 10908.06 | 8190.2 | 10872.1 | 8206.8 | 10886.8 | 10359.2 | 7009.1 | 9931.3 | 11229.9 | 12357 | 3092 | 6306.8 | 0 | 3357.3 | 1262.1 | 10223.71 | 13021.3 | 10304.7 | 12798.1 | 12095.4 | 13387.2 | 11709.7 | 13411.2 | 11825.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11307.1 | 10904.31 | 12979.4 | 10012.9 | 12636.9 | 11617 | 6312.5 | 3883.7 | 11805.1 | 8861.1 | 7583.4 | 13627.27 | 10174.2 | 8673.3 | 10167.4 | 11132.61 | 9931.3 | 11292.6 | 9804.4 | 11650 | 12199.7 | 7085.6 | 11279.6 | 8998.4 | 0 | 2060.3 | 5073.7 | 7571.7 | 11985.34 | 11330.3 | 11016.3 | 7787.2 | 0 | 4138.5 | 5460.9 | 9592.4 | 9450.2 | 10311.5 | 9515.8 | 10846.2 | 12256.5 | 10687.35 | 11565.9 | 11919.99 | 12305.7 | 8831.6 | 12651.57 | 12390.9 | 11187.2 | 12533.3 | 8525.7 | 11986.63 | 11967 | 12332.42 | 13606.3 | 7595.8 | 12543.43 | 10223.8 | 12135.19 | 11507.6 | 10849 | 8061.9 | 12074.1 | 11633.3 | 12013.77 | 11117.9 | 840.9 | 7540.9 | 10591 | 10561.5 | 8843.9 | 11002.8 | 13386.6 | 12140 | 13815.95 | 12520.39 | 12462 | 12231.1 | 13599.18 | 7406.7 | 11738.6 | 12846.6 | 10180.8 | 11876.3 | 11356.2 | 13297.8 | 9704 | 10764.7 | 13407.9 | 13721.5 | 13160.5 | 9122.93 | 10706.59 | 9222.4 | 10260.4 | 11808.89 | 36.1897 | 36.0598 | 36.4479 | 0 | 35.8899 | 0 | 0 | 50.817 | 0 | 0 | 0 | 0 | 6.4604 | 6.6941 | 6.6953 | 0 | 6.5914 | 0 | 12.0517 | 12.0967 | 12.5767 | 0 | 11.7167 | 0 | 7.5305 | 7.5685 | 7.0662 | 0 | 7.6014 | 0 | 1.6285 | 1.7817 | 1.8932 | 0 | 1.6503 | 0 | 7.0605 | 7.4746 | 7.5252 | 0 | 8.2966 | 0 | 1.7269 | 1.7633 | 1.6594 | 0 | 1.7947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33281 | 71 | 27324 | 60 | 60304 | 213 | 7.5305 | 7.5685 | 7.0662 | 0 | 7.6014 | 0 | 7.0605 | 7.4746 | 7.5252 | 0 | 8.2966 | 0 | 842000 | 1000 | 819000 | 1000 | 1655000 | 4000 | 1659000 | 1651000 | 13.5333 | 7.4416 | 1.7384 | 7.5892 | 1.7361 | 23.36% | 22.88% | 36.1468 | 50.817 | 6.6103 | 12.1104 | 1570766.83
2022-06-05 | 2023 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 292020.72 | 5:57 | 19:32 | 8073.16 | 12845.81 | 13282.15 | 12698.62 | 13134.24 | 11005.24 | 13159.34 | 12501.77 | 12914.51 | 9809.6 | 12915.56 | 13196.06 | 12899.33 | 13081.37 | 12970.44 | 12982.67 | 11318.31 | 12863.23 | 13062.71 | 12644.94 | 12672.26 | 9261.45 | 12944.01 | 12802.86 | 12526.41 | 9197.11 | 12269.66 | 12507.64 | 11464.02 | 12349.7 | 12063.54 | 12502.17 | 12571.76 | 9775.75 | 12499.08 | 11180.5 | 12539.78 | 11926.43 | 8054.77 | 11452.65 | 11508.87 | 12648.43 | 3171.2 | 6459 | 0 | 3418.4 | 3472.2 | 12269.91 | 13429.86 | 10499.32 | 13001.94 | 12295.65 | 13610.96 | 12146.35 | 12986.41 | 6949.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11564.05 | 11045.05 | 13282.65 | 10119.83 | 12832.64 | 11885.13 | 6453.78 | 3973.1 | 12133.94 | 11684.96 | 7717.48 | 13914.53 | 10436.66 | 8879.88 | 10399.47 | 11396.98 | 10155.78 | 11567.19 | 9996.01 | 11899.96 | 13046.15 | 7546.74 | 11185.59 | 9168.77 | 0 | 2105.8 | 5175.9 | 7734.48 | 12280.77 | 11587.77 | 11245.22 | 7954.97 | 0 | 3706.6 | 4934.2 | 8669.74 | 17986.27 | 19626.57 | 8599.48 | 9791.66 | 12452.25 | 10867.64 | 11736.7 | 12149.66 | 12500.34 | 8964.15 | 12851.92 | 12630.77 | 11393.93 | 12550.76 | 8516.83 | 12185.42 | 12162.17 | 12320.79 | 13689.12 | 7706.65 | 12728.58 | 10264.11 | 12313.93 | 11602.87 | 11011.3 | 8003.29 | 12248.97 | 11799.94 | 12153.45 | 11255.44 | 4820.9 | 9092.37 | 10700.58 | 10677.06 | 8924.18 | 11107.34 | 13517.25 | 12287.24 | 13911.5 | 12692.85 | 12612.35 | 12364.47 | 13703.36 | 7483.23 | 11705.12 | 13006.05 | 10320.27 | 12004.96 | 11520.97 | 13443.88 | 10117.47 | 11090.05 | 13539.85 | 13829.55 | 13310.97 | 9237.28 | 10833.34 | 9230.4 | 10385.61 | 11958.12 | 35.7411 | 35.5832 | 35.9984 | 0 | 35.3244 | 0 | 0 | 51.5734 | 0 | 0 | 0 | 0 | 5.7488 | 5.7406 | 5.866 | 0 | 5.6004 | 0 | 8.8933 | 9.1867 | 9.8083 | 0 | 9.215 | 0 | 7.6813 | 7.7258 | 7.1983 | 0 | 7.7809 | 0 | 1.568 | 1.821 | 1.931 | 0 | 1.6734 | 0 | 7.2015 | 7.6086 | 7.6983 | 0 | 8.5757 | 0 | 1.6538 | 1.794 | 1.6897 | 0 | 1.819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34173 | 73 | 28153 | 62 | 62019 | 216 | 7.6813 | 7.7258 | 7.1983 | 0 | 7.7809 | 0 | 7.2015 | 7.6086 | 7.6983 | 0 | 8.5757 | 0 | 892000 | 2000 | 829000 | 2000 | 1715000 | 3000 | 1717000 | 1712000 | 13.5833 | 7.5966 | 1.7483 | 7.771 | 1.7391 | 23.01% | 22.38% | 35.6618 | 51.5734 | 5.7389 | 9.2758 | 1648963.42
2022-06-06 | 2023 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 294718 | 5:50 | 19:33 | 8030.38 | 12779.13 | 13234.16 | 12619.06 | 13059.36 | 10917.81 | 13106.77 | 12364.99 | 12847.56 | 9760.32 | 12855.3 | 13134.37 | 12806.55 | 13031.55 | 12856.77 | 12884.83 | 11206.17 | 12855.26 | 13036.09 | 12991.84 | 13009.66 | 12577.05 | 12800.76 | 12700.65 | 12461.55 | 9157.77 | 12420.55 | 12639.58 | 12514.1 | 12624.57 | 11970.87 | 12418.14 | 12480.9 | 9702.06 | 12475.29 | 11157.53 | 12479.2 | 11865.71 | 8005.44 | 11385.75 | 11512.44 | 12647.9 | 3172.2 | 6464.57 | 0 | 4167.83 | 4821.95 | 13833.18 | 13480.47 | 10532.46 | 13003.5 | 12324.86 | 13669.15 | 12129.81 | 13718.1 | 11987.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11504 | 11261.64 | 13272.03 | 10043.87 | 12757.05 | 11818.29 | 6407.42 | 3953.5 | 12049.08 | 11742.43 | 8472.66 | 13892.52 | 10364.92 | 9441.57 | 10343.17 | 11328.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2092.6 | 5150.15 | 7706.02 | 12220.16 | 11505.94 | 11171.64 | 7945.43 | 0 | 4203.8 | 5537.29 | 9745.06 | 9482.57 | 10455.88 | 9650.41 | 10981.38 | 12387.3 | 10836.88 | 11623.01 | 12177.69 | 12476.45 | 8972.29 | 12844.29 | 12667.36 | 11391.59 | 12582.7 | 8508.36 | 12183.55 | 12144.87 | 12332.75 | 13716.39 | 7733.84 | 12736.78 | 10394.46 | 12293.85 | 11601.45 | 11035.46 | 8022.23 | 12267.09 | 11846.19 | 12172.47 | 11268.16 | 8697.45 | 9246.36 | 10734.42 | 10700.15 | 8930.74 | 11114.79 | 13554.72 | 12319.5 | 13968.35 | 12708 | 12635.42 | 12364.56 | 13757.33 | 7483.38 | 11700.76 | 12981.55 | 11871.62 | 13235.55 | 11351.55 | 13313.1 | 10712.55 | 11290.99 | 13571.81 | 13927.66 | 13172.58 | 9243.44 | 10851.52 | 9056.51 | 10403.34 | 11898.92 | 35.7411 | 35.5832 | 35.9984 | 0 | 35.3244 | 0 | 0 | 51.5734 | 0 | 0 | 0 | 0 | 5.7488 | 5.7406 | 5.866 | 0 | 5.6004 | 0 | 8.8933 | 9.1867 | 9.8083 | 0 | 9.215 | 0 | 7.68 | 7.95 | 7.22 | 0 | 7.92 | 0 | 1.31 | 1.83 | 2.05 | 0 | 1.68 | 0 | 7.2 | 7.8 | 7.75 | 0 | 8.68 | 0 | 1.41 | 1.79 | 1.78 | 0 | 1.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35078 | 74 | 28996 | 63 | 63762 | 220 | 7.68 | 7.95 | 7.22 | 0 | 7.92 | 0 | 7.2 | 7.8 | 7.75 | 0 | 8.68 | 0 | 905000 | 1000 | 843000 | 1000 | 1743000 | 4000 | 1746000 | 1739000 | 13.7167 | 7.6925 | 1.7175 | 7.8575 | 1.705 | 22.33% | 21.7% | 35.6618 | 51.5734 | 5.7389 | 9.2758 | 1572207.66
2022-06-07 | 2023 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 295600 | 5:49 | 19:31 | 7985.37 | 12479.47 | 12725.96 | 12344.14 | 12614 | 10971.55 | 12656.86 | 12179.22 | 12454.19 | 9453.6 | 12432.12 | 12685.64 | 12436.67 | 12539.13 | 12516.8 | 12499.45 | 10871.88 | 12505.38 | 12661.75 | 12587.76 | 12571.77 | 12191.6 | 12505.48 | 12430.76 | 12143.24 | 9019.85 | 12511.44 | 12694.99 | 12652.99 | 12539.17 | 12170.37 | 12440.21 | 12130.41 | 9389.7 | 12043.55 | 10780.3 | 12161.09 | 11560.87 | 7825.27 | 11102.37 | 11038.5 | 12009.51 | 3033.2 | 6193.6 | 0 | 4074.2 | 4636.3 | 13167.14 | 11584.98 | 9121.85 | 11200.37 | 10690.62 | 11767.17 | 10559.78 | 11780.6 | 10501.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11181.49 | 11023.7 | 12806.62 | 9736.24 | 12380.93 | 11430.4 | 6196.97 | 3824.8 | 11645.31 | 11400.4 | 8373.24 | 13259.97 | 10030.76 | 9781.82 | 10033.83 | 10933.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019.2 | 4996 | 7444.9 | 11807.22 | 11171.26 | 10903.2 | 7717.2 | 0 | 4043 | 5329.9 | 9388.01 | 9058.6 | 10102.01 | 9317.62 | 10624.27 | 11898.76 | 10474.6 | 11222.51 | 11728.9 | 12072.36 | 8659.4 | 12388.41 | 12162.89 | 10938.55 | 12075.25 | 8195.8 | 11641.69 | 11712.32 | 11668.54 | 13116.61 | 7409.5 | 12258.68 | 10020.7 | 11884.31 | 11210.75 | 10666.81 | 7738.7 | 11817.73 | 11394.69 | 11732.73 | 10868.45 | 11277.16 | 9650.2 | 10370.82 | 10326.89 | 8638.1 | 10722.76 | 12953.77 | 11840.21 | 13296.91 | 12215.19 | 12130.18 | 11889.29 | 13101.44 | 7196.46 | 11298.99 | 12609.73 | 11957.4 | 13198.54 | 10301.64 | 11547.47 | 11759.18 | 11262.28 | 12960.91 | 13248.79 | 12519.99 | 8993.3 | 10899.36 | 8748.41 | 9997.66 | 11709.71 | 36.85 | 36.41 | 36.82 | 0 | 36.23 | 0 | 0 | 44.73 | 0 | 0 | 46.72 | 0 | 9.3 | 9.23 | 9.17 | 0 | 8.96 | 8.99 | 13.57 | 14.1 | 13.17 | 0 | 13.66 | 13.54 | 7.39 | 7.42 | 6.83 | 0 | 7.44 | 6.26 | 1.41 | 1.63 | 2.05 | 0 | 1.53 | 1.3 | 6.87 | 7.3 | 7.24 | 0 | 7.98 | 7.12 | 1.5 | 1.61 | 1.79 | 0 | 1.67 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35948 | 75 | 29811 | 64 | 65441 | 223 | 7.39 | 7.42 | 6.83 | 0 | 7.44 | 6.26 | 6.87 | 7.3 | 7.24 | 0 | 7.98 | 7.12 | 870000 | 1000 | 815000 | 1000 | 1679000 | 3000 | 1683000 | 1676000 | 13.7 | 7.068 | 1.584 | 7.302 | 1.594 | 22.41% | 21.83% | 36.5775 | 45.725 | 9.13 | 13.608 | 1517370.53
2022-06-08 | 2023 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 297847.255 | 5:49 | 19:33 | 8379.9 | 12690.95 | 12924.46 | 12466.26 | 12798.34 | 11278.91 | 12857.23 | 12402.05 | 12594.59 | 9566.25 | 12617.13 | 12890.27 | 12645.96 | 12775.52 | 12728.29 | 12669.92 | 11037.43 | 12691.95 | 12879.55 | 12788.42 | 12774.84 | 12339.09 | 12688.53 | 12610.07 | 12844.06 | 11270.36 | 12707.96 | 12932.62 | 12893.44 | 12736.43 | 12525.67 | 12938.2 | 12292.25 | 9514.61 | 12205.53 | 10917.02 | 12339.78 | 11718.4 | 7941.3 | 11252.41 | 11162.88 | 12153.37 | 3071 | 6269.29 | 0 | 4124.2 | 4680.27 | 13490.65 | 13215.28 | 10302.36 | 12654.4 | 12077.17 | 13482.85 | 11946.26 | 13486.95 | 11891.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11333.76 | 11177.36 | 13083.5 | 9959.15 | 12576.97 | 11594.02 | 6287.01 | 3876.7 | 11805.83 | 11465.51 | 8658.29 | 13668.19 | 10176.93 | 10576.86 | 10191.48 | 11087.73 | 9872.84 | 11237.87 | 9062.5 | 11604.12 | 12603.07 | 7260.35 | 10315.56 | 8154.73 | 0 | 2051 | 5073.57 | 7551.6 | 11989.75 | 11351.57 | 11078.67 | 7838.95 | 0 | 4105.4 | 5411.6 | 9538.17 | 9195.15 | 10266.5 | 9468.94 | 10800.69 | 12066.76 | 10638.67 | 11400.04 | 11887.15 | 12257.33 | 8782.93 | 12580.31 | 12325.48 | 11097.33 | 12265.05 | 8321.41 | 11721.63 | 11890.04 | 11842.85 | 13494.51 | 7509.41 | 12444.29 | 10172.16 | 12062.46 | 11384.25 | 10822.67 | 7834.58 | 11983.03 | 11550.6 | 11885.28 | 11021.76 | 11495.35 | 9941.06 | 10503.37 | 10470.94 | 11112.92 | 11082.66 | 13262.7 | 12003.32 | 13673.03 | 12371.78 | 12298.32 | 12057.37 | 13454.65 | 7301.87 | 12674.47 | 13823.51 | 12623.5 | 13628.96 | 10468 | 11723.2 | 12613.1 | 12110.3 | 13261.77 | 13619.86 | 25208.48 | 18194.19 | 22147.67 | 17489.17 | 20105.91 | 23564.66 | 35.9676 | 35.5757 | 35.9698 | 0 | 35.3983 | 35.8611 | 0 | 44.16 | 0 | 0 | 45.1966 | 0 | 8.3005 | 8.3025 | 8.4057 | 0 | 8.1659 | 8.4074 | 11.9583 | 12.3533 | 12.1367 | 0 | 12.895 | 12.4317 | 7.3908 | 7.4399 | 6.8402 | 0 | 7.4472 | 6.424 | 1.3618 | 1.6025 | 2.0149 | 0 | 1.6033 | 1.3713 | 6.8874 | 7.3176 | 7.3094 | 0 | 8.0843 | 7.2045 | 1.4674 | 1.5683 | 1.7474 | 0 | 1.7493 | 1.5073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36847 | 77 | 30645 | 65 | 67168 | 227 | 7.3908 | 7.4399 | 6.8402 | 0 | 7.4472 | 6.424 | 6.8874 | 7.3176 | 7.3094 | 0 | 8.0843 | 7.2045 | 899000 | 2000 | 834000 | 1000 | 1727000 | 4000 | 1730000 | 1723000 | 13.7333 | 7.1084 | 1.5908 | 7.3606 | 1.6079 | 22.38% | 21.84% | 35.7545 | 44.6783 | 8.3164 | 12.355 | 1706014.6
2022-06-09 | 2023 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 298415 | 5:49 | 19:33 | 9090.6 | 13177.62 | 13443.37 | 13060.96 | 13274.13 | 11946.04 | 13364.51 | 13158.47 | 13075.89 | 11854.77 | 13111.4 | 13350.76 | 13130.42 | 13246.75 | 13189.32 | 13144.95 | 11400.06 | 13163.25 | 13330.88 | 13248.83 | 13239.97 | 12797.5 | 13139.1 | 13059.11 | 13295.06 | 11712.59 | 13175.01 | 13372.1 | 12849.41 | 13193.95 | 13006.33 | 13380.11 | 12753.44 | 9890.7 | 12644.75 | 11321.79 | 12813.92 | 12172.66 | 8247.78 | 11672.94 | 11670.16 | 12631.75 | 3326.58 | 6526.57 | 0 | 4288.79 | 4870.34 | 13883.33 | 13634.01 | 10708.05 | 13148.25 | 12550.82 | 13855.49 | 12419.31 | 13847.45 | 12346.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11778.83 | 11602.29 | 13518.32 | 10351.13 | 13070.97 | 12045.65 | 6153.27 | 4023.8 | 12262.87 | 12227.64 | 8943.37 | 13991 | 10577.53 | 10983.84 | 10594.35 | 11513.63 | 9341.42 | 10777.17 | 8556.29 | 10431.92 | 13058.36 | 7536.16 | 10952.96 | 8828.05 | 0 | 2130.4 | 5260.67 | 7840.18 | 12445.61 | 11787.35 | 11490.17 | 8133.28 | 0 | 4261.5 | 5620.7 | 9904.77 | 9545.27 | 10614.45 | 9826.74 | 11204.74 | 12509.04 | 11037.9 | 11820.36 | 12313.74 | 12697.95 | 9107.89 | 12960.85 | 12773.08 | 11516.92 | 12723.58 | 8631.88 | 12166.62 | 12339 | 12279.88 | 13837.89 | 7785.32 | 12839.66 | 9582.06 | 12496.26 | 11791.94 | 11200.77 | 8114.52 | 12412.22 | 11964.84 | 12335.6 | 11438.09 | 11929.71 | 10505.19 | 10903.8 | 10869.9 | 12075.05 | 11637.7 | 13671.68 | 12468.95 | 14042.72 | 12856.16 | 12787.78 | 12542.87 | 13841.06 | 7589.64 | 13845.36 | 14179.81 | 14023.73 | 14082.6 | 14099.74 | 14097.49 | 13099.13 | 12072.79 | 13681.65 | 13990.46 | 13194.8 | 9971.28 | 11714.16 | 9075.94 | 10536.72 | 12348.42 | 35.164 | 0 | 35.4697 | 0 | 34.8062 | 35.3911 | 0 | 0 | 0 | 0 | 45.8932 | 0 | 8.3518 | 0 | 8.1597 | 0 | 8.0709 | 8.4136 | 12.1817 | 0 | 13.4567 | 0 | 11.1867 | 11.5483 | 7.6743 | 0 | 7.0992 | 0 | 7.7189 | 6.7386 | 1.4066 | 0 | 2.0567 | 0 | 1.6723 | 1.4368 | 7.1638 | 0 | 7.6475 | 0 | 8.4615 | 7.5105 | 1.513 | 0 | 1.7873 | 0 | 1.8191 | 1.5887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37781 | 78 | 31512 | 66 | 68962 | 230 | 7.6743 | 0 | 7.0992 | 0 | 7.7189 | 6.7386 | 7.1638 | 0 | 7.6475 | 0 | 8.4615 | 7.5105 | 934000 | 1000 | 867000 | 1000 | 1794000 | 3000 | 1799000 | 1791000 | 13.7333 | 7.3077 | 1.6431 | 7.6958 | 1.677 | 22.48% | 21.79% | 35.2078 | 45.8932 | 8.249 | 12.0933 | 1708809.66
2022-06-10 | 2023 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 300061 | 5:49 | 19:33 | 8911.1 | 12483.83 | 12754.47 | 12511.87 | 12703.59 | 11613.57 | 12669.71 | 12575.93 | 12423.73 | 12711.53 | 11837.63 | 7346.91 | 12504.11 | 12560.29 | 12555.73 | 12563.9 | 11067.42 | 12502.79 | 12637.36 | 12575.84 | 12559.81 | 12225.44 | 12482.81 | 12426.17 | 12599.16 | 11396.5 | 12516.07 | 12669.14 | 12642.85 | 12404.11 | 12358.98 | 12666.82 | 12184.78 | 9917.67 | 12142.08 | 11120.85 | 12209.02 | 11725.04 | 8254.57 | 11353.38 | 11420.94 | 12127.89 | 7672.72 | 7374.26 | 0 | 4312 | 4887 | 13138.24 | 12922.1 | 10655.42 | 12539.51 | 12062.35 | 13166.79 | 11971.67 | 13118.87 | 11916.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11434.98 | 11305.3 | 12791.73 | 10336.55 | 12401.84 | 11638.73 | 7246.44 | 6567.77 | 11828.43 | 12309.93 | 10982.64 | 13245.62 | 10529.62 | 11243.74 | 10541.74 | 11279.35 | 9857.95 | 11299.5 | 9351.68 | 11355.16 | 12400.52 | 7544.37 | 10786.37 | 8836.32 | 0 | 0 | 5280.4 | 7872.16 | 11969.05 | 11472.42 | 11241.14 | 8168.89 | 0 | 0 | 5652 | 9936.1 | 9568.15 | 10527.56 | 9860.23 | 11056.95 | 11985.93 | 10897.5 | 11496.02 | 11867.99 | 12188.82 | 9152.18 | 12445.67 | 12261.41 | 11531.89 | 12323.87 | 8908.18 | 12929.85 | 11968.32 | 11847.53 | 13103.22 | 7827.93 | 12295.84 | 10450.85 | 12613.44 | 11788.91 | 11026.01 | 8142.27 | 11964.1 | 11456.66 | 11921.01 | 11200.82 | 11619.15 | 10503.55 | 10789.45 | 10759.73 | 11684.62 | 11359.39 | 12533.1 | 11603.84 | 13298.29 | 12266.89 | 12213.41 | 12021.08 | 13084.19 | 7607.99 | 13137.16 | 13460.15 | 13407.68 | 13372.32 | 12952.7 | 12997.66 | 12483.72 | 11211.91 | 12971.13 | 13256.04 | 12535.11 | 10006.38 | 11526.9 | 9100.72 | 10544.81 | 11920.66 | 35.9409 | 0 | 36.0016 | 0 | 35.4473 | 36.0139 | 0 | 0 | 0 | 0 | 46.8664 | 0 | 7.6126 | 0 | 7.6136 | 0 | 7.4527 | 7.8578 | 11.6517 | 0 | 11.54 | 0 | 10.8867 | 11.5917 | 7.8519 | 0 | 7.1176 | 0 | 7.9107 | 6.8355 | 1.425 | 0 | 2.0457 | 0 | 1.6736 | 1.4673 | 7.3465 | 0 | 7.6907 | 0 | 8.6708 | 7.5952 | 1.5326 | 0 | 1.7856 | 0 | 1.827 | 1.6238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38691 | 79 | 32361 | 67 | 70714 | 234 | 7.8519 | 0 | 7.1176 | 0 | 7.9107 | 6.8355 | 7.3465 | 0 | 7.6907 | 0 | 8.6708 | 7.5952 | 910000 | 1000 | 849000 | 1000 | 1752000 | 4000 | 1757000 | 1748000 | 13.7333 | 7.4289 | 1.6529 | 7.8258 | 1.6922 | 22.25% | 21.62% | 35.8509 | 46.8664 | 7.6342 | 11.4175 | 1658200.04
2022-06-11 | 2023 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 301978.16 | 5:49 | 19:33 | 60.49 | 77.37 | 13659.03 | 13377.98 | 13608.06 | 12188.97 | 13502.58 | 13641.15 | 13308.69 | 13574.56 | 13347.68 | 13557.35 | 13354.68 | 13460.41 | 13379.75 | 13406.47 | 11372.92 | 13289.97 | 13499.06 | 13419.11 | 13408.52 | 12982.54 | 13299.33 | 13225.75 | 13460.6 | 11875.05 | 13344.72 | 13541.01 | 13512.79 | 13365.44 | 13185.67 | 13546.16 | 12943.57 | 10032.84 | 12855.01 | 11496.88 | 12998.4 | 12339.73 | 8359.57 | 11842.49 | 11849.66 | 12874.72 | 8005.25 | 10287.56 | 0 | 0 | 4839.6 | 14022.87 | 13796.01 | 10849.68 | 13342.19 | 12742.35 | 14041.9 | 12620.15 | 14009.51 | 12526.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11949.43 | 11771.85 | 13693.09 | 10495.99 | 13264.67 | 12208.25 | 11472.3 | 9695.9 | 12449.55 | 13291.29 | 11904.01 | 14174.09 | 10736.14 | 12518.32 | 10834.08 | 11697.38 | 9972.82 | 11661.95 | 9328.85 | 11755.3 | 13146.05 | 7641.63 | 10767.72 | 8618.58 | 0 | 2159.1 | 5325.91 | 7937.44 | 12633.35 | 11968.21 | 11689.09 | 8252.06 | 0.2 | 6801.46 | 5694.7 | 10009.06 | 10385.64 | 10722.35 | 10021.15 | 11380.23 | 12947.39 | 11629.11 | 12038.24 | 12494.06 | 12932.52 | 9274.18 | 13280.41 | 12981.51 | 12444.51 | 13500.67 | 9365.48 | 14638.4 | 13535.99 | 13232.04 | 14243.78 | 10008.53 | 12469.39 | 10612.7 | 13498.11 | 12397.75 | 11404.05 | 8248.79 | 12611.05 | 11675.48 | 12530.11 | 11603.4 | 12161.33 | 10686.48 | 11069.39 | 11030.12 | 12243.45 | 11803.25 | 13856.71 | 12667.28 | 14219.4 | 13061.07 | 12985.09 | 12729.06 | 14028.19 | 7696.88 | 14010.76 | 14353.58 | 14188.85 | 14253 | 14267.43 | 14235.08 | 13299.31 | 13703.97 | 13839.71 | 14155.98 | 13368.57 | 10098.19 | 12273.01 | 9241.27 | 10679.04 | 12507.17 | 36.387 | 36.1949 | 36.4275 | 0 | 35.9077 | 0 | 0 | 45.5307 | 0 | 0 | 0 | 0 | 7.5099 | 7.6352 | 7.5572 | 0 | 7.418 | 0 | 12.2267 | 12.0333 | 12.505 | 0 | 10.8317 | 0 | 7.9768 | 8.0785 | 7.1774 | 0 | 7.9408 | 0 | 1.4497 | 1.7529 | 2.0784 | 0 | 1.6782 | 0 | 7.4453 | 7.8732 | 7.7867 | 0 | 8.6998 | 0 | 1.5422 | 1.7088 | 1.8125 | 0 | 1.8847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39666 | 81 | 33258 | 68 | 72580 | 238 | 7.9768 | 8.0785 | 7.1774 | 0 | 7.9408 | 0 | 7.4453 | 7.8732 | 7.7867 | 0 | 8.6998 | 0 | 975000 | 2000 | 897000 | 1000 | 1866000 | 4000 | 1869000 | 1862000 | 13.7333 | 7.7934 | 1.7398 | 7.9512 | 1.7371 | 22.32% | 21.85% | 36.2293 | 45.5307 | 7.5301 | 11.8992 | 1750849.49
2022-06-12 | 2023 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 303217 | 5:47 | 19:36 | 10373.72 | 13246.79 | 13495.49 | 13088.9 | 13452.94 | 11967.8 | 13272.58 | 13496.29 | 13027.32 | 13325.03 | 13056.26 | 13312.66 | 13079.25 | 13198.89 | 13094.8 | 13144.74 | 11164.35 | 13072.75 | 13263.99 | 13174.73 | 13157.8 | 12705.58 | 13041.77 | 12961.4 | 13223.28 | 11595.13 | 13082.41 | 13305.9 | 13284.52 | 13098.49 | 12891.25 | 13314.84 | 12622.45 | 9811.83 | 12594.15 | 11248.31 | 12696.75 | 12049.42 | 8108.12 | 11230.94 | 11759.42 | 12659.42 | 13829.22 | 11939.39 | 62.25 | 5274.81 | 4725.2 | 13849.02 | 13592.1 | 10619.42 | 13059.33 | 12449.87 | 13831.51 | 12260.78 | 13810.66 | 12216.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11808.71 | 11469.19 | 13643.4 | 10309.91 | 12960.51 | 11906.01 | 12177.27 | 9843.82 | 12134.71 | 13121.15 | 11811.85 | 13956.08 | 10478.61 | 13006.4 | 11305.26 | 11672.19 | 9726.27 | 11349.05 | 8738.65 | 11347.23 | 12727.77 | 7467.24 | 11120.07 | 8544.43 | 0 | 0 | 7273.07 | 7677.49 | 12289.35 | 11649.72 | 0 | 0 | 3304.01 | 10766.23 | 5581.1 | 10222.95 | 10877.96 | 10463.74 | 9831.85 | 11105.27 | 13456.08 | 11798.67 | 13148.6 | 12014.07 | 12977.26 | 9473.39 | 12987.33 | 12680.42 | 12418.42 | 13427.45 | 9273.94 | 14446.43 | 13641 | 13410.75 | 14244.91 | 10799.94 | 11827.11 | 10374.93 | 13205.59 | 12102.51 | 11126.69 | 8052.87 | 12324.1 | 11408.58 | 12255.69 | 11351.65 | 11915.78 | 10462.79 | 10811.83 | 10781.03 | 11944.77 | 11516.45 | 13590.35 | 12338.76 | 14000.41 | 12735.48 | 12673.09 | 12420.55 | 13792.6 | 7513.37 | 13797.89 | 14171.24 | 13984.85 | 14041.32 | 14044.35 | 13996.99 | 12995.78 | 13472.17 | 13634.64 | 13968.8 | 13086.97 | 9880.74 | 12014.4 | 9016.45 | 10439.34 | 12237.59 | 35.5024 | 35.2062 | 35.4568 | 0 | 34.9966 | 35.5375 | 0 | 46.3623 | 0 | 0 | 49.9741 | 0 | 5.7823 | 6.1213 | 5.7516 | 0 | 5.965 | 6.0927 | 9.6567 | 10.1067 | 9.8667 | 0 | 9.3217 | 9.6167 | 7.8264 | 7.9422 | 7.268 | 0 | 7.847 | 6.8753 | 1.3998 | 1.7181 | 2.0135 | 0 | 1.6509 | 1.4695 | 7.3145 | 7.7445 | 7.8849 | 0 | 8.6542 | 7.5661 | 1.4962 | 1.6764 | 1.7509 | 0 | 1.8463 | 1.6151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40634 | 82 | 34150 | 69 | 74433 | 241 | 7.8264 | 7.9422 | 7.268 | 0 | 7.847 | 6.8753 | 7.3145 | 7.7445 | 7.8849 | 0 | 8.6542 | 7.5661 | 968000 | 1000 | 892000 | 1000 | 1853000 | 3000 | 1858000 | 1850000 | 13.8167 | 7.5518 | 1.6504 | 7.8328 | 1.677 | 21.85% | 21.41% | 35.3399 | 48.1682 | 5.9425 | 9.7137 | 1749449.98
2022-06-13 | 2023 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 305624 | 5:47 | 19:02 | 9299 | 11801.1 | 11914.2 | 11565.8 | 11840.4 | 10591.2 | 11700.9 | 11888.7 | 11658.2 | 11923.1 | 11580.8 | 11836 | 11584.8 | 11676.2 | 11560.1 | 11611.6 | 9760.4 | 11456.1 | 11634.2 | 11585 | 11583.8 | 11255.4 | 11484.3 | 11398.5 | 11451.9 | 9104.3 | 11539 | 11661.7 | 11586.2 | 11405.1 | 11275.2 | 11611.6 | 11058.3 | 8613.8 | 11068.1 | 9864.8 | 11085.3 | 10560 | 7065.8 | 9714.4 | 12368.1 | 11309.1 | 12141.3 | 10543.9 | 6768.4 | 6259.4 | 4153.6 | 12121.2 | 12022.3 | 9436.9 | 11566.1 | 11027 | 12233.1 | 10848.4 | 12222.6 | 10765.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10543.4 | 10269 | 12304.4 | 9332 | 11595.9 | 10795.6 | 10996.2 | 8954.3 | 11083.3 | 12018.8 | 10943.9 | 12707.6 | 9502.7 | 12030 | 10445.2 | 11368.9 | 8835.6 | 10316.4 | 7694.5 | 10257.8 | 11389.8 | 6709.6 | 10080.4 | 7650.9 | 1752.1 | 12.2 | 6451.1 | 7954.7 | 9878.4 | 9832.9 | 9927.4 | 6977.8 | 8042.7 | 9565.4 | 8240.6 | 9043.2 | 9434 | 9103.6 | 8626.5 | 9776.2 | 11795.9 | 10383.5 | 11985.2 | 10885.5 | 11955.7 | 10154.4 | 11830.1 | 11203.3 | 11038.5 | 11855.6 | 8162.1 | 12799.35 | 12061.1 | 11847.3 | 12700.8 | 9601.5 | 10507 | 9218.1 | 11710 | 10779.6 | 9891.8 | 7148.7 | 10944.9 | 10098.1 | 10825.9 | 10046.1 | 10506.2 | 9191 | 9463.4 | 9464.1 | 10380.5 | 10038.2 | 12002.8 | 10877.3 | 12279.5 | 11180.6 | 11105.1 | 10828.6 | 12006.7 | 6538.9 | 10955.1 | 11230.3 | 11275.4 | 11279.8 | 11191 | 11081.7 | 10113.2 | 10486.2 | 12356.6 | 12591.5 | 11740.9 | 8794.3 | 10657.1 | 7923.4 | 9408.8 | 10915.8 | 35.5789 | 35.3725 | 35.4984 | 0 | 34.9224 | 0 | 0 | 50.3041 | 0 | 0 | 0 | 0 | 3.655 | 3.7578 | 3.5032 | 0 | 3.9037 | 0 | 14.6017 | 14.8717 | 12.9417 | 0 | 15.3333 | 0 | 7.01 | 6.9337 | 6.4697 | 0 | 7.0012 | 0 | 1.2616 | 1.4304 | 1.7691 | 0 | 1.2882 | 0 | 6.5771 | 6.8518 | 6.8809 | 0 | 7.9969 | 0 | 1.3849 | 1.3911 | 1.5455 | 0 | 1.4358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41500 | 83 | 34943 | 70 | 76086 | 245 | 7.01 | 6.9337 | 6.4697 | 0 | 7.0012 | 0 | 6.5771 | 6.8518 | 6.8809 | 0 | 7.9969 | 0 | 866000 | 1000 | 793000 | 1000 | 1653000 | 4000 | 1657000 | 1649000 | 13.25 | 6.8537 | 1.4373 | 7.0767 | 1.4393 | 20.97% | 20.34% | 35.3431 | 50.3041 | 3.7049 | 14.4371 | 1580381.15
2022-06-14 | 2023 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 315998 | 6:05 | 19:38 | 7758.66 | 9814.39 | 9737.62 | 9591.33 | 9845.95 | 8880.66 | 9902.13 | 9984.79 | 10600.63 | 10847.17 | 10713.37 | 10855.09 | 10700.79 | 10792.59 | 10761.6 | 10774.19 | 9315.26 | 10787.98 | 10902.08 | 10828.49 | 10826.93 | 10499.27 | 10752.07 | 10684.04 | 10482.08 | 8415.71 | 10754.33 | 10881.31 | 10918.49 | 10835.3 | 10715.51 | 10964.29 | 10442.95 | 8204.54 | 10180.9 | 9233.86 | 10602.87 | 10034.39 | 6762.28 | 9253.38 | 11446.13 | 10575.61 | 11027.62 | 10343.36 | 7193.22 | 8736.09 | 3933 | 11214.49 | 11172.82 | 8867.6 | 10801.83 | 10348.81 | 11365.42 | 10171.99 | 11354.81 | 10144.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9816.53 | 9431.86 | 11276.83 | 8494.46 | 10694.86 | 9854.68 | 10093.25 | 8173.63 | 10053.53 | 10875.97 | 9877.65 | 11465.05 | 8731.23 | 10812.31 | 9730.92 | 10477.86 | 8013.9 | 9330.36 | 7048.12 | 9390.6 | 10411.68 | 6160.04 | 9211.61 | 7018.64 | 3877.68 | 2189.5 | 6125.23 | 8177.68 | 10359.47 | 9850.52 | 9606.49 | 6837.63 | 9196.45 | 8865.34 | 8898.08 | 8585.36 | 9168.64 | 8860.05 | 8309.96 | 9381.04 | 11337.91 | 9928.02 | 11377.87 | 10411.74 | 11183.78 | 9771.68 | 11052.69 | 10349.74 | 10125.56 | 10944.49 | 7753.61 | 11801.94 | 11184.83 | 10951.14 | 11776.19 | 8777.56 | 10447.86 | 8826.4 | 10875.63 | 10021.37 | 9082.75 | 6572.53 | 10141.9 | 9249.51 | 10013.89 | 9393.95 | 9482.18 | 8448.24 | 8850.86 | 8880.61 | 9808.8 | 9439.28 | 11011.83 | 9966.41 | 11248.73 | 10217.13 | 10194.08 | 10054.45 | 11120.87 | 5978.98 | 11111.18 | 11435.37 | 11239.43 | 11311.11 | 11369.34 | 11297.05 | 10481.62 | 10851.56 | 10877.92 | 11119.64 | 10416.1 | 7859.32 | 9483.87 | 7296.07 | 8326.23 | 9767.98 | 31.5291 | 31.5292 | 31.646 | 0 | 31.1137 | 0 | 0 | 43.834 | 0 | 0 | 0 | 0 | 3.7977 | 4.006 | 3.6292 | 0 | 3.7843 | 0 | 7.1517 | 6.8867 | 7.48 | 0 | 6.5617 | 7.6767 | 6.11 | 6.2284 | 5.7099 | 0 | 6.1187 | 0 | 0.86429 | 1.3162 | 1.2105 | 0 | 1.0798 | 0 | 5.847 | 6.1528 | 6.1898 | 0 | 6.2092 | 0 | 0.9569 | 1.2814 | 1.0639 | 0 | 1.2155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42303 | 85 | 35696 | 72 | 77637 | 249 | 6.11 | 6.2284 | 5.7099 | 0 | 6.1187 | 0 | 5.847 | 6.1528 | 6.1898 | 0 | 6.2092 | 0 | 803000 | 2000 | 753000 | 2000 | 1551000 | 4000 | 1552000 | 1547000 | 13.55 | 6.0417 | 1.1177 | 6.0997 | 1.1294 | 18.5% | 18.52% | 31.4545 | 43.834 | 3.8043 | 7.1513 | 1480572.39
2022-06-15 | 2023 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 316249 | 5:49 | 19:40 | 10278.22 | 13251.22 | 13454.56 | 13245.64 | 13369.32 | 11965.24 | 13445.35 | 13528.98 | 13179.45 | 13391.05 | 13308.37 | 13458.54 | 13257.73 | 13366.55 | 13230.98 | 13297.09 | 11248.9 | 13147.75 | 13320.35 | 13261.28 | 13266.38 | 12896.32 | 13204.65 | 13109.9 | 13301.42 | 10277.15 | 13236.85 | 13348.66 | 13276.4 | 13142.33 | 11842.99 | 13221.45 | 12906.98 | 10907.91 | 12508.09 | 11417.13 | 12922 | 12141.68 | 8154.95 | 11894.1 | 13719.05 | 12664.33 | 13620.21 | 12437.35 | 9107.09 | 11327.17 | 4739.6 | 13600.8 | 13740.19 | 10895.82 | 13316.07 | 12774.15 | 13905.22 | 12535.48 | 13919.47 | 12485.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12096.84 | 11570.73 | 13791.6 | 10373.16 | 13156 | 12082.78 | 12360.59 | 9976.23 | 12376.38 | 13486.57 | 12133.67 | 14013.45 | 10704.69 | 13284.19 | 11929.5 | 12862.9 | 9756.65 | 11411.07 | 8580.88 | 11456.89 | 12762.7 | 7510.25 | 11290.64 | 8550.79 | 6769.82 | 2931.83 | 7460.87 | 10154.45 | 12690.32 | 12031.34 | 11702.1 | 12431.68 | 12784.06 | 10780.15 | 10875.29 | 10484.97 | 11119.69 | 10776.39 | 10064.22 | 11816.2 | 13697.72 | 12063.75 | 13713.46 | 12688.02 | 13458.55 | 11828.22 | 13306.72 | 12526.28 | 12353.69 | 13343.93 | 9432.27 | 14257.34 | 13597.26 | 13355.1 | 14205.8 | 10694.31 | 12673.7 | 10712.99 | 13258.18 | 12163.51 | 10996.37 | 8081.75 | 12753.19 | 11423.95 | 12197.52 | 11393.76 | 11529.13 | 10280.27 | 10764.07 | 10754.59 | 12061.34 | 11572.18 | 13432.98 | 12177.97 | 13636.09 | 12538.47 | 12497.88 | 12337.9 | 13573.7 | 7874.13 | 13484.9 | 13765.99 | 13632.82 | 13719.16 | 13768.5 | 13702.92 | 12813.11 | 13193.21 | 13355.21 | 13593.64 | 12945.3 | 9691.55 | 11725.58 | 8908.46 | 10171.39 | 11939.99 | 35.6724 | 35.5131 | 35.5658 | 0 | 35.0728 | 35.4392 | 0 | 47.4576 | 0 | 0 | 46.5776 | 0 | 6.4772 | 6.6186 | 6.4886 | 0 | 6.5003 | 6.5306 | 10.4983 | 9.9833 | 12.5617 | 0 | 9.8067 | 10.5233 | 7.8387 | 7.7946 | 7.0389 | 0 | 7.7668 | 6.6601 | 1.404 | 1.5575 | 1.7923 | 0 | 1.2751 | 1.4149 | 7.2931 | 7.5828 | 7.6997 | 0 | 7.5316 | 7.6098 | 1.5513 | 1.5432 | 1.556 | 0 | 1.4336 | 1.4996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43297 | 86 | 36623 | 73 | 79551 | 253 | 7.8387 | 7.7946 | 7.0389 | 0 | 7.7668 | 6.6601 | 7.2931 | 7.5828 | 7.6997 | 0 | 7.5316 | 7.6098 | 994000 | 1000 | 927000 | 1000 | 1914000 | 4000 | 1919000 | 1910000 | 13.85 | 7.4198 | 1.4888 | 7.5434 | 1.5168 | 20.06% | 20.11% | 35.4527 | 47.0176 | 6.523 | 10.6747 | 1829784.2
2022-06-16 | 2023 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 317197.495 | 5:49 | 19:39 | 10318.2 | 13186.05 | 13251.21 | 12244.47 | 13193.5 | 11654.4 | 13274.82 | 13436.09 | 13042.13 | 13355.26 | 13125.41 | 13345.2 | 13126.72 | 13215.31 | 13215.44 | 13247.32 | 11244.16 | 13161.32 | 13345.49 | 13248.82 | 13270.25 | 12812.22 | 13187.41 | 13082.4 | 13301.5 | 10181.54 | 13159.46 | 13344.25 | 13344.91 | 13208.42 | 11514.75 | 13156.6 | 12989.86 | 10965.17 | 12722.77 | 11633.85 | 13198.95 | 12638.2 | 7878.19 | 12525.4 | 14026.32 | 12864.35 | 14012.55 | 12661.68 | 10275.15 | 12061.89 | 4780.36 | 13869.5 | 13685.4 | 10707.32 | 13168.48 | 12577.06 | 13944.25 | 12380.78 | 13904.22 | 12336.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11962.04 | 11468.84 | 13831.02 | 10413.91 | 13042.57 | 12188.16 | 12265.91 | 10941.3 | 12256.96 | 13513.62 | 12026.41 | 14082.38 | 10597.42 | 12716.98 | 11807.79 | 13022.47 | 9714.65 | 11368.13 | 8553.84 | 11410.6 | 12720.36 | 7492.23 | 11219.77 | 8520.57 | 6895.06 | 7926.86 | 7393.86 | 10043 | 12550.38 | 11916.04 | 11627.91 | 12288.46 | 0 | 0 | 10766.75 | 10367.07 | 11039.89 | 10659.67 | 10118.49 | 11710.53 | 13791.38 | 11979.72 | 13871.22 | 12648.03 | 13673.4 | 11902.57 | 13549.57 | 12634.91 | 12308.84 | 13359.6 | 9337.33 | 14364 | 13651.14 | 13364.8 | 14367.03 | 10646.18 | 12562.85 | 10588.33 | 12687.11 | 11625.68 | 10103.58 | 7984.57 | 13241.4 | 11684.58 | 12176.32 | 11362.53 | 11617.23 | 10264.64 | 10713.11 | 10755.53 | 12083.1 | 11589.57 | 13873.48 | 12258.59 | 13936.67 | 12603.54 | 13305.78 | 12351.63 | 13762.23 | 7888.02 | 13811.56 | 14176.22 | 13970.3 | 14048.97 | 14075.86 | 14001.8 | 12952.42 | 13464.42 | 13543.37 | 13842.81 | 12980.6 | 9734.9 | 10294.47 | 9019.99 | 10302 | 12096.47 | 34.8739 | 34.8526 | 34.7977 | 0 | 0 | 34.942 | 0 | 45.9285 | 0 | 0 | 45.5224 | 0 | 7.8768 | 8.0911 | 8.034 | 0 | 0 | 8.2923 | 13.1 | 12.745 | 13.5 | 0 | 0 | 13.59 | 7.5751 | 7.6382 | 7.0109 | 0 | 0 | 6.6546 | 1.4261 | 1.5935 | 1.871 | 0 | 0 | 1.4295 | 7.0672 | 7.472 | 7.8129 | 0 | 0 | 7.5511 | 1.5746 | 1.574 | 1.6567 | 0 | 0 | 1.5095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44293 | 87 | 37557 | 74 | 81473 | 257 | 7.5751 | 7.6382 | 7.0109 | 0 | 0 | 6.6546 | 7.0672 | 7.472 | 7.8129 | 0 | 0 | 7.5511 | 996000 | 1000 | 934000 | 1000 | 1922000 | 4000 | 1928000 | 1918000 | 13.8333 | 7.2197 | 1.58 | 7.4758 | 1.5787 | 21.88% | 21.12% | 34.8665 | 45.7255 | 8.0735 | 13.2338 | 1813830.72
2022-06-17 | 2023 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 321808.795 | 5:49 | 19:40 | 10329 | 13175.06 | 13278.45 | 11621.09 | 13238.13 | 13243.65 | 13153.59 | 13305.32 | 13034.02 | 13184.3 | 13095.72 | 13302.55 | 13101.77 | 13170.4 | 13128.58 | 13177.32 | 11148.52 | 13037.92 | 13209.92 | 13145 | 13178.1 | 12774.2 | 13082.61 | 12965.07 | 13191.03 | 11364.03 | 13105.67 | 13240.2 | 13196.1 | 12977.1 | 12600.54 | 13297.82 | 12894.16 | 10904.31 | 12853.42 | 11804.53 | 13184.52 | 12828.38 | 7969.7 | 12420.33 | 13797.94 | 12690.77 | 13786.5 | 12490.6 | 10503.15 | 11597.43 | 4736.1 | 13665.47 | 13574.23 | 10692.29 | 13124.38 | 12554.64 | 13823.78 | 12352.45 | 13793.5 | 12307.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11942.43 | 11433.52 | 13710.35 | 10485.21 | 13009.06 | 12244.66 | 12607.82 | 11378.4 | 12198.75 | 13326.05 | 11980.03 | 13921.1 | 10557.93 | 12282.82 | 11925 | 13393.5 | 9677.09 | 11331.31 | 8520.15 | 11364.1 | 12665.05 | 7461.74 | 11180.3 | 8488.55 | 7195.85 | 8102.57 | 7721.14 | 10294.65 | 12508.2 | 11885.6 | 11567.45 | 12253.88 | 12660.44 | 10657.82 | 10722.22 | 10319.85 | 10957 | 10580.8 | 10065.79 | 11644.4 | 13598.02 | 11916.75 | 13715.9 | 12591.18 | 13526.1 | 11841.49 | 13408.74 | 12584.5 | 12263.89 | 13240.3 | 9287.36 | 14130.27 | 13494.78 | 13222.45 | 14181.27 | 10565.55 | 13280.12 | 12055.33 | 13195.15 | 12191.6 | 11726.76 | 8851.12 | 13295.81 | 12200.82 | 12086.93 | 11292.49 | 10544.89 | 8028.53 | 10615.04 | 10542.53 | 12089.92 | 11565.84 | 13856.95 | 12286.58 | 13755.03 | 12676.07 | 13859.13 | 12462.52 | 13831.83 | 10922.84 | 13649.4 | 13985.48 | 13789.3 | 13871.07 | 13877.91 | 13800.8 | 12880.48 | 13340.08 | 13377.88 | 13655.91 | 12883.09 | 9662 | 11721.66 | 8978.35 | 10241.34 | 12034.87 | 34.7339 | 34.7111 | 34.7036 | 0 | 0 | 34.8649 | 0 | 45.9018 | 0 | 0 | 45.6444 | 0 | 7.7607 | 7.9252 | 7.8949 | 0 | 0 | 8.1452 | 12.4833 | 11.9517 | 12.765 | 0 | 0 | 12.7633 | 7.5415 | 7.5708 | 7.6087 | 0 | 0 | 6.6532 | 1.3924 | 1.6103 | 1.7285 | 0 | 0 | 1.3387 | 7.0471 | 7.4468 | 6.9905 | 0 | 0 | 7.5521 | 1.5678 | 1.5892 | 1.9374 | 0 | 0 | 1.4182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45288 | 88 | 38497 | 75 | 83398 | 260 | 7.5415 | 7.5708 | 7.6087 | 0 | 0 | 6.6532 | 7.0471 | 7.4468 | 6.9905 | 0 | 0 | 7.5521 | 995000 | 1000 | 940000 | 1000 | 1925000 | 3000 | 1933000 | 1922000 | 13.85 | 7.3436 | 1.5175 | 7.2591 | 1.6282 | 20.66% | 22.43% | 34.7534 | 45.7731 | 7.9315 | 12.4908 | 1841157.11
2022-06-18 | 2023 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 325108.705 | 5:54 | 19:28 | 6970.16 | 8891.2 | 8941.31 | 7789.25 | 8896.16 | 8929.14 | 8949.91 | 9065.43 | 8768.69 | 8928.57 | 8824.87 | 8957.17 | 8839.23 | 8909.62 | 8896.54 | 8916.28 | 7568.12 | 8838.92 | 8953.43 | 8911.04 | 8931.57 | 8648.14 | 8856.3 | 8760.03 | 8950.19 | 7888.11 | 8853.34 | 8975.76 | 8969.74 | 8794.02 | 8778.51 | 9062.31 | 8732.31 | 7415.21 | 8715.73 | 8026.44 | 8945.11 | 8697.46 | 5418.7 | 8440.77 | 9615.62 | 8749.95 | 9603.77 | 8601.13 | 7070.28 | 7981.38 | 3243.8 | 9465.41 | 9212.32 | 7219.12 | 8838.76 | 8458.57 | 9419.66 | 8336.45 | 9384.67 | 8325.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8252.33 | 7715.66 | 9287.71 | 7099.17 | 8712.21 | 8296.68 | 8980.81 | 8139.08 | 8310.83 | 9082.25 | 8174.98 | 9516.39 | 7572.08 | 8453.17 | 8047.2 | 9291.89 | 6604.2 | 7764.58 | 5838.52 | 7721.96 | 8596.07 | 5073.6 | 7548.35 | 5747.5 | 5079.5 | 5500.43 | 5424.84 | 7152.51 | 8467.83 | 8131.64 | 7884.8 | 8288.77 | 8613.58 | 7226.3 | 7287.24 | 7013.52 | 7689.46 | 7197.67 | 7757.46 | 7962.67 | 9348.56 | 8124.42 | 9390.77 | 8599.43 | 9277.82 | 7965.87 | 9164.44 | 8592.27 | 8358.83 | 9043.67 | 6327 | 9407.29 | 9095.06 | 8896.94 | 9834.83 | 6709.7 | 9373.87 | 8391.94 | 9021.95 | 8584.33 | 8662.15 | 7676.91 | 9288.11 | 8466.9 | 8357.11 | 7795.08 | 8167.03 | 6118.41 | 7562.98 | 7180 | 8317.79 | 7964.46 | 9662.79 | 8452.59 | 9742.49 | 8720.19 | 9756.69 | 8604.13 | 9687.68 | 7763.9 | 9356.47 | 9687.83 | 9512.12 | 9580.86 | 9485.87 | 9547.24 | 8758.89 | 9077.47 | 9080.08 | 9328.15 | 8666.97 | 6515.66 | 7944.48 | 6064.82 | 6961 | 8147.82 | 33.9623 | 33.8448 | 33.8619 | 0 | 0 | 33.9654 | 0 | 42.2027 | 0 | 0 | 41.8259 | 0 | 6.3972 | 6.5377 | 6.3707 | 0 | 0 | 6.7237 | 10.7383 | 10.8417 | 11.805 | 0 | 0 | 11.0933 | 4.865 | 4.936 | 4.9602 | 0 | 0 | 4.3531 | 0.9317 | 1.069 | 1.3158 | 0 | 0 | 0.86814 | 4.7193 | 5.0225 | 4.6435 | 0 | 0 | 4.8567 | 1.0138 | 1.0457 | 1.3884 | 0 | 0 | 0.92398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45967 | 90 | 39143 | 77 | 84721 | 264 | 4.865 | 4.936 | 4.9602 | 0 | 0 | 4.3531 | 4.7193 | 5.0225 | 4.6435 | 0 | 0 | 4.8567 | 679000 | 2000 | 646000 | 2000 | 1323000 | 4000 | 1321000 | 1319000 | 13.5667 | 4.7786 | 1.0462 | 4.8105 | 1.093 | 21.89% | 22.72% | 33.9086 | 42.0143 | 6.5073 | 11.1196 | 1262809.22
2022-06-19 | 2023 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 325265.305 | 6:29 | 19:31 | 8677.42 | 11018.64 | 11301.39 | 9925.6 | 11317.29 | 11175.98 | 19996.45 | 20303 | 10968.92 | 11155.22 | 11095.88 | 11267.37 | 11167.01 | 11255.38 | 7139.9 | 7328.73 | 9688.95 | 11256.05 | 11369.83 | 11286.63 | 11289.3 | 10952.25 | 6693.04 | 11096.1 | 11203.39 | 9872.87 | 11138.89 | 11296.4 | 11315.73 | 11149.3 | 11123.03 | 11426.41 | 10811.22 | 9187.29 | 10965.42 | 10132.54 | 11253.54 | 10961.72 | 6823.07 | 10507.98 | 12057.3 | 11133.09 | 12168.07 | 11018.07 | 7519.42 | 10293.46 | 4144.17 | 11784.26 | 11629.1 | 9175.04 | 11201.74 | 10685.25 | 11847.17 | 10600.63 | 11749.92 | 10386.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10448.3 | 9676.55 | 11667.62 | 8905.58 | 11023.7 | 10362.52 | 11328.66 | 10148.6 | 10687.02 | 11500.85 | 10404.6 | 12078.64 | 10618.28 | 10723.18 | 10328.97 | 11769.38 | 8155.85 | 9621.08 | 7203.59 | 9516.08 | 10602.79 | 6253.86 | 9275.21 | 7079.48 | 6145.62 | 6738.36 | 6503.46 | 8643.83 | 10097.88 | 9710.17 | 9329.01 | 9930.72 | 10932.53 | 8707.41 | 10903.28 | 9117.38 | 10120.45 | 8689.91 | 10582.24 | 9751.12 | 11148.39 | 9701.32 | 11195.45 | 10240.16 | 11087.02 | 9539.49 | 10989.5 | 10254.91 | 9736.19 | 10702.39 | 7470.35 | 11094.25 | 10895.9 | 10666.86 | 11730.94 | 7896.77 | 11275.52 | 10089.92 | 10751.42 | 10188.65 | 10581.8 | 9369.27 | 11166.99 | 10148.45 | 10239.6 | 9570.88 | 9994.25 | 7495.47 | 9383.71 | 8586.73 | 10184.61 | 9744.15 | 11851.35 | 10525.79 | 11784.19 | 10644.03 | 11800.96 | 10596.68 | 11737.71 | 9502.49 | 11526.01 | 11819.15 | 11573.65 | 11685.24 | 11620.41 | 11674.22 | 10745.75 | 11103.5 | 11044.57 | 11348.23 | 10773.44 | 8124.26 | 9890.32 | 7565.47 | 8576.99 | 10048.52 | 34.8945 | 34.5536 | 34.7611 | 0 | 0 | 34.7419 | 0 | 46.5237 | 0 | 0 | 45.9527 | 0 | 5.3582 | 5.532 | 5.5105 | 0 | 0 | 5.4089 | 10.2333 | 10.22 | 10.4467 | 0 | 0 | 10.1767 | 6.4533 | 6.6302 | 6.6534 | 0 | 0 | 5.6277 | 1.185 | 1.4378 | 1.7143 | 0 | 0 | 1.1032 | 6.194 | 6.732 | 6.0983 | 0 | 0 | 6.3488 | 1.2921 | 1.413 | 1.8162 | 0 | 0 | 1.0934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46810 | 90 | 39934 | 77 | 86349 | 264 | 6.4533 | 6.6302 | 6.6534 | 0 | 0 | 5.6277 | 6.194 | 6.732 | 6.0983 | 0 | 0 | 6.3488 | 843000 | 0 | 791000 | 0 | 1628000 | 0 | 1634000 | 1628000 | 13.0333 | 6.3411 | 1.3601 | 6.3433 | 1.4037 | 21.45% | 22.13% | 34.7378 | 46.2382 | 5.4524 | 10.2692 | 1571256.25
2022-06-20 | 2023 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 326152 | 6:15 | 19:39 | 7255.52 | 9328.89 | 9482.24 | 8257.83 | 9446.25 | 9409.34 | 9324.46 | 9430.46 | 9160.23 | 5365.3 | 9194.96 | 9380.34 | 9113.94 | 9258.82 | 7631.46 | 5962.95 | 7710.48 | 9062 | 9190.7 | 9145.64 | 9105.28 | 8878.82 | 5405.13 | 9024.52 | 9159.92 | 8055 | 9158.22 | 9130.21 | 9059.77 | 9016.67 | 8900.04 | 9237.75 | 8801.1 | 7469.47 | 8953.67 | 8166.6 | 9111.64 | 8843.37 | 5473.29 | 8502.81 | 9757.92 | 8855.53 | 9739.29 | 8663.99 | 4030.1 | 7999.83 | 3253.3 | 9474.69 | 9564.38 | 7445.76 | 9226.99 | 8722.62 | 9747.72 | 8644.7 | 9697.84 | 8548.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8591.87 | 8460 | 9732.93 | 8524.05 | 7841.2 | 3901.62 | 5603.81 | 2436.73 | 8659.56 | 9589.98 | 8534.96 | 9860.56 | 8700.7 | 9632.95 | 8357.01 | 7564.98 | 6636.11 | 7795.98 | 5839.25 | 7811.46 | 8703.97 | 5135.22 | 7745.65 | 5862.59 | 5303.33 | 5718.96 | 5561.05 | 7375.64 | 8577.52 | 8245.7 | 7864.42 | 8444.01 | 9611.08 | 7488.67 | 9418.48 | 8012.1 | 8453.94 | 7285.9 | 8861.56 | 8184.82 | 9319.03 | 8128.04 | 9363.51 | 8584.29 | 9268 | 7900.9 | 9170.2 | 8543.79 | 8187.17 | 9011.11 | 6251.64 | 9377.17 | 9183.01 | 8951.53 | 9858.98 | 6553.23 | 9425.35 | 8252.56 | 8875.27 | 8486.29 | 8933.31 | 7777.8 | 9285.43 | 8354.7 | 8470.82 | 7909 | 8198.95 | 6169.48 | 7691.52 | 7097.37 | 8386.2 | 8018.58 | 9639.58 | 8593.34 | 9611.7 | 8745.21 | 9786.17 | 8728.65 | 9760.91 | 7824.94 | 9318.5 | 9617.05 | 9456.38 | 9494.82 | 9390.36 | 9456.92 | 8722.96 | 9081.24 | 9013.27 | 9362.94 | 8778 | 6575.77 | 7987.34 | 6078 | 6953 | 8157.36 | 34.2337 | 33.9765 | 34.0617 | 0 | 0 | 34.1205 | 0 | 42.8765 | 0 | 0 | 42.5522 | 0 | 6.1566 | 6.3326 | 6.2524 | 0 | 0 | 6.2536 | 9.29 | 9.4933 | 10.2017 | 0 | 0 | 9.99 | 5.216 | 5.1418 | 5.0874 | 0 | 0 | 4.4469 | 0.93144 | 1.2163 | 1.2918 | 0 | 0 | 0.93266 | 4.9673 | 5.2215 | 4.6744 | 0 | 0 | 4.9732 | 1.0031 | 1.1801 | 1.3361 | 0 | 0 | 0.94062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47480 | 90 | 40590 | 77 | 87671 | 265 | 5.216 | 5.1418 | 5.0874 | 0 | 0 | 4.4469 | 4.9673 | 5.2215 | 4.6744 | 0 | 0 | 4.9732 | 670000 | 0 | 656000 | 0 | 1322000 | 1000 | 1326000 | 1321000 | 13.4 | 4.973 | 1.0931 | 4.9591 | 1.115 | 21.98% | 22.48% | 34.0981 | 42.7143 | 6.2488 | 9.7438 | 1259987.57
2022-06-21 | 2023 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 327903.435 | 5:59 | 19:39 | 5422.9 | 6962.57 | 7015.08 | 6119.4 | 6930.13 | 6904.66 | 6864.65 | 6953.67 | 6785.27 | 3991.92 | 6783.91 | 6926.36 | 6745.23 | 6841.66 | 6788.21 | 5411.94 | 5685.14 | 6694.11 | 6801.03 | 6784.54 | 6746.28 | 6587.24 | 3993.35 | 6675 | 6800.63 | 6000.9 | 6729.99 | 6649.24 | 6783.81 | 6672.48 | 6593.87 | 6842.88 | 6632 | 5631.48 | 6713.41 | 6134.72 | 6764.18 | 6551.45 | 4063.7 | 6358.59 | 6404.46 | 6585.73 | 7289.24 | 6434.2 | 2218.1 | 6025.84 | 2935.76 | 7004.75 | 7069.43 | 5513.42 | 6802.54 | 6449.81 | 7231.51 | 6409.02 | 7232.19 | 6338.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6589.16 | 6437.5 | 7404.7 | 6537.95 | 6219.45 | 3230 | 4276.1 | 1892.1 | 6604.53 | 7437.44 | 6597.46 | 7526.83 | 6596.48 | 7499.83 | 6317.08 | 5827.04 | 5207.27 | 6118.52 | 4601.76 | 6091.76 | 6805.28 | 4002.3 | 5954.59 | 4529 | 4046 | 4409.24 | 4215.8 | 5616.25 | 6548.26 | 6302.1 | 6009.8 | 6468.47 | 7491.56 | 5599.13 | 6548.51 | 5682.07 | 6451.11 | 5484.26 | 6061.96 | 5492.5 | 7161.57 | 6223.02 | 7181.54 | 6597.23 | 7146.18 | 5985.01 | 7053.14 | 6659.04 | 6130.95 | 6732.69 | 4688.4 | 7056.94 | 6950.97 | 6700.8 | 7509.67 | 4931.4 | 7109.16 | 6201.55 | 6735.95 | 6476.99 | 6851.28 | 5687.09 | 7037.27 | 6270.87 | 6336.13 | 5887.48 | 6272.21 | 4660 | 5782.98 | 5237.08 | 6040.67 | 6015.54 | 7495.66 | 6579.8 | 7478.77 | 6694.52 | 7518.19 | 6580.15 | 7396.4 | 5903.59 | 7157.44 | 7399.21 | 7297.04 | 7318.35 | 7251.55 | 7297.31 | 6664.8 | 6910.54 | 6932.62 | 7287.7 | 6682 | 5044 | 6155.1 | 4641.4 | 4892.1 | 6370.49 | 32.4159 | 32.3385 | 32.3139 | 0 | 0 | 32.4345 | 0 | 38.9402 | 0 | 0 | 39.0249 | 0 | 6.0215 | 6.3909 | 5.8693 | 0 | 0 | 6.4634 | 10.8317 | 10.38 | 11.4117 | 0 | 0 | 10.9967 | 3.7608 | 3.7264 | 3.6034 | 0 | 0 | 3.3504 | 0.70193 | 0.86074 | 0.93884 | 0 | 0 | 0.68604 | 3.6077 | 3.7893 | 3.3742 | 0 | 0 | 3.7119 | 0.75786 | 0.83392 | 0.97081 | 0 | 0 | 0.69527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47982 | 90 | 41088 | 77 | 88668 | 265 | 3.7608 | 3.7264 | 3.6034 | 0 | 0 | 3.3504 | 3.6077 | 3.7893 | 3.3742 | 0 | 0 | 3.7119 | 502000 | 0 | 498000 | 0 | 997000 | 0 | 1000000 | 997000 | 13.6667 | 3.6102 | 0.79689 | 3.6208 | 0.81447 | 22.07% | 22.49% | 32.3757 | 38.9826 | 6.1863 | 10.905 | 950272.42
2022-06-22 | 2023 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 328213.735 | 5:58 | 19:26 | 7670.3 | 9839 | 10280.89 | 8974 | 10284.39 | 10299.14 | 9633.84 | 9954.4 | 9722.7 | 5441.9 | 9824.11 | 9992.7 | 9866.7 | 9916.97 | 9781.56 | 9840.62 | 7732.4 | 9194.2 | 9420.9 | 9454.4 | 9429.2 | 9252.2 | 5781.77 | 9613.67 | 9313.4 | 8302 | 9335 | 9257.83 | 9250.94 | 9001.39 | 8929.3 | 9344.8 | 9032.21 | 7675.3 | 9330.1 | 8486.64 | 9249 | 8957.1 | 6828.87 | 8718 | 9036.6 | 9319.58 | 10352.9 | 8767.1 | 3153.4 | 8457.19 | 4948.8 | 11301.8 | 10085.47 | 7843.6 | 9675.6 | 9071.6 | 10140.4 | 9086.1 | 10077.76 | 8751.7 | 8856.7 | 9813.06 | 9126.2 | 10143.8 | 9914.9 | 8905.9 | 11137.38 | 8127.7 | 8941.9 | 8646 | 10100.7 | 8816.6 | 9287.4 | 4382.1 | 5808.9 | 2588.8 | 8892.9 | 9918.5 | 8945.6 | 10213 | 8940.7 | 10215.3 | 8601.8 | 7893.3 | 7088.35 | 8315.99 | 6251.3 | 8168.7 | 9119.1 | 5348.4 | 7957.7 | 6044 | 5619.7 | 5980.3 | 5744.7 | 7688.6 | 8887.34 | 8509.3 | 8082.6 | 8858.2 | 10593.3 | 8136.1 | 10611.1 | 8771.8 | 9506.6 | 8215.9 | 9516.2 | 8893.9 | 10127.3 | 8734.3 | 10169 | 9398.5 | 10247.18 | 8664.6 | 10103.3 | 9573.2 | 8784.1 | 9730.5 | 6672.8 | 10145 | 10057.9 | 9823.56 | 10985.3 | 7298.5 | 10450.62 | 9131.3 | 9781.1 | 9404.2 | 9995.97 | 8670.8 | 9805.2 | 9145 | 9293.8 | 8819 | 8996.8 | 6618.8 | 8491.3 | 7731 | 9088.9 | 8697.4 | 11118.2 | 9748.2 | 11146.9 | 9938.48 | 11111.9 | 9623.4 | 10807.8 | 8574.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10140.9 | 10735 | 9983.1 | 7495.2 | 9104.9 | 6855.9 | 5170.1 | 9577.1 | 32.9355 | 32.6958 | 32.6368 | 0 | 0 | 32.8691 | 0 | 45.531 | 0 | 0 | 46.1195 | 0 | 2.9776 | 3.0868 | 2.9657 | 0 | 0 | 3.0968 | 7.37 | 8.215 | 7.885 | 0 | 0 | 8.15 | 5.8237 | 5.4852 | 5.3996 | 0 | 0 | 5.3249 | 1.1188 | 1.1697 | 1.2416 | 0 | 0 | 1.0229 | 5.589 | 5.652 | 5.106 | 0 | 0 | 5.9567 | 1.2115 | 1.1438 | 1.397 | 0 | 0 | 1.0279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48689 | 91 | 41806 | 78 | 90088 | 268 | 5.8237 | 5.4852 | 5.3996 | 0 | 0 | 5.3249 | 5.589 | 5.652 | 5.106 | 0 | 0 | 5.9567 | 707000 | 1000 | 718000 | 1000 | 1420000 | 3000 | 1423000 | 1417000 | 13.4667 | 5.5084 | 1.1383 | 5.5759 | 1.1951 | 20.66% | 21.43% | 32.7843 | 45.8253 | 3.0317 | 7.905 | 1348179.17
2022-06-23 | 2023 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 328213.735 | 5:58 | 19:26 | 9441.89 | 11312.17 | 11798.95 | 10329.37 | 11822.94 | 11754.45 | 11225.14 | 11194.95 | 11194.45 | 6172.26 | 11161.95 | 11405.24 | 11280.99 | 11312.31 | 11190.54 | 11259.22 | 9310.4 | 11093.56 | 11323.53 | 11172.26 | 11159.95 | 10739.59 | 6595.23 | 11172.14 | 11180.24 | 9840.67 | 10664.24 | 10972.25 | 11090.2 | 10869.31 | 10777.63 | 11225.05 | 10923.25 | 9337.22 | 11237.25 | 10236.71 | 11134.76 | 10712.86 | 8662.53 | 10390.49 | 10919.63 | 11297.11 | 12463.5 | 9661.92 | 3826.97 | 10182.02 | 5828.91 | 13037.8 | 11444.66 | 8974.08 | 11032.41 | 10558.62 | 11682.2 | 10283.45 | 11856.72 | 10350.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10537.08 | 10252.84 | 11910.96 | 10463.05 | 10940.83 | 5131.73 | 6765.26 | 3002.7 | 10668 | 11873.14 | 10616.72 | 12217.96 | 10646.45 | 12016.71 | 10182.75 | 9255.86 | 8290.65 | 9632.27 | 7329.5 | 9613.72 | 10831.58 | 6336.93 | 9598.95 | 7253.03 | 6719.85 | 7209.12 | 7642.89 | 9788.97 | 10610.47 | 10187 | 9640.23 | 10452.37 | 12319.43 | 9797.46 | 12251.91 | 10354.37 | 12062.57 | 10216.15 | 11551.91 | 10547.67 | 11631.45 | 9924.16 | 11632.91 | 10563.76 | 11747.21 | 9838.03 | 11535.03 | 10784.72 | 10043.09 | 10964.28 | 7498.93 | 11379.78 | 11149.04 | 10810 | 12066.94 | 8030.71 | 11500.23 | 10033.99 | 10873.83 | 10505.06 | 11146.31 | 9613.65 | 10805.03 | 9825.25 | 10329.14 | 10087.89 | 10171.75 | 8799.75 | 9301.61 | 8452.64 | 10273.88 | 9882.04 | 12218.16 | 10765.49 | 12330.78 | 11055.63 | 12328.22 | 10799.54 | 12116.77 | 9762.15 | 11839.85 | 11606.96 | 12143.78 | 12059.77 | 11917.36 | 11996.39 | 11114.02 | 11442.85 | 11518.15 | 12157.68 | 11293.95 | 8459.65 | 10277.8 | 7707.93 | 5386.72 | 10835.28 | 35.1332 | 34.8275 | 34.8888 | 0 | 0 | 34.8045 | 0 | 44.6623 | 0 | 0 | 44.6493 | 0 | 4.4302 | 4.2136 | 4.2311 | 0 | 0 | 4.3211 | 7.4817 | 7.4683 | 7.4483 | 0 | 0 | 7.2133 | 6.76 | 6.8672 | 6.8175 | 0 | 0 | 5.9037 | 1.2725 | 1.4477 | 1.5471 | 0 | 0 | 1.1633 | 6.4915 | 6.9598 | 6.1324 | 0 | 0 | 6.6475 | 1.3849 | 1.4218 | 1.7677 | 0 | 0 | 1.1675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49520 | 92 | 42625 | 79 | 91733 | 272 | 6.76 | 6.8672 | 6.8175 | 0 | 0 | 5.9037 | 6.4915 | 6.9598 | 6.1324 | 0 | 0 | 6.6475 | 831000 | 1000 | 819000 | 1000 | 1645000 | 4000 | 1648000 | 1641000 | 13.4667 | 6.5871 | 1.3577 | 6.5578 | 1.4355 | 20.61% | 21.89% | 34.9135 | 44.6558 | 4.299 | 7.4029 | 1570136.2
2022-06-24 | 2023 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 328213.735 | 5:47 | 19:31 | 9448.05 | 12218 | 12674.79 | 11074.66 | 12790.84 | 12849.14 | 12152.53 | 12201.95 | 12072.77 | 6537.3 | 12247.09 | 12392.2 | 12505.54 | 12459.49 | 12282.57 | 12462.28 | 10214.3 | 12121.79 | 12467.86 | 12316.94 | 12345.51 | 11715.57 | 7270.61 | 12368.92 | 12142.04 | 10734.02 | 11868.11 | 12014.47 | 12063.41 | 11937.51 | 11772.32 | 12227.11 | 12141.03 | 10413.7 | 12092.72 | 11106.81 | 12139.31 | 11754.88 | 9592.43 | 11903.85 | 11765.08 | 12167.04 | 13473.64 | 10392.81 | 4129.09 | 11030.4 | 6344.94 | 13902.99 | 12407.37 | 9720.78 | 11977.08 | 11447.61 | 12738.21 | 11240.1 | 12851.31 | 11227.59 | 21271.42 | 23464.5 | 11226.39 | 12762.08 | 11796.57 | 10558.07 | 14009.04 | 10237.35 | 11328.11 | 11051.6 | 12896.45 | 11312.65 | 11899.25 | 5571.24 | 9629.24 | 3258 | 11286.98 | 12503.81 | 11321.1 | 12983 | 11397.99 | 12910.32 | 10962.7 | 10002.4 | 8979.3 | 10403.58 | 7266.65 | 8735.04 | 11766.06 | 6841.12 | 10344.08 | 7854.52 | 7285.19 | 7776.9 | 8588.6 | 10789.85 | 11507.98 | 11069.12 | 10503.6 | 11369.61 | 13456.17 | 10670.33 | 13338.78 | 11312.03 | 13203.26 | 11290.64 | 12755.17 | 11655.5 | 12811.75 | 10995.89 | 12750.86 | 11655.95 | 12744.68 | 10746.72 | 12547.03 | 11789.19 | 10957.01 | 12065.59 | 8332 | 12598.82 | 12384.74 | 11938.22 | 13387.51 | 8776.7 | 12627.58 | 10910.33 | 11979.98 | 11519.05 | 12203.98 | 10278.35 | 11547.58 | 10937.76 | 11443.42 | 11162.72 | 11580.38 | 9904.47 | 10441.48 | 9671.57 | 11062.02 | 11068.32 | 13222.56 | 11632.95 | 13260.15 | 11902.65 | 13391.78 | 11672.42 | 12985.23 | 10460.75 | 12666.55 | 13134.88 | 13010.02 | 13064.28 | 12900.15 | 12964.96 | 11800.61 | 11427.35 | 12200.07 | 12895.45 | 11925.98 | 8948.29 | 10875.51 | 8193.87 | 3737.95 | 11532.83 | 37.8593 | 37.8237 | 37.7394 | 0 | 37.7148 | 37.8753 | 0 | 51.7591 | 0 | 0 | 51.32 | 0 | 2.2526 | 2.1267 | 2.2763 | 0 | 2.25 | 2.0617 | 6.9783 | 6.4067 | 7.4633 | 0 | 6.475 | 5.9933 | 7.6709 | 7.7868 | 7.6418 | 0 | 0 | 6.5722 | 0 | 1.6559 | 1.7741 | 0 | 1.9477 | 1.3351 | 7.3551 | 7.604 | 7.1361 | 0 | 7.43 | 7.4648 | 1.5643 | 1.6404 | 2.0089 | 0 | 1.59 | 1.333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50421 | 92 | 43516 | 79 | 93518 | 272 | 7.6709 | 7.7868 | 7.6418 | 0 | 0 | 6.5722 | 7.3551 | 7.604 | 7.1361 | 0 | 7.43 | 7.4648 | 901000 | 0 | 891000 | 0 | 1785000 | 0 | 1792000 | 1785000 | 13.7333 | 7.4179 | 1.6782 | 7.398 | 1.6273 | 22.62% | 22% | 37.8025 | 51.5395 | 2.1935 | 6.6633 | 1820942.69
2022-06-25 | 2023 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 328213.735 | 5:55 | 19:40 | 10265.66 | 12431.6 | 12855.35 | 11192.51 | 12404.25 | 12931.4 | 12220.15 | 12262.5 | 12091.55 | 6536.45 | 12312.89 | 12472.6 | 12642.27 | 12526.57 | 11671.4 | 12529.16 | 10152.66 | 12123.65 | 12469.49 | 12326.5 | 12366.6 | 11729.65 | 7345.01 | 12541.5 | 12074.71 | 10688.54 | 11844.26 | 11992.35 | 11968.05 | 11784.05 | 11629.28 | 12120.96 | 12110.53 | 10425.81 | 12030.64 | 11116.91 | 12146.07 | 11779.23 | 9664.57 | 11912.06 | 7601.67 | 8961.15 | 13492.29 | 10419.63 | 4125.39 | 11027.53 | 6229.91 | 11739.77 | 12509.57 | 9804.27 | 12056.35 | 11481.26 | 12756.59 | 11248.8 | 12874.97 | 11223.18 | 11336.4 | 12591.9 | 11362.85 | 12833.73 | 12475.59 | 11030.86 | 14106.37 | 10325.07 | 11211.03 | 11088.91 | 12942.52 | 11353.94 | 11933.55 | 5721.12 | 12176.55 | 4725.74 | 11336 | 12550.15 | 11370.62 | 13076.33 | 11464.21 | 12963.38 | 11014.71 | 10040.14 | 9016.08 | 10439.67 | 5527.06 | 10176.17 | 11836.24 | 6873.19 | 10370.13 | 7851.21 | 7217.88 | 7746.08 | 8514.65 | 10695.38 | 11414.2 | 10979.45 | 10438.39 | 11288.84 | 13298.25 | 10567.05 | 13226.8 | 11216.04 | 13023.7 | 11175.07 | 12624.68 | 11547.79 | 12721.45 | 10897.98 | 12693.82 | 11604.33 | 12723.7 | 10766.5 | 12585.59 | 11830.7 | 10816 | 11897.94 | 8269.56 | 12472.95 | 12319.53 | 11889.95 | 13347.47 | 8790.05 | 12539.42 | 10990.12 | 11977.08 | 11533.64 | 12237.95 | 10392.98 | 11647.12 | 11053.31 | 11446.92 | 11086.62 | 11675.55 | 9991.67 | 11166.03 | 9996.53 | 11102.08 | 11138.05 | 13319.55 | 11679.6 | 13363.74 | 11968.73 | 13390.95 | 11732.86 | 13019.67 | 10520.06 | 12850.17 | 13294.48 | 13164.93 | 13221.74 | 25695.45 | 25467.71 | 11610.85 | 12326.5 | 12405.67 | 13108.5 | 12148.97 | 9134.3 | 11112.21 | 8356.15 | 3795.97 | 11727.48 | 39.8539 | 39.6065 | 39.8073 | 0 | 0 | 39.7674 | 0 | 52.4907 | 0 | 0 | 52.5439 | 0 | 3.1026 | 3.1839 | 3.0801 | 0 | 0 | 3.2136 | 7.39 | 7.28 | 8.3733 | 0 | 0 | 5.8367 | 7.7719 | 7.8246 | 7.6774 | 0 | 0 | 6.7831 | 0 | 1.6531 | 1.7811 | 0 | 0 | 1.3212 | 7.4475 | 7.6502 | 7.148 | 0 | 0 | 7.6454 | 1.5958 | 1.644 | 2.011 | 0 | 0 | 1.3293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51321 | 92 | 44401 | 79 | 95302 | 272 | 7.7719 | 7.8246 | 7.6774 | 0 | 0 | 6.7831 | 7.4475 | 7.6502 | 7.148 | 0 | 0 | 7.6454 | 900000 | 0 | 885000 | 0 | 1784000 | 0 | 1785000 | 1784000 | 13.75 | 7.5143 | 1.5852 | 7.4728 | 1.645 | 21.1% | 22.01% | 39.7588 | 52.5173 | 3.145 | 7.22 | 1825356.22 | 1786400 | 2407956.668 | 74.19%
2022-06-26 | 2023 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 328213.735 | 5:59 | 19:42 | 10635.52 | 12859.41 | 13203.85 | 11538.23 | 13304.91 | 13075.43 | 12575.18 | 12338.76 | 12474.8 | 6783.99 | 12681.75 | 12813.4 | 13091.96 | 12907.6 | 12134.48 | 12346.68 | 10320.5 | 12303.14 | 12626.05 | 12492.25 | 12493.02 | 11890.55 | 7461.06 | 12722.25 | 12271.39 | 10839.99 | 11543.75 | 12084.08 | 12165.92 | 11962.08 | 11796.02 | 12320.17 | 12024.34 | 10404.14 | 12053.6 | 11136.34 | 12149.83 | 11795.51 | 9687.7 | 11866.34 | 7801.35 | 9192.82 | 13685.82 | 10685.47 | 4244.56 | 11326.45 | 6816.42 | 12060.48 | 12840.47 | 10076.8 | 12387.31 | 11795.13 | 13087.28 | 11568.12 | 13253.33 | 11553.75 | 11683.15 | 12927.44 | 11575.61 | 13110.79 | 12814.17 | 11313.49 | 14183.92 | 10688.91 | 11456.79 | 11430.62 | 13243.81 | 11709.65 | 12245.55 | 8955.68 | 12573.25 | 4605.36 | 11811.58 | 13061.05 | 11817.36 | 13458.67 | 11864.5 | 13361.87 | 11375.68 | 10396.75 | 9293.65 | 10775.66 | 5709.87 | 10989.09 | 12209.08 | 7095.23 | 10714.67 | 8093.74 | 7459.09 | 7984.73 | 8811.18 | 11040.17 | 11790.48 | 11343.87 | 10749.34 | 11654.32 | 13610.44 | 11000.41 | 13504.37 | 11675.96 | 13389.57 | 11604.34 | 13098.93 | 11979.25 | 13139.6 | 11306.38 | 13127.75 | 12024.33 | 13167.73 | 11043.05 | 13031.43 | 12231.22 | 11232.05 | 12359.21 | 8590.82 | 12949.96 | 12152.32 | 11521.6 | 13677.26 | 9138.9 | 12775.62 | 11337.25 | 12209.58 | 11937.86 | 12691.55 | 10792.7 | 12089.63 | 11472.55 | 11947.58 | 11610.3 | 12130.55 | 10374.2 | 11549.15 | 10382.88 | 11515.02 | 11592.09 | 13581.3 | 12129.62 | 13597.47 | 12408.44 | 13645.14 | 12203.65 | 13355.67 | 10851.63 | 12929.75 | 13653.24 | 13207.75 | 13203.11 | 13385.9 | 13564.39 | 12479.02 | 12884.15 | 12865.72 | 13491.84 | 12617.02 | 9473.33 | 11533.39 | 8681.96 | 3936.97 | 12130.92 | 41.3767 | 41.0207 | 41.0499 | 0 | 0 | 41.0885 | 0 | 51.5411 | 0 | 0 | 51.5658 | 0 | 4.2688 | 4.2225 | 4.3192 | 0 | 0 | 4.0896 | 7.99 | 8.2017 | 8.7617 | 0 | 0 | 8.3733 | 7.9996 | 8.0316 | 7.8638 | 0 | 0 | 6.95 | 1.1576 | 1.7377 | 1.7736 | 0 | 0 | 1.373 | 7.6151 | 7.8184 | 7.2455 | 0 | 0 | 7.9088 | 1.5972 | 1.7251 | 2.0145 | 0 | 0 | 1.4763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52243 | 92 | 45327 | 79 | 97138 | 272 | 7.9996 | 8.0316 | 7.8638 | 0 | 0 | 6.95 | 7.6151 | 7.8184 | 7.2455 | 0 | 0 | 7.9088 | 922000 | 0 | 926000 | 0 | 1836000 | 0 | 1848000 | 1836000 | 13.7167 | 7.7113 | 1.5105 | 7.6469 | 1.7033 | 19.59% | 22.27% | 41.1339 | 51.5535 | 4.225 | 8.3317 | 1851708.12 | 1837601 | 2412842.5687 | 76.16%
2022-06-27 | 2023 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 328213.735 | 5:52 | 19:53 | 10170.55 | 12287.32 | 12647.25 | 11012.03 | 12706.05 | 12751.75 | 11980 | 11682 | 11951.12 | 6468.03 | 12149 | 12293.35 | 12662.9 | 12361.03 | 12049.4 | 12361.44 | 10002.43 | 11883.07 | 12208.7 | 12073.25 | 12070.3 | 11501.65 | 7224.06 | 12346.45 | 11850 | 10429.77 | 11521.24 | 11668.8 | 11756.25 | 11543.7 | 11383.49 | 11874.66 | 11910.06 | 10286.41 | 11837.35 | 10921.79 | 11912.66 | 11582.21 | 9525.58 | 11726.15 | 7448.42 | 8758.26 | 13245.37 | 10175.21 | 4040.17 | 10743.24 | 6506.3 | 11533.3 | 11919.75 | 9344.46 | 11462.96 | 10933.03 | 12132.77 | 10724.26 | 12269.8 | 10691.04 | 11149.61 | 12373.8 | 11050.94 | 12622.7 | 12264.35 | 10787.57 | 13984.41 | 10200.57 | 10973.66 | 10947.64 | 12747.49 | 11194.95 | 11701.16 | 11189.3 | 12017.63 | 6514.83 | 11274.65 | 12495.52 | 11291.95 | 12929.96 | 11324.31 | 12849.83 | 10858.34 | 9940.18 | 8654.22 | 10036.63 | 5305.6 | 10245.18 | 11334.8 | 6592.27 | 9964.49 | 7523.98 | 6830.91 | 7332.29 | 8052.5 | 10098.2 | 10793.14 | 10372.89 | 9828.24 | 10642.01 | 13224.95 | 10483.85 | 13099.6 | 11094.56 | 12902.4 | 11069.74 | 12539.75 | 11432.83 | 12557.71 | 10783.13 | 12552.9 | 11491.57 | 12565.7 | 10441.03 | 12415.12 | 11666.14 | 10735.53 | 11812.65 | 8173.02 | 12360.35 | 11821.41 | 11775.11 | 13125.45 | 8707.33 | 12186.95 | 10655.97 | 11628.42 | 11351.58 | 12084.16 | 10298.76 | 11472.43 | 10929.26 | 11399.21 | 11084.89 | 11558.49 | 9909.18 | 11047.05 | 9888.82 | 10873.17 | 11101.61 | 13250.98 | 11611.81 | 12919.49 | 11614.18 | 13060.87 | 11681.92 | 12959.59 | 10298.5 | 12654.2 | 13264.95 | 13050.25 | 13097.2 | 12922.22 | 13187.14 | 11839.3 | 12342.35 | 12314.1 | 13008.91 | 12067.84 | 9069.98 | 11032.26 | 8312.64 | 3778.44 | 11630.85 | 39.1255 | 38.8074 | 38.9814 | 0 | 0 | 39.1923 | 0 | 51.5473 | 0 | 0 | 51.7753 | 0 | 4.4757 | 4.6669 | 4.5279 | 0 | 0 | 4.4949 | 8.3533 | 8.305 | 8.3983 | 0 | 0 | 8.8333 | 7.6341 | 7.6571 | 7.5324 | 0 | 0 | 6.677 | 1.2551 | 1.6252 | 1.7314 | 0 | 0 | 1.3096 | 7.3174 | 7.4852 | 6.9793 | 0 | 0 | 7.5668 | 1.5589 | 1.6029 | 1.9598 | 0 | 0 | 1.3996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53135 | 94 | 46204 | 80 | 98900 | 276 | 7.6341 | 7.6571 | 7.5324 | 0 | 0 | 6.677 | 7.3174 | 7.4852 | 6.9793 | 0 | 0 | 7.5668 | 892000 | 2000 | 877000 | 1000 | 1762000 | 4000 | 1766000 | 1758000 | 14.0167 | 7.3752 | 1.4803 | 7.3372 | 1.6303 | 20.07% | 22.22% | 39.0266 | 51.6613 | 4.5413 | 8.4725 | 1776066.04 | 1763760 | 2328674.6366 | 75.74%
2022-06-28 | 2023 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 328213.735 | 5:54 | 19:49 | 9982.87 | 12022.24 | 12468.87 | 10937.7 | 12429.1 | 12417.57 | 11630.9 | 11435.35 | 11708.36 | 6428.51 | 11935.45 | 12055.5 | 12482.28 | 12072.59 | 11850.46 | 12154.8 | 9871.2 | 11698.55 | 12022.89 | 11870.86 | 11902.14 | 11299.2 | 7216.9 | 12231.82 | 11547 | 10129.6 | 11679.39 | 11835.05 | 12018.04 | 11853.35 | 11108.13 | 11593.37 | 11561.1 | 10005.22 | 11549.75 | 10668.6 | 11613.95 | 11287.1 | 9295.37 | 11464.1 | 7330.73 | 8630.56 | 13032.31 | 10043.72 | 3974.16 | 10530.1 | 6400.87 | 11339.2 | 12051.86 | 9411.99 | 11560.58 | 10995.94 | 12229.15 | 10819.75 | 12321.75 | 10729.34 | 10868.4 | 12032.71 | 10788.4 | 12322.51 | 11919.7 | 10485.3 | 13677.92 | 9893.01 | 10627.56 | 10630.6 | 12338.32 | 10871.36 | 11301.93 | 10834.35 | 11601.63 | 10427.55 | 10900.01 | 12102.57 | 10897.1 | 12481.3 | 10915.14 | 12405.98 | 10486.2 | 9605.58 | 8620.33 | 10004.29 | 5269.27 | 10198.29 | 11259.8 | 6559.16 | 9917.02 | 7499.18 | 6887.01 | 7452.35 | 8151.38 | 10209.21 | 10889.06 | 10460.25 | 9946.08 | 10718.8 | 12798.96 | 10114.2 | 12728.9 | 10720.63 | 12523.49 | 10663.11 | 12127.45 | 11032.91 | 12128.05 | 10434.76 | 12134.99 | 11128.45 | 12107.35 | 10136.21 | 12098.23 | 11355.25 | 10365.54 | 11451.85 | 7919.04 | 11978.38 | 11423.5 | 11217.51 | 12645.48 | 8264.15 | 12079.72 | 10533.85 | 11243.15 | 10974.65 | 11718 | 10015.08 | 11159.25 | 10608.45 | 10640.9 | 10610.8 | 11219.8 | 9589.29 | 10578.79 | 9471.48 | 10454.22 | 10654.73 | 12754.92 | 11147.81 | 12380.13 | 11111.8 | 12495.27 | 11181.2 | 12425.94 | 9863.43 | 10622.88 | 12727.17 | 11159.25 | 12596.47 | 12388.13 | 12673.18 | 11367.25 | 11845.15 | 11912.01 | 12614.78 | 11663.49 | 8781.65 | 10643.59 | 7998.88 | 3660.64 | 11257.85 | 37.6665 | 37.2018 | 37.4424 | 0 | 0 | 37.4539 | 0 | 48.6735 | 0 | 0 | 48.4705 | 0 | 6.3367 | 6.4254 | 6.4728 | 0 | 0 | 6.2169 | 9.2417 | 9.18 | 9.76 | 0 | 0 | 9.3217 | 7.229 | 7.2919 | 7.3285 | 0 | 0 | 6.2999 | 1.3474 | 1.5589 | 1.6503 | 0 | 0 | 1.2237 | 6.9222 | 7.1671 | 6.7604 | 0 | 0 | 7.0952 | 1.4666 | 1.5296 | 1.8726 | 0 | 0 | 1.3119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54014 | 95 | 47052 | 82 | 100623 | 279 | 7.229 | 7.2919 | 7.3285 | 0 | 0 | 6.2999 | 6.9222 | 7.1671 | 6.7604 | 0 | 0 | 7.0952 | 879000 | 1000 | 848000 | 2000 | 1723000 | 3000 | 1724000 | 1720000 | 13.9167 | 7.0373 | 1.4451 | 6.9862 | 1.5452 | 20.53% | 22.12% | 37.4411 | 48.572 | 6.363 | 9.3758 | 1735517.27 | 1723401 | 2298977.5207 | 74.96%
2022-06-29 | 2023 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 328339.015 | 6:02 | 19:52 | 10230.41 | 12314.74 | 12679.88 | 11081.68 | 12756.48 | 12784.51 | 12000.95 | 11875.99 | 12014.48 | 9708.71 | 12246.82 | 12368.71 | 12710.77 | 12337.33 | 12060.67 | 12369.91 | 10141.19 | 11932.32 | 12250.49 | 12099.55 | 12101.27 | 11507.21 | 11728.8 | 12442.42 | 11873.12 | 10416.07 | 11943.41 | 12120.97 | 12318.87 | 12163.98 | 11444.58 | 11909.65 | 12132.74 | 10360.58 | 11837.97 | 10966.86 | 11966.84 | 11634.05 | 9582.77 | 11841.03 | 7419.99 | 8732.81 | 13163.53 | 10196.54 | 4039.67 | 10735.62 | 7479.9 | 12525.29 | 12303.11 | 9616.35 | 11805.66 | 11267.46 | 12524.45 | 11056.38 | 12654.28 | 11057.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11088.99 | 11104.15 | 12836.71 | 11294.16 | 11793.27 | 11265.65 | 12119.3 | 10828.62 | 11333.68 | 12567.85 | 11340.42 | 12965.56 | 11367.59 | 12907.63 | 10908.12 | 10002.31 | 8957.7 | 10407.39 | 5476.09 | 10616.24 | 11751.28 | 6844.09 | 10356.9 | 7835.84 | 7545.89 | 7753.01 | 8823.41 | 10674.45 | 11290.15 | 10871 | 10349.06 | 11199.12 | 13248.84 | 10534.44 | 13112.79 | 11179.15 | 10552.3 | 9712.6 | 12544.88 | 11477.28 | 12599.45 | 10838.82 | 12591.39 | 11537.05 | 12549.1 | 10437.76 | 12516.56 | 11772.2 | 10810.05 | 11765.48 | 8200.9 | 12432.6 | 11880.7 | 11620.25 | 12968.56 | 8571.14 | 12533.14 | 10582.28 | 11698.22 | 11460.93 | 12216.31 | 10338.38 | 11094.95 | 11022.6 | 11148.08 | 11141.86 | 11662.54 | 10018.07 | 10990.78 | 9977.3 | 10988.79 | 11202.77 | 13279.97 | 11693.73 | 13058.6 | 11706.94 | 13149.29 | 11755.85 | 13037.51 | 10373.55 | 12806.29 | 13327.24 | 11696.45 | 13205.4 | 13029 | 13241.76 | 11934.82 | 12474.49 | 12433.77 | 13113.16 | 12174.12 | 9253.89 | 11127.65 | 8394.11 | 3832.7 | 11782.58 | 36.2633 | 35.9944 | 36.068 | 0 | 0 | 36.2916 | 0 | 46.1895 | 0 | 0 | 46.3361 | 0 | 8.5843 | 8.5764 | 8.7768 | 0 | 0 | 8.7447 | 12.515 | 12.215 | 13.03 | 0 | 0 | 12.8833 | 7.1951 | 7.2418 | 7.1725 | 0 | 0 | 6.4688 | 1.3694 | 1.5959 | 1.6292 | 0 | 0 | 1.2823 | 6.8935 | 7.167 | 6.6674 | 0 | 0 | 7.2253 | 1.4755 | 1.5592 | 1.8503 | 0 | 0 | 1.3898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54927 | 96 | 47934 | 83 | 102411 | 283 | 7.1951 | 7.2418 | 7.1725 | 0 | 0 | 6.4688 | 6.8935 | 7.167 | 6.6674 | 0 | 0 | 7.2253 | 913000 | 1000 | 882000 | 1000 | 1788000 | 4000 | 1793000 | 1784000 | 13.8333 | 7.0195 | 1.4692 | 6.9883 | 1.5687 | 20.93% | 22.45% | 36.1543 | 46.2628 | 8.6705 | 12.6608 | 1708727.52 | 1789067 | 2213067.1374 | 80.84%
2022-06-30 | 2023 | 2022 | Year_1 | Year_1 | 2022-07-01 | 30 | 329335.745 | 5:59 | 19:41 | 8853.4 | 10600.94 | 10984.07 | 9656.05 | 11096.07 | 11109.63 | 10405.15 | 10325.27 | 10309.87 | 10197.64 | 10531.56 | 10611.43 | 10975.35 | 10625.45 | 10457.55 | 10710.04 | 8822.95 | 10275.25 | 10554.64 | 10402.59 | 10432.14 | 9930.74 | 10652.38 | 10678.55 | 10157.56 | 8869.31 | 10421.56 | 10554.12 | 10743.64 | 10584.94 | 9858.07 | 10217.53 | 10427.54 | 8887.63 | 10136.1 | 9391.83 | 10255.94 | 9985.54 | 8225.07 | 10157.16 | 6400.53 | 7516.14 | 11381.38 | 8781.58 | 3481.67 | 9289.06 | 7551.97 | 12464.65 | 10548.14 | 0 | 10199.62 | 9707.1 | 10883.22 | 9597.05 | 10853.86 | 9520.52 | 9521.73 | 10641.09 | 9480.46 | 10788.26 | 10508.45 | 9209.36 | 12290.67 | 8746.01 | 9490.17 | 9464.29 | 10953.16 | 9588.34 | 10046.46 | 9557.07 | 10310.24 | 9186.01 | 9610.66 | 10660.43 | 9609.08 | 11043.14 | 9673.19 | 10960.67 | 9287.04 | 8490.62 | 7571.34 | 8796.04 | 4621.69 | 8976.95 | 9944.02 | 5796.62 | 8805.34 | 6656.11 | 6594.57 | 6573.51 | 7690.25 | 9127.59 | 9649.77 | 9314.81 | 8889.91 | 9567.26 | 11319.5 | 8954.4 | 11167.5 | 9519 | 0 | 0 | 10705.2 | 9794.4 | 10757.9 | 9251.66 | 10747.62 | 9835.66 | 10710.34 | 8845.23 | 10683.4 | 10032.41 | 9240.83 | 9995.15 | 6992.09 | 10597.18 | 10148.35 | 9907.73 | 10924.56 | 7145.26 | 10687.66 | 8969.49 | 9852.02 | 9710.88 | 10416.12 | 8785.86 | 9442.06 | 9403.94 | 9494.2 | 9483.91 | 9947.99 | 8551.04 | 9347.32 | 8495.03 | 9336.47 | 9513.25 | 11254.2 | 9878.93 | 11062.45 | 9882.23 | 11139.66 | 9942.9 | 11072.05 | 8783.56 | 10862.12 | 11353.53 | 9905.92 | 11205.55 | 11033.33 | 11237.25 | 10091.22 | 10576.81 | 10538.96 | 11113.43 | 10320.27 | 7828.7 | 9410.58 | 7108.49 | 3248.8 | 9978.26 | 34.9642 | 34.7704 | 34.7502 | 0 | 34.5568 | 34.981 | 0 | 43.4725 | 0 | 0 | 47.0207 | 0 | 7.9504 | 8.0075 | 8.1426 | 0 | 7.7296 | 8.2094 | 12.96 | 12.1 | 13.3217 | 0 | 12.6033 | 12.63 | 6.0253 | 6.0557 | 6.0211 | 0 | 6.0109 | 5.3391 | 1.1075 | 1.3747 | 1.3313 | 0 | 1.2458 | 0.9536 | 5.7439 | 6.0038 | 5.5791 | 0 | 5.9184 | 5.9457 | 1.1872 | 1.3435 | 1.519 | 0 | 1.3461 | 1.1099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55709 | 97 | 48688 | 84 | 103941 | 287 | 6.0253 | 6.0557 | 6.0211 | 0 | 6.0109 | 5.3391 | 5.7439 | 6.0038 | 5.5791 | 0 | 5.9184 | 5.9457 | 782000 | 1000 | 754000 | 1000 | 1530000 | 4000 | 1534000 | 1526000 | 13.7 | 5.8904 | 1.2026 | 5.8382 | 1.3011 | 20.42% | 22.29% | 34.8045 | 45.2466 | 8.0079 | 12.723 | 1521482.93 | 1532134 | 1817679.0686 | 84.29%
2022-07-01 | 2023 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 329335.745 | 6:04 | 19:33 | 5919.4 | 7086.5 | 7311.3 | 7218.9 | 7356.5 | 7353.2 | 6902.9 | 6852.7 | 6903 | 6802.6 | 7065.2 | 7109.8 | 7329.9 | 7123.5 | 6958.4 | 7129.9 | 5913.7 | 6867 | 7045.9 | 6906.1 | 7028.2 | 6765.1 | 7084.2 | 7218.3 | 6787.3 | 5933.3 | 6999.3 | 7074.7 | 7208.2 | 7095.8 | 6560.8 | 6813.8 | 6996.7 | 5989.5 | 6803.7 | 6290.6 | 6851 | 6658.7 | 5492.5 | 6813.7 | 4220.8 | 4960.3 | 7540.5 | 5814.1 | 2302.5 | 6176.7 | 5241.3 | 8471.7 | 7361.3 | 5740.9 | 7072.6 | 5567.1 | 7559.5 | 6543.6 | 7484.9 | 6599.7 | 6475.4 | 7221.9 | 6572.7 | 7444.7 | 7218.4 | 6415.1 | 8365.1 | 5867.7 | 6447.6 | 6402.4 | 7394.1 | 6477.3 | 6767.3 | 6436.1 | 6937 | 6204.6 | 6469.6 | 7200.1 | 6482.9 | 7435.5 | 6505.6 | 7408.5 | 6257 | 5727.9 | 5105.5 | 5938.8 | 3115.5 | 6044.4 | 6695 | 3898.2 | 5949.1 | 4484.6 | 4488.1 | 4458 | 5218.9 | 6177.9 | 6512.2 | 6273.1 | 5986.8 | 6449.4 | 7667.5 | 6069.5 | 7537.7 | 6441 | 7446.2 | 6380.1 | 7213.2 | 6601 | 7231.1 | 6223.6 | 7214.9 | 6238.1 | 7192.1 | 5913.4 | 7220.2 | 6776.1 | 6273.2 | 6760.4 | 4536.7 | 7148.8 | 6645.9 | 6686.9 | 7318.3 | 4812.4 | 7180.3 | 6002 | 6593.3 | 6494.5 | 6962.8 | 5886.1 | 6381.6 | 6306.9 | 6381.3 | 6363.8 | 6701.6 | 5752.3 | 6252.7 | 5683.6 | 6234.6 | 6356.7 | 7470.8 | 6541.4 | 7345.3 | 6571.9 | 7406.5 | 6609 | 7360.1 | 5866.7 | 7199 | 7543.6 | 6557 | 7414.9 | 7289.8 | 7432.6 | 6673 | 7002.5 | 7020.5 | 7408.3 | 6887.9 | 5210.8 | 6256.4 | 4714.5 | 2151.6 | 6619.3 | 33.676 | 33.5203 | 33.5452 | 0 | 33.3447 | 33.6581 | 0 | 41.455 | 0 | 0 | 0 | 0 | 4.4983 | 4.6561 | 4.55 | 0 | 4.488 | 4.6959 | 8.3517 | 8.0433 | 7.8217 | 0 | 7.3767 | 8.3283 | 3.8185 | 3.8416 | 3.7981 | 0 | 3.8859 | 3.371 | 0.67673 | 0.83317 | 0.79227 | 0 | 0.76528 | 0.57568 | 3.5945 | 3.8467 | 3.5482 | 0 | 3.823 | 3.7228 | 0.72735 | 0.81827 | 0.92144 | 0 | 0.83497 | 0.66214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56242 | 99 | 49193 | 85 | 104975 | 290 | 3.8185 | 3.8416 | 3.7981 | 0 | 3.8859 | 3.371 | 3.5945 | 3.8467 | 3.5482 | 0 | 3.823 | 3.7228 | 533000 | 2000 | 505000 | 1000 | 1034000 | 3000 | 1035000 | 1031000 | 13.4833 | 3.743 | 0.72863 | 3.7071 | 0.79283 | 19.47% | 21.39% | 33.5489 | 41.455 | 4.5777 | 7.9843 | 1040845.1 | 1034333 | 1246801.876 | 82.96%
2022-07-02 | 2023 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 329648.075 | 6:02 | 19:38 | 4728.5 | 5593.8 | 5342.7 | 4249.1 | 5572.4 | 5620 | 5596.7 | 5568.6 | 5503 | 5597.6 | 5515.96 | 5596.21 | 5595.87 | 5532.4 | 5486 | 5474.5 | 4807.8 | 5491.6 | 5560.6 | 5463 | 5500.9 | 5408.3 | 5489.4 | 5500.8 | 5524.5 | 4759.6 | 5450.6 | 5466 | 5576.1 | 5558.3 | 5430.54 | 5601.7 | 5446.3 | 4598.4 | 5333.8 | 4915.5 | 5564.5 | 5380.3 | 4218 | 4554 | 3317.7 | 3885 | 5921.6 | 4536.8 | 1800.4 | 4858.3 | 4128.9 | 6650.7 | 5808 | 4520.3 | 5593.6 | 5300.5 | 5936.5 | 5239.1 | 5939.22 | 5194.89 | 5160.5 | 5825.82 | 5210.2 | 5929.2 | 5679.2 | 5038.8 | 6728.5 | 4733.9 | 5193.6 | 5128.5 | 5993.47 | 5224.5 | 5496.82 | 5244.1 | 5648.5 | 5022 | 5282.2 | 5781.8 | 5225.4 | 6069.54 | 1879.4 | 2119.4 | 5097.5 | 4669.4 | 4139 | 4800.3 | 2545.8 | 4902.9 | 5439.4 | 3155.1 | 4752.2 | 3610.9 | 3193.2 | 828.2 | 4186.2 | 4980.6 | 4361.89 | 4949.7 | 4963.2 | 5265.4 | 6038.9 | 4882.8 | 6062.97 | 5294.6 | 6116.1 | 5284.6 | 5982.7 | 5470.7 | 6039.25 | 5176.2 | 6030.1 | 5128.4 | 5912.1 | 4864.9 | 5942.6 | 5479.1 | 5038 | 5429.2 | 3734.99 | 5856.6 | 5435.4 | 5381.8 | 5999.5 | 3788.3 | 5773.9 | 4960.5 | 5483.1 | 5400.7 | 5726.5 | 4791.1 | 5300.6 | 4986.6 | 5196.4 | 5232.4 | 5385.1 | 4639.8 | 4999.7 | 4602.5 | 5143.5 | 5257.86 | 6171.88 | 5336.5 | 5941.99 | 5316.6 | 6027.4 | 5426.1 | 5988.2 | 4768.1 | 5842 | 6121.38 | 5295.5 | 6039.4 | 5989.1 | 6110.8 | 5447.8 | 5689.32 | 5663.9 | 5915.6 | 5417.8 | 4120.8 | 4983.4 | 3789.7 | 1683.2 | 5250.2 | 30.4022 | 30.299 | 30.2704 | 0 | 30.067 | 0 | 0 | 36.2986 | 0 | 0 | 0 | 0 | 3.0116 | 3.1715 | 2.9226 | 0 | 3.0432 | 0 | 8.2383 | 8.1583 | 6.22 | 0 | 7.9017 | 0 | 2.836 | 2.843 | 2.8271 | 0 | 2.9487 | 0 | 0.4178 | 0.50165 | 0.46633 | 0 | 0.43846 | 0 | 2.7827 | 2.8289 | 2.7249 | 0 | 2.8754 | 0 | 0.4534 | 0.52629 | 0.49183 | 0 | 0.49315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56663 | 100 | 49599 | 87 | 105800 | 294 | 2.836 | 2.843 | 2.8271 | 0 | 2.9487 | 0 | 2.7827 | 2.8289 | 2.7249 | 0 | 2.8754 | 0 | 421000 | 1000 | 406000 | 2000 | 825000 | 4000 | 824000 | 821000 | 13.6 | 2.8637 | 0.45606 | 2.803 | 0.49117 | 15.93% | 17.52% | 30.2596 | 36.2986 | 3.0372 | 7.6296 | 822848.37 | 824933 | 984050.6522 | 83.83%
2022-07-03 | 2023 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 329648.075 | 6:00 | 19:25 | 6361.1 | 7519.4 | 7471.5 | 6384.8 | 7450.9 | 7540.2 | 7537.3 | 7564.5 | 7382.7 | 7462.7 | 7459.3 | 7521.6 | 7555.2 | 7467.1 | 7437.8 | 7422.7 | 6578.7 | 7441.1 | 7546 | 7435.7 | 7463.1 | 7364.6 | 7399.2 | 7417.8 | 7483.8 | 6521.8 | 7400.5 | 7405.6 | 7559.4 | 7528.5 | 7384.8 | 7612.3 | 7378 | 6297.6 | 7263.1 | 6759.9 | 7565.8 | 7316.3 | 5883.5 | 7087.2 | 4416.7 | 5175.7 | 7797.6 | 6037.1 | 2395.8 | 6483.4 | 5429.3 | 8634.3 | 7825.7 | 6136.4 | 7575.6 | 7198.8 | 7976.5 | 7147.2 | 7977.1 | 7071 | 6913.2 | 7804 | 7092.3 | 7881.2 | 7751.7 | 6943.3 | 8757 | 6396.2 | 6995.1 | 6894.6 | 7932.8 | 6994.5 | 7307.35 | 7027.33 | 7511.5 | 6742.2 | 7143 | 7826 | 7052.7 | 8031 | 7542 | 7542 | 6800.1 | 6258.7 | 5567.7 | 6461.3 | 3460.2 | 6584.7 | 7276.2 | 4238.1 | 6427.6 | 4863.9 | 2929.3 | 2989.7 | 5610.3 | 6672.5 | 7207.6 | 6954.6 | 6653.2 | 7026.2 | 7923.1 | 6447.4 | 7929.9 | 6914.6 | 7993.7 | 6978 | 7820.1 | 7205.1 | 7850.6 | 6803.7 | 7855.9 | 6720.7 | 7756.8 | 6459 | 7724.7 | 7120.8 | 6473.3 | 6886.3 | 4238.2 | 7688.1 | 7129.4 | 7129.2 | 7870.8 | 5011 | 7351.8 | 6499.8 | 7210.5 | 7098.9 | 7496.5 | 6291.6 | 6979.5 | 6577.6 | 6863.1 | 6879 | 7106.2 | 6144.3 | 6702.4 | 6084.8 | 6856.3 | 7006.5 | 8227.9 | 7200.9 | 7938.1 | 7197.6 | 8067.1 | 7300.1 | 7977.2 | 6371.9 | 7950.7 | 8275.9 | 7372.2 | 8164 | 8062.9 | 8188.4 | 7418.9 | 7761.3 | 7645.6 | 8001.9 | 7400.3 | 5657.9 | 6736.5 | 5216.6 | 2300.5 | 7218.1 | 30.971 | 30.7991 | 30.8705 | 0 | 30.5466 | 0 | 0 | 40.1138 | 0 | 0 | 0 | 0 | 3.3146 | 3.7149 | 3.1675 | 0 | 3.52 | 3.3577 | 11.3867 | 11.285 | 10.61 | 0 | 10.5333 | 10.3967 | 4.0204 | 4.0524 | 3.8909 | 0 | 4.0494 | 3.6745 | 0.6777 | 0.7678 | 0.74191 | 0 | 0.66997 | 0.50054 | 3.9598 | 4.0254 | 3.7637 | 0 | 3.9137 | 4.4279 | 0.72095 | 0.79417 | 0.78918 | 0 | 0.73954 | 0.64054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57232 | 102 | 50141 | 88 | 106906 | 298 | 4.0204 | 4.0524 | 3.8909 | 0 | 4.0494 | 3.6745 | 3.9598 | 4.0254 | 3.7637 | 0 | 3.9137 | 4.4279 | 569000 | 2000 | 542000 | 1000 | 1106000 | 4000 | 1108000 | 1102000 | 13.4167 | 3.9375 | 0.67158 | 4.0181 | 0.73688 | 17.06% | 18.34% | 30.7968 | 40.1138 | 3.4149 | 10.8423 | 1114705.88 | 1107200 | 1348603.273 | 82.1%
2022-07-04 | 2023 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 329648.075 | 5:57 | 19:30 | 8437.1 | 9686.4 | 9825 | 9627 | 9780.5 | 9757.36 | 9673.57 | 9641.85 | 9458.9 | 9618.1 | 9419.1 | 9560 | 9467.9 | 9388 | 9296 | 9281 | 8038.54 | 9148.87 | 9279.9 | 9160.3 | 9207.9 | 9064.73 | 9292.1 | 9244.79 | 9160.76 | 7926.26 | 9056.3 | 9057.76 | 9218.47 | 9141.42 | 8987.67 | 9292.27 | 8871.01 | 7546.39 | 8828.74 | 8164.2 | 9177.51 | 8852.98 | 6949.7 | 6763.4 | 5578.3 | 3232.4 | 9730.16 | 6206.42 | 3007.6 | 8024.4 | 6793.4 | 10418.55 | 9715.39 | 7621.1 | 9270.8 | 8831.4 | 9776.3 | 8791.7 | 9736.5 | 8572.59 | 8535.7 | 9645.1 | 8871.63 | 9840.97 | 9794.95 | 8738 | 10827.79 | 8110.4 | 8578.76 | 8402.05 | 9809.6 | 8574.2 | 9140.9 | 8644.12 | 9396.56 | 8302.6 | 8919.6 | 9759.78 | 8779.75 | 10054.95 | 1879.4 | 2119.4 | 8505.2 | 7794.5 | 6859.65 | 7944 | 4264.8 | 8055.2 | 8956 | 5198.6 | 7845.74 | 5942.2 | 3790.7 | 4060.1 | 7137.3 | 8162.3 | 8754.34 | 8373.2 | 8004.3 | 8581.05 | 9659.64 | 7968.2 | 9695.25 | 8582.2 | 9689.64 | 8592.81 | 9539.22 | 8833.2 | 9584.4 | 8387.96 | 9554.42 | 8287.31 | 9378.03 | 8020.9 | 9357.64 | 8658.13 | 7813.04 | 8437.37 | 6133.4 | 9376.62 | 8391.8 | 7054.71 | 9595.7 | 6228.3 | 8476.78 | 7556.7 | 8786.5 | 8627.3 | 9092.31 | 7826.1 | 7219.6 | 8052.8 | 8533.9 | 8601.02 | 8665.07 | 7623.21 | 8066.8 | 7446 | 8449.9 | 8464.39 | 9901.95 | 8833.9 | 9594.96 | 8622.89 | 9653 | 8783.67 | 9627.76 | 7794.48 | 9662 | 9980.6 | 9778.3 | 9843.78 | 9772.9 | 9879.92 | 9063.54 | 9486.58 | 9421.62 | 9738 | 9115.3 | 6961.8 | 8384.9 | 6391.7 | 2842.6 | 8805.7 | 31.0304 | 30.8341 | 30.7832 | 0 | 30.4719 | 0 | 0 | 43.1425 | 0 | 0 | 0 | 0 | 3.4973 | 3.6349 | 3.3714 | 0 | 3.4243 | 3.1889 | 18.7317 | 15.7533 | 13.9017 | 0 | 12.4317 | 10.935 | 5.3099 | 5.1578 | 5.1613 | 0 | 5.3122 | 4.7526 | 0.78957 | 0.98734 | 0.77393 | 0 | 0.83596 | 0.61013 | 5.1274 | 5.0534 | 4.8654 | 0 | 5.1915 | 5.6874 | 0.81632 | 1.0231 | 0.81346 | 0 | 0.89089 | 0.78818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57933 | 103 | 50800 | 89 | 108260 | 302 | 5.3099 | 5.1578 | 5.1613 | 0 | 5.3122 | 4.7526 | 5.1274 | 5.0534 | 4.8654 | 0 | 5.1915 | 5.6874 | 701000 | 1000 | 659000 | 1000 | 1354000 | 4000 | 1358000 | 1350000 | 13.55 | 5.1388 | 0.79939 | 5.185 | 0.8664 | 15.56% | 16.71% | 30.7799 | 43.1425 | 3.4233 | 14.3507 | 1351862.27 | 1354867 | 1697284.332 | 79.83%
2022-07-05 | 2023 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 329648.075 | 5:56 | 19:39 | 9835 | 10898 | 10819 | 10665 | 10782.1 | 10819.7 | 10816.8 | 10843.9 | 10826.7 | 11117.1 | 10721.2 | 10893.8 | 10743.1 | 10678.9 | 10535.6 | 10520.1 | 9459.7 | 10641.9 | 10752.1 | 10630.6 | 10638.1 | 10478.2 | 10546.2 | 10606.2 | 10706.6 | 9341.9 | 10507.2 | 10566.8 | 10757 | 10742.7 | 10589.9 | 10825.7 | 10605.4 | 9930.6 | 10421.3 | 10467.1 | 10773 | 10487.9 | 8834 | 9072.8 | 6708.9 | 3868.1 | 11568.8 | 7474.2 | 3626.2 | 9751.2 | 8093 | 12091.8 | 11074.1 | 8875.9 | 10624.3 | 10359.5 | 11159.8 | 10142.5 | 11282.9 | 10063.7 | 10118.1 | 11277.4 | 10261.9 | 11470.5 | 11319.2 | 10152.1 | 12385 | 9565.9 | 10316.5 | 10312.1 | 11625.8 | 10545.8 | 10843.4 | 10602.8 | 11174.8 | 10159.2 | 10556.1 | 11346.5 | 10368.8 | 11710.5 | 10536 | 11621.1 | 10110.7 | 9428 | 8523.9 | 9849.3 | 5305 | 10058.2 | 10745 | 6437.7 | 9513.2 | 7382.3 | 4724.5 | 5135.2 | 9244.6 | 10114.8 | 10215.1 | 9863.1 | 9746.5 | 10640.5 | 11738.5 | 9892.1 | 11755.7 | 10274.3 | 11634.7 | 10489.8 | 11438.3 | 10741.9 | 11522.8 | 10190.8 | 11538.3 | 10121 | 11339.2 | 9801.9 | 11436.5 | 10711.8 | 9661.6 | 10402.3 | 7532.4 | 11436 | 10737.8 | 10787.6 | 11623.6 | 7667.1 | 10372.8 | 9763.3 | 10793 | 10630.8 | 11128.6 | 9533.2 | 10355.1 | 10022 | 10511.1 | 10596.1 | 10761.8 | 9380.1 | 10331.1 | 9373.4 | 10357.1 | 10368.6 | 12012.4 | 10794.7 | 11693.1 | 10416.7 | 11877.7 | 10649 | 11792.2 | 9562.6 | 11551.3 | 11901.2 | 11779.5 | 11850.8 | 11481.6 | 11904.4 | 10983.5 | 11539.2 | 11269.9 | 11665.1 | 10858 | 8339.3 | 9882.9 | 7663.3 | 3453.2 | 10626.9 | 33.3683 | 33.3282 | 33.4975 | 0 | 33.2744 | 33.4964 | 0 | 64.1589 | 0 | 0 | 0 | 0 | 2.7619 | 2.8232 | 2.4776 | 0 | 2.8079 | 2.548 | 9.8517 | 9.755 | 6.4233 | 0 | 8.3733 | 10.025 | 6.2145 | 6.1937 | 6.389 | 0 | 6.5983 | 5.6437 | 1.1228 | 1.0495 | 1.2953 | 0 | 0.99771 | 0.7514 | 6.1095 | 6.0864 | 6.141 | 0 | 6.2211 | 6.9907 | 1.156 | 1.1816 | 1.3282 | 0 | 1.0973 | 0.94912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58753 | 104 | 51607 | 90 | 109882 | 305 | 6.2145 | 6.1937 | 6.389 | 0 | 6.5983 | 5.6437 | 6.1095 | 6.0864 | 6.141 | 0 | 6.2211 | 6.9907 | 820000 | 1000 | 807000 | 1000 | 1622000 | 3000 | 1625000 | 1619000 | 13.7167 | 6.2079 | 1.0433 | 6.3097 | 1.1425 | 16.81% | 18.11% | 33.3929 | 64.1589 | 2.6837 | 8.8857 | 1636273.5 | 1622667 | 2052545.9648 | 79.06%
2022-07-06 | 2023 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 329648.075 | 5:52 | 19:30 | 11210.8 | 12491.9 | 12575.5 | 12357.6 | 12481.2 | 12611.1 | 12519.3 | 12614.6 | 12197.9 | 12360.2 | 12171.4 | 11912.3 | 12299.8 | 12106.2 | 12219.8 | 12144.2 | 10516.2 | 11969.2 | 12153.3 | 12094.5 | 12039.5 | 11874.6 | 12173.2 | 12114.2 | 11862.4 | 10334.6 | 11817.6 | 11813.9 | 11976.3 | 11919.2 | 11695.8 | 12001.6 | 11631.6 | 11072.5 | 11488.5 | 11674.6 | 11898.6 | 11577.7 | 9758.7 | 9960.6 | 7223.6 | 4163.8 | 12444.7 | 7991.8 | 3887.5 | 10516.2 | 8805.4 | 13393 | 12441.6 | 9788.7 | 11939.2 | 11448.5 | 12638.5 | 11494.5 | 12480.2 | 11094.7 | 10992.7 | 12335.1 | 11371.9 | 12570.1 | 12413 | 11218.1 | 13428.5 | 10215.8 | 10851.6 | 10680.1 | 12242.7 | 10896 | 11473.8 | 10928.3 | 11677.2 | 10450.7 | 9910.8 | 10597.2 | 9490.4 | 12633.2 | 11316.9 | 10837.9 | 10850.5 | 9842.3 | 8847.7 | 10183.8 | 5526.4 | 10424.6 | 11482.5 | 6731.8 | 10094.7 | 7709.5 | 4917.1 | 5364.2 | 9787.4 | 10669.5 | 11504.9 | 11035.4 | 10529.4 | 11222.5 | 12662.3 | 10478.3 | 12711.3 | 11239.8 | 12752.9 | 11346.2 | 12575.9 | 11666.3 | 12650.8 | 11071.9 | 12662.5 | 10943.3 | 12448.8 | 10854.9 | 12514.7 | 11571.7 | 10229.5 | 11044.5 | 7899.1 | 12125.7 | 11502.3 | 11432.3 | 12572.6 | 8063.5 | 10927.5 | 10329.4 | 11622.3 | 11414.2 | 11979.2 | 9975.7 | 11288.3 | 10460.9 | 10977.2 | 11075.4 | 11226.1 | 9751.7 | 10688.6 | 9775.4 | 11006.6 | 10936.4 | 12807.6 | 11473.8 | 12458.1 | 11162 | 12606.5 | 11413.4 | 12500.6 | 10136.8 | 9817.8 | 10261.5 | 10079 | 10117.5 | 9826.4 | 10062.9 | 9216.1 | 9735.5 | 12145.5 | 12511.8 | 11790.3 | 8975.3 | 10828.2 | 8236.1 | 3618.6 | 11368.3 | 34.9616 | 35.373 | 35.0908 | 0 | 35.2452 | 0 | 0 | 51.9932 | 0 | 0 | 0 | 0 | 3.5198 | 5.7304 | 5.6385 | 0 | 5.8276 | 0 | 9.8517 | 11.14 | 12.18 | 0 | 10.62 | 0 | 7.4194 | 6.81 | 6.8264 | 0 | 6.8516 | 0 | 1.2789 | 1.3696 | 1.474 | 0 | 1.225 | 0 | 7.1912 | 6.6513 | 6.4892 | 0 | 5.0907 | 0 | 1.3369 | 1.4569 | 1.5311 | 0 | 1.3251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59654 | 106 | 52451 | 92 | 111620 | 310 | 7.4194 | 6.81 | 6.8264 | 0 | 6.8516 | 0 | 7.1912 | 6.6513 | 6.4892 | 0 | 5.0907 | 0 | 901000 | 2000 | 844000 | 2000 | 1738000 | 5000 | 1741000 | 1733000 | 13.6333 | 6.9768 | 1.3369 | 6.3556 | 1.4125 | 19.16% | 22.22% | 35.1677 | 51.9932 | 5.1791 | 10.9479 | 1752306.4 | 1739000 | 2169470.2242 | 80.16%
2022-07-07 | 2023 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 329648.075 | 6:08 | 19:26 | 8010.5 | 8867.1 | 8841.3 | 8674.5 | 8724.2 | 8896.2 | 8892.5 | 9076.4 | 8744 | 8780 | 8821.1 | 8657.7 | 8905.9 | 8820 | 8830.6 | 8795.8 | 7942.2 | 8960.2 | 9036.2 | 8975 | 8906.6 | 8782 | 8839.2 | 8882.4 | 8906.8 | 7839.8 | 8789.1 | 8830.8 | 8887.9 | 8904.7 | 8848.4 | 9040.7 | 8557.7 | 8246 | 8622.4 | 8724.2 | 8897.8 | 8644.3 | 7322.3 | 7448.5 | 5549 | 3197.6 | 9489.4 | 6146.5 | 2999.8 | 8093.2 | 6763.4 | 10330 | 9165.4 | 7309.2 | 8816.4 | 8561.3 | 9356.3 | 8487 | 9340.3 | 8394.8 | 8311.4 | 9241.5 | 8416 | 9367.3 | 9198.7 | 8282.3 | 10220.2 | 7733.2 | 8293 | 8151.1 | 9322.8 | 8342.2 | 8758 | 8403 | 8932.6 | 8080.5 | 7615.3 | 8148.5 | 8489.7 | 9565.2 | 8595.1 | 9247.2 | 8250.9 | 7912.2 | 6746.1 | 7817.7 | 3960.1 | 7949 | 8726.9 | 5089.5 | 7767.5 | 5948.9 | 3875.7 | 4305.5 | 7333 | 7946.1 | 7987.1 | 7713.3 | 7889.1 | 8277.6 | 9221.7 | 7617.8 | 9229.4 | 8230.3 | 9237.1 | 8235.8 | 9073.3 | 8456.1 | 9094.5 | 8024.2 | 9114.3 | 7919.7 | 8941.3 | 7934.2 | 8985.4 | 8403 | 7454.2 | 8064.9 | 5831.9 | 8764.4 | 8349.8 | 8388.6 | 9139.4 | 5856.3 | 8052.2 | 7637.3 | 8343 | 8241 | 8650.7 | 7345.1 | 8245.4 | 7735.2 | 8145.1 | 8200.1 | 8332.9 | 7262.7 | 7909 | 7144.2 | 8271.1 | 8162 | 9645.6 | 8676.1 | 6540 | 5993 | 9416.3 | 8574.2 | 9305.8 | 7566.9 | 9370.9 | 9697.8 | 9579.3 | 9603 | 9432.3 | 9574.4 | 6244 | 6541 | 9265.7 | 9475.2 | 9072.8 | 6985.6 | 8402.1 | 6386.7 | 2690.1 | 8764.7 | 31.3603 | 31.6608 | 31.6608 | 0 | 33.16 | 31.4486 | 0 | 42.5054 | 0 | 0 | 0 | 0 | 3.4278 | 3.442 | 3.442 | 0 | 2.68 | 3.3923 | 13.2067 | 11.4083 | 11.4083 | 0 | 8.48 | 11.0283 | 5.1222 | 5.2092 | 5.2092 | 0 | 6.42 | 5.032 | 0.87225 | 0.92812 | 0.92812 | 0 | 1.02 | 0.79343 | 4.9473 | 5.0883 | 5.0883 | 0 | 6.1 | 4.8101 | 0.90683 | 1.0269 | 1.0269 | 0 | 1.22 | 0.8765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60327 | 107 | 53082 | 93 | 112919 | 313 | 5.1222 | 5.2092 | 5.2092 | 0 | 6.42 | 5.032 | 4.9473 | 5.0883 | 5.0883 | 0 | 6.1 | 4.8101 | 673000 | 1000 | 631000 | 1000 | 1299000 | 3000 | 1302000 | 1296000 | 13.3 | 5.3985 | 0.90838 | 5.2068 | 1.0114 | 16.83% | 19.43% | 31.8581 | 42.5054 | 3.2768 | 11.1063 | 1309431.7 | 1298734 | 1649519.1286 | 78.73%
2022-07-08 | 2023 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 329648.075 | 6:04 | 19:20 | 9187.9 | 10119.8 | 10069.1 | 9969.2 | 9952 | 10136.3 | 10137.1 | 10348.1 | 10039.1 | 10192 | 10000.4 | 10055.1 | 10047.5 | 10061.7 | 9954.5 | 9885.7 | 8775.5 | 9957.6 | 10100.73 | 10058.6 | 9981.62 | 9856.5 | 10015.32 | 10015.56 | 9930.47 | 8747.99 | 9874.6 | 9867.67 | 10011.43 | 9906.8 | 9655.73 | 9972.76 | 9465.15 | 9172.63 | 9582.8 | 9681.74 | 9862.17 | 9483.6 | 7817.2 | 8107.9 | 5986.25 | 3461.1 | 10368.97 | 6647.6 | 3221.5 | 8640.44 | 7259 | 11370.75 | 10400.51 | 8270.9 | 9978.85 | 9618.65 | 10565.2 | 9537.41 | 10575.43 | 9401.4 | 9312.05 | 10458.2 | 9514.8 | 10641.14 | 10472.49 | 9369.75 | 11611.51 | 8725.4 | 9500.48 | 9345.9 | 10723.8 | 9461 | 9937.75 | 9557.72 | 10206.26 | 9174 | 8491.85 | 9092.28 | 9539.8 | 10809.77 | 9624.09 | 10542.6 | 9238.9 | 9725.6 | 7542.4 | 8831.12 | 2512.7 | 8831.8 | 9531.2 | 5531 | 8599.2 | 6481 | 4174.3 | 4666.8 | 7892 | 8570.1 | 9068.8 | 8759.47 | 8601 | 8874.3 | 9998.27 | 8189.7 | 10071.5 | 8884.7 | 10142.9 | 8962.66 | 9991.6 | 9226.56 | 10085.27 | 8814.8 | 10152.8 | 8693.2 | 9940.1 | 8860.84 | 10027.6 | 9280.7 | 8052.3 | 8831.3 | 6429.32 | 9662.6 | 9236.6 | 9274.4 | 10211.8 | 6504.6 | 8940.2 | 8509.1 | 9098.1 | 9180 | 9606.6 | 8262.6 | 9099.1 | 8637.4 | 8977.1 | 9006.9 | 9252.9 | 8086.7 | 7968.9 | 7939.9 | 8415.1 | 8235.6 | 9679.5 | 8543.7 | 522.9 | 457.2 | 9389.5 | 8447.7 | 9327.1 | 7670.06 | 9456 | 9785 | 9853 | 9811 | 9129 | 9610 | 8544 | 9210 | 9323.9 | 9657.3 | 9145.19 | 7033.1 | 8401.7 | 6381.6 | 2715.5 | 8844.5 | 31.7238 | 31.5518 | 31.3802 | 0 | 31.3195 | 31.3957 | 0 | 45.5844 | 0 | 0 | 0 | 0 | 2.9707 | 2.7045 | 2.8025 | 0 | 2.8197 | 2.6404 | 10.1617 | 11.6983 | 11.1533 | 0 | 17.3767 | 14.915 | 5.8558 | 5.8561 | 5.697 | 0 | 5.7065 | 4.9169 | 0.96065 | 1.0719 | 1.0247 | 0 | 0.83483 | 1.0822 | 5.7242 | 5.7764 | 5.4616 | 0 | 5.525 | 5.7362 | 0.98173 | 1.1673 | 1.0802 | 0 | 0.92619 | 1.0638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61084 | 108 | 53738 | 94 | 114326 | 317 | 5.8558 | 5.8561 | 5.697 | 0 | 5.7065 | 4.9169 | 5.7242 | 5.7764 | 5.4616 | 0 | 5.525 | 5.7362 | 757000 | 1000 | 656000 | 1000 | 1407000 | 4000 | 1411000 | 1403000 | 13.2667 | 5.6065 | 0.99486 | 5.6447 | 1.0438 | 17.74% | 18.49% | 31.4742 | 45.5844 | 2.7875 | 13.061 | 1428586.63 | 1408267 | 1820667.2572 | 77.35%
2022-07-09 | 2023 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 329648.075 | 6:07 | 19:37 | 11061.7 | 12188.9 | 12269 | 12121.5 | 12197.7 | 12299.07 | 12205.5 | 12303.25 | 11966.66 | 12219.2 | 11864.9 | 11927.68 | 11966.65 | 11948.33 | 11622.24 | 11683.6 | 10230.9 | 11525.72 | 11634.05 | 11602.98 | 11593.2 | 11510.04 | 11547.89 | 11526.58 | 11504.2 | 10139.3 | 11498.83 | 11405.35 | 11583.75 | 11654.1 | 11519.2 | 11754.64 | 11511.82 | 11060.18 | 11237.81 | 11435.62 | 11641.2 | 11349.41 | 9284.6 | 9951.3 | 7051.2 | 4082.1 | 12080.31 | 7782.54 | 3840.3 | 10438.72 | 8612.8 | 12836.82 | 12280.2 | 9837.8 | 11779.3 | 11291.63 | 12187.08 | 11273.13 | 12188.4 | 10973.28 | 11062.23 | 12227.17 | 11330.34 | 12482.77 | 12307.58 | 11115.63 | 13384.2 | 10487.54 | 11253.6 | 10887.85 | 12365.4 | 11001.4 | 11715.6 | 11175.93 | 12009.6 | 10784.1 | 10276.54 | 10993.59 | 11481.7 | 12856.75 | 11548.4 | 12474.4 | 11046.7 | 12096.63 | 8834.5 | 10643.39 | 2997.4 | 10417.39 | 11390.6 | 6623.9 | 10119.5 | 7722.3 | 5087.6 | 5591.4 | 9658.91 | 10496.68 | 11082.33 | 10721.37 | 10541.1 | 10886.3 | 12161.42 | 10333.3 | 12462.33 | 11346.6 | 12519.6 | 11383 | 12570.27 | 11817.2 | 12746.4 | 11316.13 | 12844.95 | 11237.22 | 12555.81 | 11299.1 | 12595.5 | 11826.36 | 10339.52 | 11251.2 | 8238.04 | 12283.7 | 11794.76 | 11725.89 | 12803.9 | 8111.3 | 11246.4 | 10660.5 | 11550.9 | 11591.6 | 12020.58 | 10191.7 | 11333.03 | 10724.93 | 11259.7 | 11312 | 11549.1 | 9952.9 | 9559.37 | 9988.1 | 11263.4 | 11067.66 | 12767 | 11659.4 | 12508.3 | 11378.2 | 12725.1 | 11590.29 | 12587.69 | 10291.3 | 12179 | 12664.27 | 12460.7 | 12457.1 | 11749.1 | 11518.5 | 11766.88 | 12306.8 | 12105.8 | 12343.7 | 11934.1 | 9070.9 | 10885.4 | 8258.69 | 3509.3 | 11422.72 | 32.6052 | 32.3405 | 32.606 | 0 | 33.16 | 32.517 | 0 | 44.8092 | 0 | 0 | 0 | 0 | 3.9175 | 4.0333 | 3.3993 | 0 | 2.68 | 4.145 | 7.5433 | 7.8517 | 7.085 | 0 | 8.48 | 7.34 | 6.8878 | 0 | 6.6842 | 0 | 6.42 | 7.1369 | 1.2439 | 0 | 1.2964 | 0 | 1.02 | 1.2325 | 6.7387 | 0 | 6.3496 | 0 | 6.1 | 6.8727 | 1.2353 | 0 | 1.3838 | 0 | 1.22 | 1.3423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61977 | 109 | 54601 | 96 | 116077 | 322 | 6.8878 | 0 | 6.6842 | 0 | 6.42 | 7.1369 | 6.7387 | 0 | 6.3496 | 0 | 6.1 | 6.8727 | 893000 | 1000 | 863000 | 2000 | 1751000 | 5000 | 1753000 | 1746000 | 13.5 | 6.7822 | 1.1982 | 6.5152 | 1.2953 | 17.67% | 19.88% | 32.6457 | 44.8092 | 3.635 | 7.66 | 1766240.09 | 1751467 | 2234805.5108 | 78.37%
2022-07-10 | 2023 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 329898.93 | 6:05 | 19:28 | 9910.1 | 10931.31 | 10833.78 | 10747.89 | 10744.2 | 10904.15 | 10975.4 | 11185.91 | 10861.89 | 10815.82 | 10911.1 | 11043.15 | 10944.04 | 10954.58 | 10773.6 | 10785.3 | 9678 | 10778.66 | 10859.21 | 10829.5 | 10764.5 | 10700.35 | 10563.05 | 10713.9 | 10868.6 | 9590.39 | 10704.19 | 10742.59 | 10883.1 | 10916 | 10789.33 | 10977.12 | 10750.56 | 10416.9 | 10592.02 | 10752.19 | 10818.76 | 10605.98 | 8722.58 | 9323.4 | 6426.2 | 4826.68 | 10890.3 | 7182.6 | 3495.1 | 9465.84 | 7890.9 | 11637.86 | 11228 | 9074.4 | 10818.5 | 10453.61 | 11304.4 | 10461.38 | 11409.84 | 10287.2 | 10209.4 | 11300.62 | 10429.34 | 11431.4 | 11246.49 | 10287.07 | 12068.66 | 9301.8 | 10476 | 10137.1 | 11310.89 | 10176.59 | 10597.44 | 10110.95 | 10719.42 | 9678.4 | 9007.62 | 9649.93 | 10084.31 | 11263.72 | 10219.8 | 11002.63 | 9898.9 | 11184.42 | 8131.36 | 9402.2 | 4979.2 | 9776.9 | 10528 | 6228.3 | 9568.44 | 7331.8 | 4845.7 | 5346.8 | 9203.5 | 10020.07 | 10539.76 | 10205.1 | 10069.8 | 10411.06 | 11394.25 | 9612.76 | 11481.09 | 10334.2 | 11513.7 | 10375.04 | 11296.64 | 10635.27 | 11219.2 | 10103.6 | 11249.64 | 9931.16 | 10961.07 | 9893.3 | 11075.63 | 10341.51 | 9392.01 | 10115.98 | 7368.9 | 10945.28 | 10483.6 | 10441.2 | 10952.2 | 7234.8 | 10073.9 | 9554.4 | 10206.1 | 10195.5 | 10601.14 | 9170.89 | 10095.3 | 9611 | 10128.19 | 10203.8 | 10328.99 | 8972.8 | 8689.65 | 9097.7 | 10190 | 10001.3 | 11468.29 | 10272.5 | 11162.4 | 10029 | 11209.17 | 10205.28 | 11216.3 | 9248.65 | 11060.9 | 11377.79 | 11205.4 | 11382.4 | 11284.64 | 11043.38 | 10614.2 | 11131.55 | 10651.08 | 10877.2 | 10428.93 | 8313.06 | 9808.98 | 7355.12 | 3118.9 | 10114 | 32.0136 | 32.2272 | 32.264 | 0 | 32.0475 | 32.6374 | 0 | 45.8618 | 0 | 0 | 0 | 0 | 3.6092 | 3.7865 | 3.6431 | 0 | 3.739 | 3.6298 | 7.3867 | 7.6717 | 7.9817 | 0 | 6.84 | 7.6717 | 6.3326 | 6.3986 | 6.1296 | 0 | 6.5164 | 6.2505 | 1.2628 | 1.4696 | 1.3733 | 0 | 1.1826 | 1.473 | 6.2991 | 6.3872 | 5.9323 | 0 | 6.301 | 7.3027 | 1.2431 | 1.4819 | 1.4382 | 0 | 1.2694 | 1.4916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62797 | 110 | 55384 | 97 | 117673 | 325 | 6.3326 | 6.3986 | 6.1296 | 0 | 6.5164 | 6.2505 | 6.2991 | 6.3872 | 5.9323 | 0 | 6.301 | 7.3027 | 820000 | 1000 | 783000 | 1000 | 1596000 | 3000 | 1601000 | 1593000 | 13.3833 | 6.3255 | 1.3523 | 6.4445 | 1.3848 | 21.38% | 21.49% | 32.238 | 45.8618 | 3.6815 | 7.5103 | 1610948.61 | 1540173 | 1928305.007 | 79.87%
2022-07-11 | 2023 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 329898.93 | 6:05 | 19:28 | 10739.8 | 11918.9 | 11878.1 | 11836 | 11775.5 | 11929.5 | 11904.3 | 12088.5 | 11742.4 | 11720.6 | 11684.9 | 11785.7 | 11794 | 11770.8 | 11706.8 | 11638.5 | 10279.6 | 11605.5 | 11817.6 | 11812.6 | 11752 | 11541.5 | 11462.5 | 11680.7 | 11680.4 | 10373.1 | 11706.4 | 11677 | 11700 | 11659.1 | 11506.5 | 11789.5 | 11204 | 10912.1 | 11212.8 | 11442.1 | 11521.8 | 11262 | 9165.8 | 9675.4 | 7104.2 | 8340.2 | 11978.1 | 9172.9 | 6090.7 | 10392.5 | 8518.6 | 12600.2 | 12036.7 | 9708.1 | 11637.2 | 11342 | 12145.1 | 11124.1 | 12206.8 | 11137.1 | 11050 | 12251 | 11096 | 12312 | 12100 | 10936 | 12927 | 10088 | 11330.8 | 10865.8 | 12317.8 | 11053.8 | 11612 | 11046.8 | 11798.6 | 10533.8 | 9786.3 | 10494.2 | 10983 | 12311.1 | 11224.3 | 12041.9 | 10809.7 | 12210.5 | 8428.5 | 10041.2 | 5392.9 | 10213.3 | 11310.2 | 6638.7 | 10240.7 | 7808.9 | 5051.4 | 5623.8 | 9602.9 | 10439.8 | 10974.8 | 10558.4 | 10337 | 10935.5 | 12021.5 | 10052 | 12088.5 | 10750.6 | 11982.5 | 10865 | 11854.6 | 11139.9 | 11934.1 | 10579.4 | 12044.5 | 10499.9 | 11876.2 | 10665.7 | 11982.3 | 11146.8 | 9833.4 | 10516.7 | 7576.8 | 11666.2 | 10999 | 11008.2 | 11896 | 7676.4 | 10663.6 | 8684.3 | 10868.3 | 10950.5 | 11425.5 | 9801.8 | 10760.9 | 10192.5 | 10565.7 | 10580 | 10900.5 | 9366.4 | 8947.2 | 9244.8 | 10495.7 | 10309.8 | 12340.4 | 10971.4 | 12018.1 | 10671.7 | 11908.8 | 10823.4 | 11809.6 | 9609.3 | 12052.9 | 12279.3 | 11732.4 | 12261.7 | 12095.5 | 12177.3 | 11347.7 | 11967.4 | 11861.6 | 12048.6 | 11563.1 | 10936.6 | 11001.8 | 8010.2 | 3412.2 | 11051.4 | 33.124 | 32.9732 | 33.1354 | 0 | 33.16 | 33.0673 | 0 | 48.4165 | 0 | 0 | 0 | 0 | 3.7798 | 3.8992 | 3.727 | 0 | 2.68 | 3.8464 | 8.72 | 8.9717 | 9.1583 | 0 | 8.48 | 9.0433 | 6.8171 | 6.8078 | 6.7883 | 0 | 6.42 | 6.8355 | 1.4084 | 1.5175 | 1.6079 | 0 | 1.02 | 1.157 | 6.7551 | 6.7358 | 6.5392 | 0 | 6.1 | 6.391 | 1.385 | 1.5384 | 1.6508 | 0 | 1.22 | 1.2532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63689 | 112 | 56215 | 98 | 119390 | 328 | 6.8171 | 6.8078 | 6.7883 | 0 | 6.42 | 6.8355 | 6.7551 | 6.7358 | 6.5392 | 0 | 6.1 | 6.391 | 892000 | 2000 | 831000 | 1000 | 1717000 | 3000 | 1720000 | 1714000 | 13.3833 | 6.7337 | 1.3422 | 6.5042 | 1.4095 | 19.93% | 21.67% | 33.092 | 48.4165 | 3.5865 | 8.8747 | 1733033.3 | 1718133 | 2181276.13 | 78.77%
2022-07-12 | 2023 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 330198.6 | 6:00 | 19:41 | 11329.4 | 12498.5 | 12579.56 | 12406.89 | 12501.26 | 12626.8 | 12588.9 | 12753.15 | 12307.09 | 12465.95 | 12349.61 | 12490.5 | 12536.46 | 12463 | 12488.42 | 12382.08 | 11066.04 | 12496.6 | 12637.6 | 12653.5 | 12607.62 | 12435.63 | 12319.99 | 12498.27 | 12604.8 | 11012.84 | 12528.8 | 12430.8 | 12706.93 | 12846.6 | 12592.6 | 12857 | 12591.3 | 11958.4 | 11963.9 | 12474.87 | 12563.72 | 12409.34 | 10122.9 | 10882.1 | 7812.33 | 9180.7 | 13342.02 | 10012.6 | 10527.8 | 11470.5 | 9808.6 | 14256.16 | 12761.3 | 10172.4 | 12369.9 | 12057.5 | 13073.56 | 11918.6 | 12996.2 | 11837.79 | 11597.17 | 12948.89 | 11696.8 | 13037.3 | 12751.66 | 11515.5 | 13900.67 | 10686.8 | 11809.2 | 11464.19 | 13025.6 | 11656.2 | 12346.4 | 11716.3 | 12561 | 11213.3 | 11572.8 | 12447.6 | 11717.9 | 13172.85 | 11976.41 | 12886.56 | 11542.8 | 13109.92 | 9469.7 | 11267.7 | 6937.1 | 11478.4 | 12291.6 | 7140 | 10880.8 | 8303.2 | 5460.3 | 5992.8 | 10382.8 | 11230.34 | 11909.6 | 11539.7 | 11386.7 | 11768 | 13166.7 | 10978.1 | 13322.8 | 11971.06 | 13258.87 | 11951.8 | 13099.47 | 12266.49 | 13126.6 | 11567.34 | 13128.4 | 11342.35 | 12855.2 | 11467.24 | 13042.35 | 12199.94 | 10865.54 | 11200.87 | 8227.2 | 12802.41 | 11941.61 | 12065.89 | 13069.23 | 8342.2 | 11599.33 | 8126.9 | 11616.9 | 11944.9 | 12465.85 | 10650.07 | 11687.6 | 11102.79 | 11675.3 | 11773.48 | 11971.5 | 10304.53 | 9999.04 | 10404.46 | 11784 | 11547.2 | 13630.41 | 12200.57 | 13347.5 | 11859.42 | 13393.44 | 12105.5 | 13271.3 | 10722.8 | 13516 | 13837.22 | 13196.22 | 13728.24 | 13448.54 | 13496.86 | 12554.64 | 13386.26 | 13255.9 | 13434.2 | 13126.45 | 12385.34 | 12473.74 | 9008.3 | 2563.3 | 12454.7 | 32.7533 | 32.6848 | 32.8352 | 0 | 32.5709 | 33.2085 | 0 | 47.8242 | 0 | 0 | 0 | 0 | 3.4579 | 3.7894 | 3.3427 | 0 | 3.7284 | 3.6439 | 6.67 | 6.7883 | 7.4967 | 0 | 6.4 | 7.25 | 7.2435 | 7.3771 | 7.4653 | 0 | 7.3971 | 6.6802 | 1.3348 | 1.7761 | 1.5623 | 0 | 1.3348 | 1.6985 | 7.0343 | 7.2499 | 7.0817 | 0 | 7.1186 | 8.1019 | 1.3412 | 1.7999 | 1.6436 | 0 | 1.4361 | 1.7581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64651 | 113 | 57130 | 100 | 121261 | 333 | 7.2435 | 7.3771 | 7.4653 | 0 | 7.3971 | 6.6802 | 7.0343 | 7.2499 | 7.0817 | 0 | 7.1186 | 8.1019 | 962000 | 1000 | 915000 | 2000 | 1871000 | 5000 | 1874000 | 1866000 | 13.6833 | 7.2326 | 1.5413 | 7.3172 | 1.5958 | 21.31% | 21.81% | 32.8105 | 47.8242 | 3.5924 | 6.921 | 1887730.6 | 1872333 | 2387742.7771 | 78.41%
2022-07-13 | 2023 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 330198.6 | 5:57 | 19:36 | 11086.79 | 12294.5 | 12294.53 | 12167.77 | 12213 | 12360.31 | 12339.08 | 12594.04 | 12144.24 | 12269.7 | 12105.27 | 12282.17 | 12387.89 | 12224.12 | 11895.42 | 12075.45 | 10824.83 | 12234.37 | 12350.84 | 12271.11 | 12175.32 | 11988.99 | 11939.82 | 12204.84 | 12344.21 | 10778.12 | 12072.7 | 12197.44 | 12396.83 | 12398.1 | 12219.68 | 12508.84 | 12081.82 | 11602.49 | 11693.95 | 12104.39 | 12212.23 | 11997.63 | 9784.52 | 10283.62 | 7615.93 | 9003.79 | 12960.59 | 9873.02 | 10255.56 | 11077.58 | 9835.4 | 13964.25 | 12546.49 | 9953.24 | 12059.46 | 11713.53 | 12673.03 | 11594.47 | 12740.38 | 11664.42 | 11257.76 | 12653.14 | 11457.56 | 12772.56 | 12550.06 | 11274.73 | 13777.47 | 10332.63 | 11605.66 | 11139.19 | 12769.25 | 11231.83 | 11961.84 | 11386.61 | 12188.94 | 10911.23 | 11586.51 | 12343.8 | 11241.89 | 12918.15 | 11613.58 | 12550.77 | 11149.77 | 12769.61 | 9148.8 | 10853.56 | 8717.87 | 11146.95 | 11885.04 | 6819.1 | 10538.82 | 8044.5 | 5327.5 | 5850.1 | 10111.35 | 10999.45 | 11621.87 | 11229.57 | 11028.78 | 11467.39 | 12746.12 | 10664.55 | 12824.9 | 11471.48 | 12879.79 | 11504.59 | 12668.16 | 11822.41 | 12723.39 | 11267.69 | 12793.45 | 11169.15 | 12478.71 | 11256.01 | 12724.15 | 11869.9 | 10424.01 | 10838.64 | 8073.67 | 12365.87 | 11660.07 | 11714.62 | 12660.54 | 8149.16 | 11283.05 | 7937.8 | 11368.6 | 11112 | 11843.22 | 10349.6 | 11361.54 | 10786.62 | 11245.2 | 11300.8 | 11497.5 | 9964.45 | 9557.9 | 9977.64 | 11208.82 | 11015.09 | 12696.18 | 11469 | 12339.21 | 11214.02 | 12549.64 | 11485.42 | 12500.33 | 10265.06 | 12326.24 | 12671.06 | 12008.63 | 12602.19 | 12392.09 | 12485.18 | 11570.3 | 12465.98 | 11825.14 | 11883.17 | 11782.18 | 11205.81 | 11310 | 8278.8 | 7246.3 | 11314.18 | 32.7869 | 32.7771 | 32.8604 | 0 | 32.6045 | 33.0547 | 0 | 47.1328 | 0 | 0 | 0 | 0 | 3.8843 | 4.0929 | 3.8369 | 0 | 4.0176 | 3.8866 | 7.0333 | 6.9233 | 6.82 | 0 | 7.1033 | 7.06 | 6.9221 | 7.1138 | 7.133 | 0 | 7.1254 | 6.1802 | 1.3269 | 1.866 | 1.5298 | 0 | 1.3345 | 1.5275 | 6.763 | 7.0352 | 6.8037 | 0 | 6.9765 | 7.3764 | 1.3305 | 1.8714 | 1.6157 | 0 | 1.4321 | 1.6199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65592 | 115 | 58009 | 101 | 123073 | 337 | 6.9221 | 7.1138 | 7.133 | 0 | 7.1254 | 6.1802 | 6.763 | 7.0352 | 6.8037 | 0 | 6.9765 | 7.3764 | 941000 | 2000 | 879000 | 1000 | 1812000 | 4000 | 1817000 | 1808000 | 13.65 | 6.8949 | 1.517 | 6.991 | 1.5739 | 22% | 22.51% | 32.8167 | 47.1328 | 3.9437 | 6.988 | 1827614.27 | 1812667 | 2287450.3837 | 79.24%
2022-07-14 | 2023 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 330229.92 | 6:01 | 19:31 | 8991.7 | 9791.87 | 9766.8 | 9734.3 | 9668.6 | 9745.6 | 9730.05 | 9920.4 | 9746.56 | 9767.17 | 9593.5 | 9763.71 | 9630.86 | 9610 | 9188 | 9428.61 | 8411.9 | 9484.4 | 9583 | 9520.18 | 9450.4 | 9333.84 | 9346.2 | 9510.55 | 9533 | 8448.3 | 9396.5 | 9430.3 | 9561.01 | 9554.4 | 9435.2 | 9654.5 | 9500.29 | 9171.32 | 9095 | 9423.2 | 9462.9 | 9311.3 | 7729.5 | 8070.7 | 5990.3 | 7043 | 10120.8 | 7795.5 | 8097 | 8729.9 | 7762.9 | 10950.3 | 9905.7 | 8027.4 | 9468.15 | 9276.6 | 9889.08 | 9076.3 | 10121.5 | 9209.9 | 9062.1 | 10048 | 9156.4 | 10207.2 | 10036.33 | 9056.4 | 11002.5 | 8420.6 | 9285.99 | 8971.7 | 10169.55 | 9042.8 | 9521.64 | 9124.39 | 9718.9 | 8736.9 | 9340.86 | 9915 | 9130.87 | 10329.59 | 9311.5 | 10098.2 | 8968 | 10220.1 | 7536.9 | 8880 | 7252.5 | 9009.1 | 10107.4 | 7057.58 | 8514.8 | 6550 | 4277.5 | 4730.6 | 8128.7 | 8790.1 | 9274.1 | 9003.2 | 8843.2 | 9104.8 | 10072.87 | 8489.3 | 10139.1 | 9044.82 | 10175.8 | 9079 | 10008.7 | 9297.1 | 10086.76 | 8791.8 | 9998.17 | 8766.55 | 9878.7 | 8913.6 | 10026.6 | 9341 | 8256 | 8473.66 | 6379.2 | 9623.4 | 9088.6 | 9158 | 9884.7 | 6337.2 | 8757.1 | 6194.5 | 9023.7 | 8975.6 | 9398.89 | 8086.6 | 8764.12 | 8385.92 | 8695.07 | 8763.4 | 8864.03 | 7721.9 | 7338.2 | 7936.68 | 8798.78 | 8669.1 | 10159.41 | 9070.1 | 9745.9 | 8846.3 | 9946.54 | 8997.91 | 9865.1 | 8045 | 9718.2 | 9987.9 | 9453.6 | 9973.65 | 9828.62 | 9921.5 | 9061.55 | 9951.36 | 9450.2 | 9611.42 | 9291.96 | 8676.5 | 8869.17 | 6517.52 | 8423.8 | 8759.1 | 33.9231 | 33.6056 | 33.6759 | 0 | 33.5928 | 33.6158 | 0 | 42.7604 | 0 | 0 | 0 | 0 | 4.7992 | 4.5276 | 4.6305 | 0 | 4.552 | 4.1908 | 13.4567 | 13.1017 | 13.2717 | 0 | 13.1933 | 14.0617 | 5.682 | 5.3747 | 5.5472 | 0 | 5.4947 | 4.6923 | 1.1243 | 1.2888 | 1.3413 | 0 | 0.87826 | 1.0962 | 5.4761 | 5.3382 | 5.3779 | 0 | 5.1075 | 5.6724 | 1.1788 | 1.3025 | 1.4029 | 0 | 0.95814 | 1.1237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66334 | 116 | 58708 | 103 | 124508 | 341 | 5.682 | 5.3747 | 5.5472 | 0 | 5.4947 | 4.6923 | 5.4761 | 5.3382 | 5.3779 | 0 | 5.1075 | 5.6724 | 742000 | 1000 | 699000 | 2000 | 1435000 | 4000 | 1438000 | 1431000 | 13.5 | 5.3582 | 1.1458 | 5.3944 | 1.1932 | 21.38% | 22.12% | 33.6826 | 42.7604 | 4.54 | 13.417 | 1448752.48 | 1436400 | 1767333.096 | 81.28%
2022-07-15 | 2023 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 330834.22 | 6:01 | 18:53 | 5879 | 6574.3 | 6637.7 | 6561.8 | 6574.3 | 6657.1 | 6625.1 | 6805.2 | 6479.7 | 6542.8 | 6432.7 | 6572.3 | 6624.6 | 6517.7 | 6266 | 6446.2 | 5626.5 | 6494.1 | 6577 | 6520.2 | 6477.5 | 6366.4 | 6375.8 | 6495.3 | 6429.9 | 5559.7 | 6388.4 | 6405.9 | 6515.1 | 6508.8 | 6323.8 | 6557.6 | 6263.1 | 5988 | 6014.1 | 6258.3 | 6330.5 | 6211.9 | 6120 | 6009 | 3924.5 | 4635 | 6943.6 | 5111.7 | 5334.8 | 5824.9 | 5082.3 | 7873.4 | 6742.7 | 5201 | 6416.6 | 6096.4 | 6802.3 | 6131.1 | 6821.4 | 6107.6 | 5929.7 | 6762.7 | 6114.7 | 6920.6 | 6766.2 | 6013.5 | 7575.1 | 5443.5 | 6091.4 | 5849.5 | 6838.8 | 5913.9 | 6315.5 | 6032 | 6487.9 | 5671.8 | 6137.6 | 6467.7 | 5936.9 | 7030.5 | 6125.3 | 6778.3 | 5899.8 | 6854.5 | 4812.2 | 5734.4 | 4553 | 5720.8 | 6757.3 | 4945.6 | 5436.6 | 4202.2 | 2786.5 | 3055.3 | 5204.6 | 5619 | 6061.1 | 5807.2 | 5670.2 | 5976.1 | 6713 | 5480.3 | 6775.1 | 5905.7 | 6766.1 | 5864.8 | 6598 | 6048.4 | 6647.8 | 5707.1 | 6671.3 | 5640.9 | 6437 | 5687.7 | 6599.1 | 6050 | 5370.4 | 5648.4 | 4406.7 | 7243 | 6057.7 | 6097.2 | 6601.9 | 4113.4 | 5717.1 | 3982.4 | 5858.1 | 5753.8 | 6111.1 | 5204.6 | 5996 | 5623.7 | 5759.4 | 5813.9 | 5906.7 | 5074.3 | 4788.4 | 5177.8 | 5886.3 | 5779.7 | 7002.1 | 6075.4 | 6715.3 | 5908.1 | 6815.4 | 6036.2 | 6746.5 | 5346.5 | 6710.9 | 7026.9 | 6511.9 | 6934.2 | 6745.7 | 6822.5 | 6193.7 | 6978.6 | 6554.3 | 6651.2 | 6390.5 | 5900.4 | 5197.6 | 4327.2 | 6361.7 | 6001.4 | 30.3375 | 30.1064 | 29.8975 | 0 | 33.16 | 29.9648 | 0 | 36.3307 | 0 | 0 | 0 | 0 | 4.9096 | 4.8905 | 4.8523 | 0 | 2.68 | 4.7828 | 12.805 | 11.8717 | 15.7967 | 0 | 8.48 | 15.7967 | 3.4368 | 3.4171 | 3.4549 | 0 | 0 | 3.0116 | 0.42628 | 0.53417 | 0.5322 | 0 | 1.02 | 0.62672 | 3.344 | 3.3779 | 3.2774 | 0 | 0 | 3.5668 | 0.51835 | 0.56747 | 0.60508 | 0 | 1.22 | 0.58339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66833 | 117 | 59174 | 104 | 125469 | 345 | 3.4368 | 3.4171 | 3.4549 | 0 | 0 | 3.0116 | 3.344 | 3.3779 | 3.2774 | 0 | 0 | 3.5668 | 499000 | 1000 | 466000 | 1000 | 961000 | 4000 | 963000 | 957000 | 12.8667 | 3.3301 | 0.62787 | 3.3916 | 0.69886 | 18.85% | 20.61% | 30.6932 | 36.3307 | 4.4231 | 12.95 | 969880.7 | 961333 | 1145818.1592 | 83.9%
2022-07-16 | 2023 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 330834.22 | 6:06 | 19:22 | 10798.7 | 11908.4 | 11873.3 | 11772.9 | 11756.1 | 11962.3 | 12009.9 | 12227.7 | 11736.3 | 10910.8 | 11710.8 | 11840.3 | 11986.8 | 11733.6 | 11516.6 | 11745.5 | 10593.1 | 11866.1 | 11996.4 | 11859.2 | 11843.5 | 11653.1 | 11709.9 | 11915.3 | 11739.3 | 10398.3 | 11725.9 | 11733.8 | 11730.4 | 11875.1 | 11677.9 | 11928.5 | 11415.3 | 11037 | 11229.7 | 11529.1 | 11647.6 | 11500.1 | 9327.3 | 9579.9 | 7549 | 8785.8 | 12461.2 | 9738.4 | 10085.7 | 10906.4 | 9724.5 | 13275 | 12120.6 | 9816.1 | 11728.7 | 11351.6 | 12169.9 | 11343.9 | 12160.3 | 11284.5 | 10923.9 | 12019 | 11265 | 12227 | 12062.3 | 11085.4 | 12949.6 | 10061.1 | 11166.4 | 10647.5 | 12076.5 | 10721.7 | 11424.8 | 10896.8 | 11580.3 | 10263.9 | 11096.4 | 11380.4 | 10767.9 | 12203 | 11116.7 | 11886.9 | 10718 | 12015.6 | 8813.3 | 10407.5 | 7875.4 | 10574.1 | 11663.6 | 8979.9 | 9957.9 | 7687.4 | 5171.2 | 6294.8 | 9755 | 9973.8 | 11170.4 | 10769.8 | 10491.9 | 10608.1 | 11804 | 9877 | 11898.5 | 10678.7 | 12054.8 | 10787.5 | 11869.9 | 11050.2 | 11942.5 | 10589.9 | 11997.2 | 10477.8 | 11736.9 | 10648.8 | 11883 | 11159.9 | 9890.1 | 10284.2 | 8348.2 | 12474.2 | 11588.6 | 11149.3 | 12279.4 | 7982 | 10464.8 | 7338.9 | 11328.9 | 10944.4 | 11076.5 | 9545.2 | 11133.6 | 10619.1 | 10463.8 | 10479 | 10690.4 | 9328.3 | 8677.7 | 9471.4 | 10574 | 10427.6 | 11985.8 | 10850.5 | 11802.8 | 10730.7 | 11934.5 | 10910.4 | 11833.5 | 9646.2 | 11877.6 | 12213.1 | 11443.3 | 11983.4 | 11705.6 | 11811.4 | 11136.6 | 12129.3 | 11434.6 | 11618.5 | 11122.3 | 10256.6 | 8395.7 | 7982.8 | 11198.8 | 10931.6 | 32.0449 | 31.6928 | 31.2851 | 0 | 33.16 | 31.6881 | 0 | 43.5805 | 0 | 0 | 0 | 0 | 5.101 | 5.0004 | 5.0438 | 0 | 2.68 | 4.7427 | 10.4883 | 12.115 | 11.2767 | 0 | 8.48 | 11.1067 | 6.8334 | 6.8438 | 7.0603 | 0 | 6.42 | 5.8255 | 0.89766 | 1.1329 | 1.2603 | 0 | 1.02 | 1.2667 | 6.6784 | 6.7601 | 6.7292 | 0 | 6.1 | 6.973 | 1.0392 | 1.2016 | 1.3373 | 0 | 1.22 | 1.2935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67737 | 119 | 60014 | 106 | 127207 | 350 | 6.8334 | 6.8438 | 7.0603 | 0 | 6.42 | 5.8255 | 6.6784 | 6.7601 | 6.7292 | 0 | 6.1 | 6.973 | 904000 | 2000 | 840000 | 2000 | 1738000 | 5000 | 1740000 | 1733000 | 13.2667 | 6.5966 | 1.1155 | 6.6481 | 1.2183 | 16.91% | 18.33% | 31.9742 | 43.5805 | 4.5136 | 10.6933 | 1752205.4 | 1738134 | 2217221.6612 | 78.39%
2022-07-17 | 2023 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 330834.22 | 6:03 | 19:30 | 9023.76 | 9879.6 | 10017.8 | 9934.39 | 9938.2 | 9973.19 | 9888.87 | 10022.44 | 9705.74 | 9837.4 | 9585.7 | 9709.26 | 9792.3 | 9606.4 | 9268.56 | 9487.61 | 8321.1 | 9420.7 | 9579.08 | 9491.9 | 9523.6 | 9408 | 9449 | 9598.5 | 9419.7 | 8249.9 | 9362.37 | 9291.8 | 9321.6 | 9420.3 | 9163.7 | 9533.8 | 9018 | 8745.5 | 8845.8 | 9134.6 | 9234.4 | 9030.3 | 7386.05 | 7541.3 | 7696.5 | 5818.51 | 9637.9 | 7140.1 | 7687.5 | 9417.8 | 7272.46 | 10691.6 | 9876.13 | 7933.1 | 9461.7 | 9141.5 | 9881.9 | 9173.6 | 9861.6 | 8957.8 | 8836.37 | 9830.75 | 9078.8 | 10020.4 | 9085.98 | 8954.7 | 10962.48 | 8173.9 | 9000.38 | 8701.8 | 9910.14 | 8768.2 | 9071.2 | 8869 | 9376.59 | 8557.6 | 8963.1 | 9389.2 | 8575.5 | 10010.76 | 8936.6 | 9739.6 | 7796.8 | 9894.04 | 7759 | 8885.3 | 6488.3 | 8774 | 9398 | 7191.7 | 8126.8 | 6217.6 | 5069.1 | 6342.7 | 7725 | 7885.6 | 8808.7 | 8470.71 | 8285.7 | 8390.9 | 9553.37 | 7916.5 | 9524.4 | 8418.39 | 9555.72 | 8403.5 | 9337.1 | 8609.4 | 9204.79 | 8210.32 | 9428.6 | 8002.5 | 9138.78 | 8125.5 | 9257.84 | 8509.6 | 8024 | 8742.21 | 6422 | 9890.52 | 9196.63 | 8880.8 | 9809.1 | 7470.1 | 8187.7 | 5798.2 | 8747.9 | 8415.6 | 8573.2 | 7541.74 | 8865.39 | 8413.6 | 8224.38 | 8253.19 | 8501 | 7395.3 | 6789.7 | 7391.71 | 8294.64 | 8163.66 | 9388.42 | 8319.63 | 9108.2 | 8162.4 | 9370 | 8476.83 | 9399 | 7583.3 | 9066.2 | 9382.38 | 8813 | 9311.1 | 9070.3 | 9173.16 | 8409.44 | 9344.7 | 9138.8 | 8884.27 | 8163.32 | 8084.86 | 6226 | 5585.1 | 8744.2 | 8285.45 | 30.775 | 30.7832 | 30.6487 | 0 | 33.16 | 30.6438 | 0 | 41.7142 | 0 | 0 | 0 | 0 | 4.0921 | 3.4335 | 3.6745 | 0 | 2.68 | 3.758 | 8.5283 | 7.2117 | 7.2367 | 0 | 8.48 | 7.7383 | 5.445 | 5.1925 | 5.4104 | 0 | 6.42 | 5.2335 | 0.70212 | 0.92806 | 0.91113 | 0 | 1.02 | 0.72138 | 5.0423 | 4.9186 | 5.0656 | 0 | 6.1 | 4.9058 | 1.0611 | 1.0057 | 0.98395 | 0 | 1.22 | 0.8383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68468 | 121 | 60678 | 107 | 128596 | 354 | 5.445 | 5.1925 | 5.4104 | 0 | 6.42 | 5.2335 | 5.0423 | 4.9186 | 5.0656 | 0 | 6.1 | 4.9058 | 731000 | 2000 | 664000 | 1000 | 1389000 | 4000 | 1392000 | 1385000 | 13.45 | 5.5403 | 0.85654 | 5.2065 | 1.0218 | 15.46% | 19.63% | 31.2021 | 41.7142 | 3.5276 | 7.839 | 1399813.56 | 1375394 | 1637343.643 | 84%
2022-07-18 | 2023 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 331394.22 | 6:08 | 19:36 | 6870.39 | 7674.28 | 7616.23 | 7506.32 | 7496.88 | 7704.01 | 7786.14 | 7980.85 | 7717 | 7674.3 | 7707.62 | 7813.67 | 7893.82 | 7722.6 | 7368.24 | 7583.6 | 8220.9 | 9250.88 | 9268.59 | 9086.7 | 9052.69 | 8857.98 | 8887.3 | 9064.49 | 9252.94 | 8072.38 | 9001.15 | 9077.98 | 9224.93 | 9432 | 9278.16 | 9514.6 | 8983.4 | 8598.07 | 8686.1 | 9051.4 | 9251.94 | 9136.5 | 7345.8 | 7543.4 | 10058.04 | 8851.9 | 9988.1 | 7478.51 | 8015.2 | 9783.58 | 7572.6 | 10811.19 | 9255.2 | 7405.8 | 8883.5 | 8615.7 | 9338.58 | 8552.16 | 9424 | 8685.81 | 8250.9 | 9379.36 | 8418.7 | 9485.79 | 8351.9 | 8353.91 | 10360.84 | 7669.85 | 8593 | 8240.12 | 9358.2 | 8188.9 | 8629.9 | 8303.73 | 8101.82 | 7663.9 | 8471.5 | 8744.06 | 8181.03 | 9527.51 | 8444.9 | 9082.08 | 7342.6 | 9286.3 | 7390.1 | 8356.58 | 6545.16 | 8336.37 | 9077.3 | 6942.9 | 7803.9 | 6174.3 | 4920.09 | 6115.1 | 7728.09 | 7907.1 | 8766.55 | 8399.5 | 8303.49 | 8149.28 | 7954.8 | 6593.13 | 8065.9 | 7122.54 | 8042.05 | 7090.2 | 7894.9 | 7301.3 | 7857.2 | 6879.7 | 7615.83 | 6795.37 | 7718.94 | 6831.1 | 7934.1 | 7297.64 | 8684.49 | 9453.6 | 6631.73 | 10200.06 | 9503.57 | 8223.4 | 10033.95 | 7571.2 | 8996.4 | 6628.6 | 8996.6 | 8640.7 | 8817.32 | 7648.65 | 9260.1 | 8530.5 | 8375 | 8384.36 | 8641.6 | 7473.3 | 6914.4 | 7476.6 | 8428.6 | 8158.9 | 9658.1 | 8578.5 | 9332.65 | 8373.65 | 9502.6 | 8435.7 | 9539.54 | 7655.7 | 9299.1 | 9670.79 | 8994.96 | 9519.92 | 9319.9 | 9423.8 | 8654.76 | 9591.51 | 9072.01 | 9030.84 | 9010.5 | 8825.57 | 6190.23 | 5982.4 | 8857.77 | 8581 | 30.5807 | 30.5172 | 30.5438 | 0 | 33.16 | 30.7838 | 0 | 40.8884 | 0 | 0 | 0 | 0 | 3.0103 | 3.0426 | 3.0148 | 0 | 2.68 | 3.0519 | 7.3183 | 6.4633 | 6.4283 | 0 | 8.48 | 8.3633 | 5.1616 | 5.2185 | 5.4215 | 0 | 6.42 | 5.3129 | 0.22885 | 0.69785 | 0.85167 | 0 | 1.02 | 0.76194 | 4.9948 | 5.105 | 5.1834 | 0 | 6.1 | 5.1749 | 0.69301 | 0.77981 | 0.91015 | 0 | 1.22 | 0.83205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69149 | 122 | 61328 | 109 | 129923 | 358 | 5.1616 | 5.2185 | 5.4215 | 0 | 6.42 | 5.3129 | 4.9948 | 5.105 | 5.1834 | 0 | 6.1 | 5.1749 | 681000 | 1000 | 650000 | 2000 | 1327000 | 4000 | 1328000 | 1323000 | 13.4667 | 5.5069 | 0.71206 | 5.3116 | 0.88701 | 12.93% | 16.7% | 31.1171 | 40.8884 | 2.9599 | 7.4107 | 1337092.54 | 1326667 | 1727165.0989 | 76.81%
2022-07-19 | 2023 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 331394.22 | 6:08 | 19:38 | 7167.86 | 7931.3 | 7873.3 | 7850.5 | 7817.8 | 8002.8 | 7951.64 | 8087.7 | 7815.45 | 7887.96 | 7702.9 | 7813.6 | 7860.8 | 7698.8 | 7403.94 | 7567.4 | 6830.3 | 7747.4 | 7829 | 7696.9 | 7678.4 | 7541.6 | 7559.4 | 7708.7 | 7621.3 | 6689.19 | 7608.1 | 7620.6 | 7553.5 | 7552.7 | 7477.9 | 7710.3 | 7382.07 | 7067.3 | 7109.3 | 7451.24 | 7526.2 | 7391.7 | 5985.5 | 6139.2 | 8373.4 | 7682.8 | 8301.1 | 6668.8 | 6670.8 | 8031.2 | 6224.1 | 8934.7 | 7830.8 | 6213.7 | 7512.4 | 7268.27 | 7891.2 | 7212.9 | 7759 | 7246.15 | 6968.83 | 7829.31 | 6254.6 | 7965.4 | 6984.7 | 7064 | 8553.1 | 6381.1 | 7358.9 | 6809.9 | 8014.74 | 6741.9 | 7131.92 | 6883.8 | 7383.82 | 6578.6 | 7188.2 | 7460.45 | 6965.7 | 8048.46 | 7133.38 | 7729.5 | 6173.7 | 7788.4 | 6280.4 | 7078.8 | 5654.38 | 7032 | 7395.9 | 5637.8 | 6579 | 5106.8 | 5345.2 | 5534 | 6627.3 | 7137.9 | 7518 | 7108 | 7087.8 | 6614 | 7557.6 | 6186.6 | 7609.2 | 6742.2 | 7728.43 | 6737.9 | 7591.03 | 6990.6 | 7620.36 | 6696 | 7772.6 | 6650.72 | 7571.2 | 6740.1 | 7795.6 | 7217.51 | 6877.7 | 7568.7 | 5242.6 | 8157.1 | 7648.23 | 6566.86 | 8089.7 | 6030.7 | 7632.8 | 6820.3 | 7439.1 | 6883.8 | 7310.9 | 6299.4 | 7505.5 | 6810.8 | 6657.16 | 6661.5 | 6851.5 | 5883.5 | 5497 | 5891.8 | 6823.1 | 6690.4 | 7570.11 | 6722.1 | 7468.5 | 6754.7 | 7680.8 | 6949.1 | 7689.5 | 6163.5 | 7382.4 | 7651.2 | 7185.47 | 7579.28 | 7377.6 | 7411.9 | 6807.95 | 7580.66 | 7374.3 | 7308.58 | 7146.18 | 7012.1 | 6785.2 | 4916.4 | 7238.3 | 6839.1 | 33.9231 | 33.6056 | 30.6487 | 0 | 30.6298 | 30.9223 | 0 | 42.7604 | 0 | 0 | 0 | 0 | 4.7992 | 4.5276 | 3.6745 | 0 | 3.758 | 2.9187 | 13.4567 | 13.1017 | 7.2367 | 0 | 7.7383 | 6.115 | 5.682 | 5.3747 | 5.4104 | 0 | 5.2335 | 4.4222 | 1.1243 | 1.2888 | 0.91113 | 0 | 0.72138 | 0.94218 | 5.4761 | 5.3382 | 5.0656 | 0 | 4.9058 | 5.3111 | 1.1788 | 1.3025 | 0.98395 | 0 | 0.8383 | 0.93334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69740 | 122 | 61878 | 109 | 131059 | 359 | 5.682 | 5.3747 | 5.4104 | 0 | 5.2335 | 4.4222 | 5.4761 | 5.3382 | 5.0656 | 0 | 4.9058 | 5.3111 | 591000 | 0 | 550000 | 0 | 1136000 | 1000 | 1141000 | 1135000 | 13.5 | 5.2246 | 0.99756 | 5.2193 | 1.0474 | 19.09% | 20.07% | 31.9459 | 42.7604 | 3.9356 | 9.5297 | 1147505.29 | 1136600 | 1425261.8413 | 79.75%
2022-07-20 | 2023 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 331394.22 | 6:08 | 19:37 | 11454.3 | 12673.99 | 12641.9 | 12521.99 | 12622.4 | 12779.8 | 12701.52 | 12976.7 | 12563 | 12549.25 | 12527.38 | 12676.82 | 12828.73 | 12519.7 | 12105.9 | 12419.87 | 11173.39 | 12606.67 | 12711.5 | 12551.77 | 12586 | 12438.1 | 12416.35 | 12602.26 | 12505 | 11028.5 | 12534.2 | 12494.1 | 12489.4 | 12720.8 | 12514.44 | 12763.9 | 12431.6 | 11886.95 | 11818.2 | 12401 | 12547.82 | 12410.7 | 9840.2 | 10478 | 13462.94 | 12437.1 | 13347 | 10490.3 | 10846.68 | 13042.9 | 9648.57 | 14069.5 | 11439.2 | 9145.26 | 11066.8 | 10704.9 | 11535.67 | 10678.5 | 11333.97 | 10653.5 | 11674.9 | 12885.7 | 10472.3 | 13011 | 11719.2 | 11702.02 | 13708.31 | 10809.7 | 12491.3 | 11907.99 | 13417.36 | 11778.9 | 11690.37 | 11245.7 | 12444.66 | 11431.09 | 12069.4 | 12463 | 11704.41 | 13034.34 | 12003.4 | 12934.4 | 10190.9 | 13096.9 | 11074.16 | 12306.85 | 9871.5 | 12462.5 | 12757.9 | 9817.4 | 11599.4 | 9489.1 | 10836.87 | 12347.86 | 11689.53 | 12746.65 | 12852 | 12151.35 | 12067.65 | 12723.4 | 13085.86 | 11023.51 | 13145.6 | 11760.62 | 13141.21 | 11824.3 | 13013.9 | 12133.6 | 13030.79 | 11495.2 | 13172.7 | 11496.5 | 12946.71 | 11663.2 | 13197.84 | 12343.2 | 12006.1 | 12993.34 | 9118.3 | 13755.6 | 13019.98 | 12636.39 | 13468.69 | 10462.3 | 12986.1 | 11811.2 | 12660.2 | 11884.6 | 12604.9 | 11307.5 | 12781.5 | 11844.6 | 11627.2 | 11663.4 | 11901.6 | 10275.3 | 9621.8 | 10379.95 | 11745.77 | 11522.2 | 13328.57 | 11853.69 | 13102.53 | 11918.24 | 13157.6 | 11956.47 | 13075.38 | 10572.3 | 13024.87 | 13334.32 | 12799.5 | 13329.72 | 13084.3 | 13141.5 | 12340.7 | 13364.5 | 12842 | 12854.84 | 12554.63 | 12372.9 | 4887.26 | 9343 | 12787.87 | 12237.4 | 32.3272 | 32.4198 | 32.5886 | 0 | 33.16 | 32.2132 | 0 | 42.8243 | 0 | 0 | 0 | 0 | 7.315 | 7.5641 | 7.7702 | 0 | 2.68 | 7.2234 | 11.34 | 11.45 | 12.0533 | 0 | 8.48 | 11.2783 | 7.1749 | 6.8515 | 7.3277 | 0 | 6.42 | 7.282 | 0.088719 | 1.4633 | 1.5193 | 0 | 1.02 | 1.2356 | 6.9493 | 6.6345 | 6.9846 | 0 | 6.1 | 6.9715 | 1.1951 | 1.5734 | 1.6181 | 0 | 1.22 | 1.3449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70701 | 123 | 62835 | 110 | 132969 | 362 | 7.1749 | 6.8515 | 7.3277 | 0 | 6.42 | 7.282 | 6.9493 | 6.6345 | 6.9846 | 0 | 6.1 | 6.9715 | 961000 | 1000 | 957000 | 1000 | 1910000 | 3000 | 1916000 | 1907000 | 13.4833 | 7.0112 | 1.0654 | 6.728 | 1.3903 | 15.2% | 20.66% | 32.5418 | 42.8243 | 6.5105 | 10.9203 | 1928915.61 | 1911087 | 2345535.5526 | 81.48%
2022-07-21 | 2023 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 331394.22 | 6:08 | 19:37 | 9078.7 | 9896.9 | 9901.4 | 9857.5 | 9765.5 | 9928.9 | 9988 | 10201.3 | 9903.8 | 9796.3 | 9845.7 | 9903.7 | 9937.9 | 9851.4 | 9265.9 | 9518.7 | 8563.3 | 9624.5 | 9679.6 | 9652.4 | 9646.9 | 9538.5 | 9654.6 | 9720.4 | 9405.6 | 8316.6 | 9448.1 | 9372.2 | 9320.2 | 9451.4 | 9231.6 | 9547.3 | 9527.5 | 9101.5 | 9090.9 | 9468.6 | 9624.9 | 9459.3 | 9606.5 | 8878.7 | 10422.9 | 9406.1 | 9751.8 | 8094.8 | 8288.4 | 10129.9 | 7701.3 | 11276.2 | 10151.3 | 8173.6 | 9728.1 | 9420.1 | 10559 | 9702 | 10009.1 | 9371 | 9139.6 | 10226.7 | 8468.3 | 10324.5 | 9343.5 | 9185.6 | 11404.4 | 8581.5 | 9894.3 | 9472.9 | 10776 | 9323.4 | 10198.2 | 9373 | 10084.5 | 7960.1 | 9501.6 | 9967.7 | 9253.3 | 10503.3 | 9379.1 | 10312.4 | 8811.8 | 10466.8 | 8922.1 | 9948.1 | 7916.3 | 10081.8 | 10156.1 | 7894.4 | 9077.7 | 7604.5 | 8552.4 | 9954.4 | 9148.3 | 9992.7 | 10088.3 | 9447.5 | 9347.9 | 10066.5 | 10174.2 | 8691.7 | 10428 | 9307.5 | 10281.7 | 9161.5 | 10098.4 | 9486.7 | 9817.2 | 7864.4 | 10162.9 | 8846.6 | 9806.8 | 8719.5 | 9921 | 9381.3 | 9450.2 | 10295.9 | 7149 | 11172.1 | 10296.1 | 9917.1 | 10760.4 | 8276.4 | 10291.5 | 9217.3 | 9654.4 | 9095.1 | 9564.1 | 8714 | 9932.8 | 9209 | 9128.3 | 9118.1 | 9245.6 | 8122.6 | 7605.8 | 8239.9 | 9303.7 | 9161 | 10589.4 | 9153.8 | 10200.1 | 9308.9 | 10514 | 9296.2 | 10479.6 | 8224.4 | 10332.1 | 10638 | 10052.5 | 10583 | 10284.8 | 10380.8 | 9588.3 | 10624.1 | 10171.7 | 10133.6 | 9496.5 | 9919.4 | 8684.1 | 8453.9 | 10094.2 | 9609.4 | 31.9187 | 32.0467 | 32.076 | 0 | 33.16 | 31.8144 | 0 | 40.287 | 0 | 0 | 0 | 0 | 7.5576 | 7.7092 | 7.8238 | 0 | 2.68 | 7.4071 | 11.3833 | 11.705 | 12.645 | 0 | 8.48 | 11.1467 | 5.4961 | 5.269 | 5.4277 | 0 | 6.42 | 5.571 | 0.60691 | 1.2903 | 1.106 | 0 | 1.02 | 1.0708 | 5.3158 | 5.1678 | 5.1525 | 0 | 6.1 | 5.4774 | 1.0039 | 1.3541 | 1.189 | 0 | 1.22 | 1.159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71463 | 124 | 63592 | 112 | 134482 | 366 | 5.4961 | 5.269 | 5.4277 | 0 | 6.42 | 5.571 | 5.3158 | 5.1678 | 5.1525 | 0 | 6.1 | 5.4774 | 762000 | 1000 | 757000 | 2000 | 1513000 | 4000 | 1516000 | 1509000 | 13.4833 | 5.6368 | 1.0188 | 5.4427 | 1.1852 | 18.07% | 21.78% | 32.2032 | 40.287 | 6.6356 | 11.072 | 1525792.4 | 1513933 | 1830441.5432 | 82.71%
2022-07-22 | 2023 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 331394.22 | 6:07 | 19:36 | 8736.1 | 9559.2 | 9391.6 | 9302.2 | 9295.1 | 9432.7 | 9452 | 9674.2 | 9543.6 | 9653 | 9354 | 9569.1 | 9482.6 | 9319 | 8908.8 | 9135.5 | 8216.6 | 9322.6 | 9431.9 | 9323.5 | 9303 | 9124.6 | 9364.3 | 9386.2 | 9254.1 | 8139 | 9212.1 | 9169 | 9116.3 | 9365.2 | 9156.5 | 9441.1 | 9182.3 | 8760.7 | 8627.7 | 9112.2 | 9368.1 | 9089.7 | 9325.4 | 8902.3 | 9738.6 | 8550.2 | 9499.2 | 7398.3 | 8798.7 | 10013.3 | 7253.7 | 10775.9 | 6669.1 | 5367.9 | 6281.2 | 6099.3 | 6498.3 | 5935.3 | 6703 | 6168.3 | 8803.6 | 9821.6 | 8850.8 | 9925.4 | 9960.4 | 8792.2 | 11051.8 | 8305 | 9491.4 | 9113 | 10421.1 | 8983.1 | 9618.4 | 9130.3 | 9786.3 | 8921.1 | 9116.4 | 9478.3 | 8896 | 10169.7 | 9047.7 | 9953 | 8819.4 | 10092.5 | 7986.87 | 8884.2 | 7153.8 | 8946.23 | 8840.12 | 6834.91 | 7989.68 | 6574.28 | 8105.9 | 9518.5 | 8763.6 | 9629.6 | 9692.6 | 9054.2 | 8964.6 | 9696.2 | 9902 | 8313.9 | 10033.9 | 8930.4 | 9938.2 | 8884.6 | 9804.8 | 9138.7 | 9690.2 | 7612.6 | 9950.2 | 8579.2 | 9608.4 | 8677.4 | 9886.2 | 9215.6 | 8855.7 | 9729.9 | 6586.2 | 10468.7 | 9962.8 | 9665.2 | 10466.5 | 7885.1 | 9892.8 | 8830.5 | 9450.7 | 8929.5 | 9439.4 | 8398.1 | 9556.7 | 8808.7 | 8871.7 | 8810.9 | 8849.6 | 7693.6 | 7731.6 | 7787.2 | 8729.3 | 8560.7 | 10001.4 | 8687 | 6378.2 | 8567.9 | 9907.7 | 8798.3 | 9850.1 | 7608.8 | 9781.5 | 10136.4 | 9504.7 | 10031.3 | 9766.4 | 9805.7 | 9073.8 | 10071.7 | 10014.7 | 9973.5 | 9228.4 | 9558.6 | 9201.8 | 8030.6 | 9572.2 | 9073.4 | 31.9878 | 32.1901 | 32.25 | 0 | 31.9525 | 32.3874 | 0 | 41.5999 | 0 | 0 | 0 | 0 | 5.4772 | 5.5385 | 5.6489 | 0 | 5.4376 | 5.454 | 9.1083 | 9.0933 | 9.6033 | 0 | 9.175 | 8.9533 | 5.2459 | 4.9658 | 5.0652 | 0 | 5.4539 | 4.6634 | 0.55327 | 1.2074 | 1.1113 | 0 | 0.95148 | 1.1319 | 5.0848 | 4.8694 | 4.8691 | 0 | 5.2323 | 5.5002 | 1.1072 | 1.2641 | 1.1774 | 0 | 1.034 | 1.2138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72177 | 126 | 64316 | 113 | 135915 | 370 | 5.2459 | 4.9658 | 5.0652 | 0 | 5.4539 | 4.6634 | 5.0848 | 4.8694 | 4.8691 | 0 | 5.2323 | 5.5002 | 714000 | 2000 | 724000 | 1000 | 1433000 | 4000 | 1435000 | 1429000 | 13.4833 | 5.0788 | 0.99108 | 5.1112 | 1.1593 | 19.51% | 22.68% | 32.1535 | 41.5999 | 5.5112 | 9.1867 | 1438188.69 | 1434013 | 1716401.3882 | 83.55%
2022-07-23 | 2023 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 331394.22 | 6:13 | 18:58 | 5443.6 | 6127.9 | 6078.1 | 5990.8 | 5997.1 | 6143.43 | 6147 | 6338.51 | 6090.27 | 6073.8 | 6114.1 | 6205.4 | 6231.9 | 6138.34 | 5730.7 | 5931.44 | 5248.49 | 5983.3 | 6121.27 | 6056.1 | 6084.1 | 5987.6 | 6064.8 | 6091.6 | 6051.7 | 5303.7 | 6054.2 | 5971.4 | 5823.22 | 5526.1 | 5926.2 | 6141.3 | 5956.3 | 5655.3 | 5593.4 | 5868.2 | 6083.1 | 5889.5 | 6065.1 | 5743.2 | 6483.4 | 5665.4 | 6364.79 | 4889 | 5820.9 | 6532.08 | 4625 | 7190.5 | 6361.2 | 4990.8 | 6060.6 | 5842 | 6457.6 | 5783.43 | 6484.7 | 5788.31 | 5657.7 | 6390.2 | 5779.08 | 6503.3 | 6482.4 | 5678.8 | 7302.8 | 5252.4 | 6034.5 | 5759.6 | 6808.4 | 5616.9 | 6491.8 | 5749.1 | 6269.9 | 5666.4 | 5801.9 | 6412.1 | 5738.4 | 6588.9 | 5744.3 | 6504.7 | 5595.9 | 6510.5 | 5197.2 | 2598.2 | 5024.1 | 6388.1 | 6255.3 | 4082.1 | 5512.1 | 4437.1 | 4964.3 | 4674.3 | 5568 | 6174.9 | 6282.3 | 5844.4 | 5790.9 | 6299.1 | 6407.7 | 5218.2 | 6445.8 | 5603.5 | 6451.1 | 5621.3 | 6305.7 | 5787.33 | 6284.6 | 5202.4 | 6376.7 | 5374.6 | 6147 | 5346.47 | 6288.7 | 5755.01 | 5463.65 | 6054.3 | 4014 | 6558.7 | 6349.5 | 6121.2 | 6758.5 | 4935.9 | 6332.2 | 5557.8 | 5950.2 | 5566.6 | 5925.5 | 5249.9 | 6088.3 | 5567.6 | 5710.3 | 5734.6 | 5625.8 | 4872.6 | 5661.1 | 4937.8 | 5599.8 | 5511.7 | 6683.3 | 5665.5 | 4503.6 | 5486.8 | 6506.1 | 5714.7 | 6445.6 | 4893.7 | 6445.7 | 6726.6 | 6253.5 | 6642.8 | 6455.9 | 6521.6 | 5927.4 | 6669.1 | 6609.4 | 6606.4 | 5753.7 | 6321 | 6603 | 5238.4 | 6336.4 | 5948.9 | 27.1389 | 28.5218 | 28.4902 | 0 | 28.4365 | 28.5963 | 0 | 35.8596 | 0 | 0 | 0 | 0 | 3.0278 | 3.1063 | 3.0057 | 0 | 3.0508 | 2.9095 | 5.4933 | 5.4233 | 5.4383 | 0 | 5.7267 | 5.455 | 3.198 | 3.1111 | 3.1401 | 0 | 3.1854 | 2.9044 | 0.1864 | 0.41213 | 0.43256 | 0 | 0.43841 | 0.54897 | 3.107 | 3.0714 | 2.9974 | 0 | 3.0789 | 3.4247 | 0.4281 | 0.45066 | 0.45745 | 0 | 0.47939 | 0.53865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72655 | 127 | 64777 | 115 | 136850 | 375 | 3.198 | 3.1111 | 3.1401 | 0 | 3.1854 | 2.9044 | 3.107 | 3.0714 | 2.9974 | 0 | 3.0789 | 3.4247 | 478000 | 1000 | 461000 | 2000 | 935000 | 5000 | 936000 | 930000 | 12.75 | 3.1078 | 0.40369 | 3.1359 | 0.47085 | 12.99% | 15.01% | 28.2367 | 35.8596 | 3.02 | 5.5073 | 942566.42 | 935000 | 1066218.2938 | 87.69%
2022-07-24 | 2023 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 331394.22 | 6:09 | 19:28 | 9702.5 | 10658.1 | 10596.2 | 10504.6 | 10484 | 10659.7 | 10709.1 | 11029.1 | 10661.9 | 10591.9 | 10725.6 | 10824.6 | 10956.1 | 10770.2 | 10404.1 | 10629.5 | 9682.9 | 10849.1 | 11087.37 | 10979.5 | 10997.4 | 10850.6 | 10767.7 | 10935.3 | 10613.4 | 9501 | 10883.4 | 10719 | 10685.7 | 10721.1 | 10584.89 | 10821.94 | 9095.27 | 8611.5 | 8434 | 8851.97 | 9161.2 | 8966 | 9175.5 | 8815.6 | 11717 | 10546.1 | 11461.5 | 9126.4 | 10654 | 11612.4 | 8694.6 | 12598.9 | 10699.01 | 8613.6 | 10383.6 | 10047.3 | 10870.82 | 9984.6 | 10787.1 | 9858.6 | 10044.2 | 11007.6 | 10354.2 | 11327.1 | 11288.3 | 10158.33 | 12272 | 9459.9 | 10388.43 | 9955.7 | 11388.1 | 9709.1 | 11000.3 | 9849.54 | 10719.2 | 9642.6 | 10133.7 | 10941.8 | 9799.84 | 11267 | 10007.7 | 10869.6 | 9799.1 | 10892.2 | 9542.7 | 9658.1 | 8520.5 | 10882 | 10661.7 | 6994.73 | 9688.1 | 7765.5 | 8996.7 | 10169.6 | 9701.1 | 10626.97 | 10805.27 | 10235.3 | 10209.8 | 10831.7 | 11108.99 | 9348.4 | 11227.4 | 10100.7 | 11271 | 10078.4 | 11062.2 | 10342.6 | 11130.8 | 9867 | 11160.2 | 9746.7 | 10877.59 | 9705.1 | 11078.7 | 10323.8 | 9800.1 | 10611.86 | 7266.2 | 11350.4 | 11080 | 10743.2 | 11652.67 | 8957.2 | 10991.14 | 9973.6 | 10565.8 | 10033.2 | 10520.25 | 9516.4 | 10731.17 | 10039.59 | 10169.48 | 10177 | 10103.9 | 8830.1 | 10107.9 | 8841.3 | 9774.7 | 9624.5 | 11115.47 | 9736.7 | 9668.1 | 9788.6 | 11033.4 | 9989 | 10994.34 | 8568.4 | 10820.56 | 11110.7 | 10456.3 | 10980.7 | 10773.4 | 10905.3 | 10015.3 | 11042.7 | 10932.56 | 10892.9 | 10434.83 | 10579.5 | 11083.7 | 8178.4 | 10592 | 9993.1 | 30.7545 | 30.6695 | 30.2679 | 0 | 30.424 | 30.7505 | 0 | 42.9694 | 0 | 0 | 0 | 0 | 3.6837 | 3.6191 | 3.698 | 0 | 3.746 | 3.4958 | 7.4783 | 7.0767 | 7.455 | 0 | 6.98 | 7 | 6.1738 | 6.01 | 6.2846 | 0 | 5.7741 | 5.2685 | 0.47795 | 0.94047 | 1.1687 | 0 | 1.0824 | 1.1023 | 6.0206 | 5.8644 | 6.0092 | 0 | 5.6217 | 6.2239 | 0.94489 | 1.0625 | 1.2264 | 0 | 1.1419 | 1.1549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73483 | 129 | 65588 | 117 | 138483 | 379 | 6.1738 | 6.01 | 6.2846 | 0 | 5.7741 | 5.2685 | 6.0206 | 5.8644 | 6.0092 | 0 | 5.6217 | 6.2239 | 828000 | 2000 | 811000 | 2000 | 1633000 | 4000 | 1635000 | 1629000 | 13.3167 | 5.9022 | 0.95435 | 5.948 | 1.1061 | 16.17% | 18.6% | 30.5733 | 42.9694 | 3.6485 | 7.198 | 1646496.58 | 1633867 | 1985081.012 | 82.31%
2022-07-25 | 2023 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 331394.22 | 6:13 | 19:33 | 8623.18 | 9403.01 | 9387.38 | 9295.93 | 9282.75 | 9500.05 | 9448.8 | 9744 | 9360.65 | 9480.28 | 9367.85 | 9446.17 | 9654.37 | 9423.76 | 9190.88 | 9387.55 | 8684.18 | 9646.88 | 9811.88 | 9713.85 | 9644.82 | 9499.98 | 9536.18 | 9676.05 | 9689.75 | 8658.57 | 9587.35 | 9645.19 | 9682.03 | 9606.95 | 9453.55 | 9804.38 | 9492.11 | 9143.28 | 9107.77 | 9444.47 | 9706.72 | 9429.36 | 9619.45 | 9186.62 | 10322.91 | 9259.75 | 10205.24 | 9186.13 | 9536.58 | 10385.55 | 7755.84 | 11096.39 | 9756.16 | 7926.1 | 9548.18 | 9221.68 | 9980.32 | 9149.9 | 9979.06 | 9187.98 | 8815.32 | 8942.74 | 8914.12 | 9868.67 | 9764.31 | 8742.8 | 10752.95 | 8235.5 | 9374.88 | 8961.28 | 10265.47 | 8708.73 | 9830.92 | 8772.18 | 9666.65 | 8614.82 | 8890.98 | 9696.86 | 8768.08 | 9878.59 | 8835.87 | 9746.58 | 8632.95 | 9760 | 8530.47 | 8682.52 | 7740.51 | 9833.85 | 9666.67 | 6404.38 | 8759.61 | 7120.92 | 8326.9 | 9219.73 | 8952.46 | 9901.82 | 9913.04 | 9344.82 | 9253.55 | 9881.73 | 9941.23 | 8322.24 | 9960.68 | 8874.88 | 10017.29 | 8902.6 | 9917.9 | 9188.78 | 10089.92 | 8887.14 | 10149.34 | 8852.89 | 9858.18 | 8840.97 | 10019.38 | 9408.92 | 8643.83 | 9493.35 | 6588.7 | 10227.53 | 10032.22 | 9715.78 | 10743.98 | 8086.12 | 10085.22 | 9055.02 | 9661.32 | 9191.92 | 9586.25 | 8768.67 | 9795.33 | 9127.37 | 9227.25 | 9236.79 | 9193.84 | 8136.31 | 9019.29 | 7927.72 | 8689.98 | 8603.68 | 9987.54 | 8803.21 | 8900.6 | 8816.26 | 9940.81 | 8924.64 | 9891.56 | 7824.4 | 9457 | 9746.87 | 9206.99 | 9710.93 | 9578.78 | 9712.15 | 8894.15 | 9790.08 | 9563.08 | 9561.98 | 9299.95 | 9215.98 | 9693.84 | 7719.49 | 9259.98 | 8739.02 | 28.8335 | 29.2775 | 29.3179 | 0 | 29.1735 | 29.3429 | 0 | 40.1075 | 0 | 0 | 0 | 0 | 3.9736 | 4.593 | 3.6766 | 0 | 4.4068 | 3.8752 | 7.6033 | 8.515 | 7.275 | 0 | 7.7883 | 7.5983 | 5.2735 | 5.4476 | 5.4391 | 0 | 5.3397 | 4.559 | 0.88478 | 1.1735 | 1.0762 | 0 | 1.0937 | 1.0716 | 5.1753 | 5.421 | 5.2502 | 0 | 5.3417 | 5.3285 | 0.86633 | 1.2533 | 1.1311 | 0 | 1.1536 | 1.1571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74233 | 130 | 66319 | 118 | 139957 | 384 | 5.2735 | 5.4476 | 5.4391 | 0 | 5.3397 | 4.559 | 5.1753 | 5.421 | 5.2502 | 0 | 5.3417 | 5.3285 | 750000 | 1000 | 731000 | 1000 | 1474000 | 5000 | 1479000 | 1469000 | 13.3333 | 5.2118 | 1.06 | 5.3034 | 1.1123 | 20.34% | 20.97% | 29.189 | 40.1075 | 4.105 | 7.756 | 1486249.08 | 1474788 | 1787965.7641 | 82.48%
2022-07-26 | 2023 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 331394.22 | 6:27 | 19:12 | 2347.8 | 2648.3 | 2670.5 | 2632.4 | 2634.1 | 2690.5 | 2678.1 | 2763 | 2615.3 | 2617.3 | 2618.2 | 2659.3 | 2692.9 | 2632.1 | 2526.3 | 2593 | 2305.8 | 2646.7 | 2709 | 2685.9 | 2662.6 | 2606.5 | 2647.5 | 2675.5 | 2639.1 | 2288 | 2625.5 | 2623.7 | 2656 | 2673.5 | 2638.4 | 2717.6 | 2602 | 2462.7 | 2432.6 | 2563.5 | 2671.4 | 2597.5 | 2682.2 | 2522.8 | 3032.1 | 2672.5 | 2975.4 | 2638 | 2711.8 | 3036.7 | 2118.3 | 3359.3 | 2739.1 | 2122.3 | 2646.4 | 2524 | 2803.7 | 2503.9 | 2798.9 | 2497.8 | 2393.7 | 2749.8 | 2475.2 | 2790.2 | 2770.4 | 2424.3 | 3135.1 | 2205.1 | 2578.6 | 2458.8 | 2919.9 | 2387.9 | 2778.6 | 2430.4 | 2733.8 | 2383.3 | 2437.6 | 2701.3 | 2396 | 2804 | 2445.2 | 2738.8 | 2383 | 2754 | 2353 | 2488.2 | 2109 | 2751.4 | 2719.9 | 1853.8 | 2380.4 | 1911.4 | 2199.4 | 2533.4 | 2380.4 | 2719.3 | 2720.8 | 2536.5 | 2526.9 | 2744.2 | 2728.4 | 2252 | 2820.6 | 2447.8 | 2849.3 | 2450.4 | 2794.6 | 2543.6 | 2841.4 | 2412 | 2847.7 | 2392.5 | 2759.6 | 2401 | 2845.9 | 2604.9 | 2299 | 2570.7 | 1764.5 | 2911.4 | 2742.6 | 2625 | 3098.9 | 2102.5 | 2826 | 2460.2 | 2664.7 | 2508.7 | 2672.5 | 2357.6 | 2708.4 | 2484 | 2512.5 | 2528.2 | 2508 | 2163.9 | 2446.7 | 2133 | 2346.5 | 2301.5 | 2765.2 | 2330.4 | 2673.5 | 2324.9 | 2720.5 | 2348.6 | 2675.3 | 2048.2 | 2592.5 | 2716 | 2537.2 | 2698.4 | 2637.4 | 2679.5 | 2424.3 | 2715.3 | 2658.7 | 2652.5 | 2550.2 | 2515.3 | 2692.5 | 2069.9 | 2555.4 | 2370.5 | 27.3426 | 27.3993 | 27.2786 | 0 | 27.5131 | 27.3748 | 0 | 29.2241 | 0 | 0 | 0 | 0 | 4.2326 | 4.2091 | 4.1684 | 0 | 4.3236 | 4.107 | 7.135 | 6.7317 | 6.6133 | 0 | 7.08 | 6.7317 | 1.3125 | 1.2986 | 1.3764 | 0 | 1.3163 | 1.1098 | 0.19093 | 0.21441 | 0.23376 | 0 | 0.2239 | 0.22747 | 1.2563 | 1.2657 | 1.2989 | 0 | 1.2721 | 1.3301 | 0.19113 | 0.23171 | 0.25443 | 0 | 0.24128 | 0.24193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74442 | 131 | 66519 | 120 | 140364 | 388 | 1.3125 | 1.2986 | 1.3764 | 0 | 1.3163 | 1.1098 | 1.2563 | 1.2657 | 1.2989 | 0 | 1.2721 | 1.3301 | 209000 | 1000 | 200000 | 2000 | 407000 | 4000 | 406000 | 403000 | 12.75 | 1.2827 | 0.21809 | 1.2846 | 0.2321 | 17% | 18.07% | 27.3817 | 29.2241 | 4.2082 | 6.8583 | 411419.2 | 406933 | 448048.0129 | 90.82%
2022-07-27 | 2023 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 331394.22 | 7:08 | 19:31 | 2636.2 | 2950.3 | 2942.4 | 2896.5 | 2903.5 | 2969.7 | 2975.4 | 3057.2 | 2912.8 | 2955.3 | 2899.7 | 2953.2 | 2957.5 | 2908.6 | 2727.7 | 2822.5 | 2380.4 | 2812.9 | 2851.4 | 2872.6 | 2862.7 | 2813.6 | 2850.5 | 2862.5 | 2838.6 | 2481.6 | 2844.8 | 2822.8 | 2819.4 | 2818.5 | 2763 | 2885.8 | 2796.2 | 2766.9 | 2615.4 | 2747.9 | 2853.8 | 2758.4 | 2838.9 | 2679 | 3045.9 | 2666.3 | 2985.5 | 2614.9 | 2730.8 | 3083.3 | 2149.1 | 3403.1 | 3020.8 | 2348.8 | 2906.7 | 2785.1 | 3063.6 | 2735.2 | 3090.8 | 2740.4 | 2679 | 3047.2 | 2738.7 | 3100.6 | 3089.5 | 2693.7 | 3479.5 | 2456.2 | 2836.8 | 2716.6 | 3220.2 | 2655.5 | 3067.2 | 2708.7 | 3028.1 | 2666.7 | 2707.1 | 2998.4 | 2667.5 | 3110.6 | 2710.6 | 3057.7 | 2632.6 | 3069.7 | 2632.8 | 2786.1 | 2356.8 | 3072.5 | 3053.4 | 2234.3 | 2642.1 | 2135.3 | 2410.6 | 2790.1 | 2605.5 | 2988.4 | 2961.3 | 2745 | 2719.8 | 3019.8 | 2913.6 | 2428.5 | 2995.5 | 2556.7 | 3044.1 | 2614 | 2967.5 | 2703.2 | 2999.6 | 2557.2 | 3002.4 | 2526.8 | 2896.8 | 2519.1 | 2974.5 | 2728.4 | 2464.8 | 2745.5 | 1873.3 | 3099.4 | 1392.8 | 2348.7 | 3225.3 | 2225.5 | 2976.9 | 2587.6 | 2802.8 | 2630 | 2795 | 2463.8 | 2780.7 | 2605.8 | 2654.3 | 2674.4 | 2634.8 | 2285.3 | 2587.4 | 2255.9 | 2523.8 | 2434 | 3020.7 | 2537.7 | 2938.2 | 2542.1 | 2962.8 | 2564.5 | 2909.8 | 2232.2 | 2860.7 | 3005.8 | 2778.8 | 2965.4 | 2887.7 | 2934 | 2667.9 | 2994 | 2931.9 | 2931.9 | 2829.2 | 2786.2 | 2978.1 | 2291.3 | 2802.6 | 2611.5 | 27.3707 | 27.2978 | 27.1145 | 0 | 27.2711 | 27.3338 | 0 | 29.8021 | 0 | 0 | 0 | 0 | 4.2002 | 4.1534 | 4.187 | 0 | 4.1308 | 3.9324 | 7.19 | 7.2683 | 7.3867 | 0 | 6.6733 | 6.3417 | 1.5022 | 1.4479 | 1.4564 | 0 | 1.4522 | 1.2678 | 0.19619 | 0.21085 | 0.19759 | 0 | 0.22346 | 0.19097 | 1.4297 | 1.4257 | 1.3684 | 0 | 1.4379 | 1.4858 | 0.18705 | 0.22541 | 0.20618 | 0 | 0.23575 | 0.2314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74668 | 133 | 66734 | 121 | 140803 | 393 | 1.5022 | 1.4479 | 1.4564 | 0 | 1.4522 | 1.2678 | 1.4297 | 1.4257 | 1.3684 | 0 | 1.4379 | 1.4858 | 226000 | 2000 | 215000 | 1000 | 439000 | 5000 | 438000 | 434000 | 12.3833 | 1.4253 | 0.20381 | 1.4295 | 0.21716 | 14.3% | 15.19% | 27.2776 | 29.8021 | 4.1207 | 6.972 | 443229.3 | 438533 | 500821.8488 | 87.56%
2022-07-28 | 2023 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 331394.22 | 6:10 | 19:31 | 6947 | 7839.8 | 7922.5 | 7792 | 7820.9 | 7976.89 | 7933.4 | 8149.49 | 7704.4 | 7714.36 | 7741.38 | 7822.6 | 7943.9 | 7767 | 7397 | 7610.79 | 6536.3 | 7621.4 | 7711.64 | 7759.9 | 7741.55 | 7611.3 | 7696.97 | 7737.8 | 7661.13 | 6712.2 | 7688.4 | 7650.2 | 7672.9 | 7670.3 | 7568.7 | 7822.68 | 7653.78 | 7752.5 | 7590.56 | 7688.3 | 7761.2 | 7569.2 | 7717 | 7300.6 | 8411.35 | 7442.1 | 8262.77 | 7355.73 | 7619 | 8499.2 | 6035.5 | 9276.6 | 8024.38 | 6272.3 | 7781.1 | 7416.4 | 8191.15 | 7379.89 | 8140.5 | 7310.2 | 7064.3 | 8002.28 | 7273.7 | 8128.81 | 8077.7 | 7128.78 | 8987.7 | 6529.5 | 7499.8 | 7099.29 | 8392.56 | 6856.7 | 8040.7 | 6991.5 | 7879.2 | 6859.02 | 7103.81 | 7795.8 | 6943.6 | 8102.8 | 7139 | 7854.4 | 6957.4 | 7936.34 | 6744.5 | 7130.4 | 6044.59 | 7834.1 | 7776 | 5733.1 | 6843.7 | 5515.6 | 6330.87 | 7239.3 | 6854.3 | 7861.75 | 7803.01 | 7277 | 7237 | 7965.1 | 7926.5 | 6440.08 | 7981.68 | 6860.2 | 8048.2 | 7021.6 | 7893.5 | 7262.25 | 7987.88 | 6869.68 | 7998 | 6780.4 | 7742.75 | 6767 | 7939.12 | 7289.8 | 6527.3 | 7277 | 5043.5 | 8222.57 | 7423.88 | 7412.14 | 8634.2 | 5954.3 | 7930.8 | 6945.7 | 7430.9 | 7073.8 | 7515.2 | 6622 | 7457.15 | 7016.8 | 7105.36 | 7150.23 | 7087.14 | 6134.9 | 6952.8 | 6044.3 | 6778.8 | 6640.34 | 7962.2 | 6773 | 7809.84 | 6798.35 | 7858.2 | 6845.2 | 7731.6 | 5974.57 | 7618.44 | 7971.4 | 7444.3 | 7902.4 | 7672.6 | 7769.82 | 7139.2 | 7960.5 | 7782.7 | 7781.2 | 7543 | 7441.6 | 7918.9 | 6137.5 | 7471.8 | 7002.8 | 28.9101 | 28.8559 | 28.7706 | 0 | 28.6952 | 28.9174 | 0 | 35.7288 | 0 | 0 | 0 | 0 | 6.0503 | 6.0786 | 6.1434 | 0 | 5.5819 | 5.9359 | 9.0667 | 9.1417 | 9.28 | 0 | 8.8233 | 9.19 | 4.1957 | 4.0902 | 4.2085 | 0 | 4.0857 | 3.5525 | 0.55823 | 0.76303 | 0.65827 | 0 | 0.797 | 0.76097 | 4.008 | 4.0156 | 3.9428 | 0 | 3.9983 | 4.1821 | 0.53338 | 0.83097 | 0.72132 | 0 | 0.83911 | 0.9035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75276 | 134 | 67309 | 123 | 141981 | 397 | 4.1957 | 4.0902 | 4.2085 | 0 | 4.0857 | 3.5525 | 4.008 | 4.0156 | 3.9428 | 0 | 3.9983 | 4.1821 | 608000 | 1000 | 575000 | 2000 | 1178000 | 4000 | 1180000 | 1174000 | 13.35 | 4.0265 | 0.7075 | 4.0294 | 0.76566 | 17.57% | 19% | 28.8298 | 35.7288 | 5.958 | 9.1003 | 1187733.97 | 1179400 | 1382788.999 | 85.29%
2022-07-29 | 2023 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 331394.22 | 6:10 | 19:28 | 9918.5 | 10778.4 | 10879.9 | 10747.9 | 10789 | 10933.6 | 10854.2 | 11103.7 | 10678 | 10744.1 | 10608.9 | 10700.9 | 10915.8 | 10657.6 | 10355.5 | 10570.9 | 9325.1 | 10498.1 | 10628.1 | 10735.8 | 10724.2 | 10593.3 | 10633.7 | 10646.1 | 10630.2 | 9568.2 | 10616 | 10606.3 | 10581.8 | 10445.1 | 10352.8 | 10724.2 | 10559.9 | 10657.7 | 10707.8 | 10709.2 | 10760 | 10552.8 | 10556.8 | 10523.6 | 11148.6 | 10202.1 | 10979.4 | 10107.5 | 10423.8 | 11148.1 | 8490.5 | 11872.3 | 10903.6 | 8852.1 | 10673.9 | 10258.3 | 11127.8 | 10295 | 10978.8 | 10190.3 | 9821.4 | 10840.9 | 10031.9 | 10958.5 | 10957.6 | 9917.1 | 11946.3 | 9355.8 | 10362.8 | 9916.4 | 11308.6 | 9699.3 | 10955.9 | 9861.9 | 10776.8 | 9700.9 | 10037.2 | 10773.6 | 9840.6 | 11052.6 | 10021.3 | 10787.9 | 9755.2 | 10889.8 | 9581.9 | 10001.7 | 8723.3 | 10797.5 | 10720.1 | 8311.9 | 9630.4 | 7953.1 | 8963.5 | 10089.4 | 9566.5 | 10655.7 | 10573.6 | 10067.7 | 10052.5 | 10719.5 | 10697.5 | 8994.6 | 10700.6 | 9503.5 | 10861 | 9703.9 | 10723.9 | 9986.2 | 10824.9 | 9603.5 | 10877.9 | 9495 | 10750.8 | 9888.3 | 10723.9 | 10116.4 | 9043.9 | 9929.5 | 7092.5 | 10792.8 | 10143.6 | 10050.5 | 11399.7 | 8278.8 | 10651.8 | 9626.4 | 10175.2 | 9804.8 | 10349.2 | 9337.9 | 10213.9 | 9689.8 | 9692.6 | 9762.8 | 9773.5 | 8590.2 | 9533.4 | 8447.1 | 9225 | 9118.9 | 10533.2 | 9361.1 | 10401.9 | 9321.9 | 10384.7 | 9322.8 | 10333.4 | 8293.5 | 10272.5 | 10535.9 | 9997.5 | 10503 | 10308.5 | 10392.2 | 9634 | 10525.5 | 10474.9 | 10450.6 | 10276 | 10135.8 | 10615 | 8526.3 | 10049.7 | 9556.5 | 30.1128 | 30.3622 | 30.4112 | 0 | 30.0094 | 30.4583 | 0 | 40.9715 | 0 | 0 | 0 | 0 | 6.5181 | 6.5045 | 6.4839 | 0 | 6.0937 | 6.4012 | 10.13 | 9.925 | 10.4117 | 0 | 9.7167 | 9.735 | 6.1588 | 5.9933 | 6.0653 | 0 | 5.8021 | 4.9682 | 1.1789 | 1.2582 | 1.3094 | 0 | 1.1702 | 1.1191 | 6.037 | 5.9809 | 5.9069 | 0 | 5.6758 | 5.8389 | 1.1413 | 1.3183 | 1.3527 | 0 | 1.2246 | 1.3613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76113 | 136 | 68096 | 124 | 143599 | 401 | 6.1588 | 5.9933 | 6.0653 | 0 | 5.8021 | 4.9682 | 6.037 | 5.9809 | 5.9069 | 0 | 5.6758 | 5.8389 | 837000 | 2000 | 787000 | 1000 | 1618000 | 4000 | 1621000 | 1614000 | 13.3 | 5.7975 | 1.2072 | 5.8879 | 1.2796 | 20.82% | 21.73% | 30.2708 | 40.9715 | 6.4003 | 9.9837 | 1631586.5 | 1618667 | 1984934.1856 | 81.55%
2022-07-30 | 2023 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 331394.22 | 6:10 | 19:21 | 9101.05 | 9932.07 | 9946.82 | 9814.62 | 9888.35 | 10032.4 | 9950.37 | 10214.94 | 9855.45 | 9843.26 | 9833.63 | 9951.26 | 10036.78 | 9832.19 | 9554.14 | 9766.18 | 8450.47 | 9559.23 | 9675.76 | 9743.11 | 9765.38 | 9694.13 | 9780.63 | 9748.1 | 9610.33 | 8696.87 | 9638.52 | 9652.22 | 9589.15 | 9438.45 | 9329.94 | 9674.44 | 9408.15 | 9588.3 | 9689.42 | 9642.23 | 9624.97 | 9419.96 | 9441.91 | 9315.33 | 10121.03 | 9197.29 | 9866.73 | 9025.34 | 9301.19 | 10044.16 | 7550.22 | 10725.03 | 10030.35 | 8282.61 | 9762.6 | 9460.76 | 10097.28 | 9387.8 | 10153.46 | 9405.15 | 9159.79 | 10040.23 | 9390.37 | 10184.22 | 10140.97 | 8748.86 | 11001.51 | 8729.65 | 9562.46 | 9144.48 | 10488.39 | 9001.84 | 10166.72 | 9210.64 | 10037.18 | 9075.51 | 9445.1 | 10181.15 | 9272.82 | 10317.39 | 9326.28 | 10113.09 | 9059.41 | 10169.12 | 8939.15 | 9368.87 | 8103.83 | 10079.01 | 9978.42 | 7706.15 | 8920.41 | 7368.02 | 8233.12 | 9257.02 | 8747.44 | 9771.02 | 9624.83 | 9042.09 | 9021.73 | 9671.79 | 9663.5 | 7335.14 | 9704.04 | 8704.51 | 9823.83 | 8839.94 | 9724 | 9085.18 | 9780.61 | 8752.64 | 9810.39 | 8634.47 | 9702.15 | 8934.56 | 9708.02 | 9138.53 | 8206.16 | 9099.02 | 6502.32 | 9769.83 | 8848.85 | 8987.33 | 10309.67 | 7032.65 | 9641.35 | 8760.24 | 9292.6 | 8934.03 | 9406.73 | 8428.21 | 9425.35 | 8729.81 | 8951.84 | 9092.89 | 8814.23 | 7854.37 | 8913.55 | 7903.72 | 8916.57 | 8947.19 | 10154.68 | 9111.07 | 10163.94 | 9255.08 | 10127.02 | 9225.06 | 10122.24 | 8322.78 | 9770.93 | 9933.15 | 9926.74 | 10036.03 | 9972.8 | 10079.41 | 9191.89 | 9983.29 | 10122.27 | 10100.1 | 9992.01 | 9852.45 | 10221.03 | 8276.3 | 9764.07 | 9280.68 | 30.0501 | 30.2684 | 30.2857 | 0 | 29.9567 | 30.4566 | 0 | 40.4587 | 0 | 0 | 0 | 0 | 6.3479 | 6.4439 | 6.4417 | 0 | 6.0323 | 6.5569 | 9.69 | 9.674 | 10.515 | 0 | 9.258 | 9.923 | 5.6195 | 5.4676 | 5.3033 | 0 | 5.321 | 4.8296 | 1.074 | 1.2277 | 1.0942 | 0 | 1.1478 | 1.1018 | 5.5316 | 5.4711 | 5.1511 | 0 | 5.343 | 5.6158 | 1.0315 | 1.2739 | 1.1266 | 0 | 1.1936 | 1.3569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76880 | 137 | 68828 | 126 | 145091 | 405 | 5.6195 | 5.4676 | 5.3033 | 0 | 5.321 | 4.8296 | 5.5316 | 5.4711 | 5.1511 | 0 | 5.343 | 5.6158 | 767000 | 1000 | 732000 | 2000 | 1492000 | 4000 | 1496000 | 1488000 | 13.1833 | 5.3082 | 1.1291 | 5.4225 | 1.1965 | 21.27% | 22.07% | 30.2035 | 40.4587 | 6.3645 | 9.812 | 1505036.63 | 1492800 | 1826934.9276 | 81.71%
2022-07-31 | 2023 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 331394.22 | 6:13 | 19:28 | 9819.3 | 10755.5 | 10839.2 | 10700.4 | 10761.55 | 10937.23 | 10859.11 | 11112.4 | 10612.94 | 10557 | 10707.1 | 10751.3 | 10986.62 | 10729.45 | 10404.1 | 10662.1 | 9532 | 10729.4 | 10776.43 | 10820.1 | 10753.98 | 10638.86 | 10715.8 | 10776 | 10679.46 | 9694.2 | 10716.5 | 10704.2 | 10730.43 | 10750.4 | 10660.5 | 10864.8 | 10684.76 | 10795.79 | 10860.69 | 10833.74 | 10886.42 | 10782.39 | 10847.4 | 10739.4 | 11116.58 | 10159 | 10981.6 | 10045.8 | 10398.3 | 11160.35 | 8350.2 | 11889.6 | 10959.68 | 8924.7 | 10740.72 | 10373.5 | 11224.9 | 10388.4 | 11080.7 | 10313.3 | 9978.69 | 10928.48 | 10187.1 | 11030.33 | 10940.26 | 8971.6 | 11842.9 | 9312.2 | 10469.2 | 10042.6 | 11342.98 | 9818.2 | 10968.7 | 9958.22 | 10821.8 | 9766.5 | 10066.35 | 10864.9 | 9894.5 | 11033.73 | 10020.25 | 10848.71 | 9774.3 | 10941.27 | 9690.54 | 10116.22 | 8793.32 | 10949.95 | 10919.89 | 8458.9 | 9802.4 | 8087.3 | 10555.7 | 10292.5 | 9915.54 | 11067.57 | 10958.1 | 10308.9 | 10246.29 | 10993.2 | 11013.67 | 9481.15 | 11073.8 | 9956.8 | 11033.77 | 10026.63 | 10928.72 | 10260 | 11125.25 | 9847.1 | 11198.07 | 9819.1 | 11115.6 | 10267 | 11078 | 10483.02 | 9451.15 | 10534.63 | 7304 | 11086.03 | 9994.28 | 10325.53 | 11633.57 | 8040 | 10983.78 | 10080 | 10741.6 | 10257.9 | 10773.9 | 9687.04 | 10865.96 | 10108.92 | 10242.37 | 10340.8 | 10226.4 | 9051.4 | 10119.36 | 8898.98 | 9624.69 | 9632.33 | 10976.34 | 9948.4 | 11091.02 | 10112.95 | 10962.31 | 9987.1 | 10901.29 | 8922.47 | 10879.9 | 11108.9 | 11007.2 | 11021.3 | 11014.2 | 11020.5 | 10268.8 | 11059.9 | 10856.66 | 10844.8 | 10620.31 | 10525.9 | 11001.43 | 8809.8 | 10542.43 | 10099.92 | 30.0142 | 30.5054 | 30.515 | 0 | 30.1086 | 30.6337 | 0 | 41.5605 | 0 | 0 | 0 | 0 | 6.7969 | 7.0324 | 7.0181 | 0 | 6.6369 | 7.051 | 10.26 | 9.9083 | 11.17 | 0 | 8.6967 | 10.0017 | 6.0946 | 6.0754 | 5.9167 | 0 | 6.0884 | 5.3983 | 1.2966 | 1.4224 | 1.2671 | 0 | 1.3613 | 1.2735 | 5.9636 | 6.0564 | 5.712 | 0 | 6.0512 | 6.3289 | 1.2339 | 1.4629 | 1.3065 | 0 | 1.4044 | 1.561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77721 | 138 | 69647 | 127 | 146745 | 409 | 6.0946 | 6.0754 | 5.9167 | 0 | 6.0884 | 5.3983 | 5.9636 | 6.0564 | 5.712 | 0 | 6.0512 | 6.3289 | 841000 | 1000 | 819000 | 1000 | 1654000 | 4000 | 1658000 | 1650000 | 13.25 | 5.9147 | 1.3242 | 6.0224 | 1.3938 | 22.39% | 23.14% | 30.3554 | 41.5605 | 6.9071 | 10.0073 | 1668552.5 | 1654533 | 2029726.9247 | 81.52%
2022-08-01 | 2023 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 331968 | 6:14 | 19:25 | 7009.56 | 7709.71 | 7641.88 | 7583.63 | 7523.01 | 7664.35 | 7677.75 | 7863.75 | 7649.8 | 7650.3 | 7601.24 | 7724.54 | 7717.15 | 7591.36 | 7177.97 | 7404.96 | 6391.8 | 7413.2 | 7480.97 | 7532.43 | 7499.08 | 7411.91 | 7505.83 | 7494.25 | 7430.94 | 6653.39 | 7494.56 | 7471.3 | 7451.29 | 7426.28 | 7351.2 | 7586.07 | 7464.74 | 7569.13 | 7599.35 | 7587.39 | 7610.89 | 7462.76 | 7499.13 | 7443.74 | 7912.4 | 7093.43 | 7821.66 | 7032.08 | 7348.95 | 8041.71 | 5803.87 | 8647.5 | 7803.34 | 6248.38 | 7557.39 | 7295.37 | 7933.33 | 7195.3 | 7929.45 | 7189.26 | 7116.99 | 7939.53 | 7212.71 | 8020.49 | 8019.63 | 6372.9 | 8938.41 | 6280.35 | 7593.32 | 7250.32 | 8389.6 | 7072.91 | 8064.56 | 7190.42 | 7943.21 | 7074.58 | 7248.04 | 7906.25 | 7141.84 | 8140.8 | 7261.12 | 7980.89 | 7053.72 | 8047.27 | 6997.61 | 7373.46 | 6378.37 | 8033.95 | 8005.4 | 6034.89 | 7078.28 | 5785.8 | 7601.91 | 7445.12 | 7006.35 | 7917.35 | 7743.94 | 7159.08 | 7104.08 | 7773.85 | 7825.73 | 6594.59 | 7868.78 | 6813.64 | 7863.88 | 6976.6 | 7725.06 | 7177.38 | 7801.4 | 6814.27 | 7817.54 | 6735.24 | 7747.94 | 7038.38 | 7788.39 | 7234.36 | 7113.49 | 7760.88 | 5210.86 | 8318.23 | 7231.85 | 7404.62 | 8281.22 | 5687.08 | 7463.37 | 6539.96 | 7495.16 | 7044.54 | 7477.8 | 6611.84 | 7402.15 | 6776.85 | 7179.65 | 7310.98 | 7095.97 | 6243.83 | 7184.25 | 6353.12 | 7246.98 | 7225.22 | 8204.58 | 7290.81 | 8256.48 | 7431.52 | 8211.35 | 7385.52 | 8240.6 | 6618.32 | 7975.16 | 8206.65 | 8146.75 | 8147.84 | 8140.15 | 8194.3 | 7479.32 | 8193.58 | 8122.31 | 8118.69 | 7961.91 | 7859.78 | 8258.72 | 6435.85 | 7762.85 | 7368.17 | 30.2085 | 30.2729 | 30.2933 | 0 | 30.0127 | 30.4435 | 0 | 38.4987 | 0 | 0 | 0 | 0 | 5.5272 | 5.7516 | 5.7073 | 0 | 5.3581 | 5.6951 | 9.735 | 9.064 | 9.555 | 0 | 9.002 | 8.994 | 4.1062 | 3.9271 | 3.939 | 0 | 3.9962 | 3.6811 | 0.90743 | 0.88443 | 0.86932 | 0 | 0.86169 | 0.83708 | 4.0206 | 3.9246 | 3.8396 | 0 | 3.9418 | 4.3145 | 0.87353 | 0.91803 | 0.90298 | 0 | 0.90089 | 1.0214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78319 | 139 | 70236 | 129 | 147928 | 413 | 4.1062 | 3.9271 | 3.939 | 0 | 3.9962 | 3.6811 | 4.0206 | 3.9246 | 3.8396 | 0 | 3.9418 | 4.3145 | 598000 | 1000 | 589000 | 2000 | 1183000 | 4000 | 1184000 | 1179000 | 13.1833 | 3.9299 | 0.87199 | 4.0082 | 0.92338 | 22.19% | 23.04% | 30.2462 | 38.4987 | 5.6079 | 9.27 | 1190069.6 | 1183067 | 1366885.8686 | 86.55%
2022-08-02 | 2023 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 331968 | 6:20 | 19:30 | 10869.2 | 11924 | 11897.7 | 11822.8 | 11686.4 | 11917.3 | 11912.1 | 12154.9 | 11834.3 | 11702.5 | 11787.6 | 11947.6 | 11964.5 | 11764.7 | 11160.1 | 11513 | 11136.9 | 11521.9 | 11569.7 | 11614.8 | 11666.9 | 11487.8 | 11651 | 11567.5 | 11565.6 | 10340 | 11636.8 | 11590.1 | 11527.5 | 11290.4 | 11166.9 | 11615.6 | 11340 | 11589.7 | 11807 | 11655.5 | 11624 | 11429.5 | 11389.7 | 11275.7 | 11776.3 | 10818.8 | 11692.4 | 10687.3 | 11119 | 12008.4 | 9196.1 | 12441.4 | 11937.6 | 9608.1 | 11690.2 | 11263.4 | 12240.1 | 11208.9 | 12101.7 | 11204.7 | 10900.2 | 12062.1 | 11133.7 | 12256.3 | 12308.8 | 10591 | 13285.6 | 9029.1 | 11578.4 | 11082.1 | 12622.6 | 10765.3 | 12259.1 | 10954.4 | 12089.8 | 10762.3 | 11097.8 | 11997.5 | 10952 | 12344 | 11164.4 | 12098.3 | 10834.6 | 12174.3 | 10570.5 | 11132.6 | 9528 | 12016.2 | 11903.3 | 9065.4 | 10775.1 | 8729.9 | 11577.3 | 11308.1 | 10563.4 | 10802.7 | 11961.5 | 11113.6 | 10929.2 | 11983.8 | 12058.6 | 10196.2 | 12120.8 | 10763 | 11779.9 | 10688.5 | 11660.3 | 11024.9 | 11711.2 | 10416.5 | 11747.3 | 10764.1 | 11614.9 | 10680.2 | 11701.6 | 11002.2 | 10964.9 | 11798.9 | 8244.1 | 12719.5 | 11775.9 | 11623.3 | 12510.5 | 9664.9 | 11778.6 | 10724.2 | 11406.4 | 10780 | 11406 | 10214.8 | 11611.2 | 10743.6 | 10962.1 | 11144.8 | 10957.5 | 9566.3 | 10950.1 | 9701.8 | 10778.4 | 10732.9 | 11661.2 | 10633.1 | 11762.2 | 10817.6 | 11922.8 | 10873 | 12032.5 | 9796.4 | 11649.6 | 11903.5 | 11752.4 | 11681.8 | 11539 | 11617.8 | 10678.8 | 11657.9 | 11708.6 | 11653.5 | 11397.1 | 11272.3 | 11792.5 | 9583.9 | 11384.8 | 10782.1 | 32.2578 | 32.2988 | 32.4109 | 0 | 32.0107 | 32.504 | 0 | 46.1116 | 0 | 0 | 0 | 0 | 4.2809 | 4.681 | 4.2186 | 0 | 4.4592 | 4.3671 | 8.142 | 7.472 | 7.386 | 0 | 7.371 | 7.881 | 6.7441 | 6.6049 | 6.3713 | 0 | 6.5547 | 5.696 | 1.4669 | 1.5173 | 1.3796 | 0 | 1.4173 | 1.2712 | 6.6225 | 6.6207 | 6.2078 | 0 | 6.4806 | 6.6751 | 1.3932 | 1.5496 | 1.4147 | 0 | 1.4586 | 1.5545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79235 | 141 | 71120 | 130 | 149720 | 417 | 6.7441 | 6.6049 | 6.3713 | 0 | 6.5547 | 5.696 | 6.6225 | 6.6207 | 6.2078 | 0 | 6.4806 | 6.6751 | 916000 | 2000 | 884000 | 1000 | 1792000 | 4000 | 1797000 | 1788000 | 13.1667 | 6.3942 | 1.4105 | 6.5213 | 1.4741 | 22.06% | 22.6% | 32.2964 | 46.1116 | 4.4014 | 7.6504 | 1808463.2 | 1793600 | 2154840.7761 | 83.24%
2022-08-03 | 2023 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 332378.2 | 6:15 | 19:40 | 10941.2 | 11892 | 11900.9 | 11897.3 | 11743.1 | 11780.8 | 11748.6 | 11998 | 11927.3 | 11946.9 | 11858.7 | 12036.9 | 11880.8 | 11815.7 | 11297.3 | 11705.1 | 11717.5 | 11902.3 | 11905.5 | 11874.8 | 11741.4 | 11532.9 | 11653.3 | 11679.2 | 12052.2 | 10654.3 | 11882.8 | 11925.4 | 12006.7 | 11979.7 | 11894.7 | 12314.1 | 12228.1 | 12427.7 | 12399.1 | 12370.3 | 12434 | 12249.5 | 12330 | 12206.9 | 12813 | 11824.5 | 12705.5 | 11708.2 | 12187 | 13199.3 | 10171.1 | 13577.4 | 12182.1 | 9833 | 11816.5 | 11678.5 | 12235 | 11086 | 12688.5 | 11639.5 | 11410.4 | 12669.9 | 11378.4 | 12694.7 | 12701.6 | 11283.8 | 13745.1 | 10639.8 | 12235.1 | 11701.6 | 13323.9 | 11313.9 | 12879.6 | 11530.4 | 12755.9 | 11247.8 | 11723 | 12664.9 | 11545.2 | 13004.1 | 11732 | 12774.4 | 11346.2 | 12798.2 | 11059 | 11828.7 | 10008.1 | 12688.7 | 12647.5 | 9546.8 | 11408.7 | 9220.5 | 12148.4 | 11886.7 | 11316.6 | 12811.4 | 12729.1 | 11851.3 | 11705.4 | 12726.1 | 13072.1 | 10953.3 | 13214.7 | 11861.5 | 12946.2 | 11680.5 | 12893.6 | 12153.8 | 12890.7 | 11494.2 | 12885.3 | 11977.5 | 12679.2 | 11609.5 | 12621.9 | 11951.4 | 11989.6 | 12919.79 | 9066 | 13803.3 | 12973.59 | 12765.9 | 13644 | 10534.4 | 12892.3 | 11721.3 | 12519.4 | 11848.1 | 12515.9 | 11096 | 12715.5 | 11637.2 | 11895.3 | 12025.9 | 11685.9 | 10294.2 | 11736.6 | 10324.4 | 11380 | 11238.7 | 12884 | 11633.7 | 12964.58 | 11840 | 12799 | 11627.4 | 12745.7 | 10334 | 12615.2 | 12872.9 | 12778.6 | 12819.7 | 12855.6 | 12868.2 | 11870.2 | 12840.7 | 12597.7 | 12565.1 | 12274.5 | 12170.6 | 12707.8 | 10396.2 | 12385.9 | 11606.8 | 32.8129 | 32.8234 | 32.9225 | 0 | 32.7569 | 32.9943 | 0 | 48.8292 | 0 | 0 | 0 | 0 | 3.0933 | 3.1656 | 3.0708 | 0 | 3.1004 | 2.943 | 5.917 | 6.436 | 6.457 | 0 | 5.77 | 6.435 | 6.8345 | 6.7964 | 6.9897 | 0 | 7.3358 | 6.3258 | 1.4931 | 1.5513 | 1.5208 | 0 | 1.5633 | 1.4183 | 6.7046 | 6.7691 | 6.7997 | 0 | 7.1964 | 7.408 | 1.4302 | 1.5983 | 1.5568 | 0 | 1.6205 | 1.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80188 | 142 | 72077 | 132 | 151624 | 422 | 6.8345 | 6.7964 | 6.9897 | 0 | 7.3358 | 6.3258 | 6.7046 | 6.7691 | 6.7997 | 0 | 7.1964 | 7.408 | 953000 | 1000 | 957000 | 2000 | 1904000 | 5000 | 1907000 | 1899000 | 13.4167 | 6.8564 | 1.5094 | 6.9756 | 1.5892 | 22.01% | 22.78% | 32.862 | 48.8292 | 3.0746 | 6.203 | 1920923.76 | 1905134 | 2282412.6045 | 83.47%
2022-08-04 | 2023 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 332533 | 6:15 | 19:10 | 8820.8 | 9735.4 | 9724 | 9747.2 | 9571.4 | 9687.9 | 9703.9 | 9912.5 | 9747.6 | 9596.7 | 9729.1 | 9825.5 | 9916.2 | 9747.8 | 9412.9 | 9816.4 | 9703.4 | 9803.5 | 9824.9 | 9886.8 | 9881.2 | 9672.7 | 9836.3 | 9922 | 9829.9 | 8627.1 | 9814.8 | 9843.4 | 9916.9 | 9956.5 | 9742.4 | 10077.3 | 9924.1 | 10049.2 | 10003.3 | 9999.2 | 10059.3 | 9966.6 | 10014.6 | 9988.1 | 10201.8 | 9410 | 10130.9 | 9196 | 9853.4 | 10693 | 8137.7 | 10933.9 | 9075.7 | 7922.2 | 9768.5 | 9441.3 | 10232 | 9296 | 10166.6 | 9326.7 | 9005.8 | 10017.2 | 9152.3 | 10138.3 | 10106.8 | 9016.9 | 10937.7 | 8491.1 | 9832.8 | 9466 | 10709 | 9221.7 | 10281.1 | 9462.3 | 10307.7 | 9207.3 | 9313.9 | 10143.6 | 9271 | 10342.5 | 9315.7 | 10341.7 | 8976.1 | 10399.2 | 9307.8 | 10168.9 | 7264.5 | 8681.8 | 10577.2 | 8160.8 | 9268.9 | 7585.5 | 10020.9 | 9818.2 | 9266.7 | 10529.3 | 10347.8 | 9582.8 | 9455.5 | 10383.7 | 10556 | 8728.6 | 10561.1 | 9332 | 10466.3 | 9193.1 | 10322 | 9580 | 10336.8 | 9068.9 | 10361.2 | 9500.4 | 10238.9 | 9240.9 | 10138 | 9534.5 | 9492.1 | 10195.4 | 7131.2 | 11012.1 | 10293.5 | 10130.4 | 10856.2 | 8357.8 | 10243.3 | 9256.4 | 9895.6 | 9345.1 | 9893.5 | 8795.7 | 10143.5 | 9338 | 9564.6 | 9758.8 | 9545.7 | 8284.2 | 9545.9 | 8360.1 | 9593.9 | 9468.6 | 11022.6 | 9862.2 | 11172.4 | 10116.5 | 11005 | 9999 | 11017.1 | 8863.8 | 10775.7 | 11090.6 | 10951.1 | 10993.8 | 11006 | 11040.2 | 10269.3 | 11114.7 | 10724 | 10705.1 | 10515.5 | 10412.7 | 10943.8 | 8871.2 | 10588.4 | 9862.6 | 32.2302 | 32.7338 | 32.791 | 0 | 32.8806 | 32.8165 | 0 | 46.644 | 0 | 0 | 0 | 0 | 3.2482 | 3.2549 | 3.2205 | 0 | 3.3066 | 3.1805 | 14.2517 | 11.53 | 14.8083 | 0 | 12.4017 | 11.4017 | 5.5637 | 5.3552 | 5.48 | 0 | 5.6279 | 5.251 | 1.2944 | 1.2059 | 1.2651 | 0 | 1.1619 | 1.1691 | 5.4988 | 5.3362 | 5.3959 | 0 | 5.4692 | 6.1311 | 1.2572 | 1.2499 | 1.2868 | 0 | 1.2227 | 1.4128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80963 | 144 | 72862 | 134 | 153177 | 426 | 5.5637 | 5.3552 | 5.48 | 0 | 5.6279 | 5.251 | 5.4988 | 5.3362 | 5.3959 | 0 | 5.4692 | 6.1311 | 775000 | 2000 | 785000 | 2000 | 1553000 | 4000 | 1556000 | 1549000 | 12.9167 | 5.4556 | 1.2193 | 5.5662 | 1.2859 | 22.35% | 23.1% | 32.6904 | 46.644 | 3.2421 | 12.8787 | 1567286.1 | 1553961 | 1811379.0488 | 85.79%
2022-08-05 | 2023 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 332601.6 | 6:19 | 19:23 | 8345.8 | 9457.8 | 9486.8 | 9353.1 | 9383.1 | 9587.9 | 9517.1 | 9825 | 9400 | 9276.8 | 9433.7 | 9544.5 | 9687.1 | 9479.6 | 9203.5 | 9571.8 | 9383.4 | 9579.5 | 9647 | 9694.2 | 9643.9 | 9471.9 | 9624.8 | 9661.1 | 9566 | 8345.7 | 9621.5 | 9606.5 | 9650.3 | 9666.4 | 9463.2 | 9871 | 9725.1 | 9870.8 | 9833.9 | 9856.5 | 9911.2 | 9726.2 | 9766 | 9685.5 | 10596.3 | 9587.6 | 10487.9 | 9462.6 | 10025.9 | 11120.6 | 7928.4 | 11400.1 | 9872.8 | 7729.9 | 9614.6 | 9256.7 | 10125.7 | 9073.2 | 10171.5 | 9139.3 | 8859.4 | 9990.5 | 8918.9 | 10074.2 | 9979.7 | 8746.9 | 11119.5 | 8172.8 | 9539.1 | 9118 | 10619.9 | 8896.4 | 10120.2 | 9087.3 | 10043.8 | 8828.4 | 8962.8 | 9849.4 | 8854.7 | 10157.5 | 8976.8 | 10014.1 | 8692.9 | 10117.3 | 8941.6 | 9832.3 | 7856.4 | 10253.1 | 10335.8 | 7850 | 8921.7 | 7287.2 | 9928.3 | 9590.3 | 8834.6 | 10190 | 10058.3 | 9288.3 | 9190.4 | 10142.7 | 10108.5 | 8318.3 | 10188.4 | 8956.8 | 9985.8 | 8753.4 | 9890.7 | 9165.8 | 9988.9 | 8623.8 | 10062 | 9102.3 | 9943.4 | 8899.1 | 10038 | 9230.4 | 9171.9 | 10035.3 | 6822.9 | 11072.1 | 10078.6 | 9925.5 | 10989.1 | 8070.1 | 10111.9 | 8974.3 | 9639.3 | 9061.6 | 9706.2 | 8533.8 | 9929.7 | 9006.7 | 9208.4 | 9384.1 | 9163.6 | 7969.9 | 9104.1 | 7981.1 | 9034.5 | 8881.4 | 10747.7 | 9405.2 | 10787.3 | 9542.9 | 10540.5 | 9348.1 | 10497.4 | 8238.5 | 10581.2 | 10903.2 | 10773.9 | 10759 | 10754.5 | 10790.2 | 9845.6 | 10812.9 | 10846.6 | 10885.6 | 10646.5 | 10450.4 | 10964.7 | 8845.5 | 10494.8 | 9804.3 | 33.2611 | 32.9667 | 32.9514 | 0 | 33.0169 | 32.9947 | 0 | 44.4892 | 0 | 0 | 0 | 0 | 2.2683 | 2.2991 | 2.4206 | 0 | 2.4164 | 2.2596 | 5.4067 | 6.73 | 5.7367 | 0 | 5.7467 | 4.9417 | 5.0767 | 5.1096 | 5.3198 | 0 | 5.2038 | 4.9558 | 1.0674 | 1.1144 | 1.1004 | 0 | 1.0658 | 1.027 | 4.9858 | 5.0889 | 5.1922 | 0 | 5.135 | 5.7735 | 1.0277 | 1.1433 | 1.1288 | 0 | 1.106 | 1.2461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81725 | 145 | 73627 | 135 | 154699 | 430 | 5.0767 | 5.1096 | 5.3198 | 0 | 5.2038 | 4.9558 | 4.9858 | 5.0889 | 5.1922 | 0 | 5.135 | 5.7735 | 762000 | 1000 | 765000 | 1000 | 1522000 | 4000 | 1525000 | 1518000 | 13.0667 | 5.1332 | 1.075 | 5.2351 | 1.1304 | 20.94% | 21.59% | 33.0382 | 44.4892 | 2.3328 | 5.7123 | 1533638 | 1522066 | 1735088.9439 | 87.72%
2022-08-06 | 2023 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 332601.6 | 6:18 | 19:31 | 9541.1 | 10438 | 10461.8 | 10300.3 | 10379.3 | 10548.3 | 10447.7 | 10669 | 10394.3 | 10576.3 | 10194.9 | 10348.6 | 10455.1 | 10178.8 | 10026.2 | 10461.1 | 9844.9 | 10100.8 | 10191.2 | 10299.2 | 10311.6 | 10210.9 | 10305.6 | 10250.3 | 10166.6 | 9022.7 | 10324.9 | 10215.8 | 10143.2 | 9950.5 | 9715.7 | 10246.8 | 9924.3 | 10139.5 | 10386.1 | 10257.2 | 10202.9 | 9938.8 | 9918.9 | 9758.3 | 10622.6 | 9802.9 | 10584.3 | 9648 | 10362.2 | 11276.6 | 8682.5 | 11349.2 | 10522.4 | 8404.7 | 10264.5 | 9954.8 | 10775.9 | 9890.6 | 10717.9 | 9865.4 | 9606.6 | 10648.7 | 9717.7 | 10784.3 | 10814.4 | 9630.9 | 11775.1 | 9337.3 | 10164.8 | 9834.6 | 11156.4 | 9708.5 | 10861.9 | 9939.4 | 10863.2 | 9601.4 | 9899.8 | 10612.5 | 9636.5 | 10766 | 9828.9 | 10642.9 | 9704.9 | 10820.8 | 8893.8 | 9628.2 | 7786.3 | 9926.4 | 9994 | 7777.9 | 8792.8 | 7188.1 | 7766.7 | 7728.2 | 6990.2 | 7803.7 | 7880.1 | 7455.9 | 7333.2 | 7858.6 | 9458.3 | 7727.2 | 9288.8 | 8222.5 | 9268.4 | 8203.8 | 9089.1 | 8476.9 | 8855.8 | 7993.3 | 8871.8 | 8253.2 | 8632.3 | 7963.3 | 8529.5 | 8026.7 | 8339.7 | 8977 | 6320.1 | 9748 | 9100.1 | 9008.8 | 9713.3 | 7578 | 9108 | 8232.5 | 8580.7 | 7972.1 | 8379.6 | 7610 | 8856.1 | 8206.4 | 8590.1 | 8664.5 | 8441.6 | 7499 | 8534.9 | 7599 | 9384.7 | 9262.1 | 10758.2 | 9745.8 | 10927.1 | 9942.4 | 10806.2 | 9882.9 | 10803.3 | 8782.5 | 10747.5 | 10963 | 10886.5 | 10859.4 | 10852.4 | 10855.9 | 10132.1 | 10896.7 | 11034.8 | 11009.2 | 10838.2 | 10599.3 | 11095.4 | 9041.8 | 10661.9 | 10108.5 | 31.0338 | 30.7349 | 30.5114 | 0 | 30.5678 | 30.7022 | 0 | 43.6095 | 0 | 0 | 0 | 0 | 2.3866 | 2.3836 | 2.382 | 0 | 2.49 | 2.3516 | 6.0283 | 6.3133 | 6.605 | 0 | 6.43 | 6.2717 | 5.8599 | 5.6734 | 5.9157 | 0 | 5.4343 | 5.6693 | 0.98925 | 0.83411 | 1.0829 | 0 | 0.90488 | 1.0643 | 5.7678 | 5.695 | 5.7703 | 0 | 5.3574 | 6.5809 | 0.97213 | 0.96006 | 1.1106 | 0 | 0.96532 | 1.3111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82537 | 147 | 74347 | 137 | 156225 | 435 | 5.8599 | 5.6734 | 5.9157 | 0 | 5.4343 | 5.6693 | 5.7678 | 5.695 | 5.7703 | 0 | 5.3574 | 6.5809 | 812000 | 2000 | 720000 | 2000 | 1526000 | 5000 | 1528000 | 1521000 | 13.2167 | 5.7105 | 0.97508 | 5.8343 | 1.0638 | 17.08% | 18.23% | 30.71 | 43.6095 | 2.3987 | 6.3297 | 1539931.8 | 1527267 | 1930524.1506 | 79.11%
2022-08-07 | 2023 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 332601.6 | 6:17 | 18:19 | 9739.75 | 10749.7 | 10755.68 | 10849.99 | 10553.1 | 10751.4 | 10732.97 | 11168.58 | 10849.5 | 10694.13 | 10898.12 | 10967.8 | 11238.1 | 11068 | 10771.9 | 11161.2 | 10882.6 | 11189.8 | 11376.6 | 11529.22 | 11498 | 11345.45 | 11212.9 | 11330.36 | 11257.4 | 9990.58 | 11461.5 | 11379.1 | 11238.9 | 11132.1 | 11009.1 | 11425.2 | 11414.5 | 11600 | 11586.27 | 11595.2 | 11582.4 | 11340.6 | 11341.9 | 11290.4 | 12080.9 | 11138.49 | 12042.1 | 10969.1 | 11620.9 | 12674.8 | 9637.8 | 12872.96 | 11492.99 | 9149 | 11253.46 | 10849.95 | 11881.96 | 10707.84 | 11731.26 | 10863.7 | 10274.4 | 11438.27 | 10568.1 | 11516.3 | 11454.24 | 10254.3 | 12580.18 | 9675.2 | 11099.1 | 10578.8 | 12074 | 10372.8 | 11620.62 | 10461.3 | 11492.76 | 10156.9 | 10517.36 | 11430.7 | 10286.7 | 11790 | 10518.96 | 11445.1 | 10208.6 | 11511.2 | 10341.64 | 11170.3 | 9115.4 | 11697.9 | 11801.5 | 9244.88 | 10414.6 | 8588.3 | 11978.8 | 11510.1 | 10718 | 11986.9 | 11889 | 11108.54 | 11018.7 | 11985 | 11895.3 | 10059 | 11964.9 | 10743 | 11783.8 | 10636.1 | 11701.28 | 10921.8 | 11711.2 | 10340.9 | 11740.7 | 10716.1 | 11617.4 | 10721 | 11689.4 | 10864.2 | 10925.4 | 11854.2 | 8193.8 | 12745.7 | 11786.6 | 11824.3 | 12561.7 | 9743.7 | 11810.4 | 10602 | 11326.3 | 10654.6 | 11203.3 | 9978.1 | 11531.5 | 10696.7 | 11071.9 | 11290.5 | 11010.6 | 9670.6 | 11079.2 | 9706.3 | 10651.93 | 10412.09 | 12018.01 | 10926.2 | 12156.6 | 11146.24 | 12151.86 | 11085.7 | 12190.77 | 9852.6 | 11820.01 | 12194.83 | 11931.79 | 12028.7 | 12010.08 | 12003.1 | 11095.1 | 12093.3 | 11548.45 | 11573.39 | 11424.1 | 11358.87 | 11867.79 | 9833.2 | 11440.07 | 10779.14 | 32.717 | 33.019 | 33.2155 | 0 | 32.9335 | 33.2178 | 0 | 49.5671 | 0 | 0 | 0 | 0 | 2.4067 | 2.4049 | 2.2859 | 0 | 2.3289 | 2.2822 | 5.7 | 4.9333 | 5.5383 | 0 | 6.44 | 4.605 | 6.2037 | 6.1658 | 6.5302 | 0 | 6.5251 | 5.7419 | 1.2723 | 1.0949 | 1.4186 | 0 | 1.2274 | 1.1652 | 6.144 | 6.1556 | 6.4469 | 0 | 6.383 | 6.6966 | 1.2468 | 1.2261 | 1.435 | 0 | 1.2917 | 1.4264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83422 | 148 | 75235 | 138 | 157991 | 439 | 6.2037 | 6.1658 | 6.5302 | 0 | 6.5251 | 5.7419 | 6.144 | 6.1556 | 6.4469 | 0 | 6.383 | 6.6966 | 885000 | 1000 | 888000 | 1000 | 1766000 | 4000 | 1771000 | 1762000 | 12.0333 | 6.2333 | 1.2357 | 6.3652 | 1.3252 | 19.82% | 20.82% | 33.0206 | 49.5671 | 2.3417 | 5.4433 | 1780790.06 | 1766534 | 2077212.2056 | 85.04%
2022-08-08 | 2023 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 332601.6 | 6:15 | 16:35 | 4683.8 | 5242.4 | 5208.9 | 5162.1 | 5101 | 5204.2 | 5267.3 | 5404.24 | 5223.4 | 5247.4 | 5178.9 | 5288 | 5298.4 | 5189.8 | 5015.91 | 5229.24 | 4917.4 | 5051.6 | 5144.57 | 5197.9 | 5196.1 | 5128.4 | 5172 | 5197.4 | 5051.1 | 4399.37 | 5154.8 | 5088 | 5082.9 | 3663.2 | 4926.4 | 5185.13 | 5026.7 | 5054.3 | 5178.2 | 5184.4 | 5210.8 | 5087.7 | 5100.6 | 5109.8 | 5233.2 | 4717.5 | 5172.9 | 4609.1 | 4959.77 | 5551.64 | 4060.8 | 5755.03 | 5408.1 | 4207.2 | 5235.1 | 4997.8 | 5506.7 | 4932.4 | 5477.08 | 4896.3 | 4808.4 | 5439.24 | 4891.5 | 5519.6 | 5510.18 | 4832.1 | 6127.8 | 4473.7 | 5069.8 | 4743.3 | 5641.18 | 4630.1 | 5451.62 | 4775.7 | 5388.8 | 4651.4 | 4856.1 | 5342.2 | 4765.8 | 5530.56 | 4874.2 | 5383.6 | 4732.2 | 5411.4 | 4628.4 | 5121.2 | 4664.1 | 4699.7 | 5270.3 | 4332.2 | 4574.8 | 3765.5 | 5322.3 | 4865.2 | 4705.5 | 5422.9 | 5427.9 | 5010.2 | 4948 | 5406.6 | 5305.6 | 4279.4 | 5275.9 | 4621.2 | 5169.4 | 4553.7 | 5131.7 | 4705.3 | 5124 | 4417 | 5147 | 4606.4 | 5064.1 | 4610.2 | 5075.6 | 4662.3 | 4686.3 | 5121.85 | 3482.9 | 5663.7 | 5110.1 | 5054 | 5532.7 | 4044.2 | 5078.6 | 4505 | 4916.2 | 4584.2 | 4876.2 | 4306.1 | 5012.5 | 4546.4 | 4572.4 | 4717.8 | 4637.6 | 3978.9 | 4605.8 | 4085.4 | 4648.2 | 4577.35 | 5350.37 | 4664.4 | 5419.8 | 4768.7 | 5356.2 | 4779.3 | 5436.2 | 4288.4 | 5242.2 | 5462.7 | 5336.3 | 5348.1 | 5311.1 | 5339 | 4841.1 | 5368 | 5261.7 | 5269.3 | 5165.08 | 5111.4 | 5354.1 | 4275.6 | 5072.6 | 4724.4 | 29.3262 | 29.5847 | 29.4249 | 0 | 29.4761 | 29.6232 | 0 | 36.8469 | 0 | 0 | 0 | 0 | 3.4838 | 3.5727 | 3.4179 | 0 | 3.4997 | 3.07 | 10.856 | 12.386 | 10.397 | 0 | 9.706 | 9.969 | 2.8479 | 2.6306 | 2.656 | 0 | 2.6588 | 2.3293 | 0.43981 | 0.31209 | 0.43926 | 0 | 0.34122 | 0.31093 | 2.7937 | 2.6011 | 2.596 | 0 | 2.5223 | 2.7239 | 0.42466 | 0.34726 | 0.45181 | 0 | 0.36266 | 0.37869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83827 | 150 | 75624 | 140 | 158781 | 444 | 2.8479 | 2.6306 | 2.656 | 0 | 2.6588 | 2.3293 | 2.7937 | 2.6011 | 2.596 | 0 | 2.5223 | 2.7239 | 405000 | 2000 | 389000 | 2000 | 790000 | 5000 | 790000 | 785000 | 10.3333 | 2.6245 | 0.36866 | 2.6474 | 0.39302 | 14.05% | 14.85% | 29.487 | 36.8469 | 3.4088 | 10.6628 | 797828.91 | 791066 | 897304.6985 | 88.16%
2022-08-09 | 2023 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 332601.6 | 6:15 | 19:25 | 10146.4 | 11245.2 | 11627.2 | 11526.1 | 11562.5 | 11664.3 | 11383.1 | 11606.7 | 11256.7 | 11178.5 | 11219.7 | 11338.6 | 11402.8 | 11249.7 | 11000 | 11262 | 11102.2 | 11269.7 | 11344.6 | 11384.7 | 11329.4 | 11182 | 11318 | 11355.7 | 11108.5 | 9822.6 | 11193.7 | 11184.7 | 11270.1 | 9932.6 | 11092.6 | 11409.2 | 11133.1 | 11150.7 | 11242.4 | 11228.7 | 11331 | 11201.3 | 11238.5 | 11069 | 12223.5 | 11281.5 | 11987.9 | 11047.5 | 11547.1 | 12513 | 9165 | 12868.5 | 11582 | 9262.4 | 11286.3 | 10799.3 | 11722.6 | 10800.6 | 11606.1 | 10625.9 | 10374.4 | 11488.5 | 10651.7 | 11634.2 | 11597.3 | 10490.9 | 12546.3 | 9754.1 | 10935 | 10682 | 12070.6 | 10590.5 | 11652.9 | 10734.2 | 11599.5 | 10500.4 | 10605 | 11539.2 | 10528.8 | 11745.3 | 10618 | 11695.7 | 10290.5 | 11758.6 | 10736.4 | 11518.8 | 10787.8 | 11159.1 | 11873.2 | 10078.3 | 10586.8 | 8959.7 | 11865.6 | 11492.1 | 10371.8 | 9742.2 | 11614.3 | 10831.7 | 10705.4 | 11740.6 | 11838.3 | 10001 | 11916.4 | 10081.3 | 11724.6 | 10750.7 | 11658.7 | 11012.1 | 11736.2 | 10431.4 | 11818.7 | 10935.2 | 11632.5 | 10798.8 | 11631.6 | 10977.4 | 11007.9 | 11884.3 | 8357.7 | 12824.4 | 11973 | 11906.1 | 12370.1 | 9889.2 | 11983.8 | 10905.5 | 11465.4 | 10970.8 | 11508.9 | 10367 | 11810.6 | 10950.8 | 10305.3 | 10465.6 | 11082.2 | 9688.3 | 11037.4 | 9777.5 | 10598.5 | 10603.9 | 12034 | 10894.9 | 12044 | 11035 | 12014.4 | 10896.5 | 11982.7 | 9710.1 | 11742.1 | 11994.2 | 11257.5 | 3370.5 | 11929.4 | 12003.4 | 11092.7 | 11947.1 | 11867.2 | 11829.4 | 11624.7 | 11592.6 | 11890.6 | 9922.9 | 11631 | 10929.9 | 32.1284 | 31.8635 | 31.5605 | 0 | 31.7439 | 31.871 | 0 | 43.4614 | 0 | 0 | 0 | 0 | 3.1054 | 3.211 | 3.1604 | 0 | 3.2096 | 3.0403 | 7.222 | 7.107 | 7.121 | 0 | 9.915 | 10.438 | 6.4981 | 6.2196 | 6.5575 | 0 | 6.6211 | 5.75 | 1.0314 | 0.9308 | 1.3034 | 0 | 0.99512 | 0.91566 | 6.4287 | 6.1993 | 6.4908 | 0 | 6.4102 | 6.7281 | 0.99071 | 0.96122 | 1.2969 | 0 | 1.0184 | 1.1463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84717 | 151 | 76503 | 142 | 160543 | 448 | 6.4981 | 6.2196 | 6.5575 | 0 | 6.6211 | 5.75 | 6.4287 | 6.1993 | 6.4908 | 0 | 6.4102 | 6.7281 | 890000 | 1000 | 879000 | 2000 | 1762000 | 4000 | 1766000 | 1758000 | 13.1667 | 6.3292 | 1.0353 | 6.4514 | 1.0827 | 16.36% | 16.78% | 31.8335 | 43.4614 | 3.1453 | 8.3606 | 1777947 | 1762401 | 2122825.4192 | 83.02%
2022-08-10 | 2023 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 333274.67 | 6:15 | 19:21 | 10838.3 | 12124.46 | 12230.6 | 12099.9 | 12137.69 | 12316.81 | 12212.77 | 12459 | 11961.26 | 11820.53 | 11968.2 | 12043.3 | 12244.39 | 12007.25 | 11849.8 | 12169.5 | 11854.53 | 12038.97 | 12146.25 | 12182.5 | 12112.83 | 11955.8 | 12142.7 | 12195.97 | 11931.5 | 10595.3 | 12001.84 | 12010.6 | 12064.9 | 12047.8 | 11878.6 | 12204.99 | 12091.64 | 12098.2 | 12140.7 | 12159.2 | 12234.19 | 12108.88 | 12151.37 | 12016 | 12837.05 | 11954.4 | 12793.3 | 11818.67 | 12436.4 | 13331.14 | 10300.24 | 13634.06 | 12315.8 | 9964 | 12032.7 | 11653.2 | 12490.43 | 11586.4 | 12529.18 | 11512.87 | 11408.57 | 12557.05 | 11391.3 | 12596.6 | 12557.3 | 11238.28 | 13603.76 | 10776.5 | 11964.79 | 11627.11 | 13089.3 | 11509.9 | 12738.8 | 11677.86 | 12589.75 | 11457.59 | 11736.2 | 12591.88 | 11581.3 | 12892.37 | 11735.61 | 12661.2 | 11417.1 | 12732.3 | 11634.35 | 12351.18 | 11782.06 | 12698 | 12766.9 | 10968.78 | 11467.33 | 9721.4 | 12672.25 | 12228.7 | 11482.8 | 12557.28 | 12541.71 | 11808.6 | 11709.9 | 12617.7 | 12640.56 | 10817.1 | 12695.6 | 11613.2 | 12591.94 | 11535.92 | 12461.7 | 11800 | 12617.71 | 11246.49 | 12685.6 | 11723 | 12537.17 | 11682.05 | 12544.48 | 11766.5 | 11804.23 | 12607.43 | 8770.5 | 13533.4 | 12691.71 | 12584.19 | 13435.53 | 10572.4 | 12672.02 | 11642.8 | 12222.9 | 11700.7 | 12230.8 | 11059.14 | 12514.6 | 11688.76 | 11744.6 | 11905.34 | 11881.83 | 10352.1 | 11636.63 | 10175.3 | 11651.27 | 11674.75 | 12834.9 | 11700.3 | 13082.99 | 11981.1 | 12994.11 | 12005.96 | 13046 | 10810.5 | 12748.58 | 13085.23 | 12890.73 | 12890.8 | 12808.4 | 12853.51 | 12175.8 | 13049.28 | 12836.9 | 12862.68 | 12595.46 | 12558.37 | 12875.9 | 10800.2 | 12491.59 | 11950 | 34.0937 | 33.4911 | 33.3525 | 0 | 33.3565 | 33.485 | 0 | 45.0205 | 0 | 0 | 0 | 0 | 4.5014 | 4.6412 | 4.486 | 0 | 4.4799 | 4.3208 | 8.393 | 8.103 | 8.624 | 0 | 9.011 | 8.262 | 7.0311 | 6.8115 | 7.1644 | 0 | 7.1445 | 6.3397 | 1.0712 | 0.98506 | 1.2836 | 0 | 1.2005 | 1.238 | 6.9332 | 6.7561 | 7.0007 | 0 | 7.0192 | 7.3978 | 1.0397 | 1.0883 | 1.3354 | 0 | 1.2356 | 1.5169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85677 | 152 | 77465 | 143 | 162456 | 452 | 7.0311 | 6.8115 | 7.1644 | 0 | 7.1445 | 6.3397 | 6.9332 | 6.7561 | 7.0007 | 0 | 7.0192 | 7.3978 | 960000 | 1000 | 962000 | 1000 | 1913000 | 4000 | 1920000 | 1909000 | 13.1 | 6.8982 | 1.1557 | 7.0214 | 1.2432 | 16.75% | 17.71% | 33.5558 | 45.0205 | 4.4859 | 8.4786 | 1930821.46 | 1914727 | 2312280.398 | 82.81%
2022-08-11 | 2023 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 333274.67 | 6:16 | 19:27 | 10133.6 | 11230.8 | 11114.2 | 11002.9 | 10985.5 | 11200.4 | 11239.7 | 11495 | 11129.25 | 11028.8 | 11069.94 | 11183.9 | 11277.57 | 11070.63 | 10831.8 | 11167.49 | 10849.68 | 11007.99 | 11086.47 | 11133.9 | 11085.5 | 10954.9 | 11089.9 | 11145.37 | 10950 | 9777.6 | 11006.39 | 11001.5 | 11057.7 | 11054.8 | 10891.1 | 11200.6 | 10973.9 | 11016.7 | 11175.6 | 11154.8 | 11201.48 | 11059.8 | 11091.3 | 10953.7 | 11855.48 | 11042.9 | 11723.7 | 10870.8 | 11340.3 | 12289.5 | 9445.2 | 12640.03 | 11379.8 | 9252.8 | 11091.3 | 10718.3 | 11484.9 | 10626.9 | 11496.4 | 10592.8 | 10421.2 | 11375.7 | 10553.29 | 11513.15 | 11497.6 | 10388.7 | 12495.9 | 9805.4 | 10972.8 | 10624.3 | 11927.4 | 10543.8 | 11526.5 | 10685 | 11492.9 | 10490.3 | 10587.9 | 11411.82 | 10497.8 | 11607.8 | 10575.3 | 11564 | 10297.7 | 11646.7 | 10727.2 | 11415.6 | 10927.3 | 11806.9 | 11813.7 | 10166.3 | 10522.3 | 9043.4 | 11708.36 | 11306.6 | 10535.3 | 11561.1 | 11480.7 | 10743.1 | 10617.93 | 11610.8 | 11694.9 | 9908.2 | 11696.9 | 10607.8 | 11597.57 | 10613.6 | 11469.2 | 10878 | 11590.07 | 10391.94 | 11670.4 | 10848.4 | 11479.78 | 10752.3 | 11517.6 | 10934.6 | 10684.1 | 11474 | 8210.3 | 12443.68 | 11635.3 | 11498.1 | 12387.9 | 9670 | 11598 | 10618.9 | 11244.8 | 10778.39 | 11272.13 | 10151.4 | 11457.5 | 10599.9 | 10768.2 | 10935.8 | 10796.8 | 9557.8 | 10739.8 | 9521.7 | 10676.6 | 10692.2 | 11927.7 | 10829.3 | 11926.3 | 10944.3 | 11913.9 | 10935.4 | 11942.4 | 9885.7 | 11659.68 | 11884.1 | 11900.77 | 11876.2 | 11893.7 | 11927 | 11023.9 | 11845.8 | 11799 | 11727.5 | 11510.6 | 11450.1 | 11741.8 | 9879 | 11597.26 | 10872 | 33.2559 | 32.7596 | 32.6344 | 0 | 32.5266 | 32.7855 | 0 | 41.9064 | 0 | 0 | 0 | 0 | 6.4725 | 6.5451 | 6.5896 | 0 | 6.5072 | 5.9975 | 10.6433 | 10.3483 | 10.6067 | 0 | 10.5283 | 9.4333 | 6.3372 | 6.0607 | 6.3679 | 0 | 6.3017 | 5.7193 | 1.0565 | 1.1166 | 1.3491 | 0 | 1.1974 | 1.3244 | 6.2541 | 6.0374 | 6.2201 | 0 | 6.282 | 6.6057 | 1.0237 | 1.2366 | 1.3587 | 0 | 1.2322 | 1.5933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86551 | 154 | 78349 | 145 | 164212 | 457 | 6.3372 | 6.0607 | 6.3679 | 0 | 6.3017 | 5.7193 | 6.2541 | 6.0374 | 6.2201 | 0 | 6.282 | 6.6057 | 874000 | 2000 | 884000 | 2000 | 1756000 | 5000 | 1754000 | 1751000 | 13.1833 | 6.1574 | 1.2088 | 6.2798 | 1.2889 | 19.63% | 20.52% | 32.7924 | 41.9064 | 6.4224 | 10.312 | 1771380.79 | 1757466 | 2165054.3926 | 81.17%
2022-08-12 | 2023 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 333274.67 | 6:22 | 19:22 | 6245.39 | 7051.1 | 7160 | 7081.2 | 7068.05 | 7177.9 | 7080.2 | 7219.1 | 6927 | 6867.7 | 6874.5 | 6980 | 7006.7 | 6873.3 | 6713.15 | 6921.55 | 6588.2 | 6724 | 6821.6 | 6859.7 | 6837.5 | 6730.5 | 6896.6 | 6922.3 | 6581.18 | 5783 | 6688.7 | 6651.2 | 6690.6 | 6698.2 | 6550.6 | 6798.5 | 6649.1 | 6687.6 | 6766.6 | 6756.5 | 6784.5 | 6665.6 | 6692.1 | 6603.8 | 7374.3 | 6705.9 | 7250.5 | 6557.2 | 6964.39 | 7764.8 | 5797 | 8068.9 | 7061.4 | 5549.5 | 6812.6 | 6479.8 | 7121.4 | 6513.3 | 7095.68 | 6379.5 | 6329.4 | 7036.7 | 6424.4 | 7142.9 | 7139 | 6320.9 | 7954.3 | 5825.2 | 6723.3 | 6404.7 | 7477.5 | 6300.2 | 7184.4 | 6416.9 | 7111.2 | 6270.1 | 6435.8 | 7077.2 | 6372.9 | 7243.9 | 6446.8 | 7121.4 | 6266.1 | 7179.75 | 6364.7 | 6865.8 | 6569.7 | 7176.3 | 7190.2 | 6068.5 | 6257.7 | 5365.3 | 7137.7 | 6843.2 | 6294.3 | 7033.5 | 7037.2 | 6523.6 | 6478.6 | 7091.7 | 7261.3 | 6196.2 | 7391.7 | 6705.1 | 7081.7 | 6591.2 | 7130.2 | 6809.9 | 7253.7 | 6448.4 | 7348.1 | 6818.3 | 7205.5 | 6714.2 | 7299.1 | 6898.6 | 6845.1 | 7371.3 | 5208.2 | 8149 | 7526.9 | 7516.1 | 8109.5 | 6312.3 | 7587.1 | 6887 | 7180.7 | 6841.2 | 7199.6 | 6564 | 7485.4 | 6970.07 | 7057.5 | 7150.6 | 7084.8 | 6242.3 | 6983.6 | 6107.1 | 6778.3 | 6758.82 | 7712.8 | 6866.5 | 7702.7 | 6968.3 | 7677.5 | 6880.9 | 7679.2 | 6139.6 | 7452 | 7645.5 | 7675 | 7660 | 7675.7 | 7710.6 | 7006.1 | 7622.7 | 7559.5 | 7527.9 | 7329 | 7278.6 | 7519.2 | 6181.3 | 7436.5 | 6887.5 | 30.65 | 30.57 | 30.53 | 0 | 30.55 | 30.66 | 0 | 36.61 | 0 | 0 | 0 | 0 | 4.83 | 4.82 | 4.83 | 0 | 4.84 | 4.52 | 9.92 | 10.58 | 9.54 | 0 | 9.95 | 11.18 | 3.69 | 3.48 | 3.67 | 0 | 3.87 | 3.45 | 0.64 | 0.63 | 0.8 | 0 | 0.72 | 0.73 | 3.65 | 3.48 | 3.6 | 0 | 3.84 | 3.99 | 0.63 | 0.66 | 0.79 | 0 | 0.74 | 0.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87098 | 155 | 78908 | 146 | 165309 | 461 | 3.69 | 3.48 | 3.67 | 0 | 3.87 | 3.45 | 3.65 | 3.48 | 3.6 | 0 | 3.84 | 3.99 | 547000 | 1000 | 559000 | 1000 | 1097000 | 4000 | 1104000 | 1093000 | 13 | 3.632 | 0.704 | 3.712 | 0.738 | 19.38% | 19.88% | 30.592 | 36.61 | 4.768 | 10.234 | 1104538.43 | 1096734 | 1267942.6015 | 86.5%
2022-08-13 | 2023 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 333367 | 6:21 | 19:13 | 3178.76 | 3597.37 | 3573.49 | 3531.27 | 3525.14 | 3597.51 | 3615.72 | 3726.04 | 3578.28 | 3586.19 | 3560.16 | 3628.47 | 3627.14 | 3574.64 | 3402.43 | 3552.71 | 3438.17 | 3514.16 | 3555.25 | 3580.19 | 3568.54 | 3502.29 | 3535.26 | 3563.81 | 3525.78 | 3062.43 | 3550.96 | 3536.09 | 3555.81 | 3551.07 | 3485.67 | 3647.6 | 3563.16 | 3586.69 | 3640.95 | 3626.77 | 3644.91 | 3566.71 | 3577.62 | 3534.27 | 3807.92 | 3384.82 | 3746.85 | 3321.23 | 3594.95 | 4113.09 | 2903.96 | 4256.83 | 3745.77 | 2905.85 | 3604.41 | 3425.47 | 3800.75 | 3378.37 | 3817.29 | 3405.36 | 3378.64 | 3786.42 | 3384.66 | 3841.62 | 3822.68 | 3329.94 | 4336.46 | 3064.8 | 3579.66 | 3415.6 | 4043.25 | 3351.37 | 3841.91 | 3414.06 | 3826.77 | 3324.27 | 3385.67 | 3755.01 | 3336.05 | 3885.93 | 3388.89 | 3820.23 | 3286.6 | 3860.77 | 3375.47 | 3695.86 | 3468.47 | 3883.04 | 3824.88 | 3171.86 | 3319.35 | 2797.94 | 3807.26 | 3652.91 | 3315.11 | 3764.45 | 3776.2 | 3458.41 | 3427.93 | 3809.24 | 3826.3 | 3101.31 | 3833.86 | 3362.73 | 3787.24 | 3344.76 | 3753.02 | 3454.45 | 3819.05 | 3261.22 | 3829.59 | 3427.51 | 3766.98 | 3410.56 | 3781.47 | 3462.72 | 3424.14 | 3695.9 | 2556.4 | 4231.79 | 3807.32 | 3742.05 | 3850.23 | 3007.67 | 3775.65 | 3335.73 | 3595.1 | 3402.23 | 3608.53 | 3162.47 | 3702.81 | 3348.93 | 3396.86 | 3478.57 | 3420.09 | 2962.46 | 3425.12 | 2979.13 | 3424.39 | 3424.68 | 3979.28 | 3453.97 | 4003.14 | 3510.16 | 3965.8 | 3484.44 | 3973.75 | 3102.34 | 3842.01 | 3997.78 | 3962.83 | 3953.45 | 3960.87 | 3986.32 | 3567.87 | 3968.48 | 3931.98 | 3926 | 3813.84 | 3710.33 | 3880.22 | 3112.67 | 3801.4 | 3485.24 | 26.1307 | 26.7998 | 26.6727 | 0 | 26.6713 | 26.822 | 0 | 30.4335 | 0 | 0 | 0 | 0 | 4.7399 | 4.7083 | 4.8333 | 0 | 4.7821 | 4.3662 | 9.237 | 10.936 | 9.702 | 0 | 9.729 | 8.76 | 1.754 | 1.724 | 1.7298 | 0 | 1.7681 | 1.596 | 0.20752 | 0.21184 | 0.20324 | 0 | 0.23021 | 0.22544 | 1.6951 | 1.7136 | 1.6554 | 0 | 1.7328 | 1.8863 | 0.2102 | 0.23211 | 0.21704 | 0 | 0.24266 | 0.28097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87383 | 157 | 79194 | 148 | 165877 | 465 | 1.754 | 1.724 | 1.7298 | 0 | 1.7681 | 1.596 | 1.6951 | 1.7136 | 1.6554 | 0 | 1.7328 | 1.8863 | 285000 | 2000 | 286000 | 2000 | 568000 | 4000 | 567000 | 564000 | 12.8667 | 1.7144 | 0.21565 | 1.7367 | 0.2366 | 12.58% | 13.62% | 26.6193 | 30.4335 | 4.686 | 9.6728 | 572347.23 | 568867 | 617407.6661 | 92.14%
2022-08-14 | 2023 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 333367 | 6:17 | 19:25 | 7751.7 | 8702.96 | 8687.6 | 8593.94 | 8632.11 | 8730.74 | 8732.17 | 8985.72 | 8638.33 | 8632.45 | 8591.66 | 8707.53 | 8853.61 | 8665.39 | 8515.68 | 8811.94 | 8633.38 | 8768.69 | 8865.01 | 8899.33 | 8833.4 | 8679.62 | 8811.87 | 8914.21 | 8641.97 | 7550.58 | 8738.81 | 8705.25 | 8788.99 | 8888.48 | 8730.23 | 8973.03 | 8803.16 | 8787.47 | 8850.31 | 8855.17 | 8984.4 | 8897.26 | 8959.24 | 8811.16 | 9643.37 | 8670.98 | 9444.66 | 8402.74 | 9045.21 | 10255.87 | 7543.83 | 10665.51 | 9003.21 | 7089.4 | 8761.28 | 8392.64 | 9236.6 | 8339.61 | 9150.4 | 8306.61 | 8177.17 | 9066.4 | 8136.4 | 9156.66 | 9080.54 | 7966.46 | 10208.88 | 7525.54 | 8663.27 | 8248.89 | 9622.92 | 8104.11 | 9196.2 | 8281.42 | 8702.07 | 6847.05 | 8285.94 | 9117.39 | 8188.03 | 9301.88 | 8229.19 | 9199.82 | 7969.38 | 9281 | 8195.13 | 8903.58 | 8290.84 | 9271.52 | 9110.5 | 7666.85 | 8016.77 | 6751.1 | 9118.85 | 8730 | 8015.34 | 9007.02 | 9048.61 | 8390.57 | 8369.91 | 9127.1 | 9141.91 | 7467.77 | 9112.54 | 8043.89 | 9095.12 | 8050.89 | 9012.91 | 8335.24 | 9177.02 | 7885.41 | 9201.28 | 8260.26 | 9039.29 | 8218.03 | 9030.51 | 8292.89 | 8166.57 | 8792.82 | 6187.96 | 9974.12 | 9089.94 | 8912.2 | 9922.84 | 7202.75 | 8986.55 | 7973.06 | 8635.4 | 8155.41 | 8634.38 | 7575.12 | 8796.05 | 7983.42 | 8081.51 | 8263.54 | 8145.48 | 7078.95 | 8104.31 | 7076.02 | 8077.12 | 8066.66 | 9228.8 | 8052.93 | 9303.9 | 8240.19 | 9249.39 | 8238.69 | 9294.08 | 7364.28 | 8968.36 | 9261.64 | 9188.91 | 9145.15 | 9163.7 | 9230.28 | 8370.1 | 9194.13 | 9229.98 | 9174.09 | 9000.05 | 8878.48 | 9078.83 | 7407.27 | 8873.11 | 8232.49 | 27.5603 | 27.5737 | 27.5413 | 0 | 27.3827 | 27.7461 | 0 | 36.715 | 0 | 0 | 0 | 0 | 4.6902 | 5.0507 | 4.4501 | 0 | 5.1082 | 4.2926 | 9.22 | 8.814 | 8.581 | 0 | 8.695 | 8.681 | 4.6078 | 4.6021 | 4.7173 | 0 | 4.5912 | 4.1019 | 0.731 | 0.82245 | 0.82557 | 0 | 0.85521 | 0.89966 | 4.5173 | 4.5487 | 4.6158 | 0 | 4.5772 | 4.7479 | 0.71886 | 0.87761 | 0.85605 | 0 | 0.87303 | 1.0787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88078 | 158 | 79874 | 149 | 167247 | 470 | 4.6078 | 4.6021 | 4.7173 | 0 | 4.5912 | 4.1019 | 4.5173 | 4.5487 | 4.6158 | 0 | 4.5772 | 4.7479 | 695000 | 1000 | 680000 | 1000 | 1370000 | 5000 | 1373000 | 1365000 | 13.1333 | 4.524 | 0.82678 | 4.6014 | 0.88085 | 18.28% | 19.14% | 27.5608 | 36.715 | 4.7184 | 8.7982 | 1379742.74 | 1370007 | 1583340.8504 | 86.53%
2022-08-15 | 2023 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 333446.785 | 6:22 | 19:23 | 8560.2 | 9643.1 | 9789.02 | 9644 | 9815.5 | 9903.11 | 9713.19 | 10014.3 | 9610.18 | 9540 | 9551.9 | 9757 | 9600.6 | 9511.3 | 9158.2 | 9476.19 | 8946.9 | 9099.64 | 9203.21 | 9258.44 | 9277.62 | 9134.8 | 9251.9 | 9317.97 | 9241.2 | 8074.66 | 9193.28 | 9173 | 9222.04 | 9147.5 | 8969.37 | 9435.74 | 9495.19 | 9528.5 | 9591.97 | 9551.26 | 9571.94 | 9416.85 | 9475.16 | 9419.1 | 9579.65 | 8550.9 | 9427.78 | 8364.75 | 9140.3 | 10391.29 | 7553.04 | 10514.16 | 9770.1 | 7735.9 | 9388.3 | 9096.3 | 9764.12 | 8835.53 | 9993.49 | 8974.94 | 9125.78 | 10059.73 | 8962.5 | 10224.46 | 10218.4 | 8899.8 | 11395.3 | 8517.4 | 9629.2 | 9254.88 | 10683.23 | 9133.6 | 10261.92 | 9276.2 | 10252.25 | 9082.52 | 9329.6 | 10207.3 | 9119.9 | 10462 | 9281.15 | 10260 | 8962.1 | 10358 | 9351.5 | 10069 | 9459.88 | 10594.1 | 10471 | 8824.78 | 9123.3 | 7788.9 | 10293.7 | 10020.4 | 9109.5 | 10143.2 | 10089.43 | 9281.88 | 9140.41 | 10181 | 9968.16 | 8090.29 | 9788.8 | 8566.05 | 9747.53 | 8599.61 | 9588.97 | 8818.22 | 9685.3 | 8369.7 | 9656.2 | 8740.8 | 9472.83 | 8595.55 | 9411.5 | 8705.6 | 8694.46 | 9448.66 | 6592.4 | 10615.39 | 9740.09 | 9853 | 10635.01 | 8203.5 | 10009.7 | 9018.9 | 9198.2 | 8735.07 | 9302.6 | 8622 | 9956.96 | 9362.3 | 9500.48 | 9694.65 | 9697.26 | 8408.1 | 9648.9 | 8390.5 | 9506.99 | 9454.56 | 10541.97 | 9334.9 | 10573.61 | 9535.38 | 10721.92 | 9591.9 | 10810.5 | 8605.4 | 10053.2 | 10401.4 | 10312.03 | 10289.72 | 10374.2 | 10474.16 | 9490.8 | 10358.53 | 10111.54 | 10082.9 | 9921.2 | 9855.4 | 10104.14 | 8304.5 | 9881.12 | 9150 | 29.6627 | 29.733 | 29.4786 | 0 | 29.5352 | 29.819 | 0 | 42.4622 | 0 | 0 | 0 | 0 | 2.1857 | 2.0728 | 2.0915 | 0 | 2.1314 | 1.9178 | 5.445 | 5.1717 | 5.4017 | 0 | 5.86 | 4.8033 | 5.2505 | 5.0171 | 4.8292 | 0 | 5.1255 | 4.7925 | 0.8558 | 1.0359 | 0.92772 | 0 | 1.0399 | 1.1327 | 5.1789 | 4.9817 | 4.7098 | 0 | 5.2348 | 5.5028 | 0.8309 | 1.078 | 0.94052 | 0 | 1.0554 | 1.3541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88830 | 160 | 80632 | 151 | 168751 | 474 | 5.2505 | 5.0171 | 4.8292 | 0 | 5.1255 | 4.7925 | 5.1789 | 4.9817 | 4.7098 | 0 | 5.2348 | 5.5028 | 752000 | 2000 | 758000 | 2000 | 1504000 | 4000 | 1506000 | 1500000 | 13.0167 | 5.0029 | 0.99842 | 5.1216 | 1.0518 | 19.96% | 20.54% | 29.6457 | 42.4622 | 2.0798 | 5.3363 | 1516239.99 | 1504913 | 1719639.5771 | 87.51%
2022-08-16 | 2023 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 333446.785 | 6:18 | 19:15 | 7665.13 | 8444 | 8352.11 | 8296.4 | 8314.95 | 8413.1 | 8422.44 | 8657.05 | 8451.82 | 8446.12 | 8372.05 | 8496.49 | 8505.86 | 8421.74 | 8046.7 | 8358.83 | 8088.45 | 8245.83 | 8338.07 | 8397.1 | 8374.23 | 8289.99 | 8156.08 | 8296.48 | 8364.24 | 7447.39 | 8400.8 | 8363.2 | 8337.37 | 8318.92 | 8202.27 | 8519.4 | 8523.55 | 8565.81 | 8598.28 | 8591.6 | 8612.54 | 8439.35 | 8476.25 | 8440.82 | 8961.09 | 8187.24 | 8863.99 | 8062.61 | 8563.37 | 9503.07 | 7158.65 | 9704.21 | 8716.71 | 7071.23 | 8463.93 | 8207.02 | 8804.48 | 8018.21 | 8877.24 | 8114.54 | 8137.28 | 8894.2 | 8053.05 | 8978.34 | 8956.92 | 7959.67 | 9819.31 | 7479.22 | 8501.88 | 8122 | 9342.35 | 8016.49 | 8983.01 | 8128.75 | 8912.63 | 7915.05 | 8112.15 | 8812.16 | 8023.22 | 9031.73 | 8135.66 | 8904.2 | 7900.63 | 8976.53 | 8018.28 | 8732.99 | 8132.84 | 9009.71 | 8898.96 | 7604.73 | 8016.01 | 6860.85 | 8961.19 | 8647.85 | 7986.54 | 8911.02 | 8891.31 | 8330.31 | 8307.52 | 8940.85 | 8969.38 | 7518.2 | 9006.84 | 8112.44 | 8915.55 | 8081.65 | 8861.19 | 8297.34 | 9007.77 | 7918.31 | 9039.96 | 8240.48 | 8926.94 | 8264.71 | 8942.78 | 8322.45 | 8216.5 | 8746.65 | 6319.7 | 9743.57 | 9029.67 | 8895.95 | 9709.47 | 7378.07 | 8997.2 | 8141.77 | 8621.23 | 8202.29 | 8609.68 | 7754.84 | 8846.24 | 8124.28 | 8234.38 | 8367.15 | 8282.79 | 7289.42 | 8234.4 | 7265.32 | 8131.64 | 8131.28 | 9163.34 | 8131.98 | 9263.71 | 8369.95 | 9215.39 | 8335.95 | 9212.82 | 7483.5 | 9050.87 | 9284.41 | 9158.84 | 9162.96 | 9150.69 | 9179.3 | 8470.45 | 9207.24 | 9147.01 | 9162.26 | 9072.03 | 8990.82 | 9183.52 | 7627.85 | 8847.12 | 8358.55 | 31.6682 | 31.4603 | 31.5722 | 0 | 31.4013 | 31.5514 | 0 | 38.8171 | 0 | 0 | 0 | 0 | 5.6516 | 5.3493 | 5.2045 | 0 | 5.3677 | 5.3443 | 9.942 | 10.467 | 9.084 | 0 | 9.548 | 9.283 | 4.6721 | 4.4115 | 4.6117 | 0 | 4.7195 | 4.2211 | 0.94311 | 0.92154 | 1.0186 | 0 | 0.89719 | 0.93212 | 4.6356 | 4.3657 | 4.5641 | 0 | 4.6308 | 4.8685 | 0.91648 | 0.95719 | 1.0181 | 0 | 0.9364 | 1.1043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89502 | 161 | 81312 | 152 | 170097 | 478 | 4.6721 | 4.4115 | 4.6117 | 0 | 4.7195 | 4.2211 | 4.6356 | 4.3657 | 4.5641 | 0 | 4.6308 | 4.8685 | 672000 | 1000 | 680000 | 1000 | 1346000 | 4000 | 1350000 | 1342000 | 12.95 | 4.5272 | 0.94251 | 4.6129 | 0.9865 | 20.82% | 21.39% | 31.5307 | 38.8171 | 5.3835 | 9.6648 | 1355607.83 | 1347267 | 1562780.3242 | 86.21%
2022-08-17 | 2023 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 333446.785 | 6:40 | 19:03 | 2937.7 | 3264.7 | 3267.19 | 3246.32 | 3242.7 | 3257.3 | 3265.3 | 3331.9 | 3256 | 3352.9 | 3175 | 3260.1 | 3202.6 | 3184 | 3027.3 | 3152.7 | 3057 | 3112.9 | 1999.6 | 2001.7 | 3140.3 | 3077.3 | 3114.7 | 3172.4 | 3072.9 | 2655.2 | 3096.3 | 3081.1 | 3123.9 | 3161.7 | 3120.5 | 3219.5 | 3163.6 | 3179.2 | 3179 | 3192.9 | 3230.89 | 3189.3 | 3209.3 | 3166.4 | 3622.1 | 3248.1 | 3483.9 | 2152.4 | 3411.8 | 3846.1 | 2728.8 | 4004.49 | 3295.2 | 2559.6 | 3155.6 | 3017.7 | 3320.6 | 2962.7 | 3327.5 | 2957.8 | 3000.3 | 3362.75 | 2997.3 | 3420.2 | 3438.13 | 2978.69 | 3947.8 | 2820.9 | 3198.3 | 3063.5 | 3638.13 | 3019.8 | 3462 | 3103.4 | 3473.6 | 3040.5 | 3161.4 | 3524.02 | 3083.3 | 3576.5 | 3091 | 3510.5 | 2981.1 | 3528.1 | 3057.6 | 3458.6 | 3134 | 3516.8 | 3452.1 | 2851.1 | 2975.8 | 2519.5 | 3365 | 3228.9 | 2910.3 | 3408.29 | 3296.5 | 3028.4 | 3010.1 | 3317.3 | 2048.2 | 1640.8 | 3268.5 | 2860.4 | 3274.5 | 2858.8 | 3250.2 | 2956.3 | 3346.9 | 2818.5 | 3358.4 | 2998.2 | 3366 | 3054.1 | 3424.1 | 3114.1 | 2909.6 | 3119.7 | 2180.1 | 3612.1 | 3292.9 | 3244.8 | 3656.6 | 2637 | 3348.57 | 2985.4 | 3186.3 | 3051.1 | 3271.56 | 2906.12 | 3350 | 3062.9 | 2993.59 | 3036.3 | 3149.5 | 2650.5 | 3031.9 | 2591.2 | 2983.2 | 2965.4 | 3386.6 | 2893.5 | 3423.5 | 2983.4 | 3367.7 | 2984.4 | 3401.3 | 2686 | 3349.25 | 3472.2 | 3478.2 | 3444.2 | 3412.4 | 3411.8 | 3063.1 | 3421.2 | 3595.39 | 3549.5 | 3431.2 | 3371.1 | 3452.8 | 2746.8 | 3412.6 | 3099.7 | 24.7531 | 26.4633 | 26.3733 | 0 | 26.4358 | 25.0778 | 0 | 29.5322 | 0 | 0 | 0 | 0 | 3.416 | 3.0334 | 3.1533 | 0 | 3.2758 | 2.6553 | 8.548 | 7.662 | 8.174 | 0 | 7.557 | 7.632 | 1.6349 | 1.5622 | 1.7018 | 0 | 1.5528 | 1.4036 | 0.16581 | 0.13392 | 0.15664 | 0 | 0.16281 | 0.14643 | 1.5929 | 1.5509 | 1.6417 | 0 | 1.527 | 1.6457 | 0.16787 | 0.1468 | 0.16898 | 0 | 0.17202 | 0.18554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89750 | 163 | 81561 | 154 | 170596 | 484 | 1.6349 | 1.5622 | 1.7018 | 0 | 1.5528 | 1.4036 | 1.5929 | 1.5509 | 1.6417 | 0 | 1.527 | 1.6457 | 248000 | 2000 | 249000 | 2000 | 499000 | 6000 | 493000 | 493000 | 12.3833 | 1.571 | 0.15312 | 1.5916 | 0.16824 | 9.747% | 10.57% | 25.8207 | 29.5322 | 3.1068 | 7.9146 | 503879.38 | 499200 | 565047.762 | 88.35%
2022-08-18 | 2023 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 333446.785 | 6:23 | 19:10 | 3298.1 | 3667.1 | 3658.1 | 3630.1 | 3647.5 | 3664.2 | 3670.8 | 3738.7 | 3636.4 | 3667.9 | 3582.7 | 3649.9 | 3622.6 | 3598.4 | 3457.1 | 3585.3 | 3100.6 | 3157.9 | 1717.7 | 1728.1 | 3187.1 | 3133 | 3148 | 3195.5 | 2704.4 | 2394.8 | 2641.4 | 2630.1 | 2695.5 | 2710.7 | 2627.4 | 2719.9 | 3361.4 | 3301.8 | 3416.2 | 3407.9 | 3434.2 | 3377.6 | 3375.6 | 3340.9 | 3495.4 | 3161.1 | 3437 | 3093.1 | 3329.7 | 3746.9 | 2772.7 | 3850.5 | 3822.9 | 3069.3 | 3693.1 | 3554.2 | 3850.6 | 3499.2 | 3868.3 | 3507.8 | 3531.7 | 3888 | 3530.6 | 3930.7 | 3944.5 | 3507.4 | 4391.8 | 3298.8 | 3612.3 | 3482.6 | 4017.5 | 3443.8 | 3835.6 | 3504 | 3861.4 | 3450.1 | 3532 | 3868.1 | 3494.6 | 3933 | 3499.2 | 3899.7 | 3387.1 | 3915.3 | 4031.4 | 4479.7 | 4115.3 | 4550.9 | 4500.6 | 3818.2 | 3976.9 | 3413.7 | 4402.5 | 4257.1 | 3886.5 | 4460.9 | 4314.6 | 3992.2 | 3951.1 | 4343.8 | 0 | 0 | 4212.9 | 3111.3 | 4269.6 | 3832.8 | 4223 | 3935.2 | 4263.1 | 3722.6 | 4267.2 | 3881.3 | 4193.5 | 3838.9 | 4175.9 | 3886.2 | 3936.5 | 4177.9 | 2991.3 | 4717 | 4277.3 | 4231.4 | 4075.5 | 3421.6 | 4242.8 | 3798 | 3072.6 | 2919.2 | 4027.6 | 3588.2 | 4157.5 | 3793.8 | 3884.6 | 3973 | 3860.3 | 3405.6 | 3916 | 3459.7 | 3979.2 | 3985.1 | 4605.7 | 4017.2 | 4663.1 | 4131.4 | 4583.3 | 4092.6 | 4577.7 | 3657 | 4530.9 | 4692.7 | 4647.7 | 4627.3 | 4623.2 | 4632.3 | 4215.2 | 4643.8 | 4665.2 | 4648 | 4559.6 | 4508 | 4618.5 | 3774.9 | 4492.4 | 4168 | 25.1982 | 25.9996 | 25.7898 | 0 | 25.8684 | 24.7021 | 0 | 28.8409 | 0 | 0 | 0 | 0 | 7.4359 | 8.3574 | 7.1796 | 0 | 8.0066 | 7.5584 | 13.174 | 13.185 | 14.776 | 0 | 12.866 | 13.582 | 2.3014 | 2.1796 | 2.1525 | 0 | 2.2175 | 1.9623 | 0.28724 | 0.23525 | 0.24843 | 0 | 0.28064 | 0.26 | 2.2457 | 2.1676 | 2.0868 | 0 | 2.1824 | 2.2987 | 0.29328 | 0.25924 | 0.28292 | 0 | 0.29844 | 0.31776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89763 | 164 | 82143 | 156 | 171184 | 487 | 2.3014 | 2.1796 | 2.1525 | 0 | 2.2175 | 1.9623 | 2.2457 | 2.1676 | 2.0868 | 0 | 2.1824 | 2.2987 | 13000 | 1000 | 582000 | 2000 | 588000 | 3000 | 592000 | 585000 | 12.7833 | 2.1627 | 0.26231 | 2.1962 | 0.29033 | 12.13% | 13.22% | 25.5116 | 28.8409 | 7.7076 | 13.5166 | 593370.5 | 588134 | 786268.6238 | 74.8%
2022-08-19 | 2023 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 333446.785 | 6:31 | 19:14 | 7868.7 | 8831 | 8788.8 | 8684.3 | 8742.7 | 8830.6 | 8836 | 9037.42 | 8746.9 | 8734.1 | 8718.8 | 8850.9 | 8822.3 | 8759.1 | 8415.6 | 8692.1 | 8431.8 | 8632.2 | 8735.4 | 8781.2 | 8740 | 8573.4 | 8628.4 | 8779.2 | 8567.4 | 7534 | 8614.1 | 8627.2 | 8648.37 | 8584.3 | 8399.1 | 8784.4 | 8591.9 | 8631.1 | 8752.5 | 8738.6 | 8788.1 | 8608.3 | 8615 | 8511.1 | 9097.3 | 8212.8 | 8948.02 | 7993.4 | 8596.4 | 9613.9 | 7102.4 | 9952.84 | 8992.7 | 7201.2 | 8701.76 | 8369.28 | 9088.12 | 8267.2 | 9054.3 | 8245.7 | 8241.7 | 9069.2 | 8274.1 | 9181.9 | 9120.8 | 8148.53 | 10082.6 | 7614.6 | 8598 | 8161 | 9484.49 | 7993.8 | 9134.5 | 8187.29 | 9110.9 | 8010.4 | 8261.2 | 9074 | 8144.9 | 9262.88 | 8280.6 | 9106.8 | 7999.4 | 9177.7 | 8003.4 | 8907.6 | 8100 | 8998.6 | 8946.4 | 7577.7 | 7988.5 | 6791.1 | 8965.41 | 8618.7 | 7947.4 | 9128.4 | 8916.4 | 8259.8 | 8227.7 | 8975.6 | 8960.2 | 7397.6 | 8968.4 | 7987 | 7666.2 | 7591.1 | 8596.6 | 8165.2 | 8891.3 | 7716.3 | 8928.7 | 8071.6 | 8768 | 8028.8 | 8777.3 | 8113 | 8124.1 | 8659.1 | 6109.7 | 9722.61 | 8870.6 | 8749 | 9602.8 | 7090.7 | 8782.4 | 7842.6 | 8441.6 | 8011.9 | 8446.64 | 7454.4 | 8606.76 | 7810.9 | 7990.5 | 8187 | 7958.9 | 6977.9 | 8064.88 | 7081.6 | 7867.18 | 7827.4 | 8933.4 | 7841.9 | 9004.52 | 8013.5 | 8951.38 | 7980.7 | 8980.2 | 7138.4 | 8742.3 | 9003.69 | 8922.14 | 8881.4 | 8905.7 | 8954.9 | 8121.5 | 8929.43 | 8892.5 | 8876.96 | 8660.3 | 8601.7 | 8839.7 | 7220 | 8628.3 | 8017.9 | 28.207 | 28.2079 | 28.0931 | 0 | 33.16 | 27.9585 | 0 | 37.0677 | 0 | 0 | 0 | 0 | 5.0386 | 5.9172 | 4.8785 | 0 | 2.68 | 5.5944 | 9.4267 | 9.5733 | 9.285 | 0 | 8.48 | 9.5817 | 4.7198 | 4.6377 | 4.525 | 0 | 6.42 | 4.5431 | 0.65427 | 0.76501 | 0.69832 | 0 | 1.02 | 0.7942 | 4.6779 | 4.616 | 4.4006 | 0 | 6.1 | 4.6178 | 0.65362 | 0.81283 | 0.76729 | 0 | 1.22 | 0.81087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90452 | 165 | 82807 | 157 | 172531 | 492 | 4.7198 | 4.6377 | 4.525 | 0 | 6.42 | 4.5431 | 4.6779 | 4.616 | 4.4006 | 0 | 6.1 | 4.6178 | 689000 | 1000 | 664000 | 1000 | 1347000 | 5000 | 1351000 | 1342000 | 12.7167 | 4.9691 | 0.78636 | 4.8825 | 0.85292 | 15.82% | 17.47% | 29.1253 | 37.0677 | 4.8217 | 9.2693 | 1357118.6 | 1347266 | 1576475.184 | 85.46%
2022-08-20 | 2023 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 333446.785 | 6:24 | 19:12 | 6835.1 | 7919.2 | 7957.4 | 7868 | 7916 | 7985.8 | 7989.3 | 8304.5 | 7832.3 | 7586.3 | 7831.5 | 7957.9 | 7878.1 | 7884.8 | 7549.4 | 7854.7 | 7653.2 | 7816.6 | 7902.1 | 7933.5 | 7887.9 | 7721.8 | 7754.2 | 7925.6 | 7753.2 | 6724.7 | 7791.8 | 7791.1 | 7855.7 | 7866.1 | 7725 | 8022 | 7873.9 | 7905.9 | 7972 | 7968.5 | 8039.5 | 7896.2 | 7948.4 | 7834.6 | 8662.6 | 7765.8 | 8520.5 | 7620.9 | 8143.2 | 9209.9 | 6638.4 | 9591.4 | 8144.9 | 6333.7 | 7853 | 7493.9 | 8275.7 | 7388.1 | 8236 | 7390.7 | 7324.7 | 8196.6 | 7377.5 | 8321.6 | 8296 | 7238 | 9354.5 | 6594.8 | 7781.4 | 7369.4 | 8722.5 | 7198.4 | 8312.5 | 7318.6 | 8200.9 | 7077.6 | 7149.1 | 7912.9 | 7076 | 8260.9 | 7279.4 | 8089.9 | 7101.5 | 8145.7 | 7170.7 | 8007 | 7320.1 | 8340.7 | 8214.4 | 6829 | 7236.3 | 6111.6 | 8230.7 | 7904.6 | 7214.9 | 8498.3 | 8251.8 | 7576 | 7531 | 8343.6 | 8345.7 | 6688 | 8376.2 | 7324.8 | 7955.5 | 7316.4 | 8112.6 | 7541.6 | 8345.4 | 7124.8 | 8390.2 | 7509.5 | 8307.2 | 7556.5 | 8353.7 | 7662.9 | 7483.2 | 8056.6 | 5608 | 9218.4 | 8310.2 | 8201.5 | 9091.5 | 6579.2 | 8256.8 | 7312.6 | 7909.8 | 7524.3 | 8001.1 | 7010.5 | 8127.3 | 7336.4 | 7456 | 7631 | 7488.4 | 6497.2 | 7498.8 | 6461.8 | 7303 | 7297 | 8480.2 | 7328.3 | 8549.9 | 7545.4 | 8476.7 | 7473 | 8502.4 | 6641.7 | 8036.2 | 8354.6 | 8266.2 | 8272.3 | 8361 | 8444.3 | 7560.4 | 8350 | 8188.4 | 8171.7 | 8018.2 | 7914.9 | 8126.9 | 6520.9 | 7887 | 7282.5 | 28.3259 | 28.2687 | 28.2194 | 0 | 33.16 | 28.0519 | 0 | 36.0024 | 0 | 0 | 0 | 0 | 4.9493 | 5.6089 | 4.8387 | 0 | 2.68 | 5.3984 | 8.8867 | 8.8817 | 9.5117 | 0 | 8.48 | 8.12 | 4.1433 | 3.9758 | 4.1872 | 0 | 6.42 | 4.1451 | 0.70495 | 0.67798 | 0.884 | 0 | 1.02 | 0.71278 | 4.0752 | 3.9585 | 4.1168 | 0 | 6.1 | 4.0283 | 0.70473 | 0.72801 | 0.92916 | 0 | 1.22 | 0.74553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91075 | 167 | 83425 | 159 | 173769 | 497 | 4.1433 | 3.9758 | 4.1872 | 0 | 6.42 | 4.1451 | 4.0752 | 3.9585 | 4.1168 | 0 | 6.1 | 4.0283 | 623000 | 2000 | 618000 | 2000 | 1238000 | 5000 | 1237000 | 1233000 | 12.8 | 4.5743 | 0.79994 | 4.4558 | 0.86549 | 17.49% | 19.42% | 29.2052 | 36.0024 | 4.6951 | 8.776 | 1245788.3 | 1238067 | 1410775.8097 | 87.76%
2022-08-21 | 2023 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 333845.825 | 6:25 | 19:12 | 8719.8 | 9946.5 | 9952.6 | 9824.4 | 9931.6 | 10033 | 10017.8 | 10385.8 | 9843.4 | 9734.7 | 9828.9 | 9997.6 | 9875.3 | 9878.5 | 9389.8 | 9810.9 | 9340.2 | 9563.8 | 9668 | 9730.9 | 9729.4 | 9573.7 | 9566 | 9738.7 | 9514.8 | 8350.5 | 9656.4 | 9593.3 | 9602.6 | 9564.5 | 9371.3 | 9772.3 | 9531.6 | 9644 | 9753.6 | 9716.6 | 9784.5 | 9590.2 | 9632.3 | 9480.2 | 10373.1 | 9267.8 | 10197.9 | 9047.5 | 9770.3 | 10991.1 | 8019.4 | 11379.4 | 10174.5 | 7960.4 | 9837.8 | 9395.9 | 10303 | 9266.6 | 10265.4 | 9224.4 | 9159.2 | 10204.7 | 9254.4 | 10372.5 | 10352.3 | 9088.7 | 10722.7 | 9487.4 | 9728.3 | 9160 | 10780.5 | 8987.5 | 10472.3 | 9352.7 | 10324 | 9030.1 | 9239.1 | 10192.5 | 9016.8 | 10491.3 | 9255.8 | 10315.7 | 8968.6 | 10422 | 9028.7 | 10000.2 | 9206 | 10356.9 | 10178.1 | 8567.1 | 9005.6 | 7612.2 | 10106.8 | 9760.6 | 8876.9 | 10310.4 | 9975.5 | 9160.4 | 9071.9 | 10035.9 | 9971.1 | 8076.2 | 9919.2 | 8744.5 | 9793.8 | 8683.9 | 9702.9 | 8953.1 | 9869.7 | 8502.1 | 9970.2 | 8934.4 | 9873.8 | 8984.4 | 9947.5 | 9107.1 | 8913.9 | 9504.6 | 6662.2 | 10756.4 | 9810.9 | 9636.3 | 10684.1 | 7750.3 | 9727.1 | 8654.9 | 9385.2 | 8918.5 | 9489.6 | 8295.2 | 9607.9 | 8675.3 | 8732.3 | 8932.1 | 8841.7 | 7628.3 | 8765.1 | 7625.5 | 8639.6 | 8645.2 | 10230.6 | 8884.1 | 10328.5 | 9123.3 | 10137.6 | 8979 | 10078.4 | 7903.9 | 10055.9 | 10442.9 | 10349.9 | 10300.1 | 10273 | 10294.7 | 9307.8 | 10318 | 10261.4 | 10256.4 | 10020.4 | 9938.4 | 10226.5 | 8260.4 | 9890.3 | 9204.4 | 29.0086 | 28.8954 | 28.949 | 0 | 33.16 | 28.6527 | 0 | 39.7774 | 0 | 0 | 0 | 0 | 4.3985 | 4.9401 | 4.0873 | 0 | 2.68 | 4.5758 | 7.8617 | 7.5567 | 7.9267 | 0 | 8.48 | 7.21 | 5.2581 | 5.1243 | 5.1279 | 0 | 6.42 | 4.9813 | 0.83289 | 1.1381 | 1.0415 | 0 | 1.02 | 1.0364 | 5.1972 | 5.0723 | 5.0093 | 0 | 6.1 | 5.0578 | 0.81515 | 1.1829 | 1.084 | 0 | 1.22 | 1.0664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91849 | 168 | 84172 | 161 | 175283 | 501 | 5.2581 | 5.1243 | 5.1279 | 0 | 6.42 | 4.9813 | 5.1972 | 5.0723 | 5.0093 | 0 | 6.1 | 5.0578 | 774000 | 1000 | 747000 | 2000 | 1514000 | 4000 | 1518000 | 1510000 | 12.7833 | 5.3823 | 1.0138 | 5.2873 | 1.0737 | 18.84% | 20.31% | 29.7332 | 39.7774 | 4.1363 | 7.807 | 1526128.8 | 1515400 | 1751494.1869 | 86.52%
2022-08-22 | 2023 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 333845.825 | 6:25 | 19:12 | 6974.5 | 7871.7 | 7881.5 | 7773.1 | 7883.1 | 7971.7 | 7949.2 | 8238.2 | 7819.1 | 7830.3 | 7820 | 7932.9 | 7928.9 | 7890.8 | 7671.8 | 7958.4 | 7686 | 7849.5 | 1049.4 | 1054.4 | 7979.1 | 7866.4 | 1026 | 1040.6 | 7854.6 | 6932.1 | 7936.6 | 7895.5 | 7901.1 | 7892 | 7788.9 | 8061.7 | 7972.3 | 8082.3 | 8061 | 8046.8 | 8091.1 | 7961.5 | 8012.1 | 7930.5 | 8389.8 | 7589.3 | 8277.4 | 7483.4 | 7984.1 | 8935.9 | 6619.2 | 9208.6 | 8183.8 | 6456.1 | 7920.2 | 7629.4 | 8358.3 | 7531.5 | 8306.4 | 7571.1 | 7461.7 | 8269.3 | 7417.1 | 8322.7 | 8257 | 7282.5 | 8541.2 | 7653.3 | 7932.8 | 7564.5 | 8766.3 | 7457.5 | 8508.6 | 7719.5 | 8389.4 | 7425.6 | 7503.2 | 8221.5 | 7328.5 | 8445.3 | 7508 | 8396.8 | 7299.3 | 8477.4 | 7501 | 8204.2 | 6469 | 8408.6 | 8359.4 | 7146.5 | 7607.9 | 6448.6 | 8475 | 8126 | 7506.7 | 8617.3 | 8333.4 | 7720.2 | 7679.2 | 8415.7 | 8398.3 | 6868.8 | 8368.6 | 7432.6 | 8334.3 | 7416.7 | 8222.7 | 7635.2 | 8307.3 | 7275.9 | 8370.7 | 7614.3 | 8219.2 | 7546.3 | 8231.8 | 7636.9 | 7543.7 | 8039.2 | 5706.4 | 9042.7 | 8324.3 | 8202 | 9001.5 | 6686.6 | 8317.9 | 7462.5 | 7969.3 | 7512.1 | 7968.5 | 7101.7 | 8207.5 | 7503.6 | 7541.2 | 7661.8 | 7675.4 | 6651.7 | 7550.7 | 6514.9 | 7484.6 | 7488.8 | 8464.7 | 7482.3 | 8543 | 7653.1 | 8532.5 | 7650.1 | 8570.4 | 6847.7 | 8364.6 | 8624.6 | 8541.8 | 8509.2 | 8474.8 | 8495.7 | 7763.6 | 8519.7 | 8476.5 | 8482.4 | 8300.2 | 8237.5 | 8391 | 6921.2 | 8197.2 | 7706.7 | 27.3405 | 27.4243 | 27.2915 | 0 | 27.1986 | 27.5637 | 0 | 36.2777 | 0 | 0 | 0 | 0 | 4.2323 | 4.3877 | 4.0464 | 0 | 4.2391 | 4.0542 | 7.846 | 9.484 | 8.997 | 0 | 9.478 | 8.855 | 4.1487 | 4.1701 | 4.1453 | 0 | 4.2018 | 3.8894 | 0.60328 | 0.66893 | 0.62582 | 0 | 0.73047 | 0.68863 | 4.0907 | 4.1351 | 4.0427 | 0 | 4.25 | 4.4594 | 0.6021 | 0.71365 | 0.67907 | 0 | 0.74902 | 0.82618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92451 | 170 | 84799 | 163 | 176507 | 506 | 4.1487 | 4.1701 | 4.1453 | 0 | 4.2018 | 3.8894 | 4.0907 | 4.1351 | 4.0427 | 0 | 4.25 | 4.4594 | 602000 | 2000 | 627000 | 2000 | 1224000 | 5000 | 1225000 | 1219000 | 12.7833 | 4.111 | 0.66342 | 4.1956 | 0.714 | 16.14% | 17.02% | 27.3637 | 36.2777 | 4.1919 | 8.932 | 1233767.6 | 1224667 | 1444598.6003 | 84.78%
2022-08-23 | 2023 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 333845.825 | 6:35 | 18:44 | 8434.1 | 9383.7 | 9376.9 | 9298.1 | 9324.5 | 9415.2 | 9416.9 | 9732.7 | 9330.9 | 9300.9 | 9285.4 | 9418.1 | 9367.6 | 9338.1 | 9071.5 | 9359.8 | 9156.7 | 9313.3 | 9385 | 0 | 9356.3 | 9215.7 | 9264.8 | 9417.1 | 9214.2 | 8196.4 | 9271.8 | 9255.8 | 9336.5 | 9367.5 | 9239.6 | 9501 | 9333.1 | 9394.1 | 9418.1 | 9430.8 | 9524.4 | 9423.5 | 9481.9 | 9395.2 | 10138.7 | 9305.1 | 10030.3 | 9154.1 | 9686.6 | 10660.3 | 8177.7 | 10939.3 | 9605.2 | 7651 | 9328.8 | 8996.4 | 9728.9 | 8908.8 | 9693.1 | 8879.3 | 8852.4 | 9691.4 | 8866.3 | 9790.7 | 9776 | 8737.8 | 10076.5 | 9162.5 | 9397.3 | 8958.6 | 10207.1 | 8807 | 9951.9 | 9041.3 | 9771.6 | 8736.2 | 8906.2 | 9601.8 | 8655.2 | 9914.8 | 8979 | 9717.3 | 8741.9 | 9812.4 | 8826.4 | 9501.2 | 8955.4 | 9827 | 9714.7 | 8406.5 | 8952 | 7642.2 | 9787.2 | 9490.1 | 8729.1 | 9901.3 | 9674 | 9056.3 | 9007.2 | 9739.6 | 9724.2 | 8121.9 | 9775.3 | 8803.9 | 9760.1 | 8766 | 9709.8 | 9052.8 | 9832.5 | 8677.5 | 9935.2 | 9075.2 | 9840.4 | 9075.9 | 9886.7 | 9224.3 | 8931.4 | 9511.1 | 6861.7 | 10549.7 | 9792.8 | 9671.2 | 10516.3 | 8017.8 | 9766 | 8843.8 | 9456.9 | 9015.4 | 9519.3 | 8499.8 | 9629.2 | 8841.3 | 8969.8 | 9136.9 | 9003.2 | 7925.8 | 9011.2 | 7962.5 | 8882.2 | 8838.9 | 9893.7 | 8832.1 | 9898 | 9031.3 | 9939 | 8991.6 | 9963.2 | 8069.5 | 9529.8 | 9790.3 | 9725.8 | 9719.1 | 9717.5 | 9850.8 | 8998.1 | 9756.9 | 9605.3 | 9602.6 | 9517.8 | 9414.5 | 9759.5 | 8197.7 | 9318.1 | 8800.9 | 30.5202 | 30.2336 | 30.1418 | 0 | 33.16 | 30.1279 | 0 | 39.4018 | 0 | 0 | 0 | 0 | 4.7317 | 4.7178 | 4.686 | 0 | 2.68 | 4.6207 | 8.7583 | 9.1417 | 9.4233 | 0 | 8.48 | 8.8767 | 5.0142 | 4.9813 | 5.1446 | 0 | 6.42 | 5.0325 | 0.85823 | 0.91997 | 1.0229 | 0 | 1.02 | 0.95624 | 5.0364 | 4.9759 | 5.1389 | 0 | 6.1 | 5.1254 | 0.84018 | 0.97643 | 1.0631 | 0 | 1.22 | 0.99211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93186 | 172 | 85536 | 164 | 177972 | 511 | 5.0142 | 4.9813 | 5.1446 | 0 | 6.42 | 5.0325 | 5.0364 | 4.9759 | 5.1389 | 0 | 6.1 | 5.1254 | 735000 | 2000 | 737000 | 1000 | 1465000 | 5000 | 1469000 | 1460000 | 12.15 | 5.3185 | 0.95546 | 5.2753 | 1.0184 | 17.96% | 19.3% | 30.8367 | 39.4018 | 4.2872 | 8.936 | 1477333.2 | 1465914 | 1709459.7565 | 85.75%
2022-08-24 | 2023 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 334039.69 | 6:32 | 19:04 | 6219.3 | 7114.3 | 7117.7 | 7013 | 7108.3 | 7200.3 | 7200.7 | 7465.4 | 7098.8 | 6935.3 | 7055.6 | 7184.9 | 7103.1 | 7087.9 | 6829.2 | 7094.8 | 6649.3 | 6829.2 | 6918.7 | 0 | 6951.4 | 6858.6 | 6913.9 | 6969.8 | 6776.5 | 6009 | 6900.5 | 6849.7 | 6835.6 | 6753.3 | 6592.1 | 6922.1 | 6736.5 | 6820.8 | 6930.8 | 6869.3 | 6877.7 | 6741.5 | 6747.7 | 6729.3 | 7166.5 | 6481.1 | 7075.1 | 6420.7 | 6807.1 | 7648.1 | 5683.7 | 7970.9 | 7328.7 | 5753 | 7081.1 | 6767.3 | 7374.8 | 6720.1 | 7366.9 | 6637.1 | 6647.6 | 7366.9 | 6670.1 | 7493.7 | 7450.4 | 6563.5 | 7660.5 | 6878 | 7066.8 | 6703.1 | 7813.3 | 6596.8 | 7584.4 | 6824.4 | 7471.2 | 6606.4 | 6675.5 | 3702.2 | 6490.5 | 7543.3 | 6712.5 | 7512.1 | 6511.6 | 7563.8 | 6763.4 | 7284.6 | 6833.2 | 7535.1 | 7396.3 | 6227.3 | 6619.7 | 5549.1 | 7199.3 | 6942.8 | 6295.4 | 7241.3 | 7024.8 | 6505.8 | 6457.8 | 7084.6 | 6966.6 | 5688 | 6902 | 5724.8 | 6855.9 | 6110.9 | 6816.4 | 6304.3 | 6951.3 | 6043.3 | 7042.9 | 6354.7 | 6969.2 | 6381 | 7009.7 | 6466.8 | 6231.2 | 6648.3 | 4764.5 | 7516.3 | 6952.4 | 6839.2 | 7561.9 | 5601.7 | 7002.3 | 6263 | 6679.2 | 6333.4 | 6750.1 | 5961.1 | 6889.1 | 6266.7 | 6261.8 | 6344.5 | 6383.7 | 5571.2 | 6251.7 | 5469.4 | 6199.6 | 6212.8 | 7114.9 | 6189.5 | 7153 | 6357.6 | 7107.1 | 6351.7 | 7105.5 | 5213.2 | 6969.4 | 7171.8 | 7176.5 | 7139.5 | 7144.3 | 7176.4 | 6462.1 | 7130.6 | 7255.8 | 7197.3 | 7020.1 | 6933.3 | 7192.9 | 5822.1 | 6937.3 | 6448.8 | 27.5803 | 27.4664 | 27.0209 | 0 | 33.16 | 27.3765 | 0 | 34.7889 | 0 | 0 | 0 | 0 | 5.0317 | 4.9678 | 4.6922 | 0 | 2.68 | 4.9924 | 8.735 | 9.8917 | 8.1067 | 0 | 8.48 | 9.2333 | 3.7996 | 3.6124 | 3.5619 | 0 | 6.42 | 3.4911 | 0.55134 | 0.56034 | 0.54523 | 0 | 1.02 | 0.59426 | 3.7552 | 3.5966 | 3.4994 | 0 | 6.1 | 3.495 | 0.54613 | 0.58813 | 0.58265 | 0 | 1.22 | 0.61076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93729 | 173 | 86084 | 166 | 179039 | 515 | 3.7996 | 3.6124 | 3.5619 | 0 | 6.42 | 3.4911 | 3.7552 | 3.5966 | 3.4994 | 0 | 6.1 | 3.495 | 543000 | 1000 | 548000 | 2000 | 1067000 | 4000 | 1088000 | 1063000 | 12.5333 | 4.177 | 0.65423 | 4.0892 | 0.70953 | 15.66% | 17.35% | 28.5208 | 34.7889 | 4.4728 | 8.8893 | 1075676.8 | 1067600 | 1251096.8996 | 85.33%
2022-08-25 | 2023 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 334169.755 | 6:31 | 19:07 | 7669.5 | 8525.5 | 8596.7 | 8479.9 | 8555.3 | 8620.6 | 8633.1 | 8917.2 | 8549 | 8484.3 | 8492.1 | 8587.9 | 8501.9 | 8533.1 | 8123.6 | 8431 | 8123.5 | 8244.4 | 8433.7 | 0 | 8419.4 | 8295.2 | 8319.7 | 8454.8 | 8291.8 | 7349.9 | 8344.6 | 8330.5 | 8403 | 8453.3 | 8315.2 | 8575.4 | 8581.6 | 8502.4 | 8486.8 | 8490.3 | 8610.2 | 8502.2 | 8535.6 | 8565.4 | 9134.9 | 8301.6 | 8995.2 | 8182.4 | 8632.8 | 9625.8 | 7188.2 | 9963.4 | 8769.2 | 6939.3 | 8468.5 | 8138.3 | 8814.5 | 8020.3 | 8814.6 | 8020.1 | 8044.6 | 8849.8 | 8074.5 | 8970.3 | 8903.5 | 7940.7 | 9136 | 8258.7 | 8515.3 | 8094.1 | 9311.6 | 7970.4 | 9046.9 | 8216.2 | 8902 | 7929.7 | 8127.6 | 0 | 7922.4 | 9000.4 | 8102.8 | 8916.5 | 7871.2 | 8983.9 | 8130.9 | 8639 | 8198.6 | 8956.7 | 8879.3 | 7658.4 | 8071.7 | 6895.8 | 8834.9 | 8562.4 | 7820.3 | 8939.8 | 8736.6 | 8120.4 | 8067.8 | 8795.5 | 8731.3 | 7271.5 | 8785.1 | 7873.6 | 8760.2 | 7903.6 | 8657.3 | 8105.9 | 8711.7 | 7677.2 | 8786 | 7951.1 | 8604.3 | 7872.9 | 8576.1 | 7915.3 | 7975.5 | 8507 | 6106.9 | 9539.3 | 8732.2 | 8585.8 | 9384.3 | 7019.4 | 8620.4 | 7679.4 | 8292.4 | 7772.8 | 8192.7 | 7237 | 8372.9 | 7617.1 | 7823.6 | 8010.3 | 7719.2 | 6867.9 | 7869.7 | 6960.9 | 7861.3 | 7855 | 8888.5 | 7925.4 | 8942.7 | 8096.2 | 8924.7 | 8056.3 | 8878.9 | 6206.5 | 8740 | 8975.8 | 8916.6 | 8884.5 | 8864.4 | 8909.1 | 8150.3 | 8883 | 8959.2 | 8915 | 8731.3 | 8645.8 | 8987.3 | 7350.1 | 8585.1 | 8066.5 | 27.4798 | 27.2741 | 27.3679 | 0 | 27.148 | 27.2834 | 0 | 36.9499 | 0 | 0 | 0 | 0 | 4.8334 | 6.1027 | 4.5192 | 0 | 5.7721 | 5.3606 | 8.75 | 9.207 | 8.738 | 0 | 8.936 | 9.09 | 4.6005 | 4.5026 | 4.5786 | 0 | 4.5313 | 4.101 | 0.66844 | 0.72208 | 0.71563 | 0 | 0.79051 | 0.69455 | 4.5745 | 4.4899 | 4.5027 | 0 | 4.5773 | 4.6891 | 0.6705 | 0.77267 | 0.76929 | 0 | 0.82356 | 0.83549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94386 | 174 | 86722 | 167 | 180349 | 518 | 4.6005 | 4.5026 | 4.5786 | 0 | 4.5313 | 4.101 | 4.5745 | 4.4899 | 4.5027 | 0 | 4.5773 | 4.6891 | 657000 | 1000 | 638000 | 1000 | 1310000 | 3000 | 1293000 | 1307000 | 12.6 | 4.4628 | 0.71824 | 4.5667 | 0.7743 | 16.09% | 16.96% | 27.3107 | 36.9499 | 5.3176 | 8.9442 | 1320005.2 | 1310000 | 1572386.2583 | 83.31%
2022-08-26 | 2023 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 334169.755 | 6:24 | 19:12 | 9674.5 | 10875.6 | 10942.25 | 10856.4 | 10987.7 | 11111.8 | 11014.1 | 11378.9 | 10870.78 | 10679.8 | 10863.8 | 10901.8 | 11032 | 10969.3 | 10704.6 | 11022.5 | 10765.8 | 10950.2 | 11057.8 | 0 | 5404.8 | 7342.3 | 5005 | 5213.4 | 10899.8 | 9628.9 | 9923.4 | 10965.1 | 10979.46 | 10919 | 10749 | 11138.9 | 11104.16 | 11056 | 11051.4 | 11089.2 | 11188 | 10991.6 | 11030 | 11063.8 | 11422.4 | 10692.92 | 11325.14 | 10543.31 | 10977.3 | 11849.6 | 9210 | 12052.8 | 11221.2 | 8925.8 | 10959.5 | 10572.3 | 11377.1 | 10520.84 | 11273.8 | 10454 | 10284.71 | 11233.3 | 10293.4 | 11271.6 | 11242 | 10095 | 11537.2 | 10506.78 | 10887.3 | 10427.9 | 11719.8 | 10219 | 11465.11 | 10392.03 | 11211.22 | 9959.7 | 10195.5 | 0 | 9844.8 | 11287.1 | 10286.3 | 11083.3 | 10057.1 | 11174.34 | 10229.3 | 10694.9 | 10293.8 | 11222 | 11185.5 | 9789.4 | 10371 | 8876.8 | 11445.3 | 11064 | 10330.39 | 11537.59 | 11177.6 | 10470.7 | 10410.9 | 11273.7 | 11230.2 | 9514.7 | 11299.5 | 10260.14 | 11145 | 10179.5 | 11054.9 | 10430.75 | 11173.8 | 9900.87 | 11273.7 | 10329.3 | 11204.1 | 10405.6 | 11283.6 | 10511 | 10437.77 | 11020.3 | 7851.5 | 11977.6 | 11199.1 | 11134.4 | 11841.49 | 9168.4 | 11178.8 | 10120.6 | 10881 | 10345.2 | 10870.6 | 9677.28 | 10939.18 | 10238.3 | 10352.34 | 10572.6 | 10285.38 | 9070.1 | 10480.32 | 9220.2 | 10399.2 | 10414.7 | 11486.02 | 10301.6 | 11633.97 | 10572.9 | 11507.4 | 10509.03 | 11491.4 | 7600.1 | 11301.2 | 11533.6 | 11465.9 | 11479.4 | 11534.7 | 11577.9 | 10751.6 | 11509.72 | 11380.1 | 11373.8 | 11240.64 | 11181.5 | 11510.47 | 9622.1 | 11059.8 | 10539.28 | 28.8524 | 28.8822 | 28.7974 | 0 | 28.5316 | 29.0838 | 0 | 41.7605 | 0 | 0 | 0 | 0 | 4.3479 | 4.5817 | 4.0901 | 0 | 4.3275 | 4.3206 | 8.5733 | 7.715 | 8.5667 | 0 | 7.4583 | 8.43 | 6.0216 | 5.962 | 5.8934 | 0 | 5.9638 | 5.4769 | 1.0985 | 1.2309 | 1.2655 | 0 | 1.2122 | 1.1314 | 6.1197 | 5.9681 | 5.988 | 0 | 6.0983 | 6.1988 | 1.0614 | 1.2818 | 1.2831 | 0 | 1.2471 | 1.3683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95206 | 175 | 87573 | 169 | 182012 | 523 | 6.0216 | 5.962 | 5.8934 | 0 | 5.9638 | 5.4769 | 6.1197 | 5.9681 | 5.988 | 0 | 6.0983 | 6.1988 | 820000 | 1000 | 851000 | 2000 | 1663000 | 5000 | 1668000 | 1658000 | 12.8 | 5.8636 | 1.1877 | 6.0746 | 1.2483 | 20.26% | 20.55% | 28.8295 | 41.7605 | 4.3336 | 8.1487 | 1678865.38 | 1664400 | 2049695.4652 | 81.2%
2022-08-27 | 2023 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 334169.755 | 6:22 | 19:13 | 10594.4 | 11781.8 | 11633.5 | 11679.7 | 11506.8 | 11559.2 | 11675.2 | 11925.9 | 11837 | 11626.4 | 11572.4 | 11801.4 | 11482.3 | 11571.6 | 10829.2 | 11287.9 | 10893.2 | 11073.6 | 11165.6 | 0 | 10994.1 | 9585 | 5360.2 | 8255.9 | 11072.4 | 9881.9 | 10628.2 | 11121.5 | 11086.8 | 11010.7 | 10855.3 | 11250.2 | 11241.4 | 11269.5 | 11315.7 | 11262.5 | 11295.9 | 11093.5 | 11119.6 | 11143.2 | 12223.6 | 11335 | 12105.7 | 11163.2 | 11753.4 | 12615.7 | 9874.7 | 12875.7 | 11810.5 | 9513.7 | 11474.8 | 11123.9 | 11818.3 | 10874.3 | 11877.3 | 10901.9 | 11047.2 | 12013 | 11064.2 | 12134.3 | 12152.7 | 10966 | 12500 | 11501.9 | 11697.1 | 11204.5 | 12593.4 | 11015.6 | 12353.2 | 11380.6 | 12239.7 | 10994.5 | 11184.6 | 12067.7 | 10933.3 | 12339.5 | 11267.1 | 12219.9 | 10946.9 | 12283.3 | 11294.4 | 11829.1 | 11407.7 | 12214.8 | 12161.4 | 10573.2 | 11058.4 | 9473.4 | 12044.3 | 11727.2 | 10733.5 | 12032.9 | 11645.4 | 10843.8 | 10750.9 | 11729.9 | 11648.2 | 9811.1 | 11664.9 | 10540.3 | 11438 | 10444.6 | 11371.2 | 10744.3 | 9679.7 | 8655.3 | 9775.9 | 9046 | 9757.7 | 9165.2 | 9880.2 | 9288.3 | 10738.7 | 11332.6 | 8077.6 | 12330.6 | 11547.1 | 11484.2 | 12165 | 9436.4 | 11543.3 | 10472.4 | 11230.9 | 10717.1 | 11280.2 | 10076.7 | 11387.8 | 10653.4 | 10637.8 | 10860.8 | 10684.1 | 9333 | 10751.6 | 9515.2 | 11108 | 11041.7 | 12087.8 | 10975 | 12098.3 | 11173.7 | 12203.7 | 11159.6 | 12225.8 | 7635.8 | 11660.7 | 11895.5 | 11860.3 | 11911.4 | 12017.7 | 12065.2 | 11165.1 | 11939.2 | 11672.3 | 11678.3 | 11538.7 | 11459.3 | 11881.3 | 9883.5 | 11380.1 | 10797.2 | 29.3415 | 29.3935 | 29.2582 | 0 | 28.9821 | 29.6361 | 0 | 41.5276 | 0 | 0 | 0 | 0 | 4.6681 | 4.762 | 4.6354 | 0 | 4.4969 | 4.517 | 7.8067 | 7.5233 | 8.075 | 0 | 7.2583 | 7.45 | 6.3926 | 6.036 | 6.4293 | 0 | 6.1381 | 5.8077 | 1.2415 | 1.4063 | 1.4366 | 0 | 1.3173 | 1.2683 | 6.497 | 6.0344 | 6.5246 | 0 | 6.3219 | 6.5486 | 1.182 | 1.43 | 1.4465 | 0 | 1.3428 | 1.5356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96094 | 177 | 88445 | 170 | 183766 | 527 | 6.3926 | 6.036 | 6.4293 | 0 | 6.1381 | 5.8077 | 6.497 | 6.0344 | 6.5246 | 0 | 6.3219 | 6.5486 | 888000 | 2000 | 872000 | 1000 | 1754000 | 4000 | 1757000 | 1750000 | 12.85 | 6.1607 | 1.334 | 6.3853 | 1.3874 | 21.65% | 21.73% | 29.3223 | 41.5276 | 4.6159 | 7.6227 | 1768985.4 | 1754400 | 2149968.1206 | 81.6%
2022-08-28 | 2023 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 334190.655 | 6:25 | 19:10 | 10204.1 | 11587 | 11756.7 | 11618.1 | 11775 | 11880.5 | 11803.1 | 12204.8 | 11538.9 | 11127.5 | 11595.92 | 11599.9 | 11897.7 | 11722.09 | 11725.97 | 11990.1 | 11655 | 11553 | 12148 | 11925.4 | 12173.6 | 12186.9 | 11924.6 | 12082.5 | 12005.5 | 10628.59 | 11922.3 | 12031.5 | 12104.6 | 12052.5 | 11901.2 | 12281.3 | 12164.97 | 12178.3 | 12176.1 | 12203.1 | 12311.1 | 12132.7 | 12178.3 | 12165.1 | 12178.16 | 11160 | 12044.9 | 10954.1 | 11735.5 | 12999.8 | 10131.4 | 13232.3 | 12003.2 | 9549.5 | 11804.96 | 11328.84 | 12373.02 | 11400.2 | 12113.23 | 11318 | 10937.1 | 11898.8 | 10986.88 | 12018.05 | 11884.7 | 10731.4 | 12105.3 | 10910.5 | 11331.8 | 10873.3 | 12308.9 | 10644.8 | 11966.6 | 10817.43 | 11655.1 | 10391.9 | 10452 | 11701.5 | 10700 | 11563.3 | 10299.4 | 11756.4 | 10556.2 | 11430.41 | 10640.4 | 11117.5 | 10681.5 | 11733.6 | 11691.8 | 10225.12 | 10802.6 | 9276.4 | 12079.51 | 11600.9 | 11007.2 | 12423.05 | 12177.7 | 11513.68 | 11503.35 | 12223.8 | 12131.2 | 10226.6 | 12221.1 | 11100.3 | 12330.5 | 11185.9 | 12294.3 | 11577.9 | 12230.31 | 10984.6 | 12358.7 | 11464.1 | 12332.44 | 11578 | 12357.93 | 11693.5 | 11174.54 | 11826.8 | 8747.7 | 13045.5 | 12380.56 | 12190.1 | 12742.8 | 10141 | 12409.1 | 11336.5 | 11926.3 | 11662.6 | 12225.7 | 10947.7 | 12251.8 | 11431.42 | 11315.8 | 11414.1 | 11492.5 | 10036.3 | 11252.5 | 9808.2 | 10835.89 | 10542.9 | 11793.44 | 10666.8 | 11944.6 | 10918.1 | 11911.5 | 10841 | 10943.5 | 8603.5 | 11534.18 | 11793.14 | 11664.6 | 11706.8 | 11746.29 | 11816.3 | 10958.6 | 11801.26 | 11567.1 | 11546.6 | 11306.75 | 11267.6 | 11709.3 | 9824.3 | 11230 | 10693 | 29.6743 | 29.7794 | 29.5715 | 0 | 33.16 | 29.4022 | 0 | 44.0298 | 0 | 0 | 0 | 0 | 4.3123 | 4.5942 | 4.2438 | 0 | 2.68 | 4.4331 | 8.3067 | 7.5033 | 8.1033 | 0 | 8.48 | 7.2567 | 6.54 | 6.6469 | 6.4603 | 0 | 6.42 | 6.6447 | 1.3635 | 1.5635 | 1.512 | 0 | 1.02 | 1.4033 | 6.667 | 6.6332 | 6.6136 | 0 | 6.1 | 6.7853 | 1.2983 | 1.576 | 1.5201 | 0 | 1.22 | 1.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97020 | 178 | 89352 | 172 | 185598 | 531 | 6.54 | 6.6469 | 6.4603 | 0 | 6.42 | 6.6447 | 6.667 | 6.6332 | 6.6136 | 0 | 6.1 | 6.7853 | 926000 | 1000 | 907000 | 2000 | 1832000 | 4000 | 1830000 | 1828000 | 12.75 | 6.5424 | 1.3725 | 6.5598 | 1.4089 | 20.98% | 21.48% | 30.3175 | 44.0298 | 4.0527 | 7.93 | 1842054.48 | 1826867 | 2221914.4712 | 82.22%
2022-08-29 | 2023 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 334190.655 | 6:32 | 19:08 | 9291.4 | 10350.1 | 10359.2 | 10323.3 | 10342 | 10356 | 10369.8 | 10672.9 | 10394.9 | 10291.5 | 10239.9 | 10383 | 10351.6 | 10361.3 | 9817.3 | 10213 | 10022 | 10100.6 | 10191.4 | 10082.1 | 10165.6 | 10197.3 | 9755.1 | 9968.5 | 9977.4 | 8940.5 | 10121.6 | 10090.2 | 9931 | 9924.4 | 9788.2 | 10139.8 | 10081.3 | 10197.5 | 10222.1 | 10195.4 | 10241.5 | 10005.9 | 10031.7 | 10019.3 | 10954.9 | 10128.6 | 10889.3 | 10062.9 | 10475.7 | 11388 | 8621 | 11736 | 10699.5 | 8618 | 10368.5 | 9961.2 | 10685.6 | 9818.6 | 10692.5 | 9685 | 9889.7 | 10845.9 | 9902.8 | 11002.9 | 11024.8 | 9734.4 | 11499.5 | 10435.9 | 10499.9 | 10023.2 | 11465.3 | 9867.1 | 11195.8 | 10145.9 | 10999.4 | 9753 | 9797.4 | 10992.2 | 10139.9 | 10863 | 9714.8 | 11297 | 10097.5 | 10913 | 10036.7 | 10514.6 | 10070.8 | 11017.7 | 10950.8 | 9440.3 | 9852.7 | 8480.5 | 10672.8 | 10363.5 | 9517.9 | 10777.2 | 10434.5 | 9640.4 | 9521.8 | 10405.6 | 9285.7 | 9718.2 | 10458.1 | 9409.3 | 10196.6 | 9349.5 | 10185.5 | 9647.2 | 10288.1 | 9179.9 | 10462.6 | 9669.2 | 10369.6 | 9626 | 10471.7 | 9733.1 | 9586.2 | 10281 | 7459 | 11411.9 | 10610.4 | 10497.5 | 11396.9 | 8692.6 | 10549.2 | 9482.9 | 10215.2 | 9570.1 | 10063.2 | 8961.7 | 10299.9 | 9525.1 | 9608.5 | 9830 | 9559.6 | 8447.1 | 9610 | 8533.5 | 9610.4 | 9173.6 | 10803.8 | 9536.3 | 10873.7 | 9698.3 | 10711.1 | 9658.9 | 9758.7 | 7775.7 | 10524.8 | 10826 | 10744.7 | 10679.9 | 10718.8 | 10832 | 9981.1 | 10813.4 | 10523.8 | 10449.3 | 10257.3 | 10204.3 | 10642.8 | 8992.9 | 10363.7 | 9662.2 | 29.2755 | 30.0932 | 30.16 | 0 | 29.8148 | 30.4865 | 0 | 43.5557 | 0 | 0 | 0 | 0 | 3.1364 | 3.2528 | 3.0832 | 0 | 3.185 | 3.1372 | 6.1067 | 5.6117 | 5.6983 | 0 | 5.47 | 5.645 | 5.7027 | 5.5412 | 5.695 | 0 | 5.7223 | 5.1803 | 1.1105 | 1.3698 | 1.2316 | 0 | 1.2794 | 1.1666 | 5.7576 | 5.526 | 5.6941 | 0 | 5.9357 | 5.8654 | 1.0506 | 1.3875 | 1.2507 | 0 | 1.3024 | 1.4022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97838 | 180 | 90147 | 173 | 187197 | 537 | 5.7027 | 5.5412 | 5.695 | 0 | 5.7223 | 5.1803 | 5.7576 | 5.526 | 5.6941 | 0 | 5.9357 | 5.8654 | 818000 | 2000 | 795000 | 1000 | 1599000 | 6000 | 1610000 | 1593000 | 12.6 | 5.5683 | 1.2315 | 5.7558 | 1.2787 | 22.12% | 22.22% | 29.966 | 43.5557 | 3.1589 | 5.7063 | 1619150.3 | 1606600 | 1929754.5391 | 83.25%
2022-08-30 | 2023 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 334201.075 | 6:24 | 19:07 | 10568.9 | 11653.6 | 11319.8 | 11254.92 | 11299 | 11314 | 11466.83 | 11874.3 | 11775.79 | 11709.5 | 11600.3 | 11768.6 | 11641.3 | 11742.3 | 11309.29 | 11622.38 | 11645.2 | 11666.4 | 11901.3 | 11844.5 | 11717.3 | 11818.64 | 11352.3 | 11571.9 | 11598.4 | 10399.66 | 11908.5 | 11724.9 | 11614.38 | 11519.2 | 11446.8 | 11840.9 | 11900.3 | 11917.7 | 11907.8 | 11868.6 | 11942.9 | 11676.3 | 11725.5 | 11750.7 | 11914.47 | 10826.6 | 11774.23 | 10565.2 | 11382.6 | 12630.31 | 9713.3 | 12977.34 | 12201.6 | 9848.8 | 11984.1 | 11616.1 | 12406.85 | 11347.05 | 12367.08 | 11429.2 | 11445.5 | 12392.64 | 11336.9 | 12605.35 | 12534.07 | 11146.2 | 12902.5 | 11766 | 12081.8 | 11308.2 | 12976.6 | 11111.1 | 12735.1 | 11394.56 | 12412.9 | 11022.6 | 11290.5 | 12154.6 | 11604.35 | 12238.4 | 11049.6 | 12663.29 | 11519.8 | 12346.9 | 11302.1 | 11798.6 | 11378.8 | 12400.2 | 12326.4 | 10686.1 | 11321.9 | 9735.6 | 12705.94 | 12117.1 | 11464.9 | 12934.6 | 12630.3 | 11861.58 | 11659.2 | 12545.9 | 11496.9 | 11886.95 | 12601.7 | 11599.9 | 12523.49 | 11575.4 | 12504.29 | 11868.1 | 12576.4 | 11323.7 | 12663.1 | 11867.6 | 12492.6 | 11776.9 | 12577.1 | 12064.13 | 11714.77 | 12315.7 | 11715.5 | 11631.4 | 12637.49 | 12532.3 | 13398.91 | 10428.5 | 12609.43 | 11552.9 | 12439.7 | 11866.16 | 12306.1 | 11039.87 | 12383.7 | 11609.25 | 11581.3 | 11786.9 | 11565.49 | 10160.9 | 11633.58 | 10234 | 11477 | 10920.24 | 12516.3 | 11320.9 | 12586.14 | 11688.1 | 12735 | 11772.5 | 11798.4 | 10736.8 | 12373.24 | 12602.9 | 12620.72 | 12538.1 | 12561 | 12494.7 | 11565.7 | 12465.9 | 12496.9 | 12303.3 | 12428.02 | 12192.3 | 12616.29 | 10834 | 12314.6 | 11531.14 | 31.7343 | 31.8284 | 31.9642 | 0 | 31.8093 | 32.0146 | 0 | 48.1006 | 0 | 0 | 0 | 0 | 2.366 | 2.3672 | 2.3747 | 0 | 2.3636 | 2.2888 | 5.0933 | 5.1417 | 5.3117 | 0 | 5.1533 | 4.4167 | 6.5969 | 6.3397 | 6.2727 | 0 | 6.9765 | 6.2309 | 1.3584 | 1.471 | 1.4312 | 0 | 1.4472 | 1.2841 | 6.7801 | 6.3296 | 6.4343 | 0 | 7.1516 | 6.9805 | 1.2924 | 1.48 | 1.4366 | 0 | 1.4774 | 1.555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98769 | 181 | 91092 | 175 | 189071 | 540 | 6.5969 | 6.3397 | 6.2727 | 0 | 6.9765 | 6.2309 | 6.7801 | 6.3296 | 6.4343 | 0 | 7.1516 | 6.9805 | 931000 | 1000 | 945000 | 2000 | 1874000 | 3000 | 1873000 | 1871000 | 12.7167 | 6.4833 | 1.3984 | 6.7352 | 1.4483 | 21.57% | 21.5% | 31.8702 | 48.1006 | 2.3521 | 5.0233 | 1890106.7 | 1874767 | 2216561.2711 | 84.58%
2022-08-31 | 2023 | 2022 | Year_1 | Year_1 | 2022-09-01 | 31 | 334201.075 | 6:27 | 19:12 | 11301.81 | 12738.06 | 12660.24 | 12609.69 | 12399 | 12434 | 12788.81 | 13082.31 | 12756 | 12680 | 12591 | 12722 | 12638 | 12679 | 12038 | 12565 | 12303.57 | 12230.69 | 12467.88 | 12499.24 | 12277 | 12321.68 | 11974.02 | 12160.55 | 12202.04 | 10860.6 | 12465.87 | 12280.7 | 12201.4 | 12060.7 | 11854.04 | 12380.17 | 12389.54 | 12477.71 | 12483.59 | 12462.42 | 12446.03 | 12134.82 | 12138.35 | 12188.1 | 13264.01 | 12199.96 | 13029.1 | 11988.23 | 12602.89 | 13616.37 | 10563.9 | 13961.26 | 12936.62 | 10236.64 | 12577.15 | 12156.95 | 13062.15 | 11989.61 | 12979.98 | 11972.61 | 11899.76 | 12927.25 | 11998.63 | 13157.54 | 13127.19 | 11794.96 | 13382.31 | 12224.21 | 12480.82 | 11832.12 | 13386.15 | 11574.1 | 13120.64 | 11939.67 | 12890.28 | 11510.6 | 11537.5 | 12980.33 | 11887.89 | 12867.36 | 11496.16 | 13107.42 | 11847.02 | 12805.56 | 11906.38 | 12481.92 | 11951.72 | 13012.44 | 12847.23 | 11048.5 | 11680.41 | 9893.8 | 12634.51 | 12259.6 | 11324.78 | 12890.74 | 12628.53 | 11820.58 | 11721.08 | 12591.4 | 11347.92 | 11675.97 | 12487.7 | 11209.21 | 12610.26 | 11330.63 | 12499.04 | 11639 | 12600.82 | 11121.33 | 12693.2 | 11668.12 | 12527.98 | 11633.24 | 12527.94 | 11805.3 | 11278.93 | 11920.38 | 11432.1 | 11173.24 | 12356.04 | 12046.84 | 12353.88 | 11280.57 | 12440.44 | 11240.45 | 12300.7 | 11645.4 | 12144.36 | 10685.07 | 12219.4 | 11306.5 | 10955.35 | 11127.64 | 11252.9 | 9738.2 | 10956.6 | 9673.28 | 11152.36 | 10552.73 | 12384.08 | 11068.46 | 12381.87 | 11357.73 | 12372.58 | 11268.71 | 11335 | 11047.71 | 12145 | 12384.16 | 12431.32 | 12326.96 | 12334.88 | 12343.34 | 11387.04 | 12301.99 | 12279.92 | 12113.96 | 12274.15 | 11956.79 | 12334.67 | 10436.2 | 12081.34 | 11249.58 | 31.7296 | 32.1928 | 32.1058 | 0 | 32.0762 | 32.1709 | 0 | 46.5346 | 0 | 0 | 0 | 0 | 4.1275 | 4.1199 | 4.1144 | 0 | 3.8982 | 3.8314 | 6.7733 | 6.9833 | 7.0133 | 0 | 6.4817 | 6.1567 | 7.03 | 6.602 | 6.9345 | 0 | 6.5239 | 6.022 | 1.4681 | 1.5612 | 1.596 | 0 | 1.4042 | 1.2797 | 7.2484 | 6.5822 | 7.1213 | 0 | 6.7649 | 6.7074 | 1.3987 | 1.5671 | 1.5932 | 0 | 1.4268 | 1.5509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99756 | 183 | 92034 | 176 | 190987.91 | 544 | 7.03 | 6.602 | 6.9345 | 0 | 6.5239 | 6.022 | 7.2484 | 6.5822 | 7.1213 | 0 | 6.7649 | 6.7074 | 987000 | 2000 | 942000 | 1000 | 1916910 | 4000 | 1926000 | 1912910 | 12.75 | 6.6225 | 1.4618 | 6.8848 | 1.5073 | 22.07% | 21.89% | 32.0551 | 46.5346 | 4.0182 | 6.6817 | 1933758.61 | 1918000 | 2278183.6845 | 84.19%
2022-09-01 | 2023 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 334201.075 | 6:23 | 19:03 | 11660.4 | 12932.2 | 12936.92 | 12928.85 | 12885.34 | 12997.1 | 13013.8 | 13290.83 | 12981.5 | 12791.1 | 12873.92 | 12995.5 | 13022.83 | 12937.3 | 12530.1 | 12977.7 | 12567.06 | 12658.34 | 12695.7 | 12686.48 | 12682.9 | 12703.82 | 12499.7 | 12629.35 | 12780.6 | 11320.03 | 12863.7 | 12857.1 | 13085 | 12869 | 12703.3 | 13042.9 | 9871.99 | 9920.8 | 9601 | 9605.62 | 9227.6 | 9098.48 | 12955.1 | 12955 | 13488.3 | 12622.6 | 13401.85 | 12478.9 | 13078.3 | 14003.46 | 12399.9 | 13509 | 12312.8 | 11916.7 | 12989.7 | 12568.1 | 13414.61 | 12373.32 | 13365.9 | 12398.6 | 12280.12 | 13259.6 | 12304.45 | 13427.1 | 13361.6 | 12068.3 | 13611.88 | 12617.27 | 12900.2 | 12278 | 12914.59 | 13165.3 | 13503.2 | 12422.7 | 13354.2 | 11984.6 | 11976.7 | 13424.5 | 12377.07 | 13325.6 | 12028 | 13522.18 | 12346.5 | 13238.39 | 12358.05 | 12926.1 | 12407.11 | 13427.5 | 13268.4 | 11542.4 | 11271.2 | 10365.3 | 13235 | 12838.4 | 11950.9 | 13488.3 | 13186.76 | 12425.53 | 12300.5 | 13224.4 | 11921 | 11802 | 13191 | 11997 | 13116 | 12004 | 13067 | 12342 | 13096 | 11739 | 12799 | 12065 | 12911 | 12033 | 13100 | 12407 | 12142 | 12834 | 12306 | 12079 | 13147 | 13046 | 13998 | 11497 | 12797 | 12124 | 12606 | 11944 | 12934 | 11423 | 12989 | 12163 | 12237 | 12445 | 12216 | 10689 | 12264 | 10689 | 12101 | 11448 | 13430.8 | 12122.2 | 13530.25 | 12517.6 | 13402.36 | 12355.93 | 12400.1 | 12087.2 | 13277 | 13550 | 13544 | 13473.6 | 13365 | 13216 | 12612 | 13486.71 | 13356 | 13247 | 13389 | 13144 | 13519 | 11593 | 13190 | 12521 | 31.3454 | 31.8873 | 31.5166 | 0 | 31.5087 | 31.9745 | 0 | 45.7474 | 0 | 0 | 0 | 0 | 5.0752 | 5.1143 | 5.0999 | 0 | 4.8339 | 4.8064 | 8.8833 | 8.4183 | 8.825 | 0 | 8.3 | 8.3933 | 7.0858 | 6.863 | 7.0551 | 0 | 7.0466 | 6.5834 | 1.4939 | 1.6101 | 1.6455 | 0 | 1.5 | 1.3529 | 7.3475 | 6.8453 | 7.308 | 0 | 7.2979 | 7.3132 | 1.4177 | 1.611 | 1.6286 | 0 | 1.5169 | 1.6512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100756 | 184 | 93040 | 178 | 192984 | 549 | 7.0858 | 6.863 | 7.0551 | 0 | 7.0466 | 6.5834 | 7.3475 | 6.8453 | 7.308 | 0 | 7.2979 | 7.3132 | 1000000 | 1000 | 1006000 | 2000 | 1996090 | 5000 | 2003000 | 1991090 | 12.6667 | 6.9268 | 1.5205 | 7.2224 | 1.5651 | 21.95% | 21.67% | 31.6465 | 45.7474 | 4.986 | 8.564 | 2011903.65 | 1998133 | 2409413.03 | 82.93%
2022-09-02 | 2023 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 334201.075 | 6:24 | 19:07 | 10984.6 | 12304.5 | 12343.3 | 12238.2 | 12335.25 | 12475.3 | 12439.2 | 12712.9 | 12311.3 | 11969.1 | 12328.6 | 12342.3 | 12459 | 12458.8 | 12012.9 | 12448.4 | 10718.3 | 10829 | 10901.8 | 10927.89 | 10867.69 | 10948.63 | 10817.3 | 10911.9 | 10895.5 | 9631.8 | 10929.3 | 10870.3 | 11098 | 10972 | 10731.6 | 11109.1 | 12012.26 | 12061.2 | 12144.9 | 12159.8 | 12218.74 | 12003.6 | 12528.8 | 12575.9 | 13176 | 12468 | 13070 | 12185 | 12731 | 13552 | 12078 | 13140 | 11872.9 | 11466.3 | 12492.4 | 12056.5 | 12871.2 | 11895.53 | 12779.5 | 11954.63 | 11700.05 | 12558.7 | 11758 | 12725.68 | 12655.11 | 11515.38 | 12808 | 11910 | 12271.8 | 11714.1 | 12303.1 | 12528.3 | 12829.09 | 11830.9 | 12666.2 | 11431.77 | 11393.5 | 12747.17 | 11721.5 | 12640.3 | 11443.6 | 12751.9 | 11677.3 | 12511.42 | 11688.63 | 12175.8 | 11694.9 | 12709 | 12544 | 10938.7 | 11228.9 | 9809.2 | 12435.51 | 11510.5 | 11443.9 | 12919.2 | 12734.7 | 12013.3 | 11912.8 | 12689.1 | 11521.9 | 11966.4 | 12730.7 | 11532.05 | 12709.84 | 11533.2 | 12610.85 | 11964.31 | 12452.9 | 11311.6 | 12312 | 11610 | 12697.57 | 11773.1 | 12573.5 | 12055.9 | 11567.2 | 12247.72 | 11786.09 | 11612.2 | 12697 | 12395.5 | 12813.4 | 11809.2 | 12804 | 12172 | 12656.7 | 11961.5 | 12321.7 | 11063.3 | 12530.5 | 11674.1 | 11602.3 | 11617.4 | 11673.7 | 10155.7 | 11487.02 | 9945.18 | 11367.3 | 10834 | 12632.19 | 11367.3 | 12804.68 | 11892.3 | 12661.8 | 11699.1 | 11729.81 | 11454.5 | 12501.66 | 12691.5 | 12733.4 | 12652 | 12624 | 12685.2 | 11886.7 | 12654.31 | 12736.4 | 12585.2 | 12566.8 | 12477.1 | 12737.02 | 10969.7 | 12426.3 | 11827.27 | 31.1981 | 31.6067 | 31.6809 | 0 | 31.3331 | 31.7908 | 0 | 47.3741 | 0 | 0 | 0 | 0 | 3.925 | 3.9336 | 3.9116 | 0 | 3.7819 | 3.7746 | 6.535 | 7.5983 | 6.755 | 0 | 6.0067 | 6.09 | 6.936 | 6.7437 | 7.0259 | 0 | 6.8817 | 6.2825 | 1.4725 | 1.5823 | 1.642 | 0 | 1.4661 | 1.2983 | 7.1521 | 6.7184 | 7.2222 | 0 | 7.0908 | 7.0048 | 1.4014 | 1.5863 | 1.6353 | 0 | 1.4877 | 1.5767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101709 | 185 | 93996 | 179 | 194886 | 552 | 6.936 | 6.7437 | 7.0259 | 0 | 6.8817 | 6.2825 | 7.1521 | 6.7184 | 7.2222 | 0 | 7.0908 | 7.0048 | 953000 | 1000 | 956000 | 1000 | 1902000 | 3000 | 1907000 | 1899000 | 12.7167 | 6.774 | 1.4922 | 7.0376 | 1.5375 | 22.03% | 21.85% | 31.5219 | 47.3741 | 3.8653 | 6.597 | 1920505.7 | 1903034 | 2340809.2319 | 81.3%
2022-09-03 | 2023 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 334201.075 | 6:23 | 19:05 | 11901.6 | 13002.7 | 12939.4 | 12950.9 | 12503.8 | 12681.1 | 13019.1 | 13251.3 | 12764.4 | 12458.9 | 12682.9 | 12712 | 12788.1 | 12849.2 | 12487.6 | 12897.6 | 12608.4 | 12917.2 | 12737.2 | 12769.5 | 12603.5 | 12932.2 | 12830.9 | 12940.3 | 12557 | 11238.2 | 12674.4 | 12679.6 | 12717.4 | 12428.6 | 12464 | 12733.7 | 12586.9 | 12542.6 | 12628.4 | 12527.1 | 12631.5 | 12636.9 | 12727.6 | 12753.8 | 13282.3 | 12609.2 | 13017 | 12484.6 | 12968.4 | 13973.7 | 12432 | 13541 | 12389.3 | 12048 | 12950.6 | 12501.4 | 13381.4 | 12269.4 | 13378.9 | 12508.8 | 12417.5 | 13298.6 | 12456.8 | 13487.6 | 13445.4 | 12252.2 | 13657.5 | 12701 | 12787.8 | 12149.1 | 12870.9 | 13108 | 13843 | 12450.5 | 13257 | 12155.3 | 11911.7 | 13418.5 | 12133 | 13259.9 | 12127.3 | 13235.9 | 12426.3 | 13047.1 | 12332.5 | 12810.8 | 12134.2 | 13377.5 | 12239.7 | 12818.4 | 11933.4 | 10468.3 | 12997.2 | 12344.8 | 11955.1 | 13342.8 | 13056.1 | 12377.2 | 12250.5 | 13036.6 | 11952.5 | 12449.79 | 13134 | 12047.4 | 13128.1 | 11941.4 | 13061.5 | 12404.7 | 12898.6 | 11864.8 | 13121.3 | 12361.5 | 13063 | 12286.1 | 12973.9 | 12573.2 | 12127.5 | 12756.6 | 12257.2 | 12154.5 | 10885.7 | 11547.8 | 13358.9 | 12354.3 | 13316 | 12645 | 13137.8 | 12596.87 | 12670.6 | 11604.6 | 13004 | 12322.3 | 12316.5 | 12311.2 | 12299.7 | 10762.6 | 12386.9 | 10784.7 | 12234.1 | 11633.7 | 13271.4 | 12022.4 | 13542.6 | 12579 | 13424.2 | 12444.8 | 12480.7 | 12236.7 | 13284.9 | 13572.2 | 13557.4 | 13473 | 13340.3 | 13363 | 12668.4 | 13501.98 | 13445 | 13388.6 | 13147.1 | 13071.2 | 13403.2 | 11705.1 | 13119 | 12562 | 31.7174 | 32.132 | 32.0146 | 0 | 31.7091 | 32.2364 | 0 | 45.2976 | 0 | 0 | 0 | 0 | 6.191 | 6.2914 | 6.4022 | 0 | 5.997 | 6.1001 | 10.0117 | 9.7467 | 10.215 | 0 | 9.5917 | 9.9067 | 7.1981 | 6.9832 | 7.1897 | 0 | 7.1702 | 6.7257 | 1.4864 | 1.669 | 1.6423 | 0 | 1.5707 | 1.4034 | 7.4563 | 6.9684 | 7.4232 | 0 | 7.4886 | 7.4579 | 1.4053 | 1.6683 | 1.6208 | 0 | 1.5776 | 1.7213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102724 | 186 | 94997 | 180 | 196894 | 554 | 7.1981 | 6.9832 | 7.1897 | 0 | 7.1702 | 6.7257 | 7.4563 | 6.9684 | 7.4232 | 0 | 7.4886 | 7.4579 | 1015000 | 1000 | 1001000 | 1000 | 2008000 | 2000 | 2014000 | 2006000 | 12.7 | 7.0534 | 1.5544 | 7.3589 | 1.5987 | 22.04% | 21.72% | 31.9619 | 45.2976 | 6.1963 | 9.8943 | 2027201.54 | 2008400 | 2464557.0178 | 81.49%
2022-09-04 | 2023 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 334201.075 | 6:38 | 19:01 | 9206.1 | 10180.5 | 10192.2 | 10154 | 9915.2 | 10025.7 | 10177.97 | 10417.8 | 10035.7 | 9863.2 | 9902.5 | 9997 | 9940.8 | 10010.8 | 9732.67 | 10037 | 9970.5 | 10169.8 | 10031.2 | 9977.3 | 10010.7 | 10170.4 | 9998.9 | 10086 | 9777.8 | 8614.5 | 9782.3 | 9860.8 | 9923.3 | 9779.2 | 9715.1 | 10058.9 | 9885.3 | 9932.4 | 9914.6 | 9930.3 | 10042.1 | 10007.8 | 10108 | 10120.4 | 10426 | 9602.2 | 10277.5 | 9489.3 | 10030.6 | 11194 | 9438 | 10457 | 9478.1 | 9209.2 | 10026 | 9561.5 | 10398.7 | 9351.7 | 10430.39 | 9545.5 | 9454 | 10357.9 | 9494.9 | 10517.5 | 10521.7 | 9366.7 | 10760.87 | 9768.5 | 9900.8 | 9209.6 | 9962.74 | 10186.1 | 10590.5 | 9492.9 | 10330 | 9309.6 | 9119.2 | 10519.8 | 9371.1 | 10374.5 | 9279.6 | 10409.7 | 9542.6 | 10219.3 | 9427.3 | 9906.8 | 9226.8 | 10480.5 | 9344.2 | 9982.2 | 8876.5 | 8008.2 | 10229.27 | 9777.2 | 9030.6 | 10424.78 | 10145.5 | 9389.3 | 9264.22 | 10108.7 | 8977.9 | 9533.35 | 10212.7 | 9137.5 | 10099.5 | 9038.2 | 10034.1 | 9428.3 | 7423.9 | 6615.6 | 7714 | 6968.9 | 7745.3 | 7051.3 | 7645.2 | 7225.7 | 9221.6 | 9844.6 | 9299.7 | 9208.2 | 10227.1 | 9891.8 | 10071.7 | 9305.2 | 10296.3 | 9276.5 | 9858.3 | 9433.4 | 9704.9 | 8764 | 10024 | 9304.9 | 9300.2 | 9328.8 | 9214.2 | 8181.8 | 9204.1 | 8157.5 | 9288.2 | 8922 | 10201 | 9140.8 | 10439.9 | 9572.7 | 10487.17 | 9545.3 | 9608.3 | 9415.7 | 10258.7 | 10451.2 | 10380.3 | 10307.9 | 10223.7 | 10274.3 | 9578.5 | 10352 | 10347.86 | 10244.9 | 10073.5 | 10074.5 | 10324.3 | 8922.3 | 10023 | 9567.5 | 28.8591 | 30.014 | 29.659 | 0 | 29.4604 | 30.0608 | 0 | 40.2791 | 0 | 0 | 0 | 0 | 7.4663 | 7.371 | 7.4269 | 0 | 6.994 | 7.2822 | 10.7983 | 10.2517 | 11.7767 | 0 | 10.59 | 10.94 | 5.5301 | 5.581 | 5.5358 | 0 | 5.4664 | 5.197 | 1.0337 | 1.4568 | 1.1588 | 0 | 1.3565 | 1.2517 | 5.5927 | 5.5837 | 5.5427 | 0 | 5.832 | 5.7852 | 0.98004 | 1.4673 | 1.1656 | 0 | 1.3707 | 1.5281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103516 | 187 | 95747 | 182 | 198429 | 558 | 5.5301 | 5.581 | 5.5358 | 0 | 5.4664 | 5.197 | 5.5927 | 5.5837 | 5.5427 | 0 | 5.832 | 5.7852 | 792000 | 1000 | 750000 | 2000 | 1535000 | 4000 | 1539000 | 1531000 | 12.3833 | 5.4621 | 1.2515 | 5.6673 | 1.3023 | 22.91% | 22.98% | 29.6107 | 40.2791 | 7.3081 | 10.8713 | 1548250.39 | 1536467 | 1934375.9456 | 79.43%
2022-09-05 | 2023 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 334195.71 | 6:24 | 19:01 | 10072.4 | 11071.3 | 11041.6 | 11035.8 | 8997.2 | 9356.8 | 11059.6 | 11341.7 | 9105.8 | 8362.7 | 9070.6 | 8612.3 | 9135.6 | 9838 | 10394.7 | 10435.3 | 8981.8 | 11268.1 | 9365.6 | 9363.6 | 8766.6 | 10703.8 | 11076 | 11129.4 | 9136.1 | 7856.2 | 9325.7 | 9491.7 | 10066.1 | 8786.9 | 9124.7 | 9262.8 | 8325.2 | 8056.7 | 8289.5 | 8058.5 | 8142.5 | 8629.4 | 11428.6 | 11385.1 | 8462.2 | 8529.6 | 8258.7 | 8793.1 | 8424.8 | 9333.4 | 8638 | 9392 | 8150.6 | 7824 | 8530.8 | 7868.4 | 9259.9 | 7668.9 | 11401.9 | 10657.7 | 10278.4 | 11198.7 | 10382.9 | 11335.8 | 10554.4 | 8889.8 | 11542.4 | 10649.1 | 8611.7 | 7536.5 | 8208 | 8426 | 10151.3 | 8221.4 | 8397 | 8035 | 7033.6 | 9039.2 | 7170.5 | 8635.5 | 7776.3 | 7968.1 | 8133.3 | 7884.4 | 7226.3 | 7847.2 | 7115.7 | 8985.4 | 7322.8 | 8320 | 6810.5 | 6600.7 | 8052.9 | 7516.2 | 7155.5 | 8417.8 | 8250.4 | 7792 | 8140.1 | 7991.8 | 7225.1 | 8120.4 | 8313.5 | 7441.4 | 8839.7 | 7430.6 | 8495.7 | 8115.1 | 8360.6 | 8021.4 | 8587.7 | 8244.4 | 8986 | 8189 | 8987.1 | 11043.7 | 8507.3 | 9503.7 | 8587.2 | 9565 | 10915.1 | 8842.2 | 9624 | 9301.7 | 11732.8 | 10778 | 9173.7 | 10874.7 | 8796.6 | 9891.5 | 10835.5 | 9901.6 | 10578.9 | 8355.1 | 8891.2 | 8040.9 | 8670.6 | 7934.6 | 8252.2 | 8480.2 | 9083.6 | 7874.2 | 11373.6 | 10316.1 | 11258.9 | 10262.5 | 10326.7 | 10144.2 | 11291.7 | 11321.5 | 11505.4 | 11434.6 | 10520.3 | 10808.7 | 10443.2 | 11410.5 | 11101.8 | 9054.4 | 8689.8 | 10831.2 | 10284 | 8949.1 | 9939.8 | 9997 | 28.5249 | 30.032 | 29.797 | 0 | 29.5743 | 30.429 | 0 | 43.338 | 0 | 0 | 0 | 0 | 5.3188 | 5.4744 | 5.1846 | 0 | 5.1687 | 5.3872 | 8.7033 | 8.53 | 9.035 | 0 | 8.3183 | 8.86 | 6.0836 | 6.2125 | 6.4181 | 0 | 6.2823 | 5.8139 | 1.1999 | 1.5654 | 1.4269 | 0 | 1.4731 | 1.2717 | 6.2423 | 6.2181 | 6.5973 | 0 | 6.6675 | 6.3369 | 1.1468 | 1.5699 | 1.423 | 0 | 1.4927 | 1.5548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104260 | 188 | 96475 | 183 | 199896 | 561 | 6.0836 | 6.2125 | 6.4181 | 0 | 6.2823 | 5.8139 | 6.2423 | 6.2181 | 6.5973 | 0 | 6.6675 | 6.3369 | 744000 | 1000 | 728000 | 1000 | 1467000 | 3000 | 1470000 | 1464000 | 12.6167 | 6.1621 | 1.3874 | 6.4124 | 1.4374 | 22.52% | 22.42% | 29.6715 | 43.338 | 5.3067 | 8.6893 | 1474409.1 | 1467601 | 2173279.576 | 67.53%
2022-09-06 | 2023 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 334195.71 | 6:24 | 19:01 | 10577.9 | 11745 | 11755 | 11654.5 | 8757.9 | 8940.4 | 11752.6 | 12037.5 | 9539.2 | 9163.9 | 10416.4 | 10420.4 | 9534.6 | 9645.8 | 9523 | 9877.2 | 10215.3 | 11740.9 | 9498 | 9541.5 | 10085.4 | 11312.9 | 11530.3 | 11567.1 | 8328.6 | 7371.2 | 9261.1 | 9243 | 10234.7 | 9477.1 | 8910.8 | 9207.6 | 11433.8 | 11620.5 | 11423.9 | 11420 | 11663.5 | 11573.2 | 11682.8 | 11606.5 | 12285.3 | 11339.9 | 12088.9 | 11146 | 11695.1 | 12884.8 | 10725 | 11568 | 11354.2 | 11005.2 | 11985.5 | 11453.4 | 12391.2 | 11317.9 | 12305 | 11209.5 | 11205.4 | 12184 | 11262 | 12428.7 | 12306.3 | 11027.3 | 12475.4 | 11392.9 | 11609.6 | 10859.1 | 11695.3 | 11880.2 | 12382.7 | 11084.1 | 12112.4 | 10801.5 | 10809.8 | 12174.4 | 11114.9 | 12084.6 | 10939.3 | 12283.2 | 11175.9 | 12097 | 11033.2 | 11589.6 | 10994.5 | 12056.3 | 10822.3 | 11452.9 | 10982.1 | 9228.1 | 10662 | 10439.7 | 10450.7 | 11994 | 11693 | 10888.9 | 10709.6 | 11717.4 | 10671.9 | 11055.5 | 11820.3 | 10621.7 | 11756.1 | 10502.1 | 11618.6 | 10810.7 | 11641.1 | 10287.6 | 11697.8 | 10700.7 | 11555.1 | 10647.9 | 11582.4 | 10864 | 10656.9 | 11213.2 | 10682.8 | 10472.3 | 11504.5 | 11266.7 | 11333.2 | 10638.4 | 11589.8 | 10535.6 | 11206.4 | 10717.8 | 11351.7 | 10183.5 | 11519 | 10807.3 | 10529.1 | 10710.6 | 10760.5 | 9346.9 | 10569.8 | 9268.6 | 10510.2 | 10554.3 | 11938.3 | 10579 | 11939 | 10879.6 | 11851 | 10747 | 10817.9 | 10571.1 | 11890.3 | 12103.9 | 12056.1 | 12038 | 12006.6 | 12053.1 | 11103.6 | 11984.6 | 12017.3 | 12058.2 | 11983.7 | 11744.6 | 12111.2 | 10415.4 | 11643.1 | 11114.8 | 30.2653 | 30.6497 | 30.4958 | 0 | 30.3377 | 30.8052 | 0 | 46.2083 | 0 | 0 | 0 | 0 | 3.1652 | 3.2216 | 3.348 | 0 | 3.1027 | 2.9639 | 6.7833 | 6.7983 | 6.9783 | 0 | 6.1567 | 6.3217 | 6.6046 | 6.1669 | 6.4871 | 0 | 6.1588 | 6.0115 | 1.7725 | 1.4778 | 1.4961 | 0 | 1.3365 | 1.2186 | 7.3076 | 6.1641 | 6.7292 | 0 | 6.4159 | 6.7488 | 1.3897 | 1.4746 | 1.4954 | 0 | 1.362 | 1.5134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105139 | 189 | 97361 | 184 | 201653 | 565 | 6.6046 | 6.1669 | 6.4871 | 0 | 6.1588 | 6.0115 | 7.3076 | 6.1641 | 6.7292 | 0 | 6.4159 | 6.7488 | 879000 | 1000 | 886000 | 1000 | 1757000 | 4000 | 1763000 | 1753000 | 12.6167 | 6.2858 | 1.4603 | 6.6731 | 1.447 | 23.23% | 21.68% | 30.5107 | 46.2083 | 3.1603 | 6.6077 | 1771556.2 | 1757667 | 2216646.0507 | 79.29%
2022-09-07 | 2023 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 334195.71 | 6:28 | 19:00 | 10749.6 | 12401.5 | 12591.2 | 12585.4 | 12494.27 | 12643.79 | 12688.7 | 12910.2 | 12224 | 12144 | 11775.6 | 12614.6 | 12170.2 | 12563.49 | 11968.7 | 12548.2 | 12138.7 | 12399.35 | 12367.95 | 12382.61 | 12428.37 | 12419.27 | 12215.93 | 12341.6 | 12177.9 | 8840.2 | 12312.9 | 12298.5 | 12196.6 | 12085.3 | 12116.67 | 12502.55 | 9386.9 | 9322.9 | 9808.91 | 9562.62 | 12278.08 | 12012.8 | 12581.9 | 12581.8 | 12997.82 | 12119.8 | 12805.6 | 11890.6 | 12421.3 | 12530.5 | 10215 | 11132 | 10268.15 | 10317.3 | 12309.7 | 11736.3 | 12754.21 | 10866.4 | 12995 | 11883 | 11764 | 12740.34 | 11819.8 | 12986.3 | 12487.2 | 11485.1 | 13171.9 | 12179.2 | 12323.9 | 11445.6 | 12362.9 | 12525.4 | 13265.17 | 11615.5 | 12818.4 | 11344.92 | 11503.6 | 12937.4 | 11900.34 | 12897.77 | 11558.94 | 12980.8 | 11944.3 | 12818.3 | 11722.17 | 12328.2 | 11770.9 | 12990.7 | 11603.6 | 12378.7 | 11729.53 | 9791 | 12695.12 | 12302.4 | 11232.54 | 12928.34 | 12660.02 | 11786.3 | 11231.4 | 12280.1 | 11323.8 | 11812.01 | 12697.1 | 11365.46 | 12655.8 | 11309.4 | 12480.7 | 11645.27 | 12507.8 | 11002.22 | 12622.9 | 11675 | 12510.9 | 11574.8 | 12591.8 | 11843.7 | 11458.3 | 12352.4 | 11647.9 | 11420 | 12708.7 | 12563.4 | 12657.6 | 11799.81 | 12832.96 | 11556.35 | 12367.9 | 11738 | 12375.98 | 10973.4 | 12661.6 | 11800.6 | 11620.4 | 11840.3 | 11548.37 | 10088.3 | 11583.7 | 9997.2 | 11097.4 | 11024 | 12868 | 11348.6 | 12863.57 | 11648.78 | 12666 | 11300.3 | 11389.2 | 10995.5 | 12532.1 | 12813.95 | 12920.35 | 12829.13 | 12857.84 | 12890.75 | 11762.47 | 12748.56 | 12811.5 | 12802.7 | 12572.7 | 12401.3 | 12802.8 | 10743.4 | 12496.5 | 11791.4 | 31.6062 | 32.5658 | 32.3834 | 0 | 32.512 | 32.7098 | 0 | 49.4793 | 0 | 0 | 0 | 0 | 2.1565 | 1.933 | 2.0004 | 0 | 1.9433 | 1.8762 | 5.3583 | 5.0733 | 4.8517 | 0 | 5.0717 | 4.6333 | 7.0156 | 6.7084 | 6.8217 | 0 | 6.7198 | 6.3421 | 1.5073 | 1.5338 | 1.5754 | 0 | 1.4489 | 1.2585 | 7.2912 | 6.6478 | 7.1732 | 0 | 7.1085 | 7.0391 | 1.5231 | 1.5189 | 1.569 | 0 | 1.4753 | 1.5631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106101 | 191 | 98315 | 185 | 203561 | 569 | 7.0156 | 6.7084 | 6.8217 | 0 | 6.7198 | 6.3421 | 7.2912 | 6.6478 | 7.1732 | 0 | 7.1085 | 7.0391 | 962000 | 2000 | 954000 | 1000 | 1908000 | 4000 | 1913000 | 1904000 | 12.5333 | 6.7215 | 1.4648 | 7.052 | 1.5299 | 21.79% | 21.69% | 32.3554 | 49.4793 | 1.9819 | 4.9977 | 1921575.17 | 1909334 | 2318392.0144 | 82.36%
2022-09-08 | 2023 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 334195.71 | 6:28 | 18:58 | 11069.1 | 12497.9 | 12472.9 | 12480.6 | 12379 | 12538 | 12477.9 | 12711.9 | 12412 | 12278 | 12278 | 12398 | 12552.6 | 12463.7 | 12146 | 12754 | 12397.3 | 12556.1 | 12691.2 | 12656.7 | 12651 | 12655 | 12302 | 12508 | 12087.5 | 10794.9 | 12540.5 | 12521.1 | 12288.7 | 12201.8 | 12124.2 | 12514.6 | 12211 | 12408.4 | 12452.7 | 12365.5 | 12355.5 | 12259.7 | 12303.3 | 12242.6 | 11132.3 | 10116.7 | 11222.6 | 10166.6 | 11718.8 | 12762.8 | 11518 | 12620 | 11530.3 | 11095.7 | 12568.5 | 11904.9 | 13062.5 | 11834.7 | 12856.6 | 11696.2 | 11588 | 12568.9 | 11670.8 | 12837.4 | 12730.3 | 11456.4 | 12954.7 | 11983.5 | 12251.6 | 11381.3 | 12310.4 | 12519 | 13040.6 | 11636 | 12843.1 | 11214.1 | 11262.1 | 12751 | 11698.8 | 12704.9 | 11369.2 | 12950.5 | 11711.3 | 12668.6 | 11564.7 | 12146.6 | 11576.2 | 12797.2 | 11352.8 | 12185.1 | 11510.2 | 9593 | 12536.1 | 12106.9 | 11095.1 | 12734.4 | 12470.6 | 11661.7 | 11439.1 | 12438.8 | 11288.5 | 11796.7 | 12795.2 | 11421.8 | 12740.4 | 11406 | 12663.6 | 11772.2 | 12738.3 | 11144.5 | 12829.4 | 11791.8 | 12626.3 | 11635.2 | 12602.5 | 11888.1 | 11549.3 | 12467.2 | 11776.5 | 11484.1 | 12860.6 | 12637.9 | 12762.2 | 11752.5 | 12932.6 | 11493.8 | 12515.7 | 11787 | 12417.9 | 10827 | 12650.8 | 11620.9 | 11487.9 | 11753.1 | 11491.3 | 10006.9 | 11487.5 | 9984.2 | 11518.6 | 11475.6 | 13158.5 | 11607.5 | 13260 | 12069 | 13158.6 | 11856.8 | 11890.9 | 0 | 12767 | 13130 | 13202.9 | 13147.2 | 12959.2 | 12978.8 | 12157 | 13155.8 | 13127.6 | 13226.3 | 13198.5 | 12947.6 | 13281 | 11110.7 | 12768.5 | 12084.6 | 34.4599 | 34.5879 | 34.3569 | 0 | 34.3244 | 34.4062 | 0 | 48.9951 | 0 | 0 | 0 | 0 | 2.9564 | 2.8281 | 2.8154 | 0 | 2.7828 | 2.7655 | 6.6317 | 6.0617 | 5.4667 | 0 | 5.515 | 5.39 | 6.9214 | 6.9701 | 6.7536 | 0 | 6.7005 | 6.4454 | 1.4719 | 1.4738 | 1.5459 | 0 | 1.4271 | 1.2671 | 7.1832 | 6.8647 | 7.081 | 0 | 7.0766 | 7.1442 | 1.4868 | 1.4723 | 1.538 | 0 | 1.4531 | 1.5798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107070 | 191 | 99267 | 186 | 205475 | 571 | 6.9214 | 6.9701 | 6.7536 | 0 | 6.7005 | 6.4454 | 7.1832 | 6.8647 | 7.081 | 0 | 7.0766 | 7.1442 | 969000 | 0 | 952000 | 1000 | 1914000 | 2000 | 1920000 | 1912000 | 12.5 | 6.7582 | 1.4372 | 7.0699 | 1.506 | 21.27% | 21.3% | 34.4271 | 48.9951 | 2.8297 | 5.813 | 1931242.7 | 1914667 | 2321433.6286 | 82.48%
2022-09-09 | 2023 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 334195.71 | 6:31 | 18:57 | 10397.8 | 11867 | 11824.7 | 11790.5 | 11958.78 | 12089.3 | 11935.1 | 12226.9 | 11858.22 | 11350.5 | 11891.7 | 11958.4 | 12156.8 | 12051.6 | 11573.57 | 12199 | 10192.4 | 12265.4 | 12428.9 | 12315.8 | 12431.4 | 12487.6 | 12113.2 | 12343.4 | 12011.5 | 10645.6 | 12247.9 | 12300.2 | 12019.64 | 11904.9 | 12041.1 | 12383.43 | 12213.8 | 12406.3 | 12307.1 | 12298.62 | 12383.13 | 12310.68 | 12356.1 | 12306.5 | 12882.8 | 11928.7 | 12852.3 | 11731.3 | 12323.9 | 13394.53 | 11535.8 | 12430 | 11348.5 | 10939.1 | 12124.04 | 11547.24 | 12705.5 | 11360.7 | 12739.4 | 11558.09 | 11237.4 | 12275.4 | 10682.2 | 12030.4 | 11836.7 | 10423.8 | 11823.1 | 10714.1 | 11889.1 | 10620.6 | 11862.5 | 12048.8 | 12465.3 | 11192.4 | 12415.09 | 10792.3 | 10831.1 | 12382.23 | 11017.3 | 12034 | 10576.2 | 11783.2 | 11083.8 | 12152.2 | 11216.7 | 11803.4 | 11291.49 | 12477.8 | 11064.2 | 11933.6 | 11111.4 | 9318.4 | 12021.52 | 11480.5 | 10672.4 | 12606 | 12470.3 | 11242.5 | 11300.1 | 12476.2 | 10645.5 | 11299 | 12349.5 | 10818.1 | 12374 | 10843.3 | 12335.1 | 11377.1 | 12446 | 10767.7 | 12526.9 | 11339.3 | 12372 | 11233.3 | 12335.5 | 11367.79 | 11062 | 11949 | 11313.8 | 11035.1 | 12439.5 | 11928.2 | 12342.6 | 11289.6 | 12402.3 | 10996 | 11789.5 | 11208.6 | 11565.1 | 10314.6 | 12141 | 11149.4 | 11131 | 11409.4 | 10853.7 | 9542.5 | 11204.9 | 9740 | 11079.2 | 11035.16 | 12638 | 11100.1 | 12760.4 | 11580.7 | 12693.8 | 11394.3 | 11492.03 | 11061.4 | 12409.3 | 12739.34 | 12764.1 | 12687.31 | 12493.2 | 12533.9 | 11647.2 | 12667.7 | 12520.24 | 12586.97 | 12743.18 | 12444.7 | 12756.8 | 10729.8 | 12227.1 | 11603.3 | 35.9902 | 35.4456 | 35.3097 | 0 | 35.2367 | 35.3772 | 0 | 51.3347 | 0 | 0 | 0 | 0 | 2.2304 | 2.1917 | 2.1374 | 0 | 2.207 | 2.0775 | 5.4467 | 6 | 5.2683 | 0 | 5.6967 | 4.47 | 6.6492 | 6.9973 | 6.6233 | 0 | 6.5074 | 6.2013 | 1.4605 | 1.4793 | 1.5357 | 0 | 1.3813 | 1.2101 | 6.8781 | 6.9099 | 6.9443 | 0 | 6.8458 | 6.8931 | 1.4832 | 1.4751 | 1.5326 | 0 | 1.4067 | 1.5083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108016 | 193 | 100196 | 187 | 207341 | 575 | 6.6492 | 6.9973 | 6.6233 | 0 | 6.5074 | 6.2013 | 6.8781 | 6.9099 | 6.9443 | 0 | 6.8458 | 6.8931 | 946000 | 2000 | 929000 | 1000 | 1866000 | 4000 | 1872000 | 1862000 | 12.4333 | 6.5957 | 1.4134 | 6.8942 | 1.4812 | 21.43% | 21.48% | 35.4719 | 51.3347 | 2.1688 | 5.3763 | 1883529.22 | 1867733 | 2304030.8446 | 81.06%
2022-09-10 | 2023 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 334195.71 | 6:26 | 18:57 | 9761.6 | 11020.8 | 10785.7 | 10830.9 | 10762 | 10902.7 | 10902.9 | 11098.9 | 11079.3 | 10616.6 | 10657.9 | 11033.1 | 10748.6 | 10911.5 | 10355.5 | 10945.1 | 10349 | 11050.5 | 10854.3 | 11078.2 | 10841.6 | 11112.67 | 10742.5 | 10670.14 | 10826.3 | 9583.8 | 11069.8 | 11042.7 | 10749.3 | 10666.3 | 10693 | 11076.4 | 10853 | 10661.5 | 11054.2 | 11016.46 | 10761.2 | 10908.9 | 10948.4 | 10907.4 | 11368.2 | 10345 | 11141.1 | 10069.3 | 10589.4 | 11763.87 | 10073 | 11131 | 10275.3 | 9921.1 | 10980 | 10475.6 | 11494.9 | 9927.1 | 11442.2 | 10375.4 | 10212.8 | 11209.1 | 10241.4 | 11450 | 11444.8 | 10060.1 | 11641.1 | 10509.7 | 10665.1 | 9696.6 | 10698.7 | 10957.2 | 11449.6 | 10152.3 | 11327.4 | 9850.5 | 9604.8 | 11492.6 | 9864 | 11436.1 | 9856.4 | 11510.6 | 10241.4 | 11106.7 | 10250.2 | 10852.7 | 10212.7 | 11455.2 | 10020.53 | 10756.29 | 10078.1 | 8385 | 10974.1 | 10563.7 | 9187.5 | 11159.2 | 10919.5 | 10056.5 | 9849.5 | 10580.23 | 9202.8 | 9856 | 10561 | 8929.1 | 10743.1 | 9219.8 | 10570.57 | 9732 | 10602.3 | 9185.3 | 10659.2 | 9624 | 10502.2 | 9527 | 10423.1 | 9617.8 | 9556.4 | 10276 | 9030.5 | 9378.9 | 10383.5 | 9900.9 | 9444.5 | 9534.7 | 10552.7 | 9298.5 | 9948.8 | 9450.8 | 9333.3 | 8578.77 | 9285 | 9127 | 9495.7 | 9753.3 | 9209.4 | 8167.1 | 9549.2 | 8321.6 | 9610 | 9559.4 | 11493.76 | 9866.9 | 11594.5 | 10299.06 | 11312.7 | 9958.3 | 9985.2 | 9576.8 | 11543.6 | 11866.2 | 11851.3 | 11749.7 | 11662 | 11670.3 | 10551.9 | 11677 | 11788.58 | 11824.7 | 11666.6 | 11547.2 | 11931.5 | 9847 | 11456.7 | 10751.7 | 35.7061 | 35.4448 | 35.2692 | 0 | 35.2345 | 35.4138 | 0 | 49.8033 | 0 | 0 | 0 | 0 | 1.8901 | 1.8491 | 1.7292 | 0 | 1.8426 | 1.887 | 6.6133 | 6.8233 | 5.855 | 0 | 6.425 | 7.6467 | 6.0474 | 6.1587 | 5.7187 | 0 | 5.6222 | 5.6306 | 1.3757 | 1.2881 | 1.3707 | 0 | 1.1401 | 1.101 | 6.2114 | 6.1253 | 5.9902 | 0 | 5.7713 | 6.3232 | 1.397 | 1.2821 | 1.3731 | 0 | 1.1601 | 1.3747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108872 | 194 | 101011 | 189 | 209005 | 579 | 6.0474 | 6.1587 | 5.7187 | 0 | 5.6222 | 5.6306 | 6.2114 | 6.1253 | 5.9902 | 0 | 5.7713 | 6.3232 | 856000 | 1000 | 815000 | 2000 | 1664000 | 4000 | 1668000 | 1660000 | 12.5167 | 5.8355 | 1.2551 | 6.0843 | 1.3174 | 21.51% | 21.65% | 35.4137 | 49.8033 | 1.8396 | 6.6727 | 1678457.53 | 1665267 | 1995965.2542 | 83.43%
2022-09-11 | 2023 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 334195.71 | 6:20 | 18:58 | 8928.2 | 10171.9 | 10159.8 | 10168.5 | 9686 | 9375 | 10218.1 | 10494.8 | 10191 | 9720.3 | 9993.1 | 9885.7 | 10022.2 | 10240.8 | 9767.8 | 10318.7 | 9814.2 | 10295.8 | 10273.9 | 10385.1 | 10043.3 | 10337.9 | 10032.9 | 9721.6 | 9922.4 | 8683.9 | 10274.4 | 10309.1 | 10127.2 | 9939 | 9788.3 | 10167.3 | 10164.2 | 10149.4 | 10239.9 | 10096.8 | 10172 | 10238.3 | 10340.3 | 10311.9 | 10456.3 | 9696.5 | 10160.3 | 9453.5 | 9871.5 | 10959.8 | 9333.1 | 10651.5 | 9625.7 | 9305.9 | 10289.8 | 9744 | 10802.2 | 9423.2 | 10783.7 | 9700.4 | 9610.8 | 10646.4 | 9610.3 | 10879.9 | 10799.3 | 9400.7 | 10994.6 | 9857 | 10301 | 9587.4 | 10322 | 10593.8 | 10789 | 9591 | 10837.1 | 9425.4 | 9077.8 | 10832 | 8964.2 | 10789.4 | 9425 | 10587.2 | 9628.2 | 10383.1 | 9390.3 | 9952 | 9651.6 | 10823.9 | 9489.3 | 10236.4 | 9605.7 | 8031.7 | 10660.3 | 10191.3 | 9289.1 | 10913 | 10585 | 9693.3 | 9469.7 | 10588 | 9383.7 | 9827.7 | 10728.2 | 9464.9 | 10593.4 | 9425.6 | 10502.4 | 9732.6 | 10561.8 | 9194.2 | 10683.3 | 9716.7 | 10490.6 | 9571.3 | 10443 | 9772.2 | 9578.9 | 10374.4 | 9734.7 | 9501.9 | 10724 | 10526.8 | 10613.8 | 9769.6 | 10770.9 | 9517.4 | 10329.2 | 9674.3 | 10225.7 | 8943.3 | 10314.2 | 9628.4 | 9655.5 | 9897.4 | 9515.8 | 8351.8 | 9694.4 | 8390.2 | 9535.5 | 9473 | 11007.1 | 9566.7 | 11056.6 | 9945.8 | 11006.5 | 9786.5 | 9865.6 | 9489.2 | 10643.5 | 11032 | 10955.2 | 10918.6 | 10856.3 | 10951.7 | 9970 | 10925.5 | 10712.8 | 10833.5 | 10679.4 | 10479.6 | 10903.3 | 8981.7 | 10551 | 9796.3 | 32.9087 | 33.1011 | 32.6289 | 0 | 33.2867 | 33.1639 | 0 | 46.2523 | 0 | 0 | 0 | 0 | 2.9866 | 2.9592 | 2.9867 | 0 | 3.0413 | 2.7925 | 9.7883 | 11.8883 | 11.15 | 0 | 10.52 | 10.3133 | 5.5431 | 5.7169 | 5.2543 | 0 | 5.5981 | 5.2158 | 1.1918 | 1.2364 | 1.2219 | 0 | 1.2195 | 1.0522 | 5.7548 | 5.6508 | 5.5158 | 0 | 5.8738 | 5.8203 | 1.2172 | 1.2271 | 1.2273 | 0 | 1.2445 | 1.306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109675 | 195 | 101811 | 191 | 210602 | 584 | 5.5431 | 5.7169 | 5.2543 | 0 | 5.5981 | 5.2158 | 5.7548 | 5.6508 | 5.5158 | 0 | 5.8738 | 5.8203 | 803000 | 1000 | 800000 | 2000 | 1597000 | 5000 | 1600000 | 1592000 | 12.6333 | 5.4656 | 1.1844 | 5.7231 | 1.2444 | 21.67% | 21.74% | 33.0179 | 46.2523 | 2.9533 | 10.732 | 1608678.7 | 1597667 | 1886882.4556 | 84.67%
2022-09-12 | 2023 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 334195.71 | 6:31 | 19:00 | 10042.3 | 11289 | 11439.5 | 11423.5 | 11222.8 | 11475.2 | 11392.3 | 11681.5 | 11299.8 | 10709 | 11184.8 | 11316.6 | 11321.1 | 11300.1 | 10800.3 | 11412.7 | 10243 | 10511 | 11301 | 11275.5 | 10115.3 | 11406.6 | 10996.3 | 10859.3 | 10948.8 | 9696.7 | 11194.5 | 11194.8 | 11139.1 | 11066.2 | 10951.7 | 11285.9 | 10995.1 | 11170.4 | 11173.1 | 11171.8 | 11208.7 | 11238.5 | 11330.5 | 11257.9 | 12052.2 | 11228.9 | 11989.4 | 10989 | 11377.3 | 12576.4 | 10940.6 | 11848.4 | 10653.6 | 10281.7 | 11329.5 | 10730.5 | 11753.5 | 10222.8 | 11764 | 10598.3 | 10245.9 | 11318.7 | 10267.1 | 11570.1 | 11488.8 | 10101.9 | 12134.9 | 10898.7 | 11108.1 | 10393 | 11290.6 | 11571.5 | 12048 | 10734 | 11811.7 | 10357.7 | 9862.8 | 11955.2 | 10402.1 | 11905.5 | 10410.8 | 11838.5 | 10656.4 | 11659.9 | 10570.2 | 11191.1 | 10535.5 | 11817 | 10338.4 | 11122.7 | 10436.7 | 8729.4 | 11504.9 | 11044.9 | 9831.7 | 11664.5 | 11238.9 | 10384.3 | 10149 | 11042.3 | 9973.1 | 10609.6 | 11491.6 | 10155.9 | 11426.2 | 9794.1 | 11280 | 10487.3 | 11003.7 | 9745.8 | 11180.8 | 10305.6 | 11172 | 10180.7 | 10897 | 10379.8 | 10011.9 | 10805 | 10031.8 | 9955.8 | 11213.4 | 10794.7 | 11118 | 10180.2 | 11532.7 | 10202.5 | 10059.6 | 10388.5 | 10708.3 | 9605.4 | 11221.2 | 10329 | 10305 | 10310.9 | 10101.5 | 8954.8 | 10163.9 | 8981.2 | 10092.9 | 10362.1 | 11944.8 | 10374.4 | 12048.8 | 10821.2 | 11964.7 | 10611.9 | 10687.7 | 10297.2 | 11633.3 | 11802.4 | 11989.3 | 11932.6 | 11853 | 11943.5 | 10861.3 | 11903.2 | 11905.2 | 11801.7 | 11589.3 | 11525.1 | 11931.2 | 9862.2 | 11619.9 | 10785.1 | 33.1664 | 32.8316 | 32.6456 | 0 | 32.5122 | 32.6045 | 0 | 47.3763 | 0 | 0 | 0 | 0 | 3.448 | 3.5168 | 3.3479 | 0 | 3.5779 | 3.2949 | 13.4583 | 13.2467 | 13.2233 | 0 | 12.4267 | 10.5517 | 6.1575 | 6.3382 | 6.0868 | 0 | 6.0106 | 5.7692 | 1.3072 | 1.3306 | 1.3595 | 0 | 1.2954 | 1.1322 | 6.4944 | 6.2105 | 6.4473 | 0 | 6.4072 | 6.3199 | 1.329 | 1.3282 | 1.349 | 0 | 1.3133 | 1.4168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110563 | 197 | 102671 | 192 | 212342 | 588 | 6.1575 | 6.3382 | 6.0868 | 0 | 6.0106 | 5.7692 | 6.4944 | 6.2105 | 6.4473 | 0 | 6.4072 | 6.3199 | 888000 | 2000 | 860000 | 1000 | 1740000 | 4000 | 1745000 | 1736000 | 12.4833 | 6.0725 | 1.285 | 6.3759 | 1.3472 | 21.16% | 21.13% | 32.7521 | 47.3763 | 3.4371 | 12.5813 | 1752214.2 | 1741000 | 2114832.2648 | 82.32%
2022-09-13 | 2023 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 334195.71 | 6:27 | 18:47 | 9865.8 | 11098.8 | 11131.1 | 11120.3 | 10915 | 11034 | 11142.1 | 11444.8 | 10949 | 10729 | 10843 | 10948 | 10701 | 10725 | 10643 | 11090.8 | 10878 | 10943 | 11129.4 | 11161 | 11012 | 11056 | 10680 | 10763 | 10547 | 9318 | 10765 | 10607 | 10414 | 10554 | 10724 | 10803 | 10787 | 10877 | 10805.4 | 10826.1 | 11069.9 | 10966.5 | 11016.1 | 10979.9 | 11420 | 10594 | 11470 | 10449 | 11029 | 11908 | 10528 | 11444 | 10431 | 10050 | 11401 | 10456 | 10325 | 9262 | 11369.7 | 10402.6 | 10305.2 | 11221.9 | 10441.5 | 11445 | 11474 | 10250.8 | 11685.9 | 10716.6 | 10819 | 10178 | 10825 | 11004 | 11541 | 10380 | 10809.9 | 9534.3 | 9710 | 11137 | 10109 | 11073 | 9819 | 11089 | 10148 | 10575 | 10133.5 | 10479.7 | 10126.5 | 11264.9 | 10021.1 | 10707.9 | 10180 | 8296.5 | 11022.1 | 10667.5 | 9530.2 | 10876.2 | 10958.1 | 10204.7 | 10051.3 | 10906.6 | 8741 | 9318 | 10092 | 8926 | 10052 | 8825 | 9934 | 9262 | 11001 | 9628.6 | 11141.4 | 10255.5 | 11099.1 | 10231.9 | 11123.32 | 10459.1 | 9870.4 | 10644.7 | 10098.1 | 9848.1 | 11043.3 | 10664.1 | 11014.3 | 10167.7 | 11169.2 | 10005.2 | 10851.9 | 10324.1 | 10852.1 | 9354.5 | 10998.9 | 10179.4 | 9883 | 9939 | 10101 | 8701 | 9727 | 8521 | 9630.1 | 9724.9 | 11196.2 | 9853.2 | 11216.8 | 10161.1 | 11145.7 | 10013.9 | 10071.2 | 9704.8 | 10843.5 | 11127 | 11239 | 11206.1 | 10819.4 | 10884.3 | 10252.7 | 11162.3 | 10905 | 10978 | 10949 | 10717 | 11105 | 9311 | 10912 | 10179 | 33.8336 | 33.4872 | 33.4064 | 0 | 33.3407 | 33.35 | 0 | 45.8394 | 0 | 0 | 0 | 0 | 3.868 | 3.9316 | 3.7212 | 0 | 3.9209 | 3.8067 | 7.755 | 8.2 | 7.3883 | 0 | 8.2067 | 8.2667 | 5.9631 | 6.132 | 5.9388 | 0 | 5.769 | 5.4234 | 1.2755 | 1.1974 | 1.2885 | 0 | 1.1902 | 1.0289 | 6.1481 | 6.0494 | 6.2946 | 0 | 6.0273 | 6.0726 | 1.295 | 1.1941 | 1.2799 | 0 | 1.203 | 1.2974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111420 | 198 | 103491 | 193 | 214012 | 591 | 5.9631 | 6.132 | 5.9388 | 0 | 5.769 | 5.4234 | 6.1481 | 6.0494 | 6.2946 | 0 | 6.0273 | 6.0726 | 857000 | 1000 | 820000 | 1000 | 1670000 | 3000 | 1675000 | 1667000 | 12.3333 | 5.8453 | 1.1961 | 6.1184 | 1.2539 | 20.46% | 20.49% | 33.4836 | 45.8394 | 3.8497 | 7.9633 | 1686677.32 | 1671400 | 2032223.6791 | 82.24%
2022-09-14 | 2023 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 334195.71 | 6:34 | 18:47 | 10430.5 | 11446.97 | 11315.7 | 11325.62 | 11179.23 | 11291.33 | 11376.88 | 11717.3 | 11581.72 | 11429.4 | 11408 | 11582.95 | 11220.33 | 11441.5 | 10783.9 | 11199.5 | 11177.5 | 11281.49 | 11150.4 | 11241.82 | 11352.66 | 11323.5 | 11186.3 | 11323.36 | 11225.86 | 10042.57 | 11387.8 | 11375.77 | 11071 | 11218.68 | 11132.1 | 11447.77 | 11466 | 11545.2 | 11480.5 | 11509.3 | 11163.87 | 11051.59 | 11432.57 | 11471.9 | 11890.05 | 10859.1 | 11725.7 | 10664.4 | 11265.4 | 12502.71 | 10668.89 | 11902.3 | 10931.3 | 10651.5 | 11433.95 | 11168.5 | 11778.34 | 10708 | 11998.82 | 10937.3 | 10961.14 | 11917.6 | 10967.64 | 12096.08 | 11901.4 | 10722.37 | 12354.35 | 11308.2 | 11578.56 | 10958 | 11607.26 | 11801.4 | 12371.2 | 11139.04 | 10835 | 9746.5 | 10795.5 | 12052.3 | 11024.69 | 11951.34 | 10783.01 | 12098.53 | 11052.12 | 11913.8 | 10456.6 | 10912.4 | 10286.3 | 11226.05 | 10048.5 | 10603.18 | 9911 | 8180.1 | 10347.1 | 10151.7 | 10106 | 11476.7 | 10698.66 | 10017 | 10380.3 | 11173.2 | 10064.3 | 10463.9 | 11569.82 | 10415.7 | 11470.4 | 10407.5 | 11422.5 | 10642.17 | 11617.29 | 10218.47 | 11785.62 | 10801.3 | 11637 | 10813.32 | 11484.99 | 10808.3 | 10525.6 | 11197.48 | 10670.5 | 10461.3 | 11537.9 | 11252.24 | 10421.2 | 9646.9 | 11537.7 | 10427.2 | 11330.86 | 10820.93 | 11337.5 | 9834.9 | 10764.52 | 10525.3 | 10525.2 | 10621.1 | 10521 | 9231.95 | 10418.78 | 9319.9 | 10629.75 | 10714.24 | 12123.36 | 10856.36 | 12157.1 | 11117.2 | 12037.91 | 10913.89 | 10952.8 | 10639.6 | 11814.8 | 12094.8 | 12065.99 | 12057.52 | 12065.88 | 12133.3 | 11224.01 | 12030.19 | 11929.88 | 12012.4 | 12004.52 | 11755.6 | 12075 | 10335.3 | 11702.34 | 11084 | 33.6183 | 33.6919 | 33.3448 | 0 | 33.5523 | 33.6767 | 0 | 46.8522 | 0 | 0 | 0 | 0 | 3.7131 | 3.6879 | 3.5503 | 0 | 3.6495 | 3.6698 | 8.585 | 7.944 | 6.087 | 0 | 7.007 | 6.953 | 6.2461 | 6.4186 | 5.9373 | 0 | 6.2116 | 6.0147 | 1.3251 | 1.2572 | 1.2797 | 0 | 1.2917 | 1.1248 | 6.4487 | 6.3273 | 6.2637 | 0 | 6.5254 | 6.7046 | 1.3361 | 1.2531 | 1.2755 | 0 | 1.2977 | 1.4174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112322 | 199 | 104366 | 195 | 215781 | 596 | 6.2461 | 6.4186 | 5.9373 | 0 | 6.2116 | 6.0147 | 6.4487 | 6.3273 | 6.2637 | 0 | 6.5254 | 6.7046 | 902000 | 1000 | 875000 | 2000 | 1769000 | 5000 | 1774000 | 1764000 | 12.2167 | 6.1657 | 1.2557 | 6.454 | 1.316 | 20.37% | 20.39% | 33.5768 | 46.8522 | 3.6541 | 7.3152 | 1780868.7 | 1770134 | 2146098.1649 | 82.48%
2022-09-15 | 2023 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 334195.71 | 6:26 | 18:48 | 10383.6 | 11671.6 | 11699.2 | 11691.1 | 11634.1 | 11783.8 | 11581 | 11972.9 | 11704.1 | 11436.3 | 11608.6 | 11721.6 | 11629.6 | 11663.6 | 11132.3 | 11634.4 | 11563.5 | 11610.2 | 11433.2 | 11422.9 | 11711.2 | 11705.9 | 11403.8 | 11551.7 | 11469.6 | 10101.3 | 11690.8 | 11679 | 11251.4 | 11466.4 | 11399.7 | 11676 | 11711.1 | 11847.2 | 11748.1 | 11780.4 | 11803.6 | 11679.4 | 11756.1 | 11725.4 | 12494.7 | 11506.8 | 12399.5 | 11331 | 11947.9 | 13016.2 | 11186.6 | 12478 | 10886.3 | 10524.6 | 11587.5 | 11149.2 | 12096.4 | 10919.5 | 12085.2 | 10997.1 | 10862.3 | 11932.9 | 10918.4 | 12136.8 | 12035.3 | 10703 | 12376.8 | 11190.9 | 11538.9 | 10811 | 11556.5 | 11819.2 | 12283.2 | 11041.3 | 12068.1 | 10631.6 | 10565.6 | 12131 | 10942.5 | 12068.2 | 10615.3 | 12203.1 | 10866.4 | 11924.1 | 9667.6 | 10256.7 | 9574.7 | 10757.1 | 9422.9 | 10156.6 | 9679.5 | 7881.6 | 11311.5 | 10910.9 | 9941.4 | 11623.8 | 11301.3 | 10421 | 10223 | 11232.6 | 10367.8 | 10809.7 | 11819.6 | 10408.2 | 11711.6 | 10393.4 | 11660.7 | 10720.5 | 11912.3 | 10222.6 | 12078.1 | 10902.4 | 12046.4 | 11054.6 | 12187.9 | 11252.3 | 10506.8 | 11318.2 | 10479 | 10216.6 | 11583.2 | 11221.2 | 11714.5 | 10683 | 11618.4 | 10347.6 | 11545.5 | 10994 | 11639.2 | 9905.5 | 11724.7 | 10727.1 | 10495.5 | 10539.1 | 10682.6 | 9222.8 | 10484.3 | 9031.2 | 10317.9 | 10390.4 | 11925.9 | 10321 | 12078.4 | 10915.2 | 11973.7 | 10611.3 | 10659.1 | 10241.4 | 11561.3 | 11820.3 | 11928.7 | 11855.9 | 11772.5 | 11952.1 | 10882.4 | 11857 | 11638.4 | 11749.1 | 11589.2 | 11428.3 | 11917.8 | 9842.9 | 11475.3 | 10758.8 | 33.5477 | 33.7447 | 33.561 | 0 | 33.9644 | 33.8552 | 0 | 49.1497 | 0 | 0 | 0 | 0 | 2.3993 | 2.1648 | 2.2298 | 0 | 2.3775 | 2.1732 | 5.394 | 5.816 | 5.344 | 0 | 5.463 | 5.557 | 6.2048 | 6.5615 | 6.1555 | 0 | 6.0907 | 5.7656 | 1.2592 | 1.3321 | 1.2974 | 0 | 1.3287 | 1.1624 | 6.4903 | 6.402 | 6.5507 | 0 | 6.5269 | 6.358 | 1.2777 | 1.3205 | 1.2955 | 0 | 1.3382 | 1.4612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113242 | 200 | 105235 | 197 | 217562 | 600 | 6.2048 | 6.5615 | 6.1555 | 0 | 6.0907 | 5.7656 | 6.4903 | 6.402 | 6.5507 | 0 | 6.5269 | 6.358 | 920000 | 1000 | 869000 | 2000 | 1781000 | 4000 | 1786000 | 1777000 | 12.3667 | 6.1556 | 1.2759 | 6.4656 | 1.3386 | 20.73% | 20.7% | 33.7346 | 49.1497 | 2.2689 | 5.5148 | 1798019.2 | 1782533 | 2132897.1919 | 83.57%
2022-09-16 | 2023 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 334195.71 | 6:29 | 18:50 | 8835.1 | 11907.6 | 12524 | 12487.9 | 12569.6 | 12721.5 | 12586.2 | 12920 | 12658.1 | 12377.9 | 12542.5 | 12689.7 | 12633.9 | 12595.5 | 12000.5 | 12570.5 | 12544.4 | 12622 | 12555.8 | 12528.6 | 12694.5 | 12658.9 | 12442.3 | 12589 | 12374.7 | 10850.7 | 12591 | 12587 | 12205.2 | 12449.2 | 12321.9 | 12609.9 | 12519.5 | 12630.3 | 12508.86 | 12515.31 | 12673 | 12545.2 | 12527.4 | 12493.6 | 13345.4 | 12328.5 | 13189.4 | 12064.8 | 12774.3 | 13738.7 | 12007.1 | 13325.5 | 11796 | 11380.4 | 12597.7 | 12047.7 | 13039.4 | 11802.4 | 12919.7 | 11761.6 | 11682.9 | 12778.5 | 11750.7 | 12970.9 | 12839.07 | 11531.47 | 13198.7 | 12111.3 | 10891.4 | 10168.4 | 10917 | 11195.9 | 11618.6 | 10369.5 | 11456.5 | 10016.8 | 11352.9 | 13079.9 | 11771.2 | 13026.1 | 11458.7 | 13120.6 | 11748.8 | 12893.7 | 11733.9 | 12424.4 | 11651.8 | 12969.9 | 11445.5 | 12325.5 | 11593.5 | 9463.6 | 12579 | 12183 | 11056.6 | 12859.9 | 12560.9 | 11622.6 | 11435.2 | 12529.6 | 11096.7 | 11578.1 | 12662.8 | 11162.7 | 12664.8 | 11179 | 12599.8 | 11543.8 | 12767.1 | 10996.4 | 12865.5 | 11648.2 | 12808 | 11709 | 12865.5 | 11879.5 | 11266.7 | 12224 | 11477.9 | 11209.8 | 12591.4 | 12305.7 | 12535.2 | 11489.2 | 12574.5 | 11195 | 11927.6 | 11246.2 | 11899.2 | 10174.4 | 12309.8 | 11272.4 | 11319.6 | 11351.9 | 11283.8 | 9828.9 | 11112.1 | 9552.3 | 10800.9 | 10881.2 | 12494.3 | 11309.9 | 12919 | 11705 | 12504.7 | 11139.8 | 10941.3 | 10483.9 | 12103.9 | 12329.8 | 13093.6 | 13051.8 | 12234.3 | 12287.4 | 12033 | 13071.9 | 12976.9 | 13082.3 | 12998.8 | 12779.7 | 13160.6 | 10986.3 | 12766 | 12018.5 | 30.1552 | 31.8663 | 30.9865 | 0 | 31.4191 | 32.0694 | 0 | 45.9141 | 0 | 0 | 0 | 0 | 5.0382 | 5.1786 | 4.8013 | 0 | 4.9655 | 4.9647 | 8.407 | 7.714 | 8.699 | 0 | 7.877 | 8.349 | 6.6112 | 7.0613 | 6.5216 | 0 | 6.5136 | 6.4238 | 1.3641 | 1.4568 | 1.4079 | 0 | 1.4789 | 1.2928 | 6.9433 | 6.8678 | 6.9821 | 0 | 7.0507 | 7.012 | 1.3823 | 1.4433 | 1.3988 | 0 | 1.4775 | 1.6288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114218 | 202 | 106180 | 198 | 219474 | 604 | 6.6112 | 7.0613 | 6.5216 | 0 | 6.5136 | 6.4238 | 6.9433 | 6.8678 | 6.9821 | 0 | 7.0507 | 7.012 | 976000 | 2000 | 945000 | 1000 | 1912000 | 4000 | 1918000 | 1908000 | 12.35 | 6.6263 | 1.4001 | 6.9712 | 1.4661 | 21.13% | 21.03% | 31.2993 | 45.9141 | 4.9897 | 8.2092 | 1930491.11 | 1913600 | 2328438.5446 | 82.18%
2022-09-17 | 2023 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 334195.71 | 6:30 | 18:49 | 10795.07 | 11667.5 | 12610.6 | 12559.4 | 12624.5 | 12803.1 | 12726.4 | 13093 | 11641.8 | 11374.1 | 11410.5 | 11565.4 | 11617.9 | 11580.1 | 10908.7 | 11456.6 | 11532.4 | 11620.5 | 11516.7 | 11484.6 | 11680.7 | 11646.1 | 11620 | 11766.3 | 12079.7 | 10563.7 | 12671.3 | 12691 | 12357.9 | 12492.6 | 12361.2 | 12787 | 12606.5 | 12738 | 12722.4 | 12735.1 | 12777.5 | 12632.6 | 12698 | 12678.3 | 13479.9 | 12354 | 13342 | 12101.2 | 12847.4 | 13902.8 | 12017.4 | 13452.6 | 11836.8 | 11413.2 | 12661.4 | 12079.6 | 13157.6 | 11844.2 | 13122 | 11884.3 | 11748.1 | 12877.6 | 11815 | 13092 | 13029.1 | 11586 | 13214.1 | 12164.7 | 12448.2 | 11662 | 12492.2 | 12656.8 | 13088.9 | 11891.4 | 12941 | 11424.4 | 11388.9 | 12935.8 | 11805.6 | 12859.9 | 11419.6 | 13038.2 | 11723.6 | 12740.8 | 11642.9 | 12249.5 | 11528.7 | 12773 | 11372.7 | 12184.4 | 11570.5 | 9427.5 | 12464.4 | 12100.2 | 11044.5 | 12759.4 | 12541.2 | 11645.1 | 11464.5 | 12508.8 | 11170.2 | 11781.9 | 12770.6 | 11283.1 | 12691.7 | 11370.4 | 12704.8 | 11728.1 | 12843.3 | 11191.3 | 12970.6 | 11865.6 | 12901.4 | 11870.7 | 12984.3 | 12086.7 | 11313.4 | 12268 | 11547.7 | 11273 | 12643.8 | 12208.8 | 12608.4 | 11560.1 | 12680.4 | 11335.9 | 12431.2 | 11759 | 12473.4 | 10615.3 | 12550 | 11506.1 | 11535.5 | 11532 | 11467.3 | 9979.7 | 11654.4 | 9987.3 | 11244 | 11207.7 | 12917.7 | 11424.8 | 12969.1 | 11826.7 | 12863.1 | 11527.6 | 11636.3 | 11165.5 | 11877.6 | 12141.6 | 12215 | 12161.7 | 12306.3 | 12366.2 | 11351.5 | 12290.7 | 11871.7 | 11967 | 11736.5 | 11514 | 11764.9 | 9772.1 | 11641.2 | 10891.2 | 29.3937 | 30.8855 | 30.7728 | 0 | 30.488 | 31.0705 | 0 | 44.1932 | 0 | 0 | 0 | 0 | 6.1963 | 6.5218 | 6.1462 | 0 | 6.1602 | 6.2601 | 10.929 | 10.456 | 10.534 | 0 | 10.385 | 9.844 | 6.5754 | 7.0751 | 6.5008 | 0 | 6.5051 | 6.3554 | 1.3475 | 1.4879 | 1.4057 | 0 | 1.5049 | 1.2796 | 6.9337 | 6.8651 | 6.9451 | 0 | 7.0784 | 6.8903 | 1.3667 | 1.474 | 1.3989 | 0 | 1.5016 | 1.6036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115193 | 203 | 107122 | 200 | 221382 | 608 | 6.5754 | 7.0751 | 6.5008 | 0 | 6.5051 | 6.3554 | 6.9337 | 6.8651 | 6.9451 | 0 | 7.0784 | 6.8903 | 975000 | 1000 | 942000 | 2000 | 1908000 | 4000 | 1914000 | 1904000 | 12.3167 | 6.6024 | 1.4051 | 6.9425 | 1.4689 | 21.28% | 21.16% | 30.5221 | 44.1932 | 6.2569 | 10.4296 | 1927509.47 | 1909533 | 2334270.1651 | 81.8%
2022-09-18 | 2023 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 334195.71 | 6:28 | 18:44 | 11237.5 | 12655.1 | 12698.4 | 12668.9 | 12602.5 | 12827.1 | 12714.5 | 13100.8 | 12756.2 | 12374.1 | 12589.5 | 12774.1 | 12664.9 | 12671.1 | 11989.1 | 12597.7 | 12552 | 12682.1 | 12717.4 | 12684.5 | 12734.3 | 12697.1 | 12461.6 | 12605.8 | 12303.6 | 10740.9 | 12559.3 | 12567 | 12169.3 | 12261.9 | 12225.4 | 12639.5 | 12127 | 12219.1 | 12517 | 12503.9 | 11579.1 | 11489.5 | 11603.4 | 11533.3 | 12828.7 | 11860.3 | 12420 | 11339 | 12166 | 13173.8 | 11778.9 | 13064.9 | 10732.5 | 10374.2 | 11530.6 | 10977.2 | 12086.5 | 10808.6 | 11970.7 | 10839.7 | 11609.4 | 12795.4 | 11672.7 | 13058.3 | 13022.6 | 11464.2 | 13060.4 | 11776 | 12397.4 | 11674 | 12302.9 | 12593.6 | 13156.7 | 11738.8 | 13284.4 | 11524.9 | 11423 | 13328.9 | 11817.3 | 13057.8 | 11532.1 | 13328.4 | 11752 | 12873.1 | 11738 | 12422.3 | 11608 | 12937.5 | 11408.1 | 12269.6 | 11593.1 | 9415.9 | 12537.5 | 12152.1 | 11060.6 | 12776.7 | 12474.5 | 11562.4 | 11387.5 | 12447.1 | 11175.6 | 11790.3 | 12940.8 | 11351.2 | 12666.4 | 11258.2 | 12716.6 | 11702.3 | 12932.3 | 11150.5 | 13072.6 | 11833.1 | 12942.7 | 11806.8 | 13025 | 12038.8 | 11452.8 | 12462.3 | 11486.9 | 11357.1 | 12841.6 | 12262 | 12788.1 | 11577 | 12879 | 11300.3 | 12537.6 | 11812.7 | 12543.2 | 10616.2 | 12368 | 11044.7 | 11514.4 | 11527.1 | 11475.9 | 9954.1 | 11624.8 | 9950.2 | 11128.1 | 11223.9 | 13329.1 | 11538.5 | 13373.1 | 11972 | 13169.1 | 11659 | 11749.2 | 11278.7 | 13055 | 13394.6 | 13388.4 | 13318.3 | 13235.7 | 13315.5 | 12142.7 | 13317.1 | 13203.5 | 13280.2 | 13148.9 | 12886.3 | 13365.2 | 11043 | 13051.3 | 12114.4 | 30.2175 | 30.9095 | 31.0384 | 0 | 31.1353 | 31.2031 | 0 | 47.1561 | 0 | 0 | 0 | 0 | 2.7723 | 2.7666 | 2.7527 | 0 | 2.6656 | 2.5107 | 6.078 | 5.923 | 6.201 | 0 | 5.296 | 5.522 | 6.6324 | 7.0985 | 6.5756 | 0 | 6.5897 | 6.5524 | 1.3526 | 1.4569 | 1.4331 | 0 | 1.4765 | 1.2742 | 7.0172 | 6.8784 | 7.0803 | 0 | 7.1699 | 7.1091 | 1.3771 | 1.4433 | 1.4284 | 0 | 1.4816 | 1.5979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116168 | 204 | 108086 | 201 | 223312 | 612 | 6.6324 | 7.0985 | 6.5756 | 0 | 6.5897 | 6.5524 | 7.0172 | 6.8784 | 7.0803 | 0 | 7.1699 | 7.1091 | 975000 | 1000 | 964000 | 1000 | 1930000 | 4000 | 1937000 | 1926000 | 12.2667 | 6.6897 | 1.3986 | 7.051 | 1.4657 | 20.91% | 20.79% | 30.9008 | 47.1561 | 2.6936 | 5.804 | 1948542.3 | 1930773 | 2337452.3043 | 82.6%
2022-09-19 | 2023 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 334195.71 | 6:28 | 18:46 | 11493.5 | 12974.5 | 12954.9 | 12923.4 | 12875.3 | 13078.1 | 12948.8 | 13350.3 | 12997.2 | 12659.6 | 12855.1 | 13030.2 | 12996.2 | 12945.5 | 12257.2 | 12927.3 | 12871.6 | 12992.2 | 13056.1 | 13023 | 13071.3 | 13034.2 | 12747.5 | 12920.2 | 12739.4 | 11128.9 | 12976.2 | 12992.1 | 12684.8 | 12760.3 | 12643.2 | 13084.4 | 12875 | 13044.4 | 13025 | 13018.7 | 13067.2 | 12924.2 | 12993.2 | 12966.9 | 13238.8 | 12122.8 | 13116 | 11872.6 | 12595 | 13672.3 | 11785.2 | 13249.5 | 12109.7 | 11675.2 | 12977.3 | 12349.3 | 13505.9 | 12082.3 | 13491.7 | 12158.4 | 12047.8 | 13236.5 | 12094.3 | 13479.5 | 13395.2 | 11862.8 | 13693.3 | 12442 | 12540.3 | 11735.5 | 12057.8 | 12280.2 | 12680.5 | 11336 | 12143 | 10530.4 | 10904.4 | 12670.9 | 11341 | 12669.3 | 11099.6 | 12903 | 11872.9 | 13138.9 | 11073.1 | 11742.4 | 10931.8 | 12308.2 | 10602.9 | 11409.9 | 11794.4 | 9650.5 | 11131.3 | 10744.8 | 9679 | 11367.6 | 11454.9 | 10545.1 | 10547 | 11609.6 | 10654.3 | 11230.6 | 13113.2 | 11578.6 | 13039.3 | 11607.2 | 12991.6 | 11949.5 | 13169.2 | 11383.3 | 13300.4 | 12054.3 | 13186.5 | 12031.7 | 13256.5 | 12238.9 | 11667.1 | 12755.6 | 11727.8 | 11527.4 | 13022 | 12497.9 | 12977.8 | 11791 | 12872.2 | 11500.7 | 12751.4 | 12011.4 | 12702.4 | 10742.7 | 12780.8 | 11647.1 | 11719.6 | 11726 | 11663.2 | 10151.3 | 11881.4 | 10204.3 | 11384.9 | 11457.5 | 13547.7 | 11800.1 | 13577.9 | 12243.7 | 13421.8 | 11907.9 | 12073.9 | 11514.7 | 13230.8 | 13560.1 | 13538.5 | 13483.2 | 13422.7 | 13481 | 12356.4 | 13490 | 13360.5 | 13471.6 | 13379 | 13114.8 | 13612.1 | 11242.8 | 13166.6 | 12372.4 | 31.517 | 31.9137 | 31.9392 | 0 | 32.3002 | 32.0738 | 0 | 46.2171 | 0 | 0 | 0 | 0 | 4.252 | 4.2006 | 4.3124 | 0 | 4.1941 | 4.0974 | 8.04 | 6.81 | 7.278 | 0 | 7.786 | 7.087 | 6.7498 | 7.2462 | 6.6543 | 0 | 6.6773 | 6.6119 | 1.4021 | 1.4814 | 1.4808 | 0 | 1.4914 | 1.2879 | 7.1326 | 7.0356 | 7.1992 | 0 | 7.2511 | 7.1757 | 1.4231 | 1.4669 | 1.4688 | 0 | 1.4933 | 1.6164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117173 | 206 | 109049 | 203 | 225272 | 617 | 6.7498 | 7.2462 | 6.6543 | 0 | 6.6773 | 6.6119 | 7.1326 | 7.0356 | 7.1992 | 0 | 7.2511 | 7.1757 | 1005000 | 2000 | 963000 | 2000 | 1960000 | 5000 | 1964000 | 1955000 | 12.3 | 6.7879 | 1.4287 | 7.1588 | 1.4937 | 21.05% | 20.86% | 31.9488 | 46.2171 | 4.2113 | 7.4002 | 1978975.5 | 1961400 | 2378175.0963 | 82.48%
2022-09-20 | 2023 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 334195.71 | 6:29 | 18:46 | 11367 | 12511.3 | 12485.1 | 12477.3 | 12401 | 12570 | 12488.9 | 12812.5 | 12523.7 | 12262.2 | 12418.5 | 12550.1 | 12558.6 | 12490.5 | 12030.5 | 12617.3 | 12435.7 | 12553.6 | 12577.5 | 12573.4 | 12581.7 | 12576 | 12370.5 | 12495 | 12360.2 | 11048.8 | 12540.5 | 12538.5 | 12317 | 12351.3 | 12310.3 | 12617.7 | 11667.3 | 11798.9 | 11793.9 | 11777.6 | 11827.2 | 11723.3 | 11759.1 | 11752 | 13216.3 | 12269.5 | 13051.2 | 12087.7 | 12631.5 | 13720.2 | 11979.4 | 13181.2 | 11933.6 | 11570.9 | 12558.4 | 12105.8 | 12994.9 | 11898.2 | 12965.4 | 11981.5 | 11891.7 | 12836 | 11941.4 | 13070.2 | 13017.2 | 11726.2 | 13214.2 | 12129.8 | 12418.6 | 11820.8 | 12494.1 | 12657.3 | 13140.3 | 11998.1 | 12976.9 | 11629.3 | 11562.6 | 13035.9 | 11918.9 | 12961.5 | 11660.6 | 13087 | 11869.8 | 12798.9 | 11781.7 | 12298.9 | 11702 | 12845.9 | 11540.1 | 12226.4 | 11640.9 | 9542.5 | 12489.6 | 12114.2 | 11183 | 12763.2 | 12462.3 | 11701.4 | 11505.5 | 12449.2 | 11295.6 | 11822.7 | 12680.5 | 11442.1 | 12631.4 | 11466.8 | 12561.2 | 11777.9 | 12683 | 11252.6 | 12840 | 11854 | 12760.5 | 11894.5 | 12835.9 | 12038.4 | 11521 | 12426.5 | 11656.7 | 11480.6 | 12611.6 | 12202.2 | 12542.9 | 11622.3 | 12575.5 | 11404.8 | 12361.7 | 11828.2 | 12330.1 | 10625.5 | 12396.1 | 11518.9 | 11583.1 | 11574.7 | 11511.9 | 10029.1 | 11679.3 | 10061.6 | 11421.5 | 11343.6 | 13088.4 | 11658.9 | 13084.6 | 12009 | 12914.5 | 11707.4 | 11861.2 | 11525.4 | 12783.1 | 13099 | 13080.8 | 13024.1 | 12972.4 | 13041.8 | 12102.2 | 13024.1 | 12851.9 | 12965.2 | 12873.1 | 12656.5 | 13145.7 | 11148.9 | 12698.5 | 12121.2 | 30.9541 | 32.1298 | 32.1491 | 0 | 32.3102 | 29.7361 | 0 | 45.9223 | 0 | 0 | 0 | 0 | 4.7675 | 4.7732 | 4.7248 | 0 | 4.6417 | 4.4371 | 8.089 | 7.828 | 8.285 | 0 | 8.076 | 8.676 | 6.6556 | 7.1321 | 6.5799 | 0 | 6.5671 | 5.8494 | 1.3909 | 1.4503 | 1.4731 | 0 | 1.4612 | 1.1036 | 7.1611 | 6.9058 | 7.1195 | 0 | 7.1307 | 6.3747 | 1.4113 | 1.4353 | 1.4615 | 0 | 1.4607 | 1.3871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118157 | 207 | 110010 | 204 | 227208 | 621 | 6.6556 | 7.1321 | 6.5799 | 0 | 6.5671 | 5.8494 | 7.1611 | 6.9058 | 7.1195 | 0 | 7.1307 | 6.3747 | 984000 | 1000 | 961000 | 1000 | 1936000 | 4000 | 1943000 | 1932000 | 12.2833 | 6.5568 | 1.3758 | 6.9384 | 1.4312 | 20.98% | 20.63% | 31.4559 | 45.9223 | 4.6689 | 8.1908 | 1954745.7 | 1938333 | 2356111.6177 | 82.27%
2022-09-21 | 2023 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 334195.71 | 6:29 | 18:45 | 11296.3 | 12500.2 | 12474.8 | 12460.4 | 12378 | 12541.2 | 12463 | 12790.7 | 12513.2 | 12240.1 | 12404.5 | 12539.7 | 12543 | 12479 | 11970.8 | 12612.5 | 12416.5 | 12536.07 | 12561.2 | 12555.4 | 12564.9 | 12562.8 | 12348.36 | 12478.3 | 11885.3 | 10563.4 | 12044 | 12045.8 | 11850.8 | 11875.7 | 11818.5 | 12129.4 | 12423 | 12571.2 | 12554.5 | 12543 | 12594.2 | 12473.1 | 12517.6 | 12499.1 | 13240.88 | 12269.9 | 13057.8 | 12062.5 | 12579 | 13575.85 | 11934.6 | 13208.1 | 11883.9 | 11489.2 | 12547.2 | 12069.7 | 12985.6 | 11835.8 | 12971.1 | 11933.8 | 11850.3 | 12809 | 11879.4 | 13076.6 | 13025 | 11663 | 13210.1 | 12102.8 | 12415.76 | 11756 | 12477.77 | 12637.1 | 13132.18 | 11949.6 | 12966.9 | 11533.1 | 11459.8 | 13014.3 | 11880.8 | 12951 | 11581.96 | 13088.7 | 11806.1 | 12796.4 | 11715.5 | 12268.2 | 11631.35 | 12827 | 11451 | 12175.2 | 11574.6 | 9450.7 | 12437.9 | 12048.3 | 11097.5 | 12756.4 | 12441.9 | 11626.8 | 11412.12 | 12454.6 | 11219.6 | 11759.7 | 12659.9 | 11342.8 | 12605.3 | 11310 | 12535.4 | 11696.68 | 12655 | 11139.5 | 12808.4 | 11777.4 | 12725.1 | 11817.6 | 12799 | 11950.9 | 11483 | 12502.46 | 11591.9 | 11487.2 | 12601.9 | 12226 | 12597.08 | 11545 | 12594.1 | 11328.8 | 12355.5 | 11800.8 | 12326.7 | 10538 | 12383.6 | 11384.6 | 11464.1 | 11472.5 | 11386.2 | 9916.3 | 11599.8 | 9976.6 | 11293.29 | 11252.1 | 13103.5 | 11620.4 | 13101.6 | 11996.1 | 12939 | 11681.7 | 11836.9 | 11468 | 12811.5 | 13113.6 | 13100.54 | 13038.7 | 12988 | 13057.9 | 12098.2 | 13041.7 | 12865.9 | 12985.86 | 12905.6 | 12689.5 | 13176.2 | 11099.3 | 12713.5 | 12110.4 | 30.9015 | 31.9468 | 32.0711 | 0 | 32.5451 | 32.2254 | 0 | 46.8789 | 0 | 0 | 0 | 0 | 3.7527 | 3.7349 | 3.7818 | 0 | 3.6959 | 3.7444 | 5.773 | 6.058 | 6.466 | 0 | 6.563 | 6.846 | 6.4551 | 7.1067 | 6.5137 | 0 | 6.5126 | 6.4971 | 1.356 | 1.4373 | 1.4416 | 0 | 1.4437 | 1.2379 | 7.1264 | 6.8929 | 7.0735 | 0 | 7.1011 | 7.0221 | 1.3798 | 1.4219 | 1.4325 | 0 | 1.4447 | 1.5522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119142 | 208 | 110968 | 206 | 229142 | 625 | 6.4551 | 7.1067 | 6.5137 | 0 | 6.5126 | 6.4971 | 7.1264 | 6.8929 | 7.0735 | 0 | 7.1011 | 7.0221 | 985000 | 1000 | 958000 | 2000 | 1934000 | 4000 | 1940000 | 1930000 | 12.2667 | 6.6171 | 1.3833 | 7.0432 | 1.4462 | 20.91% | 20.53% | 31.938 | 46.8789 | 3.7419 | 6.3412 | 1952150.61 | 1935400 | 2334520.1296 | 82.9%
2022-09-22 | 2023 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 334195.71 | 6:28 | 18:48 | 10956.4 | 12188.7 | 12185 | 12175.6 | 12073.2 | 12229.2 | 12142.9 | 12463.7 | 12212 | 11947.47 | 12078.6 | 12223 | 12210.4 | 12150.3 | 11609.9 | 12289.6 | 12074 | 12186.6 | 12205.8 | 12195.3 | 12147.8 | 12207.7 | 12010.1 | 12138.5 | 11988.3 | 10557.7 | 12162.1 | 12164.5 | 11955.3 | 11979.3 | 11949.4 | 12284.9 | 12102.6 | 12241.8 | 12217.6 | 12235.3 | 12285.1 | 12156.8 | 12206.5 | 12196.9 | 13016.5 | 12017.4 | 12825.66 | 11804 | 12329.6 | 13495.77 | 11635.4 | 12967.5 | 11496.2 | 11086.8 | 12192.3 | 11661.2 | 12622.3 | 11446.4 | 12578.8 | 11491.5 | 11421 | 12454.8 | 11490.3 | 12739.7 | 12709.1 | 11285.3 | 12895.1 | 11738.8 | 11959.1 | 11309.5 | 12089 | 12254.1 | 12693 | 11533.58 | 12607.4 | 11104.8 | 11042 | 12671.88 | 11442.9 | 12514.4 | 11153.1 | 12756.9 | 11405.4 | 12443.56 | 11303.1 | 11887.04 | 11181.2 | 12439.19 | 10944.9 | 11750.01 | 11068.1 | 9109 | 12094 | 11764.9 | 10767 | 12473.2 | 12157.3 | 11291.4 | 11069.5 | 12218.8 | 10846.7 | 11482.5 | 12450.2 | 11071 | 12376.2 | 11088.4 | 12295.5 | 11410.8 | 12361.2 | 10863 | 12520.6 | 11459.5 | 12497.4 | 11546.1 | 12497.5 | 11693.6 | 11143.5 | 12271.4 | 11347.9 | 11203.6 | 12396.8 | 11942.5 | 12372.9 | 11306.35 | 12274 | 11058.7 | 12129.1 | 11535.6 | 12024.2 | 10322.9 | 12195.1 | 11148.06 | 11158 | 11166.7 | 11056.2 | 9339.9 | 11230.9 | 9697 | 10965.6 | 10930.2 | 12868.2 | 11299.4 | 12803.71 | 11694.9 | 12670.5 | 11302.4 | 11476.7 | 11077.8 | 12547.4 | 12808.6 | 12841.6 | 12783.8 | 12735.6 | 12811.7 | 11827.8 | 12803.56 | 12586.4 | 12725 | 12671.36 | 12415.7 | 12933.7 | 10784.4 | 12440.4 | 11814.5 | 32.0335 | 32.4733 | 32.5627 | 0 | 33.0713 | 32.6458 | 0 | 45.7922 | 0 | 0 | 0 | 0 | 4.0919 | 3.9213 | 3.9271 | 0 | 4.0267 | 3.8851 | 6.293 | 6.035 | 6.266 | 0 | 6.489 | 6.321 | 6.3869 | 6.8503 | 6.3191 | 0 | 6.3126 | 6.2888 | 1.312 | 1.3769 | 1.4008 | 0 | 1.3924 | 1.256 | 6.8315 | 6.6378 | 6.8974 | 0 | 6.8747 | 6.8076 | 1.3333 | 1.3612 | 1.3927 | 0 | 1.3986 | 1.5823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120103 | 210 | 111902 | 207 | 231029 | 629 | 6.3869 | 6.8503 | 6.3191 | 0 | 6.3126 | 6.2888 | 6.8315 | 6.6378 | 6.8974 | 0 | 6.8747 | 6.8076 | 961000 | 2000 | 934000 | 1000 | 1887000 | 4000 | 1892000 | 1883000 | 12.3333 | 6.4315 | 1.3476 | 6.8098 | 1.4136 | 20.95% | 20.76% | 32.5573 | 45.7922 | 3.9704 | 6.2808 | 1904289 | 1888466 | 2258094.2735 | 83.63%
2022-09-23 | 2023 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 334195.71 | 6:30 | 18:42 | 10899 | 12209.1 | 12219.2 | 12185 | 12064.3 | 12266.6 | 12163.1 | 12509.4 | 12236.9 | 11917.2 | 12067.7 | 12239.2 | 12218.4 | 12158.4 | 11602 | 12303.1 | 10997.7 | 11143.9 | 11165.5 | 11074.3 | 11201 | 11187.8 | 10930.1 | 11077.8 | 11954.8 | 10541.1 | 12187.2 | 12211 | 11904.3 | 11915.7 | 11807.6 | 12242.5 | 11893 | 12127.3 | 12168.6 | 12157.5 | 12179.3 | 12001 | 12039.7 | 11997.2 | 13008.9 | 11857.7 | 12766.1 | 11610.9 | 12139.1 | 13390.4 | 11462 | 12956.2 | 11455.4 | 11043.7 | 12204.8 | 11642.2 | 12707 | 11393.7 | 12700.8 | 11485.2 | 11398.4 | 12547.7 | 11442.7 | 12808.3 | 12753.2 | 11226 | 12977.6 | 11663.8 | 12072.2 | 11321.8 | 12119.9 | 12318.8 | 12927.1 | 11518.2 | 12705.9 | 11056.6 | 11015.9 | 12751.9 | 11423.8 | 12673.7 | 11124.5 | 12834.6 | 11335 | 12471.3 | 11205.2 | 11903.3 | 11109.7 | 12459.1 | 10911.1 | 11627.9 | 11153.8 | 9166.1 | 11949.7 | 11599.2 | 10515.6 | 12255.7 | 11869.9 | 10962.1 | 10737.3 | 11994.3 | 10690 | 11354.7 | 12356 | 10956.9 | 12225.7 | 10939.7 | 12126.6 | 11279.1 | 12307.8 | 10713.8 | 12488.5 | 11397.5 | 12360.1 | 11372.5 | 12162.9 | 11534 | 11099.5 | 12204.5 | 11204.3 | 11088.7 | 12360.2 | 11997 | 12290.1 | 11248.4 | 12340.9 | 10979.3 | 12018.8 | 11365.4 | 11946.1 | 10245.1 | 12128.3 | 11060.3 | 10964.9 | 10976.4 | 10871.4 | 9472.9 | 11093.7 | 9535.2 | 10796.1 | 10762.5 | 12894.3 | 11184.1 | 12900.6 | 11562.5 | 12646.5 | 11198.1 | 11382 | 10962.8 | 12481.3 | 12875.3 | 12841 | 12771.3 | 12649.7 | 12823.5 | 11682.5 | 12783.5 | 12553.1 | 12770.7 | 12881 | 12384.6 | 12969.8 | 10651.3 | 12397 | 11685.8 | 32.2215 | 32.9018 | 32.9636 | 0 | 33.5611 | 33.0816 | 0 | 46.9902 | 0 | 0 | 0 | 0 | 3.8995 | 3.9315 | 3.9052 | 0 | 3.9234 | 3.804 | 7.035 | 6.815 | 7.525 | 0 | 7.465 | 6.951 | 6.3739 | 6.8639 | 6.2424 | 0 | 6.2651 | 6.255 | 1.2893 | 1.3739 | 1.3761 | 0 | 1.3824 | 1.2293 | 6.8621 | 6.6306 | 6.8291 | 0 | 6.8579 | 6.7397 | 1.3159 | 1.3571 | 1.3669 | 0 | 1.3891 | 1.5462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121055 | 211 | 112829 | 209 | 232900 | 633 | 6.3739 | 6.8639 | 6.2424 | 0 | 6.2651 | 6.255 | 6.8621 | 6.6306 | 6.8291 | 0 | 6.8579 | 6.7397 | 952000 | 1000 | 927000 | 2000 | 1871000 | 4000 | 1876000 | 1867000 | 12.2 | 6.4 | 1.3302 | 6.7839 | 1.395 | 20.78% | 20.56% | 32.9459 | 46.9902 | 3.8927 | 7.1582 | 1887345.6 | 1871867 | 2244741.1877 | 83.39%
2022-09-24 | 2023 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 334195.71 | 6:35 | 18:44 | 11191.25 | 12319.68 | 12309.5 | 12297.1 | 12186.2 | 12377.3 | 12285 | 12556.5 | 12326.4 | 12070.59 | 12223.6 | 12345.5 | 12388.1 | 12297.5 | 12170.3 | 12453.3 | 12240.5 | 12384.2 | 12409.2 | 12293.97 | 12401.56 | 12400.9 | 12207.99 | 12328 | 12191 | 10850.5 | 12371.6 | 12368 | 12224.59 | 12158.9 | 12142.6 | 12442.3 | 12243.4 | 12400.44 | 12380.6 | 12389.4 | 12431.7 | 12310.5 | 12341.3 | 12337 | 13042.2 | 12144.1 | 12842.7 | 11951.7 | 12394.11 | 13454.4 | 11771 | 12981.4 | 11743.7 | 11347.1 | 12371.6 | 11905.8 | 12798.88 | 11700.4 | 12747.6 | 11793.6 | 11706.19 | 12644.3 | 11627 | 12871.75 | 12833.1 | 11529.4 | 13020.5 | 11956.4 | 12285 | 11674.95 | 12325.8 | 12519.69 | 12947.7 | 11875.1 | 12798.3 | 11471.49 | 11354.9 | 12864.4 | 11744.1 | 12778.2 | 11465.4 | 12884.72 | 11687 | 12616.86 | 11612 | 12275.85 | 11477.8 | 12665.9 | 11330 | 11979.3 | 11678.6 | 9603 | 12287.96 | 11998.3 | 10957.1 | 12540.45 | 12223.5 | 11437.3 | 11212.1 | 12377.6 | 11073.3 | 11721.7 | 12516.8 | 11301.6 | 12431.7 | 11321.5 | 12365.3 | 11670.65 | 12464.5 | 11068.1 | 12625.7 | 11708.8 | 12554.38 | 11692.8 | 12385.6 | 11869 | 11442.42 | 12379.2 | 11499.2 | 11428.6 | 12496.3 | 12297.3 | 12450.9 | 11588.2 | 12501.74 | 11312.8 | 12232.3 | 11696.4 | 12177.8 | 10540.3 | 12341 | 11396.4 | 11308.4 | 11318.8 | 11201.8 | 9768.9 | 11450.4 | 9840.4 | 11195.8 | 11114.63 | 12921.7 | 11515.8 | 12934.1 | 11868.2 | 12761 | 11557.4 | 11725.5 | 11459 | 12645.7 | 12947.2 | 12921.9 | 12858.9 | 12758 | 12881.6 | 11980.8 | 12870.8 | 12607.9 | 12787.2 | 12873.1 | 12505.8 | 12990.8 | 10997.7 | 12532.8 | 11983.91 | 29.7782 | 29.2483 | 31.2393 | 0 | 31.1065 | 31.6447 | 0 | 42.6627 | 0 | 0 | 0 | 0 | 5.1945 | 4.7836 | 5.1805 | 0 | 5.0899 | 5.1584 | 8.247 | 8.1 | 8.13 | 0 | 7.826 | 7.685 | 6.5152 | 6.583 | 6.4041 | 0 | 6.4068 | 6.4411 | 1.3352 | 1.3418 | 1.4251 | 0 | 1.4369 | 1.2224 | 7.0333 | 6.3227 | 7.0239 | 0 | 7.0462 | 6.9079 | 1.3595 | 1.325 | 1.4106 | 0 | 1.4376 | 1.5293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122031 | 213 | 113777 | 210 | 234816 | 637 | 6.5152 | 6.583 | 6.4041 | 0 | 6.4068 | 6.4411 | 7.0333 | 6.3227 | 7.0239 | 0 | 7.0462 | 6.9079 | 976000 | 2000 | 948000 | 1000 | 1916000 | 4000 | 1921000 | 1912000 | 12.15 | 6.4701 | 1.3523 | 6.8668 | 1.4124 | 20.9% | 20.57% | 30.6034 | 42.6627 | 5.0814 | 7.9976 | 1933815.5 | 1917467 | 2332221.5807 | 82.22%
2022-09-25 | 2023 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 334195.71 | 6:30 | 18:39 | 9948.2 | 10723.2 | 10711.4 | 10676.2 | 10634.6 | 10788.6 | 10715 | 10910.1 | 10701 | 10460.7 | 10625.1 | 10707.7 | 10802.3 | 10688.3 | 10687.8 | 10889.7 | 10732.8 | 10839 | 10836.2 | 10742.4 | 10840.6 | 10850.5 | 10703.7 | 10777.8 | 10647.8 | 9636.7 | 10759.9 | 10783.3 | 10869.6 | 10644.5 | 10638.5 | 10852.5 | 10666.8 | 10778.8 | 10777.3 | 10780.5 | 10821.7 | 10736.3 | 10762.5 | 10745.9 | 11309.8 | 10580.5 | 11160.7 | 10426.9 | 10844.1 | 11732.4 | 10394.2 | 11322.2 | 10290.3 | 10029.4 | 10783 | 10392.3 | 11105.8 | 10286.7 | 11019.2 | 10353.9 | 10208.2 | 10917 | 10163.3 | 11097.3 | 11089.1 | 10125.9 | 11146.7 | 10314.7 | 10569.7 | 10120.8 | 10645 | 10754 | 11102.1 | 10247.3 | 10992.2 | 9981 | 9936.9 | 11000.6 | 10176.2 | 10915.2 | 9965.6 | 11025.4 | 10119.6 | 10825 | 10017.8 | 10519.1 | 9910 | 10822.5 | 9784.2 | 10292.1 | 10091.1 | 8396 | 10427.4 | 10318.6 | 9655 | 10828.5 | 10664.9 | 10164.6 | 10034.4 | 10732.7 | 9897.3 | 10211.9 | 10844.4 | 9952 | 10812.1 | 9949.5 | 10805.6 | 10303.4 | 10850.8 | 9860.1 | 10993 | 10301.8 | 10948.1 | 10299.6 | 10832.4 | 10451 | 10027 | 10725.5 | 10099.2 | 10096.7 | 10912 | 10720.5 | 10865.3 | 10235.4 | 10794.6 | 9999.8 | 10691.5 | 10303.8 | 10642.3 | 9380.8 | 10785 | 10101.8 | 10009.1 | 9974.9 | 9807.5 | 8617.2 | 10048.3 | 8687.8 | 9657.9 | 9714.3 | 11077.3 | 10033.9 | 11056.5 | 10271 | 10977.4 | 10045 | 10168.7 | 10015.8 | 10800.1 | 11025 | 11042.7 | 10981.3 | 10886.8 | 11009.2 | 10294.1 | 10992.7 | 10752 | 10883.1 | 10983 | 10685.4 | 11062.5 | 9521.3 | 10657.2 | 10253.7 | 27.7138 | 29.9504 | 29.8549 | 0 | 29.6294 | 30.2016 | 0 | 41.9244 | 0 | 0 | 0 | 0 | 5.7005 | 6.0181 | 5.6191 | 0 | 5.7369 | 5.6945 | 9.346 | 9.503 | 9.118 | 0 | 9.423 | 9.204 | 5.7708 | 6.3542 | 5.7216 | 0 | 5.6849 | 5.6514 | 1.1026 | 1.366 | 1.1961 | 0 | 1.3861 | 1.2072 | 6.2472 | 6.1078 | 6.112 | 0 | 6.3513 | 6.0195 | 1.1232 | 1.3489 | 1.1872 | 0 | 1.3961 | 1.4956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122880 | 214 | 114602 | 211 | 236482 | 642 | 5.7708 | 6.3542 | 5.7216 | 0 | 5.6849 | 5.6514 | 6.2472 | 6.1078 | 6.112 | 0 | 6.3513 | 6.0195 | 849000 | 1000 | 825000 | 1000 | 1666000 | 5000 | 1672000 | 1661000 | 12.15 | 5.8366 | 1.2516 | 6.1676 | 1.3102 | 21.44% | 21.24% | 29.47 | 41.9244 | 5.7538 | 9.3188 | 1681711.5 | 1667747 | 2084132.5042 | 80.02%
2022-09-26 | 2023 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 334195.71 | 6:31 | 18:39 | 9940.86 | 10997.6 | 11124.12 | 11074.58 | 10972.7 | 11064.31 | 10974.63 | 11151.75 | 10992.68 | 10589.3 | 10830.45 | 10991.99 | 10882.5 | 10870.1 | 10571.56 | 10894.83 | 10626.87 | 10710.4 | 10766.66 | 10734.65 | 10633.4 | 10684.3 | 10309.68 | 10453.17 | 10505.37 | 9345.32 | 10761.76 | 10615.3 | 10585.96 | 10403.4 | 10527.1 | 10652.97 | 10681.62 | 10854.44 | 10681.9 | 10699.64 | 10718.76 | 10659.74 | 10777.19 | 10792.75 | 11389.3 | 10555.5 | 11229.95 | 10377.41 | 10690.38 | 11684.92 | 10135.81 | 11303.3 | 10243.69 | 9937.03 | 10855.8 | 10378.41 | 11228.5 | 10200 | 11244.28 | 10282.2 | 10287.84 | 11223.62 | 10160.7 | 11401.32 | 11423.98 | 10194.5 | 11593.79 | 10578 | 11081.45 | 10557.5 | 11109.43 | 11401.87 | 11658.77 | 10755.41 | 11589.9 | 10422.08 | 10094.8 | 11706.88 | 10490.43 | 11676.03 | 10374.86 | 11576.6 | 10493.9 | 11519.07 | 10462.19 | 11151.2 | 10304.6 | 11507.19 | 10167.15 | 10760.2 | 10500.21 | 8615.2 | 11191.04 | 10880.77 | 9982.05 | 11477.28 | 11318.89 | 10562.34 | 10313.8 | 11488.99 | 10331.06 | 10696.64 | 11555.62 | 10262.58 | 11240.6 | 10262.6 | 11210.75 | 10617.91 | 11462.22 | 10068.6 | 11648.28 | 10620.85 | 11522.09 | 10574.1 | 11369.5 | 10721.21 | 10331.35 | 11250.73 | 10477.07 | 10355.9 | 11502.2 | 11197.74 | 11461.1 | 10487.2 | 11344.05 | 10231.2 | 11181.5 | 10640.65 | 11106.99 | 9605.82 | 11308 | 10361.4 | 10051.14 | 9967.94 | 10084.02 | 8680.51 | 10034.85 | 8491.45 | 9255.9 | 9325.11 | 11109.4 | 9818.13 | 11142.58 | 10130.14 | 10948.92 | 9750.8 | 9951.21 | 9668.46 | 10874.9 | 11133.6 | 11060.9 | 11040.78 | 10967.96 | 11028.3 | 10200.99 | 11042.61 | 10795.96 | 10987.43 | 11294 | 10857.37 | 11175.4 | 9338.3 | 10547.45 | 10163.67 | 28.1488 | 30.2526 | 30.2738 | 0 | 30.4193 | 30.5095 | 0 | 44.5646 | 0 | 0 | 0 | 0 | 2.466 | 2.3756 | 2.3639 | 0 | 2.4558 | 2.3573 | 7.8833 | 5.695 | 5.7417 | 0 | 5.2967 | 5.6467 | 5.8567 | 6.0555 | 5.6039 | 0 | 5.9062 | 5.5733 | 1.174 | 1.256 | 1.2134 | 0 | 1.3537 | 1.1098 | 6.3284 | 5.8492 | 6.0663 | 0 | 6.4872 | 5.9675 | 1.197 | 1.2338 | 1.2118 | 0 | 1.3684 | 1.369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123740 | 215 | 115446 | 213 | 238179 | 646 | 5.8567 | 6.0555 | 5.6039 | 0 | 5.9062 | 5.5733 | 6.3284 | 5.8492 | 6.0663 | 0 | 6.4872 | 5.9675 | 860000 | 1000 | 844000 | 2000 | 1697000 | 4000 | 1701000 | 1693000 | 12.1333 | 5.7991 | 1.2214 | 6.1397 | 1.276 | 21.06% | 20.78% | 29.9208 | 44.5646 | 2.4037 | 6.0527 | 1711826.31 | 1698126 | 2061488.202 | 82.37%
2022-09-27 | 2023 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 334195.71 | 6:31 | 18:36 | 10518.62 | 11804.3 | 11891.5 | 11891.6 | 11732.11 | 11892.3 | 11824.1 | 12076 | 11855.92 | 11393.66 | 11736.5 | 11856.9 | 11908.1 | 11807.45 | 11506 | 11907.8 | 11660.9 | 11870.49 | 11857.4 | 11861.67 | 11873.4 | 11847.86 | 11710.1 | 11808.28 | 11661.81 | 10198.7 | 11813 | 11771.14 | 11915.6 | 11777 | 11788.2 | 11911.6 | 11638.1 | 11795.3 | 11734.8 | 11755.9 | 11867.3 | 11804.8 | 11871.6 | 11845.1 | 12497.5 | 11667.26 | 12308.5 | 11447.8 | 11786.84 | 12812.6 | 11099.6 | 12412.41 | 11149.4 | 10732.1 | 11891.74 | 11287.1 | 12300.6 | 11124.1 | 12164.5 | 11116.9 | 11019.4 | 11989.4 | 10951.7 | 12220.19 | 12187.1 | 10914.7 | 12212.87 | 11176.61 | 11638.17 | 10888.77 | 11661.87 | 11789.2 | 12275.5 | 11145.95 | 12119.5 | 10730.8 | 10539.3 | 12198.81 | 10935.9 | 12129.4 | 10735.77 | 12198.2 | 10957.81 | 11964.14 | 10788.5 | 11546.7 | 10648.77 | 11931.6 | 10523.59 | 11216.7 | 10921.55 | 8928.8 | 11552.64 | 11304 | 10227.98 | 11852.4 | 11679.6 | 10943.5 | 10764 | 11839.1 | 10531.4 | 10892.04 | 11862.2 | 10531.4 | 11922 | 10651.01 | 11915.49 | 11068 | 12018.4 | 10536 | 12177.6 | 11087.3 | 12130.57 | 11080.15 | 12007.5 | 11287.2 | 10620.46 | 11667.7 | 10904 | 10740.7 | 11963.63 | 11675.57 | 11971.2 | 10938.57 | 11989.5 | 10719.91 | 11730.4 | 11133.7 | 11685.1 | 9979.7 | 11819.7 | 10734.67 | 10544.7 | 10427.6 | 10374.5 | 9093.7 | 10488.6 | 9000.1 | 10069.7 | 10003.4 | 11826.7 | 10340.6 | 11862.3 | 10738.4 | 11653.09 | 10404.42 | 10575.3 | 10355.2 | 11618.6 | 11894.5 | 11726.48 | 11699.15 | 11676.17 | 11787.85 | 10931.75 | 11832.4 | 11507.7 | 11745.1 | 11969.2 | 11610.6 | 12042.48 | 10046.5 | 11381.2 | 10916.3 | 30.1064 | 31.5864 | 31.695 | 0 | 31.8997 | 31.8161 | 0 | 45.6235 | 0 | 0 | 0 | 0 | 3.6004 | 3.628 | 3.6406 | 0 | 3.6845 | 3.5414 | 6.61 | 6.8617 | 6.5283 | 0 | 6.9583 | 6.275 | 6.204 | 6.6303 | 6.0075 | 0 | 6.0315 | 5.7696 | 1.3135 | 1.2965 | 1.3901 | 0 | 1.3339 | 1.0738 | 6.7028 | 6.4082 | 6.6503 | 0 | 6.6082 | 6.2183 | 1.3418 | 1.2731 | 1.3764 | 0 | 1.3395 | 1.3396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124669 | 217 | 116322 | 215 | 239987 | 650 | 6.204 | 6.6303 | 6.0075 | 0 | 6.0315 | 5.7696 | 6.7028 | 6.4082 | 6.6503 | 0 | 6.6082 | 6.2183 | 929000 | 2000 | 876000 | 2000 | 1808000 | 4000 | 1801000 | 1804000 | 12.0833 | 6.1286 | 1.2816 | 6.5176 | 1.3341 | 20.91% | 20.47% | 31.4207 | 45.6235 | 3.619 | 6.6467 | 1824409.41 | 1808867 | 2173390.0631 | 83.23%
2022-09-28 | 2023 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 334195.71 | 6:31 | 18:36 | 10997.5 | 11977.2 | 11909.2 | 11981.2 | 11676.5 | 11839.3 | 11827.1 | 12049.9 | 12028.4 | 11965.5 | 11865.5 | 12018.1 | 11897.9 | 11906.8 | 11540.6 | 11897.9 | 11655.6 | 11839.7 | 11905.3 | 11886.6 | 11859.7 | 11878.4 | 11686.4 | 11768.9 | 11822.4 | 10366.7 | 11890.3 | 11882 | 11926.2 | 11784.3 | 11796.7 | 11946.1 | 11743.2 | 11957.9 | 11942 | 11903.3 | 11948 | 11862.4 | 11917.4 | 11892.1 | 12857.4 | 11908.8 | 12629.3 | 11700.2 | 12049.3 | 13103 | 11408.4 | 12755.9 | 11330.6 | 10942.8 | 11988.2 | 11496.6 | 12369.6 | 11140 | 12389.1 | 11354.1 | 11338.9 | 12306.8 | 11190.1 | 12566.5 | 12537.4 | 11162.2 | 12641.3 | 11548.6 | 11950.6 | 11235.1 | 11974.7 | 12131.1 | 12630.7 | 11455.1 | 12426.6 | 11048 | 10933.7 | 12543.1 | 11334.3 | 12536.2 | 11122.5 | 12581.7 | 11308.4 | 12340.5 | 11223.4 | 12023.6 | 11055.5 | 12323.8 | 10855.1 | 11550.1 | 11213.7 | 9154.6 | 12035.3 | 11583.7 | 10640 | 12310.6 | 11971 | 11163.6 | 10913.9 | 12141.2 | 10817.6 | 11280.7 | 12178.1 | 10838.6 | 12030.8 | 10856.9 | 11964.8 | 11203.6 | 12033 | 10596.6 | 12141.5 | 11163.5 | 12030.9 | 11111.4 | 11890.1 | 11240.4 | 10984.2 | 11971.5 | 11044.4 | 10926.5 | 12099.8 | 11819.8 | 12063.6 | 11051.3 | 12077.5 | 10783.2 | 11800.1 | 11207.8 | 11678.4 | 9972.5 | 11828.6 | 10827.7 | 10755.3 | 10749.4 | 10621 | 9242 | 10870.5 | 9412.5 | 10867.7 | 10869 | 12682.9 | 11167.9 | 12669.7 | 11560.8 | 12497 | 11184.3 | 11382.6 | 11093.7 | 12348.5 | 12624.6 | 12656.4 | 12578.7 | 12497.3 | 12620.5 | 11611.3 | 12553.6 | 12189.9 | 12418.1 | 12489.8 | 12126.8 | 12661.7 | 10586.9 | 12129 | 11589.6 | 29.7178 | 31.844 | 31.7868 | 0 | 31.9939 | 32.0698 | 0 | 46.0274 | 0 | 0 | 0 | 0 | 4.0272 | 4.0154 | 3.9904 | 0 | 3.9253 | 3.863 | 7.2983 | 7.345 | 8.0217 | 0 | 7.73 | 7.845 | 6.2409 | 6.69 | 6.186 | 0 | 6.1001 | 6.2346 | 1.2937 | 1.3121 | 1.4096 | 0 | 1.3406 | 1.1718 | 6.8045 | 6.4404 | 6.8595 | 0 | 6.7502 | 6.6647 | 1.3238 | 1.2883 | 1.3917 | 0 | 1.3544 | 1.4601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125614 | 218 | 117249 | 216 | 241839 | 655 | 6.2409 | 6.69 | 6.186 | 0 | 6.1001 | 6.2346 | 6.8045 | 6.4404 | 6.8595 | 0 | 6.7502 | 6.6647 | 945000 | 1000 | 927000 | 1000 | 1852000 | 5000 | 1870000 | 1847000 | 12.0833 | 6.2903 | 1.3056 | 6.7039 | 1.3637 | 20.76% | 20.34% | 31.4825 | 46.0274 | 3.9643 | 7.648 | 1869691.1 | 1854060 | 2236498.1914 | 82.9%
2022-09-29 | 2023 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 334195.71 | 6:31 | 18:34 | 11238.5 | 12279.4 | 12272.2 | 12273.31 | 12154.5 | 12325.99 | 12206.14 | 12460.2 | 12311.11 | 12254.5 | 12200.36 | 12327.5 | 12358.47 | 12280.2 | 12169.27 | 12413.3 | 12185 | 12358.23 | 12377.78 | 12354.2 | 12353.88 | 12363.33 | 12150.62 | 12268 | 12261 | 10751.29 | 12351.78 | 12348.2 | 12412.5 | 12192.96 | 12196.24 | 12406.12 | 12201.53 | 12411.72 | 12353.71 | 12360.28 | 12407.06 | 12294.15 | 12330.49 | 12304.31 | 13059.86 | 12084.4 | 12847.3 | 11879.24 | 12245.5 | 13382.7 | 11614.53 | 12985.63 | 11679.28 | 11279.6 | 12375.74 | 11866.23 | 12814.72 | 11575.1 | 12794.91 | 11726.9 | 11671.5 | 12665.85 | 11502.2 | 12920.13 | 12871.23 | 11464.4 | 12996.57 | 11842.21 | 12290.1 | 11584.46 | 12310.63 | 12503.8 | 12978 | 11769.2 | 12803.88 | 11335.8 | 11250.9 | 12875.78 | 11665.95 | 12807.44 | 11380.17 | 12903.69 | 11584.02 | 12610.72 | 11458.2 | 12339.01 | 11310.1 | 12691.1 | 11172.2 | 11881.13 | 11598.2 | 9345.54 | 12339.7 | 12048.37 | 10909.3 | 12608.2 | 12274.28 | 11450.1 | 11211.7 | 12451.03 | 11118.8 | 11665.97 | 12538.39 | 11173.4 | 12402.96 | 11239.99 | 12364.93 | 11591.79 | 12474 | 10967.98 | 12627.3 | 11599.2 | 12550.23 | 11581.5 | 12364.26 | 11737.26 | 11379.2 | 12372.1 | 11459.6 | 11324.3 | 12507.42 | 12267.92 | 12450.6 | 11511.48 | 12493.06 | 11218.05 | 12206.6 | 11647.83 | 12132.98 | 10489.89 | 12327.53 | 11332 | 11177.09 | 11128.57 | 10940.71 | 9597.61 | 11243.2 | 9757.14 | 11078.42 | 11097.4 | 12981.53 | 11429.7 | 12994.57 | 11846.75 | 12763.49 | 11445.62 | 11613.2 | 11325.32 | 12665.37 | 12993.7 | 12961.7 | 12904.35 | 12799.96 | 12921.26 | 11939.26 | 12913.9 | 12537.1 | 12774.95 | 12870.29 | 12472.26 | 12992.36 | 10874.96 | 12425.7 | 11916.1 | 30.6459 | 32.2609 | 32.3143 | 0 | 32.461 | 32.5481 | 0 | 47.7704 | 0 | 0 | 0 | 0 | 3.3765 | 3.4809 | 3.5224 | 0 | 3.3433 | 3.2994 | 6.175 | 6.2633 | 6.8383 | 0 | 6.485 | 6.735 | 7.1769 | 7.09 | 6.2775 | 0 | 6.1115 | 6.488 | 1.4215 | 1.3897 | 1.4199 | 0 | 1.3763 | 1.2061 | 7.1077 | 6.7731 | 6.9922 | 0 | 6.8844 | 6.8889 | 1.4 | 1.3634 | 1.3986 | 0 | 1.3911 | 1.5064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126587 | 220 | 118193 | 218 | 243749 | 659 | 7.1769 | 7.09 | 6.2775 | 0 | 6.1115 | 6.488 | 7.1077 | 6.7731 | 6.9922 | 0 | 6.8844 | 6.8889 | 973000 | 2000 | 944000 | 2000 | 1910000 | 4000 | 1913000 | 1906000 | 12.05 | 6.6288 | 1.3627 | 6.9292 | 1.4119 | 20.56% | 20.38% | 32.046 | 47.7704 | 3.4045 | 6.4993 | 1927909.82 | 1911500 | 2294713.0461 | 83.3%
2022-09-30 | 2023 | 2022 | Year_1 | Year_1 | 2022-10-01 | 30 | 334195.71 | 6:33 | 18:34 | 10812.9 | 11707 | 11708.7 | 11679.9 | 11620.6 | 11787.9 | 11664.2 | 11937.5 | 11740.9 | 11687.6 | 11687.8 | 11791.6 | 11797.1 | 11748.8 | 11656.6 | 11871.6 | 11669.5 | 11900.6 | 11918.6 | 11858.9 | 12016.6 | 11954.3 | 11850.4 | 11960.3 | 11925.5 | 10404.6 | 11892.4 | 11973.6 | 12107.2 | 11931 | 11952.8 | 12117.8 | 11898.3 | 12078.6 | 12011 | 12039.4 | 12088.5 | 12016 | 12084.8 | 12041.8 | 12923.6 | 11950.5 | 12733.8 | 11709.2 | 12131.2 | 13237.8 | 11446.5 | 12804.8 | 11144.8 | 10767 | 11827.6 | 11362.4 | 12271.2 | 11059.2 | 12269 | 11260 | 11139 | 12111 | 10972.7 | 12335.4 | 12296.3 | 10963.4 | 12400.4 | 11311.5 | 11788 | 11145.9 | 11794.1 | 12046.1 | 12403.1 | 11292 | 8734.4 | 10825.1 | 10740.5 | 6670.1 | 11127.6 | 12194.5 | 9085.3 | 12318.3 | 11042.3 | 12048.1 | 11085.5 | 11844.9 | 10878.5 | 12298.3 | 10836 | 11503.4 | 11177.9 | 9024.4 | 11978.3 | 11661.9 | 10604.3 | 12270 | 11926.4 | 11117.9 | 10891.6 | 12124.5 | 10842.5 | 11396.4 | 12310.3 | 10959.9 | 12217.2 | 11069.9 | 12190.6 | 11436.2 | 12337.8 | 10837 | 12497.8 | 11472.6 | 12431.1 | 11437.9 | 12183.1 | 11568.9 | 11156.5 | 12180.6 | 11237.5 | 11141.9 | 12391.8 | 12104.7 | 12322.4 | 11321.3 | 12302.2 | 11031.6 | 12066.4 | 11477.9 | 11923.6 | 10306 | 12128.2 | 11138.6 | 10958.3 | 10917.6 | 10780.9 | 9439.6 | 11019.3 | 9551.2 | 10792 | 10812.8 | 12615.9 | 11143.6 | 12628.9 | 11525.3 | 12445.4 | 11127.1 | 11307.3 | 11035.3 | 12282 | 12606.8 | 12568 | 12524.4 | 12437.7 | 12546.6 | 11588.6 | 12536.9 | 12042.3 | 12315.5 | 12449 | 12085.8 | 12587.6 | 10520.6 | 12005.4 | 11522.2 | 31.2013 | 32.5461 | 32.5846 | 0 | 33.1032 | 32.805 | 0 | 46.6005 | 0 | 0 | 0 | 0 | 3.662 | 3.7222 | 3.631 | 0 | 3.7506 | 3.7574 | 6.7467 | 7.0333 | 7.0217 | 0 | 6.5217 | 6.93 | 7.5135 | 6.932 | 6.233 | 0 | 6.2059 | 6.304 | 1.3991 | 1.3991 | 1.3703 | 0 | 1.4405 | 1.2162 | 6.91 | 6.5969 | 6.9069 | 0 | 6.985 | 6.661 | 1.9741 | 1.3755 | 1.344 | 0 | 1.4507 | 1.5147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127516 | 221 | 119116 | 219 | 245592 | 664 | 7.5135 | 6.932 | 6.233 | 0 | 6.2059 | 6.304 | 6.91 | 6.5969 | 6.9069 | 0 | 6.985 | 6.661 | 929000 | 1000 | 923000 | 1000 | 1843000 | 5000 | 1850000 | 1838000 | 12.0167 | 6.6377 | 1.365 | 6.812 | 1.5318 | 20.56% | 22.49% | 32.4481 | 46.6005 | 3.7046 | 6.8507 | 1859641 | 1843667 | 2244948.3091 | 82.13%
2022-10-01 | 2023 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 334195.71 | 6:33 | 18:33 | 11553.3 | 12377.5 | 12376.9 | 12382 | 12291.9 | 12449.5 | 12312 | 12529.8 | 12396.6 | 12300.2 | 12307.7 | 12421.6 | 12490.8 | 12385.9 | 12322.2 | 12540.4 | 12299 | 12464.6 | 12478.3 | 12466.7 | 12460.7 | 12462.1 | 12304.7 | 12407.1 | 12408 | 11001.9 | 12470 | 12461.1 | 12538.9 | 12323.5 | 12339.5 | 12535.4 | 12316.3 | 12517.3 | 12482.9 | 12476.8 | 12511.4 | 12415.6 | 12443.6 | 12417.6 | 12816.6 | 11978.2 | 12645 | 11841.3 | 12159.2 | 13166.6 | 11650.3 | 12836.2 | 11884.5 | 11524.9 | 12493.4 | 12027.2 | 12896.3 | 11791.7 | 12841 | 11917.8 | 11830.9 | 12699.9 | 11741.8 | 12951.1 | 12906.4 | 11684.2 | 12984.4 | 11961 | 12344.6 | 11733.6 | 12364.9 | 12544.6 | 12952.3 | 11876.8 | 12803.4 | 11526.6 | 11466.6 | 11718.7 | 11817.7 | 12802.2 | 11575.1 | 12890.6 | 11729.7 | 12627 | 11671.3 | 12378.1 | 11445.4 | 12724.4 | 11391.2 | 11993.7 | 11697.7 | 9503 | 12342.7 | 12132.5 | 11213.8 | 12686.7 | 12404.4 | 11668.5 | 11424.3 | 12497.9 | 11296.9 | 11781.9 | 12561.3 | 11364.9 | 12471.9 | 11461.7 | 12496.3 | 11811.3 | 12611 | 11288.6 | 12748 | 11861.6 | 12687.4 | 11854.3 | 12529.8 | 12003.4 | 11552.4 | 12421.1 | 11682.9 | 11558.9 | 12610.5 | 12357.8 | 12549.8 | 11720.3 | 12571.6 | 11491.5 | 12347.4 | 11851.9 | 12243 | 10752.1 | 12475 | 11602.7 | 11436.3 | 11369.3 | 11316.5 | 9832.2 | 11371.6 | 9892.7 | 11233.3 | 11235.8 | 12926.9 | 11587 | 12961.2 | 11951.4 | 12732.5 | 11564.2 | 11694.2 | 11442.3 | 12698.6 | 12983.1 | 12963.7 | 12905 | 12801.4 | 12880.3 | 12032.8 | 12898.4 | 12605.8 | 12797.9 | 12919.2 | 12559.4 | 13004.3 | 11100.1 | 12495.8 | 12044.6 | 31.5473 | 32.937 | 32.8247 | 0 | 32.8521 | 33.2076 | 0 | 46.2393 | 0 | 0 | 0 | 0 | 4.8408 | 5.0116 | 4.9392 | 0 | 4.979 | 4.9715 | 8 | 8.244 | 8.301 | 0 | 8.647 | 8.576 | 6.3945 | 7.2113 | 6.2967 | 0 | 6.3934 | 6.5518 | 1.3989 | 1.3989 | 1.4405 | 0 | 1.4359 | 1.2123 | 7.2181 | 6.8801 | 7.0967 | 0 | 7.1409 | 6.9449 | 1.4562 | 1.379 | 1.4208 | 0 | 1.4403 | 1.5254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128495 | 223 | 120071 | 221 | 225936.084 | 545.067 | 6.3945 | 7.2113 | 6.2967 | 0 | 6.3934 | 6.5518 | 7.2181 | 6.8801 | 7.0967 | 0 | 7.1409 | 6.9449 | 979000 | 2000 | 955000 | 2000 | -19655916 | -118933 | 1930000 | -19536983 | 12 | 6.5695 | 1.3773 | 7.0561 | 1.4443 | 20.96% | 20.47% | 32.6737 | 46.2393 | 4.9484 | 8.3536 | 1944478.2 | 1927533 | 2324894.0543 | 82.91%
2022-10-02 | 2023 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 334195.71 | 6:32 | 18:31 | 11660.5 | 12485.6 | 12489.8 | 12518.6 | 12351.3 | 12511.6 | 12425.1 | 12620.7 | 12491.6 | 12470.9 | 12379.6 | 12487.4 | 12569.7 | 12451.6 | 12281.8 | 12597.9 | 12239 | 12432.7 | 12509.5 | 12514.6 | 12486 | 12494.9 | 12268.4 | 12417.5 | 12438.8 | 11102.4 | 12532.4 | 12496.5 | 12536.1 | 12260.9 | 12267.8 | 12535.9 | 12217.6 | 12445.8 | 12470 | 12438.1 | 12458.3 | 12340.8 | 12324.2 | 12217.7 | 13041.2 | 12135.5 | 12839.6 | 11947 | 12306.7 | 13324.4 | 11805.9 | 13044.3 | 11947.7 | 11624.1 | 12553.2 | 12074.8 | 12956.1 | 11877.9 | 12894.6 | 11979.7 | 11926.7 | 12785.8 | 11827.6 | 13013.1 | 12992.4 | 11775.7 | 13118.3 | 12129.7 | 12483 | 11886.3 | 12526.7 | 12701.6 | 13125 | 12025.4 | 13000.8 | 11685.6 | 11631.3 | 12838.9 | 12006.3 | 12994.5 | 11761.4 | 13073.9 | 11876.6 | 12774.5 | 11871.9 | 12568.6 | 11627.6 | 12881.6 | 11575.6 | 12123 | 11823.3 | 9666.4 | 12371.4 | 12240.9 | 11330 | 12670.1 | 12339.2 | 11574.4 | 11333.1 | 12405.5 | 11186.9 | 11607.9 | 12318.8 | 11194.7 | 12117 | 11180.3 | 12088 | 11503.6 | 12170.3 | 10979.1 | 12315.3 | 11480.8 | 12278.6 | 11485.9 | 12144.6 | 11662.1 | 11379.3 | 12127.7 | 11372 | 11279.7 | 12198.5 | 12023.1 | 12172.1 | 11418.9 | 12220 | 11232.4 | 11942.5 | 11510.2 | 11879 | 10541.6 | 12145.1 | 11330.7 | 11351.8 | 11391.4 | 11206.5 | 9844.4 | 11199.6 | 9850.1 | 11402 | 11414.4 | 13106.1 | 11764.9 | 13061.5 | 12084.2 | 12877.1 | 11690 | 11821.5 | 11595.7 | 12832.3 | 13112 | 13110.7 | 13068.1 | 12949 | 13024.4 | 12138.7 | 13048 | 12708.4 | 12902.6 | 13024.6 | 12683 | 13117.8 | 11258.6 | 12607.8 | 12162.3 | 28.9987 | 31.0499 | 31.1098 | 0 | 30.8084 | 31.3724 | 0 | 45.0281 | 0 | 0 | 0 | 0 | 4.8636 | 5.2379 | 4.9472 | 0 | 5.218 | 5.167 | 8.211 | 8.617 | 8.881 | 0 | 8.469 | 8.058 | 6.4277 | 7.2134 | 6.4063 | 0 | 6.2145 | 6.6352 | 1.378 | 1.3998 | 1.4555 | 0 | 1.378 | 1.2205 | 7.2793 | 6.8883 | 7.2357 | 0 | 6.9229 | 7.0371 | 1.4704 | 1.3765 | 1.4358 | 0 | 1.3785 | 1.5355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129482 | 224 | 121020 | 223 | 227865.018 | 549.467 | 6.4277 | 7.2134 | 6.4063 | 0 | 6.2145 | 6.6352 | 7.2793 | 6.8883 | 7.2357 | 0 | 6.9229 | 7.0371 | 987000 | 1000 | 949000 | 2000 | 1928934 | 4400 | 1933000 | 1924534 | 11.9833 | 6.5794 | 1.3664 | 7.0726 | 1.4393 | 20.77% | 20.35% | 30.6678 | 45.0281 | 5.0867 | 8.4472 | 1945852.2 | 1928867 | 2349952.199 | 82.08%
2022-10-03 | 2023 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 334195.71 | 6:32 | 18:31 | 11143.7 | 11987.6 | 11942.9 | 12017.3 | 11693.7 | 11875.6 | 11782.6 | 12022 | 12059.9 | 12090.9 | 11865.2 | 12089.5 | 11912.7 | 11975.7 | 11632.1 | 11857.8 | 11645.4 | 11800.3 | 11873 | 11823.7 | 11750.9 | 11796.9 | 11655.2 | 11712.2 | 11714.4 | 10340 | 11869.6 | 11814.8 | 11854.5 | 11715.4 | 11692 | 11874.3 | 11663.7 | 11907 | 11780.8 | 11795.1 | 11856.1 | 11752 | 11782.7 | 11757.2 | 12273.5 | 11482.9 | 12095.1 | 11296.6 | 11527.8 | 12489.3 | 10964.2 | 12211.7 | 11439.6 | 11073 | 12022 | 11568.9 | 12297.2 | 11104.8 | 12486.3 | 11316.3 | 11428.6 | 12408.2 | 11294 | 12649.1 | 12632.7 | 11280.4 | 12739.1 | 11646.4 | 12114 | 11488.6 | 12170.6 | 12474.3 | 12839.1 | 11754.1 | 12757.9 | 11383.7 | 11162.1 | 12649.8 | 11586.6 | 12855.9 | 11442.1 | 12802.1 | 11568.2 | 12667.9 | 11677.5 | 12516.7 | 11408.1 | 12775.4 | 11497.7 | 12009.5 | 11532.2 | 9508 | 12226.6 | 12020 | 10889.1 | 12380.6 | 11910.1 | 11018.5 | 10734 | 12060.6 | 10789.2 | 11400.8 | 12240.9 | 11003 | 11846.8 | 10959.5 | 11825.9 | 11279 | 11979.7 | 10608.9 | 12120.6 | 11185.7 | 12049.1 | 11187.8 | 11881.1 | 11362 | 11191 | 12171 | 11232.6 | 11101.5 | 12155.8 | 12049.7 | 12049.2 | 11307.2 | 12195.4 | 11011.4 | 11778.6 | 11216.7 | 11652.5 | 10202.7 | 12047 | 11083.9 | 11280.6 | 11411.7 | 11013.8 | 9736.1 | 11430.8 | 9950.4 | 11034.5 | 11056.9 | 12880.7 | 11353.7 | 12913.1 | 11771.4 | 12715.1 | 11389 | 11574 | 11253 | 12657.8 | 12916 | 12820.1 | 12767.4 | 12707.1 | 12813.9 | 11888.2 | 12829.6 | 12631.5 | 12850.1 | 12996.3 | 12644 | 13097.2 | 10977.9 | 12426.5 | 11939.2 | 30.3631 | 31.1849 | 31.14 | 0 | 31.3848 | 31.4922 | 0 | 45.9212 | 0 | 0 | 0 | 0 | 3.3473 | 3.2879 | 3.3574 | 0 | 3.2501 | 3.2671 | 6.121 | 6.157 | 6.623 | 0 | 5.862 | 6.251 | 6.0538 | 6.7753 | 5.9243 | 0 | 6.1835 | 6.4047 | 1.3584 | 1.2805 | 1.3584 | 0 | 1.3785 | 1.1646 | 6.8951 | 6.4565 | 6.7253 | 0 | 6.9433 | 6.7688 | 1.3645 | 1.2641 | 1.346 | 0 | 1.39 | 1.468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130427 | 226 | 121953 | 224 | 229735.418 | 553.933 | 6.0538 | 6.7753 | 5.9243 | 0 | 6.1835 | 6.4047 | 6.8951 | 6.4565 | 6.7253 | 0 | 6.9433 | 6.7688 | 945000 | 2000 | 933000 | 1000 | 1870400 | 4466 | 1875000 | 1865934 | 11.9833 | 6.2683 | 1.3081 | 6.7578 | 1.3665 | 20.87% | 20.22% | 31.113 | 45.9212 | 3.302 | 6.2028 | 1886679.5 | 1870134 | 2232246.1412 | 83.78%
2022-10-04 | 2023 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 334195.71 | 6:36 | 18:30 | 10939.6 | 11674.3 | 11749.8 | 11758.3 | 11644.5 | 11834.7 | 11595.3 | 11818.4 | 11754.3 | 11758.1 | 11610.8 | 11737.4 | 11845.8 | 11715.2 | 11745.4 | 11958.3 | 11706.9 | 11959.6 | 11979.1 | 11914.8 | 12129.3 | 12056.3 | 12135.1 | 12146.2 | 12248.3 | 10623.3 | 11999.5 | 12118.3 | 12394.6 | 12343.8 | 12416.3 | 12538.5 | 12351.7 | 12565 | 12391.2 | 12416.6 | 12521.7 | 12490.3 | 12548.9 | 12512.6 | 13281.3 | 12277.5 | 13015.6 | 12038.8 | 12417 | 13586.7 | 11874.8 | 13187.5 | 11228.7 | 10904.9 | 11864.3 | 11520.9 | 12330.5 | 11142 | 12452.4 | 11484.1 | 11293.2 | 12234.2 | 11035.4 | 12383.5 | 12304.4 | 11012.7 | 12338.4 | 11238.1 | 11850.1 | 11285.3 | 11824.7 | 12217.1 | 12404.7 | 11360 | 12196.3 | 10882.1 | 10779 | 11980.2 | 11126.7 | 12112.4 | 10787.1 | 12180.4 | 10960.5 | 11931.8 | 11436.4 | 12065.6 | 11337.8 | 12553 | 11443.7 | 11987.9 | 11436.8 | 9526.3 | 12382.3 | 12115.3 | 11252.6 | 12815.2 | 12511.6 | 11625.2 | 11336.4 | 12552.8 | 11161.2 | 11721.5 | 12572.8 | 11284.9 | 12423.2 | 11359.9 | 12424.1 | 11708.1 | 12544.7 | 11083.2 | 12677.7 | 11754.9 | 12595.5 | 11675.9 | 12359.7 | 11837.6 | 11480.4 | 12427 | 11565.4 | 11420.7 | 12577 | 12326.4 | 12495.7 | 11595.4 | 12510.9 | 11300.9 | 12239.7 | 11650.2 | 12073.4 | 10513.8 | 12347.9 | 11310 | 11456.6 | 11572.9 | 11159.4 | 9816.4 | 11655.6 | 10201 | 11108.5 | 11184.7 | 12968.2 | 11480.4 | 12993 | 11903 | 12741.1 | 11397.7 | 11547.3 | 11220.1 | 12721.6 | 13010.4 | 13066.3 | 12984.4 | 12876.5 | 12925.8 | 11981.4 | 12922.4 | 12756 | 12955.6 | 13020 | 12640.2 | 13120.9 | 11013.5 | 12616.5 | 12076.5 | 31.8862 | 32.2936 | 32.2695 | 0 | 32.7048 | 32.663 | 0 | 48.2526 | 0 | 0 | 0 | 0 | 2.3926 | 2.2841 | 2.3477 | 0 | 2.3511 | 2.1861 | 5.255 | 5.435 | 5.164 | 0 | 4.886 | 4.824 | 5.9646 | 6.7736 | 6.4007 | 0 | 6.3107 | 6.5327 | 1.3584 | 1.3553 | 1.4521 | 0 | 1.4072 | 1.183 | 6.7849 | 6.9755 | 7.2757 | 0 | 7.1058 | 6.8961 | 1.3653 | 1.3365 | 1.4367 | 0 | 1.4198 | 1.4878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131376 | 227 | 122905 | 226 | 231629.485 | 558.4 | 5.9646 | 6.7736 | 6.4007 | 0 | 6.3107 | 6.5327 | 6.7849 | 6.9755 | 7.2757 | 0 | 7.1058 | 6.8961 | 949000 | 1000 | 952000 | 2000 | 1894067 | 4467 | 1898000 | 1889600 | 11.9 | 6.3964 | 1.3512 | 7.0076 | 1.4092 | 21.12% | 20.11% | 32.3634 | 48.2526 | 2.3123 | 5.1128 | 1910465.9 | 1893933 | 2284002.8237 | 82.92%
2022-10-05 | 2023 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 334195.71 | 6:32 | 18:28 | 11616.6 | 12349.9 | 12331.7 | 12361.3 | 12216.6 | 12394 | 12254.9 | 12460.3 | 12387.3 | 12298.4 | 12281.4 | 12394.8 | 12468.4 | 12364.4 | 12304.7 | 12538.4 | 12282.8 | 12445.7 | 12463.2 | 12442.7 | 12444.1 | 12447 | 12297.8 | 12394.6 | 12383.8 | 11025.5 | 12476.2 | 12450.1 | 12515.2 | 12301.5 | 12339.2 | 12519 | 12296.1 | 12511 | 12451.5 | 12447.9 | 12506.2 | 12410.7 | 12444.3 | 12409 | 13071.7 | 12258.3 | 12885.3 | 12066.2 | 12352.1 | 13352.4 | 11815.3 | 12984.2 | 11909.1 | 11651.6 | 12494.1 | 12057.8 | 12925.1 | 11786.4 | 12865.4 | 11938.1 | 11876.5 | 12725.2 | 11779.3 | 12966.9 | 12927.6 | 11730.6 | 12982.2 | 11978.2 | 12384.9 | 11807 | 12428.9 | 12644.9 | 12996 | 11989.8 | 12855.6 | 11647.4 | 11536.9 | 12703.9 | 11884.6 | 12855.4 | 11657.1 | 12929.7 | 11794.2 | 12671.8 | 11891.9 | 12577.3 | 11569.8 | 12823.5 | 11704.8 | 12118.5 | 11762.8 | 9762.9 | 12367.9 | 12198.2 | 11422.5 | 12760.3 | 12469.5 | 11706.8 | 11439.1 | 12528.4 | 11327 | 11853.4 | 12607 | 11485.9 | 12454 | 11552.9 | 12495.4 | 11865.1 | 12600.6 | 11305.1 | 12744.6 | 11895.8 | 12672.3 | 11850.9 | 12462.4 | 12046.9 | 11627.7 | 12436.6 | 11729.2 | 11587.8 | 12592.4 | 12373.5 | 12543.4 | 11764.4 | 12587.6 | 11535.5 | 12342 | 11869.4 | 12203.2 | 10782.8 | 12469.4 | 11624.3 | 11686.2 | 11753.5 | 11454.9 | 10068.5 | 11811.1 | 10422.2 | 11554.6 | 11523.4 | 12998.8 | 11654.2 | 13003.4 | 12002.6 | 12749.8 | 11613.2 | 11750 | 11531 | 12728.5 | 13012.6 | 13005.8 | 12945.3 | 12865.7 | 12946.4 | 12113.6 | 12955.5 | 12583.4 | 12775.9 | 12896.1 | 12553.8 | 13016.2 | 11156.6 | 12506.9 | 12060.3 | 32.2483 | 32.939 | 32.8053 | 0 | 33.164 | 33.0622 | 0 | 46.4043 | 0 | 0 | 0 | 0 | 3.1464 | 3.0711 | 3.135 | 0 | 3.0895 | 3.0372 | 6.015 | 5.586 | 6.355 | 0 | 6.175 | 5.337 | 6.3046 | 6.878 | 6.3373 | 0 | 6.2937 | 6.5527 | 1.3998 | 1.4016 | 1.4483 | 0 | 1.4349 | 1.2132 | 7.2203 | 7.0946 | 7.216 | 0 | 7.1287 | 6.8737 | 1.4396 | 1.3804 | 1.4287 | 0 | 1.4446 | 1.5236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132360 | 229 | 123866 | 228 | 233567.085 | 562.733 | 6.3046 | 6.878 | 6.3373 | 0 | 6.2937 | 6.5527 | 7.2203 | 7.0946 | 7.216 | 0 | 7.1287 | 6.8737 | 984000 | 2000 | 961000 | 2000 | 1937600 | 4333 | 1941000 | 1933267 | 11.9333 | 6.4733 | 1.3796 | 7.1067 | 1.4434 | 21.31% | 20.31% | 32.8437 | 46.4043 | 3.0958 | 5.8936 | 1953988.6 | 1937467 | 2320271.2641 | 83.5%
2022-10-06 | 2023 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 334195.71 | 6:35 | 18:28 | 11424.5 | 12182.6 | 12173.7 | 12212.4 | 12055.6 | 12230.4 | 12058.8 | 12246.8 | 12223 | 12077 | 12106.5 | 12228 | 12269.8 | 12171.7 | 12085.5 | 12333.7 | 12062.7 | 12225.4 | 12242.3 | 12222.3 | 12216.7 | 12225.1 | 12054.3 | 12158.7 | 12152.8 | 10799.9 | 12259.4 | 12216.7 | 12266.3 | 12046.9 | 12066.9 | 12265.6 | 12029.9 | 12267 | 12247.5 | 12216.3 | 12272.3 | 12139.1 | 12164.7 | 12137.5 | 12775.1 | 11953 | 12593.2 | 11752.5 | 12030.7 | 13002.6 | 11507 | 12693.1 | 11701.1 | 11426.6 | 12290.5 | 11847.5 | 12711.6 | 11559.8 | 12690.8 | 11712.6 | 11669.5 | 12503.5 | 11573.4 | 12760.1 | 12713.4 | 11536.6 | 12721.5 | 11725.1 | 12140.1 | 11525.2 | 12175.3 | 12330.9 | 12758.6 | 11706.3 | 12577 | 11346.8 | 11279.3 | 12401.8 | 11624.5 | 12549 | 11369.1 | 12646.7 | 11522 | 12368.1 | 11542.9 | 12232.9 | 11187.1 | 12442.1 | 11330.2 | 11730 | 11442.3 | 9446.3 | 12031.9 | 11852.8 | 11109.8 | 12442.6 | 12172.4 | 11235 | 11133.9 | 12209.6 | 10990.3 | 11528.1 | 12267.7 | 11195.3 | 12149.3 | 11245.9 | 12194 | 11553.7 | 12311.4 | 11019.6 | 12463.3 | 11636.7 | 12398.2 | 11592.1 | 12201.8 | 11785.7 | 11343.4 | 12163.9 | 11450.2 | 11324.2 | 12327.8 | 12133.8 | 12287.1 | 11560.3 | 12359.5 | 11323.5 | 12099.1 | 11646.6 | 11979.7 | 10547.5 | 12255.8 | 11371.1 | 11485.4 | 11548.8 | 11188.5 | 9844.6 | 11555.5 | 10202.1 | 11237.6 | 11171.4 | 12524.9 | 11287.8 | 12546.5 | 11607.7 | 12348.8 | 11233.2 | 11370.5 | 11171.3 | 12208.9 | 12480.7 | 12443.4 | 12422.9 | 12366 | 12477.3 | 11682.6 | 12465.3 | 11936.3 | 12145.9 | 12285.8 | 11978.1 | 12431 | 10680 | 11921.1 | 11526.9 | 33.0319 | 33.3939 | 33.2715 | 0 | 33.4125 | 33.4284 | 0 | 47.621 | 0 | 0 | 0 | 0 | 2.5605 | 2.4959 | 2.4282 | 0 | 2.4785 | 2.4225 | 4.778 | 5.052 | 5.185 | 0 | 6.538 | 4.688 | 6.2074 | 6.7231 | 6.1919 | 0 | 6.1626 | 6.2796 | 1.2805 | 1.3581 | 1.4422 | 0 | 1.3767 | 1.1363 | 7.1289 | 6.9465 | 7.0937 | 0 | 6.9778 | 6.5953 | 1.4541 | 1.3374 | 1.4241 | 0 | 1.3941 | 1.4273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133324 | 230 | 124799 | 229 | 235457.752 | 566.867 | 6.2074 | 6.7231 | 6.1919 | 0 | 6.1626 | 6.2796 | 7.1289 | 6.9465 | 7.0937 | 0 | 6.9778 | 6.5953 | 964000 | 1000 | 933000 | 1000 | 1890667 | 4134 | 1895000 | 1886533 | 11.8833 | 6.3129 | 1.3188 | 6.9484 | 1.4074 | 20.89% | 20.25% | 33.3076 | 47.621 | 2.4771 | 5.2482 | 1906833 | 1890600 | 2257932.9024 | 83.73%
2022-10-07 | 2023 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 334195.71 | 6:43 | 18:22 | 10133.8 | 10855.1 | 10906.9 | 10942.7 | 10833.3 | 11028.5 | 10807.4 | 11043.3 | 10895.6 | 10773.6 | 10841.4 | 10898.4 | 11113 | 10969.9 | 10963.3 | 11173.4 | 10943.3 | 11108.7 | 11123.6 | 11092.8 | 11130.7 | 11126.3 | 11018.2 | 11088.8 | 11042.1 | 9839 | 11115.4 | 11078.7 | 11185.2 | 11036.2 | 11068.1 | 11187.9 | 10947 | 11141.2 | 11146.3 | 11105.5 | 11173.1 | 11093.4 | 11136.7 | 11082.5 | 11970.9 | 11211 | 11815.9 | 11017.5 | 11294.5 | 12203.3 | 10788 | 11920.5 | 10524.6 | 10245.6 | 11107.9 | 10657.9 | 11495.2 | 10445.5 | 11434.7 | 10560.5 | 10365.8 | 11161.9 | 10290.8 | 11361.8 | 11296.9 | 10219.9 | 11312.9 | 10362.1 | 10826.2 | 10239.2 | 10815.7 | 11017.2 | 11355.9 | 10378.9 | 11182.9 | 10048.4 | 9981.4 | 11047.1 | 10290.8 | 11223.5 | 10105 | 11285.7 | 10220.5 | 11067.8 | 10278.8 | 10920.2 | 9961.4 | 11145.5 | 10099 | 10502.3 | 10242.2 | 8500.3 | 10796.6 | 10658.3 | 9958.6 | 11210.6 | 10976.9 | 10146.6 | 10039.2 | 11001.8 | 9798.6 | 10261.7 | 11023 | 9949.2 | 10989.1 | 10048 | 11017.2 | 10328 | 11130.9 | 9895.5 | 11257.9 | 10406.3 | 11208.5 | 10415.3 | 11033.1 | 10575.6 | 10058.8 | 10836.9 | 10181.7 | 10035.6 | 11036.2 | 10825.3 | 10991.1 | 10259.1 | 11037.8 | 10045.4 | 10819.2 | 10374.9 | 10720 | 9447 | 10920 | 10115 | 10175.1 | 10205.5 | 9996.4 | 8723.4 | 10241.5 | 9099.2 | 10154.4 | 10111.5 | 11412.2 | 10192.1 | 11452.4 | 10517 | 11222.9 | 10171.4 | 10302.1 | 10130.9 | 11198.2 | 11457.4 | 11411.5 | 11367 | 11254.3 | 11372.5 | 10610.7 | 11384.3 | 11066.2 | 11246.7 | 11364.4 | 11042.2 | 11467.3 | 9777 | 10960.8 | 10577.2 | 33.9029 | 33.3331 | 33.3226 | 0 | 33.2373 | 33.346 | 0 | 45.4015 | 0 | 0 | 0 | 0 | 4.1701 | 4.0369 | 4.017 | 0 | 4.0131 | 3.8711 | 7.699 | 8.179 | 8.013 | 0 | 8.902 | 8.05 | 5.6601 | 6.306 | 5.8494 | 0 | 5.4993 | 5.6183 | 1.184 | 1.227 | 1.4191 | 0 | 1.184 | 1.0244 | 6.3197 | 5.7285 | 6.6461 | 0 | 6.0445 | 6.0263 | 1.3878 | 1.2035 | 1.4097 | 0 | 1.2036 | 1.2903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134195 | 231 | 125640 | 231 | 237163.952 | 571.4 | 5.6601 | 6.306 | 5.8494 | 0 | 5.4993 | 5.6183 | 6.3197 | 5.7285 | 6.6461 | 0 | 6.0445 | 6.0263 | 871000 | 1000 | 841000 | 2000 | 1706200 | 4533 | 1709000 | 1701667 | 11.65 | 5.7866 | 1.2077 | 6.153 | 1.299 | 20.87% | 21.11% | 33.4284 | 45.4015 | 4.0217 | 8.1686 | 1720488 | 1706200 | 2018799.6371 | 84.52%
2022-10-08 | 2023 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 334195.71 | 6:40 | 18:24 | 8804.6 | 9537 | 9533.4 | 9583.5 | 9393.3 | 9571.7 | 9409.3 | 9591.2 | 9595.6 | 9282.2 | 9483.5 | 9603.1 | 9592.6 | 9540.7 | 9410.1 | 9650 | 9454.3 | 9640.6 | 9629.6 | 9585.8 | 9662.3 | 9648.6 | 9523.7 | 9607.6 | 9560 | 8331.4 | 9568.6 | 9620.7 | 9750.8 | 9581.9 | 9657.2 | 9772.3 | 9441.3 | 9641.5 | 9597.5 | 9605.6 | 9734.7 | 9673.9 | 9774.9 | 9682.8 | 10720.3 | 9859.9 | 10583.1 | 9673.3 | 9967 | 10859.2 | 9435.4 | 10632.4 | 9026.6 | 8814.6 | 9605.1 | 9147.3 | 9996.6 | 8896.5 | 10033.1 | 9008.8 | 9049.5 | 9853.7 | 8979.1 | 10086 | 10025.2 | 8945.2 | 9910.5 | 8871.6 | 9454.8 | 8815.5 | 9406.2 | 9527.2 | 9999.4 | 8790.1 | 9650.7 | 8450.9 | 8561.9 | 9426.9 | 8776.5 | 9589.2 | 8471.1 | 9741.1 | 8581.5 | 9396.6 | 8645.3 | 9304.3 | 8303.1 | 9571 | 8491.1 | 8883.9 | 8821.3 | 7197.4 | 9339.2 | 9247 | 8532.1 | 9805.2 | 9516.4 | 8618.9 | 8543 | 9573.6 | 8368.6 | 8835.7 | 9629.3 | 8543.2 | 9666.4 | 8599.7 | 9680.4 | 8882.2 | 9958.7 | 8567 | 10094.3 | 9116.8 | 10085.3 | 9248.5 | 9937.2 | 9406.5 | 8698 | 9482.5 | 8768.9 | 8628.2 | 9697.4 | 9446.2 | 9666.7 | 8811.4 | 9671 | 8681 | 9581.3 | 9154.3 | 9533.9 | 8254 | 9614.7 | 8825 | 8727.9 | 8740.7 | 8757.9 | 7494.2 | 8740.3 | 7617.2 | 8599.4 | 8595.5 | 9905.1 | 8729.9 | 9897.4 | 8987 | 9766.1 | 8701.4 | 8809.3 | 8621.7 | 9568 | 9832.4 | 9821.9 | 9788.5 | 9698.2 | 9848.5 | 9039.1 | 9808.6 | 9543.5 | 9761.6 | 9962 | 9590.9 | 9945 | 8243.6 | 9339.4 | 8930 | 31.0331 | 30.7206 | 30.6932 | 0 | 30.7237 | 30.7859 | 0 | 40.3878 | 0 | 0 | 0 | 0 | 4.6762 | 4.5318 | 4.4859 | 0 | 4.364 | 4.3939 | 8.769 | 8.665 | 8.992 | 0 | 7.979 | 9.352 | 4.7596 | 5.3849 | 5.0493 | 0 | 4.6266 | 4.773 | 1.0626 | 1.0969 | 1.1139 | 0 | 1.0626 | 0.91318 | 5.4032 | 4.8389 | 5.6379 | 0 | 5.2098 | 5.0503 | 1.0623 | 1.0752 | 1.1005 | 0 | 1.0841 | 1.1372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134952 | 233 | 126368 | 233 | 238643.019 | 575.933 | 4.7596 | 5.3849 | 5.0493 | 0 | 4.6266 | 4.773 | 5.4032 | 4.8389 | 5.6379 | 0 | 5.2098 | 5.0503 | 757000 | 2000 | 728000 | 2000 | 1479067 | 4533 | 1481000 | 1474534 | 11.7333 | 4.9187 | 1.0499 | 5.228 | 1.0918 | 21.34% | 20.88% | 30.7913 | 40.3878 | 4.4904 | 8.7514 | 1490888.3 | 1479000 | 1758765.1778 | 84.09%
2022-10-09 | 2023 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 334195.71 | 6:35 | 18:24 | 11317.9 | 11914.3 | 11885.8 | 12036.3 | 11668.9 | 11805.8 | 11635.8 | 11759 | 12073.9 | 12110 | 11663.4 | 11957.3 | 11728 | 11710.8 | 11560.6 | 11757.2 | 11593.6 | 11782.5 | 11748.5 | 11731.4 | 11811.3 | 11766.3 | 11776.8 | 11816.1 | 11691.9 | 10387.1 | 11741.4 | 11736.8 | 11918.2 | 11835.1 | 11904.5 | 11969.9 | 11726.3 | 11925 | 11795 | 11826.4 | 11976.3 | 11940.6 | 12016.8 | 11950.5 | 12681.7 | 11786 | 12478 | 11553 | 11888.9 | 12856.7 | 11315 | 12592.8 | 11236.5 | 10952.2 | 11790 | 11297.3 | 12181.4 | 10988.1 | 12153.4 | 11178.3 | 11238.6 | 12086.8 | 11269.1 | 12325.7 | 12413 | 11239.1 | 12465.5 | 11566.5 | 11834.8 | 11269.1 | 11908.3 | 12162 | 12519.5 | 11518.5 | 12431.3 | 11215.7 | 11078.6 | 12351.8 | 11512.9 | 12528.8 | 11290.8 | 12630 | 11480.5 | 12422.9 | 11442.4 | 12204.9 | 11078 | 12372.2 | 11167 | 11604.1 | 11154.8 | 9241.5 | 11633 | 11540.7 | 10699 | 12042.8 | 11812.8 | 10898.6 | 10779.4 | 11880.4 | 10573.4 | 11128.6 | 11881.2 | 10771.2 | 11875.9 | 10828.2 | 11870.8 | 11131.3 | 12080.7 | 10689.4 | 12191.3 | 11238.5 | 12079.9 | 11212 | 11839.2 | 11392.1 | 10964.1 | 11759.8 | 10999 | 10846.7 | 11981.6 | 11754 | 11952.6 | 11126.9 | 11994 | 10884 | 11686 | 11202.4 | 11577.2 | 10228.4 | 11847 | 11031.8 | 11030.4 | 11022.1 | 10895.8 | 9452.3 | 11070.9 | 9745.3 | 10878.8 | 10824.4 | 12248 | 10956.8 | 12263 | 11283.9 | 12085.8 | 10890.6 | 11033.7 | 10827.1 | 12273.9 | 12507 | 12475.5 | 12371 | 12201.2 | 12271.8 | 11413.2 | 12350.1 | 12273.5 | 12492.4 | 12611.8 | 12259.2 | 12654.3 | 10752.4 | 12111.2 | 11643.3 | 30.1017 | 29.765 | 29.7778 | 0 | 29.7912 | 29.8068 | 0 | 42.6016 | 0 | 0 | 0 | 0 | 3.7978 | 3.6161 | 3.6874 | 0 | 3.6327 | 3.617 | 7.047 | 7.142 | 6.801 | 0 | 6.506 | 7.178 | 5.8317 | 6.6698 | 5.9934 | 0 | 5.805 | 6.1577 | 1.2403 | 1.28 | 1.3868 | 0 | 1.2739 | 1.0954 | 6.7303 | 5.9091 | 6.9349 | 0 | 6.5774 | 6.4327 | 1.3637 | 1.2526 | 1.36 | 0 | 1.2847 | 1.3802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135892 | 234 | 127281 | 234 | 240489.019 | 580.6 | 5.8317 | 6.6698 | 5.9934 | 0 | 5.805 | 6.1577 | 6.7303 | 5.9091 | 6.9349 | 0 | 6.5774 | 6.4327 | 940000 | 1000 | 913000 | 1000 | 1846000 | 4667 | 1851000 | 1841333 | 11.8167 | 6.0915 | 1.2553 | 6.5169 | 1.3282 | 20.61% | 20.38% | 29.8485 | 42.6016 | 3.6702 | 6.9348 | 1861983.9 | 1845933 | 2171344.8014 | 85.01%
2022-10-10 | 2023 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 334195.71 | 6:35 | 18:23 | 10792.8 | 11618.5 | 11673.5 | 11723 | 11507.7 | 11730.8 | 11473.2 | 11695.7 | 11728.1 | 11566.9 | 11565.9 | 11724.5 | 11762.4 | 11654.1 | 11614.1 | 11888.1 | 11670.6 | 11863.4 | 11894 | 11855.7 | 11841 | 11857.4 | 11653.3 | 11795.5 | 11786.1 | 10361.9 | 11883.7 | 11853.2 | 11831.3 | 11604.6 | 11568 | 11882.7 | 11410.2 | 11770.5 | 11896.8 | 11784.6 | 11803.7 | 11602.7 | 11566 | 11489.5 | 12163.4 | 11333 | 12062.6 | 11134.2 | 11347.1 | 12377.4 | 10743.2 | 12145.8 | 11108.1 | 10776.3 | 11826.5 | 11302.9 | 12357.6 | 10955.6 | 12341.2 | 11219.4 | 11040.4 | 12050.3 | 11072.7 | 12306.1 | 12267.5 | 10897.9 | 12260.2 | 11133.3 | 11462.5 | 11078.2 | 11725.5 | 11993.2 | 12383 | 11228.9 | 12207.4 | 10802.2 | 10654.9 | 12006.5 | 11066.7 | 12218.5 | 10806.9 | 12328.4 | 10963.3 | 12022.7 | 11081 | 11907.1 | 10663.5 | 12167.1 | 10808.1 | 11310.6 | 10968.6 | 8995 | 11600.1 | 11440.8 | 10554.9 | 12051.1 | 11705.1 | 10596.9 | 10425 | 11761.7 | 10142.1 | 10700.4 | 11528.1 | 10279.8 | 11399.5 | 10291.6 | 11333 | 10590.9 | 11493.7 | 10042.7 | 11690.6 | 10715.1 | 11652.9 | 10721.5 | 11411.4 | 10900.8 | 10486 | 11412.3 | 10541.4 | 10372 | 11523.9 | 11346.4 | 11488.2 | 10659.2 | 11635.9 | 10441.1 | 11286.6 | 10759.8 | 11167.3 | 9735.5 | 11492.4 | 10586.7 | 10599.6 | 10597.8 | 10469.3 | 9077.6 | 10706.9 | 9378.9 | 10596.6 | 10532.1 | 12157.8 | 10669.2 | 12147.2 | 11046.9 | 11951.7 | 10597.8 | 10789.9 | 10543.9 | 11994.2 | 12317.4 | 12322.3 | 12241.2 | 12093.2 | 12181.9 | 11156.8 | 12192.4 | 11854.3 | 12119.3 | 12222.7 | 11811.5 | 12333.6 | 10251.6 | 11745 | 11232 | 31.9134 | 31.4119 | 31.3547 | 0 | 31.5654 | 31.4945 | 0 | 45.7071 | 0 | 0 | 0 | 0 | 2.39 | 2.2836 | 2.3939 | 0 | 2.3506 | 2.2841 | 5.452 | 5.248 | 5.856 | 0 | 5.532 | 5.923 | 5.8008 | 6.611 | 5.6581 | 0 | 5.5684 | 5.9663 | 1.2403 | 1.3056 | 1.3346 | 0 | 1.2403 | 1.0871 | 6.6541 | 5.8548 | 6.5395 | 0 | 6.2944 | 6.2536 | 1.3749 | 1.2737 | 1.3166 | 0 | 1.254 | 1.3695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136818 | 236 | 128166 | 236 | 242292.952 | 585.133 | 5.8008 | 6.611 | 5.6581 | 0 | 5.5684 | 5.9663 | 6.6541 | 5.8548 | 6.5395 | 0 | 6.2944 | 6.2536 | 926000 | 2000 | 885000 | 2000 | 1803933 | 4533 | 1807000 | 1799400 | 11.8 | 5.9209 | 1.2416 | 6.3193 | 1.3178 | 20.97% | 20.85% | 31.548 | 45.7071 | 2.3404 | 5.6022 | 1819215.2 | 1803933 | 2080767.106 | 86.7%
2022-10-11 | 2023 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 334195.71 | 6:36 | 18:22 | 10927.1 | 11736.4 | 11797.2 | 11827.4 | 11621.3 | 11877.4 | 11611.7 | 11830.3 | 11830.8 | 11684.5 | 11717.9 | 11842.6 | 11918 | 11824.7 | 11709.3 | 12027.4 | 11737.8 | 11944.3 | 11989 | 11950.1 | 11961.9 | 11968 | 11800 | 11928 | 11896.5 | 10436.4 | 11968.6 | 11975.8 | 11627.2 | 11800.5 | 11840 | 12028.2 | 11782.9 | 12064.7 | 12024.8 | 11972.2 | 12026.2 | 11924.7 | 11967.2 | 11933.1 | 12412.4 | 11699.9 | 12452.7 | 11451.1 | 11753.4 | 12900.4 | 11148 | 12568.2 | 11266.2 | 10952.5 | 11981.6 | 11441.8 | 12465.8 | 11057 | 12468.5 | 11294.7 | 11230.4 | 12247 | 11260.3 | 12530.2 | 12482.2 | 11065.1 | 12468.9 | 11308.1 | 11549 | 11268.9 | 11913.7 | 12219.5 | 12582.5 | 11424.9 | 12426.1 | 11008.5 | 10848 | 12216.4 | 11260.3 | 12410.2 | 11008.6 | 12519.8 | 11132.8 | 12266.6 | 11292.9 | 12144.6 | 10862.9 | 12416.9 | 11030.8 | 11550.4 | 11165.5 | 9148.4 | 11838.7 | 11655.7 | 10777.9 | 12310.9 | 12007.4 | 10865.3 | 10718.5 | 12071.7 | 10554.3 | 11184.3 | 12116.4 | 10822.4 | 12068 | 10887.7 | 12029.7 | 11211.5 | 12189.9 | 10644.1 | 12319.5 | 11295.4 | 12218.6 | 11243.9 | 11967.7 | 11437.1 | 11012.6 | 11988.4 | 11114 | 10945 | 12154.1 | 11976 | 12114.9 | 11220.5 | 12203 | 10955.1 | 11852.1 | 11305.3 | 11695.6 | 10194.9 | 12026.4 | 11098.4 | 11053.2 | 11049.2 | 10876.3 | 9437.2 | 11090 | 9719.6 | 10799.2 | 10741.5 | 12614.3 | 11023.3 | 12597.3 | 11394.1 | 12264 | 10887.3 | 11052.7 | 10764.8 | 12281.5 | 12633.3 | 12571.1 | 12522.2 | 12438.8 | 12578.2 | 11566.8 | 12548.4 | 12071.5 | 12353.3 | 12479.8 | 12094.3 | 12627.7 | 10501.9 | 11966.9 | 11493.9 | 32.4822 | 32.1872 | 32.2376 | 0 | 32.4602 | 32.31 | 0 | 46.9405 | 0 | 0 | 0 | 0 | 1.8019 | 1.7375 | 1.8261 | 0 | 1.8521 | 1.777 | 4.699 | 5.178 | 5.18 | 0 | 4.81 | 4.902 | 5.8768 | 6.7425 | 5.8803 | 0 | 5.8843 | 6.2064 | 0.0070796 | 1.3466 | 1.3855 | 0 | 1.3546 | 1.1999 | 6.823 | 5.912 | 6.8457 | 0 | 6.7549 | 6.4391 | 1.3984 | 1.3123 | 1.3617 | 0 | 1.3676 | 1.5128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137758 | 237 | 129084 | 238 | 244143.819 | 587.933 | 5.8768 | 6.7425 | 5.8803 | 0 | 5.8843 | 6.2064 | 6.823 | 5.912 | 6.8457 | 0 | 6.7549 | 6.4391 | 940000 | 1000 | 918000 | 2000 | 1850867 | 2800 | 1855000 | 1848067 | 11.7667 | 6.1181 | 1.0588 | 6.5549 | 1.3906 | 17.31% | 21.21% | 32.3354 | 46.9405 | 1.7989 | 4.9538 | 1866293.2 | 1850667 | 2139514.7682 | 86.5%
2022-10-12 | 2023 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 334195.71 | 6:37 | 18:22 | 9736.2 | 10480.5 | 10583.6 | 10654.2 | 10407.4 | 10658.9 | 10390.6 | 10645.3 | 10549.8 | 10430.2 | 10417.9 | 10484.1 | 10766.1 | 10533.8 | 10619.2 | 10944.1 | 10603.1 | 10646 | 10546 | 10539.5 | 10399.3 | 10427.8 | 10083 | 10261.3 | 10083.1 | 8952.9 | 10393 | 10281.4 | 10149.1 | 9996.2 | 10012 | 10107.9 | 9822.5 | 10066.2 | 10183.5 | 10054.3 | 10044.7 | 10008.5 | 10036.9 | 9989.9 | 10088.8 | 9448.6 | 10055.8 | 9249.9 | 9371.8 | 10366.5 | 8938.2 | 10266.9 | 10030.7 | 9786.5 | 10712.6 | 10227.1 | 11060.8 | 9848.8 | 11151.4 | 9940.3 | 10133.3 | 11072.8 | 10025.9 | 11259.3 | 11076.5 | 9685.9 | 11145.1 | 10014.5 | 10359.7 | 9970.2 | 10718.9 | 10787.8 | 11370.3 | 10139.3 | 11148.3 | 9778.4 | 9742.5 | 11143.4 | 10128.5 | 11147.8 | 10012.2 | 11224.8 | 9976.7 | 11148 | 10017.8 | 10843.2 | 9485.4 | 10943.3 | 9672.3 | 10107.8 | 9800.4 | 8017.5 | 10208.1 | 10173.3 | 9137.5 | 10382.5 | 10014.1 | 8998 | 8875.3 | 10090.5 | 8789.3 | 9355.1 | 10144.4 | 9024.4 | 10023.3 | 9076 | 10071.9 | 9423.1 | 10204.9 | 8951.1 | 10324.1 | 9547.6 | 10132 | 9283.4 | 9804.7 | 9529.5 | 9246 | 10138.6 | 9327.4 | 9158.9 | 10274.4 | 10092.5 | 10216.2 | 9444.6 | 10293.1 | 9197.3 | 9941.3 | 9414.3 | 9835.6 | 8747.1 | 10191.2 | 9406.2 | 9204.6 | 9199.6 | 9251.6 | 7912.4 | 9350.7 | 8110.3 | 9261.1 | 9250 | 10925.7 | 9467 | 10960.6 | 9808.6 | 10608.1 | 9467.3 | 9597 | 9379.4 | 10941.8 | 11197.5 | 11185.9 | 11095 | 10937 | 10973.3 | 10073.3 | 11019.9 | 10928.8 | 11210.1 | 11435.7 | 11016.8 | 11388.1 | 9408.9 | 10779.7 | 10283.8 | 31.8617 | 31.9137 | 31.7864 | 0 | 31.7558 | 21.2958 | 0 | 44.1284 | 0 | 0 | 0 | 0 | 2.408 | 2.0882 | 2.1247 | 0 | 2.3022 | 1.2818 | 5.829 | 4.971 | 5.284 | 0 | 5.344 | 5.294 | 5.2728 | 5.5922 | 4.7156 | 0 | 4.9798 | 0 | 0.0065126 | 1.0772 | 1.1534 | 0 | 1.0689 | 0 | 6.0305 | 4.9934 | 5.4858 | 0 | 5.5435 | 0 | 1.3003 | 1.0534 | 1.1498 | 0 | 1.0831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138580 | 239 | 129871 | 239 | 245747.286 | 592.4 | 5.2728 | 5.5922 | 4.7156 | 0 | 4.9798 | 0 | 6.0305 | 4.9934 | 5.4858 | 0 | 5.5435 | 0 | 822000 | 2000 | 787000 | 1000 | 1603467 | 4467 | 1606000 | 1599000 | 11.75 | 5.1401 | 0.82649 | 5.5133 | 1.1466 | 16.08% | 20.8% | 29.7227 | 44.1284 | 2.041 | 5.3444 | 1616750.9 | 1603334 | 1826247.2107 | 87.79%
2022-10-13 | 2023 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 334195.71 | 6:36 | 18:21 | 10902.9 | 11744.9 | 11813.6 | 11857.7 | 11613.5 | 11894.9 | 11602.2 | 11813.8 | 11850.1 | 11681.6 | 11741.9 | 11863 | 11944.8 | 11850 | 11697.8 | 12037.1 | 11730.9 | 11960.3 | 12007.4 | 11963.5 | 11969.1 | 11977.8 | 11825.9 | 11941.5 | 11923.3 | 10440.7 | 11949.4 | 11990.2 | 12002.1 | 11806.3 | 11861.2 | 12017.8 | 11792.3 | 12089.2 | 12036.6 | 11984.6 | 12006.3 | 11942.4 | 11982 | 11952.3 | 12441.6 | 11689.7 | 12475.1 | 11454.9 | 11720.9 | 12901.7 | 11113.5 | 12603.4 | 11258.9 | 10952.2 | 12006 | 11436.6 | 12491.4 | 11040.5 | 12501.6 | 11306.5 | 11218.4 | 12274.9 | 11255.3 | 12563 | 12513 | 11053.4 | 12489.7 | 11263.9 | 11524.3 | 11242.7 | 11918 | 12225.6 | 12616.9 | 11407.2 | 12448.3 | 10996.3 | 10851.6 | 12486.4 | 11261.6 | 12440 | 11122.4 | 12572.9 | 11117.6 | 12350.8 | 11292.7 | 12185.4 | 10817 | 12388 | 11011.2 | 11513.7 | 11147 | 9124.3 | 11821.7 | 11657 | 10773.3 | 12327.6 | 12017.2 | 10843.2 | 10677.8 | 12097.3 | 10498.7 | 11113.7 | 12103.6 | 10748.1 | 12082.5 | 10826 | 12048.6 | 11148.2 | 12200.6 | 10599.2 | 12329.9 | 11235.3 | 12224.1 | 11185.3 | 11949 | 11378.8 | 10935 | 11969.3 | 11056.1 | 10884.8 | 12142.2 | 11965.1 | 12097.5 | 11183.4 | 12217 | 10913.4 | 11864.6 | 11244 | 11673.6 | 10362.4 | 12049.7 | 11055.8 | 10976 | 10970.4 | 10782.6 | 9366 | 11003 | 9667.9 | 10844.5 | 10771.1 | 12638.5 | 11041.8 | 12649.4 | 11437.9 | 12329.2 | 10895.9 | 11082.5 | 10794.4 | 12290.7 | 12651.8 | 12592.6 | 12546.3 | 12459.8 | 12586 | 11555.9 | 12566.1 | 12051.8 | 12349.7 | 12489.6 | 12106.7 | 12649.6 | 10498.7 | 11963.7 | 11482.1 | 32.3287 | 32.4678 | 32.3965 | 0 | 32.8142 | 32.5939 | 0 | 47.3796 | 0 | 0 | 48.3434 | 0 | 2.0345 | 1.9716 | 1.8735 | 0 | 1.9332 | 1.8484 | 6.753 | 5.613 | 5.187 | 0 | 5.685 | 4.9317 | 5.8516 | 5.9853 | 5.851 | 0 | 5.8608 | 6.2292 | 0.90677 | 1.3569 | 1.3863 | 0 | 1.3655 | 1.1607 | 6.8378 | 6.7852 | 6.8586 | 0 | 6.7714 | 6.4237 | 1.4062 | 1.3194 | 1.3617 | 0 | 1.377 | 1.4543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 139522 | 240 | 130787 | 241 | 247598.486 | 598.733 | 5.8516 | 5.9853 | 5.851 | 0 | 5.8608 | 6.2292 | 6.8378 | 6.7852 | 6.8586 | 0 | 6.7714 | 6.4237 | 942000 | 1000 | 916000 | 2000 | 1851200 | 6333 | 1855000 | 1844867 | 11.75 | 5.9556 | 1.2352 | 6.7353 | 1.3837 | 20.74% | 20.54% | 32.5202 | 47.8615 | 1.9322 | 5.6339 | 1866743.7 | 1851067 | 2192328.0742 | 84.43%
2022-10-14 | 2023 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 334195.71 | 6:36 | 18:20 | 11000 | 11806.6 | 11881.1 | 11924.6 | 11677.4 | 11970.6 | 11664.8 | 11873.2 | 11919.8 | 11738.6 | 11813.1 | 11928.7 | 12021.8 | 11921.2 | 11775.8 | 12121.4 | 11817.2 | 12057 | 12095.2 | 12036.9 | 12056.5 | 12068.2 | 11909 | 12025.9 | 12001.4 | 10534.5 | 12028.2 | 12067.3 | 12070.8 | 11873 | 11946.9 | 12101.4 | 11867.1 | 12177.9 | 12109.4 | 12050.9 | 12082.6 | 12022.7 | 12065.2 | 12039.2 | 12526.1 | 11782.9 | 12561 | 11552.1 | 11823.2 | 12983.1 | 11211.9 | 12688.5 | 11356.7 | 11051.1 | 12079.3 | 11525.8 | 12568.9 | 11127.8 | 12574.9 | 11399.3 | 11315 | 12336.6 | 11350.9 | 12624.9 | 12573.9 | 11148.6 | 12538.8 | 11341.9 | 11610.9 | 11324 | 11993.6 | 12268.6 | 12678 | 11488.9 | 12520.5 | 11080.4 | 10949.8 | 12562.3 | 11365.3 | 12506.4 | 11211.6 | 12646.2 | 11212.6 | 12414.5 | 11363.2 | 12227.7 | 10895.2 | 12425.8 | 11082.5 | 11576.8 | 11186.8 | 9180.1 | 11873.8 | 11720.9 | 10846.4 | 12389.9 | 12111.1 | 10960.9 | 10800 | 12226.5 | 10588.3 | 11220.4 | 12209.8 | 10851.8 | 12165.3 | 10927.6 | 12133.1 | 11267.7 | 12291.1 | 10709 | 12415.8 | 11337.4 | 12324.9 | 11309 | 12066.2 | 11497.1 | 11031.7 | 12065.2 | 11165 | 10984.3 | 12220.8 | 12059 | 12183.7 | 11285.8 | 12304.4 | 11016.4 | 11985.6 | 11360 | 11772.3 | 10463.6 | 12144.1 | 11164.7 | 11074.2 | 11059.2 | 10866.5 | 9449.2 | 11103.8 | 9735.7 | 10905.6 | 10833.1 | 12691 | 11101.5 | 12690.3 | 11489.6 | 12376.7 | 10935.7 | 11124 | 10837.6 | 12344.1 | 12704.7 | 12643.8 | 12597.6 | 12503.4 | 12634.8 | 11604.6 | 12606 | 11742.6 | 12027.1 | 12162.2 | 11794.7 | 2322.1 | 9997.8 | 11675.5 | 11198.8 | 32.0281 | 32.0426 | 31.9329 | 0 | 32.279 | 32.0432 | 0 | 46.7183 | 0 | 0 | 0 | 0 | 2.0473 | 2.0508 | 2.1696 | 0 | 2.187 | 1.9759 | 5.394 | 5.484 | 6.235 | 0 | 7.836 | 4.601 | 5.8694 | 6.058 | 5.8708 | 0 | 5.8655 | 6.2452 | 1.3114 | 1.3813 | 1.4003 | 0 | 1.3777 | 1.1706 | 6.8911 | 6.961 | 6.8876 | 0 | 6.8023 | 6.4163 | 1.4201 | 1.3392 | 1.3658 | 0 | 1.3862 | 1.4619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140469 | 242 | 131697 | 242 | 249449.286 | 601.267 | 5.8694 | 6.058 | 5.8708 | 0 | 5.8655 | 6.2452 | 6.8911 | 6.961 | 6.8876 | 0 | 6.8023 | 6.4163 | 947000 | 2000 | 910000 | 1000 | 1850800 | 2534 | 1854000 | 1848266 | 11.7333 | 5.9818 | 1.3283 | 6.7917 | 1.3946 | 22.21% | 20.53% | 32.0652 | 46.7183 | 2.0861 | 5.91 | 1866242.1 | 1850667 | 2210957.1152 | 83.7%
2022-10-15 | 2023 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 334195.71 | 6:37 | 18:19 | 11131.7 | 11784.2 | 11923.8 | 11970.1 | 11682.7 | 11944.2 | 11717.6 | 11902.1 | 11951.1 | 11703.2 | 11845.2 | 11953.5 | 12058.2 | 11949.8 | 11821.6 | 12151.3 | 11854.3 | 12090.2 | 12114.9 | 12069.7 | 12006.1 | 12087.7 | 11949.9 | 11989.5 | 12020.7 | 10666.9 | 12058.4 | 12082.2 | 12078.3 | 11799 | 11973.3 | 12091.9 | 11899.2 | 12114.2 | 12123.3 | 12063.8 | 12094.7 | 12042.1 | 12075.1 | 12054.7 | 12501.1 | 11819.9 | 12457.9 | 11610.5 | 11853.1 | 12941.1 | 11230.3 | 12649.1 | 11487.9 | 11196 | 12118.5 | 11634.5 | 12571.8 | 11264.9 | 12501.1 | 11527.2 | 11450.7 | 12353.2 | 11478.7 | 12628.6 | 12579.9 | 11284.3 | 12526.2 | 11445.8 | 11702 | 11466.5 | 12041.9 | 12277.2 | 12671.4 | 11524.5 | 12524 | 11230.2 | 11055.9 | 12566.9 | 11434.3 | 12517.4 | 11372.7 | 12645.2 | 11363 | 12426.5 | 11405.3 | 12231.2 | 10971.9 | 12419.9 | 11206.3 | 11651.3 | 11217.4 | 9290.9 | 11907.6 | 11667.7 | 10928.5 | 12388.8 | 12167.6 | 11260.7 | 11054.1 | 12166.9 | 10812.1 | 11390.6 | 12296.9 | 11001.7 | 12175.3 | 11041.7 | 12183 | 11468.4 | 12257.6 | 10898.6 | 12379.2 | 11480.8 | 12370.3 | 11465 | 12069.6 | 11618.3 | 11116.1 | 12087.8 | 11253.2 | 11146.8 | 12247.8 | 12016.6 | 12209.4 | 11345.7 | 12316.6 | 11165.6 | 11958.3 | 11489.9 | 11762.3 | 10593.9 | 12171.6 | 11311.2 | 11212.8 | 11130.5 | 10952.6 | 9571.8 | 11124.1 | 9858 | 10975.7 | 10982.5 | 12706 | 11202.6 | 12628.6 | 11597 | 12390.5 | 11018.6 | 11248.7 | 10989.1 | 12386.2 | 12651.9 | 12664.6 | 12624.6 | 12539.4 | 12670.1 | 11710.3 | 12635 | 12133.9 | 12351.2 | 12487.6 | 12201.8 | 12716.1 | 10714.7 | 12075.4 | 11653.2 | 32.2857 | 32.0997 | 31.9315 | 0 | 32.1758 | 32.0789 | 0 | 47.1942 | 0 | 0 | 0 | 0 | 1.8921 | 1.8481 | 1.8981 | 0 | 1.9353 | 1.9356 | 5.469 | 4.71 | 4.937 | 0 | 4.736 | 9.155 | 5.9847 | 6.1253 | 5.9158 | 0 | 5.9336 | 6.3493 | 1.3363 | 1.3914 | 1.4334 | 0.0048998 | 1.396 | 1.194 | 6.9969 | 7.0611 | 6.9996 | 0 | 6.8954 | 6.5069 | 1.4516 | 1.342 | 1.3967 | 0 | 1.4023 | 1.4891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141420 | 243 | 132625 | 244 | 251321.02 | 607.8 | 5.9847 | 6.1253 | 5.9158 | 0 | 5.9336 | 6.3493 | 6.9969 | 7.0611 | 6.9996 | 0 | 6.8954 | 6.5069 | 951000 | 1000 | 928000 | 2000 | 1871734 | 6533 | 1876000 | 1865201 | 11.7 | 6.0617 | 1.126 | 6.892 | 1.4164 | 18.58% | 20.55% | 32.1143 | 47.1942 | 1.9018 | 5.8014 | 1887665.4 | 1871467 | 2240661.8493 | 83.52%
2022-10-16 | 2023 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 334195.71 | 6:38 | 18:18 | 10976.6 | 11726.9 | 11845.6 | 11860.1 | 11749.9 | 11948.4 | 11608.8 | 12003.6 | 11855 | 11615.9 | 11756 | 11849.6 | 11950 | 11833.8 | 11653.7 | 12007.3 | 11708.3 | 11953.7 | 11981.8 | 11945.9 | 11922.6 | 11935.5 | 11682.2 | 11912.7 | 11876.3 | 10494.3 | 11929.6 | 11954.1 | 11951.6 | 11737.9 | 11830.1 | 12018.7 | 11752.4 | 12050.5 | 11991.2 | 11912.8 | 11937.4 | 11895.3 | 11923.9 | 11912.6 | 12360 | 11677.3 | 12381.4 | 11460.5 | 11699.8 | 12777 | 11139.3 | 12512.6 | 11322.1 | 11023.4 | 11971.7 | 11482.8 | 12414.9 | 11111.6 | 12431.9 | 11368.1 | 11295.9 | 12211.8 | 11311.9 | 12485.6 | 12444.5 | 11122.3 | 12384.4 | 11300.4 | 11580.2 | 11319.3 | 11912.7 | 12148.8 | 12535 | 11454.3 | 12392 | 11069.3 | 10925.4 | 12427.9 | 11343.5 | 12384.4 | 11215.7 | 12507 | 11220.1 | 12311 | 11341.4 | 12104.9 | 10854.8 | 12283.1 | 11029.2 | 11487.8 | 11140.8 | 9142 | 11760.1 | 11539 | 10947.9 | 12233.9 | 12015.2 | 11176.1 | 10868.7 | 12076.5 | 10687.6 | 11222.2 | 12138.2 | 10831.2 | 12023 | 10913.6 | 12038.2 | 11265.2 | 12196.1 | 10703.8 | 12281.2 | 11284.7 | 12207.1 | 11275 | 11977.4 | 11428.1 | 11027.9 | 11931.1 | 11130.4 | 10955.5 | 12083.4 | 11924.2 | 12047.8 | 11253.9 | 12161.3 | 10979.9 | 11858.9 | 11300.2 | 11655.2 | 10417 | 12012.8 | 11128.3 | 11003.8 | 10993.1 | 10856.4 | 9411.1 | 10810.9 | 9675.6 | 10850 | 10790.7 | 12540.9 | 11090.7 | 12532.8 | 11435.5 | 12222 | 10882.1 | 11060.4 | 10796.9 | 12222.2 | 12553.8 | 12508.1 | 12475.5 | 12385.2 | 12518 | 11552.2 | 12479.6 | 11963 | 12261.9 | 12400.3 | 12043.1 | 12551.7 | 10530.8 | 11913.8 | 11492.9 | 32.1182 | 32.1517 | 31.9329 | 0 | 32.0026 | 32.0777 | 0 | 46.2863 | 0 | 0 | 0 | 0 | 2.5268 | 2.569 | 2.55 | 0 | 2.513 | 2.4674 | 5.941 | 5.858 | 6.395 | 0 | 6.069 | 6.262 | 5.8671 | 5.9918 | 5.829 | 0 | 5.8013 | 6.1986 | 1.3226 | 1.3754 | 1.4151 | 0 | 1.3738 | 1.168 | 6.8698 | 6.9146 | 6.8834 | 0 | 6.7481 | 6.3479 | 1.4336 | 1.3282 | 1.3768 | 0 | 1.3765 | 1.4617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142115 | 245 | 133541 | 246 | 253171.62 | 610.4 | 5.8671 | 5.9918 | 5.829 | 0 | 5.8013 | 6.1986 | 6.8698 | 6.9146 | 6.8834 | 0 | 6.7481 | 6.3479 | 695000 | 2000 | 916000 | 2000 | 1850600 | 2600 | 1607000 | 1848000 | 11.6667 | 5.9375 | 1.331 | 6.7528 | 1.3953 | 22.42% | 20.66% | 32.0566 | 46.2863 | 2.5252 | 6.105 | 1866037.2 | 1850533 | 2208885.688 | 83.78%
2022-10-17 | 2023 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 334195.71 | 6:38 | 18:17 | 10897.2 | 11677.9 | 11814.1 | 11825 | 11705.3 | 11924.4 | 11550.8 | 11990.4 | 11848.9 | 11565.5 | 11739.8 | 11834.7 | 11935 | 11821.2 | 11598 | 11974.7 | 11665.7 | 11942.4 | 11972.6 | 11944.1 | 11880.4 | 11894.4 | 11752.9 | 11864.2 | 11854.3 | 10429.6 | 11898.8 | 11931.2 | 11926.4 | 11693.7 | 11802.4 | 12002.8 | 11710 | 12018.5 | 12012.4 | 11942.1 | 11969.5 | 11869.5 | 11909.5 | 11881.7 | 12343 | 11615.8 | 12376.5 | 11388.9 | 11654.8 | 12788.8 | 11043.6 | 12499.7 | 11253.1 | 10950.8 | 11932.3 | 11417.6 | 12400.5 | 11140.4 | 12426.6 | 11299.1 | 11213.2 | 12230.9 | 11246.1 | 12485 | 12444.2 | 11057.1 | 12403.5 | 11251.7 | 11572.5 | 11255.4 | 11889.7 | 12149.4 | 12552.6 | 11400.3 | 12400.1 | 10997.8 | 10859.3 | 12432.1 | 11278 | 12385.3 | 11145.6 | 12517.1 | 11213.4 | 12358.5 | 11268.1 | 12105.2 | 10605.2 | 12273.3 | 10949.6 | 11428.7 | 11074 | 9072 | 11858.6 | 11497.6 | 10983 | 12312.3 | 11988.9 | 11087.8 | 10796.5 | 12102 | 10607.7 | 11158.1 | 12131.4 | 10762 | 12000.6 | 10852.4 | 12014.8 | 11202.4 | 12213.5 | 10643.9 | 12282.1 | 11223.6 | 12196.1 | 11217.1 | 12123.1 | 11376.9 | 10941.9 | 11941.4 | 11071.6 | 10903.6 | 12090.1 | 11925.5 | 12052.6 | 11205.4 | 12163.9 | 10926.3 | 11845.4 | 11232.7 | 11685.9 | 10363.9 | 11998.9 | 11068.8 | 10924.6 | 10868.2 | 10782.3 | 9363 | 10728.6 | 9605.1 | 10773 | 10723.3 | 12543.1 | 11016.5 | 12525.8 | 11358.2 | 12208.7 | 10797.5 | 10983.5 | 10710.6 | 12183.4 | 12532.3 | 12474.1 | 12448.3 | 12355.2 | 12491.5 | 11472.1 | 12452.1 | 11933.8 | 12252.1 | 12398.2 | 12018.8 | 12545.8 | 10470 | 11867.5 | 11437.4 | 32.0195 | 31.7704 | 31.5147 | 0 | 31.6258 | 31.2611 | 0 | 46.7793 | 0 | 0 | 0 | 0 | 2.0226 | 1.9398 | 1.9469 | 0 | 1.9673 | 1.8162 | 5.262 | 5.452 | 5.361 | 0 | 5.144 | 5.417 | 5.8411 | 5.9607 | 5.7946 | 0 | 5.773 | 6.1981 | 1.3124 | 1.3688 | 1.408 | 0 | 1.3752 | 1.1891 | 6.8585 | 6.8974 | 6.8584 | 0 | 6.7446 | 6.3267 | 1.429 | 1.3194 | 1.3727 | 0 | 1.3781 | 1.486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143299 | 247 | 134455 | 247 | 255017.287 | 615.067 | 5.8411 | 5.9607 | 5.7946 | 0 | 5.773 | 6.1981 | 6.8585 | 6.8974 | 6.8584 | 0 | 6.7446 | 6.3267 | 1184000 | 2000 | 914000 | 1000 | 1845667 | 4667 | 2095000 | 1841000 | 11.65 | 5.9135 | 1.3307 | 6.7371 | 1.397 | 22.5% | 20.74% | 31.6383 | 46.7793 | 1.9386 | 5.3272 | 1860813.3 | 1845600 | 2198161.1722 | 83.96%
2022-10-18 | 2023 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 334195.71 | 6:38 | 18:16 | 10772.7 | 11580.3 | 11712.8 | 11723.2 | 11600.8 | 11821.3 | 11436.6 | 11885.3 | 11749.4 | 11463.9 | 11639 | 11740.9 | 11834.6 | 11728.1 | 11485.8 | 11880 | 11566.2 | 11845.1 | 11882.6 | 11841.6 | 11789.6 | 11799.5 | 11653.3 | 11774.1 | 11752.9 | 10292.1 | 11780.3 | 11828.5 | 11875.5 | 11591.1 | 11702.2 | 11908.5 | 11571.2 | 11898.6 | 11922 | 11874 | 11905 | 11766.2 | 11813.5 | 11759.5 | 12238 | 11490.4 | 12263 | 11252.9 | 11530.9 | 12679.8 | 10919.1 | 12400.1 | 11096 | 10799.8 | 11799 | 11265.2 | 12278.6 | 10977.6 | 12319.1 | 11159.3 | 11074.5 | 12152.1 | 11107.8 | 12372.8 | 12334 | 10922.6 | 12467.5 | 11334 | 11433.6 | 11118.6 | 11769.6 | 12045.7 | 12439.9 | 11260.7 | 12289.6 | 10857.9 | 10721.8 | 12323.4 | 11137.2 | 12281.2 | 11015.3 | 12415.7 | 11083.8 | 12251.1 | 11109.6 | 11997.4 | 10440.9 | 12176.6 | 10792.9 | 11286.5 | 10930.4 | 8955.3 | 11755.1 | 11369.9 | 10850.2 | 12222.8 | 11882.9 | 10930.7 | 10654.4 | 12003.1 | 10482.5 | 11024.4 | 12040.1 | 10617.2 | 11888.3 | 10706 | 11902.4 | 11045.7 | 12112.6 | 10485.4 | 12168.5 | 11073.3 | 12087.1 | 11056.5 | 12098.8 | 11214.2 | 10805.1 | 11858.6 | 10912.8 | 10791.2 | 12007.8 | 11816.6 | 11965.6 | 11058.3 | 12052.1 | 10774.5 | 11753.5 | 11078.1 | 11668 | 10214.8 | 11880.3 | 10913.7 | 10836 | 10769.3 | 10648.6 | 9260.3 | 10608.8 | 9476.9 | 10721.8 | 10675.4 | 12470.6 | 10901.1 | 12452.5 | 11260.8 | 12163.6 | 10700.1 | 10895.9 | 10628.7 | 12111.4 | 12470.4 | 12421.4 | 12387.6 | 12299 | 12057.5 | 11383.8 | 12388.3 | 11886.1 | 12169.2 | 12298.3 | 11921.9 | 12461.4 | 10342.1 | 11821.7 | 11330.3 | 31.876 | 32.0043 | 32.0294 | 0 | 31.9843 | 32.0983 | 0 | 46.7127 | 0 | 0 | 0 | 0 | 2.3842 | 2.3939 | 2.3706 | 0 | 2.3056 | 2.2907 | 4.863 | 6.402 | 6.045 | 0 | 5.349 | 5.243 | 5.7461 | 5.8936 | 5.7006 | 0 | 5.7053 | 6.145 | 1.2905 | 1.3515 | 1.3899 | 0 | 1.374 | 1.1651 | 6.7561 | 6.8369 | 6.77 | 0 | 6.6642 | 6.2646 | 1.4086 | 1.2996 | 1.356 | 0 | 1.3702 | 1.4561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 144299 | 248 | 135360 | 249 | 256845.753 | 619.733 | 5.7461 | 5.8936 | 5.7006 | 0 | 5.7053 | 6.145 | 6.7561 | 6.8369 | 6.77 | 0 | 6.6642 | 6.2646 | 1000000 | 1000 | 905000 | 2000 | 1828466 | 4666 | 1902000 | 1823800 | 11.6333 | 5.8381 | 1.3142 | 6.6584 | 1.3781 | 22.51% | 20.7% | 31.9985 | 46.7127 | 2.349 | 5.5804 | 1843260.5 | 1828466 | 2175413.8138 | 84.05%
2022-10-19 | 2023 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 334195.71 | 6:39 | 18:18 | 10810.2 | 11622.3 | 11763.8 | 11772 | 11639 | 11869.4 | 11471.6 | 11923.4 | 11804.4 | 11504 | 11719.4 | 11845.8 | 11891 | 11819 | 11519.7 | 11930 | 11621.2 | 11896.5 | 11941.6 | 11897 | 11845 | 11852.2 | 11700.5 | 11829.1 | 11795.7 | 10330 | 11836 | 11873.9 | 11930.1 | 11644.8 | 11755 | 11960.8 | 11604.4 | 11951.9 | 11962 | 11916.9 | 11947.2 | 11810.4 | 11855.9 | 11807.8 | 12262.5 | 11517.4 | 12293.2 | 11262 | 11568.9 | 12719.2 | 10956.3 | 12440.4 | 11142.4 | 10838.6 | 11860.2 | 11281.4 | 12332.6 | 11020.3 | 12351.7 | 11171.1 | 11097.2 | 12198.5 | 11147.5 | 12425.5 | 12388.1 | 10964 | 12596.4 | 11466 | 11478.3 | 11154.9 | 11827.6 | 12093 | 12494.7 | 11295.9 | 12346.8 | 10890.1 | 10762.3 | 12378.6 | 11178 | 12335.2 | 11043.2 | 12468.5 | 11114.2 | 12302.8 | 11132.9 | 12034.2 | 10445.1 | 12209.7 | 10810.1 | 11296.1 | 10948.7 | 8966.4 | 11778.6 | 11391.7 | 10861.7 | 12253.6 | 11909.7 | 10953.9 | 10678.3 | 12030.4 | 10508.4 | 11049.5 | 12092.4 | 10652.8 | 11942.7 | 10739.9 | 11954.6 | 11078.2 | 12160.4 | 10514.4 | 12206.6 | 11105 | 12133.8 | 11086.7 | 12144.3 | 11263.5 | 10843.5 | 11899.1 | 10952.9 | 10825 | 12060.8 | 11862.6 | 12024.7 | 11096.8 | 12110.7 | 10812.1 | 11817 | 11146.2 | 11742.9 | 10271.8 | 11946.5 | 10966.7 | 10864.2 | 10796.1 | 10660.7 | 9272.3 | 10626.3 | 9473.3 | 10743.4 | 10684.8 | 12501.3 | 10928.7 | 12485.6 | 11293.5 | 12190.3 | 10702.6 | 10902.4 | 10627.1 | 12154.6 | 12507.9 | 12452.6 | 12419.7 | 12319.2 | 12460.8 | 11403.9 | 12416.7 | 11936.1 | 12207.4 | 12331.8 | 11963.4 | 12513.5 | 10372 | 11880 | 11368.2 | 32.4566 | 32.1513 | 32.1074 | 0 | 32.2798 | 32.1736 | 0 | 46.33 | 0 | 0 | 0 | 0 | 3.2873 | 3.133 | 3.1852 | 0 | 3.2472 | 2.9392 | 6.203 | 5.829 | 6.215 | 0 | 6.164 | 5.619 | 5.7419 | 5.8879 | 5.6896 | 0 | 5.6905 | 6.1553 | 1.2829 | 1.3552 | 1.3784 | 0 | 1.3778 | 1.1917 | 6.7829 | 6.8606 | 6.771 | 0 | 6.689 | 6.2513 | 1.4019 | 1.3051 | 1.3443 | 0 | 1.3743 | 1.4905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145163 | 250 | 136267 | 251 | 258680.62 | 624.333 | 5.7419 | 5.8879 | 5.6896 | 0 | 5.6905 | 6.1553 | 6.7829 | 6.8606 | 6.771 | 0 | 6.689 | 6.2513 | 864000 | 2000 | 907000 | 2000 | 1834867 | 4600 | 1767000 | 1830267 | 11.65 | 5.833 | 1.3172 | 6.671 | 1.3832 | 22.58% | 20.73% | 32.2337 | 46.33 | 3.1584 | 6.006 | 1850110.4 | 1834667 | 2185117.2223 | 83.96%
2022-10-20 | 2023 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 334195.71 | 6:40 | 18:13 | 10450.3 | 11247 | 11426.4 | 11431.2 | 11349.5 | 11560.7 | 11263.6 | 11651.2 | 11430.5 | 11124.8 | 11361.9 | 11504.3 | 11518.9 | 11480.2 | 11155.9 | 11561.2 | 11259.5 | 11539.2 | 11579.3 | 11536.6 | 11475.7 | 11482 | 11327 | 11451 | 11424.2 | 9977.8 | 11457.3 | 11493.8 | 11549.4 | 11264.1 | 11380.6 | 11592.4 | 11213.3 | 11571.6 | 11585.1 | 11529.9 | 11563.7 | 11427.3 | 11479.4 | 11427.3 | 11880 | 11111.9 | 11919.7 | 10867.2 | 11168 | 12353 | 10557.3 | 12074.3 | 10772.3 | 10479.4 | 11485.5 | 10908.2 | 11977.5 | 10667.5 | 11991.8 | 10816.5 | 10722.5 | 11831.9 | 10771.3 | 12054.5 | 12015.7 | 10581 | 12253 | 11088.8 | 11101.4 | 10795.2 | 11450.7 | 11722.5 | 12146.3 | 10919.5 | 11985.6 | 10529.2 | 10405 | 12014.3 | 10805.1 | 11970.3 | 10669.1 | 12108 | 10740.9 | 11939 | 10749.3 | 11646.6 | 10090 | 11834.9 | 10440.5 | 10918.6 | 10576.9 | 8666.2 | 11398.4 | 11016.5 | 10484.8 | 11869.4 | 11521.8 | 10569.6 | 10304.6 | 11645.4 | 10155.6 | 10666.4 | 11725.6 | 10287.3 | 11584.8 | 10379.3 | 11584 | 10712.7 | 11800.9 | 10163.9 | 11834.8 | 10728.4 | 11755.7 | 10702.8 | 11764.3 | 10884.3 | 10492.8 | 11522.9 | 10579.9 | 10452.5 | 11685.1 | 11479.8 | 11644.2 | 10715.2 | 11739.8 | 10435.7 | 11427.1 | 10753.7 | 11343 | 9920.6 | 11561.4 | 10577.4 | 10472.2 | 10398.4 | 10301.1 | 8954 | 10224.9 | 9138.9 | 10366.7 | 10307 | 12173.6 | 10582.8 | 12166.5 | 10933.3 | 11866.1 | 10367.6 | 10563.8 | 10242.6 | 11813.1 | 12182.4 | 12112.5 | 12082.4 | 11996.5 | 12132.3 | 11040.3 | 12090.8 | 11662 | 11916.6 | 12025.8 | 11632.4 | 12190.2 | 10302 | 11536.4 | 11035.6 | 30.8838 | 30.8286 | 30.9358 | 0 | 30.9661 | 31.1569 | 0 | 44.4322 | 0 | 0 | 0 | 0 | 3.7085 | 3.8291 | 3.62 | 0 | 3.8866 | 3.6349 | 8.757 | 8.433 | 8.123 | 0 | 8.184 | 7.715 | 5.509 | 5.6434 | 5.4502 | 0 | 5.4536 | 5.8742 | 1.2465 | 1.2951 | 1.3273 | 0 | 1.328 | 1.1414 | 6.4853 | 6.5568 | 6.4736 | 0 | 6.3705 | 5.9873 | 1.3564 | 1.2476 | 1.2978 | 0 | 1.3194 | 1.4296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146068 | 251 | 137147 | 253 | 260458.087 | 631.133 | 5.509 | 5.6434 | 5.4502 | 0 | 5.4536 | 5.8742 | 6.4853 | 6.5568 | 6.4736 | 0 | 6.3705 | 5.9873 | 905000 | 1000 | 880000 | 2000 | 1777467 | 6800 | 1782000 | 1770667 | 11.55 | 5.5861 | 1.2677 | 6.3747 | 1.3302 | 22.69% | 20.87% | 30.9542 | 44.4322 | 3.7358 | 8.2424 | 1792362.2 | 1777400 | 2113371.8778 | 84.1%
2022-10-21 | 2023 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 334195.71 | 6:41 | 18:10 | 10263.1 | 11077 | 11338.6 | 11345.1 | 11318.5 | 11376.9 | 11134.4 | 11411.9 | 11195.2 | 10945.4 | 11057.3 | 11235.8 | 11133.4 | 11147.1 | 10775.7 | 11209.5 | 10881.6 | 11182.9 | 11203.7 | 11145.9 | 11146.5 | 11133.6 | 11029.4 | 11124.9 | 11113.8 | 9642.1 | 11056.5 | 11144.9 | 11307.7 | 11140.9 | 11129.4 | 11341.6 | 10991.2 | 11384.1 | 11352.2 | 11320.7 | 11368.4 | 11219.7 | 11284.1 | 11221.5 | 11649.6 | 10812.5 | 11711.7 | 10586.6 | 10897.1 | 12168.5 | 10272.2 | 11847.9 | 10407.4 | 10142.4 | 11113.8 | 10543 | 11606 | 10266 | 11699.7 | 10455.6 | 10377.1 | 11554.3 | 10453.7 | 11771.6 | 11746.9 | 10297.7 | 12056.9 | 10803.6 | 10798.3 | 10480.8 | 11172.6 | 11447 | 11918.4 | 10595.9 | 11739.2 | 10222.9 | 10133.8 | 11766.2 | 10531.1 | 11728.7 | 10396.9 | 11921.9 | 10476.6 | 11732.1 | 10371.7 | 11334.8 | 9713.4 | 11506.4 | 10072.5 | 10521.7 | 10240.3 | 8359.4 | 11050.3 | 10650.8 | 10132.9 | 11555.8 | 11215.8 | 10244.1 | 9984.8 | 11321.7 | 10042.4 | 10325.4 | 11461.1 | 9962.8 | 11305.3 | 10078.2 | 11311.1 | 10396.2 | 11563.3 | 9869.1 | 11587.7 | 10394.6 | 11519.9 | 10429.4 | 11556.8 | 10548.1 | 10122.4 | 11126.6 | 10209.4 | 10052.5 | 11310.3 | 11073.1 | 11260 | 10289.5 | 11349 | 10029.4 | 11049.3 | 10365.4 | 10974.7 | 9545.9 | 11163.9 | 10173.4 | 10069.7 | 10028.9 | 9938.7 | 8613.9 | 9910.7 | 8861.1 | 10161.7 | 10105.5 | 11816.1 | 10247.7 | 11875.8 | 10639.8 | 11702.9 | 10257.8 | 10456.7 | 10051 | 11394 | 11811.9 | 11646.7 | 11631.7 | 11554.7 | 11730 | 10663.2 | 11729.3 | 11409.8 | 11642.1 | 11655.8 | 11230.6 | 11760.9 | 9958.6 | 11122.1 | 10631.7 | 31.1568 | 30.9486 | 30.8713 | 0 | 31.3477 | 30.968 | 0 | 43.9719 | 0 | 0 | 0 | 0 | 2.577 | 2.5413 | 2.5536 | 0 | 2.5054 | 2.422 | 5.856 | 4.451 | 4.32 | 0 | 4.834 | 4.731 | 5.3174 | 5.4529 | 5.2865 | 0 | 5.2309 | 5.5758 | 1.2094 | 1.2434 | 1.291 | 0 | 1.247 | 1.0619 | 6.2393 | 6.3237 | 6.2997 | 0 | 6.0793 | 5.7039 | 1.3132 | 1.1965 | 1.2702 | 0 | 1.2448 | 1.3286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146952 | 253 | 138000 | 254 | 262188.154 | 633.667 | 5.3174 | 5.4529 | 5.2865 | 0 | 5.2309 | 5.5758 | 6.2393 | 6.3237 | 6.2997 | 0 | 6.0793 | 5.7039 | 884000 | 2000 | 853000 | 1000 | 1730067 | 2534 | 1734000 | 1727533 | 11.4833 | 5.3727 | 1.2105 | 6.1292 | 1.2707 | 22.53% | 20.73% | 31.0585 | 43.9719 | 2.5199 | 4.8384 | 1744170.1 | 1730000 | 2022113.2256 | 85.55%
2022-10-22 | 2023 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 334195.71 | 6:42 | 18:11 | 10290.5 | 11261.5 | 11326.1 | 11298.8 | 11298.2 | 11416.1 | 11257.5 | 11554.4 | 11259.4 | 11123.3 | 11135.8 | 11298.6 | 11298.2 | 11268.2 | 11178.6 | 11387.8 | 11198.4 | 11352.6 | 11412.2 | 11366.1 | 11308 | 11311.3 | 11171.3 | 11272.4 | 11245.9 | 9778.8 | 11278.5 | 11329 | 11444.9 | 11257.9 | 11192.5 | 11448.7 | 11022.9 | 11444.6 | 11449.9 | 11373.8 | 11425.2 | 11265.6 | 11325.8 | 11264.5 | 11767 | 10875 | 11828.7 | 10629.2 | 10930.1 | 12266.4 | 10352 | 11973.9 | 10521.2 | 10234.7 | 11270.2 | 10668.4 | 11850 | 10437.9 | 11875.9 | 10589.3 | 10460.5 | 11681.2 | 10506.8 | 11908 | 11868.7 | 10335.6 | 12130.6 | 10824.9 | 10849.7 | 10571.9 | 11232.2 | 11604.9 | 12030.1 | 10707.7 | 11864 | 10322.2 | 10168.1 | 11899.5 | 10561 | 11852.3 | 10450.8 | 11986.7 | 10493.7 | 11812.5 | 10519.7 | 11490.3 | 9875.1 | 11712.4 | 10221.6 | 10678.2 | 10384 | 8482.8 | 11360.2 | 10817.4 | 10298.2 | 11790.6 | 11401.6 | 10395.3 | 10153.5 | 11527.7 | 10348.6 | 10537.1 | 11668.1 | 10089.1 | 11442.6 | 10185.9 | 11417.9 | 10508.6 | 11704 | 9970.6 | 11732.3 | 10522.6 | 11624.9 | 10503.9 | 11653.9 | 10667.2 | 10282.8 | 11376.5 | 10375.7 | 10241.4 | 11560.8 | 11326.7 | 11514.8 | 10495.4 | 11621.3 | 10232.3 | 11253.3 | 10538.6 | 11155.6 | 9709.2 | 11395.3 | 10361.4 | 10239.6 | 10161.7 | 10105.7 | 8760.4 | 9985.2 | 8918.8 | 10242.2 | 10181.1 | 12082 | 10389.5 | 12091.4 | 10764 | 11858.9 | 10372.9 | 10577 | 10121 | 11666.9 | 12083.1 | 12008.6 | 11968.8 | 11872.1 | 12017 | 10838.8 | 11987.5 | 11863.9 | 12073.2 | 11975.6 | 11515.8 | 12079.7 | 10180.1 | 11508.3 | 10925.6 | 31.7017 | 31.486 | 31.3323 | 0 | 31.3915 | 31.5754 | 0 | 45.6346 | 0 | 0 | 0 | 0 | 2.2962 | 2.3503 | 2.2953 | 0 | 2.3865 | 2.2198 | 5.328 | 5.571 | 5.823 | 0 | 5.229 | 5.375 | 5.383 | 5.5348 | 5.36 | 0 | 5.349 | 5.7831 | 1.2224 | 1.3523 | 1.3087 | 0 | 1.3202 | 1.1097 | 6.3796 | 6.4652 | 6.3972 | 0 | 6.2959 | 5.8557 | 1.3348 | 1.2967 | 1.2814 | 0 | 1.3161 | 1.3839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147843 | 254 | 138868 | 256 | 263941.887 | 640.533 | 5.383 | 5.5348 | 5.36 | 0 | 5.349 | 5.7831 | 6.3796 | 6.4652 | 6.3972 | 0 | 6.2959 | 5.8557 | 891000 | 1000 | 868000 | 2000 | 1753733 | 6866 | 1756000 | 1746867 | 11.4833 | 5.482 | 1.2626 | 6.2787 | 1.3226 | 23.03% | 21.06% | 31.4974 | 45.6346 | 2.3096 | 5.4652 | 1768330.7 | 1753534 | 2062995.2839 | 85%
2022-10-23 | 2023 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 334195.71 | 6:42 | 18:11 | 10529 | 11512.4 | 11551.8 | 11539 | 11537.5 | 11647.5 | 11502.7 | 11741.6 | 11529.2 | 11559.5 | 11408.5 | 11557.6 | 11553.4 | 11522 | 11452.8 | 11645.3 | 11453.3 | 11584.1 | 11651.7 | 11615.4 | 11610.8 | 11602.6 | 11408.6 | 11528 | 11478.8 | 9998.7 | 11531.8 | 11560.8 | 11665.2 | 11487.9 | 11422.6 | 11656.2 | 11447 | 11680.5 | 11671.6 | 11593.4 | 11627.3 | 11485.9 | 11531.8 | 11520.4 | 11950.7 | 11146.4 | 12002.5 | 10885.3 | 11125.4 | 12289.1 | 10574.8 | 12135.4 | 10779.7 | 10480.2 | 11547.6 | 10986.9 | 12041.5 | 10704.7 | 12046.1 | 10821.5 | 10710.7 | 11826.6 | 10771.2 | 12014.6 | 11969.7 | 10585.2 | 12104.1 | 11065.7 | 11090.2 | 10797.6 | 11488.4 | 11787.3 | 12144.3 | 10937.5 | 12013.9 | 10544.6 | 10423.6 | 12052.2 | 10821.4 | 12004.1 | 10687.5 | 12128.5 | 10740.7 | 11966.9 | 10730.6 | 11692.9 | 10061.1 | 11852.8 | 10414.3 | 10877.5 | 10640.9 | 8675 | 11691 | 11023.1 | 10502.7 | 11991.6 | 11633.5 | 10684.2 | 10496.1 | 11710.4 | 10516.9 | 10755.9 | 11789.8 | 10267.3 | 11660.9 | 10358.1 | 11617.6 | 10662.7 | 11829.7 | 10139.9 | 11864.8 | 10713.8 | 11774.6 | 10703.7 | 11805.8 | 10871.9 | 10442.8 | 11603.4 | 10531.6 | 10403.2 | 11689.1 | 11536.1 | 11671.6 | 10665.4 | 11778.6 | 10419.9 | 11419.1 | 10699.4 | 11327.7 | 9852 | 11572.3 | 10524.2 | 10407.1 | 10312.2 | 10196.9 | 8851.1 | 10137.3 | 9057.6 | 10408 | 10347.8 | 12143.1 | 10558.7 | 12140.4 | 10931.1 | 11940.2 | 10551.6 | 10752.3 | 10289.4 | 11821.5 | 12160.2 | 12117.3 | 12067.5 | 11975.9 | 12091.7 | 11012.6 | 12074.8 | 11980.3 | 12159.8 | 12074 | 11680.2 | 12155.2 | 10367.5 | 11709.2 | 11137.9 | 30.9618 | 31.1607 | 31.0948 | 0 | 31.5205 | 31.2298 | 0 | 45.5335 | 0 | 0 | 0 | 0 | 2.0094 | 1.9223 | 1.8318 | 0 | 2.0002 | 1.9488 | 5.574 | 4.671 | 4.795 | 0 | 5.063 | 5.252 | 5.4945 | 5.6475 | 5.456 | 0 | 5.4489 | 5.9311 | 1.2471 | 1.3179 | 1.3254 | 0 | 1.3457 | 1.1283 | 6.5526 | 6.6496 | 6.558 | 0 | 6.4441 | 5.9731 | 1.3654 | 1.2646 | 1.2985 | 0 | 1.34 | 1.4067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148752 | 256 | 139748 | 258 | 265724.154 | 645.467 | 5.4945 | 5.6475 | 5.456 | 0 | 5.4489 | 5.9311 | 6.5526 | 6.6496 | 6.558 | 0 | 6.4441 | 5.9731 | 909000 | 2000 | 880000 | 2000 | 1782267 | 4934 | 1785000 | 1777333 | 11.4833 | 5.5956 | 1.2729 | 6.4355 | 1.335 | 22.75% | 20.74% | 31.1935 | 45.5335 | 1.9425 | 5.071 | 1799556.4 | 1782067 | 2110037.8413 | 84.46%
2022-10-24 | 2023 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 334195.71 | 6:43 | 18:11 | 10452.7 | 11441.7 | 11483.5 | 11464.3 | 11463 | 11571.6 | 11426.3 | 11675.5 | 11441.8 | 11489.1 | 11323.2 | 11472.3 | 11469.7 | 11442.8 | 11367.9 | 11555.5 | 11354 | 11486.2 | 11554.5 | 11521.1 | 11509.3 | 11508 | 11307.2 | 11429.2 | 11387.4 | 9925.6 | 11436.7 | 11469.2 | 11577.7 | 11393.7 | 11336.8 | 11570.7 | 11410.8 | 11612.1 | 11580.7 | 11499.6 | 11541.4 | 11399 | 11448.8 | 11458.5 | 11880.5 | 11065.9 | 11946.7 | 10818.1 | 11056.5 | 12273.7 | 10498.4 | 12092.8 | 10696.8 | 10400.1 | 11464 | 10957.3 | 12002.1 | 10646.3 | 11974.7 | 10742.3 | 10652.3 | 11791.6 | 10693.8 | 11999.5 | 11955 | 10510.2 | 12137.6 | 10984.4 | 11009.3 | 10721 | 11400.5 | 11723.8 | 12113.6 | 10867.6 | 11970.6 | 10479.2 | 10346.1 | 12004.4 | 10741 | 11957.6 | 10607.1 | 12090.6 | 10662.4 | 11910.8 | 10670.4 | 11621.5 | 10010.1 | 11806.2 | 10360.4 | 10825.2 | 10579.1 | 8632.5 | 11638.5 | 10976.5 | 10456.8 | 11965.4 | 11577.8 | 10626.2 | 10451.8 | 11655.9 | 10458.1 | 10693.5 | 11741 | 10217.7 | 11594.2 | 10307.5 | 11547.2 | 10608.4 | 11776.1 | 10087 | 11805.1 | 10648.5 | 11704 | 10632.1 | 11729.7 | 10795.9 | 10382.8 | 11518.8 | 10472.7 | 10342.4 | 11620.6 | 11451.5 | 11596.6 | 10597.3 | 11708.3 | 10350.3 | 11338 | 10626.7 | 11242 | 9782.9 | 11483.7 | 10467.8 | 10351.4 | 10261.3 | 10163 | 8823.7 | 10093.5 | 9011.8 | 10374.3 | 10310.3 | 12119.1 | 10506.9 | 12120.3 | 10887.3 | 11918.1 | 10510.9 | 10718.1 | 10243.8 | 11764 | 12131.7 | 12083.8 | 12036.8 | 11938.7 | 12065.7 | 10961.8 | 12043.6 | 11955.7 | 12137.9 | 12045.1 | 11620.8 | 12132.6 | 10312.2 | 11635.2 | 11071.6 | 30.8231 | 30.7482 | 30.8276 | 0 | 31.347 | 30.9951 | 0 | 44.9883 | 0 | 0 | 0 | 0 | 2.1824 | 2.0337 | 2.0003 | 0 | 2.0421 | 1.9221 | 5.424 | 5.476 | 5.11 | 0 | 5.349 | 5.485 | 5.4493 | 5.6057 | 5.3991 | 0 | 5.4128 | 5.9136 | 1.2265 | 1.3084 | 1.3121 | 0 | 1.3385 | 1.1229 | 6.5096 | 6.6173 | 6.5069 | 0 | 6.407 | 5.9441 | 1.3459 | 1.2555 | 1.2835 | 0 | 1.3343 | 1.3986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149655 | 258 | 140624 | 259 | 267496.488 | 650.267 | 5.4493 | 5.6057 | 5.3991 | 0 | 5.4128 | 5.9136 | 6.5096 | 6.6173 | 6.5069 | 0 | 6.407 | 5.9441 | 903000 | 2000 | 876000 | 1000 | 1772334 | 4800 | 1776000 | 1767534 | 11.4667 | 5.5561 | 1.2617 | 6.3969 | 1.3236 | 22.71% | 20.69% | 30.9482 | 44.9883 | 2.0361 | 5.3688 | 1789639 | 1772200 | 2100279.9333 | 84.38%
2022-10-25 | 2023 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 334195.71 | 6:43 | 18:08 | 10398 | 11350.4 | 11354.3 | 11343.5 | 11341.9 | 11446.2 | 11317.7 | 11549.4 | 11339.1 | 11390.8 | 11216.1 | 11368.2 | 11357 | 11325.3 | 11262 | 11427.1 | 11239.7 | 11362.4 | 11422.9 | 11388.5 | 11383.9 | 11379.9 | 11211.3 | 11310.8 | 11259.3 | 9840.7 | 11310.4 | 11340.7 | 11436.7 | 11285.4 | 11218.3 | 11427.6 | 11305 | 11468.3 | 11444.1 | 11378.6 | 11415.5 | 11273.5 | 11320.6 | 11342.8 | 11720.5 | 10982.4 | 11773 | 10746.4 | 10985.4 | 12070.3 | 10427 | 11896.7 | 10621.6 | 10326.3 | 11351.8 | 10881.2 | 11827 | 10570.4 | 11807.9 | 10673.3 | 10572.5 | 11615.8 | 10625.4 | 11796.4 | 11751.1 | 10435.1 | 11910.8 | 10916.5 | 10943.2 | 10657.6 | 11291.4 | 11581.7 | 11922.6 | 10781.2 | 11787.4 | 10397.1 | 10268 | 11824.8 | 10652.5 | 11775.4 | 10517.2 | 11898.8 | 10576.8 | 11734.1 | 10589.2 | 11499.4 | 9941.9 | 11659.1 | 10286.4 | 10752.3 | 10506.7 | 8582.3 | 11505.4 | 10919.1 | 10389 | 11801.6 | 11457.3 | 10558 | 10396.8 | 11521.6 | 10388.6 | 10626.1 | 11598.2 | 10143 | 11468.8 | 10233.1 | 11434.7 | 10542.6 | 11626.9 | 10021.1 | 11659.5 | 10572.7 | 11584.1 | 10560.4 | 11614.8 | 10725.4 | 10306 | 11402.3 | 10395.4 | 10273 | 11492.2 | 11332.3 | 11468.8 | 10504 | 11560 | 10268.7 | 11234.5 | 10554.8 | 11161.8 | 9711.2 | 11363.3 | 10223.7 | 10269.3 | 10186.5 | 10078.3 | 8747.3 | 10040.6 | 8962.5 | 10305.3 | 10235.1 | 11933.1 | 10418.9 | 11933.7 | 10811.5 | 11750.8 | 10428.6 | 10637.1 | 10162.9 | 11633.9 | 11934.2 | 11897.4 | 11851.5 | 11766.6 | 11877.8 | 10869 | 11855.3 | 11794.9 | 11943.3 | 11867.1 | 11501.7 | 11943.8 | 10244.4 | 11521.4 | 11000.1 | 30.9939 | 31.1586 | 31.0687 | 0 | 31.3217 | 31.3989 | 0 | 43.6441 | 0 | 0 | 0 | 0 | 4.5105 | 4.4256 | 4.4201 | 0 | 4.4671 | 4.3983 | 8.664 | 8.426 | 8.239 | 0 | 8.202 | 8.31 | 5.3721 | 5.5267 | 5.3164 | 0 | 5.3379 | 5.8188 | 1.2214 | 1.285 | 1.3073 | 0 | 1.325 | 1.1045 | 6.4149 | 6.5157 | 6.4147 | 0 | 6.3033 | 5.855 | 1.3396 | 1.2363 | 1.2745 | 0 | 1.3172 | 1.3811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150549 | 259 | 141492 | 261 | 269250.221 | 655.133 | 5.3721 | 5.5267 | 5.3164 | 0 | 5.3379 | 5.8188 | 6.4149 | 6.5157 | 6.4147 | 0 | 6.3033 | 5.855 | 894000 | 1000 | 868000 | 2000 | 1753733 | 4866 | 1759000 | 1748867 | 11.4167 | 5.4744 | 1.2486 | 6.3007 | 1.3097 | 22.81% | 20.79% | 31.1883 | 43.6441 | 4.4443 | 8.3682 | 1771270.5 | 1753666 | 2089246.0001 | 83.94%
2022-10-26 | 2023 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 334195.71 | 6:47 | 18:10 | 10375.9 | 11319.2 | 11306.3 | 11304.9 | 11299.8 | 11401.8 | 11281.7 | 11512.4 | 11321.2 | 11372.3 | 11191.7 | 11349.9 | 11323.3 | 11286.1 | 11259.1 | 11403.1 | 11248.8 | 11369.1 | 11399.2 | 11355.5 | 11360.5 | 11361 | 11232.4 | 11311.6 | 11235 | 9810.1 | 11272.8 | 11309.6 | 11419.9 | 11291.9 | 11237.9 | 11415.4 | 11304.9 | 11440.3 | 11402.6 | 11352.3 | 11399.2 | 11274.3 | 11317.2 | 11344.8 | 11685.4 | 10942.8 | 11752.3 | 10708.6 | 10968.1 | 12070.6 | 10427.5 | 11884.7 | 10580.1 | 10295.3 | 11310.8 | 10840.7 | 11757.6 | 10532.2 | 11760.4 | 10635.2 | 10547.4 | 11568.2 | 10602.1 | 11753.5 | 11706.5 | 10423.3 | 11833.5 | 10879.5 | 10925.6 | 10621.5 | 11268.7 | 11531.6 | 11807 | 10722.3 | 11749.1 | 10361 | 10208 | 11698.1 | 10601.5 | 11643.3 | 10478.8 | 11846.3 | 10557.1 | 11679.9 | 10546.9 | 11447.2 | 9912.6 | 11611 | 10216.5 | 10716.2 | 10506.4 | 8527.6 | 11460.9 | 10861.5 | 10352.7 | 11748.9 | 11410.3 | 10513.6 | 10353.4 | 11471.4 | 10356.6 | 10615.3 | 11561.4 | 10111.5 | 11471.2 | 10173.6 | 11397.2 | 10499.9 | 11593.8 | 9986.6 | 11629.3 | 10536.6 | 11543.6 | 10543.1 | 11603.3 | 10700 | 10283.7 | 11378.4 | 10358.6 | 10238.2 | 11451.7 | 11307.3 | 11422.8 | 10468.4 | 11512.8 | 10225.4 | 11202.3 | 10524 | 11137.1 | 9674.8 | 11320.9 | 10178.4 | 10268.2 | 10194.3 | 10063.3 | 8732 | 10053.1 | 8981.8 | 10292.1 | 10234.8 | 11891.7 | 10381.7 | 11901.4 | 10759.8 | 11721 | 10403.1 | 10608.5 | 10180.3 | 11614.5 | 11917.5 | 11870.1 | 11818.3 | 11726.3 | 11843.9 | 10842.7 | 11836 | 11791.6 | 11928 | 11852.6 | 11481.5 | 11925.7 | 10219.4 | 11506.6 | 10981.6 | 30.5514 | 30.9075 | 30.7965 | 0 | 30.5981 | 30.9428 | 0 | 44.6656 | 0 | 0 | 0 | 0 | 4.0906 | 4.3466 | 4.0888 | 0 | 4.1914 | 4.1267 | 7.609 | 7.354 | 7.796 | 0 | 7.474 | 7.044 | 5.3 | 5.5054 | 5.2714 | 0 | 5.308 | 5.8206 | 1.2003 | 1.2951 | 1.2844 | 0 | 1.3433 | 1.1151 | 6.4105 | 6.5173 | 6.3191 | 0 | 6.3361 | 5.8283 | 1.3024 | 1.2353 | 1.2397 | 0 | 1.3245 | 1.3806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151440 | 261 | 142356 | 263 | 270998.688 | 660 | 5.3 | 5.5054 | 5.2714 | 0 | 5.308 | 5.8206 | 6.4105 | 6.5173 | 6.3191 | 0 | 6.3361 | 5.8283 | 891000 | 2000 | 864000 | 2000 | 1748467 | 4867 | 1751000 | 1743600 | 11.3833 | 5.4411 | 1.2476 | 6.2823 | 1.2965 | 22.93% | 20.64% | 30.7593 | 44.6656 | 4.1688 | 7.4554 | 1766429.4 | 1748400 | 2084477.6769 | 83.88%
2022-10-27 | 2023 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 334195.71 | 6:49 | 18:09 | 10338.6 | 11274.6 | 11321.5 | 11303.3 | 11335.1 | 11383.8 | 11228.4 | 11487.8 | 11271.6 | 11331.1 | 11140 | 11296.3 | 11281.3 | 11251.3 | 11220.8 | 11354.7 | 11183.5 | 11317 | 11342.4 | 11299.2 | 11311.9 | 11307.3 | 11158.9 | 11241.2 | 11198.4 | 9776.8 | 11230.1 | 11268.2 | 11376.3 | 11220.2 | 11173.5 | 11373.1 | 11226.9 | 11406.7 | 11351.3 | 11287.9 | 11332.4 | 11190.2 | 11230.1 | 11276.8 | 11661.8 | 10892.6 | 11706.9 | 10644.6 | 10885.6 | 12068 | 10355 | 11874.6 | 10549.3 | 10263.8 | 11277.8 | 10811.5 | 11785.6 | 10480.4 | 11772.8 | 10606.2 | 10532 | 11627.6 | 10557.5 | 11833.6 | 11792.9 | 10378 | 11962.3 | 10853.9 | 10941.5 | 10593.7 | 11229.5 | 11506.3 | 11931.1 | 10708.1 | 11768.8 | 10338.4 | 10227.2 | 11813.9 | 10613.2 | 11764.7 | 10451.3 | 11901.4 | 10596.9 | 11778.1 | 10515.9 | 11427.7 | 9881.8 | 11594.4 | 10224.4 | 10685.5 | 10487.7 | 8503.2 | 11331.3 | 10813.9 | 10278.5 | 11702.6 | 11351.3 | 10453.8 | 10291.7 | 11437.5 | 10273 | 10554.4 | 11498.2 | 10055 | 11420.7 | 10066.1 | 11302.3 | 10478.4 | 11499.7 | 9934.3 | 11556.3 | 10489.8 | 11456.6 | 10472.7 | 11522.6 | 10614.8 | 10225.5 | 11316.7 | 10312.9 | 10190 | 11419.3 | 11278.8 | 11383.7 | 10446.5 | 11512.5 | 10209.5 | 11148.1 | 10478 | 11069.4 | 9656.3 | 11296.8 | 10167.7 | 10236.8 | 10166.5 | 10127.4 | 8767.3 | 10022.9 | 8960.7 | 10224.9 | 10277.5 | 11961.3 | 10385.6 | 11973.1 | 10771 | 11800.4 | 10454.2 | 10660.9 | 10254.2 | 11636.5 | 12000.3 | 11918.4 | 11875.6 | 11780.2 | 11915.3 | 10851.9 | 11905.5 | 11822.2 | 11988.6 | 11902.7 | 11494.5 | 11996 | 10222.4 | 11504 | 10972.2 | 30.516 | 30.4797 | 30.237 | 0 | 30.5528 | 30.7373 | 0 | 44.4323 | 0 | 0 | 0 | 0 | 3.6624 | 3.7259 | 3.6457 | 0 | 3.5845 | 3.546 | 7.738 | 7.13 | 7.826 | 0 | 7.513 | 8.359 | 5.2558 | 5.4679 | 5.2357 | 0 | 5.2631 | 5.8278 | 1.1772 | 1.2863 | 1.2627 | 0 | 1.3288 | 1.109 | 6.3796 | 6.493 | 6.3134 | 0 | 6.3082 | 5.8223 | 1.2864 | 1.2302 | 1.2177 | 0 | 1.316 | 1.3735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152330 | 262 | 143221 | 265 | 272746.621 | 664.867 | 5.2558 | 5.4679 | 5.2357 | 0 | 5.2631 | 5.8278 | 6.3796 | 6.493 | 6.3134 | 0 | 6.3082 | 5.8223 | 890000 | 1000 | 865000 | 2000 | 1747933 | 4867 | 1752000 | 1743066 | 11.3333 | 5.4101 | 1.2328 | 6.2633 | 1.2848 | 22.79% | 20.51% | 30.5046 | 44.4323 | 3.6329 | 7.7132 | 1763357.7 | 1747867 | 2077985.1331 | 84.11%
2022-10-28 | 2023 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 334195.71 | 6:44 | 18:07 | 10152.8 | 11165.8 | 11287 | 11256.4 | 11298.9 | 11436.9 | 11249.6 | 11483.5 | 11073.4 | 11135.2 | 10960.9 | 11102.3 | 11223.2 | 11136.4 | 11222 | 11370.5 | 11170.7 | 11277.5 | 11262.1 | 11221.2 | 11171.8 | 11171.8 | 10982.6 | 11063.3 | 10898 | 9511.8 | 11078.9 | 11027 | 11166.9 | 11087 | 11080.1 | 11199.7 | 11043.5 | 11240.3 | 11125.9 | 11120.7 | 11202.5 | 11078.6 | 11122.8 | 11098.9 | 11727.3 | 10886.6 | 11724.4 | 10628.5 | 10766.6 | 12034.7 | 10276 | 11952.1 | 10342.6 | 10179.1 | 11215.9 | 10729.8 | 11753 | 10392.5 | 11757.7 | 10397.5 | 10483 | 11613.2 | 10435.9 | 11769.5 | 11711 | 10220 | 11799.3 | 10623.7 | 10748.4 | 10204.7 | 11044.8 | 11129.1 | 11824.4 | 10315.5 | 11582.5 | 9950.8 | 10022 | 11552.6 | 10393.5 | 11508.4 | 10201.8 | 11748.1 | 10332.3 | 11495.5 | 10079.2 | 10987.3 | 9321.6 | 11195.2 | 9739.9 | 10155.7 | 9949.1 | 8111.2 | 11054.1 | 10325.1 | 9837.3 | 11305.2 | 10887 | 10030.9 | 9919.6 | 11121.1 | 9875.2 | 10111.4 | 11189.8 | 9722.9 | 11307.9 | 9876.4 | 11124.4 | 10150.3 | 11339.8 | 9661.1 | 11352.9 | 10222.6 | 11345.8 | 10277.7 | 11435.4 | 10477.3 | 9935.1 | 11107.4 | 10005.5 | 9901.8 | 11149.4 | 11039.4 | 11128.3 | 10264.5 | 11301 | 10002 | 10885.6 | 10289.4 | 10907.8 | 9485.2 | 11114.5 | 10057.7 | 10153.9 | 10094.9 | 9947 | 8673.5 | 10012.5 | 8981.2 | 10122.2 | 10056.4 | 11846.2 | 10288.4 | 11844 | 10574.2 | 11569.2 | 10133.7 | 10359.2 | 9944.9 | 11152.8 | 11568.6 | 11417.5 | 11426.9 | 11501.4 | 11734.6 | 10614.9 | 11582 | 11186.7 | 11401.5 | 11184.5 | 10826.3 | 11362.4 | 9652.5 | 11000 | 10394.6 | 30.7269 | 30.9136 | 30.8884 | 0 | 31.4356 | 30.9375 | 0 | 43.8678 | 0 | 0 | 0 | 0 | 3.0194 | 2.9358 | 2.8415 | 0 | 2.7842 | 2.6969 | 5.509 | 5.593 | 5.424 | 0 | 5.335 | 4.913 | 5.2248 | 5.2952 | 5.1742 | 0 | 5.1052 | 5.5372 | 1.1768 | 1.2121 | 1.2709 | 0 | 1.2419 | 1.0274 | 6.2515 | 6.2666 | 6.3061 | 0 | 6.0261 | 5.5622 | 1.2869 | 1.1632 | 1.2447 | 0 | 1.2401 | 1.2816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153208 | 264 | 144060 | 266 | 274458.688 | 669.733 | 5.2248 | 5.2952 | 5.1742 | 0 | 5.1052 | 5.5372 | 6.2515 | 6.2666 | 6.3061 | 0 | 6.0261 | 5.5622 | 878000 | 2000 | 839000 | 1000 | 1712067 | 4866 | 1714000 | 1707201 | 11.3833 | 5.2673 | 1.1858 | 6.0825 | 1.2433 | 22.51% | 20.44% | 30.9804 | 43.8678 | 2.8556 | 5.3548 | 1728106.3 | 1712067 | 2011514.5313 | 85.11%
2022-10-29 | 2023 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 334195.71 | 6:44 | 18:07 | 9918.3 | 10835.6 | 10937.7 | 10927.2 | 10966.2 | 11028.4 | 10838.3 | 11066.4 | 10803.1 | 10954 | 10656.3 | 10812.1 | 10808.8 | 10799.2 | 10729 | 10934.8 | 10693.3 | 10785 | 10844.2 | 10820.8 | 10688.2 | 10740 | 10460.3 | 10571.2 | 10648.9 | 9337.1 | 10783 | 10755.6 | 10797.4 | 10549.4 | 10481.5 | 10755.7 | 10628.8 | 10817.6 | 10804.8 | 10635.9 | 10656.2 | 10509.9 | 10556.7 | 10640 | 11112.8 | 10233 | 11129.6 | 9962.2 | 10330.2 | 11595.2 | 9652.4 | 11366.6 | 9848.4 | 9741.7 | 10794.4 | 10237 | 11400.1 | 10004.1 | 11308.6 | 10119.7 | 9953 | 11014.9 | 10044.3 | 11253.4 | 11246.6 | 9909.7 | 11419 | 10306 | 10331.3 | 10087.2 | 10674.5 | 11102.2 | 11421.6 | 10263.4 | 11326.5 | 9920.6 | 9719.1 | 11417.1 | 10114.4 | 11399.7 | 10049.8 | 11522 | 10148.6 | 11421.3 | 10192.8 | 11157.3 | 9535.8 | 11338 | 9875.1 | 10320.8 | 10088.7 | 8202.4 | 11127.5 | 10390.8 | 9878.6 | 11396 | 10989.8 | 10035.3 | 9865.5 | 11203.2 | 10063.8 | 10288.7 | 11321.1 | 9732 | 11190.4 | 9852 | 11038.8 | 10152.3 | 11319.9 | 9688.4 | 11385.7 | 10264.4 | 11203.6 | 10167.7 | 11272.8 | 10361.7 | 9902.7 | 10986.3 | 9948.5 | 9826 | 11106.7 | 10863.4 | 11074.7 | 10014.7 | 11147.1 | 9783.9 | 10811.9 | 10155.1 | 10721 | 9254.1 | 10900.6 | 9762.1 | 9767.1 | 9652.6 | 9553.6 | 8346.1 | 9307 | 8268 | 9527.1 | 9480.5 | 11327.2 | 9670.7 | 11225.9 | 9974.3 | 11068.8 | 9631 | 9807 | 9400 | 10817.8 | 11179.1 | 11243.6 | 11259.4 | 11208.4 | 11297.6 | 10027.5 | 11080 | 11074.3 | 11250.4 | 11060.5 | 10612.9 | 11212.9 | 9381 | 10799.6 | 10127.2 | 30.3895 | 30.4638 | 30.3072 | 0 | 30.8513 | 30.4881 | 0 | 44.0158 | 0 | 0 | 0 | 0 | 2.199 | 2.1582 | 2.1252 | 0 | 2.1961 | 2.2011 | 4.366 | 4.429 | 4.752 | 0 | 4.714 | 4.474 | 5.076 | 5.139 | 4.8754 | 0 | 5.0306 | 5.3316 | 1.1339 | 1.1795 | 1.2024 | 0 | 1.2341 | 1.0068 | 6.0695 | 6.0787 | 5.937 | 0 | 5.9646 | 5.4035 | 1.2393 | 1.1293 | 1.1788 | 0 | 1.2354 | 1.2669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154057 | 266 | 144886 | 268 | 276126.155 | 674.533 | 5.076 | 5.139 | 4.8754 | 0 | 5.0306 | 5.3316 | 6.0695 | 6.0787 | 5.937 | 0 | 5.9646 | 5.4035 | 849000 | 2000 | 826000 | 2000 | 1667467 | 4800 | 1671000 | 1662667 | 11.3833 | 5.0905 | 1.1513 | 5.8907 | 1.2099 | 22.62% | 20.54% | 30.5 | 44.0158 | 2.1759 | 4.547 | 1683677.9 | 1667400 | 1946828.2981 | 85.65%
2022-10-30 | 2023 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 334195.71 | 6:53 | 18:07 | 10246.5 | 11245.3 | 11269.2 | 11263.1 | 11268.9 | 11366.7 | 11253.5 | 11440 | 11192.4 | 11193.5 | 11054.5 | 11221.3 | 11230.9 | 11195.8 | 11130.7 | 11323.1 | 11113.6 | 11263.9 | 11323 | 11270.6 | 11277.6 | 11273.5 | 11062.5 | 11188.6 | 11154.5 | 9709.4 | 11208.6 | 11244.8 | 11352.3 | 11140.1 | 11099 | 11344.2 | 11174.5 | 11397.8 | 11334.2 | 11235.8 | 11286.7 | 11143.8 | 11191.8 | 11221 | 11748.4 | 10883.9 | 11833.7 | 10642.8 | 11157.8 | 12375.4 | 10409.3 | 11969.8 | 10287.4 | 10192.2 | 11235.2 | 10703.8 | 11784.8 | 10373.1 | 11781 | 10500.5 | 10458.7 | 11589.2 | 10478.3 | 11828.1 | 11782.5 | 10311.3 | 11917.2 | 10697.1 | 11050.1 | 10505.8 | 11173.4 | 11525.9 | 11928.3 | 10651.1 | 11778.1 | 10256.5 | 10123.3 | 11798.9 | 10510.7 | 11761.6 | 10394.9 | 11895.7 | 10475.3 | 11748.8 | 10494.9 | 11463.4 | 9741.6 | 11641.5 | 10138.9 | 10563.6 | 10542.8 | 8447.7 | 11427.6 | 10748.7 | 10268.2 | 11783.5 | 11402.3 | 10458.6 | 10283 | 11529.8 | 10295.6 | 10565.8 | 11583.4 | 10004.8 | 11554.4 | 10127.2 | 11336.1 | 10424.3 | 11588.9 | 9934.8 | 11653.2 | 10516.3 | 11537.4 | 10482.9 | 11591.9 | 10634.3 | 10187.5 | 11329.9 | 10246.8 | 10150.9 | 11440.7 | 11208.1 | 11409.9 | 10348.3 | 11479.8 | 10114.4 | 11138.8 | 10461 | 11101.6 | 9540.7 | 11237.7 | 10111.4 | 10328.2 | 10347 | 9918.1 | 8781.5 | 10016.6 | 8827.9 | 10097.5 | 10109.6 | 11929.2 | 10234.5 | 11912.8 | 10602.7 | 11693.5 | 10242.9 | 10428.8 | 10132.9 | 11526.6 | 11948 | 11839.9 | 11829.7 | 11718.2 | 11868.2 | 10694.9 | 11829.8 | 11670.7 | 11905.4 | 11811.1 | 11364.7 | 11922.3 | 10033.2 | 11359.9 | 10780.6 | 30.4153 | 30.9254 | 30.764 | 0 | 30.9618 | 30.764 | 0 | 45.0896 | 0 | 0 | 0 | 0 | 1.9677 | 1.972 | 1.8906 | 0 | 1.9518 | 1.9097 | 4.402 | 5.137 | 4.101 | 0 | 4.783 | 4.999 | 5.2303 | 5.3535 | 5.1627 | 0 | 5.1594 | 5.7039 | 1.153 | 1.2429 | 1.2626 | 0 | 1.271 | 1.0573 | 6.3587 | 6.4418 | 6.3471 | 0 | 6.2052 | 5.6918 | 1.2711 | 1.1906 | 1.2282 | 0 | 1.2679 | 1.3256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154943 | 267 | 145747 | 270 | 277867.288 | 679.467 | 5.2303 | 5.3535 | 5.1627 | 0 | 5.1594 | 5.7039 | 6.3587 | 6.4418 | 6.3471 | 0 | 6.2052 | 5.6918 | 886000 | 1000 | 861000 | 2000 | 1741133 | 4934 | 1744000 | 1736199 | 11.2333 | 5.322 | 1.1974 | 6.2089 | 1.2567 | 22.5% | 20.24% | 30.7661 | 45.0896 | 1.9384 | 4.6844 | 1757408.9 | 1741133 | 2041214.8079 | 85.3%
2022-10-31 | 2023 | 2022 | Year_1 | Year_1 | 2022-11-01 | 31 | 334195.71 | 6:50 | 18:07 | 10229 | 11227.4 | 11254.5 | 11246.7 | 11246.9 | 11357.5 | 11215.7 | 11413.7 | 11152.8 | 11153.6 | 11013 | 11181.4 | 11201.7 | 11165.2 | 11095.9 | 11302.5 | 11084.8 | 11253.2 | 11315.6 | 11253.7 | 11262.3 | 11260.7 | 11054.9 | 11174.2 | 11160.6 | 9715.4 | 11203.8 | 11250.7 | 11351.7 | 11135.3 | 11101.1 | 11351.1 | 11158.8 | 11393.6 | 11337.6 | 11235.3 | 11290.5 | 11142.8 | 11193.5 | 11227.5 | 12014.1 | 10884.8 | 11845.9 | 10640.2 | 11142.6 | 12405.8 | 10393.6 | 11982 | 10270 | 10169.4 | 11220.8 | 10682.2 | 11798.5 | 10347.9 | 11777.3 | 10499.3 | 10437.5 | 11584.4 | 10454.1 | 11826.5 | 11786.2 | 10282.1 | 11921.4 | 10639.7 | 11155.4 | 10507.3 | 11156.8 | 11565.7 | 11943.9 | 10667 | 11776.8 | 10269 | 10098.1 | 11802 | 10489.9 | 11756.8 | 10369.3 | 11896.2 | 10448.6 | 11731 | 10502 | 11496.3 | 9717.8 | 11668.9 | 10140.4 | 10543.6 | 10558.4 | 8454 | 11398 | 10766.7 | 10282.3 | 11807.8 | 11419.3 | 10461.7 | 10296.8 | 11524.2 | 10277.6 | 10546.3 | 11611.2 | 10061.6 | 11615.3 | 10136.9 | 11332.8 | 10458.3 | 11586.1 | 9926.4 | 11645.4 | 10496 | 11521.3 | 10451.9 | 11586.2 | 10608.7 | 10226.1 | 11397 | 10317.7 | 10200.1 | 11484 | 11269.6 | 11453.1 | 10377 | 11552.8 | 10164.2 | 11180.4 | 10494.2 | 11129.3 | 9605.8 | 11285.9 | 10125 | 10332.9 | 10376.3 | 9950.2 | 8810.6 | 10283.5 | 9104.1 | 10121.5 | 10188.6 | 11949.6 | 10219.3 | 11901.8 | 10598.3 | 11713.9 | 10248.5 | 10455.6 | 10197.4 | 11496.6 | 11944.3 | 11845.5 | 11847.5 | 11735.6 | 11878.9 | 10668.8 | 11826.6 | 11681.4 | 11872.8 | 11791.8 | 11348 | 11916.4 | 10011.9 | 11197.1 | 10783.6 | 31.3899 | 31.4426 | 31.4511 | 0 | 32.0298 | 31.5061 | 0 | 45.5741 | 0 | 0 | 0 | 0 | 2.3283 | 2.2739 | 2.323 | 0 | 2.3209 | 2.3177 | 5.455 | 5.201 | 5.532 | 0 | 5.306 | 5.763 | 5.2085 | 5.3628 | 5.1489 | 0 | 5.1705 | 5.6979 | 1.1606 | 1.2477 | 1.2747 | 0 | 1.279 | 1.1231 | 6.3394 | 6.4633 | 6.37 | 0 | 6.192 | 5.6934 | 1.2792 | 1.1936 | 1.2406 | 0 | 1.2673 | 1.4086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155830 | 269 | 146610 | 272 | 279609.955 | 684.467 | 5.2085 | 5.3628 | 5.1489 | 0 | 5.1705 | 5.6979 | 6.3394 | 6.4633 | 6.37 | 0 | 6.192 | 5.6934 | 887000 | 2000 | 863000 | 2000 | 1742667 | 5000 | 1746000 | 1737667 | 11.2833 | 5.3177 | 1.217 | 6.2116 | 1.2779 | 22.89% | 20.57% | 31.5639 | 45.5741 | 2.3128 | 5.4514 | 1758467.6 | 1742534 | 2040365.7489 | 85.4%
2022-11-01 | 2023 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 334195.71 | 6:54 | 18:05 | 10191.4 | 11173 | 11205.4 | 11203.9 | 11187.4 | 11308.1 | 11151.3 | 11337.1 | 11108.9 | 11101 | 10976.6 | 11141.2 | 11164.4 | 11124.5 | 11031.6 | 11260.7 | 11028.7 | 11201.5 | 11279.4 | 11214.4 | 11221.6 | 11220.7 | 11019.4 | 11139 | 11123.5 | 9683.5 | 11170.6 | 11214 | 11305.4 | 11082 | 11059.6 | 11306.2 | 11117.8 | 11363.4 | 11301 | 11192.7 | 11251.9 | 11107.9 | 11158.5 | 11186.9 | 11929 | 10794.2 | 11753.4 | 10557.4 | 11075.7 | 12303.3 | 10320 | 11882.7 | 10247.5 | 10145 | 11189.4 | 10652.6 | 11753.8 | 10307.1 | 11731 | 10468 | 10406.1 | 11540.6 | 10424.5 | 11785.9 | 11740.1 | 10253.2 | 11840.7 | 10602.6 | 11115.7 | 10478.2 | 11124.2 | 11531.8 | 11898.8 | 10647.6 | 11740.9 | 10260.6 | 10084.6 | 11771 | 10469 | 11719 | 10342.7 | 11855.4 | 10420.6 | 11689.6 | 10522.9 | 11486 | 9696.1 | 11640.9 | 10128 | 10525.2 | 10529.7 | 8444.2 | 11333 | 10761.9 | 10249.6 | 11754 | 11382.3 | 10433.8 | 10259.5 | 11475.1 | 10231 | 10512.9 | 11559 | 10040.9 | 11560.7 | 10102.1 | 11286.5 | 10422.7 | 11525.5 | 9889.5 | 11594.4 | 10455.4 | 11462.7 | 10410.5 | 11531.1 | 10567 | 10207.7 | 11369.1 | 10304.1 | 10163.7 | 11430.7 | 11241.4 | 11401.6 | 10330.1 | 11512 | 10117.5 | 11141.3 | 10448.9 | 11061.8 | 9556.5 | 11225.2 | 10062.2 | 10271.5 | 10292.3 | 10038.1 | 8756.6 | 10257.4 | 9133.1 | 10224.6 | 10232.7 | 11860.4 | 10162.7 | 11829.8 | 10547.4 | 11674.3 | 10245.3 | 10435.4 | 10218 | 11437.2 | 11863.6 | 11768.9 | 11769.2 | 11709.7 | 11789.4 | 10615.6 | 11749.5 | 11726.9 | 11848.2 | 11746.3 | 11317.8 | 11843.9 | 9961.2 | 11210 | 10757.6 | 31.5246 | 31.7666 | 31.6708 | 0 | 32.5876 | 31.7657 | 0 | 45.0654 | 0 | 0 | 0 | 0 | 3.08 | 3.0622 | 3.1191 | 0 | 3.134 | 3.0667 | 5.771 | 5.342 | 5.507 | 0 | 5.408 | 6.005 | 5.181 | 5.3483 | 5.0913 | 0 | 5.1282 | 5.7717 | 1.1426 | 1.2455 | 1.2559 | 0 | 1.2826 | 1.148 | 6.3279 | 6.4455 | 6.2937 | 0 | 6.1818 | 5.5723 | 1.2617 | 1.1928 | 1.2202 | 0 | 1.2717 | 1.415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156713 | 271 | 147469 | 274 | 281346.222 | 689.467 | 5.181 | 5.3483 | 5.0913 | 0 | 5.1282 | 5.7717 | 6.3279 | 6.4455 | 6.2937 | 0 | 6.1818 | 5.5723 | 883000 | 2000 | 859000 | 2000 | 1736267 | 5000 | 1738000 | 1731267 | 11.1833 | 5.3041 | 1.2149 | 6.1642 | 1.2723 | 22.91% | 20.64% | 31.8631 | 45.0654 | 3.0924 | 5.6066 | 1752112.1 | 1736200 | 1975098.1394 | 87.9%
2022-11-02 | 2023 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 334195.71 | 6:56 | 18:03 | 10022.7 | 10970.7 | 11010.2 | 11008.6 | 10977.6 | 11122.2 | 10938.2 | 11132.3 | 10906.5 | 10899 | 10772.1 | 10938.3 | 10962.3 | 10926.3 | 10823 | 11069.4 | 10826.9 | 11014.7 | 11090.3 | 11012.8 | 10986.4 | 11023.3 | 10834.8 | 10954.7 | 10930 | 9512.2 | 10971.3 | 11021.3 | 11126.2 | 10882.8 | 10870.4 | 11132.6 | 10908.7 | 11184.7 | 11113.9 | 11002.4 | 11071.3 | 10923.7 | 10979 | 10986.8 | 11800.5 | 10584.1 | 11614.3 | 10356.6 | 10857.9 | 12211.6 | 10131.5 | 11763.3 | 10070.3 | 9962.3 | 10996.1 | 10465 | 11607.1 | 10114.4 | 11600.7 | 10291.6 | 10223.3 | 11369.9 | 10252.5 | 11652 | 11603.9 | 10080.9 | 11716.3 | 10400.7 | 10908.8 | 10291.6 | 10930.6 | 11352.7 | 11781.9 | 10449.8 | 11605.8 | 10074.6 | 9902.4 | 11630.2 | 10280.2 | 11578.7 | 10161.8 | 11724 | 10228.1 | 11542.2 | 10319 | 11293.2 | 9515 | 11472.6 | 9934.6 | 10321.4 | 10321.2 | 8277.1 | 11121 | 10548.5 | 10049.8 | 11597.8 | 11183.3 | 10225.4 | 10050.1 | 11297.9 | 10062.2 | 10342.9 | 11410 | 9862.4 | 11395.8 | 9920.1 | 11081.4 | 10239 | 11375.4 | 9712.4 | 11452.5 | 10270.4 | 11288.8 | 10239.4 | 11369.7 | 10379.4 | 10029.1 | 11212.8 | 10130.7 | 10005.2 | 11283 | 11044.8 | 11229.6 | 10153.6 | 11339 | 9935.1 | 10953 | 10259.8 | 10898.8 | 9364.3 | 11015.4 | 9913.1 | 10096 | 10096.9 | 9874.5 | 8612.6 | 10048 | 8947.4 | 10141.5 | 10101.6 | 11747.2 | 10160.7 | 11756 | 10396.3 | 11612.9 | 10127 | 10308.2 | 10180.7 | 11311.3 | 11782.2 | 11640.6 | 11641.8 | 11588.9 | 11689.3 | 10475.3 | 11651.5 | 11658.3 | 11815.9 | 11772.7 | 11231.8 | 11793.8 | 9871.2 | 11137 | 10607.5 | 30.5505 | 31.366 | 31.4277 | 0 | 32.0897 | 31.3182 | 0 | 45.259 | 0 | 0 | 0 | 0 | 2.6493 | 2.6698 | 2.6484 | 0 | 2.6742 | 2.5654 | 5.663 | 5.331 | 5.426 | 0 | 5.479 | 5.123 | 5.0676 | 5.2423 | 4.9854 | 0 | 5.0596 | 5.71 | 1.1122 | 1.2118 | 1.2265 | 0 | 1.2543 | 1.1077 | 6.1058 | 6.1988 | 6.1493 | 0 | 5.9396 | 5.4975 | 1.2287 | 1.1624 | 1.1906 | 0 | 1.2415 | 1.3653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157581 | 273 | 148317 | 275 | 283056.155 | 694.333 | 5.0676 | 5.2423 | 4.9854 | 0 | 5.0596 | 5.71 | 6.1058 | 6.1988 | 6.1493 | 0 | 5.9396 | 5.4975 | 868000 | 2000 | 848000 | 1000 | 1709933 | 4866 | 1713000 | 1705067 | 11.1167 | 5.2129 | 1.1825 | 5.9782 | 1.2377 | 22.68% | 20.7% | 31.3504 | 45.259 | 2.6414 | 5.4044 | 1725584.4 | 1709733 | 1917770.9756 | 89.15%
2022-11-03 | 2023 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 334195.71 | 6:48 | 18:04 | 10257.1 | 11219.8 | 11291 | 11276 | 11329.3 | 11392.5 | 11166.7 | 11324.4 | 11148.2 | 11118.3 | 11018.9 | 11180.6 | 11222.1 | 11165.7 | 11068 | 11322.5 | 11080.4 | 11270.7 | 11324.1 | 11255.7 | 11262.6 | 11262.6 | 11093.4 | 11208.5 | 11178.3 | 9737.9 | 11219.8 | 11265.2 | 11342.3 | 11113.9 | 11122.6 | 11352.4 | 11160.2 | 11408.3 | 11350.9 | 11244.4 | 11305 | 11172 | 11218.5 | 11242 | 11946.8 | 10835 | 11764.3 | 10599.8 | 11113.9 | 12318.5 | 10399.7 | 11911.7 | 10318.2 | 10210.3 | 11254.7 | 10711.9 | 11783.6 | 10344.1 | 11764.8 | 10535.7 | 10461 | 11573.2 | 10505.4 | 11819.8 | 11781.2 | 10326.5 | 11860.8 | 10638.2 | 11176.8 | 10546.2 | 11195.9 | 11550.6 | 11923.4 | 10691.4 | 11773.1 | 10306.2 | 10141.7 | 11803.5 | 10525.5 | 11753 | 10407.2 | 11875.4 | 10470.6 | 11714.3 | 10537.7 | 11491.7 | 9839.9 | 11666.9 | 10167 | 10595.4 | 10542.2 | 8465.7 | 11307.8 | 10789 | 10295.2 | 11772.1 | 11410.4 | 10455.1 | 10280.3 | 11589 | 10409.7 | 10689.8 | 11677.5 | 10086.7 | 11668.1 | 10153.8 | 11356.8 | 10500.1 | 11558.4 | 9954.6 | 11633.2 | 10502.6 | 11508.5 | 10480.5 | 11594.5 | 10616.5 | 10256.4 | 11502.3 | 10382.1 | 10281.3 | 11504.4 | 11371.9 | 11474.1 | 10475.8 | 11602 | 10239.3 | 11196.4 | 10510.4 | 11174.3 | 9681.2 | 11343.5 | 10202.2 | 10357.7 | 10473.1 | 10084.8 | 8809.6 | 10269.2 | 9137.7 | 10392 | 10379.8 | 11903.8 | 10422.5 | 11920.4 | 10664.7 | 11802.7 | 10396.8 | 10592.2 | 10467.7 | 11562.8 | 11940 | 11823.9 | 11811.2 | 11775.4 | 11863.7 | 10727.3 | 11829.3 | 11821.6 | 11964.1 | 11944.2 | 11471.9 | 11948.2 | 10126.1 | 11406.5 | 10867.5 | 32.8474 | 33.0519 | 32.9862 | 0 | 33.3893 | 33.3405 | 0 | 45.4922 | 0 | 0 | 0 | 0 | 4.0911 | 4.1293 | 4.3683 | 0 | 4.3123 | 4.2859 | 6.734 | 7.309 | 7.052 | 7.146 | 7.183 | 6.932 | 5.1544 | 5.3753 | 5.0867 | 4.9796 | 5.2504 | 5.86 | 1.1302 | 1.2275 | 1.2608 | 0 | 1.2971 | 1.0983 | 5.9666 | 5.7044 | 6.2758 | 6.3927 | 5.4783 | 5.8269 | 1.2459 | 1.1962 | 1.2184 | 0 | 1.2512 | 1.3573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158468 | 274 | 149184 | 277 | 284803.222 | 699.2 | 5.1544 | 5.3753 | 5.0867 | 4.9796 | 5.2504 | 5.86 | 5.9666 | 5.7044 | 6.2758 | 6.3927 | 5.4783 | 5.8269 | 887000 | 1000 | 867000 | 2000 | 1747067 | 4867 | 1751000 | 1742200 | 11.2667 | 5.2844 | 1.2028 | 5.9408 | 1.2538 | 22.76% | 21.11% | 33.1231 | 45.4922 | 4.2374 | 7.0593 | 1763079.4 | 1747067 | 1910020.1775 | 91.47%
2022-11-04 | 2023 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 334195.71 | 6:46 | 18:04 | 10558.8 | 11464.1 | 11597.2 | 11584 | 11633.8 | 11714.9 | 11488.4 | 11628.4 | 11438.5 | 11391.8 | 11317.3 | 11468 | 11529.4 | 11457.3 | 11371.2 | 11618.7 | 11382.5 | 11572.8 | 11610.3 | 11543.9 | 11475 | 11546.4 | 11395.3 | 11500 | 11475.6 | 10030.7 | 11509.1 | 11553.5 | 11626.6 | 11399.8 | 11419.6 | 11641.6 | 11448.7 | 11699.3 | 11644.4 | 11537.4 | 11603.2 | 11468.7 | 11512.8 | 11527.5 | 12215.9 | 11136.4 | 11946.6 | 10890.4 | 11424.9 | 12602.2 | 10704.6 | 12097 | 10779.7 | 10518.3 | 11555.8 | 11027.7 | 12076.1 | 10661.6 | 12059.8 | 10849.3 | 10769.1 | 11867 | 10817.3 | 12118.1 | 12078.8 | 10636.3 | 12147.6 | 10939.9 | 11474.4 | 10865.5 | 11499 | 11841.6 | 12206.4 | 10934.8 | 12062.3 | 10598.5 | 10434.4 | 12089.2 | 10762.5 | 12039 | 10709.9 | 12149.9 | 10777.7 | 11994.7 | 10860.3 | 11763.4 | 10702.8 | 12057.5 | 10714.7 | 11293.5 | 10460 | 8933.6 | 11680.7 | 11242.7 | 10619.1 | 12135.9 | 11760.4 | 10824.6 | 10642.5 | 11952 | 10719.9 | 11023.5 | 11971 | 10393.7 | 11952.8 | 10448.9 | 11704.2 | 10815.9 | 11761.5 | 10239.5 | 11907.5 | 10796.1 | 11780.5 | 10770.8 | 11869.6 | 10901.9 | 10569.6 | 11815.4 | 10701.6 | 10603.5 | 11796.7 | 11687.8 | 11778.2 | 10810.5 | 11921.1 | 10570.7 | 11484.8 | 10818.7 | 11462.2 | 9997.4 | 11668.3 | 10527.7 | 10672.1 | 10797.5 | 10415.6 | 9078.7 | 10582.6 | 9429.1 | 10665.6 | 10652.2 | 12214.6 | 10761.7 | 12184.5 | 11029.5 | 12098.9 | 10628.3 | 10897.1 | 10757 | 11911.4 | 12291.6 | 12157.5 | 12138.3 | 12110.1 | 12184.8 | 11113.1 | 12185.6 | 12115.6 | 12277.6 | 12219.1 | 11826.5 | 12303.5 | 10490.7 | 11714.2 | 11219.8 | 32.1895 | 32.2964 | 32.5516 | 0 | 32.7959 | 32.7225 | 0 | 45.672 | 0 | 0 | 0 | 0 | 3.809 | 3.866 | 3.964 | 0 | 3.9428 | 3.7617 | 9.235 | 8.351 | 8.709 | 8.245 | 8.833 | 8.735 | 5.2926 | 5.5129 | 5.2124 | 0 | 5.5105 | 6.0308 | 1.1746 | 1.282 | 1.3022 | 0 | 1.3494 | 1.1269 | 6.4986 | 6.4471 | 6.4994 | 6.8544 | 6.116 | 6.4338 | 1.3125 | 1.2351 | 1.2576 | 0 | 1.3184 | 1.4031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159378 | 276 | 150077 | 279 | 286599.889 | 704.2 | 5.2926 | 5.5129 | 5.2124 | 0 | 5.5105 | 6.0308 | 6.4986 | 6.4471 | 6.4994 | 6.8544 | 6.116 | 6.4338 | 910000 | 2000 | 893000 | 2000 | 1796667 | 5000 | 1799000 | 1791667 | 11.3 | 5.5118 | 1.247 | 6.4749 | 1.3054 | 22.62% | 20.16% | 32.5112 | 45.672 | 3.8687 | 8.6847 | 1812786.3 | 1796600 | 2069096.9525 | 86.83%
2022-11-05 | 2023 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 334195.71 | 6:48 | 18:01 | 10590.3 | 9298.9 | 11503.4 | 11765.5 | 10795.3 | 10802.5 | 11764.6 | 11829.9 | 11508.5 | 11254.1 | 11244.5 | 10465.8 | 11686.1 | 11649.8 | 11564 | 11819 | 11065.5 | 11752.2 | 11751.5 | 11612.7 | 8961.8 | 11691.2 | 11612 | 11572.7 | 11605.5 | 9995.7 | 11641.4 | 11681.6 | 11786.1 | 11317 | 10951.5 | 11160.2 | 11558.9 | 11596.6 | 11831.3 | 11525 | 11645.9 | 11647.9 | 11498.7 | 11708.4 | 12171.2 | 11327.5 | 9113.4 | 11080.6 | 11618.6 | 12656.5 | 10695.7 | 8974.3 | 11048.6 | 10747.6 | 11760.9 | 11251.3 | 12204.4 | 10861.7 | 10723.6 | 11075.8 | 10992 | 11938.7 | 11043.7 | 12178.7 | 12112.5 | 10864.9 | 12155.1 | 11125.6 | 11629.4 | 10648.1 | 11708.2 | 12013 | 12303.2 | 9293.6 | 12208.1 | 10841 | 10521.3 | 12236.7 | 8406.4 | 12144 | 10944.9 | 11692.9 | 11005.4 | 11949.6 | 10893.7 | 11881.7 | 8419.5 | 12250 | 11041.7 | 11569.9 | 7725.2 | 9215.3 | 11819.4 | 11425.6 | 10755.1 | 12296.7 | 11974 | 11112.2 | 10944.4 | 11771.9 | 9214.1 | 11205.1 | 12068.4 | 10371.3 | 12053 | 9647.2 | 11870.9 | 11007.6 | 8975.1 | 10416.6 | 11696.7 | 10989.6 | 11928.9 | 10962.7 | 9145 | 11100.2 | 10686 | 11959.9 | 9597.5 | 10783.4 | 11899.4 | 10586.9 | 10794.6 | 10307.8 | 12035 | 10778.3 | 9923.1 | 11012.7 | 9080.4 | 10201.4 | 11844.4 | 10736.4 | 10875.1 | 10165.7 | 9073.2 | 8756.8 | 10464 | 9590.7 | 10744.8 | 10857.3 | 11421.6 | 8907.5 | 9733.3 | 11221.2 | 12146.1 | 7838.1 | 10903.5 | 10955.6 | 11990 | 11766.6 | 12259.1 | 12111.5 | 12225.2 | 12278.4 | 11322.6 | 12023.9 | 12175.1 | 9997.9 | 9074.5 | 11905 | 12274.2 | 10684.3 | 11893.4 | 11347.8 | 31.9014 | 32.7107 | 32.6895 | 0 | 32.8896 | 32.989 | 0 | 44.0999 | 0 | 0 | 0 | 0 | 5.6595 | 5.5516 | 5.5863 | 0 | 5.6064 | 5.3771 | 11.069 | 10.28 | 10.566 | 0 | 10.503 | 10.18 | 5.3462 | 5.5557 | 5.2592 | 5.1544 | 5.5578 | 6.1001 | 1.2067 | 1.3003 | 1.3321 | 0 | 1.3776 | 1.1469 | 6.5754 | 6.5089 | 6.5751 | 6.9585 | 6.1632 | 6.4995 | 1.346 | 1.257 | 1.2842 | 0 | 1.3446 | 1.4294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160276 | 278 | 150942 | 280 | 288355.156 | 706.8 | 5.3462 | 5.5557 | 5.2592 | 5.1544 | 5.5578 | 6.1001 | 6.5754 | 6.5089 | 6.5751 | 6.9585 | 6.1632 | 6.4995 | 898000 | 2000 | 865000 | 1000 | 1755267 | 2600 | 1760000 | 1752667 | 11.2167 | 5.4956 | 1.2727 | 6.5468 | 1.3323 | 23.16% | 20.35% | 32.636 | 44.0999 | 5.5562 | 10.5196 | 1770942.1 | 1754867 | 2106786.0994 | 83.3%
2022-11-06 | 2023 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 334195.71 | 6:50 | 17:55 | 7886.3 | 8560.4 | 8629.9 | 8620.6 | 8645.3 | 8710.6 | 8617.2 | 8723.8 | 8548.5 | 8611.4 | 8418 | 8539.9 | 8593.3 | 8534 | 8451.1 | 8674.6 | 8457.5 | 8631.3 | 8647.7 | 8588.5 | 8536.5 | 8597.4 | 8495.8 | 8564.4 | 8542.6 | 7465.7 | 8561.3 | 8593.3 | 8662.9 | 8475.6 | 8525.1 | 8697.6 | 8496 | 8709.4 | 8693.8 | 8581.3 | 8619.1 | 8520.8 | 8578.7 | 8602.1 | 9139.4 | 8258.5 | 8915.7 | 8058.1 | 8478.1 | 9511.2 | 7859.9 | 9111 | 8060.1 | 7842.9 | 8605.6 | 8199.2 | 9051.7 | 7928.8 | 9056.4 | 8110.9 | 8020.4 | 8857.5 | 8062.2 | 9071.2 | 9041.2 | 7931.5 | 9070.3 | 8091.5 | 8554.5 | 8092.7 | 8572.6 | 8878 | 9187.3 | 8205.8 | 9051.9 | 7915.9 | 7795.2 | 9083.6 | 8017.5 | 9040.7 | 7994 | 9147.1 | 8055.4 | 9019.8 | 8135.3 | 8804.6 | 7979.2 | 9132.1 | 8049.8 | 8464 | 7988.2 | 6735.7 | 8750.7 | 8478.1 | 7925.3 | 9118.2 | 8824 | 8119.7 | 8032.9 | 8931.5 | 7902.2 | 8236.4 | 9002.2 | 7785.4 | 9000.7 | 7836.1 | 8787.3 | 8076.1 | 8836.4 | 7655.2 | 8948.3 | 8065.5 | 8833.3 | 8051.2 | 8822.4 | 8163 | 7936.5 | 8845.4 | 7982.7 | 7914.1 | 8882.4 | 8749.8 | 8833.9 | 8086.6 | 8931.8 | 7878.7 | 8593.7 | 8074.3 | 8545.4 | 7451.8 | 8714.8 | 7863.1 | 7999.8 | 8113.1 | 7839.3 | 6829.2 | 7985.2 | 7115.2 | 7916.6 | 7900.2 | 9188 | 7925.3 | 9214.5 | 8184.5 | 9048 | 7856.9 | 8062.6 | 7968.9 | 8873.6 | 9205.6 | 9109.2 | 9111.6 | 9071.7 | 9142.6 | 8258.9 | 9129 | 9087.8 | 9133.6 | 9136.2 | 8783.9 | 9206.2 | 7770.4 | 8728.4 | 8314.2 | 30.5532 | 30.6575 | 30.5998 | 0 | 31.2021 | 30.9022 | 0 | 39.8721 | 0 | 0 | 0 | 0 | 3.3634 | 3.3451 | 3.4609 | 0 | 3.5004 | 3.4059 | 7.984 | 7.703 | 7.702 | 7.703 | 7.818 | 7.438 | 4.0897 | 4.1949 | 4.0242 | 3.9341 | 4.1764 | 4.2589 | 0.94772 | 0.95428 | 1.0126 | 0 | 1.0001 | 0.85701 | 4.6288 | 4.5754 | 4.6487 | 4.8071 | 4.4457 | 4.6975 | 1.0271 | 0.93106 | 1.0042 | 0 | 0.9881 | 1.0629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160955 | 279 | 151610 | 282 | 289698.223 | 713.867 | 4.0897 | 4.1949 | 4.0242 | 3.9341 | 4.1764 | 4.2589 | 4.6288 | 4.5754 | 4.6487 | 4.8071 | 4.4457 | 4.6975 | 679000 | 1000 | 668000 | 2000 | 1343067 | 7067 | 1344000 | 1336000 | 11.0833 | 4.113 | 0.95434 | 4.6339 | 1.0027 | 23.2% | 21.64% | 30.783 | 39.8721 | 3.4151 | 7.7247 | 1354520.8 | 1343000 | 1513110.6135 | 88.76%
2022-11-07 | 2023 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 334195.71 | 7:05 | 17:59 | 8364.4 | 9162.5 | 9164.8 | 9155.3 | 9154.6 | 9243.3 | 9130.3 | 9513.8 | 9165.3 | 9247.1 | 9010.7 | 9176.5 | 9127.8 | 9098.9 | 8940.5 | 9194.5 | 8959 | 9129.4 | 9169.3 | 9104.4 | 9076.6 | 9087.5 | 8925.2 | 9015.4 | 9020.7 | 7856.7 | 9060.3 | 9091.6 | 9136.4 | 8908.6 | 8951 | 9164.3 | 8948.1 | 9216.4 | 9193.3 | 9050.9 | 9083.7 | 8968.5 | 9033.2 | 9048.7 | 9660.8 | 8589.1 | 9460.6 | 8354.3 | 8880.1 | 10176.1 | 8336.1 | 9675.2 | 8495.2 | 8262.8 | 9100.4 | 8641.9 | 9606.1 | 8361 | 9603.3 | 8534.5 | 8452.6 | 9399.8 | 8506.1 | 9667.6 | 9661.2 | 8381.2 | 9717.9 | 8558.1 | 9034 | 8536.7 | 9080 | 9417.5 | 9809 | 8663.1 | 9631.9 | 8344.7 | 8234.2 | 9657.1 | 8533.9 | 9617.3 | 8429.9 | 9738.3 | 8493.6 | 9587.2 | 8578.9 | 9326.7 | 8419.5 | 9719.1 | 8489.1 | 8947.3 | 8537.9 | 7089.5 | 9250.5 | 8931.8 | 8319 | 9636.3 | 9299.7 | 8517 | 8409.5 | 9422.2 | 8357.3 | 8643.5 | 9513.4 | 8154.7 | 9512.2 | 8209.3 | 9230.3 | 8456.8 | 9355 | 8005.7 | 9396 | 8420.4 | 9245 | 8382.5 | 9319.6 | 8498.5 | 8316.2 | 9312.6 | 8355.8 | 8275.2 | 9335.2 | 9143.2 | 9257.8 | 8395 | 9331.4 | 8167.2 | 8980.4 | 8402.9 | 8934.3 | 7708.4 | 9065.1 | 8132.7 | 8408.2 | 8586.3 | 8204 | 7161.7 | 8348.5 | 7448.4 | 8404.2 | 8413 | 9825.3 | 8477.3 | 9869.7 | 8697.5 | 9718.1 | 8446.8 | 8591.9 | 8503.1 | 9453.9 | 9864.5 | 9701.6 | 9700.5 | 9662.3 | 9757.3 | 8743.4 | 9745.8 | 9765.8 | 9936.2 | 9946.1 | 9430.3 | 9898.3 | 8255.4 | 9259.7 | 8843.1 | 28.2176 | 28.2946 | 28.0135 | 0 | 28.2109 | 28.4551 | 0 | 41.1888 | 0 | 0 | 0 | 0 | 2.5351 | 2.3711 | 2.4673 | 0 | 2.4644 | 2.4618 | 5.98 | 6.337 | 6.593 | 6.005 | 6.056 | 5.74 | 4.2443 | 4.3606 | 4.1641 | 4.0949 | 4.3187 | 4.6413 | 0.95554 | 1.0299 | 1.0391 | 0 | 1.0692 | 0.92323 | 5.0075 | 4.9399 | 4.9746 | 5.2367 | 4.7401 | 5.0182 | 1.0538 | 0.99779 | 1.0193 | 0 | 1.0579 | 1.1465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161675 | 281 | 152316 | 284 | 291118.423 | 716.667 | 4.2443 | 4.3606 | 4.1641 | 4.0949 | 4.3187 | 4.6413 | 5.0075 | 4.9399 | 4.9746 | 5.2367 | 4.7401 | 5.0182 | 720000 | 2000 | 706000 | 2000 | 1420200 | 2800 | 1422000 | 1417400 | 10.9 | 4.304 | 1.0034 | 4.9862 | 1.0551 | 23.31% | 21.16% | 28.2383 | 41.1888 | 2.4599 | 6.1185 | 1432715.7 | 1420067 | 1628171.1184 | 87.22%
2022-11-08 | 2023 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 334195.71 | 7:01 | 18:00 | 8801.3 | 9672.1 | 9656.7 | 9631 | 9656.6 | 9761.5 | 9670.4 | 10079.9 | 9679.2 | 9659.7 | 9588.9 | 9734.5 | 9700.1 | 9694.5 | 9587 | 9740.2 | 9604.7 | 9705.7 | 9779.3 | 9712.9 | 9654.7 | 9662.7 | 9514.6 | 9614.8 | 9580.4 | 8346.6 | 9623.2 | 9657.2 | 9744.1 | 9492 | 9513 | 9757.8 | 9636 | 9827.3 | 9790.9 | 9710.5 | 9775 | 9631.7 | 9703.1 | 9640.7 | 10331.3 | 9249 | 10095.3 | 8999 | 9454.9 | 10697.9 | 8841.4 | 10300.9 | 9009.2 | 8769.6 | 9634.5 | 9173.6 | 10166.6 | 8863.9 | 10193.1 | 9056.6 | 8987.8 | 10011.5 | 9017.5 | 10235.6 | 10214.3 | 8869.2 | 10273.4 | 9056.1 | 9556.2 | 9064 | 9606.6 | 10031.3 | 10348.9 | 9195.6 | 10185.4 | 8846.8 | 8688.5 | 10209.2 | 9006.1 | 10160.5 | 8900.5 | 10239.3 | 8920 | 10073.7 | 9086.7 | 9859 | 8911.2 | 10323.1 | 9021.9 | 9521 | 9139.1 | 7572.3 | 9816.3 | 9541.8 | 8891.3 | 10280.8 | 9899.9 | 9055.9 | 8949.1 | 9999.8 | 8822.2 | 9137.7 | 10061 | 8637 | 10126.9 | 8728.7 | 9846.7 | 8987.7 | 10023.6 | 8547.5 | 10070.4 | 9008.6 | 9909.2 | 8974.6 | 9952.6 | 9132.5 | 8828.9 | 9891.7 | 8883.3 | 8787.5 | 9918.2 | 9708.1 | 9836.2 | 8952.3 | 9926.6 | 8744.1 | 9603.7 | 9031.6 | 9590.9 | 8286.1 | 9706 | 8700.2 | 8986.6 | 9184.8 | 8809.7 | 7642.9 | 8920.4 | 7949.9 | 8909.6 | 8906.8 | 10383.8 | 8955.8 | 10427.6 | 9198.9 | 10246.7 | 8904.3 | 9061.3 | 8959.9 | 9913.1 | 10344.1 | 10176.3 | 10195.5 | 10185.3 | 10296.5 | 9218.8 | 10257.1 | 10101.1 | 10277.9 | 10229.2 | 9751.6 | 10275.8 | 8607.5 | 9693.3 | 9240.1 | 28.7895 | 28.6557 | 28.2515 | 0 | 28.6857 | 28.7249 | 0 | 41.1667 | 0 | 0 | 0 | 0 | 3.0426 | 2.98 | 2.8794 | 0 | 2.9456 | 2.8034 | 7.06 | 7.289 | 7.079 | 7.06 | 6.734 | 7.145 | 4.5134 | 4.6173 | 4.3898 | 4.3082 | 4.5541 | 4.8793 | 1.0245 | 1.0881 | 1.1113 | 0 | 1.1274 | 0.95948 | 5.3498 | 5.262 | 5.3029 | 5.5723 | 5.0026 | 5.2602 | 1.1287 | 1.0526 | 1.088 | 0 | 1.111 | 1.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162439 | 283 | 153065 | 286 | 292624.49 | 721.667 | 4.5134 | 4.6173 | 4.3898 | 4.3082 | 4.5541 | 4.8793 | 5.3498 | 5.262 | 5.3029 | 5.5723 | 5.0026 | 5.2602 | 764000 | 2000 | 749000 | 2000 | 1506067 | 5000 | 1509000 | 1501067 | 10.9833 | 4.5437 | 1.0621 | 5.2916 | 1.1141 | 23.38% | 21.05% | 28.6215 | 41.1667 | 2.9302 | 7.0612 | 1519971 | 1506000 | 1725781.0451 | 87.26%
2022-11-09 | 2023 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 334195.71 | 6:54 | 17:53 | 8774.4 | 9607.9 | 9613.6 | 9617.3 | 9593.8 | 9685.8 | 9529.7 | 9924.7 | 9625.2 | 9633.6 | 9487.6 | 9657.3 | 9574.8 | 9579.9 | 9506 | 9647.3 | 9515.4 | 9616.7 | 9659.1 | 9592.8 | 9554.4 | 9545.4 | 9412.7 | 9508 | 9464.1 | 8231.5 | 9489 | 9535.3 | 9619.6 | 9379.3 | 9440.9 | 9655.2 | 9577.1 | 9695.8 | 9654.3 | 9582.7 | 9671.3 | 9529.2 | 9618.9 | 9563.3 | 10353.6 | 9261.8 | 10151.3 | 9070.6 | 9487.2 | 10718.2 | 8832.1 | 10331.4 | 8905.9 | 8656.2 | 9528.8 | 9067.6 | 10068.1 | 8766.7 | 10056.6 | 8930.6 | 8880.4 | 9909.4 | 8914.6 | 10115.9 | 10098 | 8772.5 | 10426.3 | 9172.4 | 9482 | 8944.7 | 9493.8 | 9901.1 | 10251.1 | 9088.9 | 10070 | 8740 | 8599.8 | 10094 | 8914.8 | 10047.4 | 8807.2 | 10169.9 | 8867.4 | 10018.6 | 9029.8 | 9739 | 8776.8 | 10207.4 | 8889.3 | 9367.2 | 8984 | 7442.5 | 9716.9 | 9406.8 | 8812.8 | 10211.1 | 9788.4 | 8925.9 | 8806.2 | 9942.5 | 8832.9 | 9144 | 10075.5 | 8640.8 | 10001.8 | 8676.8 | 9750.4 | 8938.2 | 9909.3 | 8471.9 | 9952.5 | 8927.6 | 9806.1 | 8913.9 | 9920.9 | 9044.8 | 8806.4 | 9862.7 | 8876.4 | 8776.6 | 9899.1 | 9730.5 | 9820 | 8968.2 | 9947.8 | 8739.2 | 9548.4 | 8954 | 9496.7 | 8280.7 | 9698.4 | 8681.1 | 8929.1 | 9091.6 | 8873.6 | 7727.4 | 8836.7 | 7856.9 | 8886.7 | 8840.8 | 10311.5 | 8886.4 | 10366.5 | 9122.2 | 10140.3 | 8785.9 | 8955.9 | 8854.9 | 9939.3 | 10387.8 | 10195.4 | 10199.9 | 10154.8 | 10244.9 | 9184.8 | 10255.4 | 10246.4 | 10393.6 | 10382.2 | 9869.6 | 10394 | 8660.5 | 9748.9 | 9285.3 | 27.7016 | 27.8108 | 27.6163 | 0 | 28.066 | 27.8107 | 0 | 40.2895 | 0 | 0 | 63.292 | 0 | 2.8206 | 2.8568 | 2.7975 | 0 | 2.814 | 2.7924 | 6.125 | 5.724 | 6.784 | 6.489 | 6.016 | 5.803 | 4.3994 | 4.5093 | 4.3038 | 4.1788 | 4.5062 | 4.8599 | 1.0068 | 1.0554 | 1.1005 | 0 | 1.1092 | 0.93906 | 5.2469 | 5.1683 | 5.2595 | 5.5037 | 4.9456 | 5.2244 | 1.1119 | 1.0196 | 1.0751 | 0 | 1.0915 | 1.1676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163196 | 285 | 153810 | 287 | 294121.423 | 726.4 | 4.3994 | 4.5093 | 4.3038 | 4.1788 | 4.5062 | 4.8599 | 5.2469 | 5.1683 | 5.2595 | 5.5037 | 4.9456 | 5.2244 | 757000 | 2000 | 745000 | 1000 | 1496933 | 4733 | 1499000 | 1492200 | 10.9833 | 4.4596 | 1.0422 | 5.2247 | 1.0931 | 23.37% | 20.92% | 27.8011 | 51.7908 | 2.8162 | 6.1568 | 1510287.2 | 1506000 | 1725781.0451 | 87.26%
2022-11-10 | 2023 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 334195.71 | 6:54 | 17:59 | 9171.5 | 10011.8 | 10032.5 | 10030 | 10002 | 10125 | 9947.3 | 10378.3 | 10056.6 | 10088.5 | 9928.4 | 10095.2 | 10067.4 | 10049 | 9973.1 | 10141.9 | 9983.7 | 10091.3 | 10165.2 | 10135.2 | 10117.7 | 10102.7 | 9903.8 | 10032.8 | 9975.4 | 8693.4 | 10016.8 | 10044.7 | 10170.6 | 9979.2 | 9920.7 | 10156 | 10111.9 | 10245 | 10186.4 | 10101.2 | 10182.8 | 10037.5 | 10132.9 | 10075.3 | 10935.4 | 9770.6 | 10712.9 | 9549.7 | 9979.8 | 11253.7 | 9318 | 10912.3 | 9368.8 | 9103.2 | 10044 | 9609.9 | 10627.8 | 9367.4 | 10609.9 | 9417.4 | 9335.6 | 10417.9 | 9360.4 | 10630.4 | 10593.8 | 9205.4 | 10941.1 | 9643.9 | 9993 | 9398.1 | 9985.2 | 10411.2 | 10768.1 | 9558.5 | 10585.6 | 9201.5 | 9034.1 | 10613.1 | 9359.4 | 10567.7 | 9262.7 | 10679.2 | 9320.8 | 10546 | 9527.2 | 10307.2 | 9243.5 | 10749.9 | 9369.7 | 9856 | 9473 | 7712.5 | 10270.4 | 9928.3 | 9305.4 | 10778 | 10328.7 | 9412.2 | 9270.9 | 10533.5 | 9328.8 | 9609.2 | 10577 | 9061.5 | 10557.9 | 9150.4 | 10290.5 | 9419.7 | 10459.8 | 8933 | 10508.6 | 9423.6 | 10370.7 | 9428.6 | 10479.2 | 9571 | 9252.2 | 10360.2 | 9350.5 | 9219.6 | 10396.7 | 10216.1 | 10339.6 | 9413.1 | 10469.1 | 9216 | 10060.2 | 9444.8 | 10024 | 8733 | 10225.7 | 9156.9 | 9347.6 | 9494.9 | 9330.4 | 8106.2 | 9217.9 | 8214.9 | 9341.5 | 9308.3 | 10832.4 | 9350.5 | 10879.7 | 9588.6 | 10647.4 | 9217.2 | 9390.5 | 9315.6 | 10398.1 | 10863.9 | 10687.4 | 10691.9 | 10661.7 | 10767.9 | 9641.3 | 10742.1 | 10721.2 | 10861.6 | 10837.6 | 10299 | 10857.4 | 9067.2 | 10195 | 9706.3 | 27.4196 | 27.451 | 27.1494 | 0 | 27.5024 | 27.4098 | 0 | 38.396 | 0 | 0 | 0 | 0 | 2.9828 | 2.9337 | 3.0304 | 3.082 | 2.9539 | 2.8474 | 5.5517 | 6.4183 | 5.1983 | 5.9883 | 5.4167 | 5.3117 | 4.5271 | 4.6835 | 4.4494 | 4.3151 | 4.6344 | 5.0352 | 1.0416 | 1.0977 | 1.1401 | 0 | 1.1598 | 0.97605 | 5.4531 | 5.3944 | 5.4727 | 5.7288 | 5.1366 | 5.3822 | 1.1515 | 1.0617 | 1.1104 | 1.5268 | 1.1448 | 1.2106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163706 | 287 | 154304 | 289 | 295696.023 | 733.4 | 4.5271 | 4.6835 | 4.4494 | 4.3151 | 4.6344 | 5.0352 | 5.4531 | 5.3944 | 5.4727 | 5.7288 | 5.1366 | 5.3822 | 510000 | 2000 | 494000 | 2000 | 1574600 | 7000 | 1000000 | 1567600 | 11.0833 | 4.6075 | 1.0831 | 5.428 | 1.201 | 23.51% | 22.13% | 27.3865 | 38.396 | 2.9717 | 5.6475 | 1588351 | 1574533 | 1780254.3012 | 88.44%
2022-11-11 | 2023 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 334195.71 | 7:03 | 17:58 | 8331.9 | 9101.1 | 9110.2 | 9101.5 | 9087.8 | 9175.9 | 9033.7 | 9385.1 | 9136 | 9162.3 | 8979 | 9146.5 | 9048.5 | 9048.8 | 8957.1 | 9119.9 | 8951.8 | 9054.9 | 9131.9 | 9095.5 | 9127.4 | 9100.5 | 8952.2 | 9057 | 9004.6 | 7809.6 | 8980.8 | 9042.2 | 9204.3 | 9049 | 8990.7 | 9205 | 9117.8 | 9268.4 | 9198.7 | 9154.3 | 9227.4 | 9087.4 | 9155.1 | 9080.8 | 9913 | 8889.6 | 9737 | 8676.5 | 9153.8 | 10363.9 | 8434 | 9858.8 | 8399.4 | 8170.6 | 8988.8 | 8594.6 | 9512.7 | 8403.1 | 9486.7 | 8439.7 | 8362.8 | 9334.2 | 8433.4 | 9559.6 | 9565 | 8309.2 | 9853.4 | 8700 | 8967 | 8452.6 | 8977.9 | 9372.6 | 9683.6 | 8612.5 | 9532.3 | 8294.2 | 8138.8 | 9570 | 8432.2 | 9532.8 | 8353.9 | 9635.7 | 8425.4 | 9532.4 | 8583.7 | 9294.3 | 8337.2 | 9680.7 | 8430.8 | 8864.5 | 8512.9 | 7045.7 | 9328.7 | 8915.2 | 8336.5 | 9657.8 | 9272.3 | 8457.9 | 8336.2 | 9446.8 | 8376.7 | 8639.1 | 9534.2 | 8173 | 9521.2 | 8267.8 | 9297.9 | 8507.9 | 9455.3 | 8075 | 9497.2 | 8512.8 | 9369.3 | 8517.4 | 9465.2 | 8655.4 | 8345.4 | 9349.4 | 8429.6 | 8312.5 | 9410.7 | 9238.1 | 9347.1 | 8547.8 | 9494.7 | 8368.2 | 9105 | 8545.9 | 9066.8 | 7930 | 9298.1 | 8350.6 | 8528.2 | 8662.3 | 8513.6 | 7361.7 | 8399.7 | 7478.4 | 8433.3 | 8403.3 | 9756.1 | 8447.6 | 9801.3 | 8646.6 | 9623.8 | 8322.5 | 8474.3 | 8406.5 | 9321.3 | 9755.9 | 9548 | 9582 | 9555.9 | 9659.9 | 8672.6 | 9657.5 | 9612.9 | 9727.5 | 9744.8 | 9251.4 | 9748.2 | 8140.3 | 9100.7 | 8687.5 | 26.2283 | 26.8846 | 26.4946 | 0 | 26.8748 | 26.6345 | 0 | 38.3746 | 0 | 0 | 0 | 0 | 1.729 | 2.0195 | 2.083 | 2.0305 | 2.0083 | 1.878 | 3.7317 | 4.7983 | 4.7533 | 4.02 | 4.1117 | 4.0367 | 4.1928 | 4.3356 | 4.1456 | 3.9661 | 4.2698 | 4.547 | 0.97284 | 1.0471 | 1.0665 | 0 | 1.094 | 0.92437 | 4.9833 | 4.9383 | 5.0089 | 5.1537 | 4.7089 | 4.8968 | 1.0725 | 1.0137 | 1.0435 | 1.4565 | 1.0804 | 1.1448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164712 | 288 | 155301 | 291 | 297116.757 | 738.2 | 4.1928 | 4.3356 | 4.1456 | 3.9661 | 4.2698 | 4.547 | 4.9833 | 4.9383 | 5.0089 | 5.1537 | 4.7089 | 4.8968 | 1006000 | 1000 | 997000 | 2000 | 1420734 | 4800 | 2000000 | 1415934 | 10.9167 | 4.2428 | 1.021 | 4.9483 | 1.1352 | 24.06% | 22.94% | 26.6233 | 38.3746 | 1.958 | 4.2419 | 1433158.4 | 1420667 | 1627783.395 | 87.28%
2022-11-12 | 2023 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 334195.71 | 7:02 | 17:59 | 9221.5 | 10033.7 | 10043.2 | 10054.4 | 9996.5 | 10136.4 | 9939.5 | 10333.2 | 10091.7 | 10121.4 | 9929.1 | 10104.5 | 10042.6 | 10033.9 | 9930.1 | 10115.4 | 9967.4 | 10093.1 | 10163.1 | 10118.9 | 10146.6 | 10117 | 9991.5 | 10085 | 10034.9 | 8713.4 | 10002.6 | 10070.1 | 10257.6 | 10088.8 | 9987.1 | 10252.4 | 10122.6 | 10283.1 | 10257.4 | 10170.4 | 10245.9 | 10079.1 | 10143.4 | 10066.9 | 10969.2 | 9818.5 | 10772.9 | 9614.3 | 10160.6 | 11523.8 | 9352.7 | 10973.2 | 9371.4 | 9113.5 | 10036.5 | 9622.4 | 10604.6 | 9337.7 | 10627.6 | 9422.3 | 9373.9 | 10466.7 | 9380.4 | 10681.1 | 10658.4 | 9240.3 | 11011.8 | 9698.4 | 10074 | 9497 | 10085 | 10523 | 10867 | 9666 | 10704 | 9297 | 9100.1 | 10727.9 | 9438 | 10669 | 9352.6 | 10773 | 9406.3 | 10645.8 | 9632.3 | 10386.1 | 9324.5 | 10866.6 | 9447.2 | 9922.6 | 9521.2 | 7892.5 | 10420.7 | 9937.9 | 9309.1 | 10762.2 | 10319.7 | 9404.9 | 9263.3 | 10521 | 9332.4 | 9683.7 | 10662.2 | 9145.9 | 10622.2 | 9259.6 | 10374.9 | 9510.4 | 10545.6 | 9028.7 | 10602.9 | 9537.9 | 10446.3 | 9521 | 10576.1 | 9686.2 | 9325.4 | 10425.1 | 9438.6 | 9311.2 | 10509.9 | 10321.7 | 10459.9 | 9535.5 | 10621.6 | 9338.3 | 10182.6 | 9600.8 | 10174.8 | 8872.5 | 10375.8 | 9323.6 | 9453.7 | 9482.1 | 9467.6 | 8130.5 | 9287.3 | 8252.5 | 9347.1 | 9318.1 | 10933.2 | 9428.6 | 11003 | 9678.7 | 10720.6 | 9279.5 | 9440.8 | 9349.9 | 10500.2 | 10991.1 | 10796.9 | 10834.9 | 10812.2 | 10877.6 | 9759.6 | 10891.5 | 10707 | 10853 | 10829.5 | 10302.5 | 10896.3 | 9118.4 | 10218.3 | 9762.1 | 26.8482 | 26.9667 | 26.7886 | 0 | 27.0715 | 26.9548 | 0 | 40.4953 | 0 | 0 | 0 | 0 | 1.5328 | 1.6356 | 1.8566 | 1.7465 | 1.7514 | 1.7254 | 4.2917 | 4.125 | 5.0567 | 4.625 | 4.3267 | 4.0567 | 4.5316 | 4.731 | 4.4759 | 4.3622 | 4.6912 | 5.1647 | 1.0451 | 1.1207 | 1.1581 | 0 | 1.1818 | 1.0372 | 5.5046 | 5.4928 | 5.5644 | 5.8661 | 5.2179 | 5.5061 | 1.1605 | 1.0797 | 1.1291 | 1.3632 | 1.1632 | 1.2889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165513 | 290 | 156091 | 293 | 298701.357 | 743 | 4.5316 | 4.731 | 4.4759 | 4.3622 | 4.6912 | 5.1647 | 5.5046 | 5.4928 | 5.5644 | 5.8661 | 5.2179 | 5.5061 | 801000 | 2000 | 790000 | 2000 | 1584600 | 4800 | 1587000 | 1579800 | 10.95 | 4.6594 | 1.1086 | 5.5253 | 1.1974 | 23.79% | 21.67% | 26.926 | 40.4953 | 1.7081 | 4.4136 | 1598252.7 | 1584600 | 1804806.0137 | 87.8%
2022-11-13 | 2023 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 334195.71 | 7:03 | 17:58 | 9614.5 | 10465.9 | 10473.5 | 10488.9 | 10407.1 | 10571 | 10349.2 | 10778.6 | 10506.2 | 10512 | 10367.7 | 10540.4 | 10511.5 | 10486 | 10372.1 | 10586.8 | 10417.2 | 10544.7 | 10625.5 | 10591.4 | 10581.6 | 10562.2 | 10391.9 | 10514.9 | 10430.1 | 9071.4 | 10448 | 10499.8 | 10634.7 | 10435.4 | 10370.4 | 10622.7 | 10532.2 | 10672.8 | 10633.2 | 10545.7 | 10633.9 | 10491.4 | 10585 | 10516.6 | 11375.2 | 10192.4 | 11156.6 | 9959.8 | 10556 | 11826.6 | 9685.3 | 11360.9 | 9784.9 | 9518.1 | 10485 | 10026 | 11087.5 | 9775.5 | 11049.5 | 9810.1 | 9749.6 | 10878 | 9785.2 | 11098.5 | 11054.2 | 9631.2 | 11330.6 | 10081.6 | 10419.5 | 9832.2 | 10428.6 | 10881.8 | 11252 | 10001.7 | 11081.3 | 9631.7 | 9440.4 | 11115.7 | 9803.2 | 11067.1 | 9710.9 | 11190 | 9770 | 11044.4 | 9970.3 | 10756.9 | 9646 | 11244.2 | 9768.8 | 10263.3 | 9836.8 | 8173.6 | 10819.6 | 10317.4 | 9671.6 | 11180.9 | 10740.7 | 9823.7 | 9696.8 | 10977.6 | 9700.3 | 10044.4 | 11036.6 | 9453.1 | 10996.7 | 9567.3 | 10731.7 | 9830.7 | 10908.4 | 9330.1 | 10963.3 | 9848.1 | 10809 | 9825.2 | 10908.8 | 9978.6 | 9642.9 | 10799.2 | 9735.6 | 9621.9 | 10826.6 | 10632.1 | 10770 | 9803.4 | 10918.3 | 9590.4 | 10483 | 9876 | 10448.6 | 9090.3 | 10640.5 | 9549 | 9715.8 | 9758.1 | 9684.2 | 8342.1 | 9595.8 | 8585 | 9680.2 | 9638.9 | 11300.9 | 9757.3 | 11340.1 | 10008.3 | 11078.4 | 9579.6 | 9766.4 | 9660.1 | 10896.5 | 11358.4 | 11192.7 | 11185.4 | 11152.7 | 11226.7 | 10060.9 | 11231 | 11170.6 | 11350.9 | 11319.8 | 10771.9 | 11364.5 | 9496.4 | 10651.2 | 10178.6 | 27.7842 | 27.9856 | 28.0878 | 0 | 27.9567 | 28.0348 | 0 | 41.984 | 0 | 0 | 0 | 0 | 2.1334 | 2.5341 | 2.4146 | 0 | 2.4077 | 2.3379 | 4.992 | 5.27 | 5.811 | 5.018 | 5.353 | 5.384 | 4.7041 | 4.8867 | 4.612 | 4.4793 | 4.8362 | 5.379 | 1.0657 | 1.1474 | 1.1724 | 0 | 1.2068 | 1.017 | 5.7815 | 5.7324 | 5.7963 | 6.1105 | 5.4134 | 5.7077 | 1.192 | 1.1016 | 1.1391 | 0 | 1.186 | 1.264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166345 | 291 | 156907 | 294 | 300343.69 | 747.8 | 4.7041 | 4.8867 | 4.612 | 4.4793 | 4.8362 | 5.379 | 5.7815 | 5.7324 | 5.7963 | 6.1105 | 5.4134 | 5.7077 | 832000 | 1000 | 816000 | 1000 | 1642333 | 4800 | 1646000 | 1637533 | 10.9167 | 4.8162 | 1.1218 | 5.757 | 1.1765 | 23.29% | 20.44% | 27.9698 | 41.984 | 2.3655 | 5.3047 | 1657660.6 | 1642200 | 1873426.1579 | 87.66%
2022-11-14 | 2023 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 334195.71 | 6:56 | 17:57 | 9373.7 | 10199.3 | 10256.7 | 10247.4 | 10254.4 | 10338.5 | 10079.8 | 10503.9 | 10236.9 | 10224.1 | 10108.8 | 10275.3 | 10256.4 | 10225 | 10109.5 | 10325.5 | 10169.7 | 10305.8 | 10364.2 | 10326.5 | 10315.1 | 10304.8 | 10154.5 | 10262.5 | 10176.6 | 8849.6 | 10187.6 | 10240.5 | 10373.7 | 10188.4 | 10126.8 | 10371.8 | 10274 | 10418.9 | 10370.1 | 10282.6 | 10375.1 | 10239.6 | 10337.1 | 10279.3 | 11028.5 | 9886.8 | 10867.7 | 9701.6 | 10278 | 11493.5 | 9579 | 10997.1 | 9549.3 | 9281.5 | 10232 | 9782.6 | 10811.7 | 9523.3 | 10786.4 | 9587.4 | 9516.6 | 10602.5 | 9549.5 | 10797.7 | 10751.7 | 9370.9 | 11012.9 | 9814.8 | 10175.8 | 9610.5 | 10185.2 | 10625.1 | 10975 | 9767.5 | 10810.7 | 9401.9 | 9213.8 | 10840.9 | 9567.3 | 10779.8 | 9466.8 | 10899 | 9524 | 10746.5 | 9710 | 10483.9 | 9368.4 | 10932.9 | 9514.9 | 9994.3 | 9610.2 | 7978.3 | 10550.6 | 10089 | 9467.9 | 10941.5 | 10563.6 | 9671.2 | 9561.1 | 10722.6 | 9475.5 | 9791.4 | 10750.8 | 9204.1 | 10703.8 | 9325 | 10459.7 | 9605.8 | 10631.7 | 9106.5 | 10719 | 9630.5 | 10598.3 | 9618.1 | 10671.6 | 9779 | 9382.9 | 10536.2 | 9474.1 | 9384.9 | 10566.8 | 10375.4 | 10510.1 | 9574.3 | 10651.5 | 9370.2 | 10250.3 | 9661 | 10207.9 | 8888.5 | 10393.8 | 9322.7 | 9476.9 | 9510.8 | 9438.8 | 8147.8 | 9360.3 | 8365.2 | 9429.2 | 9377.6 | 10970.6 | 9511.6 | 11002.7 | 9746.1 | 10747.8 | 9300.7 | 9499.9 | 9382.7 | 10593.1 | 11014.2 | 10859.8 | 10863.7 | 10829.7 | 10918.2 | 9804.1 | 10918.6 | 10806.1 | 10961.1 | 10932.2 | 10455.3 | 11017.2 | 9233.2 | 10349.4 | 9897.7 | 27.5948 | 27.712 | 27.4427 | 0 | 27.5559 | 27.8004 | 0 | 39.664 | 0 | 0 | 0 | 0 | 4.0991 | 4.2642 | 4.1856 | 4.1206 | 4.2085 | 4.2851 | 8.1917 | 8.0217 | 8.3283 | 8.5917 | 8.4067 | 8.34 | 4.5511 | 4.7422 | 4.4573 | 4.3408 | 4.6975 | 5.1877 | 1.0381 | 1.1179 | 1.142 | 0 | 1.1913 | 1.0467 | 5.5703 | 5.5408 | 5.5676 | 5.8872 | 5.251 | 5.5121 | 1.1547 | 1.0772 | 1.1094 | 1.2944 | 1.1679 | 1.3006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167157 | 293 | 157703 | 296 | 301944.69 | 752.733 | 4.5511 | 4.7422 | 4.4573 | 4.3408 | 4.6975 | 5.1877 | 5.5703 | 5.5408 | 5.5676 | 5.8872 | 5.251 | 5.5121 | 812000 | 2000 | 796000 | 2000 | 1601000 | 4933 | 1604000 | 1596067 | 11.0167 | 4.6628 | 1.1072 | 5.5548 | 1.184 | 23.75% | 21.32% | 27.6212 | 39.664 | 4.1938 | 8.3133 | 1616206.9 | 1600934 | 1826688.9586 | 87.64%
2022-11-15 | 2023 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 334195.71 | 6:58 | 17:57 | 8308 | 9159.8 | 9215.1 | 9182.1 | 9234 | 9297.6 | 9181.6 | 9441.3 | 9124.4 | 9084.2 | 8999.3 | 9148.8 | 9161.7 | 9110.4 | 9051.7 | 9246.8 | 9093.6 | 9214.8 | 9254.7 | 9222.3 | 9224.4 | 9209.6 | 9079.8 | 9179 | 9092.6 | 7918.9 | 9107.6 | 9144.6 | 9272.6 | 9109.9 | 9048.5 | 9264 | 9166.1 | 9311 | 9281.4 | 9182.5 | 9254.1 | 9136.7 | 9228.6 | 9171.3 | 9908.8 | 8863 | 9781.6 | 8703.3 | 9218.4 | 10443.1 | 8577.1 | 9903.2 | 8536.1 | 8291.2 | 9145.4 | 8739.5 | 9676.6 | 8502.1 | 9661.9 | 8588.7 | 8488.1 | 9482.6 | 8523.4 | 9672.3 | 9639.2 | 8385.6 | 9865.3 | 8667.1 | 9049.6 | 8538.9 | 9058.7 | 9447.4 | 9786.9 | 8678.2 | 9605.9 | 8357.1 | 8205.1 | 9640.5 | 8496.7 | 9591.7 | 8399.8 | 9695.3 | 8443.5 | 9550.3 | 8674.5 | 9387.3 | 8393.9 | 9807 | 8512 | 8901.9 | 8624.7 | 7129.4 | 9411.4 | 9044.5 | 8432.6 | 9795.3 | 9436.8 | 8630.4 | 8525.4 | 9521.6 | 8437.5 | 8739.5 | 9609.4 | 8224 | 9526.2 | 8317.2 | 9300.6 | 8571.1 | 9484.9 | 8111.6 | 9560.9 | 8585.7 | 9438.1 | 8558.3 | 9501.6 | 8719.9 | 8387.7 | 9418.7 | 8474.3 | 8387 | 9463.1 | 9290.8 | 9414 | 8596.5 | 9545 | 8402.3 | 9166.4 | 8625.3 | 9112.6 | 7968.1 | 9336.9 | 8371.5 | 8500.8 | 8612.7 | 8486 | 7375.3 | 8470 | 7550.7 | 8441.8 | 8412.8 | 9863.2 | 8510.9 | 9913.1 | 8729.4 | 9638.8 | 8330.7 | 8497.3 | 8424.4 | 9483.6 | 9899.1 | 9723 | 9738.9 | 9712.5 | 9804.8 | 8785.4 | 9791.4 | 9684 | 9836.9 | 9826.6 | 9332.6 | 9878.2 | 8246.6 | 9231.3 | 8814.3 | 22.9527 | 22.7988 | 22.5471 | 0 | 22.7996 | 22.9079 | 0 | 31.9495 | 0 | 0 | 0 | 0 | 3.6114 | 3.7539 | 3.8396 | 3.8459 | 3.6984 | 3.5433 | 5.6067 | 5.7817 | 5.9583 | 5.6583 | 6.115 | 5.3683 | 4.0676 | 4.2163 | 4.0035 | 3.8634 | 4.1534 | 4.5007 | 0.95577 | 1.0104 | 1.0308 | 0 | 1.0687 | 0.90642 | 4.8443 | 4.8135 | 4.8689 | 5.0612 | 4.5922 | 4.8275 | 1.0512 | 0.98077 | 1.013 | 4.108 | 1.0531 | 1.1238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167882 | 295 | 158416 | 298 | 303377.224 | 757.533 | 4.0676 | 4.2163 | 4.0035 | 3.8634 | 4.1534 | 4.5007 | 4.8443 | 4.8135 | 4.8689 | 5.0612 | 4.5922 | 4.8275 | 725000 | 2000 | 713000 | 2000 | 1432534 | 4800 | 1434000 | 1427734 | 10.9833 | 4.1341 | 0.99442 | 4.8346 | 1.555 | 24.05% | 32.16% | 22.8012 | 31.9495 | 3.7154 | 5.7481 | 1445347.1 | 1432467 | 1626036.6493 | 88.1%
2022-11-16 | 2023 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 334195.71 | 6:57 | 17:56 | 9150 | 10075.5 | 10038.5 | 10015 | 10038.6 | 10125 | 10051.5 | 10473 | 10040.1 | 10135.6 | 9869.6 | 10018.6 | 10008.9 | 9962 | 9849.8 | 10081.6 | 9919.9 | 10054.6 | 10102.1 | 10074.5 | 10052.9 | 10044 | 9890.2 | 9997.8 | 9916.2 | 8631.2 | 9951.2 | 9985.6 | 10119.9 | 9929.5 | 9867.4 | 10103.1 | 9928.9 | 10096.3 | 10119.1 | 10019.7 | 10115.1 | 9984.6 | 10067.8 | 9998.3 | 10769.1 | 9603.5 | 10614 | 9427.5 | 9998.6 | 11342.3 | 9334 | 10760.8 | 9329.6 | 9059.4 | 9990.2 | 9544.2 | 10553.1 | 9307.2 | 10546.2 | 9347.3 | 9284.5 | 10371.7 | 9316.1 | 10588.7 | 10561.7 | 9169 | 10833.8 | 9530.4 | 9902.2 | 9357.6 | 9935.6 | 10348.6 | 10728.2 | 9507.6 | 10535.7 | 9153.8 | 8992.3 | 10578.9 | 9326.9 | 10533.7 | 9231.6 | 10647.4 | 9254.2 | 10483 | 9498 | 10267.9 | 9155.2 | 10714 | 9290 | 9672 | 9425.6 | 7788.5 | 10217.7 | 9820.1 | 9211.3 | 10690.5 | 10295.3 | 9413.1 | 9294.7 | 10406.4 | 9221.5 | 9552 | 10499.6 | 8996.1 | 10442.4 | 9091.4 | 10187.4 | 9362.2 | 10376.8 | 8883.2 | 10456 | 9395.3 | 10313.9 | 9352.7 | 10369.4 | 9519.1 | 9157.5 | 10281.7 | 9158 | 9139.4 | 10336 | 10110.4 | 10269.2 | 9330.7 | 10381.4 | 9125.8 | 10013 | 9415.6 | 9971.1 | 8636.5 | 10127 | 9069.3 | 9277.4 | 9421.4 | 9191.5 | 8020.4 | 9227.2 | 8200 | 9107.2 | 9133.8 | 10732.5 | 9254.9 | 10773.5 | 9493.6 | 10493 | 9109.8 | 9291.8 | 9155.1 | 10314 | 10758.6 | 10575.2 | 10585.2 | 10562.5 | 10661.4 | 9543.8 | 10630.5 | 10583.9 | 10730.7 | 10706.2 | 10166 | 10761.5 | 8976.8 | 10061.6 | 9612.7 | 24.899 | 24.6558 | 24.3735 | 0 | 24.8418 | 24.5113 | 0 | 38.5386 | 0 | 0 | 0 | 0 | 1.2701 | 1.7827 | 1.8285 | 1.7739 | 1.7533 | 1.8236 | 3.78 | 4.3083 | 3.935 | 3.6817 | 4.0683 | 4.305 | 4.4231 | 4.5917 | 4.3177 | 4.2173 | 4.539 | 5.0063 | 1.003 | 1.0675 | 1.0917 | 0 | 1.1254 | 0.94669 | 5.4047 | 5.3634 | 5.4138 | 5.7257 | 5.0626 | 5.3236 | 1.1212 | 1.0267 | 1.0725 | 2.0189 | 1.1055 | 1.1744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168675 | 297 | 159193 | 300 | 304940.49 | 762.333 | 4.4231 | 4.5917 | 4.3177 | 4.2173 | 4.539 | 5.0063 | 5.4047 | 5.3634 | 5.4138 | 5.7257 | 5.0626 | 5.3236 | 793000 | 2000 | 777000 | 2000 | 1563266 | 4800 | 1566000 | 1558466 | 10.9833 | 4.5159 | 1.0469 | 5.3823 | 1.2532 | 23.18% | 23.28% | 24.6563 | 38.5386 | 1.7054 | 4.0131 | 1577419 | 1563200 | 1773903.265 | 88.12%
2022-11-17 | 2023 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 334195.71 | 6:57 | 17:57 | 9873.5 | 10858.7 | 10813.3 | 10788.3 | 10798.7 | 10901.1 | 10820.7 | 11291.5 | 10838.6 | 10902.9 | 10670.2 | 10835.2 | 10779.8 | 10765.9 | 10702.1 | 10848 | 10713.6 | 10808.4 | 10890.1 | 10867.1 | 10873.9 | 10882.5 | 10644.1 | 10778.1 | 10689.2 | 9306.2 | 10730.2 | 10768.5 | 10930.5 | 10738.2 | 10615.1 | 10874.1 | 10795.8 | 10971.2 | 10902.7 | 10801.4 | 10901.1 | 10765.3 | 10857 | 10781.1 | 11623.2 | 10347.2 | 11445.8 | 10175.7 | 10753.6 | 12101 | 10062 | 11578.8 | 10045.2 | 9754.3 | 10756.4 | 10291.5 | 11365.4 | 10051 | 11347.6 | 10050.3 | 10002.1 | 11156.5 | 10033.7 | 11403.3 | 11368 | 9880.1 | 11605 | 10261.5 | 10663.3 | 10069.8 | 10691.8 | 11140.8 | 11542.4 | 10237.2 | 11355.1 | 9846.4 | 9674.6 | 11400.1 | 10043.7 | 11334.6 | 9942 | 11463.2 | 9975.8 | 11286 | 10225.1 | 11041.1 | 9897.9 | 11547.3 | 10031.3 | 10501.5 | 10143.3 | 8422.5 | 11087.1 | 10603.1 | 9941.7 | 11545.1 | 11099 | 10143.4 | 10002.3 | 11225 | 9934.4 | 10311.5 | 11337.1 | 9717.3 | 11260.5 | 9820.6 | 10993.4 | 10099.3 | 11197.6 | 9578.1 | 11277.5 | 10132.7 | 11118.1 | 10075.6 | 11161 | 10240.7 | 9893.8 | 11095.5 | 9999.1 | 9892.9 | 11134.9 | 10892.1 | 11064.5 | 10042.7 | 11174.3 | 9825.7 | 10776.5 | 10141.4 | 10725.7 | 9328 | 10893.3 | 9758.7 | 10009.8 | 10164.6 | 9848.3 | 8644.6 | 9897.3 | 8799.8 | 9860.2 | 9831.3 | 11592.3 | 9984.4 | 11626.8 | 10247 | 11350.5 | 9853.1 | 10064.5 | 9862.1 | 11146.6 | 11622.9 | 11415.6 | 11434.7 | 11410.1 | 11505.7 | 10318.2 | 11478.4 | 11459.4 | 11601.2 | 11527.2 | 10960.7 | 11601.9 | 9708.9 | 10869.6 | 10412.1 | 25.8713 | 26.0861 | 25.8595 | 0 | 26.1929 | 26.0612 | 0 | 41.1316 | 0 | 0 | 0 | 0 | 1.5511 | 1.8971 | 1.966 | 1.9431 | 1.7923 | 1.7591 | 3.985 | 4.9067 | 4.9 | 4.2517 | 4.1417 | 4.595 | 4.7416 | 4.9273 | 4.6159 | 4.5077 | 4.8906 | 5.473 | 1.0776 | 1.1583 | 1.1724 | 0 | 1.2225 | 1.0246 | 5.8825 | 5.8349 | 5.8847 | 6.2469 | 5.5058 | 5.7793 | 1.214 | 1.1096 | 1.1481 | 1.4815 | 1.1995 | 1.2723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169530 | 298 | 160031 | 301 | 306626.091 | 767.2 | 4.7416 | 4.9273 | 4.6159 | 4.5077 | 4.8906 | 5.473 | 5.8825 | 5.8349 | 5.8847 | 6.2469 | 5.5058 | 5.7793 | 855000 | 1000 | 838000 | 1000 | 1685601 | 4867 | 1691000 | 1680734 | 11 | 4.8593 | 1.1311 | 5.8557 | 1.2375 | 23.28% | 21.13% | 26.0142 | 41.1316 | 1.8181 | 4.4633 | 1700960.9 | 1685601 | 1910088.8031 | 88.25%
2022-11-18 | 2023 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 334195.71 | 6:58 | 17:53 | 9857.3 | 10825.9 | 10776.9 | 10757.9 | 10758.5 | 10873.4 | 10775.9 | 11235.8 | 10804.6 | 10864.5 | 10659.3 | 10838.5 | 10756.9 | 10759.6 | 10702.1 | 10834.9 | 10700.1 | 10805.9 | 10870.3 | 10841.1 | 10845.8 | 10853.9 | 10626.6 | 10757.6 | 10659.5 | 9285.1 | 10698.6 | 10742 | 10910.4 | 10735.6 | 10598.5 | 10847.1 | 10753.7 | 10922.8 | 10869.2 | 10768.4 | 10860.4 | 10734.3 | 10827.4 | 10753.2 | 11545.3 | 10303 | 11369.5 | 10136.8 | 10721.8 | 12049.1 | 10026.4 | 11502.5 | 10020.3 | 9729 | 10730.6 | 10283.5 | 11337 | 10026.2 | 11298.2 | 10030.5 | 9968.2 | 11117.6 | 9996.6 | 11351.1 | 11323.1 | 9847.1 | 11569.1 | 10231 | 10644.7 | 10061.1 | 10670.5 | 11112.8 | 11491.6 | 10224.8 | 11324.1 | 9842.3 | 9655.8 | 11372.1 | 10028.5 | 11308.9 | 9933.3 | 11415.9 | 9958.1 | 11242 | 10205.3 | 11014 | 9896.1 | 11501.4 | 10018.3 | 10484.6 | 10129.2 | 8407.1 | 11075.5 | 10613 | 9915.6 | 11486.1 | 11039 | 10097.5 | 9962.2 | 11209.7 | 9901.6 | 10272.1 | 11269.1 | 9679.5 | 11204 | 9780.5 | 10952.8 | 10064.6 | 11146.2 | 9551.5 | 11224.3 | 10098.7 | 11081.2 | 10054.9 | 11135.6 | 10210.7 | 9859.6 | 11023.5 | 9960.6 | 9858.5 | 11084.7 | 10846.5 | 11014.2 | 10008.2 | 11129.2 | 9803 | 10746.9 | 10121 | 10698.5 | 9302.3 | 10863.3 | 9738.9 | 9989.1 | 10140 | 9928.7 | 8634.4 | 9873.9 | 8773.3 | 9857.3 | 9810.6 | 11502.4 | 9941 | 11536.1 | 10199.9 | 11340.9 | 9878.9 | 10101.2 | 9866.2 | 11089.5 | 11544.8 | 11352.3 | 11359.1 | 11326.3 | 11418.6 | 10270 | 11411.1 | 11396.3 | 11558.4 | 11457 | 10925.4 | 11521.8 | 9669 | 10819.4 | 10381.7 | 26.8301 | 26.7913 | 26.7093 | 0 | 27.0038 | 26.6987 | 0 | 41.1177 | 0 | 0 | 0 | 0 | 1.8444 | 2.2031 | 2.1068 | 2.263 | 2.2186 | 2.2112 | 5.635 | 5.545 | 5.415 | 5.6333 | 5.6583 | 5.1817 | 4.705 | 4.9088 | 4.5873 | 4.4829 | 4.8731 | 5.4605 | 1.0638 | 1.1632 | 1.1606 | 0 | 1.2343 | 1.023 | 5.8674 | 5.8353 | 5.8663 | 6.2428 | 5.5041 | 5.7535 | 1.2008 | 1.1147 | 1.1359 | 1.4785 | 1.2102 | 1.2704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170382 | 300 | 160866 | 303 | 308307.024 | 772 | 4.705 | 4.9088 | 4.5873 | 4.4829 | 4.8731 | 5.4605 | 5.8674 | 5.8353 | 5.8663 | 6.2428 | 5.5041 | 5.7535 | 852000 | 2000 | 835000 | 2000 | 1680933 | 4800 | 1683000 | 1676133 | 10.9167 | 4.8363 | 1.129 | 5.8449 | 1.2351 | 23.34% | 21.13% | 26.8066 | 41.1177 | 2.1412 | 5.5114 | 1695764.9 | 1680533 | 1907244.3508 | 88.11%
2022-11-19 | 2023 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 334195.71 | 6:57 | 18:01 | 9544.5 | 10480.3 | 10436.3 | 10429.4 | 10403.8 | 10520.1 | 10419.8 | 10883.8 | 10468.4 | 10521.5 | 10321.5 | 10500.5 | 10419 | 10426 | 10357.4 | 10504.7 | 10351.6 | 10464.6 | 10537 | 10505.7 | 10510.5 | 10519.2 | 10288.2 | 10424.7 | 10329.2 | 8999.1 | 10374.7 | 10414.6 | 10578.4 | 10387.9 | 10261.4 | 10520.2 | 10428.9 | 10601.3 | 10545.6 | 10435.2 | 10526.9 | 10403.4 | 10499.1 | 10431.9 | 11226.3 | 9993.6 | 11047 | 9829.3 | 10401.9 | 11783.5 | 9711.1 | 11183.4 | 9711.8 | 9425.8 | 10405.9 | 9972.8 | 11008 | 9713.6 | 10980.9 | 9727.6 | 9672 | 10792.5 | 9700.4 | 11036.2 | 10981.3 | 9548.2 | 11258.8 | 9895.7 | 10312.8 | 9747.2 | 10347.4 | 10782 | 11184.2 | 9902.5 | 11001 | 9454.3 | 9375.7 | 11035.9 | 9729.4 | 10982.8 | 9632.1 | 11104.2 | 9655.4 | 10921.1 | 9884.5 | 10675.9 | 9598.8 | 11173.7 | 9711.5 | 10161.6 | 9812.8 | 8144.2 | 10749.4 | 10284.7 | 9607.7 | 11176.6 | 10728.5 | 9805.1 | 9675.8 | 10909.1 | 9622.2 | 9974.3 | 10963.1 | 9384.2 | 10883.1 | 9488 | 10631.3 | 9778.2 | 10831.9 | 9267.1 | 10901.1 | 9783.4 | 10764.4 | 9768.7 | 10839.1 | 9896.6 | 9562.3 | 10709.1 | 9654.7 | 9557.2 | 10767.4 | 10519.1 | 10696.2 | 9697.5 | 10797.7 | 9493.3 | 10415.1 | 9799.2 | 10376 | 8993.6 | 10520.8 | 9422 | 9680.8 | 9829.8 | 9601.1 | 8370.9 | 9572.4 | 8507.2 | 9636.9 | 9559.3 | 11212.1 | 9655.9 | 11234.7 | 9901.2 | 11079.5 | 9621.8 | 9836.8 | 9596.6 | 10780.5 | 11250.4 | 11040.7 | 11056.7 | 11028.3 | 11124.8 | 9970.8 | 11105.7 | 11095.2 | 11285 | 11179 | 10629.9 | 11231.1 | 9391.4 | 10504.2 | 10078.9 | 26.3151 | 26.509 | 26.5024 | 0 | 26.813 | 26.3965 | 0 | 40.173 | 0 | 0 | 0 | 0 | 1.8435 | 2.1627 | 2.1677 | 2.2025 | 2.1727 | 2.1273 | 5.0917 | 5.4317 | 4.895 | 5.3383 | 5.4683 | 5.0933 | 4.5476 | 4.7449 | 4.4383 | 4.3346 | 4.7207 | 5.2937 | 1.0235 | 1.1114 | 1.1199 | 0 | 1.19 | 0.99002 | 5.6527 | 5.6266 | 5.6687 | 6.031 | 5.326 | 5.5797 | 1.1558 | 1.0646 | 1.0984 | 1.6585 | 1.1664 | 1.2301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171208 | 301 | 161677 | 304 | 309938.024 | 776.8 | 4.5476 | 4.7449 | 4.4383 | 4.3346 | 4.7207 | 5.2937 | 5.6527 | 5.6266 | 5.6687 | 6.031 | 5.326 | 5.5797 | 826000 | 1000 | 811000 | 1000 | 1631000 | 4800 | 1635000 | 1626200 | 11.0667 | 4.68 | 1.087 | 5.6474 | 1.229 | 23.23% | 21.76% | 26.5072 | 40.173 | 2.1128 | 5.2197 | 1645659.3 | 1630867 | 1845926.0583 | 88.35%
2022-11-20 | 2023 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 334195.71 | 7:00 | 17:56 | 9555.9 | 10482.4 | 10439.7 | 10439.5 | 10386.4 | 10504 | 10415.8 | 10856 | 10481.1 | 10516.9 | 10327.2 | 10506.4 | 10426.2 | 10427.6 | 10343.8 | 10509.3 | 10333.8 | 10449.2 | 10540.1 | 10521.1 | 10508.6 | 10520.4 | 10281.2 | 10425.9 | 10335.4 | 9005.8 | 10392.2 | 10421.1 | 10583 | 10369.1 | 10258 | 10528.5 | 10418.6 | 10612.6 | 10558.1 | 10438.5 | 10525.9 | 10407.9 | 10497.8 | 10420.5 | 11205.5 | 9983.4 | 11036.7 | 9868 | 10394 | 11771.2 | 9688.8 | 11147 | 9716.6 | 9433.6 | 10414.5 | 9971.5 | 11010.1 | 9724.7 | 10987.3 | 9729.5 | 9669.9 | 10784.7 | 9699.7 | 11037.4 | 10987.8 | 9552.2 | 11241.3 | 9894.5 | 10303.7 | 9740.9 | 10351.6 | 10770.3 | 11182 | 9895.2 | 10999.5 | 9453.3 | 9368.2 | 11035.7 | 9724 | 10982.7 | 9624.4 | 11095 | 9638.9 | 10919.4 | 9863.4 | 10656.3 | 9582.1 | 11147.7 | 9685.5 | 10138.5 | 9797.6 | 8129.4 | 10725.9 | 10269.7 | 9613.8 | 11159.3 | 10744.4 | 9841.4 | 9706.1 | 10869.9 | 9617.9 | 9962.7 | 10956.9 | 9371.8 | 10943.3 | 9498.9 | 10665.3 | 9773.2 | 10860.8 | 9272.6 | 10920.7 | 9777.2 | 10793.7 | 9781.1 | 10871.3 | 9912.4 | 9550 | 10688.4 | 9647.4 | 9541.2 | 10769.6 | 10487.6 | 10685 | 9662.3 | 10759.1 | 9456.8 | 10409.6 | 9791.4 | 10414.8 | 8999.7 | 10483 | 9410.6 | 9660.5 | 9825.7 | 9587.9 | 8343.7 | 9548.8 | 8481.7 | 9637 | 9587.7 | 11186.3 | 9621.3 | 11208.2 | 9882.8 | 11044.3 | 9604 | 9801.9 | 9567.8 | 10734.6 | 11212.4 | 10992 | 11027.1 | 10971.7 | 11083 | 9924.1 | 11052.2 | 11051.9 | 11242.9 | 11132.7 | 10575 | 11179.1 | 9352 | 10470.3 | 10032.4 | 26.1993 | 26.3681 | 26.2599 | 0 | 26.4036 | 26.1566 | 0 | 39.662 | 0 | 0 | 0 | 0 | 2.0477 | 2.3351 | 2.3343 | 2.4183 | 2.3409 | 2.3106 | 4.3417 | 4.5367 | 4.3233 | 4.9433 | 5.355 | 4.545 | 4.5371 | 4.7043 | 4.4305 | 4.3235 | 4.6742 | 5.2411 | 1.0318 | 1.1122 | 1.1254 | 0 | 1.1731 | 0.97444 | 5.6577 | 5.5993 | 5.6607 | 6.0205 | 5.2884 | 5.5148 | 1.1655 | 1.0695 | 1.1001 | 1.1164 | 1.1543 | 1.209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172035 | 303 | 162487 | 306 | 311567.891 | 781.733 | 4.5371 | 4.7043 | 4.4305 | 4.3235 | 4.6742 | 5.2411 | 5.6577 | 5.5993 | 5.6607 | 6.0205 | 5.2884 | 5.5148 | 827000 | 2000 | 810000 | 2000 | 1629867 | 4933 | 1633000 | 1624934 | 10.9333 | 4.6518 | 1.0834 | 5.6236 | 1.1358 | 23.29% | 20.2% | 26.2775 | 39.662 | 2.2978 | 4.6742 | 1644296.5 | 1629733 | 1841258.1398 | 88.51%
2022-11-21 | 2023 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 334195.71 | 7:01 | 17:57 | 9675.9 | 10613.8 | 10639.4 | 10602 | 10640.6 | 10708.9 | 10546.5 | 10975.9 | 10611.3 | 10636.4 | 10453.9 | 10635.7 | 10547.8 | 10561.4 | 10475.4 | 10648.3 | 10479.4 | 10609.7 | 10687.4 | 10660.1 | 10661.7 | 10673.1 | 10437.1 | 10587.6 | 10485.7 | 9128.6 | 10528.9 | 10572.3 | 10744 | 10519.5 | 10412.2 | 10682.9 | 10559 | 10773.5 | 10712.9 | 10596.7 | 10679 | 10559.1 | 10650.6 | 10562 | 11317.6 | 10078.4 | 11147 | 9970 | 10501.5 | 11847.1 | 9779.9 | 11252.5 | 9843 | 9553.3 | 10549.1 | 10090.7 | 11151.7 | 9833.5 | 11133.4 | 9856.7 | 9792.4 | 10919.9 | 9829.9 | 11164.8 | 11124.4 | 9677.1 | 11345.9 | 10005.4 | 10430.8 | 9867 | 10482.8 | 10894.9 | 11327.6 | 10014.6 | 11147.5 | 9571.1 | 9487.5 | 11176.5 | 9845.5 | 11119.7 | 9752.1 | 11240.1 | 9762.3 | 11056 | 9970.3 | 10767.4 | 9755.1 | 11272.5 | 9861.7 | 10350.9 | 9932.1 | 8239.7 | 10855.9 | 10407.9 | 9723.7 | 11290 | 10869.8 | 9972.3 | 9859.5 | 10992.4 | 9789.7 | 10142.4 | 11131 | 9535.5 | 11150.3 | 9658.3 | 10832.8 | 9927.8 | 11023.6 | 9418.2 | 11091.4 | 9952.8 | 10947.6 | 9929.3 | 11026 | 10084 | 9710.8 | 10841.6 | 9792.1 | 9683.7 | 10917.4 | 10645.4 | 10849.2 | 9824.3 | 10940 | 9620.3 | 10578.7 | 9956.9 | 10564.9 | 9140.5 | 10663.5 | 9588.1 | 9817.1 | 9955.5 | 9747.7 | 8486 | 9707 | 8588.9 | 9739.1 | 9730.5 | 11314.8 | 9733.2 | 11334.9 | 9987.9 | 11157.9 | 9753.2 | 9922.8 | 9779.3 | 10866.8 | 11355 | 11142.8 | 11173.2 | 11125.1 | 11214.9 | 10044.1 | 11189.8 | 11182.7 | 11381.3 | 11260.1 | 10698.4 | 11315.2 | 9466.1 | 10605 | 10162.8 | 24.9973 | 24.7868 | 24.2371 | 0 | 24.882 | 24.6256 | 0 | 37.5075 | 0 | 0 | 0 | 0 | 1.9819 | 2.3606 | 2.3707 | 2.4477 | 2.3417 | 2.3087 | 4.7467 | 5.005 | 5.1483 | 4.8583 | 5.145 | 4.7167 | 4.5351 | 4.7335 | 4.4383 | 4.3293 | 4.6894 | 5.2916 | 1.0358 | 1.1364 | 1.1313 | 0 | 1.1995 | 0.99602 | 5.6831 | 5.6551 | 5.6817 | 6.0507 | 5.3321 | 5.5551 | 1.1702 | 1.0932 | 1.1033 | 1.1316 | 1.1791 | 1.2371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172872 | 305 | 163309 | 308 | 313219.558 | 786.667 | 4.5351 | 4.7335 | 4.4383 | 4.3293 | 4.6894 | 5.2916 | 5.6831 | 5.6551 | 5.6817 | 6.0507 | 5.3321 | 5.5551 | 837000 | 2000 | 822000 | 2000 | 1651667 | 4934 | 1655000 | 1646733 | 10.9333 | 4.6695 | 1.0998 | 5.6596 | 1.1524 | 23.55% | 20.36% | 24.7058 | 37.5075 | 2.3019 | 4.9367 | 1666895.8 | 1651533 | 1865381.2095 | 88.54%
2022-11-22 | 2023 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 334195.71 | 7:08 | 17:55 | 9570.7 | 10483.8 | 10510.6 | 10488 | 10487.7 | 10579.3 | 10467.6 | 10840.9 | 10468.2 | 10476.5 | 10321.8 | 10499.2 | 10413.8 | 10426.9 | 10319.4 | 10520.9 | 10327.4 | 10463.9 | 10552.3 | 10523.6 | 10519.4 | 10536.1 | 10303.6 | 10442.5 | 10341.5 | 9011.6 | 10405.5 | 10437.4 | 10594.8 | 10365.3 | 10265.3 | 10533.5 | 10416 | 10632.3 | 10564.8 | 10446.5 | 10527.2 | 10419.8 | 10506.1 | 10429 | 11181.9 | 9966.1 | 11036.4 | 9859.8 | 10377.5 | 11734.8 | 9659.8 | 11113.3 | 9737.3 | 9452.7 | 10433.7 | 9991.5 | 11015.4 | 9703.2 | 11014.5 | 9745.6 | 9697.3 | 10807.7 | 9722.5 | 11065.5 | 11017.6 | 9574.3 | 11235.7 | 9890.1 | 10320.9 | 9780.2 | 10379.7 | 10826 | 11201.1 | 9929.5 | 11027.6 | 9498.8 | 9396.5 | 11074.4 | 9751.4 | 11019.3 | 9658.6 | 11142.7 | 9670.8 | 10948 | 9975.5 | 10739.3 | 9920.9 | 11263.7 | 9936.8 | 10457.5 | 9894.9 | 8229.4 | 10768.7 | 10343.5 | 9653.2 | 11185.1 | 10778.2 | 9871.6 | 9745.2 | 10893.1 | 9679.6 | 10013.9 | 10988.9 | 9416 | 11009.2 | 9539.4 | 10697.2 | 9804 | 10882.6 | 9303.7 | 10953.3 | 9833.4 | 10810.2 | 9808 | 10880 | 9958.4 | 9583.3 | 10733 | 9674.4 | 9578.5 | 10805.3 | 10550.5 | 10737.7 | 9746.1 | 10848.5 | 9543 | 10461.7 | 9860.2 | 10456.7 | 9045.2 | 10579.7 | 9503 | 9718.4 | 9852.5 | 9638.3 | 8402.8 | 9663.1 | 8550.8 | 9630.5 | 9656 | 11173 | 9619 | 11188.7 | 9868.8 | 11053.6 | 9683 | 9838.9 | 9782.1 | 10714.6 | 11197.2 | 10984.3 | 11021.9 | 10985.2 | 11072 | 9909.6 | 11038.5 | 11056.3 | 11276.8 | 11116 | 10554.6 | 11149.2 | 9330.6 | 10453 | 10044.3 | 25.2735 | 24.7923 | 24.523 | 0 | 24.7418 | 24.453 | 0 | 39.3588 | 0 | 0 | 0 | 0 | 1.5501 | 1.8427 | 1.8883 | 1.8813 | 1.7926 | 1.793 | 4.4133 | 5.5217 | 3.855 | 4.3233 | 4.0417 | 3.7867 | 4.4471 | 4.6778 | 4.4042 | 4.3064 | 4.6534 | 5.2503 | 1.0315 | 1.1135 | 1.13 | 0 | 1.1721 | 0.97511 | 5.4079 | 5.5953 | 5.6573 | 6.0547 | 5.2685 | 5.5137 | 1.1527 | 1.0692 | 1.1028 | 1.1358 | 1.1504 | 1.2113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173699 | 307 | 164123 | 310 | 314854.225 | 791.6 | 4.4471 | 4.6778 | 4.4042 | 4.3064 | 4.6534 | 5.2503 | 5.4079 | 5.5953 | 5.6573 | 6.0547 | 5.2685 | 5.5137 | 827000 | 2000 | 814000 | 2000 | 1634667 | 4933 | 1637000 | 1629734 | 10.7833 | 4.6232 | 1.0844 | 5.5829 | 1.137 | 23.46% | 20.37% | 24.7567 | 39.3588 | 1.7913 | 4.3236 | 1649265.2 | 1634667 | 1837945.9301 | 88.94%
2022-11-23 | 2023 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 334195.71 | 7:02 | 17:57 | 9917.1 | 10848.6 | 10875.9 | 10853.7 | 10846.7 | 10962.9 | 10816.7 | 11185.5 | 10838.6 | 10837.2 | 10677.4 | 10864.5 | 10781.8 | 10787.3 | 10663.5 | 10889.2 | 10685 | 10843.9 | 10927.7 | 10889.4 | 10873.4 | 10897.7 | 10646 | 10800.1 | 10695.5 | 9311.5 | 10773.1 | 10800.8 | 10942.8 | 10710.5 | 10610.6 | 10891.4 | 10757.8 | 10982.5 | 10907.3 | 10774.8 | 10861.7 | 10763.2 | 10847.3 | 10770.3 | 11612.1 | 10395.3 | 11510.1 | 10252.2 | 10769 | 12014.7 | 10075.2 | 11581 | 10077.5 | 9779.5 | 10781 | 10313.7 | 11368.7 | 10034.5 | 11341.3 | 10050.2 | 10012.1 | 11134.9 | 10063.9 | 11413.2 | 11380.3 | 9909.9 | 11533.1 | 10211.6 | 10611.5 | 10090.7 | 10704.2 | 11201.5 | 11514.6 | 10280.8 | 11368.3 | 9828.1 | 9679.6 | 11419.5 | 10057.8 | 11349.9 | 9963.3 | 11442.3 | 9973.7 | 11254.3 | 10309 | 11118.5 | 10242.5 | 11598.6 | 10253.3 | 10795.2 | 10231.6 | 8489.8 | 11140.7 | 10661 | 10013 | 11540.4 | 11133.6 | 10186.7 | 10035.1 | 11244.1 | 9986.8 | 10341.8 | 11321.9 | 9723.8 | 11333.4 | 9845.1 | 11033.6 | 10120.3 | 11212.4 | 9600 | 11280.7 | 10142.7 | 11136.4 | 10106.4 | 11201.7 | 10262.9 | 9897.7 | 11083.8 | 10002.2 | 9901.6 | 11145.9 | 10897.1 | 11077.9 | 10061.6 | 11181.1 | 9849.2 | 10797.4 | 10184.3 | 10801.4 | 9321.4 | 10912.8 | 9797.4 | 10039.5 | 10189.6 | 9968.7 | 8688.4 | 9988.3 | 8892.6 | 9947.6 | 9978.5 | 11554 | 10037.4 | 11533.7 | 10226.4 | 11431.6 | 10043.9 | 10206.6 | 10121.3 | 11105.5 | 11541.5 | 11406.3 | 11425.2 | 11396.3 | 11478.4 | 10263.8 | 11399.9 | 11411.2 | 11634.2 | 11454.1 | 10921.5 | 11510.8 | 9666.2 | 10837.8 | 10424.2 | 25.4788 | 25.49 | 25.1614 | 0 | 25.5486 | 25.2429 | 0 | 40.2047 | 0 | 0 | 0 | 0 | 1.9363 | 1.754 | 1.7738 | 1.4235 | 1.7203 | 1.8352 | 3.6967 | 3.9217 | 3.735 | 2.415 | 3.8367 | 3.835 | 4.54 | 4.8393 | 4.617 | 0 | 5.0402 | 5.4776 | 1.0521 | 1.1569 | 1.1686 | 0 | 1.2239 | 1.0301 | 5.5722 | 5.8171 | 5.9266 | 0 | 5.9654 | 5.7393 | 1.1805 | 1.1093 | 1.1412 | 0 | 1.2127 | 1.2791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174554 | 309 | 164964 | 311 | 316542.825 | 796.6 | 4.54 | 4.8393 | 4.617 | 0 | 5.0402 | 5.4776 | 5.5722 | 5.8171 | 5.9266 | 0 | 5.9654 | 5.7393 | 855000 | 2000 | 841000 | 1000 | 1688600 | 5000 | 1693000 | 1683600 | 10.9167 | 4.9028 | 1.1263 | 5.8041 | 1.1846 | 22.97% | 20.41% | 25.3843 | 40.2047 | 1.7405 | 3.5733 | 1704246.8 | 1688200 | 1901343.5894 | 88.79%
2022-11-24 | 2023 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 334195.71 | 6:59 | 17:56 | 10148.5 | 11087.1 | 11125.9 | 11114 | 11083.7 | 11206.7 | 11050.1 | 11382.7 | 11071.7 | 11069.9 | 10922.8 | 11104 | 11046.3 | 11039.5 | 10907.1 | 11149.7 | 10943.7 | 11116.4 | 11188.4 | 11152.7 | 11132.5 | 11160.6 | 10910.8 | 11071.2 | 10985.5 | 9543 | 11033.7 | 11071.7 | 11198.4 | 10965.4 | 10896.5 | 11168.2 | 11032.6 | 11232.2 | 11182.1 | 11050.3 | 11132.2 | 11044.5 | 11121.3 | 11053.8 | 11848.4 | 10675.7 | 11762.2 | 10545.9 | 11074.6 | 12232.6 | 10353.5 | 11801.9 | 10308.3 | 10015.8 | 11050.3 | 10559.1 | 11607.3 | 10265.5 | 11586.6 | 10300 | 10249.7 | 11378.9 | 10291.9 | 11639.3 | 11592.9 | 10135 | 11731.5 | 10441.3 | 10848.7 | 10335.4 | 10960 | 11437.4 | 11721.5 | 10528 | 11589.2 | 10071.2 | 9913 | 11649.4 | 10288.9 | 11566.9 | 10202.2 | 11675.5 | 10206 | 11472 | 10548.9 | 11356.3 | 10475.1 | 11807 | 10493 | 11043.2 | 10470.5 | 8684.6 | 11369.8 | 10897.9 | 10247.7 | 11749.7 | 11366.4 | 10427.3 | 10273.2 | 11476.7 | 10200.2 | 10565.7 | 11520.9 | 9932.8 | 11547.5 | 10063.3 | 11280.6 | 10354.1 | 11426.8 | 9822.9 | 11497 | 10368.4 | 11370.7 | 10340 | 11449 | 10480.7 | 10110.2 | 11316.8 | 10189.8 | 10112.2 | 11364.2 | 11114 | 11304.4 | 10264.8 | 11381.8 | 10056.8 | 11054.5 | 10418.4 | 11066.8 | 9513.4 | 11139.2 | 9996.1 | 10245.4 | 10397.8 | 10267.1 | 8877.4 | 10193.2 | 9072.6 | 10150.6 | 10175.8 | 11777.6 | 10319.2 | 11766.7 | 10491.8 | 11644.9 | 10291.4 | 10468.1 | 10336.4 | 11369.2 | 11803 | 11668.5 | 11666.3 | 11644.6 | 11727.1 | 10553.7 | 11658.5 | 11613.7 | 11853 | 11703.2 | 11223.1 | 11776.7 | 9939.8 | 11070.2 | 10683.9 | 24.864 | 25.0997 | 25.044 | 0 | 25.3059 | 25.0981 | 0 | 40.4335 | 0 | 0 | 0 | 0 | 1.6826 | 1.6465 | 1.6705 | 1.7669 | 1.5832 | 1.6278 | 4.32 | 4.2033 | 3.8867 | 4.1367 | 4.55 | 3.8317 | 4.6799 | 4.9643 | 4.7229 | 4.61 | 5.1619 | 5.6207 | 1.0899 | 1.1974 | 1.1997 | 0 | 1.2666 | 1.0404 | 5.7645 | 6.0076 | 6.1306 | 6.7362 | 6.146 | 5.873 | 1.2246 | 1.1449 | 1.1706 | 1.2111 | 1.2523 | 1.293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175428 | 310 | 165822 | 313 | 318269.225 | 801.467 | 4.6799 | 4.9643 | 4.7229 | 4.61 | 5.1619 | 5.6207 | 5.7645 | 6.0076 | 6.1306 | 6.7362 | 6.146 | 5.873 | 874000 | 1000 | 858000 | 2000 | 1726400 | 4867 | 1729000 | 1721533 | 10.95 | 4.96 | 1.1588 | 6.1096 | 1.2161 | 23.36% | 19.9% | 25.0823 | 40.4335 | 1.6629 | 4.1547 | 1742552.7 | 1726267 | 1994069.2929 | 86.57%
2022-11-25 | 2023 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 334195.71 | 7:02 | 17:56 | 10197.5 | 11115.1 | 11141.8 | 11144.5 | 11096.1 | 11228.1 | 11078.9 | 11366.6 | 11099.9 | 11078.2 | 10959.2 | 11123.5 | 11093 | 11064.7 | 10945.1 | 11192.7 | 10974.4 | 11148.1 | 11199.2 | 11174.9 | 11141.2 | 11176.2 | 10970.1 | 11112 | 11012.6 | 9583 | 11069.1 | 11086.4 | 11196.7 | 10980.2 | 10945.1 | 11181.9 | 11068.7 | 11259.6 | 11203.6 | 11072.2 | 11142.5 | 11068.9 | 11141.6 | 11080.8 | 11802.7 | 10690 | 11735.5 | 10567.6 | 11105 | 12194.2 | 10385.2 | 11757.4 | 10342.7 | 10051.7 | 11067.6 | 10592.5 | 11590.8 | 10303 | 11588.4 | 10348.4 | 10307.3 | 11391.2 | 10326.1 | 11641.8 | 11600.4 | 10169.1 | 11718.4 | 10476.9 | 10911 | 10381.5 | 11021.3 | 11438 | 11707.1 | 10584.1 | 11589.4 | 10112.5 | 9970.8 | 11640.3 | 10349.1 | 11562.8 | 10268.8 | 11656.8 | 10248.2 | 11489.5 | 10595.3 | 11364.1 | 10532.7 | 11785 | 10542.7 | 11090.4 | 10511.3 | 8725.3 | 11416.2 | 10939 | 10301.8 | 11743.4 | 11389.8 | 10498.8 | 10353 | 11535.1 | 10272.2 | 10681 | 11570.8 | 10040.9 | 11584.8 | 10183.7 | 11361.7 | 10469.7 | 11486 | 9938.9 | 11566.6 | 10488 | 11461.5 | 10464.1 | 11521.8 | 10612.4 | 10216.1 | 11374.8 | 10302.3 | 10224.9 | 11415.5 | 11191.6 | 11365.2 | 10382.9 | 11438.7 | 10174.3 | 11155.2 | 10536.6 | 11157.4 | 9634.6 | 11237.2 | 10121.4 | 10333.2 | 10465.5 | 10364.6 | 8952.2 | 10250.1 | 9122.6 | 10237.6 | 10259.5 | 11776.2 | 10388.7 | 11769.1 | 10566.3 | 11659 | 10383.1 | 10555.9 | 10426 | 11404 | 11811.3 | 11683.8 | 11682 | 11660.6 | 11733.1 | 10633.8 | 11673.1 | 11660.2 | 11869.4 | 11724.8 | 11272.5 | 11785.7 | 10012.2 | 11137.6 | 10773.4 | 25.6145 | 25.0445 | 24.7805 | 0 | 25.1096 | 24.9289 | 0 | 39.8738 | 0 | 0 | 0 | 0 | 2.0519 | 1.9449 | 2.0352 | 1.9231 | 1.9401 | 1.8708 | 5.2917 | 4.575 | 4.61 | 4.6283 | 5.505 | 4.5583 | 4.6417 | 4.9505 | 4.7247 | 4.6317 | 5.1694 | 5.637 | 1.087 | 1.1994 | 1.2093 | 0 | 1.2694 | 1.0426 | 5.7441 | 6.0019 | 6.1463 | 6.7646 | 6.1657 | 5.888 | 1.2217 | 1.1476 | 1.179 | 0.98922 | 1.2556 | 1.2958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176305 | 312 | 166687 | 315 | 320002.825 | 806.333 | 4.6417 | 4.9505 | 4.7247 | 4.6317 | 5.1694 | 5.637 | 5.7441 | 6.0019 | 6.1463 | 6.7646 | 6.1657 | 5.888 | 877000 | 2000 | 865000 | 2000 | 1733600 | 4866 | 1738000 | 1728734 | 10.9 | 4.9592 | 1.1615 | 6.1184 | 1.1815 | 23.42% | 19.31% | 25.0956 | 39.8738 | 1.961 | 4.8614 | 1749582.8 | 1733600 | 2002934.3626 | 86.55%
2022-11-26 | 2023 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 334195.71 | 7:03 | 17:56 | 10083.7 | 10995.6 | 11040.2 | 11033.8 | 10977.3 | 11139.9 | 10940.7 | 11277.1 | 10989.1 | 10960.8 | 10841.5 | 11018.2 | 10972.3 | 10967.1 | 10806.8 | 11086.9 | 10856.7 | 11048.9 | 11120 | 11084.1 | 11053.1 | 11081.9 | 10845.6 | 11002.6 | 10909 | 9478.9 | 10954.8 | 10977.9 | 11108.1 | 10853.3 | 10819.2 | 11105.7 | 10980.4 | 11200 | 11127.9 | 10971 | 11054.5 | 10969.5 | 11049.5 | 11009.1 | 11844.5 | 10601.6 | 11693 | 10471.1 | 10995.1 | 12218.2 | 10267.7 | 11790.8 | 10226.1 | 9937.8 | 10942.2 | 10453.5 | 11540.3 | 10181.5 | 11543.3 | 10231.7 | 10193.2 | 11327.2 | 10213 | 11595 | 11549.7 | 10056.4 | 11666.5 | 10341.7 | 10772.8 | 10258.7 | 10883.4 | 11356.5 | 11676.9 | 10452 | 11525.6 | 9989.4 | 9853.3 | 11577.4 | 10232.7 | 11496.9 | 10144.6 | 11627.1 | 10141.1 | 11431.5 | 10464.4 | 11268.1 | 10406.9 | 11732.1 | 10417.6 | 10965.5 | 10395 | 8623.6 | 11391 | 10828.3 | 10212.6 | 11742.7 | 11376.2 | 10434.9 | 10290.9 | 11499.7 | 10139.8 | 10605.7 | 11556.1 | 9957.7 | 11565.8 | 10107.9 | 11320.9 | 10385.2 | 11463.6 | 9853.4 | 11541.3 | 10404.9 | 11411.3 | 10368.8 | 11481.5 | 10529.3 | 10112.2 | 11317.6 | 10203.6 | 10131.8 | 11354.2 | 11126.9 | 11312.5 | 10273.7 | 11400.8 | 10083.5 | 11070.1 | 10439.1 | 11064.3 | 9555.8 | 11168.9 | 10024.8 | 10203.5 | 10308.7 | 10254.2 | 8854.5 | 10116.5 | 8982 | 10101.4 | 10114.7 | 11734.1 | 10254.5 | 11727.2 | 10425.3 | 11607.9 | 10244.3 | 10420.2 | 10272.5 | 11311.3 | 11756.2 | 11606.4 | 11621.6 | 11600.1 | 11685.9 | 10495.1 | 11608.8 | 11591.1 | 11822.1 | 11663 | 11166.8 | 11725.8 | 9868 | 10990.7 | 10625 | 25.8158 | 25.3572 | 25.336 | 0 | 25.6766 | 25.2459 | 0 | 40.6689 | 0 | 0 | 0 | 0 | 1.6046 | 1.5608 | 1.5878 | 1.6077 | 1.5177 | 1.5985 | 4.075 | 4.2083 | 3.805 | 4.9683 | 3.71 | 4.8717 | 4.5958 | 4.9491 | 4.6556 | 4.5702 | 5.1379 | 5.6047 | 1.0623 | 1.2974 | 1.1881 | 0 | 1.2646 | 1.0384 | 5.748 | 6.0278 | 6.1081 | 6.6873 | 6.1328 | 5.8512 | 1.1967 | 1.2364 | 1.1626 | 1.2016 | 1.2512 | 1.2898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177174 | 314 | 167544 | 316 | 321722.2 | 811.267 | 4.5958 | 4.9491 | 4.6556 | 4.5702 | 5.1379 | 5.6047 | 5.748 | 6.0278 | 6.1081 | 6.6873 | 6.1328 | 5.8512 | 869000 | 2000 | 857000 | 1000 | 1719375 | 4934 | 1723000 | 1714441 | 10.8833 | 4.9189 | 1.1701 | 6.0925 | 1.223 | 23.79% | 20.07% | 25.4863 | 40.6689 | 1.5795 | 4.2731 | 1735235.6 | 1719266 | 1985458.205 | 86.59%
2022-11-27 | 2023 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 334195.71 | 7:04 | 17:55 | 9962.1 | 10854.9 | 10891.3 | 10893.2 | 10818.6 | 10987.5 | 10782.9 | 11111.2 | 10849.4 | 10810 | 10698.9 | 10874.7 | 10846.2 | 10828.9 | 10670.1 | 10967.9 | 10729.2 | 10941.5 | 10998.9 | 10956.8 | 10932.2 | 10959 | 10731.1 | 10891.1 | 10772.7 | 9373.5 | 10828.9 | 10864 | 10982.3 | 10717.6 | 10688.8 | 10970.6 | 10835.4 | 11066.8 | 10990.2 | 10848.5 | 10900.3 | 10840.7 | 10905.2 | 10877.9 | 11863.7 | 10505.3 | 11669.1 | 10364.1 | 10970.6 | 12376.2 | 10161 | 11832.1 | 10106.1 | 9820.3 | 10813.1 | 10330 | 11440.1 | 10050.4 | 11428.6 | 10103.3 | 10057.8 | 11175 | 10086.6 | 11494.4 | 11438.2 | 9926.3 | 11585.3 | 10192.5 | 10624.4 | 10119.5 | 10730.4 | 11249 | 11585.4 | 10321 | 11410.9 | 9870.8 | 9707.1 | 11464.3 | 10081.1 | 11378.4 | 9995.3 | 11521.6 | 9993.8 | 11301.5 | 10378.4 | 11190.7 | 10361.8 | 11705.7 | 10339.7 | 10902.7 | 10314 | 8552.6 | 11291.4 | 10729.6 | 10107 | 11716.8 | 11269.8 | 10297.1 | 10137.8 | 11372 | 9971.7 | 10422.3 | 11431.2 | 9793.8 | 11439.2 | 9946 | 11148.8 | 10215.8 | 11331.9 | 9698.4 | 11407.3 | 10244.6 | 11254.9 | 10210 | 11335.3 | 10367.8 | 9947.3 | 11155.7 | 10045.9 | 9975 | 11206.4 | 10964.3 | 11162.1 | 10112.9 | 11262.8 | 9929.5 | 10902.5 | 10281 | 10893 | 9404.3 | 10998.8 | 9868.2 | 10029.8 | 10126.1 | 10094 | 8704.4 | 9947 | 8853.7 | 9966 | 9990.1 | 11663.9 | 10104.5 | 11646.2 | 10260.4 | 11500.8 | 10064.2 | 10236.5 | 10108 | 11145.2 | 11683.2 | 11485.3 | 11514.3 | 11487.5 | 11592.9 | 10331.8 | 11497.8 | 11480.6 | 11742.4 | 11555.8 | 10991.3 | 11631.1 | 9715.9 | 10827.5 | 10463.8 | 25.6558 | 25.3285 | 25.0493 | 0 | 25.394 | 25.0079 | 0 | 39.9013 | 0 | 0 | 0 | 0 | 1.853 | 1.7668 | 1.8458 | 1.8169 | 1.8 | 1.7838 | 4.4883 | 3.92 | 4.1033 | 4.09 | 3.7967 | 4.295 | 4.5274 | 4.872 | 4.5771 | 4.5063 | 5.0357 | 5.4845 | 1.0456 | 1.2796 | 1.167 | 0 | 1.2369 | 1.0376 | 5.6585 | 5.9379 | 6.0072 | 6.5792 | 6.024 | 5.7215 | 1.1788 | 1.2192 | 1.1391 | 1.0924 | 1.2252 | 1.2877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178034 | 315 | 168391 | 318 | 323421.625 | 816.133 | 4.5274 | 4.872 | 4.5771 | 4.5063 | 5.0357 | 5.4845 | 5.6585 | 5.9379 | 6.0072 | 6.5792 | 6.024 | 5.7215 | 860000 | 1000 | 847000 | 2000 | 1699425 | 4866 | 1704000 | 1694559 | 10.85 | 4.8338 | 1.1534 | 5.988 | 1.1904 | 23.86% | 19.88% | 25.2871 | 39.9013 | 1.811 | 4.1156 | 1715033.4 | 1699400 | 1958192.1464 | 86.78%
2022-11-28 | 2023 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 334195.71 | 7:05 | 17:55 | 10027 | 10910.1 | 10948.8 | 10960 | 10867 | 11044.8 | 10827 | 11139.4 | 10913.6 | 10870 | 10758.8 | 10931.3 | 10913.7 | 10889.1 | 10720 | 11036.6 | 10794.9 | 11016.4 | 11063.3 | 11026.1 | 11003.4 | 11029 | 10821.8 | 10965.8 | 10850.5 | 9439.8 | 10912.8 | 10945 | 11064.5 | 10800 | 10770.8 | 11042.6 | 10904.5 | 11147.2 | 11069.3 | 10920.6 | 10979.9 | 10915.2 | 10992.8 | 10960.8 | 11775.5 | 10578.8 | 11649.3 | 10420.6 | 11046.3 | 12320.6 | 10203.5 | 11791.1 | 10165.8 | 9874.1 | 10871.3 | 10381.9 | 11466.5 | 10103.3 | 11440.2 | 10145.6 | 10104.7 | 11197.1 | 10155.6 | 11517.1 | 11463.9 | 9972.6 | 11558.5 | 10238.3 | 10647.9 | 10149.7 | 10756.8 | 11290.2 | 11554.7 | 10367.1 | 11409.9 | 9911.4 | 9738.8 | 11460.7 | 10114.6 | 11396.1 | 10028.2 | 11513.4 | 10029 | 11331.1 | 10453.4 | 11266 | 10444.4 | 11711.5 | 10412.6 | 10985.3 | 10367.6 | 8609.8 | 11324.6 | 10799.1 | 10158 | 11700 | 11307.8 | 10339 | 10175 | 11397.4 | 10027.3 | 10477.8 | 11446.1 | 9841.5 | 11463.2 | 9993.4 | 11203.3 | 10266 | 11360 | 9743.8 | 11434.2 | 10288.6 | 11312 | 10262.9 | 11406.2 | 10441 | 10000 | 11220 | 10094.4 | 10030.2 | 11261.9 | 11029.9 | 11215.2 | 10170.1 | 11309.2 | 9974.6 | 10955.8 | 10338.3 | 10978.8 | 9492.5 | 11055.5 | 10078.5 | 10097.6 | 10202.9 | 10148.7 | 8746.2 | 10064 | 9015.7 | 10098.1 | 10105.1 | 11688.3 | 10214.4 | 11675.7 | 10367.7 | 11528.2 | 10138 | 10312.8 | 10185.8 | 11249.7 | 11716.5 | 11555.6 | 11578.7 | 11546.5 | 11624.9 | 10443.7 | 11561 | 11566.4 | 11739.2 | 11591.9 | 11087.8 | 11653.6 | 9807.4 | 10942.4 | 10572.5 | 25.7896 | 25.3457 | 25.1305 | 0 | 25.3825 | 25.1244 | 0 | 39.0972 | 0 | 0 | 0 | 0 | 2.0402 | 2.0387 | 2.0055 | 2.0714 | 2.0186 | 1.9448 | 4.135 | 3.9917 | 3.98 | 4.4933 | 4.315 | 4.3017 | 4.5918 | 4.8779 | 4.4203 | 4.5141 | 5.0534 | 5.5143 | 1.0786 | 1.2827 | 1.0934 | 0 | 1.2414 | 1.0143 | 5.7257 | 5.9524 | 6.1674 | 6.5209 | 6.0595 | 5.7463 | 1.2138 | 1.2243 | 1.1293 | 0.93359 | 1.2285 | 1.2583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178897 | 317 | 169243 | 320 | 325129.692 | 821 | 4.5918 | 4.8779 | 4.4203 | 4.5141 | 5.0534 | 5.5143 | 5.7257 | 5.9524 | 6.1674 | 6.5209 | 6.0595 | 5.7463 | 863000 | 2000 | 852000 | 2000 | 1708067 | 4867 | 1711000 | 1703200 | 10.8333 | 4.8286 | 1.1421 | 6.0287 | 1.1646 | 23.65% | 19.32% | 25.3546 | 39.0972 | 2.0199 | 4.2028 | 1723786.7 | 1708067 | 1957529.1654 | 87.26%
2022-11-29 | 2023 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 334195.71 | 7:06 | 17:59 | 9516.6 | 10330.4 | 10368.8 | 10388.7 | 10285.1 | 10458.2 | 10246.4 | 10529.2 | 10358.5 | 10292.9 | 10206.3 | 10372.7 | 10340.7 | 10328.1 | 10171.2 | 10461.5 | 10225.4 | 10429.4 | 10473.9 | 10454.1 | 10422 | 10441.1 | 10277.3 | 10399.9 | 10280.2 | 8958.7 | 10349.6 | 10365.9 | 10479.8 | 10231.8 | 10214.4 | 10453 | 10389.2 | 10570 | 10493 | 10357.1 | 10402 | 10375.8 | 10455.4 | 10406 | 11122 | 10025.2 | 11037.3 | 9859 | 10467.1 | 11698.6 | 9725.3 | 11155.7 | 9669.6 | 9393.3 | 10333.5 | 9873.2 | 10871 | 9579.2 | 10882.6 | 9674.7 | 9634.2 | 10636.7 | 9666.8 | 10933.5 | 10897.5 | 9494.9 | 10930.9 | 9705 | 10153.4 | 9679.1 | 10257.7 | 10728.7 | 10998.5 | 9877.3 | 10851.3 | 9435.2 | 9295.4 | 10894.9 | 9652.4 | 10851.3 | 9564.1 | 10944.9 | 9550.2 | 10771.1 | 9935.6 | 10677.8 | 9940.9 | 11119.8 | 9905.6 | 10447.5 | 9862 | 8196.8 | 10725 | 10304.4 | 9659 | 11092.2 | 10722.3 | 9824.2 | 9667 | 10795.3 | 9507 | 9929.4 | 10827.4 | 9321.3 | 10840.9 | 9467.6 | 10594.5 | 9731.1 | 10737.8 | 9228.4 | 10809.4 | 9740.3 | 10700 | 9719 | 10792.8 | 9896.8 | 9478.3 | 10611.5 | 9563.3 | 9500.2 | 10661 | 10441.7 | 10612.7 | 9658.4 | 10707.6 | 9448.4 | 10369.7 | 9790.5 | 10409.6 | 9019.1 | 10471.1 | 9581.4 | 9574.9 | 9685.9 | 9630.6 | 8288.9 | 9552.2 | 8539.1 | 9556.9 | 9562.2 | 11041.3 | 9651.2 | 11034 | 9817 | 10889 | 9581.8 | 9743.6 | 9649.1 | 10608.3 | 11046.6 | 10912.2 | 10945.4 | 10896.7 | 10982.8 | 9872.8 | 10922.8 | 10930.3 | 11081.6 | 10940 | 10451 | 10994.9 | 9262.3 | 10332.8 | 9998 | 25.611 | 25.1737 | 25.2135 | 0 | 25.1788 | 25.0738 | 0 | 36.6769 | 0 | 0 | 0 | 0 | 2.8739 | 2.8546 | 2.8446 | 2.9978 | 2.7809 | 2.937 | 5.33 | 5.8717 | 5.3567 | 6.0117 | 5.7583 | 6.275 | 4.3793 | 4.655 | 4.416 | 4.3436 | 4.8069 | 5.1128 | 0.86201 | 1.1409 | 1.1439 | 0 | 1.1723 | 0.96516 | 5.5103 | 5.5367 | 5.4448 | 5.2585 | 5.6368 | 5.3931 | 0.9463 | 1.097 | 1.0751 | 0.91872 | 1.1663 | 1.197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179716 | 319 | 170050 | 322 | 326749.159 | 825.933 | 4.3793 | 4.655 | 4.416 | 4.3436 | 4.8069 | 5.1128 | 5.5103 | 5.5367 | 5.4448 | 5.2585 | 5.6368 | 5.3931 | 819000 | 2000 | 807000 | 2000 | 1619467 | 4933 | 1622000 | 1614534 | 10.8833 | 4.6189 | 1.0569 | 5.4634 | 1.0668 | 22.88% | 19.53% | 25.2502 | 36.6769 | 2.8814 | 5.7672 | 1634352.4 | 1619333 | 1803723.6798 | 89.78%
2022-11-30 | 2023 | 2022 | Year_1 | Year_1 | 2022-12-01 | 30 | 334195.71 | 7:08 | 17:55 | 9881.3 | 10721.2 | 10769 | 10791 | 10685.5 | 10884.4 | 10634.4 | 10926 | 10747.1 | 10685.8 | 10596.6 | 10766.8 | 10731.6 | 10729.5 | 10554.3 | 10868.7 | 10621.3 | 10832.8 | 10887.8 | 10867.4 | 10814.7 | 10846.5 | 10679.3 | 10807.2 | 10674.8 | 9299.6 | 10756.7 | 10777.1 | 10892.6 | 10626.7 | 10612.5 | 10860.9 | 10856.6 | 10996.6 | 10906.9 | 10788.9 | 10847.8 | 10815.4 | 10900.7 | 10821.2 | 11510.4 | 10386.2 | 11431.1 | 10245.7 | 10900 | 12131.3 | 10194.2 | 11496.4 | 10047.8 | 9760.5 | 10749.1 | 10257.3 | 11296.5 | 9941.3 | 11301.6 | 10050.8 | 10014.3 | 11071.9 | 10049.3 | 11355.2 | 11320.1 | 9875.7 | 11344.6 | 10096.5 | 10576.2 | 10073.5 | 10694.5 | 11164.1 | 11438 | 10283.7 | 11305.3 | 9831.4 | 9667.4 | 11350.8 | 10048.2 | 11288.1 | 9964.2 | 11378.1 | 9937.2 | 11200.4 | 10317.7 | 11094.6 | 10312.7 | 11524.8 | 10289.1 | 10854.9 | 10235.6 | 8510.5 | 11123.9 | 10690.2 | 10021.8 | 11484 | 11120.2 | 10184.4 | 10018.6 | 11187.3 | 9889.5 | 10343.8 | 11251.2 | 9710.3 | 11290 | 9868.8 | 11051.8 | 10126.9 | 11169.2 | 9623.7 | 11249.4 | 10175.8 | 11148.8 | 10134.2 | 11200.9 | 10320.6 | 9890.4 | 11051.1 | 9960.7 | 9909.5 | 11098.5 | 10889.4 | 11043.9 | 10099.2 | 11157.5 | 9884 | 10814 | 10224.3 | 10821.9 | 9401.7 | 10934.7 | 10000.7 | 9999 | 10088.6 | 10032.6 | 8645.8 | 9998 | 8896.5 | 9950.4 | 9944.7 | 11457.8 | 10058.3 | 11467.6 | 10237.7 | 11306.1 | 9968.7 | 10141.9 | 10066.6 | 11097 | 11486.8 | 11364.3 | 11365.6 | 11336 | 11419.2 | 10304.4 | 11355.2 | 11332 | 11485.9 | 11349.1 | 10892.8 | 11443.5 | 9657.6 | 10753.1 | 10417.6 | 25.7185 | 24.9532 | 25.086 | 0 | 24.9079 | 24.63 | 0 | 36.6423 | 0 | 0 | 0 | 0 | 3.1611 | 3.2401 | 3.1301 | 3.3582 | 3.1665 | 2.9854 | 6.0417 | 6.0917 | 5.5117 | 6.0167 | 6.0683 | 5.43 | 4.411 | 4.7642 | 4.4807 | 4.4333 | 4.9553 | 5.3874 | 0.84333 | 1.1871 | 1.1596 | 0 | 1.2325 | 1.0398 | 5.7925 | 5.8089 | 5.6596 | 5.3729 | 5.9499 | 5.6128 | 0.94427 | 1.1394 | 1.0825 | 0.91202 | 1.2211 | 1.2921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180568 | 320 | 170889 | 324 | 328432.559 | 830.867 | 4.411 | 4.7642 | 4.4807 | 4.4333 | 4.9553 | 5.3874 | 5.7925 | 5.8089 | 5.6596 | 5.3729 | 5.9499 | 5.6128 | 852000 | 1000 | 839000 | 2000 | 1683400 | 4934 | 1688000 | 1678466 | 10.7833 | 4.7386 | 1.0925 | 5.6994 | 1.0986 | 23.05% | 19.27% | 25.0591 | 36.6423 | 3.1736 | 5.86 | 1699821.2 | 1683267 | 1877770.8537 | 89.64%
2022-12-01 | 2023 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 334195.71 | 7:07 | 17:57 | 9551.9 | 10370.7 | 10393.3 | 10417.2 | 10316.7 | 10531.6 | 10274.1 | 10573.9 | 10391.9 | 10314.5 | 10257.5 | 10419.5 | 10394.3 | 10381.7 | 10345.3 | 10545 | 10395.9 | 10505.6 | 10562.5 | 10535.7 | 10491.1 | 10517.3 | 10351.2 | 10476.9 | 10330.2 | 9002.3 | 10420.7 | 10436.7 | 10561.5 | 10279.5 | 10276.4 | 10527.7 | 10536 | 10671.6 | 10498.6 | 10445 | 10505.7 | 10486.8 | 10575.3 | 10366.4 | 11209.1 | 10000.2 | 11134.3 | 9883.5 | 10487.4 | 11910.5 | 9804.7 | 11170.5 | 9744.9 | 9461.6 | 10410.8 | 9926 | 10991.5 | 9630 | 11011.5 | 9738.3 | 9700.1 | 10746.8 | 9741.2 | 11075.8 | 11047.5 | 9570.3 | 11072.8 | 9750 | 10246.6 | 9787.7 | 10366.9 | 10847.2 | 11194.7 | 9966.6 | 11033.5 | 9524 | 9364.8 | 11083.7 | 9731.2 | 11030.7 | 9649.9 | 11111 | 9618.3 | 10909.6 | 9967.4 | 10753 | 9967.8 | 11249.4 | 9933 | 10491.7 | 9888.3 | 8218 | 10764.6 | 10314.5 | 9662 | 11190.3 | 10762.3 | 9820 | 9664.7 | 10860.3 | 9578 | 10024.1 | 10987 | 9403.8 | 11016.7 | 9571.2 | 10732.4 | 9811.5 | 10903 | 9330.8 | 10983.8 | 9880.9 | 10831.8 | 9824.8 | 10900.3 | 10011.2 | 9578.7 | 10731 | 9659.2 | 9599.1 | 10797.4 | 10570.7 | 10749 | 9787.6 | 10873.2 | 9575.6 | 10501.6 | 9914.2 | 10491.6 | 9098.5 | 10614.5 | 9679.4 | 9681.3 | 9771 | 9683.8 | 8369.6 | 9656.6 | 8589.6 | 9627.2 | 9622.1 | 11292.7 | 9792.3 | 11338.4 | 9958.8 | 11108.5 | 9672.3 | 9836 | 9744 | 10879.4 | 11352.8 | 11166.6 | 11156 | 11106.7 | 11229.1 | 10051.8 | 11180.2 | 11105.4 | 11325.2 | 11211.5 | 10634.8 | 11290.1 | 9414.2 | 10459.3 | 10148.9 | 24.3278 | 23.9485 | 23.6375 | 0 | 23.8319 | 23.5816 | 0 | 37.935 | 0 | 0 | 0 | 0 | 2.1844 | 2.0539 | 2.0458 | 2.1391 | 1.9785 | 2.0079 | 4.6867 | 4.825 | 4.6983 | 4.895 | 4.81 | 4.8067 | 4.2907 | 4.6259 | 4.3492 | 4.3027 | 4.7951 | 5.2389 | 0.81733 | 1.1499 | 1.1218 | 0 | 1.1883 | 0.9773 | 5.624 | 5.625 | 5.4822 | 5.2107 | 5.7387 | 5.4633 | 0.91937 | 1.0996 | 1.0505 | 0.90673 | 1.1736 | 1.2144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181394 | 322 | 171706 | 325 | 330068.359 | 835.867 | 4.2907 | 4.6259 | 4.3492 | 4.3027 | 4.7951 | 5.2389 | 5.624 | 5.625 | 5.4822 | 5.2107 | 5.7387 | 5.4633 | 826000 | 2000 | 817000 | 1000 | 1635800 | 5000 | 1640000 | 1630800 | 10.8333 | 4.6004 | 1.0509 | 5.524 | 1.0607 | 22.84% | 19.2% | 23.8654 | 37.935 | 2.0683 | 4.7869 | 1650897.5 | 1635400 | 1784642.9 | 91.64%
2022-12-02 | 2023 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 334195.71 | 7:16 | 17:54 | 9303.4 | 10086.9 | 10118.1 | 10148.1 | 10032.1 | 10246.8 | 9985.9 | 10267.7 | 10114.5 | 10036.9 | 9983.5 | 10137.6 | 10130.8 | 10113.3 | 10123.3 | 10278.6 | 10161.4 | 10241.2 | 10293.5 | 10262.2 | 10208.1 | 10243 | 10078 | 10200.5 | 10050.9 | 8755.8 | 10156.4 | 10171.1 | 10274.5 | 10000.3 | 9997.4 | 10244.5 | 10248.5 | 10357.8 | 10156.1 | 10156.7 | 10215.3 | 10209.9 | 10302.4 | 10071.5 | 10954.8 | 9779.8 | 10836.9 | 9672.1 | 10189.8 | 11603.2 | 9551.5 | 10948.8 | 9491.4 | 9212.5 | 10143.8 | 9660.2 | 10707 | 9372.1 | 10710.5 | 9473 | 9429.4 | 10444.6 | 9467.6 | 10768.2 | 10731.8 | 9322.8 | 10761.9 | 9478.5 | 9959.3 | 9499.9 | 10082.8 | 10519.7 | 10878.2 | 9667.1 | 10720.4 | 9237.6 | 9096.1 | 10756.2 | 9436.9 | 10704.3 | 9386.5 | 10805.4 | 9353.1 | 10597.7 | 9659 | 10416.3 | 9655.7 | 10904.3 | 9629.5 | 10174.3 | 9589.8 | 7969.6 | 10446.4 | 10010.5 | 9375.9 | 10856 | 10450.4 | 9533.3 | 9379.4 | 10523.6 | 9351.4 | 9778.1 | 10733.6 | 9172.1 | 10770.4 | 9319 | 10450.7 | 9544 | 10613.8 | 9080 | 10686.7 | 9596.4 | 10531 | 9542 | 10579.4 | 9706.2 | 9329.8 | 10441.1 | 9375.2 | 9335 | 10497 | 10264.5 | 10445 | 9507.4 | 10553.4 | 9295.1 | 10204.8 | 9617.4 | 10200.8 | 8833.1 | 10310.2 | 9402.2 | 9456.7 | 9570.8 | 9402.5 | 8167 | 9359.5 | 8309 | 9309.9 | 9300 | 10950.1 | 9508.7 | 10965.9 | 9630.6 | 10748 | 9343.9 | 9502.3 | 9416.3 | 10535.2 | 10988.1 | 10826.3 | 10812.1 | 10792.2 | 10901.7 | 9725.6 | 10819.4 | 10750.6 | 10957.5 | 10899.9 | 10309.2 | 10929.7 | 9110.5 | 10125.4 | 9825.7 | 24.075 | 23.8921 | 23.5482 | 0 | 23.7471 | 23.5508 | 0 | 37.5114 | 0 | 0 | 0 | 0 | 2.2394 | 1.9964 | 2.1349 | 2.1246 | 1.6033 | 2.0126 | 5.5783 | 5.3217 | 5.305 | 5.3217 | 5.1183 | 5.8583 | 4.2031 | 4.5376 | 4.2538 | 4.2037 | 4.6744 | 5.0676 | 0.80587 | 1.2032 | 1.0998 | 0 | 1.1622 | 0.95553 | 5.4967 | 5.4999 | 5.3416 | 5.0725 | 5.5891 | 5.2957 | 0.90531 | 1.1473 | 1.0322 | 0.90568 | 1.147 | 1.187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182197 | 324 | 172498 | 327 | 331657.959 | 840.867 | 4.2031 | 4.5376 | 4.2538 | 4.2037 | 4.6744 | 5.0676 | 5.4967 | 5.4999 | 5.3416 | 5.0725 | 5.5891 | 5.2957 | 803000 | 2000 | 792000 | 2000 | 1589600 | 5000 | 1591000 | 1584600 | 10.6333 | 4.49 | 1.0453 | 5.3826 | 1.0541 | 23.28% | 19.58% | 23.7626 | 37.5114 | 2.0185 | 5.4172 | 1604469 | 1589267 | 1741731.3133 | 91.25%
2022-12-03 | 2023 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 334195.71 | 7:17 | 17:55 | 8935.3 | 9686 | 9721.6 | 9753.8 | 9630.8 | 9831.4 | 9579.4 | 9841.7 | 9719 | 9631.4 | 9583.4 | 9732.9 | 9727.9 | 9709.7 | 9709.2 | 9867.6 | 9744.6 | 9830.8 | 9874.6 | 9842.5 | 9796 | 9826.7 | 9682.6 | 9792.9 | 9663.5 | 8422 | 9759.7 | 9784.7 | 9889.7 | 9612.2 | 9617.1 | 9850.2 | 9878.9 | 9972.3 | 9776.4 | 9769.3 | 9822 | 9830.1 | 9923.7 | 9712.2 | 10578.6 | 9447.5 | 10467.1 | 9338 | 9812.7 | 11199.1 | 9198.9 | 10613.6 | 9115.9 | 8852.6 | 9744.3 | 9278.2 | 10285.5 | 8987.8 | 10320.3 | 9119.6 | 9069.8 | 10045.5 | 9101.2 | 10350 | 10320.9 | 8952.1 | 10331.3 | 9098.3 | 9573.7 | 9142.2 | 9700.8 | 10153.2 | 10457.8 | 9312.3 | 10315.2 | 8906.5 | 8751.9 | 10358.1 | 9071.4 | 10301 | 9023.3 | 10387.5 | 8994.7 | 10171.1 | 9336.6 | 10069.1 | 9339.9 | 10539.6 | 9317.3 | 9842 | 9260.9 | 7692 | 10112.1 | 9668.2 | 9089.8 | 10538.7 | 10147.3 | 9247.2 | 9103.8 | 10174.1 | 9037.4 | 9365.7 | 10343.1 | 8808.9 | 10375.2 | 8970.1 | 10079.6 | 9198.9 | 10236.3 | 8743.2 | 10296.2 | 9243.1 | 10164.7 | 9210.9 | 10207.3 | 9360.1 | 8967.9 | 10043.4 | 9041.3 | 8994.7 | 10105.4 | 9890.3 | 10065.3 | 9166.9 | 10177.5 | 8958.7 | 9843.2 | 9262.2 | 9836.6 | 8515.2 | 9932.9 | 9055.5 | 9107.1 | 9211.5 | 9060.5 | 7873 | 9017.4 | 8007 | 8991.3 | 8981 | 10557.7 | 9167.7 | 10574.1 | 9286.4 | 10364 | 9017.2 | 9175.4 | 9087.9 | 10150.9 | 10588.2 | 10427.6 | 10422.2 | 10418 | 10512.1 | 9380.6 | 10429 | 10353.4 | 10548.5 | 10489.6 | 9921.2 | 10523.2 | 8774.1 | 9752.7 | 9454.1 | 24.2609 | 23.6701 | 23.6637 | 0 | 23.6054 | 23.4069 | 0 | 35.7465 | 0 | 0 | 0 | 0 | 2.1331 | 2.1784 | 2.103 | 2.1854 | 1.8915 | 2.1644 | 4.8383 | 4.715 | 5.09 | 5.2067 | 4.7883 | 5.845 | 4.0263 | 4.3483 | 4.0947 | 4.0382 | 4.4936 | 4.8566 | 0.91949 | 1.0754 | 1.0699 | 0 | 1.1162 | 0.91895 | 5.2418 | 5.2427 | 5.118 | 4.8564 | 5.3598 | 5.0849 | 0.92267 | 1.0321 | 1.0016 | 0.94924 | 1.1067 | 1.1406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182970 | 326 | 173263 | 329 | 333189.293 | 845.867 | 4.0263 | 4.3483 | 4.0947 | 4.0382 | 4.4936 | 4.8566 | 5.2418 | 5.2427 | 5.118 | 4.8564 | 5.3598 | 5.0849 | 773000 | 2000 | 765000 | 2000 | 1531334 | 5000 | 1534000 | 1526334 | 10.6333 | 4.3096 | 1.02 | 5.1506 | 1.0255 | 23.67% | 19.91% | 23.7214 | 35.7465 | 2.1093 | 5.0806 | 1545186.2 | 1531067 | 1669043.7554 | 91.73%
2022-12-04 | 2023 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 334195.71 | 7:18 | 17:55 | 8834.4 | 9558.7 | 9604 | 9635 | 9511.5 | 9730.3 | 9460.1 | 9716.2 | 9595.9 | 9508.1 | 9461.3 | 9612.9 | 9615.6 | 9589.2 | 9619.6 | 9759 | 9610 | 9680.9 | 9737.8 | 9682.5 | 9683.9 | 9712.5 | 9578.8 | 9688.3 | 9543.2 | 8313.3 | 9645.5 | 9666.5 | 9775.9 | 9499 | 9497.3 | 9730 | 9742.8 | 9838.8 | 9646.6 | 9698 | 9742.5 | 9713.1 | 9810 | 9581.3 | 10447.4 | 9329.9 | 10325.3 | 9211.1 | 9684.1 | 11049.6 | 9080.7 | 10473.7 | 9002.1 | 8739.1 | 9630.9 | 9164.5 | 10156.6 | 8874.1 | 10194 | 9009.6 | 8964.1 | 9922.4 | 8982.9 | 10227.7 | 10205.8 | 8844 | 10201.4 | 8990.4 | 9459.4 | 9038.3 | 9595 | 10035.5 | 10344.5 | 9205.8 | 10203.5 | 8807.2 | 8647.5 | 10246.2 | 8978.7 | 10192.6 | 8923.4 | 10264.6 | 8884.2 | 10057.7 | 9215.3 | 9942.3 | 9234.8 | 10405.3 | 9203.2 | 9726.3 | 9139.7 | 7597.3 | 10097.1 | 9569.6 | 8985.6 | 10432 | 10032 | 9167.5 | 9052.5 | 10137.2 | 8948.6 | 9307.8 | 10214.1 | 8717.8 | 10239.1 | 8863.2 | 9946.9 | 9098 | 10107.4 | 8644.5 | 10173.6 | 9129 | 10041.7 | 9105.8 | 10105.4 | 9243.8 | 8867.3 | 9932.5 | 8935.4 | 8882.2 | 9991.5 | 9773.9 | 9943 | 9054.4 | 10050.5 | 8848 | 9726.1 | 9164.3 | 9722.3 | 8413.7 | 9816.7 | 8951.3 | 9008.2 | 9119.4 | 8965 | 7790.1 | 8901.7 | 7894.7 | 8856.6 | 8854.2 | 10405.9 | 9034.4 | 10417.4 | 9160.2 | 10223.2 | 8896.2 | 9049.3 | 8962.8 | 9989.5 | 10424.3 | 10268 | 10265.1 | 10255.3 | 10354.5 | 9240.7 | 10268 | 10220.2 | 10403.2 | 10327.1 | 9773.2 | 10353.5 | 8645.7 | 9617.3 | 9316.6 | 24.0894 | 23.4491 | 23.3382 | 0 | 23.3865 | 23.1758 | 0 | 35.0989 | 0 | 0 | 0 | 0 | 2.3449 | 2.3709 | 2.4332 | 2.4638 | 2.1912 | 2.3733 | 4.935 | 4.6317 | 5.065 | 5.81 | 4.7517 | 5.0983 | 3.9768 | 4.2952 | 4.0337 | 3.9867 | 4.4347 | 4.7829 | 0.9065 | 1.0717 | 1.1128 | 0 | 1.1109 | 0.91556 | 5.1694 | 5.1751 | 5.0338 | 4.7791 | 5.2946 | 5.0063 | 0.90855 | 1.0291 | 1.0166 | 0.91944 | 1.1021 | 1.1353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183734 | 327 | 174019 | 331 | 334702.559 | 850.867 | 3.9768 | 4.2952 | 4.0337 | 3.9867 | 4.4347 | 4.7829 | 5.1694 | 5.1751 | 5.0338 | 4.7791 | 5.2946 | 5.0063 | 764000 | 1000 | 756000 | 2000 | 1513266 | 5000 | 1517000 | 1508266 | 10.6167 | 4.2517 | 1.0235 | 5.0764 | 1.0185 | 24.07% | 20.06% | 23.4878 | 35.0989 | 2.3629 | 5.0486 | 1526384.8 | 1512934 | 1650096.0057 | 91.69%
2022-12-05 | 2023 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 334195.71 | 7:18 | 17:55 | 9351 | 10099.2 | 10124 | 10163 | 10012.9 | 10254.9 | 9969.9 | 10236 | 10149.7 | 10050 | 10002.2 | 10172.7 | 10152.1 | 10137 | 10177.8 | 10298.7 | 10189.6 | 10250 | 10289.9 | 10249.3 | 10156.1 | 10179.6 | 10065.6 | 10166.3 | 10064.6 | 8764.3 | 10173.1 | 10200.9 | 10299 | 9998.9 | 10009.3 | 10252 | 10268.5 | 10381.7 | 10171.2 | 10233.6 | 10264.9 | 10233 | 10325 | 10092.8 | 11042.7 | 9867.1 | 10898.1 | 9721.7 | 10216.4 | 11609.5 | 9560.2 | 11059.3 | 9514.8 | 9239.3 | 10186.7 | 9681.7 | 10721 | 9362.8 | 10771.6 | 9512.4 | 9484.7 | 10495.5 | 9510.7 | 10823.9 | 10807 | 9364.7 | 10797.6 | 9519.7 | 10002.4 | 9559 | 10157.7 | 10619 | 10951.6 | 9739.7 | 10806 | 9323.7 | 9164.8 | 10845.9 | 9520.8 | 10789.9 | 9449 | 10868.9 | 9406.2 | 10651.8 | 9753 | 10533.8 | 9789.3 | 11010.6 | 9743.9 | 10293.1 | 9694.9 | 8041.6 | 10635.8 | 10109.8 | 9498.2 | 11002.8 | 10585.6 | 9665.4 | 9535.6 | 10711.6 | 9405.9 | 9801.4 | 10756.8 | 9183 | 10787.4 | 9339.8 | 10487.5 | 9588.3 | 10656.9 | 9109.5 | 10725.2 | 9621.2 | 10581.3 | 9591.3 | 10626.3 | 9731.3 | 9329.2 | 10455.6 | 9388.3 | 9342.9 | 10500.7 | 10291.9 | 10448.9 | 9533.2 | 10581.1 | 9309.1 | 10226.4 | 9645.4 | 10211.8 | 8844.7 | 10323.8 | 9408.5 | 9490.9 | 9613.7 | 9506.7 | 8217.8 | 9356.7 | 8306.2 | 9372.3 | 9366.4 | 11033.1 | 9586.1 | 11044.8 | 9724 | 10841 | 9444.9 | 9604.7 | 9494.3 | 10603.2 | 11074.5 | 10894.4 | 10901.1 | 10876.2 | 10963.1 | 9817.5 | 10903.9 | 10916.6 | 11128.5 | 10987.2 | 10411 | 11007.8 | 9201.9 | 10228.7 | 9928.7 | 23.4477 | 23.1268 | 23.022 | 0 | 23.1576 | 22.9653 | 0 | 34.8309 | 0 | 0 | 0 | 0 | 2.662 | 2.5865 | 2.5527 | 2.7373 | 2.3584 | 2.6455 | 5.3717 | 5.335 | 5.2567 | 5.6283 | 5.3417 | 6.0267 | 4.1571 | 4.4825 | 4.2113 | 4.1759 | 4.6347 | 5.0628 | 0.95173 | 1.1166 | 1.1631 | 0 | 1.1548 | 0.95711 | 5.4501 | 5.4368 | 5.2952 | 5.0345 | 5.5723 | 5.2805 | 0.95107 | 1.0722 | 1.0589 | 0.955 | 1.1479 | 1.1869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184541 | 329 | 174817 | 332 | 336300.56 | 855.733 | 4.1571 | 4.4825 | 4.2113 | 4.1759 | 4.6347 | 5.0628 | 5.4501 | 5.4368 | 5.2952 | 5.0345 | 5.5723 | 5.2805 | 807000 | 2000 | 798000 | 1000 | 1598001 | 4866 | 1602000 | 1593135 | 10.6167 | 4.4541 | 1.0687 | 5.3449 | 1.062 | 23.99% | 19.87% | 23.1439 | 34.8309 | 2.5904 | 5.4933 | 1612543.3 | 1597600 | 1735870.9164 | 92.03%
2022-12-06 | 2023 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 334195.71 | 7:18 | 17:56 | 9419.5 | 10188.7 | 10237.5 | 10259.5 | 10134.5 | 10379.3 | 10066.8 | 10348 | 10234.1 | 10101.3 | 10096.1 | 10261.4 | 10283.4 | 10256.6 | 10339.2 | 10439.2 | 10348.6 | 10396.1 | 10445.2 | 10397.4 | 10339.1 | 10381.9 | 10229.1 | 10348.8 | 10199.3 | 8869.4 | 10303.7 | 10360.1 | 10474.6 | 10152.3 | 10165.1 | 10418.4 | 10437.6 | 10547.5 | 10327.5 | 10403.5 | 10448.4 | 10398.9 | 10503.7 | 10258.9 | 11157.3 | 9956.1 | 11009.5 | 9814 | 10380.1 | 11853.2 | 9695.4 | 11180.9 | 9624 | 9352.6 | 10308.9 | 9815.4 | 10874.2 | 9484.7 | 10920.1 | 9656.4 | 9575.7 | 10596.8 | 9599.2 | 10924.7 | 10844 | 9447 | 10847.4 | 9554.1 | 10087.8 | 9616.7 | 10211.8 | 10666.8 | 11025.4 | 9781.4 | 10860.5 | 9359.5 | 9221.5 | 10898.2 | 9572.1 | 10834.4 | 9481.4 | 10916.6 | 9437.6 | 10700.5 | 9786.8 | 10563.5 | 9820.8 | 11056.9 | 9783.9 | 10336.5 | 9783.9 | 8092.7 | 10720.1 | 10175.6 | 9584.9 | 11120.4 | 10708.5 | 9786.8 | 9658.9 | 10826.2 | 9516.5 | 9918.5 | 10892.7 | 9298.3 | 10951.5 | 9485.6 | 10657.8 | 9738.1 | 10831.8 | 9256.1 | 10904 | 9771.7 | 10757.7 | 9752.1 | 10807.7 | 9887.6 | 9441 | 10593.1 | 9533.1 | 9489.4 | 10666.6 | 10439.6 | 10620.5 | 9678.7 | 10747.3 | 9461.4 | 10397.7 | 9810.8 | 10391 | 8989 | 10500.3 | 9569.7 | 9621.6 | 9734.3 | 9667.2 | 8341.7 | 9473.8 | 8383 | 9459.4 | 9447.8 | 11059.2 | 9605.7 | 11102.9 | 9757.2 | 10895.4 | 9509 | 9679 | 9568.1 | 10646.5 | 11125.4 | 10905 | 10938.8 | 10911.9 | 11003.8 | 9852.8 | 10949.1 | 10994.8 | 11194.8 | 11098.3 | 10506 | 11072.3 | 9257.5 | 10256.7 | 9966 | 23.1869 | 22.8783 | 22.9542 | 0 | 22.9311 | 22.7004 | 0 | 34.1651 | 0 | 0 | 0 | 0 | 2.923 | 2.974 | 2.9243 | 2.9893 | 2.6972 | 2.9259 | 6.8517 | 6.02 | 5.8633 | 6.32 | 5.88 | 6.265 | 4.1744 | 4.5283 | 4.2297 | 4.1824 | 4.6952 | 5.2128 | 0.95493 | 1.1382 | 1.1671 | 0 | 1.18 | 0.96488 | 5.5077 | 5.5168 | 5.3488 | 5.0474 | 5.6813 | 5.4182 | 0.95326 | 1.0932 | 1.0606 | 0.97073 | 1.1716 | 1.196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185356 | 331 | 175624 | 334 | 337915.826 | 860.667 | 4.1744 | 4.5283 | 4.2297 | 4.1824 | 4.6952 | 5.2128 | 5.5077 | 5.5168 | 5.3488 | 5.0474 | 5.6813 | 5.4182 | 815000 | 2000 | 807000 | 2000 | 1615266 | 4934 | 1618000 | 1610332 | 10.6333 | 4.5038 | 1.081 | 5.42 | 1.0742 | 24% | 19.82% | 22.9302 | 34.1651 | 2.9056 | 6.2 | 1629892.4 | 1615200 | 1765221.8139 | 91.5%
2022-12-07 | 2023 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 334195.71 | 7:17 | 17:56 | 9494.6 | 10266.1 | 10307.8 | 10331.7 | 10213.2 | 10462.3 | 10130.9 | 10422.7 | 10305 | 10159.1 | 10168.8 | 10322.5 | 10354.7 | 10322.3 | 10419.9 | 10511.1 | 10426 | 10468.4 | 10519.5 | 10463.3 | 10421.2 | 10458.7 | 10293.3 | 10435.8 | 10305.6 | 8975.1 | 10461.4 | 10451 | 10513.2 | 10188.9 | 10208.1 | 10460.4 | 10512.3 | 10607.1 | 10389.4 | 10488.3 | 10531.9 | 10468.4 | 10575.2 | 10317 | 11287.2 | 10063.8 | 11115.6 | 9927 | 10458.2 | 11887.9 | 9846.1 | 11302.4 | 9678.6 | 9402.8 | 10366 | 9861.1 | 10936.6 | 9534.5 | 10981.3 | 9701.3 | 9644.3 | 10674.1 | 9656.6 | 11002.9 | 10972.7 | 9508.4 | 10937.8 | 9636.4 | 10178.8 | 9721 | 10305.4 | 10790.2 | 11135.3 | 9895.6 | 10975.5 | 9468.6 | 9310.8 | 11022.6 | 9671.4 | 10960.7 | 9606.7 | 11027.9 | 9540.7 | 10820.9 | 9906.6 | 10697.9 | 9939.6 | 11191 | 9894.8 | 10453.9 | 9873.6 | 8180.9 | 10783.8 | 10263.9 | 9661.6 | 11194.7 | 10773.3 | 9827.4 | 9692.5 | 10895.7 | 9576.8 | 9998.1 | 10955.5 | 9360.4 | 11007.7 | 9532.9 | 10721.6 | 9793.3 | 10877.5 | 9306.5 | 10954 | 9819.7 | 10803.3 | 9804.8 | 10870 | 9929.5 | 9516.4 | 10694.2 | 9586.5 | 9551.2 | 10736.7 | 10517.2 | 10688 | 9742 | 10818.1 | 9524.4 | 10454.9 | 9858.2 | 10450.6 | 9038 | 10557.2 | 9631.3 | 9692.7 | 9803.3 | 9693 | 8392.3 | 9529.8 | 8489.8 | 9582.8 | 9614.8 | 11202.9 | 9727.3 | 11242.1 | 9888.5 | 11054.5 | 9648.3 | 9831.4 | 9697.8 | 10773.5 | 11258.8 | 11049.2 | 11073.5 | 11061.3 | 11141.4 | 9976.9 | 11083.5 | 11078.8 | 11280 | 11206.2 | 10623.7 | 11191.8 | 9357 | 10474.2 | 10077 | 23.6711 | 23.5123 | 23.2837 | 0 | 23.4952 | 23.2345 | 0 | 36.4701 | 0 | 0 | 0 | 0 | 1.3602 | 2.063 | 2.0881 | 2.2426 | 1.8063 | 2.1907 | 4.84 | 4.47 | 5.18 | 5.2267 | 4.4833 | 4.8167 | 4.2002 | 4.5656 | 4.2698 | 4.2195 | 4.7372 | 5.2892 | 0.95555 | 1.1362 | 1.1738 | 0 | 1.1594 | 0.98479 | 5.5629 | 5.5793 | 5.4192 | 5.1195 | 5.7308 | 5.4951 | 0.95464 | 1.0874 | 1.0662 | 0.93113 | 1.1515 | 1.2201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186178 | 332 | 176437 | 336 | 339543.36 | 865.6 | 4.2002 | 4.5656 | 4.2698 | 4.2195 | 4.7372 | 5.2892 | 5.5629 | 5.5793 | 5.4192 | 5.1195 | 5.7308 | 5.4951 | 822000 | 1000 | 813000 | 2000 | 1627534 | 4933 | 1632000 | 1622601 | 10.65 | 4.5469 | 1.082 | 5.4845 | 1.0685 | 23.8% | 19.48% | 23.4394 | 36.4701 | 1.9585 | 4.8361 | 1643653.7 | 1627467 | 1772887.6866 | 91.8%
2022-12-08 | 2023 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 334195.71 | 7:20 | 17:56 | 9536.3 | 10307 | 10346.3 | 10382.9 | 10230.6 | 10479.4 | 10155.9 | 10427.9 | 10302.8 | 10146.8 | 10168.9 | 10335.7 | 10381.1 | 10357.6 | 10445.4 | 10537.7 | 10449.8 | 10486.9 | 10547.6 | 10492.6 | 10428.8 | 10469.8 | 10320.3 | 10451.1 | 10322.5 | 8997.5 | 10493.5 | 10475.2 | 10565.4 | 10229.7 | 10250.7 | 10508.2 | 10541.8 | 10627.7 | 10409.8 | 10521.7 | 10573.2 | 10497.9 | 10597.4 | 10331.1 | 11313.8 | 10076.1 | 11141.3 | 9940.2 | 10450.8 | 11887.3 | 9856.9 | 11331.3 | 9722.8 | 9434.8 | 10398.5 | 9892.5 | 10968.7 | 9559.5 | 11015.1 | 9725.3 | 9682.3 | 10711.2 | 9691.1 | 11044.1 | 11007.7 | 9539.4 | 10965.2 | 9661.1 | 10207.9 | 9749.8 | 10347.2 | 10816.4 | 11188.1 | 9929.8 | 11028.4 | 9495.7 | 9348.2 | 11061.3 | 9720.2 | 10996.3 | 9637.7 | 11064 | 9562.6 | 10837.7 | 9937.2 | 10725.5 | 9949.2 | 11221.8 | 9916.4 | 10471.1 | 9899.1 | 8194.3 | 10790.3 | 10267.6 | 9665.5 | 11198.9 | 10770.6 | 9831.2 | 9691.5 | 10884.8 | 9632.1 | 9987.5 | 10967.5 | 9358.8 | 11009.1 | 9552.3 | 10723.2 | 9793.4 | 10886.5 | 9310.4 | 10959.1 | 9825.2 | 10800 | 9804.4 | 10874.6 | 9929.2 | 9523.8 | 10758.1 | 9609.2 | 9563.3 | 10742.1 | 10632 | 10717.4 | 9773.3 | 10872.4 | 9535.8 | 10457.8 | 9869.5 | 10469.1 | 9027.8 | 10564.2 | 9632.4 | 9718.1 | 9848.4 | 9707 | 8419.3 | 9601.9 | 8562.5 | 9566.4 | 9637.2 | 11218.4 | 9730.6 | 11253.9 | 9909.1 | 11090.7 | 9674 | 9870.5 | 9719.4 | 10770 | 11274.2 | 11037.6 | 11070.1 | 11052.5 | 11141.2 | 9987.8 | 11088.1 | 11057.5 | 11271.6 | 11177.5 | 10589.7 | 11174.3 | 9335.5 | 10570.7 | 10067.6 | 25.2111 | 24.793 | 24.5785 | 0 | 24.7625 | 24.533 | 0 | 38.9844 | 0 | 0 | 0 | 0 | 0.52572 | 1.4293 | 1.4907 | 1.5304 | 1.028 | 1.468 | 2.9233 | 4.0583 | 3.7533 | 4.0183 | 3.9033 | 3.1133 | 4.2265 | 4.5733 | 4.2841 | 4.2451 | 4.7482 | 5.3188 | 0.95478 | 1.1285 | 1.1717 | 0 | 1.1611 | 0.95249 | 5.6196 | 5.6167 | 5.4563 | 5.1657 | 5.765 | 5.5171 | 0.95229 | 1.0785 | 1.0625 | 0.89009 | 1.152 | 1.1815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187002 | 334 | 177251 | 338 | 341174.56 | 870.533 | 4.2265 | 4.5733 | 4.2841 | 4.2451 | 4.7482 | 5.3188 | 5.6196 | 5.6167 | 5.4563 | 5.1657 | 5.765 | 5.5171 | 824000 | 2000 | 814000 | 2000 | 1631200 | 4933 | 1634000 | 1626267 | 10.6 | 4.566 | 1.0737 | 5.5234 | 1.0528 | 23.52% | 19.06% | 24.7756 | 38.9844 | 1.2453 | 3.6283 | 1646910.6 | 1630867 | 1773002.3561 | 91.98%
2022-12-09 | 2023 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 334195.71 | 7:13 | 17:56 | 9456.6 | 10214.6 | 10253.7 | 10297 | 10136.5 | 10394.5 | 10058.3 | 10328.2 | 10264.9 | 10100.2 | 10122.9 | 10281.9 | 10297.6 | 10272.6 | 10348.8 | 10444.4 | 10354.3 | 10392.5 | 10457.1 | 10403.9 | 10349.3 | 10381.5 | 10249.3 | 10372.6 | 10256.6 | 8940.1 | 10414 | 10399.2 | 10485.3 | 10156.4 | 10183.2 | 10437.3 | 10485.5 | 10571.8 | 10345.8 | 10452.7 | 10501.1 | 10431.5 | 10529.3 | 10278.6 | 11237 | 10005.8 | 11088.2 | 9888.4 | 10423 | 11893.5 | 9792.4 | 11261.1 | 9646.9 | 9366.6 | 10315.2 | 9823.9 | 10874.9 | 9473.3 | 10950.7 | 9665.4 | 9620.7 | 10636.8 | 9618.5 | 10963.1 | 10945.3 | 9469.3 | 10691 | 9590.3 | 10138.3 | 9689.1 | 10280.1 | 10750.1 | 11105.5 | 9870.2 | 10945.5 | 9431.9 | 9273.6 | 10985.8 | 9649.1 | 10928.5 | 9580.6 | 10981.6 | 9494.3 | 10769.6 | 9892.6 | 10681.8 | 9909.4 | 11171.2 | 9869.6 | 10421.8 | 9838.8 | 8167.4 | 10757.6 | 10234.9 | 9614.9 | 11146.6 | 10743.1 | 9833.7 | 9703.9 | 10814.8 | 9588.6 | 9952.5 | 10938.2 | 9397.9 | 10981.7 | 9519.5 | 10688.7 | 9785 | 10854.1 | 9291.3 | 10923.3 | 9794.9 | 10773.1 | 9784.6 | 10846.7 | 9920 | 9562.9 | 10752.7 | 9686.2 | 9563.8 | 10745.4 | 10541.9 | 10724.2 | 9743.5 | 10867.4 | 9530.8 | 10427.7 | 9847.4 | 10437.4 | 9001.4 | 10551.1 | 9607.9 | 9690.2 | 9823 | 9710 | 8388.6 | 9605.3 | 8535.5 | 9542.6 | 9609.1 | 11179.3 | 9694.4 | 11205.3 | 9867.2 | 11046.4 | 9627.4 | 9820.4 | 9673.8 | 10747.5 | 11246.4 | 11010.2 | 11030.9 | 11018.2 | 11112.5 | 9944.1 | 11042.3 | 11042 | 11237.9 | 11148.9 | 10559.6 | 11148 | 9319.9 | 10538.6 | 10032.5 | 25.6053 | 25.119 | 24.7757 | 0 | 24.922 | 24.722 | 0 | 38.7331 | 0 | 0 | 0 | 0 | 1.6281 | 2.0517 | 2.0351 | 1.8454 | 1.7693 | 2.0209 | 4.675 | 4.3567 | 5.2417 | 4.0933 | 5.19 | 4.7083 | 4.1993 | 4.5374 | 4.2653 | 4.2299 | 4.7276 | 5.2898 | 0.96073 | 1.1205 | 1.176 | 0 | 1.1589 | 0.94907 | 5.5805 | 5.5675 | 5.4275 | 5.1537 | 5.7268 | 5.4884 | 0.95885 | 1.0717 | 1.0667 | 0.89414 | 1.1462 | 1.1804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187820 | 336 | 178063 | 339 | 342798.627 | 875.467 | 4.1993 | 4.5374 | 4.2653 | 4.2299 | 4.7276 | 5.2898 | 5.5805 | 5.5675 | 5.4275 | 5.1537 | 5.7268 | 5.4884 | 818000 | 2000 | 812000 | 1000 | 1624067 | 4934 | 1627000 | 1619133 | 10.7167 | 4.5416 | 1.073 | 5.4907 | 1.053 | 23.63% | 19.18% | 25.0288 | 38.7331 | 1.8918 | 4.7108 | 1638848.6 | 1624000 | 1765910.1976 | 91.96%
2022-12-10 | 2023 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 334195.71 | 7:20 | 17:57 | 9474.5 | 10214.7 | 10251.1 | 10302.7 | 10131.8 | 10405.1 | 10048.6 | 10306.5 | 10282.8 | 10099.2 | 10149.1 | 10303 | 10335.8 | 10303.5 | 10367.4 | 10480.1 | 10389.6 | 10447.8 | 10486 | 10422.3 | 10367.2 | 10406.4 | 10252.1 | 10398.4 | 10269.9 | 8948.8 | 10432.4 | 10425.8 | 10512.5 | 10167.5 | 10204 | 10457.5 | 10489.2 | 10569.7 | 10346 | 10469.9 | 10533.1 | 10444.4 | 10561 | 10293.9 | 11250.8 | 10029 | 11160.7 | 9932.9 | 10491.5 | 11944.4 | 9835.8 | 11297 | 9672.8 | 9379.9 | 10336 | 9827.2 | 10900.9 | 9476.8 | 10973.4 | 9679.2 | 9634.9 | 10649.4 | 9629.7 | 10974.9 | 10954.7 | 9483.4 | 10484.7 | 9584.6 | 10136.1 | 9699.9 | 10292.5 | 10759.5 | 11119.7 | 9885.8 | 10961.5 | 9445.7 | 9281 | 11000.3 | 9655 | 10934.1 | 9593.8 | 10987.4 | 9499.3 | 10768.6 | 9897.1 | 10703 | 9941.2 | 11192.3 | 9899.8 | 10455.9 | 9844.4 | 8180.5 | 10815.3 | 10253.5 | 9654.2 | 11217.6 | 10785.2 | 9861.8 | 9720.7 | 10833.3 | 9574.4 | 9949.5 | 10932.1 | 9489.6 | 11020.2 | 9516.1 | 10700 | 9803.9 | 10865.8 | 9290.4 | 10933.2 | 9805.9 | 10777.6 | 9788 | 10862 | 9927.1 | 9603.8 | 10741.8 | 9729.5 | 9567.8 | 10776.7 | 10467 | 10732.5 | 9741 | 10870.6 | 9531.1 | 10423.7 | 9839.2 | 10421.1 | 9006 | 10547.1 | 9608.2 | 9681 | 9799.5 | 9700.4 | 8384.8 | 9587.5 | 8518.2 | 9523.2 | 9587.6 | 11194.4 | 9711.8 | 11229.4 | 9888.7 | 11046.1 | 9610.5 | 9815.8 | 9639.6 | 10741.3 | 11236.7 | 10987 | 11042.5 | 11019.3 | 11108.1 | 9959.3 | 11069.4 | 11073.6 | 11251.2 | 11129.1 | 10530.3 | 11118.2 | 9307.8 | 10541.7 | 10043.8 | 24.95 | 24.42 | 24.15 | 0 | 24.32 | 24.01 | 0 | 36.85 | 0 | 0 | 0 | 0 | 2.67 | 2.74 | 2.69 | 2.73 | 2.32 | 2.61 | 5.07 | 5.3 | 5.72 | 5.28 | 5.18 | 5 | 4.17 | 4.52 | 4.24 | 4.19 | 4.69 | 5.24 | 0.96 | 1.12 | 1.17 | 0 | 1.15 | 0.98 | 5.54 | 5.53 | 5.39 | 5.11 | 5.68 | 5.44 | 0.96 | 1.07 | 1.06 | 0.92 | 1.14 | 1.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188639 | 338 | 178876 | 341 | 344424.094 | 880.467 | 4.17 | 4.52 | 4.24 | 4.19 | 4.69 | 5.24 | 5.54 | 5.53 | 5.39 | 5.11 | 5.68 | 5.44 | 819000 | 2000 | 813000 | 2000 | 1625467 | 5000 | 1628000 | 1620467 | 10.6167 | 4.5083 | 1.076 | 5.4483 | 1.0617 | 23.87% | 19.49% | 24.37 | 36.85 | 2.6267 | 5.2583 | 1640532.6 | 1625400 | 1761682.8856 | 92.26%
2022-12-11 | 2023 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 334143.5 | 7:22 | 17:57 | 9353 | 10076.6 | 10149.7 | 10202.6 | 10012.7 | 10288.1 | 9905.7 | 10152.8 | 10144.8 | 9951.6 | 10003.8 | 10157.1 | 10207.3 | 10156.4 | 10243.1 | 10352.8 | 10271.8 | 10320.9 | 10344.2 | 10276.7 | 10234.3 | 10264.9 | 10140.9 | 10257 | 10128.5 | 8829.6 | 10290.5 | 10290.7 | 10378.2 | 10041 | 10084.2 | 10320.9 | 10338.8 | 10417.3 | 10197.1 | 10335.4 | 10413.8 | 10310.8 | 10422.2 | 10155.7 | 11086.1 | 9899.5 | 11017.7 | 9799.8 | 10396.8 | 11757.7 | 9738.3 | 11132.1 | 9531.6 | 9251.9 | 10190.5 | 9662.9 | 10747.6 | 9347.4 | 10830.3 | 9553 | 9507.8 | 10500.1 | 9493.3 | 10814.8 | 10795.8 | 9349.2 | 10293 | 9436.1 | 10008.7 | 9578.4 | 10148.7 | 10632.5 | 10962.9 | 9772.5 | 10833.5 | 9350.7 | 9168.5 | 10882.9 | 9531.8 | 10823.6 | 9492.4 | 10843.8 | 9381.8 | 10638.7 | 9783.5 | 10596.2 | 9870.9 | 11064.9 | 9798.1 | 10346.1 | 9709.7 | 8086.5 | 10696.1 | 10143.6 | 9534 | 11062.1 | 10636 | 9715.9 | 9570.5 | 10721.1 | 9470.2 | 9851.1 | 10794.3 | 9374.5 | 10864 | 9391.4 | 10556.2 | 9673 | 10718 | 9163.6 | 10791.9 | 9686.3 | 10637.6 | 9656.5 | 10705.3 | 9803.2 | 9499.2 | 10633.5 | 9597.6 | 9442.8 | 10652.5 | 10353.6 | 10597 | 9641.1 | 10739.6 | 9424.8 | 10305.8 | 9726.4 | 10301.7 | 8907.3 | 10431.5 | 9493.6 | 9555.7 | 9672.4 | 9581.7 | 8276.9 | 9474.7 | 8443.7 | 9486.6 | 9539.6 | 11101.3 | 9654 | 11152.7 | 9846.5 | 10989.4 | 9596.5 | 9776.2 | 9610.3 | 9844.8 | 10274.7 | 10070.9 | 10097.4 | 10071.4 | 10146 | 9108.8 | 10125.3 | 10181 | 10348.7 | 10238.7 | 9700.9 | 10101.7 | 8567.2 | 9689.1 | 9235.6 | 24.9 | 24.13 | 24.08 | 0 | 23.97 | 24.04 | 0 | 34.39 | 0 | 0 | 0 | 0 | 4.41 | 4.39 | 4.2 | 4.5 | 4.07 | 4.24 | 7.21 | 8.14 | 7.58 | 7.9 | 7.59 | 6.95 | 4.1 | 4.43 | 4.15 | 4.12 | 4.6 | 5.16 | 0.94 | 1.11 | 1.14 | 0 | 1.15 | 0.95 | 5.42 | 5.41 | 5.26 | 4.98 | 5.57 | 5.37 | 0.93 | 1.07 | 1.04 | 1.08 | 1.14 | 1.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189448 | 339 | 179667 | 343 | 346017.4 | 885.6 | 4.1 | 4.43 | 4.15 | 4.12 | 4.6 | 5.16 | 5.42 | 5.41 | 5.26 | 4.98 | 5.57 | 5.37 | 809000 | 1000 | 791000 | 2000 | 1593306 | 5133 | 1597000 | 1588173 | 10.5833 | 4.4267 | 1.058 | 5.335 | 1.0733 | 23.9% | 20.12% | 24.224 | 34.39 | 4.3017 | 7.5617 | 1608388.9 | 1593266 | 1739193.0749 | 91.61%
2022-12-12 | 2023 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 334143.5 | 7:14 | 17:57 | 9247.3 | 9955.6 | 10041.1 | 10095.1 | 9897.5 | 10166 | 9783.4 | 10027.3 | 10045.9 | 9855.4 | 9904.4 | 10054 | 10075.6 | 10023.3 | 10138.3 | 10209.9 | 10184.9 | 10215.9 | 10237.3 | 10163.5 | 10131.1 | 10152.5 | 10045.2 | 10157.5 | 10046.8 | 8747.7 | 10185.1 | 10190 | 10281 | 9945.3 | 10002.8 | 10240.1 | 10241.1 | 10306.8 | 10092.9 | 10229.1 | 10311 | 10214.9 | 10320.6 | 10065.2 | 11080.2 | 9828.7 | 10915.2 | 9735.1 | 10332.1 | 11685.2 | 9640.6 | 11014.9 | 9442.6 | 9155.5 | 10098 | 9565.5 | 10642.8 | 9242.8 | 10730.8 | 9456.6 | 9424.6 | 10401.3 | 9400.1 | 10707.1 | 10676.7 | 9253 | 10185.2 | 9328.3 | 9898.6 | 9459.5 | 10037.6 | 10506.6 | 10844.4 | 9643.6 | 10692.2 | 9228.5 | 9067.7 | 10729.6 | 9418.3 | 10668.4 | 9365.1 | 10712.6 | 9261.3 | 10484.6 | 9647.4 | 10459.9 | 9735.1 | 10915.3 | 9662.9 | 10210.5 | 9612.6 | 7987.5 | 10537.4 | 10013 | 9427.9 | 10919.1 | 10507 | 9587.7 | 9448.5 | 10587.3 | 9381.3 | 9753.9 | 10686.8 | 9292.5 | 10747.8 | 9304.2 | 10459.5 | 9577.2 | 10611.9 | 9077 | 10687.1 | 9579.5 | 10551.6 | 9571.4 | 10605.2 | 9701.8 | 9402 | 10522 | 9493.6 | 9342.2 | 10545.2 | 10228.4 | 10490 | 9522.8 | 10622.1 | 9321.2 | 10202.6 | 9633 | 10197.3 | 8822.8 | 10328.5 | 9385.5 | 9414.5 | 9513 | 9446.8 | 8156.1 | 9359.6 | 8358.7 | 9318.7 | 9356.9 | 10903.1 | 9481.9 | 10949.6 | 9663.1 | 10789.3 | 9426.6 | 9587.4 | 9497.8 | 10537.1 | 10989.9 | 10791.2 | 10798 | 10541.5 | 10862.3 | 9744.9 | 10834.6 | 10827 | 11001.1 | 10914 | 10355.6 | 10790.6 | 9144.6 | 10341.8 | 9835.9 | 24.91 | 24.22 | 24.23 | 0 | 24.15 | 24 | 0 | 34.74 | 0 | 0 | 0 | 0 | 4.18 | 4.09 | 4.05 | 4.3 | 3.97 | 4.02 | 6.63 | 6.57 | 6.89 | 6.98 | 6.52 | 6.58 | 4.04 | 4.37 | 4.11 | 4.07 | 4.51 | 5.06 | 0.94 | 1.09 | 1.14 | 0 | 1.07 | 0.96 | 5.34 | 5.33 | 5.2 | 4.93 | 5.43 | 5.26 | 0.93 | 1.05 | 1.03 | 1.14 | 1.07 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190249 | 341 | 180461 | 345 | 347604.76 | 890.6 | 4.04 | 4.37 | 4.11 | 4.07 | 4.51 | 5.06 | 5.34 | 5.33 | 5.2 | 4.93 | 5.43 | 5.26 | 801000 | 2000 | 794000 | 2000 | 1587360 | 5000 | 1591000 | 1582360 | 10.7167 | 4.36 | 1.04 | 5.2483 | 1.07 | 23.85% | 20.39% | 24.302 | 34.74 | 4.1017 | 6.695 | 1602630.1 | 1587400 | 1712120.828 | 92.72%
2022-12-13 | 2023 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 334143.5 | 7:15 | 17:58 | 9333.9 | 10054.9 | 10122.2 | 10174 | 10024.6 | 10287.3 | 9907.3 | 10154 | 10170 | 9967.3 | 10026.4 | 10179.7 | 10213.2 | 10177.6 | 10299.7 | 10364.8 | 10312.2 | 10332 | 10358.5 | 10286.6 | 10245.9 | 10284.2 | 10166.7 | 10265.7 | 10163.4 | 8851.8 | 10299.9 | 10305.4 | 10399.7 | 10043.6 | 10109.9 | 10354.7 | 10383.3 | 10440.1 | 10218.8 | 10365.6 | 10450.2 | 10336.7 | 10447.9 | 10190.6 | 11220.8 | 9934.4 | 11066.1 | 9840.8 | 10448.9 | 11895.7 | 9754 | 11176.9 | 9555.5 | 9258.4 | 10217.7 | 9670.1 | 10766.1 | 9354.2 | 10845.9 | 9572.6 | 9532.9 | 10534.4 | 9517.6 | 10840.1 | 10831.1 | 9368 | 10306.1 | 9442.8 | 10024.1 | 9576.8 | 10170 | 10630 | 11001.5 | 9769.8 | 10810.6 | 9352.2 | 9187.2 | 10872.9 | 9543.1 | 10818.6 | 9490.6 | 10851.9 | 9386.4 | 10604.1 | 9777 | 10602.7 | 9872.9 | 11068.5 | 9788.6 | 10340.1 | 9735.9 | 8092.5 | 10670.4 | 10138.6 | 9536.7 | 11059.6 | 10634 | 9706.7 | 9568.8 | 10759.5 | 9534.4 | 9869 | 10831.6 | 9402.3 | 10871.6 | 9410.7 | 10579.1 | 9696.3 | 10752.4 | 9190.3 | 10825.4 | 9694.9 | 10679.3 | 9689.8 | 10755.6 | 9819.5 | 9516.9 | 10654.4 | 9613.8 | 9454.5 | 10671.2 | 10358.2 | 10619 | 9648.3 | 10752.1 | 9434.2 | 10321.7 | 9746 | 10318.9 | 8924.5 | 10450.7 | 9500.2 | 9549.9 | 9682 | 9574.2 | 8271.8 | 9538 | 8485.6 | 9497.4 | 9493.8 | 11045.4 | 9585.7 | 11099.4 | 9768 | 10929.2 | 9540.2 | 9698 | 9646.6 | 10669.3 | 11115.1 | 10891.6 | 10904.9 | 10882.1 | 10986.7 | 9842.9 | 10953 | 10927.9 | 11136 | 11077.2 | 10506 | 10932.6 | 9309.2 | 10557.7 | 9932.1 | 24.59 | 24.06 | 24.11 | 0 | 24.06 | 23.91 | 0 | 33.36 | 0 | 0 | 0 | 0 | 5.25 | 5.13 | 5.01 | 5.21 | 4.78 | 4.87 | 7.85 | 7.98 | 7.4 | 8.18 | 7.76 | 7.77 | 4.06 | 4.41 | 4.14 | 4.09 | 4.54 | 5.09 | 0.95 | 1.1 | 1.15 | 0 | 1.09 | 0.94 | 5.38 | 5.38 | 5.24 | 4.97 | 5.49 | 5.29 | 0.94 | 1.06 | 1.05 | 0.99 | 1.09 | 1.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191059 | 343 | 181266 | 347 | 349213.427 | 895.6 | 4.06 | 4.41 | 4.14 | 4.09 | 4.54 | 5.09 | 5.38 | 5.38 | 5.24 | 4.97 | 5.49 | 5.29 | 810000 | 2000 | 805000 | 2000 | 1608667 | 5000 | 1611000 | 1603667 | 10.7167 | 4.3883 | 1.046 | 5.2917 | 1.05 | 23.84% | 19.84% | 24.146 | 33.36 | 5.0417 | 7.8233 | 1623080 | 1608534 | 1732448.5675 | 92.85%
2022-12-14 | 2023 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 334458.32 | 7:17 | 17:59 | 9564.6 | 10293.4 | 10380.7 | 10428.6 | 10251.1 | 10522.8 | 10120.7 | 10385.6 | 10399 | 10185.6 | 10259.7 | 10408.9 | 10451.5 | 10412.8 | 10527 | 10618.5 | 10559 | 10609.2 | 10600.2 | 10526.3 | 10503.4 | 10524.3 | 10414.6 | 10525.4 | 10406.9 | 9062.3 | 10537.2 | 10560.1 | 10661.4 | 10328 | 10373.5 | 10605.7 | 10617.7 | 10673.5 | 10461.6 | 10616.1 | 10711.1 | 10599.8 | 10710.6 | 10424.8 | 11470.1 | 10155.1 | 11335.2 | 10093.2 | 10674.4 | 12054.9 | 9963.3 | 11423.1 | 9766.4 | 9461.8 | 10445.1 | 9888.6 | 11004 | 9567.7 | 11098.5 | 9787.1 | 9747.2 | 10778.3 | 9722.6 | 11082.2 | 11065.1 | 9559 | 10540.4 | 9651.1 | 10249.5 | 9783.5 | 10404.5 | 10879.7 | 11249.9 | 9986.3 | 11066 | 9554.5 | 9400.2 | 11101 | 9761.7 | 11043.8 | 9688.9 | 11102.9 | 9600.8 | 10833.7 | 10006.8 | 10840.2 | 10081.1 | 11317.8 | 10004.1 | 10565.8 | 9951.5 | 8280.1 | 10879.4 | 10374.9 | 9765.5 | 11307.4 | 10900.7 | 9958.8 | 9823.2 | 10996 | 9713.7 | 10108.4 | 11085.9 | 9627.7 | 11123.3 | 9641.8 | 10830.9 | 9920.4 | 11012.6 | 9413.3 | 11092.8 | 9927.5 | 10949.8 | 9927.2 | 11022.7 | 10064.4 | 9734.8 | 10877.5 | 9843.1 | 9673.2 | 10915.1 | 10589.9 | 10863.1 | 9875.4 | 11007.3 | 9668.8 | 10571.2 | 9995.3 | 10568.7 | 9170.7 | 10713.2 | 9750.6 | 9812 | 9962.7 | 9788.6 | 8487.9 | 9738.9 | 8660.7 | 9724.5 | 9739.8 | 11320.9 | 9826.3 | 11378.5 | 10022.2 | 11224.4 | 9795.6 | 9949.1 | 9878.4 | 10974.3 | 11412.9 | 11180.5 | 11191.8 | 11160.1 | 11258.5 | 10101.6 | 11236.5 | 11203.6 | 11426.9 | 11361.5 | 11216.5 | 11249.6 | 10090.6 | 11194.8 | 10168.3 | 23.26 | 22.84 | 22.72 | 0 | 22.83 | 22.71 | 0 | 34.9 | 0 | 0 | 0 | 0 | 3.06 | 2.91 | 2.91 | 3.11 | 2.72 | 2.89 | 5.15 | 4.77 | 4.92 | 5.31 | 4.67 | 5.28 | 4.14 | 4.51 | 4.2 | 4.17 | 4.65 | 5.25 | 0.95 | 1.14 | 1.16 | 0 | 1.15 | 0.97 | 5.53 | 5.53 | 5.36 | 5.06 | 5.67 | 5.44 | 0.95 | 1.09 | 1.05 | 1.06 | 1.14 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191888 | 344 | 182092 | 349 | 350860.694 | 900.6 | 4.14 | 4.51 | 4.2 | 4.17 | 4.65 | 5.25 | 5.53 | 5.53 | 5.36 | 5.06 | 5.67 | 5.44 | 829000 | 1000 | 826000 | 2000 | 1647267 | 5000 | 1652000 | 1642267 | 10.7 | 4.4867 | 1.074 | 5.4317 | 1.0817 | 23.94% | 19.91% | 22.872 | 34.9 | 2.9333 | 5.0167 | 1662936.6 | 1647000 | 1770588.267 | 93.02%
2022-12-15 | 2023 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 334458.32 | 7:16 | 17:59 | 9844.7 | 10588.3 | 10665.8 | 10708.3 | 10521.9 | 10812.6 | 10384.6 | 10659.3 | 10686.1 | 10475.1 | 10549.4 | 10699.2 | 10759.6 | 10723.7 | 10816.5 | 10919.9 | 10836.8 | 10899.7 | 10893.5 | 10822.9 | 10776.3 | 10815.1 | 10702.4 | 10813.2 | 10708.3 | 9329.8 | 10831.9 | 10861.7 | 10953.5 | 10608.6 | 10643.5 | 10889.6 | 10943.6 | 10962.9 | 10755.2 | 10926.2 | 11025.1 | 10906.4 | 10988.5 | 10649.3 | 11687.4 | 10467.8 | 11526.2 | 10396.7 | 11011.7 | 12210.7 | 10252 | 11583.9 | 10064.2 | 9747.1 | 10760.5 | 10173.5 | 11302.1 | 9857 | 11352.1 | 10071.1 | 10029.5 | 11037.4 | 9975.5 | 11307.2 | 11258.1 | 9842.6 | 10832.1 | 9935.9 | 10545.2 | 10088.7 | 10704.5 | 11187.6 | 11463.9 | 10275.8 | 11337 | 9843.3 | 9657.7 | 11368.3 | 10026.5 | 11298.5 | 9960 | 11340.9 | 9879 | 11104.5 | 10311.3 | 11119.4 | 10351 | 11538.6 | 10314.5 | 10879.5 | 10260.1 | 8530.1 | 11128.4 | 10666.3 | 10035.1 | 11526.8 | 11185.3 | 10256 | 10115.3 | 11251.6 | 9994 | 10410.1 | 11328.6 | 9925.9 | 11391 | 9945.7 | 11157.6 | 10237.3 | 11227.6 | 9696.8 | 11336.1 | 10227.8 | 11245.1 | 10219.9 | 11266.2 | 10363.2 | 10019.2 | 11169.8 | 10134.7 | 9982.6 | 11198.9 | 10874.2 | 11123.3 | 10155.6 | 11267.8 | 9965.4 | 10852.1 | 10291.9 | 10876.5 | 9444.3 | 11015.6 | 10040.8 | 10115.7 | 10254 | 10111 | 8752.2 | 9992.9 | 8884.7 | 10000.6 | 10030.9 | 11485.9 | 10103.1 | 11538.4 | 10314.6 | 11430.1 | 10074.3 | 10249.1 | 10165.6 | 10776.5 | 11115.9 | 10951.3 | 10940.8 | 10949.2 | 11015.4 | 9976.5 | 10985.7 | 10886.8 | 11028 | 10930.1 | 10953 | 11029.2 | 9951 | 10921.9 | 10024.9 | 22.53 | 22.25 | 22.05 | 0 | 22.36 | 22.18 | 0 | 35.99 | 0 | 0 | 0 | 0 | 1.85 | 2.17 | 2.12 | 2.2 | 1.84 | 2.07 | 4.27 | 4.08 | 5.16 | 4.19 | 3.87 | 3.93 | 4.27 | 4.65 | 4.34 | 4.29 | 4.84 | 5.45 | 0.99 | 1.17 | 1.2 | 0 | 1.21 | 1.01 | 5.73 | 5.74 | 5.57 | 5.26 | 5.91 | 5.64 | 0.98 | 1.12 | 1.08 | 1.02 | 1.19 | 1.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192739 | 346 | 182931 | 350 | 352542.628 | 905.533 | 4.27 | 4.65 | 4.34 | 4.29 | 4.84 | 5.45 | 5.73 | 5.74 | 5.57 | 5.26 | 5.91 | 5.64 | 851000 | 2000 | 839000 | 1000 | 1681934 | 4933 | 1687000 | 1677001 | 10.7167 | 4.64 | 1.116 | 5.6417 | 1.1067 | 24.05% | 19.62% | 22.274 | 35.99 | 2.0417 | 4.25 | 1698916.9 | 1681800 | 1831242.8648 | 91.84%
2022-12-16 | 2023 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 334458.32 | 7:16 | 17:59 | 9970.7 | 10704.7 | 10773.4 | 10828.8 | 10606.7 | 10902.7 | 10511 | 10762.6 | 10802.6 | 10575.2 | 10684.5 | 10824.8 | 10898.2 | 10862.8 | 10953.3 | 11055.9 | 10964.6 | 11022.2 | 11020 | 10953.1 | 10895.5 | 10944.4 | 10808.2 | 10935.8 | 10843.5 | 9451.8 | 10973 | 10996.6 | 11058.5 | 10704.3 | 10757.8 | 10997.3 | 11051.8 | 11068 | 10886.3 | 11041.7 | 11129.4 | 10997.6 | 11085.6 | 10853.2 | 11745.1 | 10592.1 | 11577.7 | 10509.7 | 11151.2 | 12271.9 | 10393.5 | 11645.2 | 10192.5 | 9870.7 | 10892.4 | 10289.7 | 11396.3 | 9972 | 11440.5 | 10192.3 | 10160.5 | 11147.6 | 10126.7 | 11411.5 | 11320.7 | 9930.1 | 11011.8 | 10009.9 | 10674.3 | 10213.1 | 10843.2 | 11285.2 | 11539.8 | 10417.2 | 11429.8 | 9980.5 | 9745 | 11459.1 | 10143.8 | 11405.2 | 10093.4 | 11426 | 10000.7 | 11192.6 | 10434.2 | 11218.6 | 10468.1 | 11603.2 | 10428.6 | 11001.4 | 10371.3 | 8621.9 | 11231.1 | 10768.3 | 10123.4 | 11583.6 | 11250.2 | 10343.2 | 10197.8 | 11331.6 | 10113.6 | 10556.9 | 11414.1 | 10050.7 | 11472.8 | 10067.7 | 11266.9 | 10364.7 | 11315.9 | 9823.2 | 11421.1 | 10354.8 | 11342.8 | 10340.4 | 11355 | 10474.1 | 10139.4 | 11263.6 | 10257.5 | 10100.8 | 11283.5 | 10987.4 | 11211.4 | 10276 | 11349.4 | 10076.6 | 10968.5 | 10413.5 | 10971.9 | 9526.4 | 11119.6 | 10144 | 10220.3 | 10350.5 | 10216.8 | 8839 | 10086.2 | 8982.4 | 10086.3 | 10114.5 | 11547 | 10213.9 | 11596.4 | 10425.4 | 11476 | 10165.1 | 10342.8 | 10253.2 | 11338.8 | 11659.9 | 11504.1 | 11487.3 | 11489.3 | 11550.8 | 10534.3 | 11533.2 | 11534.5 | 11652.3 | 11596.1 | 11588.9 | 11665.1 | 10595.2 | 11549.9 | 10662.6 | 23.3449 | 23.1196 | 23.0079 | 0 | 23.456 | 22.892 | 0 | 38.8033 | 0 | 0 | 0 | 0 | 1.716 | 1.6175 | 1.6769 | 1.6769 | 1.1911 | 1.6145 | 3.627 | 3.667 | 3.113 | 3.433 | 3.216 | 3.345 | 4.3344 | 4.7329 | 4.4068 | 4.3698 | 4.936 | 5.5659 | 0.99281 | 1.1857 | 1.2048 | 0 | 1.2153 | 0.99724 | 5.846 | 5.8636 | 5.6804 | 5.3657 | 6.0353 | 5.7566 | 0.98564 | 1.1273 | 1.089 | 0 | 1.1996 | 1.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193599 | 348 | 183785 | 352 | 354248.961 | 910.467 | 4.3344 | 4.7329 | 4.4068 | 4.3698 | 4.936 | 5.5659 | 5.846 | 5.8636 | 5.6804 | 5.3657 | 6.0353 | 5.7566 | 860000 | 2000 | 854000 | 2000 | 1706333 | 4934 | 1710000 | 1701399 | 10.7167 | 4.7243 | 1.1192 | 5.7579 | 1.1283 | 23.69% | 19.6% | 23.1641 | 38.8033 | 1.5822 | 3.4002 | 1723917.4 | 1706200 | 1858617.3486 | 91.8%
2022-12-17 | 2023 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 334484.14 | 7:18 | 17:59 | 9048.7 | 10013.4 | 10264.3 | 10268.5 | 10254.7 | 10351.5 | 9928.9 | 10157.4 | 10257.4 | 10036 | 10139.4 | 10287 | 10333.3 | 10301.6 | 10389.6 | 10487.3 | 10265.4 | 10297.4 | 10319.6 | 10264.5 | 10141.2 | 10235.4 | 10094.3 | 10223.4 | 10186.6 | 8867.4 | 10321.4 | 10346 | 10402.8 | 10047.1 | 9856.2 | 9775.8 | 10240.9 | 10272.1 | 10068.6 | 10228.1 | 10314.4 | 10197 | 10277.6 | 10027.6 | 10948.8 | 9737.6 | 10824.2 | 9665.8 | 10250 | 11438.1 | 9596.6 | 10863.7 | 10276.1 | 9953 | 10982.6 | 10375.6 | 11509.7 | 10053.7 | 11611.9 | 10260.6 | 10202.6 | 11199.5 | 10205.4 | 11534.6 | 11471.7 | 10047.5 | 11211 | 10140 | 10777.4 | 10309.6 | 10878.2 | 11437.6 | 11705.6 | 10531.3 | 11574.9 | 10066.5 | 9860.2 | 11603.4 | 10257 | 11555.2 | 10176.5 | 11608.1 | 10089.9 | 11343.7 | 10588.8 | 11422.2 | 10636.6 | 11859.3 | 10581.4 | 11175.6 | 10509.9 | 8743.6 | 11493.3 | 10932.3 | 10289 | 11829.9 | 11429.4 | 10451 | 10290.5 | 11567.6 | 10266 | 10666.8 | 11647.3 | 10168 | 11688.9 | 10185.1 | 11419.7 | 10468.1 | 11569.1 | 9930 | 11655.5 | 10475.7 | 11518.8 | 10458.3 | 11586.9 | 10593.9 | 10274.5 | 11459 | 10369.5 | 10192.5 | 11466.1 | 11140.8 | 11418.8 | 10381.1 | 11541.9 | 10175.2 | 11120.6 | 10518.7 | 11116.6 | 9616.1 | 11251.3 | 10233.4 | 10288.6 | 10426.2 | 10302.2 | 8903.4 | 10203.3 | 9111.8 | 10167.5 | 10214.4 | 5768.2 | 4984.1 | 2630.9 | 2281.9 | 5787.6 | 4998 | 5236.1 | 5189.9 | 9952.9 | 10302.8 | 10107 | 10108.1 | 10101.1 | 10171.1 | 9163.3 | 10168.6 | 10351.7 | 10504.7 | 10452.2 | 10393.4 | 10475.9 | 9386.6 | 10352.7 | 9447.2 | 23.8532 | 23.5648 | 23.4316 | 0 | 23.6941 | 23.4303 | 0 | 39.2299 | 0 | 0 | 0 | 0 | 1.5297 | 1.4963 | 1.5421 | 1.5686 | 1.0691 | 1.508 | 3.326 | 3.529 | 3.306 | 3.433 | 3.659 | 3.51 | 4.3977 | 4.7626 | 4.4561 | 4.4229 | 4.9737 | 5.6347 | 1.0148 | 1.1936 | 1.2236 | 0 | 1.2257 | 1.0184 | 5.9403 | 5.915 | 5.7539 | 5.436 | 6.1001 | 5.8183 | 1.006 | 1.1355 | 1.1062 | 0 | 1.2106 | 1.2642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194428 | 349 | 184578 | 354 | 355865.294 | 915.4 | 4.3977 | 4.7626 | 4.4561 | 4.4229 | 4.9737 | 5.6347 | 5.9403 | 5.915 | 5.7539 | 5.436 | 6.1001 | 5.8183 | 829000 | 1000 | 793000 | 2000 | 1616333 | 4933 | 1619000 | 1611400 | 10.6833 | 4.7746 | 1.1352 | 5.8273 | 1.1445 | 23.78% | 19.64% | 23.5948 | 39.2299 | 1.4523 | 3.4605 | 1632233.2 | 1616133 | 1877110.0619 | 86.1%
2022-12-18 | 2023 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 334484.14 | 7:18 | 17:58 | 9744.4 | 10600.5 | 10669.4 | 10658.1 | 10707.4 | 10810.2 | 10544.1 | 10595.2 | 10534.9 | 10370.5 | 10384.7 | 10533.1 | 10608 | 10562.9 | 10699.3 | 10781.8 | 10707.9 | 10743.8 | 10757 | 10682.2 | 10489.6 | 10662.1 | 10517.4 | 10644.7 | 10554.3 | 9188.8 | 10688.8 | 10720.2 | 10781.9 | 10406.6 | 10473.2 | 10733.9 | 10765.2 | 10796.4 | 10601.2 | 10776 | 10870.7 | 10868.5 | 10835.9 | 10571.9 | 11669.3 | 10359.9 | 11522.1 | 10267.9 | 10871.7 | 12201.5 | 10193.6 | 11569.3 | 9904 | 9597.1 | 10598.6 | 9998.6 | 11160.3 | 9694.9 | 11235.5 | 9907 | 9882.4 | 10880.7 | 9814.9 | 11166.4 | 11131.9 | 9676.5 | 10841.9 | 9753.3 | 10388.8 | 9929.4 | 10542.5 | 11059.2 | 11369.8 | 10146.2 | 11194.7 | 9699.9 | 9506.7 | 11222.3 | 9865.5 | 11163.1 | 9804.3 | 11223.7 | 9710 | 10941.2 | 10225.9 | 11021.2 | 10251.1 | 11517.7 | 10209.4 | 10781 | 10124.6 | 8432.1 | 11067.4 | 10551.7 | 9908.1 | 11450.3 | 11014.3 | 10056.1 | 9901.8 | 11158.4 | 9873 | 10274.6 | 11271.4 | 9797.4 | 11330.6 | 9828.5 | 11023.7 | 10099.4 | 11185.5 | 9577.9 | 11259.6 | 10101.5 | 11118.8 | 10082.3 | 11170.6 | 10211.3 | 9910.7 | 11059.1 | 9998 | 9844.8 | 11082 | 10748.8 | 11024.4 | 10015.2 | 11170.3 | 9821.3 | 10725.7 | 10138.9 | 10727.8 | 9294.9 | 10864.8 | 9887.9 | 9930.5 | 10058.8 | 9945.9 | 8596.1 | 9863.5 | 8764.9 | 9826.4 | 9867.8 | 11414.7 | 9943.2 | 11481.9 | 10122.8 | 11303.7 | 9882.8 | 10057.7 | 9976.8 | 11119.8 | 11555.7 | 11321.4 | 11313.1 | 11317.9 | 11417.6 | 10262.9 | 11386.5 | 11405.6 | 11555 | 11496.6 | 11446.2 | 11526.8 | 10303 | 11390 | 10374 | 24.7342 | 24.4211 | 23.566 | 0 | 24.3442 | 24.0649 | 0 | 38.633 | 0 | 0 | 0 | 0 | 1.9969 | 1.9661 | 1.9366 | 2.0567 | 1.6392 | 1.9269 | 3.974 | 3.737 | 3.975 | 4.032 | 6.173 | 4.151 | 4.226 | 4.5871 | 4.1793 | 4.2501 | 4.7834 | 5.3914 | 0.96043 | 1.1365 | 1.1259 | 0 | 1.1694 | 0.96976 | 5.6862 | 5.6825 | 5.3766 | 5.2174 | 5.8467 | 5.5769 | 0.95359 | 1.0814 | 1.0194 | 0 | 1.1542 | 1.2039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195269 | 351 | 185416 | 356 | 357536.561 | 920.333 | 4.226 | 4.5871 | 4.1793 | 4.2501 | 4.7834 | 5.3914 | 5.6862 | 5.6825 | 5.3766 | 5.2174 | 5.8467 | 5.5769 | 841000 | 2000 | 838000 | 2000 | 1671267 | 4933 | 1675000 | 1666334 | 10.6667 | 4.5696 | 1.0724 | 5.5644 | 1.0825 | 23.47% | 19.45% | 24.2261 | 38.633 | 1.9204 | 4.3403 | 1687730.7 | 1671201 | 1802614.7125 | 92.71%
2022-12-19 | 2023 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 334484.14 | 7:14 | 17:57 | 8558.9 | 9275.6 | 9230.8 | 9239.1 | 9262.6 | 9334.3 | 9157.8 | 9458.8 | 9246.2 | 8858.1 | 9083.3 | 9192.2 | 9220.4 | 9169.8 | 9289.6 | 9337.4 | 9263.6 | 9282.6 | 9305.9 | 9255 | 9107.2 | 9235.4 | 9152.6 | 9231.5 | 9134.2 | 8050.9 | 9257.7 | 9267 | 9325.7 | 9034.6 | 9084.8 | 9270.5 | 9305.6 | 9317.4 | 9166.2 | 9305.8 | 9377.6 | 9380.7 | 9352.1 | 9146.8 | 10013.3 | 8983.2 | 9891 | 8905.1 | 9397.4 | 10502.9 | 8852.8 | 9942 | 8653.3 | 8405.2 | 9195.3 | 8720.8 | 9620.9 | 8532.3 | 9666.5 | 8663.3 | 8618.1 | 9378.8 | 8616.1 | 9644.3 | 9596.4 | 8467.4 | 9325.4 | 8485.1 | 8997.9 | 8633.7 | 9118.3 | 9505.4 | 9742.9 | 8797.6 | 9586.6 | 8442.2 | 8315.8 | 9616.1 | 8596.9 | 9570.6 | 8528.7 | 9638 | 8467.6 | 9409.5 | 8860 | 9467.2 | 8880.1 | 9851 | 8841.3 | 9288.7 | 8789.1 | 7374.6 | 9508.8 | 9142.8 | 8630.1 | 9807.3 | 9489.2 | 8763.3 | 8651.1 | 9600.7 | 8580.6 | 8891.5 | 9659.5 | 8519.1 | 9733.8 | 8557.9 | 9512.3 | 8781.5 | 9628.6 | 8366.1 | 9689.4 | 8782.1 | 9588.5 | 8774.2 | 9623.3 | 8888.4 | 8606.5 | 9492.1 | 8662.7 | 8563.9 | 9531.8 | 9266.9 | 9491 | 8718.3 | 9585.3 | 8542.1 | 9266.2 | 8812.9 | 9266.3 | 8118 | 9372 | 8613.7 | 8639.4 | 8727.4 | 8655.2 | 7513.7 | 8552.7 | 7618.8 | 8509.2 | 8523.7 | 9729.7 | 8568.7 | 9778.6 | 8741.9 | 9615.2 | 8516.2 | 8646.8 | 8605.2 | 9435.9 | 9760.6 | 9590.1 | 9601.6 | 9558.6 | 9675.7 | 8792.8 | 9639.1 | 9645.7 | 9770.9 | 9730 | 9678.2 | 9727.7 | 8809.1 | 9478.1 | 8872.7 | 23.8618 | 23.7187 | 23.478 | 0 | 23.6739 | 23.3171 | 0 | 36.4669 | 0 | 0 | 0 | 0 | 1.6459 | 1.6021 | 1.6136 | 1.6022 | 0.96009 | 1.5224 | 3.782 | 3.42 | 3.222 | 3.618 | 3.198 | 3.013 | 3.8011 | 4.0995 | 3.8883 | 3.8289 | 4.2322 | 4.5391 | 0.90394 | 0.9654 | 1.0842 | 0 | 0.97947 | 0.80475 | 4.9122 | 4.8796 | 4.8207 | 4.666 | 4.9274 | 4.7941 | 0.91833 | 0.92335 | 1.001 | 0 | 0.96442 | 1.0015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195999 | 353 | 186137 | 358 | 358982.095 | 925.267 | 3.8011 | 4.0995 | 3.8883 | 3.8289 | 4.2322 | 4.5391 | 4.9122 | 4.8796 | 4.8207 | 4.666 | 4.9274 | 4.7941 | 730000 | 2000 | 721000 | 2000 | 1445534 | 4934 | 1447000 | 1440600 | 10.7167 | 4.0648 | 0.94756 | 4.8333 | 0.96171 | 23.31% | 19.9% | 23.6099 | 36.4669 | 1.491 | 3.3755 | 1457712 | 1445133 | 1574806.7542 | 91.77%
2022-12-20 | 2023 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 334484.14 | 7:17 | 18:01 | 8525.8 | 9197.1 | 9192.6 | 9160.7 | 9216.7 | 9305.2 | 9132.4 | 9442.9 | 9213.6 | 8960.7 | 9097.4 | 9211.5 | 9215.2 | 9176.5 | 9267.9 | 9312 | 9231.8 | 9267.1 | 9283.7 | 9249.3 | 9173.1 | 9261.2 | 9106.5 | 9209 | 9080.7 | 8042.4 | 9181.7 | 9198.6 | 9307.7 | 9109.7 | 9054.8 | 9229.2 | 9297.1 | 9310.8 | 9239.5 | 9274.9 | 9330.6 | 9329.7 | 9304.4 | 9136.3 | 9952 | 9034.5 | 9840.7 | 8955.7 | 9384 | 10399.1 | 8850.2 | 9874.6 | 8623.3 | 8392.9 | 9143.8 | 8752.1 | 9561.5 | 8604 | 9621.4 | 8649 | 8615.1 | 9353.3 | 8592 | 9607.3 | 9561.6 | 8448.1 | 9340 | 8532.1 | 8963.8 | 8653.5 | 9104.3 | 9491.8 | 9688.5 | 8834.1 | 9587.9 | 8504.2 | 8306.3 | 9623.6 | 8609.5 | 9558.6 | 8559.2 | 9593.6 | 8496.7 | 9396.1 | 8932.5 | 9502.5 | 9026.3 | 9843 | 8940.4 | 9365 | 8820 | 7469.4 | 9546.8 | 9179.3 | 8679.9 | 9802.8 | 9500.5 | 8816.9 | 8711.6 | 9591.4 | 8631 | 8983.3 | 9649 | 8608.2 | 9720.9 | 8631.3 | 9522.1 | 8842.1 | 9621.4 | 8435.4 | 9683 | 8832.7 | 9580.2 | 8821.1 | 9615.3 | 8947.3 | 8739 | 9572.9 | 8781.6 | 8681.7 | 9567.4 | 9367.5 | 9506.5 | 8869.3 | 9632.7 | 8680.5 | 9295.2 | 8864.8 | 9277 | 8248.1 | 9440.1 | 8770.3 | 8834.9 | 8928.8 | 8827.7 | 7702.9 | 8718 | 7792.3 | 8794.1 | 8805.4 | 9923.6 | 8817.8 | 10005.6 | 9022.8 | 9869.8 | 8825.4 | 8950.6 | 8913.4 | 9717.8 | 9980 | 9866.9 | 9860 | 9818.7 | 9898.7 | 9103.3 | 9899.7 | 9869.3 | 9965.5 | 9941.4 | 9901.4 | 9951.4 | 9111.6 | 9723.4 | 9170.3 | 23.1685 | 23.0936 | 23.0151 | 0 | 23.5171 | 22.9748 | 0 | 35.248 | 0 | 0 | 0 | 0 | 2.0921 | 2.0424 | 2.0653 | 2.0835 | 1.7204 | 2.1006 | 4.657 | 4.468 | 4.553 | 4.843 | 5.215 | 5.392 | 3.8956 | 4.1893 | 3.9003 | 3.8772 | 4.3344 | 4.7845 | 0.82488 | 1.0952 | 1.0006 | 0 | 1.149 | 0.9626 | 4.9607 | 4.9922 | 4.7869 | 4.4999 | 5.2087 | 5.0356 | 0.82276 | 1.0538 | 0.92516 | 0 | 1.1443 | 1.1897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196727 | 354 | 186869 | 360 | 360435.961 | 930.133 | 3.8956 | 4.1893 | 3.9003 | 3.8772 | 4.3344 | 4.7845 | 4.9607 | 4.9922 | 4.7869 | 4.4999 | 5.2087 | 5.0356 | 728000 | 1000 | 732000 | 2000 | 1453866 | 4866 | 1457000 | 1449000 | 10.7333 | 4.1636 | 1.0065 | 4.914 | 1.0271 | 24.17% | 20.9% | 23.1538 | 35.248 | 2.0174 | 4.8547 | 1467157.7 | 1453667 | 1599953.3562 | 90.86%
2022-12-21 | 2023 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 334484.14 | 7:27 | 18:01 | 9735.5 | 10594.7 | 10563.4 | 10568.4 | 10583.8 | 10684.7 | 10465.7 | 10845.3 | 10624.6 | 10278.1 | 10473.8 | 10637.4 | 10592.3 | 10587.4 | 10631.5 | 10695.3 | 10604.5 | 10662.2 | 10691.2 | 10660.1 | 10542 | 10656.6 | 10458.1 | 10585.3 | 10459.5 | 9128.8 | 10596.3 | 10615.7 | 10745.5 | 10505.8 | 10390 | 10596.9 | 10728.9 | 10756 | 10644.6 | 10697.6 | 10764.5 | 10767.1 | 10745 | 10533.3 | 11478.6 | 10345.3 | 11342.7 | 10257.6 | 10829.9 | 12018.1 | 10173.4 | 11397.7 | 9824.8 | 9514.7 | 10522.9 | 10003.9 | 11029.1 | 9804 | 11056.1 | 9837.2 | 9856.9 | 10854.8 | 9780.9 | 11053.3 | 11001 | 9612.6 | 11044.2 | 10051.7 | 10401.2 | 9863.3 | 10459.9 | 10924.2 | 11152.5 | 10080.2 | 11026.3 | 9639.2 | 9431.8 | 11055 | 9798.9 | 11003.8 | 9731.6 | 11037.9 | 9686.5 | 10868.2 | 10194.8 | 10929.5 | 10243.2 | 11334.7 | 10175.9 | 10709.6 | 10080.5 | 8412.2 | 10999.4 | 10536.7 | 9924.4 | 11316.1 | 10944.3 | 10070.1 | 9930.1 | 11042.5 | 9851.1 | 10276.9 | 11123 | 9766.1 | 11203.3 | 9816 | 10955.5 | 10089.3 | 11066.4 | 9567.8 | 11143.7 | 10086.6 | 11034.5 | 10068.8 | 11077.8 | 10197.9 | 9914.1 | 10952.7 | 10002.1 | 9836.1 | 10988.3 | 10715.6 | 10945.8 | 10035.3 | 11065.1 | 9816.9 | 10691.3 | 10136.1 | 10677.4 | 9300.2 | 10822.1 | 9892.7 | 9955.3 | 10087.8 | 9975 | 8617.7 | 9815.5 | 8720.5 | 9867.1 | 9879 | 11039.5 | 9898.1 | 11367.4 | 10164.5 | 11176.9 | 9879.3 | 10048 | 9986.1 | 11039.5 | 11380.9 | 11182.5 | 11184.4 | 11220.1 | 11259.4 | 10254.9 | 11256.2 | 11230.5 | 11388.3 | 11383.9 | 11329.7 | 11386.5 | 10314 | 11080.6 | 10358.6 | 21.8872 | 21.583 | 21.7011 | 0 | 21.6664 | 21.5132 | 0 | 32.6432 | 0 | 0 | 0 | 0 | 3.441 | 3.3161 | 3.2582 | 3.5107 | 2.8989 | 3.3175 | 6.405 | 6.7567 | 6.5417 | 6.72 | 6.4533 | 6.4217 | 4.1593 | 4.5241 | 4.2488 | 4.1889 | 4.7072 | 5.251 | 0.9902 | 1.1467 | 1.1959 | 0 | 1.1821 | 0.97793 | 5.5366 | 5.5386 | 5.4104 | 5.1156 | 5.6975 | 5.449 | 0.98441 | 1.0987 | 1.0881 | 1.0864 | 1.1682 | 1.2133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197565 | 356 | 187702 | 362 | 362098.695 | 935.133 | 4.1593 | 4.5241 | 4.2488 | 4.1889 | 4.7072 | 5.251 | 5.5366 | 5.5386 | 5.4104 | 5.1156 | 5.6975 | 5.449 | 838000 | 2000 | 833000 | 2000 | 1662734 | 5000 | 1667000 | 1657734 | 10.5667 | 4.5132 | 1.0986 | 5.458 | 1.1065 | 24.34% | 20.27% | 21.6702 | 32.6432 | 3.2904 | 6.5497 | 1678637.5 | 1662600 | 1788873.7887 | 92.94%
2022-12-22 | 2023 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 334484.14 | 7:20 | 18:01 | 10161.9 | 10957.2 | 10947.7 | 10940.6 | 10997 | 11045 | 10902.2 | 11192.7 | 10954.2 | 10677.2 | 10826.6 | 10962.8 | 10942 | 10917.8 | 10957.8 | 11017.4 | 10919.3 | 10973.8 | 10987.7 | 10971.7 | 10867.3 | 10962.1 | 10813.3 | 10913.9 | 10791.9 | 9519.7 | 10923.1 | 10922.3 | 11057.4 | 10910.8 | 10750.5 | 10926.6 | 11037.6 | 11053.1 | 10965.7 | 11000 | 11108.1 | 11063.2 | 11034.9 | 10862.5 | 11659.9 | 10692.2 | 11534.8 | 10632.8 | 11121.2 | 12170 | 10566.3 | 11586.8 | 10251.9 | 9925.5 | 10888.5 | 10454.2 | 11307.7 | 10233.8 | 11333.5 | 10272.8 | 10285.7 | 11217 | 10197.9 | 11338.5 | 11293.7 | 10020.6 | 11340.8 | 10504.2 | 10837.5 | 10283 | 10835.8 | 11218.7 | 11412.6 | 10498.2 | 11302.7 | 10054.6 | 9838.2 | 11335.5 | 10225.3 | 11279.8 | 10154.7 | 11303.4 | 10165.9 | 11207.6 | 10598.6 | 11223.9 | 10640.4 | 11569.6 | 10580 | 11035 | 10507.7 | 8779.5 | 11256.9 | 10871.7 | 10330.5 | 11534.2 | 11210.9 | 10479 | 10344.7 | 11316 | 10292.5 | 10661.7 | 11360 | 10180.8 | 11433 | 10219.7 | 11228.3 | 10499.1 | 11303.1 | 9962.3 | 11382.8 | 10490.5 | 11299.9 | 10470.9 | 11335 | 10613 | 10309.8 | 11213.6 | 10398.5 | 10233.2 | 11231.7 | 10996.3 | 11193.5 | 10424.1 | 11295.7 | 10208.3 | 10979 | 10535.3 | 10988 | 9679.7 | 11102.3 | 10292.9 | 10344.2 | 10457.7 | 10364.7 | 8955.4 | 10203.8 | 9060.7 | 10305.6 | 10321 | 11514.6 | 10318.9 | 11576.9 | 10570.4 | 11422.9 | 10299.8 | 10456.7 | 10406.5 | 11308.3 | 11587.4 | 11431 | 11425.4 | 11466.6 | 11490.6 | 10642.3 | 11487.7 | 11475.8 | 11610.7 | 11595.3 | 11545.3 | 11576.4 | 10707.7 | 11361.4 | 10749.4 | 20.1047 | 19.9271 | 20.0036 | 0 | 20.0519 | 19.7121 | 0 | 31.5343 | 0 | 0 | 0 | 0 | 3.2359 | 3.1482 | 2.9739 | 3.2284 | 2.8768 | 3.0413 | 6.117 | 6.038 | 5.638 | 6.122 | 5.7 | 5.85 | 4.2372 | 4.6188 | 4.3452 | 4.2884 | 4.84 | 5.3892 | 0.99867 | 1.1764 | 1.2147 | 0 | 1.2174 | 1.0069 | 5.6792 | 5.6959 | 5.5718 | 5.2343 | 5.9018 | 5.5763 | 0.98602 | 1.1267 | 1.1012 | 0 | 1.2016 | 1.2506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198429 | 358 | 188562 | 363 | 363814.562 | 940 | 4.2372 | 4.6188 | 4.3452 | 4.2884 | 4.84 | 5.3892 | 5.6792 | 5.6959 | 5.5718 | 5.2343 | 5.9018 | 5.5763 | 864000 | 2000 | 860000 | 1000 | 1715867 | 4867 | 1721000 | 1711000 | 10.6833 | 4.6198 | 1.1228 | 5.6099 | 1.1332 | 24.3% | 20.2% | 19.9599 | 31.5343 | 3.0841 | 5.9108 | 1732654.6 | 1711132 | 1859071.0702 | 92.04%
2022-12-23 | 2023 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 334484.14 | 7:21 | 18:03 | 10057.1 | 10981.2 | 10902.4 | 10889.5 | 10940.5 | 11027 | 10960.7 | 11222.9 | 10907.5 | 10718.4 | 10763.4 | 10902 | 10891.3 | 10857.5 | 10927.4 | 10978.3 | 10880.3 | 10926.3 | 10950.4 | 10926.6 | 10813.2 | 10917.9 | 10755.6 | 10865.9 | 10736 | 9399 | 10888.7 | 10882.6 | 11021.4 | 10865.2 | 10691.9 | 10878.3 | 11012.6 | 11020.4 | 10931.1 | 10960.9 | 11042.1 | 10999.8 | 10994.3 | 10802.1 | 11657.8 | 10633.3 | 11532.8 | 10553.8 | 11086.4 | 12158.4 | 10478.4 | 11578.7 | 10121.4 | 9801 | 10819.6 | 10332.2 | 11280.5 | 10094.4 | 11300.4 | 10152 | 10178.4 | 11181.6 | 10066.1 | 11298.9 | 11256.7 | 9889.1 | 11298 | 10378.7 | 10780.6 | 10177.6 | 10782.9 | 11188.2 | 11397.6 | 10397.9 | 11278.8 | 9943.5 | 9727.4 | 11308.1 | 10113 | 11248.6 | 10036.8 | 11267.5 | 10037.5 | 11169.4 | 10501.1 | 11200.4 | 10555.4 | 11552.3 | 10493.1 | 10999.3 | 10431.5 | 8680.7 | 11217.7 | 10826.9 | 10198.9 | 11509 | 11176.2 | 10350.7 | 10213.5 | 11303.3 | 10162.9 | 10595 | 11339.6 | 10064 | 11402.7 | 10101.1 | 11191.3 | 10373.8 | 11278.3 | 9836.8 | 11357 | 10371.5 | 11270.7 | 10355.5 | 11315.9 | 10504.4 | 10193 | 11192 | 10282.2 | 10119.9 | 11208.1 | 10958 | 11162.6 | 10304.2 | 11268.1 | 10092.2 | 10937.7 | 10423.8 | 10956.3 | 9582.3 | 11069.5 | 10184.7 | 10219.9 | 10336.2 | 10249.7 | 8858.4 | 10067.6 | 8920.5 | 10160.5 | 10173.4 | 11506.8 | 10209.5 | 11575.4 | 10422.4 | 11419.5 | 10195 | 10378.5 | 10264.8 | 11281.4 | 11573 | 11400.7 | 11400.3 | 11449.4 | 11475.4 | 10565 | 11468.3 | 11446.3 | 11579.1 | 11561.9 | 11514.4 | 11561.9 | 10617.3 | 11322.3 | 10670.4 | 19.3448 | 19.1951 | 19.1074 | 0 | 19.348 | 19.0895 | 0 | 31.3356 | 0 | 0 | 0 | 0 | 3.0879 | 2.9036 | 2.9284 | 3.0555 | 2.6539 | 2.8667 | 5.776 | 5.27 | 5.864 | 6.849 | 5.304 | 5.024 | 4.2578 | 4.6354 | 4.3231 | 4.2865 | 4.83 | 5.4161 | 0.9971 | 1.1861 | 1.2021 | 0 | 1.2319 | 1.0239 | 5.6963 | 5.7096 | 5.5392 | 5.2164 | 5.8859 | 5.6065 | 0.98612 | 1.135 | 1.0923 | 0 | 1.2126 | 1.2728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199289 | 354 | 189415 | 365 | 365519.762 | 945 | 4.2578 | 4.6354 | 4.3231 | 4.2865 | 4.83 | 5.4161 | 5.6963 | 5.7096 | 5.5392 | 5.2164 | 5.8859 | 5.6065 | 860000 | -4000 | 853000 | 2000 | 1705200 | 5000 | 1715000 | 1700200 | 10.7 | 4.6248 | 1.1282 | 5.609 | 1.1398 | 24.39% | 20.32% | 19.217 | 31.3356 | 2.916 | 5.6812 | 1722584 | 1705001 | 1848458.6682 | 92.24%
2022-12-24 | 2023 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 334484.14 | 7:18 | 18:01 | 10082.8 | 10967.1 | 10882.5 | 10875.9 | 10906.5 | 10999.2 | 10931.8 | 11275.2 | 10940 | 10816.2 | 10787.2 | 10943.3 | 10885 | 10879.6 | 10918.1 | 10961 | 10856.2 | 10902.5 | 10940.8 | 10930.5 | 10794.8 | 10902 | 10729.3 | 10844.8 | 10720.9 | 9407.5 | 10875.8 | 10865.8 | 11008.8 | 10847.2 | 10660.4 | 10851.5 | 10992.1 | 11005 | 10913.9 | 10943 | 11060.2 | 11008.3 | 10978.9 | 10908.2 | 11625.3 | 10612.2 | 11485 | 10540.4 | 11069.2 | 12126.6 | 10438.2 | 11513.8 | 10110.9 | 9782.7 | 10784.1 | 10303.3 | 11230.5 | 10124.1 | 11251.2 | 10126.8 | 10191 | 11158.8 | 10086 | 11276.9 | 11231.4 | 9919.3 | 11266.7 | 10391 | 10761.9 | 10183.9 | 10770.3 | 11179 | 11377.5 | 10405.5 | 11268.7 | 9956.4 | 9739 | 11293.3 | 10123.5 | 11238.9 | 10060.4 | 11250.9 | 10050.6 | 11153.6 | 10516.3 | 11184 | 10571.5 | 11526.3 | 10515.4 | 10991.4 | 10419.6 | 8691.9 | 11193.8 | 10805.3 | 10226.7 | 11491.9 | 11172.4 | 10377.3 | 10227.8 | 11267.2 | 10163 | 10601.3 | 11314.5 | 10083 | 11386.9 | 10116.8 | 11184.1 | 10405.4 | 11241.4 | 9862.1 | 11332.5 | 10393.1 | 11259.3 | 10378.8 | 11285.4 | 10518.4 | 10216 | 11170.8 | 10306 | 10130.6 | 11185.4 | 10938.3 | 11134.9 | 10326.9 | 11249.8 | 10108 | 10914.9 | 10443.5 | 10930.5 | 9586.7 | 11051.2 | 10191.6 | 10266.4 | 10407.7 | 10245.2 | 8879.7 | 10080.5 | 8939.9 | 10169.1 | 10181.6 | 11438.7 | 10201.6 | 11509.7 | 10399.8 | 11364.4 | 10200.8 | 10381.4 | 10276.2 | 11251.1 | 11521.9 | 11375.3 | 11366.7 | 11421 | 11433.2 | 10559.7 | 11432.2 | 11410.4 | 11535.1 | 11521.5 | 11485.5 | 11537.4 | 10621.6 | 11289.2 | 10664.1 | 19.529 | 19.1839 | 19.3372 | 0 | 19.1893 | 19.0425 | 0 | 30.4309 | 0 | 0 | 0 | 0 | 3.7025 | 3.6396 | 3.4 | 3.7496 | 3.1847 | 3.5169 | 6.757 | 6.595 | 6.161 | 7.41 | 6.901 | 6.367 | 4.2398 | 4.6012 | 4.3071 | 4.2757 | 4.7898 | 5.3763 | 1.0009 | 1.1696 | 1.2025 | 0 | 1.2013 | 0.99998 | 5.6654 | 5.6619 | 5.5103 | 5.2115 | 5.8318 | 5.5662 | 0.98629 | 1.1222 | 1.0889 | 0 | 1.1867 | 1.2422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200148 | 361 | 190268 | 367 | 367224.095 | 949.933 | 4.2398 | 4.6012 | 4.3071 | 4.2757 | 4.7898 | 5.3763 | 5.6654 | 5.6619 | 5.5103 | 5.2115 | 5.8318 | 5.5662 | 859000 | 7000 | 853000 | 2000 | 1704333 | 4933 | 1703000 | 1699400 | 10.7167 | 4.5983 | 1.1149 | 5.5745 | 1.1253 | 24.24% | 20.19% | 19.2564 | 30.4309 | 3.5322 | 6.6985 | 1721417.1 | 1704067 | 1843118.5023 | 92.46%
2022-12-25 | 2023 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 334484.14 | 7:23 | 18:03 | 9465.9 | 10234.7 | 10162.5 | 10130 | 10177.2 | 10281.2 | 10226.1 | 10505.4 | 10182.6 | 10065 | 10093.2 | 10217.3 | 10185.6 | 10170.5 | 10203.2 | 10248 | 10159.3 | 10216.3 | 10237.9 | 10231.3 | 10144.4 | 10217.3 | 10056.4 | 10155.2 | 9989.4 | 8851.7 | 10139.3 | 10134.3 | 10282.3 | 10163.7 | 9975.6 | 10132 | 10241.2 | 10252.1 | 10181.3 | 10201.6 | 10299.8 | 10255.4 | 10228.5 | 10169.3 | 10803.8 | 9945.8 | 10711.5 | 9866.4 | 10322.3 | 11195.1 | 9824 | 10793.7 | 9536.6 | 9254.8 | 10102.6 | 9701 | 10510.5 | 9599.8 | 10464.7 | 9505.9 | 9517.5 | 10355.7 | 9485.5 | 10450.2 | 10418.2 | 9322.5 | 10514 | 9751.9 | 10000.7 | 9505.8 | 10030.5 | 10366.5 | 10577.4 | 9699.1 | 10469.6 | 9321.5 | 9161 | 10506.4 | 9500.9 | 10439.3 | 9410.8 | 10477.2 | 9432.3 | 10381.4 | 9751.6 | 10370 | 9767.4 | 10656.2 | 9737.8 | 10160.5 | 9693.2 | 8115.2 | 10389.2 | 10022.6 | 9525.9 | 10637.7 | 10378.3 | 9700.1 | 9569 | 10436.4 | 9488.6 | 9833.1 | 10492.3 | 9399.7 | 10563.3 | 9442.8 | 10380.8 | 9682.9 | 10453.2 | 9217.1 | 10526 | 9672.1 | 10452.2 | 9667.5 | 10477.4 | 9782.4 | 9490.3 | 10310.5 | 9544 | 9407.4 | 10360.5 | 10092.3 | 10291.3 | 9564 | 10362.6 | 9376.6 | 10119.6 | 9678.6 | 10097.6 | 8901.3 | 10202.8 | 9460.2 | 9519.4 | 9641.5 | 9505.7 | 8248.4 | 9403.5 | 8338 | 9435.6 | 9439.5 | 10561.3 | 9458.8 | 10619.7 | 9610.1 | 10515.3 | 9459.8 | 9593.8 | 9531.5 | 10398.6 | 10641.8 | 10492.1 | 10478.7 | 10506.6 | 10536.6 | 9748.8 | 10553.2 | 10493.4 | 10605.3 | 10624.7 | 10594.8 | 10630.5 | 9804.2 | 10383.9 | 9824.2 | 18.9437 | 18.5678 | 18.261 | 0 | 18.2696 | 18.1472 | 0 | 31.7143 | 0 | 0 | 0 | 0 | 2.5235 | 2.541 | 2.5237 | 2.5559 | 2.5015 | 2.3722 | 5.32 | 5.063 | 5.005 | 4.906 | 4.825 | 4.611 | 4.2134 | 4.5035 | 4.2231 | 4.1682 | 4.5542 | 5.0159 | 0.94478 | 1.1806 | 1.1265 | 0 | 1.2109 | 1.0077 | 5.4442 | 5.4271 | 5.2457 | 4.8741 | 5.5279 | 5.2394 | 0.93181 | 1.1395 | 1.0332 | 0 | 1.2014 | 1.2481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200951 | 363 | 191058 | 369 | 368809.362 | 955 | 4.2134 | 4.5035 | 4.2231 | 4.1682 | 4.5542 | 5.0159 | 5.4442 | 5.4271 | 5.2457 | 4.8741 | 5.5279 | 5.2394 | 803000 | 2000 | 790000 | 2000 | 1585267 | 5067 | 1589000 | 1580200 | 10.6667 | 4.4464 | 1.0941 | 5.2931 | 1.1108 | 24.61% | 20.99% | 18.4379 | 31.7143 | 2.5029 | 4.955 | 1601599.8 | 1585067 | 1742638.5045 | 90.96%
2022-12-26 | 2023 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 334484.14 | 7:22 | 18:04 | 10167.5 | 11018.3 | 10966.5 | 10959.8 | 10991.3 | 11076.4 | 10979 | 11298 | 10987.2 | 10844.7 | 10856.6 | 11013.1 | 10955 | 10953.2 | 10979.9 | 11032.2 | 10925.6 | 10990.9 | 11021.2 | 11019.5 | 10901 | 10991.6 | 10820.2 | 10926.7 | 10786 | 9488.3 | 10955.8 | 10942.4 | 11085.5 | 10939.2 | 10734.2 | 10912.5 | 11059.6 | 11076.6 | 10993.3 | 11011.4 | 11119.3 | 11074.2 | 11042.4 | 10976.6 | 11667.1 | 10680.4 | 11539.8 | 10620 | 11131.9 | 12170.8 | 10547.9 | 11637.6 | 10238.4 | 9915.2 | 10888.9 | 10461.3 | 11335.1 | 10276.1 | 11323.9 | 10225.2 | 10289.2 | 11232.1 | 10188 | 11339.2 | 11293.9 | 10012.1 | 11442.7 | 10632.9 | 10791.8 | 10218.7 | 10815.2 | 11204.6 | 11394.1 | 10452.9 | 11318.7 | 10026.2 | 9821.3 | 11342.3 | 10215 | 11289.1 | 10140.8 | 11302.3 | 10140.7 | 11214.1 | 10575.7 | 11227.5 | 10630.1 | 11568.3 | 10567.5 | 11031.7 | 10483.7 | 8749.3 | 11242.5 | 10857.3 | 10299.7 | 11532.1 | 11220.2 | 10474.8 | 10340.9 | 11296.6 | 10249.2 | 10654.6 | 11352.9 | 10145.7 | 11429 | 10179.4 | 11225.2 | 10459.1 | 11288.7 | 9918.4 | 11368.4 | 10459.7 | 11290.8 | 10439.6 | 11316.2 | 10581.4 | 10286.9 | 11205.2 | 10358.2 | 10190.6 | 11217.5 | 10986.9 | 11171.5 | 10395.6 | 11279.3 | 10168.5 | 10957.3 | 10507.7 | 10965.6 | 9646.5 | 11091.2 | 10248.7 | 10317.5 | 10449.8 | 10305.2 | 8926 | 10206.6 | 9071.3 | 10261.1 | 10264.7 | 11495.8 | 10280.2 | 11552.9 | 10460.4 | 11408.8 | 10260.8 | 10432.9 | 10362.2 | 11287.3 | 11558.9 | 11407 | 11402 | 11455.4 | 11475.3 | 10612.8 | 11465.8 | 11426.8 | 11566.6 | 11564 | 11523.6 | 11581.2 | 10678.4 | 11322.7 | 10709.7 | 19.2536 | 18.8972 | 18.955 | 0 | 18.9011 | 18.7226 | 0 | 30.7068 | 0 | 0 | 0 | 0 | 3.4473 | 3.3935 | 3.2754 | 3.4791 | 3.3761 | 3.3205 | 5.85 | 6.555 | 5.403 | 5.79 | 6.167 | 5.985 | 4.2604 | 4.6225 | 4.3245 | 4.2914 | 4.8154 | 5.3987 | 1.0016 | 1.1712 | 1.2011 | 0 | 1.2054 | 1.0011 | 5.6995 | 5.6858 | 5.5324 | 5.2314 | 5.8687 | 5.5874 | 0.98869 | 1.1242 | 1.0901 | 0 | 1.1924 | 1.2438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201816 | 366 | 191916 | 372 | 370524.696 | 960 | 4.2604 | 4.6225 | 4.3245 | 4.2914 | 4.8154 | 5.3987 | 5.6995 | 5.6858 | 5.5324 | 5.2314 | 5.8687 | 5.5874 | 865000 | 3000 | 858000 | 3000 | 1715334 | 5000 | 1717000 | 1710334 | 10.7 | 4.6188 | 1.1161 | 5.6009 | 1.1279 | 24.16% | 20.14% | 18.9459 | 30.7068 | 3.382 | 5.9583 | 1731877.3 | 1715067 | 1854152.2222 | 92.5%
2022-12-27 | 2023 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 334458.04 | 7:22 | 18:05 | 10051.4 | 10959 | 10882.7 | 10877.4 | 10901.9 | 10992 | 10942.2 | 11240 | 10901.4 | 10772.2 | 10764.1 | 10923.7 | 10864.1 | 10864.6 | 10884.9 | 10938 | 10840.7 | 10911.3 | 10943.4 | 10932.8 | 10817 | 10908.3 | 10735.5 | 10846.8 | 10693.4 | 9358.9 | 10866.1 | 10860.3 | 11012.1 | 10858.1 | 10641.9 | 10836.7 | 10979.2 | 11005.5 | 10922.9 | 10935.2 | 11047.7 | 10995.8 | 10971.7 | 10897 | 11613.1 | 10560.6 | 11480.9 | 10481.2 | 11032.5 | 12121.8 | 10416.3 | 11591.9 | 10103.1 | 9785.3 | 10790.5 | 10319.9 | 11258.1 | 10123.8 | 11262.4 | 10091.5 | 10139 | 11147.7 | 10051 | 11267 | 11219 | 9876.2 | 11252.1 | 10488.2 | 10745 | 10112.3 | 10740.7 | 11126.3 | 11366.1 | 10326.7 | 11208.6 | 9884.3 | 9664.7 | 11240.7 | 10056.3 | 11194.5 | 10001.9 | 11229.9 | 9988 | 11139.4 | 10427 | 11137.1 | 10492 | 11496.1 | 10421.7 | 10934.2 | 10352.4 | 8615.7 | 11157.7 | 10761.4 | 10146.5 | 11461 | 11135.5 | 10314 | 10178.3 | 11234.8 | 10079.8 | 10524.9 | 11277.1 | 9998.9 | 11360.9 | 10035 | 11146.6 | 10311.6 | 11227.5 | 9780.5 | 11304.6 | 10323.3 | 11215.1 | 10292.6 | 11242.4 | 10437.7 | 10135.2 | 11123.7 | 10213.3 | 10041.9 | 11147.5 | 10900.7 | 11105.3 | 10254.7 | 11215.7 | 10033.2 | 10878.8 | 10369 | 10888.6 | 9520.4 | 11016.4 | 10115.4 | 10155.9 | 10286.3 | 10200.6 | 8793 | 10038.5 | 8909.2 | 10109.2 | 10115.9 | 11435.6 | 10126.4 | 11510.5 | 10325.5 | 11345.3 | 10098.3 | 10284 | 10224.7 | 11220.9 | 11507.1 | 11337.8 | 11338.4 | 11395.7 | 11411.9 | 10489.7 | 11408.5 | 11387.8 | 11516.4 | 11521.6 | 11468.2 | 11534.4 | 10556.7 | 11252.9 | 10590.3 | 19.4996 | 19.0095 | 19.2075 | 0 | 18.9837 | 18.8466 | 0 | 31.0324 | 0 | 0 | 0 | 0 | 3.3681 | 3.2833 | 3.1709 | 3.4012 | 3.2774 | 3.237 | 5.666 | 5.389 | 5.369 | 5.526 | 5.476 | 5.647 | 4.2002 | 4.5548 | 4.2713 | 4.2329 | 4.7422 | 5.3124 | 0.98633 | 1.1458 | 1.1874 | 0 | 1.1699 | 0.97187 | 5.6109 | 5.5933 | 5.4581 | 5.1667 | 5.7668 | 5.5027 | 0.97382 | 1.0989 | 1.0758 | 0 | 1.1596 | 1.208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202674 | 367 | 192765 | 373 | 372223.362 | 965 | 4.2002 | 4.5548 | 4.2713 | 4.2329 | 4.7422 | 5.3124 | 5.6109 | 5.5933 | 5.4581 | 5.1667 | 5.7668 | 5.5027 | 858000 | 1000 | 849000 | 1000 | 1698666 | 5000 | 1705000 | 1693666 | 10.7167 | 4.5523 | 1.0923 | 5.5164 | 1.1032 | 23.99% | 20% | 19.1094 | 31.0324 | 3.2896 | 5.5122 | 1715757.3 | 1698334 | 1826255.4025 | 93%
2022-12-28 | 2023 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 334458.04 | 7:23 | 18:05 | 9485.6 | 10420.3 | 10318.9 | 10294 | 10346.8 | 10454.8 | 10395.5 | 10881.5 | 10395.3 | 10253 | 10231.4 | 10405.5 | 10319.5 | 10342.3 | 10329 | 10405.7 | 10309.5 | 10377.1 | 10415.2 | 10396.6 | 10254.6 | 10367.9 | 10147.3 | 10272.2 | 10086.7 | 8924 | 10293.3 | 10289.6 | 10473 | 10295 | 10038 | 10272.3 | 10431.4 | 10475.5 | 10378.5 | 10393 | 10535.7 | 10455.8 | 10433.6 | 10351.9 | 11278.3 | 9949.2 | 11118.9 | 9865.9 | 10425.4 | 11880.9 | 9795.4 | 11261.3 | 9515.6 | 9226.4 | 10198.2 | 9712.1 | 10784.1 | 9569.1 | 10776.2 | 9495.8 | 9550.4 | 10637.1 | 9466.3 | 10797.4 | 10734.7 | 9295.2 | 10721.6 | 9873.8 | 10154.1 | 9539.4 | 10137.1 | 10638.2 | 10966.3 | 9753.7 | 10737.5 | 9393.6 | 9122.2 | 10813 | 9507.2 | 10750.8 | 9418.2 | 10752.1 | 9386.9 | 10615.3 | 9828.4 | 10621.2 | 9888.6 | 11111.9 | 9829.5 | 10377.5 | 9762.9 | 8129.2 | 10682.2 | 10172.8 | 9547.9 | 11051.7 | 10607.7 | 9683.7 | 9557.3 | 10771.5 | 9471.7 | 9894.7 | 10841.8 | 9411.2 | 10907.6 | 9446.4 | 10604.1 | 9692.7 | 10773.9 | 9203.2 | 10839.9 | 9708.9 | 10687.2 | 9681.1 | 10745.7 | 9822.5 | 9537.2 | 10624.9 | 9618.7 | 9462.8 | 10659.2 | 10347.2 | 10610.3 | 9666.6 | 10771.3 | 9459.5 | 10318.5 | 9762.4 | 10326.2 | 8971.1 | 10480.7 | 9542.7 | 9573.4 | 9682.7 | 9612.8 | 8288.2 | 9445.9 | 8373.1 | 9515.3 | 9521.1 | 11121.6 | 9565.6 | 11191.7 | 9748.3 | 10969.4 | 9552.3 | 9715.5 | 9642 | 10775.7 | 11203.5 | 10949.3 | 10957.4 | 11029.9 | 11069.4 | 9914.7 | 11046.2 | 10985.7 | 11197.8 | 11197 | 11134.8 | 11216.1 | 9988.1 | 10783.7 | 10021.9 | 21.8499 | 21.4998 | 21.1306 | 0 | 21.3582 | 21.1041 | 0 | 36.0725 | 0 | 0 | 0 | 0 | 1.9711 | 1.9238 | 1.9647 | 1.9524 | 1.8498 | 1.7943 | 4.67 | 3.935 | 4.26 | 3.805 | 3.793 | 3.694 | 4.057 | 4.3693 | 4.1011 | 4.0709 | 4.5521 | 5.1036 | 0.93315 | 1.0876 | 1.1228 | 0 | 1.1174 | 0.94497 | 5.3906 | 5.364 | 5.2235 | 4.9511 | 5.5262 | 5.2938 | 0.92312 | 1.0388 | 1.0212 | 0 | 1.1035 | 1.1757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203490 | 368 | 193573 | 374 | 373840.963 | 970 | 4.057 | 4.3693 | 4.1011 | 4.0709 | 4.5521 | 5.1036 | 5.3906 | 5.364 | 5.2235 | 4.9511 | 5.5262 | 5.2938 | 816000 | 1000 | 808000 | 1000 | 1617601 | 5000 | 1622000 | 1612601 | 10.7 | 4.3757 | 1.0412 | 5.2915 | 1.0525 | 23.79% | 19.89% | 21.3885 | 36.0725 | 1.9093 | 4.0262 | 1632067.7 | 1617334 | 1731211.6983 | 93.42%
2022-12-29 | 2023 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 334458.04 | 7:21 | 18:03 | 7836.6 | 8614.9 | 8566.3 | 8540.1 | 8594.4 | 8676.7 | 8595.3 | 8999.5 | 8599.2 | 8473.1 | 8475.2 | 8624.9 | 8547 | 8564.3 | 8576.9 | 8615.9 | 8549.8 | 8612.8 | 8627.5 | 8612.1 | 8518.9 | 8598.1 | 8442.1 | 8508.6 | 8377.9 | 7404.2 | 8508.4 | 8519.4 | 8697.5 | 8586.2 | 8364.7 | 8547.9 | 8705.4 | 8725.7 | 8632 | 8648.8 | 8769.6 | 8705.8 | 8699.8 | 8667 | 9403.5 | 8323.9 | 9272.1 | 8256.4 | 8723.6 | 9917.5 | 8148.1 | 9373.7 | 7878.9 | 7647.9 | 8441.5 | 8087.9 | 8953.4 | 7938.3 | 8959.9 | 7915.7 | 7931.4 | 8840.8 | 7844.1 | 8953 | 8893.8 | 7697.2 | 8914.9 | 8196.9 | 8452.9 | 7960.4 | 8431.5 | 8857.3 | 9127.2 | 8110.6 | 8935.6 | 7809.7 | 7589.4 | 8978.5 | 7897.2 | 8917.3 | 7838.6 | 8953.2 | 7824 | 8831.2 | 8177.4 | 8839.8 | 8189.2 | 9217.6 | 8145.3 | 8613.7 | 8125.4 | 6766.3 | 8906.3 | 8517.7 | 7974.1 | 9246.3 | 8888.6 | 8123.1 | 8040.4 | 9032.6 | 7959.4 | 8304.7 | 9124.5 | 7939.5 | 9195.2 | 7955.7 | 8949.2 | 8177.9 | 9098 | 7763.4 | 9155.7 | 8203.2 | 9042.6 | 8189.5 | 9111 | 8323.4 | 8026.2 | 8950.5 | 8115.9 | 7990.2 | 9024.6 | 8748.5 | 8976.4 | 8186.5 | 9124 | 8022.1 | 8743.7 | 8264.7 | 8755 | 7641.6 | 8899.9 | 8114.6 | 8116.6 | 8210 | 8166.3 | 7047.4 | 7983.4 | 7048 | 8065.3 | 8044.9 | 9358.1 | 8024.5 | 9377.4 | 8176.9 | 9220.6 | 8041.4 | 8200.5 | 8135.2 | 9009 | 9366.1 | 9225.2 | 9186.6 | 9271.6 | 9308 | 8303.9 | 9246.5 | 9150.9 | 9321.3 | 9330.4 | 9298.9 | 9360.3 | 8353.9 | 9012.3 | 8373.1 | 24.1259 | 24.1035 | 24.0214 | 0 | 24.0828 | 24.2068 | 0 | 34.0269 | 0 | 0 | 0 | 0 | 4.8169 | 4.9397 | 4.8447 | 4.9573 | 4.9852 | 4.8968 | 9.673 | 9.2 | 9.347 | 9.619 | 9.209 | 9.627 | 3.4244 | 3.7739 | 3.5102 | 3.4675 | 3.9051 | 4.1989 | 0.76778 | 0.91895 | 0.94051 | 0 | 0.96888 | 0.79375 | 4.3812 | 4.4975 | 4.3034 | 4.1183 | 4.5999 | 4.429 | 0.77488 | 0.88416 | 0.8693 | 0 | 0.95362 | 0.98742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204168 | 370 | 194252 | 376 | 375192.163 | 975 | 3.4244 | 3.7739 | 3.5102 | 3.4675 | 3.9051 | 4.1989 | 4.3812 | 4.4975 | 4.3034 | 4.1183 | 4.5999 | 4.429 | 678000 | 2000 | 679000 | 2000 | 1351200 | 5000 | 1353000 | 1346200 | 10.7 | 3.7133 | 0.87797 | 4.3882 | 0.89388 | 23.64% | 20.37% | 24.1081 | 34.0269 | 4.9068 | 9.4458 | 1364175.1 | 1351200 | 1446692.9082 | 93.4%
2022-12-30 | 2023 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 334458.04 | 7:25 | 18:07 | 9109.9 | 9994.4 | 9942.9 | 9903.5 | 9980.7 | 10049.6 | 9983.1 | 10445.5 | 9988 | 9848.4 | 9838.8 | 10012.5 | 9909.1 | 9943.2 | 9933.2 | 9983 | 9875.1 | 9953.7 | 9961.7 | 9950.2 | 9862.4 | 9960.7 | 9699.8 | 9818.1 | 9652.9 | 8565.2 | 9845.5 | 9847.1 | 10005.5 | 9866.5 | 9612.2 | 9839.7 | 10007.3 | 10057.4 | 9932.3 | 9950.3 | 10088.2 | 10006.2 | 9977.1 | 9922.3 | 10867.1 | 9630.3 | 10733.5 | 9540.8 | 10124.7 | 11423.3 | 9438.7 | 10830.7 | 9139.6 | 8859.2 | 9797.5 | 9353.5 | 10367.1 | 9197.7 | 10353 | 9130.9 | 9180.4 | 10241.6 | 9110.7 | 10367.4 | 10332 | 8950 | 10396.1 | 9588.6 | 9760.6 | 9171.3 | 9755 | 10223.3 | 10538.9 | 9379.3 | 10393.1 | 9045.9 | 8785.6 | 10420.9 | 9152 | 10388.6 | 9120.8 | 10395.7 | 9098 | 10305.1 | 9437.9 | 10222.2 | 9507.4 | 10658.7 | 9441.7 | 9976.6 | 9369.2 | 7799 | 10233.8 | 9726.5 | 9140.8 | 10582.1 | 10214.5 | 9335.7 | 9219.1 | 10326.6 | 9170.5 | 9552.6 | 10465.3 | 9103.7 | 10536.5 | 9113 | 10229.8 | 9361.4 | 10397 | 8864.5 | 10466 | 9350.6 | 10340.1 | 9354.9 | 10403.2 | 9484.8 | 9220.3 | 10243.3 | 9280.5 | 9113.6 | 10301 | 9985.2 | 10243.3 | 9323.6 | 10383.6 | 9121.6 | 9956.8 | 9412.8 | 9966.9 | 8636 | 10114.4 | 9185.8 | 9252 | 9385.2 | 9247.5 | 8020.8 | 9156.6 | 8101.8 | 9259.7 | 9255 | 10747.8 | 9207.6 | 10774 | 9402.8 | 10612.6 | 9264.1 | 9428 | 9366.8 | 10350.4 | 10743.2 | 10611.2 | 10543.5 | 10635.5 | 10669.7 | 9542.8 | 10609.3 | 10604.5 | 10766.9 | 10800.3 | 10735.7 | 10793.8 | 9622.7 | 10459 | 9631.7 | 17.5662 | 17.4272 | 17.2602 | 0 | 17.4683 | 17.5046 | 0 | 27.0674 | 0 | 0 | 0 | 0 | 3.9528 | 3.923 | 3.941 | 3.9929 | 3.8144 | 3.7613 | 6.806 | 6.392 | 6.519 | 6.564 | 6.318 | 6.036 | 3.8591 | 4.2472 | 3.9359 | 3.859 | 4.3414 | 4.7785 | 0.89851 | 1.081 | 1.0869 | 0 | 1.1135 | 0.92694 | 5.0415 | 5.1303 | 4.9124 | 4.6408 | 5.1902 | 4.9877 | 0.89738 | 1.0441 | 0.99883 | 0 | 1.1036 | 1.1539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204952 | 371 | 195032 | 378 | 376748.096 | 980.067 | 3.8591 | 4.2472 | 3.9359 | 3.859 | 4.3414 | 4.7785 | 5.0415 | 5.1303 | 4.9124 | 4.6408 | 5.1902 | 4.9877 | 784000 | 1000 | 780000 | 2000 | 1555933 | 5067 | 1561000 | 1550866 | 10.7 | 4.1702 | 1.0214 | 4.9838 | 1.0396 | 24.49% | 20.86% | 17.4453 | 27.0674 | 3.8976 | 6.4392 | 1571488.6 | 1555866 | 1668740.8768 | 93.24%
2022-12-31 | 2023 | 2022 | Year_1 | Year_1 | 2023-01-01 | 31 | 334458.04 | 7:24 | 18:09 | 10539.1 | 11037.1 | 10970.4 | 10948.7 | 10992 | 11068.6 | 11021.4 | 11339.4 | 10988.4 | 10826.8 | 10861.8 | 11015.9 | 10953.6 | 10948.6 | 10983.4 | 11030.8 | 10790 | 10830.6 | 11019.1 | 11022 | 10904 | 10991.5 | 10839.2 | 10930.3 | 10800.9 | 9629.1 | 10922.3 | 10933.7 | 11071.6 | 10941.8 | 10765.6 | 10939.8 | 11017.1 | 10937.9 | 11022.6 | 11029.7 | 11130.9 | 11083.8 | 11009.9 | 10832.4 | 11640 | 10664.1 | 11515.1 | 10591.3 | 11110.7 | 12143 | 10530.2 | 11614 | 10220.6 | 9913.9 | 10873 | 10462.7 | 11326.8 | 10277.9 | 11322 | 10224.6 | 10279.6 | 11236.3 | 10172.4 | 11339.2 | 11296.2 | 9997.8 | 11314.6 | 10653.3 | 10624.7 | 10220.1 | 10837 | 11207.5 | 11096.6 | 10375.8 | 11299.8 | 10078.5 | 9785.1 | 11322.2 | 10157 | 11053.9 | 10151.7 | 11277.4 | 10110 | 11212.9 | 10538.7 | 11178.1 | 10599.9 | 11517.3 | 10300.8 | 11008.3 | 10447.5 | 8711.5 | 11226.9 | 10908.3 | 10258.9 | 11510.5 | 11181.4 | 10395 | 10257.3 | 11268.2 | 10184.5 | 10617 | 11323 | 10142.7 | 11397.3 | 10004.8 | 11094.4 | 9908.6 | 11294.9 | 9895.6 | 11356.9 | 10425.8 | 11262.6 | 10413.3 | 11310.9 | 10535.1 | 10287.3 | 11216 | 10381.1 | 10185.2 | 11222.7 | 10989.8 | 11178.8 | 10375.1 | 11176.2 | 10141.5 | 10950.4 | 10482.4 | 10959.2 | 9629.8 | 11092.9 | 10233.2 | 10277 | 10421.4 | 10307.5 | 8906.2 | 10136.7 | 9045.8 | 10197.7 | 10236.4 | 11563.8 | 10256.3 | 11557.9 | 10439.9 | 11399.9 | 10258.4 | 10424.5 | 10358.3 | 11277.5 | 11544.4 | 11477.1 | 11422.1 | 11515.9 | 11523.5 | 10603.4 | 11455.7 | 11411.6 | 11550.1 | 11543.4 | 11487.2 | 11549.5 | 10652.1 | 11326 | 10679.6 | 17.2582 | 16.912 | 16.8932 | 0 | 16.8808 | 16.6833 | 0 | 29.3279 | 0 | 0 | 0 | 0 | 3.1041 | 3.0323 | 2.9837 | 3.2319 | 2.9956 | 2.9345 | 5.741 | 6.019 | 5.554 | 5.402 | 5.505 | 5.061 | 4.2393 | 4.6611 | 4.2814 | 4.2169 | 4.7706 | 5.3512 | 0.98832 | 1.1707 | 1.1979 | 0 | 1.1994 | 0.99571 | 5.651 | 5.744 | 5.4991 | 5.1608 | 5.8059 | 5.5191 | 0.97176 | 1.1253 | 1.0829 | 0 | 1.1894 | 1.2382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205817 | 373 | 195887 | 380 | 378459.096 | 985.067 | 4.2393 | 4.6611 | 4.2814 | 4.2169 | 4.7706 | 5.3512 | 5.651 | 5.744 | 5.4991 | 5.1608 | 5.8059 | 5.5191 | 865000 | 2000 | 855000 | 2000 | 1711000 | 5000 | 1716000 | 1706000 | 10.75 | 4.5868 | 1.1104 | 5.5633 | 1.1215 | 24.21% | 20.16% | 16.9255 | 29.3279 | 3.047 | 5.547 | 1728235.7 | 1710934 | 1854264.2808 | 92.27%
2023-01-01 | 2023 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 334535.47 | 7:23 | 18:08 | 10561.5 | 11178.9 | 11093 | 11045.9 | 11103.9 | 11213.1 | 11151.1 | 11612.3 | 11130.9 | 10880.3 | 10979.9 | 11154.3 | 11082.5 | 11085.9 | 11075.4 | 11149.6 | 11048.5 | 11135.7 | 11165.1 | 11159.1 | 11009.7 | 11128.8 | 10909.2 | 11033.7 | 10902.5 | 9638.1 | 11071.3 | 11059.2 | 11220.7 | 11049.6 | 10837.8 | 11074.6 | 11179.1 | 11235.2 | 11152.9 | 11162 | 11299.6 | 11231.2 | 11191 | 11089.5 | 11921.1 | 10679.4 | 11779 | 10588 | 11200.8 | 12416.3 | 10541 | 11897.4 | 10229.2 | 9921.1 | 10948.2 | 10458.1 | 11527.4 | 10297.3 | 11526.4 | 10206.4 | 10268.8 | 11377.3 | 10165 | 11515 | 11452 | 9987.3 | 11493.2 | 10681.7 | 10918.2 | 10259.7 | 10901.9 | 11393.4 | 11657.3 | 10476.4 | 11523 | 10085.6 | 9776.7 | 11538.2 | 10186.1 | 11510.9 | 9995.5 | 11492.9 | 10107 | 11403.2 | 5840.6 | 6271.9 | 5796.1 | 6325 | 5729.6 | 6028.9 | 5647.1 | 4694.1 | 11404 | 11004.9 | 10249.8 | 11763.3 | 11388.4 | 10438.8 | 10287.8 | 11497 | 10143.7 | 10629.4 | 11560.4 | 10155.8 | 11669.7 | 10164.7 | 11393.4 | 10446.7 | 11528.3 | 9914.3 | 11599.8 | 10449.1 | 11465 | 10422.1 | 11504.5 | 10563.8 | 10299.6 | 11449.2 | 10394.7 | 10206.8 | 11438.2 | 11134.6 | 11375.5 | 10392.2 | 11518.5 | 10167.9 | 11078.4 | 10501.1 | 11089.6 | 9625.3 | 11229.2 | 10231.8 | 10273.7 | 10418 | 10314.6 | 8899.1 | 10163.1 | 9034.8 | 10253.9 | 10227.6 | 11839.4 | 10260.6 | 11830.4 | 10443.8 | 11656.9 | 10241 | 10421.7 | 10352 | 11494.9 | 11830.4 | 11742.8 | 11679 | 11790.7 | 11789.5 | 10624.7 | 11718.3 | 11709.6 | 11863.7 | 11822 | 11764.4 | 11851.6 | 10697.1 | 11535.8 | 10751 | 19.1922 | 19.0533 | 18.684 | 0 | 18.9494 | 18.7732 | 0 | 34.5765 | 0 | 0 | 0 | 0 | 2.298 | 2.1506 | 2.122 | 2.2595 | 2.0181 | 2.1531 | 5.519 | 6.075 | 6.029 | 5.257 | 6.23 | 5.579 | 4.2752 | 4.7039 | 4.3556 | 4.2815 | 4.8541 | 5.4665 | 0.99977 | 1.1709 | 1.2127 | 0 | 1.2101 | 1.0015 | 5.7571 | 5.8305 | 5.5968 | 5.2737 | 5.8975 | 5.6386 | 0.9811 | 1.1178 | 1.0958 | 0 | 1.1917 | 1.2463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206691 | 375 | 196713 | 382 | 380152.03 | 990 | 4.2752 | 4.7039 | 4.3556 | 4.2815 | 4.8541 | 5.4665 | 5.7571 | 5.8305 | 5.5968 | 5.2737 | 5.8975 | 5.6386 | 874000 | 2000 | 826000 | 2000 | 1692934 | 4933 | 1696000 | 1688001 | 10.75 | 4.6561 | 1.119 | 5.6657 | 1.1265 | 24.03% | 19.88% | 18.9304 | 34.5765 | 2.1669 | 5.7815 | 1710192.7 | 1692867 | 1861144.8379 | 90.96%
2023-01-02 | 2023 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 334535.47 | 7:30 | 18:09 | 10529.6 | 11108.3 | 10998.5 | 10971.3 | 11018.5 | 11125.3 | 11078.9 | 11470.4 | 11073.9 | 10838.1 | 10936.6 | 11101.4 | 11040.2 | 11032.7 | 11041.8 | 11097.9 | 10994.9 | 11074.9 | 11102.2 | 11097 | 10970.9 | 11078.8 | 10865 | 10987.8 | 10865 | 9626 | 11024.1 | 11005.9 | 11143.3 | 10982.8 | 10811.2 | 11011.2 | 11120.9 | 11149 | 11093.3 | 11100.8 | 11212.5 | 11157.1 | 11112.3 | 11033.6 | 11795.4 | 10668.2 | 11651.3 | 10581.6 | 11166.2 | 12311.9 | 10517 | 11763.6 | 10204.1 | 9897.4 | 10923.3 | 10448.6 | 11425.6 | 10284.1 | 11407.9 | 10188.9 | 10253.9 | 11302 | 10147 | 11428.9 | 11375.7 | 9969.4 | 11428.4 | 10673.6 | 10876 | 10233.2 | 10876.1 | 11312.7 | 11525.8 | 10462.9 | 11407.6 | 10075.1 | 9755.2 | 11441.5 | 10171.5 | 11397.4 | 9977.3 | 11376.6 | 10087.8 | 11289.3 | 10557.8 | 11282.3 | 10606 | 11672.1 | 10558.1 | 11085.6 | 10459.2 | 8714.3 | 11340 | 10966.8 | 10254.5 | 11647.9 | 11306.3 | 10452.8 | 10311.2 | 11378.3 | 10153.4 | 10627.4 | 11411 | 10104.3 | 11527.2 | 10106.2 | 11276.6 | 10407.9 | 11399.5 | 9892 | 11477.4 | 10438.3 | 11380.1 | 10405.4 | 11401.5 | 10551.6 | 10268.8 | 11338 | 10376 | 10187.8 | 11335.1 | 11084.5 | 11281.5 | 10384.4 | 11412.1 | 10162.2 | 11031 | 10490.8 | 11042.1 | 9628.9 | 11181.9 | 10240.5 | 10309.6 | 10459.6 | 10320.6 | 8923.6 | 10168.7 | 9022.7 | 10233.1 | 10207.9 | 11704 | 10248.4 | 11693.9 | 10445.8 | 11543.2 | 10267.9 | 10450.9 | 9932.3 | 11390.5 | 11692.8 | 11604.1 | 11542 | 11654.6 | 11659.1 | 10622.4 | 11581.6 | 11573.1 | 11709.4 | 11672.6 | 11630.1 | 11700.8 | 10675.9 | 11433.6 | 10726.5 | 20.9411 | 20.5226 | 20.3289 | 0 | 20.3843 | 20.1244 | 0 | 34.0317 | 0 | 0 | 0 | 0 | 2.5969 | 2.5424 | 2.4842 | 2.6964 | 2.6053 | 2.5743 | 5.253 | 5.208 | 5.127 | 5.044 | 5.141 | 5.348 | 4.2807 | 4.7038 | 4.3576 | 4.2852 | 4.8532 | 5.4448 | 1.0083 | 1.1641 | 1.2197 | 0 | 1.2064 | 1.0013 | 5.741 | 5.8105 | 5.5807 | 5.271 | 5.8769 | 5.6233 | 0.99125 | 1.1142 | 1.1034 | 0 | 1.1919 | 1.2462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207561 | 376 | 197573 | 384 | 381874.897 | 994.933 | 4.2807 | 4.7038 | 4.3576 | 4.2852 | 4.8532 | 5.4448 | 5.741 | 5.8105 | 5.5807 | 5.271 | 5.8769 | 5.6233 | 870000 | 1000 | 860000 | 2000 | 1722867 | 4933 | 1727000 | 1717934 | 10.65 | 4.6542 | 1.12 | 5.6506 | 1.1294 | 24.06% | 19.99% | 20.4603 | 34.0317 | 2.5832 | 5.1868 | 1739563.8 | 1722800 | 1845985.4461 | 93.33%
2023-01-03 | 2023 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 334535.47 | 7:26 | 18:10 | 9950.9 | 10539.5 | 10454.3 | 10406.4 | 10471.1 | 10571.3 | 10500.8 | 10980.7 | 10514.3 | 10241.5 | 10360.4 | 10553.4 | 10458.8 | 10481.2 | 10470 | 10534.6 | 10438.5 | 10524.5 | 10560.2 | 10543.3 | 10402.8 | 10517.2 | 10275.9 | 10418.9 | 10280.3 | 9037.7 | 10436.7 | 10430.7 | 10621.7 | 10467.7 | 10248.1 | 10469 | 10570.9 | 10618.3 | 10539.7 | 10549.1 | 10686.1 | 10602.5 | 10580.6 | 10483.1 | 11406 | 10091.4 | 11245.4 | 9997.7 | 10616.3 | 11985.6 | 9936.5 | 11381.5 | 9641.3 | 9346.7 | 10324.6 | 9860.7 | 10928.1 | 9707.3 | 10918.8 | 9625.4 | 9693.3 | 10792.9 | 9585.7 | 10934 | 10877.3 | 9415.7 | 10956.8 | 10095.1 | 10291.1 | 9660.6 | 10281 | 10783.6 | 11074.8 | 9896.3 | 10921.4 | 9524.2 | 9213 | 10977.6 | 9601.1 | 10921.6 | 9424.7 | 10887.3 | 9532.4 | 10786.6 | 9962.9 | 10750.1 | 10005.2 | 11236.5 | 9958.5 | 10503.2 | 9895 | 8215.8 | 10830.3 | 10402.1 | 9676.4 | 11200.5 | 10774.6 | 9846.2 | 9720.6 | 10915.4 | 9585 | 10034.7 | 10982.6 | 9559.5 | 11066.9 | 9579 | 10760.9 | 9846.7 | 10907.7 | 9317.8 | 10979 | 9835.4 | 10836.2 | 9807.3 | 10901.2 | 9966.5 | 9694.7 | 10829.7 | 9786.4 | 9613.5 | 10839.6 | 10529.2 | 10776.2 | 9813 | 10929.8 | 9594 | 10466.6 | 9899.6 | 10463.3 | 9094.6 | 10626.2 | 9674.9 | 9737.1 | 9882.6 | 9748.3 | 8427 | 9640.1 | 8538 | 9676.4 | 9672.4 | 11311.3 | 9691.2 | 11305.6 | 9888.6 | 11128.5 | 9728.7 | 9899.9 | 9420.2 | 10898.5 | 11295.4 | 11162.9 | 11103 | 11229.2 | 11241.8 | 10043 | 11151.9 | 11123.3 | 11294 | 11266.2 | 11213.7 | 11278.9 | 10083.5 | 10935.2 | 10128.9 | 19.9684 | 19.3321 | 19.2231 | 0 | 19.2168 | 19.0143 | 0 | 31.4176 | 0 | 0 | 0 | 0 | 3.1294 | 3.1543 | 3.1146 | 3.088 | 3.0159 | 3.094 | 6.03 | 6.046 | 6.146 | 6.233 | 5.598 | 6.406 | 4.071 | 4.4717 | 4.1395 | 4.0715 | 4.584 | 5.1027 | 0.96081 | 1.1123 | 1.1597 | 0 | 1.1509 | 0.96312 | 5.3852 | 5.4589 | 5.2371 | 4.9593 | 5.5044 | 5.298 | 0.95037 | 1.0685 | 1.0564 | 0 | 1.1398 | 1.1984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208388 | 378 | 198393 | 385 | 383513.697 | 999.867 | 4.071 | 4.4717 | 4.1395 | 4.0715 | 4.584 | 5.1027 | 5.3852 | 5.4589 | 5.2371 | 4.9593 | 5.5044 | 5.298 | 827000 | 2000 | 820000 | 1000 | 1638800 | 4934 | 1644000 | 1633866 | 10.7333 | 4.4067 | 1.0694 | 5.3071 | 1.0827 | 24.27% | 20.4% | 19.3509 | 31.4176 | 3.0994 | 6.0765 | 1654570.4 | 1638600 | 1746907.5034 | 93.8%
2023-01-04 | 2023 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 334535.47 | 7:25 | 18:09 | 10767.3 | 11222.1 | 11147.5 | 11128.1 | 11173.2 | 11252.8 | 11212.1 | 11495.9 | 11163.5 | 10955.8 | 11054.3 | 11197.4 | 11155 | 11139.4 | 11184 | 11224 | 11126.7 | 11184.3 | 11203.9 | 11202.5 | 11096.5 | 11179.2 | 11020.1 | 11114.6 | 11009.4 | 9956.5 | 11129.9 | 11116.5 | 11248.4 | 11132.2 | 11002.4 | 11138.1 | 11226.3 | 11237.4 | 11195.5 | 11206.6 | 11294.8 | 11256 | 11221.9 | 11144.8 | 11782.1 | 10911.6 | 11663.1 | 10856.7 | 11311.7 | 12249.1 | 10790.5 | 11761.7 | 10531.3 | 10233.3 | 11071.5 | 10721 | 11479.1 | 10584.2 | 11466.3 | 10523.9 | 10591.5 | 11395.3 | 10492.1 | 11483 | 11444.2 | 10316.8 | 11480.3 | 10896 | 11038.6 | 10483.3 | 11046.3 | 11381.7 | 11548.3 | 10755.6 | 11452.8 | 10460.3 | 10104.6 | 11515.4 | 10493.1 | 11467.8 | 10336 | 11420.5 | 10434.3 | 11374 | 10803.1 | 11361.2 | 10836.9 | 11678.4 | 10793.9 | 11199.2 | 10708.7 | 8995.4 | 11413.5 | 11113.5 | 10588.9 | 11663.6 | 11371.1 | 10723.6 | 10603 | 11453.3 | 10537.7 | 10871.5 | 11484.7 | 10454.6 | 11561.9 | 10471.7 | 11393.3 | 10722.4 | 11449.9 | 10235.2 | 11523.4 | 10719.8 | 11461.1 | 10706.5 | 11460.8 | 10824.1 | 10551.5 | 11396.4 | 10648.7 | 10524 | 11403.9 | 11194 | 11355.5 | 10680.5 | 11445.7 | 10498.6 | 11152.9 | 10770.2 | 11178.2 | 9970.7 | 11287 | 10577.4 | 10635.7 | 10734.1 | 10641.8 | 9241 | 10556.6 | 9441.2 | 10567 | 10576.4 | 11689 | 10549.8 | 11681.8 | 10713.5 | 11560.3 | 10589.2 | 10711.5 | 10346.1 | 11452.5 | 11686.8 | 11625.5 | 11569.4 | 11647.7 | 11651.6 | 10847.2 | 11598.3 | 11594.2 | 11702.7 | 11693.5 | 11641.7 | 11702.7 | 10906.9 | 11486.7 | 10930.1 | 17.5611 | 16.9706 | 17.1181 | 0 | 16.8829 | 16.7558 | 0 | 27.983 | 0 | 0 | 0 | 0 | 4.5827 | 4.4857 | 4.3085 | 4.5381 | 4.227 | 4.2197 | 7.628 | 8.511 | 7.152 | 7.988 | 7.709 | 8.224 | 4.3926 | 4.8416 | 4.469 | 4.4007 | 4.9678 | 5.5493 | 1.057 | 1.2289 | 1.2723 | 0 | 1.2719 | 1.0568 | 5.8544 | 5.9443 | 5.6958 | 5.3714 | 6.0037 | 5.7414 | 1.0376 | 1.1819 | 1.1517 | 0 | 1.2567 | 1.3172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209271 | 380 | 199268 | 387 | 385262.83 | 1004.8 | 4.3926 | 4.8416 | 4.469 | 4.4007 | 4.9678 | 5.5493 | 5.8544 | 5.9443 | 5.6958 | 5.3714 | 6.0037 | 5.7414 | 883000 | 2000 | 875000 | 2000 | 1749133 | 4933 | 1754000 | 1744200 | 10.7333 | 4.7702 | 1.1774 | 5.7685 | 1.189 | 24.68% | 20.61% | 17.0577 | 27.983 | 4.3936 | 7.8687 | 1766259.4 | 1749066 | 1917668.9147 | 91.21%
2023-01-05 | 2023 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 334661.92 | 7:32 | 18:11 | 10647.5 | 11126.9 | 11032.4 | 11021.2 | 11047.9 | 11137.1 | 11100.7 | 11422.5 | 11046.7 | 10812.5 | 10924.1 | 11066.8 | 11010.8 | 10996.1 | 11047 | 11079.3 | 10984 | 11037 | 11040.3 | 11038.1 | 10931.4 | 11012.1 | 10858.5 | 10941.8 | 10841 | 9805.6 | 10956.3 | 10938.8 | 11067.8 | 10957.9 | 10832.8 | 10971.3 | 11063.8 | 11073.5 | 11033.7 | 11043.3 | 11132.7 | 11092 | 11054.9 | 10970.8 | 11641.2 | 10735 | 11510.2 | 10674.5 | 11127.5 | 12109.2 | 10612.1 | 11624.5 | 10381.4 | 10083.9 | 10917.2 | 10553.4 | 11331.6 | 10440.7 | 11309.9 | 10365.9 | 10428.7 | 11230.8 | 10344.5 | 11320.2 | 11283.6 | 10166.2 | 11307.2 | 10704.4 | 10862.8 | 10306.3 | 10871.3 | 11203 | 11413.3 | 10573.9 | 11280.4 | 10275.6 | 9967.6 | 11341.6 | 10337.1 | 11294.9 | 10168.4 | 11269.5 | 10272.7 | 11209.2 | 10600.3 | 11174.5 | 10626.9 | 11497.3 | 10593.2 | 10999.5 | 10503.4 | 8834.5 | 11227 | 10901.2 | 10385.5 | 11477.5 | 11166.7 | 10517.8 | 10405 | 11249.3 | 10332.1 | 10666.2 | 11304.4 | 10269.2 | 11375.3 | 10279.7 | 11185.9 | 10521.8 | 11259.7 | 10050.1 | 11331.4 | 10520.8 | 11257.8 | 10499.1 | 11276.5 | 10639.6 | 10391.3 | 11221 | 10430.8 | 10311.8 | 11208.7 | 10969 | 11165.8 | 10484.1 | 11281.8 | 10322.1 | 10951.1 | 10573.4 | 10975.9 | 9807.5 | 11109.3 | 10415.1 | 10473.5 | 10571.3 | 10487.9 | 9106 | 10363.9 | 9277 | 10432.3 | 10430.7 | 11559.3 | 10385.2 | 11557.9 | 10564.6 | 11443.7 | 10454.3 | 10576 | 10188.5 | 11298 | 11557.7 | 11466.9 | 11416.7 | 11495.1 | 11505.9 | 10691.6 | 11455.9 | 11460.6 | 11581.9 | 11567 | 11509.9 | 11571.6 | 10747.5 | 11323.2 | 10776.6 | 18.0174 | 17.1788 | 16.9942 | 0 | 16.8599 | 16.6892 | 0 | 28.1197 | 0 | 0 | 0 | 0 | 4.7181 | 4.7514 | 4.6428 | 4.7554 | 4.6521 | 4.399 | 8.923 | 8.642 | 8.666 | 8.565 | 8.759 | 7.859 | 4.3433 | 4.7696 | 4.4155 | 4.3372 | 4.8834 | 5.4697 | 1.051 | 1.2017 | 1.262 | 0 | 1.2374 | 1.0282 | 5.7912 | 5.8517 | 5.6255 | 5.3157 | 5.885 | 5.6589 | 1.0305 | 1.1553 | 1.1405 | 0 | 1.2172 | 1.2831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210141 | 381 | 200129 | 389 | 386985.097 | 1009.8 | 4.3433 | 4.7696 | 4.4155 | 4.3372 | 4.8834 | 5.4697 | 5.7912 | 5.8517 | 5.6255 | 5.3157 | 5.885 | 5.6589 | 870000 | 1000 | 861000 | 2000 | 1722267 | 5000 | 1728000 | 1717267 | 10.65 | 4.7031 | 1.1561 | 5.688 | 1.1653 | 24.58% | 20.49% | 17.1479 | 28.1197 | 4.6531 | 8.569 | 1739896.4 | 1722134 | 1896442.2515 | 90.81%
2023-01-06 | 2023 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 334661.92 | 7:25 | 18:12 | 10828.6 | 11316.4 | 11186.4 | 11152.9 | 11204.1 | 11323.5 | 11279.6 | 11634.8 | 11270.7 | 10995.7 | 11158 | 11302 | 11236.9 | 11235.6 | 11265.2 | 11302.8 | 11213.5 | 11278.2 | 11294.8 | 11293.8 | 11189.2 | 11267.5 | 11122.8 | 11201.1 | 11106.7 | 9994.4 | 11216.6 | 11210.5 | 11347.5 | 11227.5 | 11094.5 | 11236.5 | 11331.8 | 11348.7 | 11304.9 | 11316.4 | 11414.7 | 11373.7 | 11335.2 | 11237.4 | 11920.4 | 10976.5 | 11796.3 | 10921.1 | 11392.8 | 12392.9 | 10849.5 | 11900.2 | 10560.6 | 10320.8 | 11243.5 | 10782.2 | 11589.5 | 10632.2 | 11573.7 | 10555.9 | 10622.8 | 11485.9 | 10506.1 | 11588.4 | 11541.2 | 10317.6 | 11571.8 | 10934.3 | 11110.2 | 10510.6 | 11111.7 | 11484.5 | 11689.1 | 10808.3 | 11537.7 | 10445.2 | 10143 | 11602.9 | 10529.2 | 11549.1 | 10327.6 | 11531.1 | 10449.1 | 11458.5 | 10862.7 | 11571.9 | 10999.7 | 11809.5 | 10863.6 | 11304 | 10757.8 | 9597.4 | 11535.8 | 11186.8 | 10630.7 | 11796.3 | 11457.1 | 10764.9 | 10643 | 11564.9 | 10551.8 | 10934.4 | 11613.1 | 10496.9 | 11694.6 | 10511.1 | 11490.7 | 10770.2 | 11571.8 | 10264.7 | 11645.6 | 10784.2 | 11565.1 | 10762.7 | 11589.4 | 10906 | 10628.6 | 11506.3 | 10699.1 | 10550.9 | 11505.2 | 11282.2 | 11427.5 | 10720.8 | 11563.2 | 10527.4 | 11221 | 10809.2 | 11265.3 | 9995.3 | 11376.1 | 10617.7 | 10684.3 | 10785.8 | 10692.7 | 9279.7 | 10581.5 | 9435.5 | 10611.1 | 10606.2 | 11849 | 10603.7 | 11836.6 | 10792.5 | 11717.1 | 10661.7 | 10804.3 | 10340.5 | 11570.8 | 11836 | 11747.5 | 11699 | 11789 | 11801.9 | 10928.3 | 11727.7 | 11215.6 | 11344.6 | 11318.8 | 11265.1 | 11314.3 | 10497.7 | 11109.2 | 10550.3 | 20.0515 | 19.2023 | 19.1394 | 0 | 18.975 | 18.6151 | 0 | 31.1814 | 0 | 0 | 0 | 0 | 4.0014 | 4.1023 | 4.0222 | 4.0489 | 3.9102 | 3.7157 | 7.496 | 7.285 | 7.537 | 7.834 | 7.024 | 7.053 | 4.4267 | 4.8838 | 4.5322 | 4.4426 | 5.0261 | 5.6115 | 1.074 | 1.2042 | 1.2998 | 0 | 1.2336 | 1.0273 | 5.9127 | 5.9833 | 5.7798 | 5.4848 | 6.033 | 5.8108 | 1.058 | 1.1549 | 1.1756 | 0 | 1.2184 | 1.2812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211030 | 383 | 201006 | 391 | 388743.097 | 1014.733 | 4.4267 | 4.8838 | 4.5322 | 4.4426 | 5.0261 | 5.6115 | 5.9127 | 5.9833 | 5.7798 | 5.4848 | 6.033 | 5.8108 | 889000 | 2000 | 877000 | 2000 | 1758000 | 4933 | 1762000 | 1753067 | 10.7833 | 4.8205 | 1.1678 | 5.8341 | 1.1776 | 24.22% | 20.19% | 19.1967 | 31.1814 | 3.9668 | 7.3715 | 1776107.3 | 1757800 | 1921173.1926 | 91.5%
2023-01-07 | 2023 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 334793.875 | 7:27 | 18:14 | 9457.9 | 10016.7 | 9893.5 | 9805.3 | 9900.1 | 10060.7 | 9985.2 | 10415.9 | 9998.5 | 9662.7 | 9886 | 10054 | 9955.4 | 9989.7 | 9974 | 10018.9 | 9937.9 | 10009.1 | 10046.5 | 10029.9 | 9924.8 | 10011 | 9836.6 | 9930.4 | 9850.6 | 8699.8 | 9949.1 | 9953.5 | 10137 | 9990.4 | 9826.1 | 10028.3 | 10133.1 | 10160.5 | 10095 | 10098.3 | 10211.9 | 10151.4 | 10118.5 | 10042.2 | 10770.2 | 9653 | 10643.3 | 9555.6 | 10133.3 | 11324.1 | 9497 | 10754.6 | 9194.1 | 9437.2 | 10062.7 | 9426.8 | 10380.6 | 9245.4 | 10400.7 | 9217 | 9272.1 | 10286.3 | 9134.5 | 10393.5 | 10333.8 | 8974.6 | 10295.9 | 9622.2 | 9859.7 | 9213.6 | 9862.7 | 10349 | 10585.3 | 9531.6 | 10432.7 | 9173.3 | 8870.1 | 10487.2 | 9220.5 | 10424.4 | 9035.3 | 10408.3 | 9153.1 | 10321.3 | 9579.5 | 10462.5 | 9734.4 | 10729.9 | 9588.3 | 10124.8 | 9510 | 8423.8 | 10410 | 10026.9 | 9324.9 | 10710.4 | 10342.2 | 9491 | 9372.9 | 10454.2 | 9233.4 | 9656.9 | 10512.8 | 9178.4 | 10576.9 | 9203.9 | 10319.3 | 9452.8 | 10462 | 8967.5 | 10519 | 9464.7 | 10401.3 | 9447.9 | 10445.3 | 9567.3 | 9320.8 | 10345.5 | 9386.2 | 9217.7 | 10376.8 | 10100.1 | 10314.3 | 9416.8 | 10410.6 | 9169 | 10055.3 | 9494.6 | 10012.6 | 8720.8 | 10167.5 | 9259.7 | 9338.6 | 9483.3 | 9304.1 | 8060.9 | 9216.2 | 8214 | 9228.9 | 9219.8 | 10743.6 | 9278 | 10719.1 | 9439.4 | 10585.2 | 9303.4 | 9466 | 8995.4 | 10395.3 | 10732 | 10621.1 | 10572.6 | 10660.9 | 10682.3 | 9594.7 | 10601.7 | 10614.6 | 10758.6 | 10768.5 | 10728.3 | 10741.4 | 9643.4 | 10468.2 | 9688.8 | 20.7947 | 20.3268 | 20.2911 | 0 | 20.3037 | 20.222 | 0 | 32.4353 | 0 | 0 | 0 | 0 | 2.6945 | 2.6805 | 2.7215 | 2.7196 | 2.547 | 2.5272 | 5.068 | 5.261 | 4.488 | 4.952 | 4.384 | 5.172 | 3.9739 | 4.3782 | 4.0301 | 3.9933 | 4.4615 | 4.8739 | 0.91122 | 1.099 | 1.1009 | 0 | 1.1367 | 0.9581 | 5.1321 | 5.2443 | 4.991 | 4.7531 | 5.3126 | 5.1024 | 0.91096 | 1.0603 | 1.0138 | 0 | 1.1343 | 1.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211819 | 385 | 201792 | 393 | 390311.097 | 1019.6 | 3.9739 | 4.3782 | 4.0301 | 3.9933 | 4.4615 | 4.8739 | 5.1321 | 5.2443 | 4.991 | 4.7531 | 5.3126 | 5.1024 | 789000 | 2000 | 786000 | 2000 | 1568000 | 4867 | 1571000 | 1563133 | 10.7833 | 4.2852 | 1.0412 | 5.0892 | 1.062 | 24.3% | 20.87% | 20.3877 | 32.4353 | 2.6484 | 4.8875 | 1582514.7 | 1567667 | 1671051.8915 | 93.81%
2023-01-08 | 2023 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 334767.775 | 7:33 | 18:11 | 9618.2 | 10192.1 | 10066.8 | 10021.2 | 10058.5 | 10243.2 | 10129.2 | 10615.7 | 10157.4 | 9785.2 | 10039.2 | 10216 | 10125.8 | 10156 | 10123.9 | 10193.7 | 10114.5 | 10181.5 | 10221.6 | 10197.7 | 10075.5 | 10169.7 | 9966.9 | 10086.6 | 9987.8 | 8811.3 | 10089 | 10106.6 | 10294.9 | 10131.5 | 9959.4 | 10182.5 | 10263.3 | 10301.7 | 10234 | 10230 | 10371.1 | 10297.6 | 10267.9 | 10174 | 11082.2 | 9790.4 | 10912.9 | 9697.2 | 10266.1 | 11725.8 | 9644.9 | 11061.6 | 9318.4 | 9576.8 | 10221.3 | 9558.5 | 10587 | 9375.8 | 10611.1 | 9351.3 | 9412 | 10477.3 | 9254.7 | 10602.6 | 10522.1 | 9086.9 | 10357.8 | 9748.9 | 10009.8 | 9316.3 | 9988.9 | 10480.6 | 10824.8 | 9619.1 | 10602.6 | 9263.3 | 8980.8 | 10658.3 | 9336.9 | 10587.1 | 9147.3 | 10608.4 | 9278.1 | 10501.1 | 9663.5 | 10585.8 | 9798.1 | 10917.9 | 9664.1 | 10203.3 | 9581.8 | 8484.1 | 10507.2 | 10103.3 | 9388 | 10891.3 | 10462.5 | 9561.6 | 9441.4 | 10616.7 | 9290.6 | 9743.3 | 10669.1 | 9261.9 | 10729.2 | 9279.1 | 10425.9 | 9538.2 | 10608.1 | 9049 | 10668.9 | 9568.8 | 10532.7 | 9548.8 | 10601 | 9685.6 | 9405.8 | 10470.4 | 9488.3 | 9321.7 | 10514.1 | 10338 | 10454.2 | 9488.7 | 10579.2 | 9285.5 | 10171.2 | 9604.6 | 10155.6 | 8827.6 | 10305 | 9384.9 | 9417.2 | 9551.2 | 9438.7 | 8168.9 | 9348.8 | 8336.5 | 9358.6 | 9349.2 | 10982.4 | 9392.1 | 10957.2 | 9538.3 | 10787.4 | 9409.9 | 9577.4 | 9107.5 | 10561.7 | 10982.1 | 10809.6 | 10763.4 | 10885.9 | 10911.5 | 9717.8 | 10816 | 10767.8 | 10975.5 | 11001.2 | 10975 | 10986.9 | 9783.1 | 10608.8 | 9810.8 | 22.0689 | 21.8352 | 21.6487 | 0 | 22.006 | 21.5985 | 0 | 36.076 | 0 | 0 | 0 | 0 | 2.0759 | 2.0977 | 2.0581 | 2.1335 | 2.0536 | 2.0691 | 5.0083 | 4.9033 | 4.5333 | 5.6583 | 4.88 | 5.2117 | 4.0203 | 4.4407 | 4.08 | 4.0281 | 4.5313 | 5.003 | 0.93688 | 1.1095 | 1.142 | 0 | 1.1446 | 0.94254 | 5.2662 | 5.3778 | 5.1414 | 4.8697 | 5.4145 | 5.2134 | 0.93329 | 1.0636 | 1.0445 | 1.1548 | 1.1326 | 1.173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212622 | 386 | 202587 | 394 | 391902.564 | 1024.4 | 4.0203 | 4.4407 | 4.08 | 4.0281 | 4.5313 | 5.003 | 5.2662 | 5.3778 | 5.1414 | 4.8697 | 5.4145 | 5.2134 | 803000 | 1000 | 795000 | 1000 | 1591467 | 4800 | 1596000 | 1586667 | 10.6333 | 4.3506 | 1.0551 | 5.2138 | 1.0836 | 24.25% | 20.78% | 21.8315 | 36.076 | 2.0813 | 5.0325 | 1605849.7 | 1591334 | 1695485.1788 | 93.86%
2023-01-09 | 2023 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 334767.775 | 7:32 | 18:10 | 7878.1 | 8300.3 | 8163.2 | 8155 | 8161.4 | 8300 | 8236.5 | 8572.6 | 8286.4 | 8087.4 | 8173.2 | 8307.1 | 8242.8 | 8246.9 | 8273 | 8316.8 | 8230.7 | 8271.9 | 8302 | 8277.3 | 8210.9 | 8273.7 | 8144.5 | 8215 | 8126 | 7231.6 | 8211.2 | 8204.3 | 8354.1 | 8238 | 8118.2 | 8256.4 | 8351.2 | 8368.8 | 8329.6 | 8317.1 | 8398.5 | 8351.1 | 8323.5 | 8279.6 | 8864.1 | 7984.4 | 8763.9 | 7908.9 | 8334.6 | 9319.6 | 7866.7 | 8863.5 | 7647.3 | 7852.1 | 8323.1 | 7846.5 | 8577.4 | 7687 | 8619.5 | 7698.3 | 7762.1 | 8529.2 | 7612.2 | 8602.8 | 8551.9 | 7473.8 | 8424.6 | 7989.2 | 8221 | 7704.8 | 8211.5 | 8580.6 | 8792.9 | 7943.1 | 8637.1 | 7666.8 | 7458.6 | 8683.9 | 7736.3 | 8640 | 7575 | 8660.5 | 7692.1 | 8585.7 | 7981.3 | 8662.9 | 8094 | 8877.5 | 7981.1 | 8390.5 | 7918.1 | 7053.4 | 8600.9 | 8336.5 | 7767 | 8855.6 | 8559.4 | 7904 | 7812.5 | 8658.1 | 7719.2 | 8047.4 | 8718.9 | 7689.9 | 8761.3 | 7695.6 | 8561.8 | 7892.5 | 8671.9 | 7508.5 | 8723.9 | 7906.7 | 8634.3 | 7897.4 | 8673 | 8002.7 | 7813.6 | 8581.2 | 7862.3 | 7735.7 | 8626.3 | 8495.8 | 8570.9 | 7888.1 | 8666.6 | 7712.2 | 8369.1 | 7938.2 | 8353.5 | 7345.3 | 8492.7 | 7801.8 | 7818.3 | 7914.4 | 7846.9 | 6791 | 7741.9 | 6903.7 | 7742.4 | 7740.7 | 8891 | 7711.5 | 8897.5 | 7878.7 | 8747.9 | 7729.3 | 7895.3 | 7541.9 | 8611.3 | 8890.1 | 8809.8 | 8779.4 | 8835.2 | 8859.7 | 8007.9 | 8792.4 | 8774.3 | 8891.4 | 8900.5 | 8876.9 | 8889.2 | 8033.1 | 8671 | 8067.3 | 22.3294 | 22.0944 | 21.9812 | 0 | 22.3215 | 21.9596 | 0 | 33.8729 | 0 | 0 | 0 | 0 | 1.8786 | 1.8715 | 1.8714 | 1.7301 | 1.7793 | 1.7305 | 5.53 | 6.042 | 5.848 | 5.899 | 4.907 | 5.12 | 3.4431 | 3.7641 | 3.5431 | 3.4995 | 3.8571 | 4.0009 | 0.81182 | 0.88792 | 0.98275 | 0 | 0.91876 | 0.76728 | 4.2224 | 4.2796 | 4.1799 | 4.1238 | 4.3341 | 4.3055 | 0.83524 | 0.85635 | 0.92451 | 0 | 0.91445 | 0.95392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 213275 | 338 | 203241 | 396 | 393204.764 | 1029.2 | 3.4431 | 3.7641 | 3.5431 | 3.4995 | 3.8571 | 4.0009 | 4.2224 | 4.2796 | 4.1799 | 4.1238 | 4.3341 | 4.3055 | 653000 | -48000 | 654000 | 2000 | 1302200 | 4800 | 1353000 | 1297400 | 10.6333 | 3.6846 | 0.8737 | 4.2409 | 0.89689 | 23.71% | 21.15% | 22.1372 | 33.8729 | 1.8102 | 5.5577 | 1314271.5 | 1302067 | 1393707.7999 | 93.42%
2023-01-10 | 2023 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 334767.775 | 7:26 | 18:13 | 10242.7 | 10814.7 | 10646.7 | 10628.2 | 10636.3 | 10832.5 | 10772.6 | 11128.3 | 10754.8 | 10575.8 | 10612 | 10783.1 | 10712.6 | 10718.4 | 10725.7 | 10793.3 | 10695.9 | 10756.7 | 10790.8 | 10763 | 10653.1 | 10744.6 | 10554.7 | 10671.5 | 10578.2 | 9345.2 | 10687.8 | 10684 | 10848.4 | 10686.9 | 10538.5 | 10748.5 | 10820.2 | 10852.9 | 10810.6 | 10803.9 | 10922.9 | 10863.7 | 10823.7 | 10731 | 11536.4 | 10392.1 | 11394 | 10298.3 | 10868.4 | 12064.8 | 10235 | 11511.7 | 9871 | 10134.5 | 10797.9 | 10114.9 | 11117.3 | 9931 | 11129.9 | 9898.1 | 9969.3 | 11022.7 | 9802.1 | 11127 | 11066.6 | 9623.5 | 10911.8 | 10328.2 | 10580.5 | 9849.5 | 10566.7 | 11027.8 | 11295.1 | 10187.8 | 11111.5 | 9805 | 9527.7 | 11159.6 | 9897.3 | 11100.2 | 9683.5 | 11121.8 | 9824.3 | 11028.1 | 10255.7 | 11136.2 | 10409 | 11404.1 | 10247.9 | 10795.8 | 10146.2 | 8994.2 | 11075.8 | 10689.7 | 9971.6 | 11381 | 11014.1 | 10133.6 | 9993.6 | 11109.7 | 9909.4 | 10311.8 | 11178 | 9820.4 | 11262.5 | 9855.8 | 11016.8 | 10113.7 | 11132.6 | 9608.9 | 11202.5 | 10154.5 | 11090.8 | 10117.8 | 11130.1 | 10265.6 | 9975.9 | 11026.2 | 10059.9 | 9880.4 | 11048.6 | 10914 | 10993.8 | 10080.4 | 11118.3 | 9859.8 | 10750.3 | 10191.5 | 10743.2 | 9358 | 10884.8 | 9951.6 | 9996.3 | 10134.5 | 10038 | 8664.3 | 9895.7 | 8831.7 | 9928.3 | 9949.9 | 11437.7 | 9965.7 | 11404.9 | 10102.5 | 11266.7 | 9989.1 | 10133.8 | 9650.4 | 11117.4 | 11438.5 | 11314.3 | 11267.3 | 11369.6 | 11380.2 | 10300.7 | 11312.4 | 11294.3 | 11452 | 11453.9 | 11433.6 | 11462 | 10369.6 | 11147.6 | 10400.8 | 21.7183 | 21.2746 | 21.1717 | 0 | 21.254 | 21.0388 | 0 | 35.0697 | 0 | 0 | 0 | 0 | 2.2082 | 2.1557 | 2.1345 | 2.1753 | 2.1014 | 1.9731 | 4.44 | 4.574 | 4.37 | 4.504 | 4.285 | 4.611 | 4.2089 | 4.6341 | 4.2654 | 4.2147 | 4.7473 | 5.2648 | 0.9832 | 1.145 | 1.1908 | 0 | 1.1824 | 0.98508 | 5.5523 | 5.6406 | 5.4134 | 5.1217 | 5.697 | 5.4693 | 0.97411 | 1.0986 | 1.0838 | 0 | 1.1729 | 1.2259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214122 | 389 | 204080.06 | 399 | 394882.498 | 1034 | 4.2089 | 4.6341 | 4.2654 | 4.2147 | 4.7473 | 5.2648 | 5.5523 | 5.6406 | 5.4134 | 5.1217 | 5.697 | 5.4693 | 847000 | 51000 | 839060 | 3000 | 1677734 | 4800 | 1632060 | 1672934 | 10.7833 | 4.5559 | 1.0973 | 5.4824 | 1.1111 | 24.09% | 20.27% | 21.2915 | 35.0697 | 2.1247 | 4.464 | 1694337.1 | 1677467 | 1787250.8974 | 93.86%
2023-01-11 | 2023 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 334767.775 | 7:27 | 18:11 | 9811.8 | 10410 | 10304.6 | 10260.6 | 10333.6 | 10458.3 | 10361.3 | 10842.1 | 10362.1 | 10131 | 10209.5 | 10392.6 | 10295.4 | 10311.3 | 10296 | 10365.4 | 10284.2 | 10356.6 | 10384.3 | 10354.1 | 10237.1 | 10333.4 | 10133 | 10250 | 10129.4 | 8932.2 | 10235.2 | 10253.6 | 10444.5 | 10281.5 | 10112.5 | 10330.2 | 10396.9 | 10436.8 | 10382.9 | 10386.4 | 10531.6 | 10451.3 | 10420 | 10329.3 | 11205.8 | 9973.8 | 11058.7 | 9884.6 | 10481.7 | 11759.9 | 9810.3 | 11185.4 | 9464.5 | 9721.4 | 10372.1 | 9695.3 | 10748.7 | 9531.6 | 10761.6 | 9512 | 9555.6 | 10637.3 | 9413 | 10751.6 | 10675.8 | 9229 | 10505.6 | 9879 | 10176 | 9478.5 | 10132.7 | 10639.4 | 10954.2 | 9774.4 | 10746.2 | 9399.3 | 9131.7 | 10793.8 | 9487 | 10732.5 | 9279.4 | 10758.2 | 9415.4 | 10650 | 9823.2 | 10742.1 | 9957.1 | 11057.6 | 9820 | 10374 | 9737.7 | 8631.1 | 10663.8 | 10280.9 | 9532.8 | 11021.6 | 10643 | 9743.5 | 9636.4 | 10745.4 | 9489.9 | 9870.7 | 10834.1 | 9408.5 | 10918.5 | 9451 | 10631.3 | 9715.3 | 10786.2 | 9227.1 | 10844.5 | 9736.2 | 10720.8 | 9715.1 | 10789.4 | 9864.5 | 9552.2 | 10645.1 | 9643.2 | 9479.5 | 10676 | 10522.6 | 10624.9 | 9667 | 10769.3 | 9459 | 10335.1 | 9772.5 | 10339.8 | 8999.3 | 10487.1 | 9555.5 | 9602.3 | 9739.5 | 9628.5 | 8327.1 | 9491.9 | 8452.1 | 9590.1 | 9579.7 | 11127.9 | 9580.4 | 11134.2 | 9773.8 | 10963 | 9604.5 | 9784.4 | 9318.1 | 10741.6 | 11121.7 | 10996.6 | 10959.9 | 11049.4 | 11068.2 | 9918.6 | 11024.4 | 10957.8 | 11133.6 | 11141.4 | 11138.7 | 11172.4 | 9992.3 | 10797.4 | 10024.6 | 22.5928 | 22.6392 | 22.775 | 0 | 22.6508 | 22.6925 | 0 | 34.1752 | 0 | 0 | 0 | 0 | 5.1208 | 5.1962 | 5.1417 | 5.1121 | 4.9288 | 5.0505 | 10.003 | 9.651 | 10.512 | 9.89 | 10.561 | 9.838 | 4.0424 | 4.481 | 4.1399 | 4.0699 | 4.5828 | 5.0262 | 0.95117 | 1.0961 | 1.1655 | 0 | 1.1276 | 0.93885 | 5.3456 | 5.3746 | 5.1781 | 4.9521 | 5.3803 | 5.272 | 0.95766 | 1.0505 | 1.0678 | 0 | 1.1084 | 1.1713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214937 | 390 | 204889 | 400 | 396499.764 | 1038.8 | 4.0424 | 4.481 | 4.1399 | 4.0699 | 4.5828 | 5.0262 | 5.3456 | 5.3746 | 5.1781 | 4.9521 | 5.3803 | 5.272 | 815000 | 1000 | 808940 | 1000 | 1617266 | 4800 | 1621940 | 1612466 | 10.7333 | 4.3904 | 1.0558 | 5.2504 | 1.0711 | 24.05% | 20.4% | 22.6701 | 34.1752 | 5.0917 | 10.0758 | 1632773.1 | 1617266 | 1724633.5296 | 93.77%
2023-01-12 | 2023 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 334767.775 | 7:27 | 18:14 | 9762.1 | 10335.3 | 10288.3 | 10264.9 | 10305.2 | 10395.6 | 10297.2 | 10790.3 | 10327.6 | 10086.1 | 10185.1 | 10371.5 | 10252.2 | 10295.7 | 10229.4 | 10315.8 | 10211.1 | 10295.4 | 10337.5 | 10312.5 | 10201.1 | 10299.9 | 10082.2 | 10204.2 | 10119.1 | 8931 | 10234.5 | 10231.7 | 10423 | 10280.3 | 10084.6 | 10311.3 | 10371 | 10423.6 | 10366.1 | 10355.9 | 10487.8 | 10395.5 | 10366.8 | 10288.3 | 11202.2 | 9899.4 | 11037.3 | 9502.5 | 10254.7 | 11688.1 | 9754.1 | 11184.5 | 9467 | 9722.2 | 10386.6 | 9720.3 | 10762.2 | 9527.5 | 10770.1 | 9517.3 | 9542.9 | 10614.5 | 9427.7 | 10769.9 | 10701.8 | 9256.7 | 10449.9 | 9834.4 | 10135.9 | 9445.1 | 10111.1 | 10613.9 | 10958.1 | 9749.7 | 10734.6 | 9377.7 | 9117.5 | 10783.7 | 9469.7 | 10736.3 | 9263.6 | 10768.7 | 9406.4 | 10632.6 | 9799.1 | 10734.9 | 9924.4 | 11075.6 | 9797 | 10343.9 | 9747.9 | 8615.7 | 10663 | 10249.4 | 9523.4 | 11048.5 | 10612.5 | 9706.7 | 9591.8 | 10758.3 | 9468.3 | 9856.7 | 10827.5 | 9403.5 | 10915.7 | 9430.4 | 10594.9 | 9683.7 | 10771.6 | 9194.2 | 10832.4 | 9717.4 | 10679.1 | 9675.3 | 10748 | 9831.6 | 9543.7 | 10626.1 | 9616.1 | 9457.8 | 10666.2 | 10518 | 10614.7 | 9663.1 | 10773.4 | 9447.6 | 10317.6 | 9750.4 | 10302.8 | 8968.9 | 10470 | 9541.2 | 9582.8 | 9732.4 | 9603 | 8305.1 | 9517.7 | 8464.8 | 9565.4 | 9558.5 | 11179.9 | 9563.8 | 11186.1 | 9766.6 | 11014.9 | 9608.9 | 9783.8 | 9310.6 | 10758.3 | 11176.8 | 10977.5 | 10932.9 | 11042.5 | 11077.2 | 9899.6 | 11031.6 | 10954 | 11155.5 | 11183 | 11168.3 | 11206.6 | 9962.5 | 10790.2 | 9978.7 | 20.222 | 20.0049 | 19.9303 | 0 | 20.546 | 20.2028 | 0 | 33.5161 | 0 | 0 | 0 | 0 | 3.0319 | 2.9423 | 2.997 | 3.0196 | 2.9539 | 2.7804 | 7.186 | 6.772 | 6.732 | 6.42 | 6.838 | 6.331 | 4.0641 | 4.5237 | 4.1381 | 4.0893 | 4.6008 | 5.0418 | 0.93597 | 1.0907 | 1.1433 | 0 | 1.1453 | 0.95506 | 5.358 | 5.3985 | 5.1392 | 4.9382 | 5.3964 | 5.2923 | 0.93779 | 1.041 | 1.0515 | 0 | 1.1331 | 1.1901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 215749 | 392 | 205697 | 402 | 398112.964 | 1043.667 | 4.0641 | 4.5237 | 4.1381 | 4.0893 | 4.6008 | 5.0418 | 5.358 | 5.3985 | 5.1392 | 4.9382 | 5.3964 | 5.2923 | 812000 | 2000 | 808000 | 2000 | 1613200 | 4867 | 1616000 | 1608333 | 10.7833 | 4.4096 | 1.0541 | 5.2538 | 1.0707 | 23.9% | 20.38% | 20.1812 | 33.5161 | 2.9542 | 6.7132 | 1629554.6 | 1613000 | 1721132.9749 | 93.72%
2023-01-13 | 2023 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 334767.775 | 7:35 | 18:14 | 10029.4 | 10467 | 10432.9 | 10366.7 | 10449 | 10541.9 | 10482.9 | 10743.3 | 10400.4 | 10259.4 | 10328.5 | 10451.2 | 10437.4 | 10392.3 | 10456.9 | 10499 | 10423.8 | 10489.3 | 10457.9 | 10449.7 | 10375.1 | 10451.8 | 10399.6 | 10437.3 | 10374.6 | 9306 | 10395.6 | 10398 | 10595.4 | 10527 | 10371.8 | 10246.2 | 10466.9 | 10058.9 | 10567.6 | 10585.4 | 10672.9 | 10641.2 | 10598.1 | 10556.9 | 11193.9 | 10382.5 | 11098.1 | 10057.6 | 10667.2 | 11563.3 | 10198.5 | 11156.1 | 9834.8 | 10043.5 | 10535.3 | 10029.3 | 10776.9 | 9875.5 | 10750.5 | 9866.2 | 9858.9 | 10458.5 | 9783.1 | 10739 | 10684.8 | 9618.9 | 10499.6 | 10084 | 10300.2 | 9746.2 | 10303.6 | 10589.7 | 10811 | 9991.8 | 10669.2 | 9689.9 | 9445.5 | 10675.8 | 9764.5 | 10650.5 | 9516.8 | 10640 | 9714.4 | 10586.7 | 10008.1 | 10647.1 | 10138.4 | 10828.5 | 10026.9 | 10193.7 | 9965.3 | 8881.9 | 10490.9 | 10388 | 9839.4 | 10911.3 | 10684.3 | 10056.5 | 9957.7 | 10783.5 | 9870.5 | 10215.3 | 10836.5 | 9795.6 | 10953.5 | 9824.2 | 10758.7 | 10085.3 | 10837.3 | 9619.7 | 10910.2 | 10129.9 | 10845.5 | 10114.6 | 10894.9 | 10258.1 | 9907.2 | 10698.5 | 9882.3 | 9843.1 | 10779.8 | 10662.4 | 10746.1 | 10059.6 | 10841.8 | 9888.3 | 10581 | 10171.3 | 10571.3 | 9416.5 | 10682.5 | 9977.2 | 10007.6 | 10105.1 | 10036.7 | 8708.9 | 9952.6 | 8895.7 | 9856.9 | 9897.5 | 10927.8 | 9848.3 | 10959.6 | 10019.2 | 10871.2 | 9919.8 | 10061.8 | 9652.1 | 10726.8 | 10947.2 | 10870.1 | 10817.7 | 10865.8 | 10886.6 | 10146.9 | 10889.6 | 10827.4 | 10922.2 | 10944.5 | 10939.1 | 10976.2 | 10187.7 | 10803.8 | 10197.6 | 16.3758 | 16.2707 | 16.3345 | 0 | 16.5736 | 16.0753 | 0 | 28.3868 | 0 | 0 | 0 | 0 | 2.7903 | 2.832 | 2.8583 | 2.6969 | 2.7725 | 2.4617 | 6.566 | 6.368 | 5.759 | 6.227 | 6.081 | 6.205 | 4.2375 | 4.6882 | 4.322 | 4.1956 | 4.7196 | 5.126 | 0.93526 | 1.1526 | 1.1583 | 0 | 1.1857 | 1.0226 | 5.5529 | 5.6074 | 5.3457 | 4.9483 | 5.6379 | 5.3801 | 0.92846 | 1.1094 | 1.0608 | 0 | 1.1808 | 1.2722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216574 | 394 | 206518 | 404 | 399751.031 | 1048.533 | 4.2375 | 4.6882 | 4.322 | 4.1956 | 4.7196 | 5.126 | 5.5529 | 5.6074 | 5.3457 | 4.9483 | 5.6379 | 5.3801 | 825000 | 2000 | 821000 | 2000 | 1638067 | 4866 | 1642000 | 1633201 | 10.65 | 4.5482 | 1.0909 | 5.412 | 1.1103 | 23.99% | 20.52% | 16.326 | 28.3868 | 2.7353 | 6.201 | 1655567.2 | 1638000 | 1794458.5937 | 91.28%
2023-01-14 | 2023 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 334767.775 | 7:24 | 18:10 | 11173.6 | 11538.7 | 11489.5 | 11481.9 | 11509.3 | 11595.2 | 11535.2 | 11791.5 | 11511.2 | 11416.2 | 11393.5 | 11533.4 | 11509.4 | 11489.5 | 11517.6 | 11583.8 | 11449.6 | 11539.3 | 11527.4 | 11538.1 | 11417.6 | 11526 | 11376.9 | 11448.6 | 11383 | 10330.1 | 11481.2 | 11407.4 | 11592.5 | 11449.6 | 11341.9 | 11473.1 | 11572.8 | 11578.8 | 11556.8 | 11543 | 11639.9 | 11599.7 | 11532.6 | 11499.1 | 12103.2 | 11259.6 | 11956.2 | 10945.3 | 11536.6 | 12483.5 | 11075.6 | 12047.3 | 10948.8 | 11175.2 | 11622.9 | 11144.7 | 11868.9 | 10944.1 | 11841.6 | 10963.1 | 10988.6 | 11570.9 | 10928.3 | 11897.6 | 11843 | 10773.9 | 11674 | 11256.4 | 11396.9 | 10845.2 | 11422.8 | 11728.6 | 11939.3 | 11105.2 | 11825.5 | 10831.9 | 10545.9 | 11876.6 | 10880.9 | 11823.5 | 10710.8 | 11828.4 | 10871.1 | 11745.1 | 11151.3 | 11780.4 | 11244.8 | 12025.3 | 11143.9 | 11304.6 | 11001.1 | 9917.3 | 11719.2 | 11435.1 | 10921.6 | 11989 | 11722.2 | 11089.6 | 10964.1 | 11763 | 10890.6 | 11227.8 | 11820.8 | 10786.4 | 11934 | 10825.6 | 11750.3 | 11094.5 | 11762.2 | 10598.7 | 11859.5 | 11070.8 | 11818.4 | 11058 | 11799.7 | 11220.4 | 10906.1 | 11695.8 | 10943.8 | 10844.9 | 11742.3 | 11597.7 | 11676.3 | 10996.3 | 11779.8 | 10845 | 11489.6 | 11136.8 | 11500.8 | 10342.5 | 11636.8 | 10932.6 | 10965.8 | 11047.4 | 10962.8 | 9546.9 | 10882.7 | 9801.8 | 10895.3 | 10903.6 | 12014.1 | 10893.6 | 12016.6 | 11087.1 | 11907.5 | 10925.1 | 11070.5 | 10905 | 11814.1 | 12034.2 | 11970.8 | 11911.2 | 11990.9 | 12008.1 | 11201.9 | 11960.3 | 11941.3 | 12007.9 | 12060.5 | 12068.4 | 12089.5 | 11277.4 | 11959.1 | 11281.1 | 15.5983 | 15.1418 | 15.2549 | 0 | 15.0393 | 14.8571 | 0 | 27.6455 | 0 | 0 | 0 | 0 | 3.5858 | 3.6314 | 3.4664 | 3.633 | 3.487 | 3.4552 | 6.955 | 6.547 | 6.561 | 6.837 | 6.35 | 6.326 | 4.5844 | 5.0509 | 4.6606 | 4.5613 | 5.1311 | 5.6898 | 1.062 | 1.2263 | 1.2895 | 0 | 1.2869 | 1.0911 | 6.1229 | 6.1075 | 5.8358 | 5.5274 | 6.1477 | 5.9236 | 1.0492 | 1.1743 | 1.1666 | 0 | 1.2818 | 1.3573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 217485 | 395 | 207420 | 405 | 401554.765 | 1053.4 | 4.5844 | 5.0509 | 4.6606 | 4.5613 | 5.1311 | 5.6898 | 6.1229 | 6.1075 | 5.8358 | 5.5274 | 6.1477 | 5.9236 | 911000 | 1000 | 902000 | 1000 | 1803734 | 4867 | 1811000 | 1798867 | 10.7667 | 4.9464 | 1.1912 | 5.9441 | 1.2058 | 24.08% | 20.29% | 15.1783 | 27.6455 | 3.5431 | 6.596 | 1823261.3 | 1803667 | 1984330.7753 | 90.9%
2023-01-15 | 2023 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 334767.775 | 7:26 | 18:14 | 11339.7 | 11716.6 | 11617.6 | 11597 | 11632.7 | 11746.9 | 11700.4 | 11937.1 | 11657.1 | 11580 | 11534.5 | 11682.8 | 11648.2 | 11618 | 11552 | 11717.8 | 11592.9 | 11669.7 | 11676.3 | 11689.7 | 11576.3 | 11666.8 | 11509.2 | 11593.1 | 11525.9 | 10466.5 | 11630.7 | 11525.2 | 11725 | 11598.4 | 11489.9 | 11630.4 | 11720.2 | 11732.5 | 11700 | 11701.2 | 11791.3 | 11746.4 | 11694.1 | 11639.8 | 12262.2 | 11383.1 | 12134.9 | 11078.2 | 11674.8 | 12649 | 11235.8 | 12225.3 | 11070.8 | 11288.2 | 11750.6 | 11266.3 | 11995.6 | 11069 | 11996.5 | 11090.6 | 11121.3 | 11511.8 | 11056.7 | 12036.4 | 11988.5 | 10900.4 | 11816.9 | 11385.7 | 11553 | 11010.5 | 11559.4 | 11884.6 | 12095.8 | 11261.1 | 11960 | 10969.6 | 10685.6 | 12021.2 | 11034.4 | 11972 | 10856.2 | 11984.5 | 11002.1 | 11893.1 | 11298.4 | 11933.6 | 11287 | 12181.7 | 11278.6 | 11441.7 | 11172.9 | 10052.1 | 11872.3 | 11602.9 | 11078.5 | 12158.6 | 11890 | 11255.2 | 11130.5 | 11928.2 | 11040.9 | 11346.9 | 11978.6 | 10926 | 12071.9 | 10974.3 | 11886.1 | 11232.5 | 11940.4 | 10750.8 | 12025.1 | 11223.7 | 11973.3 | 11216.3 | 11990.9 | 11364.6 | 11042.5 | 11837.8 | 11064.6 | 10979.1 | 11873.4 | 11748.1 | 11841.5 | 11129.3 | 11923.1 | 10984.3 | 11655.7 | 11276.6 | 11672.4 | 10476.8 | 11774.4 | 11078.9 | 11105.2 | 11208.2 | 11142.3 | 9704.4 | 11020.8 | 9896.2 | 11050.4 | 11068.3 | 12197.1 | 11073.3 | 12196.2 | 11244.7 | 12072.6 | 11086 | 11219.5 | 11057.5 | 11979.9 | 12217.8 | 12123.7 | 12072.8 | 12160.2 | 12167.9 | 11350.3 | 12125.6 | 12113.3 | 12214 | 12239.5 | 12226.9 | 12259.4 | 11435.7 | 12173.9 | 11443.2 | 15.7138 | 15.0578 | 14.7594 | 0 | 14.9946 | 14.7314 | 0 | 30.2144 | 0 | 0 | 0 | 0 | 2.3934 | 2.4737 | 2.3105 | 2.4043 | 2.3892 | 2.3557 | 5.13 | 4.717 | 4.691 | 5.033 | 4.705 | 5.265 | 4.6729 | 5.1498 | 4.7641 | 4.6488 | 5.2409 | 5.823 | 1.0843 | 1.2444 | 1.322 | 0 | 1.3016 | 1.0967 | 6.2634 | 6.2436 | 5.9841 | 5.6626 | 6.2703 | 6.0618 | 1.0686 | 1.1879 | 1.1913 | 0 | 1.2908 | 1.3656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218406 | 397 | 208335 | 407 | 403382.432 | 1058.133 | 4.6729 | 5.1498 | 4.7641 | 4.6488 | 5.2409 | 5.823 | 6.2634 | 6.2436 | 5.9841 | 5.6626 | 6.2703 | 6.0618 | 921000 | 2000 | 915000 | 2000 | 1827667 | 4733 | 1832000 | 1822934 | 10.8 | 5.0499 | 1.2098 | 6.081 | 1.2208 | 23.96% | 20.08% | 15.0514 | 30.2144 | 2.3878 | 4.9235 | 1846811.4 | 1827600 | 2018395.78 | 90.55%
2023-01-16 | 2023 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 334767.775 | 7:24 | 18:13 | 11224 | 11600.8 | 11478.4 | 11461.1 | 11487.4 | 11615.6 | 11566.7 | 11855.8 | 11559.4 | 11508.1 | 11427.9 | 11574.4 | 11533.3 | 11505.7 | 11438.1 | 11593.2 | 11470.5 | 11550.3 | 11558.9 | 11572.7 | 11458.6 | 11546.5 | 11391.8 | 11475.5 | 11403.5 | 10309.8 | 11510.8 | 11399.5 | 11599.8 | 11467 | 11359.2 | 11496.9 | 11605.7 | 11610.2 | 11579 | 11582.2 | 11675.1 | 11625.2 | 11570.7 | 11522.4 | 12165.2 | 11278.9 | 12041.3 | 10956.7 | 11583.6 | 12570.1 | 11110.3 | 12122.3 | 10932.8 | 11158.9 | 11637.4 | 11142.1 | 11879.9 | 10945.4 | 11886.2 | 10956.5 | 10974.3 | 11372.3 | 10912.4 | 11922.5 | 11871.8 | 10751 | 11678.3 | 11245.2 | 11418.5 | 10870.8 | 11430.8 | 11780.4 | 11979.4 | 11136.2 | 11846.4 | 10823.2 | 10524.8 | 11913.2 | 10891.7 | 11860.3 | 10702.4 | 11870.4 | 10855.4 | 11780.8 | 11186.4 | 11835.6 | 11175.2 | 12083 | 11177.7 | 11339.7 | 11051.5 | 9919.5 | 11779.3 | 11490.5 | 10951 | 12062.6 | 11774.8 | 11119.4 | 10984.6 | 11809.4 | 10893 | 11224.4 | 11867.3 | 10785.8 | 11951.3 | 10828.5 | 11776.1 | 11093.4 | 11837.2 | 10595.9 | 11919 | 11107.4 | 11857 | 11089.2 | 11878.6 | 11241.8 | 10919.3 | 11746 | 10992.3 | 10867.3 | 11774.7 | 11656.8 | 11739.7 | 11025 | 11826.7 | 10862.5 | 11598.3 | 11155.8 | 11558.4 | 10342.6 | 11672.1 | 10960.9 | 11007.7 | 11127.2 | 11016.8 | 9592.4 | 10891.4 | 9748.9 | 10962.6 | 10960.6 | 12093.4 | 10940.7 | 12098 | 11173.8 | 11974.5 | 10971.2 | 11108.3 | 10927.2 | 11881 | 12124.5 | 12036.2 | 11975.7 | 12061 | 12071.7 | 11238.1 | 12029.7 | 12000.5 | 12108.3 | 12141.4 | 12125.4 | 12165.4 | 11323.3 | 12061.8 | 11332.4 | 17.7924 | 17.1134 | 17.0102 | 0 | 16.9131 | 16.7461 | 0 | 30.7627 | 0 | 0 | 0 | 0 | 3.0671 | 3.0464 | 3.0094 | 3.1119 | 3.0772 | 3.0072 | 5.892 | 5.73 | 5.474 | 5.735 | 6.043 | 5.517 | 4.7277 | 5.1127 | 4.7708 | 4.6605 | 5.2838 | 5.8553 | 1.0723 | 1.2337 | 1.3029 | 0 | 1.2888 | 1.0944 | 6.2197 | 6.2156 | 6.0585 | 5.7307 | 6.3194 | 6.1354 | 1.0584 | 1.1798 | 1.1787 | 0 | 1.2818 | 1.3624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219318 | 398 | 209242 | 409 | 405192.565 | 1062.933 | 4.7277 | 5.1127 | 4.7708 | 4.6605 | 5.2838 | 5.8553 | 6.2197 | 6.2156 | 6.0585 | 5.7307 | 6.3194 | 6.1354 | 912000 | 1000 | 907000 | 2000 | 1810133 | 4800 | 1816000 | 1805333 | 10.8167 | 5.0684 | 1.1984 | 6.1132 | 1.2122 | 23.65% | 19.83% | 17.1151 | 30.7627 | 3.0532 | 5.7318 | 1828207.4 | 1810000 | 2016598.664 | 89.76%
2023-01-17 | 2023 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 334767.775 | 7:33 | 18:20 | 10962.6 | 11344.3 | 11236.5 | 11220.7 | 11227.1 | 11383.6 | 11315.4 | 11648.1 | 11334.6 | 11256.3 | 11198.5 | 11342.4 | 11304.3 | 11281 | 11205.9 | 11373.2 | 11250.3 | 11333.7 | 11339.1 | 11357.4 | 11222.4 | 11326.1 | 11171.5 | 11248.7 | 11179.9 | 10004.8 | 11277.3 | 11155 | 11377.4 | 11232.3 | 11138.3 | 11303 | 11382.9 | 11397.6 | 11356.7 | 11354.2 | 11462.1 | 11404.6 | 11352.8 | 11300.2 | 11984.8 | 11040.3 | 11844.1 | 10658.5 | 11335.1 | 12373.6 | 10862 | 11938.1 | 10636.6 | 10888.2 | 11413.5 | 10871.5 | 11672.4 | 10664 | 11678.8 | 10664 | 10676.1 | 11118.6 | 10604 | 11712.7 | 11653.4 | 10433.3 | 11429.9 | 10958.7 | 11177.2 | 10595.6 | 11196.2 | 11576.7 | 11784.6 | 10879.2 | 11658.4 | 10520.5 | 10207.8 | 11719.1 | 10596.7 | 11661.5 | 10392.4 | 11665.9 | 10546.2 | 11570.4 | 10922.5 | 11632 | 10898.8 | 11885.1 | 10916.9 | 11089.5 | 10780.1 | 9618 | 11590.7 | 11259 | 10654.6 | 11862.4 | 11550 | 10824.9 | 10681 | 11608.9 | 10563 | 10965.4 | 11659.3 | 10473.1 | 11751.7 | 10521.2 | 11569.9 | 10801.2 | 11632.9 | 10283.8 | 11711.6 | 10828.7 | 11642.9 | 10800.1 | 11654.5 | 10953.9 | 10619.5 | 11539 | 10704.7 | 10554.5 | 11568.8 | 11436.1 | 11520.6 | 10750.8 | 11623 | 10543.8 | 11365.7 | 10866.7 | 11313.1 | 10022.5 | 11451.4 | 10655.4 | 10716.7 | 10857.4 | 10731.9 | 9302 | 10633.7 | 9457.4 | 10683.7 | 10687.4 | 11923.8 | 10690.3 | 11925.2 | 10939.1 | 11798.6 | 10731.6 | 10881.1 | 10667.3 | 11698.1 | 11961.5 | 11866.3 | 11804.8 | 11899.7 | 11915.8 | 11018.8 | 11862.7 | 11819.2 | 11932.5 | 11954.2 | 11948.5 | 11997.1 | 11099.8 | 11876.8 | 11107.7 | 18.7402 | 17.8483 | 17.7273 | 0 | 17.7076 | 17.4246 | 0 | 31.762 | 0 | 0 | 0 | 0 | 2.6358 | 2.6684 | 2.6118 | 2.6555 | 2.6114 | 2.4788 | 4.777 | 5.1 | 5.066 | 5.248 | 5.084 | 4.705 | 4.6021 | 4.9775 | 4.6497 | 4.5479 | 5.1429 | 5.6881 | 1.0395 | 1.1944 | 1.2631 | 0 | 1.2512 | 1.0699 | 6.028 | 6.0246 | 5.8777 | 5.5611 | 6.1325 | 5.9712 | 1.0273 | 1.1433 | 1.1456 | 0 | 1.2465 | 1.3317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220211 | 400 | 210128 | 411 | 406963.965 | 1067.8 | 4.6021 | 4.9775 | 4.6497 | 4.5479 | 5.1429 | 5.6881 | 6.028 | 6.0246 | 5.8777 | 5.5611 | 6.1325 | 5.9712 | 893000 | 2000 | 886000 | 2000 | 1771400 | 4867 | 1775000 | 1766533 | 10.7833 | 4.9347 | 1.1636 | 5.9325 | 1.1789 | 23.58% | 19.87% | 17.8896 | 31.762 | 2.6103 | 4.9967 | 1789937.3 | 1771333 | 1951222.0638 | 90.78%
2023-01-18 | 2023 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 334767.775 | 7:26 | 18:17 | 10850.2 | 11233.9 | 11110.6 | 11118.5 | 11093.9 | 11266.9 | 11181.8 | 11510.2 | 11227.3 | 11122.6 | 11088.7 | 11235.4 | 11200.1 | 11166 | 11079.5 | 11271.5 | 11142 | 11229.3 | 11234.4 | 11253.2 | 11122.1 | 11224.7 | 11067.5 | 11152.6 | 11069.7 | 9876.2 | 11171 | 11040.5 | 11260.5 | 11115.2 | 11034.4 | 11200 | 11266.3 | 11299.1 | 11253.3 | 11245.1 | 11348.4 | 11293.1 | 11247.8 | 11186.2 | 11879 | 10909.9 | 11744.8 | 10511.9 | 11199 | 12261.2 | 10771.4 | 11853.9 | 10502.5 | 10765.1 | 11307.4 | 10745.4 | 11561.9 | 10523.2 | 11573.6 | 10534.5 | 10536.7 | 10988.9 | 10480 | 11613.1 | 11560.7 | 10311.1 | 11291.1 | 10808.9 | 11052.2 | 10461.2 | 11072.2 | 11456.7 | 11680 | 10762.9 | 11542.7 | 10381.1 | 10074.9 | 11614.1 | 10464.1 | 11558.3 | 10261.9 | 11557.8 | 10395.8 | 11461.2 | 10785.2 | 11512 | 10627.8 | 11765.5 | 10775.6 | 10948.5 | 10670.6 | 9482.9 | 11452.2 | 11139 | 10500 | 11735.5 | 11425.6 | 10691.5 | 10545.5 | 11508.9 | 10419.6 | 10835.5 | 11542.1 | 10330.7 | 11631.5 | 10384.3 | 11433.1 | 10655.3 | 11517.7 | 10126.9 | 11588.3 | 10693.6 | 11503.4 | 10655 | 11526.6 | 10816.4 | 10470.1 | 11413.8 | 10554.2 | 10403.3 | 11443.2 | 11295.3 | 11400.3 | 10595.2 | 11485.7 | 10376.2 | 11251.9 | 10728.4 | 11201.4 | 9865.7 | 11308.2 | 10483.8 | 10558.3 | 10710.5 | 10587.9 | 9160.2 | 10434.5 | 9270.8 | 10486.3 | 10503.6 | 11782.4 | 10509.9 | 11780.5 | 10766.8 | 11644.5 | 10563.8 | 10718.8 | 10495.8 | 11531.7 | 11806.1 | 11700.2 | 11650.3 | 11741.8 | 11757.7 | 10844.6 | 11702.7 | 11656.5 | 11783.5 | 11806.1 | 11788.2 | 11835.7 | 10921.2 | 11713.5 | 10931.6 | 20.1418 | 19.5494 | 19.3346 | 0 | 19.2666 | 19.0446 | 0 | 32.0251 | 0 | 0 | 0 | 0 | 3.5215 | 3.54 | 3.4653 | 3.5467 | 3.4767 | 3.3102 | 6.606 | 6.083 | 6.856 | 6.231 | 6.553 | 6.14 | 4.5449 | 4.9112 | 4.5981 | 4.4868 | 5.041 | 5.5672 | 1.0283 | 1.1758 | 1.2484 | 0 | 1.2153 | 1.0334 | 5.928 | 5.9207 | 5.7873 | 5.4902 | 5.9563 | 5.8576 | 1.0166 | 1.1266 | 1.1322 | 0 | 1.2095 | 1.2892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221096 | 402 | 211005 | 413 | 408716.899 | 1072.8 | 4.5449 | 4.9112 | 4.5981 | 4.4868 | 5.041 | 5.5672 | 5.928 | 5.9207 | 5.7873 | 5.4902 | 5.9563 | 5.8576 | 885000 | 2000 | 877000 | 2000 | 1752934 | 5000 | 1758000 | 1747934 | 10.85 | 4.8582 | 1.1402 | 5.8234 | 1.1548 | 23.47% | 19.83% | 19.4674 | 32.0251 | 3.4767 | 6.4115 | 1768771 | 1752800 | 1914615.7941 | 91.55%
2023-01-19 | 2023 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 334767.775 | 7:29 | 18:21 | 8572.2 | 8953.8 | 8867.9 | 8866.4 | 8857.2 | 9002.4 | 8902.1 | 9237.5 | 8977.3 | 8845.3 | 8842.7 | 8980.5 | 8920.2 | 8920.7 | 8843 | 9000.6 | 8907.1 | 8977.1 | 8970.2 | 8975 | 8879.6 | 8971.6 | 8837.7 | 8902.5 | 8833.5 | 7842.3 | 8910.2 | 8774.4 | 9010.8 | 8874.4 | 8806.2 | 8984 | 9027.7 | 9062.1 | 9027.4 | 9011.6 | 9112.2 | 9050.5 | 9019.5 | 8974.2 | 9734.3 | 8754.3 | 9624.3 | 8400.7 | 9098 | 10118.9 | 8619 | 9697.5 | 8328.6 | 8525.4 | 9064.2 | 8513.5 | 9310.8 | 8312.9 | 9328.8 | 8376.4 | 8325.9 | 8090.7 | 8305.5 | 9327.4 | 9267.1 | 8160.2 | 8987.8 | 8496 | 8773 | 8261.8 | 8780.3 | 9182.5 | 9425.7 | 8494.6 | 9252.8 | 8182.2 | 7980.9 | 9312.1 | 8267 | 9266 | 8085.1 | 9298.8 | 8214.5 | 9186.1 | 8530.1 | 9246.2 | 8276.9 | 9500.6 | 8537.9 | 8697.9 | 8468.8 | 7531.7 | 9198.8 | 8926.7 | 8276.2 | 9472.6 | 9184.9 | 8488.2 | 8404.2 | 9240.9 | 8288.7 | 8595.7 | 9350.8 | 8192.5 | 9400.4 | 8216.1 | 9175 | 8432.2 | 9302.4 | 8024 | 9353 | 8460 | 9243.8 | 8429.2 | 9275.1 | 8556.8 | 8308.7 | 9202.5 | 8364.6 | 8248.4 | 9249.3 | 9119.7 | 9197.1 | 8474.2 | 9322 | 8260.9 | 9034.6 | 8488.6 | 8951.4 | 7862.1 | 9121.9 | 8365.6 | 8438 | 8557.3 | 8423.7 | 7324.8 | 8268.2 | 7309.8 | 8242.5 | 8235.1 | 9430.8 | 8203.1 | 9450.6 | 8427.9 | 9318.1 | 8249.5 | 8384.2 | 8212.1 | 9129.9 | 9421.1 | 9335.3 | 9308.1 | 9368.1 | 9394.2 | 8482.7 | 9334.9 | 9279.3 | 9393.5 | 9420.3 | 9395.9 | 9431.9 | 8509.2 | 9317.1 | 8525 | 20.8168 | 20.291 | 19.9935 | 0 | 20.0855 | 19.9689 | 0 | 30.8767 | 0 | 0 | 0 | 0 | 3.3571 | 3.2756 | 3.2686 | 3.2221 | 3.0902 | 3.2516 | 6.717 | 6.21 | 6.816 | 6.3 | 6.276 | 5.956 | 3.8126 | 4.0707 | 3.9531 | 3.7666 | 4.1584 | 4.2628 | 0.87486 | 0.93276 | 1.0694 | 0 | 0.96353 | 0.82311 | 4.6528 | 4.6104 | 4.6686 | 4.4628 | 4.6316 | 4.6285 | 0.89644 | 0.90165 | 1.0018 | 0 | 0.967 | 1.0252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221802 | 404 | 211702 | 415 | 410115.099 | 1077.733 | 3.8126 | 4.0707 | 3.9531 | 3.7666 | 4.1584 | 4.2628 | 4.6528 | 4.6104 | 4.6686 | 4.4628 | 4.6316 | 4.6285 | 706000 | 2000 | 697000 | 2000 | 1398200 | 4933 | 1399000 | 1393267 | 10.8667 | 4.004 | 0.93273 | 4.6091 | 0.95842 | 23.29% | 20.79% | 20.2311 | 30.8767 | 3.2442 | 6.3792 | 1410435.3 | 1398133 | 1524881.2839 | 91.69%
2023-01-20 | 2023 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 334767.775 | 7:28 | 18:21 | 9459 | 9919.2 | 9831 | 9793.2 | 9810.5 | 9957.4 | 9887.5 | 10327.1 | 9918.7 | 9843 | 9752.7 | 9926.2 | 9852.2 | 9854.1 | 9730.1 | 9929.6 | 9816.6 | 9903.4 | 9932.4 | 9935 | 9809.4 | 9926.5 | 9746.4 | 9836.6 | 9733.2 | 8581.9 | 9829.4 | 9685.9 | 10003.8 | 9869.9 | 9705.7 | 9920.6 | 9963.3 | 10006.6 | 9946.9 | 9937.2 | 10068.7 | 9995.6 | 9964.2 | 9890.6 | 10899.3 | 9654.1 | 10726.9 | 9241 | 10078.2 | 11485.6 | 9435.1 | 10788.4 | 9141.3 | 9382.8 | 10009.4 | 9366 | 10354.6 | 9154.8 | 10364.3 | 9186 | 9153.7 | 8897.8 | 9135 | 10388.9 | 10341.9 | 8990.2 | 9965.7 | 9390.5 | 9669.1 | 9074.3 | 9692.2 | 10176.4 | 10500.4 | 9349.1 | 10297.5 | 8996.5 | 8754.3 | 10359.3 | 9076 | 10300 | 8879.6 | 10346 | 9029.7 | 10219 | 9355.6 | 10251.3 | 9047.8 | 10576.2 | 9349.6 | 9544.9 | 9301 | 8233 | 10204 | 9821.8 | 9116.6 | 10577.9 | 10194.4 | 9328.5 | 9218.7 | 10280.2 | 9063.9 | 9412.3 | 10330.2 | 8961.3 | 10457.1 | 8994.3 | 10134.6 | 9250.5 | 10312.7 | 8777.5 | 10355.6 | 9253.1 | 10233.5 | 9249.3 | 10280.6 | 9373.1 | 9093.9 | 10125.4 | 9167.1 | 8997.6 | 10187.3 | 10005.7 | 10116.2 | 9196 | 10260.6 | 9002.9 | 9941.2 | 9305.5 | 9843.1 | 8580.7 | 10004.1 | 9102.7 | 9124.5 | 9279.6 | 9162 | 7925.4 | 9058.8 | 8067.6 | 9038.2 | 9042.1 | 10539.5 | 9032.2 | 10536.2 | 9251.2 | 10393.6 | 9072.2 | 9233 | 9017.9 | 10171.4 | 10564.4 | 10131.7 | 10368.6 | 10457.1 | 10500.3 | 9330.3 | 10409.3 | 10402.3 | 10548.6 | 10587.8 | 10553.8 | 10582.4 | 9411.5 | 10415.5 | 9434.7 | 22.0689 | 21.8352 | 21.6487 | 0 | 22.006 | 21.5985 | 0 | 36.076 | 0 | 0 | 0 | 0 | 2.0759 | 2.0977 | 2.0581 | 2.1335 | 2.0536 | 2.0691 | 5.0083 | 4.9033 | 4.5333 | 5.6583 | 4.88 | 5.2117 | 4.0203 | 4.4407 | 4.08 | 4.0281 | 4.5313 | 5.003 | 0.93688 | 1.1095 | 1.142 | 0 | 1.1446 | 0.94254 | 5.2662 | 5.3778 | 5.1414 | 4.8697 | 5.4145 | 5.2134 | 0.93329 | 1.0636 | 1.0445 | 1.1548 | 1.1326 | 1.173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222583 | 405 | 212472 | 416 | 411658.765 | 1082.6 | 4.0203 | 4.4407 | 4.08 | 4.0281 | 4.5313 | 5.003 | 5.2662 | 5.3778 | 5.1414 | 4.8697 | 5.4145 | 5.2134 | 781000 | 1000 | 770000 | 1000 | 1543666 | 4867 | 1549000 | 1538799 | 10.8833 | 4.3506 | 1.0551 | 5.2138 | 1.0836 | 24.25% | 20.78% | 21.8315 | 36.076 | 2.0813 | 5.0325 | 1557467 | 1543400 | 1677366.4343 | 92.01%
2023-01-21 | 2023 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 334767.775 | 7:29 | 18:16 | 8858 | 9282 | 9206.4 | 9176.9 | 9191 | 9339.3 | 9237.9 | 9640.5 | 9295.4 | 9200.9 | 9154.1 | 9335.1 | 9251 | 9263 | 9138.8 | 9328.9 | 9211.8 | 9296.7 | 9309.8 | 9300.1 | 9238.4 | 9335.1 | 9194 | 9258.6 | 9156.2 | 8062.5 | 9210 | 9083.5 | 9418.4 | 9307.6 | 9175.3 | 9368.4 | 9406.3 | 9419.3 | 9351.4 | 9357.8 | 9494.4 | 9428.4 | 9396.3 | 9338.5 | 10198 | 9044.7 | 10045.4 | 8656.9 | 9491.6 | 10864.9 | 8849.3 | 10110.5 | 8570 | 8798 | 9387.7 | 8802 | 9714.8 | 8563.8 | 9725.9 | 8625.2 | 8596.4 | 9169.5 | 8580.3 | 9763.1 | 9711.3 | 8436 | 9327.2 | 8783.7 | 9097.6 | 8565.5 | 9128.6 | 9607 | 9886.8 | 8826.7 | 9701.8 | 8490.6 | 8260.1 | 9774.3 | 8554.2 | 9724.7 | 8363.6 | 9754.8 | 8498.3 | 9632.5 | 8807.5 | 9657.2 | 8121.7 | 9975.2 | 8830.5 | 9065 | 8766.8 | 7770.2 | 9662.9 | 9295.4 | 8643.7 | 10024.9 | 9625.8 | 8796.4 | 8692.1 | 9752.7 | 8572.3 | 8916.8 | 9782.5 | 8494.3 | 9900.7 | 8507.8 | 9583.8 | 8751.6 | 9746.9 | 8295.3 | 9779.3 | 8737 | 9663.2 | 8731.6 | 9710.7 | 8859.3 | 8628 | 9596.2 | 8669.9 | 8523.5 | 9657 | 9499.5 | 9587 | 8749.4 | 9763.1 | 8580 | 9415.5 | 8811.9 | 9331.4 | 8192.3 | 9550.9 | 8697.2 | 8672 | 8816.1 | 8748.6 | 7544.1 | 8632.5 | 7721.7 | 8685.2 | 8690.6 | 10111.7 | 8677.7 | 10112.6 | 8885.6 | 10015.6 | 8761.6 | 8911.8 | 8670 | 9728.8 | 10109.2 | 9702.1 | 9938.5 | 9952.8 | 10059.7 | 8952.4 | 9976.4 | 10022.2 | 10105.9 | 10158.7 | 10120.1 | 10117.9 | 8998.4 | 9989.7 | 9040.1 | 16.4944 | 16.4172 | 16.2199 | 0 | 16.3103 | 16.3967 | 0 | 25.1739 | 0 | 0 | 0 | 0 | 3.7722 | 3.8216 | 3.855 | 3.8822 | 3.7245 | 3.6027 | 6.464 | 6.628 | 7.118 | 6.933 | 6.754 | 6.095 | 3.8474 | 4.1461 | 3.924 | 3.824 | 4.2502 | 4.4918 | 0.8783 | 1.0321 | 1.0684 | 0 | 1.0758 | 0.91891 | 4.7657 | 4.7735 | 4.6963 | 4.4755 | 4.8591 | 4.8142 | 0.88792 | 1.0005 | 0.99192 | 0 | 1.0709 | 1.1404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223318 | 407 | 213204 | 418 | 413118.566 | 1087.667 | 3.8474 | 4.1461 | 3.924 | 3.824 | 4.2502 | 4.4918 | 4.7657 | 4.7735 | 4.6963 | 4.4755 | 4.8591 | 4.8142 | 735000 | 2000 | 732000 | 2000 | 1459801 | 5067 | 1463000 | 1454734 | 10.7833 | 4.0806 | 0.9947 | 4.7307 | 1.0183 | 24.38% | 21.53% | 16.3677 | 25.1739 | 3.7764 | 6.6653 | 1473105.5 | 1459667 | 1592546.8453 | 91.66%
2023-01-22 | 2023 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 334767.775 | 7:26 | 17:49 | 917 | 960.3 | 951.7 | 933.1 | 950.9 | 973.8 | 964.5 | 1002.2 | 896 | 896.1 | 892.1 | 907.8 | 899.9 | 900.1 | 877 | 895.3 | 1330.5 | 1336.9 | 1330.6 | 1331.7 | 1298.5 | 1314.5 | 1274.9 | 1294.1 | 1518.4 | 1340.7 | 1532.4 | 1511.1 | 1558.3 | 1536 | 1448.8 | 734.3 | 1661.8 | 1663.3 | 1657.9 | 1659.4 | 1682.6 | 1669.5 | 1661.3 | 1649 | 1813.9 | 1610.1 | 1788.3 | 1538.8 | 1690.5 | 1934.9 | 1574 | 1795.7 | 836.6 | 861 | 914 | 857.3 | 948.6 | 836.6 | 948.8 | 841.1 | 836.7 | 894.3 | 833.9 | 950.2 | 944.5 | 821.3 | 914.6 | 863 | 811.2 | 770.7 | 822.7 | 871 | 896.7 | 795.7 | 895.9 | 786.6 | 742.4 | 891.3 | 767.6 | 880.4 | 753.3 | 876.1 | 763.3 | 864.1 | 6447.5 | 7080.8 | 5937 | 7302.1 | 6462.1 | 6626.4 | 6413.8 | 5688.1 | 7089.8 | 6803.7 | 6321.7 | 7337.9 | 7057.9 | 6463.3 | 6389.3 | 7119.3 | 6231.2 | 6547.2 | 7131.6 | 6210 | 7230.8 | 6244.9 | 7002.2 | 6426.6 | 7147 | 6102.3 | 7176.8 | 6429.3 | 7085.1 | 6412.2 | 7123.6 | 6513.3 | 6481.7 | 7225.8 | 5929.8 | 6297 | 7232.4 | 7155.4 | 7227.5 | 6590.5 | 7343.2 | 6444.8 | 7090.5 | 6633.9 | 7013.2 | 6140.4 | 7159.8 | 6521.6 | 6708.7 | 6815.7 | 6757.7 | 5836 | 6630.1 | 5933.4 | 6647.6 | 6639.3 | 7750.8 | 6655.7 | 7752.7 | 6816 | 7625.7 | 6692.7 | 6818.5 | 6609 | 6902.8 | 7174.9 | 6878.6 | 7053.9 | 7063.2 | 7146.8 | 6349.8 | 7085.7 | 7057.5 | 7129.2 | 7150.3 | 7138.1 | 7155.5 | 6373.7 | 7057.2 | 6398.7 | 16.6941 | 16.6487 | 16.3716 | 0 | 16.4903 | 16.4961 | 0 | 28.916 | 0 | 0 | 0 | 0 | 4.6682 | 4.5201 | 4.5337 | 4.601 | 4.4261 | 4.3898 | 7.483 | 7.547 | 6.831 | 7.457 | 7.008 | 7.458 | 4.1973 | 4.4952 | 4.2437 | 4.1274 | 4.6215 | 4.9231 | 0.94406 | 1.1125 | 1.1586 | 0 | 1.1541 | 0.96885 | 5.2742 | 5.2453 | 5.155 | 4.8925 | 5.3303 | 5.2403 | 0.95315 | 1.0756 | 1.0686 | 0 | 1.1464 | 1.2049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223318 | 407 | 213833 | 419 | 413745.099 | 1089.867 | 4.1973 | 4.4952 | 4.2437 | 4.1274 | 4.6215 | 4.9231 | 5.2742 | 5.2453 | 5.155 | 4.8925 | 5.3303 | 5.2403 | 0 | 0 | 629000 | 1000 | 626533 | 2200 | 628000 | 624333 | 10.3833 | 4.4347 | 1.0676 | 5.1896 | 1.0897 | 24.07% | 21% | 16.5402 | 28.916 | 4.5231 | 7.2973 | 632699.8 | 626533 | 1740848.1828 | 35.99%
2023-01-23 | 2023 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 334767.775 | 7:36 | 18:15 | 6930.5 | 7250.8 | 7166.3 | 7132.9 | 7145.4 | 7276.2 | 7213.2 | 7521.1 | 7282 | 7207.8 | 7167.9 | 7313.5 | 7238.5 | 7248.7 | 7167 | 7309.2 | 7202.3 | 7252.7 | 7291.7 | 7293.6 | 7231 | 7308.2 | 7177.5 | 7244.3 | 7171.2 | 6320.3 | 7220.5 | 7115.1 | 7371.1 | 7280.4 | 7189.2 | 7338.6 | 7330 | 7333.3 | 7327.7 | 7316.7 | 7410 | 7363.6 | 7342.5 | 7296.3 | 8075.3 | 7194 | 7961 | 6875.8 | 7514.3 | 8581.5 | 6990 | 7996.5 | 6733.2 | 6922.2 | 7369.9 | 6915.3 | 7628.6 | 6716 | 7653.3 | 6786.5 | 6752.6 | 7386.9 | 6740.4 | 7674.6 | 7631 | 6632 | 7374.7 | 6945.9 | 7124 | 6716 | 7154.4 | 7553 | 7763.9 | 6935.6 | 7615.6 | 6676.2 | 6493.7 | 7674.9 | 6719.1 | 7625.6 | 6565.1 | 7667 | 6684.4 | 7562.2 | 6941.3 | 7626.1 | 6489.5 | 7843.3 | 6944.1 | 7122.3 | 6902.2 | 6107.5 | 7581.2 | 7326 | 6750.4 | 7855.8 | 7586.3 | 6948.5 | 6869.4 | 7637.8 | 6730.4 | 7032.9 | 7691.7 | 6655.4 | 7772.9 | 6700.4 | 7554.4 | 6912.9 | 7681.8 | 6545 | 7720.4 | 6899.7 | 7636.7 | 6913.3 | 7685.8 | 7016 | 6750.3 | 7520.8 | 6794.7 | 6681.9 | 7611.7 | 7452.2 | 7556.1 | 6909.3 | 7675.2 | 6735.4 | 7426.2 | 6918.8 | 7334.3 | 6433 | 7505.2 | 6833.3 | 6837 | 6954.7 | 6880.7 | 5952.7 | 6708.2 | 5991.9 | 6753.1 | 6777 | 7958.5 | 6807.5 | 7977.5 | 6977.1 | 7821.4 | 6850.7 | 6968.5 | 6785.6 | 7713.4 | 8020.9 | 7696.4 | 7903.8 | 7921.4 | 7939.6 | 7080.3 | 7911.9 | 7922.9 | 7972.6 | 8028.4 | 8003.9 | 8008.9 | 7139.6 | 7905.5 | 7155.3 | 16.5013 | 16.4446 | 16.2522 | 0 | 16.3571 | 16.3981 | 0 | 22.6515 | 0 | 0 | 0 | 0 | 4.7485 | 4.7611 | 4.8234 | 4.697 | 4.6514 | 4.7601 | 8.003 | 8.061 | 7.465 | 7.875 | 7.84 | 7.408 | 3.2908 | 3.461 | 3.3328 | 3.2361 | 3.4714 | 3.5566 | 0.73604 | 0.8743 | 0.9045 | 0 | 0.89976 | 0.79438 | 3.808 | 3.7664 | 3.7598 | 3.6197 | 3.7971 | 3.9206 | 0.7598 | 0.85666 | 0.85785 | 0 | 0.90074 | 0.98309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223895 | 409 | 214410 | 421 | 414894.032 | 1094.867 | 3.2908 | 3.461 | 3.3328 | 3.2361 | 3.4714 | 3.5566 | 3.808 | 3.7664 | 3.7598 | 3.6197 | 3.7971 | 3.9206 | 577000 | 2000 | 577000 | 2000 | 1148933 | 5000 | 1150000 | 1143933 | 10.65 | 3.3915 | 0.84179 | 3.7786 | 0.87163 | 24.82% | 23.07% | 16.3907 | 22.6515 | 4.7402 | 7.7753 | 1158027.7 | 1148734 | 1290647.1765 | 89%
2023-01-24 | 2023 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 334767.775 | 7:26 | 18:17 | 9899.4 | 10332.9 | 10245.4 | 10214.6 | 10228.2 | 10436.5 | 10283.6 | 10669.3 | 10341.6 | 10226.5 | 10224.4 | 10399.4 | 10353.1 | 10342 | 10231 | 10446.5 | 10331.5 | 10413.6 | 10434.2 | 10430.7 | 10332.4 | 10445.4 | 10244.9 | 10363.3 | 10256 | 9049.2 | 10334.3 | 10205.6 | 10495.6 | 10351.7 | 10235.7 | 10446.2 | 10480.4 | 10492.1 | 10454.9 | 10457.8 | 10581.9 | 10515.7 | 10476.5 | 10384.7 | 11268.4 | 10167.3 | 11122.8 | 9721 | 10605.7 | 11781.2 | 9931.7 | 11176.3 | 9604.5 | 9861.3 | 10507.1 | 9863.7 | 10816.9 | 9577.8 | 10822.5 | 9664.4 | 9616.7 | 9790.9 | 9595.2 | 10846.3 | 10793.7 | 9434.5 | 10523.4 | 9951.6 | 10157.1 | 9589.2 | 10200.2 | 10714.5 | 10939.7 | 9887.8 | 10779.8 | 9524.5 | 9219.7 | 10854.7 | 9563.7 | 10784.7 | 9360.7 | 10825.7 | 9499 | 10695.6 | 9926.8 | 10793.8 | 9267 | 11064.1 | 9919.7 | 10097.7 | 9897.6 | 8452.2 | 10782.1 | 10426.8 | 9685.3 | 11100.6 | 10748.5 | 9903 | 9786.9 | 10828.9 | 9665.3 | 10051.4 | 10901.3 | 9503.2 | 10987.4 | 9591.4 | 10720 | 9853.6 | 10855.9 | 9348.1 | 10910.6 | 9854.6 | 10810.3 | 9842.4 | 10864.5 | 9998.7 | 9625.7 | 10677.9 | 9706.1 | 9544.2 | 10747.3 | 10604.3 | 10697.6 | 9825.3 | 10838.6 | 9601.7 | 10532.4 | 9880.2 | 10441.3 | 9155.3 | 10629.6 | 9715 | 9725.9 | 9868 | 9759.2 | 8457.8 | 9541.6 | 8522.7 | 9587.3 | 9626 | 11088 | 9643.2 | 11077.6 | 9879.6 | 10967.1 | 9714.8 | 9896 | 9613.3 | 10765.5 | 11101.1 | 10742.3 | 10967.6 | 11023.3 | 11060.9 | 9952 | 10980 | 10997.6 | 11067.7 | 11088.5 | 11079.6 | 11084 | 10032.2 | 10860.9 | 10064.3 | 16.3618 | 16.2743 | 16.0762 | 0 | 16.2432 | 16.2389 | 0 | 25.9425 | 0 | 0 | 0 | 0 | 4.2725 | 4.1377 | 4.1537 | 4.3225 | 4.1242 | 3.8763 | 6.942 | 6.718 | 6.719 | 7.199 | 6.585 | 6.532 | 4.2922 | 4.6074 | 4.3059 | 4.2152 | 4.7078 | 5.0404 | 0.94878 | 1.1596 | 1.1667 | 0 | 1.2008 | 1.0085 | 5.3845 | 5.3821 | 5.2307 | 4.944 | 5.4639 | 5.3644 | 0.95611 | 1.1213 | 1.0768 | 0 | 1.1938 | 1.2537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224714 | 411 | 215225 | 423 | 416521.033 | 1099.733 | 4.2922 | 4.6074 | 4.3059 | 4.2152 | 4.7078 | 5.0404 | 5.3845 | 5.3821 | 5.2307 | 4.944 | 5.4639 | 5.3644 | 819000 | 2000 | 815000 | 2000 | 1627001 | 4866 | 1630000 | 1622135 | 10.85 | 4.5282 | 1.0969 | 5.2949 | 1.1203 | 24.22% | 21.16% | 16.2389 | 25.9425 | 4.1478 | 6.7825 | 1641228 | 1627001 | 1772588.3887 | 91.79%
2023-01-25 | 2023 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 334767.775 | 7:25 | 18:26 | 11425 | 11751.9 | 11648.7 | 11656.1 | 11627.9 | 11824.3 | 11685.2 | 11961 | 11627.1 | 11621.2 | 11651.1 | 11786.9 | 11783.2 | 11743.2 | 11677.9 | 11866.2 | 11152.5 | 11226.8 | 11240.2 | 11249.9 | 11152.4 | 11244.9 | 11113.8 | 11196.8 | 11680.6 | 10635.2 | 11765.2 | 11651.6 | 11846.1 | 11702.6 | 11650.1 | 11797.4 | 11859.6 | 11859.6 | 11829.9 | 11837.8 | 11944.6 | 11891.3 | 11843.3 | 11765.7 | 12474.2 | 11620.2 | 12333 | 11295.7 | 12010.1 | 12936 | 11436.3 | 12382.5 | 11223.2 | 11446.1 | 11907.4 | 11434.4 | 12145.8 | 11171.5 | 12163.8 | 11269.2 | 11242.4 | 11362.1 | 11228 | 12200.4 | 12135.3 | 11062.9 | 11921.9 | 11497.7 | 11641.9 | 11204.9 | 11693.3 | 12085.9 | 12229.5 | 11454.6 | 12124 | 11172 | 10827 | 12204.9 | 11176.9 | 12127.9 | 10992.6 | 12129 | 11104.7 | 12023.5 | 11506.2 | 12144.5 | 10926 | 12375.5 | 11487.3 | 11622.6 | 11381.7 | 9916.9 | 12105.8 | 11795.4 | 11286.9 | 12374.7 | 12062.2 | 11419.5 | 11294.8 | 11992.6 | 11227.7 | 11542.6 | 12172.6 | 11116.5 | 12273.8 | 11203.5 | 11923.5 | 11452.5 | 12139.8 | 10981.2 | 12222.2 | 11428.3 | 12165.8 | 11404.2 | 12182.4 | 11569.2 | 11200.4 | 12025.9 | 11265.6 | 11141.2 | 11894.2 | 11959.2 | 12008.6 | 11373.4 | 12134.8 | 11198.4 | 11882.5 | 11448 | 11832 | 10731.6 | 12000.8 | 11304.3 | 11317.8 | 11394.9 | 11309.9 | 9911.7 | 11155.9 | 10004.6 | 11258.4 | 11244.3 | 12334.8 | 11216.4 | 12329.9 | 11426.5 | 12182.8 | 11288.9 | 11432.2 | 11214.3 | 12117.1 | 12349.7 | 12072.5 | 12240.8 | 12099.5 | 12329 | 11488 | 12269.4 | 12291.2 | 12372.2 | 12348.7 | 12351.2 | 12363.7 | 11561.9 | 12201.1 | 11606.9 | 16.6779 | 16.5198 | 16.4359 | 0 | 16.7344 | 16.3808 | 0 | 32.0433 | 0 | 0 | 0 | 0 | 2.483 | 2.4069 | 2.3978 | 2.5631 | 2.46 | 2.3995 | 4.669 | 5.309 | 4.568 | 4.767 | 4.465 | 4.346 | 4.9887 | 5.3777 | 5.017 | 4.9005 | 5.5613 | 6.0638 | 1.1166 | 1.3418 | 1.3773 | 0 | 1.3837 | 1.1578 | 6.45 | 6.4249 | 6.2707 | 5.9168 | 6.512 | 6.3917 | 1.1114 | 1.2864 | 1.2513 | 0 | 1.3697 | 1.4423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225642 | 412 | 216152 | 424 | 418367.899 | 1104.6 | 4.9887 | 5.3777 | 5.017 | 4.9005 | 5.5613 | 6.0638 | 6.45 | 6.4249 | 6.2707 | 5.9168 | 6.512 | 6.3917 | 928000 | 1000 | 927000 | 1000 | 1846866 | 4867 | 1853000 | 1841999 | 11.0167 | 5.3182 | 1.2754 | 6.3277 | 1.2922 | 23.98% | 20.42% | 16.5498 | 32.0433 | 2.4517 | 4.6873 | 1865753 | 1846734 | 2079684.184 | 88.8%
2023-01-26 | 2023 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 334767.775 | 7:23 | 18:27 | 11221.3 | 11531.7 | 11429.4 | 11453.4 | 11397.2 | 11599.3 | 11445.7 | 11717 | 11532.9 | 11387.3 | 11434.3 | 11575.4 | 11575.9 | 11528.6 | 11476.4 | 11668.4 | 11531.8 | 11604.7 | 11611.3 | 11622.8 | 11518.9 | 11614.8 | 11476.4 | 11565.8 | 11472.3 | 10454.3 | 11561.2 | 11443.3 | 11637.2 | 11482.9 | 11442.8 | 11593.3 | 11653.3 | 11664.7 | 11623.3 | 11638.9 | 11736.3 | 11683.4 | 11633.9 | 11559.3 | 12238.2 | 11384.6 | 12103 | 11056.4 | 11762.6 | 12726.4 | 11195.5 | 12157.5 | 11005.9 | 11231.4 | 11693.9 | 11220 | 11931.1 | 10938.2 | 11959.5 | 11061.3 | 11031.1 | 10675.2 | 11020.9 | 12001.7 | 11945.9 | 10870.2 | 11676.9 | 11251.2 | 11414.3 | 10980.7 | 11475.2 | 11853.7 | 12016.4 | 11228.9 | 11901.8 | 10947.1 | 10650.8 | 11982 | 10972.4 | 11919.2 | 10803.9 | 11924.5 | 10896.9 | 11815.5 | 11270.1 | 11818 | 10711.2 | 12147.1 | 11244.6 | 11391 | 11135.3 | 9698.3 | 11877.8 | 11570.9 | 11051.4 | 12143.4 | 11829.1 | 11185.8 | 11058.1 | 11908.9 | 11022.3 | 11340.5 | 11961.4 | 10892.8 | 12051.9 | 10973.7 | 11859.5 | 11218.5 | 11921.1 | 10754.5 | 11996.1 | 11192.1 | 11929 | 11174.2 | 11947.7 | 11319.1 | 10975.4 | 11798.2 | 11055.3 | 10934.2 | 11821.3 | 11731.7 | 11786.8 | 11140.4 | 11902.6 | 10963.4 | 11653 | 11204.6 | 11593.2 | 10511.7 | 11759.5 | 11061.5 | 11090.5 | 11185.4 | 11075.4 | 9718.8 | 11006.5 | 9894.2 | 11058.8 | 11034.2 | 12138.2 | 11014.9 | 12157.9 | 11241.7 | 12033.5 | 11079 | 11214.2 | 11013.9 | 11919.2 | 12170 | 11832.2 | 12040.3 | 12085.4 | 12124.8 | 11306.2 | 12082.8 | 12077.5 | 12178.3 | 12188.6 | 12166.4 | 12206.6 | 11375.3 | 11974.3 | 11408.1 | 16.6803 | 16.4526 | 16.6009 | 0 | 16.4001 | 16.2973 | 0 | 27.4399 | 0 | 0 | 0 | 0 | 4.6211 | 4.4776 | 4.3432 | 4.6283 | 4.3978 | 4.4042 | 7.771 | 7.951 | 7.304 | 7.807 | 7.183 | 7.646 | 4.8456 | 5.1902 | 4.9009 | 4.7737 | 5.369 | 5.7974 | 1.1157 | 1.2755 | 1.3682 | 0 | 1.3174 | 1.106 | 6.2002 | 6.1333 | 6.053 | 5.7583 | 6.2064 | 6.1355 | 1.115 | 1.2292 | 1.2462 | 0 | 1.3068 | 1.3768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226558 | 414 | 217064 | 426 | 420186.766 | 1109.467 | 4.8456 | 5.1902 | 4.9009 | 4.7737 | 5.369 | 5.7974 | 6.2002 | 6.1333 | 6.053 | 5.7583 | 6.2064 | 6.1355 | 916000 | 2000 | 912000 | 2000 | 1818867 | 4867 | 1824000 | 1814000 | 11.0667 | 5.1461 | 1.2366 | 6.0811 | 1.2548 | 24.03% | 20.63% | 16.4863 | 27.4399 | 4.4787 | 7.6103 | 1836304.3 | 1818867 | 2024451.0736 | 89.84%
2023-01-27 | 2023 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 334767.775 | 7:23 | 18:26 | 11362.8 | 11651.6 | 11544.7 | 11578.8 | 11505.6 | 11715.2 | 11565.8 | 11827 | 11521.4 | 11510.8 | 11554.6 | 11691.1 | 11692.8 | 11645.8 | 11594.4 | 11786.4 | 11647.7 | 11730.4 | 11728.5 | 11739.4 | 11637.3 | 11733.4 | 11601.3 | 11689 | 10967.1 | 10081.8 | 11069 | 10968.6 | 11132.8 | 10990.2 | 10822.4 | 10884.4 | 11774.4 | 11789.4 | 11749.5 | 11746.9 | 11856.3 | 11810.6 | 11758.7 | 11692.7 | 12374.7 | 11542.6 | 12239.7 | 11234.5 | 11900.9 | 12819.5 | 11341.6 | 12274.8 | 10700.4 | 10898.2 | 11388.1 | 10963.1 | 11602.3 | 10700.2 | 11607.1 | 10811.1 | 11204.2 | 10896 | 11199.1 | 12119.4 | 12065.3 | 11049.7 | 11795.5 | 11391 | 11547.7 | 11145.5 | 11614.3 | 11994.6 | 12145.7 | 11387.6 | 12037.5 | 11129.6 | 10834.5 | 12123.6 | 11137.9 | 12062 | 10981.2 | 12051.2 | 11069.1 | 11946.6 | 11427.1 | 11956.1 | 10892.3 | 12285.2 | 11406.4 | 11543.8 | 11280.3 | 9883.9 | 11993.5 | 11700.6 | 11216.6 | 12266.1 | 11972.2 | 11355.2 | 11228.6 | 11883.6 | 11169.7 | 11481.5 | 12078.1 | 11053.9 | 12164.9 | 11126.5 | 11807.5 | 11363.2 | 12024.6 | 10922.3 | 12119.9 | 11337.1 | 12067.9 | 11333 | 12076.8 | 11490.6 | 11142.4 | 11938.3 | 11204.5 | 11114.4 | 11792.3 | 11868 | 11908.8 | 11309.5 | 12039.5 | 11145.1 | 11787.8 | 11375.8 | 11745.7 | 10727.8 | 11904.9 | 11246.9 | 11263.8 | 11333.2 | 11247.1 | 9909.8 | 11172.2 | 10113.2 | 11212.2 | 11204.1 | 12271.1 | 11185.5 | 12291 | 11409.3 | 12109.8 | 11234.9 | 11359.6 | 11192.9 | 12067.1 | 12307.5 | 12126.3 | 12183.3 | 12033.5 | 12268.1 | 11473.1 | 12232.5 | 12213.6 | 12302.3 | 12313.9 | 12302.9 | 12345.8 | 11529.3 | 12262.9 | 11561.4 | 17.212 | 16.6846 | 16.758 | 0 | 16.5676 | 16.4868 | 0 | 28.0801 | 0 | 0 | 0 | 0 | 4.9421 | 4.8546 | 4.8777 | 5.0404 | 4.8487 | 4.7498 | 8.142 | 8.215 | 8.32 | 8.347 | 8.829 | 8.218 | 4.9467 | 5.2911 | 4.9772 | 4.8638 | 5.4695 | 5.9206 | 1.1247 | 1.3031 | 1.3772 | 0 | 1.3479 | 1.1372 | 6.3344 | 6.2686 | 6.16 | 5.845 | 6.3564 | 6.2574 | 1.1191 | 1.2563 | 1.2502 | 0 | 1.338 | 1.4155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227475 | 415 | 217986 | 428 | 422017.433 | 1114.2 | 4.9467 | 5.2911 | 4.9772 | 4.8638 | 5.4695 | 5.9206 | 6.3344 | 6.2686 | 6.16 | 5.845 | 6.3564 | 6.2574 | 917000 | 1000 | 922000 | 2000 | 1830667 | 4733 | 1836000 | 1825934 | 11.05 | 5.2448 | 1.258 | 6.2036 | 1.2758 | 23.99% | 20.57% | 16.7418 | 28.0801 | 4.8856 | 8.3452 | 1849872.1 | 1830600 | 2066418.0413 | 88.59%
2023-01-28 | 2023 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 334767.775 | 7:23 | 18:25 | 11392.3 | 11680.9 | 11634.9 | 11635.8 | 11643.6 | 11754 | 11588.9 | 11850.8 | 11646.3 | 11534.4 | 11589.6 | 11723.8 | 11737 | 11680.6 | 11628.9 | 11826.7 | 11694 | 11780.8 | 11776.3 | 11783.7 | 11682.2 | 11775.1 | 11651.2 | 11739.7 | 11643.7 | 10615.7 | 11715.1 | 11608.2 | 11792.9 | 11642.6 | 11632.2 | 11758.4 | 11825.3 | 11845.5 | 11801.7 | 11801.8 | 11903.4 | 11854.1 | 11805.6 | 11751.6 | 12406.6 | 11575.4 | 12275.5 | 11255.6 | 11927.3 | 12860.4 | 11403.4 | 12323.6 | 11194.9 | 11414.3 | 11864.4 | 11397.5 | 12093.2 | 11111.4 | 12118.5 | 11239.1 | 11216.8 | 10924.4 | 11211.3 | 12164.8 | 12110.4 | 11054.5 | 11828.7 | 11412.3 | 11583.5 | 11168.5 | 11649.8 | 12025.6 | 12180.1 | 11412.8 | 12071.5 | 11130.6 | 10826.3 | 12149 | 11159.4 | 12083.2 | 10979.7 | 12091.3 | 11077.2 | 11972.1 | 11457.9 | 11987.1 | 10878.7 | 12312.2 | 11424.8 | 11563.4 | 11299.3 | 9831.3 | 12011.6 | 11734.2 | 11229.3 | 12301.2 | 12023.9 | 11408.7 | 11285.8 | 11999.7 | 11202.2 | 11525.5 | 12136.4 | 11078 | 12220 | 11161.3 | 11965.9 | 11395 | 12083.4 | 10940.4 | 12165.6 | 11382.4 | 12101.3 | 11363.3 | 12120 | 11528.5 | 11164.9 | 11984.3 | 11169.9 | 11140.5 | 12006.6 | 11896.3 | 11964.1 | 11318.5 | 12062.7 | 11147.8 | 11851.5 | 11418.4 | 11805.7 | 10684.6 | 11931 | 11248.8 | 11260.3 | 11336.4 | 11278.4 | 9847.5 | 11177.8 | 10088.8 | 11207.5 | 11213.7 | 12307.3 | 11213.2 | 12326 | 11437.3 | 12181.5 | 11253.6 | 11379.8 | 11212.8 | 12098.1 | 12334.2 | 12151.7 | 12202.5 | 12170.6 | 12292.9 | 11504.6 | 12258.3 | 12211.3 | 12313.7 | 12328 | 12312.2 | 12356.6 | 11547 | 12283.3 | 11569.2 | 19.3476 | 18.6913 | 18.6723 | 0 | 18.5419 | 18.3748 | 0 | 32.3742 | 0 | 0 | 0 | 0 | 3.1584 | 3.2493 | 3.1443 | 3.2987 | 3.1479 | 3.1463 | 5.032 | 5.231 | 4.984 | 5.689 | 5.3 | 4.968 | 5.0107 | 5.3549 | 5.0346 | 4.9194 | 5.5302 | 5.9794 | 1.1284 | 1.317 | 1.3843 | 0 | 1.3569 | 1.1352 | 6.4126 | 6.3511 | 6.234 | 5.906 | 6.4335 | 6.3187 | 1.1226 | 1.268 | 1.2557 | 0 | 1.3497 | 1.4127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228404 | 417 | 218912 | 430 | 423863.233 | 1119.067 | 5.0107 | 5.3549 | 5.0346 | 4.9194 | 5.5302 | 5.9794 | 6.4126 | 6.3511 | 6.234 | 5.906 | 6.4335 | 6.3187 | 929000 | 2000 | 926000 | 2000 | 1845800 | 4867 | 1851000 | 1840933 | 11.0333 | 5.3049 | 1.2644 | 6.276 | 1.2817 | 23.83% | 20.42% | 18.7256 | 32.3742 | 3.1908 | 5.2007 | 1863944.2 | 1845733 | 2056019.8256 | 89.77%
2023-01-29 | 2023 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 334767.775 | 7:28 | 18:21 | 8871.7 | 9216.1 | 9287.3 | 9220.2 | 9345.1 | 9448.7 | 9204.1 | 9516.6 | 9246.1 | 9097.8 | 9170.9 | 9310.4 | 9325.5 | 9288.1 | 9200.4 | 9437 | 9320.1 | 9415.6 | 9417.3 | 9395.3 | 9325.4 | 9420 | 9255.6 | 9369.2 | 9264.8 | 8156.8 | 9292.7 | 9192.3 | 9470.8 | 9302.4 | 9273.1 | 9454.9 | 9506.2 | 9538.5 | 9462.8 | 9470.1 | 9594.5 | 9517.1 | 9492.5 | 9457.7 | 10240.5 | 9162.3 | 10115.2 | 8748.3 | 9542.7 | 10729.6 | 9005.2 | 10185 | 8658.9 | 8888.9 | 9472.3 | 8878.6 | 9771.3 | 8593.6 | 9782.4 | 8727.1 | 8655.6 | 9482 | 8640.7 | 9807.3 | 9745.1 | 8491.2 | 9372.6 | 8846.3 | 9111.6 | 8641.1 | 9182.1 | 9655.3 | 9887.5 | 8891.9 | 9747.8 | 8571.5 | 8306.3 | 9825.3 | 8615.5 | 9763 | 8447.2 | 9781.6 | 8551.9 | 9660.2 | 8913.2 | 9604 | 8324.8 | 9992.6 | 8904.4 | 9066.1 | 8829.4 | 7549.8 | 9651.2 | 9331.2 | 8685.8 | 10029 | 9715.8 | 8926.3 | 8828.4 | 9779.1 | 8709.5 | 9079.7 | 9917.8 | 8606 | 9975.1 | 8682.3 | 9705.2 | 8901.1 | 9846.9 | 8449.5 | 9899.5 | 8906.8 | 9772.6 | 8874.2 | 9832.8 | 9014.4 | 8701.5 | 9678.6 | 8759.5 | 8655.8 | 9745.8 | 9590.7 | 9685.1 | 8871.4 | 9819 | 8657.2 | 9536.1 | 8910.7 | 9413.5 | 8237 | 9596.6 | 8755.6 | 8752.7 | 8866 | 8809.8 | 7603.7 | 8684 | 7758.2 | 8710.9 | 8715.4 | 10090.9 | 8727 | 10133.4 | 8981.1 | 9979.9 | 8774 | 8929 | 8705.1 | 9823.3 | 10180.9 | 9909.2 | 9990.4 | 9999.8 | 10061.7 | 9056.2 | 10036.9 | 9990.8 | 10114.5 | 10176.7 | 10167.9 | 10176.2 | 9142.7 | 10037.6 | 9139.7 | 20.9463 | 20.7078 | 20.6296 | 0 | 21.0712 | 20.7227 | 0 | 33.3269 | 0 | 0 | 0 | 0 | 2.499 | 2.4578 | 2.3818 | 2.4711 | 2.4799 | 2.437 | 4.879 | 5.165 | 4.835 | 5.466 | 4.925 | 4.834 | 4.0325 | 4.3181 | 4.0197 | 3.9488 | 4.3978 | 4.645 | 0.83738 | 1.0853 | 1.0312 | 0 | 1.1273 | 0.95911 | 4.9294 | 4.9708 | 4.7923 | 4.5096 | 5.0742 | 4.9924 | 0.84846 | 1.0508 | 0.95923 | 0 | 1.1318 | 1.1889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229143 | 419 | 219649 | 431 | 425334.167 | 1124.067 | 4.0325 | 4.3181 | 4.0197 | 3.9488 | 4.3978 | 4.645 | 4.9294 | 4.9708 | 4.7923 | 4.5096 | 5.0742 | 4.9924 | 739000 | 2000 | 737000 | 1000 | 1470934 | 5000 | 1473000 | 1465934 | 10.8833 | 4.227 | 1.0081 | 4.8781 | 1.0358 | 23.85% | 21.23% | 20.8155 | 33.3269 | 2.4544 | 5.0173 | 1483878.4 | 1470867 | 1596588.2847 | 92.13%
2023-01-30 | 2023 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 334767.775 | 7:25 | 18:29 | 11028.6 | 11408.8 | 11353.1 | 11402.1 | 11333.6 | 11459.6 | 11419.8 | 11616 | 11373 | 11259 | 11233.5 | 11399 | 11334.3 | 11318.9 | 11308.7 | 11491.5 | 11289.6 | 11296 | 11310.1 | 11391 | 11148.3 | 11273.5 | 11083.2 | 11218 | 11140.2 | 10209.3 | 11242.3 | 11117.1 | 11307.8 | 11063.9 | 11131 | 11231.7 | 11321.5 | 11455.5 | 11360.1 | 11400.3 | 11494.8 | 11337.7 | 11246.1 | 11283.6 | 11547 | 10904.3 | 11606.4 | 10601.7 | 11332.6 | 12185.8 | 10761.3 | 11578 | 10876.5 | 11076.5 | 11564.6 | 11051.3 | 11741.1 | 10877.8 | 11760.5 | 10859.4 | 10818.8 | 11657.2 | 10858.8 | 11814.8 | 11752.6 | 10691.9 | 11563.1 | 11109.5 | 11345.3 | 10808 | 11335.6 | 11649.9 | 11816.6 | 11099.2 | 11799.4 | 10855.3 | 10545.4 | 11916.5 | 10864.1 | 11827.4 | 10633.8 | 11816.9 | 10740.8 | 11611.8 | 11010.3 | 11559 | 10485.3 | 11894.1 | 11041.4 | 11190.8 | 10854.8 | 9464.9 | 11598.8 | 11338.4 | 10698 | 11826.5 | 11578.2 | 10944.6 | 10785.8 | 11531.1 | 10727.9 | 11093.8 | 11708.8 | 10713 | 11709.1 | 10674.9 | 11537.8 | 10853.2 | 11630.4 | 10380.2 | 11649.2 | 10879.2 | 11622.4 | 10851.2 | 11559.5 | 10932.1 | 10837.4 | 11637.6 | 10722.8 | 10695.1 | 11583.9 | 11572.3 | 11526.6 | 10973.7 | 11696.5 | 10713.4 | 11367.7 | 10895.3 | 11273.3 | 10219.5 | 11487.1 | 10837.5 | 10819.5 | 10922.3 | 10939.3 | 9452.9 | 10716.5 | 9707.5 | 10780.1 | 10850 | 12011 | 10852 | 12060.6 | 11087.4 | 11838.6 | 10919.5 | 11050.1 | 10889 | 11839.3 | 12142.6 | 11918 | 11963.7 | 11925.7 | 11996.7 | 11238.8 | 12049.8 | 11957 | 12014.1 | 11994.4 | 11966.1 | 11985.5 | 11236.1 | 12063.9 | 11312.3 | 19.5014 | 19.2546 | 19.0358 | 0 | 19.4032 | 19.3469 | 0 | 34.3182 | 0 | 0 | 0 | 0 | 2.3982 | 2.2733 | 2.2113 | 2.3559 | 2.2262 | 2.1729 | 5.389 | 4.423 | 4.885 | 5.273 | 5.056 | 5.098 | 4.8748 | 5.1726 | 4.752 | 4.8233 | 5.3544 | 5.8664 | 0.99002 | 1.2161 | 1.1754 | 0 | 1.2838 | 1.0717 | 6.1466 | 6.0535 | 5.7866 | 5.6457 | 6.2683 | 6.2411 | 0.98323 | 1.173 | 1.0782 | 0 | 1.2794 | 1.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230042 | 420 | 220543 | 433 | 427118.633 | 1128.8 | 4.8748 | 5.1726 | 4.752 | 4.8233 | 5.3544 | 5.8664 | 6.1466 | 6.0535 | 5.7866 | 5.6457 | 6.2683 | 6.2411 | 899000 | 1000 | 894000 | 2000 | 1784466 | 4733 | 1790000 | 1779733 | 11.0667 | 5.1406 | 1.1474 | 6.0236 | 1.1694 | 22.32% | 19.41% | 19.3084 | 34.3182 | 2.273 | 5.0207 | 1801214.3 | 1784333 | 1967658.0613 | 90.68%
2023-01-31 | 2023 | 2023 | Year_1 | Year_1 | 2023-02-01 | 31 | 334767.775 | 7:37 | 18:29 | 10443.7 | 10674.1 | 10625.5 | 10591.1 | 10677.4 | 10755.6 | 10690.5 | 10876.8 | 10663.1 | 10668.8 | 10535.7 | 10662.2 | 10672.4 | 10600.4 | 10638.2 | 10767 | 10463.1 | 10520.7 | 10512.4 | 10527.6 | 10454.5 | 10518.5 | 10441.3 | 10489.2 | 10598.9 | 9779.6 | 10682.1 | 10572.5 | 10744.5 | 10669.9 | 10642.4 | 10707.5 | 10789.3 | 10786.9 | 10760.6 | 10742.9 | 10816.4 | 10799.7 | 10767.2 | 10755.2 | 11509.9 | 10833 | 11404 | 10534.7 | 11120.7 | 11834.9 | 10610.4 | 11377.8 | 10232 | 10411.7 | 10784.4 | 10407 | 10981.5 | 10233.7 | 10964.2 | 10289.7 | 10272.1 | 10929.2 | 10264.6 | 11035.4 | 11044.8 | 10169.4 | 10795 | 10477.6 | 10611.9 | 10247.9 | 10667 | 10908.4 | 11049.5 | 10425.3 | 11003 | 10220.5 | 10002.3 | 11071.3 | 10258.6 | 10999.3 | 10121 | 11017.1 | 10240.4 | 10947.4 | 10411.2 | 10862 | 9973.8 | 11108.9 | 10410.9 | 10532.5 | 10338.6 | 9048.6 | 10950.4 | 10670.7 | 10266.4 | 11115.2 | 10850.6 | 10376.2 | 10292.1 | 10901.7 | 10217.7 | 10491.9 | 10922.4 | 10112.7 | 11036.3 | 10147.6 | 10826.1 | 10346.2 | 10913.3 | 9973.1 | 10985.4 | 10330.6 | 10946.6 | 10348.8 | 10965.6 | 10482.2 | 10232.4 | 10843.1 | 10181.4 | 10132.5 | 10856.2 | 10738.8 | 10799.1 | 10274.1 | 10872.8 | 10157 | 10721.8 | 10365.4 | 10702.2 | 9787 | 10802.1 | 10258.5 | 10285.4 | 10398.6 | 10301.9 | 9055.5 | 10232.4 | 9294.5 | 10268.6 | 10291.1 | 11025.8 | 10199 | 11050.7 | 10368.2 | 11024.3 | 10299.5 | 10391.3 | 10292.8 | 10959 | 11147.7 | 11011.6 | 11003 | 11018 | 11017.4 | 10450.6 | 11048.3 | 11071.6 | 11117.7 | 11128.5 | 11125 | 11160.7 | 10555.1 | 11123.6 | 10569.4 | 18.1367 | 17.8223 | 18.0777 | 0 | 17.7903 | 17.7795 | 0 | 28.8043 | 0 | 0 | 0 | 0 | 4.3155 | 4.2915 | 4.0749 | 4.3117 | 4.2631 | 4.2816 | 6.937 | 8.128 | 6.807 | 7.375 | 7.103 | 7.226 | 4.66 | 4.9686 | 4.7319 | 4.605 | 5.0381 | 5.4272 | 0.93674 | 1.2206 | 1.1933 | 0 | 1.288 | 1.078 | 5.805 | 5.7856 | 5.7498 | 5.2487 | 5.9434 | 5.7972 | 0.92925 | 1.1843 | 1.0986 | 0 | 1.2903 | 1.3389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230891 | 422 | 221383 | 435 | 428800.3 | 1133.533 | 4.66 | 4.9686 | 4.7319 | 4.605 | 5.0381 | 5.4272 | 5.805 | 5.7856 | 5.7498 | 5.2487 | 5.9434 | 5.7972 | 849000 | 2000 | 840000 | 2000 | 1681667 | 4733 | 1685000 | 1676934 | 10.8667 | 4.9051 | 1.1433 | 5.7216 | 1.1683 | 23.31% | 20.42% | 17.9213 | 28.8043 | 4.2564 | 7.2627 | 1698561.5 | 1681534 | 1886535.6595 | 89.13%
2023-02-01 | 2023 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 334767.775 | 7:22 | 18:30 | 11530.9 | 11891 | 11801.3 | 11811.3 | 11826.1 | 11924.7 | 11875.2 | 12101.6 | 11838.6 | 11775.7 | 11721.9 | 11852.5 | 11836.2 | 11795.1 | 11764.9 | 11915.8 | 11802.1 | 11873 | 11879.8 | 11886.5 | 11789.3 | 11876.7 | 11736.4 | 11829 | 11731.1 | 10748.6 | 11842.8 | 11713.7 | 11909.9 | 11774.7 | 11714.6 | 11843.7 | 11950.2 | 11957.8 | 11914.9 | 11899.2 | 11990.9 | 11939.9 | 11887.4 | 11860.8 | 12416.4 | 11610.2 | 12298.2 | 11287.2 | 11982.4 | 12914.1 | 11466.9 | 12350.6 | 11329.3 | 11533.6 | 11984.8 | 11531.8 | 12213.5 | 11293.8 | 12208.4 | 11357.7 | 11328.3 | 12124.2 | 11349.8 | 12261.6 | 12234.9 | 11198.3 | 11964.5 | 11568.8 | 11740.8 | 11267.5 | 11794 | 12079.8 | 12279.4 | 11486.1 | 12181 | 11224 | 11001.7 | 12258.1 | 11305 | 12195.3 | 11126.5 | 12239.7 | 11266.6 | 12133.1 | 11485.4 | 12028.5 | 11580.8 | 12329.6 | 11472.8 | 11832.7 | 11376.1 | 10266 | 12094 | 11767.6 | 11277.5 | 12337 | 12058.2 | 11465.8 | 11355.9 | 12119.2 | 11280.5 | 11580.6 | 12183.4 | 11186.7 | 12258.6 | 11209.1 | 12075.2 | 11449.1 | 12120.6 | 10991.1 | 12200.2 | 11417 | 12136.3 | 11404.8 | 12158.4 | 11554.7 | 11275.3 | 12046.5 | 11346.1 | 11224.7 | 12070.8 | 11959.3 | 12015.6 | 11373 | 12116.4 | 11204.8 | 11890.3 | 11449.3 | 11848.1 | 10730.4 | 11973.1 | 11299.4 | 11355.8 | 11451.3 | 11351.8 | 9940.7 | 11248.2 | 10147.3 | 11313.5 | 11317.6 | 12331.7 | 11252.2 | 12340.1 | 11471.1 | 12253.6 | 11338.8 | 11451.8 | 11302.6 | 11957.9 | 12177 | 12030.1 | 12061.1 | 12126.1 | 12141 | 11390.5 | 12112.4 | 12289.5 | 12375.6 | 12400.9 | 12385.5 | 12410.9 | 11622.6 | 12347.3 | 11639.4 | 20.8844 | 20.2552 | 20.4521 | 0 | 20.1733 | 20.0305 | 0 | 33.8521 | 0 | 0 | 0 | 0 | 3.461 | 3.4382 | 3.4168 | 3.5212 | 3.4399 | 3.3328 | 5.726 | 6.042 | 7.147 | 6.641 | 5.911 | 6.224 | 5.0888 | 5.4269 | 5.1097 | 5.0167 | 5.5768 | 5.9997 | 1.0927 | 1.2892 | 1.3441 | 0 | 1.3341 | 1.1131 | 6.4353 | 6.3575 | 6.2613 | 5.9439 | 6.4629 | 6.3952 | 1.0879 | 1.2431 | 1.2287 | 0 | 1.3282 | 1.387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231831 | 424 | 222313 | 437 | 430661.3 | 1138.267 | 5.0888 | 5.4269 | 5.1097 | 5.0167 | 5.5768 | 5.9997 | 6.4353 | 6.3575 | 6.2613 | 5.9439 | 6.4629 | 6.3952 | 940000 | 2000 | 930000 | 2000 | 1861000 | 4734 | 1866000 | 1856266 | 11.1333 | 5.3698 | 1.2346 | 6.3094 | 1.255 | 22.99% | 19.89% | 20.3591 | 33.8521 | 3.435 | 6.2818 | 1879216.1 | 1860800 | 2096073.9452 | 88.78%
2023-02-02 | 2023 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 334767.775 | 7:21 | 18:30 | 11465 | 11849.3 | 11743.2 | 11744.3 | 11761.8 | 11878.4 | 11823.7 | 12070.9 | 11792.8 | 11714 | 11678.9 | 11811.6 | 11793.9 | 11757.2 | 11715 | 11870.1 | 11754 | 11825 | 11851.3 | 11860.7 | 11744.3 | 11841.4 | 11687.1 | 11788.6 | 11704 | 10624.5 | 11813.3 | 11683.9 | 11895.3 | 11762.7 | 11668 | 11820.4 | 11928.1 | 11929 | 11902.6 | 11874.5 | 11973.3 | 11911.5 | 11857.2 | 11834.3 | 12426.1 | 11559 | 12296.6 | 11196.3 | 11943.8 | 12937.4 | 11405.1 | 12349.6 | 11252.8 | 11471.7 | 11953.1 | 11467 | 12197.7 | 11214.2 | 12198.1 | 11278.9 | 11243.9 | 12099.1 | 11257.7 | 12251.9 | 12213.2 | 11096.7 | 11938.7 | 11513 | 11702 | 11198.1 | 11754.8 | 12069.7 | 12276.2 | 11437.1 | 12172.9 | 11133.2 | 10885.1 | 12249.4 | 11230.4 | 12185.1 | 11026.3 | 12229.8 | 11179.3 | 12114.5 | 11452.9 | 12018.4 | 11554.7 | 12346.9 | 11436.5 | 11810.9 | 11332.4 | 10163.3 | 12069.5 | 11737.1 | 11195.6 | 12341.4 | 12049.6 | 11409.3 | 11289.6 | 12108.4 | 11197.1 | 11533.8 | 12177.1 | 11122.5 | 12248.5 | 11130 | 12059.7 | 11393.3 | 12105.8 | 10885.9 | 12187.2 | 11361.1 | 12110.4 | 11336.3 | 12141.8 | 11496.5 | 11200.3 | 12029.6 | 11289 | 11138.6 | 12057.6 | 11940.2 | 12002 | 11313 | 12110 | 11122 | 11866.8 | 11388.9 | 11814.1 | 10607.1 | 11950 | 11221.8 | 11293.8 | 11407.5 | 11279 | 9839.9 | 11178.6 | 10029.3 | 11251.4 | 11257.8 | 12369.7 | 11213.7 | 12373.1 | 11446.4 | 12275.2 | 11293.9 | 11420.9 | 11242.4 | 12162.4 | 12401.8 | 12232.5 | 12265.2 | 12339.7 | 12350.3 | 11523.5 | 12324.6 | 12319 | 12407.7 | 12434.5 | 12416.9 | 12435.6 | 11604.5 | 12381.2 | 11622.4 | 23.0703 | 22.5361 | 22.3651 | 0 | 22.4328 | 22.2015 | 0 | 37.7327 | 0 | 0 | 0 | 0 | 2.5311 | 2.5483 | 2.393 | 2.6087 | 2.5693 | 2.5754 | 4.892 | 5.137 | 4.552 | 4.914 | 5.032 | 4.788 | 5.1329 | 5.4517 | 5.1829 | 5.0893 | 5.6403 | 6.0054 | 1.0905 | 1.2944 | 1.3424 | 0 | 1.325 | 1.1039 | 6.4817 | 6.4262 | 6.3216 | 6.0318 | 6.5259 | 6.4071 | 1.0838 | 1.2486 | 1.2256 | 0 | 1.3166 | 1.3743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232768 | 425 | 223243 | 438 | 432519.7 | 1143.133 | 5.1329 | 5.4517 | 5.1829 | 5.0893 | 5.6403 | 6.0054 | 6.4817 | 6.4262 | 6.3216 | 6.0318 | 6.5259 | 6.4071 | 937000 | 1000 | 930000 | 1000 | 1858400 | 4866 | 1865000 | 1853534 | 11.15 | 5.4171 | 1.2312 | 6.3657 | 1.2498 | 22.73% | 19.63% | 22.5211 | 37.7327 | 2.5376 | 4.8858 | 1874859.5 | 1858200 | 2088891.4528 | 88.96%
2023-02-03 | 2023 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 334767.775 | 7:21 | 18:31 | 11363.8 | 11774.1 | 11665.5 | 11661.7 | 11680.6 | 11810.5 | 11751.2 | 11993.4 | 11708.9 | 11629.8 | 11597.1 | 11732 | 11714.6 | 11675.1 | 11630.1 | 11794 | 11676.7 | 11748.1 | 11768.2 | 11773.7 | 11655.7 | 11758.4 | 11597.3 | 11706.1 | 11606.3 | 10454 | 11720.8 | 11591 | 11817 | 11692.7 | 11572.3 | 11732.6 | 11831.6 | 11835.6 | 11815.6 | 11789.9 | 11884.9 | 11819.6 | 11762.1 | 11737.8 | 12366.1 | 11469.5 | 12240.1 | 11046.5 | 11857.6 | 12860.4 | 11304.5 | 12285.2 | 11096.9 | 11340.7 | 11863.6 | 11342.1 | 12114.2 | 11062.3 | 12103.5 | 11118.9 | 11078.3 | 12003.1 | 11093 | 12162.2 | 12123.2 | 10925.9 | 11837.9 | 11388.4 | 11604 | 11047.6 | 11657.4 | 11977.5 | 12201.8 | 11304 | 12091.7 | 10961.5 | 10699.4 | 12163.5 | 11080.2 | 12098.8 | 10855.3 | 12148.8 | 11022.7 | 12023.6 | 11310.1 | 11920.2 | 11424.4 | 12249.7 | 11295.5 | 11706.3 | 11215.5 | 10001.4 | 11992.1 | 11638 | 11042 | 12263 | 11957.7 | 11264.5 | 11137.4 | 12025.9 | 11051.4 | 11415.9 | 12109 | 10962.9 | 12179 | 10978.3 | 11980.6 | 11251.5 | 12036.9 | 10706.7 | 12115.2 | 11226.6 | 12035.3 | 11203.2 | 12074.5 | 11354.5 | 11046.3 | 11947.9 | 11158 | 10971.2 | 11987.4 | 11854.9 | 11924.3 | 11173.4 | 12038.7 | 10958.3 | 11790.5 | 11245.8 | 11738.5 | 10433.8 | 11872.4 | 11056 | 10607.3 | 10739.8 | 10599.7 | 9202 | 10513.2 | 9401 | 10565.6 | 10560.3 | 11921.4 | 10696.7 | 11927 | 10954.5 | 11830.2 | 10790.1 | 10898.1 | 10684.4 | 12082.3 | 12337 | 12160.4 | 12193.9 | 12263.5 | 12289.1 | 11407 | 12236.3 | 12233.2 | 12324.5 | 12355.5 | 12342.9 | 12376.8 | 11495.5 | 12298.7 | 11516.5 | 24.819 | 24.7474 | 24.5527 | 0 | 24.7098 | 24.5426 | 0 | 40.6451 | 0 | 0 | 0 | 0 | 2.5277 | 2.4285 | 2.4529 | 2.4139 | 2.4059 | 2.2796 | 5.305 | 5.113 | 5.574 | 5.067 | 5.137 | 5.117 | 5.1375 | 5.4662 | 5.1777 | 5.0914 | 5.6288 | 5.9753 | 1.0871 | 1.3121 | 1.3369 | 0 | 1.3361 | 1.1347 | 6.4531 | 6.426 | 6.2889 | 6.0106 | 6.4947 | 6.3922 | 1.0845 | 1.2641 | 1.2267 | 0 | 1.3277 | 1.4126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 233696 | 427 | 224156 | 440 | 434353.301 | 1147.933 | 5.1375 | 5.4662 | 5.1777 | 5.0914 | 5.6288 | 5.9753 | 6.4531 | 6.426 | 6.2889 | 6.0106 | 6.4947 | 6.3922 | 928000 | 2000 | 913000 | 2000 | 1833601 | 4800 | 1837000 | 1828801 | 11.1667 | 5.4128 | 1.2414 | 6.3442 | 1.2631 | 22.93% | 19.91% | 24.6743 | 40.6451 | 2.4181 | 5.2188 | 1850679.3 | 1833333 | 2065769.7343 | 88.75%
2023-02-04 | 2023 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 334767.775 | 7:25 | 18:38 | 10999 | 11436.1 | 11347.8 | 11333.4 | 11351.9 | 11486.9 | 11407.6 | 11687.9 | 11392.7 | 11292.1 | 11268.6 | 11414 | 11388.4 | 11359 | 11300.6 | 11475 | 11361.5 | 11436.5 | 11463.6 | 11463.6 | 11339.4 | 11447.9 | 11262.1 | 11383.5 | 11280.8 | 10038.7 | 11402.3 | 11259.3 | 11514.8 | 11384.6 | 11252.4 | 11432.1 | 11520.3 | 11527.7 | 11506.3 | 11475.4 | 11589 | 11514.1 | 11461.7 | 11431 | 12104.8 | 11106.4 | 11965 | 10634.3 | 11526.5 | 12628 | 10927.4 | 12020.2 | 10698.9 | 10966.2 | 11555 | 10973.9 | 11829.5 | 10652.3 | 11822.6 | 10724.1 | 10674.8 | 11697.1 | 10686.9 | 11883.3 | 11844.3 | 10515.6 | 11528 | 11026.7 | 11267.4 | 10650.4 | 11316.1 | 11692.8 | 11929.7 | 10943.5 | 11805.3 | 10542.7 | 10290.9 | 11880.8 | 10686.7 | 11811.2 | 10434.6 | 11876.7 | 10623.7 | 11737.7 | 10963.6 | 11639.4 | 11082.6 | 11998.9 | 10951.7 | 11395.7 | 10878 | 9625.9 | 11701.3 | 11328.5 | 10632.6 | 11995.8 | 11669.2 | 10895.5 | 10763.6 | 11735.4 | 10638.8 | 11058.3 | 11828.2 | 10567.9 | 11899.3 | 10576.1 | 11672 | 10862.3 | 11746.4 | 10294.6 | 11819 | 10853.1 | 11719.4 | 10816.5 | 11763.4 | 10970.7 | 10655.7 | 11647 | 10778.9 | 10573 | 11691.7 | 11553.4 | 11629.1 | 10793.7 | 11753.5 | 10551.2 | 11471 | 10854.1 | 11395.3 | 10038.4 | 11558.1 | 10656.8 | 10723.7 | 10892.4 | 10746.2 | 9293.1 | 10634.9 | 9488.5 | 10683.1 | 10697.5 | 12046.3 | 10703.9 | 12056.8 | 10988.8 | 11938.9 | 10800.8 | 10968.2 | 10703.3 | 11798.8 | 12086.6 | 11882.5 | 11932.1 | 12002.5 | 12027.8 | 11081.7 | 11994.8 | 11966.1 | 12068.5 | 12106.1 | 12092.8 | 12117.6 | 11159.6 | 12024.5 | 11183.9 | 26.1447 | 25.9003 | 25.8041 | 0 | 26.0396 | 25.7054 | 0 | 41.5132 | 0 | 0 | 0 | 0 | 2.2293 | 2.1279 | 2.0558 | 2.092 | 1.9932 | 2.0719 | 4.516 | 4.289 | 3.737 | 5.248 | 4.367 | 4.653 | 4.9651 | 5.2838 | 5.0158 | 4.921 | 5.4423 | 5.756 | 1.0372 | 1.2525 | 1.2799 | 0 | 1.2792 | 1.0722 | 6.1928 | 6.1759 | 6.0527 | 5.7953 | 6.2475 | 6.1739 | 1.0425 | 1.2077 | 1.1813 | 0 | 1.2742 | 1.3343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234598 | 428 | 225050 | 442 | 436142.434 | 1152.733 | 4.9651 | 5.2838 | 5.0158 | 4.921 | 5.4423 | 5.756 | 6.1928 | 6.1759 | 6.0527 | 5.7953 | 6.2475 | 6.1739 | 902000 | 1000 | 894000 | 2000 | 1789133 | 4800 | 1793000 | 1784333 | 11.2167 | 5.2307 | 1.1842 | 6.1064 | 1.208 | 22.64% | 19.78% | 25.9188 | 41.5132 | 2.095 | 4.4683 | 1805008.5 | 1788867 | 1978788.9187 | 90.4%
2023-02-05 | 2023 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 334767.775 | 7:20 | 18:32 | 10988.4 | 11481 | 11379 | 11348 | 11382.2 | 11539.8 | 11432.1 | 11767.5 | 11400.8 | 11328.3 | 11284.9 | 11461.2 | 11411.8 | 11392.6 | 11285.5 | 11489.5 | 11387.3 | 11477.6 | 11496.5 | 11487.3 | 11359.3 | 11481 | 11273.6 | 11406.9 | 11296.7 | 10004.1 | 11413.7 | 11261 | 11562.5 | 11419.9 | 11251 | 11468.7 | 11574.7 | 11589.2 | 11551.7 | 11520.4 | 11648.7 | 11553.1 | 11509.2 | 11493.1 | 12221.4 | 11095.9 | 12076.5 | 10664.7 | 11569.8 | 12747.3 | 10895.4 | 12134.8 | 10669.1 | 10941.6 | 11599.9 | 10941.1 | 11913.2 | 10610.7 | 11929.7 | 10715.5 | 10645.6 | 11752.5 | 10662.7 | 11941.6 | 11887.4 | 10488.8 | 11574.7 | 11014.1 | 11311.7 | 10668 | 11342.1 | 11791.9 | 12061.8 | 10937.8 | 11924.2 | 10540.8 | 10289.4 | 11994.2 | 10656.1 | 11922.1 | 10426 | 12006.6 | 10622.2 | 11846.8 | 10949.9 | 11721.2 | 11089 | 12131.8 | 10950.7 | 11450.4 | 10864.9 | 9618.5 | 11803.8 | 11376.2 | 10612.9 | 12126.1 | 11763.7 | 10893 | 10784.7 | 11855.6 | 10627 | 11056 | 11946.2 | 10538.8 | 12006.2 | 10548.7 | 11742.6 | 10842.4 | 11843.8 | 10275 | 11914 | 10817.3 | 11797.6 | 10788.9 | 11877 | 10954.9 | 10641.3 | 11745.7 | 10727.2 | 10531.7 | 11746.8 | 11624.3 | 11727.9 | 10772.1 | 11117.8 | 9852.2 | 10855 | 10258.2 | 10833.4 | 9500.5 | 11017.8 | 10091.4 | 10703.7 | 10873.7 | 10714.5 | 9277.8 | 10626.7 | 9473 | 10728 | 10710.9 | 12206 | 10697 | 12224.3 | 10990.5 | 12090.8 | 10789.5 | 10984.5 | 10703.5 | 11292 | 11612.5 | 11391.7 | 11462.4 | 11564.7 | 11599.7 | 10531.7 | 11561.2 | 11102.4 | 11219 | 11238 | 11226 | 11246.6 | 10205.5 | 11144 | 10213.1 | 26.5007 | 26.4378 | 26.5758 | 0 | 26.3375 | 26.7693 | 0 | 39.7897 | 0 | 0 | 0 | 0 | 4.0843 | 4.2681 | 4.0071 | 4.1635 | 4.0636 | 4.2327 | 8.812 | 8.934 | 7.94 | 8.407 | 8.234 | 8.385 | 4.94 | 5.282 | 5.0045 | 4.9175 | 5.4462 | 5.7436 | 1.0459 | 1.2687 | 1.2946 | 0 | 1.311 | 1.141 | 6.142 | 6.1375 | 6.0079 | 5.7848 | 6.2174 | 6.1721 | 1.0577 | 1.2267 | 1.1971 | 0 | 1.3 | 1.4278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 235503 | 430 | 225930 | 444 | 437920.634 | 1157.6 | 4.94 | 5.282 | 5.0045 | 4.9175 | 5.4462 | 5.7436 | 6.142 | 6.1375 | 6.0079 | 5.7848 | 6.2174 | 6.1721 | 905000 | 2000 | 880000 | 2000 | 1778200 | 4867 | 1781000 | 1773333 | 11.2 | 5.2223 | 1.2122 | 6.0769 | 1.2419 | 23.21% | 20.44% | 26.5242 | 39.7897 | 4.1365 | 8.452 | 1793912.5 | 1778133 | 1983601.4395 | 89.64%
2023-02-06 | 2023 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 334767.775 | 7:20 | 18:33 | 10563.2 | 11046.2 | 10988.5 | 10973.9 | 10989.5 | 11122.6 | 11015.6 | 11308 | 11009.3 | 10892.6 | 10873.8 | 11028.8 | 11001.3 | 10972.5 | 10914.5 | 11091.7 | 10987.1 | 11068.6 | 11079.1 | 11068.6 | 10943.1 | 11057.6 | 10856.5 | 10974.1 | 10898.5 | 9646.9 | 10988.9 | 10844.3 | 11124.7 | 10995.3 | 10883 | 11059.2 | 11096.9 | 11129.8 | 11129.9 | 11088.8 | 11195 | 11116.4 | 10961.8 | 11005.7 | 11697.9 | 10669.4 | 11572.2 | 10522.9 | 11122.1 | 12260.2 | 10467.1 | 11616 | 10270.1 | 10532.1 | 11176.9 | 10546.3 | 11466.2 | 10227.8 | 11470.9 | 10325.5 | 10244.1 | 11321 | 10259.1 | 11501.8 | 11457.8 | 10089.1 | 11102.5 | 10541 | 10863.5 | 10228 | 10909.3 | 11308.5 | 11563.9 | 10503.2 | 11433.4 | 10114.1 | 9867.9 | 11503 | 10233.3 | 11435.5 | 10004.1 | 11503 | 10183.1 | 11359.6 | 10515.5 | 11249.9 | 10662.3 | 11621.8 | 10516 | 10999.5 | 10454.2 | 9240.1 | 11330.9 | 10946.5 | 10192.5 | 11608.3 | 11264.1 | 10447.9 | 10332.1 | 11347 | 10212.1 | 10599.6 | 11421.3 | 10083.7 | 11478.3 | 10106.1 | 11232.7 | 10373 | 11327.5 | 9829.5 | 11389.6 | 10351.3 | 11287.3 | 10338.1 | 11342.9 | 10476.2 | 10199.1 | 11215.9 | 10250.5 | 10086 | 11258.6 | 11119.6 | 11195 | 10308.2 | 11319.1 | 10067.6 | 10965 | 10350.8 | 10950.8 | 9585.1 | 11103.5 | 10179.3 | 10249.3 | 10426.6 | 10253.5 | 8883.9 | 10157.5 | 9051 | 10260.9 | 10263.6 | 11668.8 | 10250.3 | 11665.4 | 10523.1 | 11561.2 | 10364 | 10537.7 | 10267.7 | 11405.5 | 11703.4 | 11500.5 | 11569.6 | 11617.8 | 11647.1 | 10630.8 | 11613.7 | 11605.9 | 11700.3 | 11747.6 | 11732.7 | 11756.4 | 10723.4 | 11664.7 | 10748.5 | 23.9283 | 23.76 | 23.6182 | 0 | 23.9427 | 23.6924 | 0 | 35.5609 | 0 | 0 | 0 | 0 | 3.668 | 3.5724 | 3.5301 | 3.6487 | 3.5272 | 3.2845 | 6.741 | 6.754 | 6.389 | 7.494 | 6.611 | 6.209 | 4.756 | 5.0756 | 4.7802 | 4.7065 | 5.1607 | 5.4234 | 0.99253 | 1.2321 | 1.215 | 0 | 1.261 | 1.1143 | 5.8243 | 5.819 | 5.6628 | 5.4553 | 5.8649 | 5.8467 | 1.0059 | 1.1958 | 1.1346 | 0 | 1.2562 | 1.3987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 236373 | 432 | 226790 | 445 | 439643.634 | 1162.4 | 4.756 | 5.0756 | 4.7802 | 4.7065 | 5.1607 | 5.4234 | 5.8243 | 5.819 | 5.6628 | 5.4553 | 5.8649 | 5.8467 | 870000 | 2000 | 860000 | 1000 | 1723000 | 4800 | 1727000 | 1718200 | 11.2167 | 4.9837 | 1.163 | 5.7455 | 1.1982 | 23.34% | 20.86% | 23.7883 | 35.5609 | 3.5385 | 6.6997 | 1738949.5 | 1722866 | 1896228.7592 | 90.86%
2023-02-07 | 2023 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 334767.775 | 7:18 | 18:34 | 11129 | 11594.2 | 11536.3 | 11523.3 | 11526.2 | 11677 | 11549.4 | 11865.6 | 11525.3 | 11419.2 | 11416.6 | 11578.4 | 11570.4 | 11523.1 | 11481.4 | 11682.1 | 11573.1 | 11661 | 11674.1 | 11657.8 | 11544.6 | 11656.8 | 11301.3 | 11593.2 | 11494.8 | 10205.4 | 11598.3 | 11440.4 | 11729.9 | 11581 | 11471.6 | 11677 | 11742.9 | 11763.6 | 11729.5 | 11688.1 | 11808.8 | 11723.7 | 11671.8 | 11650.7 | 12406.9 | 11329 | 12262.2 | 11180.1 | 11765.9 | 12896.1 | 11125.4 | 12330.1 | 10842.2 | 11109.9 | 11762.1 | 11114.3 | 12075.9 | 10778.1 | 12081.5 | 10891.1 | 10811.6 | 11911.4 | 10824.6 | 12116.1 | 12069.6 | 10664.5 | 11680 | 11115.1 | 11436.9 | 10804.6 | 11490.2 | 11926.7 | 12179.9 | 11100.6 | 12045.1 | 10704.2 | 10432.6 | 12120.1 | 10829.4 | 12048.5 | 10578.3 | 12114.8 | 10755.5 | 11966.3 | 11107.9 | 11855.6 | 11239.6 | 12244.1 | 11100.9 | 11575.8 | 11011.2 | 9746.1 | 11474.8 | 11070.8 | 10361.5 | 11784.2 | 11469.6 | 10647.3 | 10517 | 11563.9 | 10324.9 | 10698.1 | 11534.5 | 10200.1 | 11604.8 | 10222.2 | 11345 | 10498 | 11486.2 | 9989.9 | 11542.5 | 10507.7 | 11456.5 | 10532.8 | 11527.4 | 10706.9 | 10261.8 | 11281.5 | 10248.6 | 10077.1 | 11346.9 | 11227.6 | 11303.5 | 10454 | 12011.3 | 10716.9 | 11610 | 11021.6 | 11599.5 | 10197.6 | 11782.4 | 10825.4 | 10877.5 | 11043 | 10871.4 | 9424.5 | 10815.5 | 9613.7 | 10826.6 | 10843.2 | 12308.3 | 10838.9 | 12323.7 | 11123.6 | 12172.6 | 10929.2 | 11091.4 | 10848.8 | 12040.7 | 12349.4 | 12125.6 | 12200.8 | 12259.8 | 12274.5 | 11224 | 12255.9 | 12218.9 | 12334.2 | 12370.4 | 12353.4 | 12382.7 | 11312 | 12284.1 | 11326.2 | 23.6805 | 23.3362 | 23.2095 | 0 | 23.4704 | 23.1346 | 0 | 38.6655 | 0 | 0 | 0 | 0 | 1.9142 | 1.9068 | 1.8531 | 1.9465 | 1.8656 | 1.8274 | 3.609 | 3.881 | 3.912 | 4.498 | 4.026 | 4.09 | 5.0541 | 5.3697 | 5.1316 | 5.0021 | 5.5254 | 5.7985 | 1.0715 | 1.2947 | 1.3317 | 0 | 1.3259 | 1.1742 | 6.2403 | 6.2096 | 6.1289 | 5.8727 | 6.293 | 6.2307 | 1.0794 | 1.254 | 1.2314 | 0 | 1.3193 | 1.4759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 237291 | 433 | 227683 | 447 | 441447.168 | 1167.133 | 5.0541 | 5.3697 | 5.1316 | 5.0021 | 5.5254 | 5.7985 | 6.2403 | 6.2096 | 6.1289 | 5.8727 | 6.293 | 6.2307 | 918000 | 1000 | 893000 | 2000 | 1803534 | 4733 | 1808000 | 1798801 | 11.2667 | 5.3136 | 1.2396 | 6.1625 | 1.272 | 23.33% | 20.64% | 23.3663 | 38.6655 | 1.8856 | 4.0027 | 1820092.3 | 1803267 | 2015306.7574 | 89.48%
2023-02-08 | 2023 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 334767.775 | 7:18 | 18:33 | 11180.1 | 11624.8 | 11553.6 | 11549.1 | 11542.7 | 11701.5 | 11568.1 | 11864.3 | 11552.1 | 11441.9 | 11464.9 | 11613.1 | 11617.9 | 11564.3 | 11514.6 | 11713.2 | 11595.7 | 11678.7 | 11694.4 | 11676.2 | 11567.1 | 11675.1 | 11324.8 | 11622.1 | 11543.1 | 10270.2 | 11621.6 | 11479.7 | 11756.4 | 11606.5 | 11512.6 | 11692.6 | 10778.7 | 10785.4 | 10847.8 | 10816.3 | 10925 | 10852.3 | 10809.3 | 10793.7 | 11871.5 | 10835.4 | 11728.9 | 10704.2 | 11268.6 | 12380.3 | 10668.9 | 11821.5 | 10923.5 | 11177.3 | 11793.1 | 11167.1 | 12092.6 | 10841.4 | 12085.4 | 10971.5 | 10871.9 | 11916.8 | 10909.7 | 12118.4 | 12068.3 | 10728.6 | 11694.2 | 11156.6 | 11469 | 10885.2 | 11517.4 | 11946.6 | 12190.3 | 11149 | 12053 | 10761.8 | 10493.4 | 12128.9 | 10893 | 12052.7 | 10633 | 12127.9 | 10820.4 | 11969.1 | 10633.2 | 11318.5 | 10749.7 | 11711.9 | 10622.7 | 11069.8 | 10532.9 | 9353.4 | 11929.9 | 11560.6 | 10858.2 | 12262.4 | 11938 | 11131.5 | 11023 | 12009.4 | 10865.3 | 11267.6 | 12101.3 | 10772.9 | 12170.2 | 10807.7 | 11929.3 | 11078.3 | 12025.1 | 10523.6 | 12098.8 | 11073.6 | 11991.8 | 11050.2 | 12049 | 11221.7 | 10880.2 | 11902.5 | 10984.8 | 10805.1 | 11944.8 | 11808.6 | 11890.3 | 11026.2 | 12032.9 | 10790.1 | 11667.7 | 11091.1 | 11648.5 | 10290 | 11819.3 | 10905.7 | 10940.9 | 11074 | 10934.7 | 9480.3 | 10947.8 | 9692.3 | 10926.4 | 10920 | 12301.4 | 10909.5 | 12316.1 | 11174.2 | 12173.6 | 10991.8 | 11158 | 10911 | 12032.9 | 12324.8 | 12123.2 | 12187.4 | 12240.4 | 12270.6 | 11260 | 12246 | 12202.2 | 12315.2 | 12344.5 | 12334.6 | 12357.3 | 11336.2 | 12284 | 11375.4 | 25.7043 | 25.8226 | 25.9492 | 0 | 25.7466 | 26.1163 | 0 | 39.5755 | 0 | 0 | 0 | 0 | 3.856 | 4.1569 | 3.8383 | 4.0292 | 3.9868 | 3.9294 | 7.852 | 7.861 | 8.089 | 7.567 | 7.851 | 7.774 | 5.1054 | 5.4562 | 5.1702 | 5.0655 | 5.5982 | 5.8514 | 1.0888 | 1.3299 | 1.3519 | 0 | 1.364 | 1.1977 | 6.2949 | 6.2899 | 6.1664 | 5.9201 | 6.3575 | 6.3072 | 1.1029 | 1.2868 | 1.2534 | 0 | 1.3524 | 1.5075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 238200 | 435 | 228592 | 449 | 443256.901 | 1171.933 | 5.1054 | 5.4562 | 5.1702 | 5.0655 | 5.5982 | 5.8514 | 6.2949 | 6.2899 | 6.1664 | 5.9201 | 6.3575 | 6.3072 | 909000 | 2000 | 909000 | 2000 | 1809733 | 4800 | 1814000 | 1804933 | 11.25 | 5.3745 | 1.2664 | 6.2227 | 1.3006 | 23.56% | 20.9% | 25.8678 | 39.5755 | 3.9661 | 7.8323 | 1826183.9 | 1809733 | 2033561.1171 | 88.99%
2023-02-09 | 2023 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 334767.775 | 7:18 | 18:39 | 11203.9 | 11577.5 | 11502.8 | 11520.3 | 11493.3 | 11640.9 | 11512.8 | 11754.4 | 11479 | 11401.6 | 11439.2 | 11562.1 | 11587.7 | 11524 | 11513.6 | 11686.5 | 11572.2 | 11648.3 | 11639.7 | 11629.4 | 11529.7 | 11622.3 | 11359.6 | 11590.9 | 11511.2 | 10378.6 | 11587.3 | 11464.3 | 11687.5 | 11548.2 | 11485.4 | 11627.7 | 11697.7 | 11698.2 | 11693.2 | 11652.2 | 11755.3 | 11685.3 | 11639.5 | 11633.1 | 12225.2 | 11371.6 | 12083.9 | 11254.8 | 11733.8 | 12695.1 | 11163.9 | 12140.5 | 11016.4 | 11240.1 | 11748.8 | 11221.6 | 11998.2 | 10920.8 | 11989.2 | 11062.4 | 10966.3 | 11848.7 | 11020.7 | 12023.1 | 11970.4 | 10846 | 11617.5 | 11165.3 | 11467.2 | 10971.5 | 11514.5 | 11858.3 | 12050.6 | 11192.7 | 11964.7 | 10877.7 | 10630.4 | 12031.3 | 10991.6 | 11954.8 | 10759.3 | 12025.1 | 10931 | 11870.8 | 11203.6 | 11786.3 | 11301.5 | 12122.9 | 11198.3 | 11589.3 | 11091.3 | 9930.1 | 11829.9 | 11525.5 | 10938.6 | 12120.7 | 11827.1 | 11166.8 | 11071.1 | 11880.7 | 10929.2 | 11312 | 11973.3 | 10871.6 | 12025.9 | 10896 | 11841.9 | 11143.7 | 11880.8 | 10622.6 | 11968.8 | 11131.1 | 11890.1 | 11100.6 | 11928.3 | 11273.6 | 10957.3 | 11799.7 | 11042.2 | 10897.6 | 11841.7 | 11713.2 | 11786.7 | 11073.5 | 11906.1 | 10878.2 | 11611.1 | 11142.6 | 11610 | 10392.2 | 11750 | 10993.1 | 11027.1 | 11123.8 | 11038.8 | 9578.3 | 10997.4 | 9762.5 | 11022.2 | 11005.2 | 12162.9 | 10999.3 | 12174.5 | 11233.3 | 12081.9 | 11070.3 | 11217.3 | 10987.1 | 11957.5 | 12188 | 12034.1 | 12081.5 | 12129.3 | 12156.7 | 11313 | 12127.3 | 12112.2 | 12191.6 | 12212.3 | 12212.8 | 12242.3 | 11386.2 | 12186.8 | 11425.3 | 22.88 | 23.29 | 23.1 | 0 | 23.26 | 22.96 | 0 | 37.94 | 0 | 0 | 0 | 0 | 4.58 | 4.84 | 4.86 | 4.68 | 4.97 | 4.83 | 10.63 | 10.15 | 11.39 | 10.43 | 9.86 | 10.77 | 5.14 | 5.5 | 5.22 | 5.11 | 5.54 | 5.89 | 1.1 | 1.34 | 1.37 | 0 | 1.38 | 1.21 | 6.3288 | 6.3173 | 6.2002 | 5.9814 | 5.2209 | 6.3689 | 1.12 | 1.3135 | 1.275 | 0 | 1.3721 | 1.5368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239117 | 436 | 229503 | 451 | 445078.501 | 1176.667 | 5.14 | 5.5 | 5.22 | 5.11 | 5.54 | 5.89 | 6.3288 | 6.3173 | 6.2002 | 5.9814 | 5.2209 | 6.3689 | 917000 | 1000 | 911000 | 2000 | 1821600 | 4734 | 1825000 | 1816866 | 11.35 | 5.4 | 1.28 | 6.0696 | 1.3235 | 23.7% | 21.81% | 23.098 | 37.94 | 4.7933 | 10.5383 | 1838359.4 | 1821600 | 2051343.2695 | 88.8%
2023-02-10 | 2023 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 334767.775 | 7:16 | 18:42 | 10878.6 | 11258.4 | 11196.9 | 11206.9 | 11184.6 | 11341.2 | 11201 | 11464 | 11245.6 | 11112.5 | 11122.8 | 11263.3 | 11269 | 11219.3 | 11212.1 | 11376.1 | 11270.9 | 11340.6 | 11322.4 | 11315.4 | 11207.3 | 11304.9 | 11026.3 | 11266.8 | 11181.2 | 9981.5 | 11261.1 | 11126.3 | 11366.5 | 11241 | 11188 | 11333.7 | 11402.5 | 11403 | 11382.2 | 11340 | 11443.9 | 11368.4 | 11336.7 | 11336.7 | 11980.7 | 11039.2 | 11848.4 | 10903.3 | 11425.2 | 12467.3 | 10848.4 | 11916.9 | 10637.7 | 10886.1 | 11437 | 10872.6 | 11719.7 | 10543.2 | 11705.3 | 10701 | 10591.8 | 11784.3 | 10638.6 | 11747.3 | 11717.1 | 10466.3 | 11418.4 | 10842.5 | 11158.1 | 10588.8 | 11196.6 | 11539.9 | 11690 | 10820.3 | 11645.5 | 10453.2 | 10749.3 | 11718.4 | 10632 | 11643.7 | 10343.7 | 11762.4 | 10557.9 | 11585.3 | 10821.9 | 11452.4 | 10914.9 | 11811.5 | 10806 | 11220 | 10734.2 | 9529.2 | 11566.9 | 11204.1 | 10574.1 | 11873.8 | 11554.3 | 10837.9 | 10736.9 | 11632.8 | 10567.2 | 10994.1 | 11729.6 | 10514.7 | 11774.5 | 10533.4 | 11562.7 | 10800.9 | 11647 | 10250.2 | 11720.4 | 10791.7 | 11626.7 | 10767.5 | 11682.6 | 10935.7 | 10613.9 | 11532.2 | 10704.1 | 10518.4 | 11587 | 11438.6 | 11519.7 | 10732.4 | 11642.9 | 10492 | 11335.7 | 10797.7 | 11315.3 | 9999 | 11457.4 | 10609.6 | 10661.9 | 10811.2 | 10674.8 | 9242.3 | 10642.5 | 9393.3 | 10571.7 | 10565.1 | 11801.3 | 10568.1 | 11814.8 | 10811.8 | 11730.2 | 10653.1 | 10802.1 | 10575.4 | 11573.1 | 11846.1 | 11631.2 | 11696.7 | 11739.7 | 11779 | 10887.2 | 11756 | 11734.5 | 11834.6 | 11882 | 11870.6 | 11889.7 | 10977.1 | 11777.9 | 10991.4 | 22.17 | 22.5 | 22.31 | 0 | 22.39 | 21.82 | 0 | 36.83 | 0 | 0 | 0 | 0 | 4.25 | 4.41 | 4.35 | 4.13 | 4.33 | 4.1 | 8.73 | 7.62 | 7.48 | 8.08 | 8.49 | 8.37 | 4.9822 | 5.3317 | 5.0478 | 4.9561 | 5.4413 | 5.6228 | 1.0633 | 1.3085 | 1.3167 | 0 | 1.3446 | 1.1698 | 6.0831 | 6.0845 | 5.9565 | 5.7433 | 6.2186 | 6.0832 | 1.0752 | 1.2744 | 1.2223 | 0 | 1.3377 | 1.4724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240011 | 438 | 230386 | 452 | 446847.702 | 1181.4 | 4.9822 | 5.3317 | 5.0478 | 4.9561 | 5.4413 | 5.6228 | 6.0831 | 6.0845 | 5.9565 | 5.7433 | 6.2186 | 6.0832 | 894000 | 2000 | 883000 | 1000 | 1769201 | 4733 | 1774000 | 1764468 | 11.4333 | 5.2303 | 1.2406 | 6.0282 | 1.2764 | 23.72% | 21.17% | 22.238 | 36.83 | 4.2617 | 8.1283 | 1786175.1 | 1769134 | 1983344.8967 | 89.2%
2023-02-11 | 2023 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 334767.775 | 7:17 | 18:39 | 10528.9 | 10926.8 | 10883.7 | 10893 | 10851.7 | 11023.3 | 10861.7 | 11132.9 | 10885.8 | 10750.8 | 10808.5 | 10940.6 | 10977.8 | 10918.2 | 10913.7 | 11103.3 | 10977.9 | 11054.1 | 11050.3 | 11026.8 | 10931.1 | 11026.7 | 10726.5 | 10996.7 | 10917.5 | 9683.5 | 10989.8 | 10853.4 | 11114.4 | 10963.9 | 10922.6 | 11093.6 | 11128 | 11152.8 | 11121.9 | 11080.6 | 11179.7 | 11116.9 | 11071.6 | 11056.1 | 11760.1 | 10796.9 | 11607.3 | 10625.3 | 11144.4 | 12229.3 | 10563.3 | 11670.4 | 10290 | 10548.6 | 11148.3 | 10513.9 | 11429.6 | 10180.5 | 11424.4 | 10348.9 | 10235.4 | 11484.4 | 10285.8 | 11465.5 | 11435.4 | 10118.6 | 11089.5 | 10458.4 | 10819.7 | 10245.7 | 10887.7 | 11293.5 | 11405.7 | 10532.3 | 11394.7 | 10158.8 | 10397.7 | 11584 | 10289 | 11459.4 | 10025.7 | 11490.7 | 10206.1 | 11318.8 | 10554.4 | 11196.1 | 10683.3 | 11598.4 | 10544.6 | 11058.1 | 10482.6 | 9281.3 | 11323.7 | 10976.9 | 10270.3 | 11627.1 | 11309.4 | 10522.1 | 10397.8 | 11386.6 | 10263.8 | 10713.6 | 11477 | 10202.8 | 11531.9 | 10237.5 | 11304.5 | 10501.6 | 11392.3 | 9949.8 | 11462.1 | 10493.8 | 11363.4 | 10465.9 | 11417.4 | 10615.6 | 10295.9 | 11274.1 | 10392.3 | 10200.2 | 11320.5 | 11178.8 | 11248.8 | 10448.1 | 11382.3 | 10189.8 | 11058.4 | 10472.1 | 11017.4 | 9706.6 | 11198.6 | 10301.3 | 10347.3 | 10500.5 | 10340.4 | 8960.2 | 10358 | 9169 | 10298.5 | 10326.3 | 11664.3 | 10345.6 | 11673.4 | 10593.8 | 11568.7 | 10404.6 | 10560.9 | 10328.5 | 11410.8 | 11687.3 | 11498.3 | 11568.6 | 11615.2 | 11648.1 | 10695.6 | 11608.8 | 11607.4 | 11675.2 | 11724.5 | 11709.6 | 11720.2 | 10753.1 | 11646.3 | 10773.1 | 25.104 | 24.9022 | 24.7296 | 0 | 24.878 | 24.9312 | 0 | 36.6094 | 0 | 0 | 0 | 0 | 3.0415 | 2.956 | 3.0255 | 3.0922 | 2.9715 | 2.8738 | 6.315 | 6.394 | 6.715 | 6.33 | 6.375 | 6.369 | 4.9102 | 5.23 | 4.9456 | 4.8419 | 5.3224 | 5.5677 | 1.0374 | 1.3 | 1.2737 | 0 | 1.3309 | 1.1726 | 5.9382 | 5.965 | 5.8053 | 5.5459 | 6.0561 | 6.0337 | 1.0508 | 1.2651 | 1.1915 | 0 | 1.334 | 1.4694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240880 | 440 | 231250 | 454 | 448574.235 | 1186.2 | 4.9102 | 5.23 | 4.9456 | 4.8419 | 5.3224 | 5.5677 | 5.9382 | 5.965 | 5.8053 | 5.5459 | 6.0561 | 6.0337 | 869000 | 2000 | 864000 | 2000 | 1726533 | 4800 | 1729000 | 1721733 | 11.3667 | 5.1363 | 1.2229 | 5.8907 | 1.2622 | 23.81% | 21.43% | 24.909 | 36.6094 | 2.9934 | 6.4163 | 1743073.8 | 1726333 | 1932217.3287 | 89.34%
2023-02-12 | 2023 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 334767.775 | 7:15 | 18:41 | 11734.9 | 12035.8 | 11965.6 | 12001.7 | 11943.3 | 12105.9 | 11971.4 | 12157.6 | 11964.1 | 11865.5 | 11906.4 | 12021.8 | 12082.4 | 12000 | 12061.3 | 12188.5 | 12064.7 | 12128.4 | 12110.3 | 12100.2 | 12004.6 | 12096.7 | 11915.3 | 12092.9 | 12007 | 11120.2 | 12095.8 | 11978.9 | 12166.8 | 12021.4 | 12014 | 12097.9 | 12180.5 | 12174.3 | 12171.1 | 12144.2 | 12219.4 | 12180.8 | 12137.4 | 12122.4 | 12697.9 | 11972.8 | 12543.9 | 11860.6 | 12270.8 | 13120.8 | 11762.3 | 12610.9 | 11622.4 | 11812.3 | 12238.1 | 11768.1 | 12473.1 | 11531.9 | 12460.7 | 11690 | 11585 | 12500.9 | 11648.9 | 12485.9 | 12454.2 | 11492.4 | 12164 | 11710.1 | 11979.7 | 11595.1 | 12046.6 | 12360.5 | 12413.8 | 11777 | 12406.3 | 11554.9 | 11666.6 | 12574.4 | 11589 | 12456 | 11420.8 | 12468.9 | 11542.7 | 12330.4 | 11832.2 | 12291.8 | 11911.8 | 12620.8 | 11819.7 | 12199.6 | 11698.9 | 10697.4 | 12361.1 | 12079 | 11622.6 | 12621 | 12363.2 | 11804.4 | 11689.5 | 12383.9 | 11610.7 | 11891.6 | 12450.8 | 11515.5 | 12534.9 | 11560.1 | 12379.2 | 11780.7 | 12383.5 | 11359 | 12478.3 | 11756.6 | 12423.6 | 11743.2 | 12445.9 | 11913.1 | 11569.7 | 12300.9 | 11651.9 | 11559.3 | 12354.3 | 12229.7 | 12291.9 | 11710.8 | 12402.3 | 11573.8 | 12149.2 | 11794 | 12142.4 | 11212.5 | 12295.2 | 11678.7 | 11665.8 | 11718.1 | 11680.8 | 10345.5 | 11624.1 | 10580.4 | 11654 | 11647.5 | 12608.6 | 11608 | 12597.1 | 11794 | 12505.4 | 11614.8 | 11727.5 | 11614.7 | 12449.6 | 12640.9 | 12532.2 | 12556.4 | 12600.5 | 12611.8 | 11871.7 | 12575.1 | 12592 | 12634.1 | 12650.7 | 12651.5 | 12678.9 | 11945.2 | 12663.8 | 11987.5 | 19.02 | 18.8 | 18.74 | 0 | 18.22 | 18.15 | 0 | 32.9 | 0 | 0 | 0 | 0 | 3.48 | 3.29 | 3.43 | 4.68 | 3.18 | 3.22 | 7.56 | 8.34 | 7.7 | 7.911 | 7.93 | 8.016 | 5.5802 | 5.9533 | 5.6244 | 5.5176 | 6.0736 | 6.4081 | 1.2283 | 1.5026 | 1.5065 | 0 | 1.522 | 1.3473 | 6.8335 | 6.847 | 6.679 | 6.4002 | 6.9043 | 6.9108 | 1.2337 | 1.4629 | 1.3939 | 0 | 1.5096 | 1.6922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 241840 | 441 | 232206 | 456 | 450480.835 | 1190.933 | 5.5802 | 5.9533 | 5.6244 | 5.5176 | 6.0736 | 6.4081 | 6.8335 | 6.847 | 6.679 | 6.4002 | 6.9043 | 6.9108 | 960000 | 1000 | 956000 | 2000 | 1906600 | 4733 | 1913000 | 1901867 | 11.4333 | 5.8596 | 1.4214 | 6.7625 | 1.4585 | 24.26% | 21.57% | 18.586 | 32.9 | 3.5467 | 7.9095 | 1925780.5 | 1906534 | 2229437.2681 | 85.52%
2023-02-13 | 2023 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 334767.775 | 7:13 | 18:46 | 11553.1 | 11846.8 | 11818.1 | 11844.8 | 11813.4 | 11931.6 | 11757.7 | 11950.7 | 11841.1 | 11642.8 | 11737.5 | 11848.5 | 11922.9 | 11830.3 | 11886.9 | 12031.4 | 11871.3 | 11969.1 | 11960.9 | 11932.2 | 11854.7 | 11945.5 | 11737.2 | 11934 | 11861 | 10894.5 | 11940.5 | 11816.9 | 12001.5 | 11837.6 | 11849.8 | 11979.1 | 12017.9 | 12030.7 | 12028.3 | 11993.8 | 12071.1 | 12022.7 | 11971.6 | 11958.4 | 12512.5 | 11751.5 | 12369.9 | 11636.3 | 12071.4 | 12954.9 | 11537.3 | 12436.4 | 11443.4 | 11633 | 12087.7 | 11589 | 12303.3 | 11310.1 | 12301.7 | 11484 | 11393.7 | 12340.6 | 11459.8 | 12342.4 | 12310.8 | 11298.8 | 11978.2 | 11487.9 | 11806.4 | 11398.5 | 11883.3 | 12199.3 | 12261.5 | 11605.8 | 12250 | 11346.5 | 11493.5 | 12417 | 11411.9 | 12311.3 | 11211.4 | 12326.9 | 11348.6 | 12179.5 | 11643.2 | 12117.7 | 11721.4 | 12456.3 | 11619.4 | 12010.1 | 11500.7 | 10358.5 | 12189.4 | 11898.9 | 11412.6 | 12441.9 | 12153.2 | 11559.7 | 11445.8 | 12220.8 | 11374 | 11705.1 | 12293 | 11329.2 | 12364.5 | 11359.1 | 12206.9 | 11580.8 | 12227.5 | 11141.2 | 12318.1 | 11574.1 | 12248.7 | 11535.9 | 12261.7 | 11708.4 | 11391.5 | 12134.2 | 11467.9 | 11358 | 12188 | 12065.3 | 12136.6 | 11526 | 12246.7 | 11365.6 | 11983.9 | 11592.7 | 11983.1 | 10945.5 | 12134.2 | 11481.2 | 11483.6 | 11557.4 | 11504.3 | 10094.4 | 11406.3 | 10248.3 | 11459.1 | 11464.5 | 12498.8 | 11452.7 | 12501.6 | 11660.6 | 12394.9 | 11491.7 | 11610.3 | 11437.8 | 12325.7 | 12536.2 | 12382 | 12428.9 | 12476.3 | 12478.3 | 11733.9 | 12463.8 | 12427.2 | 12498.8 | 12539.8 | 12538.2 | 12575.5 | 11807 | 12515.2 | 11825.6 | 17.2 | 17.4 | 17.39 | 0 | 17.2 | 17.06 | 0 | 36.87 | 0 | 0 | 0 | 0 | 2.16 | 2.1 | 2.22 | 2.15 | 2.15 | 2.11 | 4.38 | 4.58 | 4.25 | 4.43 | 4.6 | 4.7 | 5.5145 | 5.8747 | 6.6144 | 5.4752 | 6.045 | 6.3327 | 1.2214 | 1.4433 | 1.4036 | 0 | 1.406 | 1.2993 | 6.7253 | 6.7102 | 6.6144 | 6.4015 | 6.749 | 6.8562 | 1.2367 | 1.3994 | 1.4036 | 0 | 1.3956 | 1.6373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242785 | 443 | 233148 | 458 | 452360.369 | 1195.6 | 5.5145 | 5.8747 | 6.6144 | 5.4752 | 6.045 | 6.3327 | 6.7253 | 6.7102 | 6.6144 | 6.4015 | 6.749 | 6.8562 | 945000 | 2000 | 942000 | 2000 | 1879534 | 4667 | 1883000 | 1874867 | 11.55 | 5.9761 | 1.3547 | 6.6761 | 1.4145 | 22.67% | 21.19% | 17.25 | 36.87 | 2.1483 | 4.49 | 1898020.8 | 1879400 | 2187365.4014 | 85.92%
2023-02-14 | 2023 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 334767.775 | 7:13 | 18:45 | 11614.5 | 11910.5 | 11952 | 11964.4 | 11985.4 | 12082.5 | 11893.9 | 12051.2 | 11925.1 | 11692.5 | 11830.5 | 11938.5 | 12030.8 | 11929.9 | 11964.6 | 12144.2 | 11974.9 | 12089.4 | 11974.7 | 10978.8 | 11963 | 12052.9 | 11831.8 | 12056.1 | 11964.3 | 10850.3 | 12034.9 | 11912.9 | 12120.5 | 11943.7 | 11971.9 | 12111.9 | 12147.1 | 12167.8 | 12157.2 | 12123.2 | 12217.5 | 12160.2 | 12108.4 | 12091.2 | 12676.5 | 11841.7 | 12533.3 | 11706.8 | 12182.5 | 13128.1 | 11605.3 | 12593.1 | 11485.4 | 11690.7 | 12200.2 | 11638.5 | 12429 | 11324.8 | 12439.1 | 11521.8 | 11427.1 | 12474 | 11497.4 | 12480.3 | 12445.6 | 11326.4 | 12066.2 | 11523 | 11890 | 11459.5 | 11984.9 | 12348.1 | 12413.3 | 11689.1 | 12409.4 | 11384.7 | 11552.4 | 12588.8 | 11467.8 | 12467.2 | 11235.2 | 12480.3 | 11381.7 | 12308.1 | 11723.6 | 12250.9 | 11809.6 | 12623 | 11726.2 | 12150 | 11578.7 | 10322.3 | 12315.8 | 12017.9 | 11462.3 | 12598.1 | 12285.7 | 11615.2 | 11485.4 | 12399.8 | 11430.1 | 11801.4 | 12455 | 11372.8 | 12527.8 | 11415.2 | 12348.3 | 11645.8 | 12389.1 | 11159.4 | 12476.4 | 11648.6 | 12394.4 | 11615.9 | 12420.5 | 11784.2 | 11434 | 12258.4 | 11527.8 | 11388.3 | 12318.5 | 12186.4 | 12266 | 11589.7 | 12396.2 | 11408 | 12114.7 | 11670.9 | 12099.1 | 10904 | 12260.9 | 11519.4 | 11545 | 11642.4 | 11535.5 | 10043.4 | 11490.9 | 10217.7 | 11440.2 | 11453.7 | 12653.5 | 11503.2 | 12647.7 | 11711.9 | 12538.3 | 11539.7 | 11652 | 11412.1 | 12441 | 12682.9 | 12507 | 12568.8 | 12621 | 12622.9 | 11794.8 | 12594.5 | 12535.4 | 12609.8 | 12678.5 | 12685.1 | 12708.6 | 11870.1 | 12636.8 | 11879.8 | 19.73 | 20.51 | 21.43 | 0 | 20.13 | 20.54 | 0 | 41.44 | 0 | 0 | 0 | 0 | 2.09 | 2.174 | 2.18 | 2.07 | 2.24 | 2.29 | 4.2 | 5.22 | 5 | 4.8 | 4.51 | 4.46 | 5.5819 | 5.9545 | 5.6255 | 5.5295 | 6.1209 | 6.4092 | 1.2106 | 1.4822 | 1.4943 | 0 | 1.4576 | 1.3262 | 6.7956 | 6.8144 | 6.6514 | 6.4104 | 6.8866 | 6.9314 | 1.2264 | 1.4359 | 1.389 | 0 | 1.4496 | 1.6668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243739 | 444 | 234098 | 459 | 454255.302 | 1200.333 | 5.5819 | 5.9545 | 5.6255 | 5.5295 | 6.1209 | 6.4092 | 6.7956 | 6.8144 | 6.6514 | 6.4104 | 6.8866 | 6.9314 | 954000 | 1000 | 950000 | 1000 | 1894933 | 4733 | 1902000 | 1890200 | 11.5333 | 5.8702 | 1.3942 | 6.7483 | 1.4335 | 23.75% | 21.24% | 20.468 | 41.44 | 2.174 | 4.6983 | 1912268.3 | 1894734 | 2174415.5557 | 87.14%
2023-02-15 | 2023 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 334767.775 | 7:14 | 18:40 | 11573.9 | 11913 | 11937.1 | 11935.5 | 11994.7 | 12064.3 | 11931.2 | 12041.5 | 11839.5 | 11629.7 | 11771.8 | 11883 | 11990.3 | 11880.4 | 11913.3 | 12105.1 | 11928.6 | 12044.7 | 12033 | 6270.9 | 11909.9 | 12008.2 | 11764.4 | 12002.9 | 11912.7 | 10754.2 | 11984.3 | 11864.5 | 12069.5 | 11877 | 11908 | 12058.9 | 12084.5 | 12111.7 | 12117.8 | 12072.2 | 12165.6 | 12094.1 | 12044.4 | 12035.2 | 12660.5 | 11795.9 | 12500.7 | 11637.3 | 12141.2 | 13139.5 | 11535.7 | 12573.9 | 11408.5 | 11623 | 12156.1 | 11566.9 | 12397.9 | 11231.5 | 12404.1 | 11444.5 | 11347.7 | 12435 | 11412.9 | 12446.6 | 12403.5 | 11242.2 | 12002.4 | 11436.6 | 11829.4 | 11370.8 | 11924.2 | 12300.1 | 12372.8 | 11614 | 12372.9 | 11298.8 | 11479.5 | 12563.7 | 11397.6 | 12434.8 | 11166 | 12453.2 | 11317.5 | 12276.2 | 11650.8 | 12195.5 | 11741.8 | 12586.2 | 11639.8 | 12083.7 | 11499.4 | 10217.4 | 12246.5 | 11950.3 | 11365.9 | 12547.5 | 12229.9 | 11539 | 11417.4 | 12329.8 | 11364 | 11717.5 | 12412.8 | 11272.9 | 12469.9 | 11331.3 | 12287 | 11569 | 12327.2 | 11046.4 | 12412.3 | 11564 | 12332.8 | 11525.7 | 12365.9 | 11698.8 | 11331.8 | 12198.9 | 11436.3 | 11283 | 12256 | 12134.3 | 12210.8 | 11511.7 | 12347.1 | 11312.1 | 12043.7 | 11576.9 | 12017.6 | 10794.6 | 12202.2 | 11421.9 | 11437.8 | 11530.2 | 11424.5 | 9933.9 | 11430.6 | 10175.2 | 11336.4 | 11355.7 | 12623.4 | 11420.3 | 12646.8 | 11669.4 | 12500.8 | 11462.5 | 11583.7 | 11327.1 | 12414.2 | 12677.9 | 12465.3 | 12540.2 | 12597.3 | 12604.7 | 11767 | 12595.5 | 12507.1 | 12600.7 | 12656.7 | 12662.1 | 12688.1 | 11814.3 | 12599.2 | 11826.7 | 29.5381 | 29.2956 | 29.4793 | 0 | 29.9301 | 29.5074 | 0 | 45.6786 | 0 | 0 | 0 | 0 | 2.4422 | 2.4497 | 2.4397 | 2.3581 | 2.53 | 2.5217 | 5.195 | 4.643 | 4.539 | 4.493 | 4.907 | 5.528 | 5.5746 | 5.9647 | 5.6134 | 5.5106 | 6.1187 | 6.3941 | 1.1711 | 1.446 | 1.4529 | 0 | 1.4307 | 1.3062 | 6.78 | 6.8143 | 6.6297 | 6.3932 | 6.877 | 6.9214 | 1.1865 | 1.3994 | 1.3508 | 0 | 1.4205 | 1.6436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244688 | 446 | 235042 | 461 | 456141.236 | 1205 | 5.5746 | 5.9647 | 5.6134 | 5.5106 | 6.1187 | 6.3941 | 6.78 | 6.8143 | 6.6297 | 6.3932 | 6.877 | 6.9214 | 949000 | 2000 | 944000 | 2000 | 1885934 | 4667 | 1889000 | 1881267 | 11.4333 | 5.8627 | 1.3614 | 6.7359 | 1.4002 | 23.22% | 20.79% | 29.5501 | 45.6786 | 2.4569 | 4.8842 | 1898529.7 | 1885800 | 2144927.5345 | 87.92%
2023-02-16 | 2023 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 334767.775 | 7:08 | 18:47 | 10643.8 | 10984.5 | 10983.6 | 10966.7 | 11052.3 | 11107.1 | 10996.2 | 11064.6 | 10907.7 | 10725.6 | 10815.9 | 10910.7 | 11009.5 | 10906.4 | 10937.9 | 11110.8 | 10954.1 | 11057.9 | 11040.3 | 11066.8 | 10946.5 | 11028 | 10822.2 | 11028.8 | 10941.9 | 9917 | 11001.5 | 10890.1 | 11090.9 | 10928.9 | 10969.1 | 11092 | 11109.8 | 11114.5 | 11126.1 | 10918.4 | 11124.7 | 11111.9 | 11069.1 | 11075.1 | 11622.6 | 10878.8 | 11504.1 | 10733.5 | 11164.1 | 11988.3 | 10654.3 | 11552.5 | 10479.2 | 10678.3 | 11162.6 | 10632.2 | 11377.4 | 10332.7 | 11380.2 | 10536.7 | 10433.5 | 11397.2 | 10488.5 | 11405.5 | 11357.2 | 10327.2 | 11010.1 | 10502.1 | 10875.9 | 10471.1 | 10958.4 | 11288.4 | 11357.8 | 10671.2 | 11353.9 | 10386.2 | 10560.8 | 11512.7 | 10477.6 | 11393.5 | 10263.4 | 11422.2 | 10406.6 | 11266.8 | 10712.2 | 11202.5 | 10796.3 | 11541.4 | 10782.9 | 11179.6 | 10600.3 | 9468 | 11260.8 | 11011.4 | 10467.9 | 11536.1 | 11287.8 | 10684.4 | 10579 | 11342.7 | 10487.3 | 10811 | 11449.9 | 10416.8 | 11507.5 | 10487.4 | 11347.7 | 10695.4 | 11377.8 | 10239 | 11459.4 | 10694.5 | 11381 | 10654.6 | 11418.7 | 10822.9 | 10467.9 | 11269 | 10579.9 | 10443.5 | 11352.2 | 11215.9 | 11300.8 | 10670.7 | 11413.5 | 10487.9 | 11153.1 | 10709.4 | 11132.4 | 10060.5 | 11301.3 | 10602.2 | 10590.9 | 10676.7 | 10591.1 | 9235.4 | 10576.2 | 9453 | 10584.9 | 10582.6 | 11660.7 | 10596 | 11673.2 | 10804.4 | 11570.2 | 10633.9 | 10689.6 | 10502.9 | 11483.6 | 11705.5 | 11547.9 | 11607.2 | 11628.2 | 11631.7 | 10888.3 | 11634.2 | 11582.8 | 11607.5 | 11676.2 | 11644.1 | 11722.3 | 10935.9 | 11653.9 | 10924.6 | 29.9854 | 29.7884 | 29.9117 | 0 | 29.8946 | 29.8713 | 0 | 43.9025 | 0 | 0 | 0 | 0 | 2.7956 | 2.8438 | 2.7031 | 2.863 | 2.7816 | 2.8003 | 5.91 | 6.073 | 7.727 | 6.465 | 6.704 | 6.737 | 5.2945 | 5.6243 | 5.3534 | 5.2471 | 5.7653 | 5.8879 | 1.1286 | 1.3981 | 1.3963 | 0 | 1.389 | 1.2705 | 6.227 | 6.2442 | 6.1309 | 5.9326 | 6.4058 | 6.465 | 1.1582 | 1.3573 | 1.3212 | 0 | 1.3887 | 1.5917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245560 | 448 | 235915 | 463 | 457879.369 | 1209.667 | 5.2945 | 5.6243 | 5.3534 | 5.2471 | 5.7653 | 5.8879 | 6.227 | 6.2442 | 6.1309 | 5.9326 | 6.4058 | 6.465 | 872000 | 2000 | 873000 | 2000 | 1738133 | 4667 | 1741000 | 1733466 | 11.65 | 5.5288 | 1.3165 | 6.2342 | 1.3634 | 23.81% | 21.87% | 29.8903 | 43.9025 | 2.7979 | 6.6027 | 1754974.2 | 1737667 | 1984936.5697 | 87.54%
2023-02-17 | 2023 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 334767.775 | 7:13 | 18:42 | 11757.9 | 12111.7 | 12120.4 | 12119.9 | 12168.3 | 12243.6 | 12165.8 | 12171.1 | 12001.7 | 11811.2 | 11909.1 | 12013.3 | 12132.3 | 12007.5 | 12048.3 | 12244.6 | 12071.7 | 12188.4 | 12170.2 | 12201.8 | 12053.5 | 12146.8 | 11923.9 | 12159.5 | 12069.7 | 10950.9 | 12148.1 | 12019.5 | 12212.4 | 12017.7 | 12069.4 | 12216.1 | 12240.4 | 12253.4 | 12262.3 | 12022.9 | 12261.7 | 12244.3 | 12184.5 | 12165.1 | 12778 | 11943.2 | 12623.3 | 11789.1 | 12256.9 | 13213.5 | 11735.5 | 12703.9 | 11574.6 | 11783.1 | 12302.3 | 11721 | 12530.8 | 11382.3 | 12535.7 | 11607.7 | 11510.1 | 12547.7 | 11586.5 | 12580.3 | 12533.3 | 11413.3 | 12112 | 11566.4 | 11956.2 | 11518.2 | 12064.7 | 12419.9 | 12498.6 | 11754.1 | 12500.3 | 11450.9 | 11639.3 | 12680.7 | 11561.6 | 12556.2 | 11336.3 | 12578.3 | 11461.9 | 12397.9 | 11796.5 | 12318.5 | 11872.9 | 12687.9 | 11927 | 12384.1 | 11675.1 | 10394.4 | 12382.8 | 12074.2 | 11521.2 | 12683.6 | 12393.4 | 11740.1 | 11608.4 | 12434.9 | 11516.3 | 11877.7 | 12538.5 | 11431.7 | 12617.7 | 11491.2 | 12425.2 | 11706 | 12461.9 | 11200.4 | 12545.2 | 11706.5 | 12463.5 | 11679.7 | 12498.8 | 11854 | 11476.4 | 12316.9 | 11575.9 | 11423.9 | 12379.5 | 12238.4 | 12331.7 | 11641.5 | 12455.9 | 11453.8 | 12184.9 | 11718.7 | 12172.9 | 10958.7 | 12329.6 | 11581.2 | 11554.9 | 11639.9 | 11582.5 | 10046.6 | 11516.4 | 10280.6 | 11548.4 | 11556.8 | 12712.9 | 11582.6 | 12717.9 | 11768.2 | 12626.6 | 11614.1 | 11668.5 | 11459 | 12505.2 | 12764.6 | 12578.8 | 12630.8 | 12662.3 | 12655.5 | 11789.5 | 12635.7 | 12561.8 | 12617.2 | 12738.5 | 12674.4 | 12799.8 | 11908.2 | 12717.6 | 11904.1 | 31.6815 | 31.4569 | 31.4238 | 0 | 31.5839 | 31.3265 | 0 | 47.0481 | 0 | 0 | 0 | 0 | 1.9717 | 2.0205 | 1.9602 | 1.931 | 1.9977 | 1.9314 | 4.115 | 4.138 | 3.885 | 4.732 | 3.975 | 4.104 | 5.7245 | 6.0762 | 5.7679 | 5.6476 | 6.2397 | 6.4984 | 1.2178 | 1.4876 | 1.5004 | 0 | 1.5037 | 1.3169 | 6.9404 | 6.9187 | 6.7931 | 6.5485 | 6.9724 | 7.0412 | 1.2288 | 1.443 | 1.395 | 0 | 1.4918 | 1.6587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246521 | 449 | 236869 | 465 | 459786.969 | 1214.4 | 5.7245 | 6.0762 | 5.7679 | 5.6476 | 6.2397 | 6.4984 | 6.9404 | 6.9187 | 6.7931 | 6.5485 | 6.9724 | 7.0412 | 961000 | 1000 | 954000 | 2000 | 1907600 | 4733 | 1912000 | 1902867 | 11.4833 | 5.9924 | 1.4053 | 6.869 | 1.4435 | 23.45% | 21.01% | 31.4945 | 47.0481 | 1.9687 | 4.1582 | 1926155.6 | 1907400 | 2164050.3647 | 88.14%
2023-02-18 | 2023 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 334767.775 | 7:10 | 18:41 | 11813.9 | 12170.9 | 12183.5 | 12203.7 | 12224.4 | 12314.2 | 12235.5 | 12236.9 | 12019.6 | 11852.4 | 11972.1 | 12072.8 | 12212.4 | 12080.3 | 12166.4 | 12344.7 | 12154.9 | 12281.5 | 12250.9 | 12273.7 | 12115.1 | 12232 | 12009.4 | 12232 | 12155.9 | 11048.1 | 12226.9 | 12099.4 | 12307.6 | 12093.7 | 12148.5 | 12291.6 | 12330.1 | 12317.3 | 12340.4 | 12095.4 | 12345.2 | 12334.3 | 12266.7 | 12263.1 | 12859.4 | 11919 | 12633.5 | 11824.7 | 12356.6 | 13306.5 | 11731.7 | 12714.2 | 11676.7 | 11887.4 | 12394.6 | 11805.4 | 12632.8 | 11456.8 | 12616.3 | 11702.3 | 11591.3 | 12630.3 | 11679.9 | 12666.7 | 12607.8 | 11510.2 | 12178.1 | 11629.1 | 12010.7 | 11562.5 | 12144.3 | 12494.4 | 12570.4 | 11799.3 | 12621.7 | 11541 | 11699.2 | 12771.5 | 11617.6 | 12632 | 11415.9 | 12640.2 | 11542 | 12455.8 | 11813 | 12348.7 | 11889.9 | 12730.9 | 11573.1 | 11986.2 | 11694.8 | 10451.3 | 12438.6 | 12093.9 | 11568.3 | 12732.8 | 12429.8 | 11766.7 | 11638.2 | 12483.8 | 11541.4 | 11912.5 | 12568.3 | 11462.2 | 12665.9 | 11526 | 12472.7 | 11754.6 | 12495 | 11259.8 | 12583 | 11736.4 | 12512.8 | 11721.1 | 12541.9 | 11908.2 | 11503.6 | 12344 | 11607.1 | 11461.6 | 12421.6 | 12260.6 | 12358.8 | 11674.2 | 12488.7 | 11489.3 | 12213.3 | 11766 | 12199.3 | 11037.4 | 12372.6 | 11622.9 | 11655.4 | 11715.3 | 11623 | 10151.1 | 11548.1 | 10324.5 | 11553 | 11559.9 | 12637.9 | 11533.6 | 12698.5 | 11702.2 | 12656.6 | 11595.7 | 11618.3 | 11369.6 | 12498.2 | 12780 | 12572.5 | 12625.6 | 12627.6 | 12622.3 | 11724.7 | 12600.3 | 12574.2 | 12623.3 | 12745.3 | 12687.6 | 12815.8 | 11902.2 | 12716 | 11922.8 | 24.6 | 24.96 | 25.36 | 0 | 24.86 | 24.59 | 0 | 45.46 | 0 | 0 | 0 | 0 | 2.12 | 2.08 | 2.01 | 2.08 | 2 | 2.06 | 4.46 | 4.18 | 4.37 | 4.33 | 4.38 | 4.32 | 5.8001 | 6.1765 | 5.8448 | 5.7121 | 6.3236 | 6.5573 | 1.2556 | 1.5372 | 1.5463 | 0 | 1.5541 | 1.3574 | 7.0108 | 7.0082 | 6.8735 | 6.611 | 7.0536 | 7.1108 | 1.2706 | 1.4953 | 1.4389 | 0 | 1.5332 | 1.7108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 247488 | 451 | 237825 | 466 | 461702.369 | 1219.2 | 5.8001 | 6.1765 | 5.8448 | 5.7121 | 6.3236 | 6.5573 | 7.0108 | 7.0082 | 6.8735 | 6.611 | 7.0536 | 7.1108 | 967000 | 2000 | 956000 | 1000 | 1915400 | 4800 | 1920000 | 1910600 | 11.5167 | 6.0691 | 1.4501 | 6.9446 | 1.4898 | 23.89% | 21.45% | 24.874 | 45.46 | 2.0583 | 4.34 | 1932951.1 | 1915066 | 2189778.6694 | 87.45%
2023-02-19 | 2023 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 334767.775 | 7:09 | 18:46 | 11902.2 | 12262.7 | 12268.4 | 12288.5 | 12308.8 | 12398.6 | 12307.6 | 12310.6 | 12130.3 | 11942.3 | 12064.7 | 12157.8 | 12298.2 | 12167.5 | 12256 | 12422.7 | 12249.3 | 12355.9 | 12326.1 | 12350 | 12186.9 | 12297.1 | 12090.5 | 12299.8 | 12221.4 | 11151.5 | 12292.8 | 12173.7 | 12360.4 | 12161.1 | 12214.2 | 12351.4 | 12396.1 | 12386.9 | 12396.7 | 12245.6 | 12420.2 | 12383.6 | 12327.9 | 12337.6 | 12899.7 | 12005.5 | 12699.3 | 11939.4 | 12432.4 | 13360.6 | 11843.4 | 12734.7 | 11757.1 | 11963.7 | 12464 | 11893.4 | 12695.7 | 11562.8 | 12688.4 | 11799.1 | 11681.8 | 12716.5 | 11770.5 | 12750.9 | 12690.6 | 11600.9 | 12260.5 | 11714.6 | 12125.8 | 11691.7 | 12233.4 | 12576.1 | 12667.8 | 11903 | 12692.2 | 11646.4 | 11808.7 | 12858.4 | 11723.8 | 12719.2 | 11520.3 | 12737.7 | 11639.6 | 12548.7 | 11909.1 | 12439.5 | 12004.3 | 12817.7 | 12156.6 | 12753 | 11794 | 10558.7 | 12523 | 12196.2 | 11682.3 | 12822.9 | 12520.5 | 11874.6 | 11772.1 | 12598.6 | 11665.4 | 12019.4 | 12664.3 | 11569.5 | 12751.9 | 11635.4 | 12565.2 | 11874.5 | 12577.8 | 11384.5 | 12662.1 | 11852.3 | 12595.3 | 11823.3 | 12639 | 12014.5 | 11607.3 | 12448.9 | 11714.8 | 11589.9 | 12508.3 | 12365.9 | 12453.7 | 11788.6 | 12590.3 | 11618.9 | 12312.8 | 11873.7 | 12299.1 | 11181.3 | 12472.7 | 11750.8 | 11776.4 | 11850.5 | 11743.2 | 10280.8 | 11708.2 | 10456.3 | 11677.4 | 11668.2 | 12715.3 | 11618 | 12771.4 | 11788.4 | 12734.9 | 11682.5 | 11497.9 | 11273.1 | 12565.1 | 12847 | 12636.7 | 12693.7 | 12695.8 | 12697.4 | 11795.1 | 12669.5 | 12656.9 | 12706.4 | 12835.7 | 12788 | 12899.8 | 11996.6 | 12743.5 | 12016.6 | 25.07 | 26.01 | 26.03 | 0 | 25.81 | 25.96 | 0 | 43.7 | 0 | 0 | 0 | 0 | 3.82 | 3.75 | 3.8 | 3.63 | 3.93 | 4.02 | 7.89 | 7.97 | 8.15 | 8.32 | 7.93 | 7.58 | 5.8772 | 6.2748 | 5.9339 | 5.805 | 6.3882 | 6.6626 | 1.2613 | 1.5575 | 1.5618 | 0 | 1.6852 | 1.3856 | 7.0907 | 7.1324 | 6.9493 | 6.6988 | 7.1459 | 7.2388 | 1.2778 | 1.521 | 1.4493 | 0 | 1.6089 | 1.7499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 248461 | 452 | 238790 | 468 | 463633.77 | 1223.933 | 5.8772 | 6.2748 | 5.9339 | 5.805 | 6.3882 | 6.6626 | 7.0907 | 7.1324 | 6.9493 | 6.6988 | 7.1459 | 7.2388 | 973000 | 1000 | 965000 | 2000 | 1931401 | 4733 | 1935000 | 1926668 | 11.6167 | 6.1569 | 1.4903 | 7.0427 | 1.5214 | 24.2% | 21.6% | 25.776 | 43.7 | 3.825 | 7.9733 | 1948262.7 | 1931000 | 2240213.3765 | 86.2%
2023-02-20 | 2023 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 334767.775 | 7:05 | 18:42 | 12038.1 | 12368.2 | 12368.6 | 12396 | 12413.8 | 12497.7 | 12399.8 | 12392.7 | 12284 | 12064.1 | 12182 | 12272 | 12397 | 12267.1 | 12363.5 | 12518.4 | 12355 | 12442.6 | 12405 | 12406.8 | 12303.4 | 12388.8 | 12202.7 | 12404.5 | 12317.7 | 11339.6 | 12397.9 | 12275.9 | 12452.8 | 12293.3 | 12327.7 | 12452.8 | 12492.4 | 12488.2 | 12489.1 | 12447.9 | 12535.5 | 12480.1 | 12420.6 | 12420.4 | 12918.2 | 12154.6 | 12815.7 | 12087.6 | 12521.8 | 13354.3 | 12022.3 | 12846.5 | 11900.4 | 12091.4 | 12560.4 | 12038.9 | 12760.7 | 11725.6 | 12777.2 | 11955.8 | 11828 | 12746 | 11921.4 | 12777 | 12726.2 | 11751.6 | 12334 | 11843.6 | 12242.2 | 11854.5 | 12338.8 | 12651.7 | 12729.9 | 12050.4 | 12717.6 | 11794.9 | 11963.7 | 12893.8 | 11892 | 12777.9 | 11687.5 | 12807.9 | 11798 | 12634.1 | 12058.7 | 12552.7 | 12153.5 | 12881.6 | 12067.3 | 12457.5 | 11954.5 | 10762.2 | 12625.1 | 12324 | 11845.7 | 12881.8 | 12613 | 12039.2 | 11941.4 | 12679.9 | 11846.8 | 12164.7 | 12750.9 | 11743.1 | 12820.7 | 11790.4 | 12654.1 | 12011.2 | 12672.2 | 11556.1 | 12751.2 | 11994 | 12691.8 | 11970 | 12732.8 | 12145.5 | 11786.6 | 12546.4 | 11859.2 | 11755.5 | 12597.1 | 12470 | 12553 | 11943.6 | 12668.5 | 11775.1 | 12419.7 | 12006 | 12410.5 | 11375.8 | 12570.5 | 11907.2 | 11922.2 | 11994.3 | 11923.8 | 10468.5 | 11894.6 | 10713.6 | 11862.1 | 11858.2 | 12813.9 | 11835.1 | 12842 | 11934.1 | 12807.4 | 11857.8 | 11782.1 | 11620.9 | 12709.2 | 12903.2 | 12753.6 | 12807.2 | 12807.2 | 12819.6 | 12104.2 | 12826.2 | 12849.3 | 12887.9 | 12938 | 12924.2 | 12948.2 | 12198.4 | 12929.2 | 12228.5 | 29.4779 | 29.2968 | 29.3017 | 0 | 29.374 | 29.4943 | 0 | 43.5479 | 0 | 0 | 0 | 0 | 4.9423 | 4.9946 | 4.7872 | 4.7655 | 4.8931 | 4.9579 | 8.935 | 8.046 | 7.87 | 8.07 | 9.013 | 7.945 | 5.9546 | 6.3585 | 6.0257 | 5.8935 | 6.473 | 6.7125 | 1.2615 | 1.5348 | 1.5649 | 0 | 1.669 | 1.3767 | 7.1402 | 7.1717 | 7.0178 | 6.7974 | 7.1862 | 7.314 | 1.2859 | 1.4928 | 1.4572 | 0 | 1.5948 | 1.7374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 249443 | 454 | 239765 | 470 | 465581.903 | 1228.533 | 5.9546 | 6.3585 | 6.0257 | 5.8935 | 6.473 | 6.7125 | 7.1402 | 7.1717 | 7.0178 | 6.7974 | 7.1862 | 7.314 | 982000 | 2000 | 975000 | 2000 | 1948133 | 4600 | 1953000 | 1943533 | 11.6167 | 6.2363 | 1.4814 | 7.1046 | 1.5136 | 23.75% | 21.3% | 29.389 | 43.5479 | 4.8901 | 8.3132 | 1967600.8 | 1947800 | 2280029.0488 | 85.43%
2023-02-21 | 2023 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 334767.775 | 7:10 | 18:42 | 10255.2 | 10738.1 | 10798 | 10757 | 10828.7 | 10921.7 | 10784.8 | 10880 | 10656.2 | 10373.4 | 10506 | 10643.6 | 10753.8 | 10658 | 10695.6 | 10923.6 | 10750.8 | 10882.5 | 10862.9 | 10860.1 | 10714 | 10832.7 | 10495.1 | 10816.5 | 10741.1 | 9448.6 | 10792.8 | 10641.2 | 10978.9 | 10816.5 | 10718.4 | 10965.3 | 10980.6 | 11015 | 10985.2 | 10921.1 | 11053.9 | 10954.8 | 10911.7 | 10899 | 11725 | 10385.2 | 11552.6 | 10281.1 | 10886.9 | 12239.6 | 10252.5 | 11613.7 | 10026.6 | 10273.5 | 10994.3 | 10216.4 | 11327.3 | 9841.3 | 11344.2 | 9975 | 9950.9 | 11397.9 | 10009.7 | 11385.7 | 11337.1 | 9845 | 10782.4 | 10021.6 | 10558.4 | 9995.8 | 10664.4 | 11172.4 | 11350.8 | 10250.4 | 11302.9 | 9871.6 | 10117.2 | 11461.1 | 10000.4 | 11301.9 | 9746.9 | 11438.8 | 9900 | 11189.6 | 10264 | 11006.5 | 10429.4 | 11542.2 | 10262.3 | 10854.4 | 10224.3 | 8960.8 | 11207.4 | 10748.2 | 9991.7 | 11559 | 11190.7 | 10249.1 | 10128.5 | 11284.4 | 9984.3 | 10391.7 | 11381.1 | 9836.4 | 11413.3 | 9848.2 | 11070.8 | 10124.2 | 11231 | 9600.5 | 11282.5 | 10122.2 | 11118.8 | 10080.7 | 11199.5 | 10235.5 | 9919.4 | 11010.7 | 9976 | 9811.4 | 11104.3 | 10918.6 | 11039.1 | 10105.2 | 11220.3 | 9850 | 10792.4 | 10114.3 | 10732.9 | 9390 | 10962.2 | 9973.6 | 10020.2 | 10172.9 | 10044 | 8688.5 | 10008.7 | 8859.4 | 9984.5 | 10003.1 | 11541.7 | 9967 | 11573.1 | 10166.7 | 11506.8 | 10067.4 | 10185.8 | 9952.6 | 11220.2 | 11625.1 | 11329 | 11459.7 | 11506.8 | 11535 | 10339.2 | 11494.6 | 11524 | 11622.6 | 11674.7 | 11647 | 11651.5 | 10414.8 | 11535.7 | 10450.1 | 28.1751 | 27.814 | 27.8032 | 0 | 28.1356 | 27.9653 | 0 | 42.2026 | 0 | 0 | 0 | 0 | 1.9758 | 2.0358 | 1.9082 | 2.0236 | 1.9763 | 1.9491 | 4.721 | 4.963 | 5.157 | 4.812 | 5.27 | 4.337 | 4.9665 | 5.2922 | 5.0201 | 4.9162 | 5.3455 | 5.4783 | 1.0459 | 1.2806 | 1.2867 | 0 | 1.3803 | 1.1414 | 5.8559 | 5.8733 | 5.7582 | 5.6086 | 5.897 | 6.0066 | 1.0707 | 1.2478 | 1.2145 | 0 | 1.3346 | 1.4369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250297 | 455 | 240610 | 472 | 467274.903 | 1233.333 | 4.9665 | 5.2922 | 5.0201 | 4.9162 | 5.3455 | 5.4783 | 5.8559 | 5.8733 | 5.7582 | 5.6086 | 5.897 | 6.0066 | 854000 | 1000 | 845000 | 2000 | 1693000 | 4800 | 1696000 | 1688200 | 11.5333 | 5.1698 | 1.227 | 5.8332 | 1.2609 | 23.73% | 21.62% | 27.9786 | 42.2026 | 1.9781 | 4.8767 | 1707716.9 | 1692800 | 1884100.3936 | 89.85%
2023-02-22 | 2023 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 334767.775 | 7:06 | 18:42 | 10535.4 | 10928.6 | 10912.3 | 10900.9 | 10937.8 | 11028.3 | 10969.7 | 10965 | 10815.9 | 10586.3 | 10694.5 | 10799.2 | 10917.1 | 10797.3 | 10874 | 11050.2 | 10888.4 | 10985.5 | 10959.6 | 10971.1 | 10837.5 | 10933.6 | 10701.4 | 10934 | 10852.9 | 9786.7 | 10916.6 | 10789.3 | 11030.5 | 10894 | 10854.7 | 11014.1 | 11027.8 | 11039.3 | 11031.5 | 10986.9 | 11085.3 | 11021.5 | 10977.2 | 10976.5 | 11645.6 | 10673.3 | 11505.5 | 10597.5 | 11065.3 | 12129.3 | 10527.5 | 11545.3 | 10346.6 | 10557.6 | 11085.6 | 10493.6 | 11324.8 | 10168.3 | 11339.7 | 10400.6 | 10272.6 | 11354.2 | 10351.6 | 11371.2 | 11336.3 | 10192.6 | 10882.3 | 10310.1 | 10723.4 | 10300.9 | 10832.3 | 11191.3 | 11318.2 | 10518.4 | 11297.7 | 10231.5 | 10421.2 | 11483.8 | 10335.1 | 11351.1 | 10115.6 | 11393.9 | 10245.5 | 11208.5 | 10530.9 | 11084.5 | 10643.4 | 11473.6 | 10569 | 10992.2 | 10444.7 | 9297.8 | 11176.9 | 10854.3 | 10287.8 | 11472.6 | 11172.5 | 10495.5 | 10389.1 | 11241.3 | 10300.6 | 10633.9 | 11339.4 | 10178.3 | 11400 | 10245.5 | 11179.9 | 10464.8 | 11246.8 | 10001.2 | 11308.1 | 10447.4 | 11210.2 | 10416.9 | 11259.4 | 10572.8 | 10248.5 | 11081.8 | 10302 | 10184 | 11164.7 | 11004.6 | 11103.4 | 10406.6 | 11221 | 10199.6 | 10938.9 | 10449.9 | 10904.1 | 9781 | 11068.5 | 10317.1 | 10343.2 | 10450.3 | 10351.6 | 9022.6 | 10291 | 9197.3 | 10308.1 | 10318.7 | 11413.2 | 10249.9 | 11440.2 | 10477 | 11372.9 | 10382.4 | 10503.1 | 10316.8 | 11202.4 | 11469.1 | 11293.7 | 11358.8 | 11377.2 | 11391.3 | 10556.2 | 11378.1 | 11412.5 | 11462.1 | 11503 | 11485.1 | 11498 | 10630.9 | 11434.6 | 10658.1 | 28.6711 | 28.6398 | 28.7086 | 0 | 28.58 | 28.8481 | 0 | 42.8837 | 0 | 0 | 0 | 0 | 3.1151 | 3.2704 | 3.1662 | 3.2367 | 3.1246 | 3.0885 | 7.328 | 7.044 | 7.178 | 7.177 | 7.084 | 8.064 | 5.2409 | 5.5515 | 5.2835 | 5.1788 | 5.6108 | 5.7133 | 1.0968 | 1.3642 | 1.3438 | 0 | 1.4697 | 1.2276 | 6.1196 | 6.1315 | 6.0055 | 5.8193 | 6.1923 | 6.2868 | 1.1295 | 1.3281 | 1.2756 | 0 | 1.4262 | 1.5371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 251163 | 457 | 241466 | 473 | 468990.903 | 1238.133 | 5.2409 | 5.5515 | 5.2835 | 5.1788 | 5.6108 | 5.7133 | 6.1196 | 6.1315 | 6.0055 | 5.8193 | 6.1923 | 6.2868 | 866000 | 2000 | 856000 | 1000 | 1716000 | 4800 | 1719000 | 1711200 | 11.6 | 5.4298 | 1.3004 | 6.0925 | 1.3393 | 23.95% | 21.98% | 28.6895 | 42.8837 | 3.1669 | 7.3125 | 1730910.2 | 1715933 | 1962880.836 | 87.42%
2023-02-23 | 2023 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 334767.775 | 7:11 | 18:47 | 10591.3 | 11047.5 | 11014 | 11026.6 | 11026.9 | 11108.9 | 11039.1 | 11014 | 10854.1 | 10780.4 | 10711.9 | 10830.2 | 10960.2 | 10830.3 | 10928 | 11117.5 | 10943.2 | 11037.5 | 11004.8 | 11019.5 | 10858.5 | 10967.1 | 10688.1 | 10956.4 | 10834.9 | 9700.3 | 10939.1 | 10781.9 | 11044.6 | 10883.4 | 10823.5 | 11017.7 | 10959.7 | 10968.8 | 10978.6 | 10930.3 | 11039.4 | 10981.3 | 10926 | 10888.6 | 11708.1 | 10644.9 | 11559.7 | 10549.5 | 11060 | 12190.2 | 10496.2 | 11616.8 | 10315.5 | 10530.6 | 11127.7 | 10436 | 11376.5 | 10121.2 | 11362.6 | 10308.9 | 10175.2 | 11339.4 | 10309.9 | 11396.9 | 11375 | 10158.2 | 10843.7 | 10205.3 | 10626.9 | 10120.6 | 10746.1 | 11107.7 | 11300.4 | 10358.4 | 11257.3 | 10031.8 | 10310.5 | 11441.3 | 10215.4 | 11322.1 | 9969.8 | 11400.9 | 10108.1 | 11194.6 | 10329.8 | 10958.6 | 10444.4 | 11387.4 | 10412.7 | 10949.4 | 10242.8 | 9066.3 | 11054.1 | 10698.8 | 10056.9 | 11380.6 | 11061.2 | 10290.9 | 10171.6 | 11113.4 | 10023.5 | 10389.6 | 11209.8 | 9896.1 | 11302.8 | 9978 | 11041.1 | 10202.7 | 11137.1 | 9728.1 | 11194.6 | 10190.5 | 11080.4 | 10168.5 | 11121.4 | 10304.2 | 9965.6 | 10904.2 | 10023.3 | 9876 | 10986 | 10797.5 | 10934 | 10103.9 | 11046 | 9873.2 | 10743.3 | 10183.4 | 10686.1 | 9443.5 | 10851.9 | 9969.2 | 9997.9 | 10129.9 | 9983.9 | 8694.1 | 9924.2 | 8817.9 | 9840.9 | 9862.2 | 11174.6 | 9793.5 | 11181.2 | 10042.3 | 11101.4 | 9926 | 10060.2 | 9850.2 | 10880.5 | 11194.7 | 10987.1 | 11083.4 | 11124.2 | 11143.9 | 10119.8 | 11090.6 | 0 | 7536.6 | 10588 | 10556.6 | 10570.9 | 9597.4 | 10527.9 | 9649 | 27.928 | 27.6796 | 27.568 | 0 | 27.7397 | 27.7499 | 0 | 42.2943 | 0 | 0 | 0 | 0 | 3.0184 | 2.6963 | 2.8571 | 2.8041 | 2.8025 | 2.3887 | 5.813 | 5.379 | 5.586 | 5.488 | 5.932 | 5.269 | 5.1426 | 5.4043 | 5.2166 | 5.0234 | 5.3397 | 5.363 | 1.0826 | 1.2768 | 1.3336 | 0 | 1.3306 | 1.0872 | 6.0517 | 5.9832 | 5.9736 | 5.7519 | 5.841 | 5.8873 | 1.1136 | 1.2426 | 1.2606 | 0 | 1.2819 | 1.3662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 252028 | 459 | 242284 | 476 | 470666.837 | 1242.067 | 5.1426 | 5.4043 | 5.2166 | 5.0234 | 5.3397 | 5.363 | 6.0517 | 5.9832 | 5.9736 | 5.7519 | 5.841 | 5.8873 | 865000 | 2000 | 818000 | 3000 | 1675934 | 3934 | 1678000 | 1672000 | 11.6 | 5.2483 | 1.2222 | 5.9148 | 1.253 | 23.29% | 21.18% | 27.733 | 42.2943 | 2.7612 | 5.5778 | 1690779.4 | 1675733 | 1921266.8655 | 87.22%
2023-02-24 | 2023 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 334767.775 | 7:03 | 18:49 | 10391.4 | 10783.9 | 10736.8 | 10725.6 | 10745.9 | 10837.4 | 10786.3 | 10988.3 | 10666.6 | 10735.8 | 10524 | 10620 | 10736.8 | 10612.5 | 10703.8 | 10883.1 | 10706.7 | 10798.3 | 10772 | 10783 | 10648.8 | 10744.6 | 10509.9 | 10746.8 | 10664 | 9632.2 | 10735.5 | 10597.8 | 10839.3 | 10679.9 | 10666.9 | 10836.5 | 10776.8 | 10750.8 | 10785.5 | 10763.6 | 10847.9 | 10811.8 | 10752.8 | 10676.8 | 11423 | 10473.4 | 11307 | 10391.9 | 10845.5 | 11878.5 | 10339.4 | 11332.5 | 10174.2 | 10374.1 | 10905.4 | 10292.3 | 11129.7 | 9983.3 | 11144 | 10200.4 | 10075.3 | 11132.9 | 10179.7 | 11185.6 | 11162.4 | 10029.2 | 10655 | 10079.8 | 10468.9 | 10054.7 | 10608.7 | 10961.8 | 11100.5 | 10283 | 11089 | 10003.2 | 10203 | 11268.5 | 10119.1 | 11139 | 9908.6 | 11182.9 | 10022.7 | 10997.8 | 10270.3 | 10849.1 | 10381.9 | 11235.4 | 10280 | 10722 | 10178.7 | 9118.9 | 10912.6 | 10607.4 | 10030.8 | 11223.4 | 10945.1 | 10238.7 | 10113.8 | 10971.2 | 10010.2 | 10357.5 | 11081 | 9904.6 | 11167.3 | 9989.5 | 10937.4 | 10188 | 11007.6 | 9748.1 | 11071.3 | 10182.5 | 10966.6 | 10155.5 | 11005.4 | 10301.3 | 9980.5 | 10821.7 | 10026.4 | 9908.3 | 10901.9 | 10744.6 | 10838.5 | 10142.4 | 10959 | 9931.8 | 10682 | 10192 | 10623.2 | 9549.9 | 10808.3 | 10050.2 | 10070.7 | 10176 | 10057.4 | 8844 | 10042.4 | 9037.1 | 10008.1 | 10025.4 | 11170.4 | 9949.3 | 11197.2 | 10173.2 | 11134 | 10088.3 | 10207.7 | 10022.6 | 10941.1 | 11228.6 | 11032.9 | 11105.6 | 11126 | 11145.4 | 10255.6 | 11132.3 | 11154.9 | 11217.8 | 11263.8 | 11241.1 | 11256.4 | 10328.4 | 11170.1 | 10351.6 | 27.727 | 27.5925 | 27.4796 | 0 | 27.3973 | 27.778 | 0 | 42.7263 | 0 | 0 | 0 | 0 | 2.6222 | 2.4418 | 2.5004 | 2.5106 | 2.4362 | 2.282 | 6.113 | 5.767 | 6.362 | 5.805 | 5.408 | 5.971 | 5.2423 | 5.5109 | 5.2005 | 5.1063 | 5.4639 | 5.5954 | 1.0185 | 1.4036 | 1.2564 | 0 | 1.4888 | 1.2526 | 6.1077 | 6.123 | 5.9137 | 5.6212 | 6.1393 | 6.1286 | 1.0458 | 1.3675 | 1.1897 | 0 | 1.4564 | 1.5611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 252877 | 460 | 243120 | 477 | 472346.037 | 1246.667 | 5.2423 | 5.5109 | 5.2005 | 5.1063 | 5.4639 | 5.5954 | 6.1077 | 6.123 | 5.9137 | 5.6212 | 6.1393 | 6.1286 | 849000 | 1000 | 836000 | 1000 | 1679200 | 4600 | 1683000 | 1674600 | 11.7667 | 5.3532 | 1.284 | 6.0056 | 1.3241 | 23.99% | 22.05% | 27.5949 | 42.7263 | 2.4655 | 5.9043 | 1694581.5 | 1678934 | 1940250.7996 | 86.53%
2023-02-25 | 2023 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 335090.89 | 7:06 | 18:45 | 10760.3 | 11221.3 | 11177.3 | 11175.8 | 11180.6 | 11287.5 | 11190.2 | 11613.9 | 11245.2 | 11168.3 | 11028.7 | 11137.8 | 11208.2 | 11080.8 | 11102.6 | 11313.6 | 11130.7 | 11248.3 | 11217.6 | 11213.5 | 11080.6 | 11190 | 10912.4 | 11193.6 | 11100 | 9849.9 | 11169.9 | 11024.9 | 11299.6 | 11126.1 | 11102.5 | 11293.1 | 11311.4 | 11326.1 | 11291 | 11242.3 | 11368 | 11279 | 11253.8 | 11249.1 | 11958.6 | 10829.6 | 11833.1 | 10727.8 | 11287.4 | 12472.5 | 10715.8 | 11862.7 | 10468.3 | 10708.3 | 11360.9 | 10626.7 | 11629.8 | 10294.5 | 11654.7 | 10519.1 | 10363.8 | 11653.9 | 10462.4 | 11696.6 | 11663.4 | 10292.4 | 11106.7 | 10391.1 | 10950 | 10442.8 | 11086.2 | 11520.8 | 11652.5 | 10713.3 | 11642.7 | 10347.9 | 10573.1 | 11853.3 | 10473.7 | 11720.3 | 10240.4 | 11734.1 | 10349.4 | 11528.2 | 10711.5 | 11379.9 | 10853.1 | 11830.3 | 10755.7 | 11355 | 10597.1 | 9355.4 | 11456.4 | 11119.4 | 10389.9 | 11820.6 | 11510.1 | 10671.3 | 10548.4 | 11537.1 | 10383.2 | 10825 | 11698.9 | 10308.2 | 11776.9 | 10386 | 11511.1 | 10624.5 | 11605.2 | 10093.7 | 11670.9 | 10637.9 | 11536.9 | 10580.2 | 11584.4 | 10756.7 | 10402.5 | 11441.7 | 10455.7 | 10324 | 11511.4 | 11384.2 | 11466.8 | 10652.2 | 11627.5 | 10388.7 | 11260.1 | 10668.9 | 11205.1 | 9921.5 | 11444.7 | 10522.2 | 10539.5 | 10677.4 | 10527.1 | 9141.6 | 10526.1 | 9328.8 | 10478.5 | 10486.4 | 11846.2 | 10395.5 | 11892.9 | 10693 | 11807.8 | 10577 | 10750.2 | 10489.4 | 11580.3 | 11919 | 11662.4 | 11768.9 | 11792.5 | 11810.9 | 10778.9 | 11810 | 11815.6 | 11906.2 | 11968.7 | 11944.9 | 11957.4 | 10861.3 | 11836.6 | 10884.1 | 28.5681 | 28.3283 | 28.4532 | 0 | 28.4946 | 28.5527 | 0 | 43.1499 | 0 | 0 | 0 | 0 | 2.2724 | 2.3255 | 2.2374 | 2.2964 | 2.3424 | 2.297 | 5.433 | 5.943 | 5.066 | 6.106 | 5.427 | 6.802 | 5.1581 | 5.5676 | 5.3424 | 5.2013 | 5.6619 | 5.7614 | 1.1066 | 1.3233 | 1.3779 | 0 | 1.4455 | 1.2055 | 5.9679 | 6.1188 | 6.0745 | 5.9121 | 6.1882 | 6.3465 | 1.1375 | 1.2916 | 1.304 | 0 | 1.394 | 1.5196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253763 | 461 | 243998 | 478 | 474102.57 | 1251.467 | 5.1581 | 5.5676 | 5.3424 | 5.2013 | 5.6619 | 5.7614 | 5.9679 | 6.1188 | 6.0745 | 5.9121 | 6.1882 | 6.3465 | 886000 | 1000 | 878000 | 1000 | 1756533 | 4800 | 1762000 | 1751733 | 11.65 | 5.4488 | 1.2918 | 6.1014 | 1.3293 | 23.71% | 21.79% | 28.4794 | 43.1499 | 2.2952 | 5.7962 | 1772777.5 | 1756533 | 1969313.6609 | 89.2%
2023-02-26 | 2023 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 335090.89 | 7:05 | 18:49 | 10376.6 | 10800 | 10756.4 | 10761 | 10757.2 | 10865.5 | 10775.8 | 11161.7 | 10851.1 | 10743.7 | 10666.5 | 10744.9 | 10853.7 | 10723.3 | 10719.2 | 10923.5 | 10738 | 10874.3 | 10872 | 10892.4 | 10764.6 | 10854.5 | 10556.8 | 10818.1 | 10730.7 | 9531.4 | 10787.7 | 10650.8 | 10917.2 | 10768.8 | 10730.8 | 10912.8 | 10902.1 | 10926.9 | 10922.2 | 10865.7 | 10964.9 | 10887.4 | 10852.8 | 10847.6 | 11473.8 | 10537.4 | 11360.3 | 10380.3 | 10859.6 | 11910 | 10343.8 | 11397.3 | 10131.4 | 10371.8 | 10963.8 | 10283 | 11209 | 10146 | 11224.3 | 10179.7 | 10020.9 | 11212.1 | 10121 | 11265.7 | 11228.6 | 9948.9 | 10691.1 | 10019.8 | 10545.4 | 10069 | 10682.3 | 11058.8 | 11192.4 | 10316.9 | 11175.4 | 9951.3 | 10211.2 | 11356.5 | 10111.6 | 11229.6 | 9852.3 | 11275.3 | 9981.1 | 11072.5 | 10313.6 | 10929.8 | 10433.6 | 11347.6 | 10322 | 10893.5 | 10208.1 | 8988.4 | 10998.6 | 10696.8 | 10023.2 | 11340.2 | 11062.5 | 10305.8 | 10177.1 | 11073.3 | 10014.5 | 10436 | 11226.1 | 9947.2 | 11298.7 | 10022.6 | 11067.2 | 10245.3 | 11138.2 | 9735.3 | 11199.3 | 10260.1 | 11073.6 | 10197.6 | 11109.6 | 10362.6 | 10040.3 | 10991.4 | 10083.3 | 9945.5 | 11059.1 | 10926.4 | 11008.5 | 10256.6 | 11139.8 | 9994.3 | 10821.4 | 10273.7 | 10745.3 | 9529.2 | 10971.9 | 10129.4 | 10123.7 | 10253.1 | 10124.1 | 8773.1 | 10110.2 | 8957 | 10078.7 | 10102.1 | 11347.6 | 10030 | 11387.1 | 10309.3 | 11317.8 | 10208.4 | 10359.6 | 10114.9 | 11094.3 | 11401.5 | 11178.4 | 11280.5 | 11284 | 11303.8 | 10379.2 | 11308.9 | 11317 | 11389.5 | 11440.7 | 11416.9 | 11425.9 | 10429.6 | 11343.7 | 10468 | 29.2325 | 29.0058 | 28.8475 | 0 | 29.0614 | 28.9856 | 0 | 41.3956 | 0 | 0 | 0 | 0 | 2.669 | 2.5844 | 2.5541 | 2.6092 | 2.5468 | 2.4215 | 8.056 | 5.496 | 5.371 | 5.913 | 5.052 | 5.812 | 5.1499 | 5.4339 | 5.2187 | 5.0799 | 5.4903 | 5.4981 | 1.0876 | 1.301 | 1.3362 | 0 | 1.4131 | 1.1952 | 5.9002 | 5.8846 | 5.8429 | 5.7014 | 5.943 | 6.099 | 1.1253 | 1.2753 | 1.2778 | 0 | 1.3775 | 1.5019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 254617 | 463 | 244841 | 480 | 475793.571 | 1256.067 | 5.1499 | 5.4339 | 5.2187 | 5.0799 | 5.4903 | 5.4981 | 5.9002 | 5.8846 | 5.8429 | 5.7014 | 5.943 | 6.099 | 854000 | 2000 | 843000 | 2000 | 1691001 | 4600 | 1693000 | 1686401 | 11.7333 | 5.3118 | 1.2666 | 5.8952 | 1.3116 | 23.85% | 22.25% | 29.0265 | 41.3956 | 2.5642 | 5.95 | 1706834.5 | 1690867 | 1900092.2761 | 88.99%
2023-02-27 | 2023 | 2023 | Year_1 | Year_1 | 2023-03-01 | 28 | 335090.89 | 7:06 | 18:44 | 11160.6 | 11576.6 | 11518.4 | 11541.8 | 11515.1 | 11644.2 | 11544.8 | 11930.4 | 11625.9 | 11518.2 | 11468 | 11569.6 | 11633 | 11527.4 | 11495.1 | 11702.6 | 11511.1 | 11650.2 | 11651.9 | 11695.7 | 11560.1 | 11648.2 | 11328.3 | 11591.4 | 11501.2 | 10240.7 | 11576.9 | 11433.8 | 11697.4 | 11564.8 | 11494.1 | 11669.9 | 11620.9 | 11641.2 | 11694.2 | 11628.2 | 11725.4 | 11652.5 | 11604.9 | 11565.1 | 12281 | 11357.4 | 12167.8 | 11194.6 | 11664.6 | 12728.7 | 11137.6 | 12198.2 | 10874.1 | 11147.4 | 11754.3 | 11139.3 | 12018.1 | 10887.7 | 12010.2 | 10929.5 | 10775.3 | 12008.5 | 10860 | 12063.2 | 12019.1 | 10681.7 | 11483.5 | 10804.2 | 11348.3 | 10828.4 | 11492.6 | 11837.1 | 11984 | 11103.6 | 11978.7 | 10686.2 | 10989.2 | 12157.7 | 10883.9 | 12033.3 | 10610.1 | 12078 | 10745.1 | 11874.8 | 11084.2 | 11701.4 | 11212.5 | 12117 | 11067.5 | 11683.5 | 10909.7 | 9616.1 | 11786.1 | 11426.8 | 10745.7 | 12098 | 11807.4 | 11044 | 10908.6 | 11812.5 | 10730 | 11188.6 | 11961.3 | 10665.8 | 12054.2 | 10750.1 | 11822.1 | 10978.6 | 11889.4 | 10430.1 | 11958.9 | 10980.2 | 11852.7 | 10925.8 | 11883.1 | 11082.3 | 10762.2 | 11711.5 | 10813.9 | 10638.7 | 11780.9 | 11648.4 | 11732.5 | 10969.3 | 11868.8 | 10675.3 | 11559.2 | 10991.7 | 11493.5 | 10174.9 | 11716.6 | 10814.3 | 10816.2 | 10964.1 | 10797.7 | 9363.6 | 10783.3 | 9540 | 10707.1 | 10734.6 | 12071 | 10741.4 | 12084.9 | 11031.9 | 11989.4 | 10869.9 | 11028.2 | 10755.1 | 11800.1 | 12086.2 | 11903.3 | 12006.7 | 12012.9 | 12033.1 | 11107.2 | 11997.8 | 12054.6 | 12124 | 12122.1 | 12104.9 | 12115 | 11153.7 | 12099.6 | 11246.5 | 30.4913 | 30.4178 | 30.2953 | 0 | 30.2618 | 30.3618 | 0 | 44.9333 | 0 | 0 | 0 | 0 | 2.3752 | 2.1917 | 2.2195 | 2.2734 | 2.2777 | 2.3968 | 6.062 | 5.387 | 5.059 | 5.196 | 4.983 | 5.896 | 5.5765 | 5.8693 | 5.6626 | 5.5087 | 5.9326 | 5.9929 | 1.175 | 1.4047 | 1.4474 | 0 | 1.5188 | 1.2808 | 6.462 | 6.4291 | 6.4059 | 6.2207 | 6.4833 | 6.6102 | 1.2089 | 1.3716 | 1.3751 | 0 | 1.4704 | 1.6111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 255533 | 464 | 245742 | 482 | 477603.637 | 1260.6 | 5.5765 | 5.8693 | 5.6626 | 5.5087 | 5.9326 | 5.9929 | 6.462 | 6.4291 | 6.4059 | 6.2207 | 6.4833 | 6.6102 | 916000 | 1000 | 901000 | 2000 | 1810066 | 4533 | 1814000 | 1805533 | 11.6333 | 5.7571 | 1.3653 | 6.4352 | 1.4074 | 23.72% | 21.87% | 30.3656 | 44.9333 | 2.2891 | 5.4305 | 1826508.8 | 1810000 | 2052418.1711 | 88.19%
2023-02-28 | 2023 | 2023 | Year_1 | Year_1 | 2023-03-01 | 28 | 335090.89 | 7:05 | 18:45 | 11257 | 11713.9 | 11722.1 | 11740.5 | 11737.2 | 11865.4 | 11766.2 | 12091.8 | 11702 | 11575.4 | 11622.5 | 11716.3 | 11815.5 | 11705.7 | 11739.7 | 11921.9 | 11719.5 | 11844.9 | 11808.9 | 11842.5 | 11697.7 | 11793.7 | 11522 | 11738.4 | 11555.4 | 10353.9 | 11660.8 | 11545.7 | 11812.9 | 11704 | 11572.1 | 11729.2 | 11490.5 | 11567.8 | 11671.4 | 11634.6 | 11729.3 | 11654.4 | 11551.9 | 11420.9 | 12222.8 | 11418.1 | 12125.1 | 11243.7 | 11719 | 12671.1 | 11152 | 12091.2 | 10986.4 | 11215.5 | 11833.4 | 11191.7 | 12099.6 | 11068.9 | 11917.9 | 10974.8 | 10812.6 | 11885.8 | 10944.6 | 11973.5 | 11924 | 10778.8 | 11605.4 | 11017.6 | 11345.6 | 10887.5 | 11517.7 | 11827.9 | 11940.3 | 11129.3 | 11991.9 | 10769 | 11025.5 | 12122.9 | 10932.6 | 11969.1 | 10627.7 | 12000 | 10746.5 | 11745.5 | 11090.4 | 11689.4 | 11233.6 | 12059 | 11146.6 | 11729.8 | 10935.1 | 9690.5 | 11632.8 | 11376.8 | 10635.6 | 11869.9 | 11544.6 | 10867.7 | 10786.9 | 11606.2 | 10535.4 | 11052.8 | 11738.3 | 10526.2 | 11803.3 | 10610.4 | 11627.2 | 10861.9 | 11643.6 | 10328.8 | 11720 | 10846.2 | 11670.5 | 10818.7 | 11707.4 | 11000.5 | 10626.1 | 11512.2 | 10697.9 | 10545.5 | 11572.6 | 11471.5 | 11521.1 | 10857.9 | 11650.9 | 10588.6 | 11367.4 | 10877.2 | 11312.2 | 10116.2 | 11531.5 | 10717.8 | 10748 | 10854.4 | 10694.5 | 9299.7 | 10761.2 | 9586.5 | 10774 | 10791 | 12040.7 | 10850.6 | 12126.4 | 11134.3 | 11968.1 | 10908.6 | 11070 | 10823.8 | 11865.1 | 12122.6 | 11948.6 | 12035.8 | 12019.9 | 12025.4 | 11274.4 | 12090.1 | 11984.6 | 12060.6 | 12066 | 12063.1 | 12101.1 | 11238.8 | 12089 | 11324.6 | 31.5681 | 31.3915 | 31.4672 | 0 | 31.6003 | 31.6591 | 0 | 44.775 | 0 | 0 | 0 | 0 | 3.6036 | 3.5474 | 3.6338 | 3.4576 | 3.4786 | 3.438 | 7.955 | 7.44 | 7.658 | 7.15 | 6.437 | 7.811 | 5.6812 | 5.9987 | 5.691 | 5.531 | 5.9216 | 6.09 | 1.1834 | 1.442 | 1.456 | 0 | 1.5103 | 1.3051 | 6.5988 | 6.5792 | 6.4405 | 6.2513 | 6.459 | 6.7165 | 1.2214 | 1.4085 | 1.382 | 0 | 1.4619 | 1.6413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 256453 | 466 | 246636 | 484 | 479412.437 | 1265.333 | 5.6812 | 5.9987 | 5.691 | 5.531 | 5.9216 | 6.09 | 6.5988 | 6.5792 | 6.4405 | 6.2513 | 6.459 | 6.7165 | 920000 | 2000 | 894000 | 2000 | 1808800 | 4733 | 1810000 | 1804067 | 11.6667 | 5.8189 | 1.3794 | 6.5076 | 1.423 | 23.71% | 21.87% | 31.5372 | 44.775 | 3.5265 | 7.4085 | 1825862.2 | 1808734 | 2077073.0516 | 87.08%
2023-03-01 | 2023 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 335090.89 | 7:04 | 18:45 | 11075 | 11500.3 | 11462.6 | 11479.2 | 11443.8 | 11578.1 | 11455 | 11851.4 | 11563.7 | 11453.3 | 11426 | 11567 | 11566.5 | 11517.1 | 11440.9 | 11648.1 | 11461.8 | 11600.2 | 11605.1 | 11632.4 | 11502.6 | 11603.9 | 11253.8 | 11534.5 | 11450.1 | 10145.8 | 11513.3 | 11363.9 | 11649.2 | 11503.8 | 11441.4 | 11628.4 | 11619 | 11658.5 | 11656.2 | 11591.5 | 11688.6 | 11609.3 | 11566.4 | 11550 | 12244 | 11266.3 | 12127.7 | 11081.8 | 11602 | 12731.8 | 11026.1 | 12176.4 | 10767.1 | 11034.7 | 11701.8 | 11051.1 | 11970 | 10765.5 | 11974.7 | 10828.4 | 10724.4 | 12018.8 | 10757.9 | 12030.2 | 11988.6 | 10578.9 | 11744.6 | 11078.7 | 11286.7 | 10717.9 | 11425.2 | 11791.9 | 11950.4 | 10997.5 | 11938.5 | 10589.1 | 10889.4 | 12124.9 | 10778 | 11998.2 | 10507.5 | 12035.3 | 10633 | 11832.4 | 10990.2 | 11652.8 | 11070.4 | 12099.9 | 10982.1 | 11521.6 | 10849.9 | 9545.1 | 11813.1 | 11425.2 | 10692.6 | 12115 | 11794.6 | 10969.6 | 10828.1 | 11870.2 | 10647.3 | 11156.6 | 11976.6 | 10568 | 12033.9 | 10657.2 | 11791.4 | 10904.7 | 11870.6 | 10344.3 | 11939.1 | 10910.9 | 11828.5 | 10856.1 | 11861 | 11016.1 | 10651.1 | 11706.2 | 10625.2 | 10558 | 11765.1 | 11631.6 | 11721.7 | 10896.3 | 11858.6 | 10610.9 | 11539.7 | 10923.5 | 11452.1 | 10119.6 | 11702.2 | 10760.1 | 10781.6 | 10961.8 | 10709.7 | 9322.8 | 10783 | 9547.9 | 10676.6 | 10706.8 | 12184.4 | 10791.3 | 12217.1 | 11105.6 | 12115.3 | 10881.3 | 11067.9 | 10679.9 | 11903 | 12205.4 | 12010.5 | 12116.7 | 12131.7 | 12140.1 | 11194.9 | 12137.6 | 12074.7 | 12169 | 12182.5 | 12167.2 | 12218.9 | 11181.2 | 12136.1 | 11240.1 | 28.8821 | 28.4583 | 28.3771 | 0 | 28.5351 | 28.4938 | 0 | 42.0647 | 0 | 0 | 0 | 0 | 2.8854 | 2.9034 | 2.816 | 2.913 | 2.7149 | 2.732 | 5.517 | 5.156 | 4.652 | 5.032 | 4.839 | 5.792 | 5.4689 | 5.758 | 5.5128 | 5.3948 | 5.8057 | 5.8812 | 1.1376 | 1.3871 | 1.3964 | 0 | 1.5038 | 1.2716 | 6.3234 | 6.2997 | 6.2247 | 6.047 | 6.3788 | 6.4822 | 1.1718 | 1.3566 | 1.3273 | 0 | 1.4632 | 1.5967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 257365 | 468 | 247536 | 486 | 481216.838 | 1270.067 | 5.4689 | 5.758 | 5.5128 | 5.3948 | 5.8057 | 5.8812 | 6.3234 | 6.2997 | 6.2247 | 6.047 | 6.3788 | 6.4822 | 912000 | 2000 | 900000 | 2000 | 1804401 | 4734 | 1808000 | 1799667 | 11.6833 | 5.6369 | 1.3393 | 6.2927 | 1.3831 | 23.76% | 21.98% | 28.5493 | 42.0647 | 2.8275 | 5.1647 | 1821472.3 | 1804401 | 2078735.7824 | 86.8%
2023-03-02 | 2023 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 335090.89 | 7:02 | 18:45 | 10755 | 11149 | 11120.8 | 11139.9 | 11099.2 | 11228.6 | 11101.2 | 11472.2 | 11212.7 | 11096.3 | 11076.4 | 11214.3 | 11221.1 | 11169.7 | 11113.9 | 11307.5 | 11117.2 | 11243.6 | 11249.4 | 11285.8 | 11152.5 | 11249.4 | 10926.4 | 11183.5 | 11105.8 | 9863.6 | 11170.3 | 11022.9 | 11290.6 | 11146.2 | 11097.5 | 11272.2 | 11262.6 | 11300.9 | 11302.3 | 11238.5 | 11328.9 | 11250.8 | 11211 | 11195.7 | 11886 | 10982.6 | 11765.6 | 10809.3 | 11274.3 | 12295.8 | 10758.3 | 11820.9 | 10474.5 | 10735.1 | 11354.6 | 10747.7 | 11611 | 10468.2 | 11613.6 | 10535.3 | 10452.8 | 11693.7 | 10467.9 | 11657.2 | 11616.9 | 10297.2 | 11384.6 | 10759 | 11060.6 | 10432.3 | 11096.1 | 11454.3 | 11580.8 | 10712.4 | 11533.2 | 10290.4 | 10597.9 | 11739.3 | 10475.9 | 11624.7 | 10217 | 11655.1 | 10336 | 11467.3 | 10741.1 | 11342.9 | 10792.4 | 11755.7 | 10713.1 | 11167.5 | 10621.4 | 9330.2 | 11440.2 | 11117.1 | 10400.7 | 11728.7 | 11431.9 | 10654 | 10511.6 | 11497.2 | 10339.6 | 10837.1 | 11608.5 | 10287.2 | 11671.7 | 10375.3 | 11441.7 | 10615.1 | 11508.6 | 10063.4 | 11581.2 | 10625.3 | 11484.8 | 10570.6 | 11512.5 | 10736.8 | 10378 | 11370.5 | 10266 | 10284.3 | 11439.5 | 11306.7 | 11399.3 | 10638.1 | 11521.7 | 10346.7 | 11225.7 | 10648.4 | 11163.3 | 9876.6 | 11381.5 | 10496 | 10533.1 | 10705.3 | 10523.4 | 9126.7 | 10489.5 | 9283 | 10464 | 10470.7 | 11811.9 | 10495.2 | 11852.6 | 10818.7 | 11741.5 | 10604.8 | 10779.3 | 10458.1 | 11592.8 | 11863.3 | 11661.2 | 11754.7 | 11763.8 | 11769.6 | 10907.6 | 11786.8 | 11725.1 | 11833 | 11882.9 | 11865.3 | 11875.7 | 10931.7 | 11769.4 | 10959.6 | 27.2634 | 27.0694 | 26.9453 | 0 | 26.9502 | 27.0584 | 0 | 39.2158 | 0 | 0 | 0 | 0 | 3.1022 | 3.002 | 3.0552 | 3.1267 | 3.0219 | 2.9998 | 6.075 | 6.358 | 6.192 | 6.523 | 6.303 | 5.624 | 5.2613 | 5.5353 | 5.3279 | 5.2224 | 5.5821 | 5.6115 | 1.118 | 1.3117 | 1.3667 | 0 | 1.4329 | 1.212 | 6.0436 | 6.002 | 5.9777 | 5.8725 | 6.0748 | 6.1984 | 1.1531 | 1.285 | 1.3004 | 0 | 1.3928 | 1.5222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 258251 | 469 | 248412 | 487 | 482971.171 | 1274.733 | 5.2613 | 5.5353 | 5.3279 | 5.2224 | 5.5821 | 5.6115 | 6.0436 | 6.002 | 5.9777 | 5.8725 | 6.0748 | 6.1984 | 886000 | 1000 | 876000 | 1000 | 1754333 | 4666 | 1760000 | 1749667 | 11.7167 | 5.4234 | 1.2883 | 6.0282 | 1.3307 | 23.75% | 22.07% | 27.0573 | 39.2158 | 3.0513 | 6.1792 | 1770028.5 | 1754200 | 2015774.3584 | 87.02%
2023-03-03 | 2023 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 335090.89 | 7:02 | 18:46 | 11022 | 11359.4 | 11322.4 | 11355.3 | 11301.4 | 11435.1 | 11302.6 | 11642.4 | 11423.6 | 11295.9 | 11311.3 | 11436.1 | 11447.7 | 11389.5 | 11366.8 | 11532.4 | 11358.5 | 11474.9 | 11407.7 | 11284.8 | 11407.1 | 11488.2 | 11225 | 11441.9 | 11370.3 | 10243.5 | 11417.7 | 11288.9 | 11533.4 | 11400.3 | 11360.9 | 11425.3 | 11554.1 | 11569.5 | 11562.4 | 11506.3 | 11590.9 | 11521.6 | 11483.3 | 11481.6 | 12090.4 | 11280.7 | 11989 | 11134.2 | 11571.5 | 12537.1 | 11078.6 | 12039.7 | 10843.3 | 11067.6 | 11587.3 | 11074.6 | 11822.7 | 10822.8 | 11839.2 | 10915.9 | 10848.4 | 11914.9 | 10852.9 | 11873.2 | 11825.6 | 10679.7 | 11598.3 | 11060.4 | 11356.2 | 10829 | 11392.7 | 11716 | 11830.9 | 11064.6 | 11811.6 | 10727.6 | 10973.7 | 11981.7 | 10873.8 | 11863.2 | 10620.5 | 11898.1 | 10732.9 | 11703.1 | 11104.8 | 11623.7 | 11123.9 | 12005.7 | 11082.2 | 11381 | 10981.8 | 9716.2 | 11717.4 | 11407.3 | 10845.9 | 12015.7 | 11729.2 | 11080.4 | 10963.4 | 11773.3 | 10773.7 | 11198.2 | 11883 | 10706.5 | 11975 | 10807.7 | 11768.6 | 11033.8 | 11826.3 | 10526.5 | 11893.8 | 11025.4 | 11813.2 | 11014 | 11846.7 | 11154.6 | 10788.2 | 11635.9 | 10685.7 | 10712.5 | 11701.3 | 11581.8 | 11659.4 | 11023.7 | 11791.6 | 10784 | 11524.2 | 11052.7 | 11494 | 10299.9 | 11679 | 10929.6 | 10924.3 | 11031.1 | 10955.3 | 9488.7 | 10829.7 | 9602.9 | 10790.2 | 10809.8 | 11999.6 | 10833.6 | 12026.2 | 11090.6 | 11919 | 10904.7 | 11039.6 | 10836.6 | 11806.3 | 12050.2 | 11869.9 | 11949.2 | 11959.7 | 11960.2 | 11165.4 | 11968.9 | 12005.7 | 12088.6 | 12087.4 | 12066.4 | 12073.1 | 11220 | 12015.5 | 11266 | 29.3129 | 28.9494 | 28.9422 | 0 | 28.8936 | 28.9889 | 0 | 40.7255 | 0 | 0 | 3.7243 | 0 | 4.174 | 4.0636 | 3.8944 | 4.2023 | 3.9841 | 4.021 | 7.76 | 7.863 | 7.89 | 8.096 | 8.234 | 7.642 | 5.4959 | 5.7896 | 5.5627 | 5.4664 | 5.8581 | 5.851 | 1.1569 | 1.3796 | 1.4131 | 0 | 1.5039 | 1.2533 | 6.3129 | 6.2856 | 6.2478 | 6.141 | 6.3907 | 6.4601 | 1.1901 | 1.3531 | 1.344 | 0 | 1.4622 | 1.5757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259158 | 470 | 249312 | 489 | 484770.838 | 1279.2 | 5.4959 | 5.7896 | 5.5627 | 5.4664 | 5.8581 | 5.851 | 6.3129 | 6.2856 | 6.2478 | 6.141 | 6.3907 | 6.4601 | 907000 | 1000 | 900000 | 2000 | 1799667 | 4467 | 1804000 | 1795200 | 11.7333 | 5.6706 | 1.3414 | 6.3063 | 1.385 | 23.65% | 21.96% | 29.0174 | 22.2249 | 4.0565 | 7.9142 | 1816842.4 | 1799533 | 2091980.5288 | 86.02%
2023-03-04 | 2023 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 335090.89 | 7:02 | 18:46 | 10426.3 | 10815.8 | 10836.4 | 10853.5 | 10813.3 | 10942.4 | 10747.8 | 11176.2 | 10920.5 | 10784.7 | 10737.6 | 10909.6 | 10878.9 | 10833 | 10830.8 | 11004.4 | 10843.1 | 10957.4 | 10903.4 | 10895.7 | 10831.8 | 10921.2 | 10537.4 | 10853.7 | 10730.3 | 9483.8 | 10804.6 | 10624.9 | 10946.5 | 10810.5 | 10720.8 | 10879.3 | 10934.8 | 10986.3 | 10983.2 | 10901.6 | 10991.3 | 10888 | 10853.7 | 10839.1 | 11691.1 | 10618.2 | 11555.4 | 10417.9 | 10951.4 | 12167.3 | 10372.7 | 11652.8 | 10099.1 | 10369 | 11021.9 | 10375.7 | 11305.5 | 10063.3 | 11367.7 | 10161.3 | 10095 | 11381.8 | 10128.7 | 11361.6 | 11287.1 | 9973.4 | 10976 | 10288.5 | 10644.2 | 9985.7 | 10673.1 | 11104.5 | 11269.8 | 10267.9 | 11158.6 | 9845.3 | 10170.3 | 11414 | 10038.2 | 11290.1 | 9782.6 | 11329.7 | 9878.4 | 11112.7 | 10311.6 | 11009.3 | 10384.3 | 11456.8 | 10284.1 | 10628.8 | 10231.6 | 8965.1 | 11124.6 | 10750.2 | 10023.1 | 11493.3 | 11179.8 | 10318 | 10186.5 | 11242.9 | 9934.7 | 10402.1 | 11291.8 | 9826 | 11428.9 | 9949.8 | 11138.2 | 10192.2 | 11247.3 | 9692 | 11296.3 | 10211.7 | 11153.1 | 10160 | 11194.4 | 10314.5 | 9912.3 | 10984.4 | 9809.5 | 9832.3 | 11070.5 | 10884.5 | 11017.9 | 10151 | 11126.7 | 9873 | 10853.9 | 10212.5 | 10812.8 | 9440.2 | 10947.1 | 10001.9 | 10024.3 | 10189.5 | 10022.3 | 8672.4 | 10028 | 8895 | 9961.2 | 9996.3 | 11514.4 | 10038.3 | 11588.7 | 10361.3 | 11392.3 | 10115.2 | 10269.7 | 10011.2 | 11299.1 | 11621.5 | 11373.8 | 11484.8 | 11474.1 | 11468.9 | 10499.9 | 11518.5 | 11556.8 | 11641.6 | 11675.4 | 11634.4 | 11631.6 | 10535.7 | 11590.7 | 10576.3 | 29.4863 | 28.9236 | 28.8732 | 0 | 28.8599 | 28.9571 | 0 | 39.6178 | 0 | 0 | 0.11613 | 0 | 4.5948 | 4.4777 | 4.4407 | 4.5763 | 4.5262 | 4.4514 | 7.788 | 8.158 | 7.311 | 7.96 | 7.602 | 7.946 | 5.1803 | 5.3985 | 5.2334 | 5.0966 | 5.4021 | 5.4372 | 1.092 | 1.2994 | 1.3346 | 0 | 1.3989 | 1.1987 | 5.8871 | 5.7988 | 5.8097 | 5.6736 | 5.8345 | 6.0407 | 1.1306 | 1.2769 | 1.2778 | 0 | 1.3681 | 1.5032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260016 | 472 | 250158 | 491 | 486468.305 | 1283.933 | 5.1803 | 5.3985 | 5.2334 | 5.0966 | 5.4021 | 5.4372 | 5.8871 | 5.7988 | 5.8097 | 5.6736 | 5.8345 | 6.0407 | 858000 | 2000 | 846000 | 2000 | 1697467 | 4733 | 1700000 | 1692734 | 11.7333 | 5.2913 | 1.2647 | 5.8408 | 1.3113 | 23.9% | 22.45% | 29.02 | 19.8669 | 4.5112 | 7.7942 | 1712897.8 | 1697400 | 1949184.1688 | 87.08%
2023-03-05 | 2023 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 335090.89 | 7:00 | 18:49 | 11927.1 | 12257.3 | 12213.8 | 12252.8 | 12197.7 | 12332.2 | 12198.3 | 12539.7 | 12304.3 | 12185.5 | 12202.8 | 12320.5 | 12340.4 | 12280.2 | 12281.3 | 12438.5 | 12255.9 | 12362.1 | 12339.3 | 12303.9 | 12271.5 | 12360.9 | 12079.3 | 12307 | 12209.9 | 11138.8 | 12282.3 | 12155.6 | 12392.2 | 12247.9 | 12217 | 12356.2 | 12397.5 | 12404.4 | 12399.4 | 12351 | 12442.5 | 12369.4 | 12328.4 | 12321.8 | 12922 | 12124.9 | 12809.5 | 11982.5 | 12396.8 | 13315.5 | 11911.6 | 12871.2 | 11746.2 | 11958.8 | 12472.4 | 11950.8 | 12718.5 | 11733.7 | 12693.7 | 11795 | 11725.9 | 12787.1 | 11770.7 | 12754.3 | 12655.9 | 11584.3 | 12479 | 11941.9 | 12210.7 | 11717.5 | 12259.3 | 12587.1 | 12684 | 11941.3 | 12626 | 11587.5 | 11835.7 | 12860.1 | 11762.2 | 12734 | 11535.9 | 12769.3 | 11632 | 12562.3 | 11972.9 | 12498.5 | 12003.2 | 12865.7 | 11940 | 12213.2 | 11848 | 10578.6 | 12547.4 | 12257.7 | 11715.2 | 12854.1 | 12554.2 | 11902 | 11783.5 | 12622.6 | 11648 | 12053 | 12718.4 | 11580.6 | 12779.9 | 11662.2 | 12577.6 | 11882.3 | 12614.4 | 11390.6 | 12693.6 | 11867.1 | 12606 | 11827.8 | 12640.5 | 12006 | 11635.2 | 12457.4 | 11581 | 11594.2 | 12537.3 | 12398.4 | 12491.5 | 11831.1 | 12599.6 | 11627.7 | 12355.5 | 11885.7 | 12317.8 | 11171.5 | 12488.1 | 11759.7 | 11755 | 11845.5 | 11755.2 | 10282.7 | 11744.6 | 10526.2 | 11723.5 | 11728.5 | 12872 | 11733 | 12900.8 | 11980.4 | 12772.3 | 11761.2 | 11891.6 | 11712.3 | 12688.7 | 12917.8 | 12751 | 12830.9 | 12838.2 | 12849.6 | 12077.3 | 12858 | 12853.2 | 12902.8 | 12916.6 | 12909.9 | 12935.5 | 12100.5 | 12917.8 | 12141.6 | 29.4864 | 29.0677 | 29.1984 | 0 | 29.2571 | 29.0776 | 0 | 44.0319 | 0 | 0 | 6.4096 | 0 | 2.4568 | 2.3734 | 2.4228 | 2.4745 | 2.3981 | 2.2663 | 7.114 | 6.339 | 5.528 | 6.921 | 5.342 | 5.468 | 6.0798 | 6.5817 | 6.1154 | 6.0011 | 6.4708 | 6.5172 | 1.2638 | 1.5213 | 1.5445 | 0 | 1.6492 | 1.3855 | 7.0142 | 6.9805 | 7.1205 | 6.7729 | 7.0571 | 7.1718 | 1.2976 | 1.4966 | 1.474 | 0 | 1.5965 | 1.7474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260992 | 473 | 251126 | 492 | 488404.705 | 1288.4 | 6.0798 | 6.5817 | 6.1154 | 6.0011 | 6.4708 | 6.5172 | 7.0142 | 6.9805 | 7.1205 | 6.7729 | 7.0571 | 7.1718 | 976000 | 1000 | 968000 | 1000 | 1936400 | 4467 | 1942000 | 1931933 | 11.8167 | 6.2943 | 1.4729 | 7.0195 | 1.5224 | 23.4% | 21.69% | 29.2174 | 25.2208 | 2.3987 | 6.1187 | 1954884.4 | 1936133 | 2296350.0815 | 84.31%
2023-03-06 | 2023 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 335090.89 | 7:00 | 18:49 | 11720 | 12115.1 | 12110.4 | 12156.3 | 12104 | 12244.8 | 12084.5 | 12402.4 | 12095.3 | 11905.8 | 12019.8 | 12103.1 | 12235.8 | 12106.3 | 12208.3 | 12360.1 | 12193.2 | 12305.4 | 12232.3 | 12190.2 | 12201.4 | 12267.3 | 12019.8 | 12235.7 | 12064 | 10884.4 | 12121.7 | 12015 | 12266.5 | 12142 | 12096.3 | 12191.6 | 12277.9 | 12291.3 | 12287.3 | 12251.7 | 12325.6 | 12248.6 | 12206.4 | 12209.7 | 12791.4 | 12042 | 12681.2 | 11884.2 | 12301.3 | 13202.1 | 11847.2 | 12756.3 | 11519.8 | 11723.1 | 12280.9 | 11720.3 | 12532.1 | 11577.5 | 12454.3 | 11592.3 | 11417.4 | 12430.6 | 11464.8 | 12386.2 | 12251 | 11249.1 | 12036.9 | 11480.5 | 11938.8 | 11461.4 | 11937.3 | 12353.5 | 12327.8 | 11662.6 | 12176.3 | 11219.5 | 11426 | 12453.3 | 11363.2 | 12303.6 | 11057 | 12325.4 | 11159 | 12097.7 | 11807.6 | 12294.2 | 11872.7 | 12696.2 | 11827 | 12189.1 | 11742.8 | 10447.7 | 12466 | 12194 | 11604.1 | 12726.6 | 12451.7 | 11818.3 | 11704.1 | 12522.3 | 11617.4 | 12059.7 | 12727.5 | 11586.1 | 12750.9 | 11679.8 | 12591 | 11921.9 | 12625.1 | 11369.6 | 12719.5 | 11928.4 | 12626.5 | 11848.2 | 12674.7 | 12067.3 | 11672.2 | 12554.9 | 11612.9 | 11638.9 | 12648.3 | 12543.9 | 12604.4 | 11995.8 | 12739.7 | 11742.3 | 12457.1 | 11980.5 | 12433.4 | 11223.2 | 12636.2 | 11901.5 | 11940.4 | 12047.1 | 11931.9 | 10382.4 | 11909.6 | 10594.1 | 11857.8 | 11878.6 | 13018.2 | 11895.1 | 13020.8 | 12129.8 | 12967.7 | 11960 | 12098.2 | 11877.2 | 12775.8 | 12973.2 | 12875.9 | 12941 | 12963.3 | 12990.6 | 12165.7 | 12933.6 | 12986 | 12990.3 | 13008.7 | 12976.3 | 12997.4 | 12164.7 | 13053.2 | 12225.9 | 30.1972 | 29.87 | 29.7554 | 0 | 29.9147 | 29.902 | 0 | 44.9304 | 0 | 0 | 0 | 0 | 2.8259 | 2.8222 | 2.8113 | 2.7787 | 2.8205 | 2.7533 | 5.779 | 6.017 | 5.862 | 6.154 | 6.005 | 5.663 | 6.022 | 6.5167 | 6.1096 | 5.8928 | 6.5327 | 6.5504 | 1.2591 | 1.5103 | 1.551 | 0 | 1.6778 | 1.413 | 6.897 | 6.8719 | 7.0467 | 6.627 | 7.0974 | 7.2258 | 1.2995 | 1.485 | 1.4891 | 0 | 1.6277 | 1.7803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 261951 | 475 | 252098 | 494 | 490328.172 | 1293.067 | 6.022 | 6.5167 | 6.1096 | 5.8928 | 6.5327 | 6.5504 | 6.897 | 6.8719 | 7.0467 | 6.627 | 7.0974 | 7.2258 | 959000 | 2000 | 972000 | 2000 | 1923467 | 4667 | 1927000 | 1918800 | 11.8167 | 6.2707 | 1.4823 | 6.961 | 1.5363 | 23.64% | 22.07% | 29.9279 | 44.9304 | 2.802 | 5.9133 | 1942455.9 | 1923333 | 2274908.4194 | 84.55%
2023-03-07 | 2023 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 335090.89 | 7:03 | 18:44 | 10220 | 10565.7 | 10647.7 | 10741.2 | 10663.1 | 10670.9 | 10490.1 | 10757.4 | 10609.3 | 10399.5 | 10515.6 | 10623.3 | 10680.1 | 10561.8 | 10654.4 | 10770.8 | 10678.8 | 10803.1 | 10775.9 | 10775.6 | 10714.1 | 10749.8 | 10594.8 | 10755.9 | 10454.2 | 9426.2 | 10586 | 10501.2 | 10732.5 | 10619.7 | 10460.5 | 10563.1 | 10479.5 | 10468.2 | 10513 | 10458.2 | 10554.8 | 10535.6 | 10510 | 10462.9 | 11437.3 | 10835.6 | 11315.2 | 10702.9 | 10929.7 | 11631.8 | 10479.9 | 11316.6 | 10082.6 | 10286 | 10742.7 | 10237.7 | 10961.3 | 10137.2 | 10797.2 | 10052.9 | 9900 | 10666.5 | 10065.9 | 10784.7 | 10723 | 9893.1 | 10457.9 | 10033.5 | 10135.8 | 9585.5 | 10119.2 | 10228.9 | 10495.2 | 9703.1 | 10228.5 | 9264.1 | 9775.1 | 10413.2 | 9788.8 | 10328.5 | 9397.2 | 10662.7 | 9649.8 | 10374.7 | 9665.9 | 10061.2 | 9665.9 | 10408.1 | 9712.6 | 10081.2 | 9703.2 | 8544.2 | 10312.7 | 10074.2 | 9684.8 | 10623.2 | 10456.5 | 9964.8 | 9897 | 10391.3 | 9441.1 | 9759.8 | 10320.8 | 9247.9 | 10452.9 | 9366.9 | 10293.2 | 9563.9 | 10345 | 9141.2 | 10389.6 | 9628.3 | 10367.1 | 9662.2 | 10408 | 9795.5 | 9292.7 | 10005.2 | 9263.6 | 9261.3 | 10154.9 | 9984.9 | 10096.4 | 9553.2 | 10176.6 | 9316.3 | 10017.9 | 9600.6 | 9984.4 | 8909.4 | 10122 | 9476.1 | 9428.9 | 9516.5 | 9484.7 | 8199.5 | 9309.8 | 8153.7 | 9076 | 9083.9 | 10044.1 | 9152.1 | 10082.2 | 9362 | 10044.4 | 9218.4 | 9339.5 | 9101.2 | 9810.1 | 9996.9 | 9751 | 9896.7 | 9930.3 | 9986.6 | 9367.6 | 9970.6 | 9685.6 | 9781.7 | 9960.7 | 9947.6 | 9971.2 | 9320.1 | 9628.5 | 9237.5 | 29.6075 | 29.3891 | 29.4973 | 0 | 29.3294 | 29.3285 | 0 | 42.0369 | 0 | 0 | 12.2963 | 0 | 4.5182 | 4.5099 | 4.4349 | 4.4588 | 4.5288 | 4.1921 | 11.995 | 12.06 | 11.926 | 10.587 | 10.565 | 10.593 | 5.2361 | 5.6645 | 5.4999 | 5.0489 | 5.2007 | 4.8074 | 1.1732 | 1.2137 | 1.4461 | 0 | 1.2155 | 0.94904 | 5.8624 | 5.7908 | 6.162 | 5.7497 | 5.3599 | 5.4175 | 1.2235 | 1.1974 | 1.4007 | 0 | 1.1793 | 1.202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 262783.38 | 477 | 252870.2 | 496 | 491926.038 | 1297.667 | 5.2361 | 5.6645 | 5.4999 | 5.0489 | 5.2007 | 4.8074 | 5.8624 | 5.7908 | 6.162 | 5.7497 | 5.3599 | 5.4175 | 832380 | 2000 | 772200 | 2000 | 1597866 | 4600 | 1600580 | 1593266 | 11.6833 | 5.2429 | 1.1995 | 5.7237 | 1.2406 | 22.88% | 21.67% | 29.4303 | 27.1666 | 4.4405 | 11.2877 | 1614851.3 | 1597667 | 1891978.1114 | 84.44%
2023-03-08 | 2023 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 335090.89 | 6:58 | 18:52 | 12210.8 | 12608.7 | 12551.1 | 12557.7 | 12593.6 | 12648.6 | 12643.6 | 12902.6 | 12590 | 12548.8 | 12487.3 | 12593.4 | 12594.7 | 12544.4 | 12537 | 12667.3 | 12497.3 | 12596.2 | 12604.5 | 12672.4 | 12527.4 | 12609.1 | 12331.4 | 12542.2 | 12462.2 | 11479.2 | 12542 | 12404.9 | 12630.3 | 12521.7 | 12455.1 | 12562.2 | 12639 | 12638.8 | 12651.7 | 12617.7 | 12682.7 | 12622.2 | 12572.2 | 12545.6 | 13060.9 | 12333.1 | 12955 | 12191.7 | 12647.3 | 13561.2 | 12148.6 | 13014.3 | 12049.9 | 12275.8 | 12729 | 12269.2 | 12954.3 | 12099.1 | 12918.4 | 12086.7 | 12027.8 | 12989.7 | 12074.1 | 12939.4 | 12859.6 | 11901.9 | 12744.6 | 12299.2 | 12470.3 | 11964.6 | 12496.3 | 12763.2 | 12867.3 | 12169.9 | 12711.7 | 11753.3 | 11996.2 | 13027.3 | 12047.4 | 12913.6 | 11811.6 | 12979.9 | 12025 | 12851.9 | 12178.4 | 12700.8 | 12224.7 | 13017.6 | 12135.8 | 12509.8 | 12077.7 | 10894.6 | 12802 | 12464.8 | 11960.2 | 13028.2 | 12762.8 | 12175.5 | 12068.5 | 12821.2 | 11934.8 | 12291.4 | 12891.4 | 11907.5 | 12948.9 | 11910.3 | 12777 | 12148.3 | 12791.2 | 11662.6 | 12868.3 | 12079.4 | 12796 | 12058 | 12824.8 | 12210.8 | 12000.4 | 12740.7 | 11950.7 | 11924.8 | 12776.8 | 12652.3 | 12709.6 | 12075.5 | 12800.5 | 11886.6 | 12559.1 | 12112.7 | 12525.6 | 11469.5 | 12683.5 | 11997.4 | 12056.2 | 12161.6 | 12041.2 | 10630 | 12019.1 | 10874.3 | 12005 | 12015.3 | 13048.4 | 11979.1 | 13034.2 | 12190.3 | 12962.8 | 12069.1 | 12184 | 12021.4 | 12840.3 | 13056.9 | 12962.2 | 12974.1 | 13015.2 | 13022.8 | 12290.2 | 13004.6 | 13070.8 | 13107.7 | 13107 | 13081.3 | 13106.8 | 12332.9 | 13102.6 | 12261.4 | 27.5023 | 27.086 | 26.9578 | 0 | 27.1226 | 27.0175 | 0 | 42.5183 | 0 | 0 | 6.5185 | 0 | 2.7289 | 2.6746 | 2.6988 | 2.7319 | 2.751 | 2.5936 | 5.358 | 5.362 | 5.813 | 6.509 | 7.696 | 5.265 | 6.329 | 6.8212 | 6.3399 | 6.1892 | 6.6725 | 6.7023 | 1.1372 | 1.3867 | 1.3603 | 0 | 1.534 | 1.2558 | 7.2389 | 7.2168 | 7.3109 | 6.8685 | 7.2912 | 7.3981 | 1.171 | 1.3568 | 1.3265 | 0 | 1.4989 | 1.5781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263779 | 478 | 253856 | 497 | 493899.905 | 1302.467 | 6.329 | 6.8212 | 6.3399 | 6.1892 | 6.6725 | 6.7023 | 7.2389 | 7.2168 | 7.3109 | 6.8685 | 7.2912 | 7.3981 | 995620 | 1000 | 985800 | 1000 | 1973867 | 4800 | 1979420 | 1969067 | 11.9 | 6.509 | 1.3348 | 7.2207 | 1.3863 | 20.51% | 19.2% | 27.1372 | 24.5184 | 2.6965 | 6.0005 | 1994085.7 | 1973867 | 2378020.1585 | 83%
2023-03-09 | 2023 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 335090.89 | 6:55 | 18:51 | 12190.4 | 12630.3 | 12573.6 | 12571.9 | 12608.2 | 12663.9 | 12654.6 | 12912.4 | 12595.2 | 12547.9 | 12478.8 | 12596.2 | 12595.3 | 12518.3 | 12571.2 | 12673.7 | 12576.6 | 12713.7 | 12716.6 | 12748.1 | 12625.8 | 12716.3 | 12304 | 12611.7 | 12467.3 | 11487.9 | 12622.1 | 12459.6 | 12618.4 | 12394.2 | 12305.1 | 12448 | 12500.1 | 12509.8 | 12613 | 12487.7 | 12549.7 | 12488 | 12415.4 | 12374.5 | 12741.3 | 11938.2 | 12618.6 | 11790.2 | 12269.8 | 13273 | 11863.6 | 12788.2 | 11992.4 | 12215.5 | 12697.6 | 12226.7 | 12957.2 | 12054.4 | 12942.1 | 12072.1 | 11922.6 | 12952.8 | 11998.7 | 12895.2 | 12815.6 | 11846.5 | 12684.5 | 12195.5 | 12438.9 | 11911.1 | 12455.2 | 12745.7 | 12855.7 | 12123.1 | 12632.8 | 11655.8 | 11961.4 | 13040.2 | 12008.6 | 12926.8 | 11768.5 | 12932.5 | 11968.6 | 12819.5 | 12204.9 | 12686.1 | 12321.1 | 13054.6 | 12085.6 | 12507.1 | 12102 | 10908 | 12778.6 | 12505.2 | 11877.4 | 12961.4 | 12644.2 | 12011.5 | 11893 | 12671 | 11640.7 | 12006.6 | 12644.8 | 11593.6 | 12685.9 | 11599 | 12492.3 | 11830.4 | 12493 | 11319.1 | 12561.1 | 11717.2 | 12480.7 | 11688.4 | 12518.3 | 11886.8 | 11682.5 | 12472.2 | 11570.9 | 11585.8 | 12437.1 | 12364.5 | 12427.7 | 11756.8 | 12505.5 | 11555.6 | 12251.5 | 11783.3 | 12255.2 | 11100.9 | 12400.4 | 11709.3 | 11744.5 | 11860.1 | 11752 | 10357.6 | 11726.4 | 10554.4 | 11725 | 11723.4 | 12686.5 | 11561.2 | 12647.9 | 11765 | 12620.5 | 11721 | 11875 | 11721.3 | 12486.2 | 12585.1 | 12679.3 | 12599.6 | 12593.5 | 12649 | 11764.7 | 12500 | 12931.3 | 12944.6 | 12919.6 | 12876.7 | 12892.2 | 12013.9 | 12962.6 | 12032.8 | 29.5505 | 29.3364 | 29.2906 | 0 | 29.415 | 29.3837 | 0 | 44.4863 | 0 | 0 | 13.7806 | 0 | 2.9171 | 2.7114 | 2.7837 | 2.8545 | 2.7969 | 2.6461 | 7.849 | 6.932 | 6.916 | 8.174 | 7.702 | 7.568 | 6.3771 | 6.8701 | 6.2038 | 6.225 | 6.5449 | 6.4238 | 1.195 | 1.4316 | 1.3873 | 0 | 1.514 | 1.235 | 7.2576 | 7.2268 | 7.1122 | 6.9429 | 7.0757 | 7.1153 | 1.2334 | 1.4026 | 1.3546 | 0 | 1.4812 | 1.5548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 264771 | 480 | 254821 | 499 | 495850 | 1307 | 6.3771 | 6.8701 | 6.2038 | 6.225 | 6.5449 | 6.4238 | 7.2576 | 7.2268 | 7.1122 | 6.9429 | 7.0757 | 7.1153 | 992000 | 2000 | 965000 | 2000 | 1950095 | 4533 | 1953000 | 1945562 | 11.9333 | 6.4408 | 1.3526 | 7.1218 | 1.4053 | 21% | 19.73% | 29.3953 | 29.1335 | 2.785 | 7.5235 | 1968833.9 | 1949933 | 2331884.4818 | 83.62%
2023-03-10 | 2023 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 335090.89 | 6:53 | 18:51 | 12273.1 | 12674.7 | 12623.8 | 12635.1 | 12665.8 | 12726.4 | 12708.3 | 12973.1 | 12666.9 | 12609 | 12557.5 | 12670.4 | 12671.2 | 12609.8 | 12601.5 | 12746.2 | 12569.9 | 12678.9 | 12678.1 | 12740.8 | 12607 | 12689.1 | 12407.5 | 12625.6 | 12550.1 | 11524.3 | 12620.7 | 12488.8 | 12721 | 12603.4 | 12543.6 | 12685.2 | 12724.8 | 12732.1 | 12750.1 | 12709.5 | 12778.3 | 12712.6 | 12659.3 | 12639.2 | 13159.5 | 12433.1 | 13069.2 | 12295.1 | 12742.4 | 13635.4 | 12231.5 | 13113.2 | 12105.8 | 12339.1 | 12810.9 | 12333.3 | 13041.4 | 12144 | 13006.2 | 12147.6 | 12071.8 | 13074.1 | 12118.5 | 13034.1 | 12947.8 | 11946.7 | 12827.7 | 12361.5 | 12550.3 | 12033.8 | 12573.4 | 12866.5 | 12959.2 | 12248.5 | 12757.1 | 11766.2 | 12049.2 | 13126.8 | 12111.2 | 13007.2 | 11867.3 | 13071.9 | 12084.9 | 12896 | 12277.6 | 12797.2 | 12355.9 | 13128.3 | 12216.2 | 12629.8 | 12159.2 | 10895 | 12877.4 | 12559.8 | 12028.4 | 13110.3 | 12854.8 | 12243.4 | 12131.4 | 12921.6 | 11924.6 | 12380.3 | 13004.1 | 11978.6 | 13060.1 | 11989 | 12890.9 | 12232.7 | 12913.7 | 11725 | 12989.2 | 12175.3 | 12915.4 | 12149.3 | 12944.7 | 12309.2 | 12074 | 12865.5 | 12026.6 | 12005.4 | 12906.8 | 12784.9 | 12842.7 | 12176.9 | 12935.5 | 11961.3 | 12692.5 | 12215.6 | 12644.2 | 11467.9 | 12800.3 | 12090.6 | 12150.1 | 12274.4 | 12134.9 | 10635.6 | 12105.9 | 10874.3 | 12089.3 | 12104.4 | 13189.7 | 12084.5 | 13180.5 | 12316.9 | 13107.8 | 12174.6 | 12295.4 | 12110 | 13000.7 | 13212.2 | 13097.7 | 13138.6 | 13161.4 | 13168.8 | 12405.6 | 13156.3 | 13181.1 | 13223 | 13235.3 | 13211 | 13244 | 12452.7 | 13212.9 | 12374.3 | 30.079 | 29.9967 | 29.8989 | 0 | 30.1346 | 29.9718 | 0 | 45.5271 | 0 | 0 | 19.8238 | 0 | 2.4178 | 2.3254 | 2.3616 | 2.4419 | 2.3653 | 2.3617 | 5.776 | 5.599 | 5.516 | 5.607 | 5.357 | 5.923 | 6.4484 | 6.9282 | 6.4774 | 6.3057 | 6.8143 | 6.7983 | 1.2179 | 1.4682 | 1.4704 | 0 | 1.601 | 1.3337 | 7.3296 | 7.2902 | 7.42 | 7.0167 | 7.3819 | 7.5295 | 1.2562 | 1.44 | 1.4397 | 0 | 1.5672 | 1.6791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 265774 | 481 | 255816 | 501 | 497839.039 | 1311.467 | 6.4484 | 6.9282 | 6.4774 | 6.3057 | 6.8143 | 6.7983 | 7.3296 | 7.2902 | 7.42 | 7.0167 | 7.3819 | 7.5295 | 1003000 | 1000 | 995000 | 2000 | 1989039 | 4467 | 1995000 | 1984572 | 11.9667 | 6.6287 | 1.4182 | 7.328 | 1.4764 | 21.4% | 20.15% | 30.0162 | 32.6754 | 2.379 | 5.6297 | 2008375.1 | 1988667 | 2382909.9236 | 83.46%
2023-03-11 | 2023 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 335090.89 | 6:53 | 18:49 | 12133.5 | 12529.7 | 12479.3 | 12500.9 | 12521.4 | 12586 | 12561.1 | 12833.5 | 12530.5 | 12458.8 | 12425.7 | 12539.3 | 12545.1 | 12475.3 | 12467.9 | 12616.8 | 12432.7 | 12546.8 | 12546.7 | 12604.4 | 12473.5 | 12559.9 | 12277.9 | 12496.5 | 12418.9 | 11401.7 | 12486.7 | 12354.2 | 12584.8 | 12455.7 | 12403.7 | 12551.1 | 12583.7 | 12595.2 | 12610.7 | 12567.1 | 12638 | 12570.6 | 12522.4 | 12499.4 | 13029.4 | 12293.1 | 12938.1 | 12147.2 | 12582.8 | 13488.6 | 12092.1 | 12982.8 | 11982.6 | 12212.4 | 12680.3 | 12202.9 | 12910.2 | 12011.9 | 12874.4 | 12021.5 | 11950 | 12952 | 12003.8 | 12917.5 | 12833.9 | 11830.9 | 12706.1 | 12228.1 | 12422.6 | 11907.3 | 12446.3 | 12742.5 | 12839 | 12118.9 | 12509 | 11530.8 | 12217 | 12744.4 | 11983.7 | 12888.8 | 11753.5 | 12946.8 | 11956.9 | 12770.2 | 12146.8 | 12666.8 | 12222.5 | 13003.1 | 12060.9 | 12492.9 | 12025.1 | 10780.2 | 12735.3 | 12403.5 | 11891.8 | 12935.7 | 12712 | 12094.6 | 11985.3 | 12764.2 | 11791.7 | 12238.8 | 12878.3 | 11844 | 12931 | 11857.7 | 12750.8 | 12098.9 | 12769.1 | 11609.7 | 12846 | 12045.2 | 12770.3 | 12022.9 | 12801.1 | 12180.3 | 11938.2 | 12724 | 11696.9 | 11854.9 | 12764.4 | 12633.5 | 12692.9 | 12046.9 | 12791.7 | 11838.5 | 12542.3 | 12077.8 | 12495 | 11363 | 12656.7 | 11966.8 | 12020.6 | 12127.1 | 11997.2 | 10520.6 | 11975.8 | 10767.2 | 11959.6 | 11967 | 13057.7 | 11948 | 13052.8 | 12182.3 | 12975.2 | 12035.6 | 12148.7 | 11977.1 | 12861.5 | 13071.3 | 12973.8 | 13003.1 | 13023.8 | 13032.2 | 12270.7 | 13015.9 | 13046.1 | 13083.2 | 13097.5 | 13076.6 | 13108.2 | 12311.6 | 13084.8 | 12243.2 | 31.1832 | 30.917 | 31.1331 | 0 | 30.9466 | 31.1772 | 0 | 46.6342 | 0 | 0 | 39.6171 | 0 | 2.6111 | 2.5526 | 2.4968 | 2.7433 | 2.5921 | 2.3321 | 6.454 | 6.397 | 6.323 | 6.743 | 6.83 | 6.512 | 6.4139 | 6.886 | 6.4611 | 6.2909 | 6.7889 | 6.7424 | 1.2226 | 1.4519 | 1.4813 | 0 | 1.5969 | 1.3293 | 7.2627 | 7.2179 | 7.3666 | 7.0069 | 7.3062 | 7.4833 | 1.2634 | 1.4264 | 1.4521 | 0 | 1.5595 | 1.6777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 266766 | 483 | 256799 | 502 | 499806.906 | 1315.933 | 6.4139 | 6.886 | 6.4611 | 6.2909 | 6.7889 | 6.7424 | 7.2627 | 7.2179 | 7.3666 | 7.0069 | 7.3062 | 7.4833 | 992000 | 2000 | 983000 | 1000 | 1967867 | 4466 | 1972000 | 1963401 | 11.9333 | 6.5972 | 1.4164 | 7.2739 | 1.4758 | 21.47% | 20.29% | 31.0714 | 43.1256 | 2.5547 | 6.5432 | 1986493.4 | 1967666 | 2360510.0614 | 83.36%
2023-03-12 | 2023 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 335090.89 | 6:52 | 18:49 | 10287.2 | 10695.5 | 10655.6 | 10664.8 | 10684.3 | 10745.9 | 10720.6 | 11012.4 | 10709.7 | 10635.2 | 10596.7 | 10714.7 | 10703.8 | 10650.1 | 10612.8 | 10776.2 | 10603.9 | 10705.7 | 10727 | 10779.6 | 10649 | 10728.1 | 10413 | 10652.8 | 10577.1 | 9567.1 | 10640.6 | 10503.4 | 10759 | 10629.4 | 10566.6 | 10688.3 | 10747.6 | 10771.1 | 10778.9 | 10729.7 | 10802 | 10729.4 | 10688 | 10675.5 | 11262 | 10438.2 | 11177.9 | 10286.9 | 10742.9 | 11695.4 | 10251.4 | 11216.6 | 10102.6 | 10328.5 | 10837.7 | 10326.7 | 11072.8 | 10127.9 | 11056.2 | 10144 | 10051.9 | 11076.9 | 10093.8 | 11037.9 | 10961 | 9939.7 | 10807.5 | 10310.8 | 10553.6 | 10030.3 | 10570.2 | 10897.1 | 11023.6 | 10243.9 | 10753 | 9723.7 | 10644.8 | 10638.1 | 10108.4 | 11043.8 | 9869.5 | 11129.5 | 10076.8 | 10939.5 | 10276.5 | 10821.7 | 10369.8 | 11164.2 | 10185.8 | 10631.9 | 10197.1 | 9122.7 | 10916.3 | 10598.1 | 10026.2 | 11140.6 | 10903.3 | 10237.6 | 10136.8 | 10951.4 | 9940.9 | 10370.4 | 11072.7 | 9997.6 | 11098.5 | 10001.8 | 10899.9 | 10212.3 | 10971.4 | 9755.2 | 11034.4 | 10173.5 | 10927.8 | 10146.4 | 10974.6 | 10278.1 | 10091.9 | 10916.1 | 10029.8 | 10015.9 | 10971 | 10841.2 | 10887.9 | 10220.4 | 10994.9 | 10001.7 | 10715 | 10185 | 10631.7 | 9582 | 10826 | 10123.9 | 10164.1 | 10297 | 10167.4 | 8934 | 10149.8 | 9147.3 | 10141.5 | 10151.1 | 11266.3 | 10139.6 | 11259.2 | 10352.3 | 11188.3 | 10235.1 | 10345.2 | 10168.2 | 11025.6 | 11255.3 | 11128.6 | 11180.5 | 11189.2 | 11212 | 10420.3 | 11190.1 | 11202.7 | 11245.4 | 11282.4 | 11247.1 | 11267.4 | 10442.4 | 11236 | 10473.6 | 31.0319 | 31.0081 | 31.1056 | 0 | 30.8737 | 30.99 | 0 | 44.4126 | 0 | 0 | 27.7037 | 0 | 2.2841 | 2.2616 | 2.3306 | 2.2721 | 2.4197 | 2.2104 | 5.754 | 5.868 | 6.329 | 6.688 | 6.093 | 6.549 | 5.5144 | 5.847 | 5.5429 | 5.4498 | 5.7956 | 5.6163 | 1.071 | 1.222 | 1.2655 | 0 | 1.3607 | 1.1485 | 6.0418 | 5.9723 | 6.0686 | 5.9563 | 6.0785 | 6.348 | 1.1195 | 1.2029 | 1.2697 | 0 | 1.3441 | 1.4374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 267610 | 484 | 257636 | 504 | 501482.573 | 1320.533 | 5.5144 | 5.847 | 5.5429 | 5.4498 | 5.7956 | 5.6163 | 6.0418 | 5.9723 | 6.0686 | 5.9563 | 6.0785 | 6.348 | 844000 | 1000 | 837000 | 2000 | 1675667 | 4600 | 1678000 | 1671067 | 11.95 | 5.6277 | 1.2136 | 6.0776 | 1.2747 | 21.56% | 20.97% | 31.0019 | 36.0582 | 2.2964 | 6.2135 | 1693246.2 | 1675467 | 1979852.1559 | 84.63%
2023-03-13 | 2023 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 335090.89 | 6:54 | 18:52 | 11480.3 | 11876.8 | 11829.3 | 11838.7 | 11863.7 | 11937.5 | 11909.9 | 12161.7 | 11859.6 | 11783.5 | 11775.2 | 11867.9 | 11909.2 | 11818.8 | 11830 | 11977.5 | 11809.4 | 11894.2 | 11824.1 | 11615 | 11839.4 | 11908.1 | 11647.5 | 11860.2 | 11775.8 | 10779.9 | 11831.6 | 11710 | 11935.3 | 11819.3 | 11772.8 | 11827.7 | 11936 | 11946 | 11965.5 | 11924.6 | 11993.9 | 11924.9 | 11881.2 | 11860.9 | 12300.4 | 11581.5 | 12229 | 11428.9 | 11873.8 | 12735 | 11381.4 | 12244.4 | 11328.8 | 11559 | 12014.9 | 11545.8 | 12232.8 | 11373.1 | 12218.6 | 11373.3 | 11265.1 | 12244.8 | 11313.9 | 12204.2 | 12111.9 | 11144.6 | 11973.2 | 11527 | 11801 | 11295.3 | 11824.7 | 12109.5 | 12211.2 | 11521.4 | 11929.1 | 10963.8 | 11874.2 | 11908.8 | 11376.9 | 12250.7 | 11124.6 | 12317.5 | 11333.9 | 12132 | 11552.8 | 12070.5 | 11624.6 | 12372.2 | 11546.2 | 11960.7 | 11456.9 | 10300.3 | 12147.7 | 11851.5 | 11313.2 | 12376.7 | 12132.9 | 11519.2 | 11406.1 | 12158.3 | 11222.6 | 11650.5 | 12280.1 | 11270.2 | 12332.4 | 11300.5 | 12174.7 | 11527.2 | 12198 | 11033.6 | 12271.9 | 11482.8 | 12190.6 | 11448.7 | 12234.7 | 11614.9 | 11337.7 | 12103.7 | 11160 | 11247.9 | 12171.5 | 12027 | 12111.9 | 11454.9 | 12166 | 11257.7 | 11989.9 | 11511.9 | 11946.4 | 10834.6 | 12065.4 | 11379.1 | 11382.6 | 11499.2 | 11402.3 | 9995.4 | 11303.8 | 10172 | 11273.2 | 11286.1 | 12317.9 | 11312.7 | 12294.2 | 11497.4 | 12233.7 | 11368.2 | 11486.2 | 11301.7 | 12125.5 | 12309.2 | 12225.6 | 12249.5 | 12264.7 | 12283.1 | 11580.5 | 12253.9 | 12282.1 | 12321.3 | 12325.9 | 12300.1 | 12328.8 | 11608.6 | 12332.7 | 11662.2 | 31.8999 | 31.6562 | 31.4925 | 0 | 31.7832 | 31.627 | 0 | 46.2711 | 0 | 0 | 44.7025 | 0 | 2.4148 | 2.4205 | 2.3531 | 2.4778 | 2.3915 | 2.3263 | 5.298 | 5.047 | 5.47 | 6.306 | 5.374 | 5.767 | 6.2618 | 6.6835 | 6.2536 | 6.1566 | 6.5686 | 6.4053 | 1.166 | 1.4578 | 1.407 | 0 | 1.608 | 1.3327 | 6.9744 | 6.9578 | 6.9944 | 6.6999 | 7.0652 | 7.143 | 1.2147 | 1.4342 | 1.3995 | 0 | 1.5832 | 1.6696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 268549 | 486 | 258569 | 506 | 503347.306 | 1323.4 | 6.2618 | 6.6835 | 6.2536 | 6.1566 | 6.5686 | 6.4053 | 6.9744 | 6.9578 | 6.9944 | 6.6999 | 7.0652 | 7.143 | 939000 | 2000 | 933000 | 2000 | 1864733 | 2867 | 1868000 | 1861866 | 11.9667 | 6.3882 | 1.3943 | 6.9725 | 1.4602 | 21.83% | 20.94% | 31.6918 | 45.4868 | 2.3973 | 5.5437 | 1883552 | 1864400 | 2250326.8235 | 82.85%
2023-03-14 | 2023 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 335090.89 | 6:51 | 18:48 | 11438.2 | 11832.6 | 11770.2 | 11794.7 | 11802.2 | 11878.6 | 11838.9 | 12103 | 11840.1 | 11748.9 | 11732.4 | 11844.1 | 11865.1 | 11784.4 | 11778 | 11929.5 | 11757.5 | 11842.6 | 11870.6 | 11922.1 | 11801.8 | 11864.2 | 11589.7 | 11816.1 | 11729.3 | 10663.4 | 11796.2 | 11668.4 | 11889.6 | 11770.4 | 11731.2 | 11839.1 | 11889.3 | 11898.9 | 11925 | 11883.8 | 11948.2 | 11882.2 | 11840.5 | 11821.4 | 12347.5 | 11608.6 | 12262.6 | 11443.6 | 11903.1 | 12794.9 | 11396.5 | 12295.1 | 11258.8 | 11500.6 | 11979.2 | 11490 | 12196.2 | 11285.7 | 12175.7 | 11309.7 | 11192.7 | 12179.1 | 11251.3 | 12147.3 | 12048.6 | 11074.2 | 11897 | 11452.4 | 11728.4 | 11191.7 | 11748.8 | 12033.3 | 12139.1 | 11411.4 | 11813.6 | 10804.8 | 11804.3 | 11818.2 | 11276 | 12172.2 | 11003.2 | 12245.8 | 11226.6 | 12059 | 11441.8 | 11973.2 | 11524.2 | 12292.9 | 11489 | 12081 | 11347.7 | 10087.5 | 12058.9 | 11729.1 | 11194.6 | 12307.7 | 12040.8 | 11410.1 | 11299 | 12052.6 | 11069.6 | 11519.3 | 12178 | 11119.4 | 12226.3 | 11140.2 | 12056 | 11374.4 | 12085 | 10865.7 | 12153.8 | 11327.4 | 12083.9 | 11313.9 | 12123.4 | 11470.3 | 11197.4 | 12019.7 | 11178.5 | 11149 | 12069.3 | 11951.5 | 12006.3 | 11334.3 | 12085.9 | 11108.6 | 11862.4 | 11357.7 | 11810.3 | 10618.3 | 11964.4 | 11242.7 | 11281.6 | 11415.8 | 11276.8 | 9829.2 | 11251.8 | 10041.6 | 11250.1 | 11248.9 | 12365.1 | 11253.6 | 12364.7 | 11485.2 | 12283.8 | 11346.6 | 11468.9 | 11268.9 | 12164.7 | 12376.2 | 12268.4 | 12311.8 | 12321.2 | 12334.9 | 11570.6 | 12320 | 12347.1 | 12386.6 | 12400.9 | 12369 | 12401 | 11602 | 12392.4 | 11533.2 | 32.09 | 31.8917 | 31.9137 | 0 | 32.2328 | 31.9891 | 0 | 46.2108 | 0 | 0 | 44.7407 | 0 | 2.7789 | 2.6845 | 2.6834 | 2.6504 | 2.771 | 2.7547 | 6.566 | 6.685 | 6.474 | 7.052 | 7.026 | 6.466 | 6.0809 | 6.522 | 6.1109 | 5.9833 | 6.3978 | 6.288 | 1.1776 | 1.413 | 1.4251 | 0 | 1.5513 | 1.2933 | 6.8035 | 6.7857 | 6.8792 | 6.6056 | 6.8366 | 7.0236 | 1.2223 | 1.3917 | 1.4068 | 0 | 1.5215 | 1.6278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 269506 | 502 | 259518 | 522 | 505203.639 | 1327.2 | 6.0809 | 6.522 | 6.1109 | 5.9833 | 6.3978 | 6.288 | 6.8035 | 6.7857 | 6.8792 | 6.6056 | 6.8366 | 7.0236 | 957000 | 16000 | 949000 | 16000 | 1856333 | 3800 | 1874000 | 1852533 | 11.95 | 6.2305 | 1.3721 | 6.8224 | 1.434 | 22.02% | 21.02% | 32.0235 | 45.4758 | 2.7205 | 6.7115 | 1874514.8 | 1856133 | 2211829.9347 | 83.92%
2023-03-15 | 2023 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 335090.89 | 6:56 | 18:47 | 6461.5 | 6775.9 | 6773.6 | 6755.4 | 6789.2 | 6826.5 | 6789.9 | 7067.5 | 6819.8 | 6743.6 | 6703 | 6817.1 | 6793.5 | 6777.3 | 6733 | 6860.8 | 6710.9 | 6782.7 | 6809.6 | 6837.8 | 6750 | 6822.9 | 6543.2 | 6743 | 6682.7 | 5893.5 | 6743.5 | 6616.3 | 6848.3 | 6732.5 | 6689.6 | 6848.7 | 6791.5 | 6823.7 | 6860.8 | 6798.8 | 6849.8 | 6786 | 6754.7 | 6762.4 | 7310.2 | 6531.8 | 7218.3 | 6415.7 | 6794.4 | 7758.4 | 6372.5 | 7274.7 | 6315.9 | 6492.2 | 6918.5 | 6474.3 | 7144 | 6318.6 | 7133.3 | 6351.1 | 6142.7 | 7044 | 6004.5 | 6971 | 6917.2 | 6065 | 6757.1 | 6319.8 | 6699.2 | 6277 | 6717.2 | 7017.8 | 7155.9 | 6451.4 | 7110.1 | 6215.1 | 6827.5 | 6780 | 6347.9 | 7160.2 | 6145.1 | 7245.3 | 6326.6 | 7102.2 | 6469.2 | 6942.8 | 6550.3 | 7256.2 | 6397.8 | 6776.1 | 6431.1 | 5627 | 7030.1 | 6742.1 | 6243 | 7242.4 | 7011.6 | 6422.5 | 6349.7 | 7007.9 | 6164.5 | 6518.3 | 7149.3 | 6211.7 | 7160.8 | 6201.2 | 6955.6 | 6375.1 | 7032.5 | 6017 | 7058.3 | 6331.3 | 6947.2 | 6298.7 | 6984.9 | 6405 | 6292.9 | 6988.7 | 6191 | 6208.8 | 7055.3 | 6913.7 | 6964.2 | 6396.9 | 7051.4 | 6187.1 | 6789.5 | 6331 | 6707.5 | 5885.6 | 6875.3 | 6286.6 | 6310.9 | 6421.5 | 6324.9 | 5458.9 | 6304 | 5569.9 | 6324.9 | 6334.1 | 7366.2 | 6314.1 | 7352.5 | 6475.3 | 7264.4 | 6378.5 | 6479.9 | 6336.5 | 7076.5 | 7351.3 | 7199.5 | 7266.8 | 7269.3 | 7309.5 | 6547.2 | 7277.9 | 7309.5 | 7345.1 | 7378.7 | 7352.2 | 7346.6 | 6561.6 | 7287.2 | 6470.7 | 30.2818 | 30.064 | 30.0577 | 0 | 30.0746 | 30.051 | 0 | 36.8329 | 0 | 0 | 71.4715 | 0 | 3.335 | 3.2958 | 3.3642 | 3.1865 | 3.2556 | 3.2338 | 10.993 | 11.073 | 10.134 | 10.93 | 10.541 | 10.682 | 3.3583 | 3.4831 | 3.3843 | 3.327 | 3.4179 | 3.1373 | 0.64919 | 0.76418 | 0.77742 | 0 | 0.84727 | 0.71813 | 3.4399 | 3.3877 | 3.3958 | 3.4613 | 3.4115 | 3.6743 | 0.69074 | 0.76005 | 0.79412 | 0 | 0.85472 | 0.8872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270042 | 503 | 260051 | 523 | 506268.506 | 1331.867 | 3.3583 | 3.4831 | 3.3843 | 3.327 | 3.4179 | 3.1373 | 3.4399 | 3.3877 | 3.3958 | 3.4613 | 3.4115 | 3.6743 | 536000 | 1000 | 533000 | 1000 | 1064867 | 4667 | 1067000 | 1060200 | 11.85 | 3.3513 | 0.75124 | 3.4618 | 0.79737 | 22.42% | 23.03% | 30.1058 | 54.1522 | 3.2785 | 10.7255 | 1073397 | 1064734 | 1177239.4947 | 90.44%
2023-03-16 | 2023 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 335090.89 | 6:51 | 18:48 | 9835.9 | 10216 | 10204.3 | 10226.5 | 10223.1 | 10303.1 | 10241.9 | 10539.3 | 10216.6 | 10094.1 | 10131.7 | 10219.9 | 10333.3 | 10258.7 | 10277.9 | 10386 | 10265.1 | 10356.4 | 10376.3 | 10427 | 10294.9 | 10374.1 | 10137.5 | 10323.2 | 10261.8 | 9199.1 | 10311.1 | 10177.1 | 10433.8 | 10325.6 | 10319.6 | 10423.5 | 10450 | 10427.9 | 10441.1 | 10405.8 | 10493.1 | 10467 | 10449.1 | 10449.4 | 11029.9 | 10288.4 | 10946.3 | 10146.6 | 10587 | 11465.6 | 10103.7 | 10966.2 | 9755.6 | 10000.5 | 10471.8 | 10015.6 | 10696.5 | 9776.3 | 10674.4 | 9807.9 | 9693.7 | 10679.2 | 9704.1 | 10637.6 | 10511 | 9477.1 | 10364.2 | 9878.8 | 10198.6 | 9692.4 | 10211.1 | 10506.4 | 10595.4 | 9891 | 10568.3 | 9548.4 | 10237.9 | 10233.5 | 9683.8 | 10572.6 | 9414.2 | 10602.6 | 9609.3 | 10459.9 | 9916.6 | 10403.3 | 9998.8 | 10739.7 | 9862.9 | 10319.8 | 9926.1 | 8736.2 | 10652 | 10306.1 | 9784.7 | 10865.7 | 10640.6 | 10043.3 | 9943.7 | 10705.2 | 9822.2 | 10302.2 | 10948.1 | 9887.5 | 10961 | 9895.1 | 10768.7 | 10128.8 | 10816.9 | 9575.8 | 10898.2 | 10096.1 | 10830 | 10076.3 | 10888.6 | 10242.3 | 9995.5 | 10823.2 | 9938.2 | 9914.7 | 10852.2 | 10736.2 | 10795.2 | 10151.4 | 10903.7 | 9890 | 10658.8 | 10143 | 10598.1 | 9392.6 | 10763.1 | 10007.4 | 10050.4 | 10206.7 | 10068.2 | 8704.6 | 9993.1 | 8865.1 | 10009.3 | 10031.8 | 11107.5 | 10036.8 | 11098.9 | 10264.8 | 11073 | 10148.7 | 10268.4 | 10079.5 | 10709.3 | 10935.6 | 10813.5 | 10887.7 | 10940.6 | 11007.9 | 10278.5 | 10939.6 | 10739.8 | 10782 | 10763.7 | 10779.3 | 10840.1 | 10135.3 | 10798.7 | 10046 | 29.2904 | 29.1313 | 29.1489 | 0 | 29.0027 | 29.3116 | 0 | 42.5342 | 0 | 0 | 77.5602 | 0 | 3.4289 | 3.4427 | 3.1633 | 3.506 | 3.3956 | 2.916 | 7.425 | 7.373 | 6.205 | 6.724 | 6.938 | 6.969 | 5.2449 | 5.6531 | 5.3936 | 5.2174 | 5.6514 | 5.4241 | 0.98187 | 1.2768 | 1.2586 | 0 | 1.4153 | 1.1772 | 5.7504 | 5.8189 | 5.9269 | 5.5976 | 6.0114 | 6.1045 | 1.0254 | 1.2599 | 1.2546 | 0 | 1.4034 | 1.4695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270859 | 504 | 260873 | 525 | 507900.973 | 1336.467 | 5.2449 | 5.6531 | 5.3936 | 5.2174 | 5.6514 | 5.4241 | 5.7504 | 5.8189 | 5.9269 | 5.5976 | 6.0114 | 6.1045 | 817000 | 1000 | 822000 | 2000 | 1632467 | 4600 | 1636000 | 1627867 | 11.95 | 5.4307 | 1.222 | 5.8683 | 1.2826 | 22.5% | 21.86% | 29.177 | 60.0472 | 3.3088 | 6.939 | 1648951.4 | 1632400 | 1934676.0821 | 84.38%
2023-03-17 | 2023 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 335090.89 | 6:53 | 18:49 | 10859.9 | 11240.7 | 11168 | 11149.4 | 11196 | 11255.5 | 11260.1 | 11540.3 | 11238.5 | 11195.5 | 11132.1 | 11246.5 | 11251.2 | 11206.6 | 11143.8 | 11300.5 | 11117.7 | 11221 | 11253.3 | 11297.4 | 11184 | 11257.1 | 10979 | 11186 | 11101.8 | 10127.7 | 11203.3 | 11056.9 | 11295.1 | 11173.1 | 11108.3 | 11238.1 | 11368.2 | 11332.1 | 11296 | 11266.7 | 11331.6 | 11268.2 | 11229.9 | 11289.5 | 11709.9 | 10956.1 | 11660.8 | 10864.2 | 11337.8 | 12233.4 | 10795.1 | 11664 | 10719.9 | 10907.9 | 11384.4 | 10913.7 | 11615.2 | 10765.6 | 11552.3 | 10741.1 | 10605.9 | 11548.7 | 10681.1 | 11523.3 | 11472.5 | 10524.5 | 11278.5 | 10837.2 | 11102 | 10616.2 | 11107.8 | 11390.9 | 11508.4 | 10793.1 | 11491.4 | 10495 | 11158.1 | 11152.2 | 10669.5 | 11507.7 | 10405.6 | 11600.1 | 10651.5 | 11462.6 | 10840 | 11307.5 | 10957.8 | 11673.9 | 10784.4 | 11185.9 | 10787.4 | 9613.6 | 11535.9 | 11134.2 | 10687.6 | 11754.1 | 11505.5 | 10940.7 | 10852.6 | 11516.1 | 10628.8 | 11011.4 | 11599.3 | 10652 | 11688.2 | 10659 | 11497.4 | 10879.2 | 11556.4 | 10409.1 | 11619 | 10818.3 | 11559.7 | 10847 | 11590.8 | 10958.6 | 10764.9 | 11479.7 | 10677 | 10682 | 11532.9 | 11412.8 | 11451 | 10865.8 | 11553.2 | 10660.1 | 11276.7 | 10864.7 | 11223.5 | 10208.8 | 11432.3 | 10790.9 | 10848.5 | 10980.8 | 10850.6 | 9467.9 | 10856.9 | 9741.3 | 10873.9 | 10877.5 | 11813 | 10785.8 | 11785.7 | 10963.9 | 11768.8 | 10909.7 | 10999.6 | 10876.8 | 11531.2 | 11753.9 | 11668.8 | 11717.9 | 11735 | 11759.2 | 11025.4 | 11714.4 | 11786 | 11779.1 | 11795.1 | 11762.1 | 11757.4 | 11020.8 | 11788 | 10951.8 | 25.9985 | 25.6381 | 25.484 | 0 | 25.7042 | 25.8728 | 0 | 38.5149 | 0 | 0 | 30.5225 | 0 | 3.3194 | 3.3015 | 3.2824 | 3.3158 | 3.2716 | 3.1622 | 6.599 | 5.851 | 6.143 | 6.2 | 6.272 | 5.941 | 5.7615 | 6.1241 | 5.6987 | 5.6423 | 6.0234 | 5.8629 | 0.93749 | 1.1233 | 1.1524 | 0 | 1.3732 | 1.0906 | 6.3511 | 6.3241 | 6.291 | 6.0375 | 6.4725 | 6.5803 | 0.97124 | 1.1151 | 1.132 | 0 | 1.3585 | 1.3498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 271746 | 506 | 261758 | 527 | 509664.973 | 1341.267 | 5.7615 | 6.1241 | 5.6987 | 5.6423 | 6.0234 | 5.8629 | 6.3511 | 6.3241 | 6.291 | 6.0375 | 6.4725 | 6.5803 | 887000 | 2000 | 885000 | 2000 | 1764000 | 4800 | 1768000 | 1759200 | 11.9333 | 5.8521 | 1.1354 | 6.3428 | 1.1853 | 19.4% | 18.69% | 25.7395 | 34.5187 | 3.2755 | 6.1677 | 1784846.3 | 1764000 | 2117609.2728 | 83.3%
2023-03-18 | 2023 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 335090.89 | 6:55 | 18:55 | 12233.7 | 12629.1 | 12601.9 | 12605.8 | 12641.6 | 12695.9 | 12676.7 | 12939.5 | 12624.2 | 12567.7 | 12500.6 | 12621.1 | 12646.9 | 12576.7 | 12594.5 | 12740.5 | 12547.6 | 12655 | 12651.3 | 12694.3 | 12594 | 12673.9 | 12390.7 | 12599.3 | 12507.7 | 11506.8 | 12594.5 | 12454.2 | 12705.4 | 12581.2 | 12529.7 | 12664.3 | 12696.3 | 12698.8 | 12710.9 | 12670.5 | 12739.7 | 12686.8 | 12637.5 | 12625.1 | 13144.4 | 12422.2 | 13048.2 | 12298.6 | 12735.9 | 13620.8 | 12208.4 | 13084.9 | 12082.4 | 12277.3 | 12780.1 | 12298.1 | 13018.2 | 12129.1 | 12974.7 | 12129.1 | 12049.1 | 13043.8 | 12090.8 | 12996.2 | 12924.3 | 11928 | 12765 | 12292 | 12494.1 | 11988.9 | 12526 | 12806.4 | 12923.5 | 12192.3 | 12914 | 11914.4 | 12580.5 | 12603.4 | 12079.4 | 12968 | 11840.9 | 13030.3 | 12059.4 | 12916 | 12202.9 | 12719.3 | 12292.5 | 13054 | 12125.7 | 12562 | 12127.2 | 10905.4 | 12858.4 | 12478.8 | 12026.7 | 13093.4 | 12832.8 | 12233.2 | 12133.3 | 12848.4 | 11943.1 | 12321.8 | 12955.4 | 11940 | 13012.5 | 11951.2 | 12830.3 | 12192.4 | 12857.4 | 11694.4 | 12930.7 | 12115.5 | 12874.7 | 12136 | 12913 | 12284.1 | 12030 | 12799.7 | 11932 | 11961.1 | 12852.8 | 12702.9 | 12771.2 | 12118.8 | 12851.2 | 11918.1 | 12599.3 | 12163.1 | 12485 | 11494.7 | 12739.2 | 12058.3 | 12096.4 | 12215.4 | 12088.8 | 10636.8 | 12049.6 | 10904 | 12046.9 | 11985.5 | 13083.6 | 11997.3 | 13071.8 | 12205.2 | 13013.9 | 12100.3 | 12207.2 | 12062.5 | 12874.1 | 13094.9 | 12986.5 | 13030.6 | 13038.8 | 13055.2 | 12304.1 | 13043.5 | 13116.8 | 13132.2 | 13132.5 | 13110.9 | 13129 | 12343.6 | 13119.5 | 12269.9 | 24.9633 | 24.4984 | 24.6189 | 0 | 24.6096 | 24.6709 | 0 | 37.4659 | 0 | 0 | 29 | 0 | 3.6894 | 3.6208 | 3.5464 | 3.8473 | 3.5688 | 3.5992 | 6.763 | 6.296 | 6.216 | 7.026 | 6.498 | 6.014 | 6.4384 | 6.8586 | 6.4847 | 6.3148 | 6.7006 | 6.5052 | 1.2068 | 1.4701 | 1.5255 | 0 | 1.5854 | 1.2722 | 7.1017 | 7.0446 | 7.1686 | 6.8607 | 7.1349 | 7.2966 | 1.2475 | 1.4614 | 1.4869 | 0 | 1.566 | 1.5799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 272746 | 508 | 262747 | 529 | 511644.373 | 1346 | 6.4384 | 6.8586 | 6.4847 | 6.3148 | 6.7006 | 6.5052 | 7.1017 | 7.0446 | 7.1686 | 6.8607 | 7.1349 | 7.2966 | 1000000 | 2000 | 989000 | 2000 | 1979400 | 4733 | 1985000 | 1974667 | 12 | 6.5504 | 1.412 | 7.1012 | 1.4683 | 21.56% | 20.68% | 24.6722 | 33.2329 | 3.6453 | 6.4688 | 2001362.2 | 1979334 | 2382220.8105 | 83.09%
2023-03-19 | 2023 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 335090.89 | 6:56 | 18:54 | 7794.1 | 8104.5 | 8112 | 8120.4 | 8126 | 8163.1 | 8132.3 | 8359.8 | 8112.9 | 8063.6 | 7985.9 | 8090.7 | 8077.9 | 8046.5 | 8019.9 | 8131.4 | 7977.4 | 8049.9 | 8051.4 | 7955.2 | 8014.5 | 8083.6 | 7839.8 | 8009.2 | 7941.9 | 7149 | 8024 | 7888 | 8110.6 | 8028.1 | 7936.8 | 7506.9 | 8092.6 | 8106.2 | 8126.8 | 8088.9 | 8151.7 | 8107.3 | 8073.3 | 8055.3 | 8337.1 | 7679.4 | 8269.3 | 7575.2 | 7974 | 8762.4 | 7556 | 8299.1 | 7620.2 | 7771.4 | 8201.7 | 7789.3 | 8390.3 | 7642.5 | 8368.5 | 7637 | 7579.3 | 8402.4 | 7615.1 | 8373.9 | 8317.2 | 7492 | 8168 | 7755.4 | 7951.1 | 7559.8 | 7963.8 | 8224.1 | 8316.9 | 7700.1 | 8277.3 | 7439.8 | 8033.1 | 7988.7 | 7595.9 | 8311.7 | 7397.5 | 8396.2 | 7583.3 | 8289.6 | 7720 | 8124.7 | 7791.8 | 8425.2 | 7683 | 8028.5 | 7719.1 | 6835.4 | 8290.8 | 8013.8 | 7543.9 | 8453.9 | 8219.7 | 7703.8 | 7645.2 | 8268.4 | 7570.1 | 7822.8 | 8406.7 | 7535.2 | 8422.1 | 7541.8 | 8261.9 | 7734.7 | 8305.8 | 7349.5 | 8353.3 | 7680.3 | 8269.3 | 7661.1 | 8317.7 | 7770.4 | 7600.1 | 8235.7 | 7380.9 | 7515 | 8310.5 | 8165 | 8234.5 | 7677.1 | 8281.4 | 7484.8 | 8073.9 | 7675.2 | 7794.8 | 7133.2 | 8144 | 7575.5 | 7602.3 | 7722.6 | 7604.4 | 6631.4 | 7600.4 | 6808.2 | 7680.5 | 7672.7 | 8461.9 | 7588.3 | 8481.7 | 7771.6 | 8436.8 | 7693.7 | 7791.3 | 7660.8 | 8223.7 | 8392.5 | 8317.6 | 8375.7 | 8391.1 | 8416.2 | 7811.1 | 8387.7 | 8401 | 8403.1 | 8410.5 | 8381.4 | 8397.7 | 7773.2 | 8434.2 | 7715.7 | 22.8174 | 22.533 | 22.4551 | 0 | 22.5152 | 22.6391 | 0 | 30.6879 | 0 | 0 | 52.2923 | 0 | 3.6655 | 3.59 | 3.5616 | 3.7376 | 3.5688 | 3.4765 | 12.412 | 11.687 | 11.218 | 11.137 | 11.113 | 11.65 | 4.054 | 4.25 | 4.143 | 4.0013 | 4.2211 | 3.9428 | 0.84291 | 0.81035 | 1.0213 | 0 | 0.86733 | 0.70574 | 4.3083 | 4.1827 | 4.3702 | 4.4206 | 4.2075 | 4.5482 | 0.87479 | 0.80721 | 1.0045 | 0 | 0.85777 | 0.88322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273381 | 510 | 263377 | 531 | 512904.173 | 1350.667 | 4.054 | 4.25 | 4.143 | 4.0013 | 4.2211 | 3.9428 | 4.3083 | 4.1827 | 4.3702 | 4.4206 | 4.2075 | 4.5482 | 635000 | 2000 | 630000 | 2000 | 1259800 | 4667 | 1261000 | 1255133 | 11.9667 | 4.102 | 0.84952 | 4.3396 | 0.88549 | 20.71% | 20.4% | 22.592 | 41.4901 | 3.6 | 11.5362 | 1273607.5 | 1259667 | 1470930.8068 | 85.64%
2023-03-20 | 2023 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 335090.89 | 6:54 | 18:45 | 12057.1 | 12439.2 | 12407.6 | 12407.5 | 12462.9 | 12522.7 | 12508.1 | 12776.8 | 12434.4 | 12422.9 | 12366.1 | 12454.7 | 12504.7 | 12430.4 | 12459.6 | 12609.7 | 12362.3 | 12439.5 | 12452.8 | 12531.6 | 12399.9 | 12447.8 | 12332.1 | 12449.5 | 12358.8 | 11393.9 | 12415.6 | 12268.9 | 12579.5 | 12588.5 | 12560.9 | 12581.3 | 12715.6 | 12634 | 12569.2 | 12570.4 | 12706.5 | 12716.1 | 12680.9 | 12662 | 13034.8 | 12347.8 | 12927.1 | 12199.1 | 12617 | 13481.2 | 12109.2 | 12959.3 | 12004 | 12208.7 | 12643.8 | 12211.2 | 12835.2 | 12060.3 | 12818.5 | 12024.9 | 11986.1 | 12894.4 | 11989.3 | 12843.5 | 12727.1 | 11775 | 12593.7 | 12101.5 | 12445.3 | 11932.9 | 12476.7 | 12701.2 | 12829.3 | 12144.6 | 12783.6 | 11833 | 12497.3 | 12466.2 | 11967.9 | 12758.4 | 11595.9 | 12805.1 | 11876.6 | 12675.7 | 12167.9 | 12638.1 | 12272 | 12974.3 | 12102.6 | 12468.9 | 12032.3 | 10873.9 | 12809.6 | 12389.6 | 12000.9 | 13059.9 | 12846.2 | 12306.3 | 12210.9 | 12899.4 | 12078.3 | 12395 | 12957.6 | 11979.5 | 12981.2 | 11942.7 | 12774.8 | 12164 | 12757.9 | 11648.4 | 12781.7 | 12006.9 | 12654.2 | 11942.6 | 12709.2 | 12109.6 | 12075.2 | 12745.4 | 11927.6 | 11914.1 | 12720.2 | 12605 | 12638.2 | 12065.7 | 12741.8 | 11845.7 | 12436.4 | 12007.5 | 12413.6 | 11419.7 | 12630.7 | 11981 | 12089.9 | 12220.5 | 12050 | 10632.6 | 12081.1 | 10944.8 | 12059.4 | 12043.1 | 13104.6 | 12047.1 | 13129.7 | 12260.3 | 12962.6 | 12085.2 | 12170.6 | 12051.4 | 12729.6 | 12925.4 | 12807.7 | 12925.7 | 13060.4 | 13108.3 | 12402.7 | 13028.6 | 12628.5 | 12701 | 12740.8 | 12746 | 12809.7 | 12093.6 | 12816.8 | 12014.2 | 25.3861 | 24.962 | 24.8936 | 0 | 25.0632 | 25.0086 | 0 | 39.5693 | 0 | 0 | 16.5217 | 0 | 2.9463 | 2.9265 | 2.7702 | 2.8746 | 2.8092 | 2.7443 | 5.904 | 5.574 | 5.214 | 5.858 | 5.186 | 5.79 | 6.4586 | 6.9298 | 6.4895 | 6.4163 | 6.7762 | 6.6006 | 1.1747 | 1.3954 | 1.3991 | 0 | 1.4542 | 1.2309 | 7.1403 | 7.1671 | 7.1918 | 6.9623 | 7.2265 | 7.3939 | 1.2057 | 1.3819 | 1.3865 | 0 | 1.4486 | 1.5255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274371 | 511 | 264359 | 532 | 514866.707 | 1355.4 | 6.4586 | 6.9298 | 6.4895 | 6.4163 | 6.7762 | 6.6006 | 7.1403 | 7.1671 | 7.1918 | 6.9623 | 7.2265 | 7.3939 | 990000 | 1000 | 982000 | 1000 | 1962534 | 4733 | 1970000 | 1957801 | 11.85 | 6.6118 | 1.3308 | 7.1803 | 1.3896 | 20.13% | 19.35% | 25.0627 | 28.0455 | 2.8452 | 5.5877 | 1985440.5 | 1962534 | 2389366.1902 | 82.14%
2023-03-21 | 2023 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 335090.89 | 6:55 | 18:46 | 11527.6 | 11844.1 | 11800.6 | 11824.3 | 11874 | 11917.7 | 11879.2 | 12097.2 | 11875.7 | 11816.4 | 11760.2 | 11864.9 | 11870.9 | 11806.5 | 11758 | 11887.1 | 11692.1 | 11740.2 | 11763.8 | 11832.9 | 11755.7 | 11774.2 | 11672.1 | 11815.7 | 11856.2 | 10908.8 | 11766.4 | 11687.3 | 11949.8 | 11865.7 | 11853.1 | 11994.6 | 12311 | 12275.2 | 12100.1 | 12128.3 | 12188.1 | 12149.6 | 12155.8 | 12216.9 | 12291.6 | 11714.5 | 12348.3 | 11687.3 | 12140.7 | 12908.1 | 11561.3 | 12214.1 | 11405.3 | 11590.3 | 11985.6 | 11621.1 | 12137.4 | 11431.4 | 12198.2 | 11486.8 | 11437.8 | 12274.3 | 11425.5 | 12155.3 | 12071 | 11268.6 | 12053.1 | 11708.4 | 12158.3 | 11718.5 | 12120.3 | 12366.7 | 12368.7 | 11820.7 | 12378.5 | 11515.2 | 12066.5 | 12092.3 | 11637.7 | 12343.6 | 11383.4 | 12393.4 | 11563.5 | 12249.5 | 11783.9 | 12219.4 | 11792.2 | 12505.5 | 11766.8 | 12085 | 11820 | 10603.2 | 12333 | 12041.2 | 11711.1 | 12654.5 | 12464.7 | 11969.8 | 11872.9 | 12454.7 | 11628.5 | 11877.9 | 12422.8 | 11537 | 12609.6 | 11606.2 | 12412.3 | 11815.2 | 12508 | 11432.6 | 12568.5 | 11844.7 | 12527.7 | 11876.8 | 12558.9 | 12017.8 | 11578.7 | 12201.1 | 11516.3 | 11522.7 | 12319.5 | 12150.8 | 12290 | 11659.2 | 12304.3 | 11521.8 | 12229 | 11858.4 | 12156.6 | 11124.7 | 12252 | 11622.4 | 11607.7 | 11735.7 | 11620.5 | 10216.1 | 11573.8 | 10468.7 | 11577.2 | 11516.7 | 12097.2 | 11268.3 | 12125.4 | 11467.3 | 12166.7 | 11444.6 | 11580.3 | 11470.6 | 11822.3 | 12016 | 11918.8 | 11998.7 | 12047.6 | 12044.8 | 11523.9 | 12066.6 | 11791.5 | 11806.4 | 11978.6 | 11910.2 | 11900.1 | 11327.9 | 11958.5 | 11268.8 | 27.8775 | 27.5673 | 27.7831 | 0 | 28.0115 | 27.88 | 0 | 44.0898 | 0 | 0 | 10.2102 | 0 | 1.8951 | 1.9304 | 1.9375 | 2.0594 | 2.0241 | 1.9662 | 4.45 | 4.45 | 4.546 | 5.101 | 4.731 | 5.153 | 6.2575 | 6.7335 | 6.4296 | 6.3831 | 6.7411 | 6.2372 | 1.2224 | 1.3559 | 1.4857 | 0 | 1.4058 | 1.1194 | 6.8721 | 6.8664 | 7.0752 | 7.0617 | 7.0022 | 7.039 | 1.2625 | 1.3443 | 1.4679 | 0 | 1.3957 | 1.4004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275317 | 512 | 265301 | 533 | 516746.307 | 1360 | 6.2575 | 6.7335 | 6.4296 | 6.3831 | 6.7411 | 6.2372 | 6.8721 | 6.8664 | 7.0752 | 7.0617 | 7.0022 | 7.039 | 946000 | 1000 | 942000 | 1000 | 1879600 | 4600 | 1886000 | 1875000 | 11.85 | 6.4637 | 1.3178 | 6.9861 | 1.3741 | 20.39% | 19.67% | 27.8239 | 27.15 | 1.9688 | 4.7385 | 1901098.2 | 1879533 | 2285018.8332 | 82.25%
2023-03-22 | 2023 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 335090.89 | 6:56 | 18:48 | 11829 | 12232.4 | 12187.5 | 12221.5 | 12222.6 | 12253.3 | 12247.5 | 12504.3 | 12242.7 | 12176.3 | 12120.6 | 12235.7 | 12217.2 | 12151.2 | 12108.2 | 12262.8 | 12076.5 | 12157.2 | 12182.7 | 12224.4 | 12119.9 | 12190.9 | 11897.2 | 12123.4 | 12009.6 | 10983.5 | 12122.9 | 11959 | 12209.9 | 12079.8 | 11997.5 | 12150.5 | 12186.2 | 12203.9 | 12226.4 | 12179.1 | 12237.1 | 12159.2 | 12111.7 | 12081.1 | 12763.7 | 12009.9 | 12665.8 | 11859.6 | 12219.6 | 13186.3 | 11802.8 | 12704.5 | 11632 | 11829.2 | 12334.7 | 11840.1 | 12550.8 | 11669.8 | 12500.5 | 11640.8 | 11492.4 | 12462.3 | 11591.3 | 12436.5 | 12360.6 | 11420.2 | 12205.2 | 11753.5 | 12046.8 | 11512.3 | 12042.9 | 12344.1 | 12450 | 11732.6 | 12434 | 11408.9 | 12106 | 12109.2 | 11592.3 | 12478.9 | 11335.1 | 12564.5 | 11567.6 | 12430.6 | 11751.8 | 12286.5 | 11831.1 | 12617.7 | 11675.1 | 12102 | 11683.8 | 10442.6 | 12403.9 | 12027.1 | 11507.7 | 12627.2 | 12346.7 | 11729.3 | 11619.1 | 12382 | 11487.5 | 11821.2 | 12475.1 | 11395.3 | 12513.3 | 11389.8 | 12293.1 | 11629.1 | 12357.8 | 11145 | 12424.8 | 11565.6 | 12359.7 | 11580.8 | 12409.2 | 11732.4 | 11477.3 | 12267.3 | 11367.5 | 11366.5 | 12306 | 12153 | 12223.1 | 11535.4 | 12308.9 | 11323.3 | 12067.9 | 11591.2 | 11996.4 | 10855.2 | 12185.7 | 11439.1 | 11494.6 | 11643 | 11501.1 | 10079.5 | 11440.9 | 10279.7 | 11465.6 | 11478.8 | 12615.3 | 11458.2 | 12602.9 | 11710.1 | 12513.9 | 11570.8 | 11676.2 | 11506.4 | 12385.1 | 12598.2 | 12507.6 | 12543.5 | 12548.8 | 12563.3 | 11791.1 | 12542.1 | 12599.7 | 12627.3 | 12655.4 | 12614.4 | 12631.3 | 11834.1 | 12638.9 | 11783.2 | 27.3489 | 27.0399 | 26.8987 | 0 | 26.9774 | 27.3837 | 0 | 42.2197 | 0 | 0 | 49.7817 | 0 | 3.7736 | 3.6463 | 3.6965 | 3.6951 | 3.8007 | 3.4933 | 7.499 | 7.269 | 7.19 | 6.451 | 6.866 | 6.949 | 6.3536 | 6.7232 | 6.4423 | 6.2432 | 6.561 | 6.2796 | 1.2578 | 1.4502 | 1.5651 | 0 | 1.4138 | 1.1948 | 6.9187 | 6.8185 | 7.029 | 6.8552 | 6.798 | 7.1226 | 1.3042 | 1.4389 | 1.5508 | 0 | 1.4095 | 1.4866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276278 | 514 | 266247 | 535 | 518646.441 | 1364.8 | 6.3536 | 6.7232 | 6.4423 | 6.2432 | 6.561 | 6.2796 | 6.9187 | 6.8185 | 7.029 | 6.8552 | 6.798 | 7.1226 | 961000 | 2000 | 946000 | 2000 | 1900134 | 4800 | 1903000 | 1895334 | 11.8667 | 6.4338 | 1.3764 | 6.9237 | 1.438 | 21.39% | 20.77% | 27.1297 | 46.0007 | 3.6843 | 7.0373 | 1922148.4 | 1900067 | 2300641.7743 | 82.59%
2023-03-23 | 2023 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 335090.89 | 6:55 | 18:45 | 11171.3 | 11599.3 | 11524.3 | 11525.3 | 11558.3 | 11636.6 | 11586.9 | 11935.3 | 11673.8 | 11472.4 | 11549.7 | 11671.6 | 11576.2 | 11606.4 | 11625.9 | 11760.2 | 11646.1 | 11781 | 11771.7 | 11785.9 | 11730.9 | 11802.4 | 11530.6 | 11745.6 | 11568.8 | 10465.3 | 11660.3 | 11532.3 | 11843.6 | 11756.4 | 11641.5 | 11752.4 | 11704.5 | 11762.6 | 11801 | 11765.3 | 11858.9 | 11799 | 11760 | 11680.3 | 12401.7 | 11513.5 | 12294.2 | 11338.9 | 11849.6 | 12872.4 | 11349.7 | 12336.6 | 11050.7 | 11269.8 | 11846.3 | 11311.5 | 12120.4 | 11080.5 | 12068.5 | 11131.9 | 10953.6 | 12051.2 | 11023.6 | 12002 | 11910.7 | 10857.1 | 11714.8 | 11153.5 | 11434.9 | 10798.1 | 11419.4 | 11649.5 | 11807.4 | 10958.4 | 11760.8 | 10617.9 | 11545.4 | 11383.9 | 10944.6 | 11826.1 | 10635.5 | 12003.6 | 10888.8 | 11802.3 | 10958.8 | 11535.2 | 10999.1 | 11908.7 | 11008.5 | 11534.1 | 10953 | 9726.3 | 11623.8 | 11280.3 | 10712.6 | 11918.4 | 11674.3 | 11060.8 | 10981.1 | 11632.6 | 10539.6 | 10872.5 | 11592 | 10470.8 | 11721.3 | 10392.4 | 11483 | 10735.6 | 11562.1 | 10260.6 | 11595.1 | 10651 | 11533.1 | 10662.7 | 11549.5 | 10772.4 | 10537.3 | 11368.2 | 10448 | 10458.3 | 11430.2 | 11278.8 | 11355 | 10684.3 | 11463.1 | 10470.3 | 11166.8 | 10660.3 | 11069.1 | 10030.3 | 11330.3 | 10591.5 | 10679.9 | 10853.1 | 10638 | 9338.3 | 10770.7 | 9665.6 | 10967.9 | 10977.7 | 12132.2 | 10981.2 | 12179 | 11241.4 | 12037.9 | 11076.8 | 11184.9 | 11007.2 | 11869 | 12111.8 | 11980.6 | 12040.2 | 12045.6 | 12085.5 | 11305.8 | 12096.5 | 11970 | 12043.7 | 12106.9 | 12035.4 | 12103.8 | 11241.7 | 12030.3 | 11289.1 | 28.7431 | 28.6007 | 28.6598 | 0 | 28.5971 | 28.865 | 0 | 43.8156 | 0 | 0 | 12.1926 | 0 | 2.7516 | 2.9146 | 2.8136 | 2.8917 | 2.821 | 2.7702 | 7.785 | 7.648 | 7.217 | 7.03 | 7.047 | 6.962 | 6.0203 | 6.4889 | 6.2247 | 5.948 | 6.0979 | 6.0231 | 1.202 | 1.3883 | 1.5349 | 0 | 1.2837 | 1.1368 | 6.5119 | 6.5379 | 6.7395 | 6.5513 | 6.2277 | 6.8759 | 1.2522 | 1.3762 | 1.5231 | 0 | 1.2856 | 1.4121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277199 | 515 | 267138 | 537 | 520450.707 | 1369.467 | 6.0203 | 6.4889 | 6.2247 | 5.948 | 6.0979 | 6.0231 | 6.5119 | 6.5379 | 6.7395 | 6.5513 | 6.2277 | 6.8759 | 921000 | 1000 | 891000 | 2000 | 1804266 | 4667 | 1809000 | 1799599 | 11.8333 | 6.1338 | 1.3091 | 6.574 | 1.3698 | 21.34% | 20.84% | 28.6931 | 28.0041 | 2.8271 | 7.2815 | 1822930 | 1804200 | 2170823.1704 | 83.11%
2023-03-24 | 2023 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 335090.89 | 6:40 | 18:57 | 12140.9 | 12523.5 | 12475.3 | 12493.6 | 12564.1 | 12611.3 | 12546.4 | 12820.8 | 12536.1 | 12436.2 | 12390.9 | 12507.4 | 12456.2 | 12435.6 | 12542.4 | 12617.2 | 12527.5 | 12641.5 | 12552 | 12619.1 | 12568.1 | 12596.7 | 12428.5 | 12597.5 | 12393.9 | 11469.2 | 12467.7 | 12343.3 | 12623.9 | 12579 | 12497.4 | 12551.6 | 12569 | 12581.8 | 12624.4 | 12580.4 | 12634.5 | 12584.5 | 12558.4 | 12538.2 | 13298.3 | 12538.7 | 13232.5 | 12413.9 | 12950.7 | 13757 | 12449.9 | 13273.6 | 11972.3 | 12174.6 | 12659.4 | 12194.4 | 12877.4 | 12019.5 | 12832.4 | 12073.8 | 11875.4 | 12886.9 | 11962.4 | 12803.9 | 12717.7 | 11784.3 | 12554.2 | 12090.2 | 12364.5 | 11867.1 | 12359.8 | 12668.2 | 12668.3 | 12038.7 | 12707.9 | 11764 | 12402.2 | 12424.4 | 11890.6 | 12777.1 | 11657.3 | 12817.8 | 11837.6 | 12687.6 | 12078.2 | 12587.2 | 12161.5 | 12930.9 | 11990.5 | 12416 | 12008.1 | 10879 | 12761.9 | 12392.3 | 11894.4 | 13003.6 | 12775.1 | 12211.4 | 12134 | 12778.9 | 11868.8 | 12235.9 | 12862.9 | 11828.2 | 12929.1 | 11792.2 | 12736.2 | 12111.2 | 12745.2 | 11611.6 | 12849 | 12011.5 | 12812.7 | 12073 | 12868.9 | 12216.1 | 11904.9 | 12698.8 | 11855.6 | 11857.3 | 12742.1 | 12575.2 | 12657.5 | 11981.8 | 12700.6 | 11774.1 | 12476.3 | 12056.2 | 12483.5 | 11439.6 | 12586.1 | 11855.4 | 11939.7 | 12018.6 | 11891.2 | 10622.1 | 11877.6 | 10762.4 | 11900.5 | 11910.3 | 13069.5 | 11960.9 | 13115.4 | 12218.2 | 12987.1 | 12079.7 | 12182.4 | 12016.2 | 12961.3 | 13159.9 | 13064.5 | 13072.1 | 13052 | 13076.5 | 12331.6 | 13110.9 | 13109 | 13137.3 | 13158.1 | 13059.3 | 13174.9 | 12358.5 | 13138.2 | 12449.9 | 26.9087 | 26.5937 | 26.6775 | 0 | 26.485 | 26.9611 | 0 | 39.4793 | 0 | 0 | 34.8628 | 0 | 6.5671 | 6.5262 | 6.4727 | 6.4163 | 6.4827 | 6.4431 | 11.045 | 11.492 | 11.356 | 11.441 | 10.571 | 11.043 | 6.5714 | 7.0682 | 6.8533 | 6.456 | 6.9086 | 6.7061 | 1.2892 | 1.5901 | 1.6903 | 0 | 1.564 | 1.3524 | 7.1627 | 7.1881 | 7.4718 | 7.025 | 7.2135 | 7.5903 | 1.3425 | 1.5837 | 1.6621 | 0 | 1.5546 | 1.6872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278193 | 517 | 268122 | 538 | 522421.107 | 1374.067 | 6.5714 | 7.0682 | 6.8533 | 6.456 | 6.9086 | 6.7061 | 7.1627 | 7.1881 | 7.4718 | 7.025 | 7.2135 | 7.5903 | 994000 | 2000 | 984000 | 1000 | 1970400 | 4600 | 1975000 | 1965800 | 12.2833 | 6.7606 | 1.4972 | 7.2752 | 1.566 | 22.15% | 21.53% | 26.7252 | 37.171 | 6.4847 | 11.158 | 1988718.8 | 1970334 | 2444403.4256 | 80.61%
2023-03-25 | 2023 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 335090.89 | 6:39 | 18:57 | 11610.8 | 12103.4 | 12047 | 12053.3 | 12029 | 12109.7 | 12155.1 | 12456.7 | 12084.1 | 11972.3 | 11956.8 | 12084.2 | 11999.8 | 11986.5 | 11868.2 | 12123.1 | 11822.7 | 11921.3 | 11969.8 | 12071.8 | 11868.1 | 11984.5 | 11661.6 | 11878.6 | 11861.2 | 10755 | 11979.3 | 11790.2 | 12005.4 | 11872.2 | 11810.9 | 11920.7 | 11984 | 12031.2 | 12090.1 | 12007.4 | 12052.2 | 11969.9 | 11948.2 | 11921.2 | 12607.6 | 11831 | 12558 | 11722.2 | 12155.9 | 13101.3 | 11503.3 | 12491 | 11387 | 11608.2 | 12168.8 | 11606.4 | 12445.8 | 11470.7 | 12357.4 | 11409.5 | 11286.2 | 12440.8 | 11380.1 | 12380.9 | 12300.4 | 11210.9 | 12174.5 | 11639.9 | 11913.5 | 11354.2 | 11945.8 | 12319.5 | 12306 | 11640.2 | 12405.4 | 11332.8 | 12013.1 | 12078.4 | 11439.2 | 12496.2 | 11201.1 | 12522.2 | 11428.2 | 12396.1 | 11697 | 12297.4 | 11802.4 | 12676.7 | 11672.3 | 12183.2 | 11559.9 | 10281.5 | 12317.3 | 11941.3 | 11287.5 | 12527.6 | 12246.1 | 11570.3 | 11455.5 | 12274.4 | 11273 | 11702.1 | 12377.9 | 11233.3 | 12468.4 | 11142.1 | 12230.6 | 11479.7 | 12291.1 | 10970.5 | 12365.4 | 11444.8 | 12308.2 | 11466.7 | 12342.8 | 11614.2 | 11395.9 | 12273.4 | 11204.8 | 11263.3 | 12269.4 | 12158.2 | 12195.1 | 11523.4 | 12328.1 | 11284.1 | 11969.5 | 11465.4 | 11833.7 | 10792.6 | 12179.9 | 11423.8 | 11499.8 | 11623.7 | 11519.4 | 10039.5 | 11467.2 | 10255.7 | 11483.8 | 11503.6 | 12820.7 | 11577.8 | 12765.9 | 11776.5 | 12680.5 | 11619 | 11750.5 | 11533.7 | 12367.1 | 12610.5 | 12551 | 12619.9 | 12696.1 | 12747.2 | 11795.9 | 12617.9 | 12544.1 | 12559.9 | 12516.5 | 12397.3 | 12545.8 | 11594.8 | 12572 | 11618.3 | 27.1246 | 26.9134 | 26.8715 | 0 | 26.9769 | 27.1338 | 0 | 42.103 | 0 | 0 | 53.7356 | 0 | 2.6761 | 2.7005 | 2.6083 | 2.6624 | 2.6738 | 2.5991 | 7.365 | 7.186 | 6.295 | 6.849 | 7.097 | 7.286 | 6.2835 | 6.5965 | 6.2834 | 6.1799 | 6.5201 | 6.2516 | 1.2527 | 1.5385 | 1.5604 | 0 | 1.5026 | 1.3176 | 6.7899 | 6.6808 | 6.7882 | 6.6804 | 6.7737 | 7.1087 | 1.3087 | 1.5289 | 1.552 | 0 | 1.5082 | 1.6367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279144 | 519 | 269067 | 540 | 524310.774 | 1378.6 | 6.2835 | 6.5965 | 6.2834 | 6.1799 | 6.5201 | 6.2516 | 6.7899 | 6.6808 | 6.7882 | 6.6804 | 6.7737 | 7.1087 | 951000 | 2000 | 945000 | 2000 | 1889667 | 4533 | 1892000 | 1885134 | 12.3 | 6.3525 | 1.4344 | 6.8036 | 1.5069 | 22.58% | 22.15% | 27.004 | 47.9193 | 2.6533 | 7.013 | 1906180.6 | 1889467 | 2256723.6697 | 83.73%
2023-03-26 | 2023 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 335090.89 | 6:38 | 18:59 | 12315.3 | 12764.1 | 12740 | 12765.3 | 12768.8 | 12840.9 | 12785.1 | 13064.2 | 12778.3 | 12586.4 | 12703 | 12791.1 | 12726 | 12751.5 | 12697.7 | 12888.2 | 12737.1 | 12886.7 | 12751.6 | 12885.7 | 12836.3 | 12925.9 | 12518.6 | 12813.7 | 12673.5 | 11666.3 | 12785.9 | 12643.5 | 12839.4 | 12586.6 | 12565.7 | 12740.6 | 12678.9 | 12732 | 12848.1 | 12746.5 | 12788.8 | 12720.3 | 12590.3 | 12608.7 | 13293.7 | 12426.9 | 13167.7 | 12263.1 | 12657.4 | 13726.6 | 12276 | 13235.1 | 12281 | 12491.6 | 12961.5 | 12484 | 13171.9 | 12260.9 | 13156.1 | 12313.3 | 12217.4 | 13190.4 | 12305.7 | 13228.5 | 13119 | 12099.2 | 12869.3 | 12351 | 12528.1 | 11963.2 | 12546.2 | 12765.2 | 12871 | 12194.3 | 12944.9 | 11945.5 | 12647.9 | 12630.1 | 12128.8 | 12979.8 | 11845.5 | 13120.5 | 12111.1 | 12938.6 | 12145.6 | 12698.4 | 12194.2 | 12962.4 | 12051.6 | 12481.3 | 11990.3 | 10789.2 | 12780.4 | 12348 | 11959.9 | 13060.6 | 12814.2 | 12195.6 | 12075.4 | 12778.1 | 11868 | 12242.2 | 12913.3 | 11901 | 12991.8 | 11867.1 | 12809.4 | 12182.5 | 12798.1 | 11680.3 | 12875.4 | 12129.7 | 12767.2 | 12023.2 | 12824.1 | 12257.8 | 12030.9 | 12868.4 | 11992.8 | 11998.8 | 12877.5 | 12779.6 | 12795.8 | 12158.3 | 12877.7 | 11900.4 | 12583.4 | 12130.4 | 12508.6 | 11433.6 | 12709.9 | 11946.9 | 11982.6 | 12059.7 | 11964.7 | 10535.7 | 11817.3 | 10696.2 | 12005.1 | 12052.1 | 13351.4 | 12255.1 | 13262.6 | 12370.4 | 13156.7 | 12191.5 | 12284.2 | 12083 | 13028.3 | 13198.5 | 13240.9 | 13253.1 | 13271.9 | 13311.9 | 12444.4 | 13174.1 | 13198.9 | 13247.7 | 13251.1 | 13123.1 | 13276.2 | 12409 | 13290.9 | 12526.8 | 27.4207 | 27.0453 | 27.0442 | 0 | 27.1445 | 27.1693 | 0 | 41.025 | 0 | 0 | 56.9801 | 0 | 3.8874 | 3.8541 | 3.7744 | 3.9176 | 3.822 | 3.8416 | 7.212 | 7.226 | 7.159 | 8.147 | 7.606 | 7.142 | 6.742 | 7.1732 | 6.6887 | 6.5414 | 6.9297 | 6.6343 | 1.34 | 1.673 | 1.6582 | 0 | 1.6121 | 1.3858 | 7.2909 | 7.2937 | 7.2346 | 7.0489 | 7.2312 | 7.5298 | 1.3948 | 1.6661 | 1.6411 | 0 | 1.6128 | 1.7214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280154 | 520 | 270058 | 542 | 526303.774 | 1383.133 | 6.742 | 7.1732 | 6.6887 | 6.5414 | 6.9297 | 6.6343 | 7.2909 | 7.2937 | 7.2346 | 7.0489 | 7.2312 | 7.5298 | 1010000 | 1000 | 991000 | 2000 | 1993000 | 4533 | 1998000 | 1988467 | 12.35 | 6.7849 | 1.5338 | 7.2715 | 1.6072 | 22.61% | 22.1% | 27.1648 | 49.0025 | 3.8495 | 7.4153 | 2010609 | 1992867 | 2408254.9462 | 82.75%
2023-03-27 | 2023 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 335090.89 | 6:35 | 19:00 | 12253.2 | 12625.2 | 12584.9 | 12612.5 | 12605.3 | 12687.2 | 12626.7 | 12898.3 | 12636.3 | 12522.6 | 12521.8 | 12631.2 | 12578.7 | 12568.9 | 12522.8 | 12742.6 | 12533 | 12650.1 | 12536.8 | 12703.1 | 12597.8 | 12679.9 | 12426.3 | 12630.1 | 12527.8 | 11528 | 12614.7 | 12472.4 | 12714.3 | 12553 | 12536.1 | 12669 | 12704.3 | 12718.1 | 12741 | 12688.6 | 12756.9 | 12685.8 | 12479.1 | 12646.6 | 13221 | 12468.4 | 13107.3 | 12331.2 | 12553.7 | 13650.7 | 12227.8 | 13133.2 | 12129.5 | 12322.8 | 12823 | 12332 | 13037.2 | 12119.3 | 13022.2 | 12184.3 | 12110.1 | 13105.5 | 12144.9 | 13067.3 | 13008 | 11955.1 | 12776.2 | 12276.9 | 12567.4 | 12066.7 | 12591.5 | 12881.4 | 12890.2 | 12266.5 | 12977.1 | 11983.8 | 12633.5 | 12667.8 | 12135.6 | 13030.6 | 11904.2 | 13086.4 | 12110 | 12957.6 | 12268.8 | 12778.9 | 12315.2 | 13121.5 | 12258.6 | 12711.9 | 12171.9 | 10945.6 | 12868.7 | 12516.1 | 12048 | 13137.3 | 12869.6 | 12249.4 | 12133.5 | 12881.3 | 12014.2 | 12368.1 | 12994.8 | 11982.1 | 13062.3 | 11923.4 | 12879.5 | 12229.3 | 12894.6 | 11752 | 12968.7 | 12187.7 | 12900.7 | 12146.4 | 12924.6 | 12357.4 | 12068.2 | 12856.8 | 12005.3 | 12018.4 | 12892.3 | 12775.6 | 12829.8 | 12201.7 | 12928.5 | 12000.8 | 12658 | 12217 | 12603.1 | 11546.9 | 12813.4 | 12137.1 | 12190.8 | 12295.5 | 12166.8 | 10732.2 | 12131.4 | 10935.6 | 12129.6 | 12132.8 | 13212 | 12121.1 | 13174.6 | 12310.8 | 13128.5 | 12189.3 | 12307.2 | 12135.5 | 12974.9 | 13200.9 | 13121.2 | 13140.5 | 13158.1 | 13183.4 | 12374 | 13115.9 | 13149.7 | 13190.1 | 13227 | 13063.5 | 13240.8 | 12366.9 | 13194.5 | 12450.4 | 28.0001 | 27.6116 | 27.6381 | 0 | 27.877 | 27.7375 | 0 | 43.3329 | 0 | 0 | 61.5714 | 0 | 2.7398 | 2.7206 | 2.7528 | 2.7456 | 2.8166 | 2.6351 | 6 | 5.661 | 7.69 | 6.62 | 6.305 | 5.961 | 6.7162 | 7.1795 | 6.7642 | 6.6205 | 7.0448 | 6.6888 | 1.352 | 1.6369 | 1.6991 | 0 | 1.6182 | 1.3924 | 7.2562 | 7.291 | 7.3365 | 7.1759 | 7.3057 | 7.5982 | 1.4043 | 1.6304 | 1.6746 | 0 | 1.6086 | 1.7331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 281156 | 521 | 271054 | 543 | 528293.975 | 1387.6 | 6.7162 | 7.1795 | 6.7642 | 6.6205 | 7.0448 | 6.6888 | 7.2562 | 7.291 | 7.3365 | 7.1759 | 7.3057 | 7.5982 | 1002000 | 1000 | 996000 | 1000 | 1990201 | 4467 | 1996000 | 1985734 | 12.4167 | 6.8357 | 1.5397 | 7.3272 | 1.6102 | 22.52% | 21.98% | 27.7729 | 52.4522 | 2.7351 | 6.3728 | 2008129.4 | 1990067 | 2409267.4023 | 82.6%
2023-03-28 | 2023 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 335090.89 | 6:37 | 18:58 | 11754.5 | 12109 | 12098 | 12112.6 | 12098.3 | 12190.3 | 12107.4 | 12379.6 | 12869.9 | 12765.8 | 12757.6 | 12873.5 | 12813.2 | 12816.2 | 12741.1 | 12980.2 | 12773.9 | 12901.5 | 12775.1 | 12970.5 | 12839.6 | 12924.4 | 12659.5 | 12877.1 | 12768.2 | 11746.8 | 12855 | 12711.4 | 12963.7 | 12799 | 12791.9 | 12932.5 | 12965.8 | 12979.5 | 12992.3 | 12940 | 13020.8 | 12947.4 | 12724.5 | 12920.3 | 13548.4 | 12709.5 | 13432.4 | 12569.4 | 12784.2 | 13952.4 | 12462.7 | 13450.9 | 12343.3 | 12541.8 | 13083.8 | 12546.4 | 13331.7 | 12337.7 | 13306.9 | 12418.4 | 12319.3 | 13380.7 | 12362.5 | 13339.1 | 13299.3 | 12172.8 | 13025.4 | 12493 | 12792.7 | 12294.3 | 12818.6 | 13160.1 | 13163.3 | 12483.3 | 13254.8 | 12204.1 | 12867.7 | 12900 | 12341.3 | 13295.7 | 12107.2 | 13368.4 | 12314.5 | 13218.3 | 12494.9 | 13045.3 | 12537.6 | 13425.8 | 12811.1 | 13454.1 | 12402.8 | 11190.9 | 13133.3 | 12762.4 | 12280.5 | 13437.5 | 13139.7 | 12468.6 | 12357.9 | 13168.3 | 12239.9 | 12596.3 | 13286.4 | 12200.3 | 13359 | 12147 | 13152.5 | 12443.5 | 13184.2 | 11965.2 | 13251.7 | 12410.1 | 13171.4 | 12370.9 | 13203.9 | 12580 | 12286.8 | 13121.8 | 12201.9 | 12232.2 | 13158.9 | 13020.3 | 13091.5 | 12396.2 | 13195.1 | 12211.5 | 12901.5 | 12435.6 | 12830.1 | 11768.6 | 13049.9 | 12347.2 | 12381.1 | 12472.7 | 12346.5 | 10938.1 | 12311.3 | 11105.1 | 12275.7 | 12270.4 | 13511.1 | 12334.7 | 13487.2 | 12538.4 | 13379 | 12342.9 | 12475.3 | 12268.9 | 13247.8 | 13489.6 | 13403.7 | 13431.8 | 13461.9 | 13483.7 | 12620 | 13385 | 13363.6 | 13431.6 | 13380.7 | 13258.7 | 13523.4 | 12576.7 | 13421.8 | 12657.1 | 30.6734 | 30.4348 | 30.6349 | 0 | 30.8882 | 30.6516 | 0 | 45.044 | 0 | 0 | 67.7054 | 0 | 3.2928 | 3.2607 | 3.2964 | 3.2985 | 3.3425 | 3.3655 | 7.218 | 7.148 | 7.584 | 8.507 | 7.81 | 7.384 | 6.9065 | 7.3996 | 6.9234 | 6.7978 | 7.2348 | 6.8672 | 1.3647 | 1.7275 | 1.7184 | 0 | 1.7034 | 1.4437 | 7.4753 | 7.5422 | 7.507 | 7.3209 | 7.5478 | 7.7967 | 1.421 | 1.7224 | 1.6952 | 0 | 1.6918 | 1.7989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 282172 | 523 | 272068 | 545 | 530317.841 | 1392.067 | 6.9065 | 7.3996 | 6.9234 | 6.7978 | 7.2348 | 6.8672 | 7.4753 | 7.5422 | 7.507 | 7.3209 | 7.5478 | 7.7967 | 1016000 | 2000 | 1014000 | 2000 | 2023866 | 4467 | 2026000 | 2019399 | 12.35 | 7.0216 | 1.5916 | 7.5317 | 1.6659 | 22.67% | 22.12% | 30.6566 | 56.3747 | 3.3094 | 7.6085 | 2041541.8 | 2023733 | 2456326.4455 | 82.39%
2023-03-29 | 2023 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 335090.89 | 6:38 | 18:59 | 10426.1 | 10769.3 | 10700.9 | 10713 | 10744.1 | 10817.3 | 10759.5 | 10977.6 | 10741.8 | 10646.4 | 10690.3 | 10757.1 | 10742.3 | 10723.1 | 10665.7 | 10846.1 | 10656.5 | 10738.2 | 10676.4 | 10832 | 10702.7 | 10776.6 | 10562.7 | 10725.3 | 10687.7 | 9924.7 | 10762.2 | 10645.8 | 10802.5 | 10648 | 10646.1 | 10784.9 | 10861.2 | 10872.1 | 10883.3 | 10832.9 | 10862.4 | 10783.7 | 10614.5 | 10793.3 | 10911.2 | 10330.2 | 10872.2 | 10247.2 | 10556.8 | 11333.8 | 10233.3 | 10885.5 | 10369.5 | 10515.4 | 10929.8 | 10523.7 | 11125.3 | 10391 | 11053.5 | 10456.1 | 10335.5 | 11086.4 | 10360.2 | 11043.4 | 11009.7 | 10177.3 | 10809.2 | 10434.4 | 10682.2 | 10331.5 | 10705.5 | 10963.3 | 10946.6 | 10502.8 | 10989.7 | 10302.6 | 10734 | 10796.8 | 10340.4 | 11062.8 | 10195.8 | 11050.4 | 10348.5 | 11005 | 10524.9 | 10919.2 | 10554.9 | 11184.8 | 10822.7 | 11249.6 | 10421.9 | 9554.9 | 10967.2 | 10729.4 | 10319.6 | 11157.4 | 10978.3 | 10528.6 | 10461.7 | 10978.7 | 10327.2 | 10614.6 | 11075.5 | 10310.5 | 11189.8 | 10290.2 | 11086.1 | 10538.8 | 11111.6 | 10179.6 | 11174.1 | 10525.6 | 11113.9 | 10526.3 | 11127.6 | 10688.3 | 10378.2 | 10965.1 | 10331.1 | 10357.8 | 11039.9 | 10913 | 10980.6 | 10521.4 | 11047.4 | 10379.1 | 10881.4 | 10545.9 | 10844.1 | 10046.9 | 10991.5 | 10506.1 | 10516.3 | 10553.7 | 10512.3 | 9377.9 | 10407.9 | 9494.7 | 10307.5 | 10315.1 | 11125.8 | 10288.5 | 11170 | 10458.8 | 11067 | 10340.8 | 10432.3 | 10319.3 | 11074 | 11221.1 | 11153.7 | 11160 | 11137.5 | 11137.2 | 10578.4 | 11139.9 | 11143 | 11175 | 11140.5 | 11085.2 | 11260.2 | 10590.5 | 11168.9 | 10643.9 | 30.4871 | 30.3704 | 30.3688 | 0 | 30.1932 | 30.5675 | 0 | 42.5825 | 0 | 0 | 67.7603 | 0 | 4.6393 | 4.8324 | 4.6894 | 4.8591 | 4.6626 | 4.7768 | 10.614 | 8.855 | 10.121 | 9.985 | 9.069 | 10.121 | 5.8841 | 6.2596 | 5.7208 | 5.7797 | 6.1444 | 5.7443 | 1.1962 | 1.4489 | 1.4422 | 0 | 1.4527 | 1.2309 | 6.2737 | 6.3023 | 6.0773 | 6.1766 | 6.3436 | 6.5771 | 1.2497 | 1.4473 | 1.4394 | 0 | 1.4514 | 1.5309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 283024 | 524 | 272921 | 547 | 532015.908 | 1396.333 | 5.8841 | 6.2596 | 5.7208 | 5.7797 | 6.1444 | 5.7443 | 6.2737 | 6.3023 | 6.0773 | 6.1766 | 6.3436 | 6.5771 | 852000 | 1000 | 853000 | 2000 | 1698067 | 4266 | 1702000 | 1693801 | 12.35 | 5.9222 | 1.3542 | 6.2918 | 1.4237 | 22.87% | 22.63% | 30.3974 | 55.1714 | 4.7433 | 9.7942 | 1713204.7 | 1698067 | 2074493.867 | 81.85%
2023-03-30 | 2023 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 335090.89 | 6:37 | 18:58 | 9227.5 | 9525.9 | 9476 | 9457.4 | 9501.1 | 9531.5 | 9547 | 9738.8 | 9516.2 | 9540.1 | 9426.8 | 9513.3 | 9451 | 9460.5 | 9411.9 | 9555.8 | 9397.3 | 9454.5 | 9418.7 | 9561.2 | 9427.2 | 9514.4 | 9289 | 9457.7 | 9415.6 | 8659.6 | 9461.5 | 9371.3 | 9543.7 | 9439.2 | 9420.9 | 9544.1 | 9526.5 | 9517.5 | 9552.7 | 9532.8 | 9594.8 | 9545.8 | 9476 | 9516.6 | 9599.5 | 9039 | 9552.4 | 8943.6 | 9348.4 | 10028.7 | 8962 | 9578.7 | 9081.1 | 9251.8 | 9608.3 | 9247 | 9786.1 | 9123 | 9778.9 | 9133.4 | 9128.2 | 9872.6 | 9087.6 | 9804 | 9790.7 | 8946.4 | 9671.7 | 9341.7 | 9508 | 9081.3 | 9532.3 | 9711.3 | 9785.2 | 9290.4 | 9836.3 | 9111.3 | 9600.3 | 9643.4 | 9211.3 | 9920.7 | 9083 | 9952.3 | 9240.9 | 9906 | 9306.8 | 9721.2 | 9415.3 | 9933.2 | 9178 | 9514.2 | 9169.6 | 8361 | 9708.6 | 9434.3 | 9006.6 | 9851.5 | 9653 | 9208.1 | 9137.7 | 9642.9 | 9005.7 | 9269.4 | 9750 | 8970 | 9742.6 | 8922.2 | 9624 | 9156.2 | 9632.7 | 8788.1 | 9704.1 | 9082.3 | 9639 | 9072.7 | 9673.7 | 9175.1 | 8345.6 | 8876.2 | 8315.7 | 8318.9 | 8917.8 | 8810.8 | 8871.5 | 8428.8 | 9694.6 | 8994.9 | 9487 | 9099 | 9436.3 | 8703.8 | 9613.6 | 9095.8 | 9104.8 | 9233.7 | 9115.2 | 8123.2 | 9216.2 | 8483 | 9242.7 | 9237.1 | 10019 | 9199.6 | 10002.8 | 9330.5 | 9975.8 | 9262.7 | 9356.7 | 9249 | 8721 | 8870.4 | 8763.6 | 8770.6 | 8746.6 | 8772.6 | 8231.3 | 8759 | 8862.7 | 8884.4 | 8883.5 | 8811.8 | 8938.7 | 8316.3 | 8788.3 | 8323.9 | 26.7472 | 26.7023 | 26.4999 | 0 | 26.6282 | 26.9007 | 0 | 37.7578 | 0 | 0 | 72.3496 | 0 | 4.2211 | 4.2103 | 4.2567 | 4.1895 | 4.3743 | 4.2451 | 9.695 | 10.468 | 9.677 | 10.04 | 10.087 | 9.29 | 5.1802 | 5.4981 | 5.0353 | 5.1472 | 5.3577 | 5.1393 | 0.9442 | 1.2381 | 1.1103 | 0 | 1.2524 | 1.0733 | 5.5368 | 5.5884 | 5.3161 | 5.3683 | 5.6152 | 5.8724 | 0.99679 | 1.2367 | 1.1159 | 0 | 1.2549 | 1.3305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 283777 | 526 | 273647 | 548 | 533489.308 | 1400.8 | 5.1802 | 5.4981 | 5.0353 | 5.1472 | 5.3577 | 5.1393 | 5.5368 | 5.5884 | 5.3161 | 5.3683 | 5.6152 | 5.8724 | 753000 | 2000 | 726000 | 1000 | 1473400 | 4467 | 1476000 | 1468933 | 12.35 | 5.2263 | 1.1237 | 5.5495 | 1.187 | 21.5% | 21.39% | 26.6956 | 55.0537 | 4.2495 | 9.8762 | 1486695 | 1473267 | 1846485.4748 | 79.79%
2023-03-31 | 2023 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 335090.89 | 6:35 | 19:00 | 11466.6 | 11808 | 11733.5 | 11739.1 | 11792.1 | 11808.9 | 11745.5 | 12041.3 | 11874.8 | 11722 | 11685.5 | 11809.4 | 11601.1 | 11694.9 | 11606.7 | 11731.1 | 11583.4 | 11639.3 | 11461.3 | 11691.5 | 11511.9 | 11635.1 | 11352.5 | 11547.5 | 11424.2 | 10504.5 | 11617.8 | 11441.5 | 11659.1 | 11533.7 | 11411 | 11573.7 | 11587.6 | 11605.2 | 11582 | 11541.1 | 11601.4 | 11510 | 11479.1 | 11508.8 | 12156 | 11381.9 | 12006.6 | 11208.3 | 11635.8 | 12542.8 | 11195.8 | 12134.1 | 11162.4 | 11344.7 | 11864.1 | 11290.4 | 12073.9 | 11156.4 | 11911.3 | 11092.6 | 10982.4 | 12029.1 | 11132.8 | 11932.6 | 11916.5 | 10930.2 | 11780.4 | 11332.6 | 11515.7 | 10906.6 | 11506.8 | 11661.5 | 11862.8 | 11105 | 11856.5 | 10841.6 | 11642.9 | 11540.7 | 11130.2 | 11935.4 | 10890.5 | 12074.7 | 11120.9 | 11968.8 | 11084.3 | 11578.5 | 11217.8 | 11903.9 | 11142.3 | 11601.3 | 10974.1 | 9941.6 | 11640.1 | 11298.1 | 10736.1 | 11813.7 | 11567.8 | 11005.9 | 10942.1 | 11541.8 | 10576.4 | 10976 | 11551.5 | 10615.3 | 11524.1 | 10462 | 11305.8 | 10699.5 | 11334.3 | 10204.3 | 11385.5 | 10595.4 | 11290.1 | 10524.7 | 11273.9 | 10685.6 | 10770.5 | 11478.9 | 10679.4 | 10662 | 11508.2 | 11331.6 | 11416.9 | 10779 | 11437.3 | 10537.6 | 11201.4 | 10705.3 | 11101.2 | 10089.6 | 11286.3 | 10614 | 10771.4 | 10855.9 | 10726.8 | 9532.4 | 10580.7 | 9549.7 | 10664.2 | 10673.2 | 11795.9 | 10662.8 | 11760.6 | 10872.5 | 11704.7 | 10750.8 | 10865.8 | 10716.6 | 11551.6 | 11712.3 | 11705 | 11731 | 11753.2 | 11769.8 | 10878.8 | 11608.6 | 11790.2 | 11801.8 | 11670.1 | 11574.6 | 11783.8 | 10902.4 | 11811.5 | 11042.6 | 27.3626 | 27.1041 | 27.1241 | 0 | 27.613 | 27.2969 | 0 | 40.6637 | 0 | 0 | 76.7143 | 0 | 3.4886 | 3.3824 | 3.3706 | 3.4651 | 3.3699 | 3.2675 | 7.765 | 6.885 | 7.137 | 7.379 | 6.72 | 6.987 | 6.3411 | 6.5844 | 6.304 | 6.1694 | 6.2716 | 5.8661 | 1.2695 | 1.42 | 1.5417 | 0 | 1.3659 | 1.16 | 6.7482 | 6.5972 | 6.6645 | 6.6834 | 6.3684 | 6.7436 | 1.3199 | 1.4199 | 1.5316 | 0 | 1.3618 | 1.4447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 284698 | 528 | 274530 | 550 | 535286.908 | 1405.333 | 6.3411 | 6.5844 | 6.304 | 6.1694 | 6.2716 | 5.8661 | 6.7482 | 6.5972 | 6.6645 | 6.6834 | 6.3684 | 6.7436 | 921000 | 2000 | 883000 | 2000 | 1797600 | 4533 | 1800000 | 1793067 | 12.4167 | 6.2561 | 1.3514 | 6.6342 | 1.4156 | 21.6% | 21.34% | 27.3002 | 58.689 | 3.3907 | 7.1455 | 1813782.3 | 1797533 | 2210082.4808 | 81.33%
2023-04-01 | 2024 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 335090.89 | 6:36 | 18:59 | 11627.2 | 11971 | 11942.9 | 11978.9 | 11973.7 | 12018.3 | 11947.2 | 12179.4 | 11977.7 | 11889.5 | 11859 | 11959.1 | 11891.1 | 11901.4 | 11832.5 | 12004.4 | 11823.4 | 11926 | 11825.8 | 11999.7 | 11849.1 | 11947.1 | 11695.3 | 11886.1 | 11752.3 | 10907.8 | 11861.3 | 11741.1 | 11931.1 | 11774.9 | 11705.6 | 11861.4 | 11798.1 | 11832.9 | 11921.1 | 11865 | 11907.2 | 11811.2 | 11748.3 | 11723.9 | 12365.5 | 11684 | 12167.1 | 11500.9 | 11826.7 | 12576.9 | 11496.9 | 12328.7 | 11468.6 | 11642 | 12068.6 | 11651.9 | 12254.4 | 11510.1 | 12232.3 | 11504.1 | 11449.4 | 12303.8 | 11492.9 | 12255.6 | 12205.4 | 11332.1 | 12064.9 | 11648.3 | 11794.5 | 11184.6 | 11786 | 11833.8 | 12086.3 | 11322.9 | 12047 | 11051.5 | 11896.6 | 11711.5 | 11466.4 | 12036.7 | 11162.8 | 12306 | 11463.4 | 12172.6 | 11261.4 | 11719.8 | 11261.9 | 11975.5 | 11293.6 | 11637.5 | 11214.9 | 10146.2 | 11777.2 | 11495.9 | 11086.9 | 11999 | 11790.4 | 11297.8 | 11213.3 | 11760.8 | 11015.9 | 11249.1 | 11780 | 10910.1 | 11891.2 | 10937.2 | 11700.7 | 11128 | 11683.1 | 10713.9 | 11740.5 | 11084.3 | 11685.5 | 11067.8 | 11713 | 11221.7 | 10943.2 | 11610.8 | 10925.9 | 10932.7 | 11635.4 | 11568.2 | 11596.9 | 11144.7 | 11698.3 | 10954.9 | 11466.3 | 11081.6 | 11433.9 | 10603.3 | 11632.3 | 11086.6 | 11146.5 | 11225.7 | 11127.8 | 9857.6 | 11094.3 | 10077.9 | 11203.5 | 11225.6 | 12142.9 | 11269.4 | 12183.4 | 11457.4 | 12076.4 | 11334.6 | 11408.5 | 11290.9 | 12043.3 | 12203.8 | 12116.4 | 12125.9 | 12117.4 | 12131.9 | 11552.3 | 12129.7 | 12126.5 | 12208.2 | 12153.8 | 12083.8 | 12263.7 | 11551.9 | 12148.2 | 11629 | 29.5574 | 29.4633 | 29.5773 | 0 | 29.6358 | 29.8063 | 0 | 45.23 | 0 | 0 | 38.161 | 0 | 3.0552 | 2.9887 | 2.8873 | 3.0249 | 3.1071 | 3.0292 | 14.71 | 13.79 | 13.31 | 14.309 | 12.952 | 11.439 | 6.5907 | 6.9044 | 6.6531 | 6.4713 | 6.6048 | 6.2955 | 1.3483 | 1.4674 | 1.6617 | 0 | 1.4225 | 1.2344 | 6.9954 | 6.8968 | 7.0411 | 7.0552 | 6.6541 | 7.2485 | 1.3994 | 1.4663 | 1.6412 | 0 | 1.4142 | 1.5422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 285639 | 529 | 275442 | 552 | 537133.242 | 1409.8 | 6.5907 | 6.9044 | 6.6531 | 6.4713 | 6.6048 | 6.2955 | 6.9954 | 6.8968 | 7.0411 | 7.0552 | 6.6541 | 7.2485 | 941000 | 1000 | 912000 | 2000 | 1846334 | 4467 | 1850000 | 1841867 | 12.3833 | 6.5866 | 1.4269 | 6.9819 | 1.4927 | 21.66% | 21.38% | 29.608 | 41.6955 | 3.0154 | 13.4183 | 1863880 | 1846200 | 2316103.9114 | 79.71%
2023-04-02 | 2024 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 335090.89 | 6:33 | 19:00 | 12747 | 13169.1 | 13096.7 | 13117.6 | 13159.9 | 13215.6 | 13189.5 | 13446.2 | 13163 | 13090 | 13053.9 | 13164.4 | 13091 | 13085.2 | 13038.7 | 13220.5 | 13047.1 | 13137.3 | 13031.9 | 13211.9 | 13061.5 | 13157.5 | 12921.2 | 13113.7 | 13009.5 | 12059.7 | 13094.8 | 12961.9 | 13197.7 | 13095.8 | 13044.2 | 13160 | 13179.3 | 13179 | 13222.1 | 13182.4 | 13243.5 | 13175.4 | 13141.6 | 13139.2 | 13674.7 | 12962.6 | 13574.8 | 12829.8 | 13281.4 | 14125 | 12737.9 | 13605 | 12614.7 | 12816.1 | 13309.7 | 12842.2 | 13516.5 | 12671.4 | 13498.3 | 12704.3 | 12537.2 | 13476.2 | 12600.3 | 13433.5 | 13377.3 | 12413 | 13184.9 | 12747 | 13061.1 | 12570.8 | 13059.7 | 13343.6 | 13359.1 | 12743.8 | 13417.7 | 12459.4 | 13125.4 | 13127.3 | 12639.3 | 13454.8 | 12389.2 | 13563.8 | 12599.8 | 13412.8 | 12754.5 | 13272.4 | 12840.1 | 13592.5 | 12851.3 | 13286.1 | 12704.7 | 11582.8 | 13370.2 | 13030.6 | 12567.8 | 13626.2 | 13357.7 | 12787 | 12688 | 13394.9 | 12553.8 | 12899.4 | 13511.5 | 12521.1 | 13546.9 | 12529.1 | 13392.4 | 12764.8 | 13391.4 | 12287.7 | 13475.4 | 12698.7 | 13414.8 | 12684.2 | 13449.2 | 12861.4 | 12584.3 | 13341 | 12560.4 | 12547.6 | 13389.6 | 13271.1 | 13325.5 | 12711.4 | 13411 | 12519 | 13190.7 | 12721.4 | 13136.7 | 12147.8 | 13308.1 | 12658.6 | 12703.4 | 12807.7 | 12693.1 | 11318.4 | 12654.3 | 11565.6 | 12679 | 12668.6 | 13708 | 12638.3 | 13703.2 | 12845.8 | 13624.2 | 12729 | 12832.5 | 12693.6 | 13492.7 | 13690.5 | 13625.3 | 13646.2 | 13653.1 | 13665 | 12923.2 | 13632.1 | 13684 | 13702.2 | 13606.8 | 13524.4 | 13738.7 | 12907.8 | 13719.5 | 13010.9 | 30.2451 | 30.4734 | 30.515 | 0 | 30.549 | 30.6188 | 0 | 42.322 | 0 | 0 | 69.9721 | 0 | 6.3557 | 6.333 | 6.3284 | 6.2508 | 6.2814 | 6.1169 | 10.752 | 10.706 | 11.089 | 10.894 | 10.49 | 10.409 | 7.2622 | 7.6428 | 7.3205 | 7.1163 | 7.5508 | 7.0987 | 1.4379 | 1.7508 | 1.7955 | 0 | 1.7308 | 1.3431 | 7.7552 | 7.7072 | 7.7667 | 7.6708 | 7.752 | 8.1495 | 1.501 | 1.7552 | 1.7673 | 0 | 1.7158 | 1.6645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 286679 | 530 | 276477 | 553 | 539200.575 | 1414.067 | 7.2622 | 7.6428 | 7.3205 | 7.1163 | 7.5508 | 7.0987 | 7.7552 | 7.7072 | 7.7667 | 7.6708 | 7.752 | 8.1495 | 1040000 | 1000 | 1035000 | 1000 | 2067333 | 4267 | 2073000 | 2063066 | 12.45 | 7.3319 | 1.6116 | 7.8002 | 1.6808 | 21.98% | 21.55% | 30.4803 | 56.147 | 6.2777 | 10.7233 | 2089277.8 | 2067200 | 2620498.6929 | 78.89%
2023-04-03 | 2024 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 335090.89 | 6:34 | 19:01 | 11416.4 | 11870.1 | 11872 | 11875.4 | 11934.7 | 11990.8 | 11908.1 | 12224.8 | 11871.1 | 11795.4 | 11725.8 | 11860.3 | 11755.5 | 11777.3 | 11756.1 | 11941.1 | 11789.4 | 11899.3 | 11682.3 | 11865 | 11756.7 | 11862.9 | 11590.6 | 11806.6 | 11661.4 | 10550.6 | 11747.3 | 11597.3 | 11884.8 | 11780 | 11714.2 | 11837 | 11749.1 | 11776.9 | 11864.7 | 11809.2 | 11902.5 | 11839.5 | 11797.5 | 11767.7 | 12343 | 11487.4 | 12241.8 | 11346.1 | 11802.2 | 12774.4 | 11251 | 12286.7 | 11202.3 | 11409.7 | 12003.4 | 11424.6 | 12270.1 | 11253.1 | 12195.7 | 11281.4 | 11060.7 | 12183.6 | 11171.4 | 12130 | 12091.6 | 10986.9 | 11857.9 | 11314.3 | 11585.9 | 10978.4 | 11569.8 | 11857.5 | 11967.2 | 11141.8 | 11976.9 | 10798.9 | 11683.4 | 11569.2 | 11090.2 | 12002 | 10756.7 | 12187.5 | 11060.9 | 12018 | 11150.5 | 11738.5 | 11224.9 | 12135.2 | 11127.9 | 11643.8 | 11102.8 | 9864.9 | 11865.5 | 11491.8 | 10926.6 | 12184.1 | 11899.7 | 11208.6 | 11117.1 | 11901.6 | 10864.1 | 11208.6 | 11954.1 | 10782.1 | 12047.7 | 10795.6 | 11810.2 | 11033.1 | 11875.3 | 10550.5 | 11926.7 | 10971.5 | 11847.7 | 11003.2 | 11871.3 | 11127.6 | 10848.2 | 11696.5 | 10780.1 | 10760.4 | 11770.7 | 11609.4 | 11678.4 | 10974.8 | 11783.9 | 10734.5 | 11506.8 | 10949.6 | 11442.7 | 10286.5 | 11614.3 | 10872.4 | 10926.3 | 11053.3 | 10912 | 9555 | 10955.9 | 9812.5 | 11168 | 11167.3 | 12384.5 | 11132.4 | 12405.9 | 11378.5 | 12283.1 | 11240.2 | 11351.7 | 11202.8 | 12185.2 | 12449.8 | 12287.1 | 12336.4 | 12328.6 | 12350.1 | 11485.7 | 12367.6 | 12394.8 | 12440 | 12420.9 | 12318 | 12513.2 | 11532.4 | 12394.1 | 11594.2 | 29.7817 | 29.7074 | 29.7093 | 0 | 29.929 | 29.9968 | 0 | 40.7292 | 0 | 0 | 74.8252 | 0 | 7.1894 | 7.2272 | 7.1301 | 6.9224 | 7.0225 | 6.9893 | 13.273 | 12.633 | 12.789 | 13.013 | 12.671 | 11.973 | 6.2347 | 6.5621 | 6.3769 | 6.0641 | 6.2773 | 6.0488 | 1.2692 | 1.4747 | 1.6039 | 0 | 1.3996 | 1.157 | 6.6184 | 6.5527 | 6.7081 | 6.5699 | 6.3619 | 6.982 | 1.3317 | 1.4757 | 1.5885 | 0 | 1.4017 | 1.4359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 287610 | 532 | 277382 | 555 | 541036.776 | 1418.4 | 6.2347 | 6.5621 | 6.3769 | 6.0641 | 6.2773 | 6.0488 | 6.6184 | 6.5527 | 6.7081 | 6.5699 | 6.3619 | 6.982 | 931000 | 2000 | 905000 | 2000 | 1836201 | 4333 | 1832000 | 1831868 | 12.45 | 6.2606 | 1.3809 | 6.6322 | 1.4467 | 22.06% | 21.81% | 29.8248 | 57.7772 | 7.0802 | 12.7253 | 1854610.5 | 1836134 | 2255952.9178 | 81.39%
2023-04-04 | 2024 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 335090.89 | 6:32 | 18:55 | 12643.6 | 13053.8 | 12994.2 | 13006 | 13056.7 | 13129.1 | 13068.9 | 13340.6 | 13050.2 | 12967.7 | 12936.7 | 13044.8 | 12976.4 | 12986.5 | 12914.7 | 13120 | 12935.4 | 13037.2 | 12901.3 | 13077.8 | 12933.2 | 13037.1 | 12798 | 13001.9 | 12874.7 | 11816.8 | 12965.6 | 12823.7 | 13077.8 | 12953.1 | 12913.9 | 13032.5 | 13047.7 | 13062.3 | 13089.7 | 13038.2 | 13110.7 | 13053.7 | 12957.1 | 13021.9 | 13595.6 | 12810.2 | 13462 | 12638.5 | 13112.4 | 14029.8 | 12613.8 | 13521.9 | 12469.9 | 12678.9 | 13232.4 | 12679.6 | 13463.9 | 12509.9 | 13405.9 | 12535.2 | 12367.9 | 13408.7 | 12452.5 | 13387.2 | 13358.3 | 12255.7 | 13124.1 | 12624.2 | 12929.2 | 12407.5 | 12940.2 | 13249.2 | 13254.5 | 12593.3 | 13315.4 | 12276.9 | 12978.6 | 12976 | 12441.7 | 13347.8 | 12166.2 | 13454.4 | 12415.7 | 13305.7 | 12603 | 13153.1 | 12709.9 | 13503.3 | 12765.6 | 13250.8 | 12548.8 | 11299.4 | 13300.9 | 12904.9 | 12422.1 | 13558.2 | 13264.9 | 12649.7 | 12543.5 | 13284.4 | 12319.7 | 12678.4 | 13329.8 | 12266.8 | 13370.3 | 12282.4 | 13181.1 | 12521.9 | 13235.4 | 12054.4 | 13311.1 | 12502.8 | 13227.2 | 12463.6 | 13251.2 | 12657.7 | 12384 | 13164.6 | 12334.4 | 12314.4 | 13230.7 | 13097 | 13168.1 | 12498.4 | 13246.6 | 12278.9 | 13022.3 | 12521.8 | 12953.1 | 11807.2 | 13089.7 | 12358.3 | 12439.2 | 12493.4 | 12408.2 | 10910.9 | 12435 | 11247.8 | 12507.2 | 12520.1 | 13672.9 | 12531 | 13662.8 | 12753.2 | 13580.2 | 12619.8 | 12720.5 | 12547.9 | 13426 | 13653.3 | 13591.3 | 13610.6 | 13618.7 | 13634.6 | 12832.3 | 13618.4 | 13640.7 | 13665.1 | 13657.8 | 13619.2 | 13704 | 12869.1 | 13670.9 | 12926 | 29.2062 | 28.9777 | 29.062 | 0 | 28.9544 | 29.1819 | 0 | 45.6102 | 0 | 0 | 38.4359 | 0 | 2.5423 | 2.6829 | 2.5671 | 2.7662 | 2.672 | 2.564 | 6.879 | 6.763 | 6.725 | 6.745 | 7.027 | 6.685 | 7.2441 | 7.5609 | 7.2292 | 7.0675 | 7.4444 | 7.042 | 1.4176 | 1.7814 | 1.78 | 0 | 1.7412 | 1.4212 | 7.695 | 7.6136 | 7.628 | 7.5502 | 7.6749 | 8.0954 | 1.4856 | 1.7821 | 1.7595 | 0 | 1.7334 | 1.766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 288640 | 533 | 278413 | 556 | 543082.709 | 1422.8 | 7.2441 | 7.5609 | 7.2292 | 7.0675 | 7.4444 | 7.042 | 7.695 | 7.6136 | 7.628 | 7.5502 | 7.6749 | 8.0954 | 1030000 | 1000 | 1031000 | 1000 | 2045933 | 4400 | 2059000 | 2041533 | 12.3833 | 7.2647 | 1.6283 | 7.7095 | 1.7053 | 22.41% | 22.12% | 29.0764 | 42.0231 | 2.6324 | 6.804 | 2067315.9 | 2045533 | 2568665.9507 | 79.63%
2023-04-05 | 2024 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 335090.89 | 6:33 | 18:57 | 12547.6 | 12940.5 | 12899.8 | 12929.7 | 12947.7 | 13029.5 | 12933.6 | 13202.9 | 12950.1 | 12829.5 | 12837.5 | 12944.7 | 12897.2 | 12874.1 | 12822.3 | 13054.8 | 12866.4 | 12965 | 12857 | 13006.5 | 12891.8 | 13003.2 | 12752.3 | 12971.1 | 12857.9 | 11819.8 | 12930.4 | 12782.2 | 13043.4 | 12894.7 | 12741 | 12792.2 | 13013.5 | 13025.8 | 13075.8 | 13010.3 | 13088.2 | 13024.1 | 12986.4 | 12983.6 | 13580 | 12797.9 | 13485.2 | 12645.5 | 13124.1 | 14041.4 | 12584.7 | 13520.4 | 12391.7 | 12596.5 | 13149 | 12605.2 | 13374.4 | 12409.1 | 13360.3 | 12477.9 | 12291.6 | 13315.8 | 12360.2 | 13288.6 | 13250.8 | 12170.4 | 12991.9 | 12487.1 | 12839.9 | 12326.3 | 12857.5 | 13182.7 | 13210.5 | 12521.2 | 13271.7 | 12217.8 | 12936.7 | 12920.8 | 12409.9 | 13313.6 | 12157.4 | 13420.6 | 12361.9 | 13258.1 | 12520.9 | 13078.8 | 12623.1 | 13434.1 | 12643.3 | 13182.3 | 12470.4 | 11231.5 | 13228.1 | 12800.1 | 12333.2 | 13472.9 | 13171.6 | 12538.6 | 12438.4 | 13214.6 | 12301.6 | 12659.9 | 13351.7 | 12255.8 | 13406 | 12298.2 | 13226.4 | 12534.4 | 13277.1 | 12068.7 | 13351.1 | 12502.2 | 13265.1 | 12492.6 | 13306 | 12652.3 | 12304.4 | 13128.6 | 12295.1 | 12275.9 | 13205.6 | 13053.5 | 13140.5 | 12479.9 | 13258.9 | 12295.2 | 13023 | 12490.4 | 12971.7 | 11847.2 | 13128.7 | 12418.9 | 12459.7 | 12502.8 | 12492.5 | 10993 | 12372 | 11201.3 | 12331.9 | 12354.3 | 13467.6 | 12319.5 | 13464.6 | 12540.8 | 13384.8 | 12451.1 | 12552.1 | 12384.8 | 13242.4 | 13448.6 | 13389.9 | 13408.3 | 13406.6 | 13414.6 | 12628.4 | 13413.3 | 13465.2 | 13492.4 | 13526.1 | 13480.1 | 13499.2 | 12674.6 | 13454.6 | 12739.5 | 31.6339 | 31.4272 | 31.5106 | 0 | 31.3709 | 20.0576 | 0 | 47.3729 | 0 | 0 | 35.2368 | 0 | 2.9619 | 2.9218 | 2.8236 | 3.0957 | 2.9418 | 1.7013 | 8.943 | 7.64 | 7.184 | 7.372 | 7.376 | 6.87 | 7.2704 | 7.5978 | 7.279 | 7.1014 | 7.491 | 5.1918 | 1.4361 | 1.8158 | 1.7979 | 0 | 1.7752 | 0.9794 | 7.7149 | 7.6533 | 7.6724 | 7.5796 | 7.7257 | 6.0353 | 1.5062 | 1.8166 | 1.7818 | 0 | 1.7681 | 1.2248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 289665 | 535 | 279430 | 558 | 545117.043 | 1427.067 | 7.2704 | 7.5978 | 7.279 | 7.1014 | 7.491 | 5.1918 | 7.7149 | 7.6533 | 7.6724 | 7.5796 | 7.7257 | 6.0353 | 1025000 | 2000 | 1017000 | 2000 | 2034334 | 4267 | 2038000 | 2030067 | 12.4 | 6.9886 | 1.5609 | 7.3969 | 1.6195 | 22.33% | 21.89% | 29.2 | 41.3048 | 2.741 | 7.5642 | 2056135.5 | 2034334 | 2525240.6802 | 80.56%
2023-04-06 | 2024 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 335090.89 | 6:31 | 18:58 | 11948.9 | 12290.7 | 12198.9 | 12240.8 | 12209.8 | 12305.1 | 12232.5 | 12499 | 12318.7 | 12191.4 | 12180.3 | 12287.4 | 12217.2 | 12205 | 12147.5 | 12371.6 | 12149.8 | 12188.9 | 12164.9 | 12260.6 | 12098.4 | 12215.2 | 11953.3 | 12171.2 | 12078.5 | 11025.7 | 12144.5 | 11998 | 12255.8 | 12087 | 12000.5 | 12177 | 12112.1 | 12164.1 | 12198.4 | 12121.4 | 12182 | 12078 | 12033.8 | 12050.2 | 12344 | 11665.7 | 12367.7 | 11610.4 | 12109.8 | 13014.8 | 11581.7 | 12342.5 | 11755.8 | 11954.1 | 12412.1 | 11891.2 | 12606.7 | 11739.7 | 12584.6 | 11721.7 | 11629.5 | 12582.3 | 11771 | 12608.4 | 12606.4 | 11611.6 | 12302.7 | 11811.8 | 12183.9 | 11750.6 | 12234.5 | 12564.7 | 12558.3 | 11943 | 12627 | 11614.3 | 12329.4 | 12298.7 | 11858.2 | 12691 | 11642.9 | 12771.1 | 11819.9 | 12673.3 | 11922.7 | 12406.7 | 12049.5 | 12784.2 | 11960.5 | 12395 | 11939.3 | 10641.1 | 12600.5 | 12264.7 | 11779.8 | 12810.3 | 12423.9 | 11739.4 | 11597.5 | 12482.5 | 11718.2 | 12135.2 | 12716.5 | 11725.1 | 12625 | 11672.9 | 12414.4 | 11886.9 | 12382.6 | 11330.7 | 12439.5 | 11737.1 | 12285.7 | 11590.5 | 12289.1 | 11753.3 | 11752.9 | 12476.5 | 11648.3 | 11657.9 | 12439 | 12399.6 | 12381.7 | 11892.9 | 12567.5 | 11699.4 | 12208.9 | 11718.1 | 12180.3 | 11199.9 | 12473.6 | 11874.2 | 11926.9 | 12006.9 | 11922.7 | 10415 | 11993.3 | 10738.8 | 11769 | 11798.7 | 12725.1 | 11726 | 12748.9 | 11967.3 | 12746 | 11870 | 11948.8 | 11793.1 | 12489.2 | 12714.5 | 12528 | 12601.1 | 12619.3 | 12646.7 | 12018.9 | 12680.6 | 12574.8 | 12630.6 | 12626.4 | 12601.9 | 12689.1 | 11951.7 | 12544.1 | 11990.4 | 31.1137 | 30.412 | 30.0754 | 0 | 30.3493 | 30.4497 | 0 | 42.8046 | 0 | 0 | 71.8663 | 0 | 4.7849 | 4.6974 | 4.543 | 4.6018 | 4.7987 | 4.4538 | 9.743 | 9.093 | 9.281 | 9.267 | 9.323 | 8.963 | 6.7481 | 6.9611 | 6.5241 | 6.5983 | 6.9228 | 6.3601 | 1.3963 | 1.64 | 1.6828 | 0 | 1.6271 | 1.3176 | 7.1006 | 6.9325 | 6.81 | 7.0639 | 7.0415 | 7.3522 | 1.4627 | 1.6453 | 1.6688 | 0 | 1.6293 | 1.6379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290632 | 537 | 280393 | 560 | 547038.509 | 1431.333 | 6.7481 | 6.9611 | 6.5241 | 6.5983 | 6.9228 | 6.3601 | 7.1006 | 6.9325 | 6.81 | 7.0639 | 7.0415 | 7.3522 | 967000 | 2000 | 963000 | 2000 | 1921466 | 4266 | 1926000 | 1917200 | 12.45 | 6.6858 | 1.5328 | 7.0501 | 1.6088 | 22.93% | 22.82% | 30.48 | 57.3354 | 4.6466 | 9.2783 | 1941015.9 | 1921400 | 2360223.327 | 81.41%
2023-04-07 | 2024 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 335090.89 | 6:30 | 18:59 | 12122.1 | 12377.7 | 12278.4 | 12310.8 | 12296.3 | 12339.5 | 12293.7 | 12551.3 | 12489.8 | 12327.3 | 12351.6 | 12494.1 | 12345.4 | 12368.9 | 12255.8 | 12420.1 | 12216 | 12288.7 | 12364.7 | 12344.1 | 12269.9 | 12401 | 12145.5 | 12329.9 | 12300.9 | 11388.6 | 12517.8 | 12261.3 | 12385.7 | 12255.6 | 12253.9 | 12371.7 | 12496.1 | 12517.3 | 12535.3 | 12442.4 | 12498 | 12406.2 | 12375.5 | 12407.6 | 12757.5 | 12086.8 | 12618.2 | 11937 | 12283.5 | 13136.9 | 11881.2 | 12690.9 | 12055.1 | 12242.1 | 12713.3 | 12246.2 | 12913.1 | 11924.8 | 12936.1 | 12129.8 | 12011.6 | 12914.3 | 12094.8 | 12901.1 | 12859.8 | 11923.7 | 12501.4 | 12016.7 | 12386.6 | 11853.3 | 12403.7 | 12582.3 | 12685 | 11988.7 | 12735.1 | 11778.5 | 12459.8 | 12404.1 | 11968.4 | 12702.6 | 11663.4 | 12815.1 | 11864.6 | 12585.2 | 11836.3 | 12323.1 | 11968.5 | 12631.5 | 11856 | 12298 | 11824.5 | 10658.8 | 12657.9 | 12344.2 | 11923.2 | 12908.5 | 12650.9 | 12078.7 | 11971.1 | 12642.3 | 11882.3 | 12315.9 | 12890.3 | 11916.7 | 12781.2 | 11813.7 | 12554 | 11997.5 | 12544.4 | 11490.8 | 12652.3 | 11943.7 | 12545.7 | 11858.5 | 12533.9 | 12026.7 | 11967.1 | 12717.9 | 11860 | 11895.7 | 12710.2 | 12648.1 | 12674.8 | 12136.1 | 12830 | 11905.6 | 12467.1 | 11990.3 | 12388.1 | 11409.7 | 12660.7 | 12044.6 | 11992.8 | 12017.8 | 12066.5 | 10525.7 | 11924.2 | 10726.5 | 11953.5 | 11952.9 | 12899.6 | 11927 | 12856.5 | 12103.2 | 12829.2 | 11960.2 | 12075.9 | 11936.8 | 12557.1 | 12699 | 12742.8 | 12757.3 | 12812.9 | 12839.2 | 12077.9 | 12736.3 | 12953.6 | 12811.1 | 12760.7 | 12738.6 | 12755.1 | 12023.1 | 12971.8 | 12130.3 | 32.9455 | 32.164 | 31.8602 | 0 | 32.0643 | 32.2045 | 0 | 42.7963 | 0 | 0 | 65.8298 | 0 | 5.9052 | 5.8671 | 5.6886 | 5.7309 | 5.7807 | 5.6348 | 10.386 | 9.938 | 9.762 | 10.137 | 10.504 | 10.49 | 6.8119 | 7.0207 | 6.6954 | 6.6698 | 7.0263 | 6.393 | 1.402 | 1.6748 | 1.7179 | 0 | 1.6831 | 1.3462 | 7.1697 | 7.0242 | 6.9892 | 7.1128 | 7.1791 | 7.3948 | 1.4681 | 1.6832 | 1.7055 | 0 | 1.684 | 1.6759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 291614 | 538 | 281368 | 561 | 548988.31 | 1435.6 | 6.8119 | 7.0207 | 6.6954 | 6.6698 | 7.0263 | 6.393 | 7.1697 | 7.0242 | 6.9892 | 7.1128 | 7.1791 | 7.3948 | 982000 | 1000 | 975000 | 1000 | 1949801 | 4267 | 1955000 | 1945534 | 12.4833 | 6.7695 | 1.5648 | 7.145 | 1.6433 | 23.12% | 23% | 32.2477 | 54.3131 | 5.7679 | 10.2028 | 1968791 | 1949801 | 2391947.2055 | 81.52%
2023-04-08 | 2024 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 335090.89 | 6:30 | 18:58 | 11892.6 | 12239.7 | 12314.9 | 12319.2 | 12329.6 | 12389.6 | 12258.4 | 12543.6 | 12229.1 | 12212 | 12040.7 | 12143 | 12313.6 | 12088.8 | 12288 | 12444.6 | 12241.1 | 12309.3 | 12292 | 12331.9 | 12202.6 | 12323.9 | 12020.5 | 12272.9 | 12056.7 | 10951.3 | 12168.9 | 12024.2 | 12343.6 | 12148.8 | 12063.7 | 12220.9 | 11942.4 | 12019.4 | 12225.9 | 12117.9 | 12223.7 | 12150.8 | 12124.2 | 11973.8 | 12641 | 11767 | 12572.1 | 11585.9 | 12185.1 | 13125 | 11710.7 | 12647.9 | 11494.9 | 11676.9 | 12316.6 | 11605.8 | 12658.4 | 11636.2 | 12390.9 | 11502.7 | 11231.6 | 12327.4 | 11435.9 | 12327.7 | 12376.1 | 11279.8 | 12043.1 | 11530.6 | 11745.1 | 11150.7 | 11809 | 12063.9 | 12194.2 | 11346.7 | 12178.5 | 11037 | 11926.5 | 11805.2 | 11339.9 | 12225.1 | 11002 | 12442.3 | 11299.6 | 12238.1 | 11308.8 | 11925.6 | 11367.5 | 12312 | 11446.5 | 12025.2 | 11312.5 | 10132.4 | 12134.6 | 11739.4 | 11161.3 | 12350.3 | 12017.5 | 11276.7 | 11151.4 | 12028.7 | 10923.3 | 11349.4 | 12048 | 10912.1 | 12029.8 | 10930.6 | 11826.3 | 11121 | 11868.2 | 10628.4 | 11931 | 11055.3 | 11800.4 | 10999.6 | 11828.8 | 11156.5 | 10902 | 11740.8 | 10882.6 | 10852.3 | 11825.4 | 11599.6 | 11767.1 | 10951.4 | 11795.4 | 10753.9 | 11599.4 | 11000.2 | 11494.4 | 10369 | 11616.5 | 10780.8 | 10734.6 | 10773.2 | 10740.4 | 9456.2 | 10588.5 | 9587.3 | 10884.8 | 10915.6 | 12012.8 | 10907.5 | 11938.1 | 11005.1 | 11895.6 | 10889.3 | 11041.2 | 10873.8 | 11580.8 | 11779.3 | 11733.2 | 11774.6 | 11822.2 | 11883.2 | 11011.8 | 11774.3 | 11864.5 | 11831.3 | 11915.1 | 11824.7 | 11798.2 | 10918.1 | 11862.8 | 11004.8 | 33.6488 | 33.1032 | 32.7088 | 0 | 32.9351 | 33.201 | 0 | 46.4362 | 0 | 0 | 67.7143 | 0 | 4.0468 | 3.8979 | 3.9767 | 4.0997 | 3.9283 | 4.2626 | 9.846 | 10.164 | 8.759 | 10.439 | 9.092 | 13.48 | 6.7555 | 7.0367 | 6.689 | 6.3519 | 6.4698 | 5.8073 | 1.3499 | 1.7227 | 1.555 | 0 | 1.535 | 1.2603 | 7.1159 | 7.0541 | 6.9239 | 6.6663 | 6.6272 | 6.734 | 1.4208 | 1.7307 | 1.5541 | 0 | 1.5442 | 1.5651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 292571.88 | 540.112 | 282271.06 | 563.47 | 550841.976 | 1440 | 6.7555 | 7.0367 | 6.689 | 6.3519 | 6.4698 | 5.8073 | 7.1159 | 7.0541 | 6.9239 | 6.6663 | 6.6272 | 6.734 | 957880 | 2112 | 903060 | 2470 | 1853666 | 4400 | 1856358 | 1849266 | 12.4667 | 6.5184 | 1.4846 | 6.8536 | 1.563 | 22.78% | 22.81% | 33.1194 | 57.0753 | 4.0353 | 10.2967 | 1871323.7 | 1853600 | 2275012.5411 | 81.48%
2023-04-09 | 2024 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 335090.89 | 6:30 | 18:50 | 12267.3 | 12635 | 12564.3 | 12587.8 | 12582.5 | 12705 | 12627.3 | 12922.1 | 12717.9 | 12523.9 | 12624.8 | 12727.7 | 12799.1 | 12681.5 | 12714.1 | 12859.8 | 12677.3 | 12749.9 | 12809 | 12836.8 | 12712.6 | 12834.7 | 12613 | 12816.9 | 12694.3 | 11646.4 | 12784.4 | 12647 | 12891.1 | 12743.8 | 12738 | 12842.5 | 12798.4 | 12830.5 | 12917.5 | 12856.4 | 12937.9 | 12845 | 12809.8 | 12766 | 13443.9 | 12593.1 | 13389.4 | 12456.2 | 12953.9 | 13885.2 | 12429 | 13393.5 | 12240 | 12432 | 12987.3 | 12434.4 | 13228 | 12187.7 | 13220.4 | 12329.8 | 12134.9 | 13138.1 | 12198.2 | 13128.2 | 13080.8 | 12012.5 | 12761.9 | 12252.5 | 12606.1 | 12091.6 | 12662 | 12934.7 | 12994.8 | 12302.4 | 13060.2 | 12018.5 | 12740.2 | 12726.4 | 12213.8 | 13094 | 11955.1 | 13191.6 | 12126 | 12998 | 12287.6 | 12873.2 | 12389.4 | 13194.1 | 12570.8 | 13179.6 | 12230.4 | 11027 | 12989.5 | 12648.7 | 12134 | 13236.1 | 12926.5 | 12268.6 | 12143.5 | 13034.8 | 12091.8 | 12479.6 | 13148.4 | 12036.9 | 13223.6 | 12055.5 | 12968.4 | 12232.3 | 12984.2 | 11740.6 | 13050.9 | 12204.3 | 12992.9 | 12203.5 | 13034.8 | 12417.4 | 8748.5 | 9194.4 | 8525 | 8529 | 9004.6 | 8916.1 | 8951.8 | 8597.5 | 13001.5 | 12031.1 | 12760.2 | 12239.4 | 12725 | 11572.9 | 12886.8 | 12171.1 | 12146.6 | 12162 | 12161.5 | 10618.9 | 11977.6 | 10643 | 11591.6 | 11572.4 | 13118.4 | 11857.4 | 13007.7 | 11935.2 | 12727.6 | 11684.7 | 11772.6 | 11542.4 | 12940.8 | 13124.3 | 13110.2 | 13101.8 | 13115.9 | 13144 | 12258.4 | 13091.5 | 13378.8 | 13314.6 | 13288.4 | 13202.8 | 13218.4 | 12360.5 | 13310.7 | 12466.1 | 34.0048 | 33.6645 | 33.487 | 0 | 33.4739 | 33.7048 | 0 | 48.3812 | 0 | 0 | 86.4336 | 0 | 2.8241 | 2.6998 | 2.9123 | 2.8087 | 2.7874 | 2.7151 | 6.651 | 6.468 | 7.842 | 6.41 | 6.408 | 6.986 | 7.3302 | 7.6343 | 7.3166 | 7.14 | 7.2536 | 6.8098 | 1.4503 | 1.8506 | 1.7182 | 0 | 1.6985 | 1.4575 | 7.7094 | 7.6348 | 7.6431 | 7.518 | 7.3881 | 7.8938 | 1.5242 | 1.8546 | 1.7134 | 0 | 1.7082 | 1.8104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293582 | 541 | 283235 | 564 | 552810.043 | 1444.267 | 7.3302 | 7.6343 | 7.3166 | 7.14 | 7.2536 | 6.8098 | 7.7094 | 7.6348 | 7.6431 | 7.518 | 7.3881 | 7.8938 | 1010120 | 888 | 963940 | 530 | 1968067 | 4267 | 1972642 | 1963800 | 12.3333 | 7.2474 | 1.635 | 7.6312 | 1.7221 | 22.56% | 22.57% | 33.667 | 67.4074 | 2.7913 | 6.7942 | 1987166.2 | 1967867 | 2493292.9922 | 78.93%
2023-04-10 | 2024 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 335090.89 | 6:20 | 18:50 | 9456.2 | 9817 | 9915.1 | 9959.3 | 9939.7 | 9980.6 | 9804.6 | 10023.1 | 9831.6 | 9623.5 | 9700.6 | 9808.1 | 9855 | 9741.3 | 9833.4 | 9945.9 | 9796.3 | 9814.6 | 9823.3 | 9847.8 | 9735.9 | 9848.6 | 9591.1 | 9790.6 | 9696.9 | 8787.5 | 9776.9 | 9650.3 | 9847.9 | 9692.6 | 9682 | 9826.2 | 9763.6 | 9818.4 | 9893.2 | 9809.9 | 9869.1 | 9767.9 | 9750.9 | 9719.9 | 10436.5 | 9722.1 | 10329.7 | 9587.6 | 9874.4 | 10704.7 | 9452.2 | 10339.1 | 9315.7 | 9500.3 | 9972.5 | 9497.7 | 10177.1 | 9244.9 | 10216.4 | 9377.4 | 9218.6 | 10147.4 | 9286.8 | 10155.4 | 10123 | 9148.1 | 9812.3 | 9299.6 | 9671.1 | 9165.3 | 9691.5 | 9930.6 | 9999.8 | 9265.1 | 10019.9 | 9007.5 | 9765 | 9668.2 | 9262.8 | 10051 | 8995 | 10169.2 | 9173.5 | 9984.3 | 9295 | 9785.2 | 9356 | 10142 | 9263.7 | 9709.9 | 9241.1 | 8224.9 | 9786.5 | 9553.9 | 9032.7 | 10052.2 | 9830.3 | 9261.9 | 9173.3 | 9847.2 | 8928.4 | 9300.4 | 9899.9 | 8908.3 | 9969 | 8938.7 | 9802.3 | 9125.6 | 9871.3 | 8739.4 | 9915.4 | 9099.8 | 9839.9 | 9132 | 9853.5 | 9209.8 | 6567.1 | 7208.9 | 6536.6 | 6508.3 | 7244.8 | 7112.9 | 7210.6 | 6672 | 9706.5 | 8786.5 | 9525 | 9036.4 | 9445.9 | 8397.4 | 9553.1 | 8878.2 | 8868 | 8873.6 | 8876.5 | 7729.6 | 8780.7 | 7759.6 | 8876.7 | 8892.4 | 10046.5 | 8966.4 | 10122 | 9167.2 | 9969.3 | 9011.9 | 9107 | 8925.6 | 9822.2 | 10028.4 | 9953.4 | 10005.5 | 9990.8 | 10016.1 | 9313.3 | 10041.3 | 9951.7 | 9974.8 | 10072.4 | 10029.3 | 10053.5 | 9266.6 | 9980.6 | 9288.5 | 33.7863 | 33.492 | 33.4784 | 0 | 33.5036 | 33.7723 | 0 | 44.7163 | 0 | 0 | 82.4405 | 0 | 3.9116 | 3.8358 | 3.9484 | 3.9414 | 3.6016 | 3.4013 | 18.298 | 15.882 | 16.989 | 18.089 | 11.884 | 11.045 | 5.4427 | 5.6209 | 5.5548 | 5.3146 | 5.2856 | 4.8918 | 1.1952 | 1.2338 | 1.4308 | 0 | 1.1159 | 0.96339 | 5.6548 | 5.4891 | 5.7082 | 5.7469 | 5.1691 | 5.7432 | 1.2528 | 1.2355 | 1.4321 | 0 | 1.1319 | 1.1937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 294357 | 542 | 283963 | 565 | 554308.177 | 1448.533 | 5.4427 | 5.6209 | 5.5548 | 5.3146 | 5.2856 | 4.8918 | 5.6548 | 5.4891 | 5.7082 | 5.7469 | 5.1691 | 5.7432 | 775000 | 1000 | 728000 | 1000 | 1498134 | 4266 | 1501000 | 1493868 | 12.5 | 5.3517 | 1.1878 | 5.5852 | 1.2492 | 22.2% | 22.37% | 33.6065 | 63.5784 | 3.7734 | 15.3645 | 1511836.8 | 1498000 | 1845627.354 | 81.16%
2023-04-11 | 2024 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 335090.89 | 6:20 | 19:00 | 8058.3 | 8552.8 | 8562.7 | 8540.4 | 8592 | 8616.9 | 8604.4 | 8944.3 | 8562.1 | 8363.3 | 8445 | 8570.8 | 8510.7 | 8496.4 | 8464.5 | 8586.2 | 8446.1 | 8487.2 | 8530.3 | 8555 | 8438.2 | 8566.1 | 8225.6 | 8471.9 | 8321.1 | 7347.2 | 8400.8 | 8268.8 | 8593.9 | 8493.2 | 8380.1 | 8555 | 8441.9 | 8485.7 | 8524.1 | 8427.5 | 8579.3 | 8508.3 | 8481.2 | 8440.2 | 9246.4 | 8297.9 | 9107.6 | 8123.6 | 8606.9 | 9736.3 | 8131.2 | 9200.2 | 7878.9 | 8069.8 | 8609.4 | 8067.7 | 8882.9 | 7937.4 | 8829.8 | 7857.7 | 7796.9 | 8872.3 | 7868 | 8848.1 | 8813.1 | 7734.4 | 8559.5 | 8004.7 | 8187.9 | 7611 | 8206.3 | 8461.7 | 8623.7 | 7803.3 | 8646.2 | 7430.9 | 8338.2 | 8205.6 | 7764.9 | 8671.3 | 7491.7 | 8835.5 | 7729.2 | 8664.6 | 7749.3 | 8308.5 | 7788.9 | 8687.3 | 7705.6 | 8185 | 7730.3 | 6741.6 | 8419.1 | 8057 | 7527.3 | 8751.3 | 8507.9 | 7833.4 | 7774.7 | 8495.5 | 7536.5 | 7796.5 | 8561.5 | 7429.6 | 8674.4 | 7460.8 | 8436.3 | 7675.8 | 8556.4 | 7270.1 | 8595.7 | 7654.6 | 8500.8 | 7695.9 | 8553.2 | 7783 | 7471.8 | 8299 | 7434 | 7400.4 | 8410.8 | 7590.3 | 6553.5 | 0 | 8400.4 | 7379 | 8173.5 | 7634.7 | 8112.3 | 7048.9 | 8201.4 | 7470.7 | 7437.3 | 7489.3 | 7504.5 | 6448.8 | 7381.7 | 6501.3 | 7324.1 | 7331.3 | 8455.1 | 7292.9 | 8466.2 | 7435 | 8422 | 7391.6 | 7508.3 | 7311.3 | 8019.2 | 8307.3 | 8162 | 8265.6 | 8319.8 | 8379.8 | 7498.5 | 8306 | 8223.8 | 8249.6 | 8326.1 | 8262.2 | 8280.1 | 7395.3 | 8174.7 | 7402.4 | 33.7964 | 33.402 | 33.3615 | 0 | 33.5306 | 33.6922 | 0 | 42.2693 | 0 | 0 | 50.0695 | 0 | 2.6963 | 2.488 | 2.5847 | 2.5807 | 2.5488 | 2.5096 | 6.306 | 5.645 | 6.062 | 6.574 | 5.915 | 6.279 | 4.4893 | 4.5669 | 4.5534 | 4.2885 | 4.3412 | 3.8534 | 0.89217 | 1.0047 | 1.061 | 0 | 0.98571 | 0.80124 | 4.5785 | 4.4595 | 4.5739 | 4.4755 | 4.3707 | 4.4971 | 0.94024 | 1.0088 | 1.0704 | 0 | 0.99464 | 0.98705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295026 | 543 | 284581 | 567 | 555592.443 | 1452.667 | 4.4893 | 4.5669 | 4.5534 | 4.2885 | 4.3412 | 3.8534 | 4.5785 | 4.4595 | 4.5739 | 4.4755 | 4.3707 | 4.4971 | 669000 | 1000 | 618000 | 2000 | 1284266 | 4134 | 1284000 | 1280132 | 12.6667 | 4.3488 | 0.94898 | 4.4925 | 1.0002 | 21.82% | 22.26% | 33.5565 | 46.1694 | 2.568 | 6.1302 | 1293489.8 | 1284200 | 1515337.635 | 84.75%
2023-04-12 | 2024 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 335090.89 | 6:20 | 19:00 | 12640.8 | 13190.1 | 13166.8 | 13144.3 | 13221.1 | 13280.2 | 13255.1 | 13556 | 13173.5 | 13002.8 | 13087 | 13205.8 | 13233.7 | 13145.1 | 13109.3 | 13286.5 | 13087.6 | 13136.1 | 13228.4 | 13281.3 | 13089.6 | 13228.8 | 12851 | 13133 | 13061.5 | 11700 | 13138.7 | 12983.3 | 13249.5 | 13123.9 | 13053.5 | 13197.5 | 13222.4 | 13242.9 | 13293.2 | 13190.3 | 13303.2 | 13153.1 | 13158 | 13155.5 | 13753.6 | 12858.3 | 13624.5 | 12630.9 | 13225.9 | 14218.6 | 12678.8 | 13708.6 | 12459 | 12726 | 13372.4 | 12778 | 13624.4 | 12562.7 | 13583.4 | 12499.7 | 12377.6 | 13540.6 | 12414.4 | 13502.6 | 13448.3 | 12209.9 | 13250.5 | 12704.1 | 13020.3 | 12301.1 | 13038.7 | 13360.2 | 13409.4 | 12613.3 | 13496.9 | 12038 | 13109.2 | 13106.5 | 12446.8 | 13522.5 | 12082.1 | 13626.2 | 12396.8 | 13459.5 | 12630.2 | 13261.8 | 12709.5 | 13599.4 | 12577.6 | 13143.9 | 12551.3 | 11012.5 | 13336.8 | 12951.5 | 12265.7 | 13610.5 | 13349.4 | 12614.7 | 12483.2 | 13362.6 | 12279 | 12715.7 | 13492.6 | 12235.4 | 13554.1 | 12246.1 | 13383.6 | 12558.2 | 13421.4 | 11916.2 | 13501.4 | 12527.6 | 13412.5 | 12487.5 | 13462.8 | 12662.4 | 8228.4 | 9042.7 | 8189.3 | 8139.2 | 9094 | 8964.9 | 8771.7 | 8022.5 | 13415.9 | 12195.6 | 13172.4 | 12514.3 | 13086.4 | 11607.5 | 13258.9 | 12328.5 | 12310.1 | 12429.6 | 12377.3 | 10659.4 | 12274.9 | 10828.3 | 12192.6 | 12223.1 | 13628.8 | 12324 | 13650.6 | 12585.4 | 13566.4 | 12473.3 | 12615.9 | 12278 | 13345.5 | 13582.3 | 13474.5 | 13527 | 13534.4 | 13559.2 | 12702.6 | 13550.4 | 13455.3 | 13490.6 | 13577.7 | 13522.3 | 13557.2 | 12631.7 | 13479.6 | 12647.3 | 33.7219 | 33.3877 | 33.3865 | 0 | 30.7425 | 33.686 | 0 | 48.1785 | 0 | 0 | 38.5794 | 0 | 3.1857 | 3.1625 | 3.0453 | 3.333 | 2.8938 | 2.9817 | 7.48 | 7.838 | 6.521 | 6.908 | 6.34 | 7.612 | 7.2788 | 7.521 | 7.1806 | 7.0751 | 6.5867 | 6.973 | 1.3905 | 1.7048 | 1.6928 | 0 | 1.5384 | 1.4746 | 7.6535 | 7.5044 | 7.5107 | 7.3857 | 6.8376 | 7.8625 | 1.4554 | 1.7162 | 1.6643 | 0 | 1.5349 | 1.8324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 296066 | 545 | 285569 | 569 | 557612.777 | 1456.733 | 7.2788 | 7.521 | 7.1806 | 7.0751 | 6.5867 | 6.973 | 7.6535 | 7.5044 | 7.5107 | 7.3857 | 6.8376 | 7.8625 | 1040000 | 2000 | 988000 | 2000 | 2020334 | 4066 | 2024000 | 2016268 | 12.6667 | 7.1026 | 1.5602 | 7.459 | 1.6406 | 21.97% | 22% | 32.9849 | 43.3789 | 3.1003 | 7.1165 | 2039145.3 | 2020334 | 2494067.8706 | 81.01%
2023-04-13 | 2024 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 335090.89 | 6:20 | 19:00 | 12192.6 | 12696.4 | 12749.8 | 12746.3 | 12810.4 | 12861.2 | 12778.2 | 13050.7 | 12593.2 | 12457 | 12473.1 | 12571.4 | 12696.4 | 12548 | 12588.2 | 12789.1 | 12483.1 | 12549.3 | 12626.2 | 12664.9 | 12502.5 | 12647.6 | 12303 | 12545.6 | 12457.3 | 11374.2 | 12564.6 | 12422.1 | 12655.9 | 12513.5 | 12489.8 | 12610.1 | 12587.7 | 12605.7 | 12698.8 | 12580.1 | 12690.8 | 12511 | 12568.1 | 12579.6 | 13100.7 | 12282.7 | 13025 | 12231 | 12597.8 | 13546.9 | 12081.5 | 13043.1 | 11993.3 | 12202.2 | 12772.2 | 12216.8 | 13008.5 | 12047 | 12936.1 | 12018.7 | 11823.2 | 12969 | 11965.6 | 12953.9 | 12910.4 | 11748.3 | 12660 | 12131.1 | 12358.5 | 11811.6 | 12388.7 | 12758.7 | 12732.7 | 12035.3 | 12804.9 | 11572.1 | 12469.7 | 12429.8 | 11919.5 | 12849.4 | 11632.3 | 13005.1 | 11913.1 | 12852.4 | 12116.1 | 12656.5 | 12121.8 | 13054.5 | 12062.5 | 12538.2 | 11997.2 | 10698.1 | 12656.5 | 12373.6 | 11788 | 12980.5 | 12701.8 | 12033.9 | 11933.6 | 12717.3 | 11708.1 | 12126 | 12834.5 | 11750.9 | 12949.2 | 11777.6 | 12771.1 | 12038.4 | 12831.5 | 11537.5 | 12927 | 12059.3 | 12852.7 | 12057.6 | 12901.8 | 12270.7 | 11754.2 | 12651.7 | 11775.6 | 11737 | 12779.7 | 12676.8 | 12738.2 | 12086.5 | 12921.2 | 11885.6 | 12618.7 | 12076.8 | 12568.7 | 11431.7 | 12790.4 | 12066.7 | 11891.4 | 11907.2 | 12047.4 | 10414.6 | 11815.8 | 10484 | 11867.7 | 11877.3 | 13105.7 | 11935.8 | 13187.2 | 12173.3 | 13129.7 | 12062.6 | 12205.6 | 11914.4 | 12716 | 13020.5 | 12811.1 | 12924.6 | 12948.7 | 13010.3 | 12217.6 | 13043.7 | 12573 | 12733.5 | 12881.9 | 12863 | 12934.9 | 12019.7 | 12659.5 | 12030.6 | 34.4198 | 34.1153 | 34.2199 | 0 | 34.363 | 34.3416 | 0 | 49 | 0 | 0 | 56.4 | 0 | 2.303 | 2.1791 | 2.1518 | 2.3364 | 2.1696 | 2.1061 | 6.036 | 6.629 | 5.453 | 6.629 | 6.158 | 5.687 | 7.0663 | 7.3289 | 6.9911 | 6.8257 | 7.2026 | 6.6693 | 1.4041 | 1.6364 | 1.7089 | 0 | 1.68 | 1.3961 | 7.3961 | 7.2709 | 7.2614 | 7.1907 | 7.4302 | 7.565 | 1.4715 | 1.6448 | 1.6877 | 0 | 1.6829 | 1.7332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297062 | 546 | 286549 | 570 | 559582.51 | 1460.733 | 7.0663 | 7.3289 | 6.9911 | 6.8257 | 7.2026 | 6.6693 | 7.3961 | 7.2709 | 7.2614 | 7.1907 | 7.4302 | 7.565 | 996000 | 1000 | 980000 | 1000 | 1969733 | 4000 | 1974000 | 1965733 | 12.6667 | 7.014 | 1.5651 | 7.3524 | 1.644 | 22.31% | 22.36% | 34.2919 | 52.7 | 2.2077 | 6.0987 | 1986424.1 | 1969600 | 2399551 | 82.08%
2023-04-14 | 2024 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 335090.89 | 6:20 | 19:00 | 11629.8 | 12253.5 | 12335.2 | 12263.5 | 12520.4 | 12622.7 | 12400.7 | 12731 | 12157.1 | 11839.9 | 12127.7 | 12163.1 | 12550.2 | 12252 | 12575.7 | 12702.3 | 12511.1 | 12592.7 | 12535.4 | 12540.1 | 12467.6 | 12559.8 | 12286.7 | 12513.9 | 12211.5 | 10955.4 | 12304 | 12214.8 | 12535.4 | 12495.9 | 12359.3 | 12346.8 | 12242.2 | 12256.9 | 12361.6 | 12219.2 | 12353.5 | 12271.2 | 12336.3 | 12380.3 | 13457 | 12134.3 | 13289.8 | 12360.4 | 12801 | 13856.2 | 12324.3 | 13357.3 | 11622.6 | 11789.4 | 12527 | 11862.9 | 12796.7 | 11839.4 | 12576.2 | 11657.1 | 11260.7 | 12349.4 | 11423.2 | 12332.8 | 12215.3 | 11160.5 | 12035.3 | 11593.2 | 11655.4 | 10969.8 | 11656.6 | 11864.8 | 12018.1 | 11249.7 | 12117.4 | 10804.4 | 11886.4 | 11795.4 | 11367 | 12187.9 | 10998.2 | 12431.2 | 11351.2 | 12224 | 11222.8 | 11790.2 | 11297.5 | 12085.1 | 11228.9 | 11748.8 | 11258.3 | 10008.3 | 12174.4 | 11857.5 | 11333.8 | 12566 | 12367.8 | 11649.8 | 11546.7 | 12328.7 | 11242.5 | 11837.7 | 12623.1 | 11526.6 | 12742.4 | 11527.5 | 12577.9 | 11828.3 | 12756.3 | 11274.6 | 12929.6 | 12024.6 | 12797 | 11923.1 | 12813.7 | 12208.1 | 11625.4 | 12734.5 | 11672.4 | 11671.9 | 12992.9 | 12904.9 | 12991.4 | 12173.8 | 13114.9 | 11803.4 | 12798.4 | 12129.8 | 12663.3 | 11307.5 | 12917.8 | 12007.4 | 11882.9 | 11872.3 | 11911.6 | 10284.5 | 11769.3 | 10406 | 11792 | 11773.8 | 13035.8 | 11852.5 | 12971.1 | 12060.3 | 13043.9 | 11985.4 | 12150.9 | 11821.9 | 12518.2 | 12699.3 | 12592.6 | 12707.8 | 12877.8 | 12961.1 | 12041 | 12735.6 | 11718 | 11798.3 | 11815.4 | 11755.9 | 11880.8 | 11141.8 | 11836.1 | 11236.1 | 36.2627 | 35.9905 | 36.0197 | 0 | 36.2287 | 36.0921 | 0 | 49.3 | 0 | 0 | 49.89 | 0 | 2.5883 | 2.731 | 2.8126 | 2.5855 | 2.828 | 2.7521 | 5.034 | 6.199 | 6.046 | 5.073 | 5.125 | 6.087 | 6.8506 | 7.0968 | 7.0429 | 6.3611 | 7.1629 | 6.5099 | 1.3553 | 1.6431 | 1.7141 | 0 | 1.7405 | 1.4251 | 7.1406 | 7.044 | 7.2767 | 6.6592 | 7.4094 | 7.4082 | 1.4231 | 1.6548 | 1.703 | 0 | 1.7429 | 1.766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 298031 | 547 | 287507 | 571 | 561503.311 | 1464.8 | 6.8506 | 7.0968 | 7.0429 | 6.3611 | 7.1629 | 6.5099 | 7.1406 | 7.044 | 7.2767 | 6.6592 | 7.4094 | 7.4082 | 969000 | 1000 | 958000 | 1000 | 1920801 | 4067 | 1925000 | 1916734 | 12.6667 | 6.8374 | 1.5756 | 7.1563 | 1.658 | 23.04% | 23.17% | 36.1187 | 49.595 | 2.7163 | 5.594 | 1937713.2 | 1920600 | 2331391.4686 | 82.38%
2023-04-15 | 2024 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 335090.89 | 6:20 | 19:00 | 12179 | 12460 | 12373 | 12437 | 12368 | 12303 | 12253 | 12550 | 12551 | 12498 | 12215 | 12417 | 12270 | 12244 | 12023 | 12260 | 11947 | 11985 | 12122 | 12196 | 11959 | 12103 | 11774 | 12031 | 11992 | 10864 | 12112 | 11945 | 12146 | 11921 | 11918 | 12102 | 12112 | 12171 | 12184 | 12041 | 12206 | 12003 | 11966 | 12097 | 12117 | 11164 | 11921 | 10914 | 11411 | 12589 | 11142 | 12162 | 11682 | 11940 | 12452 | 11855 | 12677 | 11603 | 12615 | 11607 | 11606 | 12742 | 11684 | 12787 | 12744 | 11502 | 12599 | 12156 | 12426 | 11880 | 12474 | 12881 | 12933 | 12156 | 12992 | 11654 | 12535 | 12631 | 12016 | 13091 | 11789 | 13201 | 12060 | 13062 | 12219 | 12828 | 12267 | 13191 | 12201 | 12772 | 12125 | 10679 | 12542 | 12432 | 11508 | 12776 | 12380 | 11588 | 11439 | 12410 | 11343 | 11803 | 12452 | 11257 | 12362 | 11181 | 12071 | 11349 | 12039 | 10702 | 12046 | 11129 | 11866 | 10977 | 11775 | 11167 | 11334 | 12114 | 11223 | 11024 | 11983 | 12031 | 11899 | 11355 | 12088 | 10984 | 11692 | 11071 | 11538 | 10406 | 11876 | 11141 | 11163 | 11264 | 11080 | 9648 | 11138 | 9866 | 11268 | 11261 | 13432 | 11903 | 13403 | 12069 | 12802 | 11583 | 11697 | 11347 | 13167 | 13450 | 13300 | 13399 | 13409 | 13436 | 12473 | 13440 | 13243 | 13325 | 13501 | 13384 | 13432 | 12449 | 13216 | 12516 | 35.7 | 35.4 | 35.3 | 0 | 35.3 | 35.8 | 0 | 49 | 0 | 0 | 49.1 | 0 | 3.6 | 3.6 | 3.5 | 3.6 | 3.8 | 3.6 | 8.5 | 8.1 | 7.8 | 8.1 | 8 | 9 | 7 | 7.1 | 6.5 | 7 | 6.8 | 6.9 | 1.3859 | 1.5664 | 1.5935 | 0 | 1.5761 | 1.4692 | 7.17 | 6.94 | 6.64 | 7.37 | 6.9 | 7.88 | 1.46 | 1.58 | 1.6 | 0 | 1.59 | 1.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 298999 | 548 | 288463 | 573 | 0 | 0 | 7 | 7.1 | 6.5 | 7 | 6.8 | 6.9 | 7.17 | 6.94 | 6.64 | 7.37 | 6.9 | 7.88 | 968000 | 1000 | 956000 | 2000 | 1916889 | 2200 | 1921000 | 1914689 | 12.6667 | 6.8833 | 1.5182 | 7.15 | 1.612 | 22.06% | 22.55% | 35.5 | 49.05 | 3.6167 | 8.25 | 1933449 | 1916866 | 2346903.8 | 81.68%
2023-04-16 | 2024 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 335090.89 | 6:20 | 18:50 | 12622 | 13090.2 | 13080.1 | 13077.7 | 13119.6 | 13191.5 | 13127 | 13425.7 | 13096.9 | 12869.2 | 13010.3 | 13116.9 | 13169.1 | 13069.4 | 13048.8 | 13240.5 | 13006.6 | 13095.6 | 13140 | 13186 | 13020.8 | 13156.7 | 12801.3 | 13064.5 | 12988.6 | 11847.8 | 13074.6 | 12940.7 | 13175.8 | 13013.1 | 12991 | 13061.9 | 13111.6 | 13124.1 | 13202 | 13067.8 | 13190 | 13027.1 | 13104.2 | 13113.5 | 13774.3 | 12914.7 | 13653.3 | 12766.6 | 13171.7 | 14127.9 | 12670.2 | 13693.3 | 12521.6 | 12740 | 13320.5 | 12754 | 13564.3 | 12543.9 | 13524.4 | 12570 | 12470.3 | 13586.5 | 12516.6 | 13550.1 | 13501.8 | 12304.9 | 13244.6 | 12681 | 12962.1 | 12381.4 | 12981.5 | 13295.4 | 13446.7 | 12599.2 | 13425.8 | 12163.5 | 13081.9 | 13069.4 | 12508.5 | 13477.3 | 12215.5 | 13565 | 12462.3 | 13395.2 | 12637.3 | 13219.8 | 12664.8 | 13581.3 | 12596.3 | 13098.5 | 12530.8 | 11175.3 | 13221.4 | 12931.9 | 12347.3 | 13551.9 | 13274.3 | 12563.5 | 12446.4 | 13270.8 | 12311.4 | 12764.6 | 13517.9 | 12366.8 | 13558.4 | 12395.1 | 13383.9 | 12625.6 | 13418.3 | 12103.4 | 13503 | 12604.2 | 13397.9 | 12569 | 13407.5 | 12775.2 | 12385.1 | 13262.4 | 12487 | 12313.2 | 13337.9 | 13275.9 | 13275 | 12609.3 | 13412.5 | 12356.9 | 13139.2 | 12575.4 | 13026.7 | 11832.5 | 13260.3 | 12529.7 | 12365.3 | 12387.1 | 12427.1 | 10779.4 | 12267.6 | 10876 | 12185.3 | 12183 | 13690.3 | 12457.7 | 13711.4 | 12650.1 | 13528.5 | 12416.2 | 12548.6 | 12232.1 | 13410.5 | 13660.2 | 13605 | 13653.5 | 13618.4 | 13655.1 | 12784.7 | 13652 | 13453.4 | 13532.1 | 13599 | 13574.3 | 13662.3 | 12741.8 | 13507.8 | 12802.7 | 34.6 | 34.4 | 34.6 | 0 | 34.39 | 34.73 | 0 | 49.55 | 0 | 0 | 49.58 | 0 | 3.79 | 3.95 | 3.49 | 4.08 | 3.82 | 3.74 | 9.17 | 9.28 | 8.11 | 9.11 | 8.99 | 9.8 | 7.55 | 7.83 | 7.55 | 7.38 | 7.62 | 7.07 | 1.47 | 1.79 | 1.8 | 0 | 1.81 | 1.54 | 7.81 | 7.73 | 7.74 | 7.76 | 7.82 | 8.1 | 1.54 | 1.8 | 1.8 | 0 | 1.81 | 1.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300035 | 549.4 | 289487 | 573.67 | 2055 | 2 | 7.55 | 7.83 | 7.55 | 7.38 | 7.62 | 7.07 | 7.81 | 7.73 | 7.74 | 7.76 | 7.82 | 8.1 | 1036000 | 1400 | 1024000 | 670 | 2055000 | 2000 | 2057930 | 2053000 | 12.5 | 7.5 | 1.682 | 7.8267 | 1.772 | 22.43% | 22.64% | 34.544 | 49.565 | 3.8117 | 9.0767 | 2073568.7 | 2054340 | 2571670 | 79.88%
2023-04-17 | 2024 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 335090.89 | 6:19 | 19:08 | 12483.3 | 12926.4 | 12909 | 12904.9 | 12952.4 | 13024.3 | 12948.8 | 13245.3 | 12923.2 | 12719.2 | 12836.7 | 12942.5 | 13026.8 | 12899.5 | 12956.9 | 13115.8 | 12920.4 | 13002.9 | 13000.6 | 13083.9 | 12911 | 13033.7 | 12720.4 | 12953.9 | 12816.2 | 11656.2 | 12894.3 | 12761.6 | 13041.4 | 12909.1 | 12877.8 | 13010.3 | 12981.4 | 12991.7 | 13035.5 | 12927.3 | 13067.8 | 12900.4 | 12957 | 12977.3 | 13608.7 | 12761.5 | 13497.3 | 12619.1 | 13005.5 | 13965.1 | 12510.1 | 13538.9 | 12357.3 | 12571.1 | 13148.9 | 12583.4 | 13399.9 | 12383.5 | 13362.4 | 12423.7 | 12317.8 | 13416.9 | 12342.6 | 13357.3 | 13311.7 | 12138.5 | 13057.3 | 12508.1 | 12850.9 | 12299.5 | 12859.2 | 13194.1 | 13317 | 12484.9 | 13290.1 | 12041.2 | 12919.2 | 12897.1 | 12344.6 | 13301.7 | 12044.9 | 13392.1 | 12295.8 | 13220.5 | 12512 | 13089.8 | 12542.4 | 13460.7 | 12494.9 | 12983.7 | 12419.2 | 11079 | 13073.6 | 12827.7 | 12238.3 | 13414.6 | 13143 | 12425.2 | 12307.3 | 13134.8 | 12180.2 | 12615.4 | 13372.4 | 12231.9 | 13414.4 | 12265.8 | 13239.1 | 12487.8 | 13275.2 | 11961.8 | 13359.6 | 12459.4 | 13253.4 | 12429.9 | 13269.7 | 12645.1 | 12246.9 | 13127 | 12375.1 | 12191.7 | 13191.2 | 13141.1 | 13141.5 | 12487.9 | 13282 | 12241.9 | 12996.2 | 12438.8 | 12887.1 | 11695.3 | 13134.3 | 12426.5 | 12243.2 | 12255 | 12313.2 | 10646.3 | 12146.2 | 10725.7 | 12042.4 | 12040.1 | 13579 | 12368.9 | 13579.4 | 12520.5 | 13389.5 | 12287 | 12413.8 | 12095.1 | 13273.8 | 13519.1 | 13543.3 | 13523.9 | 13494.4 | 13535.3 | 12654 | 13511.6 | 13296.7 | 13384.1 | 13467.2 | 13433 | 13524.4 | 12614.6 | 13358.9 | 12670.8 | 34.4338 | 34.2851 | 34.3166 | 0 | 34.2615 | 34.5298 | 0 | 49.2149 | 0 | 0 | 49.0426 | 0 | 4.5798 | 4.7805 | 4.5735 | 4.7467 | 4.761 | 4.6792 | 9.307 | 10.32 | 9.253 | 9.481 | 10.202 | 9.175 | 7.3907 | 7.6916 | 7.4044 | 7.2717 | 7.4839 | 6.9568 | 1.4491 | 1.7482 | 1.7776 | 0 | 1.767 | 1.4878 | 7.6401 | 7.5776 | 7.5758 | 7.641 | 7.6883 | 7.9693 | 1.5265 | 1.7556 | 1.7771 | 0 | 1.7717 | 1.8526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301061 | 550 | 290501 | 575 | 4088.4 | 4.4 | 7.3907 | 7.6916 | 7.4044 | 7.2717 | 7.4839 | 6.9568 | 7.6401 | 7.5776 | 7.5758 | 7.641 | 7.6883 | 7.9693 | 1026000 | 600 | 1014000 | 1330 | 2033400 | 2400 | 2038070 | 2031000 | 12.8167 | 7.3665 | 1.6459 | 7.682 | 1.7367 | 22.34% | 22.61% | 34.3654 | 49.1288 | 4.6868 | 9.623 | 2051248.7 | 2032933 | 2530279.4117 | 80.34%
2023-04-18 | 2024 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 335090.89 | 6:21 | 19:05 | 12142.2 | 12574.9 | 12635.8 | 12571.7 | 12680.3 | 12738.4 | 12597.2 | 12894.8 | 12587.8 | 12397.2 | 12503.9 | 12608.2 | 12682.7 | 12587.4 | 12634.1 | 12789.4 | 12638.2 | 12707.5 | 12717 | 12740.1 | 12623.2 | 12740.6 | 12405.2 | 12653 | 12547.3 | 11351.3 | 12596.2 | 12482.4 | 12748.5 | 12626.8 | 12569.8 | 12723.4 | 12690.1 | 12722.6 | 12750 | 12638.8 | 12776.2 | 12590.9 | 12670 | 12710.1 | 13217.4 | 12441.9 | 13120.9 | 12290.3 | 12650.8 | 13466.2 | 12219.9 | 13192.8 | 11984.9 | 12201.4 | 12783.7 | 12223.3 | 13019.1 | 12031.3 | 13000.1 | 12057.6 | 11944 | 13021.9 | 11952.1 | 12970.1 | 12945.8 | 11776 | 12681.2 | 12115.3 | 12465.6 | 11899 | 12461.6 | 12801.3 | 12922.6 | 12083.8 | 12876.5 | 11618.9 | 12552.2 | 12481 | 11942 | 12885.3 | 11628.4 | 12960.2 | 11880 | 12808.4 | 12110.8 | 12691 | 12175.5 | 13018.6 | 12095.1 | 12606.2 | 12083.9 | 10789.7 | 12708 | 12514.6 | 11842.8 | 13005.5 | 12813.6 | 12077 | 11976.7 | 12793.8 | 11813.4 | 12298.9 | 13020.6 | 11912.1 | 13077 | 11944.5 | 12893.6 | 12142.9 | 12983.1 | 11657.1 | 13016.7 | 12166.7 | 12885.1 | 12086.8 | 12914.1 | 12280.3 | 11910.7 | 12784.3 | 12031.1 | 11823.2 | 12873.9 | 12812.8 | 12841.4 | 12136.9 | 12954 | 11890.4 | 12693.4 | 12098.5 | 12577.4 | 11404.9 | 12781.3 | 12043.6 | 11882.9 | 11912.6 | 11954.1 | 10400.9 | 11809.1 | 10485.9 | 11725 | 11716.5 | 13190.5 | 12065.2 | 13177.8 | 12186 | 13028.1 | 11944.1 | 12110.2 | 11749.7 | 12898.7 | 13131.8 | 13079.4 | 13086.6 | 13087.2 | 13120.1 | 12295.6 | 13092.2 | 13097.4 | 13156.6 | 13090.6 | 13066.9 | 13132.6 | 12282.7 | 12957.3 | 12375.7 | 34.3851 | 34.0989 | 34.225 | 0 | 34.3077 | 34.4758 | 0 | 48.89 | 0 | 0 | 48.8 | 0 | 4.273 | 4.2667 | 4.314 | 4.2126 | 4.4532 | 4.2545 | 10.155 | 10.131 | 11.087 | 10.151 | 10.313 | 9.649 | 7.2228 | 7.5267 | 7.2562 | 7.0847 | 7.3345 | 6.7743 | 1.3946 | 1.7419 | 1.7272 | 0 | 1.752 | 1.4746 | 7.4228 | 7.4022 | 7.3752 | 7.433 | 7.5018 | 7.7804 | 1.4758 | 1.7505 | 1.7327 | 0 | 1.7571 | 1.8322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302059.9 | 551 | 291488.72 | 576 | 6068.067 | 7.667 | 7.2228 | 7.5267 | 7.2562 | 7.0847 | 7.3345 | 6.7743 | 7.4228 | 7.4022 | 7.3752 | 7.433 | 7.5018 | 7.7804 | 998900 | 1000 | 987720 | 1000 | 1979667 | 3267 | 1984620 | 1976400 | 12.7333 | 7.1999 | 1.6181 | 7.4859 | 1.7097 | 22.47% | 22.84% | 34.2985 | 48.845 | 4.2957 | 10.2477 | 1995963.5 | 1979600 | 2463935.9279 | 80.34%
2023-04-19 | 2024 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 335090.89 | 6:20 | 19:02 | 10573 | 11025 | 10993.9 | 10970.2 | 11059.5 | 11132.6 | 11027.1 | 11359.5 | 11037.2 | 10895.9 | 10927.9 | 11047.7 | 11073.7 | 11005.8 | 11030.1 | 11136.4 | 10999.5 | 11081.4 | 11062.2 | 11062.9 | 11075.9 | 11128.8 | 10887.5 | 11064.1 | 10946.5 | 9883.3 | 11014.2 | 10882.2 | 11181.1 | 11077 | 11027.4 | 11064.6 | 11102.6 | 11118.8 | 11159.7 | 11053.5 | 11195.2 | 11073.1 | 11126.8 | 11131.8 | 11801.9 | 10932.4 | 11699.9 | 10816.1 | 11219 | 12192 | 10686.8 | 11725.2 | 10464.2 | 10663.3 | 11239.5 | 10687.2 | 11511.1 | 10490.9 | 11490.4 | 10551 | 10435.6 | 11553.8 | 10455.7 | 11456.4 | 11417.7 | 10278.3 | 11164.8 | 10519.2 | 11000.4 | 10456.8 | 11004.9 | 11361.5 | 11470.1 | 10641.4 | 11433.5 | 10217 | 11052.7 | 11033 | 10463.6 | 11466.8 | 10210.2 | 11529.2 | 10430.7 | 11381.5 | 10671.2 | 11250.8 | 10736.6 | 11646 | 10652.1 | 11168.1 | 10628.3 | 9520 | 11304.8 | 11060.3 | 10389.8 | 11595.3 | 11313.7 | 10594.2 | 10516.3 | 11334.3 | 10394.4 | 10823.6 | 11578.9 | 10441.3 | 11600.5 | 10460.9 | 11418.8 | 10675.7 | 11485.9 | 10193.6 | 11558.3 | 10680.1 | 11439.2 | 10627.4 | 11498.2 | 10842 | 10502 | 11372.9 | 10476.6 | 10396 | 11458.6 | 11392.9 | 11381.3 | 10721.5 | 11526.4 | 10460.8 | 11218.4 | 10647 | 11127.3 | 10037 | 11344.4 | 10620.6 | 10517.1 | 10540.5 | 10582.5 | 9228.2 | 10438.2 | 9293.4 | 10443 | 10433.7 | 11847.1 | 10610.7 | 11863.4 | 10797.6 | 11664.3 | 10602.6 | 10725.4 | 10464.4 | 11572.9 | 11813.6 | 11821.6 | 11796.4 | 11790.6 | 11797.9 | 10937.3 | 11783.8 | 11717.7 | 11755.6 | 11770.1 | 11734.4 | 11799.6 | 10898.1 | 11719 | 10956.1 | 31.7004 | 31.4034 | 31.4787 | 0 | 31.8997 | 31.7357 | 0 | 43.2 | 0 | 0 | 43.7 | 0 | 4.6807 | 4.7484 | 4.5896 | 4.6497 | 4.6469 | 4.5605 | 8.911 | 8.559 | 8.205 | 8.385 | 8.583 | 8.156 | 6.1519 | 6.4238 | 6.2992 | 6.1051 | 6.3337 | 5.8 | 1.2919 | 1.4651 | 1.5798 | 0 | 1.4925 | 1.2604 | 6.243 | 6.1909 | 6.2775 | 6.3572 | 6.3392 | 6.7507 | 1.3711 | 1.473 | 1.5997 | 0 | 1.516 | 1.568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302937 | 552 | 292364 | 577 | 7815.934 | 11.933 | 6.1519 | 6.4238 | 6.2992 | 6.1051 | 6.3337 | 5.8 | 6.243 | 6.1909 | 6.2775 | 6.3572 | 6.3392 | 6.7507 | 877100 | 1000 | 875280 | 1000 | 1747867 | 4266 | 1750380 | 1743601 | 12.7 | 6.1856 | 1.418 | 6.3597 | 1.5056 | 22.92% | 23.67% | 31.6436 | 43.45 | 4.646 | 8.4665 | 1761802.4 | 1747733 | 2144093.7652 | 81.51%
2023-04-20 | 2024 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 335090.89 | 6:22 | 19:17 | 11921.4 | 12412.5 | 12385.6 | 12372.8 | 12452.6 | 12561.1 | 12384.7 | 12718.6 | 12375.9 | 12193.1 | 12269.4 | 12383.9 | 12478.9 | 12362.5 | 12441.1 | 12535.1 | 12409.3 | 12487.9 | 12459 | 12492.2 | 12499.5 | 12506.9 | 12302.6 | 12462.5 | 12292.3 | 11074.3 | 12360.9 | 12275 | 12547.9 | 12415.5 | 12403.2 | 12472.8 | 12483.5 | 12489.1 | 12534.8 | 12414.2 | 12565.7 | 12522.9 | 12501.3 | 12554 | 13128.4 | 12226.1 | 13001.5 | 12118.3 | 12534 | 13513.3 | 11964.6 | 13041.3 | 11739 | 11973.9 | 12609.7 | 11976.9 | 12908.5 | 11797.8 | 12869.8 | 11861.6 | 11684.2 | 12899.9 | 11716.8 | 12810.1 | 12761.2 | 11581.7 | 12446.3 | 11948.8 | 12290.1 | 11686 | 12306.2 | 12615.5 | 12763.4 | 11863.7 | 12720.1 | 11383.3 | 12321.4 | 12300.8 | 11673.9 | 12741.5 | 11391.6 | 12809.5 | 11609.2 | 12632.6 | 11882.9 | 12523.7 | 11914.7 | 12917.8 | 11988.2 | 12612 | 11848 | 10543.8 | 12588.2 | 12319 | 11663.4 | 12924.4 | 12643 | 11914 | 11819.9 | 12630.2 | 11570.4 | 12043.7 | 12841.3 | 11597.9 | 12901.9 | 11653 | 12737.6 | 11883.2 | 12812.6 | 11367.3 | 12886.2 | 11902.9 | 12794.7 | 11889.2 | 12856.4 | 12132.4 | 11653.9 | 12595.7 | 11745.4 | 11575.6 | 12703.4 | 12622.4 | 12633.9 | 11924 | 12793.1 | 11667.6 | 12487.6 | 11884 | 12423.7 | 11193 | 12633.4 | 11848.1 | 11630.2 | 11626.7 | 11743.6 | 10156.2 | 11521.1 | 10170 | 11500.7 | 11486.4 | 13098.6 | 11864.5 | 13071.4 | 11933.4 | 12877.9 | 11680.7 | 11830.8 | 11522.2 | 12764.2 | 13027.7 | 13083 | 13055.2 | 13031.6 | 13055.5 | 12083.6 | 12998 | 13111.9 | 13130.6 | 12973.8 | 12941.7 | 13015.8 | 12051.1 | 13162.2 | 12229.3 | 32.6753 | 32.2935 | 32.3914 | 0 | 32.882 | 32.5298 | 0 | 45.7 | 0 | 0 | 45.5 | 0 | 4.0654 | 3.9776 | 3.923 | 3.9454 | 4.1393 | 3.8618 | 9.388 | 9.631 | 9.441 | 9.092 | 9.306 | 9.556 | 6.9651 | 7.2346 | 7.0118 | 6.8101 | 7.0399 | 6.5099 | 1.4157 | 1.75 | 1.7345 | 0 | 1.7465 | 1.4473 | 7.1244 | 7.0668 | 7.0681 | 7.1061 | 7.1342 | 7.5803 | 1.5053 | 1.7537 | 1.7587 | 0 | 1.764 | 1.7919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303919 | 553 | 293337 | 578 | 9765.401 | 16.2 | 6.9651 | 7.2346 | 7.0118 | 6.8101 | 7.0399 | 6.5099 | 7.1244 | 7.0668 | 7.0681 | 7.1061 | 7.1342 | 7.5803 | 982000 | 1000 | 973000 | 1000 | 1949467 | 4267 | 1953000 | 1945200 | 12.9167 | 6.9286 | 1.6188 | 7.18 | 1.7147 | 23.36% | 23.88% | 32.5544 | 45.6 | 3.9854 | 9.4023 | 1966417.3 | 1949400 | 2386079.968 | 81.7%
2023-04-21 | 2024 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 335090.89 | 6:21 | 19:12 | 12762.6 | 13276.6 | 13323.6 | 13320.4 | 13353.7 | 13475.2 | 13301.6 | 13582.2 | 13228.3 | 12982.7 | 13167.8 | 13240.4 | 13456.5 | 13261.1 | 13392.1 | 13534.9 | 13347.7 | 13418 | 13416.2 | 13383.8 | 13440.5 | 13466.2 | 13237.7 | 13416.5 | 13273.7 | 12155.4 | 13365.8 | 13322.7 | 13465.3 | 13293 | 13317.1 | 13376.6 | 13423.4 | 13451.7 | 13526 | 13390.9 | 13518.9 | 13464.2 | 13410.3 | 13449.1 | 14146.9 | 13331.6 | 14028.4 | 13195 | 13615.3 | 14406.7 | 13013.9 | 14098.7 | 12764.3 | 12945.4 | 13559.4 | 12947.4 | 13824.3 | 12825.9 | 13721.7 | 12848.4 | 12616.7 | 13661.2 | 12688.1 | 13629.2 | 13565.2 | 12617.7 | 13199.4 | 12730.7 | 13042.1 | 12447.6 | 13050.3 | 13292.8 | 13475.8 | 12624.3 | 13414.9 | 12218.3 | 13087.4 | 13047.2 | 12499.8 | 13434.1 | 12215.7 | 13501.4 | 12401.5 | 13281.1 | 12678.6 | 13265 | 12660 | 13591.8 | 12629.9 | 13070.3 | 12586.6 | 11317.1 | 13386.3 | 13014.4 | 12639.3 | 13837.4 | 13628.6 | 12947.1 | 12828.8 | 13540 | 12513 | 12903.4 | 13654.5 | 12467.5 | 13860.5 | 12616.6 | 13692 | 12843.7 | 13712 | 12403 | 13786.9 | 12862.7 | 13691 | 12851.8 | 13687.3 | 13042.8 | 12484.3 | 13357.9 | 12647 | 12497.7 | 13511 | 13400.2 | 13466.3 | 12836.9 | 13583.7 | 12615.5 | 13380.6 | 12849.4 | 13311.1 | 12145.1 | 13478.7 | 12760.8 | 12517.4 | 12454.9 | 12599.4 | 10963.1 | 12324.2 | 10897.8 | 12122.8 | 12112.9 | 13590.2 | 12504.5 | 13606.3 | 12603.3 | 13356.9 | 12277.5 | 12416.2 | 12223 | 13370.6 | 13616.8 | 13591.9 | 13551.1 | 13515.6 | 13538 | 12762.3 | 13577.3 | 13603.8 | 13614.1 | 13555.6 | 13524.8 | 13599.3 | 12764.5 | 13694.5 | 12873.3 | 32.7732 | 32.6688 | 32.8349 | 0 | 32.8145 | 32.9869 | 0 | 47.5 | 0 | 0 | 47.1 | 0 | 3.7354 | 3.6463 | 3.5516 | 3.6747 | 3.6832 | 3.3923 | 9.165 | 9.456 | 10.006 | 9.511 | 8.797 | 8.756 | 7.9536 | 8.031 | 7.9009 | 7.4344 | 7.8277 | 7.1247 | 1.5617 | 1.9187 | 1.9065 | 0 | 1.9212 | 1.5549 | 8.0142 | 7.975 | 8.026 | 7.7644 | 7.9544 | 8.1882 | 1.627 | 1.9279 | 1.8985 | 0 | 1.926 | 1.9243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 304974 | 554 | 294371 | 579 | 11846.934 | 20.4 | 7.9536 | 8.031 | 7.9009 | 7.4344 | 7.8277 | 7.1247 | 8.0142 | 7.975 | 8.026 | 7.7644 | 7.9544 | 8.1882 | 1055000 | 1000 | 1034000 | 1000 | 2081533 | 4200 | 2087000 | 2077333 | 12.85 | 7.712 | 1.7726 | 7.987 | 1.8607 | 22.98% | 23.3% | 32.8156 | 47.3 | 3.6139 | 9.2818 | 2099866.2 | 2081467 | 2632060.0115 | 79.08%
2023-04-22 | 2024 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 335090.89 | 6:23 | 19:12 | 12950 | 13303.3 | 13322.5 | 13351 | 13333 | 13445.8 | 13284.5 | 13570 | 13327.6 | 13144.5 | 13228.9 | 13327.3 | 13447.3 | 13300.3 | 13367.6 | 13529.8 | 13322.5 | 13390 | 13428.8 | 13468.8 | 13426.3 | 13452.6 | 13241.2 | 13410.7 | 13289.6 | 12187.5 | 13373.3 | 13337.5 | 13483.2 | 13292.6 | 13325.6 | 13462.3 | 13432 | 13496.4 | 13554.5 | 13398.3 | 13528.7 | 13461.5 | 13388.5 | 13459.4 | 14080.7 | 13225.2 | 13958.1 | 13082.2 | 13515.3 | 14371 | 12935.5 | 14047.6 | 12850.7 | 13060.3 | 13604.4 | 13039.1 | 13841.4 | 12816.6 | 13819.8 | 12906.1 | 12801.7 | 13854.4 | 12860.3 | 13850.2 | 13800.7 | 12792.7 | 13430.4 | 12965.7 | 13262.6 | 12766.6 | 13323.8 | 13624.5 | 13751.7 | 12940.7 | 13749.3 | 12531.8 | 13366.9 | 13379.1 | 12833.8 | 13781.4 | 12583.3 | 13852.8 | 12771.9 | 13671 | 12962.9 | 13546.3 | 12964.5 | 13902 | 12975 | 13421.7 | 12881.1 | 11549 | 13509 | 13252.9 | 12718.3 | 13893.5 | 13619.2 | 12922.9 | 12799 | 13562.4 | 12592.4 | 13054.6 | 13797.2 | 12628.8 | 13849.3 | 12734.1 | 13689 | 12962.6 | 13706.7 | 12459.4 | 13788.8 | 12899.1 | 13665.7 | 12848.4 | 13692.8 | 13046.8 | 12651.2 | 13558.8 | 12744.7 | 12618.7 | 13634.7 | 13549.9 | 13567.3 | 12943.8 | 13696.1 | 12694.7 | 13420.4 | 12849.4 | 13345.8 | 12213.3 | 13559.2 | 12855.1 | 12642.1 | 12587.6 | 12697.2 | 11059.3 | 12502.7 | 11128.7 | 12446.4 | 12455.7 | 13981.9 | 12812.3 | 14008.6 | 12953.4 | 13746.5 | 12648.1 | 12775.7 | 12608.6 | 13716.5 | 13968 | 13990.1 | 13949.7 | 13929.2 | 13947.8 | 13121.1 | 13961 | 13942.1 | 13948.3 | 13851.3 | 13820.3 | 13942 | 13043.6 | 14056.8 | 13172.2 | 33.7028 | 33.4608 | 33.4172 | 0 | 33.7834 | 33.6031 | 0 | 48.1 | 0 | 0 | 48.1 | 0 | 2.6589 | 2.7376 | 2.6414 | 2.631 | 2.7423 | 2.5484 | 6.577 | 6.819 | 6.221 | 6.656 | 6.487 | 6.285 | 7.9976 | 8.0339 | 7.8639 | 7.5932 | 7.9132 | 7.3249 | 1.576 | 1.9519 | 1.9088 | 0 | 1.9775 | 1.6493 | 8.0579 | 7.9805 | 7.976 | 7.9226 | 8.0401 | 8.4221 | 1.6403 | 1.9644 | 1.9022 | 0 | 1.9801 | 2.0422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 306036 | 556 | 295420 | 581 | 13950.668 | 24.667 | 7.9976 | 8.0339 | 7.8639 | 7.5932 | 7.9132 | 7.3249 | 8.0579 | 7.9805 | 7.976 | 7.9226 | 8.0401 | 8.4221 | 1062000 | 2000 | 1049000 | 2000 | 2103734 | 4267 | 2107000 | 2099467 | 12.8167 | 7.7878 | 1.8127 | 8.0665 | 1.9059 | 23.28% | 23.63% | 33.5934 | 48.1 | 2.6599 | 6.5075 | 2122759.8 | 2103467 | 2630928.7179 | 79.95%
2023-04-23 | 2024 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 335090.89 | 6:18 | 19:10 | 13040.4 | 13366.5 | 13379.3 | 13399.9 | 13398.2 | 13492.3 | 13371 | 13635.4 | 13388 | 13211.6 | 13293.3 | 13391.5 | 13486.9 | 13357.2 | 13442.1 | 13565 | 13374.7 | 13427.8 | 13474.3 | 13547 | 13471.3 | 13502.5 | 13285.5 | 13448.4 | 13336.1 | 12358.3 | 13424.1 | 13376.7 | 13519.6 | 13353.4 | 13369.3 | 13499.6 | 13470.8 | 13526.3 | 13584.6 | 13439.1 | 13551.3 | 13493.6 | 13397.7 | 13477.7 | 14056.4 | 13287.7 | 13941.8 | 13146.2 | 13652.3 | 14483.7 | 13014.5 | 14024 | 12935.7 | 13132.7 | 13648.7 | 13123.1 | 13868.5 | 12906.6 | 13847.2 | 12992.5 | 12889 | 13890.7 | 12951.9 | 13879.3 | 13840.2 | 12882.5 | 13493.4 | 13051 | 13270 | 12843.7 | 13369.2 | 13638.2 | 13782.2 | 12993.9 | 13777.6 | 12660.8 | 13428.1 | 13441.8 | 12925.9 | 13816.3 | 12688.5 | 13883.5 | 12874.6 | 13723 | 12964.5 | 13552.5 | 13049.4 | 13890 | 13008.5 | 13467.3 | 12939.1 | 11802.9 | 13563.3 | 13317 | 12802.8 | 13912.5 | 13669.9 | 13056.6 | 12941.2 | 13654.1 | 12802.3 | 13167.6 | 13831.4 | 12776.9 | 13847.9 | 12840.3 | 13714.3 | 13057.2 | 13729.1 | 12588.6 | 13824 | 13016.6 | 13717.9 | 12964.2 | 13729.7 | 13171.8 | 12789.1 | 13609.2 | 12852 | 12735 | 13674.8 | 13598.3 | 13607.7 | 13030.6 | 13726.1 | 12796.8 | 13488.3 | 12971.2 | 13391.4 | 12381 | 13593.8 | 12945.3 | 12856.3 | 12837.6 | 12835.3 | 11421.4 | 12649.9 | 11411.3 | 12625.1 | 12629.5 | 13986.2 | 12894.9 | 14026.6 | 13044.7 | 13798 | 12784.9 | 12903.2 | 12770.9 | 13756.5 | 13988.2 | 13984.6 | 13944.2 | 13927.1 | 13954.2 | 13209.2 | 13980.9 | 13919.7 | 13920 | 13877.3 | 13846.9 | 13979 | 13136.3 | 14031.2 | 13218.4 | 32.253 | 32.2743 | 32.3064 | 0 | 32.4525 | 32.4089 | 0 | 44.7 | 0 | 0 | 44.8 | 0 | 3.9525 | 3.8361 | 3.8669 | 4.0662 | 4.0077 | 3.8595 | 7.754 | 9.094 | 7.953 | 8.476 | 9.004 | 8.12 | 7.9631 | 8.0062 | 7.8726 | 7.6052 | 7.9623 | 7.3475 | 1.5594 | 1.9617 | 1.9027 | 0 | 1.997 | 1.6504 | 7.7528 | 7.9679 | 7.9814 | 7.9364 | 8.08 | 8.4554 | 1.6246 | 1.9758 | 1.9004 | 0 | 1.9926 | 2.0458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307102 | 557 | 296476 | 582 | 16065.135 | 29 | 7.9631 | 8.0062 | 7.8726 | 7.6052 | 7.9623 | 7.3475 | 7.7528 | 7.9679 | 7.9814 | 7.9364 | 8.08 | 8.4554 | 1066000 | 1000 | 1056000 | 1000 | 2114467 | 4333 | 2120000 | 2110134 | 12.8667 | 7.7928 | 1.8142 | 8.029 | 1.9079 | 23.28% | 23.76% | 32.339 | 44.75 | 3.9315 | 8.4002 | 2133696.7 | 2114134 | 2649788.0769 | 79.79%
2023-04-24 | 2024 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 335090.89 | 6:10 | 19:12 | 12895.2 | 13237.2 | 13257.1 | 13289.9 | 13273.8 | 13367.5 | 13231.9 | 13503.7 | 13272.9 | 13070.1 | 13157.2 | 13264.3 | 13366.1 | 13228.6 | 13337.5 | 13461.1 | 13266.7 | 13318.3 | 13378.6 | 13418.1 | 13373.1 | 13405.3 | 13173.9 | 13346.8 | 13225.8 | 12099.1 | 13307.3 | 13261.9 | 13427.4 | 13266.4 | 13265.6 | 13406.5 | 13370.3 | 13438.6 | 13488.5 | 13347.8 | 13473.3 | 13408.3 | 13308 | 13383.5 | 14031.3 | 13218.1 | 13910.1 | 13064.1 | 13605.7 | 14467 | 12967.8 | 14017.7 | 12745.3 | 12966.7 | 13531.7 | 12964.8 | 13761.1 | 12700.3 | 13754.4 | 12801.4 | 12695.8 | 13790.4 | 12747.1 | 13782.4 | 13747 | 12694.3 | 13368.2 | 12887.8 | 13130.2 | 12643.1 | 13240.4 | 13523.8 | 13684.6 | 12792 | 13672.7 | 12433 | 13292.6 | 13314.8 | 12705.2 | 13733.9 | 12456.2 | 13796.1 | 12684.7 | 13607.7 | 12764.7 | 13452.6 | 12947.1 | 13849.8 | 12855.6 | 13415.1 | 12794.4 | 11612.7 | 13510.3 | 13223.2 | 12424.2 | 13830.4 | 13488.5 | 12777.2 | 12713.9 | 13634.1 | 12627.7 | 13070.4 | 13776.1 | 12594.7 | 13791.6 | 12661 | 13628.1 | 12905.1 | 13659.2 | 12369.8 | 13757.2 | 12870.3 | 13643.8 | 12814.4 | 13666.2 | 13015.2 | 12598.7 | 13487.2 | 12703.6 | 12513 | 13583.9 | 13481.4 | 13509.1 | 12836.4 | 13613.2 | 12544.1 | 13372.4 | 12778.7 | 13267.3 | 12055 | 13473.6 | 12727.7 | 12643.8 | 12674.9 | 12584.7 | 11137 | 12391.7 | 11086.7 | 12308.5 | 12310.7 | 13886.4 | 12674 | 13921.8 | 12847.4 | 13665.2 | 12529 | 12664.8 | 12502.3 | 13665.2 | 13910.2 | 13901.1 | 13858.1 | 13837.8 | 13857.8 | 13034.5 | 13876.9 | 13818.5 | 13831.6 | 13808 | 13761.7 | 13902.1 | 12980.8 | 13932.9 | 13054.3 | 32.4112 | 31.9335 | 32.0095 | 0 | 31.9799 | 31.9973 | 0 | 43.9 | 0 | 0 | 43.8 | 0 | 3.7031 | 3.6785 | 3.5791 | 3.8417 | 3.6587 | 3.6617 | 7.95 | 7.946 | 7.939 | 8.555 | 8.313 | 8.033 | 7.684 | 7.7462 | 7.6412 | 7.3807 | 7.6683 | 7.0321 | 1.5302 | 1.8708 | 1.8704 | 0 | 1.8982 | 1.5655 | 7.5087 | 7.6572 | 7.731 | 7.6992 | 7.7573 | 8.1185 | 1.5928 | 1.888 | 1.8658 | 0 | 1.9044 | 1.938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308159 | 559 | 297520 | 584 | 18158.401 | 33.267 | 7.684 | 7.7462 | 7.6412 | 7.3807 | 7.6683 | 7.0321 | 7.5087 | 7.6572 | 7.731 | 7.6992 | 7.7573 | 8.1185 | 1057000 | 2000 | 1044000 | 2000 | 2093266 | 4267 | 2097000 | 2088999 | 13.0333 | 7.5254 | 1.747 | 7.7453 | 1.8378 | 23.22% | 23.73% | 32.0663 | 43.85 | 3.6871 | 8.1227 | 2111855 | 2093133 | 2571840.7732 | 81.39%
2023-04-25 | 2024 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 335090.89 | 6:12 | 19:06 | 12620.6 | 12970.5 | 13004 | 13036.9 | 13029.5 | 13106.9 | 12966.7 | 13281.3 | 13013.1 | 12795.8 | 12893 | 12998.4 | 13091.8 | 12954.5 | 13047.7 | 13179 | 12983.1 | 13042.9 | 11964.7 | 5633.5 | 13053.6 | 13132.7 | 12877.2 | 13067 | 12941.3 | 11786.2 | 13020.5 | 12975.3 | 13152.3 | 12991.9 | 12977.6 | 13136.7 | 13094.6 | 13166.5 | 13210.6 | 13069 | 13204.1 | 13127.5 | 13020.2 | 13095.1 | 13760.9 | 12907.1 | 13635.7 | 12740.8 | 13025.7 | 14053.1 | 12661.3 | 13758.7 | 12451.5 | 12666 | 13245.5 | 12676.3 | 13479.6 | 12406.8 | 13479.6 | 12502.6 | 12405.9 | 13513 | 12446.7 | 13503.4 | 13464.1 | 12399.2 | 13105.3 | 12605 | 12848.7 | 12357.7 | 12945.5 | 13226.4 | 13421.3 | 12427.3 | 13389.6 | 12210.3 | 12903.8 | 13005.9 | 12156.1 | 13443.9 | 12094.8 | 13522 | 12389.5 | 13256.8 | 12473.5 | 13141.4 | 12637 | 13556.6 | 12561.3 | 13113.2 | 12495.2 | 11242 | 13268.2 | 12933.3 | 12076.4 | 13530 | 13096.9 | 12373.4 | 12386.9 | 13355.2 | 12344.7 | 12786.1 | 13503.2 | 12325.2 | 13530.1 | 12393.3 | 13340 | 12624.5 | 13388.1 | 12102.8 | 13478.9 | 12582 | 13356 | 12535.4 | 13389 | 12723.2 | 12321.2 | 13217.3 | 12411.6 | 12259.8 | 13267.3 | 13212.5 | 13239.9 | 12574.6 | 13344.6 | 12302 | 13103.5 | 12513.2 | 13003.3 | 11751.7 | 13194.3 | 12456.4 | 12355.7 | 12367.4 | 12297.9 | 10754.4 | 12099.5 | 10690.2 | 11983.3 | 11994.8 | 13533.1 | 12335.6 | 13588.5 | 12530.7 | 13343.9 | 12230.5 | 12345.9 | 12192 | 13310.9 | 13560.4 | 13535.2 | 13498.7 | 13483.8 | 13499.5 | 12687.8 | 13529.5 | 13446.4 | 13467.1 | 13448.3 | 13398.4 | 13552.3 | 12628.1 | 13559 | 12699.1 | 33.9941 | 33.4802 | 33.1816 | 0 | 33.3179 | 33.621 | 0 | 46.8 | 0 | 0 | 46.5 | 0 | 3.9124 | 3.7906 | 3.7411 | 3.7696 | 3.8138 | 3.6763 | 8.435 | 8.137 | 7.811 | 7.693 | 8.108 | 8.091 | 7.4725 | 7.5224 | 7.4357 | 7.1879 | 7.4573 | 6.8103 | 1.5221 | 1.7926 | 1.85 | 0 | 1.8314 | 1.5045 | 7.2956 | 7.4538 | 7.5885 | 7.5127 | 7.5433 | 7.883 | 1.5761 | 1.8067 | 1.8421 | 0 | 1.8296 | 1.8689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 309184 | 560 | 298539 | 585 | 20194.735 | 37.467 | 7.4725 | 7.5224 | 7.4357 | 7.1879 | 7.4573 | 6.8103 | 7.2956 | 7.4538 | 7.5885 | 7.5127 | 7.5433 | 7.883 | 1025000 | 1000 | 1019000 | 1000 | 2036334 | 4200 | 2042000 | 2032134 | 12.9 | 7.3143 | 1.7001 | 7.5462 | 1.7847 | 23.24% | 23.65% | 33.519 | 46.65 | 3.784 | 8.0458 | 2054971.3 | 2036134 | 2488891.9696 | 81.81%
2023-04-26 | 2024 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 335090.89 | 6:11 | 19:07 | 10129.5 | 10563.9 | 10609.6 | 10598.5 | 10649.8 | 10756.5 | 10658 | 10913.7 | 10522.1 | 10297.3 | 10497.7 | 10529.1 | 10771.8 | 10561.3 | 10757.9 | 10866.5 | 10689.7 | 10706.9 | 8053.8 | 4537.4 | 10719.8 | 10783.8 | 10463.7 | 10660.2 | 10579.5 | 9617.9 | 10673.1 | 10625.4 | 10688.1 | 10491.8 | 10478.1 | 10648.6 | 10540.8 | 10633.1 | 10729.8 | 10621.2 | 10694.8 | 10600.9 | 10520.7 | 10546.2 | 11068.1 | 10447.5 | 10976.5 | 10337 | 10164.6 | 11162 | 10198.9 | 11031.3 | 10135.5 | 10272.1 | 10770.5 | 10280.8 | 11012.6 | 10229.9 | 10861.8 | 10166.6 | 9952.3 | 10761.9 | 10050.2 | 10766.9 | 10725.8 | 9987 | 10401.5 | 10022 | 10226 | 9739.2 | 10239.6 | 10309.6 | 10621.6 | 9682.3 | 10490.1 | 9486.5 | 10252 | 10138.1 | 9636.2 | 10491.7 | 9490.7 | 10674.8 | 9808.2 | 10428.7 | 9639.2 | 10148.4 | 9749.6 | 10485.5 | 9692.7 | 10111.1 | 9764.7 | 8720.4 | 10279.9 | 10105.7 | 9393.2 | 10544.9 | 10313.3 | 9822.7 | 9883.6 | 10414.8 | 9637.7 | 10025 | 10632.6 | 9751.7 | 10696 | 9833 | 10576.4 | 10078.5 | 10685.6 | 9610.5 | 10822 | 10097.7 | 10769 | 10122.2 | 10819.2 | 10288.9 | 9823.5 | 10606.3 | 9965.9 | 9836.5 | 10709.7 | 10613 | 10646 | 10143.2 | 10747.4 | 9922.4 | 10543.4 | 10089.8 | 10514.3 | 9482.1 | 10647.9 | 10062.1 | 10028.3 | 10050.4 | 9953.8 | 8701.9 | 9859.3 | 8643.4 | 9728.6 | 9731.1 | 10685.6 | 9792.4 | 10761.1 | 10002.5 | 10721.4 | 9880.7 | 9950.1 | 9817.9 | 10496.9 | 10665 | 10648.5 | 10624.4 | 10615.2 | 10640.6 | 10033.8 | 10648.6 | 10595.4 | 10580.5 | 10534.9 | 10508.2 | 10631.5 | 9964 | 10681.3 | 10008.8 | 34.3171 | 34.1821 | 33.8598 | 0 | 34.0858 | 34.4096 | 0 | 45.4 | 0 | 0 | 44.9 | 0 | 5.6516 | 5.4148 | 5.4537 | 5.4555 | 5.6959 | 5.3439 | 17.236 | 17.193 | 17.496 | 17.561 | 16.548 | 14.892 | 6.0137 | 6.0957 | 5.9045 | 5.6441 | 5.8909 | 5.2555 | 1.2937 | 1.4049 | 1.5276 | 0 | 1.4158 | 1.1442 | 5.8658 | 5.9519 | 6.0106 | 5.8683 | 5.8994 | 6.1427 | 1.3357 | 1.4168 | 1.5229 | 0 | 1.4272 | 1.4229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310008 | 562 | 299348 | 587 | 21823.135 | 41.667 | 6.0137 | 6.0957 | 5.9045 | 5.6441 | 5.8909 | 5.2555 | 5.8658 | 5.9519 | 6.0106 | 5.8683 | 5.8994 | 6.1427 | 824000 | 2000 | 809000 | 2000 | 1628400 | 4200 | 1629000 | 1624200 | 12.9333 | 5.8007 | 1.3573 | 5.9565 | 1.4251 | 23.4% | 23.93% | 34.1709 | 45.15 | 5.5026 | 16.821 | 1642542.4 | 1628266 | 1978053.7904 | 82.32%
2023-04-27 | 2024 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 335090.89 | 6:09 | 19:14 | 8906.2 | 9193.6 | 9193.8 | 9223.6 | 9221.6 | 9225.3 | 9193.3 | 9453.5 | 9234.6 | 9198.6 | 9090.4 | 9175.4 | 9197.2 | 9160.4 | 9159.1 | 9237.7 | 9081.2 | 9125.1 | 9041.9 | 8143.3 | 9257.1 | 9255.5 | 9193 | 9299.2 | 9290.5 | 8186.9 | 9120.2 | 9182.2 | 9498.8 | 9418.3 | 9384.5 | 9497.5 | 9415.5 | 9511.6 | 9515.2 | 9427 | 9578.8 | 9505.7 | 9388.8 | 9433.3 | 9893.4 | 9162.1 | 9876.3 | 9047.4 | 8948.4 | 10130.6 | 8996.7 | 9934.7 | 8616.7 | 8810.7 | 9322.5 | 8868 | 9526.9 | 8600.1 | 9620.4 | 8740.9 | 8593.5 | 9586 | 8607.7 | 9487.1 | 9465.9 | 8576.1 | 9249.6 | 8857.8 | 9232.4 | 8737.5 | 9203.7 | 9548.8 | 9523.5 | 8913.4 | 9548.5 | 8550.6 | 9072.6 | 9207.3 | 8412.9 | 9594.2 | 8329.6 | 9520.2 | 8547.1 | 9385.1 | 8802.7 | 9430.9 | 9001.1 | 9824.3 | 8914.8 | 9532.6 | 8936.1 | 7953.5 | 9687 | 9382.2 | 8493.3 | 9870.9 | 9459.8 | 8749.4 | 8783.2 | 9764.2 | 8861.2 | 9168.2 | 9837.5 | 8714.8 | 9838.8 | 8753.2 | 9686.8 | 8963.6 | 9602.5 | 8333.3 | 9734.3 | 8775 | 9645.8 | 8882 | 9663.5 | 9066.4 | 8752.2 | 9531.7 | 8732.5 | 8567.6 | 9642.1 | 9528.3 | 9557.8 | 8893.8 | 9682.9 | 8707.8 | 9445.4 | 8922.6 | 9424.7 | 8319.9 | 9570.9 | 8861.6 | 8703.9 | 8762.3 | 8767.3 | 7614.5 | 8691.5 | 7674.7 | 8753.6 | 8727.1 | 9743.7 | 8653.3 | 9829.6 | 8875.1 | 9746.7 | 8790.9 | 8956.2 | 8852.3 | 9507.8 | 9693.8 | 9729.8 | 9666.1 | 9649.1 | 9689 | 8959.3 | 9705.3 | 9667.4 | 9777 | 9918.8 | 9835 | 9831.1 | 8934.9 | 9818.3 | 8963.2 | 31.9997 | 31.9507 | 31.9954 | 0 | 31.9743 | 32.1445 | 0 | 43 | 0 | 0 | 42.9 | 0 | 3.4322 | 3.5374 | 3.181 | 3.5322 | 3.4917 | 3.4506 | 13.569 | 11.808 | 9.874 | 13.287 | 9.747 | 9.902 | 5.0128 | 5.2751 | 5.1413 | 4.995 | 5.1509 | 4.5639 | 1.0555 | 1.1781 | 1.315 | 0 | 1.1937 | 0.95801 | 4.9937 | 5.1326 | 5.2281 | 5.1906 | 5.1179 | 5.3351 | 1.099 | 1.1901 | 1.3146 | 0 | 1.2147 | 1.1852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310739 | 563 | 300079 | 588 | 23280.402 | 46 | 5.0128 | 5.2751 | 5.1413 | 4.995 | 5.1509 | 4.5639 | 4.9937 | 5.1326 | 5.2281 | 5.1906 | 5.1179 | 5.3351 | 731000 | 1000 | 731000 | 1000 | 1457267 | 4333 | 1460000 | 1452934 | 13.0833 | 5.0232 | 1.1401 | 5.1663 | 1.2007 | 22.7% | 23.24% | 32.0129 | 42.95 | 3.4375 | 11.3645 | 1469405.6 | 1457200 | 1731475.8408 | 84.16%
2023-04-28 | 2024 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 335090.89 | 6:07 | 19:01 | 7669.1 | 8033.9 | 8037.7 | 8022.4 | 8099.1 | 8122.9 | 8065.3 | 8373.5 | 8047.6 | 7966 | 7960.1 | 8041.5 | 8092.2 | 8022 | 8087.8 | 8130.9 | 8017.8 | 8031.5 | 8026.1 | 8049.2 | 8091.2 | 8103.4 | 7849.3 | 8024.6 | 7955.1 | 7135.5 | 8042.8 | 7977.8 | 8148.2 | 8037.3 | 7936.8 | 8087 | 8042.5 | 8069.6 | 8132.4 | 8024.1 | 8142.6 | 8074.8 | 7992.6 | 8019.8 | 8518.8 | 7760.7 | 8403.8 | 7635.7 | 7577 | 8675.9 | 7590.1 | 8500.3 | 7528 | 7674.6 | 8194.4 | 7709.2 | 8437 | 7626.6 | 8345.8 | 7601.1 | 7439.6 | 8331.8 | 7469.6 | 8273.6 | 8233.5 | 7416.9 | 8061.5 | 7679.4 | 7800.1 | 7265.7 | 7770.1 | 7915.7 | 8217.9 | 7406.8 | 8098 | 7105.1 | 7739.6 | 7717.6 | 7199.1 | 8106.9 | 7061.8 | 8199.5 | 7306.2 | 8002.5 | 7974.2 | 8541.3 | 8110.3 | 8974.6 | 8066.4 | 8570.7 | 8078.2 | 7167.4 | 8795.3 | 8420.5 | 7881 | 9132.7 | 8960.6 | 8353.5 | 8265.8 | 8975.3 | 7992.8 | 8202.6 | 8973 | 7846 | 8956.6 | 7863.7 | 8737 | 8058.4 | 8613.7 | 7465.4 | 8812.1 | 7753.8 | 8748.6 | 7959.3 | 8706 | 8037.9 | 7883 | 8658.4 | 7934.9 | 7738.1 | 8721.5 | 8576.1 | 8651.4 | 7877.4 | 8671.1 | 7709.8 | 8490.5 | 7938.1 | 8390.6 | 7346.2 | 8483.5 | 7786 | 7678 | 7717.2 | 7632.5 | 6783.8 | 7723.5 | 6555 | 7571.5 | 7505.4 | 8688.2 | 7527.3 | 8729.4 | 7714 | 8588.3 | 7619.7 | 7737.5 | 7679.9 | 8442.2 | 8690.9 | 8649.8 | 8630.7 | 8610.1 | 8629.4 | 7833.6 | 8659.4 | 8730.9 | 8763.4 | 8832.8 | 8760.9 | 8753.6 | 7877.2 | 8755.2 | 7911.1 | 28.5777 | 28.7458 | 28.4512 | 0 | 28.4988 | 28.8838 | 0 | 39.5 | 0 | 0 | 38.3 | 0 | 3.746 | 3.7395 | 3.6434 | 3.7237 | 3.6317 | 3.491 | 13.14 | 13.396 | 13.227 | 12.658 | 12.912 | 10.854 | 4.8413 | 5.0105 | 4.843 | 4.6975 | 4.6157 | 3.991 | 0.96265 | 0.95094 | 1.1546 | 0 | 0.9344 | 0.72012 | 4.8612 | 4.7909 | 4.9824 | 4.8748 | 4.5106 | 4.6701 | 1.0078 | 0.96047 | 1.1481 | 0 | 0.95897 | 0.89075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 311370 | 565 | 300733 | 590 | 24561.802 | 50.333 | 4.8413 | 5.0105 | 4.843 | 4.6975 | 4.6157 | 3.991 | 4.8612 | 4.7909 | 4.9824 | 4.8748 | 4.5106 | 4.6701 | 631000 | 2000 | 654000 | 2000 | 1281400 | 4333 | 1281000 | 1277067 | 12.9 | 4.6665 | 0.94455 | 4.7817 | 0.99322 | 20.24% | 20.77% | 28.6314 | 38.9 | 3.6626 | 12.6978 | 1292215.2 | 1281334 | 1619950.682 | 79.1%
2023-04-29 | 2024 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 335090.89 | 6:08 | 19:15 | 12627 | 13016.6 | 13090.9 | 13090.5 | 13173.6 | 13163.5 | 13089.9 | 13357.1 | 12996.9 | 13016.5 | 12855.7 | 12988 | 13001.9 | 12893 | 13048.7 | 13108.1 | 12896.1 | 12880.8 | 12864.6 | 12899.5 | 12870.6 | 12914.8 | 12603 | 12791.1 | 12709.6 | 11716.5 | 12806 | 12740.8 | 12893.1 | 12750.6 | 12678.8 | 12842.5 | 12842.7 | 12490.4 | 12968.3 | 12858.4 | 12942.6 | 12851 | 12754.4 | 12823.1 | 13360 | 12552.5 | 13192.6 | 12377.2 | 12653.4 | 13733.3 | 12383 | 13365.4 | 12370 | 12574.1 | 13054.7 | 12563.5 | 13246.7 | 12432 | 13259.1 | 12395.7 | 12318.1 | 13274.6 | 12320.5 | 13296.6 | 13256.3 | 12296.7 | 13122.6 | 12733.3 | 12692.2 | 12183.3 | 12756.5 | 12932.7 | 13196.4 | 12357.1 | 13141.8 | 12063.1 | 12816.7 | 12786.2 | 12208.3 | 13173.5 | 12095 | 13296.1 | 12373 | 13201.1 | 12191.4 | 12759.3 | 12337.4 | 13155.4 | 12261.5 | 12737.8 | 12266.1 | 11080.2 | 12925.8 | 12555.3 | 12081.3 | 13244.7 | 13051.3 | 12458.1 | 12339.3 | 13034.2 | 12143.6 | 12373.3 | 13023 | 11997.3 | 13078.5 | 12023.7 | 12895.9 | 12251.6 | 12717.4 | 11576.7 | 12917.2 | 11921.8 | 12877.5 | 12140.6 | 12843.8 | 12291 | 12057.1 | 12797.2 | 12138.8 | 11940.8 | 12844 | 12740.5 | 12804.1 | 12094.2 | 12835.7 | 11952.6 | 12650.3 | 12159.8 | 12578.6 | 11421.2 | 12684.1 | 12104.9 | 12034.8 | 12075.6 | 11974.2 | 10666.4 | 12049 | 10564.9 | 11923.1 | 11821.9 | 12977.1 | 11935.2 | 13077.1 | 12101.2 | 12900 | 12033 | 12107.4 | 12080.9 | 12863.8 | 13087.6 | 13134.6 | 13072.7 | 13070.3 | 13032.7 | 12314.1 | 13061.5 | 13136.4 | 13114 | 13123.7 | 13086.2 | 13108.2 | 12317.7 | 13174.2 | 12380.4 | 27.2237 | 27.1408 | 27.1553 | 0 | 27.0189 | 25.2319 | 0 | 43.5 | 0 | 0 | 43.2 | 0 | 3.406 | 3.2521 | 3.1321 | 3.4442 | 3.2484 | 2.8772 | 7.211 | 7.289 | 6.808 | 7.322 | 7.107 | 7.786 | 7.5079 | 7.5516 | 7.3731 | 7.304 | 7.3573 | 6.3988 | 1.2808 | 1.4119 | 1.4573 | 0 | 1.457 | 1.1038 | 7.5638 | 7.3906 | 7.5017 | 7.5662 | 7.342 | 7.4564 | 1.3428 | 1.4264 | 1.4571 | 0 | 1.4678 | 1.3652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312391 | 566 | 301724 | 592 | 26566.669 | 53.8 | 7.5079 | 7.5516 | 7.3731 | 7.304 | 7.3573 | 6.3988 | 7.5638 | 7.3906 | 7.5017 | 7.5662 | 7.342 | 7.4564 | 1021000 | 1000 | 991000 | 2000 | 2004867 | 3467 | 2009000 | 2001400 | 13.1167 | 7.2488 | 1.3421 | 7.4701 | 1.4118 | 18.52% | 18.9% | 26.7541 | 43.35 | 3.2266 | 7.2538 | 2023067.9 | 2004867 | 2539804.3418 | 78.94%
2023-04-30 | 2024 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 335090.89 | 6:07 | 19:15 | 10397.3 | 11066.4 | 11310.6 | 11255.9 | 11379.3 | 11429.3 | 11405.8 | 11818.3 | 11377.1 | 11208.9 | 11296.5 | 11435 | 11418.3 | 11375.7 | 11379 | 11481.4 | 11228.1 | 11229.7 | 10406.5 | 2671.3 | 11278.3 | 11324.8 | 11068 | 11230.9 | 11177.6 | 10051.7 | 11285.7 | 11180.3 | 11431.2 | 11353.1 | 11273.7 | 11415.5 | 11483.1 | 11501.2 | 11498.8 | 11387 | 11524.6 | 11440.5 | 11347.2 | 11429.6 | 12099.4 | 11156.1 | 12039.4 | 11048 | 11506 | 12706.2 | 10815.8 | 12021.4 | 10699.4 | 10988.6 | 11638.5 | 11067.5 | 11866.1 | 10714.2 | 11856.2 | 10717.7 | 10591.9 | 11809 | 10590.1 | 11835.5 | 11648.6 | 10542.6 | 11547 | 10938.3 | 11152.5 | 10636.9 | 11267.6 | 11630.2 | 11819.2 | 10812.5 | 11693.8 | 10401.1 | 11365.4 | 11200.1 | 10665.1 | 11439 | 10309.2 | 11793.7 | 10548.6 | 11580.9 | 10721.2 | 11355.6 | 10977.6 | 11980.2 | 10919.4 | 11545.6 | 10889.9 | 9745.4 | 11745 | 11310.9 | 10598.9 | 12082.4 | 11740.3 | 10962.8 | 10841.9 | 11848 | 10754.2 | 11143 | 11959.1 | 10695.4 | 11973.2 | 10651.8 | 11660.5 | 10922.4 | 11572 | 10212.5 | 11831 | 10610.2 | 11728.8 | 10832.8 | 11746.5 | 11019.7 | 10825.8 | 11784.3 | 10888.8 | 10642.3 | 11802.7 | 11693.3 | 11745.5 | 10829.7 | 11765.1 | 10631.6 | 11517.7 | 10847 | 11419.9 | 9983.8 | 11494.4 | 10724.6 | 10862.5 | 10921.2 | 10747.3 | 9464.4 | 10903.6 | 9676.3 | 10674.6 | 10539 | 11952.9 | 10696.7 | 11972.5 | 10810 | 11954.9 | 10744.1 | 10895.5 | 10811.4 | 11633.5 | 11939.6 | 11960.1 | 11915.3 | 11936.3 | 11889.8 | 10927.2 | 11900.9 | 12092.5 | 12055.7 | 12062.8 | 11995.7 | 12003.5 | 10891.9 | 12078.4 | 10994.3 | 27.3779 | 27.0902 | 20.4914 | 0 | 27.0217 | 27.4004 | 0 | 39.8 | 0 | 0 | 40.3 | 0 | 4.1684 | 4.0178 | 3.0498 | 4.1993 | 3.95 | 3.791 | 9.62 | 7.693 | 8.816 | 8.202 | 9.001 | 7.921 | 6.3179 | 6.4256 | 4.3459 | 6.2391 | 6.4852 | 5.7276 | 1.1383 | 1.3058 | 0.93285 | 0 | 1.3457 | 1.144 | 6.362 | 6.1907 | 4.3848 | 6.4177 | 6.3983 | 6.7155 | 1.1999 | 1.3182 | 0.94097 | 0 | 1.3768 | 1.417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313280 | 567 | 302619 | 593 | 28343.202 | 57.8 | 6.3179 | 6.4256 | 4.3459 | 6.2391 | 6.4852 | 5.7276 | 6.362 | 6.1907 | 4.3848 | 6.4177 | 6.3983 | 6.7155 | 889000 | 1000 | 895000 | 1000 | 1776533 | 4000 | 1782000 | 1772533 | 13.1333 | 5.9235 | 1.1733 | 6.0782 | 1.2506 | 19.81% | 20.57% | 25.8763 | 40.05 | 3.8627 | 8.5422 | 1792091.6 | 1776533 | 2189571.5456 | 81.14%
2023-05-01 | 2024 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 335090.89 | 6:05 | 19:16 | 10446.1 | 10943.5 | 10931 | 10946.1 | 11014.3 | 10962.7 | 10953.5 | 11158 | 10934.6 | 10729 | 10789.2 | 10903.9 | 10941.2 | 10822.2 | 10932.4 | 10954.2 | 10879.3 | 10863.8 | 10883.1 | 81.7 | 10980.6 | 11020.8 | 10807.8 | 10949.5 | 10930.2 | 9963.8 | 10974.1 | 10922.4 | 11068.1 | 10931.7 | 10827.6 | 11008.6 | 11082.3 | 11137.4 | 11242 | 11084.4 | 11121.3 | 11014.4 | 10902.9 | 10969.1 | 11286 | 10588.8 | 11133.4 | 10478 | 10762.7 | 11611.6 | 10316.8 | 11242.4 | 10378.6 | 10611.6 | 11120.6 | 10743.7 | 11332.1 | 10418.4 | 11383.4 | 10530.8 | 10340.5 | 11234.8 | 10246.3 | 11264.1 | 11081.8 | 10184.3 | 11000.2 | 10610.4 | 10806.6 | 10326.2 | 10847.7 | 11102.2 | 11177.3 | 10530.7 | 11075.1 | 10110.1 | 10826.2 | 10774.9 | 10258.5 | 11007.5 | 10116.2 | 11241 | 10306.8 | 11072.4 | 10373.3 | 10915.1 | 10493.6 | 11252.6 | 10419.9 | 10917.4 | 10499.1 | 9467.3 | 11266.5 | 10942.3 | 10372.8 | 11483.8 | 11300.3 | 10781.3 | 10658.9 | 11355.7 | 10583.9 | 10812 | 11455.9 | 10464.2 | 11566.3 | 10564.5 | 11489.4 | 10838.4 | 11387.3 | 10418.5 | 11550.3 | 10834.4 | 11417.1 | 10694.3 | 11376.6 | 10881.7 | 10511.9 | 11294.7 | 10611.6 | 10500.5 | 11430.1 | 11208.2 | 11380.3 | 10553.8 | 11324 | 10479.2 | 11295.4 | 10799 | 11228.8 | 10013.4 | 11220.9 | 10601 | 10468 | 10475.8 | 10588.9 | 9230.5 | 10416 | 9362.1 | 10553.3 | 10533 | 11352.1 | 10480.6 | 11478.3 | 10663 | 11512.2 | 10642 | 10773.3 | 10782.4 | 11188.5 | 11329 | 11508.2 | 11444.2 | 11437 | 11370.8 | 10714.1 | 11404.6 | 11702 | 11643.1 | 11536.7 | 11490.9 | 11521 | 10685.1 | 11643.8 | 10855.4 | 27.2081 | 26.9064 | 26.6764 | 0 | 26.935 | 27.1931 | 0 | 40.5 | 0 | 0 | 40.8 | 0 | 2.9071 | 2.932 | 2.6752 | 2.8633 | 2.9123 | 2.6425 | 10.388 | 9.32 | 8.682 | 9.241 | 9.301 | 10.114 | 6.2091 | 6.4495 | 6.1217 | 6.1834 | 6.5063 | 5.8144 | 1.1763 | 1.1784 | 1.3853 | 0 | 1.2096 | 0.98332 | 6.26 | 6.212 | 6.2712 | 6.425 | 6.4473 | 6.8211 | 1.2306 | 1.192 | 1.3751 | 0 | 1.2382 | 1.2192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 314133 | 568 | 303488 | 595 | 30058.669 | 62.067 | 6.2091 | 6.4495 | 6.1217 | 6.1834 | 6.5063 | 5.8144 | 6.26 | 6.212 | 6.2712 | 6.425 | 6.4473 | 6.8211 | 853000 | 1000 | 869000 | 2000 | 1715467 | 4267 | 1719000 | 1711200 | 13.1833 | 6.2141 | 1.1866 | 6.4061 | 1.251 | 19.1% | 19.53% | 26.9838 | 40.65 | 2.8221 | 9.5077 | 1731562.9 | 1715400 | 2170770.4588 | 79.02%
2023-05-02 | 2024 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 335090.89 | 6:02 | 19:07 | 11572.9 | 11961.8 | 11867.9 | 11801.5 | 11923.2 | 12019.3 | 12038.1 | 12433.7 | 12049.8 | 11860.4 | 12068.3 | 12131.1 | 12464.6 | 12265 | 12340.8 | 12433.7 | 12272 | 12398.1 | 12552.2 | 12149.9 | 12620 | 12626.5 | 12346.1 | 12540.8 | 12434.4 | 11338.6 | 12483.6 | 12363.9 | 12599.5 | 12476.7 | 12495.6 | 12586 | 12692 | 12656.8 | 12690.6 | 12644.7 | 12751.2 | 12686.5 | 12655.9 | 12687 | 12474.3 | 11705.6 | 12665.1 | 11749.1 | 12394 | 13456.1 | 11700.6 | 12538.8 | 11783.7 | 11996.4 | 12660.2 | 12099.1 | 12922.4 | 11972.6 | 12726.4 | 11854 | 11422.6 | 12496.3 | 11492.5 | 12502.7 | 12274.7 | 11412.7 | 12044 | 11472.4 | 11872.3 | 11421.1 | 11879.3 | 12249.9 | 12291.4 | 11447.5 | 12115.1 | 10972.3 | 11872.1 | 11641.4 | 11151.2 | 11860.9 | 10774.1 | 12101.2 | 11035 | 11831.8 | 11321.3 | 11771.3 | 11615.4 | 12517.4 | 11664.1 | 12211.8 | 11684.3 | 10511.1 | 12429.2 | 12117.6 | 11562.6 | 12846.9 | 12683.2 | 12094 | 11951.8 | 12616.8 | 11755.1 | 12015.7 | 12827.3 | 11728.2 | 13077.8 | 11850.5 | 12828 | 12161.2 | 12891.8 | 11682.8 | 13065.8 | 12181.9 | 12977.1 | 12149.1 | 13046.6 | 12301.9 | 11785.1 | 12774.7 | 12104 | 11863.3 | 12853.4 | 12749.9 | 12843.1 | 12075.9 | 12883.3 | 11794.3 | 12686.9 | 12082.2 | 12575.6 | 11323.4 | 12770 | 11999.3 | 11745.5 | 11740 | 11926.6 | 10309.3 | 11472.7 | 10271.9 | 11310.8 | 11247.8 | 12459.4 | 11364.7 | 12601.8 | 11572 | 12589.1 | 11519.2 | 11641.3 | 11573.8 | 12460.3 | 12584.7 | 12722.6 | 12551 | 12484.9 | 12440.5 | 11605.1 | 12495.7 | 12695.7 | 12795.6 | 12997.4 | 12912.2 | 12882.6 | 11829.2 | 12846.6 | 11832.6 | 31.0929 | 30.5579 | 30.1401 | 0 | 30.6455 | 30.6815 | 0 | 46.8 | 0 | 0 | 47.3 | 0 | 1.9867 | 1.9346 | 1.9646 | 1.8727 | 1.781 | 1.8038 | 6.625 | 6.084 | 6.148 | 5.719 | 5.797 | 5.371 | 7.0293 | 7.4397 | 6.9557 | 6.8482 | 7.3182 | 6.2784 | 1.222 | 1.4909 | 1.4822 | 0 | 1.4629 | 1.1273 | 7.1008 | 7.2765 | 7.0379 | 7.095 | 7.3545 | 7.302 | 1.2837 | 1.5043 | 1.4681 | 0 | 1.4958 | 1.3928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315099 | 569 | 304455 | 596 | 31985.402 | 66.267 | 7.0293 | 7.4397 | 6.9557 | 6.8482 | 7.3182 | 6.2784 | 7.1008 | 7.2765 | 7.0379 | 7.095 | 7.3545 | 7.302 | 966000 | 1000 | 967000 | 1000 | 1926733 | 4200 | 1931000 | 1922533 | 13.0833 | 6.9783 | 1.3571 | 7.1945 | 1.4289 | 19.45% | 19.86% | 30.6236 | 47.05 | 1.8906 | 5.9573 | 1944100.2 | 1926467 | 2410201.9167 | 79.93%
2023-05-03 | 2024 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 335090.89 | 6:02 | 19:07 | 12356.2 | 12882.8 | 13043.2 | 13043.3 | 13106.6 | 13131.9 | 13040.3 | 13337.4 | 12746.7 | 12714.9 | 12690.8 | 12728.8 | 13081.4 | 12869.4 | 13271.2 | 13283.6 | 13155.3 | 13230 | 13156.8 | 13163.6 | 13280.6 | 13256.7 | 13006.7 | 13161.2 | 13044.5 | 11701.6 | 13138.8 | 12973.6 | 13259.3 | 13102.8 | 12961.3 | 13157.9 | 13136.7 | 13148.7 | 13297 | 13136.1 | 13208.3 | 13103 | 13000.6 | 13067.3 | 13804.7 | 12912.1 | 13690.2 | 12684.2 | 13248.1 | 14274.5 | 12674.4 | 13787.3 | 12307.3 | 12488.5 | 13254.3 | 12723.8 | 13613.1 | 12388.4 | 13477.7 | 12432.9 | 12132.1 | 13383.9 | 11967.7 | 13351.6 | 13125.1 | 11966.6 | 13072.2 | 12603.6 | 12788.1 | 12256.1 | 12867.3 | 13230.4 | 13315.4 | 12451.4 | 13218 | 11968.9 | 12926.4 | 12838.2 | 11071.3 | 0 | 12100 | 13436.1 | 12284 | 13269.3 | 12421.1 | 13073.2 | 12576.5 | 13533.5 | 12542.7 | 13144.3 | 12487.7 | 11097.4 | 13375.9 | 12914.1 | 12232 | 13675.6 | 13380.2 | 12644.4 | 12496.9 | 13388.3 | 12276.6 | 12595.9 | 13315.2 | 12065.6 | 13347.9 | 12064.6 | 13091.9 | 12311.9 | 12979.1 | 11662.6 | 13113.3 | 12160.5 | 12959.8 | 12093.2 | 13000.2 | 12287.7 | 12063 | 12859.9 | 12042.6 | 11848.5 | 12938.9 | 12769.8 | 12812.4 | 12074.5 | 12900.4 | 11779.4 | 12695.6 | 12081.3 | 12600.8 | 11227.5 | 12762.9 | 12002.3 | 11985.1 | 12081.4 | 12089.7 | 10398.4 | 11960.2 | 10567.4 | 11871 | 11901.8 | 12932.4 | 11850.4 | 12994.6 | 12010.3 | 13032.9 | 12034.2 | 12162.6 | 12083.3 | 12727.3 | 13008.7 | 12953.1 | 12918.5 | 12923.5 | 12891.2 | 12073.3 | 12946.3 | 12976.3 | 12921.9 | 13010 | 12979.4 | 12997.2 | 12055.5 | 13073 | 12061.3 | 29.5789 | 30.8098 | 30.6202 | 0 | 30.7378 | 30.7339 | 0 | 46.1394 | 0 | 0 | 45.5 | 0 | 2.3624 | 2.2339 | 2.1498 | 2.2458 | 2.1495 | 2.092 | 6.263 | 5.622 | 5.718 | 6.438 | 5.316 | 5.173 | 7.3604 | 7.6733 | 7.5477 | 7.3161 | 7.2782 | 6.2251 | 1.2695 | 1.5535 | 1.6756 | 0 | 1.3963 | 1.1682 | 7.413 | 7.5011 | 7.6032 | 7.5375 | 7.2071 | 7.5878 | 1.3375 | 1.5671 | 1.6789 | 0 | 1.4333 | 1.4427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316116 | 571 | 305450 | 598 | 33990.669 | 70.467 | 7.3604 | 7.6733 | 7.5477 | 7.3161 | 7.2782 | 6.2251 | 7.413 | 7.5011 | 7.6032 | 7.5375 | 7.2071 | 7.5878 | 1017000 | 2000 | 995000 | 2000 | 2005267 | 4200 | 2008000 | 2001067 | 13.0833 | 7.2335 | 1.4126 | 7.475 | 1.4919 | 19.53% | 19.96% | 30.4961 | 45.8197 | 2.2056 | 5.755 | 2022803.9 | 2005134 | 2482625.2685 | 80.77%
2023-05-04 | 2024 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 335090.89 | 6:03 | 19:14 | 11012.6 | 11259.6 | 11104.4 | 11226.6 | 11109.1 | 11080.6 | 11109.4 | 11397.1 | 11385.9 | 11381.2 | 11114 | 11299.7 | 11214.8 | 11196.9 | 11228.5 | 11268.7 | 11279.1 | 11527.5 | 11488.3 | 11432.2 | 11659.2 | 11629.1 | 11483.1 | 11576.7 | 11546.1 | 10453.9 | 11518.7 | 11441.3 | 11684.8 | 11605.2 | 11547.6 | 11650.4 | 11700.7 | 11692.7 | 11783.8 | 11659.3 | 11759.5 | 11653.8 | 11590.9 | 11640.6 | 12261.4 | 11538.5 | 12216.6 | 11381.6 | 11937.3 | 12669.7 | 11261.7 | 12179.3 | 10798.2 | 11005 | 11537.8 | 11177.9 | 11836.6 | 10769.7 | 11877.3 | 11017 | 10870.3 | 11916.2 | 10648.9 | 11855.4 | 11744.3 | 10693.9 | 11686.8 | 11268.9 | 11536.6 | 11216.5 | 11590.8 | 12064.4 | 11968.1 | 11329.5 | 11979.4 | 10955.5 | 11530 | 11670.1 | 11057.4 | 12036.5 | 10977.9 | 12048.3 | 11048 | 11914 | 11502.6 | 11948.8 | 11599.5 | 12378.4 | 11496 | 11999.4 | 11458.3 | 10285.5 | 12266.3 | 11831.9 | 11212.4 | 12439.3 | 12117.3 | 11471 | 11334.4 | 12228.8 | 11379.6 | 11727.3 | 12362.1 | 11327.6 | 12296 | 11312 | 12208.2 | 11592.5 | 12233 | 11107.8 | 12407.4 | 11670.2 | 12319.8 | 11611.4 | 12416.7 | 11841.8 | 11415.9 | 12368.2 | 11520.8 | 11443.9 | 12495.2 | 12483 | 12437.2 | 11858.3 | 12611.8 | 11600.4 | 12310.8 | 11760.8 | 12261.9 | 11060.9 | 12494.5 | 11805.7 | 11851.3 | 11965.8 | 11852.4 | 10308.6 | 11866.6 | 10569.6 | 11922.7 | 11946.7 | 12970.4 | 11897.3 | 13084.8 | 12104.4 | 13047.4 | 12066.3 | 12191.6 | 12139 | 12790.6 | 13041.1 | 12940.7 | 12960.1 | 12992.3 | 12966.7 | 12214.1 | 13017.7 | 12652.9 | 12709.5 | 12829.6 | 12812.2 | 12877.4 | 12098.2 | 12792.3 | 12052.2 | 33.4026 | 33.6181 | 33.4905 | 0 | 33.794 | 33.9698 | 0 | 47.9 | 0 | 0 | 49.1 | 0 | 2.0692 | 2.1509 | 2.0397 | 2.084 | 2.1604 | 2.1588 | 7.773 | 7.293 | 8.505 | 7.055 | 7.333 | 7.979 | 6.4475 | 6.876 | 6.8415 | 6.6591 | 7.1577 | 6.6254 | 1.1928 | 1.354 | 1.5975 | 0 | 1.4407 | 1.2645 | 6.4921 | 6.6833 | 6.9321 | 6.89 | 7.1236 | 7.7591 | 1.2461 | 1.3676 | 1.5966 | 0 | 1.4764 | 1.5702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317029.12 | 573.195 | 306409.22 | 600.469 | 35855.736 | 74.533 | 6.4475 | 6.876 | 6.8415 | 6.6591 | 7.1577 | 6.6254 | 6.4921 | 6.6833 | 6.9321 | 6.89 | 7.1236 | 7.7591 | 913120 | 2195 | 959220 | 2469 | 1865067 | 4066 | 1867676 | 1861001 | 13.1833 | 6.7678 | 1.3699 | 6.98 | 1.4514 | 20.24% | 20.79% | 33.655 | 48.5 | 2.1105 | 7.6563 | 1882312 | 1865000 | 2307308.498 | 80.83%
2023-05-05 | 2024 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 335090.89 | 6:17 | 19:12 | 11215.1 | 11663.5 | 11557.8 | 11535.1 | 11643.3 | 11762.8 | 11741.1 | 12094.4 | 11766.7 | 11631.1 | 11709.8 | 11801.5 | 11827.3 | 11784.8 | 11827 | 11893.7 | 11732.1 | 11786.9 | 11712.1 | 11731.9 | 11835.2 | 11804.9 | 11689.5 | 11742 | 11703.2 | 10423 | 11711.8 | 11582.8 | 11898.1 | 11807.4 | 11714.2 | 11864.2 | 11894.5 | 11914.4 | 11956.4 | 11853.6 | 11965.4 | 11875.3 | 11758.4 | 11830.9 | 12559.9 | 11750.9 | 12524.2 | 11634.7 | 12226.2 | 12996 | 11457 | 12544.7 | 11118.2 | 11377.2 | 11967.1 | 11463.1 | 12211.5 | 11168.9 | 12182.1 | 11149 | 11157.5 | 12368.5 | 11111.3 | 12271 | 12213.5 | 11058.8 | 12085.2 | 11616 | 11777.6 | 11219.5 | 11878.2 | 12224.5 | 12328.5 | 11468.1 | 12299 | 11013.4 | 11882.1 | 11903.3 | 11265.6 | 12287.9 | 11089.4 | 12390.3 | 11229.6 | 12217.3 | 11468 | 12071.4 | 11482.1 | 12468.1 | 11473.2 | 12085.8 | 11477.8 | 10134.5 | 12243.8 | 11892.4 | 11036.7 | 12508.1 | 12193.3 | 11469.8 | 11357.9 | 12315.4 | 11333.2 | 11703.7 | 12511.3 | 11212.4 | 12598.3 | 11261 | 12383.3 | 11542.6 | 12346.4 | 10951.6 | 12460.3 | 11482.3 | 12344.6 | 11430.3 | 12369.7 | 11589.2 | 11277.6 | 12273.2 | 11369.4 | 11176.2 | 12345.2 | 12242.5 | 12225.1 | 11486.7 | 12347.8 | 11163.4 | 12070.1 | 11412.1 | 11949.7 | 10611.7 | 12184 | 11403.2 | 11475.6 | 11686.9 | 11485.4 | 9930.2 | 11525.7 | 10157 | 11359.2 | 11395.3 | 12653.6 | 11444.9 | 12771.5 | 11680.3 | 12660.8 | 11614.5 | 11759.4 | 11624.4 | 12418.2 | 12703.7 | 12711.7 | 12637.8 | 12646.6 | 12629.6 | 11854.3 | 12702.4 | 12699.6 | 12736 | 12773.4 | 12743.1 | 12758.3 | 11789.1 | 12834.6 | 11866.1 | 33.013 | 33.0414 | 33.0865 | 0 | 33.1946 | 33.526 | 0 | 46.6 | 0 | 0 | 47.2 | 0 | 2.4727 | 2.5719 | 2.4842 | 2.6312 | 2.6218 | 2.5945 | 9.896 | 9.378 | 9.267 | 11.272 | 7.437 | 9.064 | 6.6941 | 6.8563 | 6.8507 | 6.7115 | 6.9264 | 6.3027 | 1.2653 | 1.408 | 1.6221 | 0 | 1.4009 | 1.245 | 6.7327 | 6.6472 | 6.9174 | 6.904 | 6.8437 | 7.4176 | 1.3233 | 1.423 | 1.6272 | 0 | 1.4487 | 1.5482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317965 | 574 | 307353 | 601 | 37731.07 | 78.667 | 6.6941 | 6.8563 | 6.8507 | 6.7115 | 6.9264 | 6.3027 | 6.7327 | 6.6472 | 6.9174 | 6.904 | 6.8437 | 7.4176 | 935880 | 805 | 943780 | 531 | 1875334 | 4134 | 1878324 | 1871200 | 12.9167 | 6.7236 | 1.3882 | 6.9104 | 1.4741 | 20.65% | 21.33% | 33.1723 | 46.9 | 2.5627 | 9.3857 | 1892395.6 | 1875200 | 2299808.5665 | 81.54%
2023-05-06 | 2024 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 335090.89 | 6:05 | 19:12 | 12201.1 | 12649.3 | 12580 | 12563.7 | 12645 | 12706.2 | 12707.5 | 13057.6 | 12723.7 | 12723 | 12594.4 | 12722.3 | 12698 | 12640 | 12664.9 | 12741.5 | 12562.4 | 12630.4 | 12616.6 | 12637.9 | 12735.8 | 12709.6 | 12534.7 | 12625.2 | 12537.4 | 11237.1 | 12615.1 | 12477.5 | 12770.6 | 12624.6 | 12519.8 | 12707.2 | 12639.6 | 12662.9 | 12753.2 | 12627.4 | 12720.4 | 12623.5 | 12518.8 | 12589.7 | 13135.4 | 12194.5 | 13088.8 | 12053.6 | 12776.8 | 13745.3 | 11964.2 | 13123.8 | 11995.2 | 12250.9 | 12879.3 | 12297.2 | 13163.6 | 12055.5 | 13096 | 12022.5 | 11915.5 | 13153.8 | 11972.4 | 13132 | 13078.9 | 11922.1 | 12881.8 | 12413.8 | 12491 | 11916.6 | 12618.5 | 12957.4 | 13153 | 12196.3 | 13195.6 | 11806.1 | 12701.2 | 12786.1 | 12075.9 | 13264.5 | 12029.6 | 13287.3 | 12102.9 | 13193.1 | 12183.9 | 12848.8 | 12174.6 | 13248.3 | 12208.5 | 12922.3 | 12119.6 | 10750.8 | 12869.2 | 12479.2 | 11683.5 | 13160.5 | 12852.7 | 12122.7 | 12013.9 | 12889.4 | 11760.7 | 12082.3 | 12865.8 | 11554 | 12910.7 | 11568.6 | 12665.3 | 11818.3 | 12653.1 | 11264.4 | 12775.2 | 11808.9 | 12640.1 | 11752.2 | 12674.1 | 11935 | 11603.8 | 12539.4 | 11701.4 | 11470.6 | 12630 | 12463.8 | 12497.8 | 11740.2 | 12601.8 | 11436.3 | 12355.5 | 11710.5 | 12226 | 10879.2 | 12442.2 | 11664.2 | 11702.9 | 11903.4 | 11702.2 | 10137.5 | 11673.9 | 10332.9 | 11557.7 | 11591 | 12834.1 | 11639.9 | 12937.6 | 11833.3 | 12859.3 | 11765.1 | 11904.8 | 11777.3 | 12547.6 | 12828.8 | 12808.9 | 12757.4 | 12813.8 | 12803.7 | 11951.3 | 12815.5 | 12823.6 | 12781.3 | 12840.8 | 12796.1 | 12816.2 | 11860.4 | 12949.8 | 11903.1 | 35.574 | 35.4067 | 35.4591 | 0 | 35.6376 | 35.6191 | 0 | 48.9 | 0 | 0 | 48.7 | 0 | 3.6977 | 3.7466 | 3.6469 | 3.7043 | 3.6942 | 3.5085 | 10.43 | 8.466 | 7.951 | 8.125 | 8.45 | 7.607 | 7.0739 | 7.2287 | 7.227 | 6.9933 | 7.0719 | 6.3637 | 1.2914 | 1.6133 | 1.6507 | 0 | 1.4991 | 1.3082 | 7.1913 | 7.2118 | 7.2437 | 7.279 | 6.6243 | 7.4783 | 1.3656 | 1.6284 | 1.6698 | 0 | 1.5398 | 1.6216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318969.1 | 575.89 | 308324.06 | 603.545 | 39698.403 | 82.8 | 7.0739 | 7.2287 | 7.227 | 6.9933 | 7.0719 | 6.3637 | 7.1913 | 7.2118 | 7.2437 | 7.279 | 6.6243 | 7.4783 | 1004100 | 1890 | 971060 | 2545 | 1967333 | 4133 | 1970725 | 1963200 | 13.1167 | 6.9931 | 1.4725 | 7.1714 | 1.565 | 21.06% | 21.82% | 35.5393 | 48.8 | 3.6663 | 8.5048 | 1983854.1 | 1967133 | 2391559.3301 | 82.25%
2023-05-07 | 2024 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 335090.89 | 6:05 | 19:16 | 12277.3 | 12720.7 | 12687.2 | 12688 | 12765 | 12810.6 | 12754.3 | 13052.5 | 12730.1 | 12647.5 | 12600.6 | 12711.8 | 12739.4 | 12630.7 | 12728.7 | 12782.1 | 12630.5 | 12675.7 | 12604.5 | 12638 | 12717 | 12693.5 | 12540.9 | 12609.3 | 12515.7 | 11418.1 | 12584 | 12454.8 | 12717 | 12594.1 | 12545.8 | 12698.3 | 12704.1 | 12727.8 | 12778.5 | 12701.9 | 12749.6 | 12660.1 | 12613.5 | 12666.1 | 13223.9 | 12420.7 | 13166.4 | 12282.6 | 12893.8 | 13731.6 | 12212 | 13202.4 | 12068.9 | 12301.4 | 12849.6 | 12346.5 | 13093.9 | 12127.6 | 13069.3 | 12144.4 | 12016.7 | 13086.5 | 12073.4 | 13052.7 | 13001 | 12012.9 | 12775.2 | 12348.1 | 12467.6 | 12064.5 | 12585.2 | 12981 | 13051.3 | 12300.3 | 13081.7 | 11990.9 | 12625.6 | 12767.7 | 12131.1 | 13160.1 | 12076.2 | 13189.5 | 12148.2 | 13084.2 | 12355.4 | 12952.5 | 12422.7 | 13311.5 | 12508.2 | 13120.5 | 12291.8 | 11109 | 13026.1 | 12662.6 | 12006.6 | 13263.7 | 12947.8 | 12293.5 | 12194.4 | 13072.9 | 12144.4 | 12422.4 | 13156.9 | 11966.1 | 13205.3 | 12005.2 | 13031.3 | 12243.5 | 13082.1 | 11751.3 | 13204.2 | 12253.1 | 13118.7 | 12294.7 | 13191.7 | 12439.8 | 12037.4 | 12938.1 | 12117.8 | 11955.3 | 13003.3 | 12885.7 | 12898.6 | 12229.8 | 13023.6 | 11994.4 | 12775.1 | 12197.7 | 12688.3 | 11476 | 12878.1 | 12172.8 | 12206.8 | 12363.6 | 12161.3 | 10665.3 | 12186.7 | 10908.3 | 12291.9 | 12296.8 | 13341.5 | 12251.6 | 13423.6 | 12433.2 | 13384.2 | 12397 | 12526.6 | 12455.7 | 13172 | 13420.9 | 13367 | 13310.1 | 13301.9 | 13289 | 12537.5 | 13369.8 | 13352.9 | 13347.6 | 13450.2 | 13420.1 | 13427.1 | 12572.1 | 13455.3 | 12602.2 | 37.1464 | 36.9525 | 36.9557 | 0 | 37.2616 | 37.3069 | 0 | 48.1 | 0 | 0 | 48.4 | 0 | 6.1754 | 6.171 | 5.9887 | 6.107 | 6.0912 | 5.9849 | 10.432 | 11.176 | 10.565 | 10.968 | 12.008 | 11.018 | 7.279 | 7.4626 | 7.5857 | 7.1231 | 7.4815 | 6.8647 | 1.3483 | 1.6741 | 1.7493 | 0 | 1.6088 | 1.4318 | 7.3691 | 7.3317 | 7.5653 | 7.4578 | 7.1466 | 8.064 | 1.4232 | 1.6926 | 1.7704 | 0 | 1.6487 | 1.7774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319974.4 | 577.19 | 309329.2 | 605.089 | 41702.737 | 86.867 | 7.279 | 7.4626 | 7.5857 | 7.1231 | 7.4815 | 6.8647 | 7.3691 | 7.3317 | 7.5653 | 7.4578 | 7.1466 | 8.064 | 1005300 | 1300 | 1005140 | 1544 | 2004334 | 4067 | 2007596 | 2000267 | 13.1833 | 7.2994 | 1.5625 | 7.4891 | 1.6625 | 21.41% | 22.2% | 37.1246 | 48.25 | 6.0864 | 11.0278 | 2021783.6 | 2004200 | 2494117.5332 | 80.36%
2023-05-08 | 2024 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 335090.89 | 6:02 | 19:13 | 13167 | 13569.9 | 13532.9 | 13524.2 | 13596.2 | 13677.1 | 13627.4 | 13932.3 | 13615.1 | 13548.2 | 13506.8 | 13614.9 | 13647.8 | 13546.3 | 13632.6 | 13705.4 | 13529 | 13614.9 | 13522.8 | 13541.2 | 13650.5 | 13627.6 | 13486.4 | 13557.3 | 13477.1 | 12357.3 | 13520.4 | 13387.5 | 13665.3 | 13538.2 | 13520 | 13653 | 13631.3 | 13637 | 13738.8 | 13654.9 | 13710.9 | 13606.8 | 13578.1 | 13614.1 | 14179.6 | 13366 | 14077.1 | 13216.6 | 13819.4 | 14666.8 | 13131.7 | 14127.2 | 13021.7 | 13250.7 | 13804.5 | 13289.2 | 14044.9 | 13076 | 14014.3 | 13105.2 | 12993.9 | 14091.6 | 13062.3 | 14056.9 | 14008.7 | 12984.5 | 13763.7 | 13320.8 | 13446 | 12966.5 | 13512.4 | 13811.9 | 13976.7 | 13127.4 | 13941.6 | 12818.1 | 13472.1 | 13566.6 | 10677 | 11591.2 | 12901.1 | 14114.3 | 13047.4 | 13927 | 13164.9 | 13713.1 | 13199.8 | 14099.3 | 13372 | 14016.1 | 13113.3 | 11874.4 | 13818.7 | 13465.8 | 12912.3 | 14122.5 | 13828.4 | 13179 | 13072 | 13915.7 | 13001.5 | 13278.5 | 13993.3 | 12832.9 | 14040.9 | 12863.6 | 13874.2 | 13146.6 | 13898.6 | 12655.1 | 13993.7 | 13123.9 | 13882.3 | 13082.7 | 13938.2 | 13271.1 | 12892.6 | 13758.5 | 12972.3 | 12842.1 | 13802 | 13705 | 13760.4 | 13106.3 | 13870.2 | 12870.1 | 13653.6 | 13105.7 | 13576 | 12355.1 | 13728.3 | 13079.5 | 13048.3 | 13178.4 | 13027.2 | 11430.7 | 12979.2 | 11623.6 | 12984.7 | 13015.8 | 14166.4 | 13041.3 | 14219.8 | 13234.5 | 14145.9 | 13141.3 | 13266.7 | 13180.2 | 13906.5 | 14162.1 | 14170.8 | 14109.2 | 14108 | 14086.8 | 13348.2 | 14142.6 | 14160.5 | 14119.5 | 14163.7 | 14150.6 | 14161.7 | 13305.1 | 14227.6 | 13351 | 35.806 | 35.9625 | 35.9979 | 0 | 36.4515 | 36.2608 | 0 | 48.2 | 0 | 0 | 48.4 | 0 | 5.3888 | 5.2635 | 5.1797 | 5.189 | 5.2572 | 5.1901 | 10.805 | 9.414 | 9.461 | 9.876 | 9.948 | 10.11 | 8.0033 | 8.1662 | 8.2341 | 7.8432 | 8.1077 | 7.3911 | 1.4495 | 1.8966 | 1.8682 | 0 | 1.8065 | 1.6059 | 8.0487 | 8.0033 | 8.1385 | 8.1459 | 7.7774 | 8.674 | 1.5333 | 1.9166 | 1.8996 | 0 | 1.8415 | 1.9904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321048 | 578 | 310399 | 606 | 43839.67 | 91 | 8.0033 | 8.1662 | 8.2341 | 7.8432 | 8.1077 | 7.3911 | 8.0487 | 8.0033 | 8.1385 | 8.1459 | 7.7774 | 8.674 | 1073600 | 810 | 1069800 | 911 | 2136933 | 4133 | 2141679 | 2132800 | 13.1833 | 7.9576 | 1.7253 | 8.1313 | 1.8363 | 21.68% | 22.58% | 36.0958 | 48.3 | 5.2447 | 9.9357 | 2155815.1 | 2136733 | 2695922.5858 | 79.26%
2023-05-09 | 2024 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 335090.89 | 6:07 | 19:17 | 13018.7 | 13424.9 | 13399.3 | 13388.5 | 13458.4 | 13533.5 | 13488 | 13809.6 | 13491.4 | 13410.2 | 13388.9 | 13493.2 | 13527.9 | 13436.4 | 13493.2 | 13587.1 | 13402.1 | 13496.2 | 13392.2 | 13409.4 | 13533 | 13504.2 | 13344.6 | 13431.9 | 13351 | 12125.9 | 13386.4 | 13254.3 | 13548.5 | 13401.8 | 13392 | 13530.4 | 13513.4 | 13531.6 | 13623.9 | 13541 | 13601.3 | 13531.5 | 13398.6 | 13491.4 | 14116.2 | 13228.8 | 14002.8 | 13057.4 | 13679.6 | 14582.4 | 12989.8 | 14093.6 | 12842.3 | 13088.4 | 13694.6 | 13130.3 | 13945.5 | 12915.1 | 13910.3 | 12915.4 | 12803.7 | 13979.6 | 12848.7 | 13935.8 | 13890.8 | 12778.7 | 13632 | 13172.1 | 13368.8 | 12833.1 | 13376.1 | 13716.8 | 13877.9 | 12979.3 | 13837.1 | 12613.3 | 13421.9 | 13442.3 | 12867.6 | 13838.6 | 12697.2 | 14006.5 | 12853.8 | 13814.6 | 13030.6 | 13605.6 | 13085.9 | 14018.2 | 13073.3 | 13636.3 | 12947.1 | 11651.3 | 13700.3 | 13333.7 | 12733.2 | 14036.1 | 13742.3 | 13034.1 | 12904.8 | 13794.2 | 12803.3 | 13159.4 | 13913.9 | 12691 | 13974.6 | 12729 | 13771 | 12988 | 13798.9 | 12449.6 | 13888.8 | 12950 | 13763.5 | 12902 | 13821.7 | 13086 | 12750 | 13660.7 | 12809.6 | 12685.7 | 13784 | 13626.6 | 13663.4 | 12957.2 | 13775.9 | 12671.6 | 13507.6 | 12929.1 | 13444.6 | 12092.6 | 13604.9 | 12881.8 | 12843.8 | 12993.9 | 12813.3 | 11185.3 | 12816.6 | 11471.6 | 12817.9 | 12837.1 | 14135.6 | 12950.6 | 14139.8 | 13130.1 | 14049.7 | 12966.3 | 13093.8 | 13009.3 | 13825.1 | 14105.7 | 14115.6 | 14049.3 | 14055.2 | 14017.8 | 13202.4 | 14071.6 | 14067.5 | 14062.3 | 14115.3 | 14085.3 | 14128.4 | 13187 | 14159.2 | 13243.4 | 36.0689 | 36.2119 | 36.4411 | 0 | 36.3973 | 36.5767 | 0 | 50.6 | 0 | 0 | 50.8 | 0.13106 | 2.9194 | 2.9107 | 2.7491 | 2.9484 | 2.8139 | 2.6309 | 7.109 | 6.321 | 6.312 | 7.108 | 6.368 | 7.372 | 7.9618 | 8.0944 | 8.1626 | 7.8401 | 8.0849 | 7.1978 | 1.4654 | 1.8999 | 1.8738 | 0 | 1.8084 | 1.6461 | 8.0013 | 7.9331 | 8.059 | 8.0873 | 7.3844 | 8.5493 | 1.5518 | 1.9185 | 1.9081 | 0 | 1.8436 | 2.0377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 322115 | 579 | 311458 | 607 | 45960.47 | 95.067 | 7.9618 | 8.0944 | 8.1626 | 7.8401 | 8.0849 | 7.1978 | 8.0013 | 7.9331 | 8.059 | 8.0873 | 7.3844 | 8.5493 | 1067000 | 1000 | 1059000 | 1000 | 2120800 | 4067 | 2124000 | 2116733 | 13.1667 | 7.8903 | 1.7387 | 8.0024 | 1.852 | 22.04% | 23.14% | 36.3392 | 33.8437 | 2.8287 | 6.765 | 2139473.4 | 2120600 | 2626488.4804 | 80.74%
2023-05-10 | 2024 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 335090.89 | 6:06 | 19:18 | 12769.5 | 13335.6 | 13461.7 | 13459.5 | 13515.6 | 13587.9 | 13529.5 | 13832.2 | 13536.3 | 13427.4 | 13439 | 13534.6 | 13579.2 | 13489.9 | 13529.7 | 13646.9 | 13448.2 | 13544.4 | 12918.1 | 5928.7 | 13573.7 | 13548.3 | 13391.3 | 13480 | 13412.7 | 12157 | 13446.5 | 13308.5 | 13596.2 | 13437.8 | 13447.8 | 13600.1 | 13559.1 | 13595.9 | 13684.2 | 13607.6 | 13668.7 | 13597.9 | 13410.7 | 13549.2 | 14166.2 | 13282.2 | 14075.8 | 13138.1 | 13710.6 | 14599.4 | 13024.7 | 14146.3 | 12886.1 | 13130.9 | 13746.4 | 13192.8 | 13991.4 | 12945.8 | 13950.4 | 12962.7 | 12860.7 | 14020.9 | 12895.6 | 13982.8 | 13933.3 | 12832.1 | 13670.8 | 13217.8 | 13417.7 | 12873.7 | 13417.9 | 13762.5 | 13923 | 13017.6 | 13886.1 | 12643.4 | 13496.3 | 13492 | 12926.3 | 13893.8 | 12744.5 | 14057.9 | 12912.3 | 13877 | 13053.6 | 13643.8 | 13087.6 | 14020 | 13190.5 | 13908.8 | 12992.5 | 11638.3 | 13726.1 | 13377.2 | 12767.5 | 14061 | 13784.5 | 13083.7 | 12958.6 | 13828.6 | 12831.1 | 13210.6 | 13957.4 | 12730.4 | 14020.2 | 12769 | 13816.4 | 13029.9 | 13844.6 | 12464.7 | 13935.4 | 13005.2 | 13816.8 | 12959.3 | 13867.7 | 13133.4 | 12797.7 | 13697.5 | 12908.4 | 12724.4 | 13818.9 | 13656 | 13694.1 | 12983.9 | 13809.3 | 12689.9 | 13511.6 | 12958.9 | 13483.5 | 12077 | 13633.5 | 12915.4 | 12867.1 | 13041.1 | 12898.6 | 11179.7 | 12842.1 | 11456.9 | 12840.9 | 12854.5 | 14167.3 | 12990.4 | 14160.5 | 13170.9 | 14099.5 | 13015.9 | 13150.6 | 13057.7 | 13863.4 | 14130.4 | 14151.9 | 14070.5 | 14077.5 | 14045.4 | 13231.1 | 14098.6 | 14078.2 | 14074.7 | 14150 | 14118.7 | 14167.7 | 13233.3 | 14178.2 | 13269.7 | 37.3133 | 37.044 | 37.1682 | 0 | 37.3012 | 37.3032 | 0 | 50.9 | 0 | 0 | 50.8 | 0 | 3.3877 | 3.2883 | 3.2731 | 3.2882 | 3.3939 | 3.141 | 7.215 | 7.205 | 6.503 | 9.48 | 6.598 | 6.729 | 7.9908 | 8.0944 | 8.1568 | 7.8104 | 7.9891 | 5.9961 | 1.4773 | 1.915 | 1.8838 | 0 | 1.8154 | 1.6049 | 8.0253 | 7.6355 | 8.0548 | 8.0988 | 4.7148 | 8.5921 | 1.5629 | 1.9287 | 1.9196 | 0 | 1.8506 | 1.9902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 323179 | 580 | 312520 | 608 | 48079.67 | 99.067 | 7.9908 | 8.0944 | 8.1568 | 7.8104 | 7.9891 | 5.9961 | 8.0253 | 7.6355 | 8.0548 | 8.0988 | 4.7148 | 8.5921 | 1064000 | 1000 | 1062000 | 1000 | 2119200 | 4000 | 2124000 | 2115200 | 13.2 | 7.6729 | 1.7393 | 7.5202 | 1.8504 | 22.67% | 24.61% | 37.226 | 50.85 | 3.2954 | 7.2883 | 2137900.3 | 2119000 | 2482771.2981 | 85.35%
2023-05-11 | 2024 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 335090.89 | 6:05 | 19:16 | 13000.9 | 13453.4 | 13400.2 | 13422.8 | 13480.1 | 13581.5 | 13514.3 | 13828.8 | 13544.7 | 13412.6 | 13440.1 | 13534.1 | 13606.8 | 13480 | 13532.9 | 13675.1 | 11632.4 | 11647 | 11070.3 | 402.7 | 11494.8 | 11469.4 | 11852 | 11905.1 | 13411.7 | 12069.4 | 13449.3 | 13311.6 | 13600.6 | 13484.7 | 13431.1 | 13571.3 | 13514.9 | 13557.1 | 13692.9 | 13610.8 | 13681.5 | 13601.5 | 13434.7 | 13554.6 | 14231.3 | 13306.3 | 14147 | 13116.8 | 13604.2 | 14443.3 | 13033 | 14149.7 | 12825.2 | 13092.6 | 13734.4 | 13154.2 | 13971.2 | 12861.3 | 13959.5 | 12878.3 | 12749.9 | 13922.1 | 12811.6 | 13905.2 | 13824 | 12737.7 | 13543.6 | 13129.7 | 13459.1 | 12794 | 13423 | 13783.2 | 13954.7 | 12960.7 | 13912.2 | 12545.4 | 13516.5 | 13497.4 | 12856.5 | 13879.6 | 12650.4 | 14056.2 | 12833.4 | 13837 | 13011.2 | 13634 | 13070.2 | 14022.1 | 13024 | 13672 | 12955.3 | 11558.7 | 13695.7 | 13316.8 | 12693.1 | 14042.1 | 13750.2 | 13015.6 | 12877.6 | 13836.2 | 12730.4 | 13173.7 | 13949.7 | 12673 | 14005.3 | 12707.8 | 13812.1 | 12975 | 13831.2 | 12391 | 13910.8 | 12946 | 13814.6 | 12884.8 | 13899.5 | 13060.2 | 12716.5 | 13674.8 | 12847.2 | 12643.7 | 13809.6 | 13661.5 | 13698 | 12921.5 | 13799.6 | 12592.5 | 13504 | 12892.1 | 13475.7 | 11997.7 | 13649.3 | 12842.6 | 12807.6 | 13027.1 | 12831.4 | 11137.1 | 12768.1 | 11350.6 | 12750.9 | 12766.8 | 14192.7 | 12975.2 | 14178.3 | 13159.9 | 14132.8 | 12997.8 | 13182 | 13001.4 | 13904.3 | 14123.4 | 14141.6 | 14059.6 | 14071.4 | 14053.9 | 13250.5 | 14118.4 | 14093.2 | 14143 | 14193.7 | 14121.3 | 14203 | 13238.8 | 14239.6 | 13315.1 | 38.9705 | 39.0213 | 39.1393 | 0 | 39.1649 | 39.3224 | 0 | 53.2 | 0 | 0 | 53.3 | 0 | 2.7214 | 2.7174 | 2.7058 | 2.7769 | 2.6551 | 2.744 | 7.475 | 7.013 | 7 | 8.104 | 6.48 | 7.079 | 7.9964 | 8.0928 | 8.1613 | 7.8451 | 8.0093 | 6.0362 | 1.4726 | 1.9046 | 1.8801 | 0 | 1.8199 | 1.6463 | 6.3227 | 7.6554 | 6.7036 | 6.6182 | 4.7009 | 8.6155 | 1.5632 | 1.9263 | 1.9158 | 0 | 1.8569 | 2.0465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324222 | 581 | 313580 | 610 | 50176.804 | 103.133 | 7.9964 | 8.0928 | 8.1613 | 7.8451 | 8.0093 | 6.0362 | 6.3227 | 7.6554 | 6.7036 | 6.6182 | 4.7009 | 8.6155 | 1043000 | 1000 | 1060000 | 2000 | 2097134 | 4066 | 2100000 | 2093068 | 13.1833 | 7.6902 | 1.7447 | 6.7694 | 1.8617 | 22.69% | 27.5% | 39.1237 | 53.25 | 2.7201 | 7.1918 | 2115647.8 | 2096867 | 2237554.2801 | 93.71%
2023-05-12 | 2024 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 335090.89 | 6:03 | 19:14 | 12844.3 | 13291.9 | 13229.9 | 13267.2 | 13332.4 | 13436.1 | 13354.5 | 13685.9 | 13414.6 | 13262.9 | 13308 | 13391.7 | 13474 | 13334.4 | 13412.6 | 13526.8 | 13359.6 | 13433.2 | 10403.4 | 0 | 13499.3 | 13480.4 | 13290.6 | 13382.4 | 13233.7 | 11923.7 | 13298.8 | 13169 | 13450.6 | 13361 | 13279.2 | 13386.8 | 13340.3 | 13380.2 | 13519.3 | 13434.9 | 13501.7 | 13433.8 | 13244 | 13395.7 | 14084.5 | 13137.6 | 14005.7 | 12979.3 | 13511.4 | 14377.3 | 12918 | 14050.5 | 12669.7 | 12946.5 | 13567.6 | 12997 | 13813.4 | 12745.2 | 13817.6 | 12770.3 | 12571.4 | 13759.4 | 12631.8 | 13715.8 | 13642.6 | 12552.9 | 13294.6 | 12893.7 | 13322.9 | 12692.5 | 13282.7 | 13607.1 | 13818.1 | 12833.8 | 13767.1 | 12392 | 13363 | 13340.3 | 12729.6 | 13710.1 | 12510.3 | 13897 | 12668.5 | 13670.1 | 12806.9 | 13444 | 12891.6 | 13871.4 | 12795.1 | 13470.1 | 12803 | 11398 | 13541.3 | 13156.2 | 12531.9 | 13897.6 | 13590.8 | 12849.4 | 12732.1 | 13717.2 | 12628.4 | 13013.7 | 13800.2 | 12511.5 | 13844.1 | 12562.7 | 13642.3 | 12827.1 | 13669.9 | 12227.9 | 13735 | 12782.6 | 13656 | 12747.1 | 13751.1 | 12918.5 | 12553.4 | 13512.9 | 12687 | 12503 | 13640.7 | 13478.6 | 13536.2 | 12787.4 | 13644 | 12442.4 | 13338.9 | 12755 | 13332.6 | 11850 | 13488.5 | 12700.6 | 12690.7 | 12913 | 12705.8 | 10983.8 | 12662.6 | 11193.5 | 12633.4 | 12655.5 | 14068.4 | 12820.3 | 14060.2 | 12992.4 | 14001.5 | 12875.6 | 13044.7 | 12889.2 | 13714.9 | 13957.8 | 13962.5 | 13893.4 | 13883.1 | 13887.4 | 13065 | 13969.9 | 13986.7 | 14015.9 | 14063.9 | 13991.7 | 14070.4 | 13080.5 | 14116.4 | 13150.7 | 40.4738 | 40.3556 | 40.4915 | 0 | 40.431 | 40.7566 | 0 | 53.1 | 0 | 0 | 53.5 | 0 | 4.0247 | 4.1568 | 4.0897 | 4.1344 | 4.1812 | 4.1178 | 7.76 | 8.435 | 7.997 | 8.626 | 8.143 | 9.096 | 7.8988 | 7.9816 | 8.052 | 7.7467 | 7.8831 | 5.953 | 1.4637 | 1.8721 | 1.8647 | 0 | 1.7872 | 1.574 | 7.0397 | 7.5733 | 7.6644 | 7.0956 | 5.6947 | 8.4579 | 1.5551 | 1.8953 | 1.9004 | 0 | 1.8274 | 1.9523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325264 | 583 | 314628 | 611 | 52261.137 | 107.067 | 7.8988 | 7.9816 | 8.052 | 7.7467 | 7.8831 | 5.953 | 7.0397 | 7.5733 | 7.6644 | 7.0956 | 5.6947 | 8.4579 | 1042000 | 2000 | 1048000 | 1000 | 2084333 | 3934 | 2087000 | 2080399 | 13.1833 | 7.5859 | 1.7123 | 7.2543 | 1.8261 | 22.57% | 25.17% | 40.5017 | 53.3 | 4.1174 | 8.3428 | 2101894.4 | 2084133 | 2520358.0861 | 82.69%
2023-05-13 | 2024 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 335090.89 | 6:04 | 19:12 | 12550.9 | 13049.4 | 13028.2 | 13048.6 | 13136.7 | 13231.7 | 13120.3 | 13461.5 | 13160 | 13037 | 13049.2 | 13140.7 | 13207.1 | 13071.4 | 13164.7 | 13240.6 | 13114.4 | 13172.6 | 13133.1 | 13034.7 | 13237.8 | 13209.4 | 13030.1 | 13112.4 | 12905.1 | 11712.5 | 13046.1 | 12916.4 | 13175 | 13084.7 | 12995.1 | 13081.9 | 12963.3 | 13051.3 | 13206.3 | 13136.5 | 13202.7 | 13152 | 13014.4 | 13129.3 | 13791.9 | 12890.7 | 13720.1 | 12754.8 | 13316.9 | 14142.6 | 12661 | 13764.8 | 12416.7 | 12701.7 | 13312.8 | 12770.1 | 13561.7 | 12547 | 13556.8 | 12579.7 | 12368.8 | 13524.3 | 12428.8 | 13466.8 | 13380.9 | 12341.5 | 12975.8 | 12672.5 | 13088.3 | 12550.2 | 13045.1 | 13425.1 | 13562.9 | 12672.5 | 13522.4 | 12261.8 | 13105.1 | 13123 | 12507.5 | 13479.9 | 12313 | 13617.7 | 12431.7 | 13398.1 | 12598.1 | 13281.2 | 12777.2 | 13704.6 | 12698.5 | 13359 | 12655.7 | 11294.3 | 13283.4 | 12991.1 | 12351.5 | 13663.4 | 13320.3 | 12615.9 | 12507.5 | 13456.4 | 12507.8 | 12883.1 | 13644 | 12407.6 | 13616 | 12423.8 | 13423.7 | 12680.7 | 13398 | 12083.1 | 13455.3 | 12631.8 | 13389 | 12548.6 | 13499.6 | 12771 | 12463.9 | 13362.8 | 12591.5 | 12429.8 | 13488.8 | 13349.9 | 13377.1 | 12686.8 | 13489 | 12376.8 | 13189.6 | 12643.5 | 13195.4 | 11790.8 | 13373 | 12603.7 | 12583.7 | 12767 | 12596.3 | 10904.3 | 12580.9 | 11143.3 | 12547 | 12559.7 | 13920.1 | 12691.3 | 13914.9 | 12866 | 13840.9 | 12744.2 | 12901.4 | 12759.3 | 13526.4 | 13779.9 | 13811.6 | 13756.8 | 13733 | 13747 | 12939.8 | 13837.1 | 13836.9 | 13857.5 | 13930.8 | 13866.7 | 13927.5 | 12942.4 | 13964 | 12991.6 | 40.8261 | 40.6413 | 40.6343 | 0 | 40.5468 | 41.0524 | 0 | 51.7 | 0 | 0 | 51.7 | 0 | 6.0429 | 6.0667 | 6.078 | 5.9515 | 6.1495 | 6.0785 | 11.353 | 10.886 | 11.587 | 11.618 | 10.724 | 10.951 | 7.8814 | 8.0538 | 7.8564 | 7.7233 | 7.999 | 7.1927 | 1.4612 | 1.8237 | 1.8434 | 0 | 1.7695 | 1.5512 | 7.9173 | 7.7853 | 7.6102 | 7.8985 | 7.7768 | 8.5062 | 1.5517 | 1.8567 | 1.8752 | 0 | 1.8148 | 1.9222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 326302 | 584 | 315664 | 613 | 54330.204 | 111.267 | 7.8814 | 8.0538 | 7.8564 | 7.7233 | 7.999 | 7.1927 | 7.9173 | 7.7853 | 7.6102 | 7.8985 | 7.7768 | 8.5062 | 1038000 | 1000 | 1036000 | 2000 | 2069067 | 4200 | 2071000 | 2064867 | 13.1333 | 7.7844 | 1.6898 | 7.9157 | 1.8041 | 21.71% | 22.79% | 40.7402 | 51.7 | 6.0612 | 11.1865 | 2086371 | 2069001 | 2596514.0642 | 79.68%
2023-05-14 | 2024 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 335090.89 | 6:04 | 19:19 | 11851.8 | 12295.2 | 12278.7 | 12266.2 | 12371.1 | 12362.2 | 12362.1 | 12717 | 12358.5 | 12305.4 | 12216.8 | 12360.3 | 12362.6 | 12277.5 | 12359 | 12425.8 | 12272.5 | 12346.4 | 12341.4 | 12393.5 | 12370.9 | 12365.9 | 12154.7 | 12260.2 | 12098.3 | 10786.8 | 12195.1 | 12035 | 12372.5 | 12242.6 | 12134.5 | 12313.3 | 12172.8 | 12222 | 12351.2 | 12272.9 | 12350.1 | 12255.1 | 12089.7 | 12169.6 | 12971.7 | 12015.8 | 12864.4 | 11809 | 12490.2 | 13422.1 | 11804.2 | 12986.8 | 11572.2 | 11833.2 | 12500.5 | 11880.7 | 12777.4 | 11676.4 | 12686.4 | 11612.9 | 11468.6 | 12739.7 | 11545.3 | 12701.2 | 12658.9 | 11510.2 | 12386.1 | 11927.9 | 12091.9 | 11452.8 | 12060.2 | 12388.7 | 12611.9 | 11611.1 | 12544.8 | 11163.4 | 12202.7 | 12118.2 | 11523 | 12555.7 | 11312 | 12766.1 | 11525.4 | 12581.5 | 11613.6 | 12244.6 | 11689.2 | 12662 | 11597 | 12210.5 | 11584.8 | 10233.4 | 12348.2 | 11976.1 | 11257.1 | 12674.9 | 12381.7 | 11642.7 | 11539.9 | 12442.9 | 11383.2 | 11760.8 | 12571.2 | 11246.5 | 12579.1 | 11257.5 | 12358.6 | 11549.9 | 12405.4 | 10948 | 12449.4 | 11478 | 12350.6 | 11437.4 | 12419.2 | 11597 | 11324.7 | 12268.4 | 11424.7 | 11213.1 | 12374.1 | 12195.6 | 12240.7 | 11419.7 | 12321 | 11087.4 | 12051.9 | 11435.6 | 12009.1 | 10555.3 | 12116.2 | 11281.3 | 11320 | 11534.1 | 11300.4 | 9793.2 | 11308.6 | 9995.4 | 11303.1 | 11317.5 | 12691.9 | 11459.1 | 12703.5 | 11667.6 | 12616.2 | 11505.8 | 11660.2 | 11533.7 | 12398.3 | 12668.9 | 12676.2 | 12622.8 | 12604.9 | 12577.6 | 11743 | 12637.6 | 12658.8 | 12662.3 | 12712.8 | 12679.5 | 12710.3 | 11738 | 12771 | 11790.5 | 37.2862 | 37.1061 | 37.1925 | 0 | 37.3412 | 37.5408 | 0 | 49.7 | 0 | 0 | 49.5 | 0 | 4.4123 | 4.4375 | 4.3571 | 4.4084 | 4.5343 | 4.5103 | 9.987 | 9.835 | 9.404 | 9.527 | 9.142 | 9.283 | 7.0382 | 7.2774 | 7.1379 | 6.9632 | 7.0424 | 6.352 | 1.3136 | 1.6118 | 1.6823 | 0 | 1.5271 | 1.3235 | 7.1049 | 7.0315 | 7.005 | 7.1035 | 6.9432 | 7.5117 | 1.3911 | 1.6424 | 1.6982 | 0 | 1.5716 | 1.6453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327273 | 585 | 316608 | 615 | 56239.671 | 115.267 | 7.0382 | 7.2774 | 7.1379 | 6.9632 | 7.0424 | 6.352 | 7.1049 | 7.0315 | 7.005 | 7.1035 | 6.9432 | 7.5117 | 971000 | 1000 | 944000 | 2000 | 1909467 | 4000 | 1912000 | 1905467 | 13.25 | 6.9685 | 1.4917 | 7.1166 | 1.5897 | 21.41% | 22.34% | 37.2934 | 49.6 | 4.4433 | 9.5297 | 1926660.4 | 1909333 | 2352994.7997 | 81.14%
2023-05-15 | 2024 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 335090.89 | 6:05 | 19:11 | 9635.2 | 10003.3 | 11709.9 | 11748.7 | 12017.2 | 12012.8 | 12037.7 | 12366.4 | 11943.2 | 11982.6 | 11623.8 | 11701.9 | 11957.6 | 11820 | 12031.2 | 12067 | 11901.6 | 11951.4 | 11989.4 | 12036.3 | 12016.2 | 12023 | 11855.1 | 11928.4 | 11801.7 | 10610.5 | 11852.9 | 11728 | 12043.2 | 11951.9 | 11859.3 | 12008.8 | 10894 | 10826 | 11931 | 11887.3 | 11956.7 | 11870 | 11736 | 11853.8 | 12466.4 | 11580.1 | 12354.9 | 11439.3 | 12097.1 | 12953.7 | 11351.6 | 12420.7 | 10670.3 | 10894.2 | 11462.6 | 10923.2 | 11706 | 10680 | 11693.3 | 10725.4 | 10680.1 | 11791.5 | 10745.2 | 11714.2 | 11685.1 | 10685.3 | 11521.2 | 11081.4 | 11652.4 | 11077.3 | 11614.3 | 11933 | 12121 | 11202 | 12133.9 | 10894.6 | 11724.9 | 11692.7 | 10964.3 | 11896.7 | 10216 | 11339.6 | 11025.9 | 12072 | 10307.7 | 10816.2 | 10398.2 | 11262.4 | 11172.4 | 11873.2 | 11188.3 | 10045.7 | 11953.8 | 11425.8 | 10984.6 | 12298.8 | 11937.5 | 11335.8 | 11224.4 | 12084.2 | 9930.2 | 10197.1 | 12067.7 | 10856 | 12254 | 11069.6 | 10752.6 | 10061.8 | 10421.7 | 9314.4 | 10739.4 | 10067.4 | 11463.9 | 10771.2 | 11586.9 | 10807.5 | 11248.4 | 12160.3 | 8831 | 11112 | 12268.5 | 12045.4 | 12086.5 | 11426.1 | 12258.1 | 11148.9 | 11970.9 | 11415.3 | 11964.2 | 10690 | 12113.4 | 11351.2 | 11395.7 | 11555.1 | 11348.4 | 9903.4 | 11360.5 | 10085.9 | 11328.7 | 11318.7 | 12602.1 | 11412.5 | 12621.6 | 11604.7 | 12553.3 | 11445 | 11635.1 | 11519.8 | 11721 | 11964.1 | 11990.1 | 11919.3 | 11899.9 | 11878.7 | 10625.8 | 9230 | 12556.5 | 12615.2 | 12641.7 | 12619.6 | 12680.8 | 11638.2 | 12752.2 | 11706.1 | 35.5147 | 35.5461 | 35.4247 | 0 | 35.2533 | 35.8181 | 0 | 47.1 | 0 | 0 | 47 | 0 | 8.5849 | 8.6801 | 8.7343 | 8.8612 | 8.5187 | 9.0805 | 12.598 | 12.145 | 13.981 | 12.983 | 11.98 | 14.322 | 6.7842 | 7.2368 | 7.1097 | 6.9099 | 7.1103 | 6.3931 | 1.3445 | 1.7571 | 1.7765 | 0 | 1.6993 | 1.5413 | 6.8164 | 6.9684 | 6.9808 | 7.0548 | 6.9043 | 7.5955 | 1.4383 | 1.7897 | 1.8066 | 0 | 1.7376 | 1.9105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 328196 | 587 | 317514 | 616 | 58061.471 | 119.267 | 6.7842 | 7.2368 | 7.1097 | 6.9099 | 7.1103 | 6.3931 | 6.8164 | 6.9684 | 6.9808 | 7.0548 | 6.9043 | 7.5955 | 923000 | 2000 | 906000 | 1000 | 1821800 | 4000 | 1826000 | 1817800 | 13.1 | 6.924 | 1.6237 | 7.0534 | 1.7365 | 23.45% | 24.62% | 35.5114 | 47.05 | 8.7433 | 13.0015 | 1838944.7 | 1821667 | 2389515.8607 | 76.24%
2023-05-16 | 2024 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 335090.89 | 6:08 | 19:11 | 12265.6 | 12701.6 | 12689.4 | 12659.4 | 12763.7 | 12774.4 | 12819.4 | 13123.5 | 12762.4 | 12710.7 | 12624.6 | 12733.1 | 12803.7 | 12712.4 | 12846.1 | 12872.9 | 12698 | 12781.3 | 12769 | 12841.9 | 12767.3 | 12831.9 | 12666.9 | 12703.6 | 12603.9 | 11398.2 | 12668.2 | 12541.6 | 12843.3 | 12730.3 | 12635 | 12762.7 | 12791.7 | 12771.1 | 12857.5 | 12810.2 | 12892.6 | 12821.6 | 12650.4 | 12798.6 | 13412.8 | 12586.8 | 13277.7 | 12440.6 | 13060.3 | 13883.3 | 12298.4 | 13319.4 | 12139.5 | 12390 | 12951.5 | 12418.1 | 13555.1 | 12300.9 | 13156.5 | 12234.9 | 12051.9 | 13157.1 | 12119.6 | 13113 | 13037.6 | 12039.9 | 12860.2 | 12425.7 | 12668.3 | 12119.9 | 12688.2 | 12989.4 | 13138.1 | 12242.7 | 13164.1 | 11936.1 | 12734 | 12756.2 | 12099.9 | 13047.8 | 12014.1 | 13219.5 | 12152.5 | 13049.9 | 12231 | 12789.2 | 12298.7 | 13225.4 | 12286.5 | 12867.8 | 12145.7 | 10978.9 | 12899.5 | 12577.9 | 11986.1 | 13257.9 | 12995.7 | 12346.6 | 12251.2 | 13025.3 | 12054.8 | 12445.7 | 13136.6 | 11957.8 | 13205.3 | 11979.4 | 13044.2 | 12307.7 | 12947.2 | 11729 | 13072.1 | 12205.7 | 13019.1 | 12191 | 13027.9 | 12405.4 | 12019.8 | 12891.4 | 12088.9 | 11984 | 13034.6 | 12800.9 | 12866.4 | 12195.8 | 12999.8 | 11928.6 | 12692.1 | 12237.9 | 12688.3 | 11460.8 | 12868.3 | 12135.8 | 12155.5 | 12241.4 | 12054.5 | 10523.3 | 12059.9 | 10742.1 | 12023.9 | 12034.8 | 13249 | 12141 | 13261.3 | 12363.3 | 13216.8 | 12169.2 | 12339.9 | 12217.7 | 13012.4 | 13228.1 | 13332.7 | 13233.2 | 13238.1 | 13221 | 12432.2 | 13237.8 | 13269.2 | 13214.9 | 13232.2 | 13269.6 | 13320.4 | 12426.7 | 13359.2 | 12502.7 | 35.6735 | 35.4499 | 35.3012 | 0 | 35.1546 | 35.8096 | 0 | 47.4 | 0 | 0 | 47 | 0 | 6.9001 | 6.978 | 6.9467 | 6.9761 | 6.6231 | 6.9997 | 11.393 | 11.349 | 11.442 | 11.478 | 10.534 | 11.017 | 7.4839 | 7.6606 | 7.532 | 7.3301 | 7.5063 | 6.789 | 1.3323 | 1.7755 | 1.7214 | 0 | 1.6979 | 1.5186 | 7.4831 | 7.4638 | 7.4023 | 7.481 | 7.3702 | 8.0278 | 1.423 | 1.8049 | 1.7598 | 0 | 1.7286 | 1.8856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329206 | 588 | 318512 | 617 | 60063.671 | 123.467 | 7.4839 | 7.6606 | 7.532 | 7.3301 | 7.5063 | 6.789 | 7.4831 | 7.4638 | 7.4023 | 7.481 | 7.3702 | 8.0278 | 1010000 | 1000 | 998000 | 1000 | 2002200 | 4200 | 2006000 | 1998000 | 13.05 | 7.3836 | 1.6091 | 7.538 | 1.7204 | 21.79% | 22.82% | 35.4778 | 47.2 | 6.9039 | 11.2022 | 2020860.9 | 2002067 | 2535266.5411 | 78.97%
2023-05-17 | 2024 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 335090.89 | 6:11 | 19:16 | 12362.3 | 12854.2 | 12785.7 | 12689.7 | 12902.4 | 12904 | 12889.6 | 13227.4 | 12891.2 | 12815.7 | 12727.2 | 12902.4 | 12859.9 | 12802.8 | 12831.9 | 12877.8 | 12740.8 | 12829.2 | 12777.5 | 12849 | 12837.2 | 12821.8 | 12677.8 | 12742.5 | 12610.7 | 11218.9 | 12681.6 | 12522.6 | 12867.1 | 12778.5 | 12682.3 | 12795.8 | 12844.6 | 12824.4 | 12895.2 | 12850.9 | 12925 | 12846 | 12688.6 | 12813.5 | 13504.3 | 12530.4 | 13413.4 | 12382.8 | 13031.8 | 13998.8 | 12302 | 13527.6 | 12043.6 | 12340.9 | 13013.3 | 12382.7 | 13326.4 | 12131.4 | 13283.9 | 12154.5 | 12040.1 | 13403.2 | 12057.3 | 13328.6 | 13284.6 | 12041.4 | 13051.5 | 12495.2 | 12756.9 | 12074 | 12690.8 | 13034 | 13253.4 | 12196.4 | 13171.5 | 11720.3 | 12787.8 | 12699.1 | 12060.8 | 13129.2 | 11821.3 | 13321 | 12028.2 | 13095.4 | 12252.8 | 12869.9 | 12315.9 | 13365.2 | 12254.9 | 12892.9 | 12285 | 10864.6 | 13143.4 | 12731.5 | 11984.4 | 13470.5 | 13121.8 | 12334.5 | 12220.4 | 13185 | 12024.4 | 12477.9 | 13331.4 | 11965.8 | 13337.5 | 11959.9 | 13105.4 | 12261.9 | 13150.9 | 11623.4 | 13228.5 | 12209.9 | 13090.9 | 12131.8 | 13146.8 | 12340.2 | 12066.6 | 13040.4 | 12129.9 | 11939.6 | 13167.7 | 12979.6 | 13022.5 | 12199.7 | 13126.3 | 11840 | 12822.3 | 12185.2 | 12774.2 | 11292.3 | 12912.7 | 12057.1 | 12071.8 | 12255.9 | 12036.4 | 10436.1 | 12116.3 | 10747.4 | 11895.4 | 11907.9 | 13388.6 | 12129.6 | 13423.7 | 12325.7 | 13355.1 | 12183.3 | 12383.2 | 12177.7 | 13128.8 | 13450.1 | 13415.1 | 13348.6 | 13306.1 | 13275.5 | 12424.9 | 13389.4 | 13382.8 | 13405.2 | 13482.9 | 13455.2 | 13497.3 | 12468.3 | 13457.2 | 12491.1 | 34.9743 | 35.133 | 34.9268 | 0 | 34.8449 | 35.4107 | 0 | 48 | 0 | 0 | 47.9 | 0 | 6.2824 | 6.3431 | 6.3383 | 6.4485 | 6.2752 | 6.5485 | 10.232 | 9.949 | 10.374 | 9.857 | 10.381 | 10.26 | 7.4349 | 7.5475 | 7.4173 | 7.2915 | 7.4104 | 6.6754 | 1.3236 | 1.7604 | 1.6759 | 0 | 1.684 | 1.5066 | 7.4142 | 7.3533 | 7.2732 | 7.4144 | 7.2558 | 7.8838 | 1.4169 | 1.7868 | 1.7152 | 0 | 1.7186 | 1.8672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330220 | 589 | 319514 | 619 | 62074.338 | 127.6 | 7.4349 | 7.5475 | 7.4173 | 7.2915 | 7.4104 | 6.6754 | 7.4142 | 7.3533 | 7.2732 | 7.4144 | 7.2558 | 7.8838 | 1014000 | 1000 | 1002000 | 2000 | 2010667 | 4133 | 2013000 | 2006534 | 13.0833 | 7.2962 | 1.5901 | 7.4324 | 1.7009 | 21.79% | 22.89% | 35.0579 | 47.95 | 6.3726 | 10.1755 | 2027803.5 | 2010601 | 2498180.0324 | 80.48%
2023-05-18 | 2024 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 335090.89 | 6:07 | 19:15 | 11749.1 | 12189.1 | 12107.6 | 12002.3 | 12182.1 | 12163 | 12154.2 | 12397.1 | 12259.2 | 12161.9 | 11986.2 | 12189.5 | 11977.2 | 11992.2 | 12042.9 | 12034.1 | 11901.6 | 11881.9 | 11820.4 | 11940.4 | 11916.9 | 11887.5 | 11747.1 | 11819 | 11699.4 | 10607.3 | 11871.5 | 11593.9 | 11931.5 | 11831.3 | 11779.1 | 11835.7 | 12146.3 | 12060.1 | 12010.7 | 11942.8 | 12031.2 | 11971.6 | 11805.2 | 12137.3 | 12984.8 | 12103.4 | 12880 | 11942.9 | 12447.3 | 13272 | 11711.5 | 12892 | 11362.9 | 11645.7 | 12272.6 | 11753.4 | 12522.8 | 11388.9 | 12621.4 | 11569.3 | 11460.3 | 12679.8 | 11436.9 | 12556.5 | 12518.6 | 11367.8 | 12368 | 11903.5 | 12312.3 | 11767.6 | 12282 | 12659 | 12758.3 | 11951.2 | 12766.5 | 11463.4 | 12328.7 | 12288.1 | 11704.1 | 12711.4 | 11433.8 | 12853.7 | 11591.9 | 12513.3 | 12001 | 12451.2 | 12145.8 | 13080.8 | 12079.6 | 12668.7 | 11979.5 | 10711.9 | 12613.9 | 12313.4 | 11515.8 | 12757.6 | 12419.6 | 11635.7 | 11520.6 | 12454.5 | 11393.1 | 11869.1 | 12683.7 | 11565.6 | 12586.9 | 11495.8 | 12470.2 | 11757.8 | 12577.7 | 11204.6 | 12697.1 | 11681.8 | 12516.2 | 11623.7 | 12567.2 | 11741.1 | 11624.6 | 12446 | 11701.3 | 11511.5 | 12547.1 | 12282.8 | 12378.2 | 11593.7 | 12455.2 | 11301 | 12165.7 | 11551.4 | 12108.6 | 10741.2 | 12282.8 | 11447.6 | 11541.9 | 11722.1 | 11454.1 | 10011.7 | 11651.3 | 10405.8 | 11428.7 | 11448.9 | 13107.7 | 11914.2 | 13029.5 | 12048.8 | 13065 | 11732.6 | 11823.5 | 11586.5 | 12529.8 | 12797.4 | 12777.6 | 12708 | 12739.5 | 12791.2 | 11945 | 12855.7 | 12505.6 | 12593.9 | 12819 | 12807.6 | 12849.6 | 11863.3 | 12741.9 | 11876 | 33.5207 | 33.4603 | 33.3022 | 0 | 33.3604 | 33.7616 | 0 | 48.5 | 0 | 0 | 49.3 | 0 | 3.1204 | 3.128 | 3.0252 | 3.2475 | 3.1318 | 3.0596 | 7.191 | 6.187 | 6.864 | 6.389 | 6.617 | 6.306 | 7.2149 | 7.1864 | 7.3007 | 7.2613 | 7.2575 | 6.5235 | 1.255 | 1.69 | 1.6142 | 0 | 1.6511 | 1.4674 | 7.1982 | 6.9831 | 7.1423 | 7.3684 | 7.0773 | 7.6587 | 1.3449 | 1.7133 | 1.6555 | 0 | 1.6907 | 1.813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331180 | 591 | 320475 | 621 | 63989.205 | 131.6 | 7.2149 | 7.1864 | 7.3007 | 7.2613 | 7.2575 | 6.5235 | 7.1982 | 6.9831 | 7.1423 | 7.3684 | 7.0773 | 7.6587 | 960000 | 2000 | 961000 | 2000 | 1914867 | 4000 | 1917000 | 1910867 | 13.1333 | 7.1241 | 1.5356 | 7.238 | 1.6435 | 21.55% | 22.71% | 33.481 | 48.9 | 3.1187 | 6.5923 | 1930898.3 | 1914800 | 2422042.4355 | 79.06%
2023-05-19 | 2024 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 335090.89 | 6:03 | 19:17 | 12191 | 12645.8 | 12644.2 | 12588.7 | 12768.3 | 12777.2 | 12708.1 | 13023.7 | 12718.1 | 12584.8 | 12610.6 | 12750.7 | 12730.4 | 12635.3 | 12709.3 | 12766 | 12627.4 | 12737.1 | 12742.6 | 12815.8 | 12822.1 | 12798.8 | 12696.6 | 12764 | 12697.2 | 11353.9 | 12710.4 | 12583.3 | 12914.8 | 12798 | 12748.2 | 12872 | 12827.5 | 12743.3 | 12977.3 | 12888.4 | 12932 | 12876.1 | 12608 | 12814.9 | 13640 | 12748.1 | 13520.5 | 12547.9 | 13134.1 | 14069.1 | 12507.4 | 13600.4 | 12025.3 | 12276.1 | 12958.5 | 12414.7 | 13257.3 | 12134.7 | 13280.9 | 12216.7 | 12089.7 | 13334.5 | 11997.6 | 13223.7 | 13137.1 | 11951.4 | 12951.9 | 12433.6 | 12740.5 | 12079.9 | 12696.9 | 13019.2 | 13225.7 | 12242.4 | 13162.9 | 11787 | 12950 | 13153 | 12161 | 13315 | 11928 | 13318 | 12132 | 13120 | 12252.5 | 12850 | 12253.2 | 13298.5 | 12189 | 12796.2 | 12196.5 | 10747.1 | 12885.9 | 12534.6 | 11784.1 | 13163.8 | 12872.2 | 12137 | 12016.7 | 13020.4 | 11995.7 | 12271.3 | 13051.4 | 11704.9 | 13150.6 | 11753 | 12876.6 | 11984.9 | 12848.9 | 11395.7 | 12898 | 11854.9 | 12768.7 | 11845.1 | 12783.6 | 11985.1 | 11784.8 | 12646.9 | 11815.9 | 11633.8 | 12761.9 | 12651.5 | 12653 | 11965.6 | 12811.1 | 11638.3 | 12417.5 | 11860.7 | 12461.8 | 11067.7 | 12645.3 | 11846.6 | 11942.8 | 12148 | 11877.3 | 10324.3 | 11916.6 | 10571.3 | 11895.2 | 11918.2 | 13420.5 | 12133.4 | 13426.8 | 12328.2 | 13245.1 | 12097.8 | 12257.6 | 12091.8 | 13164 | 13473.8 | 13412.7 | 13362.6 | 13317.9 | 13299.9 | 12518.8 | 13433.1 | 13268.4 | 13416.3 | 13482.7 | 13435.8 | 13472.2 | 12488.9 | 13505.4 | 12550.3 | 37.415 | 37.5274 | 37.371 | 0 | 37.8214 | 37.6823 | 0 | 52.1 | 0 | 0 | 51.6 | 0 | 2.8918 | 2.8784 | 2.9295 | 2.9995 | 2.9044 | 2.8407 | 7.183 | 8.928 | 7.267 | 7.893 | 7.437 | 7.787 | 7.5599 | 7.7818 | 7.7339 | 7.4837 | 7.4035 | 5.2936 | 1.4161 | 1.7538 | 1.8065 | 0 | 1.6326 | 1.4864 | 7.5096 | 7.4622 | 7.5607 | 7.5996 | 7.1547 | 0 | 1.4972 | 1.7892 | 1.8443 | 0 | 1.6789 | 1.8475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332193 | 592 | 321466 | 622 | 65986.072 | 134.8 | 7.5599 | 7.7818 | 7.7339 | 7.4837 | 7.4035 | 5.2936 | 7.5096 | 7.4622 | 7.5607 | 7.5996 | 7.1547 | 0 | 1013000 | 1000 | 991000 | 1000 | 1996867 | 3200 | 2002000 | 1993667 | 13.2333 | 7.2094 | 1.6191 | 7.4573 | 1.7314 | 22.46% | 23.22% | 37.5634 | 51.85 | 2.9074 | 7.7492 | 2014710.8 | 1996800 | 2449233.4004 | 81.53%
2023-05-20 | 2024 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 335090.89 | 6:05 | 19:18 | 12491 | 12879.5 | 11646.6 | 11552.2 | 13065.5 | 13076.3 | 12879.8 | 13194.2 | 13021.7 | 12977.2 | 12914.8 | 13035.5 | 13031 | 12991.9 | 12935.5 | 12988.4 | 12961.9 | 13053.4 | 13006.9 | 13037.9 | 13078.2 | 13031.3 | 12898.6 | 12959.1 | 12886 | 11531.3 | 12918.2 | 12794.8 | 13112.9 | 13038 | 12956.5 | 13081.6 | 13080.4 | 13038.9 | 13140.5 | 13085.7 | 13153.8 | 13092.3 | 12930.6 | 13088.1 | 13706.7 | 12838.2 | 13601.7 | 12693.1 | 13247.2 | 14100.3 | 12646.6 | 13737.2 | 11995.9 | 12245.9 | 13206.3 | 12644.1 | 13430.9 | 12429.6 | 13408.1 | 12433.5 | 12274.8 | 13469.2 | 12301.5 | 13392.6 | 13362.9 | 12252 | 13168.3 | 12697.4 | 12924.6 | 12376.8 | 12816.6 | 13200.9 | 13390 | 12514 | 13344.9 | 12072.9 | 13104 | 12935 | 12356 | 13351 | 12101 | 13415 | 13414 | 13334 | 12585 | 13104.2 | 12667.9 | 13563.4 | 12591.9 | 13165.5 | 12588.6 | 11171.6 | 13281.3 | 12963.4 | 12232.3 | 13564.7 | 13311.8 | 12604.3 | 12518.9 | 13377.7 | 12384.2 | 12756.7 | 13511.6 | 12278.3 | 13531.6 | 12288 | 13307.7 | 12556.9 | 13384.3 | 11963.1 | 13438.8 | 12523.7 | 13294.6 | 12466.3 | 13368.1 | 12630.8 | 12379.1 | 13241.2 | 12454.2 | 12270.7 | 13330.6 | 13158.4 | 13261.5 | 12486.9 | 13328.8 | 12160.7 | 12966.2 | 12496.8 | 13053.4 | 11608.4 | 13129.2 | 12345.4 | 12376.8 | 12576.1 | 12386.5 | 10726.6 | 12377.9 | 10936.3 | 12395.3 | 12405 | 13703.7 | 12539.4 | 13704.3 | 12701.6 | 13608.7 | 12542.3 | 12706.4 | 12598.6 | 13369.2 | 13674.3 | 13639.8 | 13611.7 | 13594.9 | 13574 | 12746.5 | 13589.8 | 13502 | 13651.2 | 13668.1 | 13638.6 | 13660 | 12760.5 | 13684.3 | 12818.5 | 38.5476 | 38.3607 | 38.6808 | 0 | 36.3356 | 38.7677 | 50.8092 | 49.4732 | 48.5015 | 49.3397 | 0 | 0 | 5.758 | 5.6958 | 5.8713 | 5.6775 | 6.3196 | 5.6472 | 9.4717 | 9.694 | 9.833 | 9.43 | 7.98 | 9.191 | 7.5873 | 7.9283 | 7.8105 | 7.5861 | 0 | 6.9764 | 1.4025 | 1.8339 | 1.8168 | 0 | 0.56303 | 1.5585 | 7.6956 | 7.6256 | 7.6049 | 7.7052 | 0 | 8.1552 | 1.5018 | 1.8699 | 1.8624 | 0 | 0.64492 | 1.9328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333223 | 593 | 322495.5 | 624 | 68035.272 | 138.267 | 7.5873 | 7.9283 | 7.8105 | 7.5861 | 0 | 6.9764 | 7.6956 | 7.6256 | 7.6049 | 7.7052 | 0 | 8.1552 | 1030000 | 1000 | 1029500 | 2000 | 2049200 | 3467 | 2056500 | 2045733 | 13.2167 | 7.5777 | 1.435 | 7.7573 | 1.5624 | 18.94% | 20.14% | 38.1385 | 49.5309 | 5.8282 | 9.2666 | 2063690.3 | 2048134 | 2500856.139 | 81.9%
2023-05-21 | 2024 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 335090.89 | 6:04 | 19:16 | 12665.1 | 13069.9 | 11214 | 11155.9 | 13231.2 | 13245.9 | 13078.8 | 13380.7 | 13223.5 | 13172.3 | 13043.3 | 13145.9 | 13231.9 | 13164.2 | 13084.2 | 13115.8 | 13164.1 | 13235.1 | 13024.3 | 13163.6 | 13269.5 | 13238.1 | 12802 | 12849.4 | 12983.4 | 11736.8 | 13014.4 | 12903.5 | 13200.8 | 13131.2 | 13050.5 | 13174.4 | 13163.1 | 13159.7 | 13224.6 | 13178.4 | 13241.5 | 13183.8 | 13039.5 | 13176.3 | 13816.4 | 13033.2 | 13722.6 | 12883.4 | 13466.5 | 14188.4 | 12833.5 | 13824.4 | 12027.1 | 12317.7 | 13239.6 | 12744.6 | 13495 | 12583.1 | 13464.3 | 12580.7 | 12447.3 | 13527.4 | 12472.7 | 13456.6 | 13428.8 | 12430.6 | 13262.2 | 12826.8 | 13039.9 | 12537.4 | 12994.6 | 13343.2 | 13463.8 | 12658.2 | 13423.4 | 12277.7 | 13213.3 | 13049.2 | 12522.9 | 13432.8 | 12355 | 13543.3 | 12531.4 | 13414.2 | 12702.1 | 13191.8 | 12798.1 | 13621.2 | 12725.9 | 13275.4 | 12724.8 | 11369.1 | 13438 | 13126.9 | 12449.6 | 13729.6 | 13490.8 | 12832 | 12747.7 | 13559.3 | 12548.2 | 12888.4 | 13567.1 | 12448.6 | 13582.7 | 12463.7 | 13387.7 | 12701.1 | 13457.5 | 12185 | 13500.9 | 12666 | 13371.4 | 12613.7 | 13433.4 | 12763 | 12537.9 | 13345.7 | 12608.2 | 12452 | 13448.3 | 13306.4 | 13353.7 | 12655.7 | 13427.1 | 12372.4 | 13070.3 | 12648.9 | 13151.6 | 11842.8 | 13243.8 | 12536.3 | 12548.1 | 12723.2 | 12559.3 | 10936.4 | 12574.2 | 11203.6 | 12554.3 | 12563.1 | 13723.3 | 12667.9 | 13723.2 | 12828 | 13657.2 | 12714 | 12866.8 | 12749.2 | 13434.6 | 13689.8 | 13664.8 | 13634.9 | 13623.3 | 13609.3 | 12832.2 | 13585.4 | 13563.6 | 13669.2 | 13696 | 13670.5 | 13680.6 | 12883.7 | 13704.4 | 12929.3 | 31.4932 | 28.743 | 32.2954 | 0 | 29.3933 | 17.3492 | 36.059 | 35.2084 | 36.4024 | 37.0999 | 0 | 0 | 5.8309 | 5.3497 | 6.2137 | 5.6141 | 5.712 | 3.7397 | 11.966 | 11.206 | 11.844 | 10.831 | 11.421 | 11.006 | 7.9161 | 8.0287 | 7.9011 | 7.7423 | 7.8573 | 7.0909 | 1.4744 | 1.8615 | 1.8542 | 0 | 1.7916 | 1.5802 | 7.7964 | 7.7102 | 7.7453 | 7.796 | 7.5741 | 8.2877 | 1.5759 | 1.898 | 1.8975 | 0 | 1.8325 | 1.9588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334253 | 594 | 323525 | 625 | 70093.272 | 142.467 | 7.9161 | 8.0287 | 7.9011 | 7.7423 | 7.8573 | 7.0909 | 7.7964 | 7.7102 | 7.7453 | 7.796 | 7.5741 | 8.2877 | 1030000 | 1000 | 1029500 | 1000 | 2058000 | 4200 | 2057500 | 2053800 | 13.2 | 7.7561 | 1.7124 | 7.8183 | 1.8325 | 22.08% | 23.44% | 27.8548 | 36.1924 | 5.41 | 11.379 | 2081229 | 2057600 | 2614867.8407 | 78.69%
2023-05-22 | 2024 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 335090.89 | 6:08 | 19:15 | 12730.7 | 13182.7 | 13122.4 | 13076.4 | 13233 | 13249.5 | 13251.3 | 13589 | 13230.4 | 13171.7 | 13095.6 | 13213 | 13265.2 | 13183.5 | 13300.2 | 13321.7 | 13136.4 | 13267.3 | 13117 | 13284.2 | 13239.3 | 13295.8 | 13125.7 | 13156.3 | 13042.7 | 11796 | 13106.1 | 12968.1 | 13310.3 | 13190.9 | 13115.6 | 13213.7 | 13291.1 | 13247 | 13312.1 | 13310.9 | 13379.9 | 13209.4 | 13095.7 | 13304.6 | 13952.6 | 13080.9 | 13801.7 | 12940.2 | 13544.5 | 14465.2 | 12794.6 | 13927.6 | 12589.5 | 12837 | 13420.4 | 12872.4 | 13739.2 | 12665.1 | 13648.4 | 12719.2 | 12585 | 13745.3 | 12606.1 | 13694.4 | 13600.7 | 12524.4 | 13376.7 | 12927.2 | 13157.8 | 12605 | 13176.5 | 13533.8 | 13667.1 | 12735.2 | 13693.6 | 12426.3 | 13349.8 | 13250.3 | 12629.3 | 13576.1 | 12484.2 | 13764.5 | 12664.5 | 13574.5 | 12767.1 | 13290.1 | 12824.5 | 13807.9 | 12798.1 | 13409.9 | 12707.9 | 11457.1 | 13477.5 | 13115.5 | 12484.5 | 13794 | 13500.4 | 12810.8 | 12713.8 | 13552.5 | 12600.9 | 12993 | 13731.2 | 12514 | 13780.4 | 12538.3 | 13594 | 12828.2 | 13535.8 | 12251.5 | 13667.4 | 12725.2 | 13562.5 | 12708.7 | 13590.9 | 12938.5 | 12594 | 13438.1 | 12617.3 | 12518.3 | 13566.6 | 13344.8 | 13430.8 | 12748.9 | 13557.3 | 12451.7 | 13130.6 | 12774.3 | 13224.9 | 11920.1 | 13393.6 | 12674.6 | 12702.9 | 12806.2 | 12577.8 | 11011 | 12642.6 | 11263.2 | 12639.9 | 12639 | 13933.8 | 12734.6 | 13929.1 | 12943.4 | 13864 | 12757.8 | 12917.8 | 12823.5 | 13639.3 | 13890.8 | 13961.4 | 13885.1 | 13872 | 13848 | 13006.1 | 13878.4 | 13786.5 | 13877.6 | 13934.4 | 13938.1 | 13952.2 | 13020.2 | 13998 | 13080.2 | 36.1187 | 36.1114 | 35.9963 | 0 | 35.7729 | 36.4748 | 49.2718 | 48.0858 | 48.2685 | 49.0171 | 0 | 0 | 6.4662 | 6.5732 | 6.574 | 6.5241 | 6.3386 | 6.6838 | 11.0883 | 10.785 | 11.4283 | 10.8483 | 10.9817 | 11.6717 | 8.0195 | 8.1248 | 7.9893 | 7.8373 | 7.9408 | 7.1696 | 1.4863 | 1.8898 | 1.8623 | 0 | 1.8162 | 1.6075 | 7.8855 | 7.7889 | 7.8115 | 7.7925 | 7.6212 | 8.4114 | 1.5911 | 1.9247 | 1.9078 | 0 | 1.8583 | 1.9893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335303 | 595 | 324568 | 627 | 72179.806 | 146.4 | 8.0195 | 8.1248 | 7.9893 | 7.8373 | 7.9408 | 7.1696 | 7.8855 | 7.7889 | 7.8115 | 7.7925 | 7.6212 | 8.4114 | 1050000 | 1000 | 1043000 | 2000 | 2086534 | 3933 | 2090000 | 2082601 | 13.1167 | 7.8469 | 1.7324 | 7.8852 | 1.8542 | 22.08% | 23.52% | 36.0948 | 48.6608 | 6.5267 | 11.1339 | 2104292.1 | 2086401 | 2637767.7579 | 79.1%
2023-05-23 | 2024 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 335090.89 | 6:10 | 19:15 | 12022.1 | 12412.2 | 12385.3 | 12318.5 | 12446 | 12504.6 | 12460.9 | 12748.3 | 12416.9 | 12367.1 | 12294.1 | 12407.2 | 12468.7 | 12354.1 | 12474.6 | 12519.4 | 12380.4 | 12474 | 12433.9 | 12469.6 | 12473.5 | 12472.4 | 12319.6 | 12384.7 | 12234.3 | 11162.3 | 12296.5 | 12164 | 12474.4 | 12374.3 | 12331.7 | 12449.3 | 12420.3 | 12407 | 12493.6 | 12451 | 12525.1 | 12451.1 | 12262.8 | 12418.1 | 13095.1 | 12276.8 | 12992 | 12138.4 | 12675 | 13531.7 | 12023.2 | 13089 | 11789 | 11983.8 | 12562.5 | 12034.2 | 12858.5 | 11906.7 | 12760.2 | 11876.4 | 11737.1 | 12794.1 | 11803.9 | 12766.4 | 12701.6 | 11723 | 12469 | 12005.2 | 12238.1 | 11727.6 | 12207.3 | 12520 | 12681.4 | 11837.9 | 12646 | 11546.2 | 12416.5 | 12271.4 | 11732.7 | 12622 | 11607.3 | 12797.3 | 11756.3 | 12622.3 | 11887.9 | 12373.4 | 11922.7 | 12817.2 | 11864.7 | 12420.2 | 11824.2 | 10717.2 | 12526.5 | 12199.3 | 11609.6 | 12816.3 | 12544.7 | 11892.1 | 11804.3 | 12615.3 | 11727.1 | 12042.9 | 12776.2 | 11592.8 | 12796 | 11629.4 | 12600.7 | 11858 | 12615.7 | 11384.5 | 12695.5 | 11760.7 | 12571.4 | 11765.1 | 12603.9 | 11898.5 | 11651.7 | 12451.7 | 11703.8 | 11567.7 | 12566.9 | 12412.1 | 12450.3 | 11770 | 12554.5 | 11523.5 | 12157 | 11766.8 | 12245.5 | 11064.6 | 12378.2 | 11696.2 | 11686.4 | 11812.5 | 11629.3 | 10248.7 | 11630.3 | 10422.4 | 11711 | 11703.6 | 12881.5 | 11746.2 | 12896.6 | 11925 | 12800.6 | 11770.5 | 11910.4 | 11853 | 12617.9 | 12869.6 | 12912.3 | 12847.8 | 12819.1 | 12776.8 | 11998.6 | 12838 | 12792.2 | 12877.3 | 12887.4 | 12867.5 | 12875.7 | 12003.7 | 12988.1 | 12070.1 | 34.5213 | 35.0726 | 34.8778 | 0 | 34.7348 | 35.3348 | 48.4544 | 47.4351 | 47.1774 | 47.8244 | 0 | 0 | 5.7707 | 6.0368 | 5.8946 | 6.1168 | 5.925 | 6.1166 | 10.335 | 11.1267 | 12.2667 | 10.2517 | 11.06 | 10.715 | 7.4529 | 7.5341 | 7.4128 | 7.2156 | 7.2382 | 6.5606 | 1.347 | 1.7702 | 1.7006 | 0 | 1.6969 | 1.4818 | 7.3429 | 7.2692 | 7.277 | 7.2681 | 7.0088 | 7.6697 | 1.4413 | 1.7999 | 1.737 | 0 | 1.7245 | 1.8351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336285 | 596 | 325535 | 628 | 74122.406 | 150.6 | 7.4529 | 7.5341 | 7.4128 | 7.2156 | 7.2382 | 6.5606 | 7.3429 | 7.2692 | 7.277 | 7.2681 | 7.0088 | 7.6697 | 982000 | 1000 | 967000 | 1000 | 1942600 | 4200 | 1947000 | 1938400 | 13.0833 | 7.2357 | 1.5993 | 7.3059 | 1.7076 | 22.1% | 23.37% | 34.9083 | 47.7228 | 5.9768 | 10.9592 | 1959531.6 | 1942467 | 2453586.1385 | 79.17%
2023-05-24 | 2024 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 335090.89 | 6:03 | 19:16 | 12289.7 | 12761.6 | 12815 | 12724.9 | 12887.8 | 12908.1 | 12816.2 | 13253.5 | 12792.3 | 12739.5 | 12698 | 12883.9 | 12916 | 12848.5 | 12836.1 | 12934.3 | 12758.1 | 12881.3 | 12870.4 | 12897.9 | 12919.9 | 12900.7 | 12733.1 | 12808.5 | 12712.8 | 11239.2 | 12768.2 | 12597.9 | 12976.3 | 12846.8 | 12775.4 | 12956.2 | 12988 | 12978.8 | 13057.9 | 12999.7 | 13088.4 | 12977 | 12872.3 | 12976.7 | 13567.5 | 12537.1 | 13458.4 | 12355.8 | 13044.4 | 14049.5 | 12254.6 | 13580.7 | 12026.1 | 12291.7 | 13095.1 | 12394.3 | 13457.4 | 12155.3 | 13341.9 | 12134.8 | 11944.9 | 13396.5 | 12004.8 | 13316.4 | 13237.9 | 11927.5 | 13007.1 | 12425.5 | 12753.3 | 12033.9 | 12678.2 | 13136.5 | 13298.8 | 12203.5 | 13244.3 | 11719 | 12957.7 | 12761.7 | 12037.7 | 13256.5 | 11819.7 | 13426.2 | 12012.4 | 13214.2 | 12258.7 | 12920.4 | 12366.9 | 13478.8 | 12280 | 13019.8 | 12305.5 | 10862 | 13141.2 | 12761.1 | 11894.6 | 13498.6 | 13174.6 | 12316.3 | 12221.5 | 13262.8 | 12067.5 | 12524.2 | 13453.6 | 11927.5 | 13442.7 | 11943.1 | 13196.6 | 12257 | 13266.1 | 11611.8 | 13358.2 | 12210.5 | 13198 | 12173.4 | 13267 | 12382.4 | 12030.2 | 13122.4 | 12151.3 | 11934.5 | 13251.7 | 13069.4 | 13140.7 | 12211.8 | 13262.5 | 11868.5 | 12969.4 | 12211.5 | 11652.1 | 11310.6 | 13029.1 | 12102.5 | 11791.5 | 12010.1 | 11821.4 | 10226.6 | 11748.9 | 10379.5 | 11834.6 | 11822.1 | 13684.1 | 12252.4 | 13675.2 | 12472.1 | 13548.4 | 12249.9 | 12457.9 | 12357.2 | 13315 | 13634.6 | 13681.6 | 13642.1 | 13600.2 | 13556.1 | 12567 | 13617.8 | 13510.7 | 13631.8 | 13614.7 | 13588.5 | 13611.7 | 12525.7 | 13773.4 | 12626.1 | 36.1723 | 36.0536 | 35.6827 | 0 | 35.8718 | 36.4103 | 49.9677 | 48.713 | 48.7432 | 49.5714 | 0 | 0 | 6.3767 | 6.4313 | 6.4063 | 6.4126 | 6.3904 | 6.5389 | 10.785 | 11.7883 | 10.2233 | 10.83 | 11.71 | 10.6917 | 7.6002 | 7.769 | 7.5843 | 7.3345 | 7.6636 | 6.7209 | 1.3795 | 1.7567 | 1.7169 | 0 | 1.6909 | 1.4869 | 7.3411 | 7.3551 | 7.2753 | 7.3404 | 7.3706 | 8.1948 | 1.4986 | 1.781 | 1.7702 | 0 | 1.722 | 1.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337302.7 | 598.38 | 326541.56 | 630.434 | 76139.273 | 154.6 | 7.6002 | 7.769 | 7.5843 | 7.3345 | 7.6636 | 6.7209 | 7.3411 | 7.3551 | 7.2753 | 7.3404 | 7.3706 | 8.1948 | 1017700 | 2380 | 1006560 | 2434 | 2016867 | 4000 | 2019446 | 2012867 | 13.2167 | 7.4454 | 1.6062 | 7.4795 | 1.7224 | 21.57% | 23.03% | 36.0381 | 49.2488 | 6.426 | 11.0047 | 2034435.2 | 2016801 | 2501944.38 | 80.61%
2023-05-25 | 2024 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 335090.89 | 6:07 | 18:45 | 11357.6 | 11834.5 | 11865.4 | 11783.3 | 11948.1 | 11951.6 | 11896.3 | 12262.7 | 11818.6 | 11842.6 | 11723.7 | 11854.7 | 11809.3 | 11799 | 11908.8 | 11878.7 | 11808 | 11906.5 | 11878.4 | 11877.1 | 11933.5 | 11914.9 | 11715.7 | 11812.9 | 11706.9 | 10291.8 | 11709.3 | 11565.7 | 11971 | 11853.9 | 11766.3 | 11953.3 | 12042.8 | 12034.2 | 12024.7 | 12002 | 12101.2 | 11994.7 | 11461.4 | 12012.5 | 12684.7 | 11614.2 | 12586.5 | 11426.5 | 12163.5 | 13224.3 | 11362.3 | 12722.4 | 10996.9 | 11255.4 | 12010.3 | 11343.7 | 12374.4 | 11132.3 | 12314.9 | 11117.4 | 10962 | 12406.9 | 11001.8 | 12282.3 | 12221.2 | 10947.4 | 12069.2 | 11493.3 | 11832 | 11169 | 11772.6 | 12257.8 | 12377.7 | 11335.2 | 12349.5 | 10888.8 | 10712.7 | 10584.1 | 9909.6 | 10953.3 | 9756.7 | 11045.8 | 9902.3 | 10957 | 11387.8 | 12018.5 | 11533.8 | 12615.9 | 11417.7 | 12168.6 | 11389.3 | 10072.7 | 12324.9 | 11893.4 | 11060.8 | 12675.2 | 12355.3 | 11492.7 | 11389.7 | 12478.5 | 11281.5 | 11718.3 | 12679.9 | 11139.5 | 12657.3 | 11162.3 | 12382.3 | 11440.1 | 12436.9 | 10835.7 | 12522.4 | 11379 | 12350.1 | 11320.8 | 12416.3 | 11496.1 | 11265 | 12337.2 | 11317.5 | 11137.7 | 12453 | 12230 | 12312.9 | 11343.9 | 12389.1 | 10996 | 12136.6 | 11335.9 | 12000.3 | 10449 | 12120 | 11183.1 | 11264 | 11494.4 | 11218.8 | 9725.2 | 11326.6 | 9988.8 | 11281.9 | 11285.8 | 12845.2 | 11429.4 | 12837.9 | 11612.2 | 12737.6 | 11399 | 11607.4 | 11500 | 12439.8 | 12751.8 | 12763.9 | 12722.6 | 12719 | 12704 | 11681.6 | 12725.3 | 12621.4 | 12764.6 | 12798.8 | 12753.8 | 12777.3 | 11652.6 | 12842.3 | 11732.4 | 33.7959 | 34.9826 | 34.4831 | 0 | 34.8638 | 35.3396 | 46.6676 | 45.8563 | 46.152 | 46.6759 | 0 | 0 | 7.3292 | 7.6779 | 7.2157 | 7.823 | 7.5335 | 7.6443 | 12.5717 | 11.45 | 12.6267 | 12.0733 | 12.2117 | 13.6467 | 6.7698 | 6.9257 | 6.8449 | 6.6164 | 6.9343 | 6.0825 | 1.2779 | 1.6086 | 1.5944 | 0 | 1.5667 | 1.3722 | 6.5751 | 6.6114 | 6.6225 | 6.6575 | 6.7277 | 7.368 | 1.3888 | 1.6269 | 1.6432 | 0 | 1.6094 | 1.6924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338232 | 599 | 327484 | 631 | 78006.739 | 158.733 | 6.7698 | 6.9257 | 6.8449 | 6.6164 | 6.9343 | 6.0825 | 6.5751 | 6.6114 | 6.6225 | 6.6575 | 6.7277 | 7.368 | 929300 | 620 | 942440 | 566 | 1867466 | 4133 | 1870554 | 1863333 | 12.6333 | 6.6956 | 1.484 | 6.7604 | 1.5921 | 22.16% | 23.55% | 34.693 | 46.3379 | 7.5373 | 12.43 | 1882897.4 | 1867400 | 2293556.7919 | 81.42%
2023-05-26 | 2024 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 335090.89 | 6:05 | 19:17 | 11676.2 | 12293.1 | 12264.6 | 12153.4 | 12353.1 | 12314.3 | 12378 | 12724.4 | 12349.7 | 12346 | 12179.8 | 12344.3 | 12290.2 | 12253.6 | 12283.9 | 12321.8 | 12084 | 12269.8 | 12236 | 12151.4 | 12300.9 | 12171.3 | 12049.1 | 12155.7 | 12009.4 | 10599.3 | 12084.5 | 11907.1 | 12343 | 12213.4 | 12064.9 | 12252.1 | 12261.3 | 12256.8 | 12322.3 | 12249 | 12366.3 | 12260.1 | 12065.4 | 12250 | 13092 | 11956.7 | 12970.8 | 11796.8 | 12541.4 | 13587.1 | 11661.1 | 13053.2 | 11403.8 | 11690.4 | 12446 | 11761.3 | 12815.3 | 11473.4 | 12751.3 | 11451.9 | 11305.8 | 12516.6 | 11423.3 | 12828.1 | 12765.5 | 11382.8 | 12600.7 | 11987.2 | 12130.7 | 11399.8 | 12138.7 | 12560.5 | 12811.4 | 11608.3 | 12801 | 11192.3 | 12451.9 | 12252.5 | 11502 | 12759.9 | 11300.7 | 12967.1 | 11503.2 | 12722.5 | 11633.5 | 12311.1 | 11767.1 | 12925.8 | 11640.6 | 12424.8 | 11571 | 10212.9 | 12524.1 | 12019.4 | 11201.4 | 12873.8 | 12539.4 | 11627.1 | 11509.7 | 12611 | 11318 | 11733.3 | 12738.3 | 11162.5 | 12782.5 | 11185 | 12482.3 | 11494.1 | 12534.2 | 10869 | 12614.5 | 11412.1 | 12453.5 | 11381.6 | 12513 | 11554.6 | 11015.1 | 12140.1 | 11167 | 10931.7 | 11511.2 | 10545.5 | 12150.3 | 11188.8 | 12533 | 11087.9 | 12199.9 | 11401.3 | 12107.6 | 10587.3 | 12276.8 | 11296.3 | 11315.7 | 11525.1 | 11314.3 | 9770.3 | 11328.5 | 10006.6 | 11419.3 | 11433.3 | 12992.3 | 11496.9 | 13000.9 | 11717.4 | 12943.2 | 11581.6 | 11790.1 | 11666.9 | 12681.9 | 13050.9 | 13029.3 | 12967.6 | 12921.5 | 12867.3 | 11848.7 | 12992.9 | 12886 | 13035.3 | 13065.7 | 13037.5 | 13076.4 | 11864.8 | 13124.4 | 11919 | 35.1163 | 35.1163 | 34.9694 | 0 | 34.7994 | 35.4323 | 45.9228 | 45.062 | 44.9619 | 45.2606 | 0 | 0 | 8.3712 | 8.3712 | 7.9697 | 8.2274 | 7.9886 | 8.3453 | 12.8767 | 12.8767 | 13.1883 | 12.5533 | 13.4117 | 12.8033 | 7.1134 | 7.1134 | 7.0444 | 6.8581 | 6.9582 | 6.2134 | 1.5512 | 1.5512 | 1.5195 | 0 | 1.509 | 1.3319 | 6.8295 | 6.8295 | 6.7768 | 6.7952 | 6.7798 | 7.5215 | 1.5759 | 1.5759 | 1.5756 | 0 | 1.5395 | 1.6344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 339202 | 600 | 328435 | 633 | 79920.873 | 162.8 | 7.1134 | 7.1134 | 7.0444 | 6.8581 | 6.9582 | 6.2134 | 6.8295 | 6.8295 | 6.7768 | 6.7952 | 6.7798 | 7.5215 | 970000 | 1000 | 951000 | 2000 | 1914134 | 4067 | 1918000 | 1910067 | 13.2 | 6.8835 | 1.4926 | 6.9221 | 1.5803 | 21.68% | 22.83% | 35.0867 | 45.3018 | 8.2122 | 12.9517 | 1930247.1 | 1905467 | 2353175.9861 | 80.97%
2023-05-27 | 2024 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 335090.89 | 6:03 | 19:17 | 10120.1 | 10732.6 | 10790 | 10637.4 | 10877 | 10895.1 | 10892.1 | 11139.1 | 9834.5 | 4187.1 | 10672.3 | 10769 | 10848.1 | 10739.5 | 10958.9 | 10973.3 | 10891.7 | 10984.3 | 10891.4 | 10883.8 | 11025.5 | 10948.7 | 10910.5 | 10934.1 | 10673.2 | 9346.8 | 10656.9 | 10560.7 | 11026.4 | 11024.5 | 10877 | 10979 | 10887.1 | 10877.1 | 10886.7 | 10905.8 | 11037.3 | 10958 | 10808.3 | 10863.8 | 11531.9 | 10590 | 11453.9 | 10434.5 | 11044.1 | 11993.2 | 10293.8 | 11501 | 10015.8 | 10258.3 | 10874 | 10324 | 11200 | 10133.9 | 11166.5 | 10043.8 | 9919.6 | 11143.9 | 9980 | 11078.7 | 11039.8 | 9937.1 | 10754.3 | 10232 | 10493.8 | 9931.1 | 10483.2 | 10861.5 | 11034.3 | 10057.4 | 10961.1 | 9655.1 | 10707.5 | 10503.6 | 9903.7 | 10943.2 | 9681.4 | 11093.7 | 9838.8 | 10831.9 | 9972.9 | 10603.9 | 10092.6 | 11132.8 | 10062.5 | 10693.1 | 10072.6 | 8887.3 | 10950.3 | 10497.3 | 9840.1 | 11227.1 | 10918.7 | 10174.3 | 10116.7 | 11011.9 | 10032.2 | 10422.6 | 11277.3 | 9947.5 | 11193.9 | 9946 | 10986.5 | 10204.9 | 11106.4 | 9645.4 | 11189 | 10128.2 | 11027.3 | 10018 | 11148.2 | 10281.6 | 10034.8 | 11023.6 | 10140.2 | 9950.2 | 11081.4 | 10934.4 | 11002.1 | 10187.9 | 11115.4 | 9884.1 | 10824.7 | 10125.3 | 10756.7 | 9438 | 10890.2 | 10046.8 | 10028 | 10197.5 | 10042.5 | 8665.3 | 10074.8 | 8892.8 | 10043.8 | 10061.2 | 11292.7 | 10057.6 | 11404 | 10297.5 | 11336.6 | 10193 | 10359.6 | 10266.7 | 10992.9 | 11290.3 | 11252.4 | 11223.5 | 11185.3 | 11166.9 | 10335.2 | 11264.9 | 11014.5 | 11070.2 | 11250.5 | 11191.2 | 11236.2 | 10255.7 | 11300.8 | 10311.6 | 32.5569 | 34.2164 | 33.9347 | 0 | 34.0416 | 34.4891 | 46.9238 | 45.9123 | 45.8836 | 46.7232 | 0 | 0 | 5.2192 | 5.368 | 5.3103 | 5.3722 | 5.1716 | 5.4926 | 10.88 | 10.0933 | 11.2583 | 9.795 | 9.4883 | 10.2883 | 6.2156 | 6.4782 | 6.2838 | 6.0083 | 6.2637 | 5.4722 | 1.0581 | 1.4564 | 1.3173 | 0 | 1.3967 | 1.2006 | 6.129 | 6.2166 | 6.023 | 5.9468 | 6.1422 | 6.5941 | 1.1807 | 1.4822 | 1.3918 | 0 | 1.4305 | 1.4819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340047 | 602 | 329272 | 634 | 81598.273 | 166.933 | 6.2156 | 6.4782 | 6.2838 | 6.0083 | 6.2637 | 5.4722 | 6.129 | 6.2166 | 6.023 | 5.9468 | 6.1422 | 6.5941 | 845000 | 2000 | 837000 | 1000 | 1677400 | 4133 | 1679000 | 1673267 | 13.2333 | 6.1203 | 1.2858 | 6.1753 | 1.3934 | 21.01% | 22.56% | 33.8477 | 46.3607 | 5.3223 | 10.3006 | 1690630.7 | 1671000 | 2090820.2478 | 79.92%
2023-05-28 | 2024 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 335090.89 | 6:04 | 19:05 | 8228.7 | 8567.2 | 8540.2 | 8538 | 8587.8 | 8595.4 | 8615.8 | 8803.9 | 8574.7 | 7780.5 | 8523.1 | 8583.8 | 8657.1 | 8571.3 | 8654.1 | 8700.4 | 8565.5 | 8614.2 | 8619.9 | 8635.7 | 8653 | 8649.8 | 8530.5 | 8583.8 | 8469 | 7562 | 8498.3 | 8407.7 | 8649.6 | 8537.3 | 8490.2 | 8619 | 8589 | 8590.5 | 8795.7 | 8767.2 | 8660.1 | 8597.3 | 8503.6 | 8574.1 | 9068.2 | 8463.8 | 9004.3 | 8365.1 | 8744.1 | 9394.5 | 8279.5 | 9098.9 | 8079.4 | 8255.5 | 8689.6 | 8281.7 | 8905.9 | 8196 | 8837.1 | 8102.3 | 8004.6 | 8862.8 | 8081.9 | 8819.5 | 8765.8 | 8024.9 | 8589.3 | 8229.9 | 8398.9 | 7977.5 | 8359.3 | 8621.2 | 8735.9 | 8063.2 | 8681.5 | 7769 | 8542.3 | 8395.3 | 8003.4 | 8676.5 | 7819.7 | 8805.2 | 7947.3 | 8645.2 | 8024.2 | 8447.3 | 8113.1 | 8833.2 | 8072.5 | 8486.1 | 8059.8 | 7158.2 | 8628.8 | 8379.7 | 7926.3 | 8894.6 | 8718.4 | 8220.9 | 8166.6 | 8772.5 | 8113 | 8364.7 | 8926.8 | 8013.9 | 8951.6 | 8040 | 8810.8 | 8244.8 | 8842.4 | 7837.3 | 8900.5 | 8166.4 | 8825.6 | 8198.4 | 8899.5 | 8295.1 | 8038.1 | 8658.6 | 8141.2 | 7964 | 8781.4 | 8637.8 | 8693.4 | 8126.9 | 8752.9 | 7882.3 | 8605.7 | 8143.5 | 8557.6 | 7514.7 | 8581.8 | 7977.1 | 7987.5 | 8095.4 | 7928 | 6892.9 | 7941.1 | 6999.5 | 7888.4 | 7889.4 | 8829.1 | 7957.8 | 8834.7 | 8091.4 | 8759.7 | 7952.8 | 8063.9 | 8020 | 8559.2 | 8766.9 | 8749.3 | 8740.9 | 8737.6 | 8725.5 | 8125.3 | 8755.3 | 8626.6 | 8646.5 | 8752.9 | 8730.3 | 8763 | 8086.3 | 8799.1 | 8126.2 | 33.5918 | 33.5534 | 33.2762 | 0 | 33.3843 | 33.8031 | 46.3839 | 45.6795 | 45.3862 | 46.0974 | 0 | 0 | 5.2425 | 5.714 | 5.1526 | 5.7427 | 5.4253 | 5.5796 | 11.385 | 11.4067 | 11.295 | 11.4067 | 11.42 | 11.1483 | 4.9352 | 5.0061 | 4.9903 | 4.7881 | 4.924 | 4.1765 | 0.98468 | 1.0147 | 1.1776 | 0 | 0.99579 | 0.88383 | 4.7549 | 4.8346 | 4.8597 | 4.7514 | 4.7645 | 5.1032 | 1.0543 | 1.0305 | 1.2053 | 0 | 1.0353 | 1.0935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340723 | 603 | 329936 | 636 | 82934.34 | 171.8 | 4.9352 | 5.0061 | 4.9903 | 4.7881 | 4.924 | 4.1765 | 4.7549 | 4.8346 | 4.8597 | 4.7514 | 4.7645 | 5.1032 | 676000 | 1000 | 664000 | 2000 | 1336067 | 4867 | 1337000 | 1331200 | 13.0167 | 4.8034 | 1.0113 | 4.8447 | 1.0838 | 21.05% | 22.37% | 33.5218 | 45.8867 | 5.4761 | 11.3436 | 1347483.5 | 1335867 | 1641850.4162 | 81.36%
2023-05-29 | 2024 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 335090.89 | 6:00 | 19:19 | 11282 | 11810.1 | 11830.5 | 11761.9 | 11885.6 | 11867.1 | 11950.3 | 12228.3 | 11868.7 | 10715.1 | 11757.7 | 11893.8 | 11885.1 | 11837 | 11913.1 | 11967.5 | 11791.5 | 11858.8 | 11883.5 | 11846.5 | 11929.8 | 11921.8 | 11660.7 | 11779.5 | 11663.9 | 10356.7 | 11724.8 | 11554.3 | 11951.3 | 11820.6 | 11694.3 | 11894.3 | 11885.4 | 11932.4 | 12136.6 | 12051.9 | 11989.7 | 11898 | 11694.3 | 11808.6 | 12643.1 | 11491.5 | 12512.5 | 11293 | 12060.1 | 13296.5 | 11319.4 | 12656.3 | 11092.7 | 11340.8 | 12046.8 | 11400.7 | 12374.7 | 11192.5 | 12307.6 | 11112.5 | 11055.2 | 12434.2 | 11087.7 | 12364 | 12342.7 | 11051.6 | 12082.5 | 11527.5 | 11692.4 | 11061.7 | 11696.3 | 12114.2 | 12308.1 | 11283.5 | 12291.7 | 10898.1 | 11989.5 | 11816.8 | 11151.4 | 12322.7 | 10995.6 | 12494.2 | 11158.7 | 12305.9 | 11242.2 | 11925.3 | 11461.2 | 12493.2 | 11323.6 | 12011.2 | 11275.3 | 10005.1 | 12191.7 | 11672.5 | 10972.4 | 12517.3 | 12195 | 11345.3 | 11201 | 12271.7 | 11132.9 | 11511.5 | 12442.4 | 11033.4 | 12485.9 | 11033.1 | 12197 | 11300.7 | 12283.4 | 10735.6 | 12358.7 | 11242.1 | 12191.7 | 11211.7 | 12253.1 | 11355.3 | 11113.5 | 12160.1 | 11239.2 | 11011.5 | 12273.3 | 12124.1 | 12138.7 | 11310.3 | 12303.3 | 11002.2 | 11954 | 11223.1 | 11849.2 | 10472.6 | 12068.9 | 11203.2 | 11233.2 | 11429.3 | 11232.7 | 9734 | 11192.6 | 9957.1 | 11173.6 | 11235 | 12755.1 | 11324.2 | 12806.4 | 11563.1 | 12738.9 | 11458.4 | 11592.2 | 11450 | 12393.6 | 12792.4 | 12717.2 | 12678.2 | 12657.4 | 12633 | 11668 | 12725.4 | 12555.3 | 12573.8 | 12780.4 | 12704.3 | 12764.3 | 11621 | 12762.8 | 11642.9 | 28.403 | 28.2108 | 27.886 | 0 | 28.1652 | 28.4444 | 42.0817 | 41.9 | 42.3413 | 42.4838 | 0 | 0 | 3.2383 | 3.0448 | 3.0162 | 3.1247 | 3.1149 | 2.9565 | 9.365 | 9.2533 | 9.995 | 9.1283 | 10.4433 | 8.56 | 6.8314 | 6.965 | 6.8244 | 6.6711 | 6.8099 | 6.1055 | 1.0088 | 1.1793 | 1.1793 | 0 | 1.3677 | 1.2069 | 6.6644 | 6.6348 | 6.5004 | 6.553 | 6.6284 | 7.4005 | 1.1076 | 1.1986 | 1.2591 | 0 | 1.3853 | 1.4958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341662 | 605 | 330872 | 637 | 84802.073 | 175.867 | 6.8314 | 6.965 | 6.8244 | 6.6711 | 6.8099 | 6.1055 | 6.6644 | 6.6348 | 6.5004 | 6.553 | 6.6284 | 7.4005 | 939000 | 2000 | 936000 | 1000 | 1867733 | 4067 | 1872000 | 1863666 | 13.3167 | 6.7012 | 1.1884 | 6.7302 | 1.2893 | 17.73% | 19.16% | 28.2219 | 42.2017 | 3.0826 | 9.4575 | 1883715.4 | 1867733 | 2294822.47 | 81.39%
2023-05-30 | 2024 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 335090.89 | 6:21 | 19:26 | 1551.4 | 6094.7 | 6435.6 | 6374.9 | 6466.8 | 6452.2 | 6506.1 | 6774.7 | 6452.1 | 5607.6 | 6363 | 6460.8 | 6435.3 | 6423 | 6485 | 6509.1 | 4805 | 4834.8 | 4941.3 | 4847.1 | 4883.6 | 4866.3 | 4779.9 | 4820.6 | 6277.1 | 5521.4 | 6338.4 | 6215.7 | 6472.8 | 6402.2 | 6295.9 | 6236.7 | 6396.1 | 6415.5 | 6463.1 | 6401.5 | 6452.6 | 6394.1 | 6288.6 | 6378.4 | 6928.2 | 6177.8 | 6827.6 | 6061.5 | 6539.6 | 7403.1 | 6055.3 | 6949.4 | 5965.1 | 5908.6 | 6549 | 6124.7 | 6784.7 | 6025.4 | 6742.9 | 5984.8 | 5937.8 | 6832.1 | 5969.7 | 6768.9 | 6758.5 | 5955.7 | 6541.3 | 6186.8 | 6305 | 5925.1 | 6309.7 | 6580.7 | 6736.8 | 6049.6 | 6715.5 | 5825.9 | 6530.6 | 6388 | 5969.1 | 6737.2 | 5864.1 | 6846.2 | 5977 | 6715.2 | 5987.1 | 6437.5 | 6136.4 | 6804.8 | 6047.5 | 6494.3 | 6028.5 | 5319.2 | 6634.4 | 6310.5 | 5849.7 | 6837 | 6613.8 | 6073.5 | 5954.1 | 6681.8 | 5942.7 | 6168.2 | 6770.4 | 5871.9 | 6816.6 | 5867.4 | 6613.3 | 6041.9 | 6689.3 | 5708.4 | 6723.1 | 5999.3 | 6614.6 | 5996 | 6664.1 | 6069.3 | 5946.1 | 6611.6 | 6006.2 | 5877.7 | 6690.1 | 6587.3 | 6515.3 | 6030.3 | 6678.4 | 5851.1 | 6438.2 | 5982.2 | 6370.8 | 5562.8 | 6504.2 | 5907.2 | 5961.4 | 6080.8 | 5989.4 | 5157.9 | 5942.3 | 5251.9 | 5922.1 | 5995.1 | 6945.1 | 5991.6 | 6942.6 | 6091.8 | 6871.9 | 6029.6 | 6120.6 | 6080.9 | 6657.8 | 6933.1 | 6884.4 | 6853.6 | 6853.7 | 6846.4 | 6177.8 | 6877.6 | 6812.6 | 6822.7 | 6940.7 | 6905.2 | 6917 | 6160.5 | 6910.6 | 6170.2 | 24.0904 | 24.0427 | 23.7971 | 0 | 23.9145 | 24.1017 | 29.101 | 29.5595 | 29.465 | 28.9744 | 0 | 0 | 3.3923 | 3.2631 | 3.177 | 3.4147 | 3.398 | 3.2462 | 9.7733 | 9.72 | 9.7717 | 9.755 | 10.93 | 10.4383 | 3.3102 | 3.4315 | 3.3415 | 3.2412 | 3.2996 | 2.9297 | 0.3745 | 0.51363 | 0.44922 | 0 | 0.53845 | 0.49297 | 3.2489 | 3.2316 | 3.1441 | 3.152 | 3.2218 | 3.5521 | 0.42787 | 0.50314 | 0.48784 | 0 | 0.56223 | 0.59336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342153 | 606 | 331376 | 639 | 85793.54 | 180 | 3.3102 | 3.4315 | 3.3415 | 3.2412 | 3.2996 | 2.9297 | 3.2489 | 3.2316 | 3.1441 | 3.152 | 3.2218 | 3.5521 | 491000 | 1000 | 504000 | 2000 | 991467 | 4133 | 992000 | 987334 | 13.0833 | 3.2589 | 0.47375 | 3.2584 | 0.51489 | 14.54% | 15.8% | 23.9893 | 29.275 | 3.3152 | 10.0647 | 998000.2 | 991467 | 1169962.7306 | 84.74%
2023-05-31 | 2024 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 335090.89 | 5:53 | 19:29 | 11160.5 | 13047 | 13012 | 12971.1 | 13079.9 | 13072.6 | 13124.4 | 13504.4 | 13072.1 | 11855.2 | 12933.6 | 13080.5 | 13058.7 | 13004.6 | 13049.8 | 13109.3 | 12953.2 | 13036.3 | 13054.7 | 13096.5 | 13094.3 | 13088.2 | 12853.6 | 12956 | 12851.8 | 11416.4 | 12915.8 | 12748.8 | 13124.7 | 13000.9 | 12886.1 | 13085.1 | 13061.3 | 13074.7 | 13393.7 | 13299.3 | 13152.6 | 13046.4 | 12787.4 | 13021 | 13736.8 | 12681 | 13614.7 | 12487.9 | 13217 | 14341.8 | 12478.2 | 13749.8 | 12239 | 12249.5 | 13226.8 | 12590.4 | 13544.5 | 12358.9 | 13487.1 | 12294.5 | 12209.2 | 13619.6 | 12233.9 | 13536.5 | 13495.2 | 12191.2 | 13265.1 | 12706.9 | 12900.4 | 12205.7 | 12876.7 | 13261.8 | 13478 | 12422 | 13436.9 | 11953.7 | 13172.5 | 12977.6 | 12262.9 | 13446.3 | 12103 | 13655.9 | 12318.7 | 13448.7 | 12351.9 | 13053.1 | 12569.4 | 13608.1 | 12451.5 | 13137.8 | 12412.7 | 10966.4 | 13317.4 | 12837.6 | 12063.9 | 13644.1 | 13311.9 | 12484.6 | 12264.7 | 13405.5 | 12239.7 | 12643.4 | 13550.1 | 12102.7 | 13588.1 | 12101.5 | 13314.9 | 12421.6 | 13377.8 | 11753.2 | 13449.2 | 12336.9 | 13295.2 | 12303.6 | 13325.8 | 12457.4 | 12175.3 | 13261 | 12342.5 | 12078.8 | 13372.4 | 13219.7 | 13231.8 | 12349.4 | 13332.8 | 11975.2 | 13053.2 | 12287.6 | 12947.2 | 11405.5 | 13115 | 12081.4 | 12244.8 | 12472.6 | 12236.8 | 10593.8 | 12209.3 | 10784.4 | 12095.3 | 12227.5 | 13741.8 | 12325.3 | 13742 | 12548.2 | 13684.3 | 12439.2 | 12601.9 | 12471.9 | 13380.2 | 13747.6 | 13708.1 | 13667 | 13641.2 | 13608 | 12654.2 | 13680.6 | 13596.1 | 13600.2 | 13769.1 | 13735.5 | 13750.8 | 12646.9 | 13745.7 | 12696.7 | 29.1704 | 29.8408 | 29.6183 | 0 | 30.1619 | 30.2589 | 44.0989 | 43.0652 | 43.5794 | 44.0364 | 0 | 0 | 3.7027 | 3.7643 | 3.6757 | 3.6054 | 3.735 | 3.6461 | 7.295 | 7.085 | 7.5683 | 7.725 | 7.5517 | 7.6283 | 7.5815 | 7.7816 | 7.6163 | 7.4359 | 7.6151 | 6.6561 | 1.2427 | 1.447 | 1.4687 | 0 | 1.5261 | 1.337 | 7.2538 | 7.3657 | 7.2455 | 7.274 | 7.2678 | 7.9121 | 1.338 | 1.455 | 1.517 | 0 | 1.5522 | 1.6574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343183 | 608 | 332395 | 641 | 87834.874 | 184.133 | 7.5815 | 7.7816 | 7.6163 | 7.4359 | 7.6151 | 6.6561 | 7.2538 | 7.3657 | 7.2455 | 7.274 | 7.2678 | 7.9121 | 1030000 | 2000 | 1019000 | 2000 | 2041334 | 4133 | 2045000 | 2037201 | 13.6 | 7.4477 | 1.4043 | 7.3865 | 1.5039 | 18.86% | 20.36% | 29.81 | 43.695 | 3.6882 | 7.4756 | 2059028.3 | 2041201 | 2512836.4304 | 81.23%
2023-06-01 | 2024 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 335090.89 | 6:05 | 19:23 | 7689.6 | 8077.1 | 8185.5 | 8091 | 8291.9 | 8265.4 | 8155.7 | 8424.1 | 7971.9 | 7901.1 | 7910.7 | 7985.8 | 8077.7 | 8021.1 | 8218.2 | 8126 | 8173.3 | 8238.7 | 7535.9 | 7251 | 8170.3 | 8073.6 | 8090.3 | 8123.9 | 7869 | 6930.2 | 7866.9 | 7780.8 | 8138.9 | 8143.1 | 8099.1 | 8049.4 | 8111.8 | 8091.2 | 8136.5 | 8085 | 8205.7 | 8135 | 8077 | 8184.1 | 9155.9 | 8263.6 | 9078.8 | 8142.2 | 8578.3 | 9502.1 | 7933.2 | 9119.6 | 7402.5 | 7323.4 | 8179.8 | 7615.1 | 8463.9 | 7554.3 | 8415.3 | 7569.7 | 7350.3 | 8409 | 7367.9 | 8274.6 | 8246.9 | 7324.7 | 8005 | 7565.2 | 7806.1 | 7407.2 | 7813 | 8184.1 | 8301.5 | 7498.2 | 8203.9 | 7172.3 | 7987.2 | 7795.7 | 7266.5 | 8163.1 | 7147.5 | 8271.2 | 7257.7 | 8093 | 7469.6 | 7967.7 | 7598.5 | 8452.9 | 7513.9 | 8048.3 | 7491.9 | 6659.2 | 8262.7 | 7901.3 | 7294.4 | 8446.5 | 8143.2 | 7516 | 7393.5 | 8171.1 | 7281.2 | 7641.1 | 8347.9 | 7316.8 | 8347.9 | 7297.2 | 8124.2 | 7485.6 | 8212.7 | 7077.1 | 8286.4 | 7448.3 | 8196.8 | 7454.9 | 8249.5 | 7583.1 | 7397.6 | 8139 | 7478.4 | 7313.6 | 8254.6 | 8116.2 | 8136.2 | 7497.6 | 8244.7 | 7273.2 | 7978.6 | 7457.3 | 7903.1 | 6934.3 | 8063.5 | 7380.3 | 7408.5 | 7488.5 | 7413.5 | 6420.4 | 7401.2 | 6582.2 | 7352.7 | 7393.1 | 8551.1 | 7422.2 | 8496 | 7523.3 | 8395.4 | 7378.6 | 7507.2 | 7412.5 | 8158.5 | 8425 | 8190.5 | 8159.3 | 8406.1 | 8400.6 | 7579.6 | 8379.4 | 8306.5 | 8312.2 | 8453 | 8395.2 | 8388.1 | 7547.4 | 8426.7 | 7604.3 | 28.7948 | 30.5996 | 30.0511 | 0 | 30.5391 | 30.9796 | 39.0902 | 38.5736 | 38.5422 | 39.0144 | 46.8549 | 0 | 4.6194 | 4.5629 | 4.3753 | 4.6417 | 4.6564 | 4.474 | 7.419 | 7.699 | 8.009 | 7.606 | 7.383 | 7.669 | 4.4771 | 4.657 | 4.7296 | 4.3004 | 4.4233 | 3.8812 | 0.71492 | 1.0414 | 0.91463 | 0 | 0.99406 | 0.88 | 4.4003 | 4.4183 | 4.4932 | 4.2173 | 4.3192 | 4.656 | 0.80161 | 1.036 | 0.96625 | 0 | 1.0156 | 1.0685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343821 | 609 | 333016 | 642 | 89090.274 | 188.267 | 4.4771 | 4.657 | 4.7296 | 4.3004 | 4.4233 | 3.8812 | 4.4003 | 4.4183 | 4.4932 | 4.2173 | 4.3192 | 4.656 | 638000 | 1000 | 621000 | 1000 | 1255400 | 4134 | 1257000 | 1251266 | 13.3 | 4.4114 | 0.90901 | 4.4174 | 0.97759 | 20.61% | 22.13% | 30.1928 | 40.4151 | 4.555 | 7.6308 | 1263691.4 | 1250734 | 1522696.2722 | 82.14%
2023-06-02 | 2024 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 335090.89 | 6:08 | 19:29 | 11263.5 | 11747.2 | 12006.2 | 11902.4 | 12186.6 | 12167.5 | 11947.3 | 12182.9 | 11549.2 | 11399.9 | 11463.9 | 11508.7 | 11744 | 11592.7 | 12003 | 11852 | 11927.5 | 11922.9 | 11603.1 | 11605.7 | 11759 | 11661.2 | 11501.5 | 11622 | 11116.1 | 9820.5 | 11223 | 11118.2 | 11598.2 | 11576.2 | 11502.9 | 11494.5 | 11394.2 | 11390.8 | 11448.2 | 11406.5 | 11599.7 | 11590.5 | 11377.4 | 11560.5 | 12988.5 | 11980 | 12887.2 | 11773.7 | 12381.9 | 13214 | 11587 | 12957.2 | 10619.7 | 10519.9 | 11663.2 | 10797.7 | 11984.5 | 10966 | 11775.6 | 10691.3 | 10417.6 | 11695.5 | 10502.3 | 11511 | 11472.1 | 10449.2 | 11297.7 | 10807.7 | 10979.5 | 10528.8 | 11036.3 | 11504.7 | 11614.1 | 10686.1 | 11396.6 | 10237.7 | 11270.8 | 10993.9 | 10410.2 | 11392.5 | 10160.8 | 11696 | 10410.8 | 11372.8 | 10929.2 | 11450.4 | 11098.3 | 11998.2 | 10967 | 11638.8 | 10764.2 | 9702.7 | 11984.6 | 11466.3 | 10717.5 | 12137.2 | 11674.2 | 10842.7 | 10733 | 11777.8 | 11007 | 11543.5 | 12460.9 | 11107.5 | 12319.7 | 11039.8 | 12132.1 | 11318.9 | 12258.4 | 10729.6 | 12398.9 | 11335.9 | 12225.6 | 11311.1 | 12333.7 | 11567.3 | 11326.8 | 12288.7 | 11319.3 | 11084.6 | 12328.8 | 12247.8 | 12202.6 | 11441.2 | 12428.6 | 11127.5 | 12058 | 11380.1 | 12017.9 | 10622.1 | 12275.3 | 11395.8 | 11457.9 | 11653.6 | 11411.4 | 9879.2 | 11540.3 | 10245.9 | 11240.8 | 11245.2 | 12753.5 | 11500.8 | 12562.3 | 11542.2 | 12604.4 | 11315 | 11456 | 11394 | 11920.8 | 12185.8 | 12193.3 | 12229.6 | 12383.8 | 12452.9 | 11392.8 | 12257.9 | 11971.7 | 11861.8 | 11953.2 | 11933.7 | 12012 | 11040.5 | 12144.9 | 11091.3 | 33.2307 | 33.2422 | 32.3941 | 0 | 33.7651 | 33.6637 | 47.7139 | 46.7329 | 48.0431 | 48.4171 | 0 | 0 | 3.4842 | 3.456 | 3.3887 | 3.3753 | 3.4321 | 3.3296 | 6.573 | 6.541 | 6.92 | 7.274 | 6.955 | 6.514 | 6.866 | 6.9395 | 7.2497 | 6.3888 | 7.0628 | 6.02 | 1.1865 | 1.6142 | 1.5122 | 0 | 1.5806 | 1.3104 | 6.6602 | 6.6109 | 6.9326 | 6.3283 | 6.8364 | 7.2117 | 1.2992 | 1.6284 | 1.5671 | 0 | 1.6031 | 1.6076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 344122 | 610 | 333940 | 643 | 90920.54 | 192.467 | 6.866 | 6.9395 | 7.2497 | 6.3888 | 7.0628 | 6.02 | 6.6602 | 6.6109 | 6.9326 | 6.3283 | 6.8364 | 7.2117 | 301000 | 1000 | 924000 | 1000 | 1830266 | 4200 | 1223000 | 1826066 | 13.35 | 6.7544 | 1.4408 | 6.7634 | 1.5411 | 21.33% | 22.79% | 33.2591 | 47.7268 | 3.411 | 6.7962 | 1845315 | 1823866 | 2270575.4247 | 80.33%
2023-06-03 | 2024 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 335090.89 | 6:01 | 19:22 | 11404.7 | 11882.6 | 11851.9 | 11838.1 | 12004.2 | 12048.3 | 12047.1 | 12393 | 11857.5 | 11626.4 | 11830.2 | 11894.4 | 12129.4 | 11960.4 | 12127.8 | 12233.3 | 12039 | 12147.3 | 12119.6 | 12105.6 | 12274.2 | 12202.7 | 12102 | 12202 | 11958.9 | 10466.6 | 11916.7 | 11857.2 | 12342.1 | 12333.9 | 12255.3 | 12312.7 | 12275.9 | 12299.1 | 12343.2 | 12286.1 | 12414.3 | 12383.1 | 12315.2 | 12389.8 | 12729.3 | 11668.8 | 12635.8 | 11536.1 | 12128 | 13240.8 | 11340.6 | 12802.5 | 11071.5 | 11035.2 | 12210.8 | 11375.2 | 12591 | 11263.2 | 12425.1 | 11252.8 | 10997.9 | 12326.8 | 11025.7 | 12277.9 | 12233.3 | 10991.1 | 11831.4 | 11231 | 11556.3 | 10937.5 | 11578.9 | 12025 | 12210.2 | 11102.9 | 12101 | 10631.1 | 11899.1 | 11593.1 | 10962.6 | 12045.9 | 10683.7 | 12269.2 | 10865.9 | 11986 | 11137.8 | 11948.4 | 11095.7 | 12371.4 | 11062.2 | 11718.6 | 11008 | 9732.9 | 11896.3 | 11578.8 | 10728.6 | 12333.3 | 12113.8 | 11350 | 11344.4 | 12088.7 | 10915.9 | 11353.1 | 12304.7 | 10836.5 | 12470.8 | 10866.5 | 12244.7 | 11179.1 | 12392.4 | 10647.2 | 12435.9 | 11215.9 | 12250.2 | 11173.2 | 12200.3 | 11363.9 | 10903.7 | 11922.3 | 11095.7 | 10827.3 | 12164.8 | 11876.5 | 12014.4 | 11015.7 | 12031.8 | 10669 | 11931.5 | 11166.4 | 11780.6 | 10161.5 | 11764.3 | 10910.8 | 10709.9 | 10764.4 | 10846.8 | 9312.8 | 10605.9 | 9387 | 10656.9 | 10726.9 | 12614.7 | 11164.6 | 12754.8 | 11397.8 | 12413 | 11077.6 | 11179.1 | 10970.8 | 12561.1 | 12931.5 | 12801.9 | 12754.5 | 12642.1 | 12556.4 | 11695.4 | 12791.8 | 12666.2 | 12657.3 | 12765.1 | 12735.8 | 12838.9 | 11754.7 | 12794.8 | 11818.6 | 34.2478 | 35.3861 | 35.183 | 0 | 35.3875 | 35.7512 | 49.4406 | 48.1094 | 47.9988 | 48.8556 | 0 | 0 | 3.7103 | 3.7977 | 3.5968 | 3.8218 | 3.7746 | 3.7861 | 8.17 | 7.233 | 8.528 | 7.018 | 6.541 | 8.258 | 6.9984 | 7.3421 | 7.0779 | 6.7416 | 6.9812 | 6.2177 | 1.2803 | 1.7613 | 1.5314 | 0 | 1.5301 | 1.3713 | 6.7152 | 6.9337 | 6.7165 | 6.6209 | 6.6104 | 7.5121 | 1.4053 | 1.7871 | 1.5889 | 0 | 1.5727 | 1.6823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345680 | 612 | 334864 | 645 | 92786.141 | 196.533 | 6.9984 | 7.3421 | 7.0779 | 6.7416 | 6.9812 | 6.2177 | 6.7152 | 6.9337 | 6.7165 | 6.6209 | 6.6104 | 7.5121 | 1558000 | 2000 | 924000 | 2000 | 1865601 | 4066 | 2478000 | 1861535 | 13.35 | 6.8931 | 1.4949 | 6.8515 | 1.6073 | 21.69% | 23.46% | 35.1911 | 48.6011 | 3.7479 | 7.6247 | 1880086.6 | 1865534 | 2294684.4306 | 81.3%
2023-06-04 | 2024 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 335090.89 | 6:09 | 19:23 | 12116.1 | 12623.3 | 12518.6 | 12464.3 | 12647.8 | 12641 | 12717.8 | 13094.7 | 12660.7 | 12632.1 | 12521.9 | 12659.8 | 12641.7 | 12589.5 | 12655 | 12708.7 | 12521.2 | 12588.8 | 12596.7 | 12553.2 | 12642.9 | 12636.6 | 12330 | 12501.6 | 12376.8 | 11035.8 | 12458.9 | 12270 | 12657.6 | 12558.9 | 12424.6 | 12569 | 12617.3 | 12583.6 | 12871.8 | 12797.4 | 12704.1 | 12597.1 | 12483.8 | 12582.8 | 13257.4 | 12187.6 | 13122.4 | 11995.1 | 12604.1 | 13887.4 | 12009.2 | 13283.6 | 11753.7 | 12009.7 | 12798.4 | 12160.7 | 13118.5 | 11947.8 | 13053.1 | 11865.5 | 11794.4 | 13168.8 | 11859.9 | 13091.8 | 13063.3 | 11814.2 | 12810.1 | 12275.4 | 12434 | 11767.8 | 12423.8 | 12802.5 | 13032.2 | 11957.1 | 12996.3 | 11551.1 | 12744.5 | 12536.1 | 11907.8 | 13018.5 | 11717.5 | 13236.3 | 11917 | 13032.8 | 11957.6 | 12794.5 | 12089.4 | 13133.3 | 11983.6 | 12683.8 | 11955.1 | 10612.1 | 12891.1 | 12458.3 | 11684.2 | 13214.5 | 12875.2 | 12057.2 | 11921.3 | 12899.9 | 11796.9 | 12198.1 | 13110.7 | 11706.5 | 13151.8 | 11716.6 | 12741.4 | 11982 | 12953.5 | 11391.3 | 13021.7 | 11908.3 | 12871.4 | 11899.9 | 12944.9 | 12046 | 11778.5 | 12826.8 | 11911.7 | 11680 | 12887.3 | 12741.9 | 12800 | 11950.6 | 12923.9 | 11630 | 12621 | 11878.8 | 12523.6 | 11106.2 | 12707.5 | 11775.6 | 11876.3 | 12075 | 11899.2 | 10310.2 | 11859.1 | 10516.7 | 11898.3 | 11914 | 13319.7 | 11928.6 | 13336.6 | 12146.3 | 13276.8 | 12038.4 | 12203.1 | 12126.3 | 12975.2 | 13328.9 | 13280.6 | 13241.1 | 13213.6 | 13254.4 | 12248.9 | 13269 | 13271.8 | 13153.6 | 13347.7 | 13307.5 | 13318 | 12218.6 | 13366.9 | 12080.2 | 26.4987 | 30.5411 | 30.4813 | 0 | 30.7899 | 30.9543 | 41.5227 | 41.6653 | 42.2016 | 41.4793 | 0 | 0 | 4.2401 | 4.3035 | 4.147 | 4.3663 | 4.2872 | 4.3127 | 7.708 | 8.261 | 7.152 | 7.794 | 8.396 | 8.072 | 7.3052 | 7.4578 | 7.2651 | 7.105 | 7.2789 | 6.3794 | 1.1136 | 1.4189 | 1.3085 | 0 | 1.4678 | 1.2674 | 7.0741 | 7.044 | 6.9302 | 6.9546 | 6.9731 | 7.8015 | 1.2144 | 1.4225 | 1.3627 | 0 | 1.5029 | 1.5543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346677 | 613 | 335851 | 646 | 94762.941 | 200.533 | 7.3052 | 7.4578 | 7.2651 | 7.105 | 7.2789 | 6.3794 | 7.0741 | 7.044 | 6.9302 | 6.9546 | 6.9731 | 7.8015 | 997000 | 1000 | 987000 | 1000 | 1976800 | 4000 | 1982000 | 1972800 | 13.2333 | 7.1319 | 1.3152 | 7.1296 | 1.4114 | 18.44% | 19.8% | 29.8531 | 41.7172 | 4.2762 | 7.8972 | 1993857 | 1976800 | 2428621.0889 | 81.4%
2023-06-05 | 2024 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 335090.89 | 6:08 | 19:03 | 11369.5 | 11837.9 | 11713 | 11708.3 | 11864.4 | 11873.8 | 11881.9 | 12265.2 | 11925 | 11896.8 | 11734 | 11893.3 | 11831.6 | 11785.3 | 11796 | 11884.7 | 11672.5 | 11729.6 | 11750.7 | 11810.2 | 11779.5 | 11772.9 | 11475.9 | 11639.4 | 11529.4 | 10159.5 | 11623.9 | 11428.1 | 11797.4 | 11654.5 | 11564.8 | 11709.9 | 11872.2 | 11769.3 | 11935.6 | 11848.9 | 11881.4 | 11770 | 11596.6 | 11817 | 12619.2 | 11495.7 | 12438.3 | 11271.2 | 11802.3 | 12961.4 | 11212.7 | 12615.2 | 10942.7 | 11222.9 | 11935.7 | 11291.5 | 12246.2 | 11013.9 | 12245.1 | 10889.7 | 10934.5 | 12374.4 | 10985.7 | 12328.9 | 12299.9 | 10960.6 | 12074.8 | 11471.3 | 11726.5 | 10977.7 | 11679.6 | 12082.5 | 12274.6 | 11134.2 | 12229.4 | 10679.7 | 11967.8 | 11717 | 11031.1 | 12145.1 | 10820 | 12428.9 | 10969 | 12186.5 | 11130.4 | 12014.2 | 11223.7 | 12409.6 | 11147.7 | 11899.1 | 11180.7 | 9835.2 | 12030.7 | 11697.8 | 10840.8 | 12481.6 | 12174.2 | 11294.1 | 11178.7 | 12258.5 | 10991.5 | 11448.6 | 12449.9 | 10919.8 | 12540 | 10962.6 | 12169.5 | 11222.5 | 12374 | 10671.3 | 12443.7 | 11227.9 | 12277.4 | 11223.4 | 12226 | 11382.6 | 10949.1 | 12086.3 | 11149.6 | 10864.9 | 12276 | 12129.9 | 12144.6 | 11211.7 | 12308.8 | 10883.7 | 11994.8 | 11177.3 | 11901.1 | 10373.8 | 12076.9 | 11004 | 11058.5 | 11236.1 | 11098.9 | 9578.1 | 10988.1 | 9667.7 | 10891.5 | 10910.4 | 12381.6 | 10953.3 | 12398.3 | 11186.7 | 12352.8 | 11054.4 | 11242.9 | 11112.1 | 11957.5 | 12299.5 | 12318.8 | 12282.2 | 12274.4 | 12302.1 | 11244.5 | 12292.1 | 12229.9 | 12095.3 | 12245.6 | 12215.2 | 12254.5 | 11133 | 12393.1 | 11037.9 | 32.7045 | 34.2455 | 33.7827 | 0 | 34.3055 | 34.6263 | 48.7445 | 47.5461 | 48.1699 | 49.0756 | 0 | 0 | 2.538 | 2.6245 | 2.4845 | 2.6875 | 2.7012 | 2.6369 | 6.518 | 6.378 | 6.79 | 7.978 | 6.937 | 6.272 | 6.887 | 6.9086 | 6.9188 | 6.7504 | 7.013 | 5.8696 | 1.2519 | 1.4225 | 1.4691 | 0 | 1.3977 | 1.1816 | 6.5688 | 6.5585 | 6.4419 | 6.6742 | 6.6872 | 0 | 1.3435 | 1.4351 | 1.4957 | 0 | 1.4532 | 1.4552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347608 | 614 | 336773 | 648 | 96609.741 | 204.667 | 6.887 | 6.9086 | 6.9188 | 6.7504 | 7.013 | 5.8696 | 6.5688 | 6.5585 | 6.4419 | 6.6742 | 6.6872 | 0 | 931000 | 1000 | 922000 | 2000 | 1846800 | 4134 | 1850000 | 1842666 | 12.9167 | 6.7246 | 1.3445 | 6.5861 | 1.4365 | 19.99% | 21.81% | 33.9329 | 48.384 | 2.6121 | 6.8122 | 1863080.5 | 1840333 | 2198614.9096 | 83.7%
2023-06-06 | 2024 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 335090.89 | 6:02 | 19:30 | 12171.2 | 12587.7 | 12465.1 | 12466.6 | 12633.8 | 12639.4 | 12652.4 | 12967.3 | 12618.9 | 12538.1 | 12483.8 | 12598.9 | 12656.2 | 12545.6 | 12564.6 | 12669.8 | 12523.6 | 12614 | 12621.3 | 12673 | 12670.2 | 12660.1 | 12456.7 | 12556 | 12455.4 | 11031.9 | 12507.6 | 12342.9 | 12701 | 12550.3 | 12501.8 | 12660.3 | 12589.3 | 12662.3 | 12885.7 | 12756.1 | 12668.2 | 12601.8 | 12320 | 12580.7 | 13385.3 | 12366.3 | 13298.3 | 12184.9 | 12618.7 | 13798.8 | 12130.8 | 13396.4 | 11794.4 | 12067.8 | 12802.6 | 12137.9 | 13101.6 | 11867.6 | 13052.9 | 11838.4 | 11748.9 | 13109.4 | 11794.3 | 13064.9 | 13019.8 | 11745.1 | 12718 | 12157.1 | 12456.9 | 11765.6 | 12455.9 | 12862.9 | 13044.2 | 11991.9 | 12986.5 | 11510.3 | 12715.5 | 12514.6 | 11835.4 | 12989.1 | 11625.7 | 13178.3 | 11797.8 | 12965.8 | 12071.7 | 12927.7 | 12184.3 | 13282.6 | 12069.4 | 12778.3 | 12083.6 | 10676.2 | 12911.6 | 12564.5 | 11680 | 13263 | 12901.8 | 12033.5 | 11884.1 | 12937.3 | 11716 | 12219 | 13165.6 | 11682.8 | 13257.9 | 11741.4 | 13020.3 | 11992.5 | 13089.1 | 11421 | 13162.2 | 11961.8 | 13026.6 | 11923.9 | 13054.6 | 12127.9 | 11732.4 | 12798.4 | 11888.7 | 11573.6 | 12980.3 | 12837.9 | 12854.2 | 12039.3 | 13034.4 | 11672 | 12739.6 | 11931 | 12632 | 11129.8 | 12840.4 | 11850.4 | 11818.1 | 11919.4 | 11786.6 | 10209.8 | 11731.8 | 10434.7 | 11657.1 | 11701 | 13448 | 12068.4 | 13469.1 | 12303.3 | 13404.8 | 12178.4 | 12344.8 | 12108.2 | 13015.8 | 13444.7 | 13403 | 13362 | 13352.4 | 13388.1 | 12371.2 | 13399.7 | 13357.7 | 13276.1 | 13341.5 | 13354.9 | 13430.1 | 12326.2 | 13451.6 | 12182.8 | 31.8122 | 33.11 | 32.7309 | 0 | 33.2277 | 33.5273 | 47.635 | 46.763 | 47.0042 | 47.7831 | 0 | 0 | 4.1605 | 4.4493 | 3.9084 | 4.6247 | 4.5338 | 4.2816 | 11.934 | 13.629 | 12.037 | 10.798 | 9.845 | 10.211 | 7.4872 | 7.6217 | 7.5644 | 7.3355 | 7.5572 | 6.5602 | 1.3553 | 1.7057 | 1.6615 | 0 | 1.5789 | 1.3911 | 7.1576 | 7.2045 | 7.1079 | 7.1524 | 7.1026 | 0 | 1.4688 | 1.7321 | 1.709 | 0 | 1.6301 | 1.7231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348605 | 616 | 337764 | 650 | 98590.941 | 208.667 | 7.4872 | 7.6217 | 7.5644 | 7.3355 | 7.5572 | 6.5602 | 7.1576 | 7.2045 | 7.1079 | 7.1524 | 7.1026 | 0 | 997000 | 2000 | 991000 | 2000 | 1981200 | 4000 | 1984000 | 1977200 | 13.4667 | 7.3544 | 1.5385 | 7.145 | 1.6526 | 20.92% | 23.13% | 32.8816 | 47.2963 | 4.3264 | 11.409 | 1998134.1 | 1981133 | 2391256.4298 | 82.85%
2023-06-07 | 2024 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 335090.89 | 5:57 | 19:24 | 12060.3 | 12693.7 | 12470.1 | 12377.9 | 12750.7 | 12746.3 | 12820.1 | 13193.8 | 12735.5 | 12740.2 | 12603.5 | 12731.4 | 12549.7 | 12599.9 | 12662.5 | 12716.8 | 12603.8 | 12706.6 | 12731.5 | 12791.1 | 12778.2 | 12771 | 12502.1 | 12616.5 | 12480.3 | 11058.6 | 12581.1 | 12340.5 | 12814.7 | 12698.1 | 12567.4 | 12640.5 | 12772.6 | 12797.6 | 13015.1 | 12928.1 | 12773.9 | 12766.8 | 12583.6 | 12713.9 | 13444.3 | 12312.1 | 13315.9 | 12070.3 | 12672.1 | 14050 | 11984.4 | 13482.5 | 11843.4 | 12129.1 | 12894 | 12115.4 | 13224.9 | 11971.2 | 13137.9 | 11874.1 | 11781.7 | 13258.7 | 11825.5 | 13195.1 | 13173.3 | 11799.8 | 12949.6 | 12407.9 | 12560.2 | 11783.8 | 12507.8 | 12900.5 | 13137.6 | 11832.9 | 12979.7 | 11566.4 | 12797.7 | 12630.1 | 11908.9 | 12999.4 | 11630.6 | 13322.4 | 11923.9 | 13127.8 | 12019.2 | 12910.1 | 12176.7 | 13242.3 | 12045.9 | 12782.5 | 11816.7 | 10565.3 | 13007.9 | 12516.8 | 11509 | 13333.6 | 13015.2 | 12140.5 | 11980.4 | 13035.6 | 11635.9 | 12313.2 | 13259.5 | 11709.2 | 13217.8 | 11724.9 | 12990.3 | 12046.1 | 12992.3 | 11383.5 | 13130.7 | 11944.1 | 12974.5 | 11844.2 | 12994 | 12083.2 | 11789.2 | 12939.7 | 11832.8 | 11667 | 12980.9 | 12831.4 | 12895.5 | 11953.9 | 13021.6 | 11507.1 | 12716 | 11800.3 | 12541.6 | 11043.6 | 12773.9 | 11618.3 | 11795.2 | 11128.6 | 11848.5 | 10160.2 | 11913.5 | 10595.3 | 11742.2 | 11888.3 | 13408.5 | 11974.6 | 13432.3 | 12202.9 | 13385.9 | 12133.6 | 12264.4 | 11815.5 | 13065.3 | 13443.3 | 13399.6 | 13349.1 | 13275.6 | 13346.1 | 12303.2 | 13369.4 | 13110.4 | 13396 | 13078.2 | 13355 | 13451.8 | 12309.6 | 13480 | 12159.2 | 33.161 | 34.5243 | 34.6565 | 0 | 34.4997 | 32.4476 | 48.72 | 47.8409 | 48.1358 | 48.9174 | 0 | 0 | 3.3942 | 3.4697 | 3.0567 | 3.6082 | 3.5157 | 3.1178 | 6.94 | 6.822 | 6.155 | 6.817 | 6.7 | 6.296 | 7.6159 | 7.8236 | 7.6633 | 7.4568 | 7.6082 | 5.8524 | 1.2803 | 1.4714 | 1.4885 | 0 | 1.5753 | 1.1854 | 7.3124 | 7.3766 | 7.2422 | 7.2695 | 7.2442 | 0 | 1.39 | 1.4769 | 1.5264 | 0 | 1.6099 | 1.463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349609 | 617 | 338752 | 651 | 100576.208 | 212.6 | 7.6159 | 7.8236 | 7.6633 | 7.4568 | 7.6082 | 5.8524 | 7.3124 | 7.3766 | 7.2422 | 7.2695 | 7.2442 | 0 | 1004000 | 1000 | 988000 | 1000 | 1985267 | 3933 | 1990000 | 1981334 | 13.45 | 7.3367 | 1.4002 | 7.289 | 1.4933 | 19.08% | 20.49% | 33.8578 | 48.4035 | 3.3604 | 6.6217 | 2001844.1 | 1985133 | 2430305.0701 | 81.68%
2023-06-08 | 2024 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 335090.89 | 6:02 | 19:26 | 12005.4 | 12465.8 | 12334.2 | 12282.6 | 12513.2 | 12508.4 | 12555.9 | 12860.6 | 12475 | 12462.6 | 12358.6 | 12465.4 | 12349.8 | 12362.5 | 12496.6 | 12517.9 | 12401.7 | 12460.4 | 12453.5 | 12526.4 | 12507.5 | 12502.1 | 12332 | 12405.7 | 12276.6 | 11191.3 | 12328.6 | 12133.9 | 12531.3 | 12449.9 | 12337.7 | 12374.7 | 12496.8 | 12498.5 | 13280.3 | 13206.2 | 12490.8 | 12481.6 | 12354.3 | 12467.4 | 13074.2 | 12194.5 | 12975.6 | 12050.3 | 12484.6 | 13606 | 11999.7 | 13090 | 11827 | 12038.2 | 12626.4 | 12041.3 | 12917 | 11969.2 | 12841.8 | 11891 | 11799 | 12940.3 | 11856.6 | 12874.6 | 12836.1 | 11790.6 | 12670.1 | 12200.4 | 12383.4 | 11789.4 | 12296.9 | 12632.7 | 12831.4 | 11806.5 | 12684 | 11627.7 | 12546.3 | 12399 | 11858.1 | 12676.7 | 11646.1 | 12968.7 | 11868.6 | 12782 | 11940.4 | 12630.3 | 12063.4 | 12935.3 | 11982.4 | 12572.2 | 11790.3 | 10852.1 | 12679.5 | 12352.9 | 11607.2 | 12966.2 | 12693.7 | 12029.3 | 11927.6 | 12754.6 | 11672 | 12140.6 | 12902.8 | 11684.6 | 12850.7 | 11713.3 | 12695.7 | 11986.3 | 12681.3 | 11480.1 | 12809.9 | 11881.5 | 12701.7 | 11840.1 | 12698.2 | 12044.5 | 11742.6 | 12622.1 | 11799.3 | 11705.1 | 12622 | 12512.5 | 12607.2 | 11912.2 | 12726.4 | 11606 | 12461.6 | 11830.2 | 12369.5 | 11303.2 | 12557.3 | 11723.6 | 11896 | 11795.8 | 11857.5 | 10519.9 | 11926.9 | 10857.8 | 11769 | 11903.2 | 13068.6 | 11904.1 | 13089.4 | 12089.1 | 13013.6 | 11997.2 | 12133 | 11987 | 12756.8 | 13067.1 | 13042.8 | 13010.3 | 12920.2 | 13009 | 12155.4 | 13020.7 | 13160.6 | 12116.9 | 13076.1 | 12155.1 | 12965.7 | 13017.1 | 12943.4 | 13051.6 | 34.1863 | 35.6408 | 35.5775 | 0 | 35.5333 | 36.0703 | 48.3049 | 47.1211 | 47.8123 | 48.3027 | 0 | 0 | 5.3185 | 5.5946 | 5.3215 | 5.5764 | 5.4209 | 5.5842 | 10.16 | 9.793 | 9.311 | 9.628 | 8.933 | 8.968 | 7.7663 | 7.9843 | 7.8506 | 7.6439 | 7.8048 | 6.4472 | 1.4016 | 1.7731 | 1.6619 | 0 | 1.6619 | 1.4404 | 0 | 7.4933 | 0 | 0 | 0 | 0 | 1.5289 | 1.8007 | 1.696 | 0 | 1.7202 | 1.7756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350597 | 618 | 339731 | 653 | 102536.341 | 216.6 | 7.7663 | 7.9843 | 7.8506 | 7.6439 | 7.8048 | 6.4472 | 0 | 7.4933 | 0 | 0 | 0 | 0 | 988000 | 1000 | 979000 | 2000 | 1960133 | 4000 | 1964000 | 1956133 | 13.4 | 7.5828 | 1.5878 | 7.4933 | 1.7043 | 20.94% | 22.74% | 35.4016 | 47.8852 | 5.4693 | 9.4655 | 1975834.1 | 1248067 | 1534650.215 | 81.33%
2023-06-09 | 2024 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 335090.89 | 6:00 | 19:22 | 9517.7 | 9776.1 | 9630.2 | 9606.1 | 9816 | 9810 | 9812.7 | 10008.7 | 9802.1 | 9753.7 | 9709.3 | 9779.8 | 9749.1 | 9710.5 | 9750.5 | 9774.1 | 9744 | 9786.6 | 9785.5 | 9841.3 | 9823.6 | 9830.2 | 9721.4 | 9766.9 | 9664.6 | 9061.6 | 9726.6 | 9596.4 | 9842.8 | 9772.3 | 9729.7 | 9747.8 | 9825.3 | 9820.3 | 13302.3 | 13194.5 | 9788.5 | 9794.7 | 9744 | 9801.3 | 10222.6 | 9657.1 | 10141.8 | 9573.3 | 9861.7 | 10587.6 | 9491 | 10231.8 | 9443.3 | 9563 | 9917.6 | 9584 | 10100.3 | 9500.8 | 10071.1 | 9484.5 | 9426.7 | 10125.2 | 9474.5 | 10087.6 | 10066.5 | 9423.9 | 9885.4 | 9577.9 | 9755.7 | 9415 | 9721.6 | 9956.5 | 10050.1 | 9421.7 | 9965.3 | 9320.7 | 9883.6 | 9761.7 | 9455.6 | 9938.3 | 9323.8 | 10143.2 | 9453.1 | 10016.7 | 9510.5 | 9924.2 | 9583.6 | 10135.7 | 9519.8 | 9888.2 | 9423.1 | 8956.3 | 9932.1 | 9751.9 | 9356.9 | 10142.6 | 9965.7 | 9552.9 | 9494.2 | 10011.8 | 10098.2 | 10389.8 | 11030.3 | 10032.5 | 10961 | 10076.6 | 10860.3 | 10262.7 | 10899.3 | 9893.6 | 10968.4 | 10208 | 10852.3 | 10195.1 | 10910.8 | 10325.7 | 10090.4 | 10778.4 | 10119.6 | 10059.9 | 10848.7 | 10754.3 | 10781.9 | 10208.3 | 10880.9 | 9979.2 | 10648.8 | 10189.6 | 10590.9 | 9760.9 | 10726.5 | 10041.5 | 10178.1 | 10082 | 10163.5 | 9292.2 | 10138.6 | 9391.9 | 10061 | 10153.4 | 11179.6 | 10187.9 | 11182.1 | 10324.5 | 11062.9 | 10192.5 | 10304.3 | 10218.7 | 10884.1 | 11134.4 | 11136.4 | 11120.7 | 11047.8 | 11111.9 | 10394.1 | 11115.1 | 10197.1 | 10199.2 | 10169.3 | 10165.6 | 10220.8 | 9626.8 | 10259.7 | 9657.2 | 33.7322 | 34.5834 | 34.8257 | 0 | 33.5556 | 28.2333 | 46.69 | 45.3543 | 44.6989 | 45.217 | 0 | 0 | 7.648 | 7.6574 | 7.8137 | 7.7755 | 7.3429 | 5.9406 | 11.27 | 10.797 | 11.501 | 11.043 | 11.553 | 11.568 | 7.6254 | 7.8241 | 7.7023 | 7.5029 | 7.628 |  | 1.4344 | 1.8 | 1.7155 | 0 | 1.6419 | 1.0961 | 7.142 | 7.335 | 7.0568 | 6.977 | 6.8404 | 0 | 1.5655 | 1.8348 | 1.7559 | 0 | 1.703 | 1.3463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351383 | 619 | 340549 | 654 | 104136.408 | 220.533 | 7.6254 | 7.8241 | 7.7023 | 7.5029 | 7.628 | 0 | 7.142 | 7.335 | 7.0568 | 6.977 | 6.8404 | 0 | 786000 | 1000 | 818000 | 1000 | 1600067 | 3933 | 1602000 | 1596134 | 13.3667 | 7.6565 | 1.5376 | 7.0702 | 1.6411 | 20.08% | 23.21% | 32.986 | 45.4901 | 7.363 | 11.2887 | 1609927.9 | 767868 | 912564.3071 | 84.14%
2023-06-10 | 2024 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 335090.89 | 6:07 | 19:27 | 9557 | 9851.5 | 9758.3 | 9712.5 | 9907.1 | 9909.3 | 9901.9 | 10120.1 | 9874 | 9822.3 | 9785.1 | 9858.3 | 9869.7 | 9787.8 | 9922.3 | 9953.8 | 9824.5 | 9870.8 | 9873.2 | 9925.9 | 9915.8 | 9918.9 | 9794.9 | 9849 | 9751.9 | 9063.9 | 9812.6 | 9673.8 | 9941 | 9859.9 | 9806.7 | 9846.3 | 9914.8 | 9916 | 13446.7 | 13340.6 | 9882 | 9891.7 | 9832.8 | 9889.7 | 10370.2 | 9730.5 | 10277.9 | 9633.4 | 10047.2 | 10790.8 | 9563.5 | 10387.2 | 9486.9 | 9619.9 | 10022.3 | 9654.3 | 10230.9 | 9541 | 10196.5 | 9530.9 | 9465.4 | 10251.2 | 9512.8 | 10211.1 | 10183.8 | 9460.5 | 9969.8 | 9615.8 | 9828.7 | 9454.1 | 9776.1 | 10038.8 | 10171.3 | 9464.3 | 10075 | 9343.3 | 9978.3 | 9844.1 | 9499.1 | 10044.4 | 9343.8 | 10270.9 | 9489.1 | 10127.3 | 9554.8 | 10020.1 | 9633 | 10267.6 | 9572.5 | 9982.2 | 9517.4 | 8937.5 | 10049.6 | 9840.5 | 9393.5 | 10285.3 | 10093.6 | 9630.1 | 9566.3 | 10140 | 9477.9 | 9707.8 | 10249.1 | 9393.9 | 10279.9 | 9439.9 | 10127.4 | 9599.7 | 10145.5 | 9282.3 | 10203.2 | 9548.8 | 10106.2 | 9536.3 | 10141 | 9652.9 | 9461.6 | 10036.4 | 9481.9 | 9429.8 | 10101.2 | 10019.6 | 10045.4 | 9568.8 | 10127.6 | 9393.5 | 9930.3 | 9546.3 | 9875.9 | 9179.9 | 10000 | 9430.1 | 9515.6 | 9478.9 | 9516.8 | 8769.7 | 9475.1 | 8848.4 | 9418.1 | 9507.2 | 10391.6 | 9535 | 10392.2 | 9646 | 10294.3 | 9549.8 | 9637.3 | 9558.6 | 10120 | 10347.5 | 10362.2 | 10338.9 | 10272.5 | 10333 | 9712.8 | 10331.8 | 10310.5 | 10323.9 | 10240.8 | 10277.7 | 10339.6 | 9675.2 | 10401.9 | 9717.7 | 34.3952 | 35.3519 | 35.3161 | 0 | 35.3013 | 35.7755 | 46.6352 | 45.3215 | 45.9111 | 46.4673 | 0 | 0 | 8.4606 | 8.5656 | 8.7249 | 8.586 | 8.3974 | 8.6546 | 13.556 | 13.536 | 14.733 | 13.645 | 12.416 | 12.769 | 7.7066 | 7.9177 | 7.7787 | 7.579 | 7.7327 | 6.5142 | 1.4585 | 1.8514 | 1.7493 | 0 | 1.687 | 1.4678 | 7.1984 | 7.4015 | 7.1753 | 7.0997 | 7.0178 | 0 | 1.5974 | 1.8895 | 1.8004 | 0 | 1.7537 | 1.8106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352175 | 621 | 341332 | 655 | 105707.408 | 224.467 | 7.7066 | 7.9177 | 7.7787 | 7.579 | 7.7327 | 6.5142 | 7.1984 | 7.4015 | 7.1753 | 7.0997 | 7.0178 | 0 | 792000 | 2000 | 783000 | 1000 | 1571000 | 3934 | 1572000 | 1567066 | 13.3333 | 7.5381 | 1.6428 | 7.1785 | 1.7703 | 21.79% | 24.66% | 35.228 | 46.0838 | 8.5649 | 13.4425 | 1580581.5 | 877601 | 1030871.9991 | 85.13%
2023-06-11 | 2024 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 335090.89 | 6:06 | 19:26 | 10322.5 | 10677 | 10435.5 | 10382.9 | 10740.4 | 10745.9 | 10743.5 | 11012.2 | 10703.3 | 10631.1 | 10619 | 10696.9 | 10697.8 | 10611.1 | 10723.9 | 10771.1 | 10645 | 10704 | 10653 | 10641 | 10767 | 10766 | 10624 | 10689 | 10572.4 | 9708.5 | 10626.6 | 10469.8 | 10799.8 | 10701.1 | 10639.8 | 10692.2 | 10770.6 | 10762.1 | 13348.4 | 13242.2 | 10721.9 | 10740.7 | 10674.4 | 10735.8 | 11274.7 | 10527.2 | 11191.8 | 10414.3 | 10912.1 | 11696 | 10361.2 | 11293.2 | 10216 | 10384.7 | 10860.5 | 10416.2 | 11098.5 | 10275.4 | 11046.7 | 10250.6 | 10173.6 | 11099.6 | 10254.7 | 11072.4 | 11036.3 | 10185.9 | 10802.6 | 10386.5 | 10612.7 | 10133.9 | 10571.9 | 10882.8 | 11021.6 | 10287.1 | 10921.6 | 10030.1 | 10795.5 | 10652 | 10218.4 | 10890.6 | 10036.4 | 11135.7 | 10203.4 | 10981.7 | 10303.8 | 10854 | 10385.9 | 11140.5 | 10330.3 | 10821.1 | 10288.6 | 9551.5 | 10891.8 | 10664 | 10109.5 | 11159.7 | 10934.1 | 10381.8 | 10307.5 | 11003.1 | 10225.1 | 10497.3 | 11139.4 | 10121.7 | 11170.6 | 10176.4 | 10998.1 | 10363.7 | 11017.9 | 9983.8 | 11080 | 10305 | 10970.1 | 10290.3 | 11012.3 | 10420.9 | 10193.9 | 10911.1 | 10259.1 | 10171.1 | 10993.8 | 10894.2 | 10905.4 | 10335 | 11000.7 | 10126.4 | 10784.6 | 10300.2 | 10692 | 9836.6 | 10847.1 | 10237.9 | 10269.6 | 10360.9 | 10254.3 | 9342.9 | 10220.1 | 9442.1 | 10148.8 | 10244.9 | 11276.7 | 10292.2 | 11291.5 | 10434.5 | 11217 | 10348.8 | 10467.9 | 10405.5 | 11000.3 | 11253.7 | 11255.3 | 11229.6 | 11150.8 | 11214.1 | 10504.5 | 11229.4 | 11249.1 | 11248.5 | 11159.7 | 11198.5 | 11259 | 10473.9 | 11311.3 | 10529.5 | 35.5147 | 35.5461 | 35.4247 | 0 | 35.2533 | 35.8181 | 47.5882 | 46.6861 | 46.828 | 47.1406 | 0 | 0 | 8.5849 | 8.6801 | 8.7343 | 8.8612 | 8.5187 | 9.0805 | 12.598 | 12.145 | 13.981 | 12.983 | 11.98 | 14.322 | 7.5558 | 8.0251 | 7.8847 | 7.667 | 7.8837 | 7.0896 | 1.3445 | 1.7571 | 1.7765 | 0 | 1.6993 | 1.5413 | 7.5841 | 7.7536 | 7.7554 | 7.8387 | 7.6915 | 0 | 1.4383 | 1.7897 | 1.8066 | 0 | 1.7376 | 1.9105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353088 | 622 | 342179 | 657 | 107405.075 | 228.467 | 7.5558 | 8.0251 | 7.8847 | 7.667 | 7.8837 | 7.0896 | 7.5841 | 7.7536 | 7.7554 | 7.8387 | 7.6915 | 0 | 913000 | 1000 | 847000 | 2000 | 1697667 | 4000 | 1757000 | 1693667 | 13.3333 | 7.6843 | 1.6237 | 7.7247 | 1.7365 | 21.13% | 22.48% | 35.5114 | 47.0607 | 8.7433 | 13.0015 | 1708489.3 | 1088733 | 1361608.3356 | 79.96%
2023-06-12 | 2024 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 335090.89 | 6:04 | 19:28 | 10093.6 | 10385.9 | 10219.1 | 10186.1 | 10443.1 | 10449.8 | 10447.8 | 10721.3 | 10432.3 | 10345.8 | 10342.3 | 10423.5 | 10462.4 | 10338.1 | 10441.8 | 10494.8 | 10372.6 | 10423.1 | 10430.5 | 10499 | 10480.4 | 10480.1 | 10324.7 | 10398.1 | 10303.1 | 9518.7 | 10359.2 | 10205.6 | 10498.5 | 10392.3 | 10354.2 | 10409.2 | 10463.4 | 10474.6 | 13407 | 13303.8 | 10443.5 | 10440.5 | 10377.1 | 10427.8 | 10979.3 | 10247.2 | 10895 | 10136.5 | 10605.3 | 11427.5 | 10083.8 | 10991.6 | 9968.4 | 10084.9 | 10588.9 | 10166.1 | 10810 | 10025.1 | 10773.7 | 10010.3 | 9946.9 | 10829.7 | 10006.8 | 10803.2 | 10775.5 | 9951.6 | 10524.2 | 10126.3 | 10337.9 | 9919.8 | 10301 | 10574 | 10743.4 | 10020.7 | 10644.6 | 9790.6 | 10520.4 | 10366.3 | 9976.6 | 10599.8 | 9797.1 | 10845.5 | 9956 | 10688.7 | 10050.3 | 10565.1 | 10120 | 10845.5 | 10065.3 | 10519.7 | 10019.4 | 9346.6 | 10574.7 | 10368.3 | 9854.7 | 10846.7 | 10637.3 | 10111.3 | 10041.1 | 10681.8 | 9947.2 | 10195.7 | 10818.3 | 9851.3 | 10859.7 | 9900.1 | 10679.4 | 10077.2 | 10710.5 | 9725.6 | 10769.1 | 10010.9 | 10656.5 | 10010.3 | 10693.9 | 10117.9 | 9930 | 10593.5 | 9994.7 | 9888.6 | 10674.4 | 10576.3 | 10587.3 | 10059 | 10680.5 | 9857 | 10464.3 | 10016.3 | 10335.2 | 9586.6 | 10534.5 | 9984.1 | 9972.3 | 10057.6 | 9959.2 | 9120.6 | 9907.4 | 9204.9 | 9886.5 | 9960 | 10974.6 | 10007.6 | 10997.3 | 10145.7 | 10899.2 | 10043.2 | 10139.7 | 10098.8 | 10707.7 | 10969.1 | 10956.4 | 10921.9 | 10847 | 10915.9 | 10209.2 | 10920 | 10948.2 | 10931.5 | 10867.3 | 10942.5 | 10967.1 | 10197.5 | 11020.1 | 10236.9 | 33.6072 | 35.8572 | 36.1395 | 0 | 35.9586 | 36.2524 | 49.3801 | 48.5936 | 48.8844 | 49.6086 | 0 | 0 | 4.9853 | 5.8915 | 4.6738 | 6.1008 | 5.9026 | 5.6457 | 10.582 | 10.014 | 9.363 | 9.801 | 9.225 | 9.898 | 7.852 | 7.9257 | 7.7887 | 7.5926 | 7.6912 | 6.5665 | 1.444 | 1.8629 | 1.7243 | 0 | 1.6968 | 1.4738 | 7.2506 | 7.4402 | 7.1922 | 7.1901 | 7.1865 | 0 | 1.5787 | 1.9009 | 1.7836 | 0 | 1.7565 | 1.8238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353864 | 623 | 343003 | 658 | 109058.742 | 232.4 | 7.852 | 7.9257 | 7.7887 | 7.5926 | 7.6912 | 6.5665 | 7.2506 | 7.4402 | 7.1922 | 7.1901 | 7.1865 | 0 | 776000 | 1000 | 824000 | 1000 | 1653667 | 3933 | 1598000 | 1649734 | 13.4 | 7.5694 | 1.6404 | 7.2519 | 1.7687 | 21.67% | 24.39% | 35.563 | 49.1166 | 5.5333 | 9.8138 | 1664221.5 | 991133 | 1164174.1109 | 85.14%
2023-06-13 | 2024 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 335090.89 | 6:08 | 19:12 | 10009.5 | 10269.9 | 10076.5 | 10078.5 | 10312.3 | 10302.5 | 10303.8 | 10552.2 | 10320.5 | 10255.4 | 10192.5 | 10292.8 | 10307.8 | 10189.3 | 10241.1 | 10279.9 | 10214.1 | 10249.4 | 10185.2 | 10169 | 10255.9 | 10281 | 10082.6 | 10157.5 | 10065.9 | 9345.8 | 10180.3 | 10025 | 10255.2 | 10163.5 | 10097.8 | 10120.4 | 10191.7 | 10221 | 13040.7 | 12895.9 | 10212.1 | 10182.7 | 10113.6 | 10177 | 10886.5 | 10184.3 | 10809.8 | 10099.5 | 10521.7 | 11312 | 9990.7 | 10870 | 9841.2 | 9992.4 | 10427.9 | 10022.1 | 10643.9 | 9883.6 | 10609.8 | 9865.8 | 9809.1 | 10665 | 9860.6 | 10633.4 | 10605 | 9814.4 | 10377.3 | 10008.5 | 10206.4 | 9800 | 10137.8 | 10424.3 | 10587.4 | 9906.4 | 10498.9 | 9684.1 | 10373.5 | 10250.6 | 9861.3 | 10471.4 | 9704.9 | 10711.8 | 9874.6 | 10594.7 | 9931.3 | 10450.4 | 9983.7 | 10708.9 | 9939.4 | 10382.2 | 9894.5 | 9231.2 | 10413.9 | 10210.2 | 9685.6 | 10660.1 | 10448.1 | 9918.8 | 9825.7 | 10473.9 | 9747.5 | 10013.4 | 10633.5 | 9705 | 10687.6 | 9770.8 | 10526.4 | 9945.1 | 10576.1 | 9582.5 | 10653.4 | 9898.9 | 10554.1 | 9916.4 | 10538.8 | 10027.5 | 9774.7 | 10465.6 | 9877.7 | 9774.4 | 10554.8 | 10469.4 | 10470.7 | 9975.9 | 10591 | 9790.1 | 10357.2 | 9926.3 | 10204.2 | 9527.8 | 10469.1 | 9932.4 | 9898 | 9966.8 | 9925.8 | 9066.7 | 9831.6 | 9109.9 | 9769.2 | 9824.8 | 10784.4 | 9833.5 | 10815.7 | 9973.4 | 10685.6 | 9863.4 | 9968.6 | 9955 | 10576.5 | 10830.9 | 10820.8 | 10774.5 | 10665.1 | 10729.7 | 10069.1 | 10772.8 | 10805 | 10790.4 | 10739.3 | 10811.8 | 10835.8 | 10088.2 | 10877 | 10123.8 | 30.4355 | 34.9551 | 35.2208 | 0 | 35.0443 | 35.3768 | 48.4815 | 47.6393 | 47.9686 | 48.6705 | 0 | 0 | 5.3311 | 6.5495 | 5.2537 | 6.4883 | 6.3865 | 6.112 | 10.566 | 11.22 | 11.428 | 10.262 | 10.281 | 12.179 | 7.7466 | 7.7158 | 7.7359 | 7.6078 | 7.5905 | 6.5088 | 1.4291 | 1.7923 | 1.7183 | 0 | 1.6585 | 1.4601 | 7.1425 | 7.2308 | 7.2108 | 7.3351 | 7.0987 | 0 | 1.5684 | 1.8269 | 1.7826 | 0 | 1.7284 | 1.8034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354685 | 625 | 343817 | 660 | 110688.809 | 234.867 | 7.7466 | 7.7158 | 7.7359 | 7.6078 | 7.5905 | 6.5088 | 7.1425 | 7.2308 | 7.2108 | 7.3351 | 7.0987 | 0 | 821000 | 2000 | 814000 | 2000 | 1630067 | 2467 | 1631000 | 1627600 | 13.0667 | 7.4842 | 1.6117 | 7.2036 | 1.7419 | 21.53% | 24.18% | 34.2065 | 48.19 | 6.0202 | 10.9893 | 1640369.7 | 929733 | 1121733.5097 | 82.88%
2023-06-14 | 2024 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 335090.89 | 6:08 | 19:07 | 10606.6 | 10962.9 | 10695.9 | 10671 | 11163.7 | 11180.3 | 11048.7 | 11427.9 | 11010.1 | 10956 | 10876.7 | 10955.7 | 11151.5 | 10913.4 | 11096.1 | 11131.3 | 11060.8 | 11129.2 | 11081.1 | 11160.8 | 11188.3 | 11148 | 11085.4 | 11110.8 | 10870.5 | 9854.4 | 10975.5 | 10794.6 | 11234.4 | 11254.7 | 11183 | 11153.1 | 11221.3 | 11152.4 | 12071.8 | 12006.8 | 11232 | 11268.2 | 11241.8 | 11293.5 | 11891.2 | 11000.9 | 11797.5 | 10890.7 | 11444.3 | 12420 | 10830.3 | 11929.5 | 10401.9 | 10580.8 | 11236.2 | 10675 | 11571.7 | 10575.3 | 11435.2 | 10525.3 | 10285 | 11409.3 | 10337.8 | 11306.4 | 11273.4 | 10272.5 | 11022.5 | 10593 | 10853.4 | 10280.5 | 10781.3 | 11119 | 11304.5 | 10390.6 | 11157.1 | 10089.3 | 11015.3 | 10859.6 | 10334.5 | 11277.4 | 10177.5 | 11446.4 | 10409.5 | 11352.6 | 10420.9 | 11097.5 | 10535.7 | 11404.4 | 10472.1 | 11065.2 | 10462.2 | 9559.2 | 11373.7 | 10997 | 10375.1 | 11647.1 | 11389.1 | 10729.6 | 10653.7 | 11481.5 | 10578.4 | 10908.5 | 11697.8 | 10493.8 | 11781.2 | 10573.3 | 11587.4 | 10805.5 | 11649.9 | 10286.8 | 11722.5 | 10746.1 | 11568 | 10741.6 | 11562.3 | 10886.6 | 10558.5 | 11472 | 10694.8 | 10553.8 | 11619.5 | 11497.5 | 11504.4 | 10793.5 | 11611.1 | 10541.1 | 11346.6 | 10738.8 | 11244.3 | 10148.4 | 11441.2 | 10688.8 | 10698.5 | 10817.9 | 10704.6 | 9536.3 | 10651.3 | 9662.7 | 10446.3 | 10534.4 | 11653.3 | 10520.3 | 11693.2 | 10696 | 11622.8 | 10613.4 | 10756.4 | 10710.3 | 11355.3 | 11585 | 11573.6 | 11544.2 | 11455.3 | 11571.7 | 10772 | 11556 | 11760.5 | 11724.3 | 11714.3 | 11758.1 | 11732.1 | 10795.2 | 11753.1 | 10841.6 | 31.8703 | 34.3867 | 34.5738 | 0 | 34.4066 | 34.7884 | 46.5323 | 45.8791 | 46.2142 | 46.7329 | 0 | 0 | 6.1842 | 7.3298 | 6.1042 | 7.3635 | 7.1242 | 7.2058 | 12.812 | 11.896 | 12.629 | 11.457 | 12.582 | 12.725 | 7.1316 | 7.2444 | 7.1905 | 6.9623 | 7.1588 | 6.0362 | 1.3237 | 1.6759 | 1.6086 | 0 | 1.5514 | 1.3273 | 6.6428 | 6.8141 | 6.7561 | 6.7723 | 6.7417 |  | 1.4588 | 1.7024 | 1.6655 | 0 | 1.6209 | 1.6326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355564 | 626 | 344696 | 661 | 112441.609 | 238.733 | 7.1316 | 7.2444 | 7.1905 | 6.9623 | 7.1588 | 6.0362 | 6.6428 | 6.8141 | 6.7561 | 6.7723 | 6.7417 | 0 | 879000 | 1000 | 879000 | 1000 | 1752800 | 3866 | 1756000 | 1748934 | 12.9833 | 6.954 | 1.4974 | 6.7454 | 1.6161 | 21.53% | 23.96% | 34.0052 | 46.3396 | 6.8853 | 12.3502 | 1764692.4 | 1249733 | 1499664.4933 | 83.33%
2023-06-15 | 2024 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 335090.89 | 6:09 | 19:20 | 8387.8 | 8683.2 | 8495.1 | 8464.6 | 8809.7 | 8806.9 | 8746.5 | 9059.7 | 8731.6 | 8758.4 | 8620 | 8689.5 | 8760.2 | 8658.3 | 8843.7 | 8829.9 | 8788.7 | 8861.5 | 8832 | 8849.1 | 8946.9 | 8900.1 | 8811.6 | 8871 | 8693.6 | 7805.6 | 8684.7 | 8691.8 | 8948.8 | 8899.3 | 8796.6 | 8730 | 8866.4 | 8887.9 | 8909.3 | 8879.8 | 8920 | 8886.8 | 8835.2 | 8853.1 | 9410.6 | 8589.5 | 9318.5 | 8455.9 | 9036.5 | 9930.3 | 8588.1 | 9503.2 | 8203 | 8368.7 | 8821.5 | 8405 | 9117.7 | 8336.7 | 9017.3 | 8297.3 | 8125.7 | 9016.8 | 8178.3 | 8954.2 | 8895 | 8098.2 | 8709.3 | 8334.9 | 8581.5 | 8126.4 | 8519.7 | 8777.7 | 8956.7 | 8218.3 | 8819.1 | 7909.1 | 8718.3 | 8567.6 | 8143.9 | 8951.8 | 7899.5 | 8984.1 | 8169.5 | 8977 | 8221.7 | 8750.1 | 8290.3 | 9022.3 | 8212.1 | 8676.4 | 8204.4 | 7338.1 | 8969.5 | 8642.3 | 8191.4 | 9232.5 | 9009.1 | 8505.2 | 8441.4 | 9117.1 | 8402.4 | 8644.3 | 9267 | 8256.5 | 9245.7 | 8260.8 | 9005.6 | 8413.5 | 9006.7 | 7919.3 | 9065.7 | 8232.7 | 8970.1 | 8273.4 | 9064.1 | 8365.7 | 8324.2 | 8989.3 | 8317.2 | 8186.9 | 9040.6 | 8934.8 | 8891.9 | 8297.9 | 8919.2 | 8004.8 | 8687.5 | 8188.1 | 8608.7 | 7645 | 8720 | 8114.8 | 8229.3 | 8355.4 | 8136.7 | 7143.4 | 8199.1 | 7355.5 | 8124.5 | 8169.1 | 8973.5 | 8083 | 8978.4 | 8205.1 | 9067.8 | 8189.7 | 8289.7 | 8263.2 | 8745.5 | 8937.1 | 8953.5 | 8906.9 | 8811.8 | 8890.7 | 8174.4 | 8883.5 | 9076.8 | 9056.8 | 9000.6 | 9031.6 | 9033.6 | 8232.7 | 9127.8 | 8304.4 | 28.3845 | 31.0932 | 31.1877 | 0 | 31.1695 | 31.1384 | 39.5857 | 39.2977 | 39.4496 | 39.9456 | 0 | 0 | 5.438 | 5.9123 | 5.2178 | 5.9702 | 5.9819 | 5.4573 | 15.272 | 15.327 | 15.868 | 16.246 | 15.007 | 17.316 | 5.0714 | 5.2337 | 5.2562 | 4.9693 | 5.1378 | 4.1701 | 0.97967 | 1.063 | 1.1596 | 0 | 0.98628 | 0.81753 | 4.7351 | 4.9523 | 5.0196 | 4.9162 | 4.8962 |  | 1.0593 | 1.0821 | 1.1842 | 0 | 1.0365 | 1.0086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356258 | 627 | 345376 | 663 | 113811.409 | 242.6 | 5.0714 | 5.2337 | 5.2562 | 4.9693 | 5.1378 | 4.1701 | 4.7351 | 4.9523 | 5.0196 | 4.9162 | 4.8962 | 0 | 694000 | 1000 | 680000 | 2000 | 1369800 | 3867 | 1371000 | 1365933 | 13.1833 | 4.9731 | 1.0012 | 4.9039 | 1.0741 | 20.13% | 21.9% | 30.5947 | 39.5696 | 5.6629 | 15.8393 | 1380546.7 | 1277201 | 1574124.7358 | 81.14%
2023-06-16 | 2024 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 335090.89 | 6:09 | 19:05 | 6880.1 | 7168.1 | 7022.2 | 7011.6 | 7175.4 | 7172.2 | 7221.7 | 7508.9 | 7214.1 | 7240.2 | 7105.6 | 7209.3 | 7184.5 | 7152.7 | 7148.2 | 7177.9 | 7122 | 7165.6 | 7159.5 | 7182.6 | 7217.8 | 7199.6 | 7048.6 | 7125.3 | 7004.7 | 6217.7 | 7058.7 | 7027.4 | 7141.8 | 7133.2 | 7058.3 | 7126.1 | 7139.3 | 7166.6 | 7223.9 | 7167.2 | 7208.2 | 7146.6 | 7087.4 | 7126.8 | 7732.2 | 7000.2 | 7665.6 | 6902 | 7367.9 | 8194.9 | 6872.5 | 7749 | 6695.7 | 6849.9 | 7286.8 | 6875.5 | 7506.5 | 6759.8 | 7473.7 | 6688.9 | 6663.2 | 7554.2 | 6711.4 | 7501.9 | 7491.5 | 6687.5 | 7285.3 | 6914.1 | 7044.9 | 6612.9 | 7015.2 | 7251.1 | 7455.1 | 6731.6 | 7352.4 | 6493.1 | 7251.8 | 7060.7 | 6674.5 | 7408.1 | 6507.4 | 7564.8 | 6671.9 | 7413.8 | 6721.6 | 7251.2 | 6798.6 | 7490.9 | 6717.7 | 7165.2 | 6699.9 | 5925.5 | 7349.2 | 7045.7 | 6553.3 | 7563.7 | 7341.2 | 6801.2 | 6732.5 | 7407.9 | 6656.2 | 6903.8 | 7533.4 | 6605.1 | 7600.8 | 6617.1 | 7393.1 | 6796.2 | 7461.2 | 6391 | 7491.3 | 6749.6 | 7390.8 | 6758.6 | 7443.9 | 6841.5 | 6664 | 7347.5 | 6738.6 | 6596.9 | 7439.9 | 7374.1 | 7344.3 | 6777.1 | 7449.5 | 6592 | 7213.6 | 6736.9 | 7166.6 | 6277.7 | 7280.6 | 6691.8 | 6704.1 | 6829.6 | 6716 | 5803.7 | 6647.1 | 5882.9 | 6573.3 | 6646.6 | 7567.4 | 6619.8 | 7572.8 | 6739.7 | 7551 | 6696.4 | 6792.8 | 6766.5 | 7299.1 | 7536.7 | 7518.1 | 7486.9 | 7427.6 | 7508.3 | 6799.3 | 7490.3 | 7547 | 7535.8 | 7470.7 | 7521.9 | 7537.5 | 6785.2 | 7601.7 | 6816.1 | 25.7219 | 28.9407 | 28.7675 | 0 | 28.7488 | 29.002 | 35.6873 | 35.6533 | 35.3158 | 35.5002 | 0 | 0 | 6.5473 | 5.9515 | 6.3342 | 6.0855 | 6.6124 | 5.3903 | 12.336 | 11.952 | 12.014 | 12.359 | 12.14 | 10.998 | 3.8258 | 3.917 | 3.9226 | 3.7494 | 3.8018 | 3.2984 | 0.63157 | 0.80978 | 0.77553 | 0 | 0.73591 | 0.62882 | 3.7217 | 3.7257 | 3.7602 | 3.6933 | 3.6966 |  | 0.70044 | 0.81145 | 0.81351 | 0 | 0.7679 | 0.76129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356826 | 628 | 345936 | 664 | 114934.342 | 246.667 | 3.8258 | 3.917 | 3.9226 | 3.7494 | 3.8018 | 3.2984 | 3.7217 | 3.7257 | 3.7602 | 3.6933 | 3.6966 | 0 | 568000 | 1000 | 560000 | 1000 | 1122933 | 4067 | 1126000 | 1118866 | 12.9333 | 3.7525 | 0.71632 | 3.7195 | 0.77092 | 19.09% | 20.73% | 28.2362 | 35.5391 | 6.1535 | 11.9665 | 1131669 | 1122933 | 1303718.6578 | 86.13%
2023-06-17 | 2024 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 335090.89 | 6:18 | 19:08 | 3255.5 | 3387.1 | 3306.2 | 3292.7 | 3394.8 | 3380.2 | 3402.7 | 3551.4 | 3417 | 3457.7 | 3347 | 3411.5 | 3363.6 | 3373.8 | 3396.3 | 3402.5 | 3354.2 | 3375.4 | 3374.9 | 3391.5 | 3395.6 | 3389.9 | 3312.9 | 3347.1 | 3299.7 | 2905.7 | 3331.6 | 3305.7 | 3399.6 | 3363.8 | 3313.6 | 3296.3 | 3400.8 | 3412.8 | 3414.1 | 3383.9 | 3403.9 | 3371.3 | 3337.6 | 3381.5 | 3716.7 | 3322.2 | 3655 | 3265 | 3481.5 | 3922.9 | 3219.1 | 3718.2 | 3153.2 | 3240.6 | 3452.8 | 3258.1 | 3573.8 | 3164.2 | 3598.9 | 3182.5 | 3192.7 | 3686.7 | 3178.5 | 3630.6 | 3625.4 | 3179.4 | 3528 | 3346.3 | 3452.1 | 3261.8 | 3449.2 | 3610.3 | 3673.6 | 3316.9 | 3649.5 | 3191 | 3559.7 | 3498.2 | 3253.6 | 3695.3 | 3214.3 | 3735.6 | 3267.7 | 3683.7 | 3294.3 | 3590 | 3338.2 | 3720.8 | 3302.9 | 3550.9 | 3305.4 | 2907.4 | 3634.4 | 3490.3 | 3200.3 | 3650.4 | 3604.8 | 3300 | 3261.5 | 3645.7 | 3240.4 | 3364.5 | 3694.3 | 3202.1 | 3703.8 | 3193 | 3588.9 | 3287 | 3619.6 | 3096.2 | 3634 | 3254.1 | 3566.9 | 3237.2 | 3586.5 | 3282.2 | 3244 | 3599.6 | 3266.8 | 3194.3 | 3632.1 | 3609.1 | 3577.4 | 3285.3 | 3630.6 | 3181.9 | 3492.8 | 3237.2 | 3445.6 | 3019.4 | 3532.7 | 3238.4 | 3241.6 | 3303 | 3260.1 | 2808.7 | 3222.5 | 2835.1 | 3140.7 | 3168.7 | 3624.2 | 3126.3 | 3609.9 | 3179 | 3587.3 | 3152.2 | 3203.5 | 3201.7 | 3453.1 | 3590.1 | 3574.3 | 3558.6 | 3543.2 | 3594.3 | 3210 | 3568.7 | 3586.7 | 3584.8 | 3554.4 | 3583.4 | 3585.5 | 3189 | 3621.4 | 3197.6 | 25.4795 | 26.6918 | 26.5687 | 0 | 26.6342 | 26.7175 | 27.7885 | 28.0994 | 28.0641 | 27.9687 | 0 | 0 | 8.1686 | 7.7775 | 7.5066 | 8.0074 | 7.7803 | 7.8229 | 12.706 | 13.105 | 12.171 | 13.169 | 13.131 | 12.653 | 1.6842 | 1.7251 | 1.7308 | 1.7154 | 1.7427 | 1.4826 | 0.11712 | 0.1482 | 0.15771 | 0 | 0.14849 | 0.12679 | 1.6577 | 1.6582 | 1.6799 | 1.7086 | 1.7141 |  | 0.1325 | 0.15316 | 0.16937 | 0 | 0.16244 | 0.16184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357097 | 630 | 346206 | 666 | 115473.409 | 252.733 | 1.6842 | 1.7251 | 1.7308 | 1.7154 | 1.7427 | 1.4826 | 1.6577 | 1.6582 | 1.6799 | 1.7086 | 1.7141 | 0 | 271000 | 2000 | 270000 | 2000 | 539067 | 6066 | 537000 | 533001 | 12.8333 | 1.6801 | 0.13966 | 1.6837 | 0.15586 | 8.313% | 9.257% | 26.4184 | 27.9802 | 7.8439 | 12.8225 | 543403 | 539000 | 610391.5377 | 88.3%
2023-06-18 | 2024 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 335090.89 | 6:10 | 19:26 | 9665 | 10047.2 | 9761.8 | 9735.1 | 10086.7 | 10042.1 | 10103.6 | 10482.8 | 10100.6 | 10208.7 | 9904.3 | 10055.8 | 9933.7 | 9942.7 | 9935.9 | 9994.8 | 9805.3 | 9838.9 | 9851.9 | 9866.3 | 9877.9 | 9872.2 | 9595.7 | 9714 | 9565 | 8460.4 | 9705.4 | 9611.9 | 9846.6 | 9706.6 | 9578.3 | 9786 | 9686.6 | 9714.6 | 9851.7 | 9743 | 9793.6 | 9686.9 | 9585.3 | 9654.4 | 10545.5 | 9470.7 | 10413 | 9317.7 | 9960.7 | 11154.4 | 9284.3 | 10607.1 | 9225.4 | 9460.5 | 10074.4 | 9447.6 | 10379.7 | 9282.3 | 10336 | 9198.3 | 9170.3 | 10482.1 | 9287 | 10424.4 | 10441.7 | 9262.9 | 10154.5 | 9675.5 | 9737.2 | 9124.9 | 9719.6 | 10052.1 | 10372 | 9342.2 | 10289.2 | 9036.3 | 10107.3 | 9898.7 | 9320.6 | 10432.6 | 9183.8 | 10645.8 | 9397.9 | 10497.4 | 9245.4 | 10095.7 | 9316.2 | 10361.8 | 9203.2 | 9847.6 | 9196.9 | 8084.8 | 10036.2 | 9647.8 | 8871.1 | 10339.8 | 9999.8 | 9212 | 9126.9 | 10119.1 | 9008.4 | 9319.6 | 10213.9 | 8883.5 | 10263.4 | 8873.1 | 9985.2 | 9129.2 | 10107.4 | 8662.5 | 10172.4 | 9119 | 10021.7 | 9144.1 | 10131.3 | 9271.8 | 8976.1 | 9957.5 | 9098.2 | 8894.9 | 10102.4 | 10017 | 9963.4 | 9190.8 | 10129.7 | 8944.8 | 9792.9 | 9130.4 | 9706.6 | 8506.7 | 9885.5 | 9087.9 | 9093.4 | 9249.2 | 9135.9 | 7906.4 | 9072.4 | 8012.4 | 8991.8 | 9071.6 | 10382.5 | 8992 | 10382.9 | 9161.2 | 10300 | 9108.2 | 9275.8 | 9212.3 | 10010.4 | 10395.8 | 10374.2 | 10292.9 | 10200 | 10303 | 9295.7 | 10297 | 10473 | 10454 | 10359 | 10418 | 10409 | 9290 | 10514 | 9350 | 28.9696 | 31.6922 | 31.6855 | 0 | 31.8944 | 31.8848 | 39.0532 | 39.7691 | 40.1523 | 39.0782 | 0 | 0 | 4.2974 | 4.2163 | 4.0476 | 4.4909 | 4.263 | 4.1823 | 7.702 | 7.997 | 7.532 | 8.04 | 7.852 | 7.277 | 5.5322 | 5.5405 | 5.4127 | 5.3204 | 5.2842 | 4.6281 | 0.67788 | 0.88518 | 0.88108 | 0 | 0.85764 | 0.78858 | 5.3496 | 5.2217 | 5.1121 | 5.1711 | 5.1719 |  | 0.75827 | 0.87199 | 0.96796 | 0 | 0.90696 | 0.95616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357883 | 631 | 346970 | 667 | 117018.342 | 256.8 | 5.5322 | 5.5405 | 5.4127 | 5.3204 | 5.2842 | 4.6281 | 5.3496 | 5.2217 | 5.1121 | 5.1711 | 5.1719 | 0 | 786000 | 1000 | 764000 | 1000 | 1544933 | 4067 | 1548000 | 1540866 | 13.2667 | 5.2864 | 0.81807 | 5.2053 | 0.89227 | 15.48% | 17.14% | 31.2253 | 39.5132 | 4.2496 | 7.7333 | 1552792.5 | 1544933 | 1801824.3747 | 85.74%
2023-06-19 | 2024 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 335090.89 | 6:09 | 19:25 | 11961.5 | 12439.9 | 12002.8 | 11976.8 | 12533.1 | 12495.1 | 12518.7 | 12884.2 | 12482.4 | 12499.8 | 12323.9 | 12473.3 | 12410.6 | 12371.1 | 12457.7 | 12492 | 12346.9 | 12440.5 | 12400.1 | 12439.7 | 12459.5 | 12447.3 | 12221 | 12323.3 | 12207.8 | 10793 | 12258.2 | 12209.1 | 12474.7 | 12373.6 | 12255 | 12415.5 | 12480 | 12488.1 | 12711.3 | 12612.2 | 12530.5 | 12404.9 | 12296.9 | 12415 | 13223.9 | 12169.7 | 13111.9 | 11968.1 | 12667.2 | 13777.1 | 11951.4 | 13255 | 11584 | 11877.6 | 12569.4 | 11954.2 | 12891.9 | 11697 | 12880.4 | 11676 | 11600.1 | 13050.6 | 11622.1 | 12930.6 | 12898.9 | 11568.9 | 12682.3 | 12141.6 | 12390.8 | 11676.2 | 12192 | 12561.6 | 12943.5 | 11855.4 | 12835 | 11395.3 | 12636.1 | 12413 | 11743.7 | 12871.4 | 11509.7 | 13101.3 | 11745.6 | 12870.8 | 11814.8 | 12644.4 | 11948.5 | 13013.7 | 11841.8 | 12548 | 11862 | 10431.8 | 12733.9 | 12349.7 | 11477.6 | 13065.8 | 12735 | 11902.1 | 11790.9 | 12829.3 | 11657.9 | 12083.2 | 12983.3 | 11523 | 12987.8 | 11502.5 | 12706.1 | 11800.9 | 12752 | 11150.4 | 12803.8 | 11687.8 | 12630.4 | 11630.4 | 12609.2 | 11783.9 | 11605.6 | 12679.6 | 11716.4 | 11468.6 | 12735.7 | 12669.9 | 12585.8 | 11739.2 | 12718.2 | 11356 | 12395.2 | 11605.7 | 12223.4 | 10808.2 | 12465.8 | 11558.3 | 11634.2 | 11855.5 | 11641.3 | 10059.7 | 11643.8 | 10289.8 | 11605 | 11706.6 | 13142.7 | 11753.4 | 13160.9 | 11978.9 | 13101.8 | 11883.7 | 12067.5 | 11944.6 | 12735.4 | 13088.9 | 13135.5 | 13077.3 | 13036 | 13077.6 | 12068.7 | 13070.8 | 13129 | 13129 | 13054 | 13092 | 13116 | 12032 | 13220 | 12121 | 29.4709 | 33.1207 | 33.1517 | 0 | 33.1002 | 33.6059 | 46.1213 | 44.8814 | 45.3604 | 45.8556 | 0 | 0 | 5.4699 | 5.4405 | 5.4121 | 5.4347 | 5.5947 | 5.6129 | 8.707 | 8.642 | 9.23 | 8.847 | 8.766 | 8.414 | 7.2156 | 7.3983 | 7.2977 | 7.1347 | 7.179 | 6.2987 | 1.082 | 1.4018 | 1.428 | 0 | 1.3265 | 1.2174 | 6.9872 | 6.9881 | 6.9235 | 6.9492 | 6.8975 |  | 1.1564 | 1.4143 | 1.503 | 0 | 1.391 | 1.5091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358869 | 633 | 347944 | 669 | 118970.609 | 260.533 | 7.2156 | 7.3983 | 7.2977 | 7.1347 | 7.179 | 6.2987 | 6.9872 | 6.9881 | 6.9235 | 6.9492 | 6.8975 | 0 | 986000 | 2000 | 974000 | 2000 | 1952267 | 3733 | 1956000 | 1948534 | 13.2667 | 7.0873 | 1.2911 | 6.9491 | 1.3948 | 18.22% | 20.07% | 32.4899 | 45.5546 | 5.4941 | 8.7677 | 1966084.4 | 1952134 | 2358602 | 82.77%
2023-06-20 | 2024 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 335090.89 | 6:04 | 19:22 | 11304.8 | 11632.4 | 11097.4 | 11107.2 | 11658.8 | 11651.7 | 11683.6 | 11955.4 | 11654.1 | 11649.3 | 11555.7 | 11657.4 | 11662.5 | 11584.2 | 11678 | 11707.9 | 11043.8 | 11101.3 | 11111.4 | 11187.3 | 11158.4 | 11160.9 | 11038.5 | 11097.4 | 11471.3 | 10668.8 | 11523.8 | 11483.3 | 11662.9 | 11584.7 | 11525.2 | 11634.6 | 11647.2 | 11634.9 | 13135.6 | 13048.9 | 11677.8 | 11612.4 | 11535.6 | 11603.8 | 12158.7 | 11442.3 | 12085.8 | 11344.7 | 11824.2 | 12644.5 | 11273.6 | 12166.6 | 10868.9 | 11039 | 11459.1 | 11040.7 | 11592.7 | 10813.8 | 11535.1 | 10804.7 | 11153.1 | 12067.5 | 11231.3 | 12010.1 | 11982.7 | 11158.5 | 11786.1 | 11411.7 | 11559.9 | 11154.6 | 11384.8 | 11639.1 | 11951.2 | 11252.1 | 11921 | 11033.9 | 11738.9 | 11611.8 | 11202.5 | 11905 | 11079.2 | 12093.2 | 11208.7 | 11912.4 | 11249.5 | 11784.9 | 11322.5 | 12055.3 | 11270.3 | 11725.6 | 11218.7 | 10496 | 11821.1 | 11562.8 | 11082.6 | 12088.7 | 11841.7 | 11306.4 | 11220.5 | 11906.1 | 11150.3 | 11414.8 | 12015.9 | 11080.6 | 12054.8 | 11099.9 | 11894.2 | 11305.7 | 11887.9 | 10911 | 11949 | 11219.8 | 11858 | 11212.4 | 11797.4 | 11354.9 | 11116.3 | 11780.6 | 11209.1 | 11087.3 | 11873.9 | 11803 | 11767.7 | 11250 | 11868.9 | 11053 | 11656 | 11203.2 | 11425.8 | 10758.6 | 11739.6 | 11202 | 11208 | 11278.5 | 11179.5 | 10266.1 | 11131.1 | 10371.1 | 11114.4 | 11161.4 | 12144.5 | 11181.1 | 12173.2 | 11333.2 | 12089.7 | 11242.3 | 11337.5 | 11280.2 | 11882.5 | 12136.9 | 12185 | 12136 | 12096.9 | 12119.4 | 11432.2 | 12133.2 | 12157.1 | 12145.3 | 12113.1 | 12148.4 | 12182.1 | 11426.9 | 12235.7 | 11458.9 | 29.1828 | 33.4894 | 33.4606 | 0 | 33.2626 | 33.9231 | 45.6548 | 44.631 | 45.4969 | 45.668 | 0 | 0 | 6.7456 | 6.8089 | 6.8294 | 6.8581 | 6.4645 | 6.9797 | 9.446 | 9.873 | 10.577 | 9.729 | 9.596 | 9.768 | 7.497 | 7.6927 | 7.5531 | 7.3406 | 7.4943 | 6.5237 | 1.2146 | 1.6826 | 1.5359 | 0 | 1.4779 | 1.3163 | 7.2597 | 7.2458 | 7.1293 | 7.14 | 7.1662 |  | 1.3216 | 1.7088 | 1.6278 | 0 | 1.5453 | 1.6291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 359791 | 634 | 348864 | 670 | 120807.209 | 264.467 | 7.497 | 7.6927 | 7.5531 | 7.3406 | 7.4943 | 6.5237 | 7.2597 | 7.2458 | 7.1293 | 7.14 | 7.1662 | 0 | 922000 | 1000 | 920000 | 1000 | 1836600 | 3934 | 1840000 | 1832666 | 13.3 | 7.3502 | 1.4455 | 7.1882 | 1.5665 | 19.67% | 21.79% | 32.6637 | 45.3627 | 6.781 | 9.8315 | 1846569.6 | 931267 | 1107380.2577 | 84.1%
2023-06-21 | 2024 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 335090.89 | 6:14 | 19:21 | 12634.4 | 13129.7 | 13099.4 | 13085.9 | 13194.1 | 13226 | 13217.7 | 13590.4 | 13175.4 | 13173.6 | 13036.2 | 13179.8 | 13170.7 | 13087.7 | 13180.5 | 13240.6 | 13056.6 | 13137.6 | 13142.3 | 13172 | 13199.6 | 13182.2 | 12950.7 | 13059.9 | 12938.4 | 11431.5 | 12992.6 | 12953.1 | 13231 | 13107.7 | 12992.4 | 13179.3 | 13167.3 | 13173.9 | 13398.2 | 13313.5 | 13245.9 | 13150.4 | 13046.7 | 13135.2 | 13902.4 | 12807.1 | 13808.5 | 12617.5 | 13406.3 | 14468.2 | 12607.5 | 13932.3 | 12260.2 | 12573.5 | 13319.1 | 12637.3 | 13635.8 | 12371.5 | 13584.6 | 12323.7 | 12225 | 13686.3 | 12278.2 | 13618.9 | 13582.3 | 12229.9 | 13343.6 | 12783.1 | 13019.9 | 12275 | 12894.4 | 13297.7 | 13588.5 | 12479.5 | 13551.6 | 11987.3 | 13289.2 | 13067.6 | 12358.2 | 13550.7 | 12124.7 | 13769.9 | 12359.6 | 13548.6 | 12479.8 | 13366.6 | 12606.1 | 13727.9 | 12511.9 | 13254.6 | 12505.5 | 11027.5 | 13387.1 | 13037.6 | 12128.6 | 13765.3 | 13462.5 | 12586.1 | 12463.3 | 13534.2 | 12286.2 | 12739.1 | 13671.8 | 12130.9 | 13713.7 | 12171.6 | 13458.8 | 12479 | 13515.1 | 11814.5 | 13585.6 | 12406 | 13438.5 | 12368.5 | 13457.2 | 12548.5 | 12204.9 | 13348.1 | 12374.6 | 12102.4 | 13466 | 13397.8 | 13346.6 | 12436.9 | 13484.2 | 12059.2 | 13170.7 | 12353.1 | 12951.6 | 11459.1 | 13256.8 | 12260.1 | 11870.2 | 12087.6 | 11859.1 | 10270.3 | 11870.6 | 10491.5 | 11808.6 | 11827 | 13474.8 | 12060.3 | 13513.8 | 12280.8 | 13402.6 | 12139.9 | 12319 | 12143.3 | 13377.9 | 13728.2 | 13864.5 | 13815.4 | 13764.1 | 13792 | 12782.2 | 13836.9 | 13802.3 | 13810 | 13785.6 | 13826.9 | 13875 | 12733 | 13919.8 | 12780.9 | 31.5059 | 33.7576 | 33.7635 | 0 | 33.5134 | 34.1998 | 46.5896 | 45.5196 | 46.3382 | 46.6876 | 0 | 0.12788 | 5.7821 | 6.0613 | 5.8425 | 6.0987 | 5.7942 | 6.057 | 10.48 | 9.749 | 10.406 | 10.352 | 9.996 | 10.035 | 7.724 | 7.9273 | 7.8085 | 7.5885 | 7.7549 | 6.6928 | 1.3084 | 1.7811 | 1.6292 | 0 | 1.5595 | 1.3698 | 7.4542 | 7.4458 | 7.3365 | 7.3469 | 7.3525 |  | 1.4433 | 1.8116 | 1.7216 | 0 | 1.6289 | 1.6924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360831 | 635 | 349886 | 672 | 122862.543 | 268.333 | 7.724 | 7.9273 | 7.8085 | 7.5885 | 7.7549 | 6.6928 | 7.4542 | 7.4458 | 7.3365 | 7.3469 | 7.3525 | 0 | 1040000 | 1000 | 1022000 | 2000 | 2055334 | 3866 | 2059000 | 2051468 | 13.1167 | 7.5827 | 1.5296 | 7.3872 | 1.6596 | 20.17% | 22.47% | 33.348 | 37.0526 | 5.9393 | 10.1697 | 2071161.1 | 2055334 | 2491156.0914 | 82.51%
2023-06-22 | 2024 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 335090.89 | 6:09 | 19:23 | 10440.5 | 10691 | 10615.1 | 10662.4 | 10660.6 | 10704 | 10703.5 | 10894 | 10709.1 | 10701.9 | 10619.8 | 10703.7 | 10669.8 | 10617.9 | 10684 | 10710.9 | 10593.7 | 10655.3 | 10613.9 | 10653.5 | 10686.7 | 10680.4 | 10610.9 | 10636.7 | 10491.8 | 9799.5 | 10536.1 | 10485.6 | 10703 | 10636.2 | 10618.7 | 10618.7 | 10618.7 | 10618.1 | 12696 | 12597.1 | 10681.4 | 10661.8 | 10610.1 | 10632.8 | 11277.1 | 10690.8 | 11236.7 | 10593.6 | 11037.2 | 11714.3 | 10543.5 | 11298.8 | 10300.4 | 10456.3 | 10786.7 | 10460.8 | 10961.9 | 10280.1 | 10968.8 | 10311.5 | 10283.9 | 11055.8 | 10351 | 10999.2 | 10981.2 | 10292.3 | 10828.8 | 10514.5 | 10660.2 | 10322.5 | 10570.7 | 10816 | 10975.3 | 10453.7 | 10997.6 | 10237.6 | 10814.7 | 10751.3 | 10375.8 | 10969.3 | 10270.7 | 11117.7 | 10396.2 | 10972.9 | 10431.9 | 10855.7 | 10441.2 | 11115.3 | 10462.4 | 10839.3 | 10393.9 | 9766.3 | 10873.3 | 10692.8 | 10211.9 | 11049.2 | 10844.4 | 10394.1 | 10314.7 | 10886 | 10250.3 | 10506.1 | 10964.4 | 10181.1 | 10978.1 | 10139.3 | 10847.4 | 10339.3 | 10814.1 | 9993.9 | 10866.1 | 10265 | 10810.2 | 10247.7 | 10834.2 | 10384.5 | 10250.3 | 10793.6 | 10267.6 | 10167.8 | 10831.9 | 10787.3 | 10737.2 | 10329.9 | 10843.4 | 10153 | 10636.7 | 10245.2 | 10439.2 | 9894.1 | 10752.4 | 10307 | 10318.1 | 10388.7 | 10292.3 | 9460.3 | 10254.4 | 9577.1 | 10287.2 | 10280.1 | 11125.1 | 10324.3 | 11106.6 | 10442.7 | 11051.2 | 10355.2 | 10441.4 | 10381 | 10808.8 | 10979.7 | 11060.6 | 11024.3 | 11034.5 | 11088.6 | 10458.7 | 11011 | 10950.8 | 10930 | 10874.6 | 10927.9 | 10987.5 | 10364.2 | 11078.5 | 10416.8 | 30.8398 | 33.6618 | 33.7137 | 0 | 33.4283 | 33.9639 | 45.952 | 44.9119 | 45.7128 | 45.986 | 0 | 0 | 6.1371 | 6.3097 | 6.0548 | 6.2716 | 6.0438 | 6.3367 | 9.491 | 9.435 | 10.433 | 9.818 | 9.19 | 9.729 | 7.3626 | 7.5418 | 7.4998 | 7.2187 | 7.3377 | 5.9924 | 1.2123 | 1.7455 | 1.5305 | 0 | 1.528 | 1.3477 | 7.1387 | 7.1047 | 7.0506 | 7.0107 | 7.008 |  | 1.3614 | 1.769 | 1.6268 | 0 | 1.5956 | 1.6602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361687 | 636 | 350730 | 673 | 124557.41 | 272.267 | 7.3626 | 7.5418 | 7.4998 | 7.2187 | 7.3377 | 5.9924 | 7.1387 | 7.1047 | 7.0506 | 7.0107 | 7.008 | 0 | 856000 | 1000 | 844000 | 1000 | 1694867 | 3934 | 1698000 | 1690933 | 13.2333 | 7.1588 | 1.4728 | 7.0625 | 1.6026 | 20.57% | 22.69% | 33.1215 | 45.6407 | 6.1923 | 9.6827 | 1703365.2 | 843067 | 1023576.0832 | 82.36%
2023-06-23 | 2024 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 335090.89 | 5:50 | 19:30 | 10946.5 | 11201 | 11125.3 | 11150.5 | 11177 | 11205.3 | 11223.5 | 11405.1 | 11215.8 | 11166.5 | 11141.4 | 11221.2 | 11217.7 | 11149.1 | 11225.1 | 11254.8 | 11114.2 | 11175.7 | 11167.1 | 11228.2 | 11202.2 | 11215.1 | 11108.5 | 11148.6 | 11044.7 | 10392.1 | 11092.4 | 11059.7 | 11220.8 | 11135 | 11112.5 | 11134.2 | 11162.2 | 11158.9 | 13246.5 | 13162.5 | 11215.4 | 11172.5 | 11104 | 11146 | 11661.3 | 11097.9 | 11592 | 11015.6 | 11382.1 | 12060.9 | 10917.7 | 11655.9 | 10863.2 | 11011 | 11342.6 | 11010.7 | 11514 | 10858.9 | 11485.3 | 10884.7 | 10842.8 | 11585.5 | 10917.9 | 11541.4 | 11515.2 | 10845.7 | 11338.8 | 11023.8 | 11148.3 | 10828.2 | 11112.5 | 11333.2 | 11465.6 | 10925.1 | 11445.5 | 10776.9 | 11294.8 | 11241.6 | 10869.9 | 11476.6 | 10808.5 | 11595.7 | 10904.3 | 11482.3 | 10952.4 | 11400.8 | 11000.6 | 11590.3 | 10950.7 | 11314 | 10879.3 | 10289.2 | 11359.1 | 11156.1 | 10783.2 | 11579.8 | 11348 | 10910.7 | 10828.3 | 11393.7 | 10793.2 | 11040.4 | 11478.5 | 10733.4 | 11494.6 | 10744.1 | 11377.7 | 10918.2 | 11350.1 | 10569 | 11418.7 | 10817.3 | 11364.9 | 10834.9 | 11389.7 | 10988.8 | 10791.9 | 11303.7 | 10823.5 | 10742.9 | 11354.2 | 11295.7 | 11255.1 | 10868.6 | 11330.6 | 10694.1 | 11163.4 | 10816.1 | 11020.4 | 10468 | 11239.6 | 10820.1 | 10841.8 | 10909.6 | 10786.3 | 10007.5 | 10820.3 | 10193.6 | 10760.9 | 10764 | 11544.8 | 10797.1 | 11584.8 | 10915.4 | 11349.8 | 10810.7 | 10891.9 | 10846.2 | 11444.7 | 11636.7 | 11666.1 | 11606.4 | 11539.6 | 11545.8 | 11027.8 | 11611.9 | 11716 | 11698 | 11705.7 | 11727.5 | 11756.8 | 11130.2 | 11739.9 | 11139.2 | 32.0545 | 34.0256 | 33.9945 | 0 | 33.7512 | 34.4091 | 0 | 46.3 | 0 | 0 | 0 | 0 | 6.077 | 6.2733 | 6.0481 | 6.2667 | 6.0132 | 6.2753 | 9.407 | 9.997 | 10.722 | 10.775 | 9.66 | 9.966 | 7.6536 | 7.8551 | 7.7443 | 7.5061 | 7.6843 | 6.662 | 1.3053 | 1.7799 | 1.6032 | 0 | 1.6134 | 1.3671 | 7.4091 | 7.4004 | 7.2754 | 7.2928 | 7.3034 |  | 1.4525 | 1.8099 | 1.694 | 0 | 1.6676 | 1.6922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362584 | 638 | 351617 | 674 | 126335.943 | 276.2 | 7.6536 | 7.8551 | 7.7443 | 7.5061 | 7.6843 | 6.662 | 7.4091 | 7.4004 | 7.2754 | 7.2928 | 7.3034 | 0 | 897000 | 2000 | 887000 | 1000 | 1778533 | 3933 | 1781000 | 1774600 | 13.6667 | 7.5176 | 1.5338 | 7.3362 | 1.6632 | 20.4% | 22.67% | 33.647 | 46.3 | 6.1589 | 10.0878 | 1788173.3 | 784466 | 939721.9054 | 83.48%
2023-06-24 | 2024 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 335090.89 | 5:50 | 19:30 | 11963.1 | 12410.2 | 12422.5 | 12346.5 | 12522.8 | 12544.2 | 12499.3 | 12849.9 | 12446.3 | 12400.8 | 12356.7 | 12460 | 12502.4 | 12403.4 | 12514.5 | 12608.5 | 12418.4 | 12519.4 | 12519.3 | 12522.3 | 12576.7 | 12569.4 | 12353.9 | 12454.7 | 12342.1 | 11068.5 | 12375.5 | 12346.5 | 12618.6 | 12454.9 | 12383.7 | 12549.7 | 12573.9 | 12563 | 12994.5 | 12895 | 12641.7 | 12539.3 | 12438.6 | 12536.4 | 13109.8 | 12087.8 | 13001.1 | 11944.8 | 12552 | 13625.8 | 11839.4 | 13122.5 | 11726.7 | 11975 | 12653.4 | 12028 | 12992.3 | 11813.6 | 12901.5 | 11802.1 | 11680.8 | 13021.1 | 11743.2 | 12934.1 | 12874.9 | 11667.6 | 12616.1 | 12047.8 | 12301.8 | 11668.3 | 12241.1 | 12631.5 | 12850.3 | 11828.3 | 12787.9 | 11432.5 | 12535.8 | 12306.4 | 11719.2 | 12750.3 | 11486.4 | 12990.1 | 11667.7 | 12713 | 11821.6 | 12598.6 | 11898.8 | 12989.7 | 11844.3 | 12498.9 | 11859.3 | 10626.1 | 12704.3 | 12357.7 | 11648.9 | 13125.1 | 12783.9 | 11967.7 | 11861.2 | 12881.4 | 11729.3 | 12167.8 | 13032.8 | 11639.9 | 13109.1 | 11688.6 | 12854.8 | 11954.5 | 12921 | 11424.6 | 12983.1 | 11912.4 | 12818.9 | 11878.3 | 12888.4 | 12066.5 | 11736.4 | 12716.7 | 11848.7 | 11658.9 | 12855.6 | 12756.5 | 12741.7 | 11919.3 | 12873.9 | 11633.6 | 12597.7 | 11901.3 | 12410.8 | 11172.8 | 12663.2 | 11828.7 | 11804.2 | 11949.2 | 11806 | 10326.4 | 11691.4 | 10435.1 | 11664.8 | 11665.6 | 13166.1 | 11820.4 | 13245.4 | 12029.2 | 12962.3 | 11824.1 | 11995.3 | 11869.7 | 12853 | 13227.7 | 13228 | 13183.9 | 13107.3 | 13136.7 | 12187.8 | 13209.1 | 13216.5 | 13207.7 | 13218.7 | 13253.1 | 13289.4 | 12203.4 | 13342.1 | 12239.5 | 30.6812 | 34.3153 | 34.1856 | 0 | 33.9795 | 34.7266 | 0 | 46.6 | 0 | 0 | 0 | 0 | 5.3668 | 5.6064 | 5.4816 | 5.5294 | 5.4258 | 5.5786 | 9.471 | 8.61 | 9.913 | 8.987 | 8.655 | 8.812 | 7.4459 | 7.6918 | 7.4557 | 7.2734 | 7.5249 | 6.4943 | 1.2703 | 1.7345 | 1.5412 | 0 | 1.5706 | 1.3295 | 7.1823 | 7.2384 | 7.0083 | 7.0727 | 7.1402 |  | 1.4166 | 1.7622 | 1.6282 | 0 | 1.6308 | 1.6403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363572 | 639 | 352599 | 676 | 128300.343 | 280.133 | 7.4459 | 7.6918 | 7.4557 | 7.2734 | 7.5249 | 6.4943 | 7.1823 | 7.2384 | 7.0083 | 7.0727 | 7.1402 | 0 | 988000 | 1000 | 982000 | 2000 | 1964400 | 3933 | 1967000 | 1960467 | 13.6667 | 7.3143 | 1.4892 | 7.1284 | 1.6156 | 20.36% | 22.66% | 33.5777 | 46.6 | 5.4981 | 9.0747 | 1978391.5 | 1623599 | 1945688.0625 | 83.45%
2023-06-25 | 2024 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 335090.89 | 6:00 | 19:40 | 12218.1 | 12697 | 12747.9 | 12700.9 | 12868.3 | 12936 | 12829.2 | 13228.4 | 12776.1 | 12725.8 | 12669.2 | 12775.2 | 12871.6 | 12744.2 | 12853.8 | 12963.1 | 12760.4 | 12848 | 12834.9 | 12828.6 | 12828.9 | 12862.6 | 12521 | 12673.8 | 12556.8 | 11111.5 | 12621.4 | 12595 | 12830.5 | 12588.8 | 12408 | 12745.2 | 12655.1 | 12699.4 | 12913.7 | 12778.7 | 12777.8 | 12567.8 | 12440.4 | 12557.6 | 13273.1 | 12142.1 | 13175.3 | 11930.6 | 12707.9 | 13838.8 | 11951.1 | 13286.1 | 11891.3 | 12177.7 | 12928.9 | 12208.7 | 13267.2 | 11973.4 | 13200.8 | 11932.5 | 11808.4 | 13301 | 11903.3 | 13226.5 | 13206.9 | 11858.4 | 12968.1 | 12386.3 | 12577 | 11884.3 | 12508.2 | 12967.2 | 13195.4 | 12039 | 13126.4 | 11569.6 | 12890 | 12624.2 | 11971.6 | 13192 | 11760.4 | 13471.2 | 11987.6 | 13218.6 | 12044.8 | 12917.6 | 12124.3 | 13372.7 | 12096 | 12848.8 | 12129.8 | 10714.4 | 13000.9 | 12661 | 11827.8 | 13461.1 | 13085.2 | 12150.3 | 11998.2 | 13153.1 | 11791.6 | 12317.8 | 13230.1 | 11668.9 | 13254.9 | 11701.6 | 12976 | 11974.1 | 13014.6 | 11369.4 | 13068 | 11876.1 | 12838.7 | 11746.7 | 12796.7 | 11922.3 | 11772.4 | 12831 | 11844 | 11632.4 | 12950 | 12850 | 12803.7 | 11877.3 | 12892.2 | 11466 | 12564.5 | 11739.9 | 12272.5 | 10836.6 | 12579 | 11634.2 | 11757 | 11970.8 | 11615.9 | 10114.8 | 11721.5 | 10369.9 | 11772.5 | 11793 | 13519.9 | 11998.1 | 13566 | 12237 | 13382.5 | 11976.3 | 12183.8 | 12036.6 | 13143.6 | 13511.8 | 13575.4 | 13483.9 | 13405.5 | 13446.4 | 12380.8 | 13504.8 | 13472 | 13492 | 13536 | 13570 | 13602 | 12404 | 13653 | 12457 | 31.7913 | 34.6542 | 34.5947 | 0 | 34.41 | 35.0252 | 0 | 47.8 | 0 | 0 | 0 | 0 | 4.5018 | 4.9926 | 4.3644 | 4.9802 | 4.777 | 4.8595 | 10.022 | 8.947 | 9.916 | 9.431 | 8.446 | 9.164 | 7.4671 | 7.6113 | 7.3363 | 7.2729 | 7.3928 | 6.4793 | 1.2773 | 1.6879 | 1.5308 | 0 | 1.5134 | 1.2898 | 7.2242 | 7.2172 | 6.9622 | 7.1304 | 7.038 |  | 1.4176 | 1.7146 | 1.6063 | 0 | 1.5714 | 1.5913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 364579 | 640 | 353591 | 677 | 130292.41 | 284.133 | 7.4671 | 7.6113 | 7.3363 | 7.2729 | 7.3928 | 6.4793 | 7.2242 | 7.2172 | 6.9622 | 7.1304 | 7.038 | 0 | 1007000 | 1000 | 992000 | 1000 | 1992067 | 4000 | 1997000 | 1988067 | 13.6667 | 7.2599 | 1.4598 | 7.1144 | 1.5802 | 20.11% | 22.21% | 34.0951 | 47.8 | 4.7459 | 9.321 | 2007470.8 | 1982001 | 2391694.7082 | 82.87%
2023-06-26 | 2024 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 335090.89 | 5:50 | 19:30 | 11077.7 | 11503 | 11483.5 | 11503.2 | 11512.9 | 11574.1 | 11580 | 12006.3 | 11685.7 | 11572 | 11457.6 | 11638.1 | 11458.9 | 11415.5 | 11301.3 | 11445.4 | 11256.5 | 11507.4 | 11494.2 | 11473.1 | 11672.9 | 11611.1 | 11488.1 | 11561.6 | 11456.8 | 9982.2 | 11343.5 | 11379.3 | 11769.9 | 11679.3 | 11574.5 | 11790.7 | 11831.1 | 11791.7 | 11748.7 | 11647.8 | 11850.7 | 11785.6 | 11695.3 | 11781.1 | 12695.3 | 11373.6 | 12558 | 11161.7 | 12117.5 | 13378.1 | 11375 | 12782.6 | 10676.9 | 10945.6 | 11671.4 | 10983.3 | 11928.7 | 10574.3 | 11959.8 | 10673.8 | 10592.1 | 12025 | 10685.8 | 11947.3 | 11980.8 | 10674.5 | 11762.7 | 11224.8 | 11294.4 | 10611.5 | 11228.2 | 11725.6 | 11980.8 | 10944.3 | 12051.6 | 10549.7 | 11691.5 | 11537.9 | 10811.2 | 12123.6 | 10667.4 | 12314.9 | 10836.3 | 12071.5 | 10920.5 | 11855.2 | 11029.2 | 12211.3 | 10964.9 | 11736.3 | 10910.4 | 9692.4 | 12019 | 11536.8 | 10774.8 | 12461.7 | 12079.1 | 11140.6 | 11052.7 | 12131.4 | 10889 | 11387.2 | 12419.6 | 10791.6 | 12340.2 | 10780.2 | 12119.2 | 11071.2 | 12370.6 | 10569.4 | 12501.3 | 11248.5 | 12382.5 | 11296.1 | 12501.4 | 11507.5 | 10906.8 | 12122.7 | 11071.2 | 10887.5 | 12376.8 | 12316.6 | 12300.7 | 11394.1 | 12523.4 | 11094 | 12137.5 | 11341.5 | 12108 | 10638.2 | 12351.4 | 11382 | 11235.6 | 11335 | 11383.4 | 9801.4 | 11122.2 | 9816.6 | 10893.8 | 10839.7 | 12601.1 | 11098.6 | 12606.1 | 11238.5 | 12459.4 | 10993.4 | 11182 | 10986.5 | 12304.2 | 12652.8 | 12722.5 | 12674.3 | 12568.2 | 12558 | 11413.5 | 12595.9 | 12869.6 | 12932.7 | 13009 | 12984 | 12957.4 | 11577.2 | 12863.4 | 11654.6 | 32.1927 | 34.5872 | 34.6339 | 0 | 34.4031 | 33.6701 | 0 | 48 | 0 | 0 | 0 | 0 | 3.4138 | 3.7428 | 3.4045 | 3.7012 | 3.7041 | 3.587 | 6.643 | 7.289 | 6.403 | 6.814 | 6.422 | 7.171 | 6.6673 | 6.8818 | 6.9721 | 6.4671 | 6.9217 | 5.8854 | 1.1723 | 1.503 | 1.4679 | 0 | 1.3999 | 1.1614 | 6.377 | 6.4973 | 6.6071 | 6.345 | 6.5612 |  | 1.3035 | 1.5199 | 1.5488 | 0 | 1.4702 | 1.4238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365497 | 642 | 354523 | 679 | 132137.41 | 288.267 | 6.6673 | 6.8818 | 6.9721 | 6.4671 | 6.9217 | 5.8854 | 6.377 | 6.4973 | 6.6071 | 6.345 | 6.5612 | 0 | 918000 | 2000 | 932000 | 2000 | 1845000 | 4134 | 1846000 | 1840866 | 13.6667 | 6.6326 | 1.3409 | 6.4775 | 1.4532 | 20.22% | 22.44% | 33.8974 | 48 | 3.5922 | 6.7903 | 1857152.1 | 1844867 | 2185218.6435 | 84.42%
2023-06-27 | 2024 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 335090.89 | 6:00 | 19:20 | 10099.1 | 10583 | 10757.1 | 10730.5 | 10944.7 | 10940.2 | 10744.6 | 11111.9 | 10516.1 | 10573.2 | 10430.4 | 10506.3 | 10627.6 | 10523 | 10821.4 | 10821.8 | 10704.4 | 10750 | 10721.4 | 10720 | 10772.5 | 10747.4 | 10412.9 | 10592.9 | 10411 | 9198.2 | 10495 | 10479.4 | 10727.9 | 10492.7 | 10293.6 | 10599.1 | 10411.3 | 10452 | 10648.3 | 10541.9 | 10594.4 | 10413.9 | 10303.4 | 10386.9 | 11454.6 | 10344.1 | 11281.8 | 10124.8 | 10756.4 | 11788.4 | 10064.1 | 11391.3 | 9833.8 | 10046.3 | 10792.2 | 10153 | 11153.9 | 9942.5 | 11052.8 | 9892.8 | 9773.1 | 11139.3 | 9787.9 | 11002.7 | 10935.3 | 9705.6 | 10622.5 | 10078.1 | 10331.7 | 9695.5 | 10241.7 | 10586.5 | 10914.8 | 9852 | 10864.5 | 9425.5 | 10569.2 | 10298.4 | 9702.8 | 10826.8 | 9531.8 | 10996.8 | 9728 | 10797.7 | 9808.4 | 10558.1 | 9896.8 | 10990.9 | 9842.5 | 10491.3 | 9875 | 8649 | 10667.6 | 10280.5 | 9479.2 | 11033 | 10710.1 | 9843.6 | 9722.9 | 10807.8 | 9628.3 | 9984 | 10886.8 | 9541.4 | 11015.7 | 9569.6 | 10734 | 9851 | 10924.9 | 9381.8 | 11014 | 9878.4 | 10872.9 | 9902.4 | 10938.6 | 9975.7 | 9569.4 | 10628 | 9809.2 | 9560.8 | 10816.3 | 10694.2 | 10685.3 | 9815.2 | 10798.2 | 9503.2 | 10546 | 9810.6 | 10386.5 | 9039 | 10519 | 9659.9 | 9677.1 | 9834 | 9715.5 | 8369.2 | 9645.1 | 8537.9 | 9743.2 | 9774.8 | 11116.5 | 9731.8 | 11191.8 | 9975.4 | 11106.5 | 9900.2 | 10089.4 | 9980.8 | 10727.5 | 11098.5 | 11134.5 | 11099.1 | 11049.4 | 11070.6 | 10082.9 | 11101.6 | 11156 | 11188.2 | 11173.8 | 11175 | 11211.6 | 10099.2 | 11199.1 | 10162.1 | 29.1788 | 31.3351 | 31.1625 | 0 | 31.3486 | 31.5564 | 0 | 44.98 | 0 | 0 | 0 | 0 | 3.3798 | 3.4291 | 3.3943 | 3.3915 | 3.3737 | 3.4563 | 9.051 | 9.372 | 9.829 | 9.769 | 9.067 | 9.555 | 5.9529 | 6.1583 | 6.044 | 5.8151 | 5.9197 | 5.2216 | 0.83143 | 1.0927 | 1.0086 | 0 | 0.96666 | 0.85241 | 5.8093 | 5.8937 | 5.8152 | 5.7354 | 5.7156 |  | 0.91491 | 1.0995 | 1.0549 | 0 | 1.0079 | 1.0608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366335 | 643 | 355341 | 680 | 133787.344 | 292.533 | 5.9529 | 6.1583 | 6.044 | 5.8151 | 5.9197 | 5.2216 | 5.8093 | 5.8937 | 5.8152 | 5.7354 | 5.7156 | 0 | 838000 | 1000 | 818000 | 1000 | 1649934 | 4266 | 1654000 | 1645668 | 13.3333 | 5.8519 | 0.95036 | 5.7939 | 1.0276 | 16.24% | 17.74% | 30.9163 | 44.98 | 3.4041 | 9.4405 | 1661797.7 | 1649333 | 1955192.936 | 84.36%
2023-06-28 | 2024 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 335090.89 | 6:00 | 19:40 | 12495.6 | 13081.4 | 13086.8 | 13018.7 | 13180.6 | 13232.4 | 13210.9 | 13642.2 | 13118.1 | 13045.6 | 12985 | 13126.6 | 13119.6 | 13053.4 | 13137.5 | 13213.4 | 13024.2 | 13104.1 | 13130 | 13167.1 | 13164.2 | 13158.5 | 12866.3 | 13010.5 | 12888.7 | 11373.8 | 12942.6 | 12898.4 | 13205.8 | 13050.9 | 12914.8 | 13153.4 | 13108 | 13125.5 | 13276.1 | 13177 | 13227.5 | 13098.8 | 13016.9 | 13030.7 | 13877.4 | 12679 | 13763.5 | 12463.7 | 13269.8 | 14460.4 | 12492 | 13903.9 | 12165.7 | 12447.9 | 13274.6 | 12535.8 | 13649.3 | 12308.4 | 13574.2 | 12219.4 | 12093.1 | 13672.4 | 12140.2 | 13595.3 | 13575 | 12106.3 | 13254.2 | 12583.8 | 12850.8 | 12084.9 | 12722.5 | 13158.2 | 13537 | 12329.2 | 13493.1 | 11842.6 | 11298.3 | 11156.6 | 10398.8 | 11445.4 | 10176.3 | 11554.7 | 10510.9 | 11542.6 | 12347.5 | 13294.3 | 12497.9 | 13712.4 | 12394.5 | 13185.7 | 12355.9 | 10892.2 | 13367.7 | 12902.3 | 11989.4 | 13748 | 13348.1 | 12399.8 | 12286.7 | 13485.9 | 12140.1 | 12590.1 | 13630.3 | 12026.4 | 13664.9 | 12034.6 | 13342.1 | 12327.8 | 13447.4 | 11672.6 | 13518.4 | 12252 | 13330.8 | 12217.4 | 13399.4 | 12378.2 | 12092.2 | 13275.5 | 12247.7 | 11980.7 | 13398.7 | 13306.5 | 13248.2 | 12268.9 | 13387.3 | 11895.9 | 13040.7 | 12184.8 | 12874.9 | 11309 | 13108.1 | 12089.3 | 12119.2 | 12345.9 | 12114.5 | 10471.3 | 12105.8 | 10710.8 | 12103.5 | 12144.9 | 13906.2 | 12295.7 | 13907.4 | 12528.4 | 13794 | 12399.1 | 12597.2 | 12418.3 | 13470.2 | 13876.5 | 13883.9 | 13881 | 13831.1 | 13857 | 12716.2 | 13905.3 | 13858.4 | 13838.5 | 13839.9 | 13847.3 | 13911.2 | 12658.3 | 13898.4 | 12704.1 | 31.485 | 33.4827 | 33.4947 | 0 | 33.821 | 33.7774 | 0 | 49.79 | 0 | 0 | 0 | 0 | 2.491 | 2.5312 | 2.6005 | 2.5306 | 2.6476 | 2.4882 | 5.923 | 5.681 | 5.87 | 5.389 | 5.496 | 5.781 | 7.6379 | 7.8528 | 7.6742 | 7.4605 | 7.6406 | 6.6508 | 1.2149 | 1.6354 | 1.4754 | 0 | 1.4652 | 1.2562 | 7.3443 | 7.4065 | 7.2562 | 7.2568 | 7.2628 |  | 1.3481 | 1.6588 | 1.5524 | 0 | 1.5245 | 1.5671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367355 | 644 | 356362 | 682 | 135822.077 | 296.6 | 7.6379 | 7.8528 | 7.6742 | 7.4605 | 7.6406 | 6.6508 | 7.3443 | 7.4065 | 7.2562 | 7.2568 | 7.2628 | 0 | 1020000 | 1000 | 1021000 | 2000 | 2034733 | 4067 | 2038000 | 2030666 | 13.6667 | 7.4861 | 1.4094 | 7.3053 | 1.5302 | 18.83% | 20.95% | 33.2122 | 49.79 | 2.5482 | 5.69 | 2049897.5 | 2034667 | 2438009.3619 | 83.46%
2023-06-29 | 2024 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 335090.89 | 5:50 | 18:10 | 11041.3 | 11637 | 11584.1 | 11514.5 | 11646.9 | 11754.1 | 11777.2 | 12238.1 | 11635.6 | 11618.7 | 11521.5 | 11649.4 | 11651.2 | 11576 | 11686.9 | 11774.7 | 11548.9 | 11610.2 | 11154.5 | 11046 | 11660.9 | 11615.1 | 11366.9 | 11502.9 | 11304.8 | 9924.3 | 11365.1 | 11367.6 | 11707.9 | 11560.7 | 11393.2 | 11588.6 | 11572 | 11602 | 11605.1 | 11534.2 | 11701.6 | 11565 | 11558.2 | 11555.9 | 12505.9 | 11252.5 | 12381 | 10995.1 | 11821.2 | 13104 | 11075.9 | 12602.2 | 10575.3 | 10831.2 | 11652.4 | 10914.7 | 12075.9 | 10791.1 | 11969.2 | 10676.4 | 10485.2 | 12013.6 | 10586.8 | 11924.2 | 11928.5 | 10590.9 | 11673.1 | 11043.1 | 11372.1 | 10690.1 | 11198.7 | 11722.9 | 11975.7 | 10944.7 | 12006.7 | 10539.5 | 11558 | 11472.2 | 10654 | 12038.5 | 10516.4 | 12151.4 | 10676.5 | 11955.1 | 10945.2 | 11900.9 | 11058.6 | 12281.4 | 10922.4 | 11663.5 | 10831.4 | 9529 | 11849.4 | 11362.1 | 10495 | 12225.6 | 11833.9 | 10868.5 | 10764.1 | 11936.1 | 10742.9 | 11123.9 | 12190.5 | 10610.9 | 12134.9 | 10575.8 | 11784 | 10845.8 | 11900.7 | 10246.4 | 11995.6 | 10777.9 | 11792.6 | 10718.3 | 11895.8 | 10896.9 | 10721.7 | 11924.2 | 10865.9 | 10617.9 | 11984.3 | 11963.1 | 11837.2 | 10930.2 | 12053 | 10552.1 | 11606 | 10783.4 | 11434.5 | 10013.5 | 11696.9 | 10741.2 | 10789.8 | 11025.9 | 10769.2 | 9303.2 | 10825.9 | 9550.2 | 10823.5 | 10828.1 | 12496.5 | 10896.2 | 12541.4 | 11161.7 | 12517.8 | 11071.3 | 11256.9 | 11084.9 | 12102.7 | 12558.8 | 12502 | 12455.9 | 12413.3 | 12458.4 | 11261.5 | 12515.1 | 12553.4 | 12620.4 | 12637.3 | 12652.9 | 12655 | 11330.8 | 12642.8 | 11370.5 | 30.8051 | 33.6602 | 33.5506 | 0 | 33.8029 | 33.8503 | 48.7845 | 47.4856 | 47.704 | 48.0719 | 0 | 3.1792 | 4.2199 | 4.1358 | 4.1525 | 4.2594 | 4.3445 | 4.2063 | 14.091 | 12.638 | 11.305 | 14.013 | 13.028 | 12.95 | 6.6775 | 6.7629 | 6.6678 | 6.4805 | 6.7069 | 5.8881 | 1.0744 | 1.4055 | 1.3191 | 0 | 1.3476 | 1.1146 | 6.4733 | 6.4519 | 6.3988 | 6.3852 | 6.441 |  | 1.1823 | 1.423 | 1.3731 | 0 | 1.3858 | 1.3921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 368269 | 646 | 357272 | 683 | 137639.611 | 301 | 6.6775 | 6.7629 | 6.6678 | 6.4805 | 6.7069 | 5.8881 | 6.4733 | 6.4519 | 6.3988 | 6.3852 | 6.441 | 0 | 914000 | 2000 | 910000 | 1000 | 1817534 | 4400 | 1821000 | 1813134 | 12.3333 | 6.5306 | 1.2523 | 6.43 | 1.3513 | 19.18% | 21.01% | 33.1338 | 39.0451 | 4.2197 | 13.0042 | 1831759.1 | 1817534 | 2158569.9411 | 84.2%
2023-06-30 | 2024 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 335090.89 | 5:50 | 19:30 | 12289.7 | 12834.3 | 12792.7 | 12760.4 | 12881.9 | 12922 | 12919.9 | 13368 | 12871.6 | 12907.9 | 12737.8 | 12878.7 | 12840.3 | 12783.7 | 12873.6 | 12932.8 | 12736 | 12810.2 | 12836.3 | 12888.4 | 12892.7 | 12877.6 | 12626.6 | 12752.6 | 12626 | 11099.4 | 12669.9 | 12633.3 | 12938.8 | 12828.7 | 12686.3 | 12893.5 | 12868.4 | 12890.9 | 13031.6 | 12933.1 | 12979.9 | 12840.9 | 12803.8 | 12819.7 | 13651.1 | 12404.7 | 13533.6 | 12198.2 | 13060.9 | 14311.3 | 12229.7 | 13686.5 | 11898.1 | 12202.1 | 13005.9 | 12302.5 | 13367.3 | 12010.9 | 13340.6 | 11973.9 | 11890 | 13495.5 | 11912.1 | 13412.2 | 13378.5 | 11869.8 | 13121.4 | 12488.5 | 12675.4 | 11905.2 | 12448.3 | 12890.1 | 13318.8 | 12110.7 | 13281.5 | 11638 | 12985.3 | 12758.8 | 11997.6 | 13314.5 | 11785.1 | 13565.1 | 12036.8 | 13328.2 | 12101.8 | 13059.7 | 12242.1 | 13464 | 12136.1 | 12948.5 | 12153.3 | 10679.8 | 13172.5 | 12707.8 | 11765.5 | 13532.2 | 13164.8 | 12219.4 | 12111.6 | 13275.6 | 11944.5 | 12380.1 | 13424.1 | 11786.7 | 13462.6 | 11795.5 | 13136.8 | 12104.7 | 13215.6 | 11447.3 | 13273.1 | 12003.5 | 13085.9 | 11957.6 | 13160 | 12132.9 | 11846.8 | 13048.2 | 12010.9 | 11756.9 | 13181.8 | 13082 | 13034.6 | 12036.2 | 13170 | 11663.1 | 12843.2 | 11955.8 | 12667.1 | 11084.6 | 12908.9 | 11874.3 | 11875.4 | 12104.8 | 11916.2 | 10281.3 | 11881.1 | 10489.4 | 11819.3 | 11821.9 | 13553.7 | 11953.6 | 13583.2 | 12199.4 | 13465.7 | 12058.3 | 12264.6 | 12092.5 | 12989.7 | 13384.9 | 13485.4 | 13452.6 | 13444.1 | 13492.5 | 12328.8 | 13454.4 | 13480.2 | 13475.4 | 13430.9 | 13483.7 | 13502.7 | 12255 | 13589.2 | 12316.6 | 29.6454 | 33.4457 | 33.2831 | 0 | 33.0129 | 33.4826 | 47.1934 | 46.0357 | 46.3352 | 46.776 | 0 | 0 | 4.7119 | 5.0162 | 4.9187 | 4.9944 | 4.9754 | 4.8665 | 7.556 | 7.431 | 7.669 | 8.054 | 7.888 | 7.686 | 7.4462 | 7.6441 | 7.4914 | 7.3058 | 7.478 | 6.4244 | 1.2071 | 1.6013 | 1.4792 | 0 | 1.4826 | 1.2094 | 7.1591 | 7.2126 | 7.0892 | 7.1131 | 7.0999 |  | 1.3441 | 1.6211 | 1.5521 | 0 | 1.5428 | 1.489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 369286 | 647 | 358272 | 685 | 139649.544 | 304.933 | 7.4462 | 7.6441 | 7.4914 | 7.3058 | 7.478 | 6.4244 | 7.1591 | 7.2126 | 7.0892 | 7.1131 | 7.0999 | 0 | 1017000 | 1000 | 1000000 | 2000 | 2009933 | 3933 | 2014000 | 2006000 | 13.6667 | 7.2983 | 1.3959 | 7.1348 | 1.5098 | 19.13% | 21.16% | 32.5739 | 46.5851 | 4.9138 | 7.714 | 2024481.1 | 2009867 | 2414750.4828 | 83.23%
2023-07-01 | 2024 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 335090.89 | 6:05 | 19:21 | 12015.1 | 12493.4 | 12470.9 | 12439.9 | 12546.4 | 12596.3 | 12601.6 | 12996.2 | 12551.5 | 12569.7 | 12412.9 | 12555.7 | 12519.6 | 12459.6 | 12548.6 | 12609.3 | 12424.9 | 12492.7 | 12514.9 | 12566.4 | 12520.2 | 12463.5 | 12271.7 | 12394.7 | 12292.8 | 11001 | 12327.1 | 12289.7 | 12566.5 | 12419.3 | 12281.6 | 12505.2 | 12516.5 | 12535.1 | 13081.4 | 12975.3 | 12606.8 | 12457.4 | 12404.5 | 12442.3 | 13182.7 | 12090.4 | 13067.7 | 11893.4 | 12639.9 | 13746.8 | 11908.5 | 13205.6 | 11705 | 11959.8 | 12665.4 | 12026.7 | 13000.5 | 11823.2 | 12947.5 | 11758.7 | 11684.2 | 13073.6 | 11730.8 | 12993.5 | 12980 | 11695.9 | 12722.7 | 12160.2 | 12343.4 | 11698.2 | 12134.4 | 12522 | 12933.7 | 11877.4 | 12922.5 | 11499.6 | 12630.4 | 12439.2 | 11783.2 | 12943.5 | 11616.7 | 13122.9 | 11803.4 | 12938.8 | 11868.3 | 12709.4 | 12000 | 13072.6 | 11905.6 | 12610 | 11881.6 | 10694.4 | 12804.4 | 12363.7 | 11610.1 | 13155.1 | 12821.7 | 11967.4 | 11854.7 | 12900.3 | 11738.6 | 12105.5 | 13045 | 11610.5 | 13089.1 | 11626.1 | 12795.3 | 11888 | 12853.9 | 11309.7 | 12923.3 | 11793.2 | 12767.1 | 11774.3 | 12821.6 | 11924.7 | 11665.6 | 12725.4 | 11799.4 | 11595.1 | 12829.8 | 12766.1 | 12695.2 | 11857.4 | 12841.7 | 11518.9 | 12519.6 | 11762.9 | 12258.9 | 11040.4 | 12564.9 | 11690.3 | 11712.9 | 11890.2 | 11713.9 | 10349.6 | 11682.9 | 10532.8 | 11721.3 | 11748.7 | 13280 | 11855 | 13304 | 12061 | 13214 | 11941 | 12102.4 | 11977.1 | 12880.7 | 13253.6 | 13276.6 | 13219.3 | 13184 | 13219.2 | 12192.6 | 13241.1 | 13284 | 13278.6 | 13265 | 13287.8 | 13315.7 | 12184.6 | 13351.4 | 12236.7 | 31.0705 | 33.3568 | 33.3505 | 0 | 33.1435 | 33.577 | 47.7675 | 46.872 | 47.1822 | 47.508 | 0 | 0 | 4.0204 | 4.1454 | 3.8435 | 4.2515 | 4.1375 | 4.0473 | 6.914 | 6.913 | 7.688 | 6.796 | 6.52 | 7.717 | 7.5917 | 7.7627 | 7.5886 | 7.4228 | 7.5967 | 6.5755 | 1.0722 | 1.218 | 1.3344 | 0 | 1.2807 | 1.1428 | 7.2906 | 7.2958 | 7.1415 | 7.1861 | 7.1846 |  | 1.1766 | 1.2215 | 1.3949 | 0 | 1.3553 | 1.4238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370277 | 648 | 359254 | 686 | 141616.144 | 308.933 | 7.5917 | 7.7627 | 7.5886 | 7.4228 | 7.5967 | 6.5755 | 7.2906 | 7.2958 | 7.1415 | 7.1861 | 7.1846 | 0 | 991000 | 1000 | 982000 | 1000 | 1966600 | 4000 | 1971000 | 1962600 | 13.2667 | 7.423 | 1.2096 | 7.2197 | 1.3144 | 16.3% | 18.21% | 32.8997 | 47.3324 | 4.0743 | 7.0913 | 1980784.7 | 1638067 | 1937990.6801 | 84.52%
2023-07-02 | 2024 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 335090.89 | 6:02 | 19:29 | 12389.8 | 13033.9 | 13031.5 | 12962.7 | 13138.3 | 13201.1 | 13168.1 | 13726.6 | 13088.2 | 13068.4 | 12929 | 13107.6 | 13057.5 | 13002.5 | 13094.7 | 13169 | 12973 | 13064.2 | 13093.1 | 13122.5 | 13141.2 | 13103.7 | 12798.3 | 12940.9 | 12819.2 | 11236.6 | 12860.9 | 12814.1 | 13196.3 | 13050.9 | 12866.5 | 13159.1 | 13100.3 | 13127.2 | 13069.9 | 12972.4 | 13247.6 | 13082.7 | 13032 | 13069 | 3194.8 | 2855.1 | 3149.4 | 2793.1 | 2989 | 3373.8 | 2775.7 | 3173.6 | 12049.3 | 12356 | 13252.4 | 12433.9 | 13710.8 | 12184.4 | 13625.3 | 12110.6 | 12011 | 13720.5 | 12047.7 | 13638.3 | 13593.8 | 12012.4 | 13307.5 | 12569.9 | 12847.5 | 12036.3 | 12583.8 | 13108 | 13586 | 12242.6 | 13578.1 | 11746.8 | 13185.4 | 12899.9 | 12109.7 | 13587.7 | 11884.3 | 13838.2 | 12116.1 | 13565.4 | 12228.6 | 13277.3 | 12374 | 13768.2 | 12277.9 | 13153 | 12280.1 | 10799.8 | 13447.3 | 12857.6 | 11912.6 | 13863.8 | 13447.4 | 12352 | 12229.7 | 13593.4 | 12078.5 | 12535.6 | 13759.1 | 11948.1 | 13799.2 | 11954.1 | 13400.3 | 12268.4 | 13547 | 11403.7 | 13620.8 | 12170.5 | 13381.2 | 12148.3 | 13503.2 | 12326.3 | 12017.2 | 13358.7 | 12181 | 11922.5 | 10817.8 | 0.4 | 13334.3 | 12220.7 | 13514.9 | 11838.1 | 13091.4 | 12133.5 | 12937.6 | 11285.1 | 13162.7 | 12050.1 | 12072.3 | 12311.5 | 12084.2 | 10445 | 12071.1 | 10677.1 | 12081.3 | 12100.3 | 13967.4 | 12433 | 13904 | 12308.3 | 12533.4 | 12351.7 | 12192.8 | 12988.9 | 13322.5 | 13743.2 | 13908 | 13855 | 13816.6 | 13869.6 | 12559.6 | 13867.6 | 13938.4 | 13944.1 | 13963.9 | 13949.4 | 13976.9 | 12532 | 14021.5 | 12590.3 | 32.9538 | 34.074 | 33.4544 | 0 | 33.7253 | 34.3696 | 48.022 | 46.798 | 47.3429 | 47.7785 | 0 | 0 | 4.3601 | 4.5303 | 4.3979 | 4.5419 | 4.4208 | 4.5287 | 6.787 | 6.923 | 7.436 | 7.031 | 6.687 | 7.87 | 7.6347 | 7.8501 | 7.6616 | 7.4831 | 7.672 | 6.5941 | 1.1707 | 1.5024 | 1.4775 | 0 | 1.4876 | 1.2666 | 7.3305 | 7.3758 | 7.2264 | 7.2461 | 7.2424 |  | 1.2907 | 1.5126 | 1.539 | 0 | 1.5536 | 1.5633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371228 | 650 | 360259 | 687 | 143565.211 | 312.8 | 7.6347 | 7.8501 | 7.6616 | 7.4831 | 7.672 | 6.5941 | 7.3305 | 7.3758 | 7.2264 | 7.2461 | 7.2424 | 0 | 951000 | 2000 | 1005000 | 1000 | 1949067 | 3867 | 1953000 | 1945200 | 13.45 | 7.4826 | 1.381 | 7.2842 | 1.4918 | 18.46% | 20.48% | 33.7154 | 47.4854 | 4.4633 | 7.1223 | 1961908.5 | 1947001 | 2420183.9608 | 80.45%
2023-07-03 | 2024 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 335090.89 | 6:04 | 19:28 | 12556.1 | 13093.7 | 13077.2 | 13043.7 | 13170.5 | 13229.9 | 13206.2 | 13640.7 | 13131.7 | 13115.4 | 12996.4 | 13135.5 | 13133.1 | 13049.6 | 13151.8 | 13222.9 | 13027.9 | 13114.1 | 13129 | 13170.7 | 13174.1 | 13158.3 | 12904.5 | 13025.7 | 12909.8 | 11375.6 | 12947.6 | 12914 | 13214.7 | 13073.6 | 12958.6 | 13178.8 | 13128.5 | 13144.4 | 13364.2 | 13261.2 | 13244.8 | 13118.8 | 13072.9 | 13103.7 | 13915.6 | 12738 | 13802.9 | 12523.2 | 13328.6 | 14484.2 | 12523.9 | 13940.2 | 12184.7 | 12492.6 | 13291.1 | 12570.7 | 13656.8 | 12319.6 | 13575.9 | 12252 | 12134.5 | 13697.4 | 12181.3 | 13631.2 | 13602.1 | 12143.9 | 13330.1 | 12706.7 | 12924.4 | 12186.3 | 12758 | 13197.5 | 13565.3 | 12400 | 13529.3 | 11904 | 13228 | 13003.1 | 12268.6 | 13548 | 12044.6 | 13779.1 | 12284 | 13542.5 | 12396.6 | 13320.9 | 12532.9 | 13724.7 | 12440.1 | 13209.6 | 12421.8 | 10943.4 | 13404.5 | 12950 | 12063.3 | 13787.4 | 13426.7 | 12498.3 | 12373.5 | 13517.6 | 12199.2 | 12685.4 | 13685.1 | 12084.8 | 13714.1 | 12096.2 | 13409.3 | 12397.7 | 13486.6 | 11731.3 | 13559.4 | 12319.9 | 13382.8 | 12280.9 | 13458.6 | 12476.8 | 12162.5 | 13341.8 | 12319.3 | 12059.3 | 13458.9 | 13397.1 | 13324.7 | 12370.2 | 13473.1 | 11987.8 | 13136.6 | 12289.4 | 13021.3 | 11426.1 | 13213.2 | 12203.7 | 12218 | 12444.5 | 12204.1 | 10563.5 | 12215.9 | 10776.7 | 12180.1 | 12199.5 | 13919.6 | 12383.4 | 13939.3 | 12608.8 | 13842.2 | 12453.1 | 12649.1 | 12476.8 | 13453.7 | 13834.3 | 13892.6 | 13845.2 | 13800.8 | 13842.9 | 12737.4 | 13849 | 13890.6 | 13887.3 | 13868.3 | 13898.8 | 13941.7 | 12728.7 | 13968.5 | 12787.5 | 34.557 | 35.3638 | 34.0021 | 0 | 34.9554 | 35.7282 | 48.7289 | 47.4471 | 48.0278 | 48.4404 | 0 | 0 | 4.2908 | 4.466 | 4.4273 | 4.3774 | 4.3686 | 4.3706 | 8.131 | 7.856 | 7.941 | 7.815 | 7.959 | 7.476 | 7.7477 | 7.9678 | 7.807 | 7.5975 | 7.7851 | 6.7032 | 1.212 | 1.6478 | 1.5275 | 0 | 1.5606 | 1.3029 | 7.416 | 7.4678 | 7.3271 | 7.3383 | 7.3142 |  | 1.3405 | 1.6684 | 1.5881 | 0 | 1.619 | 1.6058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 372265 | 651 | 361295 | 689 | 145621.945 | 316.733 | 7.7477 | 7.9678 | 7.807 | 7.5975 | 7.7851 | 6.7032 | 7.416 | 7.4678 | 7.3271 | 7.3383 | 7.3142 | 0 | 1037000 | 1000 | 1036000 | 2000 | 2056734 | 3933 | 2070000 | 2052801 | 13.4 | 7.6014 | 1.4502 | 7.3727 | 1.5643 | 19.08% | 21.22% | 34.9213 | 48.161 | 4.3834 | 7.863 | 2072326.1 | 2056734 | 2439133 | 84.32%
2023-07-04 | 2024 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 335090.89 | 6:06 | 19:27 | 12434.5 | 12945.8 | 12925.5 | 12902.8 | 13011.6 | 13063 | 13049.2 | 13453 | 12978.2 | 12947.3 | 12843.8 | 12978.1 | 12982.2 | 12892.3 | 12999.4 | 13060.5 | 12881.3 | 12973 | 12979.9 | 13036.6 | 13034.4 | 13031 | 12783.2 | 12894.4 | 12784.6 | 11280.4 | 12800.7 | 12784.4 | 13074.4 | 12928.1 | 12824.6 | 13044.8 | 12994.2 | 13009.4 | 13223.1 | 13120.6 | 13096 | 12973.1 | 12925.3 | 12951.3 | 13765.9 | 12617 | 13639.4 | 12407.2 | 13193.2 | 14350.9 | 12399.7 | 13788.6 | 12076.3 | 12381.3 | 13135 | 12437 | 13476.7 | 12194.5 | 13403.9 | 12132.8 | 12021.2 | 13531.4 | 12069.3 | 13464.6 | 13437.2 | 12033.7 | 13168.7 | 12558.5 | 12785.9 | 12057.3 | 12649.4 | 13060.4 | 13390.1 | 12266.6 | 13353.2 | 11775.6 | 13068 | 12847.2 | 12136.8 | 13358.6 | 11901.9 | 13588.4 | 12144.9 | 13356.3 | 12260.5 | 13144.6 | 12380.4 | 13540.1 | 12305.2 | 13046.1 | 12277.7 | 10827.1 | 13229.4 | 12802.7 | 11952.8 | 13624.1 | 13292.8 | 12395.2 | 12256.7 | 13372.7 | 12106.7 | 12564.3 | 13523.3 | 11970.4 | 13551.1 | 11989.4 | 13264.4 | 12284.5 | 13342.4 | 11619.3 | 13417.9 | 12213 | 13248.8 | 12181 | 13315 | 12368.7 | 12056 | 13192.6 | 12194.2 | 11948.4 | 13304 | 13233.1 | 13184.3 | 12259.2 | 13315 | 11884.9 | 13002.3 | 12181 | 12881 | 11316.4 | 13084.8 | 12099.3 | 12091.8 | 12303.3 | 12079.4 | 10458.8 | 12089.6 | 10676.6 | 12057.5 | 12082.3 | 13726.5 | 12253 | 13763.9 | 12471.7 | 13673.5 | 12341.2 | 12538.2 | 12351 | 13261.8 | 13629.5 | 13709.4 | 13652.2 | 13625.4 | 13669.2 | 12603.3 | 13670 | 13703.5 | 13711 | 13680 | 13714.8 | 13762 | 12519.8 | 13788.1 | 12638.6 | 34.4668 | 35.6684 | 34.729 | 0 | 35.3486 | 36.032 | 47.6834 | 46.8918 | 47.568 | 47.6324 | 0 | 0 | 5.2728 | 5.8614 | 5.2434 | 5.8068 | 5.6189 | 5.7828 | 8.731 | 9.174 | 9.089 | 9.122 | 8.471 | 9.497 | 7.619 | 7.8323 | 7.6811 | 7.4591 | 7.6545 | 6.6435 | 1.2261 | 1.6527 | 1.5337 | 0 | 1.5557 | 1.2943 | 7.3146 | 7.3715 | 7.2587 | 7.2519 | 7.2321 |  | 1.3565 | 1.6721 | 1.5939 | 0 | 1.6143 | 1.6244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373291 | 652 | 362299 | 691 | 147656.678 | 320.6 | 7.619 | 7.8323 | 7.6811 | 7.4591 | 7.6545 | 6.6435 | 7.3146 | 7.3715 | 7.2587 | 7.2519 | 7.2321 | 0 | 1026000 | 1000 | 1004000 | 2000 | 2034733 | 3867 | 2027000 | 2030866 | 13.35 | 7.4816 | 1.4525 | 7.2858 | 1.5722 | 19.41% | 21.58% | 35.249 | 47.4439 | 5.5977 | 9.014 | 2049422.3 | 2034667 | 2415544 | 84.23%
2023-07-05 | 2024 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 335090.89 | 6:06 | 19:29 | 11631.4 | 12188.1 | 12212.4 | 12166.1 | 12304.6 | 12383.8 | 12326.9 | 12853.2 | 12232.6 | 12196.9 | 12093.7 | 12243.9 | 12256.8 | 12165.6 | 12295.8 | 12368 | 12192.4 | 12291.3 | 12285.3 | 12334.1 | 12369.4 | 12331.6 | 12059.1 | 12194.3 | 12043.5 | 10557.6 | 12072.3 | 12042.7 | 12414.5 | 12265.6 | 12121.3 | 12370.8 | 12314.4 | 12349.8 | 12387.7 | 12294.8 | 12432.9 | 12311.8 | 12279.2 | 12298.8 | 13326.1 | 11917.2 | 13186.1 | 11699 | 12548.8 | 13942.1 | 11697.5 | 13365.7 | 11293.7 | 11580.9 | 12426.2 | 11646 | 12859.9 | 11421.8 | 12756.8 | 11346.6 | 11237.4 | 12905.9 | 11286.1 | 12822.3 | 12784.8 | 11252.6 | 12472.8 | 11748 | 12005 | 11242.3 | 11863.1 | 12367.2 | 12749.7 | 11441.5 | 12673.3 | 10969.2 | 12328.2 | 12028.6 | 11315 | 12697 | 11091.8 | 12955.3 | 11314.5 | 12675.8 | 11446.1 | 12410.2 | 11577.1 | 12935.3 | 11489 | 12304.2 | 11467 | 10102.5 | 12603.7 | 12072.5 | 11186.9 | 13057.8 | 12634 | 11598.6 | 11474.5 | 12763.5 | 11344.4 | 11777.9 | 12963.6 | 11201.1 | 13022.8 | 11251.4 | 12651.9 | 11551.8 | 12806 | 10885.4 | 12873 | 11496.9 | 12655 | 11487.8 | 12761.6 | 11653.9 | 11293.7 | 12546.4 | 11445.1 | 11208.7 | 12721.9 | 12615.7 | 12579.1 | 11522.2 | 12750.5 | 11180.4 | 12344.7 | 11467.8 | 12220.6 | 10656.1 | 12436.2 | 11383 | 11343.9 | 11529.5 | 11394.1 | 9821.4 | 11301.3 | 9974.6 | 11189.8 | 11209.6 | 13063.8 | 11341.4 | 13094.4 | 11555.2 | 13003.1 | 11428.5 | 11626.1 | 11434.6 | 12471.8 | 12963.1 | 12986.6 | 12945 | 12913.4 | 12967.2 | 11672.3 | 12962.6 | 12997 | 13010.8 | 12991.5 | 13026.8 | 13052.4 | 11625.1 | 13079.6 | 11694.8 | 31.2768 | 33.8936 | 32.8367 | 0 | 33.6794 | 34.1805 | 45.5033 | 45.042 | 45.4293 | 45.551 | 0 | 0 | 4.5556 | 5.3807 | 4.5915 | 5.3117 | 5.0666 | 5.0616 | 8.99 | 10.047 | 9.236 | 9.073 | 9.179 | 9.861 | 6.9038 | 7.1207 | 7.0169 | 6.7595 | 6.9592 | 6.225 | 1.145 | 1.5339 | 1.428 | 0 | 1.4468 | 1.168 | 6.6969 | 6.7661 | 6.7131 | 6.6463 | 6.6871 |  | 1.2671 | 1.5416 | 1.4903 | 0 | 1.5003 | 1.4544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 374261 | 654 | 363257 | 692 | 149578.878 | 324.533 | 6.9038 | 7.1207 | 7.0169 | 6.7595 | 6.9592 | 6.225 | 6.6969 | 6.7661 | 6.7131 | 6.6463 | 6.6871 | 0 | 970000 | 2000 | 958000 | 1000 | 1922200 | 3933 | 1925000 | 1918267 | 13.3833 | 6.8308 | 1.3443 | 6.7019 | 1.4507 | 19.68% | 21.65% | 33.1734 | 45.3814 | 4.9946 | 9.3977 | 1935327.6 | 1922134 | 2251546 | 85.37%
2023-07-06 | 2024 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 335090.89 | 6:07 | 19:17 | 10556.5 | 11008.9 | 10982.1 | 11005.9 | 11065 | 11089.9 | 11063.6 | 11515.9 | 11120.9 | 11129.7 | 10869.5 | 11077.1 | 11023.8 | 10907.6 | 11075 | 11160.2 | 11035.3 | 11207.5 | 11198.4 | 11182.7 | 11317 | 11269.1 | 11071.4 | 11160.2 | 11109.8 | 9696.2 | 10973.4 | 11055.1 | 11413.3 | 11316.1 | 11208.5 | 11453.1 | 11355.7 | 11346.7 | 11364.1 | 11316.7 | 11495.6 | 11411.5 | 11326.1 | 11315.6 | 12183.9 | 10946.6 | 12063.4 | 10789.8 | 11507.2 | 12799 | 10648.9 | 12160.2 | 10267.1 | 10532.4 | 11237.5 | 10633.6 | 11583.9 | 10257 | 11694.2 | 10370.7 | 10379.2 | 11869.4 | 10278.3 | 11716.3 | 11621.8 | 10231.4 | 11281.3 | 10618.8 | 11004 | 10174.6 | 10843.7 | 11045.7 | 11674.3 | 10300.3 | 11509.4 | 9829.1 | 11269.2 | 10793.1 | 10309.2 | 11316.7 | 9985.1 | 11779.3 | 10306.3 | 11481.2 | 10196 | 11055.6 | 10357.6 | 11516.7 | 10305.8 | 11020 | 10305.6 | 9049.4 | 11399.6 | 10873.9 | 10245.9 | 11987.9 | 11728.4 | 10805.3 | 10681.5 | 11844.2 | 10456.6 | 10798.5 | 11904.1 | 10294 | 12009.4 | 10373.3 | 11657.6 | 10610.1 | 11711.5 | 10018.7 | 11748.3 | 10489.8 | 11602.7 | 10548.3 | 11725.9 | 10682.8 | 10337.9 | 11406.4 | 10387.1 | 10191.5 | 11563.4 | 11570.5 | 11479.8 | 10644.3 | 11700.9 | 10279.8 | 11300.4 | 10497.1 | 11160 | 9770.4 | 11407.1 | 10472 | 10516.4 | 10722.7 | 10480.2 | 9083.3 | 10458 | 9288.5 | 10566.7 | 10594.9 | 11924.1 | 10521.6 | 12013.9 | 10696.4 | 12010.3 | 10644.4 | 10879.1 | 10813.8 | 11149.2 | 11625.1 | 11603.7 | 11578.9 | 11591.7 | 11723.8 | 10745.8 | 11761.4 | 11675.9 | 11689.7 | 11800.3 | 11793.9 | 11773.1 | 10536.5 | 11679.1 | 10493 | 32.2887 | 33.6457 | 30.5689 | 0 | 33.7258 | 33.6742 | 47.1526 | 46.9451 | 46.9443 | 46.3616 | 0 | 0 | 2.6575 | 2.6683 | 2.7066 | 2.6358 | 2.7717 | 2.6078 | 12.003 | 10.487 | 10.131 | 10.833 | 10.78 | 9.377 | 6.1986 | 6.5721 | 6.3796 | 6.2107 | 6.2993 | 5.6317 | 0.95082 | 1.3967 | 1.2192 | 0 | 1.2952 | 1.065 | 6.0564 | 6.2814 | 6.1311 | 6.1312 | 6.0695 |  | 1.0569 | 1.4033 | 1.2748 | 0 | 1.3396 | 1.3478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375145 | 655 | 364133 | 694 | 151333.745 | 328.667 | 6.1986 | 6.5721 | 6.3796 | 6.2107 | 6.2993 | 5.6317 | 6.0564 | 6.2814 | 6.1311 | 6.1312 | 6.0695 | 0 | 884000 | 1000 | 876000 | 2000 | 1754867 | 4134 | 1757000 | 1750733 | 13.1667 | 6.2153 | 1.1854 | 6.1339 | 1.2845 | 19.07% | 20.94% | 32.7806 | 46.8509 | 2.6746 | 10.6018 | 1765152.8 | 1754867 | 2044142 | 85.85%
2023-07-07 | 2024 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 335090.89 | 6:04 | 19:19 | 8105.4 | 8529.1 | 8601.7 | 8527.7 | 8693.4 | 8751.6 | 8700 | 9069.9 | 8512.1 | 8490.8 | 8498.7 | 8518.9 | 8757.2 | 8629.3 | 8924.8 | 8911.2 | 8824.5 | 8834.6 | 8911.7 | 8923.7 | 8840.8 | 8752.9 | 8596.1 | 8718.6 | 8673.7 | 7641.2 | 8692.6 | 8695.9 | 8846.7 | 8697.9 | 8612.4 | 8688.9 | 8790.2 | 8775.5 | 8860.6 | 8813 | 8871.4 | 8780 | 8719 | 8671.2 | 9206.8 | 8419.7 | 9129.1 | 8256.6 | 8801.2 | 9711.2 | 8280.8 | 9248.2 | 8116.7 | 8253.7 | 8880.9 | 8366.2 | 9175.3 | 8254.8 | 9061.1 | 8185.8 | 7937.1 | 8983.3 | 7946.5 | 8875.5 | 8725.9 | 7794.3 | 8465.7 | 7966.4 | 8394.6 | 7818.3 | 8223.3 | 8461.9 | 8760.1 | 7876.2 | 8660.5 | 7539.1 | 8485.2 | 8267.7 | 6602.8 | 7226.9 | 7655.8 | 8749.2 | 7745.1 | 8580.2 | 7888.4 | 8469 | 7950.3 | 8826 | 7928.6 | 8412.6 | 7954.5 | 6973.5 | 8793.5 | 8362.8 | 7914.4 | 9134.3 | 8865 | 8220.6 | 8132.6 | 8911 | 8002.4 | 8175.8 | 8893.4 | 7738.7 | 8954.1 | 7800.2 | 8664.8 | 7965.6 | 8740.4 | 7554.6 | 8795.9 | 7944.8 | 8679.8 | 7938.4 | 8715.6 | 8002.9 | 7745.4 | 8551.6 | 7907.6 | 7743.1 | 8713.1 | 8660.8 | 8627.3 | 7985.3 | 8712.7 | 7751.1 | 8492.8 | 7931.6 | 8438.3 | 7433.8 | 8544.1 | 7883.1 | 7813.5 | 7922.8 | 7900.3 | 6781.5 | 7710.5 | 6770.6 | 7707.6 | 7754.4 | 8752.8 | 7686.6 | 8756.4 | 7849.8 | 8743.1 | 7813.9 | 7935.6 | 7889 | 8368.6 | 8686.6 | 8656.1 | 8652.4 | 8615.8 | 8660.7 | 7901.5 | 8699.9 | 8524 | 8600.3 | 8636.8 | 8690.6 | 8743.6 | 7863.8 | 8682.4 | 7842.8 | 25.3404 | 29.8839 | 29.0211 | 0 | 29.6928 | 23.268 | 39.1833 | 39.8552 | 39.0425 | 38.1082 | 0 | 0 | 2.892 | 2.7999 | 2.698 | 2.9391 | 2.8749 | 2.3671 | 8.059 | 7.623 | 8.735 | 8.631 | 7.695 | 8.774 | 4.7788 | 5.0309 | 4.8652 | 4.6421 | 4.7038 | 3.1611 | 0.70165 | 0.81128 | 0.84083 | 0 | 0.78453 | 0.49238 | 4.6316 | 4.8 | 4.702 | 4.6034 | 4.5797 |  | 0.77293 | 0.81592 | 0.87815 | 0 | 0.82258 | 0.63254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375826 | 656 | 364789 | 695 | 152664.545 | 332.867 | 4.7788 | 5.0309 | 4.8652 | 4.6421 | 4.7038 | 3.1611 | 4.6316 | 4.8 | 4.702 | 4.6034 | 4.5797 | 0 | 681000 | 1000 | 656000 | 1000 | 1330800 | 4200 | 1335000 | 1326600 | 13.25 | 4.5303 | 0.72613 | 4.6633 | 0.78442 | 16.03% | 16.82% | 27.4412 | 39.0473 | 2.7618 | 8.2528 | 1340585.1 | 1330600 | 1576054.2406 | 84.43%
2023-07-08 | 2024 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 335090.89 | 6:03 | 19:20 | 7080.8 | 7457.5 | 7493.4 | 7454.5 | 7514.7 | 7531.1 | 7507.4 | 7828.3 | 7482 | 7361.2 | 7372.3 | 7473.7 | 7528.1 | 7433.5 | 7703.3 | 7681.4 | 7593.1 | 7621.9 | 7626 | 7668.6 | 7646.6 | 7641.9 | 7477.9 | 7545.3 | 7402 | 6656.4 | 7501.6 | 7449.4 | 7632.7 | 7526.9 | 7443.4 | 7574.1 | 7516.3 | 7497.2 | 7621.4 | 7556.8 | 7623.2 | 7537.8 | 7517.3 | 7510.1 | 8210.4 | 7469.4 | 8120 | 7417 | 7829.6 | 8666.7 | 7390.5 | 8269.5 | 6958.4 | 7116.8 | 7611.7 | 7165.9 | 7921.5 | 7105.7 | 7795.9 | 7068.4 | 6892.7 | 7804 | 6937.9 | 7743 | 7724.1 | 6908.1 | 7504.6 | 7107.4 | 7291.6 | 6888.5 | 7150.4 | 7416.3 | 7681.7 | 6970.5 | 7634.9 | 6700.1 | 7493.4 | 7279.6 | 6900.1 | 7616.3 | 6688.3 | 7769 | 6851.3 | 7609.9 | 6981.9 | 7472.2 | 7053.9 | 7763.8 | 7010.9 | 7471.9 | 7014.8 | 6256.1 | 7637.5 | 7356.8 | 6921.6 | 7927.7 | 7727.2 | 7168.9 | 7095.5 | 7737.8 | 6969.2 | 7191.6 | 7826.4 | 6923.9 | 7946.9 | 6976.2 | 7770.9 | 7153.1 | 7886.1 | 6833.1 | 7956 | 7175.8 | 7878.7 | 7256.4 | 7988.8 | 7400.5 | 6973.3 | 7645.5 | 7074.2 | 6933.2 | 7794.7 | 7661.4 | 7721.5 | 7129.4 | 7854.5 | 7073.3 | 7683.8 | 7263.2 | 7628.6 | 6796.6 | 7770.1 | 7199.8 | 7056.5 | 7139 | 7207.5 | 6229.5 | 7005.2 | 6205.2 | 6994 | 7045.3 | 8047.6 | 7080.3 | 8087.9 | 7224.7 | 8001.3 | 7157.7 | 7232.6 | 7181.4 | 7819.7 | 8089.8 | 8005.3 | 8002.6 | 7954.5 | 7987.5 | 7311.2 | 8030.7 | 7866.1 | 7876.6 | 7883.5 | 7918.7 | 7975.6 | 7263.4 | 7985.5 | 7266.4 | 25.5525 | 29.2608 | 28.3613 | 0 | 29.2342 | 29.4122 | 36.435 | 37.1754 | 37.1866 | 36.4058 | 0 | 0 | 2.3417 | 2.2404 | 2.1762 | 2.2797 | 2.2657 | 2.2686 | 5.702 | 5.162 | 4.92 | 5.426 | 4.834 | 5.283 | 4.0381 | 4.2355 | 4.2589 | 3.9471 | 4.0829 | 3.7925 | 0.60946 | 0.67268 | 0.73875 | 0 | 0.65823 | 0.56639 | 3.8907 | 4.04 | 4.124 | 3.9101 | 3.9709 |  | 0.67474 | 0.67283 | 0.77267 | 0 | 0.70527 | 0.7342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 376421 | 658 | 365382 | 697 | 153848.612 | 336.933 | 4.0381 | 4.2355 | 4.2589 | 3.9471 | 4.0829 | 3.7925 | 3.8907 | 4.04 | 4.124 | 3.9101 | 3.9709 | 0 | 595000 | 2000 | 593000 | 2000 | 1184067 | 4066 | 1184000 | 1180001 | 13.2833 | 4.0592 | 0.6491 | 3.9871 | 0.71194 | 15.99% | 17.86% | 28.3642 | 36.8007 | 2.262 | 5.2212 | 1191040.2 | 1184067 | 1371371.9316 | 86.34%
2023-07-09 | 2024 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 335090.89 | 6:00 | 19:08 | 10924.2 | 11377.9 | 11297.5 | 11342.9 | 11280 | 11325.1 | 11369.9 | 11703.9 | 11407 | 11363.9 | 11210.6 | 11349.6 | 11256.2 | 11260.4 | 11316.4 | 11314.3 | 11269.2 | 11429.9 | 11438 | 11433.2 | 11608.9 | 11549.7 | 11417.1 | 11512.2 | 11407.7 | 10096.9 | 11236.5 | 11348 | 11696.8 | 11561.4 | 11488.6 | 11676.9 | 11741.1 | 11701.2 | 11741.1 | 11697.9 | 11761.5 | 11634.8 | 11624.4 | 11664.7 | 12444.8 | 11536.2 | 12399.4 | 11405.3 | 12059.5 | 12954.4 | 11287 | 12252.2 | 10614.5 | 10863.8 | 11418.2 | 10894.3 | 11677.7 | 10645.7 | 11691.3 | 10641.9 | 10614.5 | 11800.1 | 10633.2 | 11734.3 | 11700.8 | 10594.5 | 11418.1 | 10880.1 | 11247.6 | 10675 | 11079.8 | 11457.1 | 11695.4 | 10772.9 | 11653.1 | 10357.2 | 10675.2 | 10529.5 | 9965.1 | 10930.9 | 9750.9 | 11015.3 | 9873.7 | 10799.2 | 10786.7 | 11498.5 | 10953.5 | 11902.8 | 10943.2 | 11549.9 | 10899.9 | 9634.8 | 11715.9 | 11266.6 | 10679.4 | 12061.3 | 11841 | 11184.8 | 11088.4 | 11916.2 | 10998.7 | 11275.1 | 12099.7 | 10886.6 | 12105.5 | 10936.3 | 11880.4 | 11143.5 | 11899.5 | 10574.3 | 11987.6 | 11070.3 | 11885.1 | 11078.1 | 12019.2 | 11270.5 | 10884.7 | 11802 | 11085.7 | 10894.7 | 11930.8 | 11874.6 | 11819.2 | 11146.9 | 11927.7 | 10844.3 | 11725.3 | 11098.7 | 11658.6 | 10376.2 | 11801.4 | 11028.8 | 10937.6 | 11032 | 11032 | 9569.3 | 10769.3 | 9504.2 | 10306.9 | 10334.7 | 11884.3 | 10531.1 | 11964.6 | 10750.3 | 11535.1 | 10451.8 | 10542.1 | 10455.4 | 11893.9 | 12132 | 12258.1 | 12247.6 | 12116.3 | 11982.1 | 11243.9 | 12228.7 | 12218.6 | 12254.1 | 12199.4 | 12220 | 12271 | 11403.4 | 12304.1 | 11439.2 | 29.4268 | 31.5057 | 30.8454 | 0 | 31.5997 | 31.7131 | 43.6609 | 44.7301 | 45.704 | 43.9958 | 0 | 0 | 2.5755 | 2.5771 | 2.5682 | 2.6721 | 2.6354 | 2.6537 | 4.5 | 4.455 | 4.892 | 4.874 | 5.022 | 5.067 | 6.4864 | 6.8283 | 6.851 | 6.4531 | 6.8553 | 6.2029 | 0.86772 | 0.9306 | 1.1308 | 0 | 0.96752 | 0.91095 | 6.2616 | 6.4843 | 6.5478 | 6.3247 | 6.5271 |  | 0.90628 | 0.92706 | 1.1572 | 0 | 1.0199 | 1.1329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 377322 | 659 | 366287 | 698 | 155647.545 | 341 | 6.4864 | 6.8283 | 6.851 | 6.4531 | 6.8553 | 6.2029 | 6.2616 | 6.4843 | 6.5478 | 6.3247 | 6.5271 | 0 | 901000 | 1000 | 905000 | 1000 | 1798933 | 4067 | 1804000 | 1794866 | 13.1333 | 6.6128 | 0.96152 | 6.4291 | 1.0287 | 14.54% | 16% | 31.0181 | 44.5227 | 2.6136 | 4.8017 | 1812423.2 | 1798733 | 2147215.8319 | 83.77%
2023-07-10 | 2024 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 335090.89 | 6:02 | 19:28 | 8747 | 9207.5 | 9268.1 | 9188.2 | 9351.7 | 9405 | 9367.8 | 9823.5 | 9238.2 | 9192.1 | 9209.8 | 9279.8 | 9378.9 | 9316.7 | 9448.7 | 9488.6 | 9335 | 9384.1 | 9402.9 | 9442.1 | 9440.7 | 9419.7 | 9174 | 9297.4 | 9157.4 | 8037.1 | 9219 | 9170.8 | 9439.1 | 9310.1 | 9187.6 | 9386.4 | 9272.1 | 9317.2 | 9440.9 | 9323.3 | 9402.8 | 9295.3 | 9254.9 | 9255.5 | 10231 | 9133.7 | 10099.2 | 9004.5 | 9626 | 10824.1 | 8929.9 | 10089.4 | 8679.3 | 8881.7 | 9534.7 | 8904.4 | 9862 | 8769.9 | 9768.3 | 8671.8 | 8585.3 | 9856.2 | 8636.1 | 9798.9 | 9719.9 | 8547.3 | 9397.9 | 8832.9 | 9081.2 | 8496.7 | 9036.1 | 9393.8 | 9697.1 | 8661.9 | 9649.2 | 8307.4 | 9387.2 | 9126.6 | 8579.3 | 9629.7 | 8391.8 | 9797.1 | 8532.8 | 9562.9 | 8590.4 | 9367.5 | 8679.1 | 9716.1 | 8625.8 | 9244.9 | 8636 | 7582.4 | 9499.3 | 9091.4 | 8426.2 | 9838.7 | 9518.2 | 8747.9 | 8661.5 | 9587.5 | 8518.8 | 8827.7 | 9719.3 | 8436 | 9794.9 | 8435.9 | 9517.1 | 8684.2 | 9651.8 | 8223.2 | 9716.4 | 8674.6 | 9584.4 | 8704.2 | 9673.7 | 8833.9 | 8519.7 | 9495.1 | 8658.6 | 8473.4 | 9657 | 9587.7 | 9526.1 | 8767 | 9678.3 | 8497.5 | 9352.7 | 8698.6 | 9269.3 | 8104 | 9462.5 | 8677.3 | 8660.5 | 8822.2 | 8720.3 | 7501.1 | 8644.4 | 7630.1 | 8644 | 8657.5 | 9898.1 | 8560.3 | 9953 | 8755.2 | 9897.5 | 8724.3 | 8863.1 | 8811.1 | 9434.7 | 9849.4 | 9814.8 | 9773.5 | 9764.4 | 9811.6 | 8854.1 | 9821.6 | 9797.7 | 9823.8 | 9850.1 | 9878 | 9885.1 | 8797.7 | 9874.9 | 8813.7 | 31.189 | 32.6388 | 30.4544 | 0 | 32.7434 | 32.7875 | 42.047 | 42.232 | 42.3396 | 41.9668 | 0 | 0 | 2.6893 | 2.5659 | 2.6167 | 2.6208 | 2.8257 | 2.5166 | 5.275 | 5.206 | 5.281 | 5.577 | 5.395 | 5.423 | 5.0477 | 5.2273 | 5.2162 | 4.9398 | 5.0703 | 4.5561 | 0.73031 | 0.81385 | 0.91844 | 0 | 0.79274 | 0.71454 | 4.8806 | 4.9306 | 4.964 | 4.8391 | 4.8577 |  | 0.78044 | 0.80355 | 0.97141 | 0 | 0.84001 | 0.91482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378061 | 660 | 367014 | 700 | 157109.746 | 345.067 | 5.0477 | 5.2273 | 5.2162 | 4.9398 | 5.0703 | 4.5561 | 4.8806 | 4.9306 | 4.964 | 4.8391 | 4.8577 | 0 | 739000 | 1000 | 727000 | 2000 | 1462201 | 4067 | 1463000 | 1458134 | 13.4333 | 5.0096 | 0.79398 | 4.8944 | 0.86205 | 15.85% | 17.61% | 31.9626 | 42.1463 | 2.6392 | 5.3595 | 1468813.8 | 1454134 | 1667788.9704 | 87.19%
2023-07-11 | 2024 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 335090.89 | 6:03 | 19:26 | 11398.6 | 11957.2 | 11882.6 | 11839.9 | 11954.3 | 12036.7 | 12045.7 | 12429.6 | 12011.6 | 11952.9 | 11867.5 | 12015.7 | 11940 | 11903.7 | 11915.6 | 12002.9 | 11775.2 | 11783.6 | 11789.5 | 11868.3 | 11814.1 | 11800.3 | 11608.3 | 11709.5 | 11699.9 | 10237.1 | 11622.8 | 11615.9 | 11948 | 11865.2 | 11753.9 | 11974.5 | 12210.8 | 12099.6 | 12141.5 | 12039.2 | 12079.2 | 11991.9 | 12008.2 | 12190.1 | 12522.1 | 11390.7 | 12437.2 | 11241.8 | 12032.4 | 13090.9 | 11269.5 | 12410.9 | 10997.5 | 11273 | 12010 | 11255.3 | 12289.1 | 11099.4 | 12249.1 | 10995.8 | 10928.4 | 12380.7 | 11025.5 | 12303.9 | 12286.2 | 11024.7 | 12014.9 | 11463.1 | 11850.2 | 11257.1 | 11665.1 | 12305 | 12357.5 | 11443.6 | 12367.9 | 10925.9 | 12008.9 | 11880.5 | 11056.4 | 12385.6 | 10883.3 | 12476.2 | 11078.2 | 12292 | 11513.5 | 12487.3 | 11661.3 | 12803.1 | 11534.5 | 12316.8 | 11499.6 | 10100.1 | 12451.4 | 12021.5 | 11166.4 | 12817.3 | 12506.9 | 11562 | 11429.3 | 12567.6 | 11220.8 | 11657 | 12643.9 | 11100 | 12616.5 | 11086.7 | 12354.1 | 11374.6 | 12422.4 | 10739.8 | 12491.1 | 11286.4 | 12310.4 | 11235.3 | 12315.2 | 11400.2 | 11181.6 | 12375.7 | 11322.3 | 11093.5 | 12463.2 | 12453.8 | 12321.7 | 11468.3 | 12557.6 | 11116.1 | 12112.2 | 11262.4 | 11992.9 | 10590.4 | 12350.8 | 11358.3 | 11392 | 11625.4 | 11405.3 | 9867.5 | 11436.5 | 10105.1 | 11514.5 | 11552.4 | 13112.3 | 11606 | 13218.5 | 11875.8 | 13146.8 | 11780.4 | 11987 | 11788.2 | 12741.2 | 13113.9 | 13154.6 | 13096.7 | 13008.5 | 13014.5 | 11984 | 13100.2 | 13094.9 | 13138.1 | 13195.4 | 13222.3 | 13246.6 | 12013 | 13189.3 | 12037.5 | 33.4044 | 34.7825 | 32.6376 | 0 | 34.7079 | 35.0937 | 46.9017 | 45.7253 | 46.5123 | 47.0581 | 0 | 0 | 4.4035 | 4.5482 | 4.5965 | 4.4666 | 4.603 | 4.6052 | 6.922 | 7.195 | 7.056 | 7.079 | 7.277 | 7.195 | 6.892 | 7.0301 | 6.8951 | 6.7969 | 7.0751 | 6.5608 | 1.017 | 1.2712 | 1.2484 | 0 | 1.3169 | 1.1233 | 6.6949 | 6.6721 | 6.5681 | 6.6559 | 6.7593 |  | 1.0864 | 1.279 | 1.3016 | 0 | 1.3535 | 1.4153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379003 | 661 | 367970 | 701 | 159001.012 | 349.067 | 6.892 | 7.0301 | 6.8951 | 6.7969 | 7.0751 | 6.5608 | 6.6949 | 6.6721 | 6.5681 | 6.6559 | 6.7593 | 0 | 942000 | 1000 | 956000 | 1000 | 1891266 | 4000 | 1896000 | 1887266 | 13.3833 | 6.875 | 1.1954 | 6.6701 | 1.2872 | 17.39% | 19.3% | 34.1252 | 46.5493 | 4.5372 | 7.1207 | 1905484.8 | 1891200 | 2214179.7225 | 85.41%
2023-07-12 | 2024 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 335090.89 | 6:07 | 19:23 | 12358.9 | 12891.8 | 12866.7 | 12836.2 | 12952.3 | 13011.1 | 12982.9 | 13401.6 | 12916.5 | 12887.1 | 12788.2 | 12925.8 | 12927.8 | 12852 | 12960.6 | 13015 | 12844.2 | 12925.5 | 12931.8 | 12993.7 | 12974.6 | 12959.8 | 12715 | 12834.2 | 12712.1 | 11209.2 | 12744.9 | 12713.8 | 13013.4 | 12883 | 12753.6 | 12936.7 | 12933.2 | 12939.8 | 13161.2 | 13064.7 | 13037.1 | 12914.1 | 12862.2 | 12907.5 | 13693.7 | 12537.6 | 13554.9 | 12337.3 | 13113.5 | 14255.9 | 12354.6 | 13574.3 | 11978.3 | 12318.3 | 13081.1 | 12386.8 | 13451.5 | 12148.4 | 13357.6 | 12073.1 | 11971.3 | 13487.3 | 12017 | 13417.6 | 13390.5 | 11971 | 13129.2 | 12532.8 | 12736.6 | 12007.9 | 12555.4 | 12980.4 | 13353.8 | 12213.9 | 13319.6 | 11732.8 | 13019.1 | 12814.6 | 12085.3 | 13339.2 | 11857.7 | 13551 | 12097.6 | 13317.7 | 12174.8 | 13137.2 | 12340 | 13494.3 | 12236.1 | 12985.6 | 12241.8 | 10742 | 13190.9 | 12741.1 | 11875.1 | 13565.2 | 13214.1 | 12314.6 | 12193.3 | 13314.6 | 12032.6 | 12454.6 | 13449 | 11885.3 | 13488.8 | 11894 | 13186.7 | 12204 | 13250.1 | 11451.5 | 13337.2 | 12119.7 | 13174.2 | 12097.6 | 13151.3 | 12271.7 | 11956.1 | 13114.9 | 12121.9 | 11877.8 | 13234.7 | 13166.8 | 13098.8 | 12169.3 | 13241.4 | 11791.6 | 12918.7 | 12085.9 | 12722.7 | 11239.8 | 12996.2 | 12010.3 | 11937.8 | 12258.1 | 12043.6 | 10413.3 | 12031.8 | 10585.8 | 12011 | 12028.7 | 13665.7 | 12165.7 | 13694.2 | 12396.8 | 13597.9 | 12260.8 | 12450.7 | 12289 | 13047.3 | 13441.4 | 13645.4 | 13593.5 | 13557.6 | 13598.6 | 12527.4 | 13607.4 | 13636 | 13659.1 | 13637.6 | 13676.7 | 13692.4 | 12510.3 | 13720.6 | 12555 | 29.845 | 33.9003 | 32.6441 | 0 | 33.4107 | 34.3104 | 46.5785 | 45.4661 | 46.1113 | 46.3006 | 0 | 0 | 5.1363 | 5.0201 | 4.8703 | 5.0342 | 4.7948 | 5.1356 | 8.049 | 7.498 | 7.545 | 7.619 | 7.733 | 8.376 | 7.489 | 7.7327 | 7.5931 | 7.3757 | 7.5706 | 6.8593 | 1.1215 | 1.4231 | 1.3488 | 0 | 1.38 | 1.1732 | 7.2539 | 7.3082 | 7.2116 | 7.2022 | 7.2128 |  | 1.2187 | 1.4291 | 1.3926 | 0 | 1.4224 | 1.4828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380024 | 663 | 368979 | 703 | 161024.279 | 352.533 | 7.489 | 7.7327 | 7.5931 | 7.3757 | 7.5706 | 6.8593 | 7.2539 | 7.3082 | 7.2116 | 7.2022 | 7.2128 | 0 | 1021000 | 2000 | 1009000 | 2000 | 2023267 | 3466 | 2026000 | 2019801 | 13.2667 | 7.4367 | 1.2893 | 7.2377 | 1.3891 | 17.34% | 19.19% | 32.8221 | 46.1141 | 4.9985 | 7.8033 | 2038549.1 | 2023267 | 2417125.0248 | 83.71%
2023-07-13 | 2024 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 335090.89 | 6:00 | 19:30 | 12330.9 | 12821.4 | 12784.6 | 12777.7 | 12860.5 | 12916.3 | 12885.2 | 13194.7 | 12834.4 | 12776.8 | 12716.5 | 12837.6 | 12864 | 12776 | 12882.8 | 12942.9 | 12764.3 | 12839.2 | 12848.9 | 12923.2 | 12881.4 | 12883.1 | 12678.5 | 12779.8 | 12668.7 | 11283.3 | 12697.8 | 12671.6 | 12917.1 | 12798.1 | 12721.4 | 12893.7 | 12864.2 | 12863.7 | 13240.2 | 13147 | 12936.9 | 12838.8 | 12798.1 | 12833.9 | 13484.8 | 12536.7 | 13377.5 | 12354.6 | 13044 | 13970.5 | 12327.5 | 13449.9 | 12031.3 | 12300 | 13004.4 | 12355.7 | 13287.4 | 12134.5 | 13220 | 12086.3 | 11990.3 | 13310.2 | 12030.9 | 13258.7 | 13231.5 | 11986.6 | 12989 | 12478.2 | 12691.8 | 12031.6 | 12581.6 | 12958.8 | 13198.1 | 12232.5 | 13169.3 | 11812.1 | 12939.2 | 12773.9 | 12094.9 | 13178.5 | 11884 | 13359.3 | 12102.9 | 13167.8 | 12207.1 | 13073.3 | 12339.2 | 13349.5 | 12258.4 | 12937.8 | 12238.9 | 10842.7 | 13058.2 | 12723.4 | 11918.8 | 13372.6 | 13099.8 | 12293.7 | 12171 | 13161.1 | 12039.9 | 12469.9 | 13297.4 | 11943.3 | 13344.4 | 11966.8 | 13142.2 | 12243.8 | 13161.3 | 11638.8 | 13238.6 | 12181.9 | 13119 | 12154.7 | 13174.5 | 12350.9 | 11994.4 | 13049.4 | 12155.4 | 11953.4 | 13139.1 | 13098.6 | 13039.1 | 12231.5 | 13152.6 | 11887.2 | 12891.3 | 12146.8 | 12798.3 | 11377.4 | 12983.5 | 12103.4 | 12016.4 | 12279.4 | 12096.4 | 10536.7 | 12042.5 | 10700.4 | 12023.6 | 12038.4 | 13477.8 | 12190.9 | 13515.1 | 12413.9 | 13412.5 | 12262.6 | 12447.5 | 12279 | 12826.1 | 13123 | 13118.3 | 13070.4 | 13033.8 | 13059.4 | 12195.3 | 13079.4 | 13489 | 13482.1 | 13447.5 | 13484.3 | 13513.7 | 12527.5 | 13557.7 | 12598.2 | 32.8149 | 33.9409 | 31.5011 | 0 | 33.478 | 34.3365 | 0 | 45.8 | 0 | 0 | 0 | 0 | 5.55 | 5.5593 | 5.2773 | 5.6651 | 5.5254 | 5.7897 | 9.13 | 7.937 | 9.026 | 8.693 | 8.379 | 8.864 | 7.5151 | 7.7583 | 7.6162 | 7.4169 | 7.614 | 6.9071 | 1.1385 | 1.5281 | 1.4152 | 0 | 1.4719 | 1.2052 | 7.2912 | 7.3523 | 7.2522 | 7.2494 | 7.2689 |  | 1.2483 | 1.5383 | 1.4566 | 0 | 1.5177 | 1.5243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381041 | 664 | 369982 | 704 | 163037.479 | 356.267 | 7.5151 | 7.7583 | 7.6162 | 7.4169 | 7.614 | 6.9071 | 7.2912 | 7.3523 | 7.2522 | 7.2494 | 7.2689 | 0 | 1017000 | 1000 | 1003000 | 1000 | 2013200 | 3734 | 2018000 | 2009466 | 13.5 | 7.4712 | 1.3518 | 7.2828 | 1.457 | 18.09% | 20.01% | 33.2143 | 45.8 | 5.5611 | 8.6715 | 2028245.1 | 1650133 | 1967679.7624 | 83.86%
2023-07-14 | 2024 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 335090.89 | 6:00 | 19:30 | 12058.8 | 12608.2 | 12622.9 | 12572.7 | 12719.7 | 12778.7 | 12734.5 | 13146.9 | 12618 | 12546.4 | 12501.4 | 12634.7 | 12664.7 | 12582.3 | 12675.7 | 12766.1 | 12570.4 | 12656.3 | 12662.8 | 12710.1 | 12718.4 | 12690.7 | 12463.4 | 12583.1 | 12470.4 | 10964.3 | 12482.3 | 12457.1 | 12780.7 | 12634.5 | 12532.4 | 12755.6 | 12689 | 12720.4 | 12863.9 | 12758 | 12804.2 | 12683.7 | 12638.7 | 12673.1 | 13589.3 | 12370.1 | 13452.1 | 12153.5 | 12911.3 | 14111.8 | 12119.1 | 13593.8 | 11722.2 | 12007.9 | 12822.4 | 12076.8 | 13206.2 | 11830.6 | 13120.9 | 11787.7 | 11668.6 | 13229.3 | 11712.2 | 13158.6 | 13124 | 11665.6 | 12820.8 | 12176.9 | 12423 | 11704.6 | 12243.8 | 12730.1 | 13121.2 | 11942.7 | 13066.4 | 11486.9 | 12753.7 | 12526.9 | 11778.9 | 13085.1 | 11541.7 | 13306.5 | 11770.8 | 13036 | 11924.7 | 12931 | 12052.5 | 13319 | 11974.9 | 12742.8 | 11962 | 10514.5 | 12898.5 | 12514.4 | 11617.4 | 13346.2 | 13020.9 | 12072.4 | 11948 | 13061.6 | 11712.4 | 12201.5 | 13253.2 | 11645.4 | 13324.1 | 11673.2 | 13013.5 | 11955.6 | 13104.2 | 11323.4 | 13176.9 | 11913.9 | 12991.2 | 11883.3 | 13070.5 | 12078.2 | 11721.5 | 12916.1 | 11874.4 | 11652.3 | 13045.8 | 12970.1 | 12918.3 | 11951.4 | 13066.4 | 11575 | 12734.7 | 11879.7 | 12573.4 | 11036.7 | 12812.8 | 11811.1 | 11757.8 | 11982.1 | 11768.4 | 10189.3 | 11753.5 | 10362.2 | 11699.3 | 11719.1 | 13466.3 | 11919.1 | 13502.1 | 12129.4 | 13399 | 11973.2 | 12183.2 | 11944.6 | 13059.6 | 13455.9 | 13437.3 | 13395.9 | 13349 | 13376.4 | 12261 | 13402.3 | 13446.6 | 13441.8 | 13394 | 13430.1 | 13464.2 | 12222.1 | 13507.7 | 12294.3 | 32.2292 | 33.6542 | 31.2188 | 0 | 33.2316 | 34.0654 | 0 | 46.2 | 0 | 0 | 0 | 0 | 4.938 | 4.9777 | 4.8106 | 5.0224 | 4.8795 | 4.9635 | 8.125 | 8.107 | 8.403 | 8.223 | 7.689 | 7.368 | 7.3072 | 7.5687 | 7.4394 | 7.2219 | 7.3913 | 6.7028 | 1.0952 | 1.5016 | 1.3735 | 0 | 1.4443 | 1.1796 | 7.0936 | 7.1646 | 7.0646 | 7.049 | 7.0604 |  | 1.207 | 1.5111 | 1.4205 | 0 | 1.4895 | 1.4916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382042 | 665 | 370973 | 705 | 165022.68 | 360.133 | 7.3072 | 7.5687 | 7.4394 | 7.2219 | 7.3913 | 6.7028 | 7.0936 | 7.1646 | 7.0646 | 7.049 | 7.0604 | 0 | 1001000 | 1000 | 991000 | 1000 | 1985201 | 3866 | 1990000 | 1981335 | 13.5 | 7.2719 | 1.3188 | 7.0864 | 1.4239 | 18.14% | 20.09% | 32.8799 | 46.2 | 4.932 | 7.9858 | 2000593 | 1984001 | 2367685.7943 | 83.79%
2023-07-15 | 2024 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 335090.89 | 6:06 | 19:25 | 10960.8 | 11243.2 | 11166 | 11183.4 | 11219.3 | 11248 | 11254.8 | 11507.8 | 11264.9 | 11190.1 | 11134.2 | 11247 | 11230.7 | 11155.1 | 11216.8 | 11251.7 | 11074 | 11117.8 | 11140 | 11228.6 | 11161 | 11181.4 | 11000.8 | 11080.7 | 11006.3 | 10247 | 11048.1 | 11006.4 | 11178.7 | 11034.2 | 10988.3 | 11139.1 | 11155.6 | 11173.2 | 12890.5 | 12790.3 | 11203.2 | 11109.8 | 11062.9 | 11123.5 | 11639.9 | 10977.3 | 11541.3 | 10908.2 | 11293.2 | 12080.7 | 10753.2 | 11630 | 10778.9 | 10976.2 | 11355.8 | 10945.6 | 11553.1 | 10767.1 | 11539.7 | 10795.9 | 10753.7 | 11641.9 | 10856.9 | 11617.5 | 11581.3 | 10799.5 | 11372.3 | 11007.3 | 11144.1 | 10750.5 | 11022.8 | 11253.8 | 11532.2 | 10846 | 11476 | 10620.1 | 11324 | 11191.1 | 10807.4 | 11469.1 | 10645 | 11663 | 10792.7 | 11466.5 | 10829.9 | 11353.4 | 10850.5 | 11613.6 | 10846 | 11261.4 | 10798.9 | 10090.7 | 11393.6 | 11167.7 | 10673 | 11634.2 | 11410 | 10858.9 | 10758.1 | 11425.7 | 10709.1 | 10994.7 | 11562.4 | 10658.6 | 11559.9 | 10649.2 | 11404.1 | 10838.1 | 10679.6 | 9139.3 | 11106.8 | 10364.2 | 11023.3 | 10381.2 | 11054.6 | 10512.8 | 10452.2 | 11120.3 | 10518.1 | 10438 | 11187.9 | 11135.1 | 11101.7 | 10592.5 | 11026.5 | 10227.8 | 10809.5 | 10347.9 | 10680.7 | 9947.7 | 10921 | 10370.8 | 10746.2 | 10806 | 10698.3 | 9840.7 | 10687.7 | 9925 | 10702.2 | 10710.8 | 11659.9 | 10718.6 | 11723.3 | 10888 | 11622.2 | 10790.3 | 10875.8 | 10821.4 | 11541.7 | 11741.4 | 11755 | 11702.1 | 11651.5 | 11661.3 | 11010.7 | 11689.4 | 11765.6 | 11738.6 | 11688.7 | 11732.3 | 11780.5 | 11069.1 | 11811.1 | 11105.6 | 31.7728 | 33.2833 | 31.6915 | 0 | 32.9794 | 33.6829 | 44.9539 | 43.9018 | 44.8101 | 44.8567 | 0 | 0 | 7.0782 | 7.183 | 7.0422 | 7.0763 | 6.9249 | 7.1743 | 11.09 | 10.959 | 11.712 | 10.642 | 10.787 | 12.169 | 7.4529 | 7.5772 | 7.3856 | 7.3805 | 7.4786 | 6.804 | 1.145 | 1.4931 | 1.3898 | 1.6571 | 1.4602 | 1.2003 | 7.2306 | 7.1829 | 7.042 | 7.2291 | 7.1383 |  | 1.256 | 1.5043 | 1.4321 | 1.6717 | 1.509 | 1.5177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382936 | 666 | 371850 | 707 | 166787.68 | 363.933 | 7.4529 | 7.5772 | 7.3856 | 7.3805 | 7.4786 | 6.804 | 7.2306 | 7.1829 | 7.042 | 7.2291 | 7.1383 | 0 | 894000 | 1000 | 877000 | 2000 | 1765000 | 3800 | 1768000 | 1761200 | 13.3167 | 7.3465 | 1.3909 | 7.1646 | 1.4818 | 18.93% | 20.68% | 32.682 | 44.6306 | 7.0798 | 11.2265 | 1774928.2 | 831599 | 981368.6116 | 84.74%
2023-07-16 | 2024 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 335090.89 | 6:12 | 19:24 | 11658.6 | 12175.3 | 12169 | 12141.5 | 12260.3 | 12323.9 | 12265.5 | 12688.9 | 12208.4 | 12077 | 12086.3 | 12209.2 | 12215 | 12168.8 | 12235.9 | 12314.3 | 12101.2 | 12128.4 | 12181.2 | 12250.7 | 12167.7 | 12174.5 | 11839.2 | 11996.8 | 11907.1 | 10539.3 | 11999.6 | 11935 | 12169.2 | 11976.5 | 11861.7 | 12126.9 | 12039.6 | 12119 | 12225.4 | 12084.9 | 12163.7 | 12010.1 | 11979.3 | 12002.9 | 12999.2 | 11776.3 | 12875.1 | 11617.9 | 12333 | 13594.7 | 11518.1 | 12994.3 | 11357.8 | 11629.1 | 12387.3 | 11663.7 | 12748.2 | 11393.3 | 12707.3 | 11381.4 | 11284.4 | 12778.3 | 11334.2 | 12712 | 12664.2 | 11289.3 | 12336.4 | 11673.3 | 11966.1 | 11246.2 | 11660 | 12085.6 | 12646.2 | 11407.9 | 12511.8 | 10907.9 | 12248.6 | 11892.3 | 11255.8 | 12442.4 | 10925.3 | 12743.2 | 11147.4 | 12365.8 | 11375.9 | 12263.1 | 11412.3 | 12730.8 | 11417.6 | 12180.5 | 11460.8 | 10089.6 | 12464.8 | 12050.2 | 11202.6 | 12874.8 | 12502.9 | 11572 | 11399.1 | 12612.3 | 11359 | 11777.7 | 12788.7 | 11228.1 | 12683.2 | 11249.7 | 12347.4 | 11487.8 | 12407.4 | 10781.8 | 12484 | 11291.9 | 12264.9 | 11214.4 | 12340.1 | 11372.2 | 11309.8 | 12440.8 | 11413.8 | 11231.3 | 12487.8 | 12470.6 | 12340.1 | 11506.2 | 12502.1 | 11092.7 | 12046.7 | 11228.7 | 11852.3 | 10486.6 | 12212 | 11309 | 11366.7 | 11516.8 | 11335.5 | 9840.8 | 11287.7 | 9971.9 | 11086.6 | 11063.6 | 12695.8 | 11163.1 | 12745.5 | 11355.3 | 12631.6 | 11197.8 | 11406.9 | 11254.8 | 12222 | 12595.9 | 12576.8 | 12548.9 | 12555.5 | 12618.2 | 11457.3 | 12559.1 | 12675.5 | 12669.3 | 12643.5 | 12665 | 12677.7 | 11396.7 | 12676.8 | 11460.8 | 29.1168 | 32.8913 | 30.4401 | 0 | 32.4842 | 33.311 | 44.5947 | 43.8253 | 44.6936 | 44.7295 | 0 | 0 | 5.6498 | 5.7318 | 5.3536 | 5.7646 | 5.5507 | 5.8398 | 9.917 | 9.031 | 9.927 | 9.26 | 9.279 | 9.204 | 6.9447 | 7.0693 | 6.9433 | 6.8355 | 7.0057 | 6.1294 | 1.0779 | 1.4338 | 1.3225 | 1.5555 | 1.3936 | 1.0962 | 6.7738 | 6.7388 | 6.6682 | 6.7501 | 6.7708 |  | 1.1879 | 1.4358 | 1.3734 | 1.5657 | 1.4431 | 1.3966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 383996 | 667 | 372793 | 708 | 168685.08 | 367.867 | 6.9447 | 7.0693 | 6.9433 | 6.8355 | 7.0057 | 6.1294 | 6.7738 | 6.7388 | 6.6682 | 6.7501 | 6.7708 | 0 | 1060000 | 1000 | 943000 | 1000 | 1897400 | 3934 | 2001000 | 1893466 | 13.2 | 6.8213 | 1.3133 | 6.7403 | 1.4004 | 19.25% | 20.78% | 31.6487 | 44.4608 | 5.6484 | 9.4363 | 1910216.6 | 1896400 | 2276637.0472 | 83.3%
2023-07-17 | 2024 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 335090.89 | 6:00 | 19:40 | 11558.8 | 12060.8 | 12104.9 | 12063 | 12208 | 12254.5 | 12152.5 | 12633.5 | 12129.3 | 12050.6 | 11951.9 | 12108.1 | 12126.3 | 12043.1 | 12123.4 | 12230.5 | 12029.9 | 12101.6 | 12111.2 | 12149.6 | 12154.6 | 12131.4 | 11858.3 | 11995.2 | 11875.4 | 10432.9 | 11917.1 | 11868.5 | 12210.3 | 12043.3 | 11916.4 | 12173.4 | 12129.3 | 12185.8 | 12213.1 | 12102.5 | 12240.2 | 12098.6 | 12071.3 | 12120.5 | 13096.9 | 11709.2 | 12966.8 | 11526 | 12290.4 | 13674.3 | 11461.4 | 13114.4 | 11175.3 | 11443 | 12293.1 | 11522.9 | 12732.1 | 11242.5 | 12616.3 | 11219.6 | 11132.7 | 12763.2 | 11173.9 | 12689.8 | 12657.1 | 11147.2 | 12315 | 11633.3 | 11897.4 | 11177.5 | 11694.2 | 12268.6 | 12644 | 11421.6 | 12583.9 | 10983.8 | 12213.2 | 11983.7 | 5661.9 | 6361.1 | 11018 | 12869.7 | 11236.5 | 12587.1 | 11477.1 | 12484.2 | 11543.4 | 12909.5 | 11466.4 | 12275.6 | 11455.6 | 10063.7 | 12462.8 | 12018.9 | 11095 | 12950.5 | 12544.1 | 11513.1 | 11382.8 | 12616.6 | 11189.7 | 11662.7 | 12833.2 | 11102.9 | 12842.2 | 11120.8 | 12450.2 | 11394.5 | 12592.7 | 10774.9 | 12677.2 | 11359.7 | 12449.1 | 11318.8 | 12555.6 | 11521 | 11184.9 | 12442.3 | 11315.7 | 11123.1 | 12586.6 | 12514 | 12449.5 | 11435.5 | 12636.2 | 11078.5 | 12219.7 | 11346.4 | 12075.3 | 10558.4 | 12330.2 | 11313.8 | 11273.9 | 11473.2 | 11286.9 | 9763.8 | 11186.6 | 9883.7 | 11194.8 | 11211.3 | 13173.5 | 11443.2 | 13228 | 11669.4 | 13091.3 | 11489.6 | 11688.3 | 11468.2 | 12679.4 | 13181.2 | 13107.3 | 13076.8 | 13035.5 | 13095.9 | 11793.1 | 13091.7 | 13134.6 | 13172.5 | 13189.8 | 13148.3 | 13186.1 | 11750.3 | 13171 | 11837.3 | 32.9782 | 33.8325 | 31.5819 | 33.5315 | 33.4626 | 34.2059 | 0 | 46 | 0 | 0 | 46.4 | 0 | 4.5332 | 4.5804 | 4.5525 | 4.4985 | 4.4701 | 4.5862 | 7.345 | 7.687 | 7.557 | 7.698 | 7.462 | 6.955 | 6.891 | 7.0343 | 6.8596 | 6.7466 | 6.8646 | 6.3051 | 1.0659 | 1.4135 | 1.3049 | 1.542 | 1.3408 | 1.1279 | 6.6986 | 6.7255 | 6.6247 | 6.6909 | 6.7 |  | 1.1678 | 1.4138 | 1.3537 | 1.5576 | 1.3915 | 1.4293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 384943 | 669 | 373748 | 710 | 170580.813 | 371.867 | 6.891 | 7.0343 | 6.8596 | 6.7466 | 6.8646 | 6.3051 | 6.6986 | 6.7255 | 6.6247 | 6.6909 | 6.7 | 0 | 947000 | 2000 | 955000 | 2000 | 1895733 | 4000 | 1898000 | 1891733 | 13.6667 | 6.7835 | 1.2992 | 6.6879 | 1.3856 | 19.15% | 20.72% | 33.2654 | 46.2 | 4.5368 | 7.4507 | 1909019.3 | 1894200 | 2235733.0232 | 84.72%
2023-07-18 | 2024 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 335090.89 | 6:05 | 19:35 | 11345.9 | 11829.2 | 11894.3 | 11847.3 | 12010.8 | 12072.6 | 11952.4 | 12379.9 | 11890.9 | 11797.1 | 11723 | 11874.5 | 11928.3 | 11816.1 | 11936.1 | 12044.2 | 11864.4 | 11942.9 | 11941.8 | 11970.2 | 12000.9 | 11978.7 | 11723.6 | 11846.6 | 11722.6 | 10284.5 | 11750 | 11718.7 | 12059.8 | 11889.6 | 11783.1 | 12046.2 | 11967.3 | 12008.3 | 12035.9 | 11951.6 | 12097.5 | 11948.4 | 11930.8 | 11957.8 | 12953.7 | 11594.5 | 12820 | 11409.6 | 12233.5 | 13601.2 | 11366.2 | 12959 | 10995.6 | 11256.4 | 12104.4 | 11352.6 | 12545 | 11141.6 | 12414.3 | 11056.8 | 10960.4 | 12547.1 | 10995.2 | 12484.3 | 12450.5 | 10970.2 | 12094 | 11422.1 | 11711.4 | 10998.8 | 11516.4 | 12087 | 12438.7 | 11245.4 | 12375.6 | 10814.1 | 12032 | 11794.1 | 11047.7 | 12413.5 | 10840.3 | 12642.5 | 11046.4 | 12362.6 | 11308 | 12291 | 11362.9 | 12715.4 | 11295.8 | 12077 | 11292.1 | 9915.6 | 12215.8 | 11836.2 | 10918.4 | 12706.4 | 12336.5 | 11329.3 | 11203.8 | 12410.1 | 11051.9 | 11495.7 | 12631.2 | 10943.4 | 12665.6 | 10978.1 | 12293.1 | 11236.1 | 12416.4 | 10604.7 | 12495.7 | 11219.5 | 12269.1 | 11160.7 | 12368.9 | 11371.2 | 11006.1 | 12256.6 | 11147.8 | 10971.1 | 12388.4 | 12319.1 | 12271 | 11274.8 | 12437.2 | 10939.4 | 12050.6 | 11195.4 | 11891.3 | 10400.7 | 12152.1 | 11152.5 | 11124.2 | 11292.5 | 11082.1 | 9600.4 | 11051.2 | 9712.9 | 11008 | 11022.9 | 12924.7 | 11249.5 | 13009.4 | 11479.8 | 12845.3 | 11285.3 | 11488.8 | 11204.9 | 12472 | 12956.7 | 12860.9 | 12830.3 | 12789.8 | 12858 | 11612 | 12867.9 | 12856.3 | 12905.1 | 12965.8 | 12928.8 | 12949.6 | 11574.8 | 12899.4 | 11637.8 | 33.2459 | 34.7758 | 31.9229 | 34.4732 | 34.3636 | 35.227 | 0 | 46.5 | 0 | 0 | 46.7 | 0 | 4.7542 | 4.8905 | 4.6449 | 4.8507 | 4.7768 | 4.7675 | 7.953 | 8.011 | 8.06 | 8.055 | 8.32 | 8.151 | 6.8071 | 6.9924 | 6.8423 | 6.6805 | 6.6991 | 6.2359 | 1.0457 | 1.4006 | 1.2892 | 1.5189 | 1.2847 | 1.1099 | 6.6014 | 6.6708 | 6.5848 | 6.6045 | 6.5604 |  | 1.1488 | 1.4001 | 1.3415 | 1.5327 | 1.3443 | 1.4069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385788 | 670 | 374688 | 711 | 172459.547 | 375.8 | 6.8071 | 6.9924 | 6.8423 | 6.6805 | 6.6991 | 6.2359 | 6.6014 | 6.6708 | 6.5848 | 6.6045 | 6.5604 | 0 | 845000 | 1000 | 940000 | 1000 | 1878734 | 3933 | 1783000 | 1874801 | 13.5 | 6.7095 | 1.2749 | 6.6044 | 1.3624 | 19% | 20.63% | 34.0014 | 46.6 | 4.7808 | 8.0917 | 1891475.3 | 1877200 | 2208697.312 | 84.99%
2023-07-19 | 2024 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 335090.89 | 6:07 | 19:07 | 9623.9 | 10084.4 | 10089.1 | 10077.8 | 10151.6 | 10182.9 | 10164.6 | 10540.8 | 10111.9 | 10067.8 | 9965 | 10099.3 | 10077.2 | 10025.6 | 10091.9 | 10159.8 | 10004.5 | 10071.8 | 10105.5 | 10143.9 | 10116.5 | 10113.1 | 9810.1 | 9964 | 9852.2 | 8683.3 | 9940.4 | 9888.2 | 10117.4 | 9928.6 | 9775.3 | 10063.6 | 9991.6 | 10030.2 | 10123.6 | 10032.4 | 10101.4 | 9946.8 | 9910.9 | 9948.1 | 10732.5 | 9603.1 | 10566.8 | 9407 | 10068.2 | 11156.2 | 9383.9 | 10702.7 | 9285.2 | 9523 | 10217 | 9573.5 | 10567.5 | 9419.2 | 10444.1 | 9315.1 | 9251.7 | 10545.8 | 9304.7 | 10524.7 | 10509.5 | 9293.8 | 10222.6 | 9691.1 | 9861.6 | 9280.1 | 9732 | 10150 | 10453.5 | 9443.7 | 10394.4 | 9059.6 | 10109 | 9896.5 | 9306 | 10440.3 | 9163.6 | 10642.2 | 9353.4 | 10464 | 9477.5 | 10257.3 | 9594.7 | 10620 | 9498.2 | 10145.4 | 9472.7 | 8320.9 | 10293.9 | 9902.3 | 9158.9 | 10618.4 | 10274.3 | 9434.9 | 9324.8 | 10337.7 | 9204.2 | 9547.9 | 10465.3 | 9064.5 | 10487.8 | 9093.4 | 10154.6 | 9322.8 | 10267.7 | 8817.1 | 10322.4 | 9254.4 | 10140.1 | 9227.4 | 10233.7 | 9381 | 9143.2 | 10137.7 | 9236.7 | 9062.9 | 10238.2 | 10238.6 | 10120 | 9304.1 | 10246.8 | 9139.8 | 9942.8 | 9243.9 | 9813.9 | 8547.7 | 9980.4 | 9143.3 | 9327.9 | 9345.9 | 9129.2 | 7929.6 | 9154.5 | 8068.6 | 9081.7 | 9099.8 | 10554.7 | 9220.5 | 10603.1 | 9415 | 10515.2 | 9295 | 9434.8 | 9290.2 | 10262.1 | 10614.7 | 10581.3 | 10526.7 | 10489.9 | 10506.7 | 9499.3 | 10508.2 | 10653.3 | 10670.4 | 10664.1 | 10640.9 | 10668 | 9555.6 | 10702.6 | 9619.1 | 29.1726 | 33.4071 | 31.9092 | 33.2407 | 33.2307 | 33.6352 | 0 | 46.5 | 0 | 0 | 46.5 | 0 | 3.7811 | 3.6753 | 3.6846 | 3.7261 | 3.7972 | 3.3893 | 11.601 | 11.214 | 10.868 | 11.526 | 11.209 | 10.312 | 5.6802 | 5.7643 | 5.6272 | 5.5788 | 5.5001 | 5.0723 | 0.90318 | 1.0887 | 1.0731 | 1.2663 | 1.0143 | 0.86356 | 5.5759 | 5.5797 | 5.5167 | 5.6056 | 5.4536 |  | 0.97271 | 1.0891 | 1.1026 | 1.2878 | 1.0587 | 1.093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 386582 | 671 | 375465 | 713 | 174026.014 | 379.533 | 5.6802 | 5.7643 | 5.6272 | 5.5788 | 5.5001 | 5.0723 | 5.5759 | 5.5797 | 5.5167 | 5.6056 | 5.4536 | 0 | 794000 | 1000 | 777000 | 2000 | 1566467 | 3733 | 1568000 | 1562734 | 13 | 5.5371 | 1.0349 | 5.5463 | 1.1006 | 18.69% | 19.84% | 32.4326 | 46.5 | 3.6756 | 11.1217 | 1578120.6 | 1564333 | 1842234.7497 | 84.91%
2023-07-20 | 2024 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 335090.89 | 6:00 | 19:30 | 8563.5 | 8985.5 | 9004.4 | 8970.6 | 9076.6 | 9116.9 | 9088 | 9401 | 9005.7 | 8926.1 | 8933.1 | 9037.4 | 9006.9 | 8999.5 | 9075.5 | 9087.8 | 8955.3 | 8956.1 | 8990.2 | 9064.7 | 9024.1 | 9017 | 8825.3 | 8921.1 | 8833.3 | 7923.9 | 8937.4 | 8845 | 9038 | 8901.8 | 8780.5 | 8990.6 | 8923.2 | 9030.8 | 9110.9 | 9013.3 | 9027 | 8884.2 | 8834.3 | 8813.6 | 9578.3 | 8731.9 | 9476.2 | 8609.7 | 9116.1 | 10060.2 | 8562.9 | 9567.6 | 8456.6 | 8654.4 | 9204.4 | 8700.8 | 9471.8 | 8533.8 | 9397.2 | 8519.1 | 8368.3 | 9401.9 | 8450.6 | 9376.1 | 9344.3 | 8422.6 | 9050.6 | 8622.1 | 8886.8 | 8480.7 | 8801.8 | 9219.2 | 9346 | 8650.5 | 9338.2 | 8375.6 | 9088.8 | 9003.6 | 8475.1 | 9405 | 8375.4 | 9470.5 | 8477.1 | 9351.7 | 8750.7 | 9387.1 | 8823.2 | 9639.4 | 8729.5 | 9247.7 | 8690.8 | 7733.5 | 9475 | 9092.9 | 8514.2 | 9681.5 | 9346.6 | 8645.7 | 8514 | 9479 | 8643.7 | 8877.1 | 9600.8 | 8471 | 9563.5 | 8470.7 | 9308.4 | 8649.4 | 9317.1 | 8183.8 | 9361.2 | 8526.8 | 9139.5 | 8416.8 | 9163 | 8576.1 | 8538.8 | 9320.3 | 8586.4 | 8427 | 9381.3 | 9418.8 | 9257.3 | 8595.3 | 9343.3 | 8455.1 | 9087.2 | 8514.5 | 8981.6 | 7950.7 | 9149.5 | 8472 | 8655.2 | 8700.3 | 8480.6 | 7395.1 | 8474.4 | 7558.2 | 8505.2 | 8531 | 9758.4 | 8580.5 | 9722.8 | 8726.2 | 9647.9 | 8613 | 8714.1 | 8663.4 | 9427.8 | 9676.8 | 9789.1 | 9725.1 | 9725 | 9732.4 | 8810.9 | 9618.4 | 9789.3 | 9762.3 | 9727.4 | 9676.1 | 9690.7 | 8776.7 | 9868.5 | 8892.9 | 30.0602 | 32.4338 | 30.3224 | 32.4053 | 32.3526 | 32.5429 | 0 | 42.2 | 0 | 0 | 42.6 | 0 | 2.9773 | 2.9148 | 2.9151 | 2.899 | 2.9524 | 2.8659 | 6.211 | 5.816 | 5.836 | 6.339 | 7.023 | 6.663 | 5.1259 | 5.209 | 5.1946 | 5.0546 | 5.0859 | 4.7406 | 0.75312 | 0.99483 | 0.93491 | 1.0923 | 0.95424 | 0.79374 | 4.9641 | 4.9274 | 4.9491 | 4.9592 | 4.8967 |  | 0.83722 | 0.99191 | 0.9846 | 1.0945 | 0.99186 | 1.0194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 387297 | 672 | 376192 | 714 | 175453.48 | 382.067 | 5.1259 | 5.209 | 5.1946 | 5.0546 | 5.0859 | 4.7406 | 4.9641 | 4.9274 | 4.9491 | 4.9592 | 4.8967 | 0 | 715000 | 1000 | 727000 | 1000 | 1427466 | 2534 | 1440000 | 1424932 | 13.5 | 5.0684 | 0.92053 | 4.9393 | 0.98658 | 18.16% | 19.97% | 31.6862 | 42.4 | 2.9208 | 6.3147 | 1435258.1 | 1423467 | 1671219.7432 | 85.18%
2023-07-21 | 2024 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 335090.89 | 6:00 | 19:28 | 10647.3 | 11178.5 | 11086 | 11086.6 | 11112.9 | 11192.3 | 11254.8 | 11625 | 11254.2 | 11123 | 11123.6 | 11286.8 | 11179.8 | 11148 | 11169.3 | 11257 | 11101.8 | 11215 | 11233.5 | 11277.6 | 11176.8 | 11236.1 | 10793.2 | 10968.4 | 10684.8 | 9487.5 | 11010.6 | 10867.8 | 11050.1 | 10948.6 | 10807.7 | 10998.1 | 11007.8 | 10973.7 | 11026.7 | 10967 | 11045.4 | 10960.8 | 10963 | 11039.1 | 11866.9 | 10882.6 | 11862.7 | 10740.5 | 11413.7 | 12307.9 | 10582.8 | 11808.5 | 10318.9 | 10581.9 | 11332.6 | 10630.7 | 11647.6 | 10426.9 | 11531.3 | 10288.5 | 10257 | 11532.7 | 10351 | 11557.1 | 11567.3 | 10363.4 | 11317.4 | 10827.6 | 10798.9 | 10129.6 | 10611.3 | 11033.7 | 11421.2 | 10297.3 | 11357.1 | 9876 | 11162.7 | 10891 | 10298.1 | 11457.7 | 10097 | 11720.5 | 10372.8 | 11563.6 | 10407.9 | 11105.1 | 10587.9 | 11590.9 | 10472.1 | 11213.6 | 10422.8 | 9215.3 | 11312.9 | 10909.9 | 10064 | 11601.8 | 11335.1 | 10484.1 | 10359.2 | 11465.4 | 10389.9 | 10802.1 | 11807 | 10360.4 | 11858 | 10360.1 | 11557.6 | 10596.7 | 11568.9 | 9979.7 | 11590.4 | 10418.9 | 11404.1 | 10369.6 | 11434.3 | 10426.2 | 10434.6 | 11510.3 | 10495.8 | 10277.2 | 11474.2 | 11496.7 | 11290.7 | 10387 | 11377.4 | 10196.4 | 11078.2 | 10246.1 | 10866.3 | 9516.1 | 11129.5 | 10205.5 | 10500.8 | 10559.7 | 10199.5 | 8911.7 | 10265.5 | 9124.6 | 10263.8 | 10310.5 | 11929.5 | 10539 | 11928.1 | 10737.1 | 11835 | 10547.7 | 10701.3 | 10566.3 | 11451 | 11785.8 | 11692.7 | 11724.2 | 11770.2 | 11823.2 | 10809.4 | 11769.1 | 11821.4 | 11779.9 | 11811.3 | 11727.3 | 11744.5 | 10635.2 | 11806.8 | 10682.9 | 32.9541 | 34.1761 | 32.5253 | 34.056 | 34.0398 | 34.4336 | 0 | 48 | 0 | 0 | 48.6 | 0 | 2.6978 | 2.5986 | 2.5026 | 2.6867 | 2.7155 | 2.3887 | 6.291 | 5.783 | 5.992 | 6.404 | 5.842 | 6.112 | 6.4382 | 6.3375 | 6.4899 | 6.1798 | 6.4756 | 5.8151 | 1.0408 | 1.1176 | 1.2459 | 1.4305 | 1.1371 | 0.91296 | 6.2204 | 6.093 | 6.3413 | 6.1753 | 6.2646 |  | 1.1078 | 1.1199 | 1.2672 | 1.4578 | 1.1752 | 1.1549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 388174 | 673 | 377051 | 715 | 177194 | 385.667 | 6.4382 | 6.3375 | 6.4899 | 6.1798 | 6.4756 | 5.8151 | 6.2204 | 6.093 | 6.3413 | 6.1753 | 6.2646 | 0 | 877000 | 1000 | 859000 | 1000 | 1740520 | 3600 | 1734000 | 1736920 | 13.4667 | 6.2893 | 1.1475 | 6.2189 | 1.2138 | 18.24% | 19.52% | 33.6975 | 48.3 | 2.5983 | 6.0707 | 1753861.1 | 1737401 | 2054951.4756 | 84.55%
2023-07-22 | 2024 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 335090.89 | 6:07 | 19:30 | 8847.4 | 9359.5 | 9325.2 | 9287.8 | 9348.9 | 9470.4 | 9453.6 | 9786 | 9377.4 | 9231.5 | 9306.1 | 9439.1 | 9379.9 | 9329.5 | 9390.6 | 9441.3 | 9217.4 | 9161.1 | 9170.5 | 9286.4 | 9221.6 | 9168.5 | 9108.2 | 9159 | 9099.6 | 8007.3 | 9162.3 | 9113.7 | 9365.8 | 9271.6 | 9130.6 | 9244.9 | 9200.9 | 9237.6 | 9354.2 | 9273.4 | 9358.8 | 9276.3 | 9254.3 | 9214.1 | 10153.6 | 9154.8 | 9986.3 | 9008.9 | 9620.2 | 10577.2 | 8959.8 | 10123.5 | 8707.5 | 8922.4 | 9515 | 8874.1 | 9750.8 | 8706.6 | 9646 | 8623.1 | 8586.8 | 9717.1 | 8748.1 | 9713 | 9715.3 | 8764.7 | 9414.4 | 8911.2 | 9119.4 | 8463.3 | 9045.1 | 9291.7 | 9653.5 | 8723.2 | 9620.1 | 8486.9 | 9353 | 9287.7 | 8637.9 | 9794.1 | 8579.5 | 9814.8 | 8650.2 | 9715.8 | 8804.9 | 9536.1 | 8912 | 9768.6 | 8758.2 | 9317.6 | 8601.9 | 7633.9 | 9346.3 | 8994.8 | 8291.9 | 9546.2 | 9227.6 | 8509.6 | 8434 | 9273.8 | 8354.8 | 8729.8 | 9569.6 | 8403.6 | 9497.5 | 8395.3 | 9393.5 | 8626.3 | 9595 | 8201.5 | 9681.6 | 8585 | 9616.9 | 8761 | 9705.7 | 8823.8 | 8448.5 | 9274.4 | 8493 | 8306.3 | 9307.5 | 9248 | 9094.1 | 8406.7 | 9180.3 | 8253.7 | 9047.3 | 8435.8 | 8906.4 | 7796.2 | 9025.2 | 8402.9 | 8536.2 | 8623.3 | 8436.6 | 7236.4 | 8470 | 7592.8 | 8507.3 | 8482.7 | 10028 | 8719 | 10015 | 8865.3 | 9774.3 | 8623.3 | 8743.8 | 8607.6 | 9731.5 | 9952.7 | 10135.5 | 10031 | 10009.1 | 10004.6 | 9029.7 | 9907.1 | 10264.2 | 10165.9 | 10129.8 | 10059.6 | 10063.6 | 9030.5 | 10404.1 | 9180.3 | 28.0709 | 30.4341 | 27.1068 | 30.3887 | 30.4336 | 30.6259 | 0 | 44.2 | 0 | 0 | 42.1 | 0 | 2.738 | 2.6875 | 2.611 | 2.7631 | 2.6502 | 2.55 | 9.224 | 11.026 | 9.642 | 7.498 | 7.839 | 7.283 | 5.2846 | 5.2958 | 5.3805 | 5.1683 | 5.0823 | 4.8694 | 0.72477 | 0.74349 | 0.88517 | 0.93325 | 0.71716 | 0.67456 | 5.1258 | 5.0768 | 5.2231 | 5.1461 | 4.8985 |  | 0.77911 | 0.7311 | 0.92205 | 0.94639 | 0.76158 | 0.84533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 388912 | 674 | 377773 | 717 | 178648.5 | 389.733 | 5.2846 | 5.2958 | 5.3805 | 5.1683 | 5.0823 | 4.8694 | 5.1258 | 5.0768 | 5.2231 | 5.1461 | 4.8985 | 0 | 738000 | 1000 | 722000 | 2000 | 1454500 | 4066 | 1457000 | 1450434 | 13.3833 | 5.1802 | 0.77973 | 5.0941 | 0.83093 | 15.05% | 16.31% | 29.51 | 43.15 | 2.6666 | 8.752 | 1463854.3 | 1450333 | 1721976.144 | 84.22%
2023-07-23 | 2024 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 335090.89 | 6:06 | 19:29 | 9475.4 | 9891.2 | 9873.9 | 9853.1 | 9923.9 | 9945.9 | 9948.9 | 10306.4 | 9929.9 | 9938.9 | 9760.5 | 9890.3 | 9851.1 | 9819.2 | 9906.3 | 9944.5 | 9793.2 | 9815.2 | 9822 | 9883.2 | 9851.7 | 9844 | 9584.3 | 9712.4 | 9641 | 8541.8 | 9651.2 | 9594.6 | 9868.5 | 9744.3 | 9674.4 | 9880.7 | 9926.8 | 9968 | 9984.5 | 9921.4 | 9989.6 | 9872.7 | 9830.2 | 9887.2 | 10559.6 | 9541.4 | 10393.9 | 9353.9 | 9924.6 | 11046.7 | 9357.4 | 10570.8 | 9160.7 | 9389.4 | 9984.7 | 9434.5 | 10289.3 | 9247.9 | 10299.4 | 9226.9 | 9195.4 | 10434.5 | 9181 | 10335.2 | 10329.4 | 9167.5 | 10065.9 | 9605.1 | 9751.2 | 9202.3 | 9667.4 | 10036.2 | 10304.7 | 9378.8 | 10236.8 | 9065.3 | 10037.6 | 9826.6 | 9298.8 | 10308.6 | 9116.6 | 10516.1 | 9311.1 | 10315.4 | 9362.7 | 10044.1 | 9522.2 | 10394.8 | 9377.9 | 9987.4 | 9349.7 | 8296.2 | 10179.8 | 9762.7 | 9128.6 | 10478 | 10217.3 | 9490.9 | 9388.5 | 10238.5 | 9290.2 | 9635 | 10463.3 | 9261.8 | 10448.7 | 9235.2 | 10201.4 | 9472.9 | 10301.4 | 8969.3 | 10385.2 | 9435.3 | 10236.7 | 9412.9 | 10309.3 | 9558.5 | 9366 | 10323.4 | 9472.8 | 9321.3 | 10401.7 | 10513.4 | 10275.7 | 9670.6 | 10459.6 | 9513.9 | 10093.2 | 9467.7 | 10027.2 | 8952 | 10285.2 | 9578.8 | 9737.2 | 9759.8 | 9624.6 | 8375.9 | 9555.7 | 8503.7 | 9620.6 | 9640.8 | 10876 | 9659.1 | 10925.5 | 9853 | 10823.1 | 9761.9 | 9868.9 | 9773.5 | 10595.6 | 10901.3 | 10879.2 | 10845.4 | 10799.8 | 10828.4 | 9976.1 | 10844.3 | 10894.8 | 10924.9 | 10982.1 | 10917.3 | 10931 | 9949.1 | 10921.4 | 10010.7 | 30.5075 | 31.8182 | 30.1769 | 31.7266 | 31.7465 | 31.9857 | 0 | 40.8 | 0 | 0 | 40.9 | 0 | 4.5394 | 4.7069 | 4.4817 | 4.6797 | 4.6872 | 4.5265 | 10.49 | 10.718 | 10.165 | 9.806 | 9.667 | 9.04 | 5.5668 | 5.5959 | 5.5925 | 5.4809 | 5.7653 | 5.7999 | 0.75893 | 0.74935 | 0.94527 | 0.95792 | 0.78855 | 0.82846 | 5.3517 | 5.3184 | 5.3791 | 5.4117 | 5.5318 |  | 0.81347 | 0.73596 | 0.97405 | 0.98854 | 0.83914 | 0.85689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 389695 | 675 | 378568 | 718 | 180220.547 | 393.667 | 5.5668 | 5.5959 | 5.5925 | 5.4809 | 5.7653 | 5.7999 | 5.3517 | 5.3184 | 5.3791 | 5.4117 | 5.5318 | 0 | 783000 | 1000 | 795000 | 1000 | 1572047 | 3934 | 1576000 | 1568113 | 13.3833 | 5.6336 | 0.83808 | 5.3985 | 0.86801 | 14.88% | 16.08% | 31.3269 | 40.85 | 4.6036 | 9.981 | 1582130.5 | 1570400 | 1835150.7929 | 85.57%
2023-07-24 | 2024 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 335090.89 | 5:55 | 19:26 | 9417.8 | 9887.9 | 9883.6 | 9859.5 | 9926 | 9978 | 9987 | 10399.3 | 9954.6 | 9885.5 | 9880.9 | 9994 | 10022.9 | 9985 | 10033.8 | 10100.9 | 9952.2 | 10047.3 | 10065 | 10108.8 | 10071 | 10063.9 | 9799.7 | 9919.8 | 9734.2 | 8590.8 | 9826.9 | 9764.5 | 10055.2 | 9918.7 | 9813 | 10011.8 | 9876.5 | 9927.6 | 10036.9 | 9954.5 | 10023.8 | 9914.1 | 9863.5 | 9848.7 | 10690.1 | 9590.7 | 10578.9 | 9441.9 | 10122.3 | 11333.1 | 9448.6 | 10704.3 | 9313.3 | 9524 | 10187.2 | 9494.7 | 10498.3 | 9429.6 | 10347.4 | 9250.2 | 9170.9 | 10428.8 | 9305.9 | 10415.4 | 10412.3 | 9259.8 | 10055.8 | 9552.1 | 9697.2 | 9174.6 | 9490.9 | 9919.6 | 10280.7 | 9334 | 10227.1 | 8977.3 | 9973.9 | 9763.3 | 9177.6 | 10255.6 | 8995.5 | 10442 | 9172.4 | 10240 | 9391.6 | 10156.4 | 9545.9 | 10503.6 | 9418.1 | 10059.1 | 9396 | 8291.1 | 10241.2 | 9843.9 | 9115.6 | 10550.2 | 10237.8 | 9439.3 | 9330.1 | 10296.1 | 9221.9 | 9518.4 | 10402.8 | 9051 | 10477.4 | 9073.7 | 10165.3 | 9294.2 | 10265.6 | 8799.1 | 10287.2 | 9162.1 | 10121.1 | 9171.4 | 10118.7 | 9247.3 | 9073.6 | 10000.9 | 9145.5 | 8967.7 | 10117.9 | 10184.1 | 9985.2 | 9214.8 | 10107.3 | 9055 | 9804 | 9140 | 9720.5 | 8448.5 | 9857.5 | 9038.7 | 9249.9 | 9294.1 | 9064.7 | 7859.5 | 9066.3 | 8038.1 | 9069.3 | 9099.7 | 10488.3 | 9154 | 10565.5 | 9370.8 | 10462.9 | 9238.3 | 9365 | 9259.3 | 10161.5 | 10527.4 | 10519.6 | 10451.5 | 10420.2 | 10434.2 | 9475.9 | 10434.6 | 10523.2 | 10573.7 | 10594.3 | 10534.7 | 10546.1 | 9460.4 | 10631.2 | 9528.2 | 29.1537 | 31.6695 | 27.7975 | 31.4882 | 31.5122 | 31.8524 | 0 | 45.7 | 0 | 0 | 42.9 | 0 | 3.4471 | 3.4113 | 3.2611 | 3.3956 | 3.4414 | 3.0482 | 5.937 | 7.908 | 5.933 | 7.354 | 6.361 | 7.896 | 5.5079 | 5.6038 | 5.54 | 5.3328 | 5.3846 | 5.3454 | 0.7619 | 0.81268 | 0.95735 | 1.0215 | 0.81524 | 0.80157 | 5.355 | 5.3622 | 5.3753 | 5.3011 | 5.1902 |  | 0.83299 | 0.79902 | 1.002 | 1.0352 | 0.85187 | 0.83856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390493 | 677 | 379341 | 719 | 181777.5 | 397.6 | 5.5079 | 5.6038 | 5.54 | 5.3328 | 5.3846 | 5.3454 | 5.355 | 5.3622 | 5.3753 | 5.3011 | 5.1902 | 0 | 798000 | 2000 | 773000 | 1000 | 1556953 | 3933 | 1568000 | 1553020 | 13.5167 | 5.4524 | 0.86171 | 5.3168 | 0.89327 | 15.8% | 16.8% | 30.5789 | 44.3 | 3.3341 | 6.8982 | 1565579.2 | 1550534 | 1810754.1171 | 85.63%
2023-07-25 | 2024 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 335090.89 | 6:09 | 19:20 | 9332 | 9638.3 | 9709 | 9698.2 | 9759.6 | 9714.4 | 9645.1 | 10022.6 | 9655.9 | 9766.8 | 9568.1 | 9637 | 9697.8 | 9620.6 | 9716.3 | 9770.8 | 9667.4 | 9674.5 | 9671.1 | 9738.4 | 9743.9 | 9716.9 | 9594 | 9666.4 | 9627.5 | 8581.2 | 9588.8 | 9587.4 | 9877.4 | 9725.2 | 9594.9 | 9809.6 | 9690.8 | 9691.7 | 9865.7 | 9732.6 | 9795.2 | 9639.1 | 9633.5 | 9639.8 | 10076.7 | 9145.3 | 9949.2 | 8946 | 9612.6 | 10631 | 9116.4 | 10145.6 | 8960.6 | 9192.3 | 9747 | 9309 | 10043.6 | 9077.8 | 10115.2 | 9193.1 | 8978.9 | 10054.3 | 8955.1 | 10024.9 | 9951.3 | 8923 | 9695.7 | 9218.2 | 9512.4 | 9187.1 | 9227.8 | 9815.2 | 9900.6 | 9258.5 | 9838.5 | 8897.5 | 9611.2 | 9501.2 | 8914.4 | 9860 | 8754.9 | 10033.2 | 8934.7 | 9888.4 | 9374.4 | 10013.8 | 9424.5 | 10321.9 | 9288.1 | 9818.9 | 9248.1 | 8147.9 | 9934.5 | 9582 | 8877.1 | 10120.6 | 9833.2 | 9171.6 | 9084.1 | 9947.9 | 8881.4 | 9135.8 | 9904 | 8817.3 | 9971.8 | 8847 | 9807.5 | 9106.1 | 9943.7 | 8697.8 | 10024 | 9096.5 | 9937 | 9173.8 | 10039.7 | 9248.8 | 8886.1 | 9740.2 | 9050.9 | 8881 | 9905.6 | 9922.7 | 9803.3 | 9197.8 | 9986.3 | 9102.6 | 9658.2 | 9074 | 9661.8 | 8614.5 | 9891.9 | 9230 | 9327.6 | 9394.7 | 9262.2 | 7993.7 | 9168.2 | 8136.2 | 9254.8 | 9246.9 | 10174 | 9098.8 | 10204.1 | 9230 | 10256.7 | 9268.6 | 9406.2 | 9409.3 | 9735.9 | 10017.9 | 10031.3 | 10010.4 | 10015 | 10069.5 | 9213.6 | 9989.4 | 9815.5 | 9947.4 | 9984.4 | 9936.3 | 9973.8 | 9054.7 | 9960.1 | 9125.3 | 31.0855 | 31.391 | 26.816 | 31.1894 | 31.1119 | 31.4577 | 0 | 46.6 | 0 | 0 | 43 | 0 | 3.2355 | 3.5047 | 2.9345 | 3.6297 | 3.4712 | 3.4154 | 8.798 | 8.455 | 8.799 | 8.152 | 8.128 | 8.811 | 5.4165 | 5.6205 | 5.3514 | 5.2879 | 5.3755 | 5.2295 | 0.70784 | 0.87063 | 0.89847 | 1.0541 | 0.861 | 0.8122 | 5.3484 | 5.4259 | 5.2279 | 5.2947 | 5.3103 |  | 0.77811 | 0.85701 | 0.93627 | 1.0623 | 0.89096 | 0.85008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 391248 | 678 | 380098 | 721 | 183294.481 | 401.667 | 5.4165 | 5.6205 | 5.3514 | 5.2879 | 5.3755 | 5.2295 | 5.3484 | 5.4259 | 5.2279 | 5.2947 | 5.3103 | 0 | 755000 | 1000 | 757000 | 2000 | 1516981 | 4067 | 1509000 | 1512914 | 13.1833 | 5.3802 | 0.86738 | 5.3215 | 0.89579 | 16.12% | 16.83% | 30.5086 | 44.8 | 3.3651 | 8.5238 | 1525844.1 | 1504799 | 1806036.9973 | 83.32%
2023-07-26 | 2024 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 335090.89 | 6:14 | 19:29 | 7870.5 | 8372.6 | 8408.4 | 8271.7 | 8503.1 | 8584.2 | 8535.3 | 8888 | 8329.9 | 8235.9 | 8301.7 | 8376.5 | 8476 | 8384.7 | 8613.1 | 8620.7 | 8554.2 | 8639.4 | 8577.2 | 8562.9 | 8715.6 | 8638.9 | 8573 | 8640.7 | 8270.3 | 7289.3 | 8342.5 | 8368.5 | 8753.7 | 8720.4 | 8601.1 | 8727.1 | 8663 | 8620.7 | 8649.9 | 8644.4 | 8794.8 | 8688.4 | 8642.9 | 8653 | 9585 | 8595.7 | 9430.2 | 8446 | 8960.7 | 10022.1 | 8351.8 | 9527.4 | 7778.2 | 7970.1 | 8568.8 | 8038.4 | 8904.6 | 7923.2 | 8823.2 | 7859.9 | 7709.6 | 8843.4 | 7734.4 | 8768.9 | 8714.7 | 7690.9 | 8404.9 | 7937.1 | 8181.1 | 7702.4 | 8029 | 8332.3 | 8683.6 | 7779 | 8616.7 | 7462.1 | 8386 | 8158.8 | 7662.2 | 8570.9 | 7465.6 | 8754.8 | 7632.7 | 8542.3 | 7722.6 | 8399.7 | 7827.9 | 8712.4 | 7757.2 | 8333.3 | 7832.1 | 6884.4 | 8584.2 | 8219.8 | 7706.6 | 8996.2 | 8805.8 | 8149.8 | 8066.6 | 8798.7 | 7821 | 8100 | 8882.4 | 7735.1 | 8959 | 7740.5 | 8714.9 | 7958.6 | 8823 | 7520.8 | 8863.3 | 7915.2 | 8735.9 | 7842.7 | 8794.1 | 8032.5 | 7790.6 | 8645.2 | 7792.2 | 7734.5 | 8738.6 | 8805.1 | 8659.8 | 7948.3 | 8779 | 7860.2 | 8513.1 | 7916.8 | 8423.8 | 7416.5 | 8620 | 7913.9 | 7988.6 | 8020.8 | 7940.6 | 6820.7 | 7864.9 | 6884.3 | 8148 | 8146.1 | 9202.1 | 8029.1 | 9271.7 | 8200.1 | 9282 | 8225.3 | 8368.2 | 8276.9 | 8845.9 | 9238.4 | 9058.1 | 9038.8 | 9042.4 | 9114.2 | 8257.2 | 9131.7 | 8940.6 | 9068 | 9186.8 | 9167.5 | 9195.9 | 8241.2 | 9020.8 | 8184.3 | 28.4953 | 30.726 | 25.955 | 30.5914 | 30.6807 | 31.1447 | 0 | 43.6 | 0 | 0 | 38.9 | 0 | 3.3245 | 3.3269 | 3.1603 | 3.1623 | 3.1724 | 3.2858 | 7.45 | 7.632 | 5.894 | 7.731 | 6.227 | 5.951 | 4.6224 | 4.9407 | 4.9069 | 4.5041 | 4.6784 | 4.643 | 0.46261 | 0.68824 | 0.66322 | 0.66316 | 0.74452 | 0.72047 | 4.596 | 4.6985 | 4.6458 | 4.3985 | 4.5541 |  | 0.51689 | 0.67543 | 0.70535 | 0.68861 | 0.75358 | 0.75824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 391922 | 680 | 380642 | 722 | 184629.881 | 405.667 | 4.6224 | 4.9407 | 4.9069 | 4.5041 | 4.6784 | 4.643 | 4.596 | 4.6985 | 4.6458 | 4.3985 | 4.5541 | 0 | 674000 | 2000 | 544000 | 1000 | 1335400 | 4000 | 1215000 | 1331400 | 13.25 | 4.7159 | 0.65704 | 4.5786 | 0.68301 | 13.93% | 14.92% | 29.5989 | 41.25 | 3.2387 | 6.8142 | 1342848 | 1327467 | 1566211.5551 | 84.76%
2023-07-27 | 2024 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 335090.89 | 6:15 | 19:28 | 6018.7 | 6291.4 | 6339.9 | 6313.2 | 6398.7 | 6415 | 6336 | 6592.6 | 6337.2 | 6381.2 | 6224.1 | 6325.9 | 6275.9 | 6268.8 | 6394.4 | 6394.2 | 6337.4 | 6376.1 | 6337.3 | 6346.6 | 6401 | 6375.2 | 6254.1 | 6321.7 | 6177.6 | 5478.1 | 6227.1 | 6224 | 6461.8 | 6403.8 | 6359.3 | 6461.8 | 6571.2 | 6553.9 | 6503.2 | 6474.3 | 6541.2 | 6481.1 | 6505 | 6523.4 | 6739.3 | 6030.6 | 6664.8 | 5931.1 | 6403.9 | 7228.8 | 5903.1 | 6702.2 | 5847.5 | 6011.8 | 6415.5 | 6080.9 | 6649.9 | 5884.8 | 6714.8 | 5957.6 | 5931.3 | 6836.3 | 5879.3 | 6739.7 | 6710.5 | 5872.7 | 6510.8 | 6150.1 | 6378.5 | 6013.6 | 6359.9 | 6640.3 | 6766.2 | 6093.6 | 6721.4 | 5857.4 | 6541.2 | 6395.5 | 5985.2 | 6743.2 | 5658.4 | 6310.8 | 5963.3 | 6699.9 | 6114.3 | 6628.2 | 6207.4 | 6891.9 | 6141.9 | 6596.8 | 6156.9 | 5423.4 | 6798.1 | 6497.7 | 6056.5 | 7056.7 | 6839.9 | 6287.1 | 6224.4 | 6905.6 | 6161.9 | 6384.9 | 7038.3 | 6107.5 | 7053.7 | 6106 | 6845.7 | 6285.6 | 6929 | 5932.2 | 6978.3 | 6263.2 | 6865.3 | 6238.1 | 6934.3 | 6369.1 | 6139.7 | 6844.5 | 6185.6 | 6120.2 | 6964.5 | 7004.2 | 6801 | 6306.5 | 6971 | 6216.9 | 6742.2 | 6268.1 | 6580.5 | 5810.9 | 6814.2 | 6260 | 6342.9 | 6352.3 | 6296.6 | 5415.3 | 6213.2 | 5401.5 | 6318.3 | 6318.6 | 7278.9 | 6317.1 | 7350.5 | 6464.8 | 7256.5 | 6390 | 6486.9 | 6425.9 | 7021.2 | 7342.5 | 7172.5 | 7160.8 | 7156 | 7216.7 | 6548.4 | 7258.5 | 7169.8 | 7262.7 | 7344.4 | 7317.4 | 7329.8 | 6536.1 | 7188.7 | 6508.5 | 24.4868 | 29.1682 | 21.918 | 29.1669 | 29.4421 | 29.7516 | 0 | 39.9 | 0 | 0 | 35.5 | 0 | 3.4437 | 3.3448 | 3.3599 | 3.3363 | 3.3766 | 3.4712 | 7.509 | 6.274 | 6.943 | 6.915 | 6.69 | 7.384 | 3.3171 | 3.4654 | 3.3442 | 3.3724 | 3.54 | 3.5201 | 0.40109 | 0.43224 | 0.49939 | 0.5429 | 0.47991 | 0.47628 | 3.2372 | 3.3419 | 3.2758 | 3.3795 | 3.4848 |  | 0.43815 | 0.42555 | 0.51218 | 0.55402 | 0.50732 | 0.50651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 392428 | 681 | 381291 | 724 | 185658.481 | 409.667 | 3.3171 | 3.4654 | 3.3442 | 3.3724 | 3.54 | 3.5201 | 3.2372 | 3.3419 | 3.2758 | 3.3795 | 3.4848 | 0 | 506000 | 1000 | 649000 | 2000 | 1028600 | 4000 | 1152000 | 1024600 | 13.2167 | 3.4265 | 0.47197 | 3.3438 | 0.49062 | 13.77% | 14.67% | 27.3223 | 37.7 | 3.3887 | 6.9525 | 1034442.3 | 1025600 | 1160552.3902 | 88.37%
2023-07-28 | 2024 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 335090.89 | 6:12 | 19:27 | 6817.4 | 7118 | 7060.4 | 7023.8 | 7089 | 7128.1 | 7150.3 | 7439.6 | 7150.4 | 7223.4 | 7037.7 | 7149.4 | 7057.9 | 7076.9 | 7070.9 | 7114.7 | 6979.8 | 7004.4 | 7037.5 | 7074.9 | 7059.6 | 7046.6 | 6866.5 | 6959.1 | 6784.3 | 6027 | 6921.9 | 6862.4 | 7067.8 | 6963 | 6876.2 | 7030.9 | 6995.7 | 7033.1 | 7083.8 | 7012 | 7060.7 | 6961.2 | 6965.2 | 6942 | 7489.4 | 6673.2 | 7387.8 | 6566.4 | 7066.2 | 7991 | 6542.5 | 7464.8 | 6590 | 6770.3 | 7217.9 | 6772.8 | 7461.3 | 6612.7 | 7464.1 | 6605.3 | 6620.6 | 7611.9 | 6628.1 | 7557 | 7571.6 | 6630.1 | 7322.6 | 6952.8 | 7030.6 | 6623.2 | 7043.6 | 7348.6 | 7527.4 | 6789.6 | 7522.1 | 6564.7 | 7309.1 | 7189.8 | 6701.5 | 7591 | 6609 | 7707.2 | 6737.9 | 7582.8 | 6756.4 | 7378.7 | 6839 | 7598.9 | 6736.6 | 7229.1 | 6716.6 | 5907.2 | 7322.4 | 7036.9 | 6465.3 | 7549.6 | 7307.4 | 6701.9 | 6617.7 | 7365 | 6587.1 | 6844.2 | 7509.8 | 6519.5 | 7508.3 | 6489.4 | 7276.8 | 6674.9 | 7351.1 | 6292 | 7388.8 | 6613.7 | 7253.1 | 6583.2 | 7312.8 | 6690.1 | 6590.2 | 7323.6 | 6649.2 | 6520.2 | 7398.3 | 7457.6 | 7275.1 | 6723.5 | 7398.4 | 6588.2 | 7114 | 6609.3 | 7024.8 | 6153.8 | 7209.7 | 6622.2 | 6745.1 | 6763.6 | 6651.6 | 5746.2 | 6609.8 | 5699.9 | 6739.6 | 6753.3 | 7768.3 | 6707.3 | 7810 | 6844.8 | 7725.9 | 6807.7 | 6912.8 | 6872.8 | 7480.2 | 7809.2 | 7741.5 | 7694.1 | 7676 | 7723.6 | 6943.3 | 7713.5 | 7745.5 | 7796.5 | 7837.6 | 7808.1 | 7807.6 | 6951.2 | 7811 | 6965.6 | 26.478 | 30.0673 | 26.1035 | 29.8909 | 29.9621 | 30.5157 | 0 | 38.2 | 0 | 0 | 35.7 | 0 | 5.3683 | 5.2942 | 5.1837 | 5.2664 | 5.2726 | 5.3989 | 7.817 | 7.607 | 7.907 | 7.957 | 7.733 | 7.222 | 3.7238 | 3.8105 | 3.6621 | 3.6691 | 3.7407 | 3.7643 | 0.42239 | 0.58958 | 0.52888 | 0.59416 | 0.61179 | 0.61366 | 3.7118 | 3.6474 | 3.5197 | 3.6597 | 3.6923 |  | 0.48952 | 0.56988 | 0.58207 | 0.58251 | 0.63879 | 0.65369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 392991 | 682 | 381854 | 725 | 186781.815 | 413.8 | 3.7238 | 3.8105 | 3.6621 | 3.6691 | 3.7407 | 3.7643 | 3.7118 | 3.6474 | 3.5197 | 3.6597 | 3.6923 | 0 | 563000 | 1000 | 563000 | 1000 | 1123334 | 4133 | 1124000 | 1119201 | 13.25 | 3.7284 | 0.56008 | 3.6462 | 0.58608 | 15.02% | 16.07% | 28.8363 | 36.95 | 5.2974 | 7.7072 | 1127516.8 | 1121800 | 1277935.946 | 87.78%
2023-07-29 | 2024 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 335090.89 | 6:08 | 19:40 | 8216.2 | 8627.4 | 8750.3 | 8696.4 | 8840.1 | 8853 | 8734.3 | 9088.5 | 8625.1 | 8625.1 | 8531.2 | 8604.5 | 8705.1 | 8609.7 | 8828 | 8812 | 8761 | 8819.7 | 8768.9 | 8805 | 8875.1 | 8829.9 | 8694.7 | 8778.2 | 8532.2 | 7502.4 | 8551.3 | 8561.6 | 8851.9 | 8790.5 | 8677.1 | 8796.6 | 8701.3 | 8695.6 | 8700.1 | 8668 | 8800.6 | 8735.1 | 8767.9 | 8711.3 | 9133.2 | 8213.2 | 9042.1 | 8099.1 | 8717.1 | 9809 | 8177.2 | 9186.1 | 7985 | 8164.1 | 8761 | 8173 | 9093.1 | 8174.3 | 8911.5 | 8021.1 | 7852 | 8967.3 | 7941.4 | 8894.1 | 8873.6 | 7908.6 | 8606.3 | 8193.3 | 8369.5 | 7924.6 | 8353.9 | 8788.1 | 8877.6 | 8176.3 | 8893.6 | 7929 | 8615.2 | 8616.3 | 7977.8 | 9074.1 | 7860.8 | 8901 | 8058.4 | 9030 | 8216.6 | 8914.2 | 8349 | 9143.6 | 8181 | 8730.1 | 8090.4 | 7182.9 | 8842.9 | 8496.8 | 7818.5 | 9044.4 | 8826.3 | 8184.3 | 8119.8 | 8887.2 | 7963.4 | 8252.1 | 9015.1 | 7912.7 | 9110.6 | 7931.4 | 8901.2 | 8164.8 | 9014.2 | 7777 | 9085.5 | 8186.3 | 8950.1 | 8191.8 | 9020.1 | 8318.9 | 7930 | 8752.5 | 8097.5 | 7931.1 | 8951.4 | 8915.6 | 8848.7 | 8091.9 | 8900.2 | 8024 | 8752.7 | 8196.2 | 8691.4 | 7601.6 | 8748.5 | 8028.2 | 8156.4 | 8211.2 | 8028.1 | 6958 | 8069.1 | 6987.8 | 8279.2 | 8279.6 | 9438.6 | 8235.5 | 9497.7 | 8388.4 | 9410.7 | 8315.8 | 8456.9 | 8392.9 | 9163.5 | 9485.4 | 9373.8 | 9350 | 9327 | 9385 | 8505.1 | 9371.9 | 9405.2 | 9495.7 | 9667.5 | 9632 | 9582.7 | 8598.4 | 9439.9 | 8565.2 | 27.863 | 30.4116 | 21.4015 | 30.1127 | 30.2496 | 30.9193 | 0 | 39.5 | 0 | 0 | 38.3 | 0 | 6.0665 | 6.1996 | 6.2274 | 6.2043 | 5.9392 | 6.4907 | 9.324 | 9.379 | 9.547 | 9.466 | 9.069 | 9.89 | 4.7107 | 4.9634 | 4.7353 | 4.5514 | 4.7272 | 4.7836 | 0.66286 | 0.75543 | 0.81926 | 0.90954 | 0.78375 | 0.75705 | 4.5926 | 4.7623 | 4.6055 | 4.5497 | 4.6124 |  | 0.73807 | 0.73556 | 0.86429 | 0.90729 | 0.82421 | 0.80777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 393678 | 683 | 382540 | 727 | 188149.5 | 417 | 4.7107 | 4.9634 | 4.7353 | 4.5514 | 4.7272 | 4.7836 | 4.5926 | 4.7623 | 4.6055 | 4.5497 | 4.6124 | 0 | 687000 | 1000 | 686000 | 2000 | 1367685 | 3200 | 1370000 | 1364485 | 13.5333 | 4.7453 | 0.78132 | 4.6245 | 0.81287 | 16.47% | 17.58% | 28.493 | 38.9 | 6.188 | 9.4458 | 1374604.7 | 1366467 | 1609421.3558 | 84.9%
2023-07-30 | 2024 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 335090.89 | 6:08 | 19:32 | 9793 | 10280.7 | 10300.7 | 10220.5 | 10383.7 | 10448.3 | 10404.9 | 10842.1 | 10299.8 | 10285.7 | 10246.8 | 10334.9 | 10384.1 | 10354.2 | 10443.4 | 10477.6 | 10360.7 | 10405.7 | 10401.6 | 10435.8 | 10462.7 | 10444.9 | 10215.9 | 10343.3 | 10167.3 | 8906.2 | 10182.7 | 10164.5 | 10520.1 | 10347.3 | 10268.3 | 10498.1 | 10454 | 10454 | 10458.6 | 10409.6 | 10547.1 | 10444.2 | 10473.1 | 10455.9 | 11166 | 9947.9 | 11032.9 | 9775.8 | 10550.2 | 11797.3 | 9862.7 | 11160.9 | 9617 | 9859.8 | 10555.3 | 9926.9 | 10865.6 | 9700.7 | 10864.9 | 9646.5 | 9555.6 | 10948.8 | 9590.7 | 10840.2 | 10798.2 | 9534 | 10503.3 | 9951.2 | 10237.4 | 9610.2 | 10207.6 | 10597.5 | 10835.9 | 9808.5 | 10799.5 | 9468.6 | 10483 | 10310.3 | 9672.2 | 10839.9 | 9525.6 | 10999 | 9608.4 | 10756 | 9806.4 | 10644 | 9928.5 | 10949.3 | 9754.7 | 10446.6 | 9720.1 | 8587.4 | 10664.8 | 10158 | 9485.7 | 11003 | 10699 | 9866.1 | 9752.5 | 10740.6 | 9543.5 | 9851.8 | 10854.6 | 9411.9 | 10983.6 | 9450.4 | 10656.2 | 9674.9 | 10790.4 | 9216.1 | 10842.4 | 9745.1 | 10667.9 | 9705.9 | 10731 | 9870.5 | 9444.1 | 10485.1 | 9595.1 | 9413.5 | 10695.2 | 10696.7 | 10583.3 | 9656.2 | 10670.7 | 9598.9 | 10451.5 | 9755.1 | 10338.2 | 9031.8 | 10474.9 | 9626.6 | 9639.8 | 9623.5 | 9649.3 | 8273.3 | 9404.3 | 8252.2 | 9512.7 | 9549.1 | 11044.7 | 9639.5 | 11084.9 | 9784.9 | 10989.4 | 9678.8 | 9859.9 | 9733.8 | 10713.9 | 11107.4 | 10985.1 | 10974 | 10967.1 | 11005.4 | 9888.7 | 10951.7 | 11175.2 | 11178.9 | 11188.9 | 11163.2 | 11176.4 | 10004.6 | 11092.1 | 10042.2 | 29.9414 | 30.7936 | 25.5509 | 30.4596 | 30.403 | 31.1959 | 0 | 42.5 | 0 | 0 | 41.4 | 0 | 4.7813 | 4.8385 | 4.8418 | 4.8255 | 4.731 | 4.9682 | 7.833 | 7.66 | 7.902 | 7.681 | 7.659 | 7.706 | 5.726 | 6.0274 | 5.8154 | 5.6719 | 5.743 | 5.6903 | 0.72334 | 1.0528 | 0.93833 | 1.1015 | 1.0801 | 0.99794 | 5.7087 | 5.787 | 5.6073 | 5.6526 | 5.6475 |  | 0.82299 | 1.0326 | 1.0098 | 1.0973 | 1.1017 | 1.0525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 394501 | 684 | 383352 | 727 | 189779.3 | 419.4 | 5.726 | 6.0274 | 5.8154 | 5.6719 | 5.743 | 5.6903 | 5.7087 | 5.787 | 5.6073 | 5.6526 | 5.6475 | 0 | 823000 | 1000 | 812000 | 0 | 1629800 | 2400 | 1634000 | 1627400 | 13.4 | 5.779 | 0.98233 | 5.6806 | 1.0195 | 17% | 17.95% | 29.7241 | 41.95 | 4.831 | 7.7402 | 1639188.7 | 1621000 | 1944008.0193 | 83.38%
2023-07-31 | 2024 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 335090.89 | 6:08 | 19:32 | 11331.3 | 11849.8 | 11819.8 | 11786 | 11921.4 | 12056.1 | 11965.7 | 12355.6 | 11843 | 11814.6 | 11785.4 | 11897.3 | 11943.3 | 11826.5 | 11812 | 11860.6 | 11667.4 | 11649.2 | 11735 | 11868.3 | 11730.4 | 11763.6 | 11367.9 | 11548.1 | 11614.1 | 10355.3 | 11654.4 | 11628.4 | 11681 | 11445 | 11362.5 | 11645.8 | 11622.4 | 11740.3 | 11888.7 | 11743 | 11715.5 | 11486.5 | 11496.2 | 11448.9 | 12076.5 | 11187.9 | 12013.5 | 11076.3 | 11531 | 12416.5 | 10796.7 | 11909 | 11116.9 | 11374.2 | 12067.2 | 11417.3 | 12328.5 | 11256.8 | 12240.7 | 11100.1 | 10979.1 | 12269.6 | 11136.1 | 12292.2 | 12204 | 11073.5 | 11774.6 | 11301.7 | 11564.9 | 10985.8 | 11573 | 11916.4 | 12166 | 11115.5 | 12107.2 | 10766.5 | 11819.9 | 11683.5 | 11010.7 | 12187.4 | 10899.2 | 12325.5 | 11074.9 | 12233 | 11078.3 | 11872.5 | 11115.3 | 12209.4 | 11059.5 | 11687 | 11044.6 | 9785.5 | 11914.1 | 11524.8 | 10778.6 | 12257.2 | 12026.4 | 11219.7 | 11079.4 | 12030 | 10942.1 | 11293.4 | 12075.2 | 10739.4 | 11918.3 | 10660.3 | 11651.3 | 10840.2 | 11669.3 | 10238.1 | 11739.3 | 10671.5 | 11604.5 | 10672.7 | 11663.1 | 10867.5 | 10785.6 | 11692.7 | 10752.9 | 10576.3 | 11583.1 | 11619.2 | 11386.6 | 10616 | 11433.8 | 10449.9 | 11248.8 | 10620.7 | 11190.4 | 9865.6 | 11326.9 | 10545.9 | 10774.5 | 10817.3 | 10516 | 9132.9 | 10648.2 | 9478.8 | 10908.6 | 10884.1 | 12471.9 | 11189.7 | 12579.3 | 11363.5 | 12467.7 | 11265.4 | 10994 | 10600 | 12272.3 | 12684.3 | 12654.6 | 12613.8 | 12468.7 | 12467.7 | 11594.7 | 12564.9 | 12570.6 | 12507.8 | 12456.2 | 12407.9 | 12481.3 | 11445.6 | 12652.3 | 11598.6 | 30.24 | 31.81 | 27.25 | 31.47 | 31.4 | 32.3 | 0 | 44.9 | 0 | 0 | 43.45 | 0 | 5.03 | 5.12 | 4.86 | 5.1 | 4.98 | 5.28 | 8.59 | 7.4 | 7.61 | 7.47 | 7.57 | 8.01 | 6.86 | 6.95 | 6.58 | 6.6 | 6.6 | 6.87 | 0.91 | 1.22 | 1.08 | 1.33 | 1.23 | 1.16 | 6.84 | 6.73 | 6.43 | 6.64 | 6.53 |  | 1.01 | 1.21 | 1.13 | 1.34 | 1.24 | 1.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 395430 | 685 | 384259 | 728 | 191609.2 | 422.2 | 6.86 | 6.95 | 6.58 | 6.6 | 6.6 | 6.87 | 6.84 | 6.73 | 6.43 | 6.64 | 6.53 | 0 | 929000 | 1000 | 907000 | 1000 | 1829900 | 2800 | 1834000 | 1827100 | 13.4 | 6.7433 | 1.155 | 6.634 | 1.19 | 17.13% | 17.94% | 30.745 | 44.175 | 5.0617 | 7.775 | 1843251.7 | 1819868 | 2237671.9488 | 81.33%
2023-08-01 | 2024 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 335090.89 | 6:08 | 19:32 | 10412.7 | 10833.4 | 10849.7 | 10802.4 | 10938.8 | 11027.4 | 10879 | 11293.9 | 10835.2 | 10728 | 10735.3 | 10822.3 | 11087.6 | 10884.4 | 10913.4 | 11069.3 | 10788 | 10795.6 | 10830.6 | 10927.6 | 10846.2 | 10857.6 | 10717.5 | 10772.7 | 10643.5 | 9535.5 | 10683.6 | 10652.3 | 10864.3 | 10767.7 | 10742.8 | 10886.9 | 10910 | 10894.5 | 10910.2 | 10868.9 | 10972.3 | 10868.2 | 10898 | 10886.7 | 11156.9 | 10228.4 | 11031.8 | 10061.4 | 10633.2 | 11579.3 | 10113.2 | 11150.3 | 10309.9 | 10513.7 | 11175.5 | 10618.7 | 11377.3 | 10457.6 | 11409.4 | 10331.1 | 10214.1 | 11461.9 | 10166.2 | 11315.7 | 11219.3 | 10138.2 | 10995.3 | 10510.4 | 10874.5 | 10321.2 | 10848.9 | 11163.6 | 11363.9 | 10359.1 | 11212.2 | 9978.2 | 11012.8 | 10780.9 | 10248.8 | 11239.7 | 10090.5 | 11400.5 | 10194.2 | 11178 | 10364.1 | 11037 | 10477.3 | 11417.1 | 10427.1 | 11024.3 | 10481.4 | 9290.2 | 11375.4 | 10987 | 10364.3 | 11608.5 | 11274.6 | 10520.4 | 10394.3 | 11326.6 | 10420.6 | 10831.8 | 11524.8 | 10376.5 | 11405.4 | 10368.7 | 11223.8 | 10576 | 11314.2 | 10044.3 | 11417.9 | 10540.5 | 11262.7 | 10460.6 | 11273 | 10627.8 | 10444.4 | 11297.8 | 10550.9 | 10367.3 | 11378.7 | 11392.6 | 11287.7 | 10617 | 11383.8 | 10511.1 | 11152.6 | 10560.3 | 11010.2 | 9857 | 11298.3 | 10603.2 | 10603 | 10610 | 10522.4 | 9081 | 10395.8 | 9226.9 | 10119.9 | 10100 | 11336.2 | 10183.3 | 11396.7 | 10313 | 11325.1 | 10195.3 | 10359.6 | 10233.4 | 11155.4 | 11419 | 11411.5 | 11342.9 | 11257.6 | 11313.1 | 10449.6 | 11325.3 | 11368.8 | 11496.9 | 11544.5 | 11496.6 | 11504.2 | 10560 | 11476.9 | 10622 | 30.2005 | 31.736 | 25.4707 | 31.537 | 31.5184 | 32.2071 | 0 | 43.3 | 0 | 0 | 43.3 | 0 | 5.5165 | 5.7592 | 5.5439 | 5.6237 | 5.4922 | 5.6407 | 8.858 | 8.463 | 8.205 | 7.884 | 7.773 | 8.39 | 6.2427 | 6.4622 | 6.0908 | 6.2111 | 6.5075 | 6.205 | 0.82149 | 1.1978 | 1.0063 | 1.2431 | 1.2644 | 1.0922 | 6.2687 | 6.2532 | 5.9324 | 6.2382 | 6.4372 |  | 0.91944 | 1.1874 | 1.0656 | 1.2467 | 1.28 | 1.1428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 396290 | 686 | 385122 | 730 | 193325.882 | 426.2 | 6.2427 | 6.4622 | 6.0908 | 6.2111 | 6.5075 | 6.205 | 6.2687 | 6.2532 | 5.9324 | 6.2382 | 6.4372 | 0 | 860000 | 1000 | 863000 | 2000 | 1716682 | 4000 | 1720000 | 1712682 | 13.4 | 6.2865 | 1.1042 | 6.2259 | 1.1403 | 17.56% | 18.32% | 30.445 | 43.3 | 5.596 | 8.2622 | 1728566.8 | 1716667 | 2092603.2513 | 82.03%
2023-08-02 | 2024 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 335090.89 | 6:10 | 19:34 | 10055 | 10391.6 | 10332.7 | 10326.1 | 10373.5 | 10441 | 10339.5 | 10663.4 | 10466.2 | 10589.7 | 10267.4 | 10386.9 | 10345.8 | 10302.1 | 10405.6 | 10449.8 | 10376.9 | 10452.5 | 10370 | 10428.4 | 10512.8 | 10461 | 10348 | 10396.8 | 10142.8 | 9026.9 | 10148.9 | 10154.9 | 10485.9 | 10461.3 | 10388.3 | 10477.9 | 10309.2 | 10335 | 10345.6 | 10279.3 | 10462.7 | 10423.6 | 10486.5 | 10412.8 | 11147 | 10067.4 | 10999.2 | 9871.7 | 10553.7 | 11604.8 | 9912.6 | 11092 | 9690.3 | 9960.2 | 10465.7 | 9943 | 10736.6 | 9702.8 | 10805.9 | 9670.1 | 9744.5 | 11001.2 | 9745.1 | 10919.7 | 10835.5 | 9740 | 10569 | 10095.2 | 10437.2 | 9857.2 | 10383.3 | 10771.3 | 10948.9 | 10017.8 | 10905.6 | 9684.9 | 10638.1 | 10514.2 | 9884.2 | 11034.6 | 9784.1 | 11095.6 | 9887.1 | 11033.4 | 10044.9 | 10814.7 | 10184.3 | 11146.2 | 10046.4 | 10685.4 | 9967.4 | 8913.4 | 10827.9 | 10489.9 | 9749.7 | 11029.4 | 10577.5 | 9618.3 | 9614.3 | 10630.6 | 9636.9 | 10137.5 | 10856.1 | 9641.7 | 10745.9 | 9551.3 | 10516.8 | 9764.8 | 10628.5 | 9270.3 | 10762.8 | 9704.8 | 10699.8 | 9818.2 | 10852.5 | 9966 | 9749.7 | 10617.1 | 9728.7 | 9558.3 | 10635.5 | 10698.8 | 10507.1 | 9849.1 | 10629.5 | 9633.7 | 10328.6 | 9735.1 | 10274.1 | 9076.6 | 10434.4 | 9702.9 | 9863.5 | 9901 | 9685.8 | 8433.3 | 9647.3 | 8754.7 | 9884 | 9882.6 | 11561.1 | 10174.3 | 11668.1 | 10368.2 | 11532.7 | 10237.8 | 10369.7 | 10107.5 | 11343.5 | 11744.7 | 11730.9 | 11696 | 11536.9 | 11525.5 | 10588.9 | 11645.2 | 11519.1 | 11687.2 | 11723.7 | 11690.2 | 11744.6 | 10613.2 | 11758 | 10659.5 | 28.6729 | 30.9658 | 23.388 | 30.6586 | 30.6265 | 31.4584 | 0 | 40.2743 | 0 | 0 | 39.9 | 0 | 7.0049 | 6.9541 | 6.9478 | 7.1361 | 6.783 | 7.3789 | 10.336 | 9.949 | 11.263 | 10.201 | 10.012 | 11.049 | 5.8653 | 6.0241 | 5.9117 | 5.8606 | 5.8771 | 6.1392 | 0.87469 | 1.103 | 1.0676 | 1.2492 | 1.1245 | 1.0702 | 5.7959 | 5.79 | 5.7618 | 5.8941 | 5.7787 |  | 0.96559 | 1.0887 | 1.1232 | 1.2431 | 1.158 | 1.1262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397117 | 687 | 385953 | 731 | 194978.9 | 430.333 | 5.8653 | 6.0241 | 5.9117 | 5.8606 | 5.8771 | 6.1392 | 5.7959 | 5.79 | 5.7618 | 5.8941 | 5.7787 | 0 | 827000 | 1000 | 831000 | 1000 | 1653018 | 4133 | 1656000 | 1648885 | 13.4 | 5.9463 | 1.0816 | 5.8041 | 1.1175 | 18.19% | 19.25% | 29.295 | 40.0871 | 7.0341 | 10.4683 | 1662907.1 | 1652267 | 1980518.3164 | 83.43%
2023-08-03 | 2024 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 335090.89 | 6:10 | 19:34 | 8678.7 | 8984.4 | 9020.7 | 8987.3 | 9091.1 | 9133.9 | 8967.9 | 9293.3 | 9025.9 | 9133 | 8901.2 | 8950.1 | 9070 | 8973.9 | 9080.9 | 9124.4 | 9017.6 | 9049.2 | 9070.7 | 9123.8 | 9091.7 | 9100.7 | 8866.9 | 8964.3 | 8843.3 | 7850 | 8930.4 | 8870.5 | 9074.5 | 8946 | 8858.1 | 9054.2 | 9026.9 | 9049.2 | 9086.6 | 9011.4 | 9087.4 | 8932 | 8969.4 | 8968.5 | 10054.6 | 9098.5 | 9952.8 | 8942.5 | 9547.6 | 10487.8 | 8786.4 | 9925.7 | 8381.5 | 8610.1 | 9196.8 | 8609.4 | 9500.1 | 8450.4 | 9430.2 | 8448.9 | 8346.2 | 9511.8 | 8385.6 | 9485.1 | 9397.3 | 8345.7 | 9061.6 | 8592.5 | 8878.9 | 8345.7 | 8849.9 | 9210.8 | 9406.4 | 8491.1 | 9342.4 | 8192.9 | 9099 | 8931.2 | 8379.1 | 9369.7 | 8250.8 | 9476 | 8353.7 | 9318.5 | 8232.2 | 9124.4 | 8595.3 | 9524.9 | 8507.6 | 9082.8 | 8442.4 | 7511.8 | 9265.3 | 8943.2 | 8377.9 | 9647.9 | 9370.6 | 8634.5 | 8503.8 | 9348.4 | 8401.4 | 8823.8 | 9618.9 | 8419.8 | 9565.5 | 8425.5 | 9319.8 | 8621.7 | 9401.3 | 8128.9 | 9472.9 | 8527.6 | 9336.5 | 8525.8 | 9432.4 | 8679.8 | 8461.7 | 9315.1 | 8593.6 | 8405.7 | 9469.7 | 9520.9 | 9318.3 | 8694.8 | 9439.1 | 8481.6 | 9132.5 | 8531.3 | 9035 | 7928.2 | 9234.6 | 8562.4 | 8610.4 | 8539.3 | 8596.3 | 7380.3 | 8227.1 | 7308.7 | 8028.2 | 8057.1 | 9594.3 | 8328.6 | 9661.3 | 8481.1 | 9482.9 | 8332.3 | 8447.7 | 8279.1 | 9320.4 | 9663.9 | 9612.9 | 9567.9 | 9536 | 9570.6 | 8644.2 | 9522.6 | 9640.4 | 9704.9 | 9735.8 | 9712.7 | 9725.8 | 8689.3 | 9716.2 | 8732.3 | 27.97 | 30.77 | 23.36 | 30.45 | 30.45 | 31.19 | 0 | 39.9 | 0 | 0 | 39.6 | 0 | 5.4 | 5.47 | 5.07 | 5.46 | 5.27 | 5.56 | 8.6 | 8.51 | 8.76 | 8.08 | 7.9 | 9.01 | 4.95 | 5.11 | 5.17 | 4.83 | 5.01 | 4.86 | 0.71 | 0.96 | 0.9 | 1 | 0.98 | 0.88 | 4.93 | 4.91 | 5.03 | 4.82 | 4.98 |  | 0.79 | 0.95 | 0.96 | 0.99 | 1.01 | 0.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397835 | 689 | 386663 | 733 | 196403.549 | 434.467 | 4.95 | 5.11 | 5.17 | 4.83 | 5.01 | 4.86 | 4.93 | 4.91 | 5.03 | 4.82 | 4.98 | 0 | 718000 | 2000 | 710000 | 2000 | 1424649 | 4134 | 1424000 | 1420515 | 13.4 | 4.9883 | 0.905 | 4.934 | 0.93833 | 18.14% | 19.02% | 29.0317 | 39.75 | 5.3717 | 8.4767 | 1432094.9 | 1416134 | 1688729.6801 | 83.86%
2023-08-04 | 2024 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 335090.89 | 6:12 | 19:26 | 9485.2 | 9993.1 | 10070.4 | 10013.4 | 10142.8 | 10188.2 | 10036.2 | 10361 | 9984.4 | 9924.6 | 9918.4 | 9962.8 | 10086.8 | 10005.4 | 9962.3 | 10129.9 | 9886.1 | 9926.2 | 9992.6 | 10087.8 | 9978.7 | 10002.6 | 9774.7 | 9845.6 | 9754.7 | 8665 | 9870.5 | 9792.7 | 9973.7 | 9864.2 | 9766.5 | 9980.4 | 9872.6 | 9947 | 10031.6 | 9898.5 | 9994.7 | 9829 | 9869.6 | 9836.7 | 11139.2 | 10002.6 | 10983.7 | 9829.8 | 10520.3 | 11678.1 | 9732.5 | 11011.9 | 9344.9 | 9577.5 | 10217.9 | 9573.7 | 10484.6 | 9353.3 | 10470.6 | 9322.5 | 9312.2 | 10601.7 | 9346.4 | 10600.1 | 10466.8 | 9299.3 | 9986.1 | 9349 | 9907.4 | 9313.1 | 9849.8 | 10236.1 | 10434.7 | 9389.1 | 10312.3 | 9019.8 | 10073.9 | 9807.9 | 9207.4 | 10293.9 | 9031.1 | 10378.7 | 9097.5 | 10208.1 | 9427.8 | 10134.3 | 9523.1 | 10594 | 9480.2 | 10121.9 | 9411.3 | 8375.8 | 10165.9 | 9894.8 | 9158.8 | 10492.4 | 10156.9 | 9350.5 | 9226.2 | 10124.3 | 8958.5 | 9409.7 | 10267 | 8940.7 | 10331.1 | 8956.3 | 10039 | 9157.9 | 10164.9 | 8699.8 | 10265.4 | 9137.6 | 10220.5 | 9303 | 10382.3 | 9442.4 | 8989.5 | 9852.6 | 9039.6 | 8842.2 | 10017.8 | 9948.9 | 9891.6 | 9062.8 | 9945.1 | 8945.4 | 9809 | 9186.1 | 9793.7 | 8498 | 9809.7 | 9060.3 | 8985.5 | 9006.4 | 9011.9 | 7700.9 | 8609.2 | 7798 | 9025.5 | 9030.9 | 10600.3 | 9279.7 | 10625.8 | 9412.4 | 10467 | 9255.4 | 9377.2 | 9255.7 | 10091.4 | 10488.4 | 10430.9 | 10416.6 | 10443.2 | 10548.7 | 9503.2 | 10375.4 | 10441.6 | 10463.5 | 10477.6 | 10425.4 | 10430.8 | 9370.8 | 10498.5 | 9425.3 | 29.1344 | 30.8629 | 24.1625 | 30.6271 | 30.5541 | 31.2774 | 0 | 41.3 | 0 | 0 | 39.9 | 0 | 4.5026 | 4.895 | 4.3026 | 4.891 | 4.6432 | 4.8101 | 8.264 | 7.836 | 8.872 | 7.486 | 8.317 | 8.166 | 5.5388 | 5.6121 | 5.725 | 5.427 | 5.1264 | 5.3853 | 0.81719 | 1.0606 | 1.0172 | 1.1364 | 0.99942 | 0.95957 | 5.513 | 5.4084 | 5.596 | 5.434 | 5.1215 |  | 0.90748 | 1.0422 | 1.0835 | 1.1257 | 1.0452 | 1.0164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398629 | 690 | 387433 | 734 | 197962.215 | 438.6 | 5.5388 | 5.6121 | 5.725 | 5.427 | 5.1264 | 5.3853 | 5.513 | 5.4084 | 5.596 | 5.434 | 5.1215 | 0 | 794000 | 1000 | 770000 | 1000 | 1558666 | 4133 | 1562000 | 1554533 | 13.2333 | 5.4691 | 0.9984 | 5.4146 | 1.0367 | 18.26% | 19.15% | 29.4364 | 40.6 | 4.6741 | 8.1568 | 1566751.8 | 1558600 | 1844480.666 | 84.5%
2023-08-05 | 2024 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 335090.89 | 6:11 | 19:26 | 10619.8 | 11101.8 | 11110.2 | 11093.2 | 11193.7 | 11231.6 | 11082.9 | 11453 | 11096.1 | 10982.6 | 10939.1 | 11017.4 | 11122.2 | 11006.3 | 10933.4 | 11094.3 | 10880.8 | 10943.1 | 10961.6 | 11067.6 | 11038.7 | 11030.7 | 10852.2 | 10924 | 10826.1 | 9694.7 | 10884.3 | 10809 | 11016.9 | 10930.3 | 10881.3 | 11049.4 | 11011.2 | 11065.2 | 11047.8 | 10968.5 | 11073.2 | 10917.1 | 10989.1 | 10993.9 | 11849 | 10817.2 | 11729.3 | 10679.5 | 11257.2 | 12327.9 | 10450.1 | 11749 | 10401.2 | 10630.4 | 11248.3 | 10634.1 | 11503.9 | 10370.1 | 11515.1 | 10391.2 | 10315.7 | 11574.6 | 10375.2 | 11560.6 | 11393.7 | 10348.9 | 10893.6 | 10378.3 | 10877.3 | 10279.4 | 10803.7 | 11161.9 | 11361.4 | 10355.9 | 11222.3 | 9990.8 | 11011.7 | 10796 | 10234.7 | 11243.1 | 10072.9 | 11366.9 | 10152.3 | 11191.9 | 10350.7 | 11041.2 | 10445.3 | 11433.2 | 10369.9 | 11004.6 | 10362.6 | 9260.1 | 11255.6 | 10896.3 | 10327.2 | 11672.4 | 11310.6 | 10514.2 | 10375.6 | 11349.4 | 10284.5 | 10782.2 | 11557.8 | 10282.8 | 11485.3 | 10275.8 | 11268.5 | 10483.5 | 11394.8 | 9947.5 | 11474.2 | 10441.5 | 11312.6 | 10423.9 | 11367.9 | 10588.4 | 10345.5 | 11238.3 | 10418.1 | 10235.5 | 11337.8 | 11362.3 | 11215.4 | 10523.2 | 11289.4 | 10322.4 | 11103.1 | 10461.5 | 10981.5 | 9623.6 | 11168.5 | 10405.5 | 10573.4 | 10547.2 | 10383.9 | 9068.5 | 10160.1 | 9083.7 | 10065.3 | 10068.7 | 11507.9 | 10287.9 | 11563.6 | 10423.9 | 11457.4 | 10290.1 | 9869 | 9469.3 | 11118.1 | 11403.8 | 11425.5 | 11408.8 | 11351.7 | 11436.9 | 10436.7 | 11340.7 | 11392.6 | 11403.1 | 11516.6 | 11416.1 | 11407.4 | 10413.2 | 11493.5 | 10467.8 | 27.0807 | 31.3965 | 25.707 | 31.0332 | 31.0344 | 31.7143 | 0 | 42.4713 | 0 | 0 | 42.7 | 0 | 5.304 | 5.5202 | 5.2359 | 5.4971 | 5.2447 | 5.5049 | 9.347 | 8.703 | 10.153 | 8.66 | 8.973 | 9.406 | 6.2703 | 6.3966 | 6.2707 | 6.1312 | 6.1047 | 6.0589 | 0.93072 | 1.1969 | 1.1239 | 1.292 | 1.1794 | 1.0691 | 6.2311 | 6.1957 | 6.151 | 6.1563 | 6.1041 |  | 1.0292 | 1.181 | 1.1855 | 1.2887 | 1.23 | 1.1276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 399502 | 691 | 388292 | 736 | 199688.5 | 442.733 | 6.2703 | 6.3966 | 6.2707 | 6.1312 | 6.1047 | 6.0589 | 6.2311 | 6.1957 | 6.151 | 6.1563 | 6.1041 | 0 | 873000 | 1000 | 859000 | 2000 | 1726285 | 4133 | 1729000 | 1722152 | 13.25 | 6.2054 | 1.132 | 6.1676 | 1.1737 | 18.24% | 19.03% | 29.661 | 42.5857 | 5.3845 | 9.207 | 1737074.7 | 1726267 | 2084120.1634 | 82.83%
2023-08-06 | 2024 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 335090.89 | 6:10 | 19:22 | 10764.5 | 11120.7 | 11202.4 | 11181.5 | 11305.9 | 11330.4 | 11122.8 | 11546.3 | 11201 | 11254.4 | 11068.1 | 11143.7 | 11321.3 | 11171 | 11328.2 | 11380.6 | 11227.4 | 11340.7 | 11287.2 | 11388.8 | 11368.8 | 11418.7 | 11332.9 | 11335.8 | 11128.2 | 10031.9 | 11139.1 | 11128.7 | 11424 | 11380.5 | 11339.7 | 11419.3 | 11323.3 | 11345.4 | 11494.4 | 11424.9 | 11413.7 | 11368.5 | 11412.5 | 11408.3 | 11779.4 | 10914.6 | 11568 | 10800.7 | 11344.2 | 12263.4 | 10579.1 | 11603.6 | 10630.6 | 10871.5 | 11450.9 | 10866.4 | 11741.3 | 10725.7 | 11636.1 | 10714.4 | 10508.9 | 11726.5 | 10592.9 | 11677.5 | 11524.9 | 10539.4 | 11269.1 | 10841.7 | 11132.1 | 10677.7 | 11213.9 | 11671.8 | 11744.7 | 10889.2 | 11795.7 | 10633.5 | 11401.5 | 11414 | 10676.6 | 11763.9 | 10657.1 | 11849.1 | 10725.3 | 11680 | 10900.9 | 11572.8 | 10971 | 11974.9 | 10939.2 | 11578.7 | 10332.2 | 9753.3 | 11498.5 | 11230.9 | 10558.5 | 11843.4 | 11607.4 | 10942.3 | 10867.5 | 11555.3 | 10536.1 | 11051.5 | 11796.3 | 10642.8 | 11885 | 10696.4 | 11728.1 | 11015.7 | 11633.6 | 10488.3 | 11819 | 10926 | 11745.8 | 10963.3 | 11677 | 11206.5 | 10665.7 | 11593.1 | 10844.1 | 10709.9 | 11734.4 | 11714.4 | 11633.7 | 10967.4 | 11687 | 10840.8 | 11475 | 10994.7 | 11405.1 | 10288.8 | 11619.3 | 10934.3 | 11004.1 | 10861.8 | 10806.9 | 9470.6 | 10636.2 | 9584.5 | 10578.2 | 10579.4 | 11894.5 | 10765.6 | 11873.3 | 10951.9 | 11941.9 | 10666.6 | 10896.3 | 10805.2 | 11545.1 | 11786.5 | 11871.7 | 11831.3 | 11845.8 | 11934.4 | 10971 | 11792 | 11876.2 | 11817.4 | 11870.7 | 11962.6 | 11889 | 10905.9 | 11899.4 | 10974.7 | 28.1262 | 30.5508 | 24.2428 | 30.403 | 30.2429 | 30.9427 | 0 | 40.1868 | 0 | 0 | 40.3 | 0 | 7.9134 | 7.9786 | 7.9123 | 7.8294 | 7.6601 | 8.2277 | 11.97 | 11.275 | 11.7767 | 12.035 | 11.6783 | 11.8 | 6.4058 | 6.6549 | 6.3325 | 6.2939 | 6.5247 | 6.4007 | 0.95368 | 1.2635 | 1.1646 | 1.3142 | 1.3133 | 1.1647 | 6.4322 | 6.4956 | 6.274 | 6.3704 | 6.5358 |  | 1.0457 | 1.249 | 1.2157 | 1.3332 | 1.3438 | 1.2179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400397 | 693 | 389186 | 737 | 201470.749 | 446.667 | 6.4058 | 6.6549 | 6.3325 | 6.2939 | 6.5247 | 6.4007 | 6.4322 | 6.4956 | 6.274 | 6.3704 | 6.5358 | 0 | 895000 | 2000 | 894000 | 1000 | 1782249 | 3934 | 1786000 | 1778315 | 13.2 | 6.4354 | 1.1957 | 6.4216 | 1.2342 | 18.58% | 19.22% | 29.0847 | 40.2434 | 7.9202 | 11.7558 | 1795559 | 1771600 | 2183348.2946 | 81.14%
2023-08-07 | 2024 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 335090.89 | 6:15 | 19:28 | 10208.9 | 10619.5 | 10617.7 | 10588.9 | 10669.4 | 10698.6 | 10551.2 | 10928 | 10579.2 | 10600.8 | 10464.9 | 10560.8 | 10642.8 | 10551.4 | 10663.1 | 10703.9 | 10537.3 | 10558.3 | 10607.9 | 10711.1 | 10626.9 | 10668.9 | 10418 | 10511.4 | 10442.7 | 9313.9 | 10480.9 | 10441.3 | 10642.3 | 10513.2 | 10400.3 | 10621.8 | 10606.1 | 10670.9 | 10770.7 | 10693.9 | 10695.8 | 10526 | 10556.4 | 10561.3 | 11472.4 | 10518.9 | 11317.7 | 10379.8 | 10966 | 11929.5 | 10090.6 | 11283.4 | 9952.2 | 10183.3 | 10758.2 | 10204.3 | 11055.8 | 10037.1 | 10987.8 | 9959.7 | 9901.3 | 11095 | 9929.3 | 11054.7 | 10926.9 | 9920.9 | 10600.8 | 10150.1 | 10524.9 | 10008.6 | 10537 | 10897.6 | 11054.5 | 10191.7 | 11024.8 | 9891.6 | 10739.9 | 10643.5 | 10004.9 | 11011.8 | 9906 | 11093.8 | 9964.6 | 10936 | 10211.6 | 10856.4 | 10273.5 | 11189.7 | 10211.3 | 10806.3 | 9870.1 | 9055.8 | 10808.9 | 10554.2 | 9894.4 | 11143.4 | 10878.5 | 10171.7 | 10076.2 | 10824.5 | 9794.5 | 10302.7 | 11028.9 | 9874 | 11133.6 | 9905.6 | 10936.6 | 10194.8 | 10893.1 | 9654.4 | 11018.7 | 10091.9 | 10868.6 | 10014.3 | 10872.2 | 10213.6 | 9922.3 | 10812.5 | 10076.1 | 9888.5 | 10970.3 | 10925.2 | 10861 | 10126.3 | 10916.8 | 9999.5 | 10704.7 | 10077 | 10560.9 | 9412.8 | 10797.8 | 10069.7 | 10103.8 | 10049.3 | 10038.8 | 8672 | 9759.6 | 8810.1 | 9860.7 | 9879 | 11213.4 | 10075.8 | 11211.2 | 10236.1 | 11186.3 | 10043.7 | 10194.2 | 10064.2 | 10840.7 | 11132.3 | 11137.8 | 11102.2 | 11127.2 | 11206.1 | 10200 | 11050.4 | 11182.8 | 11172 | 11208.2 | 11200.3 | 11204.9 | 10174.1 | 11217 | 10249.8 | 25.3765 | 30.4232 | 21.0066 | 30.2339 | 30.0816 | 30.7817 | 0 | 39.1069 | 0 | 0 | 39 | 0 | 8.8077 | 8.7893 | 8.7518 | 8.8224 | 8.5515 | 9.0215 | 13.062 | 12.589 | 13.28 | 12.811 | 11.955 | 12.902 | 5.9401 | 6.0382 | 5.9295 | 5.8298 | 5.8947 | 5.7617 | 0.85744 | 1.1752 | 1.056 | 1.1873 | 1.223 | 1.0802 | 6.0134 | 5.8978 | 5.8663 | 5.8909 | 5.9398 | 0 | 0.94968 | 1.1619 | 1.1179 | 1.1994 | 1.2551 | 1.1368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401239 | 694 | 390019 | 739 | 203139.483 | 450.667 | 5.9401 | 6.0382 | 5.9295 | 5.8298 | 5.8947 | 5.7617 | 6.0134 | 5.8978 | 5.8663 | 5.8909 | 5.9398 | 0 | 842000 | 1000 | 833000 | 2000 | 1668734 | 4000 | 1672000 | 1664734 | 13.2167 | 5.899 | 1.0965 | 5.9216 | 1.1368 | 18.59% | 19.2% | 27.9839 | 39.0534 | 8.7907 | 12.7665 | 1681882.7 | 1668133 | 2024407.7529 | 82.4%
2023-08-08 | 2024 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 335090.89 | 6:15 | 19:36 | 10749.4 | 11193.8 | 11155.1 | 11129.9 | 11228.7 | 11289.3 | 11126 | 11474 | 11147.3 | 11182.8 | 11015 | 11122.7 | 11221.7 | 11132.8 | 11275.9 | 11324.2 | 11127.2 | 11192.6 | 11187.4 | 11294.7 | 11205.8 | 11270.9 | 11058.4 | 11134.5 | 11030.2 | 9847.4 | 11056.7 | 11039.4 | 11274.7 | 11117.2 | 11023.3 | 11204.9 | 11188.9 | 11226.8 | 11447.3 | 11379.4 | 11309.8 | 11196.1 | 11172.1 | 11196.5 | 11626.5 | 10711.4 | 11456.7 | 10556.8 | 11108.8 | 12125.3 | 10288 | 11471.7 | 10514 | 10753.3 | 11348.8 | 10772.7 | 11653.8 | 10626.7 | 11563.5 | 10574.1 | 10440 | 11649.9 | 10492.2 | 11617.3 | 11486.1 | 10461.1 | 11111 | 10589.3 | 11003.4 | 10421.7 | 11004.9 | 11350.7 | 11514.5 | 10512.1 | 11462.9 | 10188.4 | 11166.4 | 10997.7 | 10351.7 | 11344.6 | 10199.4 | 11508.5 | 10291.9 | 11270.3 | 10513.2 | 11183.8 | 10563.1 | 11590.3 | 10548.4 | 11180.1 | 10154.4 | 9385.7 | 11260.3 | 10993.9 | 10447.8 | 11733.9 | 11520.5 | 10786.5 | 10648.7 | 11492.5 | 10380.6 | 10898.8 | 11664.6 | 10463.1 | 11680.6 | 10492.7 | 11488 | 10780 | 11405.5 | 10159.6 | 11538.2 | 10622.5 | 11427.7 | 10556.2 | 11428.7 | 10803.3 | 10473.2 | 11387.8 | 10648.9 | 10468.7 | 11490.6 | 11540.2 | 11365 | 10698.2 | 11469.4 | 10537.3 | 11211.1 | 10636.8 | 11078.9 | 9936.9 | 11363.6 | 10611.4 | 10707.6 | 10574.7 | 10542.7 | 9173.3 | 10147.2 | 9074.8 | 10216.6 | 10229.7 | 11659 | 10446.2 | 11719.1 | 10649.6 | 11617.7 | 10457.8 | 10537.9 | 10355.1 | 11401.8 | 11708.6 | 11783.6 | 11735.8 | 11707.5 | 11734.2 | 10796.3 | 11673.2 | 11635 | 11599.9 | 11554.6 | 11639.5 | 11669.8 | 10716.6 | 11757.1 | 10829 | 27.4379 | 30.6057 | 24.4102 | 30.3802 | 30.2529 | 30.8575 | 0 | 40.0778 | 0 | 0 | 40.3 | 0 | 7.5018 | 7.4596 | 7.244 | 7.5647 | 7.1542 | 7.7715 | 10.999 | 10.753 | 10.881 | 10.606 | 10.756 | 10.828 | 6.098 | 6.3244 | 5.9204 | 6.0117 | 6.2062 | 6.0748 | 0.90968 | 1.2544 | 1.071 | 1.2634 | 1.2866 | 1.1435 | 6.1404 | 6.2043 | 5.8831 | 6.1153 | 6.266 | 0 | 1.0045 | 1.2364 | 1.1319 | 1.2717 | 1.3178 | 1.1974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402122 | 695 | 390893 | 740 | 204888.949 | 454.667 | 6.098 | 6.3244 | 5.9204 | 6.0117 | 6.2062 | 6.0748 | 6.1404 | 6.2043 | 5.8831 | 6.1153 | 6.266 | 0 | 883000 | 1000 | 874000 | 1000 | 1749466 | 4000 | 1755000 | 1745466 | 13.35 | 6.1059 | 1.1548 | 6.1218 | 1.1933 | 18.91% | 19.49% | 28.9907 | 40.1889 | 7.4493 | 10.8038 | 1762301.6 | 1749466 | 2083578.0092 | 83.96%
2023-08-09 | 2024 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 335090.89 | 6:15 | 19:35 | 9756.4 | 10135.6 | 10149.7 | 10073.6 | 10225.8 | 10339.5 | 10139.7 | 10433.2 | 10040.3 | 10290.3 | 9966.2 | 10052.6 | 10198.2 | 10076.4 | 10267.1 | 10334.1 | 10234.4 | 10330.6 | 10253.3 | 10304.3 | 10397.6 | 10352 | 10307.3 | 10338.4 | 10104.7 | 8879.4 | 10082.3 | 10115.1 | 10455.4 | 10442.7 | 10345.3 | 10445.3 | 10288.4 | 10322.9 | 10368.8 | 10317.8 | 10474.7 | 10407.7 | 10461.7 | 10407.7 | 11094.7 | 10011.3 | 10932.4 | 9816.4 | 10531.3 | 11594.3 | 9731.2 | 11055.4 | 9399.9 | 9623.7 | 10295 | 9646.8 | 10642.5 | 9548.8 | 10522.2 | 9484.5 | 9318.8 | 10622.9 | 9374.7 | 10568.3 | 10455.1 | 9343 | 10169.6 | 9705.9 | 10027.5 | 9466.5 | 10014.1 | 10473 | 10618.3 | 9698.1 | 10612.1 | 9362.7 | 10294.5 | 10184.8 | 9525.1 | 10655.8 | 9398.2 | 10760.8 | 9498.2 | 10579.3 | 9734.1 | 10469.9 | 9821.1 | 10835.4 | 9695.5 | 10348.9 | 9603.2 | 8548.4 | 10384.1 | 10128 | 9386.7 | 10771.5 | 10531.6 | 9758.4 | 9684.2 | 10576.3 | 9296.6 | 9870.9 | 10687.6 | 9424.3 | 10816.2 | 9451.2 | 10602.3 | 9722.5 | 10696.5 | 9213.1 | 10779.9 | 9722.1 | 10654 | 9729.3 | 10740.4 | 9924.5 | 9451.2 | 10409 | 9635.7 | 9408.4 | 10602 | 10605.6 | 10494 | 9706.7 | 10566.1 | 9555.7 | 10377.6 | 9708.1 | 10244.6 | 8994.1 | 10427.9 | 9618.4 | 9659.4 | 9625 | 9543.4 | 8280.7 | 9380.3 | 8339.7 | 9404.7 | 9402.3 | 10999 | 9659.7 | 11044.1 | 9820.4 | 10862.1 | 9622.2 | 9682.7 | 9476.8 | 10590.4 | 10953.4 | 10974 | 10972.8 | 10928.2 | 10965.7 | 9933 | 10898.8 | 10815.7 | 10878.3 | 10920.2 | 10864.1 | 10912.6 | 9848.5 | 11016.1 | 9940 | 27.38 | 30.69 | 21.65 | 30.46 | 30.32 | 31.07 | 0 | 40.11 | 0 | 0 | 40.2 | 0 | 6.84 | 6.82 | 6.54 | 6.88 | 6.53 | 7.06 | 9.8 | 9.68 | 10.95 | 9.63 | 9.36 | 10.97 | 5.47 | 5.78 | 5.61 | 5.42 | 5.55 | 5.55 | 0.83 | 1.11 | 1.04 | 1.15 | 1.11 | 1.01 | 5.5 | 5.67 | 5.61 | 5.54 | 5.61 | 0 | 0.92 | 1.09 | 1.09 | 1.16 | 1.15 | 1.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402932 | 697 | 391697 | 741 | 206498.416 | 458.8 | 5.47 | 5.78 | 5.61 | 5.42 | 5.55 | 5.55 | 5.5 | 5.67 | 5.61 | 5.54 | 5.61 | 0 | 810000 | 2000 | 804000 | 1000 | 1609467 | 4133 | 1611000 | 1605334 | 13.3333 | 5.5633 | 1.0417 | 5.586 | 1.0783 | 18.72% | 19.3% | 28.595 | 40.155 | 6.7783 | 10.065 | 1621202.3 | 1609400 | 1895486.4991 | 84.91%
2023-08-10 | 2024 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 335090.89 | 6:15 | 19:30 | 10581 | 11007.1 | 10940.6 | 10915.6 | 10958.7 | 11065.3 | 10983.1 | 11162.3 | 10904.1 | 10994.6 | 10783.8 | 10920.2 | 10396.6 | 10647.7 | 10957.5 | 11038.3 | 10893.2 | 10969.5 | 10919.7 | 11008.5 | 11001 | 10985.9 | 10891.1 | 10932.4 | 10744.4 | 9512.5 | 10797.7 | 10752.2 | 11044 | 11017.1 | 10943.5 | 11056.7 | 10923.6 | 10962 | 10966.2 | 10869.1 | 11067.8 | 10995.3 | 11044.2 | 10991.7 | 11579.4 | 10670.1 | 11542.2 | 10472.3 | 11107 | 12082.5 | 10282.2 | 11627.9 | 10147.8 | 10399.2 | 11038.2 | 10384.4 | 11377.4 | 10216.4 | 11279.8 | 10202.5 | 10128.4 | 11425.5 | 10191.5 | 11402.7 | 11299.8 | 10184.4 | 11011 | 10545.4 | 10840.3 | 10248.8 | 10828.8 | 11260.7 | 11407.2 | 10447.9 | 11345.9 | 10095.9 | 11076.1 | 10955.7 | 10280 | 11420.6 | 10148.3 | 11508.5 | 10276.4 | 11372.7 | 10469.2 | 11229.3 | 10523.5 | 11560.5 | 10423.8 | 11095.2 | 10421.1 | 9249.2 | 11137.6 | 10898.1 | 10090.6 | 11462.3 | 11228.9 | 10439.5 | 10350 | 11250.6 | 10017 | 10597 | 11392.6 | 10152.2 | 11542 | 10217.2 | 11341.3 | 10469.1 | 11397.6 | 9954.7 | 11484.1 | 10473.8 | 11334.8 | 10279.9 | 11425.3 | 10639.5 | 10169.5 | 11163.4 | 10431.1 | 10186.3 | 11415.6 | 11392.7 | 11321 | 10507.8 | 11372.8 | 10333.8 | 11156.7 | 10449.2 | 11066.1 | 9716.7 | 11225.4 | 10398.5 | 10410.6 | 10333.4 | 10282.4 | 8928.8 | 10184.9 | 8948.2 | 10102.8 | 10134.8 | 11726 | 10420.6 | 11743.8 | 10547.2 | 11534.8 | 10297.4 | 9947.1 | 9427.7 | 11229.4 | 11561.4 | 11587.8 | 11611 | 11593.4 | 11677.6 | 10636.9 | 11559.3 | 11384 | 11407.5 | 11413.6 | 11365.1 | 11434.8 | 10435.3 | 11560.2 | 10552.4 | 28.1881 | 30.6306 | 20.345 | 30.4224 | 30.2926 | 31.0277 | 0 | 40.7151 | 0 | 0 | 41.1 | 0 | 6.1695 | 6.4686 | 5.9577 | 6.5141 | 6.2732 | 6.685 | 10.279 | 10.453 | 9.83 | 9.936 | 10.029 | 10.42 | 5.236 | 6.1402 | 6.0103 | 5.9244 | 5.849 | 6.0237 | 0.91275 | 1.213 | 1.1116 | 1.2697 | 1.2456 | 1.1196 | 5.8454 | 6.0117 | 5.9483 | 5.8661 | 5.7678 | 0 | 1.0028 | 1.1846 | 1.1898 | 1.2802 | 1.2825 | 1.1755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403799 | 698 | 392557 | 743 | 208219.416 | 462.867 | 5.236 | 6.1402 | 6.0103 | 5.9244 | 5.849 | 6.0237 | 5.8454 | 6.0117 | 5.9483 | 5.8661 | 5.7678 | 0 | 867000 | 1000 | 860000 | 2000 | 1721000 | 4067 | 1724000 | 1716933 | 13.25 | 5.8639 | 1.1454 | 5.8878 | 1.1859 | 19.53% | 20.14% | 28.4844 | 40.9076 | 6.3447 | 10.1578 | 1732491.9 | 1711133 | 1998572.6627 | 85.62%
2023-08-11 | 2024 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 335090.89 | 6:12 | 19:23 | 10091.3 | 10448.1 | 10339.5 | 10351.8 | 10285.5 | 10376.7 | 10351.2 | 10624.1 | 10356.7 | 10425.7 | 10225.4 | 10349.1 | 10215.8 | 10248.6 | 9931.6 | 10116.8 | 9769.3 | 9789.8 | 9830.8 | 10013.7 | 9825.7 | 9844.1 | 9667.7 | 9725.3 | 9638.7 | 8677.4 | 9856.5 | 9675.5 | 9858 | 9791.2 | 9734.3 | 9874.2 | 9751.5 | 9859.1 | 9939.1 | 9782.1 | 9885 | 9791.2 | 9851.6 | 9782.3 | 10809.5 | 9973 | 10823.8 | 9788 | 10432.4 | 11402.5 | 9634.9 | 10855 | 9573.5 | 9790.7 | 10330.4 | 9716.7 | 10495.1 | 9364.7 | 10558.1 | 9454.9 | 9515.3 | 10715.7 | 9610.4 | 10709 | 10641.4 | 9612.2 | 10396.5 | 9949.8 | 10158.6 | 9614.7 | 10162.1 | 10529.6 | 10745.1 | 9796.7 | 10671.7 | 9465.1 | 10444.7 | 10247.6 | 9697.1 | 10696.7 | 9538.8 | 10847 | 9662.5 | 10615.3 | 9776.5 | 10494.2 | 9802.4 | 10826 | 9720.6 | 10336.2 | 9748.3 | 8701.8 | 10302.7 | 10177.6 | 9269.9 | 10480.3 | 10179 | 9430.2 | 9299.4 | 10194.7 | 9142.4 | 9568.9 | 10325.2 | 9166.4 | 10267.6 | 9135.6 | 10038.8 | 9305.5 | 10102.7 | 8804.6 | 10194.3 | 9249.8 | 10023.8 | 9187.4 | 10197.1 | 9418.5 | 9205.3 | 10080.3 | 9305.5 | 9122.4 | 10203 | 10165.2 | 10066.6 | 9334.6 | 10125.7 | 9178.2 | 9908.8 | 9250 | 9820.7 | 8651.7 | 10009.2 | 9287.1 | 9311.1 | 9303.4 | 9265.2 | 7989.6 | 9162.5 | 8175.9 | 9389.8 | 9431.4 | 10782.3 | 9598.9 | 10781.7 | 9684.3 | 10745.2 | 9590.9 | 9670.7 | 9535.3 | 10425.4 | 10723.4 | 10736.7 | 10738.8 | 10677.4 | 10753.6 | 9767.3 | 10661.9 | 10626.2 | 10667.1 | 10615.8 | 10584 | 10643.3 | 9717.8 | 10794.3 | 9837.7 | 26.1483 | 30.3049 | 26.9621 | 30.2346 | 30.0027 | 30.8298 | 0 | 39.8163 | 0 | 0 | 40.3 | 0 | 5.592 | 5.864 | 5.2874 | 5.9162 | 5.6292 | 5.917 | 8.998 | 9.309 | 9.761 | 9.209 | 8.767 | 9.376 | 5.0932 | 5.5663 | 5.7333 | 5.6529 | 5.2879 | 5.6618 | 0.82183 | 1.1174 | 1.0179 | 1.1618 | 1.1352 | 1.0821 | 5.7746 | 5.3987 | 5.6315 | 5.5718 | 5.207 | 0 | 0.9145 | 1.0875 | 1.1044 | 1.1692 | 1.1718 | 1.1383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404603 | 700 | 393342 | 744 | 209802.883 | 466.933 | 5.0932 | 5.5663 | 5.7333 | 5.6529 | 5.2879 | 5.6618 | 5.7746 | 5.3987 | 5.6315 | 5.5718 | 5.207 | 0 | 804000 | 2000 | 785000 | 1000 | 1583467 | 4066 | 1586000 | 1579401 | 13.1833 | 5.4992 | 1.0561 | 5.5167 | 1.0976 | 19.2% | 19.9% | 29.0804 | 40.0582 | 5.701 | 9.2367 | 1592970.4 | 1572666 | 1878953.7284 | 83.7%
2023-08-12 | 2024 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 335090.89 | 6:13 | 19:25 | 10092.5 | 10348.6 | 10305.2 | 10259.8 | 10319.2 | 10472.1 | 10321 | 10707.7 | 10339.2 | 10473.8 | 10244.9 | 10321.2 | 10465.9 | 10304 | 10560.3 | 10580.7 | 10506.7 | 10595.7 | 10515.7 | 10552.4 | 10655.5 | 10624.7 | 10493.7 | 10576.4 | 10398.5 | 9225.9 | 10331 | 10403.7 | 10714.3 | 10572.8 | 10463.6 | 10703.8 | 10551.1 | 10596.1 | 10600.8 | 10542.3 | 10711.2 | 10599.8 | 10607.5 | 10587.5 | 11277.7 | 10378.6 | 11161.8 | 10259.7 | 10671.9 | 11656.7 | 9919.5 | 11132.6 | 9606.4 | 9814.4 | 10462.3 | 9809.5 | 10837.6 | 9698.7 | 10646.9 | 9690.7 | 9454.1 | 10703.2 | 9582.8 | 10665 | 10584.7 | 9527.7 | 10409.6 | 10005.4 | 10130.4 | 9678.3 | 10199.7 | 10709 | 10796.9 | 10046.2 | 10848.4 | 9780.4 | 10495 | 10561.1 | 9822.4 | 11060 | 9877.5 | 10981.4 | 9921 | 11074.1 | 10144.6 | 10891.2 | 10195.7 | 11121.1 | 10015.6 | 10602.1 | 9781.8 | 8822.7 | 10487.4 | 10247.7 | 9536.8 | 10895 | 10701.8 | 9995 | 9961.8 | 10692.8 | 9613.2 | 9991.8 | 10880.8 | 9648.2 | 10952.8 | 9766.5 | 10806.2 | 9994.8 | 10961.2 | 9567.5 | 11083.9 | 10022.3 | 10926.8 | 10084.2 | 10964 | 10275.8 | 9602.8 | 10522 | 9902.7 | 9689.7 | 10821.6 | 10739.7 | 10724.8 | 9939.2 | 10754.1 | 9841.4 | 10647.6 | 10061.9 | 10576.6 | 9378.2 | 10696.8 | 9957.6 | 9869 | 9818 | 9890 | 8550.6 | 9634.8 | 8478.8 | 9736.3 | 9796.1 | 11335.3 | 10138.2 | 11332.9 | 10236.3 | 11275.3 | 10115.9 | 10232 | 10024.5 | 10950.3 | 11175 | 11204.4 | 11222.6 | 11225.2 | 11303.9 | 10250.2 | 11105.4 | 11100.3 | 11150.1 | 11152 | 11107.7 | 11165.3 | 10224 | 11261.9 | 10332.8 | 26.6426 | 30.4299 | 20.9447 | 30.1724 | 30.0108 | 30.8667 | 0 | 40.7729 | 0 | 0 | 40.7441 | 0 | 6.6234 | 6.7037 | 6.3246 | 6.7241 | 6.4257 | 6.8439 | 9.982 | 9.907 | 10.118 | 9.394 | 9.207 | 10.636 | 5.1522 | 6.1473 | 5.8394 | 5.6904 | 5.6831 | 5.9313 | 0.8391 | 1.2054 | 1.0665 | 1.1703 | 1.2032 | 1.1092 | 5.8184 | 5.993 | 5.7834 | 5.8142 | 5.6073 | 0 | 0.92871 | 1.1749 | 1.1453 | 1.1778 | 1.2386 | 1.1642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405433 | 701 | 394139 | 746 | 211454.683 | 471 | 5.1522 | 6.1473 | 5.8394 | 5.6904 | 5.6831 | 5.9313 | 5.8184 | 5.993 | 5.7834 | 5.8142 | 5.6073 | 0 | 830000 | 1000 | 797000 | 2000 | 1651800 | 4067 | 1624000 | 1647733 | 13.2 | 5.7406 | 1.0989 | 5.8033 | 1.1383 | 19.14% | 19.61% | 28.1779 | 40.7585 | 6.6076 | 9.874 | 1662071 | 1651800 | 1976600.8215 | 83.57%
2023-08-13 | 2024 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 335090.89 | 6:15 | 19:25 | 9190.5 | 9568.3 | 9649.3 | 9589.9 | 9734 | 9747.5 | 9537.5 | 9929.2 | 9574.5 | 9504.4 | 9493.8 | 9598.2 | 9672.7 | 9585.3 | 9730.2 | 9759.8 | 9652 | 9741.4 | 9637.6 | 9666.6 | 9759.2 | 9722.5 | 9642.9 | 9693.5 | 9487.4 | 8333 | 9447.6 | 9477.6 | 9786.9 | 9741.4 | 9660.4 | 9793.2 | 9433 | 9477.7 | 9737.8 | 9628.5 | 9611.4 | 9581.9 | 9622.2 | 9526.7 | 10416.8 | 9395.5 | 10264.5 | 9237.3 | 9749.1 | 10808.8 | 9143.7 | 10380.3 | 8911.6 | 9096.3 | 9750.4 | 9102.9 | 10079.5 | 8952.5 | 9941.2 | 8916.6 | 8765.5 | 9997.9 | 8881.9 | 9998.2 | 9874.9 | 8863.6 | 9518 | 9031.3 | 9383.4 | 8797.5 | 9320.4 | 9725.3 | 9896.6 | 8941.1 | 9824.3 | 8627.2 | 9566.1 | 9406.9 | 8786.7 | 9893.2 | 8715.6 | 9951.6 | 8819.7 | 9886.6 | 8921 | 9686.1 | 9004 | 10033.5 | 8945.9 | 9575.6 | 8902.2 | 7934.8 | 9745.5 | 9452 | 8805.8 | 10154.4 | 9905.9 | 9148.4 | 9056 | 9947.6 | 8901.2 | 9281.7 | 10156 | 8900.4 | 10140 | 8930.9 | 9961.6 | 9168.5 | 10071.8 | 8697.3 | 10173.2 | 9172.1 | 10031.7 | 9174 | 10106.9 | 9363.3 | 8951.3 | 9848 | 9116.9 | 8913.8 | 10058.9 | 10035.7 | 9939.3 | 9173.9 | 10011.3 | 9050.5 | 9829.9 | 9207.3 | 9719.3 | 8552.9 | 9911.1 | 9144.4 | 9132.5 | 9066.6 | 9064 | 7828.5 | 8872.8 | 7774.9 | 8724.2 | 8765.8 | 10152 | 8939.1 | 10179.3 | 9071.3 | 10095.7 | 8902 | 9092 | 8975.9 | 9906.9 | 10219.7 | 10187.6 | 10150 | 10077.3 | 10134.9 | 9151.9 | 10083.1 | 10228.7 | 10263.2 | 10259.4 | 10236.6 | 10283.2 | 9257.3 | 10324.3 | 9327.1 | 26.4985 | 29.9906 | 19.5818 | 29.7436 | 29.6555 | 30.2958 | 0 | 38.5687 | 0 | 0 | 38.9 | 0 | 7.0344 | 7.4107 | 6.7605 | 7.4366 | 7.1625 | 7.6667 | 10.766 | 10.13 | 11.734 | 10.705 | 10.619 | 11.21 | 4.5883 | 5.3641 | 5.1463 | 5.0336 | 5.0175 | 5.111 | 0.7613 | 1.0918 | 0.93685 | 1.0546 | 1.1001 | 0.98818 | 5.1896 | 5.2403 | 5.0787 | 5.1405 | 4.9597 | 0 | 0.84126 | 1.06 | 1.0181 | 1.0597 | 1.138 | 1.0409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 406193 | 702 | 394925 | 747 | 212964.95 | 475.133 | 4.5883 | 5.3641 | 5.1463 | 5.0336 | 5.0175 | 5.111 | 5.1896 | 5.2403 | 5.0787 | 5.1405 | 4.9597 | 0 | 760000 | 1000 | 786000 | 1000 | 1510267 | 4133 | 1544000 | 1506134 | 13.1667 | 5.0435 | 0.98882 | 5.1218 | 1.0263 | 19.61% | 20.04% | 27.6276 | 38.7343 | 7.2452 | 10.8607 | 1519989.6 | 1502000 | 1752080.6291 | 85.73%
2023-08-14 | 2024 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 335090.89 | 6:18 | 19:20 | 9875.2 | 10257.9 | 10356 | 10283.1 | 10457.5 | 10511.3 | 10299.4 | 10750.4 | 10269.6 | 10180.9 | 10221.8 | 10303.5 | 10423.9 | 10320.8 | 10460.6 | 10522.5 | 10370.9 | 10453.9 | 10364.3 | 10421.9 | 10482.1 | 10443.2 | 10252.4 | 10380.1 | 10195.2 | 8968.7 | 10207 | 10180.6 | 10474.6 | 10342.4 | 10248 | 10480.3 | 10073.3 | 10154.6 | 10432.4 | 10257.8 | 10227.6 | 10177.5 | 10119.9 | 10101.8 | 11373.1 | 10280.4 | 11232.6 | 10080.9 | 10657.7 | 11767.3 | 9918.4 | 11315.7 | 9600.6 | 9807.9 | 10550.1 | 9855.5 | 10897.1 | 9690.4 | 10777.1 | 9637.4 | 9448.5 | 10780.2 | 9565.6 | 10792.3 | 10672.4 | 9538.9 | 10300.3 | 9784.7 | 10123.6 | 9498.8 | 10070.8 | 10540.4 | 10686.9 | 9682.8 | 10625.3 | 9338.8 | 10329.3 | 10168.9 | 9500.6 | 10694.7 | 9431.4 | 10779.4 | 9538.1 | 10696.3 | 9703.5 | 10493.8 | 9822.4 | 10883.2 | 9717.8 | 10425.3 | 9702.1 | 8617.5 | 10550.3 | 10215.5 | 9512 | 10969.7 | 10613.7 | 9744.5 | 9611.9 | 10679.9 | 9470.1 | 9901.5 | 10763.4 | 9391.7 | 10750.5 | 9370.3 | 10492.1 | 9609.1 | 10588 | 9086.6 | 10686.8 | 9568.4 | 10561.4 | 9618.8 | 10702.1 | 9811.1 | 9491.6 | 10387.4 | 9569.9 | 9327 | 10543.2 | 10574.7 | 10416.9 | 9542.4 | 10494.2 | 9415.2 | 10269.7 | 9617.9 | 10187.2 | 8949.1 | 10362.5 | 9534.5 | 9465 | 9450.6 | 9467.7 | 8080.3 | 9297.9 | 8270.3 | 9259.2 | 9333.6 | 11024.2 | 9682.6 | 11040.1 | 9817.1 | 10976.2 | 9660.5 | 9812.2 | 9631.6 | 10624.8 | 10925.2 | 10947.8 | 10902.3 | 10866.4 | 10889.9 | 9859.1 | 10827.1 | 10998 | 11021.1 | 10982.8 | 10932.7 | 11019.8 | 9900 | 11116.4 | 9988 | 27.01 | 30.41 | 23.61 | 30.27 | 30.21 | 30.7 | 0 | 40.7 | 0 | 0 | 40.7 | 0 | 5.61 | 6.63 | 5.43 | 6.69 | 6.18 | 6.58 | 9.84 | 10.03 | 9.46 | 9.72 | 9.57 | 9.96 | 5.04 | 5.76 | 5.63 | 5.46 | 5.39 | 5.5 | 0.86 | 1.18 | 1.06 | 1.18 | 1.16 | 1.07 | 5.6 | 5.66 | 5.58 | 5.61 | 5.3 | 0 | 0.92 | 1.14 | 1.14 | 1.19 | 1.2 | 1.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407012 | 703 | 395729 | 749 | 214582.883 | 479.467 | 5.04 | 5.76 | 5.63 | 5.46 | 5.39 | 5.5 | 5.6 | 5.66 | 5.58 | 5.61 | 5.3 | 0 | 819000 | 1000 | 804000 | 2000 | 1617933 | 4334 | 1620000 | 1613599 | 13.0333 | 5.4633 | 1.085 | 5.55 | 1.1183 | 19.86% | 20.15% | 28.7017 | 40.7 | 6.1867 | 9.7633 | 1627725 | 1617933 | 1889936.6721 | 85.61%
2023-08-15 | 2024 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 335090.89 | 6:19 | 19:18 | 7517.7 | 7745.1 | 7810.7 | 7790.9 | 7854.9 | 7942.3 | 7771.9 | 8166 | 7778.7 | 7732.8 | 7767.6 | 7813.2 | 7932.8 | 7858.2 | 7896.8 | 7998.1 | 7787.6 | 7822.9 | 7811.7 | 7894.7 | 7831.5 | 7833.8 | 7660.9 | 7747.6 | 7691.4 | 6801.3 | 7762.2 | 7673.5 | 7865.9 | 7794.6 | 7753.1 | 7945.9 | 7702.7 | 7828.4 | 7914.7 | 7791.6 | 7855.4 | 7783.3 | 7716.7 | 7741.7 | 8618.6 | 7675.3 | 8450.1 | 7473.2 | 8020.2 | 9024.2 | 7485.8 | 8579.1 | 7382 | 7531.9 | 8073.8 | 7528.4 | 8307.1 | 7336.6 | 8271.5 | 7368.5 | 7299.4 | 8378.3 | 7332.3 | 8377.7 | 8252.4 | 7305 | 7927.5 | 7439.4 | 7842.7 | 7386.6 | 7796.3 | 8235.3 | 8284.7 | 7511.7 | 8229.5 | 7222.1 | 7981.4 | 7845.7 | 7316.3 | 8270.1 | 7240.2 | 8304.4 | 7236.3 | 8167.5 | 7572 | 8186 | 7708.4 | 8549.3 | 7615.2 | 8214 | 7588.2 | 6763 | 8146.3 | 8037.1 | 7315.2 | 8419.4 | 8136.2 | 7432.3 | 7321.9 | 8171.1 | 7222.6 | 7559.4 | 8256 | 7197.5 | 8218.8 | 7171.5 | 7983.5 | 7315.2 | 8048.8 | 6916.5 | 8100.8 | 7292.5 | 7976 | 7274.1 | 8080.2 | 7439.1 | 7292.2 | 7991.6 | 7315.2 | 7147 | 8085 | 8204.9 | 8017.4 | 7469 | 8196.4 | 7335.6 | 7873.2 | 7374.8 | 7775.2 | 6911.2 | 8058.2 | 7394.5 | 7390 | 7354.6 | 7351.4 | 6310.3 | 7225 | 6439.6 | 7177.1 | 7248.4 | 8664 | 7528 | 8720.9 | 7668.7 | 8635.2 | 7546.8 | 7647.7 | 7489.6 | 8456.8 | 8746.6 | 8754 | 8694.3 | 8587.7 | 8620.9 | 7763.5 | 8596.7 | 8739.6 | 8771.6 | 8810.4 | 8767.4 | 8852.7 | 7864.7 | 8847.9 | 7917.1 | 26.6676 | 30.0223 | 22.7177 | 29.9642 | 29.8303 | 30.3973 | 0 | 38.9 | 0 | 0 | 39.1 | 0 | 3.5978 | 4.1859 | 3.421 | 4.1941 | 3.9703 | 3.894 | 6.545 | 7.014 | 6.774 | 6.513 | 6.51 | 6.77 | 3.91 | 4.2422 | 4.2505 | 4.1814 | 4.0528 | 4.288 | 0.65347 | 0.84073 | 0.81244 | 0.91001 | 0.84063 | 0.80938 | 4.1257 | 4.112 | 4.1505 | 4.2462 | 3.9932 | 0 | 0.71073 | 0.81011 | 0.88687 | 0.90862 | 0.88406 | 0.8653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407637 | 705 | 396355 | 750 | 215829.817 | 483.733 | 3.91 | 4.2422 | 4.2505 | 4.1814 | 4.0528 | 4.288 | 4.1257 | 4.112 | 4.1505 | 4.2462 | 3.9932 | 0 | 625000 | 2000 | 626000 | 1000 | 1246934 | 4266 | 1248000 | 1242668 | 12.9833 | 4.1542 | 0.81111 | 4.1255 | 0.84428 | 19.53% | 20.46% | 28.2666 | 39 | 3.8772 | 6.6877 | 1252558.6 | 1246934 | 1420864.8216 | 87.76%
2023-08-16 | 2024 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 335090.89 | 6:14 | 19:20 | 9628.3 | 9979.9 | 10032.9 | 9962.5 | 10097.2 | 10237.6 | 10046.6 | 10488.4 | 10001.9 | 10030.1 | 9968 | 10052.7 | 10263.4 | 10078.7 | 10301.7 | 10394.9 | 10293.8 | 10469.5 | 10310.7 | 10300.2 | 10521 | 10435.3 | 10382.2 | 10482 | 10206.2 | 8922.5 | 10095.9 | 10160 | 10572.5 | 10456.6 | 10391.8 | 10580.2 | 10166.9 | 10209.6 | 10268.1 | 10352.9 | 10316.9 | 10267.3 | 10275.7 | 10249.3 | 11210.6 | 10122.3 | 11023.9 | 9885.6 | 10490.7 | 11596.3 | 9891.1 | 11200.3 | 9449.5 | 9641.7 | 10335.3 | 9637.8 | 10657.8 | 9476.7 | 10523 | 9478.1 | 9344.5 | 10619.4 | 9433.4 | 10666 | 10534.8 | 9399.5 | 10138.7 | 9579.9 | 10064 | 9491.5 | 10069.3 | 10517.6 | 10629.2 | 9682.9 | 10530.9 | 9317.8 | 10236.3 | 10098.7 | 9444.2 | 10611 | 9361.9 | 10626.6 | 9362.3 | 10500.4 | 9722.2 | 10451.1 | 9845.6 | 10858.8 | 9714 | 10383.3 | 9633.3 | 8587.8 | 10452.7 | 10147.3 | 9508.3 | 10890 | 10637.7 | 9851.5 | 9762.9 | 10721 | 9527.3 | 10023.2 | 10912.4 | 9606.9 | 10959.8 | 9650.8 | 10762.5 | 9858 | 10914.6 | 8921.7 | 11015.2 | 9949.9 | 10897.5 | 9988.6 | 10957.5 | 10200.3 | 9679.8 | 10563 | 9836.1 | 9605.9 | 10849.9 | 10930 | 10794.2 | 9983.1 | 10931.6 | 9861.2 | 10648.6 | 10044.5 | 10499.7 | 9281.7 | 10776 | 9892.9 | 9898.7 | 9786.6 | 9800 | 8510.2 | 9543.3 | 8390.9 | 9423.2 | 9451.5 | 11071.9 | 9753.6 | 11109.9 | 9921.8 | 10948.5 | 9662.9 | 9846.7 | 9634.9 | 10851.5 | 11129.6 | 11102.3 | 11076.7 | 10994.4 | 11031.8 | 10033 | 11020.9 | 11333.7 | 11358.2 | 11469.4 | 11330.6 | 11336.3 | 10159.4 | 11317.8 | 10242.3 | 26.9172 | 30.5801 | 28.3626 | 30.3189 | 30.2123 | 30.9409 | 0 | 41.3578 | 0 | 0 | 42 | 0 | 4.6783 | 5.0206 | 4.7058 | 4.9696 | 4.7166 | 4.9938 | 7.728 | 8.358 | 8.285 | 8.467 | 7.887 | 8.494 | 5.0622 | 5.9033 | 5.6682 | 5.5213 | 5.6361 | 5.707 | 0.85778 | 1.1429 | 1.0851 | 1.2083 | 1.1526 | 1.0677 | 5.5117 | 5.7816 | 5.6389 | 5.6868 | 5.5639 | 5.6834 | 0.9375 | 1.1085 | 1.1672 | 1.2148 | 1.2053 | 1.1366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408448 | 706 | 397174 | 752 | 217455.284 | 488 | 5.0622 | 5.9033 | 5.6682 | 5.5213 | 5.6361 | 5.707 | 5.5117 | 5.7816 | 5.6389 | 5.6868 | 5.5639 | 5.6834 | 811000 | 1000 | 819000 | 2000 | 1625467 | 4267 | 1627000 | 1621200 | 13.1 | 5.583 | 1.0858 | 5.6444 | 1.1283 | 19.45% | 19.99% | 29.5553 | 41.6789 | 4.8475 | 8.2032 | 1635167.8 | 1625400 | 1915809.9325 | 84.84%
2023-08-17 | 2024 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 335090.89 | 6:16 | 19:11 | 7296.2 | 9886.9 | 9817.8 | 9751.7 | 9863.4 | 9985.5 | 9861.3 | 10238.2 | 8793.5 | 5630.2 | 9759.4 | 9862.2 | 9944.2 | 9847.7 | 9855.7 | 10012.6 | 9820.4 | 9953.1 | 9852.9 | 9884.4 | 9970.1 | 9929.5 | 9784.8 | 9885.8 | 9675.5 | 8491.1 | 9696.1 | 9686.1 | 9989.8 | 9869.4 | 9789.4 | 9980.1 | 9670.5 | 9721.2 | 9910.4 | 9837.6 | 9786.8 | 9734.9 | 9784.4 | 9725.6 | 10744.5 | 9686.2 | 10566.1 | 9498.9 | 9946 | 11055.2 | 9285.7 | 10710.4 | 9144.2 | 9357.9 | 10024.7 | 9330.6 | 10363.8 | 9101.4 | 10250.2 | 9121.8 | 9047.7 | 10401.7 | 9151.5 | 10419.7 | 10323.4 | 9140.9 | 9916.6 | 9350.5 | 9702.1 | 9115 | 9704.4 | 10163.3 | 10321.9 | 9326.7 | 10280.4 | 8982.5 | 9949.5 | 9789.4 | 9133.3 | 10288.9 | 9022 | 10393.3 | 9068.2 | 10212.8 | 9338 | 10118.7 | 9442.5 | 10525.2 | 9325.8 | 10028.1 | 9259 | 8240 | 10062 | 9790 | 9056.6 | 10510.3 | 10192.8 | 9354.1 | 9267 | 10306.9 | 9091.2 | 9561.6 | 10479.8 | 9139.6 | 10498.2 | 9153.2 | 10244.8 | 9338.5 | 10365.9 | 8874.3 | 10446.1 | 9377.5 | 10005.4 | 9295.1 | 10041.6 | 9479.3 | 9173.1 | 9916.2 | 9279.4 | 9112.4 | 10033 | 10081.3 | 9963.6 | 9341.9 | 10036.1 | 9188.6 | 10028.1 | 9376.5 | 9766.5 | 8713.8 | 9918.2 | 9256.6 | 9287.8 | 9247.7 | 9193.5 | 7950.7 | 9111 | 8047.1 | 9076.9 | 9111.6 | 10193.7 | 9253.5 | 10204 | 9364.7 | 10158 | 9205 | 9361.6 | 9263.8 | 9888.2 | 10103.5 | 10087.5 | 10084.8 | 10077 | 10149.9 | 9355.4 | 10044 | 10490.9 | 10511.7 | 10124.3 | 10081.9 | 10522.8 | 9395.4 | 10165.8 | 9384.5 | 28.3089 | 30.3032 | 19.6044 | 30.0281 | 29.8712 | 30.644 | 0 | 40.4 | 0 | 0 | 41.0862 | 0 | 6.1026 | 6.2238 | 5.8345 | 6.2334 | 5.9671 | 6.3218 | 9.769 | 9.416 | 9.42 | 9.786 | 8.817 | 8.996 | 4.6365 | 5.5425 | 5.2467 | 5.2348 | 5.3071 | 5.2746 | 0.76742 | 1.1327 | 0.93982 | 1.0821 | 1.1685 | 1.0679 | 5.3469 | 5.4552 | 5.2512 | 5.4197 | 5.2055 | 5.2628 | 0.84517 | 1.1019 | 1.0175 | 1.0948 | 1.2088 | 1.1253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409264 | 708 | 397944 | 753 | 218993.484 | 490.8 | 4.6365 | 5.5425 | 5.2467 | 5.2348 | 5.3071 | 5.2746 | 5.3469 | 5.4552 | 5.2512 | 5.4197 | 5.2055 | 5.2628 | 816000 | 2000 | 770000 | 1000 | 1538200 | 2800 | 1583000 | 1535400 | 12.9167 | 5.207 | 1.0264 | 5.3236 | 1.0656 | 19.71% | 20.02% | 28.1266 | 40.7431 | 6.1139 | 9.3673 | 1548122.3 | 1538200 | 1809152.1766 | 85.02%
2023-08-18 | 2024 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 335090.89 | 6:16 | 19:28 | 9480.8 | 11792.1 | 11709.3 | 11692.3 | 11716.4 | 11881.5 | 11716.9 | 12163.1 | 11007 | 10733 | 11649.8 | 11783.7 | 11887.2 | 11752.4 | 11822 | 11982.3 | 11777.5 | 11946.2 | 11854 | 11884.3 | 11981.3 | 11947.4 | 11706.1 | 11858.6 | 11608.7 | 10188.3 | 11659.1 | 11643.8 | 11990.1 | 11827.2 | 11714.2 | 11946.2 | 11706.4 | 11791.3 | 11955.9 | 11875.4 | 11852.5 | 11781.2 | 11829.6 | 11759 | 13031.1 | 11644.1 | 12778.4 | 11383.6 | 12001.9 | 13439 | 11205.9 | 13002.4 | 10944.6 | 11205.4 | 12014.8 | 11269 | 12433.5 | 11009.6 | 12324.2 | 10953.4 | 10882.7 | 12530.5 | 10962.7 | 12543.8 | 12403.5 | 10935.2 | 11920.8 | 11260.6 | 11620.5 | 10930 | 11616.8 | 12197.6 | 12358 | 11178.4 | 12311.6 | 10769 | 11901.4 | 11739.8 | 10953.1 | 12369.9 | 10845.1 | 12476.1 | 10865.5 | 12277.4 | 11242.9 | 12193.6 | 11337.5 | 12677.7 | 11180 | 12016.2 | 11103.6 | 9890.1 | 12107.1 | 11767.2 | 10944.2 | 12666 | 12257.4 | 11211 | 11062 | 12407.4 | 10962.9 | 11559.6 | 12683.8 | 11013.6 | 12678.9 | 11044.7 | 12339.7 | 11277.9 | 12484.2 | 10697.1 | 12576.4 | 11270 | 12089.4 | 11210.4 | 12138.4 | 11416.2 | 11094.3 | 12005.4 | 11201.4 | 10974.7 | 12112.1 | 12191.5 | 12044.1 | 11284.6 | 12116.8 | 11061.4 | 12064.6 | 11242.8 | 11783.6 | 10415.5 | 11963.3 | 11122.5 | 11169.7 | 11118.8 | 10978.5 | 9514 | 10957.1 | 9687.4 | 10889 | 10943.8 | 12351.7 | 11192.6 | 12370 | 11360.2 | 12318.3 | 11184 | 11368.9 | 11177.3 | 12068.5 | 12315.6 | 12315.2 | 12296.1 | 12258.6 | 12317.2 | 11412.6 | 12221.8 | 12839.7 | 12891.9 | 12406.8 | 12344.7 | 12928.7 | 11483.6 | 12403 | 11542.5 | 26.6897 | 30.7094 | 22.7684 | 30.5935 | 30.5244 | 31.0085 | 0 | 44.8 | 0 | 0 | 45.2 | 0 | 3.6752 | 4.3175 | 3.4828 | 4.2936 | 4.0231 | 3.9472 | 6.624 | 7.34 | 6.32 | 6.687 | 7.679 | 7.252 | 6.6368 | 6.7764 | 6.4317 | 6.4064 | 6.4741 | 6.4884 | 1.0441 | 1.3189 | 1.2582 | 1.423 | 1.3493 | 1.2483 | 6.7431 | 6.716 | 6.502 | 6.6949 | 6.3945 | 6.5195 | 1.1235 | 1.294 | 1.3399 | 1.4379 | 1.4078 | 1.3215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410135 | 709 | 398900 | 754 | 220850.617 | 494.8 | 6.6368 | 6.7764 | 6.4317 | 6.4064 | 6.4741 | 6.4884 | 6.7431 | 6.716 | 6.502 | 6.6949 | 6.3945 | 6.5195 | 871000 | 1000 | 956000 | 1000 | 1857133 | 4000 | 1825000 | 1853133 | 13.2 | 6.5356 | 1.2736 | 6.595 | 1.3208 | 19.49% | 20.03% | 28.7156 | 45 | 3.9566 | 6.9837 | 1870158.5 | 1857133 | 2210756.8206 | 84%
2023-08-19 | 2024 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 335090.89 | 6:20 | 19:23 | 11362.4 | 11753.9 | 11749.2 | 11723.6 | 11811.4 | 11847.9 | 11683.3 | 11989.5 | 11817.1 | 11525.9 | 11662.8 | 11756.4 | 11861.4 | 11731.3 | 11829.7 | 11933.3 | 11764.1 | 11867.3 | 11803 | 11829.2 | 11877.8 | 11854.5 | 11584.7 | 11794.5 | 11609.6 | 10244.4 | 11682 | 11652.2 | 11895 | 11766.1 | 11673.2 | 11782.5 | 11760.9 | 11853.5 | 12018 | 11926 | 11919.1 | 11838.2 | 11894.9 | 11804.2 | 13013.4 | 11695.3 | 12392.4 | 11404.5 | 11903.8 | 12727.3 | 11277.4 | 12494.4 | 11024.3 | 11291.8 | 11956.3 | 11367.5 | 12205.9 | 11062.2 | 12167.3 | 11014.8 | 10968.3 | 12280 | 11050 | 12306.6 | 12230.6 | 11025.8 | 11904.1 | 11383.8 | 11683.3 | 11018.8 | 11677.1 | 12122.7 | 12465.5 | 11288.2 | 12177.2 | 10864 | 11890.8 | 11787.4 | 11036.6 | 12223.7 | 10949.5 | 12226 | 10928 | 12142.5 | 11399 | 12147.8 | 11483.5 | 12421.7 | 11323.8 | 12021.9 | 11236.9 | 10022.4 | 12054.2 | 11820.1 | 11040.2 | 12371.2 | 12134.5 | 11286.4 | 11128.8 | 12199.1 | 11006.7 | 11616.5 | 12387 | 11061.9 | 12353.7 | 11107.4 | 12174.4 | 11337.9 | 12260.4 | 10748.8 | 12639.7 | 11339.7 | 12181 | 11267.8 | 12200.2 | 11468.6 | 11143.1 | 12030.7 | 11252.7 | 11021 | 12202.5 | 12311.4 | 12143.7 | 11362.3 | 12228.8 | 11131.4 | 12130 | 11336.8 | 11822.3 | 10487.4 | 12068.8 | 11206.3 | 11244.1 | 11184.8 | 11105.9 | 9590.3 | 10985.5 | 9717.9 | 10937.6 | 11025.3 | 12564.6 | 11352.8 | 12583 | 11541.6 | 12527.9 | 11365.4 | 11555.9 | 11302.6 | 12262.8 | 12520.6 | 12523.3 | 12519.4 | 12490.9 | 12540.6 | 11598 | 12439.3 | 12938.8 | 13006 | 12562.2 | 12498.9 | 13085.1 | 11629.2 | 12573.3 | 11677.6 | 28.5409 | 31.952 | 25.6653 | 31.7888 | 31.752 | 32.2809 | 0 | 47.6 | 0 | 0 | 48.3 | 0 | 3.0743 | 3.0508 | 2.8911 | 3.0685 | 3.0012 | 2.9202 | 6.258 | 6.03 | 5.689 | 5.923 | 7.078 | 5.515 | 6.7625 | 6.84 | 6.4993 | 6.5839 | 6.7796 | 6.7797 | 1.0344 | 1.2984 | 1.2402 | 1.4249 | 1.3691 | 1.2778 | 6.881 | 6.7971 | 6.5854 | 6.8705 | 6.8946 | 6.616 | 1.1123 | 1.2753 | 1.3125 | 1.4456 | 1.4062 | 1.3366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411091 | 710 | 399808 | 756 | 222714.484 | 499 | 6.7625 | 6.84 | 6.4993 | 6.5839 | 6.7796 | 6.7797 | 6.881 | 6.7971 | 6.5854 | 6.8705 | 6.8946 | 6.616 | 956000 | 1000 | 908000 | 2000 | 1863867 | 4200 | 1861000 | 1859667 | 13.05 | 6.7075 | 1.2741 | 6.7741 | 1.3148 | 19% | 19.41% | 30.33 | 47.95 | 3.001 | 6.0822 | 1876936.7 | 1863800 | 2248781.7894 | 82.88%
2023-08-20 | 2024 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 335090.89 | 6:21 | 19:16 | 7480.4 | 7790.1 | 7781 | 7749.6 | 7837.3 | 7869.6 | 7786.2 | 8000.2 | 7823.9 | 7599.5 | 7687.3 | 7772.5 | 7885.3 | 7761.2 | 7838.6 | 7933.7 | 7765.7 | 7851.5 | 7777.7 | 7796.4 | 7838.4 | 7822.8 | 7651.5 | 7758.1 | 7622.7 | 6720.5 | 7716.1 | 7666.3 | 7861.1 | 7720.4 | 7649.3 | 7774.9 | 7730.3 | 7818.9 | 7901.3 | 7826.5 | 7877.4 | 7777.7 | 7816.5 | 7743.4 | 8405.7 | 7529.5 | 8236 | 7334.9 | 7736.3 | 8696.9 | 7289.3 | 8371.5 | 7280.5 | 7429.9 | 7983.2 | 7487.6 | 8239.2 | 7287.2 | 8191.1 | 7282.3 | 7245.9 | 8296.8 | 7312.3 | 8346.3 | 8251.7 | 7299.4 | 7863 | 7433.6 | 7770.6 | 7339.9 | 7744.8 | 8193.3 | 8255.2 | 7537 | 8222.5 | 7250.9 | 7923.7 | 7870 | 7290.7 | 8277.9 | 7263.5 | 8260.2 | 7237.9 | 8180.7 | 7601.8 | 8216.1 | 7670.5 | 8492.2 | 7570 | 8101.2 | 7509.5 | 6709.2 | 8100.7 | 7904 | 7314.1 | 8388.4 | 8108.6 | 7428.1 | 7325.4 | 8158.5 | 7219.1 | 7639.8 | 8308.8 | 7257.6 | 8248.1 | 7242.4 | 8036.4 | 7386.7 | 8113.8 | 6914.6 | 8196.2 | 7398.6 | 8037.3 | 7323.8 | 7900.3 | 7463.3 | 7347 | 7997.2 | 7337.3 | 7191.3 | 8084.7 | 8171.6 | 8004.7 | 7394.8 | 8089.6 | 7242.5 | 7871.7 | 7378.1 | 7724.5 | 6807.3 | 7919.8 | 7279.8 | 7321.2 | 7283.6 | 7238.1 | 6263 | 7129 | 6303.4 | 7218.6 | 7260.3 | 8492.1 | 7401.3 | 8492.4 | 7516.7 | 8389.5 | 7375.1 | 7502 | 7385.7 | 8207.2 | 8472.5 | 8482.7 | 8475.4 | 8429.5 | 8481.1 | 7595.5 | 8397.4 | 8539.6 | 8569.4 | 8522.3 | 8453.6 | 8586.3 | 7662.5 | 8550.2 | 7686.2 | 28.7363 | 32.304 | 24.0448 | 32.3492 | 32.3572 | 32.6338 | 0 | 42.8 | 0 | 0 | 43.2 | 0 | 2.3932 | 2.4993 | 2.396 | 2.371 | 2.4718 | 2.5112 | 7.011 | 6.428 | 5.887 | 7.424 | 7.572 | 5.326 | 4.2852 | 4.3621 | 4.0757 | 4.222 | 4.2828 | 4.3392 | 0.6261 | 0.8388 | 0.74338 | 0.88266 | 0.87831 | 0.83092 | 4.3036 | 4.2343 | 4.0086 | 4.282 | 4.2873 | 4.1854 | 0.68355 | 0.82154 | 0.81345 | 0.88819 | 0.91162 | 0.87833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411712 | 711 | 400428 | 757 | 223951.7 | 503.267 | 4.2852 | 4.3621 | 4.0757 | 4.222 | 4.2828 | 4.3392 | 4.3036 | 4.2343 | 4.0086 | 4.282 | 4.2873 | 4.1854 | 621000 | 1000 | 620000 | 1000 | 1237216 | 4267 | 1239000 | 1232949 | 12.9167 | 4.2612 | 0.80003 | 4.2169 | 0.83278 | 18.77% | 19.75% | 30.4042 | 43 | 2.4404 | 6.608 | 1242341.1 | 1237200 | 1427946.9071 | 86.64%
2023-08-21 | 2024 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 335090.89 | 6:19 | 19:25 | 10827.6 | 11372.8 | 11515 | 11428.2 | 11551.8 | 11509.6 | 11475.3 | 11773.8 | 10759.4 | 8739.8 | 11330.4 | 11355.1 | 11446.1 | 11425.9 | 11510.2 | 11531.3 | 11397.5 | 11400.2 | 11293.9 | 11417.5 | 11286 | 11271.8 | 8436.8 | 10856 | 10958.5 | 9867.4 | 11170 | 11041 | 11208.7 | 10999.6 | 10793.1 | 11069.6 | 10778.1 | 10817.1 | 11346.4 | 11170.1 | 10977.4 | 10888.5 | 10940.8 | 10822.3 | 12105.1 | 11331.7 | 12023.5 | 11155.3 | 11668.6 | 12272.8 | 10903.9 | 11837.5 | 10693.9 | 10907.9 | 11409.4 | 10841.9 | 11679.4 | 10805.5 | 11489.2 | 10532.6 | 10616.8 | 11661.2 | 10828.7 | 11776.6 | 11725.2 | 10742.2 | 11450.3 | 10938.1 | 10942.9 | 10360 | 11019.7 | 11300.8 | 11806.4 | 10752.3 | 11362.5 | 10165.4 | 11253.8 | 10949.8 | 10584.1 | 11393.9 | 10388.5 | 11443.7 | 10405.9 | 11122.5 | 10545.6 | 11188.6 | 10631.4 | 11482.2 | 10604.1 | 11147.3 | 10475.3 | 9388.4 | 11058.3 | 10792.7 | 10231.5 | 11419.9 | 11169.2 | 10447.4 | 10305.4 | 11154.3 | 10109.5 | 10447.4 | 11117.4 | 9985.7 | 11149.8 | 9954.1 | 10899.1 | 10176.3 | 11005.1 | 9661.4 | 11190.3 | 10161.3 | 11113.9 | 10303.7 | 10933.8 | 10499 | 10057.6 | 10845 | 10104.2 | 9927.5 | 10892.7 | 10954.5 | 10829.9 | 10108.8 | 10932.9 | 10073.8 | 10915.1 | 10440.9 | 10931.1 | 9648.1 | 10900.5 | 10128.1 | 10083.5 | 10149 | 10204.6 | 8719.8 | 10054.5 | 9107.5 | 10403.8 | 10427.1 | 11158.5 | 10213.6 | 11218.6 | 10435.6 | 11449.2 | 10492.9 | 10682.3 | 10557.4 | 10868.9 | 11150.4 | 11092.6 | 11031 | 10985 | 11056.6 | 10287 | 11073.5 | 11318.2 | 11345.8 | 11085.1 | 11108.3 | 11529 | 10498.8 | 11074.6 | 10262.2 | 31.0262 | 33.4045 | 29.5919 | 33.3465 | 33.3707 | 33.6977 | 0 | 48.8 | 0 | 0 | 48.5 | 0 | 2.6849 | 2.7747 | 2.5624 | 2.6783 | 2.6679 | 2.6448 | 4.921 | 5.024 | 6.224 | 5.114 | 4.871 | 5.001 | 6.6496 | 6.5348 | 6.5944 | 6.2808 | 6.1311 | 5.9853 | 0.99465 | 1.1274 | 1.2026 | 1.3428 | 1.1233 | 1.0094 | 6.7005 | 6.483 | 6.6557 | 6.5744 | 6.1776 | 5.8712 | 1.0713 | 1.1071 | 1.2599 | 1.3603 | 1.1591 | 1.0596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412598 | 713 | 401275 | 759 | 225678.818 | 507.533 | 6.6496 | 6.5348 | 6.5944 | 6.2808 | 6.1311 | 5.9853 | 6.7005 | 6.483 | 6.6557 | 6.5744 | 6.1776 | 5.8712 | 886000 | 2000 | 847000 | 2000 | 1727118 | 4266 | 1729000 | 1722852 | 13.1 | 6.3627 | 1.1333 | 6.4104 | 1.1695 | 17.81% | 18.24% | 32.4063 | 48.65 | 2.6688 | 5.1925 | 1737975.1 | 1727067 | 2149434.7649 | 80.35%
2023-08-22 | 2024 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 335090.89 | 6:17 | 19:26 | 12090.7 | 12475.4 | 12458.3 | 12421 | 12510.3 | 12547.6 | 12534.4 | 12785.3 | 12478.3 | 11221.5 | 12366.1 | 12485.6 | 12464 | 12417.1 | 12464.7 | 12512.7 | 12383.2 | 12452.3 | 12430.6 | 12482.5 | 12486.4 | 12477.8 | 11301.2 | 12390.1 | 12279.4 | 10996.1 | 12301.2 | 12289.9 | 12519.7 | 12430.6 | 12312.5 | 12423.4 | 12433.1 | 12476.9 | 12896.8 | 12823 | 12548.6 | 12462.9 | 12485 | 12419.7 | 13516.2 | 12370.7 | 12818.8 | 11987.8 | 12534.1 | 13245.8 | 11975.4 | 12909.4 | 11770.6 | 12008.8 | 12576.4 | 12038.3 | 12808.3 | 11870.3 | 12745.8 | 11779.4 | 11749.3 | 12856.6 | 11819.4 | 12861.2 | 12777.6 | 11759.2 | 12598.3 | 12166.4 | 12356.1 | 11820.1 | 12347.3 | 12678.3 | 13057.5 | 11717 | 12772.5 | 11620.1 | 12557.6 | 12440.9 | 11851.3 | 12796.9 | 11716.6 | 12875.4 | 11837.4 | 12770.2 | 12025 | 12676.7 | 12130 | 12912.7 | 12015.7 | 12581.6 | 11979.6 | 10668.5 | 12631.8 | 12381.2 | 11725.8 | 12899.1 | 12692.9 | 12022.5 | 11933 | 12743.4 | 11759.1 | 12155 | 12833 | 11716.8 | 12847.6 | 11700.2 | 12678.5 | 11951.1 | 12741.3 | 11395.4 | 13206 | 12004.5 | 12696.5 | 11895.5 | 12532.8 | 12072.5 | 11803 | 12636.3 | 11925.6 | 11731.4 | 12732.1 | 12808.5 | 12679.6 | 11990 | 12753.2 | 11830 | 12438.1 | 11958.1 | 12451 | 11164.1 | 12628.2 | 11874 | 11988.9 | 11993.2 | 10652 | 9937.4 | 11816.6 | 10458.8 | 11824.8 | 11827.2 | 13022.3 | 11978.5 | 13040.7 | 12153 | 12968.8 | 11988.3 | 12164 | 11969.9 | 12793.6 | 13028.8 | 13010.2 | 12989.3 | 12962 | 12990.9 | 12247.2 | 12945.2 | 13767.7 | 13808.8 | 13035 | 13014.9 | 13848.7 | 12447 | 13047.2 | 12284.5 | 0 | 33.3128 | 0 | 32.9769 | 32.7461 | 33.5603 | 0 | 47 | 0 | 0 | 47.6318 | 0 | 5.5069 | 5.8312 | 5.4377 | 5.8283 | 5.6204 | 5.8579 | 9.315 | 8.504 | 9.275 | 9.117 | 9.92 | 9.536 | 7.1385 | 7.246 | 7.0418 | 6.9145 | 7.1516 | 7.1291 | 1.0337 | 1.3274 | 1.2633 | 1.4393 | 1.4105 | 1.317 | 7.2977 | 7.2382 | 7.1229 | 7.273 | 7.2958 | 7.1011 | 1.1219 | 1.3087 | 1.325 | 1.4704 | 1.4472 | 1.3684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413584 | 714 | 402257 | 760 | 227640.1 | 511.667 | 7.1385 | 7.246 | 7.0418 | 6.9145 | 7.1516 | 7.1291 | 7.2977 | 7.2382 | 7.1229 | 7.273 | 7.2958 | 7.1011 | 986000 | 1000 | 982000 | 1000 | 1961282 | 4134 | 1966000 | 1957148 | 13.15 | 7.1036 | 1.2985 | 7.2214 | 1.3403 | 18.28% | 18.56% | 33.149 | 47.3159 | 5.6804 | 9.2778 | 1975109.1 | 1961133 | 2404431.502 | 81.56%
2023-08-23 | 2024 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 335090.89 | 6:23 | 19:19 | 9372.1 | 9921.3 | 9994.9 | 9907.7 | 10084.9 | 10129.8 | 10037.5 | 10439.6 | 9856.9 | 8595 | 9794.1 | 9899.2 | 9992.6 | 9877.2 | 9959.4 | 10052 | 9834.9 | 9869.7 | 9896.8 | 10002.8 | 9872.2 | 9902.1 | 8664.8 | 9727.1 | 9686.7 | 8593.1 | 9774.2 | 9711.8 | 9893.9 | 9718.8 | 9625 | 9854.3 | 9849.4 | 9919.9 | 10048.4 | 9942.8 | 9949.1 | 9774.7 | 9808.6 | 9758.9 | 10764.1 | 9748.9 | 10510.4 | 9539 | 10027.4 | 11050 | 9341.9 | 10554.7 | 9198.1 | 9427.5 | 10068.9 | 9444.2 | 10420.5 | 9348.5 | 10278.6 | 9228.5 | 9027.6 | 10297.8 | 9151.5 | 10294.5 | 10115.8 | 9081 | 9793.2 | 9290.1 | 9529.8 | 8947.8 | 9476.6 | 9897.4 | 10074.7 | 8604.6 | 10032.4 | 8822.3 | 9754.3 | 9619.8 | 8995.4 | 10103.1 | 8911 | 10216.9 | 9041.7 | 10104.1 | 9193 | 9906.5 | 9313.3 | 10261 | 9192.4 | 9826.6 | 9109.4 | 8100.6 | 10086.6 | 9660.2 | 9134.9 | 10593.1 | 10378.4 | 9575.1 | 9457.4 | 10436.7 | 9337.7 | 9695.7 | 10598.5 | 9287.6 | 10546.6 | 9289.2 | 10257.1 | 9516.7 | 10327.2 | 8960.9 | 10434.4 | 9410.2 | 10184.4 | 9308.1 | 10177.5 | 9481.8 | 9331.9 | 10291.4 | 9483.5 | 9313.5 | 10426.1 | 10521.7 | 10303.5 | 9564 | 10407.6 | 9347.8 | 9240.5 | 9244.3 | 9906.2 | 8735.5 | 10169.4 | 9354.4 | 9532.3 | 9479.9 | 8379.4 | 7897.4 | 9221.9 | 8080.8 | 9097.3 | 9132 | 10603.3 | 9309.9 | 10602.9 | 9455.6 | 10483.9 | 9282.9 | 9429.8 | 9291.3 | 10251.1 | 10585.8 | 10538.6 | 10492.8 | 10481.5 | 10545.6 | 9484.3 | 10455.8 | 10643.1 | 10667.9 | 10532.2 | 10515.9 | 10686.9 | 9564.8 | 10661.6 | 9583.4 | 0 | 29.4902 | 0 | 29.1637 | 29.1753 | 29.7392 | 0 | 38.3579 | 0 | 0 | 39.1 | 0 | 9.0008 | 8.9464 | 8.6994 | 9.1498 | 8.6248 | 9.1801 | 12.395 | 12.856 | 13.119 | 13.085 | 12.016 | 14.154 | 5.3061 | 5.4264 | 5.3192 | 5.0443 | 5.4513 | 5.2411 | 0.80499 | 1.0536 | 0.98435 | 1.0829 | 1.1392 | 1.0045 | 5.375 | 5.3131 | 5.2689 | 5.1845 | 5.4982 | 5.1655 | 0.88288 | 1.0317 | 1.0665 | 1.0934 | 1.1877 | 1.0609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414362 | 715 | 403067 | 762 | 229192.4 | 515.933 | 5.3061 | 5.4264 | 5.3192 | 5.0443 | 5.4513 | 5.2411 | 5.375 | 5.3131 | 5.2689 | 5.1845 | 5.4982 | 5.1655 | 778000 | 1000 | 810000 | 2000 | 1552300 | 4266 | 1585000 | 1548034 | 12.9333 | 5.2981 | 1.0116 | 5.3009 | 1.0538 | 19.09% | 19.88% | 29.3921 | 38.7289 | 8.9335 | 12.9375 | 1561380.8 | 1552200 | 1843521.6967 | 84.2%
2023-08-24 | 2024 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 335090.89 | 6:25 | 19:15 | 10094 | 10398.8 | 10370.5 | 10303.9 | 10422.8 | 10427.3 | 10402.1 | 10675.6 | 10428.4 | 9322 | 10237 | 10382.9 | 10278.6 | 10276.3 | 10327.9 | 10320.6 | 10242.9 | 10311.3 | 10250.1 | 10287.7 | 10320.2 | 10288.8 | 10133.7 | 10220.4 | 10013.9 | 8888.3 | 10054.8 | 10054.5 | 10313.5 | 10236.3 | 10153.4 | 10262.4 | 10107.9 | 10164.5 | 10393.3 | 10327.5 | 10293 | 10216.7 | 10284.7 | 10163.3 | 11356.5 | 10426 | 11014.2 | 10138.8 | 10639.7 | 11423.3 | 10035.4 | 11072.9 | 9649.1 | 9904.8 | 10366.7 | 9866.3 | 10599.7 | 9665.3 | 10593 | 9564.8 | 9661.3 | 10775.5 | 9701.1 | 10771.6 | 10707.7 | 9706.9 | 10541.5 | 10105.6 | 10179.4 | 9725.2 | 10234.3 | 10566.3 | 10705.9 | 9020.4 | 10673.6 | 9586.1 | 10494.5 | 10323.9 | 9791.8 | 10705.3 | 9626.9 | 10798 | 9738.4 | 10680.7 | 9928.8 | 10572.3 | 10027.4 | 10807.5 | 9894.9 | 10453.8 | 9828.2 | 8792.6 | 10573.6 | 10285.1 | 9512.5 | 10670.9 | 10380.2 | 9662.9 | 9571.5 | 10401.6 | 9408.9 | 9788.4 | 10469.3 | 9346.5 | 10491.1 | 9309.6 | 10285.1 | 9529.1 | 10432.9 | 9078.4 | 10589.3 | 9552 | 10445.4 | 9639.1 | 10553.9 | 9767.9 | 9448.2 | 10258 | 9488.2 | 9332.8 | 10321.7 | 10384.2 | 10236.7 | 9549.2 | 10264.4 | 9407.5 | 8857.3 | 9565 | 10114.5 | 8968.9 | 10209 | 9476.3 | 9594.3 | 9647.3 | 7228.8 | 7547.2 | 9502 | 8499.3 | 9726.6 | 9746.9 | 10881 | 9870 | 10909.1 | 9998.8 | 10818.9 | 9851.9 | 10023.7 | 9903.3 | 10638.7 | 10854.2 | 10839.8 | 10828.6 | 10834.4 | 10859.2 | 10117.4 | 10835 | 11238.8 | 11254.1 | 10801.1 | 10783.7 | 11275.9 | 10180.7 | 10877.6 | 10074.1 | 0 | 30.5808 | 0 | 30.3567 | 30.2275 | 30.8482 | 0 | 40.7 | 0 | 0 | 40.9 | 0 | 7.3412 | 7.5882 | 7.0635 | 7.6429 | 7.2693 | 7.8741 | 11.283 | 11.187 | 11.144 | 11.255 | 10.525 | 11.623 | 5.7069 | 5.7942 | 5.7723 | 5.5555 | 5.5443 | 5.7902 | 0.83166 | 1.1606 | 1.0465 | 1.1638 | 1.2028 | 1.1707 | 5.8891 | 5.7678 | 5.8167 | 5.7966 | 5.7031 | 5.7477 | 0.91067 | 1.1365 | 1.1254 | 1.1867 | 1.2469 | 1.2211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415179 | 717 | 403836 | 763 | 230803.685 | 520.267 | 5.7069 | 5.7942 | 5.7723 | 5.5555 | 5.5443 | 5.7902 | 5.8891 | 5.7678 | 5.8167 | 5.7966 | 5.7031 | 5.7477 | 817000 | 2000 | 769000 | 1000 | 1611285 | 4334 | 1583000 | 1606951 | 12.8333 | 5.6939 | 1.096 | 5.7869 | 1.1379 | 19.25% | 19.66% | 30.5033 | 40.8 | 7.4632 | 11.1695 | 1621765.2 | 1611133 | 1975526.7614 | 81.55%
2023-08-25 | 2024 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 335090.89 | 6:25 | 19:16 | 9782.7 | 10149.9 | 10177 | 10098.7 | 10255.2 | 10276.1 | 10233.7 | 10525.2 | 10133.3 | 10059.2 | 10033.1 | 10125.7 | 10174.6 | 10113.6 | 10318.8 | 10297.2 | 10263.7 | 10345.2 | 10289.4 | 10298.2 | 10370.3 | 10335.1 | 10213.4 | 10285.7 | 10118.8 | 8970.6 | 10084.6 | 10132.4 | 10385.7 | 10308.5 | 10221.6 | 10322.1 | 10304.8 | 10325.5 | 10535.6 | 10512.7 | 10414 | 10320.8 | 10363.1 | 10291.8 | 10968.5 | 10134.8 | 10789.2 | 9938.5 | 10468.6 | 11295.2 | 9961.9 | 10917.3 | 9507.5 | 9724.2 | 10268.5 | 9741.2 | 10550.6 | 9661.3 | 10425.5 | 9522.5 | 9407.4 | 10526.8 | 9466.8 | 10512.7 | 10435 | 9430 | 10253.5 | 9840.7 | 9892.2 | 9526.1 | 9999.5 | 10382.8 | 10307.5 | 8254.6 | 10472.9 | 9386.5 | 10226.9 | 10133.5 | 9528.4 | 10546.4 | 9447.8 | 10600.2 | 9562 | 10529.3 | 9762.4 | 10407 | 9850.9 | 10680.2 | 9741.9 | 10308.7 | 9615 | 8636.1 | 10434.3 | 10156.5 | 9507 | 10714.3 | 10516.3 | 9863.2 | 9793.3 | 10569.8 | 9627.2 | 9972 | 10716.7 | 9588.5 | 10765 | 9617.2 | 10562.6 | 9847.1 | 10646.6 | 9381.7 | 10891.3 | 9883 | 10608.4 | 9839.2 | 10658.1 | 9995.5 | 9645.5 | 10488.3 | 9794.2 | 9609.2 | 10627.9 | 10665.3 | 10545.2 | 9836.4 | 10609.1 | 9691.3 | 9366.1 | 9764.2 | 10287.8 | 9198.2 | 10457.7 | 9748.9 | 9823.7 | 9805.5 | 8000 | 8114 | 9651.9 | 8527.5 | 9439.7 | 9468.7 | 10779.4 | 9626.7 | 10810.9 | 9774.2 | 10695.6 | 9603.8 | 9776.2 | 9608 | 10593.5 | 10854.4 | 10801.2 | 10757.9 | 10720.9 | 10757.9 | 9888.2 | 10754.2 | 11121.1 | 11122.3 | 10765.3 | 10774.8 | 11145.1 | 10059.4 | 10908.6 | 10024.1 | 0 | 30.5042 | 0 | 30.2309 | 30.1934 | 30.7601 | 0 | 40.6 | 0 | 0 | 41 | 0 | 7.0875 | 7.2441 | 6.8709 | 7.367 | 6.9884 | 7.2853 | 11.755 | 10.564 | 11.223 | 10.817 | 10.632 | 11.2 | 5.511 | 5.7885 | 5.6355 | 5.3751 | 5.6209 | 5.5657 | 0.84303 | 1.1299 | 1.0549 | 1.1716 | 1.1899 | 1.0962 | 5.6852 | 5.7891 | 5.7204 | 5.6545 | 5.7941 | 5.5423 | 0.91872 | 1.1042 | 1.1323 | 1.193 | 1.2372 | 1.1433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415988 | 718 | 404642 | 765 | 232412.351 | 524.533 | 5.511 | 5.7885 | 5.6355 | 5.3751 | 5.6209 | 5.5657 | 5.6852 | 5.7891 | 5.7204 | 5.6545 | 5.7941 | 5.5423 | 809000 | 1000 | 806000 | 2000 | 1608666 | 4266 | 1612000 | 1604400 | 12.85 | 5.5828 | 1.0809 | 5.6976 | 1.1214 | 19.36% | 19.68% | 30.4222 | 40.8 | 7.1405 | 11.0318 | 1619359.4 | 1594200 | 1950195.8197 | 81.75%
2023-08-26 | 2024 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 335090.89 | 6:19 | 19:10 | 8878.2 | 9208.2 | 9195.6 | 9139.1 | 9254.9 | 9295.8 | 9269.8 | 9576.8 | 9224 | 9095.6 | 9123.7 | 9236.8 | 9222.3 | 9170.4 | 9154.4 | 9269.8 | 9059.3 | 9122 | 9145.9 | 9224.7 | 9143.1 | 9141.4 | 8950.6 | 9053.6 | 8995.4 | 8082.3 | 9100.5 | 9021.8 | 9190.9 | 9065.3 | 8992.2 | 9167.7 | 9154.6 | 9209.2 | 9402.5 | 9315.2 | 9254.3 | 9127.2 | 9163 | 9122.1 | 9956.1 | 9034.3 | 9641.6 | 8827.6 | 9233.9 | 10108.1 | 8650.3 | 9716.7 | 8649.9 | 8859.3 | 9336.5 | 8853.6 | 9601.9 | 8710.5 | 9523.1 | 8653.5 | 8649.3 | 9697 | 8668.6 | 9650.6 | 9572.3 | 8643.1 | 9338.4 | 8916.1 | 9182.2 | 8821.3 | 9206.5 | 9643.1 | 9867.8 | 9034.9 | 9626.3 | 8630.5 | 9373.7 | 9277.7 | 8725.8 | 9631.3 | 8608.1 | 9678.7 | 8722.8 | 9572.2 | 8985.4 | 9561.8 | 9039.3 | 9897.3 | 9016 | 9563.8 | 9012.5 | 8093.3 | 9638.2 | 9406.6 | 8752.8 | 9850 | 9606.7 | 8945.4 | 8841.4 | 9626.6 | 8732.7 | 9109.1 | 9775.5 | 8726.8 | 9750.8 | 8693.3 | 9526.2 | 8880.5 | 9574.1 | 8419 | 9718.8 | 8845.4 | 9467.1 | 8708.2 | 9518 | 8854.5 | 8853 | 9600.4 | 8874 | 8720.1 | 9665.4 | 9753.8 | 9576.3 | 8961.5 | 9680 | 8781 | 9487.4 | 8853.8 | 9200.2 | 8280.6 | 9485.1 | 8829.2 | 8967 | 8990.1 | 8837.4 | 7725.7 | 8893.3 | 7964.3 | 8895.1 | 8916.9 | 10064.6 | 9020.2 | 10084.4 | 9140.4 | 10027.8 | 9026.3 | 9177.8 | 9061.6 | 9765.4 | 10036.5 | 9966.1 | 9954.7 | 9935.6 | 9995.8 | 9169.7 | 9976.2 | 10121.3 | 10171.4 | 9915.1 | 9905.8 | 10265.6 | 9231.4 | 10005.7 | 9150.7 | 0 | 30.4125 | 0 | 30.2458 | 30.1344 | 30.7589 | 0 | 39.9 | 0 | 0 | 40.6819 | 40.7 | 5.9861 | 6.1125 | 5.7865 | 6.2144 | 5.9862 | 6.2362 | 10.188 | 9.667 | 9.464 | 9.608 | 9.238 | 9.924 | 4.3262 | 4.509 | 4.6982 | 4.6347 | 4.5484 | 4.5962 | 0.76841 | 1.066 | 0.92687 | 1.0847 | 1.1466 | 1.0689 |  |  | 4.7706 | 4.6793 | 4.6544 | 4.6846 | 0.84379 | 1.0404 | 1.0063 | 1.1043 | 1.1942 | 1.1167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 416720 | 720 | 405383 | 766 | 233881.352 | 528.8 | 4.3262 | 4.509 | 4.6982 | 4.6347 | 4.5484 | 4.5962 | 0 | 0 | 4.7706 | 4.6793 | 4.6544 | 4.6846 | 732000 | 2000 | 741000 | 1000 | 1469001 | 4267 | 1470000 | 1464734 | 12.85 | 4.5521 | 1.0102 | 4.6972 | 1.0509 | 22.19% | 22.37% | 30.3879 | 40.4273 | 6.0537 | 9.6815 | 1476714.2 | 1468867 | 1612238.3087 | 91.11%
2023-08-27 | 2024 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 335090.89 | 6:21 | 19:10 | 9321.2 | 9654.6 | 9714.2 | 9675 | 9761 | 9779.5 | 9739.9 | 10047.9 | 9655.4 | 9501.7 | 9530.8 | 9654 | 9686.5 | 9584.5 | 9734.4 | 9784.7 | 9752.7 | 9853 | 9728.4 | 9745.9 | 9844.2 | 9783 | 9745.8 | 9784.2 | 9572.5 | 8467 | 9566.8 | 9581.2 | 9876.2 | 9864.1 | 9794.5 | 9840.2 | 9701.7 | 9710.1 | 9919.2 | 9890.1 | 9870.1 | 9826.8 | 9887.1 | 9773 | 10917.1 | 9862.7 | 10486.9 | 9547.7 | 10169.7 | 10981.9 | 9611.2 | 10616.1 | 8989.4 | 9191.7 | 9732.2 | 9167.5 | 10041.1 | 9133.7 | 9846 | 8980.6 | 8953.7 | 10025.1 | 8992.7 | 10007.3 | 9956.9 | 8999.1 | 9741.9 | 9308.1 | 9516.7 | 8980.8 | 9470.5 | 9727.4 | 10110.6 | 8858.2 | 9775.9 | 8739.6 | 9664 | 9398 | 8976 | 9755 | 8748 | 9905 | 8891 | 9742 | 9097.5 | 9657.8 | 9168.4 | 9970 | 9100.4 | 9623.8 | 9123 | 8119.4 | 9829.1 | 9559.1 | 8967.9 | 10068.3 | 9854.1 | 9241.4 | 9178.5 | 9912.6 | 8986 | 9325.1 | 9991.8 | 8907.1 | 10086.5 | 8924.9 | 9895.5 | 9154.2 | 10016.3 | 8740.5 | 10196.1 | 9187.5 | 10003.7 | 9233.3 | 10083 | 9343.7 | 9058.8 | 9828.2 | 9094.8 | 8933.8 | 9886.4 | 9965.9 | 9824 | 9188 | 9919.8 | 9036.7 | 9569.9 | 9203.9 | 9633.8 | 8551.7 | 9767.9 | 9113.5 | 9195.6 | 9180.2 | 8592.6 | 7795.2 | 9034.6 | 8016.1 | 9091.5 | 9076 | 10187.3 | 9145.3 | 10269.1 | 9286.4 | 10124.2 | 9108.7 | 9264.7 | 9177.4 | 10052.1 | 10314.1 | 10266.3 | 10235.2 | 10166.6 | 10183.2 | 9423.7 | 10228.9 | 10534 | 10576.5 | 10342.7 | 10321 | 10694.3 | 9598.5 | 10331.1 | 9483.7 | 0 | 30.99 | 0 | 30.76 | 30.65 | 31.24 | 0 | 41.2 | 0 | 0 | 41.6 | 41.8 | 6.18 | 6.24 | 6.04 | 6.29 | 6 | 6.26 | 10.06 | 9.24 | 9.58 | 9.6 | 8.94 | 9.95 | 4.74 | 5.11 | 5.38 | 5 | 4.9 | 5.12 | 0.8 | 1.12 | 1.02 | 1.12 | 1.16 | 1.09 | 4.94 | 4.6 | 5.47 | 5.39 | 4.85 | 5.04 | 0.88 | 1.09 | 1.11 | 1.14 | 1.21 | 1.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 417490 | 721 | 406144 | 768 | 235406.6 | 533.067 | 4.74 | 5.11 | 5.38 | 5 | 4.9 | 5.12 | 4.94 | 4.6 | 5.47 | 5.39 | 4.85 | 5.04 | 770000 | 1000 | 761000 | 2000 | 1525248 | 4267 | 1528000 | 1520981 | 12.8167 | 5.0417 | 1.0517 | 5.0483 | 1.0967 | 20.86% | 21.72% | 30.91 | 41.5333 | 6.1683 | 9.5617 | 1534142.5 | 1525133 | 1722484.4156 | 88.54%
2023-08-28 | 2024 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 335090.89 | 6:22 | 19:09 | 10360 | 10693.3 | 10693.6 | 10666.5 | 10730.9 | 10770.4 | 10715.7 | 10970.1 | 10695.4 | 10637.4 | 10618.9 | 10718.3 | 10700.2 | 10670.6 | 10629.5 | 10726.8 | 10579.6 | 10672.5 | 10648 | 10689.2 | 10656 | 10667.9 | 10538.4 | 10600.6 | 10531.9 | 9362 | 10565.1 | 10538.9 | 10713.7 | 10607.5 | 10557.7 | 10673.3 | 10671 | 10709.7 | 11009.1 | 10912.6 | 10747.7 | 10668.9 | 10681.6 | 10661 | 11692.5 | 10674.1 | 11534.7 | 10427.3 | 11100.1 | 12021 | 10329.2 | 11607.9 | 10084.9 | 10333 | 10799.1 | 10313.9 | 11013.2 | 10107.8 | 10942.3 | 10057 | 10022.1 | 11070 | 10098.3 | 11063.5 | 11001.1 | 10068.4 | 10824.5 | 10445 | 10760.8 | 10156.5 | 10752.9 | 11238.5 | 11426.6 | 10403.6 | 11362.1 | 10015.2 | 11021.2 | 10925.7 | 10150.1 | 11359.2 | 10038.6 | 11448 | 10163.5 | 11304.4 | 10465 | 11241.7 | 10573.4 | 11573.4 | 10458.3 | 11146 | 10359.6 | 9169.1 | 11085.6 | 10879.9 | 10062.7 | 11450.8 | 10925.5 | 10290.3 | 10176.7 | 10945.1 | 10045.9 | 10454.3 | 11054.5 | 10016.8 | 11096.7 | 9990.9 | 10921.1 | 10271.7 | 10924.2 | 9726.5 | 11085 | 10238.9 | 10934 | 10217.9 | 10944.6 | 10369.6 | 10101.6 | 10903.6 | 10197.3 | 10036 | 10950.5 | 11030.6 | 10896.6 | 10289.2 | 11222 | 10168.4 | 11033.7 | 10300 | 10952.1 | 9572.1 | 11126.5 | 10218.9 | 10362.3 | 10350.9 | 10184.9 | 8829.6 | 10074.3 | 8861.2 | 10187.3 | 10177.7 | 11717.8 | 10382.5 | 11760.9 | 10555.6 | 11189.3 | 10226.8 | 10414.4 | 10305.2 | 11070.2 | 11274.7 | 11258.6 | 11237.3 | 11234.8 | 11277.6 | 10566.8 | 11248.9 | 11558.1 | 11473.6 | 11266.4 | 11277.7 | 11573.9 | 10590.3 | 11279.3 | 10577.2 | 0 | 30.8642 | 0 | 30.5998 | 30.5385 | 31.1842 | 0 | 41.3 | 0 | 0 | 41.9 | 42.2 | 7.3593 | 7.4302 | 6.9651 | 7.7335 | 7.2268 | 7.5321 | 11.454 | 10.559 | 12.942 | 11.72 | 11.083 | 11.763 | 5.7524 | 6.0022 | 5.7361 | 5.5834 | 5.4085 | 5.6725 | 0.87145 | 1.2446 | 1.0601 | 1.2091 | 1.2757 | 1.2375 | 5.8279 | 5.833 | 5.8676 | 6.0342 | 5.3756 | 5.6341 | 0.95368 | 1.2168 | 1.1438 | 1.2422 | 1.3311 | 1.2889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 418343 | 722 | 406993 | 770 | 237101.085 | 537.267 | 5.7524 | 6.0022 | 5.7361 | 5.5834 | 5.4085 | 5.6725 | 5.8279 | 5.833 | 5.8676 | 6.0342 | 5.3756 | 5.6341 | 853000 | 1000 | 849000 | 2000 | 1694485 | 4200 | 1699000 | 1690285 | 12.7833 | 5.6925 | 1.1498 | 5.7621 | 1.1961 | 20.2% | 20.76% | 30.7967 | 41.8 | 7.3745 | 11.5868 | 1708260.2 | 1694467 | 1964835.2024 | 86.24%
2023-08-29 | 2024 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 335090.89 | 6:22 | 19:09 | 9672.7 | 9973.9 | 9881.7 | 9861.6 | 9948.2 | 9931.7 | 9939.1 | 10220.4 | 9952.9 | 10056.8 | 9768.2 | 9923 | 9847.1 | 9789.2 | 9776.8 | 9855.1 | 9688.1 | 9744.6 | 9737.6 | 9826.8 | 9822.7 | 9788.3 | 9642.4 | 9736.7 | 9559.2 | 8508.8 | 9506.6 | 9559.7 | 9797.9 | 9724.8 | 9641.1 | 9755.9 | 9685.2 | 9728.7 | 9797.2 | 9714.8 | 9793.2 | 9717.4 | 9784.8 | 9702.9 | 10554.5 | 9696.5 | 10417.4 | 9473.2 | 9995 | 10936.7 | 9347.8 | 10489 | 9161.2 | 9387.8 | 9947.5 | 9387.4 | 10188.4 | 9212.1 | 10135.2 | 9157.5 | 9091.9 | 10250.1 | 9171.4 | 10243.5 | 10157.7 | 9187.9 | 10018.8 | 9679.8 | 9567.4 | 9259.4 | 9801 | 10134.8 | 10364.7 | 9451.3 | 10294.4 | 9142.4 | 10029 | 9948.4 | 9345.4 | 10378.9 | 8835.9 | 10064.8 | 9403.7 | 10411.8 | 9068.9 | 9973.9 | 9539.1 | 10409.7 | 9426.6 | 10020.1 | 9410.1 | 8366.8 | 9984.3 | 9485 | 9109.9 | 10306.3 | 10054.6 | 9374.9 | 8999.2 | 9979.4 | 9104.9 | 9417.8 | 10162.5 | 9036.1 | 10154.8 | 9020.3 | 9975.3 | 9251.8 | 10078 | 8824.8 | 10158 | 9258.2 | 10055.6 | 9255 | 10167.4 | 9413 | 9063.3 | 9852.4 | 9211.5 | 9048.2 | 10051.6 | 10068.8 | 10014.2 | 9283.6 | 10078.5 | 9209.7 | 9869.6 | 9266.4 | 9808.9 | 8672.5 | 9961.4 | 9265.4 | 9277.7 | 9234.9 | 9243.9 | 7964.4 | 9026 | 7926.1 | 9025.1 | 9185.7 | 10398.8 | 9252.8 | 10469.2 | 9375.1 | 10369.1 | 9253.6 | 9451.7 | 9324.5 | 10437.1 | 10627.4 | 10602 | 10515.6 | 10414.5 | 10398.1 | 9605.6 | 10517.1 | 10736.7 | 10761.6 | 10846.5 | 10807.4 | 10767.1 | 9878.2 | 10817.8 | 9930.1 | 0 | 30.2704 | 0 | 30.1082 | 30.0098 | 30.4926 | 0 | 41.9 | 0 | 0 | 42.7341 | 43.1365 | 4.1841 | 4.5293 | 4.151 | 4.5472 | 4.362 | 4.4056 | 8.307 | 8.399 | 9.215 | 7.81 | 7.355 | 8.695 | 5.3045 | 5.4708 | 5.3119 | 5.2115 | 5.2173 | 5.4782 | 0.74231 | 1.1106 | 0.93042 | 1.0494 | 1.1232 | 1.112 | 5.5307 | 5.5061 | 5.3947 | 5.5506 | 5.3306 | 5.5284 | 0.80995 | 1.0857 | 1.0093 | 1.083 | 1.1786 | 1.1589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 419122 | 724 | 407766 | 771 | 238647.552 | 541.667 | 5.3045 | 5.4708 | 5.3119 | 5.2115 | 5.2173 | 5.4782 | 5.5307 | 5.5061 | 5.3947 | 5.5506 | 5.3306 | 5.5284 | 779000 | 2000 | 773000 | 1000 | 1546467 | 4400 | 1549000 | 1542067 | 12.7833 | 5.3323 | 1.0113 | 5.4735 | 1.0542 | 18.97% | 19.26% | 30.2203 | 42.5902 | 4.3632 | 8.2968 | 1558095.1 | 1546333 | 1839032.0907 | 84.08%
2023-08-30 | 2024 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 335090.89 | 6:20 | 19:07 | 11980.3 | 12416 | 12345.6 | 12288.7 | 12436.5 | 12456.9 | 12381 | 12738.8 | 12421.9 | 12300.2 | 12226 | 12394.8 | 12406.6 | 12312.3 | 12303.1 | 12418.1 | 12130.6 | 12108.9 | 12195.6 | 12378.6 | 12110.4 | 12138 | 11947.3 | 12001 | 11946.6 | 10778.9 | 12137 | 11960.8 | 12133.2 | 12085.9 | 11989.1 | 12144.7 | 12152.6 | 12200.4 | 12317.1 | 12179 | 12256.2 | 12120.2 | 12127.1 | 12023.7 | 13022.5 | 12142.6 | 12905.8 | 11906.7 | 12478.4 | 13387.1 | 11637.2 | 12875.3 | 11601.1 | 11892.1 | 12502.9 | 11867.6 | 12808 | 11689.3 | 12696.2 | 11587.4 | 11579.8 | 12837.1 | 11639.8 | 12820.8 | 12657.6 | 11586.4 | 12462.4 | 11970.2 | 12323.2 | 11729.8 | 12330.8 | 12697.3 | 12928.4 | 11913.8 | 12837 | 11466.7 | 12544.9 | 12365.6 | 11687 | 12741.7 | 11439.3 | 12869.4 | 11557 | 12644.9 | 11943.9 | 12692.2 | 12091.7 | 13009.4 | 11908.5 | 12538.6 | 11788 | 10489 | 12484.9 | 12151.6 | 11419 | 12787.3 | 12464.4 | 11670.9 | 11539.7 | 12445.8 | 11354.4 | 11721 | 12510.6 | 11236 | 12527.6 | 11210.5 | 12330.9 | 11466.6 | 12323.2 | 10903.4 | 12399.7 | 11325.2 | 12313 | 11382.6 | 12383.7 | 11524.5 | 11332.7 | 12242.4 | 11386.6 | 11202.1 | 12230.4 | 12263.1 | 12154 | 11363.8 | 12191.9 | 11173 | 11949.4 | 11283.7 | 11852 | 10485.7 | 11997.5 | 11209.3 | 11406.5 | 11419.3 | 11168.9 | 9743.1 | 11216.4 | 9935.9 | 11430.9 | 11491.3 | 12998.5 | 11762.8 | 13005.7 | 11907.1 | 12923.6 | 11755.8 | 11928.5 | 11721.6 | 12869.9 | 13100.5 | 13055.6 | 12982.4 | 12888.7 | 12920.7 | 11956.7 | 12978.8 | 13090.6 | 13124.8 | 13265 | 13241.8 | 13255.1 | 12241.2 | 13235.9 | 12227.1 | 0 | 31.1321 | 0 | 31.0895 | 30.8648 | 31.5392 | 0 | 46.1 | 0 | 0 | 46.5 | 47 | 4.0657 | 4.3542 | 4.0976 | 4.3265 | 4.1361 | 4.2557 | 7.603 | 7.303 | 7.87 | 7.706 | 7.46 | 7.564 | 6.7948 | 6.8473 | 6.7001 | 6.6804 | 6.5301 | 6.9319 | 1.0655 | 1.3073 | 1.3063 | 1.4689 | 1.3063 | 1.3908 | 6.992 | 6.908 | 6.9834 | 7.2427 | 6.6362 | 7.019 | 1.1519 | 1.2765 | 1.3837 | 1.5137 | 1.3725 | 1.4348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420096 | 725 | 408723 | 773 | 240572.2 | 546.133 | 6.7948 | 6.8473 | 6.7001 | 6.6804 | 6.5301 | 6.9319 | 6.992 | 6.908 | 6.9834 | 7.2427 | 6.6362 | 7.019 | 974000 | 1000 | 957000 | 2000 | 1924648 | 4466 | 1928000 | 1920182 | 12.7833 | 6.7474 | 1.3075 | 6.9635 | 1.3555 | 19.38% | 19.47% | 31.1564 | 46.5333 | 4.206 | 7.5843 | 1938926.9 | 1924533 | 2319484.088 | 82.97%
2023-08-31 | 2024 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 335090.89 | 6:20 | 19:07 | 11999.5 | 12439.5 | 12313.1 | 12366.4 | 12324.7 | 12350 | 12320.7 | 12620.1 | 12449.1 | 12284.8 | 12215.2 | 12412 | 12341.9 | 12243.4 | 12398.4 | 12482 | 12319.1 | 12383.6 | 12405.4 | 12471.7 | 12474.2 | 12441.5 | 12317.4 | 12413.1 | 12272.8 | 10928.6 | 12251.4 | 12262.1 | 12533.1 | 12434.2 | 12381.6 | 12499.1 | 12471.4 | 12489.6 | 12711.6 | 12621.1 | 12566.6 | 12477.6 | 12539.4 | 12445.3 | 13323 | 12306.1 | 13098.6 | 12062.7 | 12625.3 | 13617.6 | 11846.4 | 13164.7 | 11551.3 | 11824.2 | 12464.7 | 11854.3 | 12787.1 | 11697.1 | 12680.1 | 11601.1 | 11463.8 | 12754.1 | 11543 | 12725.1 | 12532.9 | 11580.7 | 12379.7 | 11924.3 | 12220 | 11613.7 | 12192.3 | 12580.7 | 12781.4 | 11790 | 12688.5 | 11392.5 | 12415.7 | 12312.8 | 11606 | 12751.4 | 11505.3 | 12806.6 | 11599 | 12702.1 | 11847.2 | 12594.5 | 11922 | 12909.8 | 11802.1 | 12428.2 | 11740.7 | 10464.4 | 12549.4 | 12208.6 | 11584.6 | 12956.4 | 12698.6 | 11955.5 | 11824 | 12743.1 | 11686.5 | 12066.9 | 12923.8 | 11640.4 | 12983.2 | 11688.6 | 12764.7 | 11946.6 | 12833.1 | 11330.9 | 12924.4 | 11890 | 12792.2 | 11888.8 | 12884.7 | 12087.8 | 11635.6 | 12668.4 | 11887.2 | 11684.7 | 12776 | 12888.6 | 12723.8 | 11914 | 12801.3 | 11779.9 | 12590.3 | 11907.7 | 12445 | 11051.9 | 12672.6 | 11844.1 | 11942.9 | 11870.4 | 11800.9 | 10209.5 | 11624 | 10233.9 | 11718.3 | 11714.7 | 13081.3 | 11853.3 | 13085.7 | 12002.3 | 13053 | 11881.8 | 12075.2 | 11855 | 12712.8 | 12934.8 | 12961.4 | 12891.3 | 12911.2 | 12966.1 | 11993.3 | 12903.5 | 12935.7 | 12963.2 | 13091.3 | 13044.1 | 13001.9 | 12009.1 | 13062 | 12051.4 | 0 | 31.8303 | 0 | 31.7599 | 31.6012 | 32.1505 | 0 | 46.9 | 0 | 0 | 47.5 | 47.1 | 4.056 | 4.3704 | 4.0629 | 4.3431 | 4.252 | 4.1999 | 8.075 | 7.684 | 7.751 | 8.276 | 7.693 | 8.37 | 6.7567 | 7.0309 | 6.7948 | 6.5929 | 6.8313 | 6.8374 | 1.0697 | 1.3516 | 1.328 | 1.4613 | 1.434 | 1.3498 | 6.9776 | 7.1189 | 7.1431 | 7.1518 | 6.9739 | 6.9363 | 1.1526 | 1.3202 | 1.404 | 1.5079 | 1.4892 | 1.3967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 421078 | 727 | 409699 | 774 | 242522.286 | 550.6 | 6.7567 | 7.0309 | 6.7948 | 6.5929 | 6.8313 | 6.8374 | 6.9776 | 7.1189 | 7.1431 | 7.1518 | 6.9739 | 6.9363 | 982000 | 2000 | 976000 | 1000 | 1950086 | 4467 | 1955000 | 1945619 | 12.7833 | 6.8073 | 1.3324 | 7.0503 | 1.3784 | 19.57% | 19.55% | 31.8355 | 47.1667 | 4.214 | 7.9748 | 1965306.3 | 1950067 | 2348953.3983 | 83.02%
2023-09-01 | 2024 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 335090.89 | 6:20 | 19:06 | 12197.9 | 12583.2 | 12490.2 | 12473.3 | 12593.9 | 12605.4 | 12523.1 | 12893.8 | 12531.1 | 11480.5 | 12396.1 | 12558.1 | 12543 | 12462.5 | 12477.3 | 12564.9 | 12404.5 | 12488 | 12464.4 | 12544.7 | 12499.7 | 12501.7 | 12343.4 | 12426.1 | 12269.9 | 10974.3 | 12340.6 | 12293.9 | 12536.6 | 12430.7 | 12340.7 | 12486.2 | 12659.8 | 12707.7 | 12743.3 | 12666 | 12560.8 | 12462.6 | 12501.5 | 12422.5 | 13355.6 | 12418.5 | 13137.8 | 12204.1 | 12676.7 | 13670.6 | 11942.4 | 13251.2 | 11765.4 | 12030.5 | 12667.7 | 12026.5 | 12945.5 | 11846.4 | 12837.3 | 11754.9 | 11686.7 | 12968.2 | 11788.2 | 12951.2 | 12854.3 | 11770.8 | 12678.7 | 12252.3 | 12428.6 | 11879.3 | 12448.4 | 12869.7 | 13024.7 | 12097.8 | 12974.5 | 11661.1 | 12660 | 12564.5 | 11883.5 | 12978.6 | 11728.6 | 13083 | 11852.5 | 12937.2 | 12157 | 12878.4 | 12206.1 | 13204.4 | 12108.6 | 12725.5 | 12011.2 | 10704.2 | 12677 | 12421.1 | 11691.8 | 13030.6 | 12733 | 11953.3 | 11831 | 12758.6 | 11671.6 | 12081 | 12868.3 | 11621.5 | 12935.6 | 11643.7 | 12753.8 | 11914.4 | 12834.3 | 11341 | 12911.9 | 11908.4 | 12813.1 | 11906.5 | 12890.8 | 12125.8 | 11632.7 | 12603.7 | 11817.3 | 11634.2 | 12538.6 | 12554.2 | 12677.1 | 11857.1 | 12738.8 | 11754.1 | 12566 | 11924.3 | 12491.8 | 11089.4 | 12626.5 | 11840 | 11900.1 | 11852.3 | 11796 | 10180.1 | 11573.5 | 10154 | 11832.2 | 11863.2 | 13337.8 | 12098.8 | 13347.3 | 12248 | 13226.2 | 12061.5 | 12225 | 12044.7 | 13088.2 | 13352 | 13363 | 13312.9 | 13288.2 | 13304 | 12345.6 | 13298.3 | 13307.6 | 13321.6 | 13392.7 | 13366.1 | 13353.6 | 12395.4 | 13429.2 | 12436.5 | 0 | 32.2306 | 0 | 32.119 | 31.9922 | 32.5478 | 0 | 46.1 | 0 | 0 | 46.7 | 47.2 | 4.6214 | 4.7958 | 4.651 | 4.6649 | 4.7164 | 4.7859 | 8.975 | 8.695 | 8.604 | 8.917 | 8.889 | 9.69 | 6.8429 | 7.0229 | 6.7955 | 6.6706 | 6.7987 | 7.0538 | 1.076 | 1.3563 | 1.3291 | 1.4732 | 1.4291 | 1.3668 | 7.0809 | 7.1132 | 7.1623 | 7.2457 | 6.9315 | 7.1699 | 1.16 | 1.3257 | 1.4019 | 1.5254 | 1.4813 | 1.418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 422070 | 728 | 410684 | 776 | 244492.286 | 555 | 6.8429 | 7.0229 | 6.7955 | 6.6706 | 6.7987 | 7.0538 | 7.0809 | 7.1132 | 7.1623 | 7.2457 | 6.9315 | 7.1699 | 992000 | 1000 | 985000 | 2000 | 1970000 | 4400 | 1974000 | 1965600 | 12.7667 | 6.8641 | 1.3384 | 7.1172 | 1.3854 | 19.5% | 19.47% | 32.2224 | 46.6667 | 4.7059 | 8.9617 | 1985752.3 | 1969867 | 2379589.5843 | 82.78%
2023-09-02 | 2024 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 335090.89 | 6:20 | 19:04 | 12345.3 | 12803.6 | 12683.5 | 12686.9 | 12807.3 | 12852.4 | 12779.6 | 13119.9 | 12814.9 | 12680.3 | 12684.3 | 12799.5 | 12876.3 | 12704 | 12801.3 | 12875.2 | 12747.6 | 12747.2 | 12818.2 | 12874.4 | 12868.9 | 12838.1 | 12727.2 | 12771.4 | 12541.6 | 11469.3 | 12651.4 | 12638.8 | 12808 | 12751.8 | 12681.7 | 12812.3 | 13250.4 | 13313 | 13292.5 | 13202.4 | 12819.4 | 12690.9 | 12792.6 | 12705.2 | 13435.8 | 12616.8 | 13283.7 | 12418.8 | 12925.8 | 13749.4 | 12210 | 13348.1 | 12059.5 | 12327.1 | 12903.4 | 12371.6 | 13125.1 | 12209.9 | 13121.4 | 12186.5 | 11967.3 | 13020.4 | 12079.3 | 13014.1 | 12865 | 11998.4 | 12606.5 | 12245.2 | 12740.8 | 12225.3 | 12685.7 | 12985.5 | 13188.5 | 12351 | 13096.8 | 11964.2 | 12785.3 | 12710 | 12105.8 | 13020.9 | 12012.7 | 13189 | 12078.1 | 12996.1 | 12321.7 | 12952.1 | 12430.7 | 13267.4 | 12303.8 | 12855.5 | 12302.4 | 11059.9 | 12834 | 12614.5 | 12113.4 | 13287.1 | 13014.8 | 12366.3 | 12249.6 | 13094 | 12149.8 | 12459.9 | 13149.6 | 12086.9 | 13155.5 | 12118 | 13057.3 | 12353.5 | 13016.6 | 11796.1 | 13140.2 | 12299.8 | 13002.8 | 12211.6 | 13204.9 | 12511.3 | 12050.5 | 12905.4 | 12265.4 | 12115.7 | 12982.9 | 13074.5 | 13005.9 | 12317.4 | 12969.4 | 12172 | 12876.3 | 12307.5 | 12772.6 | 11538.7 | 12989.1 | 12296.1 | 12359.2 | 12335 | 12247.4 | 10636.2 | 12071.7 | 10595.8 | 12188.3 | 12171.9 | 13445 | 12336.2 | 13456.4 | 12443.7 | 13357.9 | 12319.6 | 12476.9 | 12332.7 | 13139 | 13333.3 | 13370 | 13322.5 | 13269.7 | 13304.8 | 12542.4 | 13355.5 | 13262.1 | 13290.2 | 13496.7 | 13374.6 | 13302.5 | 12476.4 | 13528.1 | 12633.9 | 0 | 32.7315 | 0 | 32.6587 | 32.4741 | 33.1163 | 0 | 45.6 | 0 | 0 | 46.1 | 46.2 | 6.1412 | 6.2485 | 6.1123 | 6.0477 | 6.0878 | 6.2536 | 10.086 | 10.224 | 10.278 | 9.621 | 10.007 | 10.39 | 7.1157 | 7.3458 | 6.9839 | 6.8999 | 7.131 | 7.2558 | 1.1319 | 1.4233 | 1.3823 | 1.5384 | 1.5149 | 1.4859 | 7.3645 | 7.4306 | 7.3624 | 7.5246 | 7.272 | 7.3766 | 1.2191 | 1.3938 | 1.4527 | 1.5974 | 1.5658 | 1.5245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 423082 | 730 | 411689 | 778 | 246501.353 | 559.267 | 7.1157 | 7.3458 | 6.9839 | 6.8999 | 7.131 | 7.2558 | 7.3645 | 7.4306 | 7.3624 | 7.5246 | 7.272 | 7.3766 | 1012000 | 2000 | 1005000 | 2000 | 2009067 | 4267 | 2013000 | 2004800 | 12.7333 | 7.122 | 1.4128 | 7.3885 | 1.4589 | 19.84% | 19.75% | 32.7452 | 45.9667 | 6.1485 | 10.101 | 2028549.4 | 2008867 | 2476576.6911 | 81.11%
2023-09-03 | 2024 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 335090.89 | 6:20 | 19:04 | 12347.3 | 12811.7 | 12676 | 12678.9 | 12783 | 12837.3 | 12798.3 | 13107.5 | 12802.7 | 12664.5 | 12674.4 | 12799.2 | 12862.8 | 12704.7 | 12815.3 | 12869.4 | 12754.2 | 12747 | 12808.8 | 12864.2 | 12867.2 | 12829.6 | 12718.1 | 12763.6 | 12540.8 | 11484.5 | 12640.8 | 12632.8 | 12807.2 | 12751.2 | 12676 | 12819.2 | 13298.7 | 13345.5 | 13297.7 | 13229.8 | 12818.8 | 12695.8 | 12768.2 | 12695 | 13508.7 | 12645.3 | 13325 | 12443.3 | 12958.7 | 13824.7 | 12282.6 | 13421.8 | 12053.1 | 12310.3 | 12890.1 | 12371 | 13131.3 | 12219.3 | 13115.1 | 12166 | 11949.1 | 13028.9 | 12063 | 13024.1 | 12861.9 | 11985.9 | 12602.6 | 12217.1 | 12745.9 | 12225.3 | 12673.7 | 12988.3 | 13201.1 | 12346.5 | 13102.3 | 11953.7 | 12833.7 | 12720.8 | 12147.8 | 13057.5 | 12002.1 | 13193.4 | 12082.3 | 13014.6 | 12337.6 | 12965.7 | 12454.1 | 13293.1 | 12322.8 | 12866.6 | 12302.8 | 11080.9 | 12827.6 | 12608.5 | 12106.6 | 13283 | 13006.1 | 12339.5 | 12222.8 | 13094.2 | 12174.1 | 12464 | 13179.4 | 12097.7 | 13179.1 | 12128.2 | 13057.5 | 12360.7 | 13047.7 | 11819.8 | 13154.9 | 12305.9 | 13031 | 12274 | 13219.5 | 12512.1 | 12087.1 | 12915.8 | 12286.8 | 12121.2 | 12994.7 | 13103.5 | 13020.1 | 12317.4 | 12991.2 | 12170.9 | 12884.5 | 12327.4 | 12772.9 | 11546 | 12983.7 | 12301.8 | 12341.3 | 12307.9 | 12233.8 | 10619.9 | 12122.4 | 10710.7 | 12084.6 | 12147.3 | 13481.6 | 12357.5 | 13497.1 | 12463.7 | 13404.1 | 12346.9 | 12501.5 | 12324.1 | 13162.3 | 13375.7 | 13387.4 | 13341.5 | 13300.2 | 13340.1 | 12549.5 | 13381.8 | 13288.7 | 13323.1 | 13543.6 | 13424 | 13347.4 | 12497 | 13544.5 | 12635 | 0 | 32.2622 | 0 | 32.1036 | 31.9563 | 32.6216 | 0 | 45.2 | 0 | 0 | 46 | 45.8 | 6.433 | 6.603 | 6.3323 | 6.4966 | 6.2623 | 6.5902 | 10.804 | 10.478 | 10.581 | 10.279 | 9.403 | 11.519 | 6.6754 | 9.6205 | 6.9776 | 6.9186 | 6.9758 | 7.0921 | 1.1391 | 1.421 | 1.3825 | 1.5337 | 1.5064 | 1.4891 | 7.1728 | 7.1451 | 7.3796 | 7.532 | 7.0163 | 7.2157 | 1.2257 | 1.3926 | 1.4452 | 1.596 | 1.5547 | 1.5245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 424094 | 731 | 412696 | 779 | 248511.953 | 563.533 | 6.6754 | 9.6205 | 6.9776 | 6.9186 | 6.9758 | 7.0921 | 7.1728 | 7.1451 | 7.3796 | 7.532 | 7.0163 | 7.2157 | 1012000 | 1000 | 1007000 | 1000 | 2010600 | 4266 | 2017000 | 2006334 | 12.7333 | 7.3767 | 1.412 | 7.2436 | 1.4565 | 19.14% | 20.11% | 32.2359 | 45.6667 | 6.4529 | 10.5107 | 2030104.3 | 2010467 | 2438136 | 82.46%
2023-09-04 | 2024 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 335090.89 | 6:28 | 18:51 | 12313.8 | 12755.9 | 12662.4 | 12645.7 | 12728 | 12788 | 12740.5 | 13057.9 | 12702.4 | 12580.7 | 12588 | 12729.8 | 12743.9 | 12661.6 | 12741.1 | 12805.7 | 12650.1 | 12732.3 | 12703 | 12788.7 | 12751.7 | 12755.1 | 12604 | 12689.7 | 12538.9 | 11279.1 | 12595.7 | 12571.7 | 12802.7 | 12683.6 | 12605.8 | 12756.8 | 13088.8 | 13087.1 | 13092.9 | 13032.6 | 12835.6 | 12730.3 | 12760.6 | 12674.5 | 13436.1 | 12556.4 | 13227.2 | 12339.9 | 12820.1 | 13785.9 | 12191.3 | 13409.6 | 12043.2 | 12298.6 | 12884.2 | 12302.3 | 13162.1 | 12125.9 | 13037 | 12024 | 11954.4 | 13178.5 | 12073.2 | 13192.3 | 13078.4 | 12018.1 | 12818.2 | 12342.9 | 12601.6 | 12063.7 | 12582.5 | 12958.9 | 13115.5 | 12215.8 | 13034.9 | 11824.6 | 12751 | 12655.5 | 12015.5 | 13029.5 | 11878.3 | 13146 | 12006.1 | 12995.8 | 12272.8 | 12935.9 | 12340.8 | 13273.8 | 12242.4 | 12831.6 | 12155.8 | 10892.1 | 12838.5 | 12600.4 | 11969.2 | 13233 | 12973.2 | 12238.8 | 12105.1 | 13020.8 | 12025.8 | 12415.2 | 13169.5 | 11989.3 | 13202.1 | 11989.1 | 13011.6 | 12252.1 | 13035.5 | 11662.4 | 13115 | 12184.7 | 13025.5 | 12168.5 | 13087.8 | 12381.2 | 12015.6 | 12914.3 | 12174.9 | 11990.8 | 12995.9 | 13117.9 | 12958.2 | 12192.5 | 13022.2 | 12064 | 12819.7 | 12216.4 | 12723.8 | 11335.2 | 12887.3 | 12141.5 | 12199.1 | 12142.6 | 12076.1 | 10455.7 | 11951.8 | 10561.9 | 11956.8 | 11979.2 | 13359.7 | 12195.7 | 13377.4 | 12354.2 | 13283.2 | 12165.7 | 12329.6 | 12179 | 13119.3 | 13371.6 | 13363.6 | 13318.6 | 13314.8 | 13341.5 | 12428.5 | 13310.5 | 13345.4 | 13353.2 | 13410.7 | 13381.2 | 13385 | 12484.3 | 13411.7 | 12500.3 | 0 | 31.49 | 0 | 31.35 | 31.24 | 31.88 | 0 | 46.2 | 0 | 0 | 46.8 | 46.8 | 4.6 | 4.81 | 4.42 | 4.82 | 4.53 | 4.67 | 9.16 | 8.89 | 8.33 | 8.3 | 8.37 | 8.94 | 6.61 | 9.22 | 6.83 | 6.77 | 6.81 | 6.93 | 1.12 | 1.4 | 1.37 | 1.51 | 1.43 | 1.44 | 7.05 | 7.12 | 7.25 | 7.4 | 7.15 | 7.11 | 1.21 | 1.37 | 1.43 | 1.57 | 1.49 | 1.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 425103 | 732 | 413697 | 781 | 250514.02 | 567.933 | 6.61 | 9.22 | 6.83 | 6.77 | 6.81 | 6.93 | 7.05 | 7.12 | 7.25 | 7.4 | 7.15 | 7.11 | 1009000 | 1000 | 1001000 | 2000 | 2002067 | 4400 | 2007000 | 1997667 | 12.3833 | 7.195 | 1.3783 | 7.18 | 1.425 | 19.16% | 19.85% | 31.49 | 46.6 | 4.6417 | 8.665 | 2018849.3 | 1994867 | 2410852 | 82.75%
2023-09-05 | 2024 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 335090.89 | 6:29 | 18:48 | 12128 | 12586.3 | 12490.1 | 12471.5 | 12548.3 | 12614.7 | 12556.6 | 12904.2 | 12544.4 | 12426.7 | 12413.2 | 12568.9 | 12570 | 12493.7 | 12547.1 | 12632 | 12472.6 | 12559.5 | 12526.8 | 12603.4 | 12578.3 | 12570.3 | 12414.7 | 12506.2 | 12312.7 | 10934.2 | 12413.7 | 12335.2 | 12642 | 12521 | 12389.7 | 12472.6 | 12789.9 | 12865.3 | 12862.2 | 12789.5 | 12674.2 | 12559 | 12592.7 | 12505.3 | 13304.2 | 12341.4 | 13100 | 12120.6 | 12614.5 | 13652.2 | 12000.5 | 13277.1 | 11776.6 | 12065.6 | 12711.5 | 12076.9 | 13003.3 | 11868.5 | 12878.4 | 11740.7 | 11656.6 | 13025.9 | 11781.5 | 13040.7 | 12901 | 11754.8 | 12645.5 | 12140.1 | 12410 | 11813.7 | 12390.9 | 12806.9 | 12974.6 | 12006.3 | 12886.9 | 11543.2 | 12582.9 | 12475.8 | 11774.7 | 12900 | 11615.8 | 13012.5 | 11745.6 | 12852.3 | 12070.2 | 12789.8 | 12169.2 | 13149.7 | 12043.9 | 12687.2 | 11968.3 | 10635 | 12717.2 | 12418.5 | 11713.1 | 13117.2 | 12836.2 | 12046.9 | 11911.3 | 12866.1 | 11751.7 | 12217.9 | 13044.4 | 11757 | 13058.6 | 11747.5 | 12845.7 | 12020.3 | 12895.6 | 11389.7 | 12977.1 | 11976.1 | 12847.5 | 11922.9 | 12921.8 | 12156 | 11766.5 | 12767.6 | 11959.7 | 11725.1 | 12587 | 12549.3 | 12807.7 | 11964.1 | 12872.6 | 11815.3 | 12656.8 | 11995.2 | 12544.6 | 11051.3 | 12714.6 | 11886 | 11979.8 | 11947 | 11838.3 | 10216.4 | 11679.7 | 10294.6 | 11741.6 | 11754.5 | 13253.2 | 11994.8 | 13295.6 | 12187.2 | 13172.5 | 11958.7 | 12132.3 | 11983.1 | 12998.9 | 13286.5 | 13244.9 | 13205.6 | 13203.3 | 13232.4 | 12271.8 | 13216.7 | 13255.7 | 13265.1 | 13315.9 | 13283.1 | 13300.5 | 12324.6 | 13302.6 | 12334.4 | 0 | 32.6109 | 0 | 32.5335 | 32.4824 | 32.9858 | 0 | 48.8 | 0 | 0 | 49.3 | 49.3 | 2.949 | 3.054 | 2.9856 | 3.1176 | 3.0758 | 3.0178 | 6.447 | 6.428 | 6.39 | 6.732 | 6.29 | 6.394 | 6.4821 | 6.8967 | 6.7353 | 6.6996 | 6.5069 | 6.8963 | 1.1017 | 1.3778 | 1.4062 | 1.4871 | 1.3807 | 1.3666 | 6.9461 | 7.0362 | 7.1839 | 7.2459 | 6.8693 | 7.0227 | 1.1785 | 1.3393 | 1.4385 | 1.5459 | 1.4516 | 1.4184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 426097 | 734 | 414683 | 782 | 252486.886 | 572.4 | 6.4821 | 6.8967 | 6.7353 | 6.6996 | 6.5069 | 6.8963 | 6.9461 | 7.0362 | 7.1839 | 7.2459 | 6.8693 | 7.0227 | 994000 | 2000 | 986000 | 1000 | 1972866 | 4467 | 1977000 | 1968399 | 12.3167 | 6.7028 | 1.3534 | 7.0507 | 1.3954 | 20.19% | 19.79% | 32.6532 | 49.1333 | 3.0333 | 6.4468 | 1988461.2 | 1965067 | 2340021 | 83.98%
2023-09-06 | 2024 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 335090.89 | 6:22 | 18:59 | 11617.3 | 12124.8 | 12121.7 | 12049.8 | 12233.7 | 12262.7 | 12167.1 | 12506.4 | 12074.1 | 11945.3 | 12025.8 | 12130.1 | 12170.9 | 12111.8 | 12161.8 | 12230.8 | 12097 | 12191.5 | 12110.2 | 12157.9 | 12197 | 12175.9 | 12098.2 | 12136.4 | 11993.5 | 10627.7 | 11980.9 | 11875.2 | 12178.1 | 12268.6 | 12198.1 | 12271.4 | 12438.1 | 12493.2 | 12447.4 | 12405.1 | 12380.2 | 12315.4 | 12370.3 | 12240.4 | 13009.1 | 12078.1 | 12867.3 | 11910 | 12387 | 13311.1 | 11712.8 | 12949.4 | 11384.4 | 11658.1 | 12310.6 | 11678.2 | 12524.2 | 11423.6 | 12483.4 | 11331.7 | 11276.9 | 12599.1 | 11382.5 | 12584.9 | 12437.5 | 11328.2 | 12065.3 | 11662.8 | 12012.8 | 11458.6 | 11998.9 | 12434.1 | 12524.8 | 11607.9 | 12447.6 | 11132.8 | 11064.9 | 10982.2 | 10352.1 | 11338 | 10207 | 11450.4 | 10350.6 | 11318.4 | 11656 | 12383.9 | 11776.7 | 12707.8 | 11647.2 | 12280.9 | 11605.3 | 10293.4 | 12420.8 | 12081.2 | 11411.8 | 12784.6 | 12503.3 | 11736.8 | 11609.1 | 12569.4 | 11543.7 | 12009.4 | 12818.8 | 11562.4 | 12799.4 | 11540.1 | 12605.5 | 11779.3 | 12639.7 | 11146.1 | 12718.5 | 11730.9 | 12588.3 | 11679.7 | 12619.4 | 11875.7 | 11583.7 | 12563.2 | 11735.4 | 11500.8 | 12577.4 | 12697.7 | 12517.3 | 11706.2 | 12597.6 | 11564 | 12403.4 | 11743.4 | 12274.3 | 10805.9 | 12460.1 | 11634.4 | 11754.2 | 11755.1 | 11587.4 | 10009.9 | 11544.6 | 10167.2 | 11543.8 | 11539.7 | 12780.5 | 11569.6 | 12819.6 | 11758.7 | 12767.4 | 11594.6 | 11801.4 | 11700.3 | 12547 | 12790.7 | 12770.5 | 12736.3 | 12773.2 | 12783.3 | 11846.2 | 12758.4 | 12661.9 | 12673.8 | 12757.6 | 12703.8 | 12713.2 | 11832.8 | 12824.9 | 11766.2 | 0 | 34.2984 | 0 | 34.4644 | 34.4461 | 34.51 | 0 | 47.2 | 0 | 0 | 47.6 | 47.365 | 3.3123 | 3.358 | 3.2982 | 3.373 | 3.371 | 3.2565 | 5.514 | 6.033 | 5.816 | 6.129 | 6.279 | 6.187 | 6.21 | 6.6797 | 6.5393 | 6.4168 | 6.3542 | 6.5742 | 1.0763 | 1.3035 | 1.3774 | 1.4468 | 1.3241 | 1.289 | 6.66 | 6.7703 | 6.9805 | 6.9621 | 6.6717 | 6.7057 | 1.1482 | 1.2664 | 1.417 | 1.5017 | 1.3888 | 1.3393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 427052 | 735 | 415645 | 784 | 254396.753 | 576.733 | 6.21 | 6.6797 | 6.5393 | 6.4168 | 6.3542 | 6.5742 | 6.66 | 6.7703 | 6.9805 | 6.9621 | 6.6717 | 6.7057 | 955000 | 1000 | 962000 | 2000 | 1909867 | 4333 | 1914000 | 1905534 | 12.6167 | 6.4624 | 1.3028 | 6.7917 | 1.3436 | 20.16% | 19.78% | 34.4297 | 47.3883 | 3.3282 | 5.993 | 1923742.8 | 1909667 | 2246796.6145 | 85%
2023-09-07 | 2024 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 335090.89 | 6:23 | 18:57 | 11061.5 | 11689.1 | 11594.8 | 11554.1 | 11706.2 | 11729.9 | 11650.5 | 11984.7 | 11604.1 | 11248.1 | 11478.3 | 11655.9 | 11649.1 | 11561.3 | 11710.9 | 11754.5 | 11718.1 | 11791.8 | 11735.3 | 11767.5 | 11783 | 11778.7 | 11563.4 | 11675.2 | 11530 | 10176.5 | 11557 | 11511.2 | 11789.4 | 11724.7 | 11617.2 | 11716.3 | 11591.3 | 11683.9 | 11767.2 | 11676.3 | 11770.7 | 11674 | 11753 | 11562.7 | 12652.8 | 11627.1 | 12503.1 | 11368.1 | 12038.1 | 13031 | 11396.4 | 12672.5 | 10828.9 | 11083.2 | 11777.1 | 11105.7 | 12084.7 | 10940.6 | 11925.2 | 10782.8 | 10557.9 | 11932.5 | 10792.4 | 11961 | 11656.2 | 10767.7 | 11486.5 | 10937.9 | 11234 | 10605.7 | 11247.9 | 11646.1 | 11894.4 | 10841.2 | 11746.1 | 10394 | 11485.8 | 11285.4 | 10652.2 | 11727.3 | 10444.8 | 11883.7 | 10545.2 | 11668.5 | 10875.9 | 11655.1 | 10970.4 | 11982 | 10823.8 | 11465.3 | 10747.1 | 9523 | 11542 | 11209.3 | 10482 | 11932.6 | 11735.9 | 10889 | 10745.4 | 11679.1 | 10501.1 | 10964.9 | 11803.3 | 10501.7 | 11879.1 | 10512.4 | 11658.8 | 10755.7 | 11796.1 | 10206.8 | 11901.9 | 10735.8 | 11824.1 | 10809.1 | 11860.4 | 10932.2 | 10556.6 | 11580.5 | 10704.5 | 10478.2 | 11662.5 | 11759.2 | 11590.3 | 10718.3 | 11638.2 | 10535 | 11436.3 | 10717.8 | 11273.8 | 9809.5 | 11423.9 | 10558 | 10747.3 | 10729.2 | 10545.2 | 9149.8 | 10497.5 | 9264.9 | 10641.1 | 10679.3 | 12233.3 | 10950.9 | 12311.5 | 11172.6 | 12205.6 | 10968.8 | 11128.9 | 10931.7 | 12047.3 | 12338.6 | 12220.3 | 12186.6 | 12202.5 | 12222.9 | 11309.1 | 12266.4 | 12208.7 | 12256.6 | 12502.7 | 12428.5 | 12328.6 | 11328.5 | 12264.8 | 11265.8 | 0 | 35.85 | 0 | 35.75 | 35.81 | 35.99 | 0 | 49.6 | 0 | 0 | 49 | 49.57 | 2.68 | 2.63 | 2.67 | 2.65 | 2.66 | 2.74 | 6.63 | 6.19 | 6.25 | 6.31 | 6.45 | 6.12 | 6.01 | 6.91 | 6.39 | 6.08 | 5.9 | 6.29 | 1.04 | 1.26 | 1.36 | 1.37 | 1.27 | 1.23 | 6.45 | 6.54 | 6.82 | 6.58 | 6.17 | 6.41 | 1.11 | 1.22 | 1.39 | 1.42 | 1.32 | 1.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 427971 | 737 | 416542 | 786 | 256206.8 | 581.133 | 6.01 | 6.91 | 6.39 | 6.08 | 5.9 | 6.29 | 6.45 | 6.54 | 6.82 | 6.58 | 6.17 | 6.41 | 919000 | 2000 | 897000 | 2000 | 1810047 | 4400 | 1812000 | 1805647 | 12.5667 | 6.2633 | 1.255 | 6.495 | 1.29 | 20.04% | 19.86% | 35.85 | 49.39 | 2.6717 | 6.325 | 1822638.5 | 1809800 | 2141583.7097 | 84.51%
2023-09-08 | 2024 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 335090.89 | 6:26 | 18:57 | 10915.5 | 11392.2 | 11309.6 | 11227.8 | 11411.1 | 11480.1 | 11416.4 | 11820.9 | 11384.2 | 11359.8 | 11305.8 | 11458.4 | 11524.6 | 11448.1 | 11430.8 | 11570.3 | 11391.2 | 11528.4 | 11550.3 | 11603.3 | 11611.6 | 11608.3 | 11360.7 | 11511.4 | 11456.2 | 10132 | 11460.8 | 11449.6 | 11697 | 11518.6 | 11419 | 11654.9 | 11704.1 | 11806.3 | 11842.4 | 11751.9 | 11754.2 | 11600.4 | 11599.8 | 11485.8 | 12206.8 | 11198.6 | 12063.3 | 10973.8 | 11573.8 | 12545.9 | 10853.9 | 12183.8 | 10735.7 | 11002.2 | 11720.4 | 11084.6 | 12029.2 | 10803.4 | 11974.2 | 10764.7 | 10676 | 12085.9 | 10719.6 | 12080.2 | 11930 | 10664.3 | 11625.7 | 11033.9 | 11356.5 | 10773.3 | 11390.2 | 11855 | 12040.8 | 10973.5 | 11922.7 | 10531.6 | 10695.4 | 10570.1 | 9893.2 | 10917.2 | 9777.6 | 11075.7 | 9856.5 | 10947.5 | 11023.4 | 11851.5 | 11108.6 | 12216.7 | 11003.2 | 11699.5 | 10930.7 | 9705.8 | 11754.9 | 11430.8 | 10717 | 12229.6 | 11942 | 11048.6 | 10897.8 | 11933.5 | 10743 | 11194.8 | 12088.4 | 10718.1 | 12112.5 | 10725.3 | 11846.7 | 10955.2 | 11939.9 | 10381.8 | 12005.5 | 10938 | 11849.7 | 10866.1 | 11926.4 | 11074.5 | 10735.9 | 11762.5 | 10899.1 | 10673.3 | 11911.7 | 12036.7 | 11844.3 | 10948.5 | 11923.3 | 10762.6 | 11683.8 | 10944 | 11542.2 | 10076.7 | 11690.6 | 10801 | 10965.4 | 10935.9 | 10755.3 | 9331.1 | 10695.1 | 9403.6 | 10566.2 | 10552.1 | 12216 | 10782.4 | 12214.7 | 10966.7 | 12051.2 | 10749.2 | 10929.7 | 10713.1 | 12046.4 | 12354.8 | 12345 | 12281.2 | 12231 | 12227.7 | 11141.9 | 12240.2 | 12175 | 12301.4 | 12318.6 | 12332 | 12374.7 | 11266.3 | 12380.7 | 11282.3 | 0 | 37.7125 | 0 | 37.5979 | 37.6514 | 37.672 | 0 | 50.6 | 0 | 0 | 50.5 | 50.6 | 2.69 | 2.8684 | 2.701 | 2.7111 | 2.7109 | 2.6264 | 6.247 | 7.284 | 6.093 | 7.518 | 6.652 | 6.685 | 6.3134 | 6.3545 | 6.2561 | 6.1152 | 6.1427 | 6.2487 | 1.0399 | 1.2449 | 1.3177 | 1.4214 | 1.3045 | 1.2524 | 6.6163 | 6.458 | 6.4967 | 6.6213 | 6.4572 | 6.3965 | 1.1135 | 1.2075 | 1.352 | 1.4482 | 1.3819 | 1.2984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 428876 | 738 | 417449 | 787 | 258012.953 | 585.4 | 6.3134 | 6.3545 | 6.2561 | 6.1152 | 6.1427 | 6.2487 | 6.6163 | 6.458 | 6.4967 | 6.6213 | 6.4572 | 6.3965 | 905000 | 1000 | 907000 | 1000 | 1806153 | 4267 | 1810000 | 1801886 | 12.5167 | 6.2384 | 1.2635 | 6.5077 | 1.3003 | 20.25% | 19.98% | 37.6584 | 50.5667 | 2.718 | 6.7465 | 1818283.1 | 1806200 | 2132362.8706 | 84.7%
2023-09-09 | 2024 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 335090.89 | 6:26 | 18:56 | 11661.7 | 12216.8 | 12138.8 | 12093.4 | 12206.9 | 12266.3 | 12173 | 12552.5 | 12149.4 | 12144 | 11973.2 | 12183.4 | 12172.1 | 12100 | 12080.1 | 12242.6 | 12057.5 | 12172 | 12169.2 | 12225.3 | 12202.5 | 12205.4 | 11931.5 | 12082.2 | 11957.9 | 10513.5 | 12007.6 | 11972.9 | 12274.7 | 12117.5 | 11970.2 | 12217.9 | 12190.7 | 12285 | 12289.6 | 12203.1 | 12324.5 | 12178.8 | 12213.6 | 12098.8 | 13022.9 | 11820.7 | 12823.5 | 11537.6 | 12254.4 | 13421.9 | 11501.8 | 13008.8 | 11222.2 | 11511.8 | 12337.3 | 11557.4 | 12685.4 | 11327 | 12546.9 | 11200.9 | 11098.7 | 12674.7 | 11220.3 | 12694.3 | 12562.2 | 11221.1 | 12292.2 | 11690.8 | 11922.8 | 11228 | 11896.3 | 12425.7 | 12660.4 | 11435.6 | 12532.8 | 10964.5 | 12173.4 | 11986.6 | 11211.4 | 12570.8 | 11060.2 | 12714.4 | 11144.4 | 12491.1 | 11180.2 | 12056.3 | 11299.9 | 12436.3 | 11168.2 | 11935.6 | 11059.3 | 9818.4 | 12317.7 | 11938.2 | 11152.7 | 12795.6 | 12472.3 | 11468.1 | 11310 | 12502.4 | 11088.1 | 11585.1 | 12594.2 | 11071.4 | 12623.6 | 11082.4 | 12334.2 | 11330.8 | 12445.1 | 10694.7 | 12534.5 | 11328.5 | 12346.6 | 11210.1 | 12451.8 | 11474.4 | 11101.3 | 12295.9 | 11275.6 | 11052.7 | 12285.1 | 12327.9 | 12362.5 | 11332.7 | 12456.4 | 11167.4 | 12144.4 | 11312.9 | 12016.6 | 10467.1 | 12230.1 | 11249.2 | 11353.8 | 11344.7 | 11188.2 | 9671.2 | 11123 | 9814 | 11121.1 | 11130.1 | 12793.3 | 11321.5 | 12858 | 11552.9 | 12762.1 | 11344.4 | 11568.1 | 11322.8 | 12457.3 | 12821 | 12720.9 | 12699.4 | 12717.6 | 12758.4 | 11618.1 | 12753.3 | 12762.9 | 12772.6 | 12830.9 | 12760.5 | 12749.5 | 11611.9 | 12844.4 | 11603.3 | 0 | 36.205 | 0 | 36.1843 | 36.2738 | 36.3879 | 0 | 51.5663 | 0 | 0 | 51.9 | 51.8 | 2.3944 | 2.2953 | 2.2236 | 2.2945 | 2.3014 | 2.2071 | 5.833 | 6.053 | 5.267 | 5.694 | 5.461 | 5.155 | 6.6672 | 6.6392 | 6.6103 | 6.354 | 6.4098 | 6.4687 | 1.0835 | 1.3278 | 1.3834 | 1.4714 | 1.3916 | 1.2894 | 7.0236 | 6.8129 | 6.8955 | 6.9252 | 6.8035 | 6.637 | 1.1632 | 1.2843 | 1.4268 | 1.4995 | 1.4733 | 1.3435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 429839 | 740 | 418391 | 789 | 259908.62 | 589.067 | 6.6672 | 6.6392 | 6.6103 | 6.354 | 6.4098 | 6.4687 | 7.0236 | 6.8129 | 6.8955 | 6.9252 | 6.8035 | 6.637 | 963000 | 2000 | 942000 | 2000 | 1895667 | 3667 | 1901000 | 1892000 | 12.5 | 6.5249 | 1.3245 | 6.8496 | 1.3651 | 20.3% | 19.93% | 36.2628 | 51.7554 | 2.2861 | 5.5772 | 1908805 | 1895467 | 2248350.1795 | 84.3%
2023-09-10 | 2024 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 335090.89 | 6:28 | 18:55 | 11277 | 11823.5 | 11755.1 | 11678.6 | 11841.5 | 11856.9 | 11760 | 12151.7 | 11756.8 | 11737.6 | 11582.5 | 11799.5 | 11755.5 | 11710.3 | 11624.1 | 11797.6 | 11630.3 | 11774.1 | 11780.2 | 11812 | 11817.4 | 11812 | 11559.4 | 11695.6 | 11570.6 | 10167.9 | 11616.4 | 11587.6 | 11909.2 | 11748.9 | 11576.4 | 11852.9 | 11737.9 | 11819.1 | 11866 | 11757.6 | 11911.7 | 11758.5 | 11793.6 | 11681 | 12667 | 11443.2 | 12473.3 | 11178.8 | 11898.8 | 13024.5 | 11140.2 | 12636.5 | 10830.4 | 11118.4 | 11925.5 | 11172 | 12291.8 | 10903.9 | 12188.4 | 10858 | 10632.3 | 12308.3 | 10813.4 | 12291.4 | 12068.4 | 10823.9 | 11929.1 | 11303.2 | 11593.9 | 10872.6 | 11546.2 | 12069.9 | 12324.9 | 11087.6 | 12193.5 | 10645.9 | 11811.2 | 11598.9 | 10850.7 | 12251.4 | 10735.8 | 12349.6 | 10831.1 | 12125.7 | 11147.9 | 12061.1 | 11270.6 | 12499.8 | 11127.8 | 11903.5 | 11033.5 | 9748.1 | 11939.2 | 11556.3 | 10791.5 | 12435.6 | 12107.1 | 11093.5 | 10954.9 | 12149.9 | 10774.5 | 11277.3 | 12307.4 | 10753.3 | 12297.2 | 10753.1 | 11979.5 | 10994.6 | 12087.1 | 10311.3 | 12163.4 | 10964.4 | 11974.8 | 10876.5 | 12085.1 | 11103 | 10781 | 11952.4 | 10948.3 | 10725 | 12063.9 | 12206 | 11987.9 | 10950.4 | 12089.5 | 10809.4 | 11775.5 | 10961.7 | 11659.5 | 10153 | 11871.1 | 10897.8 | 10978.3 | 10956 | 10872.7 | 9379.2 | 10782.5 | 9499.6 | 10845.5 | 10830.1 | 12575.9 | 11067.7 | 12654.9 | 11305.8 | 12524.9 | 11059.8 | 11278.2 | 11023.4 | 12246.5 | 12615.7 | 12491.8 | 12470.2 | 12493.2 | 12549.8 | 11392 | 12569.2 | 12447.3 | 12499.2 | 12627.6 | 12570.3 | 12558 | 11400.4 | 12591 | 11362.3 | 0 | 35.4742 | 0 | 35.5733 | 35.5851 | 35.7422 | 0 | 50.9 | 0 | 0 | 51 | 50.9 | 3.1591 | 3.1338 | 3.0951 | 3.0822 | 3.0629 | 3.0394 | 6.05 | 5.623 | 5.459 | 5.647 | 6.079 | 6.26 | 6.3668 | 6.3784 | 6.3348 | 6.1308 | 6.1418 | 6.2745 | 1.052 | 1.2724 | 1.3603 | 1.4472 | 1.3298 | 1.2469 | 6.7104 | 6.5586 | 6.6559 | 6.6715 | 6.5595 | 6.4591 | 1.1314 | 1.228 | 1.4005 | 1.4726 | 1.4124 | 1.2978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 430766 | 741 | 419310 | 790 | 261750.954 | 593.467 | 6.3668 | 6.3784 | 6.3348 | 6.1308 | 6.1418 | 6.2745 | 6.7104 | 6.5586 | 6.6559 | 6.6715 | 6.5595 | 6.4591 | 927000 | 1000 | 919000 | 1000 | 1842334 | 4400 | 1844000 | 1837934 | 12.45 | 6.2712 | 1.2848 | 6.6025 | 1.3238 | 20.49% | 20.05% | 35.5937 | 50.9333 | 3.0954 | 5.853 | 1855828.3 | 1842267 | 2176579.5094 | 84.64%
2023-09-11 | 2024 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 335090.89 | 6:29 | 19:00 | 11444.8 | 12010.1 | 11945 | 11865.8 | 12032 | 12039.6 | 11931.3 | 12291.1 | 11924.1 | 11988.6 | 11785.4 | 11974.4 | 11976.6 | 11902.2 | 11906.3 | 12034.2 | 11878.6 | 11985.9 | 11968.9 | 12018.5 | 11990.3 | 11998.4 | 11795.3 | 11903.2 | 11765.6 | 10371.1 | 11811.5 | 11787.5 | 12080.3 | 11940.1 | 11804.7 | 12024.1 | 11993.6 | 12088.6 | 12106 | 12009.7 | 12070.9 | 11946.9 | 11983.9 | 11877.3 | 12858.9 | 11690.1 | 12655.3 | 11461 | 12109.9 | 13319.3 | 11372.7 | 12835.7 | 11087.8 | 11373.2 | 12121 | 11412 | 12480.1 | 11162.6 | 12338 | 11098.2 | 10996.8 | 12528 | 11109.9 | 12546.7 | 12420.5 | 11076.5 | 12122.3 | 11531.1 | 11784.3 | 11117.2 | 11747.3 | 12212.3 | 12456.7 | 11302.2 | 12320 | 10849.4 | 11940 | 11810.5 | 11052.3 | 12344.3 | 10924.3 | 12464.8 | 11029 | 12221.8 | 11357.1 | 12172.2 | 11481.1 | 12633.3 | 11349.9 | 12062.6 | 11253.4 | 9970.2 | 11694.5 | 11402.3 | 10673.1 | 12190 | 11898.8 | 11040.1 | 10941.5 | 11963.2 | 11072.8 | 11525.1 | 12476.9 | 10996.3 | 12468.1 | 10998.6 | 12176.3 | 11270.6 | 12264.2 | 10570.3 | 12345.4 | 11224.3 | 12184.6 | 11156.5 | 12278.4 | 11362.5 | 11039 | 12111.9 | 11210.3 | 10981.4 | 12218.8 | 12335.1 | 12150.5 | 11163.4 | 12217.2 | 11015.4 | 11965.8 | 11221.1 | 11847.3 | 10342.4 | 12007.7 | 11081.2 | 11212.4 | 11184.6 | 11031.8 | 9565 | 10937.6 | 9627.3 | 10988.3 | 10956.2 | 12653.8 | 11194.6 | 12713.6 | 11403.1 | 12563.3 | 11160.8 | 11369.7 | 11132.2 | 12333.9 | 12711 | 12620.1 | 12589.9 | 12595 | 12641.2 | 11498.8 | 12617.6 | 12682.7 | 12713.5 | 12767.8 | 12728.6 | 12732.3 | 11569.4 | 12714.5 | 11575.3 | 0 | 33.3062 | 0 | 33.1626 | 32.9277 | 33.5787 | 0 | 47.5677 | 0 | 0 | 48.1 | 48 | 4.5571 | 4.7887 | 4.5554 | 4.7654 | 4.5933 | 4.7721 | 7.104 | 7.38 | 9.922 | 7.533 | 6.725 | 7.245 | 6.3839 | 6.4554 | 6.3731 | 6.1289 | 6.184 | 6.2873 | 1.047 | 1.297 | 1.3629 | 1.4336 | 1.3639 | 1.2712 | 6.7819 | 6.6278 | 6.7401 | 6.7319 | 6.6071 | 6.4871 | 1.1325 | 1.2534 | 1.4019 | 1.4616 | 1.443 | 1.3188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 431712 | 742 | 420241 | 792 | 263621.9 | 597.733 | 6.3839 | 6.4554 | 6.3731 | 6.1289 | 6.184 | 6.2873 | 6.7819 | 6.6278 | 6.7401 | 6.7319 | 6.6071 | 6.4871 | 946000 | 1000 | 931000 | 2000 | 1870946 | 4266 | 1874000 | 1866680 | 12.5167 | 6.3021 | 1.2959 | 6.6626 | 1.3352 | 20.56% | 20.04% | 33.2438 | 47.8892 | 4.672 | 7.6515 | 1883685 | 1870867 | 2225800.4332 | 84.05%
2023-09-12 | 2024 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 335090.89 | 6:25 | 18:43 | 11670.7 | 12191.3 | 12104.5 | 12041 | 12175.3 | 12239.8 | 12109.8 | 12402.4 | 12079.2 | 12157.6 | 11984.9 | 12136.3 | 12174.9 | 12100.9 | 12116.5 | 12219.3 | 12062.9 | 12152.2 | 12151 | 12211 | 12168.9 | 12189.1 | 11994.9 | 12091 | 11975 | 10590 | 12014.9 | 11989.5 | 12247.3 | 12125.4 | 12015.3 | 12200.3 | 12287.3 | 12361.4 | 12388.2 | 12287.2 | 12274.1 | 12157.3 | 12195.2 | 12092.7 | 12910.8 | 11895.9 | 12730.7 | 11648.9 | 12290.2 | 13349.3 | 11476.9 | 12876.8 | 11320.9 | 11611.5 | 12304.4 | 11644.1 | 12616.3 | 11367.5 | 12509.3 | 11331.3 | 11257.2 | 12659.1 | 11327.8 | 12667.1 | 12556.6 | 11291.3 | 12266.8 | 11727.2 | 11992.5 | 11357.6 | 11971.6 | 12400.2 | 12598.1 | 11532 | 12492.6 | 11066.9 | 12173.5 | 12023 | 11293.1 | 12480.7 | 11129.4 | 12577.4 | 11223.7 | 12354.6 | 11573.4 | 12277.4 | 11680.4 | 12746.7 | 11578.2 | 12259.8 | 11469.5 | 10180.9 | 12323.1 | 11978 | 11282.6 | 12763.5 | 12477.2 | 11641.2 | 11524.9 | 12534 | 11344.4 | 11789.4 | 12636.9 | 11272 | 12625.6 | 11252.4 | 12392 | 11532.3 | 12460.1 | 10817.6 | 12550.8 | 11507.5 | 12431.2 | 11458.9 | 12515 | 11676 | 11320.5 | 12394.9 | 11497 | 11282.1 | 12453.1 | 12614 | 12399.6 | 11542.3 | 12506.2 | 11389.4 | 12228.9 | 11536.9 | 12133.1 | 10706.4 | 12336.7 | 11454.5 | 11590.3 | 11561.5 | 11346.9 | 9879.1 | 11344.2 | 9986 | 11255 | 11218 | 12807.8 | 11511.9 | 12868.3 | 11700.9 | 12780.1 | 11477.2 | 11685.7 | 11414.9 | 12552.9 | 12863.8 | 12801.1 | 12764.8 | 12755.5 | 12791.8 | 11791.3 | 12786.4 | 12445.8 | 12480.1 | 12490.8 | 12460.3 | 12480.4 | 11468.7 | 12452.9 | 11476.2 | 0 | 32.4964 | 0 | 32.3416 | 32.1591 | 32.7726 | 0 | 47.4562 | 0 | 0 | 47.9 | 47.8 | 4.6256 | 4.8282 | 4.6306 | 4.8038 | 4.6167 | 4.7814 | 7.304 | 7.2 | 9.621 | 7.04 | 6.705 | 7.32 | 6.5216 | 6.6249 | 6.4884 | 6.254 | 6.3651 | 6.4688 | 1.0527 | 1.3391 | 1.3628 | 1.4435 | 1.428 | 1.3549 | 6.9508 | 6.8266 | 6.8872 | 6.9201 | 6.8711 | 6.6888 | 1.1361 | 1.2934 | 1.405 | 1.4706 | 1.5074 | 1.3949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 432673 | 743 | 421191 | 794 | 265526.754 | 600.933 | 6.5216 | 6.6249 | 6.4884 | 6.254 | 6.3651 | 6.4688 | 6.9508 | 6.8266 | 6.8872 | 6.9201 | 6.8711 | 6.6888 | 961000 | 1000 | 950000 | 2000 | 1904854 | 3200 | 1908000 | 1901654 | 12.3 | 6.4538 | 1.3302 | 6.8574 | 1.3679 | 20.61% | 19.95% | 32.4424 | 47.7187 | 4.7144 | 7.5317 | 1918070.4 | 1904800 | 2288498.1401 | 83.23%
2023-09-13 | 2024 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 335090.89 | 6:26 | 18:51 | 11046.1 | 11530.1 | 11425.4 | 11348.8 | 11475.3 | 11556.9 | 11494.4 | 11780.5 | 11409.5 | 11489.1 | 11334.2 | 11464.1 | 11471.3 | 11431.4 | 11390.2 | 11504.4 | 11348.1 | 11444.7 | 11460.6 | 11511.8 | 11480.7 | 11439.5 | 11290.2 | 11392.6 | 11265.5 | 9914.5 | 11301.6 | 11282.1 | 11555.1 | 11423.6 | 11276.2 | 11521.1 | 11508.9 | 11576.8 | 11601.1 | 11516.2 | 11597.8 | 11469.6 | 11503.5 | 11407.4 | 12352.5 | 11323.9 | 12189.1 | 11079.7 | 11690.8 | 12752.3 | 10932.5 | 12337.9 | 10607.6 | 10891.2 | 11588.6 | 10907.4 | 11886 | 10616 | 11826.7 | 10598.5 | 10579.3 | 11998.7 | 10626 | 12003.3 | 11868 | 10602.1 | 11652.7 | 11080.4 | 11295.8 | 10647.2 | 11283.5 | 11746.8 | 11926.7 | 10852.6 | 11825.5 | 10427.6 | 11496 | 11365.1 | 10588.6 | 11835.7 | 10460.4 | 11910.7 | 10532.7 | 11694.7 | 10961.3 | 11738 | 11077.2 | 12135 | 10945.5 | 11653.7 | 10802.1 | 9605.6 | 11690.3 | 11326.5 | 10552 | 12068.7 | 11765.8 | 10880.8 | 10767.3 | 11804.6 | 10592.5 | 11084.8 | 11954.2 | 10573.5 | 11993.2 | 10580.1 | 11750.8 | 10860.1 | 11813.9 | 10203.1 | 11895.9 | 10835 | 11771 | 10773.8 | 11847.3 | 10981.4 | 10641.9 | 11693.9 | 10799.7 | 10575.3 | 11789.6 | 11895.5 | 11715.8 | 10779.4 | 11813.2 | 10672.1 | 11556.4 | 10816.8 | 11437.7 | 10025.9 | 11621.9 | 10700.1 | 10794.9 | 10755 | 10582.6 | 9192.4 | 10587.9 | 9360.4 | 10567 | 10560.7 | 12242.2 | 10903.3 | 12303.7 | 11093.9 | 12194.7 | 10884.8 | 11096.8 | 10797.9 | 11944.5 | 12280.1 | 12217.8 | 12191.2 | 12181.5 | 12224.4 | 11214 | 12232.2 | 12240.3 | 12269.2 | 12272.9 | 12242 | 12278.9 | 11209.8 | 12258 | 11240.7 | 0 | 31.946 | 0 | 31.7308 | 31.6153 | 32.2457 | 0 | 46.1378 | 0 | 0 | 46.6504 | 46.7 | 4.5577 | 4.8748 | 4.6191 | 4.8724 | 4.6106 | 4.832 | 7.804 | 8.092 | 8.447 | 7.715 | 7.466 | 8.165 | 6.0816 | 6.191 | 6.0741 | 5.86 | 5.8906 | 6.0718 | 0.96827 | 1.2809 | 1.2582 | 1.3337 | 1.3611 | 1.3532 | 6.5337 | 6.4333 | 6.4644 | 6.4996 | 6.364 | 6.263 | 1.0414 | 1.2355 | 1.3052 | 1.3541 | 1.4399 | 1.405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 433580 | 744 | 422092 | 795 | 267328.421 | 605.133 | 6.0816 | 6.191 | 6.0741 | 5.86 | 5.8906 | 6.0718 | 6.5337 | 6.4333 | 6.4644 | 6.4996 | 6.364 | 6.263 | 907000 | 1000 | 901000 | 1000 | 1801667 | 4200 | 1806000 | 1797467 | 12.4167 | 6.0282 | 1.2592 | 6.4263 | 1.2968 | 20.89% | 20.18% | 31.8845 | 46.4961 | 4.7278 | 7.9482 | 1814357.6 | 1801667 | 2154576.4521 | 83.62%
2023-09-14 | 2024 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 335090.89 | 6:48 | 18:52 | 7708.2 | 8095.5 | 8032.3 | 7970.5 | 8065 | 8159.4 | 8105 | 8370.3 | 8020.7 | 8023.4 | 7904.7 | 7995.5 | 8055.3 | 7946.8 | 8020.8 | 8118.9 | 7950.5 | 7934.5 | 7902.5 | 7941.2 | 7866.8 | 7840.6 | 7655.2 | 7750.6 | 7568.6 | 6730.9 | 7715.2 | 7626.9 | 7807.1 | 7744.2 | 7586.3 | 7761.1 | 7833.7 | 7815.1 | 7811.8 | 7735.9 | 7816.9 | 7748.7 | 7824.4 | 7818.6 | 8400.9 | 7546.1 | 8274.1 | 7383 | 7851.6 | 8757.3 | 7318.7 | 8426.5 | 7370 | 7569.5 | 8051.3 | 7587.5 | 8258.1 | 7454 | 8234.6 | 7289.4 | 7234.4 | 8304.2 | 7258.4 | 8256.3 | 8080.9 | 7294.1 | 7959.8 | 7620.5 | 7070.1 | 7003.1 | 7790.4 | 8116.2 | 7854.4 | 7404.5 | 8255.9 | 7197.7 | 7999 | 7862.8 | 7347.5 | 7639.5 | 6697.3 | 7513.1 | 7315.1 | 8158.9 | 7069.4 | 7905.9 | 7623.3 | 8393.5 | 7489 | 8004.9 | 7370.5 | 6561.6 | 8109.9 | 7335.3 | 7298.7 | 8450.5 | 8215.3 | 7542 | 7211.8 | 8197.7 | 7417.2 | 7746 | 8457 | 7366.2 | 8372.7 | 7336.1 | 8089.2 | 7499.6 | 8216.3 | 7028.4 | 8238.6 | 7425.2 | 8108.8 | 7390.5 | 8160.7 | 7436.6 | 7398.6 | 8085.1 | 7441.2 | 7273.9 | 8172.6 | 8214.3 | 8087.3 | 7417 | 8175.8 | 7320.2 | 7920.9 | 7364.9 | 7818.5 | 6881.8 | 7980 | 7315.4 | 7425.3 | 7409.7 | 7287 | 6326.3 | 7290.9 | 6439.4 | 7383.1 | 7395.2 | 8712.3 | 7596.9 | 8756.5 | 7725.8 | 8644.8 | 7597.1 | 7708 | 7559.7 | 8461.9 | 8754.9 | 8660.2 | 8645 | 8602.6 | 8648.6 | 7779.3 | 8649.4 | 8658.6 | 8743.3 | 8843 | 8786.7 | 8797.7 | 7885 | 8736.9 | 7893.9 | 0 | 30.0001 | 0 | 29.9344 | 29.8616 | 30.3044 | 0 | 39.2254 | 0 | 0 | 40.1 | 40.6472 | 4.0207 | 4.2704 | 3.8373 | 4.2323 | 4.0311 | 4.1485 | 8.019 | 7.675 | 8.317 | 7.751 | 7.029 | 8.101 | 4.1075 | 4.0926 | 3.9823 | 3.9816 | 3.9284 | 4.1251 | 0.70212 | 0.80632 | 0.84819 | 0.91185 | 0.87092 | 0.85377 | 4.3097 | 4.1307 | 4.1387 | 4.2594 | 4.1726 | 4.1909 | 0.74687 | 0.78212 | 0.89653 | 0.92351 | 0.9382 | 0.90505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 434202 | 745 | 422718 | 796 | 268573.021 | 609.6 | 4.1075 | 4.0926 | 3.9823 | 3.9816 | 3.9284 | 4.1251 | 4.3097 | 4.1307 | 4.1387 | 4.2594 | 4.1726 | 4.1909 | 622000 | 1000 | 626000 | 1000 | 1244600 | 4467 | 1246000 | 1240133 | 12.0667 | 4.0363 | 0.83219 | 4.2003 | 0.86538 | 20.62% | 20.6% | 30.0251 | 39.9909 | 4.09 | 7.8153 | 1251127.2 | 1244533 | 1443859.8604 | 86.19%
2023-09-15 | 2024 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 335090.89 | 6:40 | 18:51 | 9026.8 | 9562.5 | 9597.2 | 9526 | 9690.4 | 9765.3 | 9696.3 | 10082.7 | 9508.4 | 9442.7 | 9466.5 | 9561.5 | 9677.3 | 9558 | 9706.5 | 9756.1 | 9615.3 | 9628.3 | 9575.4 | 9639.2 | 9554.5 | 9564.3 | 9301.5 | 9416.1 | 9202.3 | 8170.7 | 9319.2 | 9264.7 | 9506.5 | 9392.5 | 9184.2 | 9377.4 | 9201.7 | 9255.4 | 9395.8 | 9288.3 | 9398.2 | 9320.2 | 9353.3 | 9185.7 | 10302.1 | 9312.7 | 10121.2 | 9127.1 | 9678.6 | 10707.2 | 8941 | 10262 | 8821.9 | 9030.2 | 9637.6 | 9012.9 | 9949.6 | 9000 | 9755.2 | 8769.5 | 8655.1 | 9865.5 | 8791 | 9839.4 | 9751.5 | 8756.4 | 9506.5 | 9064.1 | 9218.6 | 8631.8 | 9196.8 | 9496.1 | 9814.9 | 8792.6 | 9692.7 | 8462.3 | 9466.2 | 9241.4 | 8751.8 | 9692.9 | 8540.8 | 9793.4 | 8700.2 | 9611.4 | 8748.7 | 9472.4 | 8807.2 | 9776.2 | 8710.3 | 9298.7 | 8694.9 | 7671.9 | 9408 | 9055.8 | 8486.3 | 9788.3 | 9482.6 | 8754.3 | 8681.2 | 9524.1 | 8456.9 | 8727.3 | 9546.6 | 8317.4 | 9631.6 | 8331.9 | 9344.6 | 8537 | 9441.4 | 8021.5 | 9466.9 | 8452.6 | 9363.3 | 8494.5 | 9443.2 | 8579.6 | 8367.1 | 9209.2 | 8438.5 | 8262.5 | 9302.4 | 9340.8 | 9196.4 | 8399 | 9283 | 8289.2 | 9028.7 | 8405.7 | 8932.1 | 7797.9 | 9051.8 | 8290.3 | 8329.4 | 8342.8 | 8263.4 | 7129.5 | 8188.7 | 7252.5 | 8297.1 | 8282.4 | 9659.3 | 8441.1 | 9654.6 | 8566.1 | 9581.9 | 8410.2 | 8550.8 | 8392.7 | 9353.6 | 9672.1 | 9613.3 | 9553.5 | 9571.6 | 9605.6 | 8636.3 | 9575.4 | 9703.5 | 9707.8 | 9749.3 | 9695.7 | 9705 | 8676.9 | 9787.1 | 8695.7 | 0 | 32.2526 | 0 | 32.1885 | 32.1426 | 32.3742 | 0 | 43.7177 | 0 | 0 | 43.3 | 43.1 | 4.2218 | 4.4185 | 4.0945 | 4.3356 | 4.2382 | 4.3541 | 7.604 | 7.696 | 8.431 | 7.644 | 7.562 | 8.123 | 5.0558 | 5.0715 | 4.9691 | 4.756 | 4.6959 | 4.6911 | 0.77836 | 1.0069 | 1.0009 | 1.0465 | 1.0086 | 0.94864 | 5.3339 | 5.1982 | 5.2257 | 5.1873 | 4.8992 | 4.8419 | 0.83904 | 0.97429 | 1.0522 | 1.0592 | 1.0841 | 0.97861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 434953 | 747 | 423430 | 798 | 270030.621 | 614.067 | 5.0558 | 5.0715 | 4.9691 | 4.756 | 4.6959 | 4.6911 | 5.3339 | 5.1982 | 5.2257 | 5.1873 | 4.8992 | 4.8419 | 751000 | 2000 | 712000 | 2000 | 1457600 | 4467 | 1459000 | 1453133 | 12.1833 | 4.8732 | 0.96497 | 5.1144 | 0.9979 | 19.8% | 19.51% | 32.2395 | 43.3726 | 4.2771 | 7.8433 | 1464253.8 | 1457600 | 1741536.613 | 83.7%
2023-09-16 | 2024 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 335090.89 | 6:42 | 18:55 | 9182.7 | 9590.9 | 9473.2 | 9515.3 | 9515.7 | 9543.5 | 9526.5 | 9935.2 | 9602.1 | 9663.7 | 9390.7 | 9590.5 | 9510.4 | 9468.1 | 9573.8 | 9610.4 | 9514.5 | 9557 | 9541.3 | 9608.9 | 9566.3 | 9566.5 | 9310.9 | 9448.9 | 9279.4 | 8207.3 | 9378.5 | 9304.2 | 9550.4 | 9411.6 | 9224.5 | 9477.5 | 9414.3 | 9470.8 | 9550.1 | 9448.1 | 9522.9 | 9401.5 | 9460.5 | 9361.9 | 10188.6 | 9164.4 | 10011.8 | 8983.4 | 9557.4 | 10655.1 | 8966.3 | 10202.2 | 8813.3 | 9066.5 | 9656.4 | 9052.5 | 9975.5 | 8899.5 | 9871.4 | 8809.2 | 8778.4 | 10050.1 | 8863.1 | 10046.9 | 9927.2 | 8842.2 | 9669.7 | 9179.6 | 9361.3 | 8780.2 | 9328.5 | 9704.5 | 9968.7 | 8957.3 | 9855.7 | 8600.2 | 9598.5 | 9388.9 | 8846.6 | 9881.4 | 8694.6 | 10028.8 | 8811.3 | 9814 | 8990.4 | 9675.9 | 9083.2 | 10070.4 | 8992.9 | 9606.6 | 8946.6 | 7921.3 | 9760.2 | 9395.6 | 8711.8 | 10016.6 | 9663.9 | 8936.9 | 8863.7 | 9730.5 | 8749.5 | 9143.1 | 10013.6 | 8789.8 | 10070.4 | 8798.5 | 9834.8 | 9038.9 | 9974.7 | 8489.2 | 10033.5 | 9008.6 | 9905.6 | 9015.4 | 9997.3 | 9148.1 | 8856.2 | 9848.2 | 9025.8 | 8839.8 | 9957.3 | 10102.9 | 9866.2 | 9107.1 | 10036.1 | 8984.8 | 9684.3 | 9028.7 | 9605.4 | 8439.7 | 9809.4 | 9029.5 | 9146.1 | 9170.6 | 9049.2 | 7814.5 | 9021.9 | 7939.2 | 8925.8 | 8885 | 10222.1 | 8924.6 | 10323.7 | 9114.6 | 10122.4 | 8898.6 | 9081.6 | 8927.2 | 9918.7 | 10250.4 | 10210.7 | 10184.4 | 10211.6 | 10230.2 | 9274.7 | 10211.7 | 10131.9 | 10180.2 | 10303.1 | 10220.1 | 10197.7 | 9177.7 | 10273.2 | 9200.6 | 0 | 33.7319 | 0 | 33.8302 | 33.9334 | 33.8575 | 0 | 44.2 | 0 | 0 | 44.5 | 44.4 | 3.103 | 3.0337 | 2.9479 | 3.0915 | 3.057 | 3.0006 | 5.958 | 6.997 | 6.117 | 6.579 | 7.001 | 6.232 | 4.9555 | 5.009 | 4.912 | 4.8177 | 5.033 | 4.993 | 0.8254 | 0.9272 | 1.0501 | 1.1173 | 0.99305 | 0.93654 | 5.1891 | 5.1683 | 5.1745 | 5.1991 | 5.3342 | 5.1749 | 0.87766 | 0.89501 | 1.0762 | 1.1342 | 1.0763 | 0.96786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 435707 | 748 | 424183 | 800 | 271532.421 | 618.6 | 4.9555 | 5.009 | 4.912 | 4.8177 | 5.033 | 4.993 | 5.1891 | 5.1683 | 5.1745 | 5.1991 | 5.3342 | 5.1749 | 754000 | 1000 | 753000 | 2000 | 1501800 | 4533 | 1504000 | 1497267 | 12.2167 | 4.9534 | 0.97493 | 5.2067 | 1.0045 | 19.68% | 19.29% | 33.8383 | 44.3667 | 3.0389 | 6.4807 | 1509464.6 | 1496933 | 1750348.7621 | 85.52%
2023-09-17 | 2024 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 335090.89 | 6:28 | 18:48 | 9367.6 | 9839.8 | 9791.4 | 9762.8 | 9802.6 | 9815.9 | 9885.2 | 10144.7 | 9729.6 | 9734.8 | 9668.7 | 9760.4 | 9783.4 | 9723.5 | 9738.8 | 9843.1 | 9685.6 | 9747.3 | 9722 | 9815.5 | 9812.3 | 9786.6 | 9671.3 | 9738 | 9598.8 | 8575 | 9637.3 | 9596.4 | 9851 | 9742.2 | 9579.3 | 9812.6 | 9665.3 | 9708.3 | 9720.4 | 9682.8 | 9875.3 | 9736.5 | 9752.5 | 9658.1 | 10338.3 | 9530.7 | 10245 | 9385 | 9887.3 | 10813.9 | 9388.3 | 10419.6 | 9123.4 | 9325.1 | 9894.7 | 9340.6 | 10145.6 | 9262.2 | 10011.4 | 9139.7 | 8621.2 | 9937.8 | 8915.9 | 9844.8 | 9492.5 | 8959.1 | 9535.1 | 9219.7 | 9501.4 | 9017.8 | 9499.5 | 9803.3 | 10011.3 | 9181.2 | 9930 | 8914.5 | 9695.4 | 9653.9 | 9074.2 | 10054.3 | 9020.4 | 10118.1 | 9137.1 | 10039.6 | 9246 | 9871.6 | 9363.5 | 10123.4 | 9221.1 | 9728 | 9141.3 | 8123.8 | 9839.4 | 9511.6 | 8955.1 | 10088.3 | 9864.1 | 9234.8 | 9146.5 | 9870.3 | 8937.1 | 9243.9 | 9864 | 8801.1 | 9935.7 | 8802.4 | 9691.9 | 8990 | 9761.8 | 8476.1 | 9810.1 | 8917.7 | 9692.5 | 8939.2 | 9791.8 | 9069.7 | 8872 | 9584.5 | 8876.9 | 8691.7 | 9632 | 9639.5 | 9548.6 | 8810.1 | 9605.2 | 8757.8 | 9436.4 | 8902.9 | 9389.7 | 8312.4 | 9466.8 | 8777.2 | 8808.8 | 8855.7 | 8747.6 | 7541 | 8684.9 | 7773.1 | 9073.8 | 9080.6 | 10243.2 | 9168.3 | 10298.8 | 9314.9 | 10194 | 9189.6 | 9304.3 | 9195 | 10075.3 | 10299.7 | 10291 | 10243.4 | 10247.5 | 10276.1 | 9479.5 | 10268.8 | 10125.5 | 10165.5 | 10209 | 10186 | 10214.2 | 9410.3 | 10290.5 | 9446.4 | 0 | 31.7453 | 0 | 31.7429 | 31.7173 | 31.8695 | 0 | 40.6 | 0 | 0 | 40.1 | 40.5 | 5.0971 | 5.0209 | 5.059 | 5.0656 | 4.941 | 4.9597 | 9.923 | 9.341 | 9.922 | 11.049 | 9.977 | 10.198 | 5.2729 | 5.3528 | 5.1502 | 4.9603 | 4.935 | 5.2514 | 0.76806 | 1.1002 | 0.99644 | 1.0512 | 1.1067 | 1.1315 | 5.6421 | 5.5181 | 5.456 | 5.5145 | 5.1636 | 5.4627 | 0.82865 | 1.0676 | 1.0299 | 1.0678 | 1.1826 | 1.1649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 436477 | 750 | 424934 | 801 | 273048.355 | 622.933 | 5.2729 | 5.3528 | 5.1502 | 4.9603 | 4.935 | 5.2514 | 5.6421 | 5.5181 | 5.456 | 5.5145 | 5.1636 | 5.4627 | 770000 | 2000 | 751000 | 1000 | 1515934 | 4333 | 1518000 | 1511601 | 12.3333 | 5.1538 | 1.0257 | 5.4595 | 1.0569 | 19.9% | 19.36% | 31.7687 | 40.4 | 5.0239 | 10.0683 | 1525051.4 | 1515867 | 1848448.7234 | 82.01%
2023-09-18 | 2024 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 335090.89 | 6:32 | 18:45 | 4945.4 | 5172.1 | 5162.3 | 5141.9 | 5152.7 | 5140.1 | 5162.1 | 5319.7 | 5145.5 | 5160.9 | 5015.6 | 5117.8 | 5034.1 | 5033.2 | 5181.6 | 5218.9 | 5111.2 | 5203.1 | 5174 | 5221.8 | 5236.2 | 5220.1 | 5135.5 | 5168 | 5065.9 | 4502 | 5103 | 5070.6 | 5239.3 | 5201.2 | 5097.1 | 5198.3 | 5134.9 | 5167.1 | 5166.1 | 5148 | 5228.7 | 5184 | 5195.7 | 5156.8 | 5536.7 | 4990.7 | 5463 | 4935.7 | 5242.4 | 5834.9 | 4896.6 | 5551.9 | 4687.9 | 4816.9 | 5113.8 | 4802 | 5377.5 | 4825.5 | 5238.5 | 4763.9 | 4659.3 | 5335.3 | 4709.7 | 5309.2 | 5294.9 | 4724.4 | 5142.5 | 4891.2 | 4671.6 | 4480.3 | 4963.8 | 5157.6 | 5320.3 | 4782.2 | 5264.9 | 4600.8 | 5148.6 | 5019.1 | 4742.6 | 5273.5 | 4643.7 | 5361.5 | 4724.8 | 5260.6 | 4184.8 | 5011.2 | 4820.1 | 5327.5 | 4771.9 | 5089.1 | 4733.1 | 4202.8 | 5227.6 | 4990.6 | 4719.6 | 5447.7 | 5321 | 4947.1 | 4910.3 | 5343.9 | 4817.7 | 4991.1 | 5408.3 | 4779.5 | 5443.2 | 4768.9 | 5315 | 4900.3 | 5333 | 4617.8 | 5353.7 | 4840.8 | 5247.7 | 4800.7 | 5263.7 | 4870.4 | 4806.2 | 5284.9 | 4879.4 | 4789.2 | 5360.6 | 5407.3 | 5290.3 | 4913.2 | 5333.3 | 4811.3 | 5154.6 | 4804.9 | 5087.8 | 4511.3 | 5205.2 | 4799.5 | 4910.8 | 4880.9 | 4801.4 | 4216.7 | 4776.5 | 4225.9 | 4706.2 | 4695.1 | 5371.1 | 4701.4 | 5398.3 | 4784 | 5330.5 | 4718.7 | 4784.6 | 4757.5 | 5164.9 | 5341.3 | 5314.6 | 5303.1 | 5316.2 | 5352.1 | 4841.4 | 5330.7 | 5312 | 5315.4 | 5357 | 5335 | 5331.2 | 4781.1 | 5346.1 | 4787.8 | 0 | 29.1423 | 0 | 29.2355 | 29.055 | 29.2672 | 0 | 33.7 | 0 | 0 | 33.6 | 33.5 | 4.1225 | 4.0609 | 4.0866 | 4.0549 | 3.9091 | 3.9942 | 9.039 | 8.208 | 9.196 | 8.962 | 8.748 | 7.934 | 2.6749 | 2.8384 | 2.7203 | 2.5675 | 2.7253 | 2.5964 | 0.39624 | 0.50788 | 0.51223 | 0.51334 | 0.5383 | 0.47897 | 2.74 | 2.7956 | 2.7387 | 2.6802 | 2.7695 | 2.5987 | 0.42424 | 0.49467 | 0.53631 | 0.52078 | 0.57572 | 0.49288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 436883 | 751 | 425334 | 803 | 273852.555 | 627.4 | 2.6749 | 2.8384 | 2.7203 | 2.5675 | 2.7253 | 2.5964 | 2.74 | 2.7956 | 2.7387 | 2.6802 | 2.7695 | 2.5987 | 406000 | 1000 | 400000 | 2000 | 804200 | 4467 | 803000 | 799733 | 12.2167 | 2.6871 | 0.49116 | 2.7204 | 0.50743 | 18.28% | 18.65% | 29.175 | 33.6 | 4.038 | 8.6812 | 807821.4 | 803067 | 950589.1364 | 84.48%
2023-09-19 | 2024 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 335090.89 | 6:30 | 18:26 | 5224.7 | 5471 | 5472.2 | 5407.8 | 5546.7 | 5556.7 | 5527 | 5731.1 | 5456.9 | 5511 | 5357.2 | 5452.6 | 5426 | 5387.6 | 5586.2 | 5576.5 | 5547.5 | 5585.7 | 5445 | 5455.1 | 5502.5 | 5476.3 | 5353.4 | 5407.8 | 5316.8 | 4711.9 | 5312.2 | 5292.9 | 5459.1 | 5432.9 | 5329.1 | 5440.4 | 5575.5 | 5602.8 | 5515.2 | 5495.2 | 5546 | 5467.1 | 5509.3 | 5526.2 | 5882.8 | 5285 | 5841.5 | 5209.1 | 5581.9 | 6228.6 | 5223.1 | 5906.4 | 5033 | 5185.2 | 5478.4 | 5220.7 | 5656.7 | 5056.9 | 5759.3 | 5120.7 | 4938.9 | 5930.4 | 4923.6 | 5695.3 | 5366.5 | 4985.2 | 5608.5 | 5397 | 5566.9 | 5432.4 | 5783.3 | 6120.3 | 6101.6 | 5646.6 | 6127.7 | 5449 | 5871.2 | 5910.3 | 5441.9 | 6188.6 | 5442.2 | 6126.9 | 5474 | 6108.8 | 5773.2 | 6208.8 | 5856.9 | 6411.5 | 5787.1 | 6178 | 5691.1 | 5073.4 | 6266.2 | 5993.4 | 5548.4 | 6375.4 | 6148.7 | 5647.5 | 5554.4 | 6224.7 | 5591.8 | 5866.4 | 6373.3 | 5635.6 | 6275.6 | 5573.9 | 6117.5 | 5737.6 | 6162 | 5366.4 | 6216.4 | 5712.1 | 6077.8 | 5598.9 | 6128.3 | 5762.4 | 5716.2 | 6343.8 | 5751.2 | 5648.3 | 6358.9 | 6489.3 | 6291.1 | 5858.3 | 6443.5 | 5755.2 | 6136.8 | 5723.4 | 6069.8 | 5359.4 | 6267.8 | 5802.9 | 5915.2 | 5959.4 | 5824.3 | 5044.3 | 5796.6 | 5167.4 | 6052.5 | 6066.6 | 7035.8 | 6128.3 | 7003.2 | 6235.4 | 6985.1 | 6134.9 | 6230.6 | 6145.3 | 6730.1 | 6964.8 | 7019.8 | 6974.1 | 6974 | 7014.3 | 6302.6 | 6967.9 | 6944.4 | 6932.1 | 6833 | 6821.1 | 6879.1 | 6203.9 | 7003.2 | 6313.2 | 0 | 28.7378 | 0 | 28.8503 | 28.7242 | 28.9143 | 0 | 35.3 | 0 | 0 | 36.7 | 37.1 | 3.0702 | 2.9865 | 2.9107 | 3.0306 | 2.9623 | 3.1704 | 7.251 | 6.566 | 6.091 | 6.813 | 6.304 | 6.195 | 2.824 | 2.8928 | 2.8415 | 2.9738 | 3.1953 | 3.4183 | 0.3232 | 0.43871 | 0.42148 | 0.45079 | 0.56794 | 0.57602 | 2.9589 | 2.9224 | 2.9525 | 3.2288 | 3.2929 | 3.5005 | 0.35001 | 0.42775 | 0.44271 | 0.46434 | 0.60809 | 0.59318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 437324 | 753 | 425825 | 804 | 274780.2 | 632.133 | 2.824 | 2.8928 | 2.8415 | 2.9738 | 3.1953 | 3.4183 | 2.9589 | 2.9224 | 2.9525 | 3.2288 | 3.2929 | 3.5005 | 441000 | 2000 | 491000 | 1000 | 927645 | 4733 | 929000 | 922912 | 11.9333 | 3.0243 | 0.46302 | 3.1427 | 0.48101 | 15.31% | 15.31% | 28.8067 | 36.3667 | 3.0218 | 6.5367 | 932856.6 | 924800 | 1083225.6255 | 85.37%
2023-09-20 | 2024 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 335090.89 | 6:46 | 18:41 | 8073.2 | 8588.3 | 8996.7 | 8988.8 | 9147.3 | 9012.4 | 8719.5 | 8862.9 | 8316.6 | 8375.1 | 8151.1 | 8263.1 | 8315.4 | 8177.1 | 8566.7 | 8502.1 | 8471.1 | 8400.5 | 8135.7 | 8194.8 | 8260.9 | 8222.6 | 8047 | 8144.7 | 7853 | 6958.7 | 7945.7 | 7877.3 | 8084.5 | 7994.4 | 7868.5 | 8052.3 | 7923.5 | 7934.4 | 8068.4 | 7985.8 | 8120 | 8011.7 | 8028.5 | 7941.9 | 8970.2 | 8201.1 | 8610.6 | 7931.4 | 8192.5 | 8991.7 | 7936.4 | 8990.1 | 7564.6 | 7741.1 | 8243.3 | 7662.6 | 8471.5 | 7692.4 | 8278.6 | 7431.6 | 7490.2 | 8598.6 | 7546.4 | 8409.3 | 8339.1 | 7541.2 | 8246.4 | 7846.4 | 8372.2 | 8222.7 | 8391.8 | 8993.8 | 8824 | 8384.2 | 8939.4 | 8158.5 | 8483.8 | 8757.4 | 7934.6 | 9145.4 | 8079.4 | 8764.2 | 7803.4 | 8625.7 | 8423.3 | 8980.8 | 8606.4 | 9260.1 | 8443.9 | 8938.1 | 8318.1 | 7438.4 | 8941 | 8668.4 | 8031.7 | 9067 | 8777.6 | 8107.3 | 7958 | 8797.6 | 8070 | 8408.5 | 8961.6 | 8026.2 | 8604.1 | 7874.6 | 8411.8 | 8032.6 | 8374.3 | 7454.6 | 8462.1 | 7853.9 | 8229.4 | 7622.4 | 8226.7 | 7804.3 | 8146.9 | 8951.9 | 8110.3 | 8013.3 | 8796.6 | 9030.5 | 8683.3 | 8351.9 | 8931.9 | 8148.1 | 8396.8 | 7797.1 | 8238.3 | 7601.9 | 8789 | 8281.6 | 8633.4 | 8648.1 | 8378.1 | 7378 | 8500.9 | 7518.9 | 8615.6 | 8579.4 | 9458.7 | 8500.5 | 9506.6 | 8653.9 | 9565.4 | 8581.3 | 8726.5 | 8640 | 8986 | 9252 | 9245 | 9236.9 | 9303.9 | 9385.7 | 8576.6 | 9285 | 9120.3 | 9120.5 | 9079.2 | 9069.9 | 9117.2 | 8280.2 | 9233.1 | 8354.1 | 31.189 | 30.6728 | 0 | 30.732 | 30.5849 | 30.8961 | 0 | 41.2 | 0 | 0 | 42.8 | 42.8 | 3.1873 | 3.1 | 3.0769 | 3.0799 | 2.9567 | 2.9246 | 6.802 | 6.444 | 6.214 | 6.039 | 6.039 | 5.831 | 4.4072 | 4.3207 | 4.4242 | 4.4173 | 4.6807 | 4.6658 | 0.65629 | 0.67607 | 0.72942 | 0.84151 | 0.76219 | 0.69715 | 4.6221 | 4.4304 | 4.652 | 4.7905 | 4.9215 | 4.7887 | 0.70393 | 0.64199 | 0.75505 | 0.83381 | 0.82581 | 0.73495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 437983 | 754 | 426507 | 806 | 276117.6 | 636.733 | 4.4072 | 4.3207 | 4.4242 | 4.4173 | 4.6807 | 4.6658 | 4.6221 | 4.4304 | 4.652 | 4.7905 | 4.9215 | 4.7887 | 659000 | 1000 | 682000 | 2000 | 1337400 | 4600 | 1338000 | 1332800 | 11.9167 | 4.486 | 0.7271 | 4.7008 | 0.74926 | 16.21% | 15.94% | 30.815 | 42.2667 | 3.0542 | 6.2282 | 1344365.1 | 1336267 | 1601366.595 | 83.45%
2023-09-21 | 2024 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 335090.89 | 6:29 | 18:45 | 10178.7 | 10549.2 | 10548 | 10510.7 | 10598.3 | 10503.6 | 10497.1 | 10769.9 | 10549.4 | 10604.2 | 10339.9 | 10533.3 | 10453.5 | 10420 | 10563.4 | 10553.1 | 10659.1 | 10869.8 | 10898.3 | 10867.2 | 10910 | 10977.8 | 10752 | 10828.5 | 10698.8 | 9554.9 | 10752.7 | 10733.4 | 10964.7 | 10945.4 | 10805 | 10969.4 | 10868 | 10923.4 | 10829.2 | 10877.8 | 11142.1 | 10964.3 | 10943.6 | 10868.7 | 11384.4 | 10555.8 | 11429 | 10396.5 | 11052.9 | 12018.1 | 10288.6 | 11398.9 | 9859.5 | 10103.1 | 10721.9 | 10295.3 | 11076.6 | 9996.1 | 11142.9 | 10163 | 9909.4 | 11090.3 | 9795.9 | 10986.9 | 10800.3 | 9752.2 | 10729 | 10286.7 | 10663.9 | 10058.1 | 10580.9 | 10942.3 | 11095.1 | 10184.4 | 10926 | 9756.9 | 10736.1 | 10585.4 | 10026.8 | 11032.9 | 9924.5 | 11139.1 | 9995.1 | 11036.2 | 10203.2 | 10820.8 | 10282.9 | 11221.1 | 10148.3 | 10729.9 | 10130.6 | 8969.6 | 11007.1 | 10573.7 | 9986.1 | 11303.7 | 11031.5 | 10316.7 | 10206 | 11032.6 | 9939.5 | 10343.7 | 11104.9 | 10055.1 | 11108.5 | 10038.3 | 11022.7 | 10339.5 | 11197 | 9794.8 | 11304.4 | 10340.6 | 11145.6 | 10330.7 | 11315.3 | 10497.6 | 10154.6 | 11169.4 | 10349.2 | 10137.9 | 11242.3 | 11406.4 | 11194.7 | 10498.7 | 11393.1 | 10367.5 | 11044 | 10400.5 | 10972 | 9771.2 | 11191.1 | 10425.1 | 10600.5 | 10644.7 | 10501.6 | 9064.3 | 10415.6 | 9237.9 | 10445.4 | 10465.9 | 11774.4 | 10528.2 | 11807.6 | 10734.5 | 11792 | 10658.2 | 10794.1 | 10634.5 | 11485.7 | 11755.2 | 11663.5 | 11621.1 | 11670.8 | 11698.1 | 10770.4 | 11672.5 | 11312.1 | 11460.1 | 11631.3 | 11625.6 | 11651.6 | 10663.2 | 11553.5 | 10704 | 31.2314 | 31.0367 | 0 | 31.0581 | 30.9184 | 31.3899 | 0 | 45.7 | 0 | 0 | 46 | 46.2 | 3.9265 | 3.7733 | 3.4087 | 4.1049 | 3.8489 | 3.4812 | 7.609 | 7.462 | 7.722 | 7.23 | 6.976 | 7.806 | 5.5628 | 5.9001 | 5.7257 | 5.5911 | 5.8696 | 5.961 | 0.85426 | 0.9918 | 0.95101 | 1.1662 | 1.0424 | 0.99369 | 5.9762 | 6.2104 | 6.1827 | 6.2595 | 6.3008 | 6.2907 | 0.91053 | 0.94885 | 0.97097 | 1.1501 | 1.1203 | 1.0379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 438832 | 756 | 427367 | 808 | 277820.888 | 641.2 | 5.5628 | 5.9001 | 5.7257 | 5.5911 | 5.8696 | 5.961 | 5.9762 | 6.2104 | 6.1827 | 6.2595 | 6.3008 | 6.2907 | 849000 | 2000 | 860000 | 2000 | 1703288 | 4467 | 1705000 | 1698821 | 12.2667 | 5.7684 | 0.99991 | 6.2034 | 1.0231 | 17.33% | 16.49% | 31.1269 | 45.9667 | 3.7572 | 7.4675 | 1714291.2 | 1702134 | 2090188.5628 | 81.43%
2023-09-22 | 2024 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 335090.89 | 6:33 | 18:43 | 11445.4 | 11746.5 | 11623.8 | 11574.4 | 11670.1 | 11726.5 | 11714.6 | 12053.8 | 11780.2 | 12084.8 | 11575.4 | 11770.4 | 11550.1 | 11588.8 | 11754.9 | 11682.2 | 11765.2 | 11865.1 | 11796.8 | 11744.3 | 11911 | 11880.7 | 11714 | 11827.1 | 11618.8 | 10178 | 11494.7 | 11584.1 | 11964.3 | 11844.9 | 11703.2 | 11926.9 | 12076.1 | 11980.9 | 11906.2 | 11898.2 | 12055.5 | 11987.3 | 12008.3 | 12034.5 | 13078.3 | 11944.3 | 12887.3 | 11689.4 | 12482 | 13479 | 11738.1 | 12993.1 | 10850.9 | 11166.1 | 11706.5 | 11145.5 | 12008.1 | 10873.6 | 11980.4 | 10766.5 | 10887.3 | 12256.4 | 10945.9 | 12195.1 | 12122.6 | 10941.9 | 12082 | 11696.1 | 10956.8 | 10686.5 | 11662 | 12081.1 | 12392.6 | 11273.2 | 12189.9 | 10849.7 | 12027.2 | 11862.4 | 11196.3 | 12306.2 | 11048.3 | 12499.3 | 11193.2 | 12305.2 | 11339.3 | 12064.5 | 11511.5 | 12489 | 11372.7 | 12062.3 | 11206.6 | 9993.4 | 12043.5 | 11690.9 | 10863.9 | 12291.8 | 11978.2 | 11243.1 | 11223.8 | 12128.8 | 11088.5 | 11444.3 | 12392.9 | 11008.1 | 12662.4 | 11123 | 12405.3 | 11136.5 | 12500.7 | 10828.6 | 12514.9 | 11414.6 | 12387.3 | 11407.1 | 12426.5 | 11599.4 | 11000.7 | 12066.8 | 11285.8 | 11019 | 12202.5 | 12287.6 | 12279 | 11266.6 | 12369.4 | 11231.6 | 12153.8 | 11450.4 | 12082.4 | 10655.1 | 12186.2 | 11271.9 | 11325.2 | 11315.7 | 11257.3 | 9681.7 | 11120.9 | 9771.6 | 11182.5 | 11183.2 | 12878 | 11519.4 | 12929.7 | 11772.9 | 12843.1 | 11559 | 11684 | 11410 | 12443.4 | 12730.8 | 12713 | 12696.8 | 12754 | 12815.5 | 11801.7 | 12761.3 | 12627.7 | 12650.7 | 12797.5 | 12749.9 | 12716.9 | 11644.4 | 12740 | 11681.7 | 32.1495 | 32.1626 | 0 | 32.0423 | 31.8392 | 32.5394 | 0 | 47.3 | 0 | 0 | 47.8 | 48.0944 | 3.7761 | 3.9978 | 3.6737 | 3.9393 | 3.767 | 3.9499 | 6.986 | 7.189 | 7.235 | 7.887 | 6.521 | 7.02 | 6.1953 | 6.2654 | 6.4028 | 5.9587 | 5.9955 | 6.1394 | 0.92885 | 1.0746 | 1.0503 | 1.232 | 1.1377 | 1.0641 | 6.741 | 6.5291 | 7.0549 | 6.8032 | 6.6635 | 6.6172 | 0.99519 | 1.0285 | 1.0626 | 1.2169 | 1.2157 | 1.1135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 439770 | 757 | 428308 | 809 | 279693.022 | 645.8 | 6.1953 | 6.2654 | 6.4028 | 5.9587 | 5.9955 | 6.1394 | 6.741 | 6.5291 | 7.0549 | 6.8032 | 6.6635 | 6.6172 | 938000 | 1000 | 941000 | 1000 | 1872134 | 4600 | 1877000 | 1867534 | 12.1667 | 6.1595 | 1.0813 | 6.7348 | 1.1054 | 17.55% | 16.41% | 32.1466 | 47.7315 | 3.8507 | 7.1397 | 1884966 | 1870600 | 2252014.6071 | 83.06%
2023-09-23 | 2024 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 335090.89 | 6:30 | 18:42 | 11647.1 | 12136 | 11977.5 | 11992.5 | 12011.2 | 12042 | 12051.3 | 12377.4 | 12129.3 | 12131.5 | 11900.2 | 12138.9 | 11949 | 11886.8 | 11918.8 | 11999.1 | 11838.7 | 11931.3 | 11951.7 | 11997.5 | 11997.8 | 11993.3 | 11752.2 | 11907.6 | 11775 | 10457.6 | 11818.3 | 11778 | 12026 | 11796.4 | 11596.5 | 12008.2 | 12082.6 | 12116.3 | 12089 | 12019.5 | 12102.9 | 11916.7 | 11842.3 | 11895.9 | 12361.8 | 11488.8 | 12254.6 | 11329.4 | 11902.3 | 12860.6 | 11221.3 | 12379.7 | 11137.9 | 11443.7 | 12043.5 | 11469.5 | 12385.2 | 11233.1 | 12313.5 | 11176.9 | 11202.2 | 12484.3 | 11230.8 | 12492.7 | 12433.2 | 11262.3 | 12238.4 | 11711.3 | 11806.2 | 11163.5 | 11830.4 | 12185.8 | 12560.3 | 11389.4 | 12368.9 | 10884.6 | 12135.7 | 11852.4 | 11262.3 | 12304.7 | 11020.2 | 12465.2 | 10677.1 | 11709.7 | 11380.3 | 12055.4 | 11444.1 | 12520.8 | 11402.1 | 12038.8 | 11276.9 | 9988.3 | 12264.5 | 11701.2 | 11228.4 | 12662.8 | 12320.9 | 11484.6 | 11349.1 | 12374.5 | 11249.9 | 11618 | 12434.1 | 11135.6 | 12471.7 | 11131 | 12199 | 11379.6 | 12129.8 | 10705.5 | 12175.1 | 11192.2 | 12011.9 | 11086.4 | 12131.8 | 11257.8 | 11152.3 | 12140.4 | 11309.9 | 11094 | 12163.6 | 12284.7 | 12091.5 | 11294 | 12198.5 | 11155.7 | 11850.4 | 11129 | 11719.4 | 10421.3 | 12021.3 | 11159.5 | 11383.7 | 11376.2 | 11161.3 | 9725.6 | 11152.3 | 9873.4 | 11072.8 | 11055.9 | 12373 | 11114.4 | 12304.4 | 11257.6 | 12344 | 11163.6 | 11416.6 | 11204.8 | 12134.1 | 12315.5 | 12297.3 | 12204.7 | 12240.2 | 12295.1 | 11293 | 12236 | 12472.8 | 12506.8 | 12666.7 | 12631.2 | 12564.2 | 11511.5 | 12473.7 | 11521.4 | 32.9827 | 32.9733 | 34.1127 | 32.823 | 32.6829 | 33.2641 | 0 | 48.3 | 0 | 0 | 49.1 | 48.4882 | 3.6449 | 4.0143 | 3.5752 | 3.9399 | 3.8297 | 3.7841 | 6.893 | 7.019 | 6.88 | 6.9 | 6.765 | 7.123 | 6.3285 | 6.3503 | 6.0905 | 6.0259 | 6.0796 | 5.924 | 0.95635 | 1.0919 | 1.0048 | 1.2633 | 1.1611 | 1.0293 | 6.9084 | 6.6577 | 6.7428 | 6.8933 | 6.7839 | 6.4176 | 1.0241 | 1.0445 | 1.0163 | 1.2476 | 1.2414 | 1.0764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440715 | 759 | 429239 | 811 | 281562.955 | 650.467 | 6.3285 | 6.3503 | 6.0905 | 6.0259 | 6.0796 | 5.924 | 6.9084 | 6.6577 | 6.7428 | 6.8933 | 6.7839 | 6.4176 | 945000 | 2000 | 931000 | 2000 | 1869933 | 4667 | 1872000 | 1865266 | 12.2 | 6.1331 | 1.0845 | 6.734 | 1.1084 | 17.68% | 16.46% | 33.1398 | 48.6294 | 3.798 | 6.93 | 1882984.7 | 1868400 | 2243910.5045 | 83.27%
2023-09-24 | 2024 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 335090.89 | 6:34 | 18:40 | 9709.7 | 10137.4 | 10180 | 10143.4 | 10387.8 | 10331.8 | 10089.9 | 10366 | 10037.1 | 10078.3 | 9883.5 | 10006.7 | 10009.4 | 9890.7 | 10284.9 | 10211.2 | 10243.4 | 10239.4 | 10112.6 | 10134.1 | 10163 | 10156.3 | 10061.8 | 10094.2 | 9832.8 | 8796.1 | 9901.4 | 9889.4 | 10119.4 | 10072.9 | 9871 | 10051.6 | 9999.9 | 10012.8 | 9992.8 | 9923.5 | 10083.9 | 9994.2 | 10032.5 | 9957.1 | 10923.8 | 10096.9 | 10814.2 | 9877.5 | 10563.6 | 11361.2 | 10029.8 | 10926.8 | 9306 | 9521.4 | 10033.7 | 9581.1 | 10322.6 | 9456.6 | 10238.6 | 9336 | 9202 | 10256.9 | 9281.8 | 10193.4 | 10092.2 | 9239.8 | 10028.8 | 9711.3 | 9744.9 | 9327.7 | 9779.1 | 10183 | 10362.3 | 9587.2 | 10376.6 | 9299.6 | 10016.8 | 10093.1 | 9434.6 | 10531.6 | 9486.4 | 10493.1 | 9546.3 | 10484.8 | 9605.7 | 10229.2 | 9825.9 | 10464.5 | 9528.8 | 10067.9 | 9433.2 | 8399.5 | 10163.3 | 9770.5 | 9177.6 | 10305.8 | 10093.5 | 9505.5 | 9492.6 | 10106.7 | 9198.5 | 9478.9 | 10222 | 9095.4 | 10321.2 | 9121.5 | 10073.3 | 9327.9 | 10100.3 | 8847.5 | 10163.8 | 9297.8 | 9996 | 9189.2 | 10007.1 | 9295.1 | 9148.2 | 10006.3 | 9238 | 9059.5 | 10073.5 | 10090.2 | 10035.7 | 9244.1 | 10068.6 | 9168.8 | 9853.9 | 9240.7 | 9711.4 | 8670.5 | 9913.9 | 9177.6 | 9434.9 | 9553 | 9146 | 8003 | 9467.2 | 8497.9 | 9893.8 | 9941.9 | 11081.9 | 10032.5 | 11031.4 | 10143.9 | 11086.3 | 10065.5 | 10268.1 | 10120.8 | 10613.9 | 10772.7 | 10974.3 | 10935.9 | 10969.9 | 11016.2 | 10118.9 | 10850.1 | 10526.9 | 10555.9 | 10514.3 | 10559 | 10632.9 | 9823 | 10843.5 | 9953.8 | 33.2142 | 33.2002 | 33.3963 | 33.1562 | 32.9293 | 33.6192 | 0 | 45.9157 | 0 | 0 | 45.8 | 46.835 | 4.2062 | 4.2365 | 4.0678 | 4.1239 | 4.0687 | 4.0267 | 7.617 | 7.672 | 8.147 | 7.503 | 7.921 | 7.993 | 5.3418 | 5.461 | 5.5316 | 5.0415 | 5.0051 | 5.3936 | 0.77935 | 0.96471 | 0.91659 | 1.0356 | 0.97882 | 0.9644 | 5.8241 | 5.8278 | 6.0384 | 5.7442 | 5.5247 | 5.7891 | 0.84355 | 0.92117 | 0.93943 | 1.0212 | 1.0522 | 1.0151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 441513 | 761 | 430027 | 813 | 283143 | 655.133 | 5.3418 | 5.461 | 5.5316 | 5.0415 | 5.0051 | 5.3936 | 5.8241 | 5.8278 | 6.0384 | 5.7442 | 5.5247 | 5.7891 | 798000 | 2000 | 788000 | 2000 | 1580045 | 4666 | 1582000 | 1575379 | 12.1 | 5.2958 | 0.93991 | 5.7914 | 0.96543 | 17.75% | 16.67% | 33.2526 | 46.1836 | 4.1216 | 7.8088 | 1590662.9 | 1578733 | 1945731.7684 | 81.14%
2023-09-25 | 2024 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 335090.89 | 6:30 | 18:38 | 11538.4 | 11999.6 | 11957.8 | 11970.2 | 11989.1 | 12068.1 | 12035.7 | 12389.4 | 11948.3 | 11984.6 | 11844.9 | 11981.7 | 12013.2 | 11915.5 | 12012.5 | 12068.1 | 11978.2 | 12044.6 | 12014.8 | 12079.7 | 12047.8 | 12047.6 | 11895.9 | 11978.1 | 11796.8 | 10484.6 | 11829.4 | 11817.2 | 12081.3 | 12012.7 | 11828.8 | 12029.5 | 12181.3 | 12230.6 | 12213.3 | 12154.7 | 12102.2 | 12024.7 | 12079.9 | 11964.6 | 12757.5 | 11792.6 | 12617.1 | 11623.3 | 12243.9 | 13253.3 | 11595 | 12746.5 | 11238.3 | 11520.3 | 12127.1 | 11548.9 | 12415 | 11338 | 12327 | 11209.9 | 11166.3 | 12474.8 | 11241.8 | 12440.8 | 12341.2 | 11187.9 | 12174.5 | 11707.7 | 11828.4 | 11211.6 | 11799 | 12166.4 | 12419.9 | 11412.6 | 12312.6 | 11010 | 12030.5 | 11899.2 | 11256.9 | 12335.4 | 11120.8 | 12441.5 | 11217.7 | 12280.2 | 11482.8 | 12169.7 | 11617.3 | 12509.6 | 11457.7 | 12081.8 | 11336.8 | 10049.6 | 12088.6 | 11683.9 | 11093.4 | 12471.8 | 12192.7 | 11446.7 | 11327.6 | 12227.1 | 11166.5 | 11547.7 | 12316.2 | 11069.2 | 12439.3 | 11073.5 | 12217.8 | 11371.5 | 12292.5 | 10759 | 12360 | 11368.9 | 12258.1 | 11341.2 | 12349.2 | 11558.4 | 11136.2 | 12133.7 | 11354.2 | 11141.3 | 12260.2 | 12407 | 12211.6 | 11417.9 | 12367.5 | 11336.9 | 12068.2 | 11425.3 | 12003.4 | 10637.3 | 12189.9 | 11352 | 11477.6 | 11456.7 | 11336.7 | 9785.4 | 11264.9 | 9946.9 | 11345.4 | 11326 | 12730.7 | 11472.2 | 12803.5 | 11708.4 | 12684.5 | 11546.5 | 11709.3 | 11520.3 | 12532.6 | 12839.3 | 12785.1 | 12714 | 12723.2 | 12733.6 | 11821.2 | 12761.7 | 12784.8 | 12802 | 12866.9 | 12848.8 | 12861.4 | 11772.6 | 12865.8 | 11880.6 | 32.6617 | 32.5564 | 32.7848 | 32.5093 | 32.2826 | 32.9305 | 0 | 47.9 | 0 | 0 | 48.2 | 48.3693 | 3.5756 | 3.9304 | 3.5921 | 3.8768 | 3.7099 | 3.8529 | 6.833 | 7.299 | 7.71 | 7.682 | 7.102 | 7.903 | 6.2842 | 6.2774 | 6.2511 | 6.0119 | 6.0432 | 6.1238 | 0.97505 | 1.1282 | 1.0728 | 1.3048 | 1.1943 | 1.1031 | 6.889 | 6.8388 | 6.9492 | 0 | 6.6161 | 6.6825 | 1.0483 | 1.0746 | 1.0852 | 1.2903 | 1.2772 | 1.1546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 442464 | 762 | 430971 | 814 | 285031.7 | 659.867 | 6.2842 | 6.2774 | 6.2511 | 6.0119 | 6.0432 | 6.1238 | 6.889 | 6.8388 | 6.9492 | 0 | 6.6161 | 6.6825 | 951000 | 1000 | 944000 | 1000 | 1888700 | 4734 | 1893000 | 1883966 | 12.1333 | 6.1652 | 1.1297 | 6.7951 | 1.155 | 18.32% | 17% | 32.6209 | 48.1564 | 3.7563 | 7.4215 | 1902344.1 | 1887200 | 2264133.0783 | 83.35%
2023-09-26 | 2024 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 335090.89 | 6:32 | 18:35 | 8809.4 | 9426.7 | 9534.3 | 9400.3 | 9702.8 | 9793.9 | 9601 | 10158 | 9427.5 | 9187 | 9561.2 | 9628 | 9857.3 | 9718.1 | 10032.9 | 10047 | 10066.9 | 10206 | 10229.9 | 10160.6 | 10340 | 10314.7 | 10123.5 | 10239.3 | 10042.1 | 8776.7 | 9966 | 10095.7 | 10401.8 | 10203 | 9855.5 | 10280.4 | 9952.6 | 10066.6 | 10247.6 | 10093.7 | 10176.6 | 10020.8 | 10055.2 | 9918.9 | 11176 | 10155.7 | 11009.6 | 9958 | 10496.3 | 11490.6 | 9719.7 | 10986.1 | 8958.3 | 9141.5 | 9864.6 | 9199 | 10296.2 | 9168.7 | 10094 | 9142.4 | 8710.6 | 9993.4 | 8885.7 | 9922.3 | 9820.6 | 8840.3 | 9644.6 | 9097.5 | 9503.4 | 9147.9 | 9426.3 | 10143.7 | 10021.6 | 9193.2 | 9863.8 | 8756.9 | 9549.1 | 9413.7 | 8737.2 | 9828.9 | 8566.6 | 9875.7 | 8643.2 | 9749.7 | 9544.5 | 10163.5 | 9606.1 | 10622.7 | 9454.5 | 10050.6 | 9211.7 | 8200.9 | 9811.2 | 9569.9 | 8783.3 | 10124.7 | 9850.2 | 9085.2 | 8996.4 | 9882 | 8685.1 | 9019.7 | 9885.1 | 8623.5 | 9922.6 | 8610.8 | 9654.7 | 8788.6 | 9788.9 | 8290.6 | 9767.5 | 8691.2 | 9659.4 | 8772 | 9742.8 | 8887.2 | 8649.1 | 9420.6 | 8647.1 | 8429.5 | 9482.6 | 9607 | 9425 | 8688.3 | 9637 | 8655 | 9323.4 | 8749.2 | 9397.2 | 8255.8 | 9509.9 | 8756.2 | 8800.3 | 8819.8 | 8815.4 | 7552.7 | 8844.3 | 7862.9 | 9348 | 9430.9 | 11139.2 | 9674.7 | 11306.6 | 10005.4 | 11078.7 | 9932.5 | 10024.7 | 9736.8 | 10905 | 11215.3 | 11087.2 | 11142.4 | 11219.7 | 11194.8 | 10271.3 | 11222.6 | 10752.5 | 10926.1 | 11213.6 | 11177.7 | 11120 | 9952.9 | 11088.1 | 10062.7 | 34.2117 | 34.0289 | 34.1226 | 34.0486 | 34.165 | 34.4321 | 0 | 47.8 | 0 | 0 | 45.9 | 48.6805 | 2.6807 | 2.7657 | 2.7779 | 2.722 | 2.7089 | 2.6596 | 7.462 | 6.707 | 6.506 | 7.076 | 5.196 | 5.974 | 5.0759 | 5.4458 | 5.3418 | 4.8106 | 4.5969 | 5.3525 | 0.77749 | 0.98861 | 0.89221 | 1.0239 | 0.88668 | 0.98476 | 5.4697 | 5.7929 | 5.8218 | 5.4301 | 0 | 5.7405 | 0.83431 | 0.94137 | 0.92182 | 1.0095 | 0.96253 | 1.0381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 443245 | 764 | 431740 | 816 | 286576.5 | 664.6 | 5.0759 | 5.4458 | 5.3418 | 4.8106 | 4.5969 | 5.3525 | 5.4697 | 5.7929 | 5.8218 | 5.4301 | 0 | 5.7405 | 781000 | 2000 | 769000 | 2000 | 1544800 | 4733 | 1546000 | 1540067 | 12.05 | 5.1039 | 0.92561 | 5.651 | 0.95128 | 18.14% | 16.83% | 34.1682 | 47.4602 | 2.7191 | 6.4868 | 1553216.9 | 1542600 | 1883214.2417 | 81.91%
2023-09-27 | 2024 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 335090.89 | 6:36 | 18:34 | 8736.4 | 9183.3 | 9212.7 | 9192.5 | 9293.4 | 9212.2 | 9074.9 | 9335.7 | 9068.9 | 9046.8 | 8778 | 8972.3 | 8848.2 | 8769.2 | 8978.3 | 9018 | 8856.1 | 8838.5 | 8863.8 | 8935.7 | 8810.9 | 8815.6 | 8714.6 | 8761.7 | 8564.1 | 7570.4 | 8685.7 | 8628.9 | 8953.3 | 8901.4 | 8731.8 | 8868.4 | 8811.8 | 8775.9 | 8763.3 | 8734.9 | 8922 | 8858.1 | 8938.8 | 8824.2 | 9734 | 8965 | 9719.9 | 8836.4 | 9317.6 | 10202.8 | 8637.7 | 9668.2 | 8083 | 8302 | 8850 | 8308.8 | 9187.9 | 8220.1 | 8928.9 | 7956.4 | 7946.9 | 9043 | 8072.7 | 9121.9 | 9067.1 | 8125.2 | 8892.9 | 8486.8 | 8467.6 | 7935.6 | 8447.3 | 8727 | 9082.7 | 8082 | 8850.1 | 7769.8 | 8777.6 | 8509.7 | 8113.4 | 9034.2 | 8030.1 | 9210 | 8154.6 | 9090.5 | 8125.4 | 8787.2 | 8237.6 | 9026.9 | 8089.1 | 8613.1 | 7929.7 | 7070.8 | 8668.1 | 8323.9 | 7780.7 | 8941.4 | 8680.8 | 8049.4 | 8016.5 | 8648.9 | 7837.9 | 8111.5 | 8861.4 | 7790.7 | 8790.5 | 7775 | 8627.3 | 7970.7 | 8720 | 7526.4 | 8783.1 | 7966 | 8706.4 | 7988.5 | 8846.1 | 8066.6 | 7797.4 | 8547 | 7955.2 | 7768.9 | 8700.3 | 8679.7 | 8642.8 | 7846.7 | 8684.5 | 7821 | 8515.4 | 7949.1 | 8479.9 | 7391.6 | 8512.6 | 7819.6 | 7820.1 | 7858.2 | 7774.2 | 6720.2 | 7674.1 | 6757.1 | 7479.3 | 7457.2 | 9029.8 | 7830.4 | 8950.9 | 7973 | 8806.1 | 7730.2 | 7798.3 | 7595.7 | 8657.7 | 8895.4 | 8932.7 | 8997.6 | 9061.6 | 9036.8 | 8076.6 | 8929.4 | 8781.2 | 8786.6 | 8712.1 | 8684 | 8744.2 | 7899.5 | 8951.4 | 8004.6 | 33.1688 | 32.7231 | 32.894 | 32.7715 | 32.6441 | 32.7925 | 0 | 43.5 | 0 | 0 | 43.1 | 43 | 2.9393 | 2.8442 | 2.8571 | 2.8237 | 2.8252 | 2.7356 | 11.067 | 11.062 | 10.982 | 12.142 | 10.482 | 11.229 | 4.6802 | 4.5775 | 4.7537 | 4.3346 | 4.1637 | 4.2046 | 0.77532 | 0.72523 | 0.85274 | 0.96681 | 0.6774 | 0.65515 | 4.9902 | 4.8789 | 5.1691 | 4.7301 | 4.7332 | 4.595 | 0.82345 | 0.68868 | 0.84498 | 0.95836 | 0.74232 | 0.69254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 443945 | 765 | 432399 | 818 | 287931.889 | 669.4 | 4.6802 | 4.5775 | 4.7537 | 4.3346 | 4.1637 | 4.2046 | 4.9902 | 4.8789 | 5.1691 | 4.7301 | 4.7332 | 4.595 | 700000 | 1000 | 659000 | 2000 | 1355389 | 4800 | 1356000 | 1350589 | 11.9667 | 4.4524 | 0.77544 | 4.8494 | 0.79172 | 17.42% | 16.33% | 32.8323 | 43.2 | 2.8375 | 11.1607 | 1363683.6 | 1354467 | 1620169.1409 | 83.6%
2023-09-28 | 2024 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 335090.89 | 6:29 | 18:35 | 9542.8 | 9946 | 9878.1 | 9838.7 | 9999 | 10059.6 | 9964.6 | 10378 | 9979.1 | 10072.3 | 9904.3 | 10087 | 6790.4 | 9792 | 9108.6 | 8683.5 | 9851.2 | 9633.6 | 9760.3 | 9812.6 | 7428 | 7466.4 | 9217.2 | 9474.6 | 8814.2 | 7953.2 | 9342.1 | 9198.8 | 9272.5 | 9090 | 8764.3 | 8846.3 | 9359.5 | 9345.1 | 9074.5 | 9010.6 | 9090.3 | 8999 | 9154.7 | 9323.6 | 10536.2 | 9676.4 | 10466.5 | 9571 | 9948.8 | 10814.1 | 9146.6 | 10308.4 | 9316.2 | 9593.8 | 10071.7 | 9338.6 | 10240 | 9219.8 | 10094.7 | 8838.7 | 9294.5 | 10509.1 | 9443.5 | 10563.4 | 10488.7 | 9415.2 | 10235 | 9698 | 9936.3 | 9350.1 | 9936.6 | 10247.1 | 10666.2 | 9461.7 | 10539.8 | 9127.6 | 10182 | 10087.9 | 9368.2 | 10568.7 | 9274.5 | 10515.9 | 9330.2 | 10449 | 9179.5 | 10002.3 | 9149.8 | 10303.1 | 9071.2 | 9663.1 | 9217.8 | 8025.2 | 9959.3 | 9590.7 | 9020.7 | 10382.1 | 10086 | 9218.8 | 9102.6 | 10158.6 | 9141.4 | 9657 | 10551.4 | 9471.9 | 10666.6 | 9429 | 10581.9 | 9803.7 | 10889.4 | 9340.9 | 11054.7 | 10051.5 | 10975.9 | 10127.5 | 11171.5 | 10449.4 | 9651.2 | 10781.5 | 9981.1 | 9794 | 11028.2 | 11185.8 | 11072.1 | 10292 | 11281.5 | 10241.2 | 10962.9 | 10375.6 | 11040.7 | 9731.8 | 11183.2 | 10383.7 | 10193.5 | 10068.7 | 10381.8 | 8784.9 | 9792.6 | 8568.4 | 9368.5 | 9296.9 | 11102.4 | 9695.8 | 11007.7 | 9737.3 | 10759.1 | 9476.4 | 9656.4 | 9427.9 | 10609.6 | 10948.3 | 11046.2 | 11045 | 11030.9 | 11050.1 | 9977.1 | 11021.2 | 10879 | 10892.6 | 10810.3 | 10740 | 10749.8 | 9674.2 | 11155.9 | 9930.3 | 34.7791 | 34.3341 | 34.6079 | 34.5446 | 34.6504 | 34.6651 | 0 | 45.8 | 0 | 0 | 48.2 | 48.0481 | 2.0357 | 2.0123 | 1.9797 | 2.1071 | 2.0665 | 2.1207 | 6.573 | 5.954 | 5.751 | 6.276 | 7.697 | 7.027 | 5.2258 | 4.7103 | 5.036 | 5.0125 | 5.2731 | 5.2716 | 0.84146 | 0.825 | 0.89921 | 1.0953 | 0.97498 | 0.92352 | 5.7 | 5.0952 | 5.5839 | 5.7124 | 6.0906 | 5.7781 | 0.89655 | 0.7842 | 0.88272 | 1.0897 | 1.0517 | 0.96738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 444711 | 767 | 433210 | 819 | 289503.6 | 673.867 | 5.2258 | 4.7103 | 5.036 | 5.0125 | 5.2731 | 5.2716 | 5.7 | 5.0952 | 5.5839 | 5.7124 | 6.0906 | 5.7781 | 766000 | 2000 | 811000 | 1000 | 1571711 | 4467 | 1574000 | 1567244 | 12.1 | 5.0882 | 0.92658 | 5.66 | 0.94538 | 18.21% | 16.7% | 34.5969 | 47.3494 | 2.0537 | 6.5463 | 1580537.1 | 1570533 | 1883820.7176 | 83.37%
2023-09-29 | 2024 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 335090.89 | 6:32 | 18:34 | 11501.8 | 12040.7 | 11967.1 | 11929.5 | 12081.8 | 12144.8 | 12029.2 | 12404.3 | 11908.6 | 11982.4 | 11703.5 | 11893.2 | 11907.6 | 11785.2 | 11890.6 | 12000.7 | 11809.6 | 11809.5 | 11746.8 | 11797.2 | 11727.1 | 11728.4 | 11404.7 | 11562 | 11283.9 | 9935.1 | 11391.2 | 11328.2 | 11647.8 | 11574.3 | 11372.8 | 11614.6 | 11687.9 | 11716.7 | 0 | 6710.3 | 11725.9 | 11612 | 11704.2 | 11565.9 | 12415.5 | 11354.3 | 12309.2 | 11098.4 | 11848.9 | 12868.3 | 11145.1 | 12451.5 | 10871 | 11130.7 | 11890.9 | 11069.4 | 12168.2 | 11010 | 11923.7 | 10639.4 | 10662.9 | 12091.7 | 10854.4 | 12107.1 | 12006.4 | 10818.4 | 11801.3 | 11221 | 11380.7 | 10740.6 | 11344.4 | 11855.4 | 12058.9 | 10965.8 | 11962.6 | 10558.3 | 11650.3 | 11512.2 | 10767.5 | 12028.5 | 10633.9 | 12086.5 | 10713.4 | 11911.3 | 11075.2 | 11903.4 | 11238.4 | 12293.2 | 11038.2 | 11765.9 | 10925.2 | 9682.2 | 11824.8 | 11393.1 | 10648.7 | 12191.9 | 11835.9 | 10928.6 | 10808.8 | 11963.4 | 10813.4 | 11259.3 | 12206.7 | 10810.7 | 12272.9 | 10792.1 | 12025.3 | 11095.5 | 12097.2 | 10476.4 | 12168.3 | 11090.8 | 11989.7 | 10984.8 | 12085.3 | 11238.3 | 10923.2 | 12079.4 | 11137 | 10896.2 | 12155.5 | 12314.4 | 12091.2 | 11182 | 12267.1 | 11077.9 | 11885.5 | 11116.9 | 11791.2 | 10357.2 | 12050.2 | 11128.1 | 11340.6 | 11350.4 | 11116.9 | 9645.1 | 11113.6 | 9844.3 | 11121 | 11102.1 | 12765.3 | 11346.1 | 12831.6 | 11600.4 | 12755.7 | 11423 | 11615.2 | 11322.5 | 12534.8 | 12859.4 | 12688.4 | 12693.8 | 12704.1 | 12712.2 | 11678.9 | 12746.7 | 12506.2 | 12596.7 | 12797.2 | 12785.9 | 12800.3 | 11732.1 | 12689.6 | 11670.4 | 35.5047 | 35.2115 | 35.4515 | 35.3005 | 35.4447 | 35.5655 | 0 | 49.7526 | 0 | 0 | 50.8 | 50.9 | 2.4096 | 2.2716 | 2.2978 | 2.4404 | 2.4205 | 2.3995 | 5.652 | 6.127 | 5.342 | 6.09 | 6.253 | 5.372 | 6.2132 | 6.024 | 6.0173 | 5.7488 | 5.8726 | 6.1095 | 1.0056 | 1.0924 | 1.0981 | 1.3067 | 1.1302 | 1.1225 | 6.8158 | 6.5721 | 6.7271 | 6.5732 | 6.8614 | 6.7892 | 1.0701 | 1.0384 | 1.077 | 1.2993 | 1.2178 | 1.1743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 445619 | 768 | 434139 | 821 | 291333.956 | 678.333 | 6.2132 | 6.024 | 6.0173 | 5.7488 | 5.8726 | 6.1095 | 6.8158 | 6.5721 | 6.7271 | 6.5732 | 6.8614 | 6.7892 | 908000 | 1000 | 929000 | 2000 | 1830356 | 4466 | 1834000 | 1825890 | 12.0333 | 5.9976 | 1.1259 | 6.7231 | 1.1461 | 18.77% | 17.05% | 35.4131 | 50.4842 | 2.3732 | 5.806 | 1843422.2 | 1829467 | 2199692.8489 | 83.17%
2023-09-30 | 2024 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 335090.89 | 6:32 | 18:29 | 10337 | 10702.5 | 10583.5 | 10586.9 | 10637.1 | 10646.5 | 10578.4 | 10991.2 | 10757.5 | 10942.1 | 10520.8 | 10771 | 10552.5 | 10578.2 | 10416.4 | 10563.7 | 10383.4 | 10500.9 | 10567.4 | 10611.7 | 10526.3 | 10538.2 | 10236.9 | 10391.5 | 10201.3 | 9001.7 | 10360.3 | 10282.5 | 10498.1 | 10311.5 | 10049.1 | 10385.6 | 10378.4 | 10431.2 | 10412.1 | 10307 | 10416.8 | 10262.1 | 10304 | 10240.3 | 11265.5 | 10149 | 11151.1 | 9970.6 | 10599.4 | 11607.9 | 9909.3 | 11245.2 | 9807.3 | 10075.5 | 10737.1 | 10053.8 | 11037 | 9834.9 | 10930.8 | 9655.1 | 9749 | 11109.4 | 9872.8 | 11147.3 | 11089 | 9885.5 | 10821.1 | 10222.6 | 10212 | 9731.4 | 10305.6 | 10779.9 | 11073.4 | 9924.6 | 10897.7 | 9548.7 | 10607.1 | 10412.4 | 9756.4 | 10937.4 | 9596.1 | 11111.2 | 9757 | 10937.5 | 9967.9 | 10796.9 | 10121.3 | 11191.9 | 9954.9 | 10654.1 | 9865.9 | 8739.3 | 10779.2 | 10334.2 | 9665.1 | 11200 | 10800.8 | 9859.9 | 9712.5 | 10923.7 | 9746.5 | 10164.6 | 11079 | 9673.2 | 11107.3 | 9655.5 | 10774.1 | 9888.2 | 10847.8 | 9294.2 | 10889.2 | 9798.6 | 10711.4 | 9732.4 | 10805.4 | 9890.5 | 9703.7 | 10717.3 | 9830.8 | 9615.5 | 10829 | 10939.8 | 10738.6 | 9830.6 | 10886 | 9707.7 | 10521 | 9766.5 | 10370.6 | 9035.4 | 10608 | 9754.7 | 9917.1 | 9913.6 | 9764.3 | 8451.1 | 9660.9 | 8518.8 | 9495.7 | 9466.9 | 10997.8 | 9604 | 11032.9 | 9788.1 | 10928.5 | 9686.1 | 9852.9 | 9663.8 | 10613.1 | 10947.7 | 10823.9 | 10854.5 | 10910.4 | 10936.5 | 9908 | 10913.4 | 10610.9 | 10704.5 | 10791.3 | 10766 | 10770.1 | 9759.6 | 10858.7 | 9797.2 | 34.3131 | 33.9505 | 33.9769 | 33.9582 | 33.9556 | 34.0981 | 0 | 46 | 0 | 0 | 45.9 | 45.8 | 2.9101 | 2.7474 | 2.81 | 2.8823 | 2.8118 | 2.7522 | 6.094 | 5.28 | 5.192 | 5.456 | 5.063 | 5.506 | 5.4904 | 5.2949 | 5.2939 | 5.161 | 5.0947 | 5.0829 | 0.9223 | 0.96658 | 0.99564 | 1.1927 | 1.0199 | 0.909 | 5.9909 | 5.7613 | 5.8801 | 5.8718 | 5.911 | 5.5855 | 0.98138 | 0.91564 | 0.97454 | 1.1868 | 1.087 | 0.95321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 446452 | 770 | 434954 | 823 | 292976.823 | 682.933 | 5.4904 | 5.2949 | 5.2939 | 5.161 | 5.0947 | 5.0829 | 5.9909 | 5.7613 | 5.8801 | 5.8718 | 5.911 | 5.5855 | 833000 | 2000 | 815000 | 2000 | 1642867 | 4600 | 1644000 | 1638267 | 11.95 | 5.2363 | 1.001 | 5.8335 | 1.0164 | 19.12% | 17.42% | 34.0421 | 45.9 | 2.819 | 5.4318 | 1653467.2 | 1641134 | 1937066.0059 | 84.72%
2023-10-01 | 2024 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 335090.89 | 6:33 | 18:32 | 10564.9 | 11100 | 11030.2 | 10966.2 | 11153.5 | 11285.6 | 11095.6 | 11545.8 | 11033.4 | 11015.3 | 10887.6 | 11065.6 | 11148.1 | 10992.8 | 11188.3 | 11240.9 | 11123.5 | 11185.7 | 11163.1 | 11198.8 | 11208.2 | 11182.9 | 10950.6 | 11101.9 | 10864.3 | 9545.4 | 10922.8 | 10898.3 | 11204.4 | 11039.8 | 10806.1 | 11120.7 | 10988.6 | 11054.4 | 11113.5 | 11047 | 11120.2 | 10972.5 | 11062.8 | 10878.4 | 11929 | 10819.3 | 11767.5 | 10652.9 | 11224.5 | 12302.6 | 10557.3 | 11923.6 | 10171.3 | 10429 | 11210 | 10506.1 | 11557.4 | 10328.2 | 11428.5 | 10168.9 | 10054.9 | 11534.3 | 10118.9 | 11490.4 | 11364.7 | 10103.3 | 11129.1 | 10504.8 | 10635.2 | 10108.4 | 10726.3 | 11183.1 | 11488.2 | 10330 | 11353 | 9932.9 | 10989.5 | 10850.2 | 10116.8 | 11382.6 | 10020.1 | 11506.1 | 10145.3 | 11360.3 | 10354.5 | 11202 | 10480.1 | 11572.6 | 10309.9 | 11004.4 | 10223.3 | 9032.7 | 10993.9 | 10618.6 | 9881.5 | 11383.1 | 11009 | 10115.2 | 10003.5 | 11030.7 | 9795.5 | 10197.1 | 11095.4 | 9701.6 | 11253.3 | 9717.5 | 10999.7 | 9997.6 | 11129.3 | 9492.3 | 11195.8 | 10049.4 | 11071.9 | 10055.5 | 11121.6 | 10198.3 | 9730.9 | 10715.3 | 9902.1 | 9665.5 | 10918.5 | 10997.6 | 10842.9 | 9882.2 | 10929.9 | 9790.1 | 10724.4 | 9988.8 | 10590.6 | 9146.6 | 10700.1 | 9763.7 | 9944.9 | 9919.6 | 9706.8 | 8454.6 | 9744.1 | 8616.2 | 9843.1 | 9831.4 | 11725.9 | 10217.8 | 11729.3 | 10427.8 | 11503.9 | 10166.2 | 10303.9 | 10046.5 | 11507.7 | 11870.6 | 11675.1 | 11672.8 | 11687.9 | 11700.7 | 10600.3 | 11737.5 | 11705 | 11800.7 | 11941.5 | 11909.1 | 11897.9 | 10727.9 | 11792.4 | 10719.4 | 34.4977 | 34.2467 | 34.3608 | 34.2829 | 34.1599 | 34.542 | 0 | 47.8 | 0 | 0 | 46.9 | 47.5367 | 2.5984 | 2.6955 | 2.5786 | 2.6543 | 2.6136 | 2.6403 | 6.401 | 7.064 | 6.09 | 5.948 | 5.595 | 7.507 | 5.7315 | 5.7254 | 5.6447 | 5.4109 | 5.1748 | 5.5078 | 0.94664 | 1.0701 | 1.0394 | 1.2438 | 1.0524 | 1.0766 | 6.2842 | 6.25 | 6.3041 | 6.2091 | 6.0298 | 6.12 | 1.0121 | 1.0188 | 1.0396 | 1.2405 | 1.128 | 1.1241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 447326 | 771 | 435799 | 825 | 294689.3 | 687.533 | 5.7315 | 5.7254 | 5.6447 | 5.4109 | 5.1748 | 5.5078 | 6.2842 | 6.25 | 6.3041 | 6.2091 | 6.0298 | 6.12 | 874000 | 1000 | 845000 | 2000 | 1712477 | 4600 | 1716000 | 1707877 | 11.9833 | 5.5325 | 1.0715 | 6.1995 | 1.0938 | 19.37% | 17.64% | 34.3484 | 47.4122 | 2.6301 | 6.4342 | 1724176.7 | 1710800 | 2023231.3525 | 84.56%
2023-10-02 | 2024 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 335090.89 | 6:35 | 18:33 | 11524.3 | 11966.2 | 11839.8 | 11816.6 | 11901.6 | 12001 | 11944.6 | 12270.8 | 11907.3 | 11922.3 | 11768.4 | 11945.9 | 11945 | 11843.1 | 11931.5 | 12005.3 | 11873.5 | 11962.9 | 11991.1 | 12041.4 | 12003.8 | 12023.2 | 11817.7 | 11930.1 | 11788.9 | 10423 | 11827.6 | 11805 | 12055.9 | 11922.7 | 11787.2 | 12025 | 12153.1 | 12186.4 | 10551.7 | 10507.1 | 12106.4 | 11991 | 12049.8 | 11926.2 | 12716 | 11743.3 | 12567.7 | 11547.5 | 12168.7 | 13126.3 | 11499 | 12675.1 | 11096.6 | 11391.2 | 12067.5 | 11447.6 | 12377.4 | 11182.1 | 12292.7 | 11096.2 | 11064 | 12451.7 | 11103.4 | 12407.7 | 12252.9 | 11060.6 | 12101.3 | 11575 | 11818.8 | 11142.8 | 11767.2 | 12179.5 | 12429.7 | 11379.7 | 12295.3 | 10953 | 11964.5 | 11875.2 | 11116.2 | 12319.3 | 11014.1 | 12425 | 11131.3 | 12293.4 | 11459.5 | 12216.8 | 11571.5 | 12582.7 | 11417.5 | 12073.7 | 11335.8 | 10015.8 | 12151.3 | 11770.1 | 11065.2 | 12562.4 | 12244.6 | 11416.8 | 11286.7 | 12299.4 | 11127.2 | 11611.4 | 12420.8 | 11109.8 | 12474.8 | 11073.9 | 12258.2 | 11375.3 | 12303.3 | 10732.8 | 12376.5 | 11355.4 | 12249.6 | 11284.5 | 12226.2 | 11463.3 | 11156.7 | 12181.4 | 11327.2 | 11083.6 | 12262.4 | 12399.3 | 12205.2 | 11329.2 | 12333.4 | 11232.2 | 12045.5 | 11334.7 | 11962.4 | 10493.8 | 12147.5 | 11254 | 11396.7 | 11373.9 | 11233.8 | 9715.8 | 11130 | 9822.2 | 11089.3 | 11044.6 | 12680.3 | 11329 | 12684.4 | 11556.5 | 12559.8 | 11317.4 | 11508.7 | 11245.1 | 12430.9 | 12693.3 | 12669 | 12622.9 | 12651.3 | 12643.2 | 11631 | 12569.3 | 12589.3 | 12645.1 | 12728.7 | 12706.7 | 12710.5 | 11698.8 | 12738.4 | 11724.7 | 34.3687 | 34.0079 | 34.1527 | 34.1525 | 34.1955 | 34.3038 | 0 | 48.2 | 0 | 0 | 48.5 | 48.6017 | 2.7855 | 2.7646 | 2.7123 | 2.6442 | 2.7563 | 2.6296 | 6.167 | 6.071 | 5.822 | 5.571 | 6.538 | 6.102 | 6.1908 | 6.1716 | 6.0954 | 5.8868 | 6.2289 | 6.0016 | 1.0174 | 1.1886 | 1.1429 | 1.351 | 1.245 | 1.157 | 6.8779 | 6.8373 | 6.9184 | 6.9126 | 6.94 | 6.7406 | 1.0876 | 1.1301 | 1.1435 | 1.3553 | 1.3391 | 1.224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 448269 | 773 | 436738 | 826 | 296564.7 | 691.867 | 6.1908 | 6.1716 | 6.0954 | 5.8868 | 6.2289 | 6.0016 | 6.8779 | 6.8373 | 6.9184 | 6.9126 | 6.94 | 6.7406 | 943000 | 2000 | 939000 | 1000 | 1875400 | 4334 | 1879000 | 1871066 | 11.9667 | 6.0958 | 1.1837 | 6.8711 | 1.2133 | 19.42% | 17.66% | 34.1968 | 48.4339 | 2.7154 | 6.0452 | 1889202.8 | 1873800 | 2233743.8033 | 83.89%
2023-10-03 | 2024 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 335090.89 | 6:33 | 18:31 | 11665.8 | 12080.1 | 11943.2 | 11937.8 | 12000.7 | 12115.4 | 12078.7 | 12411.8 | 12034.3 | 12021.4 | 11888 | 12064.6 | 12059.2 | 11947.2 | 12021.9 | 12112.5 | 11966.1 | 12056.7 | 12087.7 | 12149.2 | 12089.2 | 12117.1 | 11918.9 | 12025.6 | 11901.3 | 10620.2 | 11946.8 | 11918.6 | 12142.4 | 12010.6 | 11888.6 | 12110.2 | 12325.7 | 12369.9 | 12353.9 | 12292.1 | 12192 | 12087.4 | 12135.4 | 12027.2 | 12802.2 | 11880.4 | 12625.1 | 11688.4 | 12262.8 | 13215.5 | 11625.9 | 12763 | 11298 | 11581.9 | 12189.9 | 11615.7 | 12474 | 11359.3 | 12392.2 | 11315 | 11284.7 | 12567.8 | 11330.6 | 12534.7 | 12425.2 | 11038.9 | 12224.7 | 11735.3 | 11958.9 | 11361.3 | 11899.5 | 12291.3 | 12506.2 | 11555.7 | 12389.7 | 11177.9 | 12097.5 | 12011.8 | 11323.8 | 12422.2 | 11225.6 | 12498 | 11328.7 | 12380.3 | 11635 | 12328.2 | 11711.4 | 12662.9 | 11584.3 | 12183.8 | 11502.9 | 10241 | 12246.4 | 11894.9 | 11308.3 | 12634 | 12319.8 | 11573.2 | 11447.4 | 12388.8 | 11344.1 | 11740.4 | 12466.3 | 11310.5 | 12535.3 | 11286.7 | 12343.8 | 11552.4 | 12368.4 | 10937.7 | 12445 | 11525 | 12336.8 | 11468.8 | 12390 | 11667.2 | 11351.4 | 12258.6 | 11497.7 | 11303.7 | 12340 | 12468.5 | 12296.3 | 11526.7 | 12406 | 11440.9 | 12143.5 | 11519.5 | 12073.1 | 10717.8 | 12245.8 | 11486.5 | 11603.7 | 11561.8 | 11455.7 | 9928.3 | 11349.9 | 10020.7 | 11281.5 | 11238.1 | 12750.9 | 11504 | 12738.9 | 11707.3 | 12636.4 | 11492.5 | 11636.5 | 11423.9 | 12523.3 | 12769.5 | 12781.5 | 12700.1 | 12738.8 | 12737.5 | 11778.8 | 12703.8 | 12702.2 | 12736.2 | 12804.7 | 12795.4 | 12805.4 | 11858.2 | 12815.8 | 11863.4 | 34.6652 | 34.3919 | 34.5077 | 34.5793 | 35.028 | 34.6315 | 0 | 47.7676 | 0 | 0 | 48 | 47.6 | 3.4611 | 3.4712 | 3.3925 | 3.3687 | 3.4273 | 3.3541 | 6.595 | 7.678 | 7.417 | 6.252 | 6.299 | 6.815 | 6.2604 | 6.2475 | 6.15 | 5.9638 | 6.3138 | 6.0795 | 1.0303 | 1.2212 | 1.1668 | 1.3768 | 1.2575 | 1.1881 | 6.9786 | 6.9477 | 7.0066 | 7.0347 | 7.0645 | 6.8864 | 1.1002 | 1.1626 | 1.1601 | 1.386 | 1.3573 | 1.2561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 449225 | 774 | 437689 | 828 | 298465 | 696.4 | 6.2604 | 6.2475 | 6.15 | 5.9638 | 6.3138 | 6.0795 | 6.9786 | 6.9477 | 7.0066 | 7.0347 | 7.0645 | 6.8864 | 956000 | 1000 | 951000 | 2000 | 1900300 | 4533 | 1904000 | 1895767 | 11.9667 | 6.1692 | 1.2068 | 6.9864 | 1.237 | 19.56% | 17.71% | 34.6339 | 47.7892 | 3.4125 | 6.8427 | 1913676.4 | 1898800 | 2272177.367 | 83.57%
2023-10-04 | 2024 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 335090.89 | 6:33 | 18:30 | 11841.7 | 12234.8 | 12131 | 12132.2 | 12208.8 | 12289.2 | 12226 | 12555.8 | 12200.7 | 12156.6 | 12039.5 | 12225.3 | 12224.4 | 12112.6 | 12182.2 | 12288.3 | 12134.7 | 12232 | 12241.1 | 12292.1 | 12244.8 | 12270.3 | 12081.8 | 12186.3 | 12052.9 | 10768.2 | 12096.7 | 12067.1 | 12281.8 | 12156.3 | 12039.5 | 12251.8 | 12482.8 | 12536.3 | 12522.6 | 12449.5 | 12325.5 | 12227.9 | 12271.6 | 12166.5 | 12936.6 | 12024.4 | 12778.3 | 11863.4 | 12395.3 | 13348.4 | 11778.6 | 12901 | 11478.7 | 11758.2 | 12342.3 | 11786.3 | 12629.6 | 11548.2 | 12536.1 | 11485.4 | 11462.1 | 12722.9 | 11504.6 | 12682.2 | 12567.8 | 11288.3 | 12382 | 11917.8 | 12081.3 | 11512.1 | 12038.4 | 12416 | 12639.5 | 11697.8 | 12521.5 | 11285.6 | 12234.8 | 12151.1 | 11469.4 | 12551.6 | 11355.4 | 12628.3 | 11459.3 | 12505.3 | 11755.5 | 12428.1 | 11835.8 | 12772.9 | 11700.2 | 12298.6 | 11617.9 | 10338.2 | 12280.6 | 11807.5 | 11427.6 | 12745.7 | 12455.7 | 11703.8 | 11574.9 | 12504.6 | 11455.9 | 11864.3 | 12581.2 | 11437.6 | 12649.2 | 11408.4 | 12461.6 | 11669.7 | 12426.2 | 10977.5 | 12560.5 | 11669.7 | 12418.4 | 11533.4 | 12497.5 | 11824.9 | 11483.3 | 12384.5 | 11629.1 | 11424.7 | 12462.4 | 12597.7 | 12424.4 | 11645.5 | 12526.8 | 11566.4 | 12279.5 | 11663.4 | 12208.6 | 10831.8 | 12372.5 | 11610.5 | 11696.8 | 11650.2 | 11555 | 9991.6 | 11431.6 | 10081.8 | 11425.3 | 11423.6 | 12854.9 | 11620.8 | 12857.3 | 11825.2 | 12755.2 | 11634.3 | 11798.2 | 11574.6 | 12629.7 | 12885.4 | 12871.8 | 12787.8 | 12842.3 | 12837.8 | 11904 | 12807 | 12811.5 | 12831.5 | 12896 | 12893 | 12907.7 | 11966.6 | 12911.6 | 11967.5 | 34.7901 | 34.5508 | 34.5782 | 34.6931 | 34.8656 | 34.9817 | 0 | 48 | 0 | 0 | 48.2 | 48.1 | 3.9823 | 3.9329 | 3.9903 | 3.9383 | 4.1679 | 4.1544 | 6.897 | 6.686 | 6.725 | 6.622 | 7.27 | 7.212 | 6.3072 | 6.2769 | 6.1514 | 5.9153 | 6.0689 | 6.1066 | 1.0306 | 1.233 | 1.1804 | 1.3719 | 1.2473 | 1.2017 | 7.0769 | 7.0179 | 6.9845 | 6.7817 | 6.7269 | 6.956 | 1.1008 | 1.1761 | 1.1799 | 1.3859 | 1.3489 | 1.2672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450194 | 775 | 438648 | 830 | 300386.29 | 700.8 | 6.3072 | 6.2769 | 6.1514 | 5.9153 | 6.0689 | 6.1066 | 7.0769 | 7.0179 | 6.9845 | 6.7817 | 6.7269 | 6.956 | 969000 | 1000 | 959000 | 2000 | 1921290 | 4400 | 1925000 | 1916890 | 11.95 | 6.1377 | 1.2108 | 6.924 | 1.2431 | 19.73% | 17.95% | 34.7432 | 48.1 | 4.0277 | 6.902 | 1934817.4 | 1919933 | 2261252.7301 | 84.91%
2023-10-05 | 2024 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 335090.89 | 6:33 | 18:29 | 11856 | 12229.6 | 12122.7 | 12123.2 | 12209.2 | 12269.6 | 12196.8 | 12519.7 | 12199.2 | 12181.8 | 12052.1 | 12220.4 | 12215.1 | 12114 | 12178.8 | 12277.4 | 12130.7 | 12228.7 | 12244.7 | 12302 | 12243.5 | 12270.4 | 12095.1 | 12192.7 | 12058.6 | 10811.9 | 12092 | 12069.4 | 12278.9 | 12168.4 | 12047 | 12246.4 | 12495.3 | 12550.9 | 12550.5 | 12477.5 | 12304.2 | 12226.1 | 12275.5 | 12181.4 | 12904.9 | 12029.5 | 12744.2 | 11873.9 | 12310.2 | 13262.1 | 11772.1 | 12858.5 | 11516.8 | 11779 | 12332.2 | 11793.6 | 12601.1 | 11543.1 | 12504.8 | 11495 | 11494.2 | 12685.3 | 11558.5 | 12630.8 | 12506 | 11494.2 | 12370.6 | 11939.5 | 12097.6 | 11567.4 | 12066.8 | 12418.8 | 12643.1 | 11728.2 | 12527 | 11364.1 | 12237.9 | 12167.1 | 11461.5 | 12405.4 | 11291.7 | 12560.3 | 11456.5 | 12356.5 | 11776.8 | 12423.1 | 11849.3 | 12764.8 | 11728.9 | 12296.4 | 11631.3 | 10398.3 | 12279.2 | 11722.5 | 11477.4 | 12726.4 | 12439.6 | 11709 | 11583.1 | 12486.4 | 11476.6 | 11878.6 | 12566 | 11466.9 | 12631.6 | 11446.7 | 12398.4 | 11689.6 | 12465.8 | 11092.1 | 12557.3 | 11688.7 | 12455.9 | 11621.2 | 12516.7 | 11858.1 | 11505.4 | 12364.8 | 11648.1 | 11472.7 | 12445.2 | 12580.3 | 12408.3 | 11668.4 | 12519.2 | 11597.9 | 12265 | 11691.5 | 12212.3 | 10915.2 | 12376.2 | 11652.1 | 11714.3 | 11658.2 | 11579.6 | 10022.5 | 11459.1 | 10112.5 | 11429.9 | 11511.6 | 12834.7 | 11651 | 12843.7 | 11845.6 | 12734.1 | 11656 | 11821.3 | 11629.8 | 12630.5 | 12866.7 | 12846.7 | 12768.4 | 12814.7 | 12814.3 | 11926.8 | 12799.5 | 12803 | 12821.1 | 12878.4 | 12871.2 | 12885.2 | 11979.3 | 12894.2 | 11991.5 | 33.59 | 33.48 | 33.53 | 33.39 | 33.11 | 33.83 | 0 | 46.2 | 0 | 0 | 46.55 | 46.51 | 5.1 | 5.21 | 5.11 | 5.2 | 5.25 | 5.28 | 8.62 | 9.03 | 9.34 | 9.3 | 8.43 | 9.18 | 6.26 | 6.23 | 6.1 | 5.87 | 5.99 | 6.06 | 1.03 | 1.23 | 1.18 | 1.37 | 1.25 | 1.2 | 7.02 | 6.95 | 6.95 | 6.72 | 6.64 | 6.91 | 1.1 | 1.17 | 1.18 | 1.39 | 1.35 | 1.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 451163 | 777 | 439608 | 831 | 302308.024 | 705.333 | 6.26 | 6.23 | 6.1 | 5.87 | 5.99 | 6.06 | 7.02 | 6.95 | 6.95 | 6.72 | 6.64 | 6.91 | 969000 | 2000 | 960000 | 1000 | 1921734 | 4533 | 1926000 | 1917201 | 11.9333 | 6.085 | 1.21 | 6.865 | 1.2417 | 19.88% | 18.09% | 33.4883 | 46.42 | 5.1917 | 8.9833 | 1935378.1 | 1920667 | 2268603 | 84.66%
2023-10-06 | 2024 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 335090.89 | 6:34 | 18:28 | 11757.7 | 12122 | 12023.3 | 12017.5 | 12106.5 | 12178.3 | 12104 | 12419.6 | 11777.6 | 11359.8 | 11955.1 | 12127.2 | 12109.7 | 12017.8 | 12101.2 | 12182.3 | 12053 | 12163.2 | 12155.6 | 12207.5 | 12170.6 | 12190 | 12026.3 | 12115.1 | 11961.5 | 10702.7 | 11994.7 | 11974.4 | 12200.9 | 12095.6 | 11981.4 | 12174.7 | 12408.9 | 12481.5 | 12444.2 | 12375.5 | 12228.1 | 12164.3 | 12200.3 | 12097 | 12860.3 | 11952.8 | 12690.5 | 11779.1 | 12345.3 | 13286 | 11739.9 | 12834.9 | 11417.3 | 11667 | 12227 | 11684 | 12509.5 | 11458.9 | 12420.1 | 11423.8 | 11381.4 | 12592.3 | 11454.5 | 12557.2 | 12450.2 | 11391.4 | 12264.9 | 11818.9 | 11971.3 | 11424.2 | 11934 | 12274.5 | 12518.5 | 11597 | 12396.7 | 11242.4 | 12098.8 | 12014.3 | 11372.2 | 12404.7 | 11287.5 | 12494.3 | 11381.2 | 12376 | 11663.3 | 12306.7 | 11727.2 | 12635.2 | 11598.2 | 12173.8 | 11477.3 | 10269.8 | 12220.5 | 11874.5 | 11349.6 | 12618.3 | 12319.7 | 11581.2 | 11457.1 | 12373.8 | 11365.7 | 11758.1 | 12469 | 11351.6 | 12519.6 | 11336.5 | 12337.8 | 11607.3 | 12371.3 | 10998.3 | 12459.7 | 11592.7 | 12367.8 | 11530.6 | 12434.3 | 11764 | 11386.6 | 12254.1 | 11549.1 | 11359.4 | 12344.3 | 12478.8 | 12296.3 | 11568.6 | 12424.1 | 11499.7 | 12156.3 | 11596.3 | 12121.5 | 10827.3 | 12288.2 | 11540.8 | 11579.7 | 11510.9 | 11459.8 | 9904.6 | 11111.3 | 9982.1 | 11459.3 | 11452.2 | 12727.6 | 11554.2 | 12735.2 | 11735 | 12618.1 | 11541.7 | 11706.3 | 11548.6 | 12517.6 | 12775.9 | 12735.8 | 12658.9 | 12691.8 | 12701.8 | 11812.8 | 12686.1 | 12693.9 | 12714.6 | 12784.7 | 12781.4 | 12799.4 | 11875.8 | 12780.3 | 11870.4 | 32.0429 | 32.0565 | 31.9919 | 31.7503 | 31.6079 | 32.2722 | 0 | 44.8 | 0 | 0 | 45.2 | 45 | 5.9134 | 6.0239 | 5.9637 | 6.1953 | 5.7896 | 6.2676 | 9.386 | 9.233 | 9.777 | 9.225 | 9.521 | 9.937 | 6.1164 | 6.1019 | 5.9992 | 5.7375 | 5.8873 | 5.9455 | 0.99888 | 1.2115 | 1.1403 | 1.3341 | 1.2759 | 1.1831 | 6.9074 | 6.8394 | 6.8384 | 6.5782 | 6.5218 | 6.7807 | 1.0725 | 1.1551 | 1.1349 | 1.3482 | 1.3592 | 1.2414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 452123 | 778 | 440559 | 833 | 304213.5 | 710 | 6.1164 | 6.1019 | 5.9992 | 5.7375 | 5.8873 | 5.9455 | 6.9074 | 6.8394 | 6.8384 | 6.5782 | 6.5218 | 6.7807 | 960000 | 1000 | 951000 | 2000 | 1905476 | 4667 | 1908000 | 1900809 | 11.9 | 5.9646 | 1.1906 | 6.7443 | 1.2185 | 19.96% | 18.07% | 31.9536 | 45 | 6.0256 | 9.5132 | 1919031.1 | 1904467 | 2249325.9701 | 84.67%
2023-10-07 | 2024 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 335090.89 | 6:39 | 18:26 | 11483.4 | 11815.8 | 11714 | 11697.3 | 11796.6 | 11840.1 | 11798.1 | 12100.9 | 11803 | 11818.6 | 11653 | 11823.8 | 11787.7 | 11706.9 | 11751.2 | 11851.9 | 11708.1 | 11816.4 | 11815.4 | 11877.5 | 11809.6 | 11841.1 | 11673.9 | 11753.3 | 11640.2 | 10421.8 | 11679.1 | 11653.7 | 11849.8 | 11732.1 | 11612.3 | 11825 | 12086.7 | 12147.3 | 12121.3 | 12043.7 | 11895 | 11789.5 | 11834.5 | 11749.5 | 12430.4 | 11558.1 | 12271 | 11387.4 | 11926.2 | 12821.1 | 11336.9 | 12399.9 | 11124.3 | 11305.9 | 11917.2 | 11373.9 | 12175 | 11142.9 | 12098.3 | 11117.3 | 11092.6 | 12286 | 11162.6 | 12253.8 | 12162.5 | 11111.6 | 11982.3 | 11550.2 | 11707 | 11194 | 11692.7 | 12023.5 | 12253.2 | 11347.9 | 12147.3 | 10975.3 | 11858.7 | 11757.1 | 11134.6 | 12132.4 | 11028 | 12235 | 11128 | 12111.1 | 11377.5 | 12012.6 | 11431.1 | 12341.6 | 11324.6 | 11889.5 | 11232.9 | 10027.8 | 11944.8 | 11644 | 11093.4 | 12319.8 | 12026.6 | 11318.8 | 11202 | 12084.2 | 11117.5 | 11493.7 | 12174.4 | 11086.8 | 12208.9 | 11069.1 | 12014.7 | 11320.1 | 12033.8 | 10700.7 | 12116 | 11282.8 | 12024.2 | 11212.5 | 12090.1 | 11440 | 11110.5 | 11968.4 | 11271.3 | 11069.2 | 12048.8 | 12171.8 | 11999 | 11281.2 | 12114.4 | 11210.3 | 11840.9 | 11282.7 | 11789 | 10544.1 | 11978.6 | 11255.4 | 11324.1 | 11281.7 | 11157.3 | 9673.6 | 11097.1 | 9779.6 | 11038.1 | 11059.8 | 12347.9 | 11205.8 | 12392.8 | 11398.9 | 12257.3 | 11199.4 | 11362.6 | 11198.1 | 12153.9 | 12410.1 | 12379.2 | 12306.1 | 12336.5 | 12347.5 | 11501.9 | 12344.1 | 12312.9 | 12329.2 | 12375.8 | 12374 | 12401.8 | 11517.1 | 12383.6 | 11528.1 | 32.4741 | 32.3206 | 32.3219 | 32.1874 | 31.9798 | 32.6211 | 0 | 45.1 | 0 | 0 | 45.7 | 45.4528 | 6.3617 | 6.5281 | 6.2684 | 6.4157 | 6.1811 | 6.529 | 9.591 | 9.823 | 9.561 | 9.25 | 8.78 | 10.377 | 5.941 | 5.9365 | 5.7757 | 5.7255 | 6.0234 | 5.7611 | 0.94703 | 1.1975 | 1.0703 | 1.3149 | 1.2589 | 1.1571 | 6.7271 | 6.6438 | 6.5862 | 6.8943 | 6.8254 | 6.5672 | 1.0101 | 1.1414 | 1.0708 | 1.3055 | 1.3235 | 1.2145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 453060 | 780 | 441486 | 835 | 306070.157 | 714.667 | 5.941 | 5.9365 | 5.7757 | 5.7255 | 6.0234 | 5.7611 | 6.7271 | 6.6438 | 6.5862 | 6.8943 | 6.8254 | 6.5672 | 937000 | 2000 | 927000 | 2000 | 1856657 | 4667 | 1860000 | 1851990 | 11.7833 | 5.8605 | 1.1576 | 6.7073 | 1.1776 | 19.75% | 17.56% | 32.3175 | 45.4176 | 6.3807 | 9.5637 | 1869900.3 | 1855667 | 2231317.7012 | 83.16%
2023-10-08 | 2024 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 335090.89 | 6:36 | 18:25 | 11498.4 | 11888.4 | 11795.2 | 11784.6 | 11886 | 11935.1 | 11863.9 | 12193 | 11864.7 | 11862.8 | 11723.9 | 11889.6 | 11862.9 | 11796.1 | 11862 | 11944 | 11813.9 | 11917.6 | 11912.6 | 11970 | 11917.7 | 11937.8 | 11765.5 | 11853.6 | 11714.6 | 10410.7 | 11749.6 | 11728.4 | 11956 | 11848.1 | 11700 | 11917.6 | 12123.8 | 12189.3 | 12151.7 | 12074.6 | 12010.2 | 11916.8 | 11954.7 | 11849.7 | 12583.2 | 11632.8 | 12420.1 | 11463 | 12046 | 13023.2 | 11395.5 | 12548 | 11122.4 | 11363.7 | 12011.1 | 11421.9 | 12307 | 11192.6 | 12208.7 | 11118.8 | 11074.6 | 12394.7 | 11148.6 | 12347.6 | 12241.5 | 11113.9 | 12049.1 | 11560.7 | 11745.1 | 11155.2 | 11720.9 | 12066.1 | 12339.8 | 11324.4 | 12206.3 | 10911.2 | 11911 | 11807.8 | 11103.7 | 12231.1 | 10985.2 | 12315.5 | 11087.1 | 12172 | 11338.3 | 12064.6 | 11388.3 | 12404 | 11265 | 11884.3 | 11193.9 | 9919.2 | 11993.1 | 11658 | 11049.5 | 12418.9 | 12117.5 | 11352.9 | 11237.9 | 12182.2 | 11116.8 | 11510.2 | 12264.1 | 11050.6 | 12329.8 | 11018.2 | 12115.5 | 11311.5 | 12147.1 | 10673.6 | 12225.7 | 11291.9 | 12115.4 | 11220 | 12198.3 | 11467.6 | 11100.3 | 12042.4 | 11277 | 11044.8 | 12127.9 | 12245.5 | 12073.5 | 11259.3 | 12188.1 | 11177.9 | 11910.2 | 11296.3 | 11851.8 | 10486.2 | 12027.7 | 11211.2 | 11330.2 | 11316.4 | 11163.7 | 9654.7 | 11092 | 9754.1 | 11123.5 | 11129.6 | 12542.3 | 11278.2 | 12567.7 | 11488.5 | 12468.2 | 11310.3 | 11492.1 | 11261.2 | 12311.4 | 12591 | 12545.2 | 12469.4 | 12513.1 | 12533 | 11575.6 | 12504.1 | 12520.2 | 12547 | 12594.7 | 12584.5 | 12606.7 | 11620.9 | 12565.4 | 11634.8 | 32.948 | 32.7063 | 32.6586 | 32.6828 | 32.4926 | 33.0329 | 0 | 45 | 0 | 0 | 45.3 | 45.2121 | 6.2644 | 6.1933 | 6.2298 | 6.2562 | 6.0943 | 6.3444 | 10.751 | 10.06 | 10.415 | 9.962 | 10.094 | 9.591 | 5.9207 | 5.9052 | 5.7912 | 5.6893 | 5.9941 | 5.7728 | 0.98536 | 1.1882 | 1.1125 | 1.3384 | 1.2454 | 1.1467 | 6.7023 | 6.6447 | 6.6279 | 6.8302 | 6.8374 | 6.5978 | 1.0463 | 1.1291 | 1.0987 | 1.3298 | 1.3109 | 1.2045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 454001 | 781 | 442419 | 836 | 307937.491 | 719.267 | 5.9207 | 5.9052 | 5.7912 | 5.6893 | 5.9941 | 5.7728 | 6.7023 | 6.6447 | 6.6279 | 6.8302 | 6.8374 | 6.5978 | 941000 | 1000 | 933000 | 1000 | 1867334 | 4600 | 1872000 | 1862734 | 11.8167 | 5.8456 | 1.1694 | 6.7067 | 1.1865 | 20.01% | 17.69% | 32.7535 | 45.1707 | 6.2304 | 10.1455 | 1880439.9 | 1866600 | 2229360.0153 | 83.73%
2023-10-09 | 2024 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 335090.89 | 6:36 | 18:24 | 11308.8 | 11691.5 | 11616 | 11602.8 | 11699.7 | 11759.7 | 11658.4 | 12016.2 | 11678.7 | 11698.6 | 11550.7 | 11702 | 11680 | 11618.7 | 11694.3 | 11765.3 | 11646.4 | 11751.2 | 11732.4 | 11782 | 11746 | 11758.4 | 11588.3 | 11674 | 11517.7 | 10204.1 | 11557.7 | 11534 | 11768 | 11678.9 | 11531.6 | 11737.9 | 11878.9 | 11942.9 | 11916.8 | 11833.1 | 11809.8 | 11722.9 | 11763.7 | 11653.8 | 12443.4 | 11478.5 | 12288.1 | 11316.7 | 11883.5 | 12858.7 | 11234.1 | 12421.7 | 10895.3 | 11181.3 | 11809.5 | 11215.3 | 12118.6 | 10980.3 | 12017.9 | 10911.7 | 10864 | 12215.4 | 10925 | 12160.8 | 12048.8 | 10898.3 | 11860.9 | 11360.7 | 11565.8 | 10971.5 | 11538.5 | 11917.3 | 12164.8 | 11164.7 | 12036.6 | 10742.7 | 11715 | 11613.9 | 10898.7 | 12047.2 | 10785.7 | 12129.1 | 10908 | 12007.1 | 11218.4 | 11968.8 | 11298.6 | 12291.5 | 11106.1 | 11677.8 | 11069.4 | 9828 | 11873.8 | 11522.2 | 10872.4 | 12247.4 | 11931.6 | 11129.7 | 11010.5 | 12001.6 | 10908.9 | 11328.8 | 12111.2 | 10872.8 | 12176.8 | 10853.2 | 11960.5 | 11125.8 | 11992.1 | 10502.2 | 12056.2 | 11110.4 | 11950.2 | 11035.3 | 12028.3 | 11275.2 | 10938.9 | 11891.3 | 11107.8 | 10890.6 | 11978.5 | 12102.9 | 11917.1 | 11110.3 | 12040.2 | 11014 | 11749.3 | 11115.7 | 11690 | 10323.3 | 11873.3 | 11050.9 | 11135.4 | 11109.1 | 11006.1 | 9493.5 | 10928.5 | 9617.5 | 10959 | 10955.1 | 12382.5 | 11090 | 12422.7 | 11331.6 | 12287.5 | 11115.9 | 11301.9 | 11060.2 | 12138.9 | 12421.7 | 12377.5 | 12298.1 | 12343 | 12371.2 | 11414.9 | 12352.5 | 12324.3 | 12358.2 | 12404.5 | 12403 | 12436.3 | 11451.7 | 12406.6 | 11457.5 | 32.5906 | 32.4523 | 32.4274 | 32.2872 | 32.1079 | 32.711 | 0 | 44.7 | 0 | 0 | 44.9977 | 44.8923 | 6.3621 | 6.3938 | 6.3351 | 6.3764 | 6.2902 | 6.5103 | 10.477 | 9.493 | 10.826 | 10.451 | 9.486 | 9.97 | 5.8749 | 5.7795 | 5.6837 | 5.5694 | 5.8802 | 5.9815 | 0.97322 | 1.1545 | 1.1027 | 1.3211 | 1.2222 | 1.1318 | 6.6639 | 6.5066 | 6.5117 | 6.6697 | 6.7161 | 6.6381 | 1.0389 | 1.0957 | 1.0995 | 1.3142 | 1.2833 | 1.1874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 454928 | 783 | 443337 | 838 | 309776.558 | 723.933 | 5.8749 | 5.7795 | 5.6837 | 5.5694 | 5.8802 | 5.9815 | 6.6639 | 6.5066 | 6.5117 | 6.6697 | 6.7161 | 6.6381 | 927000 | 2000 | 918000 | 2000 | 1839067 | 4666 | 1841000 | 1834401 | 11.8 | 5.7949 | 1.1509 | 6.6177 | 1.1698 | 19.86% | 17.68% | 32.4294 | 44.8633 | 6.378 | 10.1172 | 1852353.2 | 1838467 | 2206329.9557 | 83.33%
2023-10-10 | 2024 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 335090.89 | 6:37 | 18:23 | 11171.9 | 11589.4 | 11635.3 | 11631.7 | 11686.3 | 11784.8 | 11701 | 12062.6 | 11745.7 | 11760.8 | 11621.5 | 11783.1 | 11717.3 | 11678.8 | 11695.9 | 11795.5 | 11667.5 | 11777.7 | 11768.7 | 11811.2 | 11771 | 11787.8 | 11591.9 | 11692.7 | 11531.1 | 10161.9 | 11587.6 | 11545.6 | 11800.5 | 11700.2 | 11542.9 | 11767.8 | 11842.8 | 11908.8 | 11867.3 | 11786.6 | 11851.4 | 11755 | 11803.5 | 11683.8 | 12533.5 | 11488.6 | 12367.7 | 11289.4 | 11885.3 | 12909.2 | 11198.1 | 12500.2 | 10870.4 | 11174 | 11856.4 | 11186.6 | 12158.1 | 10919.1 | 12073.5 | 10850.1 | 10851.6 | 12290.6 | 10925.1 | 12262.9 | 12147.6 | 10903.1 | 11917.1 | 11382.3 | 11569.4 | 10916.9 | 11560.7 | 11957.5 | 12242.7 | 11130.3 | 12105.6 | 10705.6 | 11788.1 | 11671 | 10898.8 | 12139.9 | 10783.2 | 12231.7 | 10893.1 | 12086.1 | 11212.3 | 12020 | 11272.3 | 12365.3 | 11127.9 | 11834.3 | 11057.8 | 9785.1 | 11890.6 | 11523.8 | 10807.5 | 12290.5 | 11977.4 | 11092.8 | 10960.2 | 12022.2 | 10853.5 | 11323 | 12162.9 | 10835.7 | 12236.9 | 10804.1 | 11961.7 | 11055.3 | 12049.2 | 10469 | 12118.9 | 11062.4 | 11997.4 | 10988.2 | 12058.8 | 11224.2 | 10881.9 | 11915.4 | 11038.2 | 10763.6 | 11995.3 | 12134.7 | 11921.8 | 11054.6 | 12056.4 | 10932 | 11748.6 | 11031.5 | 11665.5 | 10228.4 | 11853.6 | 10955.4 | 11077.8 | 11061 | 10927.7 | 9435.9 | 10865.5 | 9592.4 | 10903 | 10887 | 12467.3 | 11085.2 | 12514.2 | 11341 | 12361.7 | 11095.1 | 11295.5 | 11027.7 | 12185.4 | 12491.5 | 12414.6 | 12337.4 | 12400.4 | 12439.7 | 11422.5 | 12410.2 | 12420.1 | 12464.3 | 12553.7 | 12540.4 | 12557 | 11472.7 | 12444.8 | 11444.2 | 31.5026 | 31.3357 | 31.3619 | 31.2344 | 31.1462 | 31.6551 | 0 | 46.1 | 0 | 0 | 46.4 | 46.4 | 4.0072 | 4.0108 | 3.7927 | 4.1261 | 4.0638 | 4.1595 | 8.196 | 7.841 | 9.047 | 8.222 | 7.655 | 8.394 | 5.8766 | 5.7754 | 5.6677 | 5.5579 | 5.8428 | 5.9645 | 0.96332 | 1.163 | 1.0883 | 1.3121 | 1.2206 | 1.1312 | 6.7051 | 6.5273 | 6.5218 | 6.7203 | 6.7034 | 6.6308 | 1.0267 | 1.1001 | 1.0951 | 1.3043 | 1.2857 | 1.1933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 455897 | 784 | 444257 | 840 | 311617.8 | 728.533 | 5.8766 | 5.7754 | 5.6677 | 5.5579 | 5.8428 | 5.9645 | 6.7051 | 6.5273 | 6.5218 | 6.7203 | 6.7034 | 6.6308 | 969000 | 1000 | 920000 | 2000 | 1841242 | 4600 | 1886000 | 1836642 | 11.7667 | 5.7808 | 1.1464 | 6.6348 | 1.1675 | 19.83% | 17.6% | 31.3727 | 46.3 | 4.0267 | 8.2258 | 1854243 | 1839933 | 2197658.3474 | 83.72%
2023-10-11 | 2024 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 335090.89 | 6:36 | 18:22 | 9092.2 | 9367.3 | 9714.4 | 9767.8 | 9853 | 9858.2 | 9440.5 | 9720.8 | 9357 | 9588.8 | 9204 | 9336.9 | 9472.5 | 9385.4 | 9709.1 | 9706.1 | 9791 | 10072.3 | 10010.5 | 9932.3 | 10130.8 | 10133.1 | 9873 | 10008.3 | 9849.9 | 8660.2 | 9865.2 | 9843.6 | 10128.3 | 9812.5 | 9561.8 | 9971.1 | 9949.3 | 10106.5 | 10055.9 | 9980.3 | 10054.3 | 9799.4 | 9778.8 | 9780.8 | 10576.2 | 9698.7 | 10380.7 | 9531.2 | 9920.8 | 10874.2 | 9292.1 | 10461.9 | 8853.8 | 9096.4 | 9753.3 | 9290.5 | 10206.9 | 8915.2 | 10171.2 | 9145.7 | 8861 | 10259 | 8766.7 | 9981.3 | 9769.8 | 8694.5 | 9600.6 | 9070.1 | 9665 | 9172.7 | 9550.1 | 10159.5 | 10185.4 | 9271.7 | 9960.7 | 8910.4 | 9686.1 | 9643.3 | 8823.5 | 10058.8 | 8674 | 9794.6 | 8470.1 | 9529.1 | 9786.5 | 10378.5 | 10127.7 | 10921.4 | 9863.7 | 10478.7 | 9584.8 | 8511.7 | 10119.6 | 9902.1 | 9075.6 | 10448.3 | 10185.1 | 9394 | 9304 | 10334.4 | 9109 | 9541.7 | 10350.7 | 9241.4 | 10663.6 | 9252.3 | 10364.5 | 9563.8 | 10379.2 | 9041.7 | 10421.6 | 9438.3 | 10273.8 | 9307.4 | 10353.2 | 9483.2 | 9359.5 | 10375.9 | 9561.6 | 9367.1 | 10404.3 | 10463.6 | 10327.4 | 9534.6 | 10324.2 | 9335.8 | 10043.7 | 9399.9 | 9970.4 | 8714.6 | 10127.5 | 9424.5 | 9750.6 | 9802.1 | 9588.5 | 8328 | 9714.6 | 8553.2 | 10120.1 | 10138.7 | 11700.5 | 10335.9 | 11842.9 | 10719.3 | 11596.4 | 10423.7 | 10565.9 | 10316.2 | 11753.8 | 12077.8 | 11798.9 | 11757.6 | 11687.4 | 11681.7 | 10873.3 | 11921 | 11752.3 | 11859.6 | 12118.8 | 12010.9 | 11980.1 | 11022.5 | 11758.7 | 11021.9 | 32.96 | 32.8511 | 32.893 | 32.8659 | 33.0024 | 33.3941 | 0 | 46.3 | 0 | 0 | 46.9 | 48.7 | 2.822 | 2.7978 | 2.8458 | 2.8633 | 2.8689 | 2.9703 | 5.733 | 6.024 | 5.599 | 5.687 | 5.303 | 5.853 | 4.6472 | 4.9615 | 4.755 | 4.6943 | 5.1624 | 5.827 | 0.78487 | 0.95371 | 0.92915 | 1.1161 | 1.0294 | 1.0784 | 5.2324 | 5.5772 | 5.41 | 5.5474 | 5.8891 | 6.4464 | 0.84204 | 0.90343 | 0.92024 | 1.1101 | 1.0914 | 1.1393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 456627 | 786 | 445076 | 842 | 313203.291 | 733.2 | 4.6472 | 4.9615 | 4.755 | 4.6943 | 5.1624 | 5.827 | 5.2324 | 5.5772 | 5.41 | 5.5474 | 5.8891 | 6.4464 | 730000 | 2000 | 819000 | 2000 | 1585491 | 4667 | 1545000 | 1580824 | 11.7667 | 5.0079 | 0.98195 | 5.6837 | 1.0011 | 19.61% | 17.61% | 32.9944 | 47.3 | 2.8614 | 5.6998 | 1594959 | 1584067 | 1886559.8727 | 83.97%
2023-10-12 | 2024 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 335090.89 | 6:37 | 18:22 | 10505.4 | 10897.8 | 11038.8 | 11026 | 11102.7 | 11043.6 | 10867.5 | 11327.5 | 10953.3 | 10945.8 | 10950.1 | 11048 | 11050.8 | 11054.8 | 10886.3 | 11016.9 | 10894.4 | 11025.9 | 11063.1 | 11132.9 | 10997.9 | 11039.1 | 10841.7 | 10895.1 | 10888.7 | 9667.2 | 11028.2 | 10897.5 | 11126.9 | 11033.5 | 10923.5 | 11127 | 11184.8 | 11242.8 | 11157.7 | 11099.6 | 11240.3 | 11137.6 | 11232.9 | 11126.5 | 11943.6 | 10766.1 | 11736.9 | 10622.5 | 11243 | 12413.3 | 10607.9 | 11937.8 | 10261.6 | 10535.6 | 11236.6 | 10653.2 | 11583.3 | 10284.1 | 11584.8 | 10372 | 10205.9 | 11672.3 | 10287.6 | 11520.7 | 11352.1 | 10207.4 | 11039.5 | 10571.1 | 11023.6 | 10355.6 | 10957.3 | 11367.4 | 11628 | 10592 | 11480.2 | 10182 | 11019.1 | 11004.5 | 10164.1 | 11436.3 | 10044.3 | 11480.9 | 10134.3 | 11299 | 10626.6 | 11487 | 10650.1 | 11774.7 | 10472.9 | 11149.9 | 10318.3 | 9160 | 11313 | 10816.6 | 10237.5 | 11744 | 11413.8 | 10515.7 | 10400.2 | 11456.2 | 10270.2 | 10760.6 | 11611.4 | 10277.8 | 11620.4 | 10214.6 | 11367.3 | 10450.6 | 11432.1 | 9914.3 | 11558.9 | 10537.2 | 11434.4 | 10470.1 | 11444.2 | 10650 | 10321.2 | 11293 | 10440 | 10238.2 | 11488 | 11622 | 11433.6 | 10567.5 | 11509 | 10355.1 | 11195.3 | 10479.5 | 11008.5 | 9623.8 | 11218.3 | 10358.1 | 10608.7 | 10635.3 | 10356 | 8999 | 10380.3 | 9165.6 | 10339.9 | 10387.4 | 11966.7 | 10517.7 | 12048.5 | 10814.9 | 11903.9 | 10656.4 | 10834 | 10545.1 | 11817.5 | 12125.9 | 12056.5 | 11964.1 | 11944 | 11941.5 | 10952.3 | 12008.4 | 11983.1 | 12021.2 | 12244.1 | 12208.8 | 12151.9 | 11028.3 | 12039.5 | 10997.5 | 33.1755 | 33.0525 | 33.002 | 32.9914 | 33.0128 | 33.2748 | 0 | 47.4 | 0 | 0 | 47.4 | 48.1023 | 3.3571 | 3.348 | 3.3386 | 3.4034 | 3.4343 | 3.2479 | 6.187 | 7.031 | 6.32 | 6.69 | 6.864 | 6.442 | 5.5561 | 5.4766 | 5.3815 | 5.3465 | 5.5852 | 5.7926 | 0.91789 | 1.1069 | 1.0469 | 1.277 | 1.122 | 1.0965 | 6.3285 | 6.1927 | 6.178 | 6.4289 | 6.3904 | 6.4481 | 0.97681 | 1.0463 | 1.0306 | 1.268 | 1.3411 | 1.1579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 457503 | 787 | 445954 | 843 | 314950.558 | 737.933 | 5.5561 | 5.4766 | 5.3815 | 5.3465 | 5.5852 | 5.7926 | 6.3285 | 6.1927 | 6.178 | 6.4289 | 6.3904 | 6.4481 | 876000 | 1000 | 878000 | 1000 | 1747267 | 4733 | 1752000 | 1742534 | 11.75 | 5.5231 | 1.0945 | 6.3278 | 1.1368 | 19.82% | 17.96% | 33.0848 | 47.6341 | 3.3549 | 6.589 | 1758873.3 | 1746000 | 2086977.0912 | 83.66%
2023-10-13 | 2024 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 335090.89 | 6:37 | 18:20 | 11337.1 | 11736.3 | 11650.5 | 11637.2 | 11720.1 | 11810.7 | 11710.2 | 12065.4 | 11715.5 | 11701.2 | 11593.6 | 11731 | 11719.8 | 11668.5 | 11674.6 | 11766.4 | 11635.9 | 11746.7 | 11737.7 | 11801.7 | 11747.9 | 11770.2 | 11579.5 | 11681.4 | 11543.1 | 10221.1 | 11585.2 | 11540.6 | 11787.7 | 11668.1 | 11538.7 | 11770.8 | 11915.2 | 11983.4 | 11935.7 | 11859.4 | 11848.7 | 11745.5 | 11787.3 | 11670.5 | 12495.6 | 11502.2 | 12337.7 | 11342.3 | 11915.8 | 12902.8 | 11260.5 | 12455.2 | 10895.6 | 11193.9 | 11839.1 | 11230.3 | 12141.2 | 10989.8 | 12047.5 | 10910.5 | 10865.3 | 12224.5 | 10932.3 | 12187.8 | 12083.3 | 10901.3 | 11849.8 | 11345.2 | 11567.6 | 10954.1 | 11519.3 | 11950 | 12157.6 | 11160.5 | 12013.9 | 10743.6 | 11717 | 11612.1 | 10885.1 | 12049.7 | 10768.8 | 12126.3 | 10871.9 | 12007.7 | 11265.4 | 11982 | 11338.1 | 12332.6 | 11199.2 | 11844.2 | 11107.4 | 9857.4 | 11899.4 | 11569.7 | 10888.5 | 12279.5 | 11978.5 | 11186.5 | 11069.6 | 12036.7 | 10896.8 | 11368.9 | 12122.8 | 10884.9 | 12222.9 | 10868.1 | 11995.3 | 11138.4 | 12034.1 | 10562.1 | 12113.6 | 11156.5 | 11995.2 | 11064.5 | 12053.6 | 11306.4 | 10967.5 | 11897.4 | 11120.2 | 10884.1 | 11995.3 | 12113.9 | 11942.9 | 11094.6 | 12057.6 | 11014.2 | 11763.5 | 11148 | 11715.6 | 10304.6 | 11864.3 | 11043.4 | 11115.1 | 11087.3 | 11002.3 | 9491.4 | 10882.8 | 9595.3 | 10878.7 | 10877.6 | 12377.3 | 11089.5 | 12458.7 | 11358.3 | 12300.1 | 11097.4 | 11280.7 | 10989.6 | 12177.6 | 12464.9 | 12379.1 | 12301 | 12352.8 | 12376.6 | 11443.7 | 12381.7 | 12337.8 | 12379.4 | 12457.8 | 12447.7 | 12481.8 | 11477 | 12405.1 | 11462.8 | 33.1496 | 32.881 | 32.9083 | 32.9215 | 32.9127 | 33.2221 | 0 | 46.8 | 0 | 0 | 47.2 | 47.3 | 3.9667 | 4.1367 | 4.0243 | 4.1132 | 4.1965 | 4.0528 | 7.956 | 7.631 | 7.802 | 7.439 | 7.354 | 8.236 | 5.8391 | 5.7499 | 5.6602 | 5.5214 | 5.8457 | 5.9519 | 0.98578 | 1.1648 | 1.1275 | 1.3348 | 1.1793 | 1.1279 | 6.7198 | 6.5768 | 6.5732 | 6.7222 | 6.7405 | 6.6855 | 1.0461 | 1.0999 | 1.1 | 1.3317 | 1.4052 | 1.1878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 458431 | 789 | 446874 | 845 | 316792.2 | 742.533 | 5.8391 | 5.7499 | 5.6602 | 5.5214 | 5.8457 | 5.9519 | 6.7198 | 6.5768 | 6.5732 | 6.7222 | 6.7405 | 6.6855 | 928000 | 2000 | 920000 | 2000 | 1841642 | 4600 | 1844000 | 1837042 | 11.7167 | 5.7614 | 1.1533 | 6.6696 | 1.1951 | 20.02% | 17.92% | 32.9992 | 47.1 | 4.0817 | 7.7363 | 1855049.6 | 1839800 | 2195068.5823 | 83.82%
2023-10-14 | 2024 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 335090.89 | 6:37 | 18:18 | 10989.8 | 11455.4 | 11391.1 | 11355.9 | 11468.9 | 11564 | 11432.8 | 11812.9 | 11416.8 | 11393.1 | 11280.5 | 11442.7 | 11408.9 | 11365 | 11373.6 | 11464.1 | 11340.8 | 11454.7 | 11428 | 11483.4 | 11444.9 | 11456.2 | 11248.6 | 11359.4 | 11217.4 | 9874 | 11263.8 | 11214.9 | 11482.1 | 11362.7 | 11191.6 | 11467.6 | 11502.1 | 11578.6 | 11517.8 | 11436.6 | 11542.4 | 11419.2 | 11476.8 | 11368.7 | 12212.4 | 11092.7 | 12070.5 | 10925.6 | 11595.1 | 12685.5 | 10844.3 | 12182.4 | 10560.9 | 10844.7 | 11550.1 | 10875.4 | 11892.6 | 10612.1 | 11803.6 | 10587.2 | 10498.6 | 11957.8 | 10592.2 | 11926.5 | 11802.3 | 10552.9 | 11536 | 10955.3 | 11229.8 | 10580.7 | 11170.1 | 11655 | 11918.2 | 10769.2 | 11736.3 | 10376.3 | 11411.6 | 11271.2 | 10517.5 | 11787.5 | 10398.3 | 11876.8 | 10499.9 | 11738.6 | 10855.9 | 11676.6 | 10931.3 | 12059.1 | 10779.5 | 11500.8 | 10701.6 | 9487.9 | 11588.1 | 11228.5 | 10506.6 | 12031.4 | 11698.5 | 10806.1 | 10697.8 | 11778.3 | 10530.5 | 10987.1 | 11851.4 | 10514.9 | 11958 | 10480.3 | 11677.4 | 10751.1 | 11752.6 | 10187.1 | 11835.1 | 10765.1 | 11673.2 | 10660 | 11788.7 | 10919.3 | 10575.7 | 11601.5 | 10735.3 | 10512.3 | 11717.8 | 11834.4 | 11652.9 | 10701.7 | 11774.4 | 10617 | 11444.5 | 10769.5 | 11402.3 | 9954.7 | 11492.6 | 10646.6 | 10734.5 | 10718.3 | 10625.4 | 9170.8 | 10490.2 | 9220.2 | 10512.1 | 10504.4 | 12101.1 | 10657.4 | 12177.1 | 10916.1 | 12011.7 | 10664.7 | 10867.5 | 10617.9 | 11875.9 | 12196.3 | 12094.6 | 12017.5 | 12060.5 | 12093.3 | 11030.1 | 12098.4 | 12080.8 | 12125.6 | 12195.2 | 12171.5 | 12203.2 | 11075.5 | 12163.2 | 11066.4 | 33.0622 | 32.8554 | 32.8191 | 32.7983 | 32.727 | 33.2249 | 0 | 44.6 | 0 | 0 | 44.6 | 44.5 | 5.6148 | 5.5692 | 5.6788 | 5.4153 | 5.5167 | 5.6384 | 10.497 | 10.413 | 11.154 | 10.517 | 9.869 | 10.702 | 5.5876 | 5.4924 | 5.4044 | 5.2806 | 5.5886 | 5.6634 | 0.96646 | 1.1279 | 1.1009 | 1.2923 | 1.1484 | 1.094 | 6.4174 | 6.2762 | 6.2597 | 6.4061 | 6.4354 | 6.3572 | 1.0224 | 1.0685 | 1.0714 | 1.2908 | 1.3593 | 1.1479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 459334 | 790 | 447767 | 847 | 318582.425 | 747.2 | 5.5876 | 5.4924 | 5.4044 | 5.2806 | 5.5886 | 5.6634 | 6.4174 | 6.2762 | 6.2597 | 6.4061 | 6.4354 | 6.3572 | 903000 | 1000 | 893000 | 2000 | 1790225 | 4667 | 1793000 | 1785558 | 11.6833 | 5.5028 | 1.1217 | 6.3587 | 1.1601 | 20.38% | 18.24% | 32.9145 | 44.5667 | 5.5722 | 10.5253 | 1802471.9 | 1788534 | 2115267.6496 | 84.55%
2023-10-15 | 2024 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 335090.89 | 6:38 | 18:15 | 11245.5 | 11662.3 | 11591.1 | 11592.2 | 11649.6 | 11732.9 | 11616.7 | 11947.8 | 11624.6 | 11609.8 | 11493.4 | 11647.4 | 11623.2 | 11575 | 11608.8 | 11698.6 | 11560.9 | 11661.6 | 11641.4 | 11702 | 11661.4 | 11681.4 | 11483.2 | 11586.6 | 11445 | 10108.1 | 11509 | 11458.1 | 11699.9 | 11583.9 | 11423.8 | 11667.4 | 11762.4 | 11845.7 | 11794.4 | 11707.9 | 11737.5 | 11638.7 | 11660.1 | 11589.3 | 12362.9 | 11352.4 | 12225.3 | 11190 | 11523.6 | 11706.2 | 11109.3 | 12328.5 | 10796.1 | 11087.2 | 11758.7 | 11113 | 12053.3 | 10839 | 11974.1 | 10809.9 | 10709.8 | 12121.9 | 10820.8 | 12095.7 | 11963.9 | 10783.6 | 11744 | 11219.9 | 11485.1 | 10837.8 | 11450.7 | 11878.1 | 12107.9 | 11048.2 | 11951.5 | 10641.8 | 11658.2 | 11547.5 | 10575 | 11563.3 | 10400.8 | 11806.6 | 10764 | 11963.9 | 11156.4 | 11925.7 | 11219.7 | 12266.3 | 11064.3 | 11754.6 | 10968 | 9736.3 | 11732.1 | 11157.1 | 10758.1 | 12188.9 | 11862.3 | 11029.3 | 10906.4 | 11930.9 | 10751.8 | 11258.8 | 12017.4 | 10781 | 12101.1 | 10723.9 | 11864.3 | 11004.2 | 11913.1 | 10425.3 | 11995.4 | 11018 | 11865.4 | 10927.3 | 11918.9 | 11152 | 10845.4 | 11822.7 | 10984.1 | 10759.8 | 11891.4 | 12047.2 | 11843.7 | 10970.2 | 11970.6 | 10880.6 | 11647.2 | 11016.3 | 11597.9 | 10179.4 | 11755.5 | 10898.8 | 10996.7 | 10991.3 | 10864.2 | 9388.3 | 10779.7 | 9475.4 | 10806.5 | 10810.6 | 12326.4 | 10987.7 | 12400 | 11263.2 | 12242.6 | 11007.9 | 11214.7 | 10949.9 | 12122.7 | 12419.8 | 12329.7 | 12258 | 12296.2 | 12327 | 11363.9 | 12325.5 | 12295.2 | 12346.3 | 12416 | 12396.9 | 12432.5 | 11405.1 | 12387.5 | 11404.6 | 30.877 | 30.6549 | 30.5486 | 30.66 | 30.7097 | 30.9723 | 0 | 43.7 | 0 | 0 | 43.7 | 43.7 | 4.7475 | 4.7496 | 4.8741 | 4.7057 | 4.9807 | 4.7714 | 8.174 | 8.506 | 8.614 | 8.057 | 8.701 | 8.681 | 5.6734 | 5.5929 | 5.5072 | 5.3685 | 5.6892 | 5.8114 | 0.97308 | 1.1489 | 1.1194 | 1.3141 | 1.1686 | 1.152 | 6.5351 | 6.4026 | 6.385 | 6.535 | 6.5683 | 6.5298 | 1.03 | 1.0847 | 1.0877 | 1.3109 | 1.3863 | 1.2067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460252 | 792 | 448680 | 848 | 320405.4 | 751.933 | 5.6734 | 5.5929 | 5.5072 | 5.3685 | 5.6892 | 5.8114 | 6.5351 | 6.4026 | 6.385 | 6.535 | 6.5683 | 6.5298 | 918000 | 2000 | 913000 | 1000 | 1822975 | 4733 | 1828000 | 1818242 | 11.6167 | 5.6071 | 1.146 | 6.4926 | 1.1844 | 20.44% | 18.24% | 30.7371 | 43.7 | 4.8048 | 8.4555 | 1836415.2 | 1821400 | 2163457.2883 | 84.19%
2023-10-16 | 2024 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 335090.89 | 6:50 | 17:51 | 6982.6 | 7296.9 | 7265 | 7257 | 7273.3 | 7282.8 | 7251.1 | 7479 | 7290.2 | 7243.6 | 7185.8 | 7309.5 | 7183.4 | 7209.7 | 7160.4 | 7213.3 | 7146.4 | 7202.5 | 7205.6 | 7249.9 | 7159 | 7007.8 | 6991.8 | 7067.4 | 6979.9 | 6169.7 | 7113.9 | 7015.7 | 7176.4 | 7104.2 | 6948.3 | 7114.5 | 7218.5 | 7222.8 | 7165.8 | 7092.9 | 7220.4 | 7188.9 | 7259.2 | 7240.3 | 7882.1 | 6999.2 | 7772.6 | 6869.7 | 7376.2 | 8255.8 | 6889 | 7878.2 | 6680.3 | 6886.8 | 7325.3 | 6883 | 7570.7 | 6685.4 | 7540.2 | 6382.9 | 6572.7 | 7688.8 | 6660.1 | 7612.7 | 7369.8 | 6686.3 | 7330.8 | 6903.6 | 7192 | 6732 | 7186.2 | 7503.2 | 7767.6 | 6939.2 | 7628 | 6699.7 | 7374.1 | 7279.2 | 6724.8 | 7646.1 | 6629.1 | 7653.2 | 6665 | 7513.6 | 6984.3 | 7609.2 | 7010.1 | 7818 | 6852.7 | 7340.6 | 6792.6 | 6000.7 | 7404.8 | 7128.4 | 6630 | 7732.6 | 7484.5 | 6869 | 6793.3 | 7584 | 6721.6 | 7031.6 | 7669.9 | 6717.8 | 7742.9 | 6695.1 | 7516.4 | 6889.8 | 7617.3 | 6529.4 | 7674 | 6912.7 | 7541.3 | 6861.5 | 7628 | 7020.9 | 6771.7 | 7495 | 6881.2 | 6732 | 7624.3 | 7720.1 | 7576.2 | 6933.8 | 7699.1 | 6861.1 | 7416.9 | 6931.2 | 7346.8 | 6400.9 | 7500.3 | 6866.5 | 6938.3 | 6932.8 | 6848.2 | 5911.5 | 6802 | 5988.9 | 6792.8 | 6802.1 | 7876.7 | 6850.4 | 7939.7 | 7027.8 | 7881.4 | 6886.5 | 6981.7 | 6729.7 | 7567.5 | 7839.3 | 7705.5 | 7709.2 | 7737.1 | 7801.8 | 7012.4 | 7781.8 | 7811.9 | 7838.3 | 7876.1 | 7857 | 7895.9 | 6995.8 | 7853.3 | 7021.9 | 26.3928 | 26.2049 | 26.397 | 26.4004 | 26.4274 | 26.5342 | 0 | 35.8 | 0 | 0 | 36.3 | 36.4 | 5.2711 | 5.4868 | 4.9661 | 5.6417 | 5.5343 | 4.8128 | 11.263 | 10.519 | 13.419 | 10.128 | 13.816 | 10.357 | 3.5936 | 3.4795 | 3.5044 | 3.4712 | 3.603 | 3.5814 | 0.61325 | 0.69182 | 0.6745 | 0.80184 | 0.73157 | 0.70115 | 3.9297 | 3.7378 | 3.8105 | 3.78 | 3.9696 | 3.814 | 0.64228 | 0.65948 | 0.67183 | 0.80836 | 0.87002 | 0.73491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460825 | 794 | 449255 | 850 | 321549.158 | 756.8 | 3.5936 | 3.4795 | 3.5044 | 3.4712 | 3.603 | 3.5814 | 3.9297 | 3.7378 | 3.8105 | 3.78 | 3.9696 | 3.814 | 573000 | 2000 | 575000 | 2000 | 1143758 | 4867 | 1144000 | 1138891 | 11.0167 | 3.5388 | 0.70236 | 3.8403 | 0.73115 | 19.85% | 19.04% | 26.3928 | 36.1667 | 5.2855 | 11.5837 | 1151038 | 1140666 | 1316800.1874 | 86.62%
2023-10-17 | 2024 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 335090.89 | 6:40 | 18:16 | 8114.8 | 8532.1 | 8479.9 | 8436.2 | 8532.4 | 8613.3 | 8566.2 | 8964.1 | 8540.2 | 8513.4 | 8440.1 | 8580.7 | 8506.9 | 8507.4 | 8528.1 | 8582.7 | 8477.1 | 8539.8 | 8554.3 | 8595.4 | 8533.3 | 8506 | 8292.1 | 8409.9 | 8296.6 | 7320.1 | 8374.4 | 8308.8 | 8505.2 | 8399.8 | 8221.9 | 8482.6 | 8542.9 | 8587.9 | 8573.5 | 8497.1 | 8579.5 | 8467.3 | 8507.3 | 8451 | 9242.6 | 8208.7 | 9122 | 8083.3 | 8665.7 | 9723.3 | 8087.8 | 9248.6 | 7876.4 | 8100.6 | 8604.7 | 8135.1 | 8905.8 | 7921.1 | 8931.4 | 7871.9 | 7926.7 | 9178.5 | 7909 | 9086.9 | 8997.2 | 7889.4 | 8817.3 | 8329.4 | 8452.9 | 7903.5 | 8428.5 | 8761.3 | 9089.1 | 8027.3 | 8936.4 | 7767.3 | 8672.2 | 8481.6 | 7947.7 | 8954.9 | 7823.9 | 9077.6 | 7928 | 8942.3 | 8101.1 | 8760.2 | 8177.2 | 9093.9 | 8062.6 | 8634.7 | 8010.9 | 7078.3 | 8729.8 | 8392.4 | 7805.2 | 9075.5 | 8765.7 | 8033 | 7890.4 | 8849.9 | 7893.3 | 8177.3 | 8983 | 7841.6 | 9069.4 | 7857.9 | 8812.2 | 8091.9 | 8931.6 | 7671.7 | 9005.5 | 8124.2 | 8859.7 | 8029.9 | 8974.4 | 8236 | 7906.2 | 8757.1 | 8051.8 | 7889.7 | 8977.2 | 9082.3 | 8920.6 | 8136.7 | 9060.1 | 8078.2 | 8728.4 | 8145 | 8631.1 | 7557.1 | 8845.6 | 8088.6 | 8240 | 8250.2 | 8112.1 | 7023.9 | 8060 | 7093.2 | 7993.7 | 8003 | 9241.5 | 8008.3 | 9286.3 | 8186 | 9245.4 | 8104.6 | 8245.1 | 8131.2 | 8874.8 | 9213.6 | 9166.4 | 9099.9 | 9156.2 | 9194.2 | 8214.8 | 9140.1 | 9120 | 9181.5 | 9257.3 | 9208.6 | 9225 | 8188.4 | 9217.8 | 8215.1 | 25.4425 | 25.2637 | 25.152 | 25.1106 | 25.2634 | 25.5267 | 0 | 36 | 0 | 0 | 36.5 | 36.3 | 3.6946 | 3.4267 | 3.4725 | 3.5207 | 3.4351 | 3.3416 | 6.791 | 7.08 | 6.998 | 6.628 | 6.307 | 7.19 | 4.1742 | 7.4262 | 4.102 | 3.9988 | 4.1671 | 4.1709 | 0.52515 | 0.60246 | 0.59017 | 0.62673 | 0.6475 | 0.59718 | 4.7037 | 4.5792 | 4.6833 | 4.4586 | 4.7239 | 4.581 | 0.55107 | 0.56613 | 0.57206 | 0.651 | 0.78414 | 0.63306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 461501 | 795 | 449930 | 852 | 322895.2 | 761.6 | 4.1742 | 7.4262 | 4.102 | 3.9988 | 4.1671 | 4.1709 | 4.7037 | 4.5792 | 4.6833 | 4.4586 | 4.7239 | 4.581 | 676000 | 1000 | 675000 | 2000 | 1346042 | 4800 | 1348000 | 1341242 | 11.6 | 4.6732 | 0.5982 | 4.6216 | 0.62624 | 12.8% | 13.55% | 25.2931 | 36.2667 | 3.4819 | 6.8323 | 1356294.5 | 1343400 | 1572306.0749 | 85.44%
2023-10-18 | 2024 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 335090.89 | 6:42 | 18:27 | 10940.9 | 11360.9 | 11245.7 | 11202.1 | 11291.6 | 11406.3 | 11366.3 | 11740.2 | 11355 | 11376.9 | 11217.6 | 11380 | 11312.4 | 11300.9 | 11320.4 | 11384 | 11268.3 | 11356.3 | 11371.4 | 11430.3 | 11380.7 | 11384.4 | 11191.1 | 11291.1 | 11160.3 | 9872.4 | 11206.5 | 11168.8 | 11406 | 11295.5 | 11127.4 | 11374.8 | 11548.5 | 11602.9 | 11539 | 11476.9 | 11470.8 | 11371.5 | 11378.6 | 11303.1 | 12037.3 | 11049.4 | 11880.4 | 10894.4 | 11546.3 | 12564.5 | 10856.8 | 12005.2 | 10557 | 10839.2 | 11468 | 10868.6 | 11747.9 | 10631.7 | 11700.1 | 10564.3 | 10521.6 | 11892.5 | 10579.8 | 11816.3 | 11693.8 | 10554.4 | 11549.7 | 11072.2 | 11202.4 | 10582.6 | 11181 | 11567.8 | 11821.3 | 10727.2 | 11704 | 10418.2 | 11403.1 | 11292.3 | 10570.8 | 11678.1 | 10372.6 | 11743.2 | 10581.3 | 11683.2 | 10864 | 11602.2 | 10997.1 | 11921.4 | 10822.8 | 11470.1 | 10732.3 | 9500.8 | 11619.2 | 11209.5 | 10528.2 | 11926 | 11608.2 | 10824.1 | 10699.1 | 11689.7 | 10606.9 | 10983 | 11747.2 | 10501.7 | 11818.2 | 10479.1 | 11581.4 | 10768.2 | 11635.5 | 10162.1 | 11710.4 | 10730 | 11585 | 10664.5 | 11634.5 | 10855.1 | 10593.2 | 11572.7 | 10709.6 | 10493.5 | 11620.7 | 11754.4 | 11564.4 | 10699.2 | 11674.3 | 10609.6 | 11369.6 | 10730 | 11319.5 | 9926 | 11466.8 | 10601.6 | 10802.6 | 10830.9 | 10644.4 | 9203 | 10605.1 | 9375.8 | 10522.4 | 10539.2 | 11991.5 | 10695.1 | 12019.7 | 10916.2 | 11916.5 | 10767.8 | 10933.4 | 10774.3 | 11745.3 | 12036.6 | 11979.2 | 11901 | 11959.5 | 11983.5 | 11018.2 | 11943.6 | 11997 | 12032.5 | 12074.7 | 12040.8 | 12068.3 | 11060.3 | 12083.8 | 11075.6 | 26.5984 | 26.3507 | 26.4511 | 26.2783 | 26.4855 | 26.5637 | 0 | 37.8 | 0 | 0 | 38.2 | 38.4 | 3.1078 | 3.0949 | 3.1874 | 3.1315 | 3.0573 | 3.0039 | 5.363 | 5.549 | 5.518 | 5.774 | 5.692 | 5.529 | 5.4472 | 22.9207 | 5.3297 | 5.1536 | 5.3911 | 5.4983 | 0.76517 | 0.84781 | 0.86851 | 0.95871 | 0.89918 | 0.8618 | 6.2997 | 6.2301 | 6.2923 | 6.2833 | 6.3012 | 6.22 | 0.789 | 0.79086 | 0.82183 | 0.9692 | 1.087 | 0.91325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 462400 | 797 | 450821 | 853 | 324677.892 | 766.333 | 5.4472 | 22.9207 | 5.3297 | 5.1536 | 5.3911 | 5.4983 | 6.2997 | 6.2301 | 6.2923 | 6.2833 | 6.3012 | 6.22 | 899000 | 2000 | 891000 | 1000 | 1782692 | 4733 | 1787000 | 1777959 | 11.75 | 8.2901 | 0.86686 | 6.2711 | 0.89519 | 10.46% | 14.27% | 26.4546 | 38.1333 | 3.0972 | 5.5708 | 1795318.7 | 1773334 | 2114256 | 83.88%
2023-10-19 | 2024 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 335090.89 | 6:43 | 18:27 | 10422.4 | 10899.3 | 10762.9 | 10652.1 | 10845.2 | 10976.9 | 10906.9 | 11413.9 | 10906 | 10932.8 | 10760.2 | 10950.7 | 10854.3 | 10859 | 10841.2 | 10934.4 | 10814 | 10918.9 | 10939.7 | 10983.2 | 10946.2 | 10932.7 | 10693 | 10821.6 | 10684.8 | 9395.6 | 10728.9 | 10694.1 | 10980.1 | 10832.3 | 10617.8 | 10952.3 | 10968.8 | 11022.3 | 10976.9 | 10907.4 | 11050 | 10910.6 | 10901.7 | 10842 | 11863.4 | 10542.3 | 11672.1 | 10369.4 | 11118.2 | 12482.4 | 10349.3 | 11840.7 | 10044.5 | 10309.7 | 11032.6 | 10344.9 | 11402.1 | 10109.9 | 11342.9 | 10050.2 | 10021.3 | 11589.8 | 10070.4 | 11509.7 | 11386.2 | 10036.9 | 11153 | 10556.7 | 10725.9 | 10069.2 | 10696.2 | 11190.4 | 11545.4 | 10207 | 11360.4 | 9915.7 | 10959.5 | 10781.5 | 10051.4 | 11370.4 | 9950 | 11505.6 | 10049.8 | 11343.7 | 10359.4 | 11232.3 | 10487.7 | 11680.6 | 10314.7 | 11058.4 | 10234 | 9054.7 | 11205.8 | 10714.5 | 9987.5 | 11629.9 | 11214.9 | 10269.3 | 10145.3 | 11340.3 | 10071.3 | 10466.4 | 11452.5 | 10002.4 | 11541.1 | 9985.4 | 11206.6 | 10248.3 | 11332.1 | 9707.8 | 11387.2 | 10234.3 | 11201.7 | 10184.4 | 11326.3 | 10365.9 | 10088.2 | 11204.3 | 10229.2 | 10011.1 | 11281.5 | 11435.9 | 11210 | 10195.4 | 11359.6 | 10120.6 | 10955.8 | 10239.1 | 10869.4 | 9460 | 11066.2 | 10118.3 | 10277.6 | 10296.5 | 10138.1 | 8767.2 | 10079.1 | 8910.9 | 10116.9 | 10135.2 | 11847.7 | 10232.6 | 11907.5 | 10461.1 | 11750.1 | 10282.1 | 10463.4 | 10258.7 | 11473.7 | 11922 | 11779.6 | 11694.9 | 11786.4 | 11830.3 | 10575 | 11779.2 | 11781.1 | 11813.1 | 11926.3 | 11895.3 | 11942.3 | 10586.1 | 11895.9 | 10605.1 | 29.0136 | 28.5043 | 28.4901 | 28.5312 | 28.6434 | 28.6683 | 0 | 42 | 0 | 0 | 42.6 | 42.1 | 2.0387 | 2.0458 | 1.9891 | 2.0046 | 1.8611 | 2.0758 | 4.075 | 4.061 | 3.771 | 3.962 | 3.829 | 4.877 | 5.2644 | 7.3897 | 5.1426 | 4.972 | 5.2103 | 5.3281 | 0.72858 | 0.77814 | 0.78116 | 0.94912 | 0.83993 | 0.81655 | 6.093 | 6.033 | 6.0895 | 6.0784 | 6.1016 | 6.0362 | 0.74133 | 0.71759 | 0.73523 | 0.93768 | 1.0241 | 0.87003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 463264 | 798 | 451681 | 855 | 326395.225 | 771.067 | 5.2644 | 7.3897 | 5.1426 | 4.972 | 5.2103 | 5.3281 | 6.093 | 6.033 | 6.0895 | 6.0784 | 6.1016 | 6.0362 | 864000 | 1000 | 860000 | 2000 | 1717333 | 4734 | 1721000 | 1712599 | 11.7333 | 5.5512 | 0.81558 | 6.0719 | 0.83766 | 14.69% | 13.8% | 28.6418 | 42.2333 | 2.0025 | 4.0958 | 1729052.4 | 1712267 | 2022480.1825 | 84.66%
2023-10-20 | 2024 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 335090.89 | 6:53 | 18:02 | 10451.8 | 10917.7 | 10783.8 | 10682.8 | 10880.1 | 11020.3 | 10930.2 | 11418.3 | 10929.6 | 10939.5 | 10783 | 10973.6 | 10876.8 | 10884.6 | 10845.3 | 10947.1 | 10821.8 | 10928.8 | 10949.8 | 10999.2 | 10934.3 | 10707.2 | 10706.8 | 10838.7 | 10718.3 | 9429 | 10758.7 | 10724.9 | 11014.2 | 10861.7 | 10657.3 | 10985.9 | 11027.7 | 11088.3 | 11018.4 | 10954.8 | 11101 | 10961.2 | 10971.5 | 10884.5 | 11904.6 | 10583.8 | 11728.2 | 10427.4 | 11150.2 | 12510.3 | 10389.9 | 11885 | 10073.9 | 10343.6 | 11066.9 | 10388 | 11446.5 | 10149.2 | 11376.6 | 10062 | 10003.5 | 11600.7 | 10058.2 | 11505.9 | 11315.8 | 10037 | 11159.2 | 10560.4 | 10768.2 | 10107 | 10736.3 | 11231.7 | 11591.8 | 10291.8 | 11407.9 | 9952.4 | 11013 | 10864.5 | 10100 | 11417 | 9998.6 | 11549.4 | 10091.2 | 11388.2 | 10393.7 | 11273.2 | 10528.6 | 11719.1 | 10261.4 | 10912.5 | 10266 | 9089.1 | 11257.9 | 10766.2 | 10042.4 | 11691.4 | 11274.1 | 10335.3 | 10206.2 | 11388.1 | 10111.2 | 10501.2 | 11489.4 | 10035.4 | 11589.4 | 10022.2 | 11258.6 | 10297.1 | 11380.4 | 9757.1 | 11435.4 | 10267.5 | 11252.5 | 10230.2 | 11381.9 | 10412 | 10109.9 | 11241.1 | 10260 | 10045.8 | 11308.2 | 11463.6 | 11243.3 | 10236.3 | 11396.7 | 10153.9 | 10993.2 | 10274.9 | 10931.3 | 9498.3 | 11095.2 | 10161.5 | 10336.2 | 10351.1 | 10166.6 | 8805.2 | 10124.8 | 8948.2 | 10148 | 10167.9 | 11899.4 | 10262.5 | 11960.2 | 10507.8 | 11797.2 | 10322.1 | 10503.9 | 10293.7 | 11537.3 | 11980.4 | 11828.9 | 11745.7 | 11832.2 | 11870.8 | 10617.6 | 11831.8 | 11866.3 | 11864.8 | 12001.3 | 11960 | 11999.1 | 10641.9 | 11960.4 | 10661.1 | 30.5285 | 30.3696 | 30.4037 | 30.3722 | 30.606 | 30.7113 | 0 | 44.1 | 0 | 0 | 45.1 | 44.7 | 1.9564 | 1.8838 | 1.9086 | 1.9565 | 1.8215 | 1.8601 | 4.222 | 4.056 | 4.707 | 4.882 | 4.205 | 4.393 | 5.2763 | 6.2555 | 5.1736 | 4.9913 | 5.2649 | 5.3787 | 0.74306 | 0.77303 | 0.77878 | 1.0017 | 0.84629 | 0.78829 | 6.1418 | 6.0844 | 6.1558 | 6.1362 | 6.1903 | 6.1206 | 0.7598 | 0.71232 | 0.72805 | 0.97737 | 1.037 | 0.8453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 464130 | 800 | 452545 | 857 | 328118.226 | 775.667 | 5.2763 | 6.2555 | 5.1736 | 4.9913 | 5.2649 | 5.3787 | 6.1418 | 6.0844 | 6.1558 | 6.1362 | 6.1903 | 6.1206 | 866000 | 2000 | 864000 | 2000 | 1723001 | 4600 | 1726000 | 1718401 | 11.15 | 5.39 | 0.82185 | 6.1382 | 0.84331 | 15.25% | 13.74% | 30.4986 | 44.6333 | 1.8978 | 4.4108 | 1734578.6 | 1711534 | 2031189.507 | 84.26%
2023-10-21 | 2024 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 335090.89 | 6:48 | 17:47 | 8185 | 8619 | 8617 | 8518 | 8791 | 8879 | 8726 | 9185 | 8631 | 8523 | 8566 | 8681 | 8862 | 8701 | 9019 | 9044 | 9068 | 9195 | 9133 | 9125 | 9179 | 9154 | 9068 | 9113 | 8845 | 7767 | 8919 | 8895 | 9221 | 9250 | 9084 | 9190 | 9147 | 9182 | 9111 | 9099 | 9315 | 9256 | 9262 | 9150 | 9929 | 8865 | 9802 | 8757 | 9338 | 10502 | 8762 | 9990 | 8180 | 8357 | 9072 | 8479 | 9429 | 8345 | 9263 | 8280 | 8099 | 9333 | 8097 | 9283 | 9120 | 8009 | 8917 | 8369 | 8627 | 8001 | 8561 | 8851 | 9238 | 8118 | 9003 | 7770 | 8758 | 8528 | 7983 | 8976 | 7807 | 9073 | 7857 | 8834 | 8101 | 8741 | 8190 | 9163 | 8103 | 8713 | 8084 | 7175 | 9011 | 8578 | 8047 | 9457 | 9252 | 8582 | 8554 | 9383 | 8282 | 8554 | 9433 | 8192 | 9665 | 8252 | 9350 | 8462 | 9432 | 8029 | 9434 | 8368 | 9269 | 8357 | 9356 | 8492 | 8197 | 9099 | 8394 | 8190 | 9227 | 9292 | 9176 | 8291 | 9269 | 8262 | 8948 | 8335 | 8862 | 7695 | 9020 | 8199 | 8375 | 8361 | 8155 | 7135 | 8203 | 7200 | 7926 | 7896 | 8897 | 7769 | 8974 | 7980 | 9011 | 7895 | 8083 | 7960 | 8227 | 8549 | 8389 | 8390 | 8584 | 8739 | 7837 | 8584 | 8429 | 8455 | 8416 | 8420 | 8491 | 7556 | 8549 | 7571 | 30.2 | 30.1 | 30.3 | 30.2 |  | 30.2 | 0 | 41.9 | 0 | 0 | 39.3 | 39.3 | 2.4 | 2.5 | 2.5 | 2.5 |  | 2.5 | 10.7 | 10.3 | 9.9 | 12.2 |  | 16.2 | 4.2 | 5.5 | 4.4 | 4.1 |  | 3.8 | 0.62 | 0.59 | 0.68 | 0.86 |  | 0.48 | 4.78 | 5.02 | 5.13 | 4.77 |  | 4.33 | 0.64 | 0.54 | 0.63 | 0.83 |  | 0.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 464836 | 802 | 453222 | 858 | 329496.4 | 780.3 | 4.2 | 5.5 | 4.4 | 4.1 | 0 | 3.8 | 4.78 | 5.02 | 5.13 | 4.77 | 0 | 4.33 | 706000 | 2000 | 677000 | 1000 | 1378174 | 4633 | 1380000 | 1373541 | 10.9833 | 4.4 | 0.646 | 4.806 | 0.634 | 14.68% | 13.19% | 30.2 | 40.1667 | 2.48 | 11.86 | 1387360 | 1374467 | 1597752.8172 | 86.03%
2023-10-22 | 2024 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 335090.89 | 6:52 | 18:16 | 10062.4 | 10523.4 | 10464.2 | 10435.2 | 10519.2 | 10604 | 10539.9 | 10999.8 | 10510 | 10566.5 | 10333.1 | 10528.7 | 10423.2 | 10425.2 | 10434.3 | 10501.2 | 10381.5 | 10456.6 | 10475.9 | 10531.9 | 10475 | 10463 | 10229.3 | 10359.1 | 10206.9 | 8992.5 | 10278.8 | 10231.2 | 10503.7 | 10379.5 | 10160.1 | 10465.7 | 10496.2 | 10550.6 | 10492.7 | 10436.5 | 10568.6 | 10429.5 | 10412.8 | 10360.4 | 11314.6 | 10076 | 11158.3 | 9928.6 | 10643.9 | 11983.2 | 9886.6 | 11292.5 | 9622.9 | 9878.5 | 10571.9 | 9906 | 10935.5 | 9712.9 | 10849.2 | 9615.6 | 9504.1 | 11025.5 | 9599.7 | 10907.8 | 10680.7 | 9602.9 | 10591.6 | 10110.1 | 10240 | 9609 | 10208.6 | 10673.6 | 11032.5 | 9815.3 | 10851.5 | 9464.4 | 10504.3 | 10338 | 9639.4 | 10920 | 9526.9 | 11023.9 | 9634 | 10876 | 9881.6 | 10720.6 | 10029.3 | 11123.9 | 8550 | 0 | 9764.8 | 8576.9 | 10762.8 | 10261.5 | 9570 | 11147 | 10744.6 | 9854.1 | 9732.5 | 10860.3 | 9649.2 | 10006.2 | 10940.1 | 9554.9 | 11016 | 9537.4 | 10700.5 | 9799 | 10821.8 | 9272.9 | 10798.9 | 9586.7 | 10718.7 | 9749.1 | 10841.7 | 9892.5 | 9627.7 | 10706.6 | 9765.5 | 9555.9 | 10616.1 | 10909.9 | 10687.9 | 9728.1 | 10828.6 | 9647.2 | 10445.4 | 9761.6 | 10394.7 | 9033.7 | 10546.4 | 9578 | 9848.1 | 9879.5 | 9698 | 8386.4 | 9667.2 | 8562.4 | 9732.4 | 9745.9 | 11312.1 | 9767.2 | 11370.3 | 10005.4 | 11250.9 | 9866.2 | 10025.1 | 9876.1 | 10948.5 | 11368.1 | 11233 | 11158.3 | 11249.1 | 11284.4 | 10088.9 | 11230.9 | 11284.3 | 11339.1 | 11350.5 | 11353.3 | 11380.3 | 10110.4 | 11377 | 10126.6 | 29.9 | 29.47 | 29.64 | 29.51 |  | 29.64 | 0 | 40.5 |  |  | 41.49 | 40.25 | 2.91 | 2.83 | 2.87 | 2.81 |  | 2.65 | 5.17 | 5.46 | 5.21 | 5.51 |  | 4.88 | 5 | 5.67 | 4.89 | 4.71 |  | 5.06 | 0.69 | 0.74 | 0.74 | 0.95 |  | 0.72 | 5.82 | 5.72 | 5.8 | 5.79 |  | 5.71 | 0.71 | 0.68 | 0.68 | 0.92 |  | 0.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 465664 | 803 | 454032 | 860 | 331128.093 | 784.333 | 5 | 5.67 | 4.89 | 4.71 | 0 | 5.06 | 5.82 | 5.72 | 5.8 | 5.79 | 0 | 5.71 | 828000 | 1000 | 810000 | 2000 | 1631693 | 4033 | 1635000 | 1627660 | 11.4 | 5.066 | 0.768 | 5.768 | 0.752 | 15.16% | 13.04% | 29.632 | 40.7467 | 2.814 | 5.246 | 1642139 | 1630467 | 1929934.1997 | 84.48%
2023-10-23 | 2024 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 335090.89 | 6:58 | 18:00 | 10326.1 | 10799.5 | 10703.2 | 10671.3 | 10758.8 | 10886.6 | 10799.1 | 11266.5 | 10772.6 | 10831.6 | 10594.7 | 10787.4 | 10705.5 | 10674.8 | 10719.5 | 10787.3 | 10675.8 | 10750.3 | 10759.5 | 10815.9 | 10763.1 | 10749.7 | 10517 | 10648.5 | 10501.9 | 9244.3 | 10561.8 | 10518.5 | 10803.6 | 10668.2 | 10453.5 | 10769 | 10800.6 | 10861.5 | 10790.7 | 10734.9 | 10874.7 | 10732.6 | 10720.8 | 10664.8 | 11715.3 | 10422.4 | 11544.9 | 10278.8 | 10978.6 | 12290.4 | 10201.2 | 11665.4 | 9865.9 | 10125.9 | 10845.1 | 10166.2 | 11214.2 | 9959.7 | 11137 | 9868.5 | 9865.2 | 11413.8 | 9900.1 | 11325.5 | 11204.9 | 9869.5 | 10989.1 | 10413.2 | 10535.9 | 9886.1 | 10505.7 | 10998.2 | 11347.3 | 10104.9 | 11156.1 | 9740.8 | 10787 | 10625.2 | 9898.6 | 11218 | 9787.6 | 11316.9 | 9889 | 11163.7 | 10192.4 | 11057.3 | 10325.5 | 11479.5 | 10110.9 | 10849.5 | 10042.1 | 8824.4 | 11027.4 | 10549.4 | 9818.2 | 11428 | 11022.2 | 10108 | 9984.4 | 11147.2 | 9887.2 | 10299.1 | 11251.8 | 9849.2 | 11337.3 | 9825.4 | 11022.1 | 10086.2 | 11158.3 | 9557.3 | 11227.5 | 10069.8 | 11065.4 | 10063.3 | 11190.9 | 10221.8 | 9925.2 | 11013.7 | 10064.2 | 9837.2 | 11058.8 | 11242.7 | 11015.4 | 10022.5 | 11181.8 | 9964.1 | 10775.5 | 10087.2 | 10729.6 | 9335.5 | 10893.6 | 9902.6 | 10134.6 | 10136.2 | 10005.9 | 8640.6 | 9913.7 | 8766.6 | 9972.4 | 9986.2 | 11629.9 | 10039.7 | 11700.5 | 10289.9 | 11555.3 | 10127.1 | 10300.9 | 10119.3 | 11284.2 | 11723.1 | 11567.2 | 11486.5 | 11568.8 | 11597.1 | 10380.5 | 11562.1 | 11593.5 | 11667.4 | 11738.6 | 11699.9 | 11729.2 | 10415.4 | 11706.9 | 10430.6 | 31.25 | 30.64 | 30.56 | 30.68 | 30.65 | 30.67 | 0 | 43.1 | 0 | 0 | 43.6 | 43.3 | 2.64 | 2.67 | 2.6 | 2.61 | 2.57 | 2.57 | 4.82 | 6.16 | 4.84 | 4.77 | 4.79 | 4.58 | 5.15 | 5.66 | 5.05 | 3.28 | 5.07 | 5.22 | 0.75 | 0.86 | 0.8 | 1.05 | 0.85 | 0.77 | 6.04 | 5.95 | 6.06 | 6.01 | 6.03 | 5.94 | 0.77 | 0.79 | 0.76 | 1.09 | 1.02 | 0.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 466515 | 805 | 454878 | 861 | 332818.826 | 789.133 | 5.15 | 5.66 | 5.05 | 3.28 | 5.07 | 5.22 | 6.04 | 5.95 | 6.06 | 6.01 | 6.03 | 5.94 | 851000 | 2000 | 846000 | 1000 | 1690733 | 4800 | 1694000 | 1685933 | 11.0333 | 4.905 | 0.84667 | 6.005 | 0.87667 | 17.26% | 14.6% | 30.7417 | 43.3333 | 2.61 | 4.9933 | 1702285.9 | 1674667 | 1989364.782 | 84.18%
2023-10-24 | 2024 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 335090.89 | 6:46 | 18:08 | 10142.2 | 10601.4 | 10422.4 | 10391.6 | 10470 | 10648.7 | 10575 | 11055.1 | 10592.5 | 10608.3 | 10465.2 | 10634.2 | 10590.4 | 10573.5 | 10592.4 | 10669.3 | 10570.1 | 10665 | 10679.9 | 10729.3 | 10687.5 | 10677 | 10457.4 | 10582.4 | 10434.1 | 9179 | 10494.6 | 10460.8 | 10744.5 | 10614.4 | 10407.9 | 10707.8 | 10722.9 | 10793.2 | 10719.9 | 10652.5 | 10793.9 | 10657.6 | 10675.5 | 10604.1 | 11660.6 | 10371.7 | 11503.5 | 10223 | 10901 | 12231.6 | 10132.6 | 11621.1 | 9782.9 | 10037.8 | 10743.6 | 10060.9 | 11111.6 | 9857.4 | 11021 | 9779.5 | 9746 | 11270.5 | 9806 | 11188.5 | 11064.7 | 9772.1 | 10872.6 | 10307.9 | 10442.2 | 9809.4 | 10416.9 | 10918 | 11245.9 | 10042.4 | 11066 | 9669.5 | 10691.4 | 10533.5 | 9795 | 10990.4 | 9476.6 | 11075.1 | 9795.6 | 11057.2 | 10119 | 10965.2 | 10229.8 | 11397.6 | 10048 | 10782.3 | 9950 | 8835.9 | 10909.7 | 10476.2 | 9727.5 | 11319.8 | 10915.1 | 10007.8 | 9880.2 | 11041.4 | 9826.8 | 10278.9 | 11213 | 9834.3 | 11301.7 | 9807.4 | 10988.9 | 10063.5 | 11108.9 | 9535.6 | 10889.8 | 9750.8 | 11017.6 | 10021.1 | 11126.9 | 10177.8 | 9904.6 | 10957.7 | 10040.9 | 9797.3 | 11067.4 | 11224.4 | 10982.8 | 10011.6 | 11139.7 | 9921.2 | 10735.9 | 10044 | 10669.4 | 9284 | 10841 | 9735.8 | 10076.2 | 10068.2 | 9916.8 | 8584.6 | 9847.3 | 8713.6 | 9920 | 9930.2 | 11634.4 | 10052.3 | 11695.3 | 10284.9 | 11514.4 | 10081 | 10251.9 | 10065.9 | 11274.8 | 11698.5 | 11568.1 | 11481.1 | 11567.3 | 11601.4 | 10373.7 | 11551 | 11560.6 | 11627.4 | 11697 | 11647.7 | 11711.7 | 10398.4 | 11679.1 | 10410.3 | 30.8486 | 30.4582 | 30.0092 | 30.2616 | 30.3308 | 30.489 | 0 | 42.6 | 0 | 0 | 42.6 | 42.5 | 2.581 | 2.4028 | 2.558 | 2.5183 | 2.5805 | 2.5143 | 6.1 | 5.063 | 7.815 | 5.561 | 5.146 | 5.993 | 5.0833 | 5.9843 | 5.0402 | 4.7837 | 5.0635 | 5.0617 | 2.6145 | 0.8668 | 0.79526 | 1.1303 | 0.89915 | 0.83776 | 5.958 | 5.9459 | 6.0323 | 5.956 | 6.0275 | 5.9568 | 0.76483 | 0.80176 | 0.77647 | 1.2072 | 1.0276 | 1.0174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 467358 | 806 | 455720 | 863 | 334497.026 | 793.933 | 5.0833 | 5.9843 | 5.0402 | 4.7837 | 5.0635 | 5.0617 | 5.958 | 5.9459 | 6.0323 | 5.956 | 6.0275 | 5.9568 | 843000 | 1000 | 842000 | 2000 | 1678200 | 4800 | 1682000 | 1673400 | 11.3667 | 5.1694 | 1.1906 | 5.9794 | 0.93255 | 23.03% | 15.6% | 30.3996 | 42.5667 | 2.5258 | 5.9463 | 1689228 | 1677200 | 1983355 | 84.56%
2023-10-25 | 2024 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 335090.89 | 6:50 | 18:03 | 10505.1 | 11007.1 | 10853.5 | 10810.2 | 10899.7 | 11096.9 | 10972 | 11432.6 | 10948.8 | 10930.5 | 10786.7 | 10974 | 10889.1 | 10866.1 | 10882 | 10981.2 | 10831.3 | 10900.2 | 10909.6 | 10959.3 | 10877 | 10882.5 | 10655.4 | 10765 | 10560.4 | 9308.6 | 10722.4 | 10659.1 | 10922.9 | 10805.4 | 10576.5 | 10843 | 10717.9 | 10807.8 | 10780.9 | 10677.6 | 10867.6 | 10776.7 | 10772.9 | 10664.9 | 11891.1 | 10571.5 | 11730.5 | 10419.3 | 11069.8 | 12382.2 | 10315.5 | 11829.8 | 10000.5 | 10260.9 | 10984 | 10275.4 | 11358.1 | 10062.7 | 11263.6 | 9976.4 | 9955.5 | 11518.4 | 10034.8 | 11446 | 11317.4 | 10016.5 | 11069.7 | 10463.2 | 10607.1 | 9911 | 10587.1 | 11041.6 | 11453.9 | 10161.2 | 11232 | 9773 | 10872.1 | 10647 | 9946 | 11240.5 | 9788.8 | 11344.5 | 9886.7 | 11165.9 | 10232.9 | 11112.1 | 10308.7 | 11521 | 10167.3 | 10939.1 | 10077.8 | 8969.3 | 11012.5 | 10621.1 | 9817.4 | 11397.8 | 10969.3 | 10044.7 | 9904.4 | 11107.6 | 9831.2 | 10279.8 | 11219 | 9873.7 | 11305.7 | 9864.8 | 11032.3 | 10100.5 | 11102.8 | 9587.3 | 11172.6 | 10099.8 | 10985.2 | 10024.8 | 11121.6 | 10298.9 | 9929.2 | 11029.4 | 10136 | 9901.9 | 11179.8 | 11363.4 | 11123.9 | 10177.6 | 11320.5 | 10092.6 | 10880.9 | 10200.9 | 10832.6 | 9447.1 | 11023.8 | 10067.6 | 10273.1 | 10257 | 10106.9 | 8755.3 | 10052.4 | 8902.4 | 10134.7 | 10144.8 | 11841.7 | 10242.6 | 11946.3 | 10496 | 11746 | 10284.7 | 10468.9 | 10266.4 | 11450.8 | 11933.4 | 11655 | 11609.7 | 11733.6 | 11801.2 | 10601.3 | 11787.9 | 11696.7 | 11790.3 | 11871.7 | 11849.2 | 11893.5 | 10567.7 | 11780.8 | 10557.6 | 31.13 | 30.61 | 30.5 | 30.7 | 30.67 | 30.83 | 0 | 41.8 | 0 | 0 | 42.2 | 42.5 | 2.42 | 2.25 | 2.21 | 2.28 | 2.2 | 2.13 | 5.56 | 5.58 | 4.92 | 5.86 | 5.11 | 5.4 | 6.44 | 6.22 | 5.09 | 4.83 | 5.2 | 5.15 | 0.88 | 0.72 | 0.82 | 1.16 | 0.91 | 0.88 | 6.18 |  | 6.22 | 6.08 | 6.14 | 6.36 | 0.78 | 0.81 | 0.8 | 1.25 | 1.02 | 1.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 468217 | 808 | 456573 | 865 | 336202.626 | 798.667 | 6.44 | 6.22 | 5.09 | 4.83 | 5.2 | 5.15 | 6.18 | 0 | 6.22 | 6.08 | 6.14 | 6.36 | 859000 | 2000 | 853000 | 2000 | 1705600 | 4734 | 1708000 | 1700866 | 11.2167 | 5.4883 | 0.895 | 6.196 | 0.95167 | 16.31% | 15.36% | 30.74 | 42.1667 | 2.2483 | 5.405 | 1717261.4 | 1703534 | 2041559.8951 | 83.44%
2023-10-26 | 2024 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 335090.89 | 6:52 | 18:06 | 10765.9 | 11248.6 | 11132.6 | 11038.6 | 11206.3 | 11319.5 | 11172.5 | 11622.9 | 11183.1 | 11198.3 | 11036 | 11223.1 | 11160.6 | 11145.2 | 11116.9 | 11235 | 11111.3 | 11223.7 | 11225.7 | 11272.2 | 11217.9 | 11209.4 | 11002.6 | 11133.1 | 10980.6 | 9666 | 11052.7 | 11021.9 | 11293.1 | 11147.5 | 10933 | 11244.9 | 11274.5 | 11338.5 | 11252.9 | 11174.9 | 11327 | 11190.3 | 11214.8 | 11161.9 | 12147.8 | 10923.7 | 11986.6 | 10751.3 | 11405.8 | 12533.5 | 10622.2 | 12114 | 10313.6 | 10588.7 | 11328.9 | 10622.3 | 11697.1 | 10352.9 | 11604.8 | 10322 | 10227.5 | 11815.3 | 10303.3 | 11741.1 | 11519.3 | 10269.1 | 11373.3 | 10787.1 | 11008.7 | 10315.2 | 10957.4 | 11476.5 | 11790.1 | 10564.1 | 11612.1 | 10168.4 | 11239.8 | 11074.4 | 10318 | 11655.3 | 10176.8 | 11757.3 | 10289.9 | 11590 | 10651.6 | 11529 | 10744.1 | 11941.4 | 10562.3 | 11335.4 | 10444.6 | 9295.1 | 11407.2 | 11010.7 | 10234.8 | 11841.6 | 11472.8 | 10528.6 | 10416.8 | 11543.4 | 10251.5 | 10736.9 | 11681.6 | 10256.3 | 11769.9 | 10247.6 | 11487.1 | 10498 | 11580.1 | 9959 | 11663.8 | 10482 | 11504.5 | 10464.2 | 11636.4 | 10635.3 | 10327 | 11401.2 | 10470.4 | 10237.3 | 11396.6 | 11506.4 | 11425.2 | 10440.8 | 11591.8 | 10366.7 | 11187.1 | 10493.8 | 11142.7 | 9721.8 | 11323.3 | 10401.3 | 10506.4 | 10479.8 | 10387.5 | 8965.5 | 10259.6 | 9065.9 | 10363.5 | 10360.3 | 12037.7 | 10490.7 | 12115.4 | 10743.8 | 11935.2 | 10493.4 | 10691.9 | 10468.1 | 11754.8 | 12131.2 | 11998.8 | 11918.6 | 12001.3 | 12023.3 | 10833 | 11994 | 11942.1 | 12008.2 | 12096.5 | 12071.6 | 12135.6 | 10870.2 | 12086 | 10857.6 | 31.653 | 31.4796 | 31.573 | 31.4855 | 31.605 | 31.6498 | 0 | 44.2 | 0 | 0 | 44.9 | 45 | 2.3379 | 2.5044 | 2.3372 | 2.4424 | 2.3243 | 2.4119 | 5.238 | 5.992 | 5.336 | 5.915 | 5.016 | 4.846 | 6.6638 | 6.8037 | 5.1974 | 5.0781 | 5.2551 | 5.2661 | 0.85136 | 0.90569 | 0.84487 | 1.2066 | 0.95603 | 0.92129 | 6.3168 | 6.3774 | 6.4062 | 6.2771 | 6.3154 | 6.3216 | 0.80083 | 0.8016 | 0.82761 | 1.3005 | 1.0654 | 1.1022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 469104 | 810 | 457451 | 866 | 337960.36 | 803.333 | 6.6638 | 6.8037 | 5.1974 | 5.0781 | 5.2551 | 5.2661 | 6.3168 | 6.3774 | 6.4062 | 6.2771 | 6.3154 | 6.3216 | 887000 | 2000 | 878000 | 1000 | 1757734 | 4666 | 1762000 | 1753068 | 11.2333 | 5.7107 | 0.94764 | 6.3358 | 0.98304 | 16.59% | 15.52% | 31.5743 | 44.7 | 2.393 | 5.3905 | 1770155.2 | 1756600 | 2085862.304 | 84.21%
2023-10-27 | 2024 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 335090.89 | 6:48 | 18:07 | 10123.6 | 10551.2 | 10455.3 | 10377.8 | 10536.8 | 10621.3 | 10493.6 | 10886.6 | 10501 | 10503.6 | 10363.8 | 10533.6 | 10472.8 | 10467.7 | 10428.2 | 10543.3 | 10429.3 | 10534.7 | 10544.7 | 10595 | 10543.5 | 10536.1 | 10329.8 | 10452.4 | 10313.9 | 9078.8 | 10383.1 | 10351.6 | 10605.6 | 10453.5 | 10256.6 | 10567.2 | 10576.1 | 10645.5 | 10590.2 | 10506.1 | 10648.3 | 10507.7 | 10579.6 | 10464.6 | 11402.9 | 10237 | 11247.8 | 10081.6 | 10683.2 | 11791.2 | 9950.5 | 11374.7 | 9691.8 | 9950.6 | 10642.1 | 9997.8 | 10994 | 9723.6 | 10899.6 | 9691.7 | 9530.1 | 11038.1 | 9669.9 | 10943.4 | 10396.4 | 9659.8 | 10613.4 | 10121.9 | 10332.6 | 9690.8 | 10288.6 | 10778.7 | 11062.6 | 9913.2 | 10890.9 | 9546.4 | 10556.8 | 10391.3 | 9699.2 | 10931 | 9556.2 | 11047.8 | 9674.2 | 10887.5 | 10001.7 | 10818.6 | 10080.7 | 11210 | 9905.1 | 10635.4 | 9793.4 | 8729.4 | 10672.7 | 10349.8 | 9592.2 | 11085.2 | 10743.8 | 9866.1 | 9762.6 | 10808.2 | 9639.5 | 10061.8 | 10947.8 | 9605.5 | 11007.3 | 9592.2 | 10738.5 | 9832.2 | 10834.8 | 9322.7 | 10893.8 | 9801.7 | 10741.6 | 9770.6 | 10868.7 | 9946.8 | 9669.2 | 10674.5 | 9790.9 | 9587.4 | 10735.4 | 10876.9 | 10690.2 | 9793 | 10857.9 | 9717 | 10472.8 | 9816.8 | 10428.9 | 9095.1 | 10596.4 | 9739.8 | 9868.5 | 9856.2 | 9726.8 | 8408.7 | 9620.8 | 8490.7 | 9747 | 9745.5 | 11285.1 | 9838.5 | 11346.2 | 10076.3 | 11171.3 | 9839 | 10019.9 | 9859 | 11030.2 | 11366 | 11242 | 11171.1 | 11231.8 | 11262.1 | 10143.6 | 11227.3 | 11191.3 | 11252.7 | 11377.3 | 11330.7 | 11365.4 | 10207.8 | 11354.2 | 10199.5 | 31.69 | 31.61 | 31.69 | 31.49 | 31.39 | 31.9 | 0 | 44.3 | 0 | 0 | 44.8 | 45.2 | 2.8 | 2.91 | 2.67 | 2.89 | 2.78 | 2.74 | 6.37 | 6.64 | 6.1 | 6.8 | 6.03 | 6.25 | 6.11 | 6.21 | 4.87 | 4.78 | 4.93 | 4.95 | 0.81 | 0.8 | 0.8 | 1.15 | 0.93 | 0.87 | 5.89 | 5.96 | 5.96 | 5.84 | 5.88 | 5.91 | 0.77 | 0.98 | 0.79 | 1.24 | 1.02 | 1.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 469935 | 811 | 458274 | 868 | 339608.56 | 808.133 | 6.11 | 6.21 | 4.87 | 4.78 | 4.93 | 4.95 | 5.89 | 5.96 | 5.96 | 5.84 | 5.88 | 5.91 | 831000 | 1000 | 823000 | 2000 | 1648200 | 4800 | 1651000 | 1643400 | 11.3167 | 5.3083 | 0.89333 | 5.9067 | 0.97333 | 16.83% | 16.48% | 31.6283 | 44.7667 | 2.7983 | 6.365 | 1659990.1 | 1647133 | 1954094 | 84.29%
2023-10-28 | 2024 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 335090.89 | 6:50 | 18:10 | 7470.3 | 7684.2 | 7596.6 | 7577.3 | 7647.1 | 7705.2 | 7639.5 | 7856.2 | 7693 | 7695.1 | 7581.9 | 7695.4 | 7642.2 | 7615.1 | 7617.4 | 7694.6 | 7581.4 | 7631.5 | 7654.8 | 7698.6 | 7655.6 | 7665.3 | 7549.1 | 7615 | 7507.2 | 6715.3 | 7561.9 | 7536.3 | 7687.4 | 7608 | 7516.9 | 7656.2 | 7750.9 | 7784.5 | 7777.2 | 7712.1 | 7681.7 | 7613.5 | 7645.6 | 7616.8 | 8009.4 | 7391.3 | 7961 | 7300.8 | 7703.4 | 8287.5 | 7272.8 | 8030.6 | 7186.1 | 7379.8 | 7739 | 7394.9 | 7914.3 | 7176.3 | 7922.3 | 7205.3 | 7186.1 | 8038.5 | 7226.8 | 8004.4 | 7902.8 | 7204.1 | 7800.3 | 7498.9 | 7657.8 | 7286.7 | 7650.6 | 7945 | 8061.8 | 7445.8 | 8000 | 7195.7 | 7796.9 | 7757.4 | 7269.2 | 8023.8 | 7194.2 | 8050.2 | 7274.4 | 8001.5 | 7509.9 | 7986.3 | 7559.4 | 8182.7 | 7450.1 | 7888.7 | 7376 | 6589.5 | 7889.5 | 7711.7 | 7208.1 | 8081.2 | 7872.7 | 7344.5 | 7273.2 | 7924.7 | 7257.5 | 7551.8 | 8020.7 | 7243.7 | 8042.4 | 7214.9 | 7918 | 7383.2 | 7929.5 | 7016.2 | 7978.3 | 7357.8 | 7892.2 | 7333 | 7948.4 | 7465.7 | 7300.7 | 7911 | 7359.1 | 7233.6 | 7844.8 | 7829.6 | 7885.6 | 7424 | 7982.6 | 7338.9 | 7754.7 | 7341.3 | 7715.9 | 6880.1 | 7877 | 7376.5 | 7479.8 | 7485.4 | 7353.6 | 6386.7 | 7334.1 | 6472.1 | 7399.6 | 7412.4 | 8311.2 | 7479.3 | 8360.1 | 7637.5 | 8258.4 | 7510.7 | 7621.8 | 7519.8 | 8213.6 | 8386 | 8336.1 | 8286.5 | 8295.2 | 8309.3 | 7711.4 | 8327.2 | 8313 | 8319.5 | 8407.9 | 8371.8 | 8393.9 | 7745.9 | 8410.4 | 7753.9 | 31.6667 | 31.5892 | 31.5477 | 31.584 | 31.7419 | 31.9462 | 0 | 40.2 | 0 | 0 | 41.2 | 41.3 | 2.787 | 2.7954 | 2.8341 | 2.6879 | 2.721 | 2.7545 | 6.741 | 7.05 | 7.167 | 6.157 | 6.197 | 7.549 | 4.6028 | 3.1947 | 3.7159 | 3.6874 | 3.8096 | 3.8812 | 0.58484 | 0.56637 | 0.58388 | 0.86227 | 0.73462 | 0.69784 | 4.32 | 4.3281 | 4.2969 | 4.3377 | 4.3531 | 4.3826 | 0.559 | 0.69983 | 0.57939 | 0.91817 | 0.80638 | 0.83619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470543 | 813 | 458888 | 870 | 340827.293 | 812.8 | 4.6028 | 3.1947 | 3.7159 | 3.6874 | 3.8096 | 3.8812 | 4.32 | 4.3281 | 4.2969 | 4.3377 | 4.3531 | 4.3826 | 608000 | 2000 | 614000 | 2000 | 1218733 | 4667 | 1218000 | 1214066 | 11.3333 | 3.8153 | 0.67164 | 4.3364 | 0.73316 | 17.6% | 16.91% | 31.6793 | 40.9 | 2.7633 | 6.8102 | 1226242.6 | 1217333 | 1448342.2686 | 84.05%
2023-10-29 | 2024 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 335090.89 | 6:51 | 18:04 | 10226 | 10643.6 | 10573.6 | 10493 | 10687.2 | 10733.1 | 10569.1 | 11061.8 | 10621 | 10684.2 | 10458.9 | 10643.5 | 10552.5 | 10561.7 | 10554.6 | 10641.9 | 10548.1 | 10661.3 | 10634.7 | 10670.5 | 10647.7 | 10628.5 | 10423.8 | 10554.8 | 10344.1 | 9103.7 | 10432.6 | 10402 | 10677.1 | 10540 | 10339 | 10629.4 | 10605.3 | 10658.3 | 10617.5 | 10540.7 | 10711.5 | 10589.6 | 10662.7 | 10523.3 | 11662.8 | 10370.5 | 11486.5 | 10216 | 10803.9 | 12070.6 | 10064.8 | 11628.4 | 9773.2 | 10041 | 10719.3 | 10072 | 11089.8 | 9819.3 | 11022.2 | 9736.8 | 9741.2 | 11307 | 9793.4 | 11225.8 | 11043.4 | 9763.8 | 10887.3 | 10290.9 | 10434 | 9745.2 | 10381.2 | 10851.3 | 11239.9 | 9999.6 | 11034 | 9646.5 | 10679.5 | 10507.4 | 9800.1 | 11101.5 | 9668.9 | 11211.6 | 9782.8 | 11046.6 | 10080.9 | 10928.3 | 10138 | 11333.1 | 9966 | 10687 | 9862.1 | 8764.2 | 10796.7 | 10396.2 | 9625.4 | 11186.8 | 10789 | 9876.4 | 9822.9 | 10861.9 | 9690.1 | 10113.6 | 11033.8 | 9656.5 | 11151.6 | 9634.6 | 10859.1 | 9895.7 | 11017.7 | 9404 | 11082.7 | 9928.9 | 10921.3 | 9939.2 | 11047.8 | 10086.8 | 9726.9 | 10761.5 | 9859.7 | 9648.5 | 10737 | 10708.4 | 10810.6 | 9859.8 | 10977.2 | 9806 | 10598.4 | 9936.9 | 10572.1 | 9221 | 10723.7 | 9851.4 | 9898.2 | 9886.5 | 9843.1 | 8473.6 | 9707.7 | 8589.7 | 9801.7 | 9774.8 | 11263 | 9737.1 | 11339.6 | 10008.4 | 11227.7 | 9866 | 10065.2 | 9871.6 | 10752.1 | 11168.2 | 11039.5 | 11013.9 | 11164.9 | 11206.5 | 10022.4 | 11114.7 | 10956.6 | 10993.7 | 11026.7 | 10997.6 | 11075.2 | 9838.6 | 11161.7 | 9882.1 | 32.0391 | 31.8129 | 31.8032 | 31.7983 | 32.1783 | 31.8046 | 0 | 44.2 | 0 | 0 | 44.7 | 43.9 | 2.4598 | 2.5003 | 2.3681 | 2.4469 | 2.3808 | 2.3731 | 5.421 | 6.11 | 5.074 | 4.996 | 4.482 | 4.809 | 6.0543 | 4.155 | 4.9445 | 4.8276 | 4.9116 | 4.8168 | 0.7814 | 0.74507 | 0.8166 | 1.1628 | 0.95452 | 0.84636 | 5.9581 | 5.9908 | 6.0416 | 5.9839 | 5.9089 | 5.7877 | 0.74138 | 0.91821 | 0.7981 | 1.2527 | 1.0406 | 1.0175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 471385 | 814 | 459712 | 871 | 342487.2 | 817.5 | 6.0543 | 4.155 | 4.9445 | 4.8276 | 4.9116 | 4.8168 | 5.9581 | 5.9908 | 6.0416 | 5.9839 | 5.9089 | 5.7877 | 842000 | 1000 | 824000 | 1000 | 1659907 | 4700 | 1664000 | 1655207 | 11.2167 | 4.9516 | 0.88446 | 5.9452 | 0.96143 | 17.86% | 16.17% | 31.9061 | 44.2667 | 2.4215 | 5.1487 | 1670757.6 | 1657666 | 1960185 | 84.57%
2023-10-30 | 2024 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 335090.89 | 6:52 | 18:05 | 9245.6 | 9634.2 | 9594.6 | 9532.8 | 9699.3 | 9772.9 | 9647.2 | 10114 | 9635.7 | 9709.6 | 9588.2 | 9725.4 | 9708.4 | 9698.7 | 9733.4 | 9820.2 | 9730.8 | 9828.7 | 9821.5 | 9860.9 | 9774.9 | 9792.8 | 9538.7 | 9663.8 | 9425.9 | 8356.6 | 9643 | 9550.3 | 9758 | 9555 | 9362.1 | 9607.7 | 9565.2 | 9608.7 | 9642.9 | 9491.8 | 9639.2 | 9557 | 9664.7 | 9473 | 10787.2 | 9604 | 10653.7 | 9461.8 | 10071.3 | 11278.5 | 9388.7 | 10769.3 | 8968.6 | 9202.9 | 9868.3 | 9198.9 | 10233 | 9080.6 | 10042.1 | 8909.2 | 8885.2 | 10236.9 | 8976 | 10227.1 | 10122.6 | 8940 | 9902.1 | 9383.4 | 9367.8 | 8685.1 | 9293.2 | 9586.3 | 10187 | 8957.3 | 9997.4 | 8660 | 9729.4 | 9491 | 8960.3 | 10046.9 | 8796.2 | 10262.5 | 8928 | 10062.7 | 8830.2 | 9667.6 | 8714.8 | 9890.7 | 8608.6 | 9218.8 | 8686.5 | 7617.2 | 9223.2 | 9025.4 | 8350.9 | 9557.8 | 9327.7 | 8632 | 8558.5 | 9125.1 | 7993.3 | 8303.4 | 9097.3 | 7929.7 | 9314 | 7965.9 | 9045.1 | 8184.2 | 9170 | 7794.1 | 9222.9 | 8243.4 | 9142.3 | 8301.6 | 9246.9 | 8336.7 | 8003.1 | 8909.6 | 8147.2 | 7955.5 | 8950.9 | 9075.2 | 8925.4 | 8217.3 | 9107.7 | 8125.9 | 8755 | 8201.2 | 8772.4 | 7598.6 | 8861.7 | 8124.2 | 8276.6 | 8295.5 | 8115.1 | 7019.6 | 8135.8 | 7198.1 | 8271 | 8257.9 | 9339.3 | 8132.5 | 9575.8 | 8429.9 | 9367.4 | 8273.9 | 8434.5 | 8353.3 | 9258.1 | 9629.9 | 9355.1 | 9289.7 | 9273.2 | 9286 | 8450.6 | 9404.8 | 9372.6 | 9525.8 | 9761.4 | 9724.5 | 9716.9 | 8624.8 | 9462.2 | 8527.6 | 32.3535 | 31.8843 | 31.918 | 31.8787 | 31.7224 | 31.8551 | 0 | 43.2 | 0 | 0 | 41.9 | 41.9 | 2.5354 | 2.4574 | 2.3779 | 2.5033 | 2.4602 | 2.3395 | 5.873 | 5.785 | 5.155 | 6.009 | 5.083 | 5.247 | 5.7279 | 3.8323 | 4.7194 | 4.4368 | 4.1429 | 4.1509 | 0.80129 | 0.66129 | 0.80038 | 1.0949 | 0.74903 | 0.69281 | 5.4902 | 5.4083 | 5.6093 | 5.3141 | 4.9106 | 4.8997 | 0.75442 | 0.82045 | 0.78046 | 1.1722 | 0.83908 | 0.83626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 472153 | 816 | 460409 | 873 | 343946.694 | 822.333 | 5.7279 | 3.8323 | 4.7194 | 4.4368 | 4.1429 | 4.1509 | 5.4902 | 5.4083 | 5.6093 | 5.3141 | 4.9106 | 4.8997 | 768000 | 2000 | 697000 | 2000 | 1459494 | 4833 | 1461000 | 1454661 | 11.2167 | 4.5017 | 0.79994 | 5.272 | 0.86714 | 17.77% | 16.45% | 31.9353 | 42.3333 | 2.4456 | 5.5253 | 1468172 | 1457867 | 1750693.4965 | 83.27%
2023-10-31 | 2024 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 335090.89 | 6:57 | 18:00 | 6281 | 6574.7 | 6506.7 | 6505.2 | 6544.8 | 6618.5 | 6540.1 | 6848.7 | 6571.7 | 6551.8 | 6431.4 | 6565.1 | 6506.9 | 6494 | 6496.8 | 6563.6 | 6473.9 | 6525.7 | 6529.8 | 6559.7 | 6544 | 6533.7 | 6412.2 | 6487.1 | 6371.5 | 5604.5 | 6439.4 | 6410.3 | 6578.6 | 6483.5 | 6369.6 | 6551.1 | 6646.8 | 6673.3 | 6591.6 | 6556.3 | 6642.2 | 6568.5 | 6621 | 6572.8 | 7156 | 6370.5 | 7071 | 6284.3 | 6703 | 7511.4 | 6189.8 | 7154.5 | 6026.4 | 6187.9 | 6604.2 | 6194.1 | 6836.1 | 6056.9 | 6747.4 | 5899.4 | 6000.6 | 6953.8 | 6046.5 | 6917.8 | 6848 | 6030.3 | 6676.6 | 6311.6 | 6318.6 | 6128.1 | 6459 | 6904.8 | 6962.1 | 6324.2 | 6861.6 | 6088.8 | 6612.5 | 6587.9 | 6060.2 | 6955.6 | 6017.5 | 6919.2 | 6039 | 6842.3 | 6456.3 | 6978.9 | 6601.8 | 7282 | 6438.8 | 6946.5 | 6324.8 | 5678.5 | 7039.1 | 6698.1 | 6256.3 | 7246 | 6916.5 | 6301.3 | 6066.8 | 7030.8 | 6424.5 | 6759.4 | 7397.9 | 6489.8 | 7344.1 | 6451.9 | 7167.3 | 6640.6 | 7239.4 | 6271.9 | 7310.7 | 6644.1 | 7158.3 | 6564.2 | 7278.4 | 6741 | 6604.8 | 7401.2 | 6691.4 | 6589.5 | 7428.4 | 7660.9 | 7394.5 | 6929.2 | 7612.3 | 6819.8 | 7170.9 | 6719.8 | 7168 | 6333.2 | 7419 | 6874.5 | 7192.6 | 7211 | 6947.5 | 6096.3 | 7111.2 | 6299.4 | 7382.6 | 7378.7 | 8445.4 | 7335.3 | 8547.7 | 7550.6 | 8428.1 | 7416.3 | 7551.6 | 7463 | 8161.8 | 8466.9 | 8273.8 | 8255.9 | 8342.4 | 8386.5 | 7575.1 | 8390.7 | 8179 | 8302.9 | 8462.8 | 8434.1 | 8456.1 | 7535.3 | 8273.6 | 7481.5 | 31.25 | 30.54 | 30.44 | 30.83 | 30.8 | 31.12 | 0 | 35.6 | 0 | 0 | 37.4 | 38.21 | 4.98 | 4.91 | 4.59 | 5.01 | 4.81 | 4.74 | 12.51 | 11.78 | 9.4 | 11.44 | 10.92 | 10.74 | 3.82 | 2.56 | 3.07 | 3.01 | 3.39 | 3.66 | 0.58 | 0.39 | 0.56 | 0.78 | 0.58 | 0.59 | 3.53 | 3.53 | 3.57 | 3.47 | 4 | 4.28 | 0.54 | 0.49 | 0.54 | 0.83 | 0.67 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 472673 | 817 | 460986 | 875 | 345040.094 | 827.133 | 3.82 | 2.56 | 3.07 | 3.01 | 3.39 | 3.66 | 3.53 | 3.53 | 3.57 | 3.47 | 4 | 4.28 | 520000 | 1000 | 577000 | 2000 | 1093400 | 4800 | 1094000 | 1088600 | 11.05 | 3.2517 | 0.58 | 3.73 | 0.63167 | 17.84% | 16.93% | 30.83 | 37.07 | 4.84 | 11.1317 | 1099506.7 | 1091400 | 1261096 | 86.54%
2023-11-01 | 2024 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 335090.89 | 6:54 | 17:57 | 8040.3 | 8378.3 | 8261.4 | 8252.9 | 8292.1 | 8348.9 | 8314.1 | 8668.6 | 8352 | 8417.3 | 8153.6 | 8322.1 | 8192.3 | 8218.8 | 8114.9 | 8222.2 | 8080.2 | 8155.3 | 8178.4 | 8193.4 | 8229 | 8207.5 | 8078.2 | 8164.8 | 8006.1 | 7022.3 | 8040.8 | 8042.1 | 8295.6 | 8205.2 | 8041.7 | 8244.6 | 8317.3 | 8344.9 | 8277.2 | 8239.3 | 8342.9 | 8251.6 | 8298.7 | 8218.8 | 8879.6 | 7911.2 | 8777.5 | 7801.7 | 8364.9 | 9464.3 | 7807.6 | 8925.3 | 7564.2 | 7762.4 | 8281 | 7755.6 | 8533.9 | 7582.5 | 8495.5 | 7519.4 | 7493.8 | 8665.5 | 7602.2 | 8640 | 8566.8 | 7593.3 | 8327 | 7913.6 | 7990.2 | 7515.1 | 7978.5 | 8395.8 | 8630 | 7717.2 | 8494.5 | 7434.4 | 8216.8 | 8102.5 | 7561.6 | 8577.5 | 7477.7 | 8682.3 | 7604.1 | 8606.6 | 7800.9 | 8453.3 | 7905.7 | 8785.3 | 7737 | 8323.2 | 7634 | 6815.1 | 8455.9 | 8097.8 | 7549.2 | 8793.6 | 8484.4 | 7786.6 | 7705.2 | 8560.4 | 7622 | 7948.5 | 8687.1 | 7591.3 | 8792.7 | 7574.7 | 8527.9 | 7769.8 | 8631.9 | 7382.5 | 8674.1 | 7760.8 | 8520.2 | 7735.6 | 8610.7 | 7830.7 | 7646.8 | 8460 | 7719.8 | 7564 | 8509.2 | 8635.6 | 8438.4 | 7579.6 | 8547.6 | 7617.2 | 8228.8 | 7700.1 | 8173.7 | 7103.9 | 8311.4 | 7652.7 | 7770.6 | 7782.5 | 7653.4 | 6613 | 7662 | 6757.9 | 7922.2 | 7956.1 | 9238.6 | 7966.9 | 9366.1 | 8218.5 | 9171.4 | 8055.8 | 8178 | 8078.1 | 9048.4 | 9388.4 | 9186.6 | 9141.1 | 9222.5 | 9236.5 | 8311.3 | 9253.2 | 9252.7 | 9314.5 | 9475.5 | 9429.1 | 9455.5 | 8373.6 | 9308.4 | 8319 | 31.0594 | 30.4095 | 30.4259 | 30.4698 | 30.4572 | 30.5147 | 0 | 40.6 | 0 | 0 | 41.2 | 38.6 | 3.5484 | 3.4136 | 3.3239 | 3.3408 | 3.3511 | 3.2651 | 10.371 | 11.485 | 9.829 | 11.34 | 9.829 | 10.12 | 4.9298 | 4.5929 | 3.9008 | 3.8053 | 3.9378 | 4.1067 | 0.69476 | 1.9077 | 0.67202 | 0.94924 | 0.72403 | 0.71119 | 4.6319 | 4.5661 | 4.5642 | 4.4821 | 4.6599 | 4.8083 | 0.66062 | 0.67849 | 0.65644 | 1.0015 | 0.81274 | 0.85103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 473325 | 819 | 461645 | 877 | 346345.894 | 831.933 | 4.9298 | 4.5929 | 3.9008 | 3.8053 | 3.9378 | 4.1067 | 4.6319 | 4.5661 | 4.5642 | 4.4821 | 4.6599 | 4.8083 | 652000 | 2000 | 659000 | 2000 | 1305800 | 4800 | 1307000 | 1301000 | 11.05 | 4.2122 | 0.94315 | 4.6188 | 0.7768 | 22.39% | 16.82% | 30.5561 | 40.1333 | 3.3738 | 10.4957 | 1313783.6 | 1303267 | 1498538.7883 | 86.97%
2023-11-02 | 2024 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 335090.89 | 6:57 | 18:03 | 8437.8 | 8759.9 | 8793.8 | 8769.5 | 8866.3 | 8841.2 | 8712.3 | 9044.3 | 8709.6 | 8806.5 | 8486 | 8666.1 | 8586.2 | 8558.9 | 8650 | 8723 | 8655.7 | 8775.8 | 8692.1 | 8680 | 8807.6 | 8745.8 | 8701.5 | 8762.2 | 8544.4 | 7443.3 | 8484.2 | 8551.7 | 8890.6 | 8839.3 | 8676.1 | 8870.4 | 8813 | 8859.9 | 8792.5 | 8794.4 | 8947.4 | 8875.6 | 8883.2 | 8790.3 | 9960.7 | 8867.3 | 9811.3 | 8741.3 | 9302.5 | 10459.1 | 8633.5 | 9926.8 | 7906.5 | 8125.5 | 8662.5 | 8120.2 | 8967.5 | 7949 | 8916 | 7910.5 | 7882.9 | 9131.9 | 7946.3 | 9094.5 | 9021.3 | 7938.7 | 8846.1 | 8400.9 | 8446.9 | 7940 | 8452.9 | 8880.2 | 9152.9 | 8175.1 | 8973.2 | 7890.5 | 8719.7 | 8576.7 | 8012.8 | 9082.9 | 7906.1 | 9193.9 | 8029.2 | 9068.1 | 8238.3 | 8956.5 | 8321.7 | 9275.5 | 8120.2 | 8709.9 | 8000.7 | 7113.4 | 8720.7 | 8415.6 | 7833.7 | 9117.7 | 8881.4 | 8171.5 | 8090.7 | 8853.8 | 7815.2 | 8123.6 | 8931.1 | 7763.5 | 9173 | 7859 | 8924.7 | 8068.2 | 9081.4 | 7691.9 | 9130.2 | 8105.9 | 9078.4 | 8232.3 | 9192.2 | 8312.5 | 7806.2 | 8670.3 | 7998.1 | 7814.5 | 8854 | 8985 | 8822.7 | 8015.6 | 8976 | 8035.9 | 8646.7 | 8133.8 | 8646.4 | 7542.2 | 8788.3 | 8087.3 | 8035.9 | 7929.9 | 8086.9 | 6921 | 7773.7 | 6809.3 | 7979.9 | 7988.2 | 9221.4 | 7933.2 | 9333.6 | 8194.6 | 9157.7 | 8055.5 | 8190.8 | 8090.2 | 9095.9 | 9452.5 | 9260.3 | 9185.7 | 9222.4 | 9215.2 | 8300 | 9274.4 | 9312.1 | 9356.2 | 9474.5 | 9429 | 9489.3 | 8390.7 | 9390.3 | 8379.3 | 30.9659 | 30.5253 | 30.6231 | 30.5522 | 30.5841 | 30.5577 | 0 | 40 | 0 | 0 | 40 | 40.3 | 2.2858 | 2.2427 | 2.3331 | 2.3388 | 2.1576 | 2.2711 | 5.063 | 5.367 | 5.157 | 6.161 | 5.637 | 5.774 | 4.1808 | 4.2441 | 4.2371 | 3.9557 | 3.9973 | 4.054 | 0.0053266 | 0.67296 | 0.71293 | 0.97138 | 0.75948 | 0.71316 | 4.8733 | 4.8707 | 5.0883 | 4.7845 | 4.7764 | 4.793 | 0.68896 | 0.7721 | 0.70378 | 1.039 | 0.85355 | 0.85891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 474019 | 821 | 462323 | 879 | 347713.494 | 836.6 | 4.1808 | 4.2441 | 4.2371 | 3.9557 | 3.9973 | 4.054 | 4.8733 | 4.8707 | 5.0883 | 4.7845 | 4.7764 | 4.793 | 694000 | 2000 | 678000 | 2000 | 1367600 | 4667 | 1368000 | 1362933 | 11.1 | 4.1115 | 0.63921 | 4.8644 | 0.81938 | 15.55% | 16.84% | 30.6347 | 40.1 | 2.2715 | 5.5265 | 1375369.3 | 1366134 | 1583444 | 86.28%
2023-11-03 | 2024 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 335090.89 | 6:50 | 18:00 | 9124.5 | 9532 | 9547.4 | 9512.1 | 9636.6 | 9660.9 | 9528.8 | 9846.3 | 9458.5 | 9466.5 | 9226.5 | 9462.3 | 9405.3 | 9376.3 | 9438.3 | 9534.5 | 9434.2 | 9539 | 9491.5 | 9506.4 | 9540.3 | 9524.4 | 9355.4 | 9452.3 | 9262 | 8130.3 | 9320.6 | 9310.7 | 9562.4 | 9435 | 9236 | 9504.9 | 9488.4 | 9561.6 | 9544.8 | 9462.2 | 9581.7 | 9468.1 | 9507.4 | 9399.4 | 10491.5 | 9344.4 | 10316.7 | 9196.6 | 9787 | 11022 | 9100.1 | 10472.1 | 8678.2 | 8902.1 | 9520 | 8905.5 | 9856.9 | 8702.2 | 9776.1 | 8679 | 8611.7 | 9966.1 | 8680 | 9933.6 | 9818.2 | 8651.4 | 9609.1 | 9094.3 | 9206.3 | 8673.1 | 9197.4 | 9680.6 | 9949.1 | 8887.2 | 9773.3 | 8562.7 | 9448.4 | 9293.5 | 8676.1 | 9817.7 | 8540.5 | 9909.5 | 8640.4 | 9758.7 | 8943 | 9707.4 | 9022 | 10093.1 | 8864.7 | 9511.1 | 8765.9 | 7799.4 | 9587.8 | 9266.7 | 8630.3 | 10005.5 | 9690.7 | 8876.1 | 8779.6 | 9684.7 | 8614.4 | 8957.7 | 9800.5 | 8486.6 | 9937.7 | 8543.3 | 9623.3 | 8755.9 | 9729 | 8319.4 | 9774.5 | 8745.7 | 9639.2 | 8743.2 | 9720.5 | 8849.6 | 8568.5 | 9469.7 | 8678.7 | 8493.8 | 9551.1 | 9697.3 | 9493.8 | 8645.3 | 9628.5 | 8585 | 9274.8 | 8714.3 | 9233.3 | 8021.5 | 9368.2 | 8589.5 | 8630.7 | 8587.9 | 8524.3 | 7355.6 | 8416.5 | 7425 | 8546.6 | 8547.2 | 9939 | 8596.9 | 10064.6 | 8821.9 | 9854.6 | 8600.3 | 8764.3 | 8619.4 | 9642.2 | 10062 | 9854.6 | 9800.7 | 9859.8 | 9895.5 | 8925.9 | 9960.4 | 9722.1 | 9813 | 9842.2 | 9827.9 | 9928.3 | 8827.1 | 9888.2 | 8839 | 30.9262 | 30.6211 | 30.7291 | 30.661 | 30.5449 | 30.7306 | 0 | 42.9 | 0 | 0 | 42.8 | 42.9 | 2.3626 | 2.2834 | 2.1018 | 2.3846 | 2.3346 | 2.1087 | 5.407 | 5.61 | 5.743 | 5.257 | 5.062 | 5.225 | 4.5698 | 4.5711 | 4.4511 | 4.2943 | 4.3384 | 4.3363 | 0.0064912 | 0.7489 | 0.74729 | 1.0448 | 0.85193 | 0.80126 | 5.3588 | 5.2728 | 5.3721 | 5.2477 | 5.2142 | 5.166 | 0.74239 | 0.85396 | 0.73824 | 1.1159 | 0.94207 | 0.94731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 474770 | 822 | 463053 | 880 | 349189.1 | 841.333 | 4.5698 | 4.5711 | 4.4511 | 4.2943 | 4.3384 | 4.3363 | 5.3588 | 5.2728 | 5.3721 | 5.2477 | 5.2142 | 5.166 | 751000 | 1000 | 730000 | 1000 | 1475606 | 4733 | 1479000 | 1470873 | 11.1667 | 4.4268 | 0.70011 | 5.2719 | 0.88998 | 15.82% | 16.88% | 30.7021 | 42.8667 | 2.2626 | 5.384 | 1483970.6 | 1474267 | 1712223.96 | 86.1%
2023-11-04 | 2024 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 335090.89 | 6:52 | 18:04 | 8832.4 | 9259 | 9189.6 | 9165.2 | 9240.4 | 9337.4 | 9244.6 | 9593.7 | 9182.1 | 9140.9 | 8978.6 | 9179.3 | 9129 | 9104.6 | 9130.1 | 9226.6 | 9128.2 | 9234.4 | 9241.2 | 9259.9 | 9286.7 | 9273.5 | 9108.9 | 9204.8 | 9079.2 | 7950.1 | 9095.3 | 9100.2 | 9353 | 9224.6 | 9057.4 | 9327.2 | 9379 | 9425.3 | 9370.1 | 9309.3 | 9435.4 | 9320.9 | 9380.3 | 9293.2 | 10109.8 | 8986.5 | 9967.8 | 8838.5 | 9454.1 | 10661.9 | 8791.5 | 10096 | 8443.9 | 8661 | 9273.4 | 8664.6 | 9606.2 | 8449.8 | 9550 | 8489.5 | 8392.9 | 9740.2 | 8435.7 | 9655.2 | 9519.8 | 8393.2 | 9322.8 | 8834.3 | 9023.9 | 8538.6 | 9029.5 | 9540.3 | 9766.9 | 8754.7 | 9613.4 | 8434.8 | 9265.3 | 9151.2 | 8505.1 | 9665.3 | 8400.7 | 9714.9 | 8478.2 | 9575.4 | 8798.9 | 9564.9 | 8880.2 | 9957.1 | 8738.9 | 9366.7 | 8641.4 | 7690.7 | 9497.6 | 9167.8 | 8555.9 | 9939.8 | 9620.2 | 8806.4 | 8707 | 9671.4 | 8621.6 | 8954 | 9824.1 | 8495 | 9968.6 | 8597.7 | 9677.1 | 8828.5 | 9787.8 | 8392.8 | 9847.9 | 8853.7 | 9681.7 | 8797.3 | 9754 | 8948.3 | 8558.6 | 9497.4 | 8733.9 | 8546.7 | 9650.5 | 9766.2 | 9610.4 | 8708.3 | 9747.9 | 8702 | 9411.6 | 8842.2 | 9385.6 | 8155.9 | 9501.5 | 8697.1 | 8672.1 | 8571.5 | 8633.1 | 7440.2 | 8311.3 | 7307.5 | 8338 | 8335.6 | 9752.1 | 8436.4 | 9774.6 | 8625.7 | 9634.4 | 8408 | 8574.9 | 8402.5 | 9333.8 | 9679.6 | 9585.1 | 9521.9 | 9625 | 9672.2 | 8622.3 | 9590.8 | 9506 | 9562 | 9611.2 | 9590.5 | 9649.1 | 8559 | 9700.8 | 8577.4 | 30.52 | 30.19 | 30.18 | 30.27 | 30.25 | 30.47 | 0 | 41.6 | 0 | 0 | 42 | 41.6 | 2.77 | 2.71 | 2.74 | 2.62 | 2.67 | 2.77 | 7.56 | 7.45 | 6.78 | 6.55 | 7.31 | 6.71 | 4.42 | 4.44 | 4.29 | 4.19 | 4.34 | 4.19 | 0.74 | 0.75 | 0.72 | 1.01 | 0.88 | 0.79 | 5.18 | 5.14 | 5.17 | 5.15 | 5.22 | 4.98 | 0.71 | 0.85 | 0.71 | 1.07 | 0.96 | 0.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 475501 | 824 | 463777 | 882 | 350640.161 | 846.067 | 4.42 | 4.44 | 4.29 | 4.19 | 4.34 | 4.19 | 5.18 | 5.14 | 5.17 | 5.15 | 5.22 | 4.98 | 731000 | 2000 | 724000 | 2000 | 1451061 | 4734 | 1451000 | 1446327 | 11.2 | 4.3117 | 0.815 | 5.14 | 0.87167 | 18.9% | 16.96% | 30.3133 | 41.7333 | 2.7133 | 7.06 | 1459323.8 | 1449800 | 1670561 | 86.79%
2023-11-05 | 2024 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 335090.89 | 6:53 | 18:02 | 9066.2 | 9480.4 | 9458.5 | 9422.4 | 9553.2 | 9571.2 | 9435.8 | 9839 | 9426.3 | 9464.8 | 9245 | 9426.2 | 9367.4 | 9346.2 | 9336.7 | 9453.2 | 9347.7 | 9468.2 | 9454.4 | 9480.7 | 9499.6 | 9487.9 | 9334.8 | 9427.2 | 9301.4 | 8155.4 | 9328.9 | 9326 | 9586.2 | 9463.2 | 9293.3 | 9558.9 | 9602.8 | 9646.9 | 9604.1 | 9547 | 9680.3 | 9555.9 | 9618.3 | 9513.4 | 10428.6 | 9269.2 | 10272 | 9137.4 | 9734.9 | 10958.2 | 9041 | 10400.7 | 8675.9 | 8904.1 | 9518.6 | 8931.4 | 9864.3 | 8649.6 | 9814.7 | 8719.8 | 8646.9 | 10037.3 | 8687.4 | 9956.8 | 9834.6 | 8653.2 | 9573.8 | 9048.7 | 9301.2 | 8745.9 | 9259.6 | 9769.8 | 10014.9 | 8964 | 9843.2 | 8639.8 | 9506.4 | 9366.4 | 8717.7 | 9888.4 | 8592 | 9953.8 | 8694.8 | 9823.5 | 9011.1 | 9802 | 9121 | 10205.1 | 8964.6 | 9623.7 | 8840 | 7885.5 | 9712 | 9396 | 8742.6 | 10160.3 | 9821.1 | 9006.3 | 8924.4 | 9841.3 | 8773 | 9137.9 | 10012.8 | 8685.9 | 10102.9 | 8746.1 | 9834.5 | 8968.7 | 9957.5 | 8511.1 | 10011.5 | 8964.7 | 9871.1 | 8965 | 9966.5 | 9094.8 | 8798.5 | 9757.4 | 8918.8 | 8737.7 | 9831.6 | 10019.2 | 9776.4 | 8917.8 | 9943.3 | 8877.7 | 9542.5 | 8960.1 | 9523.3 | 8291.8 | 9672 | 8894.7 | 8923.7 | 8876 | 8817.3 | 7622.4 | 8695.2 | 7644.4 | 8820.5 | 8822.6 | 10288.9 | 8874.9 | 10372.8 | 9109.2 | 10153.4 | 8890.2 | 9068.4 | 8906 | 9973.4 | 10374.9 | 10199.9 | 10127.6 | 10218.8 | 10249.5 | 9184.1 | 10230.3 | 10157.6 | 10243.6 | 10326.9 | 10297 | 10360.5 | 9188.9 | 10313 | 9168.1 | 31.276 | 31.0461 | 31.081 | 31.0626 | 31.4677 | 31.2636 | 0 | 41.6 | 0 | 0 | 41.9 | 41.7 | 3.51 | 3.5229 | 3.6138 | 3.3791 | 3.3909 | 3.3528 | 7.929 | 7.319 | 7.478 | 7.716 | 7.575 | 7.495 | 4.4743 | 4.5079 | 4.3602 | 4.2346 | 4.3939 | 4.3975 | 0.72125 | 0.77625 | 0.74086 | 1.0293 | 0.90577 | 0.87101 | 5.2997 | 5.2675 | 5.3248 | 5.2689 | 5.3443 | 5.2924 | 0.71497 | 0.8783 | 0.72602 | 1.0973 | 0.98503 | 1.0042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 476253 | 825 | 464526 | 884 | 352136.228 | 850.8 | 4.4743 | 4.5079 | 4.3602 | 4.2346 | 4.3939 | 4.3975 | 5.2997 | 5.2675 | 5.3248 | 5.2689 | 5.3443 | 5.2924 | 752000 | 1000 | 749000 | 2000 | 1496067 | 4733 | 1498000 | 1491334 | 11.15 | 4.3947 | 0.84073 | 5.2996 | 0.90097 | 19.13% | 17% | 31.1995 | 41.7333 | 3.4616 | 7.5853 | 1504639.3 | 1494867 | 1724400.482 | 86.69%
2023-11-06 | 2024 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 335090.89 | 6:50 | 18:02 | 8929.3 | 9319.1 | 9307 | 9285.1 | 9397.5 | 9397.1 | 9264.4 | 9655.7 | 9273.5 | 9325.6 | 9103.3 | 9270.8 | 9229.7 | 9222.4 | 9173.2 | 9297.9 | 9181.3 | 9309.1 | 9310.9 | 9343.2 | 9350.7 | 9341.3 | 9177.7 | 9276.8 | 9143.5 | 8022.2 | 9190.2 | 9174.5 | 9427.5 | 9303.3 | 9133.7 | 9396.1 | 9438.7 | 9486.7 | 9435.9 | 9375.9 | 9506.2 | 9385 | 9447.9 | 9345.2 | 10258.1 | 9115.9 | 10100.3 | 8991.4 | 9557.1 | 10762 | 8889.6 | 10239.3 | 8543.9 | 8767.5 | 9383.5 | 8817.7 | 9730 | 8527.3 | 9666.6 | 8581 | 8532.3 | 9903.6 | 8554.4 | 9807.8 | 9687.9 | 8526.2 | 9415.9 | 8892.5 | 9139.8 | 8591.4 | 9099.6 | 9598.9 | 9842.2 | 8812 | 9671.5 | 8491.8 | 9352.2 | 9199.5 | 8573.2 | 9711.8 | 8442.9 | 9796.8 | 8553.7 | 9658 | 8861.9 | 9626.7 | 8932.4 | 10016.5 | 8786.7 | 9419.1 | 8679.3 | 7723 | 9501.3 | 9210.2 | 8571 | 9954.3 | 9636.8 | 8844.7 | 8764.7 | 9627.6 | 8550 | 8924.8 | 9772.7 | 8490.5 | 9857.9 | 8538 | 9579.2 | 8760.1 | 9690 | 8304.3 | 9736.7 | 8735.3 | 9554 | 8723.4 | 9703.1 | 8854.5 | 8603.7 | 9522.5 | 8713.2 | 8529 | 9596.9 | 9770.5 | 9539.3 | 8702.4 | 9688.9 | 8651.2 | 9318.2 | 8753.6 | 9284.1 | 8051.8 | 9422.7 | 8676.9 | 8718.3 | 8672.2 | 8601.1 | 7447.1 | 8520.5 | 7504.7 | 8629.6 | 8629.7 | 10070.2 | 8693.2 | 10161.8 | 8913 | 9932.4 | 8691.2 | 8862.4 | 8713 | 9786.3 | 10164.7 | 9981.8 | 9916.2 | 9999.4 | 10040.2 | 9004 | 10032 | 9949.8 | 10037.1 | 10132 | 10100.4 | 10163.3 | 9009.6 | 10099.4 | 8978.2 | 30.6426 | 30.3924 | 30.3398 | 30.517 | 31.0766 | 30.6607 | 40.3693 | 41.5314 | 41.862 | 40.1576 | 41.4433 | 41.1309 | 2.905 | 2.8671 | 2.8421 | 2.8468 | 2.8413 | 2.8101 | 6.201 | 5.799 | 5.758 | 5.583 | 6.102 | 5.853 | 4.3953 | 4.4409 | 4.2893 | 4.1569 | 4.2957 | 4.3132 | 0.71955 | 0.76075 | 0.7388 | 1.0216 | 0.88762 | 0.86097 | 5.2052 | 5.1806 | 5.2353 | 5.1553 | 5.2212 | 5.1958 | 0.71253 | 0.86052 | 0.72334 | 1.0899 | 0.96816 | 0.99154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 476992 | 827 | 465260 | 885 | 353603.561 | 855.6 | 4.3953 | 4.4409 | 4.2893 | 4.1569 | 4.2957 | 4.3132 | 5.2052 | 5.1806 | 5.2353 | 5.1553 | 5.2212 | 5.1958 | 739000 | 2000 | 734000 | 1000 | 1467333 | 4800 | 1470000 | 1462533 | 11.2 | 4.3152 | 0.83155 | 5.1989 | 0.891 | 19.27% | 17.14% | 30.6048 | 41.0824 | 2.8521 | 5.8827 | 1475652.6 | 1466334 | 1690395.4092 | 86.75%
2023-11-07 | 2024 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 335090.89 | 6:55 | 18:00 | 7085 | 7376.8 | 7319.1 | 7303.9 | 7377.3 | 7430.8 | 7341.7 | 7653.5 | 7377.4 | 7400.6 | 7252.3 | 7385.2 | 7358.4 | 7346.9 | 7344.6 | 7432.2 | 7343.7 | 7466.2 | 7467.6 | 7481 | 7546 | 7519.3 | 7458.2 | 7506.9 | 7423.3 | 6481.8 | 7380.5 | 7406.7 | 7669.6 | 7594.1 | 7497 | 7688.1 | 7759.5 | 7770.4 | 7689 | 7660.9 | 7779 | 7712.7 | 7768.2 | 7722.6 | 8483.1 | 7530.3 | 8373.6 | 7427.1 | 7934 | 8938 | 7361.6 | 8470.1 | 6834.6 | 7020.5 | 7499.4 | 7071.4 | 7781.9 | 6853.9 | 7779.4 | 6909.1 | 6864.9 | 7961.9 | 6846 | 7871.8 | 7749.7 | 6810.4 | 7519.6 | 7093.1 | 7366.8 | 6935.6 | 7328.5 | 7744.9 | 7918 | 7099.5 | 7777.2 | 6829.6 | 7521.6 | 7401.2 | 6882.7 | 7808 | 6770.4 | 7844.6 | 6845.7 | 7720.8 | 7155.3 | 7754.3 | 7233.2 | 8100.4 | 7127 | 7662.9 | 7021.8 | 6286.9 | 7779.2 | 7534 | 7051.2 | 8197.4 | 7951.1 | 7297.6 | 7231.4 | 7975.6 | 7147.3 | 7436.8 | 8167.4 | 7086.4 | 8271.8 | 7143.4 | 8054.7 | 7334.5 | 8157.7 | 6961.9 | 8196.2 | 7337.9 | 8070.9 | 7329.4 | 8136.4 | 7436.8 | 7160.1 | 7942.3 | 7285.9 | 7119.5 | 8044.4 | 8193.9 | 7997.9 | 7318.4 | 8157.2 | 7282.8 | 7827.2 | 7346.5 | 7778.1 | 6802.1 | 7957.7 | 7305 | 7282.7 | 7220.7 | 7253.7 | 6231.4 | 7076.4 | 6215.8 | 7022.2 | 7032.9 | 8197.2 | 7072.6 | 8259.6 | 7255.4 | 8067.9 | 7065.5 | 7195.1 | 7109.4 | 7888.3 | 8221.2 | 8079.3 | 8050.1 | 8107.9 | 8141.1 | 7308.4 | 8130.4 | 7932.2 | 8005.1 | 8072.2 | 8049.1 | 8123.5 | 7223.9 | 8116.1 | 7212.1 | 30.1643 | 29.9642 | 29.8963 | 30.036 | 30.2999 | 30.1564 | 37.9883 | 39.3244 | 40.0116 | 38.5017 | 39.6822 | 39.1282 | 2.284 | 2.2573 | 2.2477 | 2.3133 | 2.2933 | 2.0842 | 4.256 | 3.857 | 4.145 | 3.962 | 5.135 | 3.792 | 3.5545 | 3.7038 | 3.6435 | 3.456 | 3.6768 | 3.5763 | 0.61477 | 0.62067 | 0.65101 | 0.87391 | 0.75102 | 0.65909 | 4.0863 | 4.1713 | 4.2788 | 4.0848 | 4.3155 | 4.1568 | 0.61397 | 0.70247 | 0.63909 | 0.92592 | 0.82939 | 0.79504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 477589 | 828 | 465864 | 887 | 354800.961 | 860.467 | 3.5545 | 3.7038 | 3.6435 | 3.456 | 3.6768 | 3.5763 | 4.0863 | 4.1713 | 4.2788 | 4.0848 | 4.3155 | 4.1568 | 597000 | 1000 | 604000 | 2000 | 1197400 | 4867 | 1198000 | 1192533 | 11.0833 | 3.6018 | 0.69508 | 4.1823 | 0.75098 | 19.3% | 17.96% | 30.0862 | 39.1061 | 2.2466 | 4.1912 | 1202725.7 | 1195200 | 1372223.7887 | 87.1%
2023-11-08 | 2024 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 335090.89 | 6:52 | 18:01 | 6743.1 | 7052.2 | 7056.1 | 7026.7 | 7129 | 7194.8 | 7057.9 | 7349.1 | 7018.4 | 7018.3 | 6895.8 | 7018.9 | 7034 | 6979 | 7069.8 | 7136.2 | 7052.1 | 7135.1 | 7088.6 | 7105.2 | 7135.9 | 7124.2 | 7004.4 | 7072.9 | 6934 | 6083.6 | 6986.4 | 6965.3 | 7164.2 | 7072.8 | 6947 | 7132.9 | 7153.7 | 7186.7 | 7162.2 | 7108.1 | 7202.1 | 7124.6 | 7183.9 | 7108.6 | 7868.8 | 6999.7 | 7758.7 | 6897.9 | 7339 | 8255.6 | 6818 | 7854.7 | 6472.7 | 6602.5 | 7115.6 | 6630.8 | 7366.3 | 6452 | 7339.7 | 6512.1 | 6474.8 | 7516.2 | 6403.1 | 7433 | 7318.1 | 6416.8 | 7137.6 | 6740.2 | 6969.9 | 6561.5 | 6942.5 | 7329 | 7506.7 | 6724.3 | 7369 | 6482.5 | 7134.1 | 7022.8 | 6530.2 | 7418.2 | 6429.9 | 7448 | 6503.3 | 7343.8 | 6777.5 | 7360.3 | 6873.4 | 7661.2 | 6732.7 | 7238.7 | 6643.8 | 5932.9 | 7277 | 7075.5 | 6559.6 | 7611.4 | 7351.6 | 6720.6 | 6635.1 | 7394.1 | 6575.3 | 6834.6 | 7482.4 | 6491.5 | 7561.6 | 6521.6 | 7370.5 | 6690.2 | 7415.2 | 6316.7 | 7490 | 6690.6 | 7382.7 | 6693.2 | 7432.1 | 6784.9 | 6557.1 | 7242.5 | 6649.7 | 6489.1 | 7333.1 | 7439.7 | 7274.8 | 6644.6 | 7398.4 | 6595.2 | 7119.5 | 6685.9 | 7071.6 | 6160.6 | 7206 | 6607.3 | 6612.8 | 6573.3 | 6560.8 | 5651.5 | 6383.8 | 5626.1 | 6353.5 | 6370.2 | 7566.2 | 6499.3 | 7606.8 | 6644.1 | 7384.8 | 6451.5 | 6557.3 | 6447.8 | 7353.6 | 7654.9 | 7519.2 | 7471.2 | 7516.5 | 7538.2 | 6768.3 | 7543.6 | 7512.2 | 7560.7 | 7611.2 | 7578.6 | 7622.1 | 6763.8 | 7620.3 | 6759.9 | 29.0727 | 28.7241 | 28.633 | 28.6978 | 28.8737 | 28.9197 | 36.6683 | 37.7426 | 37.8005 | 36.7561 | 38.0549 | 37.3794 | 1.4521 | 1.8036 | 1.7768 | 1.8058 | 1.8485 | 1.7889 | 3.548 | 3.975 | 3.817 | 3.768 | 3.718 | 3.683 | 3.4361 | 3.469 | 3.4032 | 3.2992 | 3.355 | 3.3292 | 0.58656 | 0.60419 | 0.60268 | 0.82285 | 0.70032 | 0.62891 | 3.9271 | 3.8914 | 3.9749 | 3.907 | 3.9186 | 3.839 | 0.58237 | 0.68635 | 0.59192 | 0.8745 | 0.77501 | 0.75483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 478152 | 830 | 466421 | 889 | 355917.828 | 865.333 | 3.4361 | 3.469 | 3.4032 | 3.2992 | 3.355 | 3.3292 | 3.9271 | 3.8914 | 3.9749 | 3.907 | 3.9186 | 3.839 | 563000 | 2000 | 557000 | 2000 | 1116867 | 4866 | 1116000 | 1112001 | 11.15 | 3.382 | 0.65759 | 3.9097 | 0.71083 | 19.44% | 18.18% | 28.8202 | 37.4003 | 1.746 | 3.7515 | 1121191.1 | 1114800 | 1292224.353 | 86.27%
2023-11-09 | 2024 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 335090.89 | 6:50 | 18:01 | 7204.3 | 7512.8 | 7525.7 | 7498.9 | 7620.7 | 7638.5 | 7493 | 7794.5 | 7495.3 | 7477 | 7353.1 | 7487.2 | 7489.2 | 7445.8 | 7495.5 | 7589.6 | 7490.6 | 7579.9 | 7548.9 | 7570.2 | 7589.6 | 7581.7 | 7469.3 | 7536 | 7410.7 | 6496.6 | 7439 | 7435.2 | 7665.9 | 7568.7 | 7428.9 | 7636.9 | 7642.1 | 7679.1 | 7664.8 | 7607.7 | 7710.2 | 7625.1 | 7676.6 | 7587.1 | 8316.8 | 7388.4 | 8319 | 7373.9 | 7845.9 | 8814.6 | 7298.7 | 8411.2 | 6909.9 | 7086 | 7595 | 7075.9 | 7879.2 | 7005.6 | 7760.3 | 6936.2 | 6859.9 | 7951.1 | 6894.1 | 7896 | 7798.8 | 6872 | 7586.7 | 7122.9 | 7382.9 | 6913.2 | 7303.9 | 7714.9 | 7943.3 | 7089 | 7761.4 | 6836 | 7546.2 | 7399.1 | 6896.8 | 7813 | 6771.8 | 7860.4 | 6849.9 | 7730.8 | 7158.9 | 7764.7 | 7266 | 8040.6 | 7127.2 | 7667 | 7032.7 | 6276 | 7706.5 | 7486.3 | 6964.1 | 8073.9 | 7802.2 | 7129.2 | 7040.4 | 7838.3 | 6953.6 | 7242.3 | 7938.4 | 6905.1 | 8040.8 | 6934.2 | 7833.1 | 7125.1 | 7936.2 | 6770.9 | 7975 | 7122.2 | 7864.2 | 7135.1 | 7927.2 | 7223.1 | 6988.2 | 7746.9 | 7088.7 | 6925.5 | 7837.1 | 7971.9 | 7768.7 | 7129.3 | 7918.2 | 7063.6 | 7602.4 | 7135.4 | 7563.9 | 6591.9 | 7711.2 | 7081.7 | 7116 | 7088 | 7027 | 6074.1 | 6952.5 | 6153.7 | 7019.9 | 7039.5 | 8245.5 | 7095.4 | 8304.1 | 7275 | 8127.5 | 7111.8 | 7190.2 | 6995.5 | 7996 | 8316.4 | 8193.1 | 8132.5 | 8191.8 | 8211.6 | 7364.4 | 8194.1 | 8203.4 | 8245.8 | 8292.3 | 8257 | 8306.4 | 7365.2 | 8287.1 | 7362.9 | 29.21 | 28.84 | 28.65 | 28.8 | 28.82 | 28.95 | 37.63 | 38.54 | 29.04 | 37.71 | 38.69 | 38.04 | 2.76 | 2.84 | 2.81 | 2.83 | 2.63 | 2.75 | 5.47 | 6.05 | 5.3 | 5.73 | 5.63 | 5.72 | 3.67 | 3.71 | 3.66 | 3.48 | 3.56 | 3.6 | 0.62 | 0.65 | 0.65 | 0.86 | 0.74 | 0.71 | 4.18 | 4.14 | 4.25 | 4.12 | 4.19 | 4.17 | 0.62 | 0.74 | 0.64 | 0.92 | 0.82 | 0.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 478751 | 831 | 467020 | 891 | 357111.8 | 870.1 | 3.67 | 3.71 | 3.66 | 3.48 | 3.56 | 3.6 | 4.18 | 4.14 | 4.25 | 4.12 | 4.19 | 4.17 | 599000 | 1000 | 599000 | 2000 | 1193972 | 4767 | 1195000 | 1189205 | 11.1833 | 3.6133 | 0.705 | 4.175 | 0.76333 | 19.51% | 18.28% | 28.8783 | 36.6083 | 2.77 | 5.65 | 1198733.4 | 1192667 | 1383123 | 86.23%
2023-11-10 | 2024 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 335090.89 | 6:54 | 17:59 | 9625.7 | 10076.4 | 10013 | 9991.3 | 10081.9 | 10160.6 | 10047.5 | 10462.7 | 10000.5 | 10043.2 | 9803.5 | 10007.5 | 9943.6 | 9917.3 | 9925.2 | 10025.8 | 9929.5 | 10039.5 | 10002.1 | 10044.5 | 10023.7 | 10011.8 | 9837.1 | 9941.2 | 9799.7 | 8616.9 | 9834.3 | 9818.7 | 10094.9 | 9984.3 | 9768.7 | 10053.1 | 10112.7 | 10151.7 | 10091.6 | 10033.5 | 10173.1 | 10053.2 | 10130.5 | 9998 | 10982.6 | 9764.6 | 10836.7 | 9642 | 10292.5 | 11533.7 | 9550.8 | 10943.3 | 9184.9 | 9431.1 | 10072.9 | 9423.7 | 10437.2 | 9240.3 | 10414.2 | 9224.1 | 9194.6 | 10655.9 | 9190.6 | 10552.1 | 10403.6 | 9169 | 10197.5 | 9638.8 | 9886.7 | 9297 | 9841.2 | 10323 | 10625.2 | 9497.3 | 10459.3 | 9165.3 | 10074.7 | 9962.6 | 9239.2 | 10527.7 | 9157.2 | 10536.3 | 9218.7 | 10417.2 | 9560.6 | 10368.5 | 9702.4 | 10780.1 | 9518.6 | 10222.4 | 9415 | 8355.5 | 10350.1 | 9921.5 | 9237.3 | 10729.8 | 10327.1 | 9451.7 | 9358 | 10456.2 | 9261.3 | 9622.1 | 10517 | 9193.9 | 10654.5 | 9184.2 | 10323.9 | 9437.5 | 10453.5 | 8934.7 | 10506.3 | 9409.4 | 10362.2 | 9424.5 | 10481.3 | 9549.2 | 9282.4 | 10296.2 | 9403.1 | 9207.8 | 10351 | 10466.3 | 10295.4 | 9276 | 10379.6 | 9243.4 | 10057.2 | 9423.6 | 10001.1 | 8648.3 | 10076.4 | 9223.8 | 9398.1 | 9417.9 | 9236 | 8010.8 | 9237.6 | 8152.4 | 9250.3 | 9255 | 10738.2 | 9250.3 | 10779.4 | 9472.7 | 10638.5 | 9333.6 | 9511.2 | 9370.9 | 10410.6 | 10797 | 10688.2 | 10588.9 | 10692.2 | 10717.4 | 9561.9 | 10658.3 | 10731.2 | 10785 | 10824.8 | 10789.6 | 10817.5 | 9615.5 | 10856.5 | 9634.8 | 28.7954 | 28.5 |  | 28.5601 | 29.0121 | 28.3239 | 37.438 | 38.9953 | 22.0844 | 37.2206 | 37.9281 | 37.5677 | 4.3101 | 4.2742 |  | 4.2912 | 4.1932 | 3.9655 | 8.256 | 7.682 |  | 8.558 | 8.154 | 7.929 | 4.5568 | 4.5975 |  | 4.3346 | 4.4738 | 4.4089 | 0.67606 | 0.74341 | 0.44536 | 0.96343 | 0.81449 | 0.69647 | 5.5445 | 5.4795 |  | 5.5132 | 5.5297 | 5.4735 | 0.67696 | 0.84428 | 0.44104 | 1.0171 | 0.89718 | 0.83398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 479546 | 833 | 467808 | 892 | 358688.761 | 874.867 | 4.5568 | 4.5975 | 0 | 4.3346 | 4.4738 | 4.4089 | 5.5445 | 5.4795 | 0 | 5.5132 | 5.5297 | 5.4735 | 795000 | 2000 | 788000 | 1000 | 1576961 | 4767 | 1580000 | 1572194 | 11.0833 | 4.4743 | 0.7232 | 5.5081 | 0.78508 | 16.16% | 14.25% | 28.6383 | 35.2057 | 4.2069 | 8.1158 | 1586799.5 | 1576066 | 1809213.583 | 87.11%
2023-11-11 | 2024 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 335090.89 | 6:51 | 18:02 | 10800.8 | 11184.5 | 11063.2 | 11044.9 | 11110 | 11200.9 | 11153.5 | 11467.4 | 11122 | 11129.4 | 10957.2 | 11133.1 | 11106.9 | 11058.9 | 11068.9 | 11172.2 | 11051.4 | 11158.7 | 11145.5 | 11219.9 | 11156.1 | 11169.2 | 11006.2 | 11098.1 | 10975 | 9729.9 | 11023.2 | 10995.4 | 11207.1 | 11086.5 | 10939.9 | 11171.2 | 11396.3 | 11468.4 | 11399.3 | 11333.1 | 11290.9 | 11197.4 | 11237.7 | 11119.4 | 11884 | 10908.7 | 11755.2 | 10803 | 11373.7 | 12328.9 | 10717.2 | 11835.3 | 10357.7 | 10625.7 | 11230.9 | 10613.5 | 11492.4 | 10398.5 | 11483.4 | 10375.8 | 10339.3 | 11645.2 | 10347.5 | 11593.7 | 11492 | 10325.7 | 11263.9 | 10806.9 | 10996.3 | 10388.4 | 10973.7 | 11342.4 | 11583.3 | 10620.2 | 11462.5 | 10253.1 | 11157.6 | 11078.7 | 10374.6 | 11512.2 | 10259.2 | 11533.7 | 10320.7 | 11425 | 10679.4 | 11381 | 10822.1 | 11687.2 | 10633.1 | 11253.3 | 10515.6 | 9325.8 | 11261.9 | 10858.9 | 10356.7 | 11671 | 11358.3 | 10592.5 | 9810.8 | 11107.8 | 10382.9 | 10786.4 | 11500.8 | 10318.6 | 11615.3 | 10313.2 | 11389.2 | 10598.8 | 11450.6 | 10042.3 | 11524.6 | 10582.3 | 11423.5 | 10583.1 | 11498.6 | 10735.5 | 10409.5 | 11351.7 | 10555.4 | 10323.5 | 11383.3 | 11526.7 | 11356 | 10490.3 | 11459.5 | 10456.4 | 11165.7 | 10606.7 | 11121.8 | 9783.1 | 11256.2 | 10443.4 | 10605.1 | 10625.4 | 10422.4 | 9041.4 | 10413.1 | 9214.6 | 10444 | 10479.3 | 11755.5 | 10541.1 | 11789.1 | 10755.5 | 11679.4 | 10598.7 | 10758.1 | 10616.3 | 11507.4 | 11787.2 | 11715.7 | 11623.8 | 11717.5 | 11744.2 | 10826.8 | 11693.8 | 11719.2 | 11756.8 | 11792.1 | 11765.1 | 11806.4 | 10860.7 | 11808.5 | 10859.2 | 25.5586 | 25.0452 | 25.0035 | 25.062 | 25.0172 | 24.912 | 35.3708 | 37.6382 | 15.4814 | 35.151 | 37.2953 | 35.7516 | 3.223 | 3.2519 | 3.1657 | 3.2715 | 3.0956 | 3.0726 | 5.712 | 6.117 | 5.917 | 5.787 | 5.803 | 6.019 | 4.9771 | 5.0054 | 4.8708 | 4.7433 | 4.8927 | 4.866 | 0.74683 | 0.82074 | 0.83178 | 1.0798 | 0.92165 | 0.80073 | 6.151 | 6.0983 | 6.1991 | 6.1786 | 6.1748 | 6.1728 | 0.74532 | 0.93475 | 0.79908 | 1.1497 | 1.0194 | 0.96297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480429 | 835 | 468682 | 894 | 360438.095 | 879.533 | 4.9771 | 5.0054 | 4.8708 | 4.7433 | 4.8927 | 4.866 | 6.151 | 6.0983 | 6.1991 | 6.1786 | 6.1748 | 6.1728 | 883000 | 2000 | 874000 | 2000 | 1749334 | 4666 | 1753000 | 1744668 | 11.1833 | 4.8925 | 0.86692 | 6.1624 | 0.93521 | 17.72% | 15.18% | 25.0997 | 32.7814 | 3.18 | 5.8925 | 1762103 | 1748200 | 2027139.838 | 86.24%
2023-11-12 | 2024 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 335090.89 | 6:50 | 18:01 | 10730.4 | 11140.1 | 11034.3 | 11009.8 | 11096.3 | 11161.7 | 11106 | 11458.3 | 11105.4 | 11132.2 | 10916.4 | 11108.9 | 11069.9 | 11032.5 | 11011.2 | 11139.1 | 11018 | 11145.4 | 11127.7 | 11189.2 | 11142.8 | 11150.6 | 10965.7 | 11079 | 10937.2 | 9634 | 10988.4 | 10956.7 | 11195.2 | 11050.4 | 10881 | 11156.9 | 11296.8 | 11340.1 | 11294.7 | 11226.8 | 11289.1 | 11179.1 | 11231.3 | 11088.5 | 11906.9 | 10809.5 | 11775.5 | 10692.2 | 11336.7 | 12338.8 | 10601 | 11852.1 | 10260.2 | 10533.3 | 11207 | 10519 | 11515.1 | 10282.3 | 11489.7 | 10213.4 | 10276.8 | 11685.1 | 10262.8 | 11626.9 | 11513.5 | 10240.1 | 11296 | 10780.7 | 10992.7 | 10361.4 | 10970.5 | 11387 | 11638.7 | 10588.9 | 11509.4 | 10210.3 | 11175.9 | 11082.9 | 10316.9 | 11528 | 10209.6 | 11584.3 | 10272.9 | 11475.2 | 10641.4 | 11415.1 | 10788.7 | 11761.2 | 10591 | 11277 | 10472.9 | 9288.6 | 11361.1 | 10978.9 | 10276.4 | 11714.2 | 11369.1 | 10498.7 | 10355.5 | 11439.1 | 10308.9 | 10728.3 | 11536.1 | 10258.9 | 11099.7 | 10090.8 | 11400.3 | 10541.7 | 11490.9 | 9983.9 | 11562.3 | 10524.1 | 11430.7 | 10456.9 | 11466.6 | 10649.2 | 10347.6 | 11386.6 | 10501.2 | 10278.6 | 11394.2 | 11591.4 | 11391.3 | 10457.4 | 11516 | 10412.2 | 11162.8 | 10549.8 | 11150.1 | 9727.4 | 11275.9 | 10406 | 10590.4 | 10603.1 | 10390.3 | 9026.6 | 10390.5 | 9183.2 | 10415 | 10418.1 | 11862.5 | 10488.3 | 11913.8 | 10741 | 11781.7 | 10561.3 | 10745.2 | 10564.9 | 11606.2 | 11924.1 | 11822.9 | 11732 | 11828.8 | 11850.5 | 10835.5 | 11814.4 | 11838.6 | 11885.7 | 11941.6 | 11906.7 | 11948.7 | 10880.9 | 11933.3 | 10874 | 25.2998 | 24.785 | 24.747 | 24.7979 | 24.8491 | 24.6974 | 0 | 37.3 | 0 | 0 | 38.083 | 37.3 | 2.2993 | 2.2259 | 2.2613 | 2.2643 | 2.3062 | 2.2247 | 4.663 | 4.48 | 4.564 | 5.112 | 4.976 | 4.542 | 4.8956 | 4.9705 | 4.8215 | 4.7212 | 4.8698 | 4.8306 | 0.72682 | 0.79791 | 0.83464 | 1.0907 | 0.90963 | 0.78276 | 6.083 | 6.0462 | 6.1357 | 6.1293 | 6.1507 | 6.1761 | 0.73303 | 0.90845 | 0.80076 | 1.1599 | 1.0076 | 0.94269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 481310 | 836 | 469556 | 896 | 362186.095 | 884.333 | 4.8956 | 4.9705 | 4.8215 | 4.7212 | 4.8698 | 4.8306 | 6.083 | 6.0462 | 6.1357 | 6.1293 | 6.1507 | 6.1761 | 881000 | 1000 | 874000 | 2000 | 1748000 | 4800 | 1752000 | 1743200 | 11.1833 | 4.8515 | 0.85708 | 6.1202 | 0.92541 | 17.67% | 15.12% | 24.8627 | 37.561 | 2.2636 | 4.7228 | 1760742.8 | 1747000 | 2010289.3745 | 86.9%
2023-11-13 | 2024 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 335090.89 | 6:51 | 17:50 | 8372.1 | 8730.6 | 8653.3 | 8625 | 8722.8 | 8778.3 | 8719.1 | 9067.6 | 8727.3 | 8734.9 | 8539.1 | 8714 | 8682.6 | 8639.5 | 8670.1 | 8765.7 | 8667.8 | 8777.2 | 8742.6 | 8781.5 | 8779.1 | 8766.7 | 8621.9 | 8704.5 | 8556.4 | 7528.3 | 8598 | 8573.7 | 8814.7 | 8700.3 | 8541.2 | 8785.1 | 8836 | 8882.6 | 8829.9 | 8775.1 | 8885.5 | 8782.8 | 8834.7 | 8722.5 | 9605.2 | 8555 | 9494.7 | 8455.5 | 9014.9 | 10092.2 | 8375 | 9581.6 | 8025.6 | 8233.8 | 8798.4 | 8288.4 | 9105.2 | 8059.6 | 9094.8 | 8077.7 | 8032.8 | 9264.1 | 8029.8 | 9206.6 | 9085.4 | 8010.7 | 8857.7 | 8374.4 | 8589.9 | 8075.2 | 8554.5 | 8949.2 | 9227.1 | 8245.2 | 9062.1 | 7950.4 | 8774.5 | 8644.1 | 8061.4 | 9140 | 7961.4 | 9166.9 | 8015.6 | 9048.3 | 8282.4 | 8968 | 8405.3 | 9313.4 | 8247.2 | 8847 | 8170.3 | 7250.5 | 8949.3 | 8605.6 | 8013.1 | 9283.9 | 8952.5 | 8207.3 | 8107.2 | 9036.7 | 8051.3 | 8378.6 | 9154.8 | 8011.7 | 8956.5 | 7784.1 | 8986.8 | 8239.5 | 9096.8 | 7803.6 | 9150.3 | 8220 | 9024.4 | 8214.2 | 9113.2 | 8331 | 8084.1 | 8979.5 | 8199.6 | 8028.8 | 9005.3 | 9167.4 | 8990.4 | 8179.2 | 9103.5 | 8121.8 | 8777.7 | 8227.5 | 8744.3 | 7584.5 | 8856.7 | 8125.2 | 8251 | 8261.4 | 8112.3 | 7039.6 | 8103.9 | 7172.8 | 8165.3 | 8168.5 | 9456.9 | 8182.3 | 9500.3 | 8373.7 | 9370.7 | 8230.2 | 8369.9 | 8249 | 9147.2 | 9490.7 | 9370 | 9300.3 | 9385.2 | 9419.6 | 8439.6 | 9379.4 | 9393.1 | 9438.4 | 9502.8 | 9465.5 | 9501.8 | 8460.1 | 9476 | 8459 | 25.2222 | 24.9127 | 24.4232 | 24.9066 | 24.8221 | 24.6524 | 0 | 35.4 | 0 | 0 | 35.2952 | 34.9 | 2.1827 | 2.1562 | 2.1238 | 2.2182 | 2.2156 | 2.1741 | 4.286 | 4.742 | 4.711 | 4.494 | 4.245 | 4.346 | 3.8864 | 4.0448 | 3.962 | 3.8236 | 3.9092 | 3.8989 | 0.60706 | 0.61235 | 0.69751 | 0.91346 | 0.68968 | 0.605 | 4.6287 | 4.6321 | 4.7178 | 4.5793 | 4.6905 | 4.6977 | 0.62551 | 0.70011 | 0.67833 | 0.94794 | 0.78694 | 0.73414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 482004 | 838 | 470245 | 898 | 363563.495 | 889 | 3.8864 | 4.0448 | 3.962 | 3.8236 | 3.9092 | 3.8989 | 4.6287 | 4.6321 | 4.7178 | 4.5793 | 4.6905 | 4.6977 | 694000 | 2000 | 689000 | 2000 | 1377400 | 4667 | 1379000 | 1372733 | 10.9833 | 3.9208 | 0.68751 | 4.6577 | 0.7455 | 17.53% | 16.01% | 24.8232 | 35.1984 | 2.1784 | 4.4707 | 1384783.5 | 1376266 | 1550299.6078 | 88.77%
2023-11-14 | 2024 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 335090.89 | 7:12 | 17:59 | 8487.6 | 8809.5 | 8713.4 | 8691.5 | 8758.3 | 8844 | 8811.4 | 9100 | 8799.7 | 8820 | 8630.6 | 8796.1 | 8766.8 | 8721.8 | 8718.5 | 8834.1 | 8705 | 8800 | 8798.7 | 8854.4 | 8811.5 | 8818.6 | 8671.6 | 8755.9 | 8650.2 | 7651.8 | 8695 | 8664.3 | 8864.7 | 8739.5 | 8616.6 | 8844.1 | 8959.2 | 9010.3 | 8961.2 | 8904.9 | 8944 | 8852.6 | 8890.8 | 8798.4 | 9554 | 8645.5 | 9455.3 | 8551.7 | 9033.1 | 9935.5 | 8428.1 | 9508.9 | 8135.2 | 8345.8 | 8871.9 | 8393.4 | 9145.9 | 8169.3 | 9121.5 | 8185.6 | 8154.1 | 9293.4 | 8140.3 | 9241 | 9142.7 | 8126.4 | 8934.7 | 8508.6 | 8697.7 | 8225.4 | 8683.9 | 9048.4 | 9271.5 | 8406.7 | 9155.1 | 8130.1 | 8879.8 | 8795.8 | 8211.9 | 9215.8 | 8116.2 | 9224.4 | 8171.5 | 9128.6 | 8447 | 9079.9 | 8549.4 | 9370.4 | 8402.5 | 8956.7 | 8320.8 | 7403.9 | 9056 | 8740 | 8187.7 | 9341.2 | 9047.9 | 8372.9 | 8273.2 | 9087.4 | 8195.7 | 8530.8 | 9205.7 | 8168 | 9295.3 | 8159.1 | 9071.8 | 8380.6 | 9154.4 | 7940.5 | 9211.1 | 8353.5 | 9105.8 | 8346.4 | 9179.1 | 8463.8 | 8244.5 | 9077.7 | 8348.5 | 8191.2 | 9087.6 | 9242.8 | 9072.1 | 8346.3 | 9183.5 | 8285 | 8883.2 | 8377.2 | 8855.1 | 7740.6 | 8979.7 | 8301.7 | 8411.6 | 8414 | 8298.6 | 7197.4 | 8241.4 | 7308.4 | 8283 | 8296.5 | 9435.1 | 8298 | 9472.6 | 8478.7 | 9361.5 | 8354.9 | 8481.4 | 8376.2 | 9186.6 | 9466.2 | 9386.7 | 9315.6 | 9389 | 9418.8 | 8549 | 9379 | 9397.3 | 9427.4 | 9455.1 | 9425.3 | 9465.9 | 8555.7 | 9477.3 | 8559.4 | 26.1414 | 25.6614 | 26.4108 | 25.6552 | 25.6635 | 25.7067 | 0 | 35.1 | 0 | 0 | 34.8 | 35.1 | 3.2554 | 3.2477 | 3.1984 | 3.2863 | 3.2289 | 3.1328 | 6.062 | 5.999 | 5.335 | 7.457 | 6.514 | 6.025 | 3.9539 |  | 3.9285 |  | 3.9429 |  | 0.59136 |  | 0.67475 |  | 0.75632 |  | 4.7553 |  | 4.8137 |  | 4.8212 |  | 0.59733 |  | 0.65189 |  | 0.84071 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 482703 | 839 | 470942 | 899 | 364954.5 | 893.733 | 3.9539 | 0 | 3.9285 | 0 | 3.9429 | 0 | 4.7553 | 0 | 4.8137 | 0 | 4.8212 | 0 | 699000 | 1000 | 697000 | 1000 | 1391005 | 4733 | 1394000 | 1386272 | 10.7833 | 3.9418 | 0.67414 | 4.7967 | 0.69665 | 17.1% | 14.52% | 25.8732 | 35 | 3.2249 | 6.232 | 1399130.1 | 1388800 | 1595910.7953 | 87.02%
2023-11-15 | 2024 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 335090.89 | 6:57 | 17:57 | 9125.4 | 9526.8 | 9362.1 | 9348.6 | 9399.8 | 9543.2 | 9504.4 | 9890.4 | 9520.1 | 9506.9 | 9321.7 | 9516.2 | 9450.1 | 9427.2 | 9359.4 | 9507.4 | 9370.5 | 9499.4 | 9488.1 | 9534.2 | 9512.9 | 9505.1 | 9340.3 | 9440.9 | 9319.5 | 8198.5 | 9366.9 | 9332.7 | 9585.6 | 9449.5 | 9287.3 | 9558.5 | 9613.1 | 9658.1 | 9607.4 | 9555.6 | 9689.1 | 9571.2 | 9632.7 | 9496.5 | 10450.1 | 9272.2 | 10332.4 | 9163.4 | 9776.9 | 11007.3 | 9080.1 | 10432.1 | 8737.5 | 8967.3 | 9588.2 | 9025.9 | 9916.6 | 8737.3 | 9917.7 | 8790 | 8742.7 | 10105.6 | 8735.7 | 10041.2 | 9911.9 | 8716.1 | 9670.6 | 9132.9 | 9331.9 | 8782.6 | 9303.5 | 9758.2 | 10054 | 8971.5 | 9872.5 | 8649.9 | 9542.1 | 9403.4 | 8747.9 | 9944.9 | 8633.9 | 9967 | 8692.9 | 9830.8 | 9024.1 | 9782.1 | 9145.6 | 10182.2 | 8983.7 | 9649.6 | 8899.6 | 7904 | 9782.7 | 9400.8 | 8750.2 | 10162.7 | 9788.3 | 8966.5 | 8865.9 | 9869.7 | 8759.2 | 9129.8 | 9980.1 | 8716.6 | 10088.2 | 8722.2 | 9788.4 | 8966.3 | 9921.5 | 8484.8 | 9983.2 | 8949.9 | 9845.4 | 8945.4 | 9945.4 | 9077.9 | 8810.2 | 9807.6 | 8941.8 | 8757.2 | 9826.7 | 10016.5 | 9818.2 | 8932.1 | 9953 | 8868.5 | 9579.1 | 8989.5 | 9553.5 | 8293.5 | 9684.6 | 8881.8 | 9030.1 | 9050.5 | 8884.3 | 7699.8 | 8854.4 | 7820.3 | 8865 | 8876.5 | 10300.2 | 8882.8 | 10363.2 | 9104 | 10233.5 | 8972.5 | 7298.2 | 0 | 9963.6 | 10353.6 | 10188.1 | 10105.1 | 10212.9 | 10256.3 | 9166.3 | 10213.9 | 10246.5 | 10311.1 | 10371 | 10328 | 10378.2 | 9201.5 | 10317.4 | 9189.5 | 21.7243 | 21.112 |  | 21.39 | 20.8463 | 20.8125 | 0 | 24.7 | 0 | 0 | 24.6155 | 24.2 | 2.7061 | 2.7809 | 2.8232 | 2.7735 | 2.7242 | 2.5469 | 5.4 | 5.488 | 5.882 | 5.527 | 5.842 | 4.997 | 4.2975 |  | 4.2281 |  | 4.223 |  | 0.72901 |  | 0.78826 |  | 0.85735 |  | 5.2165 |  | 5.2302 |  | 5.2304 |  | 0.72866 |  | 0.75942 |  | 0.95276 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 483458 | 841 | 471682 | 901 | 366443.5 | 898.467 | 4.2975 | 0 | 4.2281 | 0 | 4.223 | 0 | 5.2165 | 0 | 5.2302 | 0 | 5.2304 | 0 | 755000 | 2000 | 740000 | 2000 | 1489000 | 4734 | 1491000 | 1484266 | 11 | 4.2496 | 0.79154 | 5.2257 | 0.81361 | 18.63% | 15.57% | 21.177 | 24.5052 | 2.7258 | 5.5227 | 1497876.1 | 1498187 | 1732907.7698 | 86.46%
2023-11-16 | 2024 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 335090.89 | 6:58 | 17:56 | 9301.9 | 9727.3 | 9602.2 | 9577.4 | 9648.5 | 9817.3 | 9698.5 | 10105.2 | 9700.1 | 9649.8 | 9515.6 | 9704.2 | 9670.5 | 9620.1 | 9632.3 | 9769.8 | 9664.5 | 9796.9 | 9737.9 | 9774.1 | 9789.8 | 9771.3 | 9612.8 | 9710.7 | 9534.2 | 8380.6 | 9574.5 | 9552.7 | 9830.8 | 9716.9 | 9508.1 | 9785.8 | 9845.6 | 9895.5 | 9828.8 | 9781.3 | 9920.6 | 9808.6 | 9869.5 | 9734.9 | 10716.2 | 9511.3 | 10601.6 | 9397.9 | 10028.8 | 11266.7 | 9306.9 | 10705 | 8905.2 | 9138.9 | 9782.8 | 9196.5 | 10139.6 | 8941.2 | 10108.5 | 8964.6 | 8915.6 | 10306.8 | 8893.3 | 10226.9 | 10094.9 | 8877.4 | 9870.9 | 9334.6 | 9538.7 | 8957.5 | 9494.5 | 9963.9 | 10263.7 | 9159.1 | 10081.9 | 8836.5 | 9744.9 | 9605 | 8937.9 | 10155.1 | 8816 | 10182.7 | 8888.6 | 10048.8 | 9221.9 | 10004.3 | 9334.3 | 10401.5 | 9167.3 | 9836.1 | 9089.6 | 8063.1 | 9982.9 | 9602.1 | 8960.9 | 10405.4 | 10036.1 | 9189.5 | 9073.8 | 10111.8 | 8961.1 | 9333.1 | 10200 | 8902.4 | 10345.2 | 8924.3 | 10039.9 | 9163.3 | 10187.3 | 8691.9 | 10249.8 | 9167.8 | 10119.2 | 9189.3 | 10226.9 | 9323.6 | 9000.6 | 10018.1 | 9123.1 | 8931.4 | 10030.6 | 10226.8 | 10024.7 | 9106.9 | 10156.1 | 9053.4 | 9793.3 | 9198.7 | 9779.9 | 8480.8 | 9892.4 | 9060.4 | 9193.9 | 9210 | 9040.2 | 7829.1 | 9015.7 | 7954.7 | 9033 | 9046.2 | 10520.3 | 9081.2 | 10600.1 | 9314.1 | 10450.6 | 9152.3 | 9310.5 | 9160.9 | 10207.2 | 10607.3 | 10454.5 | 10366.5 | 10459.2 | 10497.2 | 9394.2 | 10478.9 | 10466.4 | 10535.2 | 10623.9 | 10576.8 | 10621 | 9425.2 | 10551.6 | 9400.2 | 20.1094 | 19.9131 | 20.2916 | 20.0267 | 19.6701 | 19.3264 | 0 | 22.4 | 0 | 0 | 21.7 | 20.8592 | 2.8026 | 2.889 | 2.8312 | 2.9212 | 2.8678 | 2.5829 | 5.467 | 5.576 | 5.161 | 5.746 | 5.615 | 5.405 | 4.3753 |  | 4.2851 |  | 4.2709 |  | 0.74774 |  | 0.79969 |  | 0.88645 |  | 5.3342 |  | 5.3789 |  | 5.3308 |  | 0.71557 |  | 0.746 |  | 0.94884 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 484229 | 843 | 472450 | 903 | 367976.695 | 903.4 | 4.3753 | 0 | 4.2851 | 0 | 4.2709 | 0 | 5.3342 | 0 | 5.3789 | 0 | 5.3308 | 0 | 771000 | 2000 | 768000 | 2000 | 1533195 | 4933 | 1535000 | 1528262 | 10.9667 | 4.3105 | 0.81129 | 5.348 | 0.80347 | 18.82% | 15.02% | 19.8896 | 21.6531 | 2.8158 | 5.495 | 1543035 | 1532133 | 1777842.825 | 86.18%
2023-11-17 | 2024 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 335090.89 | 6:59 | 17:55 | 7829.4 | 8153.4 | 8089.7 | 8078.8 | 8137.1 | 8222.9 | 8134.3 | 8451.5 | 8169.6 | 8125.6 | 7996.5 | 8161.9 | 8119.2 | 8077.5 | 8061 | 8188.8 | 8078.4 | 8178.5 | 8160.9 | 8193.3 | 8201 | 8192 | 8044.3 | 8125.8 | 8004.2 | 7034.2 | 8035.3 | 8010.9 | 8240.2 | 8126.9 | 7979.4 | 8219.3 | 8258.1 | 8301.3 | 8260.4 | 8208.2 | 8321.6 | 8224.3 | 8274.5 | 8174.7 | 8967.1 | 7969.9 | 8870.9 | 7873 | 8383.6 | 9421.7 | 7766.6 | 8954.6 | 7493.3 | 7692.6 | 8230.3 | 7748 | 8523.9 | 7532.5 | 8510.6 | 7546.3 | 7452.9 | 8653 | 7446.8 | 8572.2 | 8417.8 | 7441.4 | 8257.3 | 7801.8 | 8008.1 | 7553.2 | 7997.1 | 8396.5 | 8643.6 | 7725.3 | 8488.4 | 7444.7 | 8224.2 | 8092.4 | 7532.2 | 8555.3 | 7425.9 | 8579.4 | 7493.1 | 8445.2 | 7775.9 | 8430.8 | 7871.5 | 8771.4 | 7727.4 | 8302.7 | 7668.2 | 6802.4 | 8409.3 | 8107.4 | 7532 | 8751.6 | 8443.1 | 7724.8 | 7641.3 | 8494.6 | 7527.2 | 7864.6 | 8605.5 | 7506.2 | 8691.5 | 7510.8 | 8443.5 | 7717.7 | 8557.5 | 7313.7 | 8611.5 | 7711.4 | 8482.4 | 7710.1 | 8561.9 | 7818.7 | 7576.6 | 8437.7 | 7679.2 | 7520.9 | 8451.8 | 8626.9 | 8437.3 | 7700 | 8570.8 | 7636.8 | 8235.5 | 7713.8 | 8203.8 | 7143.6 | 8348.3 | 7655.6 | 7751.1 | 7755.1 | 7645.7 | 6607.6 | 7599.4 | 6706.6 | 7651.7 | 7654.7 | 8885 | 7664.3 | 8958.2 | 7862.9 | 8816.3 | 7730.6 | 7859.5 | 7758.6 | 8613.4 | 8947.7 | 8814.2 | 8750.4 | 8829.5 | 8860 | 7926.3 | 8841.2 | 8813.5 | 8875.3 | 8977.8 | 8935.7 | 8969.1 | 7954.9 | 8881.8 | 7926.6 | 20.8248 | 20.3167 | 19.5718 | 20.5659 | 19.9642 | 19.9364 | 0 | 22.9 | 0 | 0 | 21.9 | 22.1 | 2.7968 | 2.8415 | 2.8775 | 2.8348 | 2.7522 | 2.5449 | 5.84 | 5.727 | 5.265 | 5.262 | 5.888 | 5.509 | 3.7502 |  | 3.7061 |  | 3.6839 |  | 0.67357 |  | 0.71872 |  | 0.71532 |  | 4.4322 |  | 4.4552 |  | 4.4597 |  | 0.67532 |  | 0.69399 |  | 0.82057 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 484877 | 844 | 473098 | 905 | 369267.6 | 908.333 | 3.7502 | 0 | 3.7061 | 0 | 3.6839 | 0 | 4.4322 | 0 | 4.4552 | 0 | 4.4597 | 0 | 648000 | 1000 | 648000 | 2000 | 1290905 | 4933 | 1293000 | 1285972 | 10.9333 | 3.7134 | 0.70254 | 4.449 | 0.72996 | 18.92% | 16.41% | 20.1966 | 22.3 | 2.7746 | 5.5818 | 1297829.5 | 1289201 | 1487985.421 | 86.64%
2023-11-18 | 2024 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 335090.89 | 7:02 | 17:56 | 7730.2 | 8050.6 | 8020.1 | 8008.9 | 8074.4 | 8146.9 | 8055.3 | 8346.7 | 8030 | 8006.7 | 7858.4 | 8012 | 7966.5 | 7931.3 | 7950.2 | 8046.6 | 7948.6 | 8034.3 | 8000.1 | 8025.5 | 8029.3 | 8022.4 | 7859.8 | 7946.7 | 7826.8 | 6886.6 | 7864.9 | 7836.3 | 8039.6 | 7910.8 | 7782.2 | 8020.8 | 8063.6 | 8113.9 | 8082.6 | 8015.4 | 8115.3 | 8016.8 | 8063.5 | 7981.4 | 8713.4 | 7750.3 | 8619.5 | 7658.2 | 8174 | 9180.9 | 7558.8 | 8695.5 | 7358.6 | 7555.4 | 8072.4 | 7587.2 | 8354 | 7372.8 | 8339.8 | 7396.9 | 7341.4 | 8510.3 | 7360.7 | 8450.2 | 8288.2 | 7358.2 | 8126.4 | 7688.6 | 7889.7 | 7426 | 7861.3 | 8257.6 | 8503.1 | 7597.8 | 8354.4 | 7335.2 | 8085.4 | 7975.8 | 7365.6 | 8433.4 | 7313.7 | 8432.2 | 7368.3 | 8332.7 | 7654.8 | 8302.7 | 7760.9 | 8629.4 | 7609.8 | 8172.7 | 7537.3 | 6682 | 8267.3 | 7951 | 7365.1 | 8564.9 | 8249.2 | 7557.9 | 7476.8 | 8323.1 | 7364.1 | 7677.4 | 8394.1 | 7321.3 | 8473 | 7324.6 | 8236.4 | 7535.4 | 8353.1 | 7140.8 | 8409.2 | 7534.5 | 8290.7 | 7532.1 | 8374.1 | 7641 | 7407.2 | 8258.9 | 7509 | 7355.7 | 8269.8 | 8431.7 | 8256.4 | 7528 | 8388.2 | 7476.7 | 8061.4 | 7551.4 | 8032.1 | 6995.7 | 8174.9 | 7490.1 | 7590.7 | 7597.7 | 7490.2 | 6478.7 | 7425.1 | 6555.3 | 7466.4 | 7474.4 | 8733.5 | 7525 | 8788.2 | 7699.5 | 8632 | 7562.8 | 7687.8 | 7578.5 | 8477.2 | 8804.2 | 8680 | 8608.4 | 8683.7 | 8715.4 | 7790.7 | 8689 | 8731.7 | 8770.7 | 8837.4 | 8797.6 | 8832.7 | 7833.6 | 8769.1 | 7815.3 | 20.6133 | 20.3784 | 20.434 | 20.493 | 20.1536 | 19.8829 | 0 | 23.3 | 0 | 0 | 22.3 | 22.3 | 2.3386 | 2.305 | 2.3053 | 2.354 | 2.2445 | 2.1448 | 4.498 | 4.445 | 4.192 | 4.335 | 4.69 | 4.521 | 3.7212 |  | 3.6192 |  | 3.6332 |  | 0.65007 |  | 0.69105 |  | 0.73847 |  | 4.4213 |  | 4.3955 |  | 4.4237 |  | 0.64586 |  | 0.66599 |  | 0.83539 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 485513 | 846 | 473733 | 906 | 370534.6 | 913.2 | 3.7212 | 0 | 3.6192 | 0 | 3.6332 | 0 | 4.4213 | 0 | 4.3955 | 0 | 4.4237 | 0 | 636000 | 2000 | 635000 | 1000 | 1267000 | 4867 | 1268000 | 1262133 | 10.9 | 3.6579 | 0.6932 | 4.4135 | 0.71575 | 18.95% | 16.22% | 20.3259 | 22.6333 | 2.282 | 4.4468 | 1272782.3 | 1264933 | 1475464.6705 | 85.73%
2023-11-19 | 2024 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 335090.89 | 7:02 | 17:56 | 8151.2 | 8486.8 | 8379.8 | 8364.8 | 8429.5 | 8552.2 | 8486.3 | 8844.4 | 8507.7 | 8475.7 | 8344.2 | 8507.2 | 8460.3 | 8425.6 | 8407.8 | 8528.5 | 8415.3 | 8515.7 | 8509.3 | 8545.9 | 8534.9 | 8532.1 | 8360 | 8453.1 | 7923.4 | 6968.5 | 7964.6 | 7930.5 | 8139.1 | 8011.8 | 7887.2 | 8130.9 | 8581 | 8638.6 | 8606.8 | 8533.7 | 8653.2 | 8551.7 | 8596.7 | 8485.5 | 9301.5 | 8265.1 | 9189.3 | 8169 | 8712.6 | 9779.5 | 8077.1 | 9274.7 | 7834.7 | 8042.4 | 8606.4 | 8092.4 | 8909.2 | 7870.4 | 8886.7 | 7877.5 | 7839.6 | 9058.2 | 7841.8 | 9005.7 | 8874.3 | 7826.3 | 8675.9 | 8197.1 | 8381 | 7892.1 | 8351.7 | 8771.9 | 9033.2 | 8070.5 | 8871.3 | 7780.7 | 8588.8 | 8458.1 | 7868.6 | 8938.2 | 7755.9 | 8962.3 | 7816 | 8840.7 | 8137.7 | 8825.2 | 8238.3 | 9180.1 | 8088.2 | 8682.2 | 8004.7 | 7110 | 8785.8 | 8459.3 | 7855.6 | 9123.7 | 8784 | 8035.6 | 7939.1 | 8881.1 | 7465.9 | 7785.6 | 8474.2 | 7382.6 | 8610 | 7430.8 | 8344.9 | 7629.8 | 8908.5 | 7604.8 | 8961.6 | 8030.2 | 8837.5 | 8027 | 8915.8 | 8151.6 | 7910.6 | 8809.9 | 8014.1 | 7852.6 | 8816.4 | 8985 | 8798.9 | 8009.8 | 8929.6 | 7959.2 | 8592.5 | 8052.2 | 8562.6 | 7454.9 | 8696.9 | 7971.4 | 8062.7 | 8066.7 | 7956.1 | 6879.7 | 7884.1 | 6973.4 | 7968.4 | 7967.8 | 9276.9 | 7994.3 | 9330.6 | 8192.4 | 9192.4 | 8055.8 | 8193 | 8066.9 | 8990.9 | 9344.4 | 9197.9 | 9119.7 | 9217.3 | 9253 | 8267.1 | 9215.1 | 9239.6 | 9273.1 | 9349.8 | 9313.5 | 9356.4 | 8295.9 | 9312.3 | 8269.8 | 21.3989 | 21.1107 | 21.2158 | 21.1766 | 20.8855 | 20.7059 | 0 | 24 | 0 | 0 | 23.2 | 23.3 | 2.3817 | 2.3983 | 2.4193 | 2.3657 | 2.3641 | 2.1651 | 4.286 | 4.321 | 4.131 | 3.824 | 4.501 | 3.961 | 3.8576 |  | 3.7752 |  | 3.8172 |  | 0.659 |  | 0.71064 |  | 0.79455 |  | 4.659 |  | 4.6723 |  | 4.7147 |  | 0.65884 |  | 0.68493 |  | 0.87857 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 486186 | 848 | 474406 | 908 | 371874.562 | 918.067 | 3.8576 | 0 | 3.7752 | 0 | 3.8172 | 0 | 4.659 | 0 | 4.6723 | 0 | 4.7147 | 0 | 673000 | 2000 | 673000 | 2000 | 1339962 | 4867 | 1342000 | 1335095 | 10.9 | 3.8167 | 0.7214 | 4.682 | 0.74078 | 18.9% | 15.82% | 21.0822 | 23.5 | 2.349 | 4.1707 | 1346594.9 | 1345298 | 1555271.8038 | 86.5%
2023-11-20 | 2024 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 335090.89 | 7:01 | 17:56 | 8591.5 | 8970 | 8894.8 | 8849.1 | 8984.8 | 9060.1 | 8998.3 | 9339.8 | 8968.9 | 8944.6 | 8805 | 8975.6 | 8940.3 | 8893.8 | 8889 | 9018 | 8905.3 | 9019.2 | 9001 | 9037.1 | 9038.3 | 9028.3 | 8864.5 | 8961.2 | 8817.9 | 7751.8 | 8860.8 | 8827 | 9070.8 | 8943.7 | 8785.5 | 9053.4 | 9086.9 | 9153.3 | 9099.6 | 9028.2 | 9161.6 | 9062.8 | 9119.1 | 8993.7 | 9876.7 | 8764.7 | 9761.4 | 8675.3 | 9243.8 | 10394.6 | 8585.6 | 9865.1 | 8258.5 | 8471.4 | 9076.6 | 8530.3 | 9410 | 8319.9 | 9360.8 | 8303.5 | 8263.2 | 9557.3 | 8261.6 | 9483.8 | 9351 | 8248.3 | 9139.4 | 8638.8 | 8828.2 | 8301.9 | 8786.3 | 9240.5 | 9502.3 | 8500 | 9329.3 | 8196.8 | 9031.9 | 8905.6 | 8277.6 | 9415.9 | 8170.4 | 9431.1 | 8236.6 | 9319.8 | 8575.5 | 9300.9 | 8676.7 | 9671 | 8514.7 | 9138 | 8420.1 | 7490 | 9246.9 | 8909.1 | 8303.7 | 9637.4 | 9310.5 | 8535.6 | 8437.3 | 9357.6 | 8322.8 | 8669.4 | 9474.7 | 8287.7 | 9601.3 | 8277.3 | 9312.3 | 8508 | 9437.6 | 8049.1 | 9492.3 | 8493.4 | 9369.7 | 8509.7 | 9462.5 | 8622.7 | 8347.9 | 9306.9 | 8466.1 | 8290.8 | 9304.7 | 9495.2 | 9293.4 | 8459.5 | 9428 | 8414.1 | 9081.8 | 8519.1 | 9056.1 | 7885.7 | 9190.7 | 8421.1 | 8527.4 | 8523.7 | 8416.2 | 7274.7 | 8347.7 | 7383.1 | 8413.2 | 8416.9 | 9770 | 8424.8 | 9826.6 | 8626.4 | 9685.7 | 8491.4 | 8638.4 | 8515.8 | 9463.8 | 9842.2 | 9683.3 | 9604.7 | 9714.5 | 9743.1 | 8698.2 | 9694 | 9707 | 9775.6 | 9863.4 | 9817.5 | 9853.8 | 8744.3 | 9794.6 | 8715.4 | 22.2662 | 21.8547 | 21.9508 | 22.1111 | 21.6183 | 21.7797 | 0 | 24.5 | 0 | 0 | 23.7 | 24.2 | 3.0225 | 2.9976 | 3.0663 | 3.07 | 2.8388 | 2.8312 | 6.535 | 6.281 | 6.358 | 6.769 | 6.024 | 5.774 | 3.9832 |  | 3.9285 |  | 3.947 |  | 0.6653 |  | 0.74079 |  | 0.82868 |  | 4.8769 |  | 4.935 |  | 4.938 |  | 0.67217 |  | 0.71302 |  | 0.91547 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 486900 | 849 | 475119 | 910 | 373296.296 | 922.867 | 3.9832 | 0 | 3.9285 | 0 | 3.947 | 0 | 4.8769 | 0 | 4.935 | 0 | 4.938 | 0 | 714000 | 1000 | 713000 | 2000 | 1421734 | 4800 | 1424000 | 1416934 | 10.9167 | 3.9529 | 0.74492 | 4.9166 | 0.76689 | 18.84% | 15.6% | 21.9301 | 24.1333 | 2.9711 | 6.2902 | 1429484.4 | 1420133 | 1635778.1837 | 86.82%
2023-11-21 | 2024 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 335090.89 | 7:01 | 17:57 | 8581.2 | 8984.2 | 8878.2 | 8833.9 | 8960.2 | 9061.3 | 9007.1 | 9367.9 | 8953.8 | 8909.3 | 8802.8 | 8966 | 8918.4 | 8880.9 | 8897.2 | 9010.3 | 8908.4 | 9020.4 | 8985.8 | 9032 | 9023.5 | 9019.2 | 8828 | 8931.3 | 8791.3 | 7729.1 | 8831.9 | 8798.5 | 9026.9 | 8882.1 | 8734.6 | 9007.8 | 9061.8 | 9137.4 | 9081.4 | 9004.1 | 9119.8 | 9010.9 | 9066.8 | 8958.8 | 9835.1 | 8735.1 | 9721.1 | 8649 | 9217.4 | 10333.9 | 8549.9 | 9813.7 | 8252.1 | 8462.9 | 9062.3 | 8501.9 | 9381.1 | 8292.4 | 9345.8 | 8254 | 8257.7 | 9558.2 | 8253.2 | 9457 | 9304.3 | 8232.6 | 9081.7 | 8574.4 | 8809.6 | 8285.8 | 8779.1 | 9197.5 | 9471.7 | 8465.2 | 9297.4 | 8163.9 | 9002 | 8868.2 | 8251.6 | 9372.7 | 8140.6 | 9379.8 | 8206.5 | 9275.3 | 8518.4 | 9231.9 | 8617.3 | 9603.4 | 8459.9 | 9071 | 8375.7 | 7446.5 | 9208.8 | 8864.4 | 8285.4 | 9603.7 | 9275.7 | 8503.2 | 8402.2 | 9323.3 | 8303 | 8639.1 | 9424.3 | 8256.1 | 9529.9 | 8238.5 | 9245.1 | 8469.5 | 9357.5 | 8012.4 | 9411.5 | 8441.6 | 9290.5 | 8451.8 | 9393.5 | 8578.7 | 8323.5 | 9261.6 | 8435.3 | 8261 | 9206 | 9384.5 | 9227 | 8398.6 | 9351 | 8360 | 9022.9 | 8474.8 | 9009.8 | 7838.3 | 9119.9 | 8368.1 | 8497.7 | 8500.2 | 8376.1 | 7242.7 | 8325.5 | 7374.8 | 8360.9 | 8371.6 | 9725.2 | 8400.8 | 9784 | 8601.2 | 9652.2 | 8467.9 | 8612.8 | 8477.2 | 9420.2 | 9781.5 | 9632 | 9559.2 | 9668.1 | 9707.8 | 8675.4 | 9645.9 | 9647.8 | 9706.3 | 9762.4 | 9731.2 | 9774.2 | 8695 | 9728 | 8679.5 | 21.6646 | 21.2343 | 21.4091 | 21.3616 | 21.0285 | 20.9836 | 0 | 24.3 | 0 | 0 | 23.7 | 23.7 | 2.8314 | 2.8839 | 2.8985 | 2.9674 | 2.8238 | 2.7271 | 5.207 | 4.952 | 5.022 | 5.47 | 5.394 | 5.019 | 4.0266 |  | 3.9098 |  | 3.938 |  | 0.68549 |  | 0.72444 |  | 0.8476 |  | 4.9273 |  | 4.9328 |  | 4.9328 |  | 0.68474 |  | 0.70146 |  | 0.93218 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 487612 | 851 | 475828 | 911 | 374711.7 | 927.733 | 4.0266 | 0 | 3.9098 | 0 | 3.938 | 0 | 4.9273 | 0 | 4.9328 | 0 | 4.9328 | 0 | 712000 | 2000 | 709000 | 1000 | 1415404 | 4866 | 1418000 | 1410538 | 10.9333 | 3.9581 | 0.75251 | 4.931 | 0.7728 | 19.01% | 15.67% | 21.2803 | 23.9 | 2.8554 | 5.1773 | 1423559.6 | 1413601 | 1638857.2885 | 86.26%
2023-11-22 | 2024 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 335090.89 | 7:01 | 17:56 | 8901.3 | 9302 | 9176.8 | 9148.7 | 9247.9 | 9390.7 | 9293.5 | 9704.6 | 9281.9 | 9230.7 | 9138.2 | 9311.4 | 9250.2 | 9225.7 | 9220.2 | 9326.8 | 9236.4 | 9377.3 | 9339.3 | 9376.6 | 9387.5 | 9377.3 | 9196.4 | 9300.6 | 9154.8 | 8045.7 | 9180 | 9151 | 9393 | 9245.6 | 9129.9 | 9387 | 9433.2 | 9492 | 8342.1 | 8286.3 | 9506.8 | 9401.1 | 9468.1 | 9329 | 10271.5 | 9104.7 | 10162.3 | 9014.3 | 9594.5 | 10796.8 | 8909.6 | 10239.5 | 8567.9 | 8789.4 | 9400.7 | 8842.7 | 9741.9 | 8583.8 | 9730.8 | 8626.1 | 8588.4 | 9940.8 | 8575.9 | 9845.3 | 9700.1 | 8565.5 | 9466.7 | 8936.2 | 9167.6 | 8629.6 | 9132.1 | 9595.4 | 9863.3 | 8825.8 | 9677.5 | 8500.5 | 9369.3 | 9230.8 | 8588.8 | 9759.8 | 8460.7 | 9782.7 | 8545.9 | 9660.3 | 8902.9 | 9634 | 8989.6 | 10037.3 | 8836 | 9493.4 | 8738.1 | 7787.7 | 9566 | 9244.4 | 8617.4 | 9985.8 | 9625.7 | 8813.6 | 8708.5 | 9684.7 | 8582 | 8973.5 | 9806.4 | 8579.3 | 9931.6 | 8569.8 | 9643.1 | 8799.4 | 9768.6 | 8344.8 | 9815.7 | 8776.6 | 9685.7 | 8795.4 | 9757.9 | 8903.1 | 8640.1 | 9610.4 | 8742.1 | 8567.5 | 9601.3 | 9810.6 | 9602.2 | 8743.3 | 9754.9 | 8706.9 | 9368.9 | 8802.7 | 9364.5 | 8162.7 | 9510.6 | 8720.2 | 8833 | 8816 | 8705.4 | 7527.2 | 8647.8 | 7659.1 | 8687.3 | 8693.6 | 10153.5 | 8741.7 | 10200.2 | 8948.8 | 10056.1 | 8805.8 | 8963.4 | 8809.1 | 9859.9 | 10243.2 | 10082.8 | 9999.7 | 10113 | 10133.9 | 9038.2 | 10084.8 | 10096.8 | 10173.1 | 10233.9 | 10206.6 | 10245.8 | 9096.6 | 10164.7 | 9082.6 | 19.2164 | 19.7842 | 19.7511 | 19.4724 | 19.6046 |  | 0 | 23.3 | 0 | 0 | 22.6 |  | 2.0844 | 1.9636 | 1.998 | 2.0923 | 2.0449 |  | 5.359 | 5.325 | 5.167 | 5.155 | 5.24 |  | 4.1409 |  | 4.0495 |  | 4.0812 |  | 0.73301 |  | 0.77652 |  | 0.87639 |  | 5.1269 |  | 5.1556 |  | 5.1524 |  | 0.72896 |  | 0.74496 |  | 0.94836 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 488350 | 852 | 476566 | 913 | 376182.763 | 932.533 | 4.1409 | 0 | 4.0495 | 0 | 4.0812 | 0 | 5.1269 | 0 | 5.1556 | 0 | 5.1524 | 0 | 738000 | 1000 | 738000 | 2000 | 1471063 | 4800 | 1473000 | 1466263 | 10.9167 | 4.0906 | 0.79531 | 5.145 | 0.80743 | 19.44% | 15.69% | 19.5657 | 22.95 | 2.0367 | 5.2492 | 1479683.6 | 1469534 | 1706224.5145 | 86.13%
2023-11-23 | 2024 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 335090.89 | 7:02 | 17:55 | 8768.3 | 9167.5 | 9074.5 | 9045.5 | 9172.3 | 9259.4 | 9156.4 | 9536.7 | 9119.2 | 9078.7 | 8984.6 | 9156.5 | 9099.4 | 9065.4 | 9060.5 | 9178.6 | 9077.3 | 9201.2 | 9167.2 | 9209.1 | 9218.4 | 9206.7 | 9028.8 | 9131.1 | 8991.3 | 7896.2 | 9010 | 8980.7 | 9221.6 | 9079.8 | 8967 | 9219.4 | 9267.1 | 9317.4 | 9272.3 | 9206.5 | 9351.1 | 9240.6 | 9304.2 | 9163.7 | 10039.9 | 8899.5 | 9938.1 | 8817.9 | 9387.8 | 10559.8 | 8706.5 | 10001.5 | 8429.9 | 8648.2 | 9259.1 | 8688 | 9598 | 8447.6 | 9560.1 | 8483.5 | 8447.4 | 9779.4 | 8440.6 | 9690.1 | 9537.3 | 8417.8 | 9357.6 | 8822.9 | 9035.5 | 8508.8 | 9003.3 | 9462.7 | 9723.3 | 8704.6 | 9558.5 | 8386.4 | 9248.6 | 9107.8 | 8473.9 | 9626.4 | 8345.9 | 9643 | 8416.2 | 9503.5 | 8770.2 | 9489.2 | 8844 | 9886.9 | 8687.9 | 9331 | 8589.1 | 7654.7 | 9400.7 | 9104.2 | 8474.1 | 9829.4 | 9480.4 | 8687.8 | 8597.1 | 9558.8 | 8486.3 | 8840 | 9668.9 | 8432.3 | 9771 | 8426.6 | 9483.2 | 8661.9 | 9604.9 | 8213.5 | 9654.7 | 8642.6 | 9527.3 | 8658.2 | 9594.7 | 8772.5 | 8488.1 | 9461.8 | 8610.1 | 8454 | 9463.9 | 9672.6 | 9469.2 | 8610.3 | 9614.4 | 8568.5 | 9235.1 | 8669.4 | 9215.6 | 8026 | 9359.6 | 8577.5 | 8696.2 | 8663.2 | 8554 | 7404.5 | 8507.7 | 7531.5 | 8546.1 | 8546.8 | 10001 | 8613.2 | 10072.1 | 8838.1 | 9908.7 | 8672.8 | 8830 | 8662.2 | 9686.3 | 10061.1 | 9905.4 | 9832.8 | 9936.6 | 9969.6 | 8905.2 | 9925.7 | 9915.8 | 10010.5 | 10055 | 10037.6 | 10061 | 8936 | 10005.4 | 8940.3 | 19.583 | 20.1698 | 20.5722 | 19.7062 | 19.776 | 19.9775 | 0 | 23.5 | 0 | 0 | 22.9 | 22.8624 | 1.7295 | 1.8605 | 1.7592 | 1.7531 | 1.5707 | 1.9098 | 5.683 | 5.499 | 5.624 | 5.872 | 5.936 | 5.629 | 4.0569 |  | 3.9527 |  | 4.0185 |  | 0.7182 |  | 0.751 |  | 0.85892 |  | 5.0282 |  | 5.0321 |  | 5.0761 |  | 0.71836 |  | 0.72701 |  | 0.93533 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 489078 | 854 | 477293 | 915 | 377632.6 | 937.4 | 4.0569 | 0 | 3.9527 | 0 | 4.0185 | 0 | 5.0282 | 0 | 5.0321 | 0 | 5.0761 | 0 | 728000 | 2000 | 727000 | 2000 | 1449837 | 4867 | 1451000 | 1444970 | 10.8833 | 4.0093 | 0.77604 | 5.0455 | 0.79357 | 19.36% | 15.73% | 19.9641 | 23.0875 | 1.7638 | 5.7072 | 1457911.7 | 1448467 | 1673778.2934 | 86.54%
2023-11-24 | 2024 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 335090.89 | 7:03 | 17:56 | 8753.7 | 9168.4 | 9087.8 | 9039.8 | 9186.9 | 9253.8 | 9186.1 | 9537.9 | 9124.5 | 9095.3 | 8989 | 9155.2 | 9095.5 | 9071.8 | 9048.3 | 9177.3 | 9074.6 | 9193 | 9162.6 | 9202.5 | 9213.5 | 9204.2 | 9032.5 | 9130.8 | 8990.9 | 7898.5 | 9009.1 | 8974.8 | 9216.5 | 9073.9 | 8973.6 | 9226.2 | 9266.7 | 9326.9 | 9233.3 | 9165.9 | 9346.7 | 9245.1 | 9316.1 | 9163.8 | 10066 | 8921.4 | 9989.4 | 8849.1 | 9440.5 | 10627.1 | 8773.8 | 10046.1 | 8428.8 | 8646.7 | 9261.8 | 8693.5 | 9585.7 | 8477.5 | 9554.4 | 8477.4 | 8441 | 9767.5 | 8429.1 | 9685.1 | 9541.5 | 8408.2 | 9339.6 | 8814.9 | 9017.9 | 8494.7 | 8988.3 | 9455.4 | 9717.7 | 8689.1 | 9534.7 | 8371.4 | 9239.3 | 9086.4 | 8463.1 | 9611.8 | 8333.1 | 9625.1 | 8387.2 | 9491.8 | 8767.7 | 9487.2 | 8859.2 | 9896.5 | 8687.3 | 9329.4 | 8583.5 | 7655.9 | 9403.1 | 9111.5 | 8494.1 | 9836.7 | 9493.8 | 8702.1 | 8602.6 | 9561.2 | 8500.3 | 8866.8 | 9683.8 | 8459.7 | 9779.8 | 8451.4 | 9501.2 | 8683.5 | 9630.5 | 8231.7 | 9689.8 | 8683.3 | 9556.4 | 8687.5 | 9648.6 | 8814.3 | 8509 | 9493.1 | 8636.6 | 8473.4 | 9488.2 | 9702.7 | 9501.2 | 8643.2 | 9645 | 8605.2 | 9262.8 | 8695.2 | 9230.9 | 8057 | 9389.7 | 8608.2 | 8715.7 | 8685.6 | 8592.4 | 7426.2 | 8505.4 | 7536.2 | 8508.6 | 8532.3 | 10015.5 | 8628.2 | 10083.7 | 8856.3 | 9914.1 | 8679.8 | 8827.6 | 8664.9 | 9712 | 10099.3 | 9932.8 | 9859.2 | 9966.5 | 9996 | 8916.3 | 9948.6 | 9957.8 | 10038.1 | 10109.2 | 10069.2 | 10110.4 | 8963.9 | 10035.1 | 8959.1 | 21.5024 | 21.1717 | 21.3924 | 21.1599 | 20.9609 | 20.8783 | 0 | 23.3 | 0 | 0 | 23 | 22.9 | 2.5567 | 2.5154 | 2.5611 | 2.5921 | 2.0978 | 2.4346 | 5.912 | 5.614 | 6.557 | 5.941 | 6.663 | 6.793 | 4.0671 |  | 3.9614 |  | 3.9914 |  | 0.72306 |  | 0.76036 |  | 0.84553 |  | 5.0113 |  | 5.0331 |  | 5.0753 |  | 0.71854 |  | 0.73182 |  | 0.9315 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 489806 | 856 | 478022 | 917 | 379083.5 | 942.333 | 4.0671 | 0 | 3.9614 | 0 | 3.9914 | 0 | 5.0113 | 0 | 5.0331 | 0 | 5.0753 | 0 | 728000 | 2000 | 729000 | 2000 | 1450900 | 4933 | 1453000 | 1445967 | 10.8833 | 4.0066 | 0.77632 | 5.0399 | 0.79395 | 19.38% | 15.75% | 21.1776 | 23.0667 | 2.4596 | 6.2467 | 1459513.9 | 1450200 | 1667234.1327 | 86.98%
2023-11-25 | 2024 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 335090.89 | 6:59 | 17:45 | 6621.3 | 6921.5 | 6824.5 | 6790.9 | 6888 | 6972.9 | 6931.8 | 7212.5 | 6919.9 | 6875.3 | 6824.4 | 6939.5 | 6896.6 | 6880.8 | 6855.7 | 6948.4 | 6860.7 | 6928.7 | 6949.3 | 6969.4 | 6992 | 6984.7 | 6867.6 | 6932 | 6813.9 | 5991.5 | 6841.6 | 6819.8 | 7010.2 | 6916.4 | 6813.6 | 6996.1 | 7004.7 | 7049.6 | 7035.9 | 6980.5 | 7060.7 | 6995.2 | 7045.9 | 6946.6 | 7589.9 | 6769.2 | 7533.5 | 6701.4 | 7151.6 | 8012.2 | 6633.2 | 7571.9 | 6403.2 | 6567.7 | 7022.8 | 6601.3 | 7268.4 | 6453.5 | 7221.9 | 6430.8 | 6383.1 | 7353.3 | 6403.3 | 7314.3 | 7201.1 | 6378.6 | 7015.5 | 6615.4 | 6802.2 | 6423.2 | 6786.9 | 7138.3 | 7320 | 6567.5 | 7178.8 | 6326.6 | 6978.1 | 6860.1 | 6398.3 | 7246.1 | 6294 | 7259.7 | 6348.1 | 7165.3 | 6620.7 | 7153.4 | 6682.4 | 7452.7 | 6565.4 | 7042.8 | 6495.9 | 5795.8 | 7108.2 | 6907.2 | 6416.6 | 7411.4 | 7165.5 | 6569.2 | 6500.2 | 7221 | 6442.5 | 6716.1 | 7332.5 | 6410.9 | 7398.6 | 6414.5 | 7202.5 | 6594 | 7292.8 | 6245.9 | 7336.5 | 6585 | 7234.5 | 6587.4 | 7298.4 | 6684.7 | 6456.2 | 7185.2 | 6556.2 | 6424.5 | 7205.5 | 7355.9 | 7202.6 | 6584 | 7309.5 | 6535.2 | 7030.6 | 6595.1 | 6993.5 | 6114.5 | 7137.6 | 6552.2 | 6625.5 | 6574.1 | 6556.2 | 5658.6 | 6459.9 | 5725.9 | 6445.7 | 6464.5 | 7560.5 | 6543.3 | 7602.5 | 6704 | 7476.7 | 6569.4 | 6678.1 | 6574.4 | 7328.5 | 7596 | 7477.7 | 7438.4 | 7501.8 | 7530.5 | 6750.5 | 7496.2 | 7504.2 | 7552.6 | 7610.3 | 7581.6 | 7607.8 | 6774 | 7549.7 | 6765.8 | 21.4458 | 21.1805 | 21.2823 | 21.2488 | 20.9937 | 20.8049 | 0 | 22.5 | 0 | 0 | 22.2 | 22.1 | 2.5049 | 2.6022 | 2.6385 | 2.5854 | 2.5263 | 2.283 | 5.767 | 5.517 | 5.353 | 5.599 | 5.594 | 5.301 | 3.1213 |  | 3.1229 |  | 3.1161 |  | 0.59614 |  | 0.62125 |  | 0.63073 |  | 3.5589 |  | 3.6736 |  | 3.7263 |  | 0.60299 |  | 0.6036 |  | 0.7148 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490357 | 857 | 478573 | 918 | 380181.496 | 947.333 | 3.1213 | 0 | 3.1229 | 0 | 3.1161 | 0 | 3.5589 | 0 | 3.6736 | 0 | 3.7263 | 0 | 551000 | 1000 | 551000 | 1000 | 1097996 | 5000 | 1100000 | 1092996 | 10.7667 | 3.1201 | 0.61604 | 3.6529 | 0.64046 | 19.74% | 17.53% | 21.1593 | 22.2667 | 2.5234 | 5.5218 | 1104209.3 | 1095867 | 1225731.3505 | 89.41%
2023-11-26 | 2024 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 335090.89 | 7:42 | 17:44 | 780.2 | 820.5 | 823.6 | 817.8 | 831.3 | 833.9 | 831.6 | 866.8 | 813.1 | 822.3 | 811.9 | 825.6 | 821.8 | 819.4 | 838.6 | 840 | 831.8 | 833.9 | 831.4 | 829.1 | 842.6 | 840.2 | 823.7 | 830.7 | 813.3 | 713.4 | 819.8 | 817.6 | 842.6 | 837.8 | 819.4 | 839.5 | 831.8 | 833.8 | 837.7 | 832 | 838.3 | 835.5 | 839.7 | 833.1 | 924.3 | 823.9 | 914.6 | 812.9 | 859.7 | 986 | 802.7 | 926.3 | 767.8 | 789.7 | 844.5 | 789.6 | 878.4 | 776.3 | 864 | 733.5 | 762.9 | 885.7 | 767.3 | 878 | 864.9 | 765.9 | 830.4 | 783.1 | 809.8 | 762.8 | 788.6 | 837.5 | 878.7 | 776 | 858.6 | 743.5 | 836.8 | 784.3 | 754.2 | 819.4 | 669.8 | 707.6 | 759.7 | 856.6 | 769.2 | 839.1 | 781.5 | 871.1 | 772.7 | 835 | 764.6 | 681.8 | 835.9 | 812.6 | 753.3 | 881.5 | 857 | 787.9 | 785 | 864.6 | 765.4 | 795.4 | 876.5 | 759.2 | 887.4 | 758.8 | 863.5 | 783.5 | 874.8 | 740 | 877.9 | 781.4 | 865.3 | 783.3 | 860.5 | 790.8 | 766.9 | 854.4 | 777.6 | 757.5 | 860.9 | 869.5 | 854.7 | 781 | 868.1 | 772.4 | 837.8 | 777 | 826 | 721.7 | 844.3 | 771.7 | 781.1 | 781 | 774.1 | 664.2 | 758.7 | 659.4 | 736.8 | 756.4 | 876.8 | 754.5 | 879.7 | 771.1 | 867.5 | 761.2 | 772.1 | 772 | 832.5 | 869.1 | 860.4 | 856.3 | 860.7 | 869.9 | 779 | 866.3 | 864.2 | 864 | 870.7 | 866.8 | 867.2 | 769.3 | 872.4 | 768.4 | 17.5107 | 17.3333 | 17.2601 | 17.3879 | 17.192 | 17.108 | 0 | 16.1 | 0 | 0 | 15.9352 | 15.8 | 2.3242 | 2.3445 | 2.4524 | 2.3857 | 2.4066 | 2.356 | 9.608 | 8.899 | 9.128 | 8.462 | 9.135 | 10.21 | 0.40399 |  | 0.42386 |  | 0.39998 |  | 0.05836 |  | 0.067095 |  | 0.071706 |  | 0.39285 |  | 0.40431 |  | 0.3931 |  | 0.062318 |  | 0.066007 |  | 0.080177 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490422 | 859 | 478637 | 920 | 380309 | 952.733 | 0.40399 | 0 | 0.42386 | 0 | 0.39998 | 0 | 0.39285 | 0 | 0.40431 | 0 | 0.3931 | 0 | 65000 | 2000 | 64000 | 2000 | 127504 | 5400 | 125000 | 122104 | 10.0333 | 0.40928 | 0.06572 | 0.39675 | 0.069501 | 16.06% | 17.52% | 17.2987 | 15.9451 | 2.3782 | 9.2403 | 130525.2 | 116800 | 130524.4767 | 89.49%
2023-11-27 | 2024 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 335090.89 | 7:15 | 17:53 | 6155.6 | 6508.6 | 6549.6 | 6454 | 6632.8 | 6710.7 | 6598.8 | 6911.2 | 6426 | 6451.4 | 6382.1 | 6460.9 | 6599.9 | 6496.8 | 6619 | 6677.7 | 6579.4 | 6558.2 | 6625.3 | 6633.6 | 6628.8 | 6617.2 | 6423.6 | 6532.9 | 6376.4 | 5643.1 | 6453.3 | 6394.5 | 6557.4 | 6450 | 6304.2 | 6502.9 | 6530.9 | 6548.1 | 6589.7 | 6521.9 | 6576.3 | 6476.5 | 6449.6 | 6446.1 | 6876.8 | 6180.4 | 6844.1 | 6161.4 | 6565.5 | 7353.4 | 5967.3 | 6797.6 | 6035.7 | 6174.2 | 6652.1 | 6198.6 | 6903 | 6153 | 6778.9 | 6036.6 | 5639 | 6789.4 | 5785.4 | 6626.6 | 6277 | 5768.2 | 6189.5 | 5899 | 6402.6 | 6098 | 6429.5 | 6742.4 | 6923.1 | 6194.6 | 6869.2 | 5957.2 | 6576.1 | 6520.7 | 6040 | 6880.2 | 5993.6 | 6898.2 | 6059.7 | 6850.7 | 6172.3 | 6704.4 | 6255.9 | 6997.7 | 6194.1 | 6671.7 | 6199.5 | 5493.2 | 6774.9 | 6531.2 | 5939.3 | 6873.7 | 6659.7 | 6144.4 | 6069.9 | 6760.6 | 6049.7 | 6342.9 | 6853.2 | 6021.7 | 6747.2 | 5919.4 | 6538.4 | 6075.2 | 6595.7 | 5698.8 | 6645.1 | 5998.8 | 6553.9 | 5968.6 | 6636.1 | 6047.2 | 6151.4 | 6826.6 | 6097.9 | 6008.4 | 6705 | 6867.7 | 6651.1 | 6079.5 | 6737.7 | 5997.5 | 6446.4 | 5998.5 | 6367.2 | 5542.6 | 6524 | 5959.3 | 6164.9 | 6252.2 | 5982.4 | 5217.7 | 6124.7 | 5375.7 | 5980.6 | 6003.9 | 6883.6 | 5914.4 | 6902.5 | 6080.8 | 6840.6 | 6044 | 6150.2 | 6110 | 6637.4 | 6897 | 6737.6 | 6686.2 | 6730.2 | 6819.9 | 6106.1 | 6768.6 | 6802.1 | 6877 | 7021.9 | 7001.6 | 6997.5 | 6212.2 | 6826.6 | 6150.1 | 18.3181 | 18.1455 | 18.0604 | 18.0912 | 18.0591 | 18.1042 | 0 | 20.8 | 0 | 0 | 20.7 | 20.6 | 2.7423 | 2.6733 | 2.6831 | 2.7862 | 2.6604 | 2.5627 | 5.546 | 5.62 | 5.405 | 6.03 | 5.424 | 5.922 | 3.0221 |  | 2.9127 |  | 2.9836 |  | 0.39683 |  | 0.40142 |  | 0.53769 |  | 3.436 |  | 3.3574 |  | 3.4677 |  | 0.40467 |  | 0.4041 |  | 0.59665 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490938 | 861 | 479146 | 922 | 381329.4 | 957.867 | 3.0221 | 0 | 2.9127 | 0 | 2.9836 | 0 | 3.436 | 0 | 3.3574 | 0 | 3.4677 | 0 | 516000 | 2000 | 509000 | 2000 | 1020400 | 5134 | 1021000 | 1015266 | 10.6333 | 2.9728 | 0.44531 | 3.4204 | 0.46847 | 14.98% | 13.7% | 18.1297 | 20.7 | 2.6847 | 5.6578 | 1025538.9 | 1018734 | 1175798.7307 | 86.64%
2023-11-28 | 2024 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 335090.89 | 7:09 | 17:53 | 6900.7 | 7237.3 | 7159.1 | 7127.4 | 7202.4 | 7271.3 | 7238.6 | 7550.6 | 7219.4 | 7228 | 7091.7 | 7225.7 | 7165.1 | 7158.2 | 7175.7 | 7227 | 7137.2 | 7154.5 | 7202.7 | 7230.9 | 7211.9 | 7208.4 | 7061.9 | 7140.8 | 7030.8 | 6191.3 | 7072.2 | 7038.6 | 7241.5 | 7164.5 | 7030.2 | 7219.2 | 7248.3 | 7279.8 | 7237.9 | 7191.7 | 7282.9 | 7202.9 | 7267.9 | 7190.1 | 3155.8 | 2802.8 | 3088.6 | 2747.2 | 2939 | 3301.9 | 2688.2 | 3070.7 | 6632.3 | 6812.5 | 7269.5 | 6817.2 | 7522.7 | 6667.8 | 7485.2 | 6646.5 | 6527.8 | 7670.3 | 6583 | 7534.1 | 7227.4 | 6609.5 | 7247.1 | 6849.3 | 7084.5 | 6648.3 | 7053.8 | 7370.2 | 7629.1 | 6786.6 | 7488.3 | 6535.4 | 7254.4 | 7123 | 6639.9 | 7534.4 | 6552.5 | 7574.9 | 6615.2 | 7485 | 6806 | 7385.5 | 6930.2 | 7686.8 | 6790.8 | 7305.9 | 6741.6 | 5971.2 | 7434.1 | 7118.5 | 6618.3 | 7700.5 | 7419.1 | 6806.2 | 6738 | 7495.7 | 6662 | 6924.7 | 7561.2 | 6598.9 | 7655.5 | 6597.3 | 7424.7 | 6794.6 | 7517.5 | 6406.6 | 7569 | 6776.1 | 7465.5 | 6783.5 | 7519.2 | 6866 | 6676.8 | 7441.9 | 6766.6 | 6634.8 | 7461.4 | 7595.3 | 7432.8 | 6775.3 | 7546.4 | 6719.4 | 7259.1 | 6792.5 | 7233.3 | 6305 | 7352.6 | 6743.7 | 6862.8 | 6874.2 | 6767.5 | 5856.2 | 6737.7 | 5950.4 | 6790.8 | 6797.5 | 7836.2 | 6755.5 | 7888.9 | 6927.3 | 7784.5 | 6833.1 | 6945.2 | 6878.6 | 7577.4 | 7879 | 7765.1 | 7711 | 7774 | 7814.1 | 6989.3 | 7783.4 | 7811.2 | 7848.4 | 7896.5 | 7863.3 | 7884.6 | 7000.9 | 7869.4 | 7002.8 | 17.26 | 17.14 | 17.17 | 17.2 | 17.07 | 16.95 | 0 | 17.9 | 0 | 0 | 18.1 | 17.8 | 2.52 | 2.68 | 2.84 | 2.83 | 2.77 | 2.63 | 5.57 | 5.5 | 6.03 | 6.1 | 6.07 | 5.96 | 3.26 |  | 1.91 |  | 3.21 |  | 0.52 |  | 0.29 |  | 0.61 |  | 3.86 |  | 3.87 |  | 3.88 |  | 0.53 |  | 0.52 |  | 0.67 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 491473 | 863 | 479717 | 924 | 382432.2 | 962.8 | 3.26 | 0 | 1.91 | 0 | 3.21 | 0 | 3.86 | 0 | 3.87 | 0 | 3.88 | 0 | 535000 | 2000 | 571000 | 2000 | 1102800 | 4933 | 1102000 | 1097867 | 10.7333 | 2.7933 | 0.47333 | 3.87 | 0.57333 | 16.95% | 14.81% | 17.1317 | 17.9333 | 2.7117 | 5.8717 | 1107452.6 | 1134655 | 1326967 | 85.51%
2023-11-29 | 2024 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 335090.89 | 7:11 | 17:53 | 6919.6 | 7258.1 | 7120.3 | 7061.5 | 7168.7 | 7273 | 7259.4 | 7569.1 | 7243.9 | 7244.3 | 7127.6 | 7256.5 | 7201.7 | 7194.4 | 7208 | 7262.4 | 7178.6 | 7198.5 | 7236.6 | 7261.7 | 7254.1 | 7244.7 | 7114.9 | 7188.5 | 7057.5 | 6222.4 | 7110.6 | 7071.3 | 7286 | 7214.4 | 7004.4 | 7244.3 | 7277.5 | 7317.3 | 7268.6 | 7225.5 | 7317.3 | 7245.1 | 7294.6 | 7211.8 | 7825.3 | 6956.8 | 7737.3 | 6870.2 | 7392 | 8311 | 6829 | 7818.1 | 6678.3 | 6857.8 | 7323.7 | 6877.5 | 7572.2 | 6699.8 | 7533 | 6650.9 | 6674.4 | 7735.8 | 6691.8 | 7658.1 | 7575 | 6682.4 | 7374.5 | 6974.5 | 7126.7 | 6674.2 | 7087.7 | 7390.6 | 7665.2 | 6801.1 | 7514 | 6545 | 7287.8 | 7140.1 | 6666.6 | 7556 | 6570.9 | 7605.5 | 6643.5 | 7514.4 | 6772.4 | 7398.7 | 6937 | 7705.1 | 6805.4 | 7321.3 | 6770.2 | 5992.7 | 7463.2 | 7098.1 | 6644.6 | 7719.2 | 7426.3 | 6812.5 | 6745.6 | 7494.3 | 6647.5 | 6923.4 | 7539.2 | 6594.2 | 7628.8 | 6579.5 | 7390.6 | 6770.7 | 7476.8 | 6373.6 | 7525.1 | 6741.7 | 7415.9 | 6735.2 | 7461.1 | 6813.7 | 6673.6 | 7431.8 | 6732.3 | 6609.8 | 7428.9 | 7574.3 | 7399.1 | 6759 | 7513 | 6688.5 | 7220.4 | 6738.1 | 7169.2 | 6250.8 | 7305.6 | 6698 | 6848.9 | 6866.4 | 6735.1 | 5840.9 | 6729.2 | 5949 | 6817.6 | 6815.9 | 7833 | 6762.3 | 7876.9 | 6922.9 | 7795.7 | 6841.1 | 6958.3 | 6890.9 | 7541.7 | 7840.9 | 7732 | 7680.8 | 7751.6 | 7802.8 | 6964.7 | 7750.1 | 7781.6 | 7815 | 7882.5 | 7842.3 | 7848.2 | 6965.7 | 7825.3 | 6962.4 | 17.6404 | 17.4594 | 17.613 | 17.4804 | 17.3861 | 17.1578 | 0 | 18.7 | 0 | 0 | 18.5 | 18.3 | 2.5177 | 2.4649 | 2.4273 | 2.6158 | 2.4673 | 2.2909 | 4.763 | 4.965 | 4.468 | 5.27 | 4.913 | 4.489 | 3.3063 |  | 3.2177 |  | 3.221 |  | 0.52076 |  | 0.52202 |  | 0.60757 |  | 3.9222 |  | 3.9034 |  | 3.8962 |  | 0.52455 |  | 0.51445 |  | 0.67341 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 492047 | 864 | 480287 | 926 | 383571.83 | 967.867 | 3.3063 | 0 | 3.2177 | 0 | 3.221 | 0 | 3.9222 | 0 | 3.9034 | 0 | 3.8962 | 0 | 574000 | 1000 | 570000 | 2000 | 1139630 | 5067 | 1141000 | 1134563 | 10.7 | 3.2483 | 0.55012 | 3.9073 | 0.5708 | 16.94% | 14.61% | 17.4562 | 18.5 | 2.464 | 4.8113 | 1144891.1 | 1138466 | 1331894.4597 | 85.48%
2023-11-30 | 2024 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 335090.89 | 7:09 | 17:53 | 8352.8 | 8727.6 | 8491 | 8490 | 8524.5 | 8654.9 | 8669.1 | 9021.4 | 8726.7 | 8746.1 | 8541 | 8728.7 | 8579.5 | 8600.2 | 8554.8 | 8632.1 | 8526 | 8581.3 | 8651.8 | 8696.9 | 8633.2 | 8641.9 | 8454.3 | 8560.6 | 8465 | 7458.5 | 8514.6 | 8464.7 | 8685.4 | 8566.4 | 8410.9 | 8671.4 | 8753 | 8810.8 | 8718.9 | 8677.7 | 8789.9 | 8681.9 | 8737.4 | 8646.5 | 9373.9 | 8355.3 | 9254.6 | 8272.8 | 8806.4 | 9882.2 | 8145.9 | 9330.8 | 7978.9 | 8196.4 | 8753.9 | 8240.5 | 9045.8 | 7997.1 | 9040.4 | 8009.9 | 8039 | 9310.1 | 8038 | 9227.6 | 9147.3 | 8050.2 | 8937.7 | 8455.5 | 8616.9 | 8074.3 | 8573.1 | 8955.7 | 9265.5 | 8262 | 9116.5 | 7956.2 | 8806.2 | 8678.1 | 8076.9 | 9174.8 | 7978.7 | 9198.7 | 8040.4 | 9122.7 | 8275.6 | 8982.2 | 8427.4 | 9365.4 | 8269.8 | 8885.4 | 8180.8 | 7258.8 | 8973.9 | 8607.4 | 8014.7 | 9330.3 | 8974.5 | 8221.2 | 8131.9 | 9082.9 | 8071.4 | 8382.6 | 9165 | 7988.3 | 9253.4 | 7988.3 | 8955.3 | 8201.8 | 9075.5 | 7739.2 | 9125.2 | 8159.9 | 8977.1 | 8142.8 | 9022.9 | 8233.3 | 8065.3 | 8973.1 | 8169.8 | 8005.7 | 8966.1 | 9137 | 8946.8 | 8132.9 | 9062.4 | 8074.7 | 8703.2 | 8153.9 | 8664.4 | 7537.2 | 8807.2 | 8075.9 | 8227.9 | 8231.5 | 8128.4 | 7027.3 | 8062.8 | 7164.4 | 8197.4 | 8197.8 | 9469.5 | 8155.9 | 9527.7 | 8373.2 | 9420.9 | 8269.8 | 8414.8 | 8301.9 | 9135 | 9495.7 | 9355.3 | 9303.6 | 9409.8 | 9451.7 | 8430 | 9395.1 | 9316 | 9378.2 | 9467 | 9421.2 | 9440.6 | 8401.6 | 9436.3 | 8406.8 | 18.8967 | 18.7465 | 18.9622 | 18.7213 | 18.7099 | 18.5695 | 0 | 20.6 | 0 | 0 | 20.4 | 20.3 | 2.6553 | 2.6922 | 2.6014 | 2.7682 | 2.6559 | 2.5003 | 5.841 | 5.954 | 6.206 | 5.737 | 6.146 | 5.647 | 3.7253 |  | 3.6389 |  | 3.3858 |  | 0.60151 |  | 0.60515 |  | 0.66589 |  | 4.552 |  | 4.6181 |  |  |  | 0.60908 |  | 0.59092 |  | 0.73966 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 492736 | 866 | 480975 | 928 | 384942.43 | 972.933 | 3.7253 | 0 | 3.6389 | 0 | 3.3858 | 0 | 4.552 | 0 | 4.6181 | 0 | 0 | 0 | 689000 | 2000 | 688000 | 2000 | 1370600 | 5066 | 1373000 | 1365534 | 10.7333 | 3.5833 | 0.62418 | 4.5851 | 0.64655 | 17.42% | 14.1% | 18.7677 | 20.4333 | 2.6455 | 5.9218 | 1378981.2 | 1369134 | 1538991.6614 | 88.96%
2023-12-01 | 2024 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 335090.89 | 7:10 | 17:54 | 8240 | 8606.9 | 8441.9 | 8414.3 | 8480.4 | 8568.8 | 8578.3 | 8937.4 | 8600.6 | 8640.1 | 8424 | 8608.6 | 8477.6 | 8494.9 | 8402 | 8500.9 | 8353.9 | 8420.4 | 8467.6 | 8523.8 | 8436.1 | 8442.4 | 8243.6 | 8354.4 | 8289.3 | 7274.4 | 8362.1 | 8297.8 | 8482.5 | 8350.9 | 8169.6 | 8447.8 | 8551.7 | 8619.7 | 8553.1 | 8489.8 | 8576 | 8454.7 | 8504.5 | 8416.5 | 8903.7 | 7917.8 | 8808 | 7833.3 | 8410.5 | 9488.2 | 7781.4 | 8905.3 | 7874.7 | 8092.1 | 8629.9 | 8111.1 | 8907.7 | 7884.1 | 8894.3 | 7882.4 | 7909.1 | 9156.9 | 7918.1 | 9074 | 8993.7 | 7923.6 | 8797.8 | 8343.9 | 8479.5 | 7971.4 | 8460.7 | 8849.6 | 9144.4 | 8153.9 | 8995 | 7868.1 | 8686.3 | 8579.9 | 7974.8 | 9093.6 | 7903 | 9086.6 | 7955.3 | 9025.2 | 8206.8 | 8904.1 | 8351.9 | 9252.9 | 8167.3 | 8775 | 8073.2 | 7166.7 | 8891.1 | 8525.3 | 7897.4 | 9172.9 | 8829.9 | 8085.4 | 7983.5 | 8922 | 7931.9 | 8243 | 9002.7 | 7853.6 | 9070.2 | 7841.8 | 8780.9 | 8061 | 8864.7 | 7605.1 | 8912.9 | 8004.4 | 8755.7 | 7962.9 | 8819.4 | 8073.8 | 7958.1 | 8867.3 | 8013.8 | 7878.9 | 8836.3 | 9034.6 | 8821.8 | 8052.6 | 8943.7 | 7972.5 | 8568.9 | 8014.5 | 8522.2 | 7439.2 | 8691.3 | 7976.2 | 8168.5 | 8190.1 | 8028.4 | 6959.9 | 8025 | 7102.6 | 8122.7 | 8117.2 | 9332.6 | 8060.5 | 9364.4 | 8259.9 | 9290.3 | 8150.1 | 8292.4 | 8197.2 | 8900.5 | 9238.1 | 9152.8 | 9099.5 | 9226.5 | 9287.8 | 8254.5 | 9178.1 | 9111.4 | 9168 | 9177.5 | 9104.4 | 9201.4 | 8177.2 | 9233.7 | 8207.3 | 20.143 | 19.5991 | 19.7654 | 19.9619 | 19.4482 | 19.6504 | 0 | 21 | 0 | 0 | 20.7 | 20.9 | 3.558 | 3.6334 | 3.6104 | 3.7464 | 3.6151 | 3.4955 | 9.033 | 8.727 | 7.541 | 9.469 | 8.748 | 8.453 | 3.754 |  | 3.4951 |  | 3.5549 |  | 0.59339 |  | 0.58562 |  | 0.70358 |  | 4.5831 |  | 4.4362 |  | 4.6167 |  | 0.59964 |  | 0.57622 |  | 0.77927 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 493411 | 868 | 481657 | 930 | 386289.1 | 977.933 | 3.754 | 0 | 3.4951 | 0 | 3.5549 | 0 | 4.5831 | 0 | 4.4362 | 0 | 4.6167 | 0 | 675000 | 2000 | 682000 | 2000 | 1346670 | 5000 | 1353000 | 1341670 | 10.7333 | 3.6013 | 0.62753 | 4.5453 | 0.65171 | 17.42% | 14.34% | 19.7613 | 20.8667 | 3.6098 | 8.6618 | 1354130 | 1345334 | 1508018.2432 | 89.21% | 25 | 4545
2023-12-02 | 2024 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 335090.89 | 7:10 | 17:55 | 8602.7 | 8998.9 | 8826.3 | 8695 | 8905.9 | 9059.3 | 8994 | 9391.2 | 8993.3 | 8692.4 | 8837.6 | 9018 | 8937.8 | 8920.4 | 8967.7 | 9036.7 | 8957.8 | 9052.4 | 9033.8 | 9054.8 | 9056.9 | 9038.2 | 8877.9 | 8981.7 | 8818.1 | 7733.8 | 8857.5 | 8828.2 | 9082.6 | 8995.9 | 8813.5 | 9055.3 | 9078.7 | 9092.3 | 9064.9 | 9026.2 | 9159.2 | 9058.9 | 9132.3 | 8986.4 | 9856.9 | 8753.6 | 9750.1 | 8668.6 | 9250.9 | 10325.2 | 8609.2 | 9847.2 | 8274.2 | 8496.3 | 9079.4 | 8522.6 | 9373.4 | 8325.9 | 9275.5 | 8081 | 8288.1 | 9583.1 | 8303.9 | 9499.9 | 9397.6 | 8294.6 | 9194.7 | 8694.8 | 8864.6 | 8312.3 | 8816.2 | 9214.4 | 9535.5 | 8479.3 | 9349.3 | 8159 | 9046.9 | 8895.7 | 8271.2 | 9288.5 | 8184.7 | 9436.8 | 8250 | 9341.7 | 8492.9 | 9196.8 | 8614.7 | 9607.7 | 8475.8 | 9099.7 | 8369.6 | 7444.5 | 9308.5 | 8899.5 | 8294.8 | 9646.8 | 9292.3 | 8515.7 | 8423.6 | 9393.3 | 8339.7 | 8659.4 | 9460.8 | 8257.3 | 9573.1 | 8253.5 | 9279.9 | 8493.6 | 9398 | 8018 | 9460.4 | 8471.9 | 9314.4 | 8397.2 | 9429.6 | 8592.7 | 8358.4 | 9313.6 | 8447.9 | 8297.9 | 9307.4 | 9499.2 | 9305.5 | 8457.1 | 9431.3 | 8405 | 9063 | 8502.6 | 9038.4 | 7870.4 | 9179.9 | 8416.5 | 8414.8 | 8546.7 | 8456.9 | 7299 | 5303.4 | 7379.7 | 8374.3 | 8373 | 9679.1 | 8339.7 | 9780.7 | 8581 | 9626 | 8457 | 8590.2 | 8483.4 | 9461.5 | 9844.9 | 9654.2 | 9578.9 | 9637 | 9661.3 | 8665.1 | 9683.6 | 9756.2 | 9835.4 | 9924.1 | 9855.9 | 9894.2 | 8784 | 9785.4 | 8758 | 21.3666 | 20.88 | 20.9351 | 21.0206 | 20.8577 | 20.9161 | 0 | 23.9 | 0 | 0 | 23.9 | 24.1 | 3.9285 | 3.7468 | 3.8026 | 3.981 | 3.7212 | 3.6805 | 6.913 | 7.074 | 7.003 | 7.429 | 7.611 | 7.292 | 3.8917 |  | 3.7641 |  | 3.6813 |  | 0.61681 |  | 0.63005 |  | 0.72398 |  | 4.8203 |  | 4.9063 |  | 4.8672 |  | 0.62484 |  | 0.61857 |  | 0.8045 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 494125 | 870 | 482360 | 932 | 387705.5 | 982.867 | 3.8917 | 0 | 3.7641 | 0 | 3.6813 | 0 | 4.8203 | 0 | 4.9063 | 0 | 4.8672 | 0 | 714000 | 2000 | 703000 | 2000 | 1416400 | 4934 | 1413000 | 1411466 | 10.75 | 3.779 | 0.65695 | 4.8646 | 0.68264 | 17.38% | 14.03% | 20.996 | 23.9667 | 3.8101 | 7.2203 | 1424741.7 | 1414800 | 1605562 | 88.12% | 25 | 0
2023-12-03 | 2024 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 335090.89 | 7:08 | 17:57 | 7111.5 | 9519.8 | 9368.4 | 9131.2 | 9477.9 | 9609.3 | 9558.2 | 9971.6 | 8468.7 | 7301.5 | 9368.3 | 9556.2 | 9510.1 | 9472.1 | 9534.2 | 9602.7 | 9528.1 | 9633.7 | 9620.6 | 9653.9 | 9635 | 9622.6 | 9440.3 | 9557.3 | 9394.7 | 8253.9 | 9431 | 9405.2 | 9676 | 9578.4 | 9392.3 | 9647.5 | 9692.6 | 9687 | 9650.2 | 9619.4 | 9775.5 | 9672.3 | 9751.4 | 9587.1 | 10479.6 | 9299.3 | 10382.6 | 9219.7 | 9889.8 | 11110 | 9149.6 | 10457.6 | 8760.6 | 8992.7 | 9630.8 | 9033.3 | 9999.6 | 8879.7 | 9899.7 | 8802.9 | 8762.9 | 10145.5 | 8778 | 10047.5 | 9940.5 | 8772.2 | 9731.9 | 9203.9 | 9392.6 | 8788.2 | 9344.7 | 9734.6 | 10091.2 | 8957.4 | 9888.9 | 8612.6 | 9571.3 | 9386.1 | 8768.5 | 9950.1 | 8649.8 | 9983.8 | 8711.5 | 9856.6 | 8814.2 | 9694.2 | 9069.1 | 10135.3 | 8931.8 | 9576.8 | 8893.5 | 7864.5 | 9857.8 | 9392.8 | 8794.5 | 10227.7 | 9859.2 | 9037.7 | 8937.8 | 9970.6 | 8836 | 9169.1 | 10012.1 | 8736 | 10149.5 | 8747.4 | 9839.4 | 9007.1 | 9980.6 | 8525.1 | 10048.4 | 8991 | 9932.2 | 9023.3 | 10051.1 | 9136 | 8845.1 | 9855.1 | 8947.4 | 8782.7 | 9855.9 | 10045.3 | 9855.4 | 8932.8 | 9977.1 | 8901.8 | 9613.8 | 9033.4 | 9615.9 | 8350.3 | 9717.3 | 8909.4 | 8918.2 | 9048.3 | 8959.7 | 7722.6 | 6488.6 | 7804.7 | 8825.4 | 8833.6 | 10123.8 | 8738.1 | 10209 | 8983.4 | 10100.6 | 8876.9 | 9033.6 | 8931.2 | 9746.8 | 10136.3 | 9976.5 | 9922.1 | 10044.9 | 10095.6 | 9008.1 | 10024 | 9941.2 | 10020.8 | 10114.1 | 10071.5 | 10091.6 | 8979.3 | 10049.1 | 8960.9 | 20.01 | 19.65 | 19.79 | 19.83 | 19.48 | 19.38 | 0 | 21.9 | 0 | 0 | 21.6 | 21.4 | 3.33 | 3.16 | 3.24 | 3.32 | 3.09 | 3.06 | 6.41 | 6.84 | 6.47 | 7.42 | 6.66 | 6.8 | 4.1 |  | 3.93 |  | 3.82 |  | 0.64 |  | 0.66 |  | 0.75 |  | 5.16 |  | 5.25 |  | 5.17 |  | 0.65 |  | 0.65 |  | 0.84 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 494878 | 872 | 483106 | 934 | 389198.164 | 987.8 | 4.1 | 0 | 3.93 | 0 | 3.82 | 0 | 5.16 | 0 | 5.25 | 0 | 5.17 | 0 | 753000 | 2000 | 746000 | 2000 | 1492664 | 4933 | 1495000 | 1487731 | 10.8167 | 3.95 | 0.68333 | 5.1933 | 0.71333 | 17.3% | 13.74% | 19.69 | 21.6333 | 3.2 | 6.7667 | 1501786.5 | 1491733 | 1702812 | 87.6% | 25 | 741
2023-12-04 | 2024 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 335090.89 | 7:10 | 17:56 | 8030.1 | 10128.5 | 9906.1 | 9722.7 | 9998.8 | 10139.5 | 10110.7 | 10563.5 | 9813.3 | 9160.5 | 9972 | 10172.8 | 10031.5 | 10025.6 | 10038.3 | 10139.5 | 10045.5 | 10163.3 | 10172.3 | 10215 | 10172.1 | 10171.4 | 9954.5 | 10093.1 | 9945.1 | 8745.8 | 9998.7 | 9958.5 | 10219.7 | 10084.9 | 9900.7 | 10196.3 | 10265.1 | 10257.5 | 10215.3 | 10182.2 | 10339.8 | 10215.3 | 10291.9 | 10109.7 | 11036.6 | 9768.6 | 10917.2 | 9691 | 10398.5 | 11710.1 | 9629.5 | 11000.9 | 9330 | 9580.5 | 10233.2 | 9623.6 | 10600.2 | 9377.3 | 10548.8 | 9350.6 | 9356.3 | 10815.8 | 9361.7 | 10727.2 | 10605.4 | 9349.4 | 10390.9 | 9829.5 | 10005.5 | 9393 | 9967.6 | 10424.2 | 10755.9 | 9588.3 | 10567 | 9233.4 | 10200.6 | 10049.8 | 9358.8 | 10646.7 | 9244.7 | 10651.5 | 9286.5 | 10527.3 | 9489.5 | 10427.9 | 9770.6 | 10899 | 9609.8 | 10305.9 | 9510.3 | 8439.1 | 10509.1 | 10030.5 | 9380.7 | 10899 | 10477.7 | 9609.4 | 9493.8 | 10601.9 | 9399.8 | 9772.9 | 10644.4 | 9312 | 10807.5 | 9308.4 | 10473 | 9579.6 | 10609.6 | 9063.2 | 10669.9 | 9555 | 10528.8 | 9564.9 | 10622.2 | 9684.2 | 9417 | 10496.4 | 9519.8 | 9362 | 10468.7 | 10702 | 10484.4 | 9513.1 | 10618.1 | 9468.9 | 10205 | 9591.7 | 10202.7 | 8859.1 | 10319.6 | 9469.8 | 9637.1 | 9648 | 9519.4 | 8222.5 | 9465.4 | 8365.6 | 9504.4 | 9506 | 10949.7 | 9423.4 | 11052.5 | 9706.3 | 10874.3 | 9548.5 | 9713.7 | 9601.1 | 10649.2 | 11061.7 | 10870.9 | 10790.5 | 10907 | 10936.9 | 9780.5 | 10911.6 | 10954 | 11033.5 | 11101 | 11054.5 | 11078.6 | 9841 | 11020 | 9829 | 18.78 | 18.55 | 18.82 | 18.59 | 18.36 | 18.14 | 0 | 20.8 | 0 | 0 | 20.3 | 19.9 | 3.15 | 3.19 | 3.11 | 3.28 | 3.17 | 2.93 | 6.65 | 6.9 | 6.23 | 6.75 | 7.2 | 6.76 | 4.24 |  | 4.06 |  | 3.91 |  | 0.68 |  | 0.7 |  | 0.77 |  | 5.38 |  | 5.48 |  | 5.46 |  | 0.68 |  | 0.69 |  | 0.86 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 495679 | 873 | 483908 | 935 | 390794.9 | 992.867 | 4.24 | 0 | 4.06 | 0 | 3.91 | 0 | 5.38 | 0 | 5.48 | 0 | 5.46 | 0 | 801000 | 1000 | 802000 | 1000 | 1596736 | 5067 | 1601000 | 1591669 | 10.7667 | 4.07 | 0.71667 | 5.44 | 0.74333 | 17.61% | 13.66% | 18.54 | 20.3333 | 3.1383 | 6.7483 | 1607306.4 | 1595068 | 1779913 | 89.61% | 27 | 778
2023-12-05 | 2024 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 335090.89 | 7:13 | 17:56 | 9485.8 | 9978.5 | 9788.2 | 9443.2 | 9899.3 | 10044.4 | 10063.1 | 10531.2 | 9750.7 | 9513.5 | 9908.9 | 10093.6 | 9997.8 | 10011.8 | 9996.5 | 10057.6 | 9984.2 | 10091.8 | 10107 | 10138.7 | 10115.7 | 10110.9 | 9905.6 | 10035.2 | 9893.6 | 8693.7 | 9934.6 | 9900.8 | 10112.3 | 10043 | 9864.3 | 10147.7 | 10224.1 | 10209.2 | 10165.4 | 10135.3 | 10294.5 | 10176.8 | 10254.1 | 10069.1 | 11000.7 | 9742.3 | 10883.9 | 9671.7 | 10379.4 | 11665.1 | 9607.1 | 10958.9 | 9258.7 | 9503.9 | 10162.4 | 9560.5 | 10531 | 9344.7 | 10476.3 | 9290.6 | 9287.1 | 10738.8 | 9287 | 10642.6 | 10518.2 | 9272.2 | 10308 | 9741.3 | 9933.1 | 9311.3 | 9887.4 | 10338.5 | 10670.6 | 9506.6 | 10474.3 | 9142.9 | 10119.1 | 9960.3 | 9277.9 | 10559.4 | 9171.6 | 10556.1 | 9205.5 | 10438.7 | 9540.5 | 10329.8 | 9715.4 | 10826.6 | 9548 | 10245.9 | 9439.8 | 8386.2 | 10439.5 | 9970.4 | 9327.4 | 10834.6 | 10423.9 | 9557 | 9439.4 | 10547.1 | 9354.2 | 9721.7 | 10594.5 | 9267.8 | 10767 | 9268.9 | 10428 | 9532 | 10568.5 | 9030 | 10630.8 | 9530.1 | 10493.1 | 9534.7 | 10593.5 | 9665.6 | 9370.3 | 10463 | 9472.6 | 9325 | 10420.2 | 10671.5 | 10443 | 9486.1 | 10591.5 | 9442.2 | 10160.6 | 9553.8 | 10159.8 | 8833.5 | 10293.9 | 9448 | 9605.6 | 9610.3 | 9497.4 | 8200.4 | 9447.7 | 8359.4 | 9503.6 | 9505 | 10963.1 | 9425.6 | 11066 | 9724.1 | 10900.4 | 9573.2 | 9738.2 | 9618.8 | 10657.5 | 11064.6 | 10879.8 | 10794.4 | 10928 | 10933.7 | 9770.8 | 10906.5 | 10930 | 11035 | 11119.7 | 11072.4 | 11082.5 | 9839 | 11018 | 9835.4 | 18.7889 | 18.3412 | 18.6964 | 18.495 | 18.1703 | 18.0442 | 0 | 21.1 | 0 | 0 | 20.7 | 20.4 | 3.1476 | 3.2914 | 3.3052 | 3.3073 | 3.2297 | 3.0453 | 7.157 | 7.464 | 6.852 | 7.649 | 7.364 | 7.276 | 4.2274 |  | 4.0551 |  | 3.8997 |  | 0.69594 |  | 0.7068 |  | 0.77296 |  | 5.3996 |  | 5.4714 |  | 5.4463 |  | 0.69236 |  | 0.69357 |  | 0.86601 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 496475 | 875 | 484745 | 937 | 392386.431 | 997.867 | 4.2274 | 0 | 4.0551 | 0 | 3.8997 | 0 | 5.3996 | 0 | 5.4714 | 0 | 5.4463 | 0 | 796000 | 2000 | 837000 | 2000 | 1591531 | 5000 | 1629000 | 1586531 | 10.7167 | 4.0607 | 0.72523 | 5.4391 | 0.75065 | 17.86% | 13.8% | 18.4227 | 20.7333 | 3.2211 | 7.2937 | 1601850.4 | 1590600 | 1785184.8688 | 89.1% | 29 | 0
2023-12-06 | 2024 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 335090.89 | 7:12 | 17:56 | 0 | 0 | 8912.2 | 8684.3 | 9224.2 | 9362.6 | 9368.7 | 9739.3 | 9843.2 | 9659.6 | 9705.7 | 9882.9 | 9819.7 | 9805.1 | 9833.3 | 9892.8 | 9746.1 | 9847 | 9923.3 | 9955.7 | 9933 | 9924.8 | 9731.5 | 9853.4 | 9702.3 | 8527.6 | 9750.3 | 9713 | 9924.7 | 9870.5 | 9677.3 | 9956.9 | 10028 | 10025.2 | 8030.3 | 8027.9 | 10089.8 | 9975.7 | 10053.4 | 9887.5 | 10780.8 | 9548.4 | 10673.1 | 9480.4 | 10181.1 | 11458.4 | 9424.1 | 10747.5 | 9079.8 | 9316.2 | 9971.4 | 9382.5 | 10333.4 | 9178 | 10276.2 | 9116.4 | 9099.7 | 10515.4 | 9100.5 | 10434.2 | 10310.3 | 9086.9 | 10092.2 | 9531 | 9757.8 | 9143 | 9705.5 | 10143.8 | 10471 | 9332.3 | 10280.3 | 8967.9 | 9928.5 | 9768.4 | 9106.5 | 10356.4 | 8997.5 | 10358.2 | 9033.3 | 10241.3 | 9376.9 | 10124.6 | 9520.5 | 10616.1 | 9357.5 | 10042.9 | 9250.2 | 8224.5 | 10239.7 | 9777.7 | 9123.8 | 10608.4 | 10195.8 | 9346.9 | 9236.6 | 10324.4 | 9151.6 | 9519.3 | 10376.8 | 9080.3 | 10542 | 9079.9 | 10213.1 | 9334.5 | 10355.2 | 8847 | 10418.7 | 9332.8 | 10280.1 | 9339.7 | 10368.1 | 9462.2 | 9174.3 | 10236.8 | 9279.4 | 9132.4 | 10204.5 | 10455.5 | 10229 | 9291.9 | 10380.9 | 9261.2 | 9946.2 | 9359.1 | 9944.7 | 8662.6 | 10093.1 | 9259.1 | 9395 | 9398.8 | 9311.1 | 8029.1 | 9223.4 | 8153.6 | 9260.9 | 9260.5 | 10694.7 | 9202.4 | 10805.7 | 9498.5 | 10653.3 | 9346.4 | 9509.3 | 9377.8 | 10409.5 | 10810.4 | 10626.1 | 10544.4 | 10664.6 | 10669.5 | 9544 | 10657.9 | 10657.5 | 10757.5 | 10838.2 | 10792.8 | 10811 | 9604.9 | 10745.3 | 9597.9 | 19.336 | 18.4599 | 18.6907 | 18.7235 | 18.2064 | 17.9977 | 0 | 21.5 | 0 | 0 | 21 | 20.6 | 3.2378 | 3.3143 | 3.3123 | 3.356 | 3.2268 | 3.0429 | 6.356 | 7.445 | 6.419 | 6.7 | 6.522 | 7.131 | 4.1715 |  | 4.0099 |  | 3.8434 |  | 0.69716 |  | 0.70408 |  | 0.76661 |  | 5.303 |  | 5.3774 |  | 5.346 |  | 0.69383 |  | 0.69336 |  | 0.86067 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 497234 | 876 | 485491 | 939 | 393920.031 | 1002.8 | 4.1715 | 0 | 4.0099 | 0 | 3.8434 | 0 | 5.303 | 0 | 5.3774 | 0 | 5.346 | 0 | 759000 | 1000 | 746000 | 2000 | 1533600 | 4933 | 1502000 | 1528667 | 10.7333 | 4.0082 | 0.72262 | 5.3421 | 0.74929 | 18.03% | 14.03% | 18.569 | 21.0333 | 3.2483 | 6.7622 | 1543428.9 | 1532867 | 1753684.6513 | 87.41% | 35 | 0
2023-12-07 | 2024 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 335090.89 | 7:12 | 17:57 | 9380.6 | 9836.7 | 9622.4 | 9451.8 | 9699.7 | 9849.2 | 9868.2 | 10307.4 | 9819.5 | 9635.2 | 9673.1 | 9860.2 | 9749.9 | 9765.2 | 9744.4 | 9812.1 | 9737.3 | 9835 | 9851 | 9886.4 | 9846.2 | 9843.9 | 9642 | 9769.1 | 9641.4 | 8479.6 | 9693.7 | 9649.2 | 9848.1 | 9786.2 | 9597.9 | 9881.4 | 9963.2 | 9960.7 | 9900.7 | 9860.3 | 10021.8 | 9903.3 | 9979.8 | 9816.9 | 10700.9 | 9477.8 | 10591.8 | 9413.2 | 10101.2 | 11362.5 | 9349.7 | 10664.4 | 9046 | 9285 | 9925.2 | 9347.5 | 10274.7 | 9118.5 | 10240.6 | 9075.9 | 9077.1 | 10486.5 | 9076.8 | 10410.8 | 10285.6 | 9065.4 | 10078 | 9514.2 | 9721.9 | 9107.5 | 9672 | 10102.5 | 10436.3 | 9295 | 10249.3 | 8926.2 | 9894.3 | 9727.9 | 9074.2 | 10314.3 | 8962.8 | 10318.7 | 8994.5 | 10204.9 | 9330.2 | 10069 | 9466.1 | 10568.5 | 9313.9 | 9995.3 | 9212.2 | 8188.6 | 10198.8 | 9739.3 | 9093.1 | 10572.4 | 10157.3 | 9307.1 | 9193.1 | 10292.1 | 9124.3 | 9481.6 | 10333 | 9039 | 10490.7 | 9035.6 | 10163.5 | 9292.3 | 10302.3 | 8804.4 | 10321.9 | 9235.9 | 10228.7 | 9294.3 | 10322.6 | 9407.5 | 9130.6 | 10186.8 | 9234.6 | 9086.4 | 10146.9 | 10390.8 | 10172.1 | 9224 | 10309.7 | 9197.9 | 9891.9 | 9309.9 | 9893.2 | 8604 | 10019.8 | 9193.5 | 9341.3 | 9346.4 | 9244.4 | 7981.2 | 9169.4 | 8103.1 | 9223.5 | 9223.1 | 10629 | 9150.6 | 10726.9 | 9432 | 10584.2 | 9284.7 | 9448.6 | 9320 | 10334.9 | 10728.9 | 10552.5 | 10466 | 10591.9 | 10602.4 | 9469.4 | 10573.9 | 10591.6 | 10678.9 | 10757.4 | 10711.5 | 10728.1 | 9534.4 | 10668.3 | 9523.5 | 19.2561 | 18.5779 | 18.8896 | 18.8499 | 18.3618 | 18.161 | 0 | 21.9 | 0 | 0 | 21.6051 | 21.1 | 3.1534 | 3.0253 | 3.0577 | 3.2158 | 2.9735 | 2.8952 | 5.988 | 5.785 | 6.127 | 6.245 | 6.066 | 5.816 | 4.1494 |  | 3.9658 |  | 3.8427 |  | 0.69029 |  | 0.69873 |  | 0.80584 |  | 5.292 |  | 5.3411 |  | 5.3185 |  | 0.68689 |  | 0.68828 |  | 0.87701 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 498014 | 877 | 486270 | 941 | 395472 | 1007.8 | 4.1494 | 0 | 3.9658 | 0 | 3.8427 | 0 | 5.292 | 0 | 5.3411 | 0 | 5.3185 | 0 | 780000 | 1000 | 779000 | 2000 | 1551969 | 5000 | 1556000 | 1546969 | 10.75 | 3.986 | 0.73162 | 5.3172 | 0.75073 | 18.35% | 14.12% | 18.6827 | 21.535 | 3.0535 | 6.0045 | 1561731 | 1551267 | 1740524.2951 | 89.13% | 28 | 0
2023-12-08 | 2024 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 335090.89 | 7:13 | 17:57 | 9456.8 | 9911.7 | 9840.7 | 9775.7 | 9919.4 | 9988.5 | 9919.7 | 10404.1 | 9886.1 | 9762 | 9749 | 9922.6 | 9880.3 | 9850.1 | 9862 | 9951.9 | 9880.9 | 9997.1 | 9988.6 | 10013.3 | 9977.8 | 9980.8 | 9772.2 | 9901.6 | 9757.8 | 8571.2 | 9801.1 | 9761.5 | 9967.6 | 9903 | 9723.6 | 10009 | 10079.9 | 10065.4 | 9973.8 | 9939 | 10156.4 | 10040.5 | 10119.3 | 9942.2 | 10865.7 | 9596 | 10734 | 9537.5 | 10211.5 | 11503.2 | 9481.4 | 10796.8 | 9129.4 | 9360.2 | 10029 | 9422.4 | 10390.8 | 9203.6 | 10315.3 | 9161.3 | 9127.8 | 10538.3 | 9132.9 | 10473 | 10334.9 | 9113.8 | 10130.4 | 9557.5 | 9782.7 | 9189.5 | 9711.8 | 10149.3 | 10505.4 | 9363 | 10316 | 8987.9 | 9947.4 | 9789.3 | 9128.4 | 10362.2 | 9018.5 | 10373.7 | 9039.4 | 10264.4 | 9422.1 | 10143.2 | 9568.8 | 10661.5 | 9405.8 | 10099.5 | 9284.3 | 8267.4 | 10259.2 | 9807.6 | 9160 | 10649.1 | 10231.9 | 9365.1 | 9259.4 | 10357.7 | 9205.1 | 9566.2 | 10439.2 | 9120.5 | 10570.9 | 9110.6 | 10247.7 | 9382.1 | 10401.7 | 8884 | 10466.1 | 9373 | 10329.4 | 9387.5 | 10442.1 | 9509.7 | 9209.6 | 10279.1 | 9344.7 | 9173.8 | 10256.1 | 10505.1 | 10272.6 | 9319.6 | 10428.3 | 9309.4 | 10002.7 | 9405.1 | 10011.9 | 8705.6 | 10141.1 | 9307.7 | 9451.5 | 9453.2 | 9352.2 | 8081.5 | 9295.1 | 8198.4 | 9311.2 | 9301.4 | 10722.2 | 9232 | 10816.3 | 9505.5 | 10655.9 | 9339.8 | 9517.5 | 9385.4 | 10406.3 | 10809.5 | 10653.6 | 10557.2 | 10682.8 | 10694 | 9535.3 | 10651.9 | 10698.9 | 10788.8 | 10846.2 | 10804.3 | 10821.5 | 9612.2 | 10754.8 | 9609.7 | 20.806 | 20.8561 | 20.6332 | 20.6532 | 20.7521 | 20.5343 | 0 | 29.8 | 0 | 0 | 29.6 | 29.3 | 1.9871 | 2.0608 | 2.0223 | 2.0157 | 2.0426 | 1.9332 | 5.376 | 5.575 | 5.525 | 4.964 | 4.708 | 5.13 | 4.1882 | 3.9215 | 4.024 |  | 3.964 |  | 0.68375 |  | 0.69735 |  | 0.80255 |  | 5.374 | 5.3176 | 5.4728 |  | 5.4404 |  | 0.69469 | 0.97234 | 0.69899 |  | 0.89549 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 498802 | 879 | 487055 | 942 | 397039.498 | 1012.8 | 4.1882 | 3.9215 | 4.024 | 0 | 3.964 | 0 | 5.374 | 5.3176 | 5.4728 | 0 | 5.4404 | 0 | 788000 | 2000 | 785000 | 1000 | 1567498 | 5000 | 1570000 | 1562498 | 10.7333 | 4.0244 | 0.72788 | 5.4012 | 0.81538 | 18.09% | 15.1% | 20.7058 | 29.5667 | 2.0103 | 5.213 | 1577076.7 | 1566666 | 1757867.6454 | 89.12% | 32 | 0
2023-12-09 | 2024 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 335090.89 | 7:10 | 17:56 | 9515.9 | 9955.8 | 9873.8 | 9820.7 | 9961 | 10032.5 | 9953.9 | 10409.5 | 9933.3 | 9867.5 | 9778.2 | 9970.5 | 9893.4 | 9891.9 | 9851.8 | 9962.3 | 9872.4 | 9988.7 | 9990.2 | 10015.4 | 9986.4 | 9989.6 | 9770 | 9907.1 | 9738.4 | 8556.8 | 9794.4 | 9750.8 | 9947.3 | 9876.3 | 9697.4 | 9987.3 | 10076 | 10056.3 | 10008.2 | 9979.9 | 10140.6 | 10012.4 | 10094.3 | 9924.1 | 10821.2 | 9548 | 10682.7 | 9488.8 | 10167.9 | 11447.1 | 9447.9 | 10759.3 | 9137.6 | 9373.3 | 10027.6 | 9429.8 | 10384.4 | 9206.4 | 10319.1 | 9152 | 9152.6 | 10558.2 | 9163.5 | 10500.5 | 10365.2 | 9148.8 | 10180.6 | 9602.5 | 9811.5 | 9221.7 | 9760.3 | 10206.4 | 10521.3 | 9388.5 | 10341.9 | 9011.7 | 9969.8 | 9816.3 | 9145.8 | 10388.2 | 9029.4 | 10403.4 | 9079.2 | 10293.5 | 9449.4 | 10161.1 | 9602.4 | 10687.4 | 9438.8 | 10125.6 | 9300.8 | 8283.2 | 10282.7 | 9833.2 | 9180.6 | 10671.8 | 10238.3 | 9364.3 | 9267.2 | 10385.6 | 9215.5 | 9573.7 | 10457.4 | 9135.8 | 10622.4 | 9133.7 | 10284.5 | 9408.2 | 10431.3 | 8915.5 | 10489.7 | 9398.6 | 10354.7 | 9408.9 | 10476.4 | 9530.5 | 9207.5 | 10278 | 9356.5 | 9179.7 | 10264.9 | 10508.4 | 10283.7 | 9304.5 | 10413 | 9292.4 | 10011.7 | 9411.9 | 10007.6 | 8666.7 | 10114.3 | 9276.2 | 9420.3 | 9419.2 | 9327 | 8058.1 | 9258.3 | 8174.5 | 9286.7 | 9280 | 10742.8 | 9247.5 | 10809.6 | 9501.6 | 10645 | 9333.2 | 9507.6 | 9383.5 | 10397.6 | 10794.4 | 10652.3 | 10557.6 | 10691.7 | 10709.8 | 9528.2 | 10637.5 | 10685.6 | 10770.4 | 10826.2 | 10793.9 | 10802.1 | 9605.9 | 10764 | 9600.3 | 23.7935 | 23.5548 | 23.6926 | 23.5371 | 23.8632 | 23.6893 | 0 | 36.7 | 0 | 0 | 37 | 36.7 | 1.9996 | 2 | 2.0616 | 2.0435 | 1.9772 | 1.8039 | 4.623 | 4.294 | 4.5 | 4.529 | 4.461 | 4.427 | 4.1791 | 4.5994 | 4.0022 | 4.2677 | 3.9725 | 4.1066 | 0.66516 | 0.81026 | 0.68508 | 1.0628 | 0.80232 | 0.85418 | 5.3783 | 5.3139 | 5.4539 |  | 5.4555 | 5.3686 | 0.66097 | 0.96618 | 0.67445 |  | 0.87036 | 0.94926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 499591 | 881 | 487841 | 944 | 398607.964 | 1017.8 | 4.1791 | 4.5994 | 4.0022 | 4.2677 | 3.9725 | 4.1066 | 5.3783 | 5.3139 | 5.4539 | 0 | 5.4555 | 5.3686 | 789000 | 2000 | 786000 | 2000 | 1568466 | 5000 | 1571000 | 1563466 | 10.7667 | 4.1879 | 0.81331 | 5.394 | 0.82424 | 19.42% | 15.28% | 23.6884 | 36.8 | 1.9809 | 4.4723 | 1578184.8 | 1567667 | 1750719.4798 | 89.54% | 31 | 0
2023-12-10 | 2024 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 335090.89 | 7:13 | 17:58 | 9594.1 | 10042.4 | 9963.5 | 9919.1 | 10025.7 | 10132.7 | 10052.6 | 10461.7 | 9970.2 | 9921.9 | 9819.8 | 10000.3 | 9949.7 | 9933.1 | 9937.9 | 10043.3 | 9960.3 | 10068.1 | 10038.9 | 10056.6 | 10044.7 | 10041.7 | 9824.8 | 9963.9 | 9795.5 | 8599.1 | 9825.4 | 9779.2 | 9992.2 | 9924.3 | 9777.6 | 10053.9 | 10132.1 | 10166.5 | 10072.1 | 10033.1 | 10195.8 | 10088.4 | 10169.5 | 9991.4 | 10941.4 | 9649.2 | 10815 | 9590.9 | 10277.1 | 11575.8 | 9525.6 | 10867.7 | 9189.9 | 9423.8 | 10090.7 | 9477.2 | 10447.8 | 9274.6 | 10370.3 | 9201.4 | 9196 | 10609.1 | 9210.6 | 10552 | 10413.2 | 9195.1 | 10238.2 | 9666.3 | 9857.1 | 9267.1 | 9811.4 | 10254 | 10570.1 | 9441.2 | 10401.7 | 9056.8 | 10022.8 | 9879.6 | 9194.2 | 10456.1 | 9096.7 | 10466.9 | 9137.1 | 10372.2 | 9485 | 10222.5 | 9645.6 | 10738.2 | 9483.3 | 10179 | 9347.3 | 8317.9 | 10341.9 | 9875.3 | 9248.5 | 10757.7 | 10334.6 | 9458.6 | 9356.9 | 10467.9 | 9268 | 9624.8 | 10510.9 | 9197.4 | 10657.9 | 9185.9 | 10329.2 | 9464.2 | 10481.1 | 8960.4 | 10549.4 | 9463.7 | 10405.6 | 9465.9 | 10515 | 9589 | 9272.9 | 10359.6 | 9422.7 | 9242.6 | 10333.6 | 10601.7 | 10365.4 | 9392.7 | 10512.5 | 9392.9 | 10087 | 9483.6 | 10084.2 | 8764.2 | 10224.5 | 9380.3 | 9526.5 | 9526.5 | 9422.4 | 8141.8 | 9346.2 | 8251.4 | 9393.4 | 9385.9 | 10851.5 | 9331.2 | 10941.6 | 9624.6 | 10756.8 | 9437.2 | 9614.9 | 9485.8 | 10527.6 | 10946.8 | 10772.6 | 10674.6 | 10804.5 | 10819.3 | 9658.4 | 10777.8 | 10817.1 | 10916 | 10954.6 | 10930.2 | 10954.7 | 9734.9 | 10880 | 9724.6 | 22.8206 | 22.6841 | 22.6817 | 22.6472 | 23.0641 | 22.7689 | 0 | 35.2 | 0 | 0 | 35.6 | 35.2 | 2.1592 | 2.2011 | 2.159 | 2.114 | 2.0798 | 2.0744 | 5.314 | 4.832 | 5.019 | 5.069 | 4.741 | 4.57 | 4.181 | 4.6002 | 4.0282 | 4.2668 | 3.9862 | 4.1321 | 0.67525 | 0.81531 | 0.69868 | 1.0723 | 0.81263 | 0.87583 | 5.3899 | 5.3278 | 5.4965 |  | 5.4868 | 5.4137 | 0.66938 | 0.97231 | 0.68576 |  | 0.8829 | 0.97156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500385 | 882 | 488634 | 946 | 400188.231 | 1022.867 | 4.181 | 4.6002 | 4.0282 | 4.2668 | 3.9862 | 4.1321 | 5.3899 | 5.3278 | 5.4965 | 0 | 5.4868 | 5.4137 | 794000 | 1000 | 793000 | 2000 | 1580267 | 5067 | 1584000 | 1575200 | 10.75 | 4.1991 | 0.82499 | 5.423 | 0.83638 | 19.65% | 15.42% | 22.7778 | 35.3333 | 2.1312 | 4.9242 | 1590227.4 | 1579534 | 1765137 | 89.49% | 32 | 0
2023-12-11 | 2024 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 335090.89 | 7:13 | 17:58 | 9759.6 | 10180.5 | 10123.8 | 10083.2 | 10198.4 | 10265.9 | 10155.2 | 10598.9 | 10120 | 10129.9 | 9968.8 | 10132.9 | 10108 | 10085.3 | 10099.1 | 10193.4 | 10117.4 | 10226.8 | 10198.9 | 10222.4 | 10217.3 | 10208.3 | 10015.2 | 10148.6 | 9974.5 | 8753.4 | 10006.8 | 9963.4 | 10181.2 | 10101.9 | 9950.4 | 10236 | 10296.3 | 10348.5 | 10258.2 | 10211.3 | 10387 | 10265.8 | 10347.3 | 10157.8 | 11102.9 | 9799.3 | 10963.4 | 9743 | 10431.7 | 11725.3 | 9648.7 | 11032.9 | 9346.6 | 9589.9 | 10259.2 | 9650.6 | 10627.4 | 9431.2 | 10555.9 | 9371 | 9352 | 10786.4 | 9239.4 | 10735.7 | 10583.1 | 9336.3 | 10389.8 | 9786.1 | 10022.9 | 9413.7 | 9973.3 | 10416.9 | 10748.8 | 9594.5 | 10573.6 | 9203.7 | 10181.7 | 10041.1 | 9341.8 | 10629.9 | 9248.5 | 10612 | 9248.4 | 10492.2 | 9629.1 | 10379.8 | 9790.4 | 10895.4 | 9614.3 | 10314 | 9471.6 | 8422.5 | 10472.4 | 10003.3 | 9341.5 | 10877.4 | 10458 | 9582.5 | 9482.9 | 10583.2 | 9385.6 | 9750.3 | 10643.5 | 9305.6 | 10795.9 | 9298.6 | 10460.9 | 9574 | 10607.5 | 9075.4 | 10675.9 | 9564.8 | 10538.1 | 9580.1 | 10656.2 | 9699.6 | 9373.8 | 10471.9 | 9531.7 | 9344.9 | 10441.6 | 10704.6 | 10454.7 | 9492.2 | 10618.5 | 9481.1 | 10190.2 | 9585.3 | 10191.6 | 8850.8 | 10325.4 | 9468.9 | 9612.8 | 9607.7 | 9502 | 8211 | 9445.3 | 8340 | 9472.3 | 9466.2 | 10990.4 | 9446.4 | 11051.7 | 9717.1 | 10848.4 | 9510 | 9692.8 | 9567.5 | 10640.7 | 11051.6 | 10880.8 | 10796.4 | 10941.3 | 10937.4 | 9748.9 | 10883.3 | 10916.9 | 11018.1 | 11059.9 | 11029.2 | 11057.3 | 9822.5 | 11022.7 | 9821.4 | 23.596 | 23.5433 | 23.6485 | 23.4043 | 23.6931 | 23.6994 | 0 | 36.8 | 0 | 0 | 36.3 | 36.3 | 2.2501 | 2.3704 | 2.233 | 2.2038 | 2.2787 | 2.124 | 6.105 | 5.294 | 5.862 | 4.901 | 5.008 | 5.215 | 4.2408 | 4.442 | 4.0806 | 4.3265 | 4.0303 | 4.1746 | 0.69905 | 0.85605 | 0.71816 | 1.0967 | 0.82775 | 0.88506 | 5.433 | 5.5021 | 5.582 |  | 5.5853 | 5.4938 | 0.69629 | 1.001 | 0.70492 |  | 0.89773 | 0.98483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 501191 | 884 | 489435 | 948 | 401789.498 | 1027.8 | 4.2408 | 4.442 | 4.0806 | 4.3265 | 4.0303 | 4.1746 | 5.433 | 5.5021 | 5.582 | 0 | 5.5853 | 5.4938 | 806000 | 2000 | 801000 | 2000 | 1601267 | 4933 | 1603000 | 1596334 | 10.75 | 4.2158 | 0.84712 | 5.5192 | 0.85695 | 20.09% | 15.53% | 23.5974 | 36.4667 | 2.2433 | 5.3975 | 1611795.9 | 1600467 | 1793191.6144 | 89.25% | 33 | 0
2023-12-12 | 2024 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 335090.89 | 7:08 | 18:05 | 8398 | 8742 | 8681.6 | 8644.4 | 8740.8 | 8802.3 | 8733.7 | 9116.2 | 8715.3 | 8706.7 | 8587.4 | 8728.5 | 8699.5 | 8681.6 | 8683.6 | 8762.4 | 8681.3 | 8767.8 | 8775.3 | 8788.3 | 8784.1 | 8780.5 | 8598.7 | 8715.2 | 8561.5 | 7524.3 | 8595.6 | 8558.4 | 8749.9 | 8678.3 | 8540.1 | 8786.4 | 8834.8 | 8873 | 8820.1 | 8767.3 | 8904.3 | 8796.5 | 8865.7 | 8731.9 | 9510.4 | 8418.3 | 9397.6 | 8350.9 | 8951.9 | 10054.2 | 8261.9 | 9459.6 | 8044.4 | 8259 | 8834.7 | 8301.4 | 9151.2 | 8117 | 9090.8 | 8070.1 | 8054.4 | 9302.4 | 8058.5 | 9235.9 | 9106.6 | 8043.3 | 8923.6 | 8408.9 | 8631.2 | 8103 | 8587.8 | 8966.4 | 9264.5 | 8257.6 | 9110.3 | 7934.9 | 8775.3 | 8652.7 | 8036.1 | 9148.6 | 7956.4 | 9137.7 | 7971.1 | 9038.1 | 8276.4 | 8929.1 | 8410.7 | 9355 | 8265.5 | 8870.6 | 8185.6 | 7258.1 | 9031.6 | 8641.5 | 8046.7 | 9365.4 | 9017.2 | 8266.9 | 8185.4 | 9122.4 | 8081.1 | 8389.8 | 9156 | 8006.8 | 9296.9 | 8004.5 | 9009.5 | 8239.5 | 9122.8 | 7800.1 | 9176.7 | 8220 | 9064 | 8234.4 | 9150.4 | 8338 | 8067.6 | 9000 | 8202.7 | 8028.3 | 9004.5 | 9208.6 | 8992.5 | 8191.8 | 9136.1 | 8169.4 | 8777.7 | 8239.5 | 8761.2 | 7634.9 | 8909.2 | 8168.2 | 8270.9 | 8268.6 | 8203.5 | 7073.6 | 8133 | 7186.5 | 8181.7 | 8179.3 | 9475.7 | 8167.9 | 9538.8 | 8383.3 | 9370 | 8220.6 | 8377.1 | 8272.9 | 9175.3 | 9513.8 | 9374.4 | 9308 | 9415.4 | 9427.6 | 8417.6 | 9389.5 | 9388.6 | 9476.7 | 9529.7 | 9500.6 | 9528 | 8471.4 | 9511.7 | 8462.9 | 23.0388 | 22.9082 | 22.8606 | 22.9274 | 23.3383 | 22.8827 | 0 | 32.7 | 0 | 0 | 32.9299 | 32.6 | 2.8358 | 2.8722 | 2.8491 | 2.8109 | 2.7205 | 2.6263 | 4.977 | 5.632 | 5.677 | 4.633 | 5.488 | 4.958 | 3.6959 | 3.8811 | 3.5757 | 3.7814 | 3.5285 | 3.6936 | 0.59022 | 0.75065 | 0.60271 | 0.94566 | 0.73184 | 0.79286 | 4.712 | 4.6399 | 4.6967 |  | 4.7106 | 4.6296 | 0.59336 | 0.882 | 0.60099 |  | 0.79679 | 0.88062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 501885 | 886 | 490126 | 950 | 403169.098 | 1032.6 | 3.6959 | 3.8811 | 3.5757 | 3.7814 | 3.5285 | 3.6936 | 4.712 | 4.6399 | 4.6967 | 0 | 4.7106 | 4.6296 | 694000 | 2000 | 691000 | 2000 | 1379600 | 4800 | 1381000 | 1374800 | 10.95 | 3.6927 | 0.73566 | 4.6778 | 0.75075 | 19.92% | 16.05% | 22.9926 | 32.7433 | 2.7858 | 5.2275 | 1387087.4 | 1378400 | 1537393.9112 | 89.66% | 31 | 0
2023-12-13 | 2024 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 335090.89 | 7:15 | 18:05 | 9322.2 | 9737.3 | 9663.8 | 9643 | 9707.3 | 9806.3 | 9750.6 | 10173.2 | 9683.1 | 9612.9 | 9550.9 | 9704.9 | 9702.8 | 9656.5 | 9697.4 | 9788.9 | 9715.3 | 9813 | 9779.5 | 9798.2 | 9789.1 | 9784.1 | 9588.8 | 9717.5 | 9529.6 | 8369 | 9576.7 | 9537.4 | 9741.9 | 9668.3 | 9520.5 | 9778.3 | 9828.4 | 9883.7 | 9803.9 | 9741.9 | 9907.7 | 9787.8 | 9873.3 | 9712.6 | 10650.7 | 9410.2 | 10552.7 | 9376 | 10020.3 | 11268 | 9242.2 | 10567 | 8934.7 | 9167.7 | 9810.9 | 9215.7 | 10170.8 | 9018.8 | 10087.5 | 8957.9 | 8934.6 | 10311.7 | 8934.7 | 10248.9 | 10107.6 | 8928.1 | 9894.2 | 9336 | 9548.7 | 8961.8 | 9491.7 | 9912.5 | 10218 | 9111.6 | 10042.7 | 8736.5 | 9668.1 | 9524.2 | 8878.9 | 10083 | 8761.4 | 10085.8 | 8777.5 | 9983.9 | 9164.7 | 9868.2 | 9309.2 | 10377.4 | 9159 | 9811.7 | 9074.4 | 8043.7 | 9979.4 | 9557.8 | 8927 | 10379.6 | 10011.8 | 9186 | 9082.4 | 10117.8 | 8976 | 9329.8 | 10187.8 | 8927.3 | 10360.3 | 8929.8 | 10059.9 | 9204 | 10205.1 | 8724.6 | 10275 | 9216.5 | 10140.1 | 9229.4 | 10253.2 | 9353 | 9015.6 | 10077.2 | 9193.8 | 9002.2 | 10090.5 | 10339.8 | 10100.8 | 9191.4 | 10253.5 | 9158.8 | 9847.4 | 9254.7 | 9841.1 | 8539.8 | 9977.1 | 9139.2 | 9282.8 | 9276.3 | 9182.7 | 7930.7 | 9113.9 | 8053.9 | 9176.7 | 9175.9 | 10670.8 | 9184.4 | 10716.3 | 9423.8 | 10536.2 | 9257.3 | 9435.2 | 9284 | 10292.2 | 10682.8 | 10519 | 10429.4 | 10583 | 10619.1 | 9456.3 | 10537.6 | 10486.1 | 10616.3 | 10671 | 10642.3 | 10687.5 | 9483.3 | 10624.9 | 9488.1 | 23.0558 | 22.8702 | 22.752 | 22.746 | 22.9499 | 22.7729 | 0 | 35.6 | 0 | 0 | 35.8 | 35.3 | 1.8189 | 1.9151 | 1.8997 | 1.8803 | 1.9639 | 1.9156 | 3.62 | 3.672 | 3.603 | 3.586 | 3.675 | 3.634 | 4.0787 | 4.0914 | 3.9639 | 4.1464 | 3.9102 | 4.0626 | 0.68394 | 0.86074 | 0.69895 | 1.1004 | 0.80573 | 0.85826 | 5.3089 | 5.2019 | 5.3262 |  | 5.3579 | 5.2465 | 0.68337 | 0.90932 | 0.69052 |  | 0.88027 | 0.95955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 502656 | 887 | 490898 | 951 | 404705.8 | 1037.533 | 4.0787 | 4.0914 | 3.9639 | 4.1464 | 3.9102 | 4.0626 | 5.3089 | 5.2019 | 5.3262 | 0 | 5.3579 | 5.2465 | 771000 | 1000 | 772000 | 1000 | 1536702 | 4933 | 1541000 | 1531769 | 10.8333 | 4.0422 | 0.83467 | 5.2883 | 0.82461 | 20.65% | 15.59% | 22.8578 | 35.5667 | 1.8989 | 3.6317 | 1546345.4 | 1535734 | 1721974.7562 | 89.18% | 31 | 0
2023-12-14 | 2024 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 335090.89 | 7:15 | 17:59 | 9667.5 | 10072.6 | 9975.4 | 9948 | 10004.8 | 10128.5 | 10064.6 | 10495.5 | 10024.8 | 9970.1 | 9878.2 | 10050.6 | 10014.3 | 9988.2 | 9961.5 | 10081.5 | 9984.2 | 10097.6 | 10084.7 | 10120.1 | 10076.9 | 10080.7 | 9862.1 | 10004.2 | 9847.4 | 8646 | 9895 | 9849.3 | 10040 | 9955.2 | 9804.3 | 10096.7 | 10157.2 | 10216.2 | 9946.2 | 9890.9 | 10241.5 | 10104.1 | 10180.5 | 10009.7 | 10948.4 | 9658.7 | 10830.7 | 9613.3 | 10257.1 | 11549.1 | 9524 | 10893.2 | 9260.4 | 9512.2 | 10159 | 9566.3 | 10512.9 | 9313.9 | 10465.8 | 9264.5 | 9280.8 | 10717.7 | 9275.1 | 10663.8 | 10531.7 | 9270.9 | 10285.5 | 9708.9 | 9927.7 | 9347.7 | 9898.8 | 10349.4 | 10650.6 | 9525.8 | 10500 | 9149.8 | 10076.3 | 9965.1 | 9264.5 | 10561.3 | 9167.7 | 10504.3 | 9158.6 | 10418.1 | 9567 | 10326.4 | 9729.5 | 10838.3 | 9558.7 | 10240.2 | 9449.1 | 8391.8 | 10363.5 | 9941.1 | 9274 | 10760.5 | 10356 | 9487.6 | 9372.6 | 10476.7 | 9296.6 | 9668.7 | 10528.2 | 9220.5 | 10700.6 | 9216.6 | 10369.5 | 9476.1 | 10513.5 | 8981.7 | 10568.5 | 9464.8 | 10429.8 | 9467.5 | 10507 | 9573.4 | 9298.6 | 10356.8 | 9458.9 | 9246.2 | 10349 | 10590.1 | 10345.9 | 9412.6 | 10495.1 | 9384.4 | 10073.7 | 9463 | 10065.4 | 8756.5 | 10227.3 | 9361 | 9507.8 | 9497.1 | 9380 | 8111.1 | 9322.3 | 8241.1 | 9386.5 | 9390 | 10966.5 | 9430.2 | 11014 | 9691.5 | 10812 | 9471.8 | 9646.8 | 9495 | 10648.3 | 11044.1 | 10894.8 | 10788.3 | 10923.7 | 10933.6 | 9731.7 | 10867.9 | 10869.6 | 11004.2 | 11067.3 | 11020.3 | 11056.3 | 9809 | 10997.6 | 9821.9 | 23.77 | 23.62 | 23.5 | 23.44 | 23.72 | 23.66 | 0 | 37.3 | 0 | 0 | 36.9 | 36.8 | 1.94 | 1.86 | 1.79 | 1.98 | 1.93 | 1.95 | 4.62 | 4.64 | 3.78 | 4.42 | 4.34 | 4.54 | 4.22 | 4.19 | 4.04 | 4.3 | 3.97 | 4.17 | 0.71 | 0.89 | 0.72 | 1.14 | 0.82 | 0.88 | 5.55 | 5.39 | 5.51 | 5.47 | 5.53 | 5.44 | 0.7 | 0.94 | 0.71 | 1.08 | 0.9 | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 503453 | 889 | 491694 | 954 | 406292.4 | 1042.6 | 4.22 | 4.19 | 4.04 | 4.3 | 3.97 | 4.17 | 5.55 | 5.39 | 5.51 | 5.47 | 5.53 | 5.44 | 797000 | 2000 | 796000 | 3000 | 1586600 | 5067 | 1588000 | 1581533 | 10.7333 | 4.1483 | 0.86 | 5.4817 | 0.88667 | 20.73% | 16.18% | 23.6183 | 37 | 1.9083 | 4.39 | 1596889.2 | 1585066 | 1774874 | 89.31% | 32 | 0
2023-12-15 | 2024 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 335090.89 | 7:16 | 18:04 | 9474 | 9893.7 | 9781.3 | 9730.5 | 9847.8 | 9945.3 | 9872.1 | 10303.4 | 9846.8 | 9802.1 | 9706.6 | 9872 | 9835.6 | 9814.1 | 9778.2 | 9904 | 9806.6 | 9920.2 | 9917.8 | 9939.9 | 9915.1 | 9916.5 | 9709.6 | 9846.9 | 9689 | 8498.8 | 9724.5 | 9690 | 9884.7 | 9808.3 | 9650.1 | 9936.6 | 9990.6 | 10046.5 | 9966 | 9904.6 | 10077.3 | 9933.3 | 10010.7 | 9850.3 | 10768.5 | 9506.7 | 10647.5 | 9452.2 | 10086.7 | 11353.6 | 9352.8 | 10713.3 | 9087.4 | 9332.6 | 9966.7 | 9382.6 | 10324 | 9154.5 | 10262.3 | 9094.6 | 9097.4 | 10510.1 | 9104.5 | 10449.2 | 10319.2 | 9097.3 | 10106.8 | 9544 | 9733.2 | 9168.1 | 9699.7 | 10152.7 | 10434.6 | 9341.3 | 10277.4 | 8985.9 | 9866.7 | 9778.3 | 9063.4 | 10341.6 | 8951.3 | 10312.3 | 9000.5 | 10197.3 | 9282.8 | 10098.4 | 9506.7 | 10547 | 9346.1 | 10001.9 | 9249.1 | 8210.2 | 10144.4 | 9740.4 | 9074.2 | 10547.3 | 10169.7 | 9332.6 | 9230.3 | 10274.4 | 9113.5 | 9477.2 | 10336.8 | 9055.6 | 10514.5 | 9050.5 | 10199.5 | 9319.2 | 10349.4 | 8834.9 | 10410.2 | 9321.2 | 10284.8 | 9342.3 | 10388.2 | 9452.7 | 9123.3 | 10178.3 | 9301.7 | 9091.8 | 10195.6 | 10431.2 | 10204.3 | 9269 | 10362.4 | 9249.1 | 9942.5 | 9339.9 | 9943.8 | 8626.9 | 10080 | 9223.3 | 9361.7 | 9342.5 | 9258.3 | 8000.9 | 9170.5 | 8102.6 | 9199.2 | 9191.4 | 10747.6 | 9242.7 | 10794.5 | 9492 | 10595.6 | 9290.9 | 9468.2 | 9293.6 | 10404.9 | 10801 | 10641.8 | 10554.6 | 10694.4 | 10704.9 | 9532.3 | 10646.8 | 10631.6 | 10742.5 | 10793.2 | 10758 | 10795.7 | 9585.1 | 10754.6 | 9598.3 | 23.1308 | 22.8417 | 22.8695 | 22.7159 | 23.0087 | 22.7267 | 0 | 36.2 | 0 | 0 | 36.2 | 35.7 | 2.1093 | 2.0673 | 1.9722 | 2.0351 | 1.8745 | 1.8748 | 5.193 | 4.634 | 4.539 | 5.105 | 4.279 | 4.826 |  | 4.1277 |  | 4.2117 |  | 4.0837 |  | 0.88324 |  | 1.1234 |  | 0.86764 |  | 5.2974 |  | 5.2891 |  | 5.2837 |  | 0.93643 |  | 1.0793 |  | 0.97017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 504236 | 891 | 492473 | 955 | 407849.8 | 1047.6 | 0 | 4.1277 | 0 | 4.2117 | 0 | 4.0837 | 0 | 5.2974 | 0 | 5.2891 | 0 | 5.2837 | 783000 | 2000 | 779000 | 1000 | 1557400 | 5000 | 1559000 | 1552400 | 10.8 | 4.141 | 0.9581 | 5.29 | 0.9953 | 23.14% | 18.81% | 22.8822 | 36.0333 | 1.9889 | 4.7627 | 1568021.2 | 1555734 | 1721979.6702 | 90.35% | 33 | 0
2023-12-16 | 2024 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 335090.89 | 7:17 | 17:59 | 9305.3 | 9707.8 | 9588.4 | 9556.1 | 9660.4 | 9743 | 9686.8 | 10082.1 | 9654.2 | 9650 | 9505.7 | 9668.3 | 9630.1 | 9610.2 | 9586.8 | 9701.5 | 9606.7 | 9711.1 | 9709.1 | 9734.1 | 9712.5 | 9713.7 | 9519.8 | 9649.1 | 9503.7 | 8335.4 | 9527.8 | 9493.7 | 9689.1 | 9621.7 | 9476.3 | 9753.6 | 9790.6 | 9848.7 | 9541.9 | 9479.2 | 9882.3 | 9746.7 | 9751.9 | 9655.1 | 10626 | 9372 | 10483.6 | 9312.6 | 9950.6 | 11187.5 | 9233.3 | 10557.6 | 8901.6 | 9141.6 | 9766.1 | 9198.1 | 10114.3 | 8974.6 | 10066.7 | 8927.7 | 8924.5 | 10326.8 | 8932 | 10241.9 | 10111.5 | 8915.1 | 9890.7 | 9344.5 | 9561.2 | 8995.8 | 9529.1 | 9998.1 | 10252.8 | 9190.7 | 10099.4 | 8849 | 9700.6 | 9615.4 | 8905.2 | 10165.1 | 8802.5 | 10142.7 | 8849.6 | 10008.7 | 9180.3 | 9989.9 | 9362.9 | 10373.5 | 9200.4 | 9830.9 | 9085.5 | 8072.3 | 9958 | 9576.6 | 8928.7 | 10361 | 9987.1 | 9162.9 | 9062.4 | 10101.9 | 8944.3 | 9324.8 | 10170.3 | 8902.7 | 10328.8 | 8904.1 | 10017.5 | 9152.2 | 10160.3 | 8673.6 | 10200.3 | 9139.9 | 10078.9 | 9157 | 10184 | 9272.1 | 8976.4 | 9992.8 | 9132.5 | 8932 | 9997.1 | 10228.7 | 10004.5 | 9080.8 | 10149.3 | 9067.1 | 9752.1 | 9151.9 | 9741.1 | 8468.4 | 9884.4 | 9050.7 | 9175.9 | 9168.2 | 9094.2 | 7848.7 | 8989.4 | 7937.8 | 9057.1 | 9042.7 | 10557.9 | 9073.5 | 10624.7 | 9343 | 10430 | 9135.8 | 9317.8 | 9135 | 10234.8 | 10631.6 | 10464.8 | 10378.7 | 10502.8 | 10518.5 | 9380.1 | 10476.2 | 10459.6 | 10564.4 | 10627.8 | 10593.1 | 10639.4 | 9443.6 | 10580.3 | 9453.8 | 23.37 | 23.2497 | 23.1869 | 23.1135 | 23.5235 | 23.1691 | 0 | 34.8 | 0 | 0 | 34.9 | 34.8 | 2.398 | 2.4181 | 2.4881 | 2.4466 | 2.4752 | 2.4455 | 6.252 | 5.586 | 5.312 | 5.938 | 5.427 | 5.835 |  | 4.026 |  | 4.1032 |  | 3.4074 |  | 0.86285 |  | 1.1032 |  | 0.71962 |  | 5.1612 |  | 5.251 |  | 5.1653 |  | 0.91162 |  |  |  | 0.94591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 505004 | 893 | 493242 | 957 | 409379.165 | 1052.533 | 0 | 4.026 | 0 | 4.1032 | 0 | 3.4074 | 0 | 5.1612 | 0 | 5.251 | 0 | 5.1653 | 768000 | 2000 | 769000 | 2000 | 1529365 | 4933 | 1533000 | 1524432 | 10.7 | 3.8455 | 0.89522 | 5.1925 | 0.92877 | 23.28% | 17.89% | 23.2688 | 34.8333 | 2.4453 | 5.725 | 1539293.4 | 1527934 | 1692026.0274 | 90.3% | 25 | 0
2023-12-17 | 2024 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 335090.89 | 7:18 | 18:00 | 9691.7 | 10107.7 | 9994 | 9979.1 | 10026.4 | 10165.1 | 10076.2 | 10462.2 | 10020.2 | 10016.8 | 9866.4 | 10033.4 | 9996.5 | 9961.5 | 9982.4 | 10095 | 10006.7 | 10117.1 | 10103.1 | 10137.7 | 10104.7 | 10102.5 | 9897 | 10033.7 | 9862.4 | 8653.3 | 9906 | 9868.1 | 10065.5 | 10019.8 | 9850.5 | 10127.9 | 10165.7 | 10225.7 | 10083.9 | 10047 | 10271.4 | 10145.2 | 10214 | 10037.2 | 11055.7 | 9745 | 10881.5 | 9663.2 | 10348.2 | 11643.2 | 9603.2 | 10977.5 | 9255.2 | 9501.2 | 10159.6 | 9565.7 | 10523.7 | 9336.6 | 10464.3 | 9275.4 | 9272.6 | 10740.6 | 9277.9 | 10644.2 | 10513.3 | 9265.6 | 10264.1 | 9709.8 | 9908.3 | 9314.6 | 9885.7 | 10339.1 | 10652.3 | 9505.9 | 10482.2 | 9157.2 | 10083.5 | 9972.3 | 9267.2 | 10557 | 9100.8 | 10478 | 9212.8 | 10412.1 | 9515.5 | 10322.7 | 9669.2 | 10785.9 | 9505.1 | 10192.1 | 9380.8 | 8330.5 | 10322.9 | 9888.1 | 9265.8 | 10750.3 | 10358.8 | 9510.2 | 9405.5 | 10464.1 | 9249.7 | 9655.8 | 10516.5 | 9209.3 | 10667.7 | 9202.5 | 10347.5 | 9465.2 | 10505.6 | 8971.5 | 10560 | 9464.1 | 10434.9 | 9483.9 | 10553.1 | 9615.5 | 9283.8 | 10337.5 | 9437 | 9232.5 | 10331.8 | 10583.2 | 10338 | 9390.5 | 10488.8 | 9371 | 10080.4 | 9480.7 | 10083.9 | 8761.5 | 10216.7 | 9355.5 | 9489 | 9490.6 | 9399.6 | 8115.1 | 9307.2 | 8215.9 | 9371.2 | 9355.9 | 10915.1 | 9387 | 10982 | 9652.7 | 10768.8 | 9429.7 | 9605.9 | 9447.3 | 10550 | 10964.4 | 10774.1 | 10692.7 | 10844.5 | 10876.1 | 9694.3 | 10818.2 | 10777.8 | 10881.7 | 10950.7 | 10920.3 | 10957.5 | 9734.8 | 10903.7 | 9737.6 | 22.2881 | 22.1322 | 22.0499 | 22.1834 | 22.3957 | 22.1728 | 0 | 34.3 | 0 | 0 | 34.3 | 34.3 | 2.3479 | 2.345 | 2.3235 | 2.3558 | 2.3785 | 2.2327 | 5.86 | 5.432 | 4.888 | 5.785 | 5.773 | 5.592 |  | 4.1521 |  | 4.2384 |  | 4.1178 |  | 0.90489 |  | 1.1289 |  | 0.88338 |  | 5.3428 |  |  |  | 5.3316 |  | 0.95447 |  |  |  | 0.98481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 505803 | 894 | 494035 | 959 | 410964.3 | 1057.467 | 0 | 4.1521 | 0 | 4.2384 | 0 | 4.1178 | 0 | 5.3428 | 0 | 0 | 0 | 5.3316 | 799000 | 1000 | 793000 | 2000 | 1585135 | 4934 | 1589000 | 1580201 | 10.7 | 4.1694 | 0.97239 | 5.3372 | 0.96964 | 23.32% | 18.17% | 22.2037 | 34.3 | 2.3306 | 5.555 | 1595891.5 | 1583800 | 1742248.4369 | 90.91% | 30 | 0
2023-12-18 | 2024 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 335090.89 | 7:20 | 17:58 | 9498.1 | 9879.1 | 9762.7 | 9747.2 | 9782.2 | 9936.1 | 9845.2 | 10231.7 | 9810.3 | 9793.9 | 9660.9 | 9829.7 | 9782.1 | 9754.6 | 9739.5 | 9858.6 | 9782.5 | 9900.5 | 9885.6 | 9924.3 | 9898 | 9896.4 | 9702 | 9832.5 | 9672.2 | 8488.6 | 9702.8 | 9666.4 | 9862.5 | 9797.2 | 9639.6 | 9922 | 9962.6 | 10034.7 | 9955.4 | 9903.2 | 10057.4 | 9934.4 | 10020.2 | 9834 | 10796.4 | 9519.8 | 10649.8 | 9443.1 | 10115 | 11405.6 | 9395.6 | 10741.6 | 9066.2 | 9312.9 | 9941.9 | 9363.9 | 10299.7 | 9117.4 | 10263 | 9102.8 | 9087.4 | 10528.9 | 9102.8 | 10438.9 | 10324 | 9101.7 | 10046.3 | 9514.7 | 9722.2 | 9144.2 | 9708.7 | 10159.5 | 10457.7 | 9344.3 | 10294 | 9002 | 9897.7 | 9800.6 | 9100.5 | 10379.4 | 9012.8 | 10358.6 | 9046.8 | 10234.2 | 9373.2 | 10175.3 | 9501.9 | 10607.1 | 9341.9 | 10018.6 | 9208.6 | 8195.1 | 10129 | 9731.7 | 9088.5 | 10538 | 10166.4 | 9334.2 | 9227.8 | 10252.3 | 9085.6 | 9473.8 | 10322.7 | 9034.7 | 10473.2 | 9030.5 | 10156.7 | 9289.7 | 10296.9 | 8798.2 | 10354.4 | 9277.7 | 10229.1 | 9301.2 | 10333.8 | 9421.4 | 9109.6 | 10171.5 | 9247.5 | 9046.1 | 10132.8 | 10418.1 | 10145 | 9244.2 | 10313.6 | 9223.1 | 9885.5 | 9299.6 | 9882 | 8616.9 | 10053.9 | 9217.5 | 9352.9 | 9358.8 | 9245.1 | 7982.5 | 9169.3 | 8117.1 | 9237.8 | 9235.7 | 10751.2 | 9245.3 | 10804.8 | 9497.1 | 10612.4 | 9310.6 | 9472.1 | 9344.8 | 10412.9 | 10802.2 | 10639.8 | 10552.9 | 10694.6 | 10716.4 | 9543.4 | 10649.5 | 10685.2 | 10766.3 | 10823.8 | 10774.1 | 10811 | 9596.6 | 10757 | 9607.5 | 21.9262 | 21.2977 | 21.455 | 21.304 | 21.3271 | 21.3518 | 0 | 31.2 | 0 | 0 | 30.9 | 31.1 | 3.4228 | 3.4753 | 3.4503 | 3.5097 | 3.5187 | 3.4515 | 6.345 | 6.313 | 6.153 | 6.298 | 7.091 | 6.6783 |  | 4.0642 |  | 4.1587 |  | 4.0477 |  | 0.90211 |  | 1.1292 |  | 0.91256 |  | 5.1911 |  | 5.2281 |  | 5.2039 |  | 0.95216 |  | 1.1031 |  | 1.0052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 506585 | 896 | 494815 | 961 | 412520.699 | 1062.667 | 0 | 4.0642 | 0 | 4.1587 | 0 | 4.0477 | 0 | 5.1911 | 0 | 5.2281 | 0 | 5.2039 | 782000 | 2000 | 780000 | 2000 | 1556399 | 5200 | 1558000 | 1551199 | 10.6333 | 4.0902 | 0.9813 | 5.2077 | 1.0202 | 23.99% | 19.59% | 21.4436 | 31.0667 | 3.4714 | 6.4797 | 1566876.3 | 1555467 | 1715918.0728 | 90.65% | 35 | 0
2023-12-19 | 2024 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 335090.89 | 7:22 | 18:01 | 8810.9 | 9155.4 | 9038 | 9034 | 9043.7 | 9204.4 | 9118.3 | 9437.9 | 9088.3 | 9029.8 | 8973.5 | 9111.2 | 9084.2 | 9053.8 | 9073.9 | 9157 | 9040.1 | 9149.2 | 9149.8 | 9191.5 | 9165.3 | 9170.2 | 9015.9 | 9108.6 | 8963.3 | 7934 | 8990.6 | 8957.5 | 9126.2 | 9070.3 | 8943.7 | 9170.9 | 9250.7 | 9311.6 | 9203.1 | 9146.8 | 9263.6 | 9172.9 | 9237 | 9094 | 9887.1 | 8870.2 | 9764.2 | 8804.3 | 9355.5 | 10349.5 | 8748 | 9846.3 | 8464.6 | 8671.8 | 9198.9 | 8702.3 | 9488.6 | 8498.2 | 9438.8 | 8494.9 | 8469.7 | 9639.2 | 8498.7 | 9568.1 | 9475.9 | 8489.5 | 9239.6 | 8785.1 | 8993.4 | 8516.2 | 8982.4 | 9344.3 | 9561.5 | 8676.3 | 9435.7 | 8381.9 | 9129 | 9045.7 | 8457 | 9499.8 | 8390.9 | 9474.7 | 8413.4 | 9386 | 8700.4 | 9346 | 8830.3 | 9691.1 | 8684.4 | 9242.3 | 8570.2 | 7676.1 | 9316.3 | 9022.4 | 8463.1 | 9631.6 | 9342.8 | 8659.3 | 8583.1 | 9417.5 | 8485.7 | 8817.1 | 9484.7 | 8442.4 | 9597.4 | 8438.7 | 9367.8 | 8661.4 | 9444.7 | 8224.2 | 9510.3 | 8650.6 | 9408.1 | 8651.5 | 9487.3 | 8770.2 | 8491 | 9353.9 | 8620.9 | 8460.7 | 9351.4 | 9560 | 9352.9 | 8639.7 | 9487.2 | 8612.1 | 9146.5 | 8665.1 | 9138.2 | 8093 | 9311.8 | 8621.8 | 8728.1 | 8723.6 | 8640.9 | 7506.3 | 8551.7 | 7592 | 8593.5 | 8589.4 | 9815.6 | 8620.1 | 9831.4 | 8821.3 | 9689.1 | 8656.6 | 8798.1 | 8663.1 | 9542.5 | 9820.7 | 9745.5 | 9680.4 | 9774 | 9783.1 | 8852.7 | 9713.7 | 9756.7 | 9818.3 | 9831.2 | 9789.8 | 9830.5 | 8889.8 | 9806.5 | 8922 | 20.7071 | 20.3153 | 20.1957 | 20.1545 | 20.2033 | 20.1186 | 0 | 31.2 | 0 | 0 | 31.1 | 30.9 | 2.7864 | 2.8114 | 2.8312 | 2.8405 | 2.8518 | 2.8906 | 4.85 | 5.053 | 5.29 | 4.998 | 5.109 | 5.462 |  | 3.9008 |  | 3.9668 |  | 3.8724 |  | 0.85535 |  | 1.1147 |  | 0.85002 |  | 4.8222 |  | 4.8693 |  | 4.8593 |  | 0.90518 |  | 1.0841 |  | 0.94329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 507309 | 898 | 495536 | 962 | 413959.699 | 1067.667 | 0 | 3.9008 | 0 | 3.9668 | 0 | 3.8724 | 0 | 4.8222 | 0 | 4.8693 | 0 | 4.8593 | 724000 | 2000 | 721000 | 1000 | 1439000 | 5000 | 1442000 | 1434000 | 10.65 | 3.9133 | 0.94002 | 4.8502 | 0.97752 | 24.02% | 20.15% | 20.2824 | 31.0667 | 2.8353 | 5.127 | 1448581.7 | 1437133 | 1601318.8503 | 89.75% | 34 | 10750
2023-12-20 | 2024 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 335090.89 | 7:26 | 17:57 | 8270.8 | 8624.4 | 8511.2 | 8501.7 | 8522.1 | 8651.1 | 8574.4 | 8933.1 | 8559.2 | 8473.9 | 8448.3 | 8593.9 | 8547.8 | 8531.3 | 8525.7 | 8622.3 | 8540 | 8635.8 | 8634.3 | 8670.4 | 8644.2 | 8648.6 | 8484.7 | 8578.9 | 8438.6 | 7415.4 | 8479 | 8438.1 | 8613.7 | 8554.4 | 8425.6 | 8657.3 | 8673.7 | 8739.4 | 8690 | 8624.3 | 8743.7 | 8655.2 | 8718.7 | 8573.7 | 9389.9 | 8344.8 | 9281.5 | 8273.7 | 8845.1 | 9886.8 | 8227.3 | 9355.4 | 7925.1 | 8133.6 | 8680.7 | 8167.8 | 8985.1 | 7966.7 | 8933.5 | 7947 | 7928.4 | 9146.3 | 7955.2 | 9073.1 | 8976.6 | 7952.5 | 8736.7 | 8264.8 | 8474.3 | 7971.4 | 8444 | 8835 | 9071.5 | 8137.7 | 8933.4 | 7832.8 | 8616.5 | 8511.2 | 7916 | 8993.2 | 7820.2 | 8979.3 | 7875.5 | 8887 | 8152 | 8831 | 8274.1 | 9201.9 | 8138.5 | 8720.5 | 8054.9 | 7153.9 | 8823.1 | 8496.1 | 7922.2 | 9158.5 | 8862.8 | 8152.9 | 8073.4 | 8920.1 | 7929.6 | 8278.7 | 9004.6 | 7900.8 | 9127.8 | 7899.5 | 8867.1 | 8118.1 | 8975.4 | 7694.1 | 9028.7 | 8121.8 | 8913 | 8126.6 | 8989.4 | 8230 | 7952.3 | 8861.4 | 8077.3 | 7916.2 | 8890.2 | 9062.6 | 8858.6 | 8078.8 | 8994.1 | 8063.5 | 8642.7 | 8133.3 | 8630.7 | 7545.9 | 8791.1 | 8059.5 | 8152.1 | 8150.1 | 8061.7 | 6968.8 | 7977.3 | 7038.9 | 8022.4 | 8023.8 | 9314.7 | 7989.2 | 9336.6 | 8247.3 | 9172.1 | 8068.8 | 8217.2 | 8097.6 | 9013.7 | 9340.6 | 9231.8 | 9163.6 | 9267.2 | 9266.7 | 8276.8 | 9217.4 | 9233.1 | 9306.3 | 9362.2 | 9314.3 | 9343.6 | 8325 | 9281.3 | 8339.3 | 21.2287 | 20.711 | 20.7408 | 20.7095 | 20.6254 | 20.6834 | 0 | 29.1 | 0 | 0 | 28.8 | 28.1816 | 3.2717 | 3.2887 | 3.2876 | 3.3941 | 3.4364 | 3.3412 | 6.208 | 6.991 | 5.916 | 6.691 | 6.535 | 6.463 |  | 3.6077 |  | 3.6631 |  | 3.55 |  | 0.78395 |  | 1.0227 |  | 0.744 |  | 4.439 |  | 4.4874 |  | 4.4242 |  | 0.83398 |  | 0.99968 |  | 0.83878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 507992 | 899 | 496215 | 964 | 415315.699 | 1072.733 | 0 | 3.6077 | 0 | 3.6631 | 0 | 3.55 | 0 | 4.439 | 0 | 4.4874 | 0 | 4.4242 | 683000 | 1000 | 679000 | 2000 | 1356000 | 5066 | 1359000 | 1350934 | 10.5167 | 3.6069 | 0.85023 | 4.4502 | 0.89081 | 23.57% | 20.02% | 20.7831 | 28.6939 | 3.3366 | 6.4673 | 1364666.3 | 1355066 | 1480470.3328 | 91.53% | 35 | 6534
2023-12-21 | 2024 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 335090.89 | 7:25 | 18:04 | 9591.5 | 9991.4 | 9883.2 | 9870.7 | 9932.2 | 10028.3 | 9917.6 | 10284.3 | 9894.7 | 9822.5 | 9782.4 | 9946.2 | 9898.1 | 9879.4 | 9847.8 | 9978.9 | 9886.6 | 10002.5 | 9996.1 | 10044.9 | 9995.9 | 10010.2 | 9823.6 | 9942.5 | 9796.8 | 8611.9 | 9844.3 | 9793.3 | 9973.9 | 9906 | 9757.6 | 10027.3 | 10069.2 | 10157.3 | 10084.6 | 10009.3 | 10140.1 | 10037.2 | 10101.6 | 9928.8 | 10799.7 | 9655 | 10671.1 | 9587.3 | 10224.4 | 11274.9 | 9528.8 | 10742.7 | 9185.9 | 9428.3 | 10058.6 | 9488.8 | 10383.7 | 9275.5 | 10334.6 | 9213.8 | 9210.4 | 10571 | 9219.2 | 10491.6 | 10393 | 9221.4 | 10154.7 | 9648.4 | 9847.8 | 9273.7 | 9810 | 10247.9 | 10480.7 | 9462.4 | 10343.9 | 9109.5 | 9990.9 | 9894.3 | 9198.3 | 10412.9 | 9110.5 | 10396.9 | 9155.2 | 10300.8 | 9479.8 | 10250.2 | 9652.8 | 10625.3 | 9478.7 | 10133.6 | 9350.6 | 8301.4 | 10207.1 | 9843.1 | 9186.5 | 10552.2 | 10241.2 | 9430.2 | 9333 | 10313.5 | 9186.5 | 9599.8 | 10391.2 | 9164 | 10515.8 | 9160.2 | 10250.6 | 9413.1 | 9995.2 | 8409.7 | 10433.4 | 9423.1 | 10326 | 9431.7 | 10403.8 | 9556.1 | 9217.1 | 10256.2 | 9380.1 | 9184.5 | 10251.3 | 10466 | 10250.9 | 9370.5 | 10388.5 | 9358.2 | 10007.3 | 9439.9 | 10009 | 8739 | 10169.4 | 9354.8 | 9477.1 | 9465.3 | 9365.9 | 8090.8 | 9284.8 | 8216.2 | 9093.3 | 9299.7 | 10746.6 | 9265.8 | 10764.5 | 9609.3 | 10611.9 | 9423.2 | 9592.2 | 9442.4 | 10457.3 | 10774.3 | 10685 | 10596.9 | 10720.2 | 10711.7 | 9641.4 | 10653.2 | 10687.1 | 10745.1 | 10799.3 | 10753 | 10786.9 | 9703 | 10751.4 | 9727.1 | 23.6072 | 22.9003 | 22.9345 | 22.8466 | 22.7543 | 22.6893 | 0 | 32.9 | 0 | 0 | 32.7 | 32.8 | 3.3096 | 3.4325 | 3.3254 | 3.5092 | 3.4587 | 3.3324 | 5.783 | 5.807 | 5.703 | 5.704 | 5.917 | 5.506 |  | 4.0994 |  | 4.1938 |  | 4.0698 |  | 0.89465 |  | 1.1639 |  | 0.86389 |  | 5.2564 |  | 5.2879 |  | 5.2789 |  | 0.9475 |  | 1.134 |  | 0.96891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 508782 | 901 | 497000 | 966 | 416884.699 | 1077.667 | 0 | 4.0994 | 0 | 4.1938 | 0 | 4.0698 | 0 | 5.2564 | 0 | 5.2879 | 0 | 5.2789 | 790000 | 2000 | 785000 | 2000 | 1569000 | 4934 | 1571000 | 1564066 | 10.65 | 4.121 | 0.97415 | 5.2744 | 1.0168 | 23.64% | 19.28% | 22.9554 | 32.8 | 3.3946 | 5.7367 | 1580113.2 | 1567667 | 1727234.4809 | 90.76% | 34 | 1114
2023-12-22 | 2024 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 335090.89 | 7:31 | 18:04 | 8566.3 | 8899.5 | 8806.5 | 8778.9 | 8833.7 | 8969.8 | 8914.2 | 9222.3 | 8814.7 | 8806.6 | 8720.8 | 8856.1 | 8848.7 | 8810.8 | 8804.9 | 8898.9 | 8829.3 | 8933.8 | 8895.1 | 8937.6 | 8922.3 | 8917.8 | 8773 | 8874.8 | 8725.8 | 7686.2 | 8761.3 | 8706 | 8884.1 | 8859.9 | 8717.4 | 8932.1 | 8964.7 | 9031.6 | 8985.1 | 8926 | 9035.5 | 8929.5 | 8992.4 | 8845.4 | 9593 | 8616.4 | 9518.5 | 8529.3 | 9162.4 | 10036.7 | 8553.1 | 9590.9 | 8186 | 8411.3 | 8962.7 | 8463.8 | 9259 | 8274.8 | 9216.4 | 8212.2 | 8236.3 | 9418.6 | 8223.5 | 9364.1 | 9274.6 | 8240.2 | 9022.6 | 8563.8 | 8758 | 8212.8 | 8715 | 9049 | 9307.4 | 8356.4 | 9186.7 | 8046.6 | 8882.3 | 8764.8 | 8162 | 9210.3 | 8070.2 | 9220.2 | 8129.1 | 9121.5 | 8308.6 | 8936.4 | 8450 | 9327.6 | 8328 | 8907.2 | 8270.7 | 7320.6 | 9068.4 | 8690.3 | 8183.1 | 9407.7 | 9137.4 | 8419.4 | 8314.9 | 9196.7 | 8203.1 | 8540.2 | 9247.1 | 8153.4 | 9343.7 | 8177.1 | 9118.9 | 8388.3 | 9156.1 | 7901.4 | 9259.9 | 8383.2 | 9147.1 | 8372.9 | 9223.8 | 8494.6 | 8176 | 9095.6 | 8348.9 | 8162.1 | 9119.4 | 9271.7 | 9103 | 8310.1 | 9215.2 | 8320.5 | 8905.7 | 8383.3 | 8879.6 | 7771.4 | 9037.8 | 8310.8 | 8347.9 | 8329.6 | 8321.7 | 7159.4 | 8129.3 | 7180.1 | 8278.4 | 8294.9 | 9509.2 | 8269 | 9532.5 | 8526 | 9432.7 | 8378 | 8535.2 | 8386.2 | 9320.7 | 9588.3 | 9523.3 | 9442 | 9489.3 | 9485.2 | 8610 | 9497 | 9499.2 | 9544.8 | 9568.4 | 9535.7 | 9572.9 | 8652.5 | 9514.3 | 8666.7 | 25.3155 | 24.7104 | 24.5 | 24.6907 | 24.5171 | 24.5135 | 0 | 34.9 | 0 | 0 | 34.8 | 34.9 | 3.2104 | 3.4371 | 3.3895 | 3.3661 | 3.3311 | 3.1974 | 6.131 | 6.384 | 6.167 | 6.112 | 6.776 | 6.0233 |  | 3.7888 |  | 3.8775 |  | 3.8181 |  | 0.83613 |  | 1.027 |  | 0.83741 |  | 4.6517 |  | 4.7043 |  | 4.6952 |  | 0.88351 |  | 1.0135 |  | 0.93646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 509486 | 903 | 497698 | 968 | 418280.5 | 1082.8 | 0 | 3.7888 | 0 | 3.8775 | 0 | 3.8181 | 0 | 4.6517 | 0 | 4.7043 | 0 | 4.6952 | 704000 | 2000 | 698000 | 2000 | 1395801 | 5133 | 1398000 | 1390668 | 10.55 | 3.8281 | 0.90019 | 4.6838 | 0.94448 | 23.52% | 20.16% | 24.7079 | 34.8667 | 3.3219 | 6.2656 | 1405651.2 | 1393800 | 1525799.2095 | 91.35% | 45 | 15225
2023-12-23 | 2024 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 335090.89 | 7:22 | 18:02 | 9591.6 | 10013.2 | 9881.6 | 9868.1 | 9930.6 | 10074.1 | 9987.7 | 10424.4 | 9935.5 | 9859.6 | 9809.1 | 9973.6 | 9934.5 | 9910.1 | 9918.1 | 10008.1 | 9927.5 | 10041.7 | 10006.3 | 10056.2 | 10010.2 | 10019 | 9831.6 | 9946.5 | 9792 | 8593.9 | 9782.6 | 9778.1 | 9990.8 | 9943 | 9776.6 | 10051.9 | 10079.9 | 10145.8 | 10016.2 | 9977.1 | 10184.8 | 10065.4 | 10111.9 | 9932.8 | 10929.7 | 9649 | 10778.7 | 9585.5 | 10252.7 | 11543.2 | 9502 | 10850.7 | 9174.7 | 9417.8 | 10069.5 | 9485.2 | 10450 | 9259.2 | 10383.4 | 9200.7 | 9203.2 | 10661.6 | 9203.6 | 10551.8 | 10434.2 | 9198 | 10187.2 | 9640.7 | 9828.8 | 9227.4 | 9781.8 | 10207.1 | 10538.8 | 9383.1 | 10371 | 9034.6 | 9973.7 | 9850 | 9151.6 | 10428.8 | 9057.2 | 10428.9 | 9110.6 | 10289.2 | 9344.8 | 10086.3 | 9541.1 | 10604.2 | 9379.2 | 10060.7 | 9292.9 | 8231.8 | 10229.7 | 9766.5 | 9146.2 | 10640 | 10256.7 | 9416.5 | 9313.9 | 10334.3 | 9146 | 9543 | 10402.6 | 9110 | 10542 | 9108.5 | 10240.3 | 9374 | 10378.2 | 8881 | 10451.2 | 9389.7 | 10313.8 | 9400.4 | 10437.3 | 9537.8 | 9152.6 | 10234.6 | 9335.5 | 9131.4 | 10264.4 | 10486.2 | 10244.8 | 9299.5 | 10394.3 | 9296.6 | 9978.5 | 9411.2 | 9991.5 | 8673 | 10127.3 | 9289.8 | 9440.3 | 9441 | 9320 | 8057.6 | 9258.5 | 8163.8 | 9298 | 9283.5 | 10802.4 | 9291.2 | 10833 | 9538.1 | 10666.3 | 9347.8 | 9524.6 | 9358.8 | 10421.7 | 10819.2 | 10666 | 10579.4 | 10733.6 | 10768.4 | 9566.3 | 10662.8 | 10689.5 | 10780.5 | 10837.9 | 10795.5 | 10825.4 | 9615.3 | 10744.7 | 9619.7 | 23.6869 | 23.2557 | 23.3793 | 23.2971 | 23.435 | 23.2891 | 0 | 35.2 | 0 | 0 | 35.2 | 35.3 | 2.5024 | 2.5602 | 2.5606 | 2.5486 | 2.5476 | 2.4694 | 5.76 | 5.302 | 5.388 | 5.341 | 5.558 | 5.896 |  | 4.0954 |  | 4.1925 |  | 4.0518 |  | 0.9037 |  | 1.1472 |  | 0.87123 |  | 5.309 |  | 5.3157 |  | 5.2885 |  | 0.95773 |  | 1.1155 |  | 0.97601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 510277 | 904 | 498483 | 970 | 419850.5 | 1087.8 | 0 | 4.0954 | 0 | 4.1925 | 0 | 4.0518 | 0 | 5.309 | 0 | 5.3157 | 0 | 5.2885 | 791000 | 1000 | 785000 | 2000 | 1570000 | 5000 | 1573000 | 1565000 | 10.6667 | 4.1132 | 0.97403 | 5.3044 | 1.0164 | 23.68% | 19.16% | 23.3905 | 35.2333 | 2.5315 | 5.5408 | 1580419.2 | 1568867 | 1725732.3737 | 90.91% | 27 | 0
2023-12-24 | 2024 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 335090.89 | 7:20 | 18:02 | 8759.4 | 9150.3 | 9071.4 | 9060.9 | 9120.4 | 9232.4 | 9143.1 | 9502.7 | 9066.1 | 9010.1 | 8943.8 | 9091.4 | 9060.7 | 9035.8 | 9103.6 | 9137 | 9072.1 | 9150.4 | 9128.3 | 9166.5 | 9150.1 | 9150.1 | 8970.5 | 9072.7 | 8926.1 | 7834.8 | 8933.2 | 8916.3 | 9118.9 | 9075.8 | 8923.5 | 9171.3 | 9193.1 | 9242.5 | 9175.1 | 9126.3 | 9277.7 | 9182.2 | 9247.1 | 9079.3 | 10020.1 | 8851.8 | 9872.1 | 8772.1 | 9380.7 | 10548.5 | 8701.1 | 9977.6 | 8370.4 | 8594.4 | 9181.1 | 8644.8 | 9519.5 | 8453.5 | 9465.5 | 8397.9 | 8391.8 | 9720.7 | 8395.1 | 9628.5 | 9524.1 | 8394.4 | 9280.5 | 8790.7 | 8966.9 | 8426.6 | 8934.2 | 9364.6 | 9629.1 | 8599.7 | 9472.2 | 8284 | 9121.5 | 9008.8 | 8372.2 | 9544.7 | 8256.2 | 9506.2 | 8341.1 | 9428.9 | 8641.8 | 9382.3 | 8781.6 | 9776.3 | 8619.8 | 9240.4 | 8514.5 | 7563.8 | 9343.8 | 8981.5 | 8386.5 | 9732.3 | 9399.3 | 8622.9 | 8541.5 | 9453 | 8387.7 | 8763.9 | 9540.8 | 8362.6 | 9675.7 | 8349.8 | 9390.1 | 8575.8 | 9230.4 | 7887.9 | 9562.6 | 8584.6 | 9450.6 | 8587.7 | 9545.4 | 8703.6 | 8409.3 | 9363 | 8531 | 8355.3 | 9399.7 | 9599.2 | 9379.8 | 8544.2 | 9514 | 8518.2 | 9129.6 | 8596.5 | 9116.7 | 7967.3 | 9288.3 | 8519.7 | 8603.7 | 8590.5 | 8524.4 | 7353.6 | 8425.2 | 7452 | 8475.3 | 8469.9 | 9896.9 | 8517.3 | 9929.1 | 8751.4 | 9769.9 | 8551.6 | 8714.5 | 8549.2 | 9578.9 | 9943 | 9798.6 | 9717.4 | 9838.9 | 9871.5 | 8783.7 | 9789.8 | 9822.6 | 9900.7 | 9982.8 | 9927.2 | 9962.9 | 8835.1 | 9899.2 | 8837.4 | 22.8654 | 22.6035 | 22.6722 | 22.6148 | 22.6515 | 22.7298 | 0 | 32.4 | 0 | 0 | 32.3 | 32.5 | 2.6346 | 2.708 | 2.7091 | 2.6867 | 2.7263 | 2.6431 | 4.463 | 4.57 | 4.583 | 4.903 | 5.288 | 5.051 |  | 3.7967 |  | 3.8786 |  | 3.7583 |  | 0.85604 |  | 1.0681 |  | 0.82777 |  | 4.8048 |  | 4.8218 |  | 4.7705 |  | 0.90642 |  | 1.0455 |  | 0.92619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 511001 | 906 | 499202 | 971 | 421287.7 | 1092.8 | 0 | 3.7967 | 0 | 3.8786 | 0 | 3.7583 | 0 | 4.8048 | 0 | 4.8218 | 0 | 4.7705 | 724000 | 2000 | 719000 | 1000 | 1437200 | 5000 | 1440000 | 1432200 | 10.7 | 3.8112 | 0.9173 | 4.799 | 0.95938 | 24.07% | 19.99% | 22.6895 | 32.4 | 2.6847 | 4.8097 | 1445783.3 | 1435134 | 1575488.2505 | 91.09% | 35 | 0
2023-12-25 | 2024 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 335090.89 | 7:23 | 18:02 | 8447.2 | 8828.2 | 8744.1 | 8733 | 8767.9 | 8908.5 | 8850.7 | 9195.5 | 8746.2 | 8721.5 | 8632.9 | 8777.5 | 8753.6 | 8730.3 | 8763.9 | 8824.3 | 8740.7 | 8821.9 | 8810.7 | 8845.9 | 8826.7 | 8821.6 | 8660.1 | 8762.5 | 8606.5 | 7562.8 | 8642.1 | 8610.5 | 8797.7 | 8751.3 | 8602 | 8835.3 | 8902.8 | 8955.5 | 8909.1 | 8852.6 | 8939.2 | 8847.5 | 8917.4 | 8756.1 | 9606.2 | 8494.9 | 9473.8 | 8422.7 | 9003.1 | 10117.8 | 8347.2 | 9573.8 | 8088 | 8298.7 | 8875.5 | 8357.5 | 9199.8 | 8168.9 | 9150.7 | 8127 | 8095.5 | 9369.4 | 8102.2 | 9281.9 | 9189.1 | 8106.8 | 8947.2 | 8484.5 | 8659 | 8122.2 | 8622.6 | 9027.9 | 9284.3 | 8303.1 | 9151.8 | 8012.2 | 8805.7 | 8719.2 | 8095.2 | 9235.3 | 8029.1 | 9226.1 | 8076.5 | 9130.2 | 8343.2 | 9059.5 | 8477.9 | 9426.1 | 8312.8 | 8916.5 | 8210.2 | 7169.6 | 9035.8 | 8672.1 | 8105.7 | 9386.9 | 9048.6 | 8292.2 | 8206.5 | 9123.5 | 8103.1 | 8444.2 | 9197 | 8063.5 | 9327.3 | 8050.6 | 9041.8 | 8261.5 | 8062.1 | 7831.5 | 9207 | 8264.7 | 9103.5 | 8271.7 | 9177.8 | 8390.2 | 8111.1 | 9045.5 | 8233.3 | 8069.1 | 9066.8 | 9258.6 | 9037.1 | 8244.9 | 9168.3 | 8215.3 | 8809.9 | 8287.8 | 8806.6 | 7676.1 | 8954.2 | 8220.8 | 8321.7 | 8312.1 | 8243.1 | 7114.9 | 8134.2 | 7188.2 | 8202.8 | 8203.7 | 9571.3 | 8247.7 | 9629.6 | 8472.8 | 9460.8 | 8284 | 8436.1 | 8276.2 | 9251.8 | 9594.6 | 9468.2 | 9403.8 | 9515.2 | 9546.8 | 8510 | 9473.5 | 9451.2 | 9529.1 | 9596.2 | 9556.3 | 9599.9 | 8525.8 | 9543.5 | 8531.6 | 22.6504 | 22.3533 | 22.3981 | 22.2677 | 22.3866 | 22.3658 | 0 | 32.3 | 0 | 0 | 32.3 | 32.2 | 2.4889 | 2.5019 | 2.4987 | 2.5295 | 2.4671 | 2.5028 | 4.708 | 4.907 | 4.81 | 4.597 | 5.297 | 4.845 |  | 3.5266 |  | 3.8167 |  | 3.4247 |  | 0.83617 |  | 1.0417 |  | 0.81224 |  | 4.5763 |  | 4.6693 |  | 4.6439 |  | 0.88605 |  | 1.0187 |  | 0.90621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 511699 | 908 | 499896 | 973 | 422674.3 | 1098 | 0 | 3.5266 | 0 | 3.8167 | 0 | 3.4247 | 0 | 4.5763 | 0 | 4.6693 | 0 | 4.6439 | 698000 | 2000 | 694000 | 2000 | 1386600 | 5200 | 1388000 | 1381400 | 10.65 | 3.5893 | 0.89669 | 4.6298 | 0.93698 | 24.98% | 20.24% | 22.4037 | 32.2667 | 2.4981 | 4.8607 | 1394573.1 | 1385334 | 1523929.1538 | 90.91% | 27 | 0
2023-12-26 | 2024 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 335090.89 | 7:23 | 18:03 | 8770.5 | 9168.5 | 9032.2 | 9008.1 | 9062.3 | 9212.4 | 9148.2 | 9539.9 | 9116.5 | 9071.9 | 8969.9 | 9128.7 | 9082.1 | 9062.6 | 9069.8 | 9144.6 | 9067 | 9173.6 | 9157.6 | 9153.6 | 9190.3 | 9177.2 | 9043.8 | 9140.5 | 8986.1 | 7854 | 8920.9 | 8970.8 | 9204.8 | 9146.7 | 8970.5 | 9236.9 | 9233.1 | 9291 | 9253.6 | 9197.4 | 9342.2 | 9229.7 | 9303.5 | 9134 | 10050.1 | 8877.5 | 9910.3 | 8810 | 9392.2 | 10556.4 | 8718.9 | 10007.6 | 8389.9 | 8612.2 | 9208.2 | 8667.7 | 9550 | 8470.4 | 9499 | 8431.4 | 8404.7 | 9733.5 | 8410.7 | 9645.1 | 9543 | 8412.4 | 9298.8 | 8807.6 | 8994.4 | 8452.6 | 8958.3 | 9392.5 | 9641.2 | 8627.8 | 9491.2 | 8305.9 | 9128.4 | 9026 | 8388.5 | 9551.6 | 8302.4 | 9560.8 | 8359.2 | 9448.6 | 8636 | 9376.3 | 8772 | 9785.3 | 8621 | 9261 | 8543 | 7461.9 | 9392.8 | 9005.7 | 8403.9 | 9739.9 | 9385.8 | 8613.3 | 8530 | 9458.6 | 8391.2 | 8772.6 | 9562.6 | 8379.6 | 9687.4 | 8359.6 | 9394.7 | 8584.2 | 9518.7 | 8127 | 9578.3 | 8599.2 | 9462.5 | 8609.8 | 9551.5 | 8740.1 | 8426.7 | 9403.8 | 8566.8 | 8383.3 | 9425 | 9644.5 | 9408.1 | 8592.5 | 9569.9 | 8569.6 | 9177.5 | 8634.4 | 9170.8 | 8003.1 | 9333.4 | 8570.9 | 8679 | 8665.8 | 8578.8 | 7414.7 | 8497 | 7493.8 | 8524.3 | 8527.6 | 9952.1 | 8572.9 | 10012.2 | 8811.1 | 9834.7 | 8603 | 8772.3 | 8602.3 | 9622.8 | 9981.6 | 9843.7 | 9766.1 | 9893.7 | 9930.4 | 8841.8 | 9853.7 | 9813.5 | 9904.8 | 9974.5 | 9948 | 9984.3 | 8857.8 | 9909.8 | 8860.1 | 23.8209 | 23.7971 | 23.6942 | 23.7505 | 23.9487 | 23.6307 | 0 | 35.9 | 0 | 0 | 36 | 35.7 | 1.7733 | 1.7561 | 1.7546 | 1.7358 | 1.7332 | 1.6642 | 4.131 | 4.426 | 3.703 | 4.519 | 4.748 | 3.524 |  | 3.6864 |  | 3.9791 |  | 3.564 |  | 0.87176 |  | 1.0907 |  | 0.83842 |  | 4.8289 |  | 4.8988 |  | 4.8685 |  | 0.92947 |  | 1.0616 |  | 0.94015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 512428 | 910 | 500618 | 975 | 424116.633 | 1103.2 | 0 | 3.6864 | 0 | 3.9791 | 0 | 3.564 | 0 | 4.8289 | 0 | 4.8988 | 0 | 4.8685 | 729000 | 2000 | 722000 | 2000 | 1442333 | 5200 | 1447000 | 1437133 | 10.6667 | 3.7432 | 0.93361 | 4.8654 | 0.97707 | 24.94% | 20.08% | 23.7737 | 35.8667 | 1.7362 | 4.1752 | 1450718 | 1441200 | 1583531.1274 | 91.01% | 37 | 0
2023-12-27 | 2024 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 335090.89 | 7:26 | 18:03 | 8501.1 | 8901 | 8824.3 | 8798.5 | 8851 | 8967.8 | 8916.5 | 9261 | 8838.5 | 8777.4 | 8698.8 | 8850.3 | 8817.4 | 8792.7 | 8828.9 | 8894.8 | 8814.3 | 8895.4 | 8881.1 | 8900.6 | 8894.8 | 8888.4 | 8720.7 | 8828.1 | 8678.3 | 7621 | 8676.4 | 8685.1 | 8879.3 | 8820.4 | 8663.4 | 8910.1 | 8935.7 | 8996.5 | 8944.3 | 8887.1 | 9028.5 | 8927.9 | 8996.3 | 8844.8 | 9772.4 | 8643.8 | 9634.4 | 8563 | 9139.2 | 10276.8 | 8479.3 | 9729.7 | 8142 | 8355.8 | 8940.5 | 8414 | 9275.9 | 8234 | 9220.7 | 8181.5 | 8153.4 | 9437.7 | 8157.8 | 9352.4 | 9244.4 | 8160.1 | 9002.5 | 8523.1 | 8709.8 | 8176.9 | 8666.8 | 9091.8 | 9328.6 | 8355.9 | 9189.8 | 8051.7 | 8843.1 | 8748.4 | 8113.6 | 9261.2 | 8038.2 | 9243.7 | 8081.9 | 9144.2 | 8365.5 | 9087.2 | 8503.2 | 9474 | 8349.7 | 8956.9 | 8251.7 | 7321.5 | 9088.9 | 8727.1 | 8148.6 | 9448.5 | 9120.6 | 8363.9 | 8274.5 | 9192 | 8139.7 | 8495.5 | 9253.6 | 8116.6 | 9419.9 | 8110.2 | 9137.4 | 8326.2 | 9256.2 | 7903.3 | 9311.3 | 8349.1 | 9204.3 | 8372.8 | 9299.4 | 8486.4 | 8157 | 9095.2 | 8301.7 | 8114.6 | 9134.9 | 9315 | 9116.6 | 8284.5 | 9243.4 | 8263.6 | 8902.1 | 8376.4 | 8907.2 | 7740.1 | 9020.2 | 8235.9 | 8327.9 | 8307.1 | 8268.7 | 7122.7 | 8131.3 | 7177.6 | 8112.1 | 8118.9 | 9501.8 | 8181.2 | 9555.8 | 8406.9 | 9381.4 | 8200.8 | 8353.9 | 8192.9 | 9172.1 | 9521.3 | 9385.1 | 9312.9 | 9436.7 | 9467.5 | 8445.8 | 9404.3 | 9374.1 | 9453.6 | 9528.7 | 9488.9 | 9525.7 | 8444.2 | 9455.1 | 8454.2 | 24.365 | 24.002 | 24.1784 | 23.8816 | 24.0279 | 23.9083 | 0 | 33.1 | 0 | 0 | 33 | 32.9 | 3.1863 | 3.1369 | 3.0782 | 3.1837 | 3.0086 | 2.9448 | 5.863 | 5.577 | 5.474 | 5.822 | 5.666 | 5.423 |  | 3.5197 |  | 3.8085 |  | 3.3673 |  | 0.83997 |  | 1.0556 |  | 0.78773 |  | 4.6043 |  | 4.6929 |  | 4.5805 |  | 0.89173 |  | 1.0312 |  | 0.88488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 513129 | 911 | 501314 | 977 | 425510.9 | 1108.2 | 0 | 3.5197 | 0 | 3.8085 | 0 | 3.3673 | 0 | 4.6043 | 0 | 4.6929 | 0 | 4.5805 | 701000 | 1000 | 696000 | 2000 | 1394267 | 5000 | 1394000 | 1389267 | 10.6167 | 3.5652 | 0.89444 | 4.6259 | 0.93593 | 25.09% | 20.23% | 24.0605 | 33 | 3.0897 | 5.6375 | 1402193.8 | 1393267 | 1518055.5085 | 91.78% | 40 | 410
2023-12-28 | 2024 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 335090.89 | 7:24 | 18:08 | 9954.6 | 10413.5 | 10319.5 | 10279.8 | 10362.6 | 10501.4 | 10439.1 | 10876 | 10343.9 | 10244.5 | 10188.3 | 10362.2 | 10318.6 | 10298.8 | 10309.1 | 10389.1 | 10308.4 | 10429.2 | 10416.4 | 10433.1 | 10420.3 | 10413.6 | 10217 | 10346.1 | 10171.2 | 8931.9 | 10156.8 | 10179.6 | 10406 | 10341.8 | 10155.4 | 10440.7 | 10482.1 | 10549.3 | 10456.5 | 10404.1 | 10582.1 | 10465.7 | 10543.4 | 10354.8 | 11402 | 10048.3 | 11236.3 | 9979.7 | 10659.9 | 11962.3 | 9914.8 | 11352.2 | 9533.6 | 9779.1 | 10464 | 9842.1 | 10852.6 | 9634.7 | 10784.9 | 9554 | 9545.8 | 11050 | 9547.5 | 10948.4 | 10825.7 | 9550 | 10569.7 | 10003.5 | 10205.8 | 9586.1 | 10166.6 | 10657.1 | 10935.2 | 9800.4 | 10774.8 | 9436.5 | 10352.3 | 10254.1 | 9512 | 10858 | 9424.8 | 10836 | 9467.6 | 10715.3 | 9820.4 | 10673.1 | 9998.6 | 11122.2 | 9809.4 | 10516.7 | 9671.7 | 8591.3 | 10648.1 | 10192.9 | 9537.5 | 11046.9 | 10645.8 | 9759.6 | 9643.3 | 10757.2 | 9541.6 | 9967.8 | 10839.4 | 9529.2 | 11021.1 | 9507.2 | 10674.5 | 9752.8 | 10822.7 | 9248 | 10897.5 | 9786.3 | 10752 | 9783.8 | 10842.7 | 9928.6 | 9592.9 | 10708.5 | 9752.1 | 9531.9 | 10710.8 | 10981.5 | 10691.6 | 9749.2 | 10870.5 | 9716.3 | 10412.7 | 9811.9 | 10424.9 | 9087.4 | 10582.7 | 9727.1 | 9829.1 | 9818 | 9740.2 | 8403.8 | 9592.1 | 8467.9 | 9611.1 | 9619.4 | 11297.3 | 9719.6 | 11380.1 | 10013.5 | 11171.8 | 9757.5 | 9944.2 | 9717.3 | 10939.6 | 11353.3 | 11155.9 | 11064.2 | 11231.8 | 11271.7 | 10059.7 | 11213.7 | 11134.5 | 11214.7 | 11320.7 | 11297.6 | 11349.5 | 10065.8 | 11236.8 | 10051.6 | 23.8843 | 23.1117 | 23.1201 | 22.9699 | 22.8649 | 22.7003 | 0 | 34.4 | 0 | 0 | 34.1 | 34 | 3.1633 | 3.2221 | 3.1381 | 3.2431 | 3.2792 | 3.199 | 5.913 | 5.769 | 5.459 | 5.885 | 5.46 | 5.596 |  | 4.0292 |  | 4.4003 |  | 3.9214 |  | 0.95928 |  | 1.1992 |  | 0.91877 |  | 5.419 |  | 5.543 |  | 5.4632 |  | 1.0149 |  | 1.1707 |  | 1.0306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 513952 | 913 | 502133 | 979 | 427146.2 | 1113.333 | 0 | 4.0292 | 0 | 4.4003 | 0 | 3.9214 | 0 | 5.419 | 0 | 5.543 | 0 | 5.4632 | 823000 | 2000 | 819000 | 2000 | 1635300 | 5133 | 1638000 | 1630167 | 10.7333 | 4.117 | 1.0258 | 5.4751 | 1.072 | 24.92% | 19.58% | 23.1085 | 34.1667 | 3.2075 | 5.6803 | 1646956.1 | 1634067 | 1788971.1806 | 91.34% | 38 | 1041
2023-12-29 | 2024 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 335090.89 | 7:24 | 18:07 | 9193.1 | 9618.4 | 9518.3 | 9473 | 9562.6 | 9686.1 | 9666.4 | 10060.2 | 9578.2 | 9460.1 | 9437.2 | 9600.5 | 9535.2 | 9530.5 | 9539.3 | 9600.9 | 9520 | 9622.6 | 9636.9 | 9659.8 | 9653.2 | 9641.5 | 9467.3 | 9584 | 9429.4 | 8282 | 9428.1 | 9433.9 | 9658.3 | 9587 | 9414.3 | 9680.3 | 9717.6 | 9778.4 | 9699 | 9645.6 | 9804.4 | 9698.6 | 9762.4 | 9610.9 | 10490.8 | 9282.4 | 10365.3 | 9224.4 | 9856.4 | 11059.8 | 9143.1 | 10450.6 | 8829 | 9062.4 | 9690.4 | 9129.4 | 10038.9 | 8923.9 | 9998.2 | 8860.5 | 8850.8 | 10248.4 | 8852.6 | 10148.9 | 10039.2 | 8857.5 | 9817.8 | 9292.4 | 9470.3 | 8895.3 | 9430.4 | 9898.9 | 10145.9 | 9101.9 | 9995.8 | 8766.9 | 9606.7 | 9522.5 | 8816.5 | 10072.3 | 8740.2 | 10038.1 | 8778 | 9926.6 | 9122 | 9911.4 | 9298.4 | 10329.5 | 9126.4 | 9790.8 | 8998 | 7991.5 | 9936.8 | 9500.4 | 8886.7 | 10302.6 | 9925.4 | 9099.5 | 8999.8 | 10028.1 | 8912.3 | 9293.7 | 10109.7 | 8878.4 | 10272.4 | 8868.5 | 9962.9 | 9103.2 | 10091.6 | 8629.9 | 10165.4 | 9130.2 | 10033.8 | 9130 | 10135.6 | 9268.6 | 8948.8 | 9957.7 | 9095.7 | 8878.1 | 9998.5 | 10206.4 | 9965.1 | 9067.5 | 10107 | 9040.6 | 9719.9 | 9149.3 | 9719.1 | 8454.8 | 9854 | 9042.3 | 9140.5 | 9141.2 | 9052.7 | 7813.8 | 8952.7 | 7905.8 | 8977.1 | 8975.8 | 10493.8 | 9037.9 | 10564 | 9299.6 | 10373.4 | 9061.7 | 9231.8 | 9061 | 10174.2 | 10548.6 | 10377.2 | 10294.8 | 10428.7 | 10464.3 | 9349.8 | 10419 | 10395.6 | 10463.4 | 10522.4 | 10501.1 | 10544.3 | 9368.7 | 10473.6 | 9360.9 | 23.4564 | 22.8287 | 22.9166 | 22.8733 | 22.8297 | 22.6972 | 0 | 33 | 0 | 0 | 33.1 | 33 | 3.2076 | 3.2641 | 3.1728 | 3.2253 | 3.2203 | 3.09 | 5.942 | 6.067 | 5.28 | 5.56 | 5.971 | 5.365 |  | 3.8035 |  | 4.1616 |  | 3.701 |  | 0.90839 |  | 1.1276 |  | 0.87835 |  | 5.0364 |  | 5.1997 |  | 5.0573 |  | 0.96224 |  | 1.1069 |  | 0.98446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 514714 | 915 | 502896 | 981 | 428665.8 | 1118.4 | 0 | 3.8035 | 0 | 4.1616 | 0 | 3.701 | 0 | 5.0364 | 0 | 5.1997 | 0 | 5.0573 | 762000 | 2000 | 763000 | 2000 | 1519600 | 5067 | 1521000 | 1514533 | 10.7167 | 3.8887 | 0.97144 | 5.0978 | 1.0179 | 24.98% | 19.97% | 22.9336 | 33.0333 | 3.1967 | 5.6975 | 1529402.6 | 1518200 | 1671302.4847 | 90.84% | 38 | 401
2023-12-30 | 2024 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 335090.89 | 7:21 | 18:06 | 9107.8 | 9530.5 | 9462.4 | 9406 | 9510.8 | 9611.1 | 9567.5 | 9927 | 9456.9 | 9345.1 | 9300.5 | 9460.6 | 9403.4 | 9386.5 | 9449.8 | 9502.1 | 9412.1 | 9494.6 | 9491.6 | 9519.8 | 9507.7 | 9488.5 | 9318.9 | 9428.7 | 9259 | 8132.6 | 9285.7 | 9272.7 | 9490.1 | 9426 | 9246.7 | 9517.3 | 9518.9 | 9581.8 | 9457 | 9407 | 9612.7 | 9511.8 | 9575.1 | 9434.3 | 10368.3 | 9163.4 | 10221.2 | 9089.5 | 9694.9 | 10913.3 | 8992.5 | 10332.4 | 8685.8 | 8910.8 | 9531.9 | 8961.9 | 9893.3 | 8781.6 | 9839 | 8720 | 8712.8 | 10096.4 | 8713.3 | 9976.9 | 9876.1 | 8716 | 9645.7 | 9131.5 | 9323.4 | 8747.7 | 9283 | 9745.4 | 10005.5 | 8964.2 | 9854 | 8640.8 | 9481 | 9385.7 | 8696.6 | 9927.1 | 8607.2 | 9918.1 | 8675.2 | 9811.2 | 8994.9 | 9770.8 | 9099 | 10155.2 | 8935.1 | 9584.2 | 8858.9 | 7842.5 | 9724 | 9348.9 | 8717 | 10108.1 | 9734.6 | 8909 | 8818 | 9809.4 | 8713.8 | 9096.2 | 9904.1 | 8675.2 | 10059 | 8678.2 | 9745.1 | 8906.1 | 9872.4 | 8436.9 | 9923.2 | 8903.9 | 9803.7 | 8907.9 | 9899.4 | 9026.4 | 8743.6 | 9715.5 | 8870.1 | 8667.2 | 9752.7 | 9955.3 | 9708 | 8851.2 | 9859.9 | 8828.4 | 9483.1 | 8921.6 | 9465.5 | 8264.6 | 9625.9 | 8832.7 | 8907.7 | 8890.2 | 8833.4 | 7621.6 | 8724 | 7715.4 | 8763.9 | 8770.7 | 10236.2 | 8817.2 | 10325.4 | 9073.6 | 10123.6 | 8840.9 | 9010.1 | 8862.5 | 9936.3 | 10311.5 | 10130.9 | 10053.3 | 10166.4 | 10209.8 | 9132.4 | 10180.8 | 10130.4 | 10214.5 | 10306.1 | 10267.4 | 10317.8 | 9155.7 | 10250.5 | 9132.9 | 17.7553 | 17.6992 | 17.5018 | 17.6765 | 17.8075 | 17.8622 | 0 | 26.9 | 0 | 0 | 27.1 | 26.9 | 3.661 | 3.6777 | 3.6871 | 3.6785 | 3.6444 | 3.5148 | 5.663 | 5.911 | 5.357 | 5.661 | 5.986 | 5.411 |  | 3.7196 |  | 4.0374 |  | 3.5586 |  | 0.91005 |  | 1.1086 |  | 0.88155 |  | 4.8552 |  | 5.054 |  | 4.8169 |  | 0.95927 |  | 1.0854 |  | 0.98403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 515466 | 917 | 503642 | 982 | 430156.967 | 1123.467 | 0 | 3.7196 | 0 | 4.0374 | 0 | 3.5586 | 0 | 4.8552 | 0 | 5.054 | 0 | 4.8169 | 752000 | 2000 | 746000 | 1000 | 1491167 | 5067 | 1495000 | 1486100 | 10.75 | 3.7719 | 0.96672 | 4.9087 | 1.0096 | 25.63% | 20.57% | 17.7171 | 26.9667 | 3.6439 | 5.6648 | 1500772.7 | 1489334 | 1646904.5621 | 90.43% | 36 | 0
2023-12-31 | 2024 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 335090.89 | 7:25 | 18:08 | 9836.2 | 10283.5 | 10222.3 | 10159.8 | 10266.6 | 10370.1 | 10297.7 | 10698.4 | 10208.7 | 10106.8 | 10055.5 | 10235.7 | 10160.6 | 10147.9 | 10181.5 | 10265.9 | 10173.6 | 10283.8 | 10271.3 | 10307.3 | 10275.3 | 10252.5 | 10063.6 | 10190.3 | 10019 | 8804.7 | 10056.6 | 10030.8 | 10244.2 | 10162.9 | 9997.2 | 10288.1 | 10299.5 | 10376.5 | 10232.1 | 10162.7 | 10393.3 | 10284.9 | 10363.2 | 10202 | 11225.5 | 9901.3 | 11060.8 | 9832.5 | 10463.9 | 11750.2 | 9727.7 | 11190.8 | 9387.7 | 9634 | 10293.4 | 9694.2 | 10681.7 | 9460.3 | 10627.6 | 9420.1 | 9422.6 | 10911.2 | 9404.8 | 10799.9 | 10691.8 | 9423.1 | 10441.4 | 9892.8 | 10077.9 | 9475.9 | 10054.2 | 10551.1 | 10816.9 | 9696.8 | 10655.1 | 9348.4 | 10259 | 10148.7 | 9405.5 | 10730.2 | 9312.5 | 10721.7 | 9363.1 | 10585.1 | 9750.9 | 10558.9 | 9882.4 | 10996.7 | 9680.4 | 10394.4 | 9592 | 8519.4 | 10538.6 | 10122.4 | 9451.5 | 10951.3 | 10523.3 | 9626.2 | 9518.2 | 10631.3 | 9441.6 | 9859.2 | 10722.3 | 9414.1 | 10889.5 | 9391.7 | 10549.7 | 9644.3 | 10692.9 | 9136.6 | 10766.2 | 9661.9 | 10625 | 9651.5 | 10714.1 | 9793.3 | 9482.7 | 10540.9 | 9609.9 | 9398.5 | 10577.9 | 10796 | 10532.3 | 9595 | 10685.7 | 9565.6 | 10279.5 | 9677.5 | 10274 | 8952.7 | 10420 | 9567.6 | 9662 | 9653.1 | 9561.5 | 8261 | 9449.1 | 8353.7 | 9480.1 | 9478.1 | 11069.4 | 9531.9 | 11150.8 | 9804 | 10959.7 | 9573.9 | 9752.8 | 9574.7 | 10731.4 | 11141.9 | 10951 | 10864.5 | 10999.4 | 11052 | 9868.8 | 10999.5 | 10941.1 | 11029.8 | 11136.7 | 11094 | 11153.7 | 9890.9 | 11061.3 | 9868.6 | 20.0359 | 19.8755 | 19.9833 | 19.7814 | 19.9011 | 19.8969 | 0 | 29.2 | 0 | 0 | 29 | 28.9 | 3.9236 | 3.8525 | 3.8215 | 4.0942 | 3.9347 | 3.865 | 7.202 | 6.815 | 7.438 | 6.765 | 7.01 | 7.497 |  | 3.8996 |  | 4.3142 |  | 3.8031 |  | 0.95973 |  | 1.1801 |  | 0.92232 |  | 5.2567 |  |  |  | 5.2177 |  | 1.0125 |  | 1.1532 |  | 1.0298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 516278 | 918 | 504450 | 984 | 431769.367 | 1128.6 | 0 | 3.8996 | 0 | 4.3142 | 0 | 3.8031 | 0 | 5.2567 | 0 | 0 | 0 | 5.2177 | 812000 | 1000 | 808000 | 2000 | 1612400 | 5133 | 1617000 | 1607267 | 10.7167 | 4.0056 | 1.0207 | 5.2372 | 1.0652 | 25.48% | 20.34% | 19.9123 | 29.0333 | 3.9152 | 7.1212 | 1623522 | 1610800 | 1738739.7051 | 92.64% | 37 | 206
2024-01-01 | 2024 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 335090.89 | 7:26 | 18:08 | 10098 | 10550.2 | 10483 | 10427.1 | 10541.4 | 10631.1 | 10537.5 | 10931.2 | 10454.1 | 10366.5 | 10312.7 | 10490.4 | 10421.2 | 10329.1 | 10451.3 | 10542.4 | 10435 | 10543.9 | 10537 | 10586.1 | 10543.5 | 10518.4 | 10329.8 | 10452.1 | 10279.4 | 9034.1 | 10299 | 10289.4 | 10514.5 | 10438.5 | 10246 | 10547.2 | 10577.7 | 10651.9 | 10380.1 | 10315.6 | 10662.5 | 10559.7 | 10652.6 | 10474.7 | 11426.4 | 10143.2 | 11256 | 10081.9 | 9846.4 | 11342.7 | 9979.4 | 11396.9 | 9644.3 | 9910.5 | 10578.5 | 9954.4 | 10945.4 | 9726.1 | 10914.5 | 9664.2 | 9683.5 | 11179.1 | 9670.7 | 11070.7 | 10964.1 | 9672.7 | 10719.3 | 10153.9 | 10341.5 | 9726.9 | 10321.4 | 10819.5 | 11076.8 | 9959 | 10938 | 9605 | 10538.6 | 10429.1 | 9669.9 | 11007.3 | 9573.5 | 11008.9 | 9631.3 | 10876.9 | 9995.4 | 10810.8 | 10139.1 | 11235.8 | 9920.2 | 10661.6 | 9808.1 | 8721 | 10554.4 | 9981.9 | 9673.6 | 11174.4 | 10278.4 | 9476.3 | 9775.9 | 10873.3 | 9644.1 | 10088.3 | 10950 | 9634.4 | 11117.5 | 9612.8 | 10803.7 | 9880.3 | 10942.9 | 9343 | 11022.9 | 9906.5 | 10876.2 | 9870.4 | 10947.2 | 10035.6 | 9659.8 | 10657.9 | 9837.6 | 9636.4 | 10814.7 | 11053.9 | 10799.2 | 9837.7 | 10949.3 | 9806.5 | 10526.6 | 9918.8 | 10458.6 | 9174.2 | 10028.3 | 9480.8 | 9900.1 | 9885.9 | 9803.8 | 8469.1 | 9706.8 | 8571.5 | 9719.8 | 9530.5 | 11327.4 | 9807.9 | 11409.9 | 10099.2 | 11210.3 | 9839.2 | 10037.7 | 9862.7 | 11055.7 | 11407.3 | 11237.2 | 11151.5 | 11275.3 | 11311.9 | 10170.4 | 11283.2 | 11232.1 | 11318.2 | 11387 | 11352.3 | 11427.7 | 10201.3 | 11179.6 | 10152.9 | 17.6753 | 17.6434 | 17.6428 | 17.5945 | 17.7029 | 17.7143 | 0 | 27.8 | 0 | 0 | 27.8 | 27.7 | 3.3658 | 3.3994 | 3.3532 | 3.4082 | 3.3714 | 3.2943 | 5.385 | 5.738 | 5.577 | 5.776 | 5.482 | 5.907 |  | 3.9869 |  | 4.3467 |  | 3.8627 |  | 0.96585 |  | 1.1995 |  | 0.92976 |  | 5.3151 |  | 5.5189 |  | 5.3331 |  | 1.0184 |  | 1.1637 |  | 1.0377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 517109 | 920 | 505274 | 986 | 433417.034 | 1133.733 | 0 | 3.9869 | 0 | 4.3467 | 0 | 3.8627 | 0 | 5.3151 | 0 | 5.5189 | 0 | 5.3331 | 831000 | 2000 | 824000 | 2000 | 1647667 | 5133 | 1651000 | 1642534 | 10.7 | 4.0654 | 1.0317 | 5.389 | 1.0733 | 25.38% | 19.92% | 17.6622 | 27.7667 | 3.3654 | 5.6442 | 1659606 | 1647000 | 1791219.6862 | 91.95% | 35 | 920
2024-01-02 | 2024 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 335090.89 | 7:25 | 18:08 | 10020.5 | 10470.7 | 10395.2 | 10333.9 | 10437.3 | 10558.4 | 10479.4 | 10864.8 | 10381.4 | 10259 | 10235.6 | 10425.5 | 10363 | 10324 | 10363.1 | 10468.9 | 10356.2 | 10477.6 | 10467.9 | 10512.3 | 10463 | 10441 | 10242.2 | 10374.9 | 10197.1 | 8961 | 10264.1 | 10224.6 | 10436 | 10350.3 | 10165.1 | 10462.2 | 10501.9 | 10570.8 | 10479.3 | 10406.6 | 10587 | 10476.2 | 10563.2 | 10397.6 | 11407.8 | 10061.9 | 11233.5 | 9993 | 10035.6 | 11572.7 | 9759.1 | 11371 | 9573.4 | 9842.6 | 10498 | 9869 | 10887.7 | 9666.2 | 10829.2 | 9563.7 | 9606.8 | 11118.2 | 9598.5 | 11007.6 | 10888.6 | 9602.3 | 10604 | 10040.4 | 10255.7 | 9634.9 | 10219.8 | 10702.5 | 11006.9 | 9846.2 | 10822.2 | 9491.9 | 10390.5 | 10228.5 | 9460.2 | 10758.5 | 9403.1 | 10869.2 | 9530.7 | 10776.4 | 9874 | 10682.8 | 9912.3 | 10832.7 | 9816.7 | 10535.4 | 9706.1 | 8631.6 | 10490.8 | 9839.5 | 9569.2 | 11103.7 | 10717.5 | 9824.1 | 9704.4 | 10791 | 9555.7 | 9975.8 | 10858.5 | 9527.8 | 11028.4 | 9512.6 | 10695 | 9794 | 10848 | 9274.3 | 10917.8 | 9794.3 | 10763.8 | 9782.5 | 10868.6 | 9933.2 | 9595.9 | 10691.8 | 9745.8 | 9536.5 | 10723.8 | 10965.5 | 10702.6 | 9744.6 | 10849.3 | 9699.2 | 10415.8 | 9815.6 | 10414.1 | 9082.4 | 10563.5 | 9711.6 | 9786.7 | 9777 | 9702.2 | 8372.9 | 9596 | 8493.4 | 9637.2 | 9641.8 | 11268.5 | 9700.2 | 11368 | 9978.5 | 11135.3 | 9733.2 | 9913.5 | 9752.4 | 10940.2 | 11350.7 | 11157 | 11065.9 | 11213.3 | 11251.8 | 10058 | 11217.8 | 11137.7 | 11245.8 | 11343.4 | 11300.3 | 11372 | 10079.3 | 11263.6 | 10066.8 | 18.8453 | 18.4975 | 18.6425 | 18.4725 | 18.6023 | 18.6051 | 0 | 28.8 | 0 | 0 | 28.7 | 28.5 | 3.544 | 3.5158 | 3.5046 | 3.6519 | 3.4384 | 3.5022 | 5.335 | 5.452 | 5.615 | 5.826 | 5.785 | 5.767 |  | 4.0079 |  | 4.4181 |  | 3.8241 |  | 0.95944 |  | 1.1854 |  | 0.9197 |  | 5.3062 |  | 5.4282 |  | 5.2854 |  | 1.0125 |  | 1.155 |  | 1.0272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 517933 | 921 | 506092 | 988 | 435052.6 | 1138.733 | 0 | 4.0079 | 0 | 4.4181 | 0 | 3.8241 | 0 | 5.3062 | 0 | 5.4282 | 0 | 5.2854 | 824000 | 1000 | 818000 | 2000 | 1635566 | 5000 | 1639000 | 1630566 | 10.7167 | 4.0834 | 1.0215 | 5.34 | 1.0649 | 25.02% | 19.94% | 18.6109 | 28.6667 | 3.5262 | 5.63 | 1648127.3 | 1634867 | 1770592.2828 | 92.33% | 33 | 1124
2024-01-03 | 2024 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 335090.89 | 7:26 | 18:09 | 5220.9 | 10659.6 | 10545.4 | 10474.5 | 10594.9 | 10729.5 | 10665.1 | 11073.4 | 8226.9 | 5183.5 | 10405.6 | 10597.3 | 10523 | 10506.1 | 10529.2 | 10636.4 | 10534.4 | 10650.3 | 10644.4 | 10681.3 | 10642.9 | 10615.3 | 10417.4 | 10552.8 | 10369.1 | 9111.8 | 10436.4 | 10398.7 | 10620.4 | 10547.8 | 10342 | 10639 | 10685.4 | 10743.9 | 10673.1 | 10587.3 | 10774.6 | 10665.7 | 10749 | 10568.4 | 11545.8 | 10206.9 | 11386 | 10133.1 | 10809.8 | 11982 | 10070 | 11519.7 | 9746.4 | 10020.1 | 10681.1 | 10042.4 | 11073.1 | 9805.2 | 11036.3 | 9752.5 | 9776.7 | 11300.8 | 9774.5 | 11194.6 | 11085 | 9777.9 | 10784.3 | 10205.8 | 10374.7 | 9731.8 | 10402.8 | 10878.1 | 11187.4 | 10010.2 | 11011.9 | 9646.3 | 10614.2 | 10472.1 | 9721.6 | 11069.9 | 9625 | 11093.6 | 9697.2 | 10961.4 | 10043.4 | 10850.2 | 10172.8 | 11300.1 | 9972 | 10699 | 9883.7 | 8767.5 | 10832.8 | 10422.8 | 9725.8 | 11270 | 10886.7 | 9977.4 | 9851.7 | 10986.3 | 9727.8 | 10146.2 | 11030.7 | 9684.7 | 11198.3 | 9663.9 | 10868.3 | 9945.1 | 11028.2 | 9424 | 11097.8 | 9957.4 | 10951.7 | 9949.6 | 11040.8 | 10099.7 | 9754.8 | 10870.5 | 9902.7 | 9695.6 | 10893.1 | 11125.7 | 10875.6 | 9890.7 | 11023.5 | 9851 | 10589.1 | 9978.4 | 10592.5 | 9225.8 | 10732.2 | 9864.4 | 9806 | 9952.1 | 9870.2 | 8519.1 | 6452.7 | 8602.8 | 9780.8 | 9786.3 | 11387.3 | 9840.7 | 11472.9 | 10126.1 | 11279.1 | 9893.9 | 10077 | 9883.6 | 11089 | 11468.1 | 11289.4 | 11204.1 | 11331.6 | 11370.2 | 10195 | 11333.5 | 11285.9 | 11374.1 | 11478.2 | 11435.7 | 11486.4 | 10227.2 | 11411.3 | 10204.3 | 18.5478 | 18.194 | 18.4516 | 18.1038 | 18.2814 | 18.2569 | 0 | 28.7 | 0 | 0 | 28.7 | 28.6 | 3.5131 | 3.5393 | 3.4391 | 3.5546 | 3.4582 | 3.408 | 5.804 | 5.749 | 6.016 | 6.246 | 5.461 | 5.566 |  | 4.0374 |  | 4.4557 |  | 3.8444 |  | 0.96748 |  | 1.2042 |  | 0.92444 |  | 5.3645 |  | 5.4884 |  | 5.3307 |  | 1.0234 |  | 1.1741 |  | 1.0345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 518760 | 923 | 506921 | 990 | 436700.967 | 1143.8 | 0 | 4.0374 | 0 | 4.4557 | 0 | 3.8444 | 0 | 5.3645 | 0 | 5.4884 | 0 | 5.3307 | 827000 | 2000 | 829000 | 2000 | 1648367 | 5067 | 1652000 | 1643300 | 10.7167 | 4.1125 | 1.032 | 5.3945 | 1.0773 | 25.1% | 19.97% | 18.3059 | 28.6667 | 3.4854 | 5.807 | 1660667.5 | 1647533 | 1790152.882 | 92.03% | 26 | 1825
2024-01-04 | 2024 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 335090.89 | 7:30 | 18:09 | 4927.9 | 9920.3 | 9847.8 | 9777.7 | 9921.2 | 10040.6 | 9964.4 | 10315.4 | 7790.4 | 8078.8 | 9757.4 | 9949.7 | 9869.7 | 9858.6 | 9843.6 | 9937.9 | 9864.4 | 9962.6 | 9939.2 | 9918.6 | 9959.3 | 9960.3 | 9739.6 | 9857.1 | 9732.6 | 8544.9 | 9781.9 | 9747.3 | 9940 | 9882.7 | 9714.6 | 9970.6 | 10002.5 | 10070.7 | 9612.3 | 9518.3 | 10072.7 | 9994 | 10074.6 | 9930.8 | 10774.8 | 9669.4 | 10646.5 | 9592.3 | 10177.1 | 11169.5 | 9458.6 | 10718.9 | 9133.7 | 9392 | 10011.2 | 9419.8 | 10335.5 | 9172.5 | 10316.8 | 9167.6 | 9189.7 | 10554.6 | 9173.5 | 10460.7 | 10349 | 9186.3 | 10088.7 | 9558.9 | 9789.6 | 9185.4 | 9760 | 10198.8 | 10445.3 | 9418.3 | 10338.5 | 9089.2 | 9946.5 | 9867 | 9132.7 | 10375.2 | 9054.5 | 10383.7 | 9124.1 | 10268.4 | 9447.6 | 10201.1 | 9570.5 | 10570.2 | 9392.4 | 10074.2 | 9263.6 | 8232.3 | 10101.4 | 9567.6 | 9143.7 | 10545.5 | 10204.2 | 9354 | 9237.6 | 10300.1 | 9160.3 | 9575.4 | 10339 | 9113.3 | 10491.2 | 9080.4 | 10201.5 | 9350.8 | 10294 | 8856 | 10371.4 | 9348.7 | 10267.3 | 9344.8 | 10358 | 9486.9 | 9217 | 10232.6 | 9297.9 | 9113 | 10236.8 | 10391.8 | 10211.8 | 9284.3 | 10342 | 9274.5 | 9958.6 | 9370.3 | 9963.7 | 8691.2 | 10117.5 | 9301.8 | 9366.4 | 9410.8 | 9316.6 | 8005.2 | 8989.2 | 8147.2 | 9271.6 | 9125.6 | 10690.9 | 9288.9 | 10811.6 | 9569.2 | 10591.4 | 9326.1 | 9500.5 | 9348.5 | 10364.7 | 10679.1 | 10546.9 | 10497.6 | 10648.5 | 10694.8 | 9657.9 | 10636.7 | 10554.7 | 10616.5 | 10686.6 | 10655.4 | 10699.6 | 9587.6 | 10618.4 | 9560.2 | 15.7333 | 15.4797 | 15.654 | 15.3052 | 15.4532 | 15.4942 | 0 | 26.3 | 0 | 0 | 26.3 | 26.1 | 3.4269 | 3.4265 | 3.3377 | 3.4438 | 3.2826 | 3.3448 | 5.392 | 5.399 | 5.566 | 6.032 | 5.421 | 5.052 |  | 4.0649 |  | 4.1706 |  | 4.0988 |  | 0.92303 |  | 1.1034 |  | 0.89532 |  | 5.2235 |  | 5.2031 |  | 5.1753 |  | 0.98022 |  | 1.0806 |  | 1.0013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 519538 | 925 | 507701 | 992 | 438251.8 | 1148.8 | 0 | 4.0649 | 0 | 4.1706 | 0 | 4.0988 | 0 | 5.2235 | 0 | 5.2031 | 0 | 5.1753 | 778000 | 2000 | 780000 | 2000 | 1550833 | 5000 | 1554000 | 1545833 | 10.65 | 4.1114 | 0.97392 | 5.2006 | 1.0207 | 23.69% | 19.63% | 15.5199 | 26.2333 | 3.377 | 5.477 | 1563002.5 | 1548933 | 1733081.8922 | 89.37% | 29 | 9470
2024-01-05 | 2024 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 335090.89 | 7:26 | 18:09 | 9371.7 | 10065.8 | 10015 | 9946.5 | 10080.9 | 10208.4 | 10110.5 | 10537.2 | 10046 | 9980.6 | 9905.6 | 10087.1 | 10012.9 | 9996.9 | 10004.4 | 10114 | 10009 | 10107.2 | 10128.3 | 10156.8 | 10123 | 10116.3 | 9891.7 | 10027.6 | 9853.2 | 8654.1 | 9929.8 | 9887.3 | 10086 | 10003.9 | 9802.6 | 10082.5 | 10133.3 | 10186.5 | 10051.2 | 9978.7 | 10226.5 | 10107.9 | 10179.1 | 10022.5 | 11025.4 | 9714.1 | 10842.8 | 9628.1 | 10280.7 | 11542.5 | 9580 | 10997.6 | 9278.5 | 9537 | 10170.5 | 9571.3 | 10545.7 | 9331.4 | 10502.2 | 9292.7 | 9294.9 | 10754.3 | 9307.1 | 10665.1 | 10553.9 | 9303.2 | 10275.7 | 9722.4 | 9898.5 | 9301.3 | 9878 | 10333.8 | 10644.6 | 9508.8 | 10471.6 | 9158 | 10107.6 | 9960.7 | 9263.4 | 10506.1 | 9154.1 | 10570.9 | 9233.9 | 10422.6 | 9514.4 | 10281.6 | 9645.5 | 10731.4 | 9474.5 | 10173.6 | 9305.3 | 8288 | 10297.8 | 9898.2 | 9214.4 | 10704.7 | 10333.2 | 9470.1 | 9366.5 | 10428 | 9214.9 | 9606.4 | 10466.1 | 9158.7 | 10629.1 | 9152.7 | 10288.3 | 9412.9 | 10430.7 | 8902.5 | 10487.5 | 9408.9 | 10357.8 | 9402.2 | 10436.4 | 9536.1 | 9221.8 | 10280.8 | 9348.4 | 9161.3 | 10302.6 | 10502.3 | 10275.5 | 9337.7 | 10409.1 | 9305.1 | 10008.8 | 9422 | 9976.6 | 8701.5 | 10143.5 | 9319.9 | 9415.7 | 9419 | 9323.2 | 8050.2 | 9244.8 | 8183 | 9315.2 | 9318.3 | 10875.3 | 9379.7 | 10958.3 | 9624.1 | 10755 | 9406.3 | 9585 | 9423.5 | 10545.1 | 10947.4 | 10768.2 | 10690.1 | 10818.5 | 10858.6 | 9695.5 | 10813.7 | 10700.2 | 10825.8 | 10926.5 | 10895.9 | 10968.7 | 9715.5 | 10865.8 | 9717.8 | 18.8655 | 18.498 | 18.5445 | 18.4043 | 18.4913 | 18.3696 | 0 | 29.8 | 0 | 0 | 29.7 | 29.5 | 2.7897 | 2.7889 | 2.698 | 2.8347 | 2.8018 | 2.6879 | 5.499 | 4.802 | 4.835 | 5.483 | 5.454 | 5.159 |  | 4.1253 |  | 4.2299 |  | 4.128 |  | 0.92704 |  | 1.14 |  | 0.88904 |  | 5.3392 |  | 5.3185 |  | 5.2843 |  | 0.98583 |  | 1.1131 |  | 0.99724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520336 | 926 | 508490 | 993 | 439832.368 | 1153.8 | 0 | 4.1253 | 0 | 4.2299 | 0 | 4.128 | 0 | 5.3392 | 0 | 5.3185 | 0 | 5.2843 | 798000 | 1000 | 789000 | 1000 | 1580568 | 5000 | 1585000 | 1575568 | 10.7167 | 4.1611 | 0.98535 | 5.314 | 1.0321 | 23.68% | 19.42% | 18.5289 | 29.6667 | 2.7668 | 5.2053 | 1592124.7 | 1579667 | 1752467.6355 | 90.14% | 32 | 755
2024-01-06 | 2024 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 335090.89 | 7:26 | 18:11 | 9784.4 | 10230.3 | 10147.4 | 10091.4 | 10194.2 | 10359.5 | 10301.8 | 10716.7 | 10217.3 | 10177.7 | 10064.3 | 10251.6 | 10169.6 | 10160.4 | 10140 | 10256.3 | 10147.7 | 10260.8 | 10278.8 | 10314.7 | 10270.4 | 10267.4 | 10041.5 | 10177.1 | 10014.6 | 8791.5 | 10074.7 | 10035.2 | 10247 | 10168.1 | 9978.7 | 10272.6 | 10330.4 | 10385 | 10157.4 | 10094.9 | 10417.2 | 10298.6 | 10374.7 | 10214.7 | 11164.9 | 9857.9 | 11007.7 | 9783.8 | 10441.1 | 11708.5 | 9706.6 | 11137.3 | 9420.2 | 9682.9 | 10327.7 | 9714.8 | 10708.8 | 9474.2 | 10666.5 | 9442.2 | 9451.4 | 10946.3 | 9457.9 | 10829.7 | 10724.4 | 9459.4 | 10443.4 | 9887.1 | 10114.9 | 9494.4 | 10072.5 | 10544.9 | 10861.8 | 9706.8 | 10680.3 | 9351.7 | 10298.1 | 10164.5 | 9445.2 | 10754.1 | 9336.4 | 10760.1 | 9402.1 | 10625.1 | 9708.6 | 10494.6 | 9843.5 | 10952.9 | 9664.5 | 10376.4 | 9579.1 | 8502.6 | 10519.2 | 10100.8 | 9406.1 | 10921.7 | 10530.5 | 9659.2 | 9549.8 | 10632.2 | 9423.1 | 9821.1 | 10678.9 | 9376.9 | 10831.6 | 9338.9 | 10488.6 | 9609.2 | 10645.2 | 9096 | 10709 | 9609.4 | 10576.2 | 9607.3 | 10670.8 | 9747.5 | 9451.6 | 10529.2 | 9578.3 | 9399.1 | 10543.5 | 10759.8 | 10517 | 9570 | 10652.8 | 9523.7 | 10228.5 | 9628.5 | 10237.1 | 8906.7 | 10371.9 | 9530.1 | 9648.9 | 9660.3 | 9539.2 | 8247 | 9454.5 | 8357.5 | 9510.4 | 9515.5 | 11054.4 | 9551.8 | 11147.5 | 9794.7 | 10970 | 9599.5 | 9781.1 | 9605.1 | 10734.3 | 11142.5 | 10946.4 | 10869.4 | 10998.3 | 11042.6 | 9869.3 | 11003.8 | 10910 | 11023.1 | 11130.1 | 11096.8 | 11148.9 | 9893.4 | 11074.1 | 9875.1 | 18.6065 | 18.2099 | 18.3598 | 18.0668 | 18.2065 | 18.1344 | 0 | 29 | 0 | 0 | 28.9 | 28.6 | 3.3079 | 3.3636 | 3.2511 | 3.3599 | 3.2364 | 3.2132 | 5.724 | 5.871 | 5.202 | 6.299 | 5.594 | 5.462 |  | 4.144 |  | 4.2885 |  | 4.1552 |  | 0.93851 |  | 1.1609 |  | 0.90033 |  | 5.3673 |  | 5.4617 |  | 5.2739 |  | 0.99499 |  | 1.13 |  | 1.0062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 521148 | 928 | 509296 | 995 | 441442.834 | 1158.733 | 0 | 4.144 | 0 | 4.2885 | 0 | 4.1552 | 0 | 5.3673 | 0 | 5.4617 | 0 | 5.2739 | 812000 | 2000 | 806000 | 2000 | 1610466 | 4933 | 1614000 | 1605533 | 10.75 | 4.1959 | 0.99991 | 5.3676 | 1.0437 | 23.83% | 19.45% | 18.264 | 28.8333 | 3.2887 | 5.692 | 1622228.9 | 1608734 | 1778095.406 | 90.48% | 35 | 603
2024-01-07 | 2024 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 335090.89 | 7:27 | 18:12 | 10117.2 | 10564 | 10455.2 | 10398.6 | 10514.8 | 10665.9 | 10589.8 | 10997.7 | 10539.1 | 10471.9 | 10375.6 | 10571 | 10473.4 | 10465.8 | 10456 | 10573.3 | 10464.3 | 10591.1 | 10583.8 | 10626.7 | 10589.2 | 10584.4 | 10359.6 | 10493.9 | 10323.1 | 9076.2 | 10383 | 10340 | 10553.3 | 10474.4 | 10286.1 | 10579.1 | 10630.8 | 10693.6 | 10570.2 | 10489.9 | 10724.1 | 10612 | 10687.5 | 10517.3 | 11418.1 | 10184.7 | 11278.4 | 10104 | 10783.2 | 11847.6 | 10041 | 11394.6 | 9721.7 | 9988.5 | 10653.9 | 10021.3 | 11007.7 | 9765.4 | 10975.3 | 9738.2 | 9747.1 | 11217.2 | 9760.2 | 11116.2 | 11027.6 | 9758.7 | 10761 | 10189.5 | 10418.3 | 9773.6 | 10380.6 | 10842.8 | 11128.9 | 9989.9 | 10964 | 9631 | 10608.2 | 10457.5 | 9691.8 | 10951.9 | 9608.9 | 11032.1 | 9685.9 | 10921.7 | 10009 | 10817.8 | 10150.5 | 11215 | 9956.2 | 10687.3 | 9863.7 | 8744.7 | 10826.7 | 10393.6 | 9699.6 | 11189.3 | 10850.6 | 9972.8 | 9860 | 10929.6 | 9689.8 | 10113.2 | 10958.5 | 9655.9 | 11110.1 | 9627.4 | 10813.2 | 9909 | 10940.5 | 9382.1 | 11010.4 | 9913.2 | 10880.9 | 9897.1 | 10946.3 | 10043.5 | 9730.6 | 10816.4 | 9859 | 9664.6 | 10846.2 | 11040.2 | 10817.8 | 9851.1 | 10942.1 | 9806.1 | 10546.8 | 9929.6 | 10539.1 | 9178.2 | 10687.3 | 9809.8 | 9918.1 | 9935.8 | 9797.6 | 8475.8 | 9740.3 | 8593.8 | 9795.8 | 9792.8 | 11290.6 | 9832.9 | 11378 | 10098.4 | 11215.2 | 9878.7 | 9984.9 | 9903.3 | 11014.2 | 11354.9 | 11200.8 | 11135 | 11244.9 | 11283.3 | 10159 | 11243.7 | 11193.9 | 11294.7 | 11352.8 | 11325.5 | 11373.2 | 10186.1 | 11305.7 | 10176.6 | 16.3847 | 16.104 | 16.2017 | 15.929 | 16.2334 | 16.2018 | 0 | 27.1 | 0 | 0 | 27.3 | 27 | 3.4959 | 3.4174 | 3.3915 | 3.4831 | 3.3275 | 3.306 | 6.052 | 5.939 | 6.478 | 6.573 | 6.321 | 5.837 |  | 4.2518 |  | 4.3836 |  | 4.255 |  | 0.96517 |  | 1.1956 |  | 0.92312 |  | 5.4994 |  | 5.5801 |  | 5.4054 |  | 1.0225 |  | 1.1621 |  | 1.0311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 521984 | 930 | 510124 | 997 | 443098.835 | 1163.733 | 0 | 4.2518 | 0 | 4.3836 | 0 | 4.255 | 0 | 5.4994 | 0 | 5.5801 | 0 | 5.4054 | 836000 | 2000 | 828000 | 2000 | 1656001 | 5000 | 1660000 | 1651001 | 10.75 | 4.2968 | 1.028 | 5.495 | 1.0719 | 23.92% | 19.51% | 16.1758 | 27.1333 | 3.4036 | 6.2 | 1668649.8 | 1654267 | 1832667.3831 | 90.27% | 35 | 5699
2024-01-08 | 2024 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 335090.89 | 7:40 | 18:13 | 8470.6 | 8807.9 | 8846.1 | 8735.7 | 8959.4 | 9074.4 | 8946.8 | 9238 | 8834.7 | 8855.4 | 8741 | 8858.7 | 8932.6 | 8848.8 | 9049.2 | 9089.9 | 9055 | 9152.3 | 9094.9 | 9107.8 | 9160.1 | 9135.4 | 8999.2 | 9103.8 | 8904.2 | 7791.5 | 8875.3 | 8897.7 | 9145 | 9106.3 | 8959.5 | 9166.9 | 9165 | 9196.3 | 9060.2 | 9009.3 | 9178.3 | 9178 | 9234.1 | 9133.9 | 9541 | 8676.2 | 9452.3 | 8587.1 | 9174.8 | 9998.3 | 8566.4 | 9521.3 | 8210.1 | 8420.5 | 9002.7 | 8468.3 | 9302.8 | 8362.6 | 9182 | 8278.7 | 8189.4 | 9327.6 | 8196.1 | 9236.3 | 9194 | 8196.5 | 9048.9 | 8664.6 | 8830.1 | 8350.4 | 8848.4 | 9205 | 9361.6 | 8570.6 | 9314.6 | 8290.3 | 8994.8 | 9000.5 | 8315.4 | 9363.3 | 8272.4 | 9339.3 | 8328.6 | 9307.4 | 8604.7 | 9241.3 | 8737 | 9495.7 | 8560.5 | 9144.8 | 8449.8 | 7506.7 | 9177.4 | 8895.5 | 8221.1 | 9370.8 | 9152 | 8508.6 | 8420.1 | 9201.7 | 8278.9 | 8619.2 | 9237.7 | 8216 | 9398.4 | 8215 | 9196.2 | 8468.3 | 9305.7 | 8029.9 | 9366.6 | 8470.6 | 9328.4 | 8537.3 | 9405.4 | 8641.6 | 8289.4 | 9144.3 | 8414.4 | 8245.1 | 9193.1 | 9328.1 | 9155 | 8413.4 | 9248.2 | 8372.8 | 9010.3 | 8509.1 | 9014.5 | 7852.1 | 9096.7 | 8384.7 | 8400 | 8491.7 | 8399.1 | 7241.9 | 8373.9 | 7451.2 | 8476.6 | 8479.4 | 9616.2 | 8505.5 | 9744 | 8730.9 | 9556.3 | 8547.8 | 8638.3 | 8597.5 | 9476.4 | 9761.2 | 9658.3 | 9590.7 | 9632.7 | 9634.2 | 8893 | 9696.8 | 9605.9 | 9654 | 9697.1 | 9668.1 | 9711.2 | 8856 | 9690.4 | 8853.4 | 14.1104 | 14.0589 | 13.8316 | 13.9725 | 14.0799 | 14.1347 | 0 | 24.5 | 0 | 0 | 24.4 | 24.4 | 3.1278 | 3.2271 | 3.1667 | 3.2997 | 3.1911 | 3.1807 | 5.287 | 5.123 | 4.901 | 5.137 | 5.048 | 4.876 |  | 3.8252 |  | 3.849 |  | 3.8804 |  | 0.86331 |  | 0.95086 |  | 0.85296 |  | 4.7495 |  | 4.6595 |  | 4.6616 |  | 0.90617 |  | 0.92975 |  | 0.94021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 522695 | 931 | 510832 | 999 | 444511.5 | 1168.933 | 0 | 3.8252 | 0 | 3.849 | 0 | 3.8804 | 0 | 4.7495 | 0 | 4.6595 | 0 | 4.6616 | 711000 | 1000 | 708000 | 2000 | 1412665 | 5200 | 1416000 | 1407465 | 10.55 | 3.8515 | 0.88904 | 4.6902 | 0.92538 | 23.08% | 19.73% | 14.0314 | 24.4333 | 3.1988 | 5.062 | 1423994.2 | 1411133 | 1570518.6781 | 89.85% | 33 | 50095
2024-01-09 | 2024 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 335090.89 | 7:41 | 18:14 | 9491.1 | 9916.4 | 9819.5 | 9715.7 | 9889.1 | 10005.5 | 10005.2 | 10226.7 | 9836.5 | 9700.6 | 9871.4 | 9944.5 | 9787 | 9899.7 | 9739 | 9826.2 | 9703.4 | 9782.5 | 9778.8 | 9845.6 | 9837.6 | 9788.6 | 9827.4 | 9855.2 | 9652.9 | 8585.4 | 9667.6 | 9627.2 | 9909.1 | 9949.2 | 9867.5 | 9981.1 | 10248 | 10228.8 | 10022.9 | 10053.6 | 10069.3 | 10061.6 | 10117.6 | 10028.6 | 10509.4 | 9689.8 | 10405.1 | 9596.9 | 10165.7 | 10940.7 | 9609.5 | 10490.2 | 9278.3 | 9553.1 | 9912.5 | 9496 | 10109.4 | 9237.6 | 10127 | 9223 | 9333.7 | 10352 | 9385.1 | 10318.5 | 10200.3 | 9331.9 | 9978.6 | 9582.6 | 9840.2 | 9377.8 | 9819.4 | 10116.6 | 10264.7 | 9502.4 | 10159.9 | 9150 | 9902.8 | 9769 | 9246.4 | 10085.5 | 9095.1 | 10131.7 | 9163.6 | 10025.5 | 9499.9 | 10000.4 | 9617.9 | 10347.2 | 9547.2 | 10076.5 | 9496.4 | 8450.1 | 10125.4 | 9886.2 | 9235.6 | 10258.8 | 10033.2 | 9494.2 | 9439.3 | 10117.5 | 9324.9 | 9641.9 | 10282.5 | 9329.8 | 10392.6 | 9346 | 10206 | 9607.8 | 10294.1 | 9087.3 | 10370.3 | 9586 | 10337.1 | 9626.8 | 10396.4 | 9755 | 9394.7 | 10251.9 | 9575.8 | 9402.4 | 10255.7 | 10389.9 | 10233.7 | 9552.1 | 10313.4 | 9520.7 | 10071.7 | 9643.5 | 10110.1 | 8957.4 | 10187.3 | 9543.9 | 9584.7 | 9620.9 | 9559 | 8242.6 | 9440.3 | 8329.4 | 9429.9 | 9514.8 | 10505.6 | 9538.9 | 10535.1 | 9752.9 | 10499.1 | 9609.2 | 9697.5 | 9645.9 | 10091.3 | 10287 | 10204.5 | 10150.1 | 10301.8 | 10397.4 | 9659 | 10265.2 | 10304.6 | 10345.4 | 10402.3 | 10371.7 | 10375.5 | 9614.2 | 10292.4 | 9586.4 | 14.0164 | 13.9427 | 13.9158 | 13.9271 | 14.0405 | 13.9911 | 0 | 23.8 | 0 | 0 | 24.2 | 23.3 | 4.1163 | 4.1654 | 4.1302 | 4.2235 | 4.1645 | 4.2019 | 7.263 | 7.013 | 7.245 | 6.902 | 7.909 | 7.7567 |  | 4.1179 |  | 4.2495 |  | 4.1168 |  | 0.92796 |  | 1.0813 |  | 0.90692 |  | 5.1854 |  | 5.2131 |  | 5.0088 |  | 0.9778 |  | 1.0532 |  | 1.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 523480 | 933 | 511615 | 1001 | 446071.635 | 1174 | 0 | 4.1179 | 0 | 4.2495 | 0 | 4.1168 | 0 | 5.1854 | 0 | 5.2131 | 0 | 5.0088 | 785000 | 2000 | 783000 | 2000 | 1560135 | 5067 | 1564000 | 1555068 | 10.55 | 4.1614 | 0.97205 | 5.1357 | 1.0109 | 23.36% | 19.68% | 13.9723 | 23.7667 | 4.167 | 7.3481 | 1573410.2 | 1558667 | 1726576.5768 | 90.27% | 37 | 33354
2024-01-10 | 2024 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 335090.89 | 7:26 | 18:14 | 10133.9 | 10609.7 | 10424.6 | 10383.5 | 10476.2 | 10634.2 | 10570.2 | 10948.2 | 10534.5 | 10516.1 | 10366.8 | 10559.7 | 10467 | 10467.9 | 10451.3 | 10560.1 | 10451.9 | 10550.4 | 10561.3 | 10618.7 | 10559.5 | 10562.8 | 10340.8 | 10466.4 | 10325.5 | 9087.6 | 10358.1 | 10322.2 | 10529 | 10478.7 | 10354 | 10567.5 | 10630.7 | 10709.5 | 10617.7 | 10557.9 | 10684.6 | 10584.7 | 10649.1 | 10505 | 11375.8 | 10186.1 | 11217.3 | 10084.9 | 10792.5 | 11864.8 | 10035 | 11333 | 9712 | 9967.4 | 10630.5 | 9998.3 | 10967.1 | 9760.8 | 10920.1 | 9722.4 | 9719.3 | 11152.7 | 9741 | 11060.5 | 10977.4 | 9742.1 | 10719.8 | 10168.5 | 10386 | 9751.6 | 10354.2 | 10788.6 | 11069.9 | 9961.2 | 10913.9 | 9600.3 | 10572 | 10444.4 | 9714.5 | 10976.8 | 9613.3 | 11009.8 | 9684.1 | 10895.5 | 9979.1 | 10770.3 | 10136 | 11147 | 9932.9 | 10649.3 | 9856.5 | 8736.1 | 10844.9 | 10376.8 | 9688.6 | 11163.4 | 10811.8 | 9958.8 | 9842.2 | 10908.1 | 9717.6 | 10108.9 | 10926.2 | 9638.8 | 11056.6 | 9617.4 | 10768.9 | 9910.2 | 10889.7 | 9370.4 | 10963.1 | 9883.7 | 10846.5 | 9894.5 | 10922.2 | 10034.9 | 9739.5 | 10797.8 | 9873.5 | 9677.9 | 10812.2 | 11000.5 | 10787.9 | 9850.9 | 10904.8 | 9796.9 | 10535.9 | 9933.4 | 10551.3 | 9178.8 | 10669.5 | 9805.8 | 9949.4 | 9977.5 | 9832.1 | 8501.3 | 9796.3 | 8658.8 | 9846.3 | 9841.3 | 11235.5 | 9829.1 | 11315.6 | 10077.6 | 11158.3 | 9883.4 | 9994.8 | 9941 | 10973.2 | 11301.3 | 11158.1 | 11088.3 | 11186.4 | 11219.1 | 10143.8 | 11194.4 | 11205 | 11282.2 | 11350.2 | 11306.1 | 11348.5 | 10208.9 | 11272.2 | 10200.8 | 17.3896 | 17.2229 | 17.2995 | 17.1053 | 17.2571 | 17.1556 | 0 | 27.1 | 0 | 0 | 27.1 | 26.5 | 3.4726 | 3.3284 | 3.393 | 3.4478 | 3.3139 | 3.354 | 6.242 | 5.838 | 6.347 | 5.661 | 5.772 | 6.184 |  | 4.25 |  | 4.3646 |  | 4.2561 |  | 0.96541 |  | 1.1881 |  | 0.93059 |  | 5.2693 |  | 5.3138 |  | 5.3272 |  | 1.0187 |  | 1.1444 |  | 1.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 524314 | 935 | 512442 | 1003 | 447725.302 | 1179 | 0 | 4.25 | 0 | 4.3646 | 0 | 4.2561 | 0 | 5.2693 | 0 | 5.3138 | 0 | 5.3272 | 834000 | 2000 | 827000 | 2000 | 1653667 | 5000 | 1657000 | 1648667 | 10.8 | 4.2902 | 1.028 | 5.3034 | 1.0644 | 23.96% | 20.07% | 17.2383 | 26.9 | 3.3849 | 6.0073 | 1666307.7 | 1651666 | 1766781.0217 | 93.48% | 35 | 2770
2024-01-11 | 2024 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 335090.89 | 7:26 | 18:16 | 10888.5 | 11283.7 | 11101.1 | 11070.9 | 11154.8 | 11303.2 | 11267.3 | 11564.9 | 11204.8 | 11166.9 | 11076.3 | 11233.1 | 11175 | 11156.6 | 11134.1 | 11247.3 | 11137.3 | 11236.8 | 11239.8 | 11317.8 | 11238 | 11259.2 | 11078 | 11181.2 | 11053.8 | 9862.5 | 11094.7 | 11062.6 | 11218.3 | 11152.9 | 11064.4 | 11234.5 | 11505.6 | 11571.9 | 11494 | 11443.7 | 11355.3 | 11267.5 | 11308.5 | 11177.6 | 11899.9 | 10914.8 | 11752.4 | 10854.3 | 11416.8 | 12358.4 | 10791.9 | 11857.7 | 10531.4 | 10787.5 | 11316.5 | 10806.8 | 11598.2 | 10581.4 | 11550 | 10525 | 10546.6 | 11759.9 | 10558.3 | 11684.2 | 11611.1 | 10557.9 | 11397.1 | 10952.9 | 11112.8 | 10565 | 11107.3 | 11441.7 | 11669.8 | 10769.7 | 11561.9 | 10416.2 | 11259.1 | 11176.8 | 10536.1 | 11594.3 | 10427.4 | 11623.6 | 10503.1 | 11524.9 | 10783.8 | 11428 | 10905.2 | 11747.8 | 10728.9 | 11316.1 | 10631.9 | 9456.9 | 11453.5 | 11053.6 | 10500.2 | 11747 | 11438.7 | 10743.3 | 10621.5 | 11503.1 | 10507.9 | 10857.3 | 11512.5 | 10421.9 | 11647.1 | 10408.1 | 11422.4 | 10704.2 | 11498.5 | 10145.1 | 11577.1 | 10681.8 | 11490.1 | 10686 | 11547.5 | 10828.8 | 10525.6 | 11427.3 | 10655.5 | 10474.2 | 11418.4 | 11598 | 11397.4 | 10634.9 | 11508.2 | 10594.7 | 11202.8 | 10728.3 | 11224.8 | 9922.3 | 11322 | 10604.1 | 10732.6 | 10735.4 | 10623.6 | 9189.7 | 10578.9 | 9368.3 | 10576.4 | 10583.2 | 11792.9 | 10615.1 | 11856.4 | 10836.1 | 11706.3 | 10650.1 | 10740.7 | 10679.8 | 11587.4 | 11861.9 | 11750.2 | 11674 | 11772.8 | 11795.6 | 10905.3 | 11765.4 | 11752.5 | 11815.6 | 11870 | 11845.3 | 11887.4 | 10949.7 | 11831.7 | 10948.1 | 19.8811 | 19.4492 | 19.4804 | 19.2337 | 19.3126 | 19.1631 | 0 | 31.8 | 0 | 0 | 31.8 | 31.7 | 2.5966 | 2.6474 | 2.7297 | 2.6756 | 2.6063 | 2.5371 | 4.92 | 5.425 | 5.456 | 5.272 | 5.547 | 5.305 |  | 4.6094 |  | 4.7535 |  | 4.6224 |  | 1.0404 |  | 1.2856 |  | 1.001 |  | 5.7532 |  | 5.8496 |  | 5.7226 |  | 0.21788 |  | 0.23539 |  | 0.2551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 525205 | 936 | 513323 | 1004 | 449489.4 | 1184 | 0 | 4.6094 | 0 | 4.7535 | 0 | 4.6224 | 0 | 5.7532 | 0 | 5.8496 | 0 | 5.7226 | 891000 | 1000 | 881000 | 1000 | 1764098 | 5000 | 1770000 | 1759098 | 10.8333 | 4.6618 | 1.109 | 5.7751 | 0.23613 | 23.79% | 4.089% | 19.42 | 31.7667 | 2.6321 | 5.3208 | 1777997.8 | 1763533 | 1895455.1944 | 93.04% | 34 | 0
2024-01-12 | 2024 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 335090.89 | 7:25 | 18:21 | 10607.4 | 11091.6 | 10890.5 | 10850.7 | 10939.7 | 11124.2 | 11066.8 | 11455 | 11022.2 | 10969.4 | 10861.7 | 11052.2 | 10957.5 | 10953.1 | 10936 | 11051.3 | 10948.3 | 11055.1 | 11061.1 | 11122 | 11054.6 | 11066.1 | 10848.2 | 10977.4 | 10819.3 | 9522 | 10858.1 | 10816.5 | 11018.7 | 10950.8 | 10839.7 | 11050.8 | 11146.8 | 11224.1 | 11135.6 | 11075.8 | 11184.6 | 11076.6 | 11133.6 | 10973.8 | 11836.8 | 10659.3 | 11676 | 10571.5 | 11246.4 | 12303.1 | 10506.1 | 11792.3 | 10171.3 | 10442.5 | 11120.4 | 10477.4 | 11444 | 10230.6 | 11398.8 | 10169.7 | 10181.6 | 11635.3 | 10197.1 | 11544.6 | 11453.2 | 10196.1 | 11212.9 | 10664.9 | 10866.9 | 10205.2 | 10834.1 | 11266.6 | 11535.2 | 10436.4 | 11389.7 | 10053 | 11052.1 | 10932.2 | 10174.1 | 11443.2 | 10066.2 | 11479.7 | 10136.7 | 11369.2 | 10453.9 | 11238.7 | 10606.1 | 11617.3 | 10403 | 11114.5 | 10308.3 | 9130.9 | 11279.2 | 10817.6 | 10134.8 | 11621.2 | 11270.1 | 10396.5 | 10271.1 | 11368.1 | 10139.3 | 10545.9 | 11372.1 | 10068.8 | 11512.7 | 10043.6 | 11240.5 | 10341.9 | 11345.8 | 9786 | 11418.7 | 10329.5 | 11303.6 | 10340 | 11353 | 10468.9 | 10153.5 | 11243.5 | 10312.6 | 10107.4 | 11251.5 | 11437.9 | 11233.2 | 10257.2 | 11347.5 | 10220.4 | 10988 | 10362.1 | 11000.1 | 9558.5 | 11105.9 | 10218.8 | 10374.6 | 10399.3 | 10247.3 | 8858.2 | 10209.2 | 9023 | 10248.5 | 10264.7 | 11696.7 | 10290.9 | 11772.6 | 10578.4 | 11608.5 | 10358.2 | 10466.9 | 10372 | 11462.5 | 11785.6 | 11640 | 11570.4 | 11674.6 | 11700.3 | 10672.7 | 11675.7 | 11661.8 | 11744.1 | 11799.7 | 11767.9 | 11809.1 | 10708.8 | 11726.2 | 10705.9 | 22.0991 | 21.7746 | 21.8358 | 21.7116 | 21.7786 | 21.6742 | 0 | 34.8 | 0 | 0 | 34.8 | 34.8 | 2.1828 | 2.1555 | 2.1512 | 2.2026 | 2.217 | 2.3003 | 4.018 | 4.307 | 4.308 | 4.433 | 4.542 | 5.4567 |  | 4.3901 |  | 4.5419 |  | 4.6218 |  | 1.0633 |  | 1.2719 |  | 0.99145 |  | 5.9198 |  | 5.9429 |  | 5.8836 |  | 0.24695 |  | 0.22541 |  | 0.24403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 526077 | 938 | 514186 | 1006 | 451216.6 | 1189 | 0 | 4.3901 | 0 | 4.5419 | 0 | 4.6218 | 0 | 5.9198 | 0 | 5.9429 | 0 | 5.8836 | 872000 | 2000 | 863000 | 2000 | 1727200 | 5000 | 1731000 | 1722200 | 10.9333 | 4.5179 | 1.1089 | 5.9154 | 0.2388 | 24.54% | 4.037% | 21.8123 | 34.8 | 2.2016 | 4.5108 | 1740475.3 | 1726400 | 1917083.1267 | 90.05% | 43 | 566
2024-01-13 | 2024 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 335090.89 | 7:21 | 18:17 | 9472.3 | 9910.3 | 9727.6 | 9681.7 | 9786.6 | 9926.1 | 9877.8 | 10287 | 9860.2 | 9807.4 | 9714.3 | 9895.2 | 9805.6 | 9804.8 | 9781.1 | 9885.1 | 9777.9 | 9880.9 | 9911.6 | 9953.3 | 9912.1 | 9909.5 | 9719.9 | 9832.6 | 9686.3 | 8537.2 | 9713.1 | 9676.8 | 9875.6 | 9820.1 | 9710 | 9916.2 | 9961.9 | 10017.3 | 9827.6 | 9771.9 | 10026.4 | 9918.1 | 9978.3 | 9847 | 10697.4 | 9545.5 | 10550.3 | 9475.9 | 10106 | 11221.4 | 9406 | 10652 | 9131.1 | 9371.7 | 9965.2 | 9407.2 | 10312.4 | 9170.8 | 10256.7 | 9142.2 | 9138.5 | 10495.3 | 9156.4 | 10397.9 | 10305.8 | 9148.9 | 10052.6 | 9529.6 | 9750.4 | 9171.8 | 9711.8 | 10150.2 | 10412.3 | 9375.4 | 10258.5 | 9034.3 | 9921.6 | 9802.5 | 9129.3 | 10317.1 | 9026.3 | 10346.2 | 9098.8 | 10218.5 | 9378.3 | 10119.2 | 9521.9 | 10508.5 | 9342.1 | 9996.5 | 9283.2 | 8224.9 | 10150 | 9742.9 | 9099.5 | 10498.6 | 10138.1 | 9341.9 | 9248 | 10246.7 | 9142.8 | 9508.5 | 10306.8 | 9084.4 | 10433 | 9053.4 | 10157 | 9338.6 | 10272.3 | 8838.4 | 10343.4 | 9326.5 | 10224.2 | 9322.8 | 10169.5 | 9433.7 | 9149.8 | 10152.2 | 9303.8 | 9113.3 | 10186.1 | 10370.6 | 10159.7 | 9280.2 | 10284.1 | 9232.6 | 9927 | 9357 | 9923.4 | 8644 | 10046.4 | 9244.2 | 9358 | 9366.5 | 9257.5 | 8009.6 | 9209.5 | 8130.2 | 9229.4 | 9219.4 | 10128.3 | 8589 | 10719 | 9496.7 | 10537.4 | 9284.4 | 9391.7 | 9320.2 | 10358.3 | 10715 | 10550.8 | 10485 | 10588.1 | 10630.1 | 9569.4 | 10591.8 | 10564.1 | 10643.6 | 10702.1 | 10680.1 | 10728.3 | 9593.3 | 10632.4 | 9591.6 | 15.7899 | 16.3566 | 16.4383 | 16.06 | 16.4654 | 16.2829 | 0 | 18.63 | 0 | 0 | 18.23 | 17.96 | 2.5883 | 2.5894 | 2.501 | 2.6061 | 2.4599 | 2.3928 | 5.561 | 5.217 | 5.84 | 6.081 | 5.418 | 5.3517 |  | 4.0929 |  | 4.1923 |  | 4.2621 |  | 0.97431 |  | 1.2037 |  | 0.94456 |  | 5.2784 |  | 5.292 |  | 5.2364 |  | 0.29946 |  | 0.27692 |  | 0.29189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 526861 | 940 | 514964 | 1008 | 452772.035 | 1193.867 | 0 | 4.0929 | 0 | 4.1923 | 0 | 4.2621 | 0 | 5.2784 | 0 | 5.292 | 0 | 5.2364 | 784000 | 2000 | 778000 | 2000 | 1555435 | 4867 | 1558000 | 1550568 | 10.9333 | 4.1824 | 1.0408 | 5.2689 | 0.28942 | 24.89% | 5.493% | 16.2322 | 18.2733 | 2.5229 | 5.5781 | 1564807.3 | 1554334 | 1724245.4286 | 90.15% | 75 | 60841
2024-01-14 | 2024 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 335090.89 | 7:25 | 18:26 | 9927.4 | 10402.1 | 10244.1 | 10192.1 | 10294.9 | 10445.7 | 10398.6 | 10760.2 | 10346.3 | 10297.5 | 10181.1 | 10368.9 | 10284.1 | 10279.1 | 10258.3 | 10371.7 | 10244 | 10347.5 | 10385.7 | 10437.7 | 10372 | 10381.5 | 10153.2 | 10278.8 | 10138.6 | 8921 | 10188.1 | 10139.2 | 10340.4 | 10265.6 | 10161 | 10381.1 | 10430.4 | 10503.7 | 10432.6 | 10362.6 | 10495.9 | 10380.2 | 10453.8 | 10306.3 | 11149.6 | 9977.2 | 10998.6 | 9880.5 | 10564.2 | 11642.2 | 9829.2 | 11106.4 | 9528.3 | 9778.3 | 10446.7 | 9837.5 | 10783.2 | 9575.3 | 10742.9 | 9550.2 | 9553 | 10975.9 | 9561.4 | 10877.4 | 10799.7 | 9567 | 10534.1 | 9994.8 | 10195.3 | 9567.3 | 10167.1 | 10611 | 10887.6 | 9798.5 | 10742.2 | 9437.6 | 10397.8 | 10268 | 9562.7 | 10798.7 | 9444.5 | 10839.9 | 9519.4 | 10713.8 | 9810.5 | 10601.8 | 9951.8 | 10983.4 | 9755.4 | 10454.2 | 9685.3 | 8577.3 | 10624.6 | 10191.3 | 9514 | 10952.4 | 10598.1 | 9743.6 | 9634.6 | 10696.9 | 9537.2 | 9907 | 10728.7 | 9455 | 10866.5 | 9436.2 | 10576.5 | 9717.7 | 10689.8 | 9194.5 | 10761.9 | 9703.1 | 10643.9 | 9700.8 | 10708.1 | 9821.5 | 9533.2 | 10587.5 | 9686.8 | 9484.9 | 10611.5 | 10781.2 | 10580.5 | 9640.6 | 10695.9 | 9597.6 | 10336.3 | 9727.3 | 10321.3 | 8968 | 10451.8 | 9594.1 | 9730.5 | 9738 | 9616.1 | 8311.9 | 9555.6 | 8451.4 | 9600.3 | 9604.2 | 11037.2 | 9650.8 | 11103.7 | 9889 | 10939.4 | 9681.6 | 9782.8 | 9714.2 | 10774.1 | 11098.9 | 10960.3 | 10898 | 10994 | 11028.7 | 9972.3 | 10995.1 | 10981.6 | 11050 | 11110 | 11073.9 | 11118.3 | 9977.9 | 11047.4 | 9986.9 | 20.2769 | 20.1982 | 20.1083 | 20.09 | 20.2766 | 20.1801 | 0 | 31 | 0 | 0 | 31.2 | 31 | 2.6351 | 2.6626 | 2.5895 | 2.6498 | 2.586 | 2.5395 | 5.15 | 4.915 | 4.668 | 5.293 | 5.222 | 4.914 |  | 4.1832 |  | 4.3033 |  | 4.3462 |  | 0.99129 |  | 1.2164 |  | 0.95938 |  | 5.4809 |  | 5.4978 |  | 5.4094 |  | 0.2477 |  | 0.22726 |  | 0.24165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 527680 | 941 | 515775 | 1010 | 454395.769 | 1198.867 | 0 | 4.1832 | 0 | 4.3033 | 0 | 4.3462 | 0 | 5.4809 | 0 | 5.4978 | 0 | 5.4094 | 819000 | 1000 | 811000 | 2000 | 1623734 | 5000 | 1627000 | 1618734 | 11.0167 | 4.2776 | 1.0557 | 5.4627 | 0.23887 | 24.68% | 4.373% | 20.1884 | 31.0667 | 2.6104 | 5.027 | 1635054.2 | 1622666 | 1789223.6856 | 90.69% | 44 | 0
2024-01-15 | 2024 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 335090.89 | 7:32 | 18:22 | 10563.2 | 11047.8 | 10833.5 | 10793.7 | 10866.2 | 11074.5 | 11042.8 | 11397.4 | 10964.5 | 10926.2 | 10815.7 | 10999.1 | 10934.5 | 10919 | 10892.9 | 11010.7 | 10896 | 11010.9 | 11032.5 | 11079.7 | 11023.4 | 11023.6 | 10827.7 | 10955.3 | 10800.9 | 9494.4 | 10838.9 | 10794.3 | 11000.7 | 10924.9 | 10821 | 11032.7 | 11143.6 | 11221.1 | 11130.4 | 11074.7 | 11167.3 | 11053.8 | 11119.1 | 10970.2 | 11787.9 | 10629.7 | 11639.1 | 10540 | 11213.7 | 12270.8 | 10464.2 | 11741.7 | 10139.2 | 10406.3 | 11091.1 | 10472.8 | 11419.1 | 10204.4 | 11379.7 | 10161.6 | 10159.5 | 11601.9 | 10165.5 | 11512.5 | 11432.7 | 10157.4 | 11173.4 | 10620.8 | 10867.5 | 10209.5 | 10831.8 | 11253.9 | 11513.1 | 10432.5 | 11368.6 | 10038.2 | 11026.8 | 10918.9 | 10153.2 | 11420.7 | 10051.6 | 11456.3 | 10118.5 | 11344.1 | 10442.7 | 11236.6 | 10587.7 | 11618 | 10399.5 | 11109.2 | 10328 | 9140.6 | 11282.2 | 10837.2 | 10138.3 | 11601.4 | 11239.3 | 10376.1 | 10248.1 | 11354.8 | 10179.8 | 10575.1 | 11394.9 | 10088.7 | 11518.8 | 10067.3 | 11253.7 | 10365.1 | 11360.8 | 9816.1 | 11437.2 | 10361.8 | 11328.1 | 10356.2 | 11378.2 | 10500.5 | 10174.8 | 11261.9 | 10331.9 | 10131.8 | 11263.4 | 11448.1 | 11249.6 | 10292.8 | 11365.5 | 10253.2 | 11007 | 10389.4 | 11017.2 | 9596.8 | 11137.8 | 10091.2 | 10409 | 10422.4 | 10280.8 | 8887.6 | 10209.1 | 9029 | 10242.9 | 10239.7 | 11721.3 | 10332.3 | 11784.6 | 10577.7 | 11629.5 | 10381 | 10493.8 | 10378.6 | 11473.1 | 11791.8 | 11655.5 | 11583 | 11687.8 | 11720.9 | 10677.6 | 11681.4 | 11671.8 | 11743.4 | 11791.3 | 11763.4 | 11814.5 | 10712.8 | 11726.4 | 10712.3 | 20.6182 | 20.2698 | 20.1088 | 20.0885 | 20.1945 | 20.0484 | 0 | 35.1 | 0 | 0 | 35 | 34.2 | 1.9348 | 1.9478 | 1.9397 | 1.9017 | 1.9707 | 1.9122 | 3.953 | 3.902 | 3.768 | 3.746 | 4.406 | 3.787 |  | 4.4404 |  | 4.589 |  | 4.645 |  | 1.0512 |  | 1.285 |  | 1.02 |  | 5.8972 |  | 5.9094 |  | 5.8483 |  | 0.25071 |  | 0.22984 |  | 0.24949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 528551 | 943 | 516638 | 1011 | 456121.836 | 1203.933 | 0 | 4.4404 | 0 | 4.589 | 0 | 4.645 | 0 | 5.8972 | 0 | 5.9094 | 0 | 5.8483 | 871000 | 2000 | 863000 | 1000 | 1726067 | 5066 | 1731000 | 1721001 | 10.8333 | 4.5581 | 1.1187 | 5.885 | 0.24335 | 24.54% | 4.135% | 20.2214 | 34.7667 | 1.9345 | 3.927 | 1739069.7 | 1724533 | 1916214.1552 | 90% | 38 | 198
2024-01-16 | 2024 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 335090.89 | 7:20 | 18:20 | 10129.6 | 10602.2 | 10434.9 | 10369.5 | 10490.9 | 10633.6 | 10592.9 | 11002.2 | 10531.6 | 10499.4 | 10369.8 | 10566.2 | 10489.7 | 10475.3 | 10448.4 | 10573.8 | 10457.3 | 10575.9 | 10600 | 10636.8 | 10584.2 | 10582.7 | 10355.8 | 10487.9 | 10346.3 | 9085.4 | 10373.5 | 10332.2 | 10548.6 | 10475 | 10358 | 10593.3 | 10663.9 | 10723.3 | 10650.2 | 10592.3 | 10737.1 | 10614.2 | 10685.9 | 10537.3 | 11451.2 | 10181.5 | 11285.1 | 10096 | 10790.7 | 11980.1 | 10033.2 | 11403.9 | 9708.2 | 9961.6 | 10641.3 | 10030.8 | 11019.1 | 9776 | 10970.7 | 9728.1 | 9726.5 | 11228 | 9731 | 11118.6 | 11018.3 | 9731.7 | 10755.2 | 10177.8 | 10404.9 | 9765.7 | 10364.9 | 10816.6 | 11130.4 | 9976 | 10958.5 | 9597.6 | 10594.1 | 10450 | 9726.2 | 11007.5 | 9609.7 | 11072.4 | 9705.4 | 10932.6 | 9984.3 | 10786 | 10137.3 | 11227.4 | 9943.9 | 10669.4 | 9873.3 | 8741.9 | 10845.8 | 10378.8 | 9694.5 | 11229.9 | 10837.5 | 9953.7 | 9846.5 | 10951.7 | 9740.2 | 10125.2 | 11005.5 | 9667.2 | 11128.4 | 9644.8 | 10817.6 | 9935 | 10950.6 | 9401 | 11028.2 | 9933.2 | 10896.7 | 9920.5 | 10975.8 | 10069 | 9760.6 | 10844.9 | 9903.4 | 9708 | 10864.8 | 11070.6 | 10844.7 | 9876.4 | 10989.2 | 9835.7 | 10584.5 | 9959.2 | 10581.5 | 9205.9 | 10725.6 | 9684.4 | 9986.2 | 9996.3 | 9863.9 | 8522.2 | 9807.7 | 8658.6 | 9852 | 9847.2 | 11382.7 | 9908.6 | 11455.7 | 10147.8 | 11293 | 9945.3 | 10067.4 | 9951.8 | 11078.3 | 11461.7 | 11286.5 | 11219.9 | 11331.1 | 11372.4 | 10227.5 | 11334.2 | 11307.3 | 11396.7 | 11455.2 | 11429.4 | 11486.3 | 10253.7 | 11352.8 | 10258.5 | 21.9101 | 21.7725 | 21.7968 | 21.6902 | 21.9258 | 21.8363 | 0 | 36.3 | 0 | 0 | 36.1 | 35.8 | 1.8514 | 1.7596 | 1.7293 | 1.9109 | 1.8966 | 1.8755 | 4.345 | 4.232 | 4.664 | 4.633 | 5.547 | 4.883 |  | 4.3158 |  | 4.4318 |  | 4.5182 |  | 1.0236 |  | 1.2486 |  | 0.99925 |  | 5.6611 |  | 5.6727 |  | 5.6199 |  | 0.25288 |  | 0.23316 |  | 0.25174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 529387 | 945 | 517469 | 1013 | 457782.102 | 1208.933 | 0 | 4.3158 | 0 | 4.4318 | 0 | 4.5182 | 0 | 5.6611 | 0 | 5.6727 | 0 | 5.6199 | 836000 | 2000 | 831000 | 2000 | 1660266 | 5000 | 1663000 | 1655266 | 11 | 4.4219 | 1.0905 | 5.6512 | 0.24592 | 24.66% | 4.352% | 21.822 | 36.0667 | 1.8372 | 4.7173 | 1672182.3 | 1659200 | 1833206.064 | 90.51% | 39 | 0
2024-01-17 | 2024 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 335090.89 | 7:30 | 18:10 | 9674 | 10119.7 | 9974.4 | 9940.9 | 10023.3 | 10156.7 | 10125.5 | 10506 | 10060.8 | 10035.8 | 9878.6 | 10087.5 | 10000.5 | 9986.4 | 9987.2 | 10086.4 | 9989 | 10090.9 | 10108.3 | 10148.2 | 10099.9 | 10097.5 | 9893.2 | 10010 | 9847.3 | 8656.4 | 9887.4 | 9846 | 10073.1 | 10017.1 | 9889.6 | 10111.8 | 10136.8 | 10195.6 | 10133.4 | 10077.9 | 10235.5 | 10123.7 | 10196.9 | 10032.9 | 10957.5 | 9676.5 | 10786.1 | 9601.6 | 10273.3 | 11560.4 | 9524.7 | 10920.6 | 9245.7 | 9491.8 | 10145.1 | 9544.2 | 10522.3 | 9322.4 | 10473.8 | 9275 | 9260.7 | 10730.8 | 9273.5 | 10616.6 | 10532.2 | 9280 | 10253.8 | 9702 | 9893.4 | 9289.2 | 9863.3 | 10313.7 | 10636.5 | 9496.1 | 10452.5 | 9141.6 | 10096.4 | 9952.3 | 9261.4 | 10525.4 | 9158.3 | 10588.8 | 9242.8 | 10454.8 | 9490.8 | 10283.9 | 9644.4 | 10730 | 9458 | 10156.3 | 9413.7 | 8320.1 | 10341.2 | 9887.5 | 9210.4 | 10717.1 | 10327.6 | 9474.9 | 9380.5 | 10432.1 | 9252.7 | 9605.8 | 10483.9 | 9172.6 | 10600.5 | 9153.2 | 10275.1 | 9418.6 | 10418 | 8909.5 | 10486.7 | 9404.2 | 10358.3 | 9410.1 | 10419.7 | 9545.7 | 9244.3 | 10305.9 | 9385.1 | 9187.9 | 10314.7 | 10515.9 | 10293.7 | 9356.4 | 10434.2 | 9310.7 | 10037.8 | 9442.2 | 10031.2 | 8720.5 | 10168.9 | 9319.3 | 9457 | 9465.5 | 9353.5 | 8076.6 | 9283.8 | 8211.1 | 9340.6 | 9343.3 | 10862.7 | 9388.4 | 10932.3 | 9613 | 10772.4 | 9432.7 | 9529.6 | 9450.4 | 10530.3 | 10934.2 | 10749.9 | 10677.3 | 10799.3 | 10841.1 | 9682.8 | 10787 | 10773.5 | 10864.2 | 10945.4 | 10902.8 | 10955.2 | 9719.7 | 10807.2 | 9710.4 | 19.0085 | 18.8538 | 18.6057 | 18.8945 | 18.9899 | 19.1039 | 0 | 30.4 | 0 | 0 | 30.9 | 30.6 | 2.8632 | 2.8128 | 2.8949 | 2.8917 | 2.7815 | 2.6204 | 5.221 | 5.165 | 5.319 | 5.03 | 5.263 | 5.191 |  | 4.0782 |  | 4.173 |  | 4.2358 |  | 0.97377 |  | 1.1861 |  | 0.93279 |  | 5.305 |  | 5.3112 |  | 5.2346 |  | 0.24368 |  | 0.22381 |  | 0.23898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530185 | 947 | 518259 | 1015 | 459363.303 | 1214.067 | 0 | 4.0782 | 0 | 4.173 | 0 | 4.2358 | 0 | 5.305 | 0 | 5.3112 | 0 | 5.2346 | 798000 | 2000 | 790000 | 2000 | 1581201 | 5134 | 1584000 | 1576067 | 10.6667 | 4.1623 | 1.0309 | 5.2836 | 0.23549 | 24.77% | 4.457% | 18.9094 | 30.6333 | 2.8108 | 5.1982 | 1592324.2 | 1580201 | 1740700.9494 | 90.78% | 33 | 0
2024-01-18 | 2024 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 335090.89 | 7:20 | 18:10 | 10029.6 | 10503.2 | 10373.3 | 10314.3 | 10429.9 | 10566.7 | 10531.5 | 10946.1 | 10449.6 | 10425.9 | 10279.7 | 10484.1 | 10397.4 | 10383.5 | 10368 | 10488.8 | 10367.4 | 10486.5 | 10503.7 | 10548.1 | 10495.2 | 10490.9 | 10270.4 | 10386.5 | 10235.5 | 8997 | 10279.3 | 10239.9 | 10463.7 | 10398.8 | 10259.6 | 10499.9 | 10553.9 | 10622.7 | 10544.3 | 10491.4 | 10645 | 10525.5 | 10598 | 10433 | 11393.6 | 10079.4 | 11227.1 | 9995 | 10703 | 11932.4 | 9936.8 | 11366.9 | 9623.8 | 9880.4 | 10551.8 | 9935.1 | 10935.6 | 9699.8 | 10880.6 | 9645.8 | 8682.9 | 10735.8 | 9653.2 | 11037.5 | 10955.4 | 9658.5 | 10668 | 10099.1 | 10307.8 | 9675.2 | 10276.1 | 10744.6 | 11062.3 | 9894.2 | 10896.2 | 9530.8 | 10521.4 | 10373.5 | 9651.9 | 10964 | 9542.7 | 11021.6 | 9632.8 | 10889.3 | 9913.2 | 10721.8 | 10052.6 | 11170.3 | 9865.2 | 10581.5 | 9798.4 | 8672.2 | 10671.1 | 10152.4 | 9607.2 | 11139.8 | 10737.2 | 9863.9 | 9755.9 | 10853.5 | 9634.6 | 10022.1 | 10913.7 | 9563 | 11054.8 | 9545 | 10725.9 | 9830.8 | 10858.8 | 9283.3 | 10951.4 | 9825 | 10797.9 | 9800 | 10781.4 | 9956.1 | 9645.7 | 10759.4 | 9796.7 | 9593.2 | 10768.5 | 10969.2 | 10735.6 | 9774.9 | 10879.2 | 9711.3 | 10475.6 | 9840.5 | 10462 | 9102.7 | 10605.9 | 9736.1 | 9877.1 | 9894.9 | 9773.2 | 8436.8 | 9688 | 8559.8 | 9736.1 | 9740.1 | 11286.5 | 9775.4 | 11368.5 | 10019.5 | 11216.6 | 9843.6 | 9953.6 | 9858.3 | 10961.8 | 11357.1 | 11189.9 | 11116.7 | 11229.8 | 11268 | 10102.2 | 11235.7 | 11217.9 | 11299.5 | 11383.8 | 11335.3 | 11383.1 | 10112.1 | 11240 | 10105.8 | 18.8248 | 18.7267 | 18.7291 | 18.6171 | 18.7664 | 18.7376 | 0 | 29.4 | 0 | 0 | 29.5 | 29.1 | 3.2757 | 3.1701 | 3.1243 | 3.2718 | 3.0733 | 3.002 | 5.907 | 5.412 | 5.166 | 5.782 | 5.022 | 5.131 |  | 4.2217 |  | 4.3315 |  | 4.3906 |  | 1.0128 |  | 1.2316 |  | 0.9802 |  | 5.4894 |  | 5.5155 |  | 5.4121 |  | 0.25115 |  | 0.23174 |  | 0.24891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 531013 | 948 | 519081 | 1017 | 461007.103 | 1219.133 | 0 | 4.2217 | 0 | 4.3315 | 0 | 4.3906 | 0 | 5.4894 | 0 | 5.5155 | 0 | 5.4121 | 828000 | 1000 | 822000 | 2000 | 1643800 | 5066 | 1647000 | 1638734 | 10.8333 | 4.3146 | 1.0749 | 5.4723 | 0.24393 | 24.91% | 4.458% | 18.7336 | 29.3333 | 3.1529 | 5.4033 | 1656092.9 | 1642133 | 1805614.967 | 90.95% | 41 | 0
2024-01-19 | 2024 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 335090.89 | 7:30 | 18:10 | 10564.1 | 10982.7 | 10876.4 | 10828.1 | 10933.3 | 11029.3 | 10988.3 | 11342.3 | 10937.3 | 10901.7 | 10811.3 | 10974.2 | 10922.9 | 10901 | 10867.3 | 10984.3 | 10853.6 | 10951.2 | 10971.4 | 11034.9 | 10948.7 | 10968.8 | 10764.6 | 10866.1 | 10742.6 | 9478.4 | 10801.4 | 10745.5 | 10915.9 | 10855.4 | 10743.6 | 10936.5 | 11086.4 | 11163.4 | 11095.9 | 11031 | 11062.5 | 10963.7 | 11021.2 | 10879.2 | 11681.3 | 10610.1 | 11530.2 | 10518.5 | 11150.1 | 12139.8 | 10449.7 | 11646.7 | 10143.8 | 10413.6 | 11038.3 | 10472.4 | 11352.4 | 10220.5 | 11302.8 | 10150.9 | 10163.1 | 11506 | 10175.3 | 11423.9 | 11353.5 | 10172.3 | 11121 | 10644.4 | 10825.2 | 10192.8 | 10790.5 | 11179.2 | 11407.5 | 10430.6 | 11287.2 | 10046.6 | 10969.3 | 10872.1 | 10163.2 | 11328.6 | 10044.3 | 11382.4 | 10146.3 | 11282.7 | 10462.8 | 11162.6 | 10587.8 | 11530.4 | 10404.8 | 11055.6 | 10317.4 | 9137.4 | 11188 | 10813.1 | 10116.1 | 11493.3 | 11176.4 | 10389.8 | 10264 | 11257.1 | 10133.5 | 10561.9 | 11296.9 | 10083 | 11414 | 10064.5 | 11172 | 10353 | 11256.4 | 9798.8 | 11332.6 | 10336.7 | 11229.3 | 10325.7 | 11245.7 | 10477 | 10153.4 | 11177.8 | 10322.4 | 10095.8 | 11182.1 | 11367 | 11165.5 | 10289.9 | 11276.1 | 10233.1 | 10942.9 | 10368.3 | 10937.6 | 9573 | 11060.7 | 10230 | 10393.7 | 10409.3 | 10255.6 | 8869.4 | 10207.7 | 9018.1 | 10258.7 | 10261.9 | 11611 | 10323.4 | 11680.4 | 10566.3 | 11531.6 | 10363.6 | 10475.1 | 10375.9 | 11383.7 | 11684.5 | 11560.4 | 11485.8 | 11581.9 | 11607.8 | 10639.6 | 11586.2 | 11571.4 | 11630.3 | 11688 | 11659.8 | 11704.9 | 10661.7 | 11590.9 | 10660.9 | 20.1331 | 19.8577 | 19.822 | 19.7626 | 19.9466 | 19.8019 | 0 | 32.2 | 0 | 0 | 32.5 | 31.8 | 2.5777 | 2.5582 | 2.5075 | 2.6489 | 2.5128 | 2.4244 | 5.2 | 4.77 | 4.508 | 5.136 | 5.091 | 4.61 |  | 4.4519 |  | 4.5901 |  | 4.6397 |  | 1.0731 |  | 1.307 |  | 1.0325 |  | 5.8481 |  | 5.883 |  | 5.7792 |  | 0.26086 |  | 0.23983 |  | 0.2606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 531880 | 950 | 519940 | 1019 | 462725.369 | 1224.267 | 0 | 4.4519 | 0 | 4.5901 | 0 | 4.6397 | 0 | 5.8481 | 0 | 5.883 | 0 | 5.7792 | 867000 | 2000 | 859000 | 2000 | 1718266 | 5134 | 1722000 | 1713132 | 10.6667 | 4.5606 | 1.1375 | 5.8368 | 0.25376 | 24.94% | 4.348% | 19.8873 | 32.1667 | 2.5382 | 4.8858 | 1731568.2 | 1717467 | 1905903.5198 | 90.11% | 29 | 0
2024-01-20 | 2024 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 335090.89 | 7:30 | 18:10 | 10349.3 | 10847.5 | 10740.1 | 10665.9 | 10781.2 | 10908 | 10862.5 | 11236.8 | 10774.4 | 10742 | 10622.7 | 10814.9 | 10744.6 | 10741.7 | 10700.2 | 10826.9 | 10713.1 | 10837.4 | 10854 | 10887.9 | 10855.7 | 10852.1 | 10617.7 | 10747.8 | 10596.3 | 9309.3 | 10635.3 | 10593.6 | 10814.8 | 10746.7 | 10610.2 | 10849.7 | 10890.8 | 10957.2 | 10902.4 | 10842 | 10988.6 | 10879.2 | 10942.5 | 10761.9 | 11658 | 10441.7 | 11493.9 | 10336.3 | 11042.9 | 12149.8 | 10286.6 | 11622.5 | 9933.6 | 10198.3 | 10900.1 | 10261.3 | 11256.9 | 10001.4 | 11208.3 | 9961.5 | 9939.7 | 11432.4 | 9957.6 | 11335.6 | 11253.5 | 9954 | 10986 | 10403.6 | 10633.1 | 9978 | 10592.1 | 11068.7 | 11339 | 10206.2 | 11188.7 | 9825 | 10825 | 10683.9 | 9941.8 | 11242.3 | 9828 | 11298 | 9933.9 | 11187.2 | 10233.3 | 11033.1 | 10373.4 | 11454.1 | 10187.6 | 10931.7 | 10106.3 | 8960.8 | 11095 | 10656.3 | 9933.7 | 11451.6 | 11100.4 | 10215.1 | 10096.2 | 11201.9 | 9971.8 | 10382.2 | 11245.5 | 9916 | 11354.7 | 9891.7 | 11081.5 | 10176.4 | 11194.9 | 9628.6 | 11265.7 | 10168.8 | 11141.8 | 10149.4 | 11223.9 | 10321 | 9984.1 | 11094.7 | 10144.9 | 9923.5 | 11106.6 | 11297.1 | 11040.1 | 10064.1 | 11205 | 10055.7 | 10829.5 | 10195.3 | 10824 | 9402.5 | 10961.5 | 10059.5 | 10204.1 | 10210.9 | 10084 | 8709.3 | 10025.9 | 8862.4 | 10051 | 10059.3 | 11576.6 | 10132.2 | 11646.6 | 10378.1 | 11490.1 | 10165.9 | 10278.6 | 10175.8 | 11314.8 | 11655.7 | 11511.8 | 11440.4 | 11535 | 11568.7 | 10467.3 | 11540.1 | 11510.3 | 11595.2 | 11643.6 | 11625.8 | 11680.1 | 10490.3 | 11565 | 10489.7 | 21.3349 | 21.2704 | 21.0841 | 21.2486 | 21.3138 | 21.2797 | 0 | 32.8 | 0 | 0 | 33 | 32.9 | 2.5484 | 2.5312 | 2.4765 | 2.6333 | 2.5294 | 2.4183 | 5.019 | 4.777 | 4.469 | 5.02 | 4.7 | 4.855 |  | 4.3658 |  | 4.4907 |  | 4.5624 |  | 1.0491 |  | 1.2657 |  | 1.0368 |  | 5.7223 |  | 5.7441 |  | 5.6653 |  | 0.25456 |  | 0.23412 |  | 0.25497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 532735 | 952 | 520790 | 1020 | 464422.836 | 1229.333 | 0 | 4.3658 | 0 | 4.4907 | 0 | 4.5624 | 0 | 5.7223 | 0 | 5.7441 | 0 | 5.6653 | 855000 | 2000 | 850000 | 1000 | 1697467 | 5066 | 1702000 | 1692401 | 10.6667 | 4.473 | 1.1172 | 5.7106 | 0.24788 | 24.98% | 4.341% | 21.2553 | 32.9 | 2.5229 | 4.8067 | 1709848.4 | 1696534 | 1859981.74 | 91.21% | 46 | 0
2024-01-21 | 2024 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 335090.89 | 7:30 | 18:20 | 10255.8 | 10719.2 | 10630.2 | 10572.7 | 10665.4 | 10805.9 | 10764 | 11127.3 | 10687.5 | 10632.5 | 10557.7 | 10737.3 | 10667.2 | 10667.8 | 10628.2 | 10752.1 | 10635.6 | 10742.3 | 10765.5 | 10801.7 | 10752.6 | 10759.6 | 10531.4 | 10648.7 | 10502.1 | 9237.1 | 10560.9 | 10502.2 | 10699.8 | 10624.7 | 10506.7 | 10737 | 10794.7 | 10849.3 | 10799.2 | 10740.8 | 10856.1 | 10754 | 10805.3 | 10647.3 | 11481.9 | 10343.7 | 11334.2 | 10240.4 | 10908.9 | 11948.7 | 10166.3 | 11438.4 | 9879.1 | 10140.7 | 10816.1 | 10197.6 | 11140.6 | 9937.6 | 11101.6 | 9895.1 | 9901.6 | 11321.7 | 9912.3 | 11239.8 | 11155.3 | 9907.2 | 10883.6 | 10331.2 | 10577 | 9915.5 | 10532.3 | 10958.6 | 11227.3 | 10144 | 11084.3 | 9767.1 | 10750 | 10758.45 | 9895.1 | 11118.3 | 9772.8 | 11188.4 | 9943 | 11179 | 10159.4 | 10913.1 | 10298.4 | 11317.1 | 10118.8 | 10823.9 | 10035.5 | 8889.9 | 10953.2 | 10554 | 9845.3 | 11291.8 | 10960.4 | 10108.9 | 9989.1 | 11054.9 | 9876.3 | 10272.3 | 11102.2 | 9828.1 | 11207.2 | 9803.3 | 10957.3 | 10082.2 | 11054.7 | 9543.5 | 11134.2 | 10070.3 | 11021.5 | 10065.5 | 11086.2 | 10204.9 | 9886.3 | 10953.3 | 10049.8 | 9839.3 | 10978.3 | 11145.9 | 10962.7 | 10005.8 | 11065.9 | 9960.6 | 10724.9 | 10100.4 | 10707.2 | 9308.6 | 10837.9 | 9946.4 | 10103.6 | 10116.2 | 9980 | 8625.9 | 9918.6 | 8758.1 | 9958.9 | 9952.9 | 11413.9 | 10049.4 | 11486.3 | 10286.8 | 11334.1 | 10073.5 | 10193.1 | 10078.4 | 11170 | 11490.1 | 11349.3 | 11281 | 11377.2 | 11413.3 | 10392.5 | 11382.2 | 11350.6 | 11431.4 | 11494.5 | 11471.9 | 11508.9 | 10401.4 | 11421.9 | 10406.2 | 19.8534 | 19.6749 | 19.6615 | 19.6687 | 19.8659 | 19.8009 | 0 | 32.2 | 0 | 0 | 32.3 | 32 | 2.5612 | 2.5166 | 2.4641 | 2.6132 | 2.5666 | 2.4877 | 5.252 | 5.237 | 4.92 | 4.891 | 4.69 | 4.941 |  | 4.3708 |  | 4.4908 |  | 4.5545 |  | 1.0501 |  | 1.2723 |  | 1.0143 |  | 5.6647 |  | 5.6978 |  | 5.61 |  | 0.25902 |  | 0.24067 |  | 0.25967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 533583 | 954 | 521630 | 1022 | 466103.37 | 1234.4 | 0 | 4.3708 | 0 | 4.4908 | 0 | 4.5545 | 0 | 5.6647 | 0 | 5.6978 | 0 | 5.61 | 848000 | 2000 | 840000 | 2000 | 1680534 | 5067 | 1684000 | 1675467 | 10.8333 | 4.4721 | 1.1122 | 5.6575 | 0.25312 | 24.87% | 4.474% | 19.7542 | 32.1667 | 2.5349 | 4.9885 | 1693328.95 | 1678733 | 1848425.4328 | 90.82% | 43 | 0
2024-01-22 | 2024 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 335090.89 | 7:30 | 18:10 | 9219.6 | 9656.8 | 9547.1 | 9501.9 | 9583.5 | 9712.7 | 9663.3 | 10072.8 | 9615.5 | 9553.7 | 9491.1 | 9660.4 | 9603.1 | 9586.9 | 9578.2 | 9680 | 9574.4 | 9686.5 | 9694.6 | 9726.3 | 9704.6 | 9693.4 | 9499.6 | 9608.4 | 9474.8 | 8317.4 | 9495.3 | 9454.7 | 9659.5 | 9614.1 | 9498.4 | 9712.8 | 9740 | 9797.5 | 9752.5 | 9699.7 | 9838.3 | 9731.8 | 9737.2 | 9630 | 10525.4 | 9303.9 | 10377.8 | 9210.4 | 9843.1 | 11050.2 | 9169.3 | 10512.3 | 8881.3 | 9118.3 | 9742.5 | 9180 | 10093.8 | 8928 | 10069.2 | 8916.8 | 8911.4 | 10317.6 | 8910.5 | 10209.8 | 10104.3 | 8898 | 9836.8 | 9270.9 | 9544.6 | 8940.6 | 9488.7 | 9927.6 | 10229.9 | 9125.9 | 10044.7 | 8767.2 | 9698 | 9537 | 8901.7 | 10085.3 | 8785.9 | 10173.2 | 8874.5 | 10028.7 | 9118.6 | 9831.4 | 9227.5 | 10304.3 | 9071.7 | 9742.6 | 8975.6 | 7989.3 | 9817.2 | 9081 | 8866.7 | 10313.1 | 9942.6 | 9124.5 | 9023.7 | 10038.9 | 8878.2 | 9225.5 | 10089.9 | 8818.4 | 10196.1 | 8805.3 | 9906.1 | 9062.1 | 10037.6 | 8583.4 | 10109.9 | 9070.6 | 9951.8 | 9002.4 | 10051.6 | 9208 | 8868.7 | 9863.5 | 9017.5 | 8823.6 | 9931.8 | 10102.2 | 9914 | 9006.1 | 10043.7 | 8957.6 | 9666.7 | 9074.5 | 9655 | 8398.8 | 9796.6 | 8958.2 | 9072.4 | 9067.1 | 8962.7 | 7752 | 8889.6 | 7829.7 | 8879.2 | 8870.9 | 10370.8 | 8963.7 | 10447.9 | 9175.7 | 10278.8 | 8989.1 | 9088 | 9005.7 | 10045.8 | 10438.8 | 10263.5 | 10203.3 | 10303.4 | 10348.7 | 9253.9 | 10317.8 | 10290.4 | 10384.5 | 10462.7 | 10418.8 | 10468 | 9274.5 | 10347.8 | 9284.6 | 21.9208 | 21.9171 | 21.9248 | 21.7241 | 21.9609 | 21.9847 | 0 | 33.9 | 0 | 0 | 34 | 33.8 | 3.0243 | 3.0009 | 2.6898 | 3.0128 | 2.9382 | 2.7853 | 6.28 | 6.544 | 6.029 | 6.359 | 6.083 | 6.382 |  | 4.0462 |  | 4.1454 |  | 4.1452 |  | 0.96144 |  | 1.2161 |  | 0.909 |  | 5.1235 |  | 5.1601 |  | 5.0282 |  | 0.22483 |  | 0.21358 |  | 0.22531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 534348 | 955 | 522387 | 1024 | 467619.57 | 1239.533 | 0 | 4.0462 | 0 | 4.1454 | 0 | 4.1452 | 0 | 5.1235 | 0 | 5.1601 | 0 | 5.0282 | 765000 | 1000 | 757000 | 2000 | 1516200 | 5133 | 1519000 | 1511067 | 10.6667 | 4.1123 | 1.0288 | 5.1039 | 0.22124 | 25.02% | 4.335% | 21.9054 | 33.9 | 2.9086 | 6.2795 | 1526897.4 | 1515133 | 1666976.4746 | 90.89% | 44 | 20289
2024-01-23 | 2024 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 335090.89 | 7:30 | 18:10 | 9914 | 10360.8 | 10255 | 10163.1 | 10252.6 | 10372.4 | 10380.2 | 10652.2 | 10317.3 | 10200.1 | 10241.9 | 10388.8 | 10287.7 | 10311.5 | 10248.7 | 10343.6 | 10197.3 | 10333.6 | 10346.4 | 10368.9 | 10394.2 | 10391.9 | 10191.9 | 10296.9 | 10209.4 | 9004 | 10204.1 | 10196.2 | 10347.7 | 10299.5 | 10266.7 | 10390.1 | 10599.8 | 10596.8 | 10546 | 10462.5 | 10506.9 | 10474.5 | 10545.8 | 10421.7 | 11064.8 | 10143.8 | 10971.5 | 10066.6 | 10598.8 | 11465.4 | 9897.8 | 11013.4 | 9619 | 9856.4 | 10461.6 | 9924.7 | 10717.5 | 9653.5 | 10709.3 | 9642.1 | 9593 | 10859.2 | 9631.5 | 10771 | 10715.3 | 9629 | 10463.9 | 9985.7 | 10224.2 | 9656.5 | 10215.6 | 10611.7 | 10805.1 | 9896 | 10723.9 | 9537.4 | 10389.7 | 10323.3 | 9603 | 10738.9 | 9505.8 | 10759.5 | 9571.2 | 10643.3 | 9889.9 | 10580.4 | 10041.4 | 10930 | 9891.3 | 10527.7 | 9810.1 | 8718.2 | 10633.5 | 10347.6 | 9584.9 | 10905.3 | 10642.3 | 9918.4 | 9816.1 | 10752.7 | 9742.1 | 10147.9 | 10856.8 | 9685.9 | 10884.1 | 9661.6 | 10638 | 9912.3 | 10723.3 | 9369.7 | 10807.9 | 9909.4 | 10691.9 | 9846.9 | 10754.7 | 10044.1 | 9757.9 | 10689.5 | 9881.9 | 9677 | 10728.6 | 10885.4 | 10707.2 | 9870.9 | 10817.9 | 9820.5 | 10502.6 | 9942.3 | 10482.1 | 9176.6 | 10617.1 | 9796.9 | 9900.1 | 9907 | 9804.7 | 8470.9 | 9722.7 | 8610.5 | 9812.2 | 9821 | 11040.8 | 9892 | 11113.4 | 10107.6 | 11043.1 | 9920.6 | 10034.6 | 9946.7 | 10812.9 | 11105.1 | 10973.2 | 10906.7 | 10983.5 | 11013.1 | 10137.7 | 11013 | 10982.7 | 11043.3 | 11110.5 | 11085.6 | 11136.2 | 10177.5 | 11019.2 | 10133.3 | 14.8038 | 14.6755 | 14.3919 | 14.7806 | 14.7912 | 14.9893 | 0 | 26.1 | 0 | 0 | 26.4 | 26.3 | 3.1603 | 3.0951 | 3.1997 | 3.1255 | 3.1294 | 2.8748 | 5.296 | 5.42 | 4.904 | 5.406 | 4.852 | 4.704 |  | 4.2592 |  | 4.3707 |  | 4.4234 |  | 1.034 |  | 1.2074 |  | 1.0101 |  | 5.4066 |  | 5.4078 |  | 5.3577 |  | 0.26055 |  | 0.24141 |  | 0.26069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 535169 | 957 | 523207 | 1026 | 469252.237 | 1244.667 | 0 | 4.2592 | 0 | 4.3707 | 0 | 4.4234 | 0 | 5.4066 | 0 | 5.4078 | 0 | 5.3577 | 821000 | 2000 | 820000 | 2000 | 1632667 | 5134 | 1637000 | 1627533 | 10.6667 | 4.3511 | 1.0838 | 5.3907 | 0.25422 | 24.91% | 4.716% | 14.7387 | 26.2667 | 3.0975 | 5.097 | 1645744.8 | 1631600 | 1802426.5753 | 90.52% | 44 | 1056
2024-01-24 | 2024 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 335090.89 | 7:30 | 18:10 | 10378.6 | 10850.8 | 10720.4 | 10650.3 | 10750.7 | 10910.9 | 10829.2 | 11186.8 | 10772.1 | 10697.5 | 10654.5 | 10827.5 | 10760.6 | 10757.6 | 10740.7 | 10851.1 | 10709.7 | 10813.2 | 10829.5 | 10863.4 | 10816.2 | 10824.2 | 10610.3 | 10730.4 | 10613.1 | 9337.3 | 10624.1 | 10595.7 | 10786.7 | 10724.2 | 10613.2 | 10819.1 | 10904.3 | 10967.6 | 10863.9 | 10793.2 | 10931.8 | 10841.4 | 10892.3 | 10743.3 | 11511.6 | 10387.8 | 11371.6 | 10263.6 | 10952.2 | 11976.5 | 10224.4 | 11498.1 | 9968.5 | 10223.9 | 10893.1 | 10288.4 | 11217.3 | 10028 | 11164.2 | 9995.4 | 9980.7 | 11375.3 | 9991.9 | 11288.8 | 11222 | 9994 | 10940.4 | 10391.7 | 10655.2 | 9993 | 10624.7 | 11034.8 | 11301.7 | 10217.6 | 11156.9 | 9832.5 | 10838.9 | 10697.7 | 9975.5 | 11195.1 | 9847.5 | 11261.6 | 9947.6 | 11148.4 | 10207.1 | 10981.3 | 10353 | 11376.2 | 10173.5 | 10887.9 | 10113 | 8960.1 | 11051.4 | 10645.9 | 9924.5 | 11357.5 | 11034.7 | 10200.6 | 10081.8 | 11118.6 | 9953.8 | 10331.1 | 11155.6 | 9866 | 11269.2 | 9862 | 11001.9 | 10133.7 | 11101.4 | 9583.1 | 11175.6 | 10128.9 | 11063.9 | 10119 | 11116.1 | 10266.9 | 9947.5 | 11005.6 | 10096.2 | 9887 | 11030.2 | 11213.4 | 10999.7 | 10081.8 | 11124.5 | 10023.2 | 10774.9 | 10139.6 | 10777.4 | 9382.8 | 10915.2 | 10019.8 | 10174.6 | 10193.9 | 10058.9 | 8701.1 | 9964.1 | 8795.9 | 10041.5 | 10043 | 11434.8 | 10105.7 | 11499.3 | 10336.2 | 11373 | 10145.8 | 10269.7 | 10169.4 | 11175.9 | 11500.1 | 11340.9 | 11280.3 | 11384.4 | 11424.2 | 10402.1 | 11385.9 | 11349.1 | 11420.7 | 11495.1 | 11463 | 11512 | 10438.1 | 11389 | 10403.2 | 17.874 | 17.4816 | 17.3125 | 17.3173 | 17.437 | 17.3113 | 0 | 30.9 | 0 | 0 | 30.9 | 30.5 | 2.1276 | 2.1127 | 2.1629 | 2.1547 | 2.0347 | 2.0302 | 3.812 | 4.084 | 3.769 | 4.108 | 3.966 | 4.401 |  | 4.411 |  | 4.5562 |  | 4.576 |  | 1.0528 |  | 1.2766 |  | 1.0218 |  | 5.7074 |  | 5.749 |  | 5.6035 |  | 0.26017 |  | 0.24234 |  | 0.26142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 536023 | 959 | 524050 | 1028 | 470942.637 | 1249.867 | 0 | 4.411 | 0 | 4.5562 | 0 | 4.576 | 0 | 5.7074 | 0 | 5.749 | 0 | 5.6035 | 854000 | 2000 | 843000 | 2000 | 1690400 | 5200 | 1693000 | 1685200 | 10.6667 | 4.5144 | 1.1171 | 5.6866 | 0.25465 | 24.75% | 4.478% | 17.4556 | 30.7667 | 2.1038 | 4.0233 | 1703150.5 | 1689400 | 1874752.3981 | 90.11% | 45 | 5235
2024-01-25 | 2024 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 335090.89 | 7:30 | 18:10 | 9611.9 | 10006.4 | 9918 | 9833.4 | 9965 | 10070.3 | 10009.5 | 10350.3 | 9965.9 | 9885.2 | 9865.9 | 10003.3 | 9970.5 | 9949.8 | 9950.5 | 10034.3 | 9922 | 10010.7 | 10018.1 | 10054.5 | 10001.7 | 10017.7 | 9828.7 | 9930.8 | 9798 | 8687.1 | 9831.2 | 9784.4 | 9964.2 | 9907.6 | 9825.7 | 10001.5 | 10131.7 | 10172.4 | 10135 | 10079.5 | 10096.9 | 10013.1 | 10050.1 | 9939.1 | 10655.8 | 9672.3 | 10531.7 | 9572.2 | 10141.7 | 11114.2 | 9517.8 | 10628.6 | 9286.2 | 9516.2 | 10078.4 | 9570.1 | 10377.6 | 9344.5 | 10324.5 | 9303.5 | 9285.7 | 10514.7 | 9304.7 | 10439.2 | 10362.9 | 9300.1 | 10092.9 | 9615.9 | 9864.6 | 9311.8 | 9843.2 | 10191.7 | 10447.9 | 9506.6 | 10324.7 | 9167.6 | 10023.6 | 9913.7 | 9293.4 | 10342.4 | 9188.3 | 10400.7 | 9270.2 | 10293.1 | 9492.6 | 10134.7 | 9611.8 | 10509.8 | 9470.5 | 10070 | 9407.9 | 8357 | 10205.3 | 9851.2 | 9240.4 | 10509.6 | 10217.2 | 9502.9 | 9400 | 10270.7 | 9275.3 | 9611.5 | 10326 | 9201.9 | 10442.7 | 9194.1 | 10198.9 | 9447.7 | 10282 | 8958.4 | 10350 | 9437.3 | 10240.7 | 9432.7 | 10301.1 | 9566.6 | 9270.7 | 10121.7 | 9406 | 9217.6 | 10223.7 | 10374.5 | 10179.7 | 9411.6 | 10301.5 | 9356.9 | 9987.7 | 9452.1 | 9978.8 | 8762.3 | 10121.4 | 9362.3 | 9492.1 | 9503.6 | 9385.5 | 8122 | 9316.7 | 8239.8 | 9394.8 | 9396.9 | 10659.5 | 9455.8 | 10723.6 | 9646.5 | 10595.5 | 9489.6 | 9591.5 | 9517.5 | 10427.9 | 10740.8 | 10610.2 | 10546 | 10620 | 10650 | 9727.9 | 10632.7 | 10594.6 | 10662.6 | 10755.4 | 10724.5 | 10760.2 | 9767.6 | 10647.4 | 9740.6 | 21.38 | 21.37 | 21.1 | 21.06 | 21.31 | 21.42 | 0 | 33.9 | 0 | 0 | 34.2 | 34.2 | 2.72 | 2.45 | 2.49 | 2.6 | 2.42 | 2.22 | 6.03 | 6.33 | 6.34 | 5.8 | 5.84 | 5.55 |  | 4.28 |  | 4.41 |  | 4.45 |  | 1.03 |  | 1.21 |  | 1.01 |  | 5.32 |  | 5.35 |  | 5.28 |  | 0.27 |  | 0.26 |  | 0.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 536814 | 961 | 524836 | 1029 | 472513.837 | 1254.867 | 0 | 4.28 | 0 | 4.41 | 0 | 4.45 | 0 | 5.32 | 0 | 5.35 | 0 | 5.28 | 791000 | 2000 | 786000 | 1000 | 1571200 | 5000 | 1574000 | 1566200 | 10.6667 | 4.38 | 1.0833 | 5.3167 | 0.26667 | 24.73% | 5.016% | 21.2733 | 34.1 | 2.4833 | 5.9817 | 1581713.1 | 1569601 | 1735203 | 90.46% | 60 | 1019
2024-01-26 | 2024 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 335090.89 | 7:20 | 18:00 | 9565.9 | 9979.3 | 9871.4 | 9780 | 9909.1 | 10033 | 9956.9 | 10321.4 | 9959.1 | 9831.3 | 9836.4 | 10000.4 | 9949.6 | 9937.3 | 9942.5 | 10023.1 | 9908 | 10018.8 | 10032.8 | 10062.3 | 10030 | 10033 | 9852.8 | 9945.2 | 9825.9 | 8660.9 | 9851.6 | 9799.2 | 10003.4 | 9940.7 | 9860.6 | 10055 | 10142.8 | 10181.2 | 10120.1 | 10068.1 | 10145.9 | 10063.4 | 10112.5 | 9994.6 | 10764.8 | 9703.3 | 10627.2 | 9609.7 | 10231.8 | 11256.9 | 9542.4 | 10740.8 | 9245 | 9479.6 | 10090.9 | 9558.1 | 10420.5 | 9291 | 10388.8 | 9297.3 | 9267 | 10570.4 | 9269.8 | 10487 | 10397.6 | 9257.2 | 10106.6 | 9574.7 | 9898.7 | 9308.8 | 9859.8 | 10249 | 10493.9 | 9501.7 | 10355.7 | 9139.2 | 10061.2 | 9925.2 | 9271 | 10394.1 | 9156.7 | 10457.9 | 9250.4 | 10345.5 | 9487.3 | 10167.9 | 9609.3 | 10558.4 | 9446.2 | 10110.9 | 9411.9 | 8338.6 | 10263.9 | 9907.6 | 9235.6 | 10584.2 | 10278.9 | 9501.6 | 9419.1 | 10358.8 | 9297.4 | 9625.5 | 10405 | 9194.4 | 10511.4 | 9190.7 | 10261 | 9460.6 | 10343 | 8956.9 | 10416.7 | 9416.9 | 10301.9 | 9427.8 | 10374.8 | 9561.9 | 9270.1 | 10164.7 | 9415.6 | 9208 | 10275.4 | 10438 | 10239.1 | 9407.5 | 10365.9 | 9353.6 | 10023 | 9453.1 | 10021.2 | 8754.3 | 10181 | 9370 | 9491.7 | 9494.1 | 9392 | 8117 | 9337 | 8249.8 | 9398.6 | 9398.5 | 10713.3 | 9448.8 | 10801.7 | 9680.5 | 10649.5 | 9478.3 | 9588.9 | 9520.9 | 10470.1 | 10784.9 | 10641.8 | 10577.8 | 10664.7 | 10693.3 | 9750 | 10675.1 | 10614.1 | 10691 | 10784.1 | 10766.8 | 10804.3 | 9756.3 | 10717.5 | 9742.4 | 16.126 | 16.0038 | 15.6788 | 16.1151 | 16.1573 | 16.4343 | 0 | 27.1 | 0 | 0 | 27.6 | 27.6 | 2.7984 | 2.7341 | 2.8238 | 2.9134 | 2.7319 | 2.5657 | 5.213 | 4.657 | 4.7 | 4.94 | 4.471 | 4.441 |  | 4.1771 |  | 4.2618 |  | 4.3305 |  | 0.98808 |  | 1.2206 |  | 0.95692 |  | 5.1749 |  | 5.2249 |  | 5.1527 |  | 0.27542 |  | 0.25965 |  | 0.27384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 537607 | 962 | 525624 | 1031 | 474086.837 | 1259.933 | 0 | 4.1771 | 0 | 4.2618 | 0 | 4.3305 | 0 | 5.1749 | 0 | 5.2249 | 0 | 5.1527 | 793000 | 1000 | 788000 | 2000 | 1573000 | 5066 | 1578000 | 1567934 | 10.6667 | 4.2564 | 1.0552 | 5.1842 | 0.26964 | 24.79% | 5.201% | 16.0859 | 27.4333 | 2.7612 | 4.737 | 1584714.1 | 1572067 | 1729341.5191 | 90.91% | 43 | 0
2024-01-27 | 2024 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 335090.89 | 7:20 | 18:10 | 6974.2 | 7295.3 | 7185 | 7108.1 | 7238.1 | 7379.3 | 7331.6 | 7609.6 | 7287.6 | 7178.6 | 7191.8 | 7319.1 | 7287 | 7270 | 7265.3 | 7350.6 | 7246.4 | 7325.7 | 7330.1 | 7340.7 | 7335.3 | 7323.4 | 7183.5 | 7259.7 | 7151.6 | 6281.1 | 7169.9 | 7123.1 | 7293.4 | 7249.7 | 7192.9 | 7351.6 | 7335.2 | 7363.6 | 7351.4 | 7295.7 | 7392.7 | 7323.1 | 7364.6 | 7282.6 | 7956.3 | 7067.7 | 7847.7 | 6966.3 | 7465.1 | 8415.1 | 6920.9 | 7947.9 | 6744.2 | 6918.6 | 7399.7 | 6963.5 | 7672.8 | 6791.7 | 7639.2 | 6762.5 | 6735.6 | 7792.5 | 6759.3 | 7738.3 | 7663.7 | 6755.9 | 7356.1 | 6931.5 | 7189.7 | 6731.3 | 7169.6 | 7477.2 | 7748.7 | 6881.9 | 7615.3 | 6630.4 | 7375.8 | 7242.2 | 6743.4 | 7655.2 | 6656.9 | 7723.4 | 6740.1 | 7609.2 | 6849.5 | 7402.4 | 6942.3 | 7726.1 | 6818.1 | 7338.9 | 6797.9 | 6014.4 | 7466 | 7183.5 | 6656 | 7757.2 | 7501.5 | 6881.8 | 6822.1 | 7562.7 | 6725.9 | 6959.4 | 7623.3 | 6644.2 | 7705.4 | 6637.2 | 7483 | 6840.3 | 7575.1 | 6475.4 | 7610.4 | 6802.6 | 7506.6 | 6811.2 | 7556.8 | 6904.2 | 6694.7 | 7426.9 | 6796.8 | 6638.9 | 7511.6 | 7612.6 | 7450.1 | 6796.9 | 7556.4 | 6743.3 | 7279.4 | 6808.7 | 7244.4 | 6303.3 | 7386 | 6752.6 | 6829.1 | 6829.4 | 6771.9 | 5839.9 | 6696 | 5908.1 | 5619.7 | 2.7 | 7840.7 | 6785.2 | 7902.9 | 6939.8 | 7784.7 | 6820.5 | 6895.7 | 6843.2 | 7590.6 | 7888.8 | 7762.4 | 7720.3 | 7781.7 | 7815.7 | 7008.7 | 7793.6 | 7751.9 | 7810.5 | 7877 | 7857 | 7887 | 6994.8 | 7823.7 | 6989.1 | 18.549 | 18.4196 | 18.1864 | 18.3917 | 18.4777 | 18.464 | 0 | 27.2 | 0 | 0 | 27.3 | 27 | 2.3495 | 2.2146 | 2.1827 | 2.302 | 2.2546 | 2.1605 | 4.303 | 3.811 | 4.207 | 4.098 | 3.94 | 3.669 |  | 3.2204 |  | 3.2665 |  | 3.2708 |  | 0.76339 |  | 0.90216 |  | 0.74607 |  | 3.7179 |  | 3.7075 |  | 3.6374 |  | 0.2325 |  | 0.22172 |  | 0.22601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 538187 | 964 | 526189 | 1033 | 475227.57 | 1264.933 | 0 | 3.2204 | 0 | 3.2665 | 0 | 3.2708 | 0 | 3.7179 | 0 | 3.7075 | 0 | 3.6374 | 580000 | 2000 | 565000 | 2000 | 1140733 | 5000 | 1141000 | 1135733 | 10.8333 | 3.2526 | 0.80387 | 3.6876 | 0.22674 | 24.72% | 6.149% | 18.4147 | 27.1667 | 2.244 | 4.0047 | 1145786.9 | 1138334 | 1236913.0545 | 92.03% | 49 | 10235
2024-01-28 | 2024 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 335090.89 | 7:30 | 18:20 | 7969.3 | 8353 | 8199.5 | 8131.1 | 8214.4 | 8426.6 | 8398.3 | 8751.3 | 8343.4 | 8213.8 | 8229.6 | 8378.5 | 8324.2 | 8307.1 | 8262.6 | 8383.1 | 8264.8 | 8370.4 | 8375.1 | 8382.2 | 8370.6 | 8367 | 8204.9 | 8293.9 | 8181.2 | 7182.9 | 8186.2 | 8141.3 | 8333.4 | 8285.9 | 8221.3 | 8408.4 | 8403 | 8432.4 | 8414.5 | 8358 | 8471.8 | 8384.7 | 8426.5 | 8338 | 9106.6 | 8080.5 | 8988.2 | 7973.8 | 8530.4 | 9606.9 | 7928 | 9096 | 7691.9 | 7894.6 | 8438 | 7953.8 | 8751.6 | 7747.2 | 8720.1 | 7729.1 | 7698.5 | 8907.2 | 7717.4 | 8847.1 | 8755.2 | 7714.4 | 8435 | 7940.7 | 8239.3 | 7726.1 | 8204.1 | 8576.7 | 8863.4 | 7891.7 | 8708 | 7591.6 | 8425.7 | 8278.8 | 7712.2 | 8745.9 | 7611.5 | 8822.7 | 7701.9 | 8694.5 | 7878.2 | 8495.5 | 7991.6 | 8895.7 | 7858.6 | 8444.9 | 7809.4 | 6918.9 | 8584.4 | 8258.2 | 7657 | 8911.2 | 8596.8 | 7884.2 | 7807 | 8694.6 | 7723.5 | 7994 | 8757 | 7632.8 | 8847.5 | 7625 | 8590.3 | 7847.5 | 8689.3 | 7434.3 | 8740.7 | 7828.3 | 8617 | 7834.8 | 8689.7 | 7939.4 | 7691.4 | 8559.4 | 7820.8 | 7639.3 | 8644.3 | 8767 | 8566.3 | 7824.6 | 8702.2 | 7763.8 | 8383.9 | 7837.3 | 8335.6 | 7257.7 | 8498.7 | 7773.2 | 7875.3 | 7875.1 | 7794.5 | 6731.3 | 7712.5 | 6799 | 7793.8 | 7789.5 | 9052.4 | 7836.6 | 9143.9 | 8026.9 | 9001.1 | 7880.1 | 8008.1 | 7886.5 | 8765.7 | 9121.6 | 8946 | 8916.9 | 8981.6 | 9032 | 8103.1 | 9019.3 | 8906.7 | 8996.7 | 9092.8 | 9080.6 | 9112 | 8094.5 | 9004 | 8066.8 | 21.4103 | 21.3669 | 21.3191 | 21.2729 | 21.4756 | 21.5259 | 0 | 31.8 | 0 | 0 | 31.9 | 31.5 | 3.3209 | 3.2652 | 3.2627 | 3.2036 | 3.2744 | 3.2266 | 7.394 | 7.835 | 7.66 | 7.5 | 7.049 | 7.813 |  | 3.7299 |  | 3.7625 |  | 3.8348 |  | 0.8745 |  | 1.0544 |  | 0.87515 |  | 4.3538 |  | 4.252 |  | 4.2223 |  | 0.26028 |  | 0.24884 |  | 0.25692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 538850 | 966 | 526848 | 1035 | 476545.037 | 1270.067 | 0 | 3.7299 | 0 | 3.7625 | 0 | 3.8348 | 0 | 4.3538 | 0 | 4.252 | 0 | 4.2223 | 663000 | 2000 | 659000 | 2000 | 1317467 | 5134 | 1318000 | 1312333 | 10.8333 | 3.7757 | 0.93467 | 4.276 | 0.25535 | 24.75% | 5.972% | 21.3951 | 31.7333 | 3.2589 | 7.5418 | 1323720.2 | 1316201 | 1419084.8972 | 92.75% | 33 | 1455
2024-01-29 | 2024 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 335090.89 | 7:30 | 18:10 | 8298.3 | 8684.7 | 8459.1 | 8399.1 | 8601.6 | 8757 | 8716.5 | 9091.2 | 8674.7 | 8560.1 | 8565.9 | 8713.3 | 8680 | 8657.5 | 8643.2 | 8743.6 | 8630.5 | 8735.8 | 8747 | 8762.9 | 8745.7 | 8741.4 | 8554 | 8661.8 | 8529.1 | 7490.4 | 8560.3 | 8529.6 | 8719 | 8652 | 8568.4 | 8765.4 | 8748.5 | 8775.9 | 8762 | 8706.4 | 8835.2 | 8742.5 | 8780.3 | 8667.8 | 9499.1 | 8433.8 | 9365 | 8330.8 | 8890.7 | 9999.2 | 8262.3 | 9474.5 | 8005 | 8208.8 | 8793.5 | 8270.9 | 9118.3 | 8067.8 | 9067.8 | 8030.1 | 8004.9 | 9250.1 | 8015.2 | 9189 | 9095.6 | 8011.2 | 8773.5 | 8274 | 8540.9 | 7997.9 | 8511.4 | 8891.3 | 9186.6 | 8185.1 | 9041.2 | 7879.3 | 8720.6 | 8594.3 | 7999.9 | 9081.2 | 7912.2 | 9144.4 | 7977.1 | 9011.7 | 8176.4 | 8837.4 | 8295.5 | 9229 | 8163.6 | 8763.5 | 8088.6 | 7176.8 | 8940.7 | 8562.3 | 7969.5 | 9269.4 | 8949.1 | 8217.9 | 8126.7 | 9028.4 | 8013.8 | 8301 | 9091.4 | 7926.9 | 9192.4 | 7930.8 | 8918.4 | 8152.8 | 9033.8 | 7720.1 | 9084.2 | 8144.8 | 8965.2 | 8148.4 | 9041.9 | 8266.3 | 7979.8 | 8883.6 | 8136.5 | 7938.5 | 8969 | 9086.9 | 8897.4 | 8097.1 | 9019 | 8041.8 | 8707.9 | 8141.1 | 8638.8 | 7488.7 | 8798.7 | 8036.1 | 8139 | 8151.8 | 8054.7 | 6957.1 | 7986.9 | 7050.4 | 8075.3 | 8077.3 | 9363.8 | 8108 | 9441.9 | 8295.3 | 9309 | 8149.8 | 8300.7 | 8174.5 | 9074.5 | 9438.2 | 9263.5 | 9214.5 | 9294 | 9339.4 | 8373.6 | 9321.9 | 9258.7 | 9352.4 | 9452.8 | 9421.3 | 9448.1 | 8387.4 | 9357.5 | 8374.1 | 22.9554 | 22.7065 | 22.5714 | 22.6094 | 22.694 | 22.7168 | 0 | 34.1 | 0 | 0 | 34.1 | 34.2 | 1.6631 | 1.6748 | 1.7474 | 1.6368 | 1.58 | 1.6386 | 3.473 | 3.739 | 3.723 | 3.693 | 4.212 | 3.836 |  | 3.828 |  | 3.8788 |  | 3.9343 |  | 0.90014 |  | 1.0579 |  | 0.87788 |  | 4.5859 |  | 4.4555 |  | 4.4234 |  | 0.23719 |  | 0.22205 |  | 0.23327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 539540 | 967 | 527532 | 1037 | 477912.971 | 1274.867 | 0 | 3.828 | 0 | 3.8788 | 0 | 3.9343 | 0 | 4.5859 | 0 | 4.4555 | 0 | 4.4234 | 690000 | 1000 | 684000 | 2000 | 1367934 | 4800 | 1371000 | 1363134 | 10.6667 | 3.8804 | 0.94531 | 4.4883 | 0.23084 | 24.36% | 5.143% | 22.7089 | 34.1333 | 1.6568 | 3.7793 | 1375359.2 | 1366134 | 1466321.241 | 93.17% | 34 | 0
2024-01-30 | 2024 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 335090.89 | 7:30 | 18:00 | 4766.9 | 4986.9 | 4879.4 | 4849.4 | 4961.1 | 5025.2 | 5026.7 | 5227 | 5009.7 | 4933.3 | 4933.1 | 5017.5 | 4990.8 | 4977.5 | 4996.6 | 5033.9 | 4948.6 | 5005.8 | 5019.2 | 5028.1 | 5039.7 | 5030.6 | 4938.3 | 4981.9 | 4914.1 | 4310.1 | 4925.7 | 4906.2 | 5029.3 | 4997.5 | 4958.5 | 5066.4 | 5048.2 | 5057.2 | 5071.2 | 5024.4 | 5081.2 | 5035.3 | 5055.3 | 5017 | 5442.3 | 4844.9 | 5386.3 | 4774.9 | 5124.7 | 5774.2 | 4740.1 | 5442.4 | 4632.7 | 4756.6 | 5081.1 | 4794.7 | 5266.8 | 4654.8 | 5260.2 | 4663.8 | 4640.7 | 5362.8 | 4650.3 | 5329.1 | 5275.7 | 4641.8 | 5053.3 | 4757.3 | 4985 | 4677.6 | 4960.6 | 5202.1 | 5359.3 | 4778.6 | 5264.7 | 4590.7 | 5109.4 | 5014.1 | 4657.9 | 5288.1 | 4608.8 | 5335 | 4663.1 | 5260.9 | 4771.5 | 5174.1 | 4850.2 | 5389.3 | 4771 | 5134.2 | 4722.7 | 4192.2 | 5210 | 5032.3 | 4638.2 | 5398.3 | 5221.9 | 4799.5 | 4755.9 | 5266 | 4692.7 | 4876.7 | 5349.3 | 4650.4 | 5390.9 | 4645.8 | 5236.2 | 4781.8 | 5295.7 | 4527.6 | 5320.1 | 4767 | 5244.9 | 4760.6 | 5268.7 | 4834.1 | 4687.7 | 5214.7 | 4766.2 | 4657.1 | 5289.2 | 5353.4 | 5222.9 | 4814 | 5321.7 | 4746 | 5122.1 | 4767.4 | 5075.3 | 4441.9 | 5205.6 | 4767.1 | 4820.5 | 4825.8 | 4773.7 | 4122.4 | 4725.3 | 4166 | 4808.7 | 4812.5 | 5574.4 | 4816.4 | 5633.6 | 4937.9 | 5532.9 | 4853.1 | 4933.8 | 4880.2 | 5386.4 | 5609.3 | 5505.7 | 5495.6 | 5509.1 | 5542.7 | 4994.6 | 5551.5 | 5500.8 | 5537.8 | 5607.5 | 5581.7 | 5612 | 4978.5 | 5547.4 | 4964.6 | 22.1123 | 22.0061 | 22.0302 | 21.9051 | 21.9332 | 22.2103 | 0 | 28.5 | 0 | 0 | 28.8 | 28.8 | 2.5877 | 2.5647 | 2.447 | 2.6929 | 2.5662 | 2.3789 | 6.353 | 4.954 | 4.714 | 5.074 | 4.528 | 5.788 |  | 2.3633 |  | 2.3402 |  | 2.4202 |  | 0.5728 |  | 0.64096 |  | 0.52085 |  | 2.4756 |  | 2.4645 |  | 2.4522 |  | 0.17121 |  | 0.16957 |  | 0.16733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 539939 | 969 | 527935 | 1038 | 478713.571 | 1279.067 | 0 | 2.3633 | 0 | 2.3402 | 0 | 2.4202 | 0 | 2.4756 | 0 | 2.4645 | 0 | 2.4522 | 399000 | 2000 | 403000 | 1000 | 800600 | 4200 | 799000 | 796400 | 10.5 | 2.3746 | 0.5782 | 2.4641 | 0.16937 | 24.35% | 6.874% | 22.0329 | 28.7 | 2.5396 | 5.2352 | 802776.7 | 798934 | 834501.4244 | 95.74% | 38 | 47639
2024-01-31 | 2024 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 335090.89 | 7:30 | 18:20 | 9721 | 10216.4 | 10067.5 | 9989.7 | 10151.6 | 10325.3 | 10261.8 | 10681.7 | 10143.9 | 10065 | 9997.1 | 10185.9 | 10095.6 | 10088.8 | 10114.1 | 10178.6 | 10086.3 | 10191 | 10140.9 | 10170.9 | 10139.6 | 10136.1 | 9900 | 10029.1 | 9928.1 | 8725 | 9946 | 9912.5 | 10094.9 | 10018 | 9920 | 10172.9 | 10212.9 | 10232.4 | 10202.2 | 10146.7 | 10291.3 | 10163.1 | 10199.9 | 10069.9 | 10898.6 | 9688.6 | 10752.5 | 9578.3 | 10255.6 | 11414 | 9524.4 | 10857.2 | 9332.1 | 9580.1 | 10234.7 | 9678.9 | 10601 | 9383.6 | 10595.2 | 9379.7 | 9392.9 | 10816.5 | 9370.5 | 10757.1 | 10650.9 | 9370.5 | 10299 | 9668.5 | 9963.6 | 9320 | 9897.6 | 10292.7 | 10665.7 | 9478.1 | 10486.5 | 9117.3 | 10124.9 | 9962 | 9287 | 10511.5 | 9188.7 | 10581.2 | 9256.5 | 10449.8 | 9404.2 | 10192.1 | 9533.8 | 10617.3 | 9379.8 | 10052 | 9356.3 | 8246.2 | 10298.1 | 9843 | 9265.4 | 10774.9 | 10470 | 9651.5 | 9579.1 | 10501.2 | 9169.7 | 9490.4 | 10376.9 | 9038.1 | 10673.6 | 9078.5 | 10340.7 | 9334.6 | 10526.3 | 8895.1 | 10556.6 | 9344.8 | 10478.7 | 9499.9 | 10587 | 9579 | 9084.1 | 10139.9 | 9266.7 | 9059.6 | 10220.2 | 10398.1 | 10158.4 | 9283.6 | 10344.4 | 9241 | 9970.3 | 9349.5 | 9967.5 | 8662.5 | 10116.1 | 9258.3 | 9420.8 | 9456.9 | 9281.7 | 8049.5 | 9305.2 | 8246.9 | 9669.8 | 9655.1 | 11183.4 | 9718.5 | 11296 | 9972 | 11138.1 | 9789.7 | 9983.2 | 9779.4 | 10932.2 | 11335.4 | 11125.8 | 11071.9 | 11147.8 | 11180.8 | 10056.2 | 11187.7 | 11171.4 | 11270.6 | 11360.9 | 11330.2 | 11366.6 | 10122.9 | 11275.2 | 10112.8 | 24.353 | 24.213 | 24.1214 | 24.1099 | 24.3698 | 24.5176 | 0 | 37.2 | 0 | 0 | 36.9 | 37 | 3.3576 | 3.3179 | 3.2655 | 3.287 | 3.4253 | 3.4573 | 6.909 | 7.26 | 6.82 | 6.765 | 6.849 | 6.853 |  | 4.3773 |  | 4.4476 |  | 4.6765 |  | 1.0367 |  | 1.2425 |  | 1.0236 |  | 5.4216 |  | 5.264 |  | 5.4537 |  | 0.24993 |  | 0.23099 |  | 0.25991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 540741 | 970 | 528733 | 1039 | 480306.838 | 1282.933 | 0 | 4.3773 | 0 | 4.4476 | 0 | 4.6765 | 0 | 5.4216 | 0 | 5.264 | 0 | 5.4537 | 802000 | 1000 | 798000 | 1000 | 1593267 | 3866 | 1598000 | 1589401 | 10.8333 | 4.5005 | 1.1009 | 5.3798 | 0.24694 | 24.46% | 4.59% | 24.2808 | 37.0333 | 3.3518 | 6.9093 | 1604626.8 | 1591667 | 1746556.8899 | 91.13% | 42 | 1916
2024-02-01 | 2024 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 335090.89 | 7:30 | 18:10 | 9611 | 10073.3 | 9789.2 | 9721.9 | 10028.1 | 10156.5 | 10098.8 | 10530.6 | 10054.1 | 9937.2 | 9895.6 | 10086.3 | 9996.6 | 9965.3 | 10003.2 | 10082.9 | 9971.6 | 10081.9 | 10090 | 10122.5 | 10086.4 | 10083.2 | 9874.6 | 9993.6 | 9845.8 | 8645.8 | 9878.3 | 9843.8 | 10056.8 | 9989.8 | 9861.4 | 10093.1 | 10135.1 | 10155.6 | 10118 | 10064.4 | 10210.5 | 10087.2 | 10144.6 | 10003.2 | 10975.9 | 9717.9 | 10790.1 | 9599.9 | 10264.5 | 11509.4 | 9533.6 | 10946.7 | 9236.1 | 9479.9 | 10135.5 | 9544 | 10509.5 | 9300.4 | 10464.8 | 9259.4 | 9250.4 | 10697.8 | 9265.3 | 10625.9 | 10520.3 | 9262.1 | 10186.2 | 9614.7 | 9898.6 | 9277.4 | 9849.3 | 10324.3 | 10609.6 | 9489 | 10456 | 9135.1 | 10075.1 | 9941.9 | 9246.1 | 10486.5 | 9159.6 | 10570.5 | 9220.9 | 10422.9 | 9524.3 | 10317 | 9649.1 | 10752.1 | 9491.1 | 10173.2 | 9414.6 | 8340.4 | 10343.4 | 9926.4 | 9237.7 | 10749 | 10375 | 9517.3 | 9415.5 | 10473.7 | 9248.5 | 9633 | 10530.4 | 9202.4 | 10649.6 | 9191.2 | 10325 | 9437.8 | 10464.2 | 8936.3 | 10531.2 | 9412.5 | 10376.3 | 9430.1 | 10457.2 | 9556.2 | 9287.8 | 10323.5 | 9423 | 9191.2 | 10358.5 | 10556.2 | 10287.9 | 9407.2 | 10476.6 | 9344.4 | 10065.6 | 9441.4 | 10032.3 | 8737.4 | 10221.9 | 9344.7 | 9486.5 | 9491.6 | 9347.9 | 8098.2 | 9305.2 | 8208.3 | 9397.6 | 9391.9 | 10911.3 | 9441.6 | 11035.2 | 9691.2 | 10843.7 | 9488.4 | 9673.1 | 9503.2 | 10624.7 | 11043.4 | 10832.2 | 10776 | 10861 | 10897.1 | 9782.1 | 10901.9 | 10843.1 | 10951.8 | 11003 | 10986 | 11060 | 9804.4 | 10950.3 | 9815.1 | 23.5863 | 23.5077 | 23.3521 | 23.493 | 23.705 | 23.5819 | 0 | 35.1 | 0 | 0 | 35.6 | 35.5 | 2.3539 | 2.3296 | 2.2985 | 2.4543 | 2.3387 | 2.2478 | 4.221 | 4.786 | 5.058 | 5.299 | 4.552 | 5.308 |  | 4.3467 |  | 4.4184 |  | 4.5363 |  | 1.0575 |  | 1.2588 |  | 1.0193 |  | 5.3597 |  | 5.2384 |  | 5.2675 |  | 0.26542 |  | 0.2474 |  | 0.26638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 541537 | 972 | 529537 | 1041 | 481890.438 | 1287.8 | 0 | 4.3467 | 0 | 4.4184 | 0 | 4.5363 | 0 | 5.3597 | 0 | 5.2384 | 0 | 5.2675 | 796000 | 2000 | 804000 | 2000 | 1583600 | 4867 | 1596000 | 1578733 | 10.6667 | 4.4338 | 1.1119 | 5.2885 | 0.25973 | 25.08% | 4.911% | 23.5376 | 35.4 | 2.3371 | 4.8707 | 1594349.2 | 1582000 | 1747077.0284 | 90.55% | 39 | 0
2024-02-02 | 2024 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 335090.89 | 7:38 | 18:30 | 10091.2 | 10590.8 | 10392.8 | 10328.3 | 10549.6 | 10678.7 | 10642.8 | 11007.9 | 10532.6 | 10400.7 | 10341.3 | 10534.4 | 10459.1 | 10431.6 | 10452.2 | 10544.2 | 10399.7 | 10492.3 | 10482.6 | 10534.1 | 10458 | 10469 | 10233 | 10358.2 | 10222.4 | 8982.9 | 10276.5 | 10227.4 | 10436.8 | 10360 | 10225.5 | 10481.6 | 10461.1 | 10514.9 | 10489.5 | 10413.9 | 10566.6 | 10451.5 | 10503.7 | 10328 | 11325.2 | 10078.1 | 11143.5 | 9933.8 | 10625.2 | 11815.3 | 9899.2 | 11317.7 | 9621.8 | 9871.2 | 10558.5 | 9950.9 | 10926.2 | 9706.8 | 10866.3 | 9619.5 | 9613.9 | 11086 | 9655.4 | 11040.4 | 10945.3 | 9658.7 | 10590.8 | 10009.4 | 10250.3 | 9603.1 | 10208.6 | 10688.2 | 10984.5 | 9836.8 | 10819.9 | 9463.5 | 10449.8 | 10298.1 | 9602.8 | 10869.8 | 9502.3 | 10954.4 | 9568.6 | 10817.5 | 9861 | 10686.4 | 9952.4 | 11095.7 | 9793.9 | 10491.3 | 9754.1 | 8606.4 | 10614.9 | 10228.4 | 9513.5 | 11019.6 | 10689.5 | 9813.6 | 9692.7 | 10729.6 | 9470.5 | 9828.5 | 10724 | 9367.8 | 10873 | 9372.2 | 10536.1 | 9605.2 | 10642.1 | 9095.5 | 10682.1 | 9553.5 | 10538.5 | 9569.8 | 10575.1 | 9690 | 9427.5 | 10467.3 | 9564.6 | 9326.3 | 10508.6 | 10695.9 | 10431.2 | 9563.9 | 10622 | 9500.4 | 10206.3 | 9561.1 | 10145.1 | 8882.8 | 10396.9 | 9528.2 | 9666.7 | 9678 | 9557 | 8253.1 | 9492.3 | 8387 | 9593.1 | 9587.1 | 11010 | 9590.7 | 11129.6 | 9848.3 | 11012.1 | 9702.6 | 9884.7 | 9725.8 | 10687.9 | 11076.5 | 10891.1 | 10835.7 | 10928.9 | 10980.3 | 9901.7 | 10974.6 | 10887.4 | 10964.4 | 11024.5 | 10989.8 | 11058.4 | 9866.5 | 10995.2 | 9874.4 | 24.1812 | 24.1947 | 23.8391 | 24.0396 | 23.941 | 24.15 | 0 | 37.3 | 0 | 0 | 37 | 36.5 | 3.079 | 2.9772 | 2.9255 | 2.9818 | 2.8722 | 2.9284 | 6.54 | 6.226 | 6.292 | 5.654 | 6.334 | 6.32 | 4.7616 | 4.5497 | 4.7054 | 4.6283 | 4.5046 | 4.5777 | 1.0207 | 1.0945 | 0.94128 | 1.3083 | 1.1539 | 1.0192 |  | 5.5631 | 5.6569 | 5.4536 | 5.504 | 5.2787 | 0.23785 | 0.26779 | 0.21714 | 0.24878 | 0.22269 | 0.25732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 542365 | 973 | 530334 | 1043 | 483518.6 | 1292.8 | 4.7616 | 4.5497 | 4.7054 | 4.6283 | 4.5046 | 4.5777 | 0 | 5.5631 | 5.6569 | 5.4536 | 5.504 | 5.2787 | 828000 | 1000 | 797000 | 2000 | 1628162 | 5000 | 1622000 | 1623162 | 10.8667 | 4.6212 | 1.0896 | 5.4912 | 0.24193 | 23.58% | 4.406% | 24.0576 | 36.9333 | 2.9607 | 6.2277 | 1639675.1 | 1626100 | 1809650.9205 | 89.86% | 44 | 10854
2024-02-03 | 2024 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 335090.89 | 7:35 | 18:21 | 4643.6 | 4874 | 4820 | 4798 | 4888 | 4912.4 | 4906.6 | 5113.8 | 4865.8 | 4862.2 | 4789 | 4871.4 | 4847 | 4833.9 | 4883.9 | 4909.4 | 4842.5 | 4882.1 | 4871.9 | 4885.3 | 4889.7 | 4880.8 | 4780 | 4829.4 | 4729.3 | 4153.1 | 4761.1 | 4734.4 | 4852.2 | 4834.7 | 4766.5 | 4870.8 | 4792.7 | 4820.7 | 4862.4 | 4818.9 | 4872 | 4822.2 | 4841.8 | 4767.8 | 5275.8 | 4694.5 | 5200.8 | 4623.2 | 4961.8 | 5574.6 | 4605.1 | 5282.5 | 4476.4 | 4595 | 4910 | 4609.2 | 5091.1 | 4517.6 | 5049.6 | 4482.2 | 4453.8 | 5150.4 | 4490 | 5115.1 | 5065.2 | 4485.5 | 4894.8 | 4624.7 | 4711.8 | 4414.1 | 4698.2 | 4892.3 | 5085.1 | 4476.1 | 4985.1 | 4336.5 | 4859.6 | 4744.5 | 4439.7 | 5012 | 4368.8 | 5082.9 | 4438.8 | 4997 | 4479.6 | 4872.3 | 4510.8 | 5042.2 | 4452.8 | 4769.9 | 4451.3 | 3913.7 | 4864.3 | 4683.5 | 4336.9 | 5047.5 | 4889.5 | 4500.1 | 4462.8 | 4920.4 | 4337.4 | 4492.8 | 4919.2 | 4281.3 | 4982 | 4275.8 | 4826.8 | 4403.5 | 4880.7 | 4163.2 | 4898.7 | 4378.5 | 4830.3 | 4379.4 | 4857.3 | 4441 | 4329.1 | 4796.8 | 4381 | 4277.6 | 4847.2 | 4875.9 | 4797.3 | 4353.5 | 4845.1 | 4308.8 | 4698 | 4372.2 | 4657.5 | 4030.4 | 4716.3 | 4296 | 4356.2 | 4363.9 | 4308.1 | 3716.4 | 4273.9 | 3768.8 | 4306.9 | 4308.7 | 4983 | 4303.9 | 5000.6 | 4394.8 | 4934.1 | 4326.9 | 4406.3 | 4352.2 | 4788.6 | 4975.4 | 4925.7 | 4905.8 | 4923.9 | 4954 | 4439.3 | 4932.5 | 4945 | 4959.3 | 4972.2 | 4955.6 | 4974 | 4419.7 | 4983.1 | 4434.8 | 20.6473 | 20.6011 | 20.4225 | 20.5578 | 20.5642 | 20.7575 | 0 | 25.4 | 0 | 0 | 25.2 | 25.0151 | 3.4059 | 3.5289 | 3.4423 | 3.4566 | 3.5136 | 3.565 | 6.998 | 7.281 | 7.33 | 7.007 | 7.006 | 7.88 | 2.2671 | 2.2639 | 2.3023 | 2.2433 | 2.1975 | 2.1856 | 0.37575 | 0.42359 | 0.36359 | 0.49565 | 0.43863 | 0.39334 | 2.4171 | 2.4228 | 2.4178 | 2.3667 | 2.3008 | 2.2467 | 0.082685 | 0.098882 | 0.081162 | 0.093623 | 0.085078 | 0.093115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 542750 | 975 | 530701 | 1045 | 484268.105 | 1298 | 2.2671 | 2.2639 | 2.3023 | 2.2433 | 2.1975 | 2.1856 | 2.4171 | 2.4228 | 2.4178 | 2.3667 | 2.3008 | 2.2467 | 385000 | 2000 | 367000 | 2000 | 749505 | 5200 | 748000 | 744305 | 10.7667 | 2.2433 | 0.41509 | 2.362 | 0.089091 | 18.5% | 3.772% | 20.5917 | 25.205 | 3.4854 | 7.2503 | 752474.5 | 748867 | 818010.6174 | 91.55% | 69 | 203420
2024-02-04 | 2024 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 335090.89 | 7:45 | 18:15 | 2702.4 | 2829 | 2823.5 | 2803.8 | 2855.5 | 2854.9 | 2855 | 2966 | 2832.7 | 2847.6 | 2785.1 | 2835.6 | 2805.6 | 2813 | 2829 | 2840.8 | 2791.8 | 2808.8 | 2819.2 | 2828.6 | 2832.2 | 2828.1 | 2763.8 | 2791.2 | 2734.5 | 2401.2 | 2766.4 | 2743.7 | 2810.5 | 2801.8 | 2760.3 | 2820 | 2774.3 | 2787.1 | 2816.5 | 2785.3 | 2809.9 | 2785.8 | 2796.1 | 2765.5 | 3009.1 | 2679.8 | 2975.7 | 2639 | 2854.1 | 3231.8 | 2625.6 | 3017.5 | 2611.5 | 2681.1 | 2868.1 | 2685.4 | 2976.2 | 2634.6 | 2945.7 | 2609.1 | 2593.3 | 3002.8 | 2620 | 2985.9 | 2961 | 2620.3 | 2842.7 | 2689 | 2740.2 | 2561.2 | 2734.8 | 2841.7 | 2968.2 | 2596 | 2903.2 | 2517.1 | 2840.6 | 2762 | 2588 | 2914.4 | 2539.7 | 2972.6 | 2592 | 2919.5 | 2588.5 | 2823.6 | 2615 | 2918.9 | 2579.2 | 2764.5 | 2579.9 | 2263.3 | 2815.8 | 2705.7 | 2499.7 | 2918.2 | 2831.9 | 2608.5 | 2588.5 | 2846.8 | 2507.6 | 2587.6 | 2837 | 2459.7 | 2884 | 2458.1 | 2791 | 2528.9 | 2815.6 | 2390.8 | 2819.2 | 2497.5 | 2778.5 | 2506.2 | 2779.6 | 2518.7 | 2481.1 | 2750.8 | 2498.2 | 2445.1 | 2769.4 | 2793.2 | 2731.7 | 2501.4 | 2767.2 | 2459.6 | 2628.8 | 2468 | 2628.6 | 2294.9 | 2689.4 | 2456.9 | 2511.8 | 2525.6 | 2469.6 | 2134.8 | 2462 | 2178.6 | 2490.3 | 2498 | 2874.5 | 2484.6 | 2878.5 | 2530.5 | 2854.7 | 2500.8 | 2542.4 | 2526.4 | 2746.3 | 2856.5 | 2826.2 | 2815.7 | 2827.4 | 2849.7 | 2549.5 | 2833.2 | 2855.2 | 2853.5 | 2868.4 | 2854.3 | 2858 | 2536.3 | 2864.9 | 2540.2 | 16.8754 | 16.8402 | 16.6186 | 16.8248 | 16.762 | 16.8455 | 0 | 21 | 0 | 0 | 20.6 | 20.5 | 2.4212 | 2.4499 | 2.4473 | 2.4133 | 2.4809 | 2.4208 | 5.613 | 5.373 | 5.433 | 5.397 | 5.396 | 5.088 | 1.3634 | 1.3762 | 1.3728 | 1.3568 | 1.2986 | 1.3001 | 0.16881 | 0.18999 | 0.1533 | 0.2154 | 0.19021 | 0.16514 | 1.3781 | 1.3839 | 1.3611 | 1.3573 | 1.2945 | 1.2804 | 0.031613 | 0.037961 | 0.030758 | 0.036279 | 0.032644 | 0.035012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 542973 | 977 | 530912 | 1047 | 484700.105 | 1303.4 | 1.3634 | 1.3762 | 1.3728 | 1.3568 | 1.2986 | 1.3001 | 1.3781 | 1.3839 | 1.3611 | 1.3573 | 1.2945 | 1.2804 | 223000 | 2000 | 211000 | 2000 | 432000 | 5400 | 430000 | 426600 | 10.5 | 1.3447 | 0.18047 | 1.3425 | 0.034045 | 13.42% | 2.536% | 16.7944 | 20.7 | 2.4389 | 5.3833 | 434723.3 | 427666 | 477020.0738 | 89.65% | 86 | 47008
2024-02-05 | 2024 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 335090.89 | 7:30 | 18:29 | 10553.3 | 11010.1 | 10636.5 | 10611.5 | 10999.8 | 11062.8 | 11034.4 | 11379.8 | 10956 | 10961.6 | 10820.1 | 10982.7 | 10922 | 10913.6 | 10949.8 | 10997.5 | 10895 | 10974.1 | 10996.1 | 11051 | 10991.5 | 10999.3 | 10797.4 | 10900 | 10759 | 9483.4 | 10804.7 | 10764.2 | 10963.8 | 10913.4 | 10791.8 | 10985.1 | 11104.9 | 11161.2 | 11092.2 | 11039.5 | 11089.8 | 10995.8 | 11041.7 | 10912.9 | 11646.9 | 10598.2 | 11493 | 10460.9 | 11140.2 | 12181.1 | 10438.3 | 11628.4 | 10136.3 | 10402.6 | 11041.7 | 10456.7 | 11349 | 10238.4 | 11292.9 | 10143.9 | 10130.7 | 11494 | 10156 | 11409.6 | 11325.9 | 10151 | 11116.7 | 10623.1 | 10774.6 | 10123.5 | 10735.1 | 11127.3 | 11385.6 | 10251.5 | 11254.1 | 9940.2 | 10939 | 10806.4 | 10094.9 | 11288.5 | 9987.1 | 11348.4 | 10071.7 | 11245.5 | 10370.1 | 11131.2 | 10519.4 | 11472 | 10342.6 | 11011.2 | 10266.4 | 9074.9 | 11227.2 | 10777.2 | 10090 | 11511.9 | 11194.5 | 10395.5 | 10275.3 | 11283.3 | 10153.2 | 10511.8 | 11288.9 | 10020.5 | 11422.6 | 10019.1 | 11164.1 | 10311.1 | 11250.4 | 9754.2 | 11318.9 | 10277.2 | 11215.4 | 10292.1 | 11279.9 | 10436.1 | 10121 | 11138.3 | 10270.9 | 10057.5 | 11174.5 | 11298.5 | 11138 | 10206.9 | 11244.1 | 10155.2 | 10811.7 | 10301.7 | 10922.5 | 9515.9 | 11040.1 | 10143.5 | 10336.3 | 10377.1 | 10201.2 | 8817.5 | 10166.2 | 8994 | 10198.8 | 10208.3 | 11528.5 | 10212.8 | 11579.5 | 10449.7 | 11477.1 | 10307.2 | 10488.1 | 10336.8 | 11276.7 | 11582.3 | 11481.4 | 11409 | 11489 | 11515 | 10537.4 | 11487.1 | 11537.4 | 11578.5 | 11612.8 | 11579.7 | 11615.6 | 10575.3 | 11613.3 | 10598.4 | 19.7094 | 19.2888 | 19.142 | 19.1336 | 19.1901 | 19.1177 | 0 | 32.3 | 0 | 0 | 32.4 | 31.9 | 2.2691 | 2.266 | 2.2397 | 2.3252 | 2.3021 | 2.3418 | 4.63 | 5.024 | 4.555 | 4.958 | 4.725 | 4.886 | 4.7331 | 4.684 | 4.8155 | 4.7674 | 4.7475 | 4.8297 | 0.84738 | 0.89033 | 0.78896 | 1.1137 | 0.99138 | 0.85705 | 5.842 | 5.8508 | 5.8524 | 5.8444 | 5.8178 | 5.703 | 0.19393 | 0.22294 | 0.18011 | 0.20422 | 0.18874 | 0.21692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 543840 | 978 | 531768 | 1049 | 486414.971 | 1308.533 | 4.7331 | 4.684 | 4.8155 | 4.7674 | 4.7475 | 4.8297 | 5.842 | 5.8508 | 5.8524 | 5.8444 | 5.8178 | 5.703 | 867000 | 1000 | 856000 | 2000 | 1714866 | 5133 | 1720000 | 1709733 | 10.9833 | 4.7629 | 0.9148 | 5.8184 | 0.20115 | 19.21% | 3.457% | 19.2636 | 32.2 | 2.2907 | 4.7963 | 1727094.7 | 1713933 | 1945302.6429 | 88.11% | 60 | 0
2024-02-06 | 2024 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 335090.89 | 7:29 | 18:30 | 9967.8 | 10393 | 10306.8 | 10277.1 | 10361.1 | 10426.3 | 10424.4 | 10783.7 | 10353.8 | 10387.1 | 10208.2 | 10374.8 | 10292.4 | 10289.5 | 10300.5 | 10354.5 | 10238.8 | 10313.1 | 10340.4 | 10395.6 | 10338.7 | 10344.6 | 10123.6 | 10234.1 | 10094.5 | 8933.8 | 10142.4 | 10096.3 | 10297 | 10234.9 | 10102.6 | 10315 | 10371.5 | 10437.6 | 10405.3 | 10340.1 | 10394.8 | 10282.4 | 10321.3 | 10189.6 | 10993.2 | 9914.9 | 10861.3 | 9787.7 | 10453 | 11530.9 | 9775.2 | 10979.9 | 9560.8 | 9812.7 | 10412.6 | 9856.1 | 10726.6 | 9640.1 | 10675.8 | 9555.1 | 9564.8 | 10896 | 9591.3 | 10824.2 | 10738.5 | 9589.7 | 10519.4 | 10032.8 | 10149.4 | 9528.2 | 10117.6 | 10478.8 | 10796.7 | 9706.3 | 10649.5 | 9402.3 | 10344.7 | 10205.2 | 9573.9 | 10690 | 9464.6 | 10786.9 | 9563.6 | 10673.8 | 9752.9 | 10492.8 | 9878.7 | 10837.6 | 9716.4 | 10354.2 | 9637.2 | 8552 | 10542.6 | 10116.5 | 9451.8 | 10839.6 | 10507.9 | 9729 | 9622.6 | 10597.5 | 9536.1 | 9858.1 | 10655.2 | 9410.9 | 10751.8 | 9417.4 | 10464.7 | 9671.3 | 10547.4 | 9146.3 | 10618.3 | 9613.7 | 10488.5 | 9614.8 | 10540.2 | 9739.3 | 9482.3 | 10462.2 | 9621.8 | 9432.5 | 10511.1 | 10637.4 | 10440.5 | 9593.7 | 10572.1 | 9527.7 | 10127 | 9620.9 | 10192.5 | 8919.4 | 10346.9 | 9520.1 | 9697.5 | 9726.7 | 9571.2 | 8284.5 | 9528 | 8452 | 9608.4 | 9629.1 | 10972.6 | 9649.9 | 11037.4 | 9869 | 10922.9 | 9726.4 | 9888.5 | 9751 | 10701.2 | 11039.6 | 10922.5 | 10848.9 | 10924.4 | 10949.2 | 9945.3 | 10934.9 | 10972.9 | 11025.7 | 11079.4 | 11047.2 | 11082.9 | 9982.4 | 11048 | 10003.3 | 21.4313 | 21.0029 | 20.6049 | 20.8263 | 20.6883 | 20.7382 | 0 | 33 | 0 | 0 | 33.3 | 32.6 | 2.9609 | 2.886 | 2.7878 | 2.8419 | 2.6574 | 2.6174 | 6.563 | 6.057 | 5.369 | 5.496 | 5.28 | 5.421 | 4.5947 | 4.5424 | 4.6514 | 4.6544 | 4.5992 | 4.6724 | 0.84551 | 0.90661 | 0.77836 | 1.1032 | 1.0024 | 0.87973 | 5.5245 | 5.5009 | 5.4965 | 5.5348 | 5.4919 | 5.4131 | 0.20975 | 0.24428 | 0.19858 | 0.22859 | 0.20667 | 0.23308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 544657 | 980 | 532574 | 1051 | 488031.505 | 1313.467 | 4.5947 | 4.5424 | 4.6514 | 4.6544 | 4.5992 | 4.6724 | 5.5245 | 5.5009 | 5.4965 | 5.5348 | 5.4919 | 5.4131 | 817000 | 2000 | 806000 | 2000 | 1616534 | 4934 | 1619000 | 1611600 | 11.0167 | 4.6191 | 0.9193 | 5.4936 | 0.22016 | 19.9% | 4.008% | 20.882 | 32.9667 | 2.7919 | 5.6977 | 1627747.4 | 1615667 | 1837931.4727 | 87.91% | 58 | 4690
2024-02-07 | 2024 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 335090.89 | 7:39 | 18:31 | 9699.8 | 10165.3 | 10124.1 | 10076.4 | 10188.6 | 10254.1 | 10241.7 | 10630.2 | 10119 | 10124.3 | 9987.2 | 10155.6 | 10092.2 | 10084.3 | 10137.7 | 10176.9 | 10076.2 | 10165.7 | 10170.7 | 10215.9 | 10178.7 | 10173.6 | 9970.1 | 10076.4 | 9912.1 | 8740.9 | 9948.8 | 9914.3 | 10137.4 | 10089.3 | 9960.2 | 10163.4 | 10220.1 | 10272.1 | 10214.9 | 10164.5 | 10259.4 | 10153.5 | 10212.8 | 10079.9 | 10981.7 | 9827.2 | 10815 | 9693.8 | 10379.9 | 11552.5 | 9673.2 | 10967.3 | 9337 | 9582.9 | 10206.8 | 9632.2 | 10551.7 | 9441.7 | 10483.3 | 9350.2 | 9338.5 | 10707.7 | 9359 | 10615 | 10520.3 | 9353.4 | 10289.3 | 9783.1 | 9926.9 | 9321.6 | 9881.4 | 10291.4 | 10589.2 | 9513.5 | 10436.9 | 9176.4 | 10107.7 | 9964 | 9321.4 | 10468.8 | 9206.7 | 10560.6 | 9298.3 | 10411.6 | 9534.7 | 10283 | 9651.4 | 10667.6 | 9508.5 | 10155.5 | 9449.1 | 8368.3 | 10393.1 | 9949.1 | 9313.6 | 10734 | 10381.2 | 9592.1 | 9483.9 | 10494.7 | 9374.7 | 9699.4 | 10538.6 | 9268 | 10673.3 | 9269.2 | 10368.7 | 9538.5 | 10465.7 | 9024.3 | 10542.4 | 9489.8 | 10413.5 | 9506.1 | 10488 | 9621.6 | 9339.4 | 10349.3 | 9487.8 | 9296 | 10408.3 | 10536.5 | 10348 | 9441.7 | 10475.6 | 9387 | 10133.2 | 9505 | 10092.2 | 8787 | 10234.6 | 9374.7 | 9538.7 | 9565.6 | 9415.6 | 8142.9 | 9371.3 | 8294.6 | 9382 | 9391 | 10753.8 | 9395.5 | 10812.2 | 9605.8 | 10704.2 | 9455.7 | 9629.2 | 9489 | 10443.2 | 10794.6 | 10685.5 | 10613.3 | 10696.1 | 10728.4 | 9670.3 | 10693.2 | 10717.2 | 10765.6 | 10808.3 | 10772.1 | 10812.1 | 9681 | 10809 | 9701.5 | 20.8879 | 20.7212 | 20.7289 | 20.6506 | 20.7061 | 20.728 | 0 | 30.3 | 0 | 0 | 30.5766 | 30.1 | 3.6664 | 3.5951 | 3.5457 | 3.6224 | 3.4649 | 3.4722 | 6.755 | 6.695 | 6.46 | 7.036 | 6.431 | 6.798 | 4.4274 | 4.9449 | 4.5146 | 4.4743 | 4.4403 | 4.441 | 1.9319 | 1.4521 | 0.79112 | 1.0918 | 1.0349 | 0.92658 | 5.5099 | 5.3571 | 5.3651 | 5.3518 | 5.3047 | 5.2603 | 0.21548 | 0.25263 | 0.2052 | 0.23508 | 0.21462 | 0.24174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 545459 | 982 | 533367 | 1052 | 489620.038 | 1318.4 | 4.4274 | 4.9449 | 4.5146 | 4.4743 | 4.4403 | 4.441 | 5.5099 | 5.3571 | 5.3651 | 5.3518 | 5.3047 | 5.2603 | 802000 | 2000 | 793000 | 1000 | 1588533 | 4933 | 1592000 | 1583600 | 10.8667 | 4.5404 | 1.2047 | 5.3582 | 0.22746 | 26.53% | 4.245% | 20.7371 | 30.3255 | 3.5611 | 6.6958 | 1599423.8 | 1586201 | 1847716.6512 | 85.85% | 48 | 4130
2024-02-08 | 2024 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 335090.89 | 7:26 | 18:37 | 11638 | 11997.9 | 11928 | 11921.9 | 11981.4 | 12039.2 | 12024.8 | 12301.9 | 11948.8 | 11956.9 | 11830.5 | 11972.9 | 11928.5 | 11904.6 | 11938.5 | 11988.2 | 11865.7 | 11947.5 | 11968.1 | 12052.4 | 11958.8 | 11988.1 | 11815.3 | 11902.1 | 11779.8 | 10778.9 | 11829.3 | 11782.3 | 11930.4 | 11865.3 | 11789.1 | 11946.3 | 12352.8 | 12413.3 | 12339.4 | 12297.1 | 12062.7 | 11978.2 | 11975.4 | 11897.3 | 12570.4 | 11706.3 | 12413.7 | 11615.3 | 12164.8 | 13030.3 | 11543.2 | 12527.2 | 11357.8 | 11580.6 | 12048.9 | 11608.9 | 12311.1 | 11398.7 | 12281.4 | 11369.9 | 11388 | 12463.5 | 11406.1 | 12401.7 | 12336 | 11377.5 | 12136 | 11749.5 | 11874.4 | 11383.1 | 11860.1 | 12170.3 | 12359.9 | 11560.5 | 12277.5 | 11295.2 | 12000 | 11941.1 | 11374.5 | 12298.7 | 11313.8 | 12342.9 | 11370.3 | 12263.7 | 11599.2 | 12177.3 | 11709.1 | 12479.2 | 11566.4 | 12088 | 11432.6 | 10414.4 | 12212.4 | 11861.9 | 11359.9 | 12476.3 | 12199.3 | 11590.4 | 11475.9 | 12259.3 | 11406.4 | 11701 | 12285.7 | 11306.5 | 12408.3 | 11305.3 | 12210.9 | 11559.7 | 12233 | 11073.5 | 12325.7 | 11504.5 | 12251.3 | 11518.1 | 12295.4 | 11661.2 | 11401.4 | 12196.8 | 11513.9 | 11368.9 | 12202 | 12349.4 | 12172.4 | 11504.7 | 12280.3 | 11460.5 | 12013.7 | 11560.2 | 11990.5 | 10899.3 | 12140.1 | 11476 | 11617.7 | 11610.3 | 11489.8 | 10141.7 | 11452.4 | 10359.2 | 11488.9 | 11489.8 | 12526.6 | 11489.8 | 12575.7 | 11681 | 12467.8 | 11524.3 | 11661.3 | 11559.4 | 12364.6 | 12585.1 | 12531.8 | 12445.1 | 12520.3 | 12532.2 | 11755.5 | 12514.3 | 12547.3 | 12567.9 | 12604.4 | 12582.4 | 12633.5 | 11792.2 | 12630.8 | 11798.7 | 21.0616 | 20.6129 | 20.8635 | 20.5986 | 20.68 | 20.6632 | 0 | 33.2 | 0 | 0 | 33.2 | 32.7 | 3.2518 | 3.2056 | 3.1376 | 3.3026 | 3.1741 | 3.0974 | 7.121 | 6.1567 | 6.9417 | 6.4467 | 7.305 | 6.548 | 5.438 | 5.4754 | 5.5411 | 5.5258 | 5.5193 | 5.5453 | 1.1023 | 1.1369 | 0.9957 | 1.3569 | 1.2894 | 1.1688 | 6.7178 |  | 6.7437 | 6.7715 | 6.7539 | 6.7216 | 0.25526 | 0.29367 | 0.23814 | 0.27261 | 0.25185 | 0.29246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 546411 | 983 | 534313 | 1054 | 491509.238 | 1323.267 | 5.438 | 5.4754 | 5.5411 | 5.5258 | 5.5193 | 5.5453 | 6.7178 | 0 | 6.7437 | 6.7715 | 6.7539 | 6.7216 | 952000 | 1000 | 946000 | 2000 | 1889200 | 4867 | 1895000 | 1884333 | 11.1833 | 5.5075 | 1.175 | 6.7417 | 0.26733 | 21.33% | 3.965% | 20.7466 | 33.0333 | 3.1948 | 6.7532 | 1904310.4 | 1888734 | 2231887.2587 | 84.62% | 36 | 3146
2024-02-09 | 2024 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 335090.89 | 7:22 | 18:37 | 11787.9 | 12147.7 | 12067.9 | 12060.2 | 12120.8 | 12179.4 | 12164.5 | 12444.3 | 12099.8 | 12101.1 | 11988.3 | 12128.5 | 12082.1 | 12062.7 | 12088.8 | 12137.4 | 12021.1 | 12103.4 | 12131.1 | 12215.6 | 12116.3 | 12158.5 | 11973.9 | 12059.9 | 11943.1 | 10832.8 | 11988.8 | 11948.9 | 12090.2 | 12017.7 | 11950.6 | 12108.5 | 12519.8 | 12574.6 | 12507.6 | 12467.4 | 12225.1 | 12140.8 | 12167.6 | 12057.9 | 12746.7 | 11874.4 | 12584.4 | 11773.8 | 12320.4 | 13196.4 | 11705.4 | 12698.6 | 11493.1 | 11722.8 | 12207.4 | 11755.8 | 12472.8 | 11541.2 | 12425.2 | 11490.7 | 11512.3 | 12607 | 11532.5 | 12551.4 | 12483.6 | 11505.3 | 12285.9 | 11888.9 | 12021 | 11523.5 | 12006.2 | 12323.6 | 12509.6 | 11702.9 | 12431.3 | 11406 | 12138.7 | 12078.6 | 11499.8 | 12442.3 | 11425.1 | 12494.2 | 11487.5 | 12406.8 | 11734.3 | 12320.2 | 11834.7 | 12637.7 | 11704.6 | 12232.6 | 11567.1 | 10434.8 | 12339 | 11994.9 | 11487.6 | 12619.4 | 12358.5 | 11735 | 11619.1 | 12396.6 | 11520.6 | 11814.2 | 12424.8 | 11421.3 | 12557.9 | 11433.6 | 12352.2 | 11695.4 | 12387.9 | 11183.2 | 12476.1 | 11648.4 | 12391.5 | 11650.2 | 12429.6 | 11803 | 11520.7 | 12330 | 11642.1 | 11482.1 | 12339 | 12478.4 | 12307.9 | 11618.6 | 12422.7 | 11572 | 12147.3 | 11687.9 | 12119.5 | 10930.1 | 12273.5 | 11591.3 | 11726.9 | 11717.1 | 11606.5 | 10141 | 11565.3 | 10355.8 | 11599.2 | 11606.2 | 12708.9 | 11625.8 | 12769.1 | 11830.9 | 12640.7 | 11665.2 | 11813.9 | 11684.2 | 12534.9 | 12772.5 | 12704.9 | 12618.7 | 12694.2 | 12710.3 | 11907.9 | 12690.1 | 12699.9 | 12737.9 | 12777.8 | 12757.9 | 12819.4 | 11941.9 | 12802.7 | 11954.3 | 21.5766 | 21.3828 | 21.3022 | 21.1956 | 21.3094 | 21.4558 | 0 | 38.3 | 0 | 0 | 38.2 | 37.5 | 2.0322 | 1.9637 | 2.0023 | 1.9861 | 2.0071 | 1.9654 | 5.459 | 5.75 | 5.599 | 5 | 5.162 | 4.743 | 5.5266 | 5.5785 | 5.6562 | 5.6121 | 5.6003 | 5.6393 | 1.1345 | 1.1671 | 1.0337 | 1.3898 | 1.3041 | 1.1883 | 6.8642 | 6.9848 | 6.9138 | 6.9021 | 6.8892 | 6.8689 | 0.23451 | 0.26744 | 0.21811 | 0.24634 | 0.22717 | 0.26879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 547373 | 985 | 535270 | 1056 | 493420.4 | 1328.2 | 5.5266 | 5.5785 | 5.6562 | 5.6121 | 5.6003 | 5.6393 | 6.8642 | 6.9848 | 6.9138 | 6.9021 | 6.8892 | 6.8689 | 962000 | 2000 | 957000 | 2000 | 1911162 | 4933 | 1915000 | 1906229 | 11.25 | 5.6022 | 1.2029 | 6.9038 | 0.24373 | 21.47% | 3.53% | 21.3704 | 38 | 1.9928 | 5.2855 | 1927106.8 | 1910600 | 2263757.7141 | 84.4% | 32 | 293
2024-02-10 | 2024 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 335090.89 | 7:23 | 18:38 | 11748.4 | 12102.2 | 12020.3 | 12022.2 | 12067.8 | 12130 | 12112.4 | 12398.7 | 12056 | 12051.6 | 11935.7 | 12073.7 | 12037.5 | 12002.6 | 12039.2 | 12088.9 | 11964.5 | 12050 | 12075.8 | 12161.1 | 12058.5 | 12102.7 | 11933.8 | 12014.4 | 11895 | 10826.6 | 11934.8 | 11896 | 12041.7 | 11969.8 | 11904.4 | 12052.4 | 12480.7 | 12533.8 | 12469.3 | 12415.6 | 12159.8 | 12072 | 12103.5 | 11997 | 12668.7 | 11835.8 | 12510.7 | 11733.9 | 12268.3 | 13115 | 11665 | 12623.4 | 11456.9 | 11679.3 | 12147.9 | 11714.6 | 12408.4 | 11511.8 | 12367.1 | 11464 | 11490.2 | 12546.4 | 11505.4 | 12483.4 | 12417.5 | 11476.7 | 12221.4 | 11838.7 | 11963.9 | 11466.7 | 11941.9 | 12242.8 | 12426.4 | 11643.3 | 12344.2 | 11362.6 | 12074.1 | 12012.9 | 11454.8 | 12360.7 | 11389.1 | 12410.9 | 11448.5 | 12332.1 | 11656 | 12226.1 | 11752.7 | 12541.3 | 11639.5 | 12144.4 | 11501.1 | 10402 | 12262.4 | 11928.6 | 11444 | 12534.4 | 12281.3 | 11674.4 | 11567.8 | 12323 | 11485.2 | 11766.8 | 12346.4 | 11360 | 12481.2 | 11392.3 | 12279.9 | 11646.7 | 12301.2 | 11147.7 | 12391.1 | 11593.6 | 12314.7 | 11597.1 | 12349.6 | 11753.9 | 11458.5 | 12247.3 | 11592.2 | 11442.9 | 12263.4 | 12393.4 | 12227.4 | 11575.9 | 12334.5 | 11530.2 | 12077.7 | 11639.2 | 12066.6 | 10923.1 | 12200.4 | 11553.6 | 11684.6 | 11677.6 | 11571.5 | 10143.7 | 11517.8 | 10355.1 | 11577 | 11580.2 | 12613.1 | 11573.1 | 12681.5 | 11782.2 | 12554.5 | 11618.8 | 11767.9 | 11644.5 | 12455.1 | 12680 | 12618.9 | 12534.3 | 12606.6 | 12621.7 | 11850.4 | 12603 | 12613.5 | 12644.2 | 12690 | 12671.9 | 12725.7 | 11886.4 | 12718.9 | 11892 | 23.1348 | 22.5903 | 22.507 | 22.5952 | 22.3395 | 22.3094 | 0 | 34.7 | 0 | 0 | 34.6 | 34.3 | 3.758 | 3.8235 | 3.7194 | 3.8426 | 3.7507 | 3.7878 | 7.573 | 7.01 | 7.445 | 8.301 | 8.203 | 7.484 | 5.497 | 5.5338 | 5.608 | 5.5568 | 5.5542 | 5.5986 | 1.1487 | 1.1706 | 1.0438 | 1.3952 | 1.3042 | 1.187 | 6.7862 | 6.8909 | 6.8263 | 6.8221 | 6.7926 | 6.7744 | 0.2443 | 0.2805 | 0.22865 | 0.25723 | 0.2386 | 0.27868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 548332 | 987 | 536221 | 1058 | 495322.172 | 1333.133 | 5.497 | 5.5338 | 5.608 | 5.5568 | 5.5542 | 5.5986 | 6.7862 | 6.8909 | 6.8263 | 6.8221 | 6.7926 | 6.7744 | 959000 | 2000 | 951000 | 2000 | 1901772 | 4933 | 1906000 | 1896839 | 11.25 | 5.5581 | 1.2083 | 6.8154 | 0.25466 | 21.74% | 3.737% | 22.5794 | 34.5333 | 3.7804 | 7.6693 | 1917794.2 | 1901067 | 2244869.1602 | 84.68% | 50 | 0
2024-02-11 | 2024 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 335090.89 | 7:23 | 18:38 | 11744.1 | 12108.1 | 12035.6 | 12031.8 | 12096.7 | 12137.8 | 12117.1 | 12427.6 | 12071.1 | 12063.3 | 11946.9 | 12082.3 | 12051.4 | 12012.6 | 12048.6 | 12101.4 | 11976 | 12057.5 | 12081.8 | 12165.2 | 12067.4 | 12105.1 | 11927.3 | 12011.3 | 11884.1 | 10752.4 | 11926.1 | 11887 | 12055 | 11961.7 | 11900.6 | 12051 | 12458 | 12511.6 | 12251.6 | 12217.6 | 12163.6 | 12075.1 | 12105.2 | 11997.5 | 12680.3 | 11819 | 12518.3 | 11711.5 | 12269.2 | 13140.9 | 11650.3 | 12632.2 | 11431.8 | 11660.6 | 12149.2 | 11691.3 | 12414.9 | 11493.3 | 12367.7 | 11425.7 | 11448.1 | 12549.9 | 11471 | 12483 | 12416.8 | 11448.3 | 12224.2 | 11828.5 | 11947.9 | 11437.2 | 11929 | 12239.9 | 12431 | 11619.4 | 12343.4 | 11315 | 12066 | 12003.1 | 11420.9 | 12361.6 | 11342 | 12418.6 | 11409.6 | 12330.4 | 11633.9 | 12229.7 | 11735.5 | 12545.5 | 11606.6 | 12139.9 | 11481.6 | 10330.5 | 12259.6 | 11912.3 | 11403.1 | 12535.8 | 12283.5 | 11662.7 | 11552.6 | 12319.6 | 11438.2 | 11740.2 | 12344.2 | 11319.5 | 12478.6 | 11349.8 | 12271.2 | 11616.5 | 12303 | 11090.3 | 12392.4 | 11566.1 | 12316.4 | 11577.9 | 12351.9 | 11723.3 | 11414.1 | 12243.2 | 11561 | 11394.1 | 12257.7 | 12393.5 | 12215.4 | 11544 | 12330.9 | 11495.9 | 12068.9 | 11605.6 | 12051.2 | 10848.1 | 12183.4 | 11517.9 | 11651.1 | 11641.9 | 11532.7 | 10055.7 | 11482.8 | 10284.7 | 11545 | 11550.9 | 12611.4 | 11542.7 | 12682.6 | 11758.5 | 12558.8 | 11594.3 | 11740.9 | 11619.3 | 12450.3 | 12678.4 | 12610.5 | 12526.4 | 12596.5 | 12618.9 | 11830.6 | 12604 | 12617.5 | 12641.6 | 12689.8 | 12674 | 12729.1 | 11860.4 | 12715.9 | 11858.8 | 22.6139 | 22.2245 | 22.2172 | 22.1095 | 22.1602 | 22.1303 | 0 | 35.6 | 0 | 0 | 35.7 | 35.3 | 3.1766 | 3.0376 | 3.1396 | 3.1208 | 3.0575 | 2.0563 | 6.609 | 6.475 | 6.147 | 6.208 | 5.92 | 6.229 | 5.4974 | 5.5317 | 5.6029 | 5.5577 | 5.5503 | 5.5946 | 1.1458 | 1.178 | 1.0435 | 1.3967 | 1.3111 | 1.1938 | 6.7621 | 6.8633 | 6.7926 | 6.792 | 6.7615 | 6.7426 | 0.24638 | 0.28432 | 0.2312 | 0.25986 | 0.24171 | 0.28225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 549289 | 988 | 537172 | 1060 | 497221.839 | 1338 | 5.4974 | 5.5317 | 5.6029 | 5.5577 | 5.5503 | 5.5946 | 6.7621 | 6.8633 | 6.7926 | 6.792 | 6.7615 | 6.7426 | 957000 | 1000 | 951000 | 2000 | 1899667 | 4867 | 1905000 | 1894800 | 11.25 | 5.5558 | 1.2115 | 6.7857 | 0.25762 | 21.81% | 3.797% | 22.2426 | 35.5333 | 2.9314 | 6.2647 | 1915399.9 | 1898934 | 2228229.7468 | 85.22% | 45 | 354
2024-02-12 | 2024 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 335090.89 | 7:26 | 18:35 | 9564.6 | 9899.2 | 9828 | 9793.8 | 9866.3 | 9923.6 | 9954.6 | 10241 | 9888.4 | 9894.3 | 9766.5 | 9899.1 | 9842.3 | 9831.1 | 9843.3 | 9900.4 | 9781.6 | 9853.7 | 9882.3 | 9937.1 | 9884.9 | 9896 | 9737.2 | 9811.1 | 9697.5 | 8744.4 | 9725.7 | 9693 | 9899.4 | 9797.6 | 9725.7 | 9884.7 | 10033.2 | 10072.2 | 9909.6 | 9866 | 9972.6 | 9886.2 | 9924.1 | 9816.2 | 10382 | 9532.1 | 10280.7 | 9424.8 | 10002.4 | 10870.2 | 9411.5 | 10376.8 | 9268.1 | 9478.1 | 9947.5 | 9510.3 | 10210.4 | 9316 | 10190 | 9288.5 | 9295.7 | 10372.1 | 9299.7 | 10286.4 | 10230.4 | 9292.8 | 10021.7 | 9624 | 9737.1 | 9228.6 | 9713.9 | 10036 | 10279 | 9417.3 | 10146.7 | 9158.6 | 9917.6 | 9795 | 9272 | 10171.3 | 9168.2 | 10253.8 | 9255.6 | 10155.1 | 9450.3 | 10057.6 | 9566 | 10360.5 | 9438 | 9965 | 9336.8 | 8452.9 | 10094.4 | 9770.6 | 9217.1 | 10333.8 | 10075.9 | 9459.7 | 9374.4 | 10139.1 | 9287.8 | 9573.9 | 10198 | 9209.2 | 10280.7 | 9195.1 | 10043.7 | 9421.5 | 10101.9 | 8978.1 | 10176.4 | 9359.2 | 10071.3 | 9358.8 | 10106.3 | 9479.6 | 9311.2 | 10139.6 | 9406.8 | 9272.5 | 10140.8 | 10284.3 | 10070.5 | 9454.4 | 10215.8 | 9380.6 | 9897.3 | 9408.7 | 9860.5 | 8883.3 | 10039.6 | 9409.2 | 9545.2 | 9568.5 | 9438.6 | 8303.5 | 9427.4 | 8496.1 | 9570.7 | 9586 | 10660.1 | 9594.9 | 10755.6 | 9789.1 | 10639 | 9660.3 | 9796.5 | 9672.9 | 10510.4 | 10770.1 | 10660.5 | 10592.3 | 10625.4 | 10664.4 | 9879.8 | 10677.5 | 10694.2 | 10733.2 | 10804.6 | 10773.8 | 10799.2 | 9917.3 | 10755.5 | 9909.1 | 21.4132 | 21.1572 | 21.2036 | 21.1527 | 21.1664 | 21.2128 | 0 | 32.1 | 0 | 0 | 32.1 | 32.4 | 2.7673 | 2.8415 | 2.8054 | 2.9436 | 2.7755 | 1.348 | 5.026 | 6.672 | 5.223 | 5.56 | 5.382 | 5.163 | 4.6217 | 4.65 | 4.6961 | 4.6772 | 4.6888 | 4.802 | 0.9257 | 1.0106 | 0.83582 | 1.132 | 1.1004 | 1.0597 | 5.4143 | 5.4877 | 5.4166 | 5.4068 | 5.4397 | 5.5468 | 0.23783 | 0.2803 | 0.22818 | 0.26264 | 0.24324 | 0.27286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550072 | 990 | 537958 | 1061 | 498785.106 | 1342.933 | 4.6217 | 4.65 | 4.6961 | 4.6772 | 4.6888 | 4.802 | 5.4143 | 5.4877 | 5.4166 | 5.4068 | 5.4397 | 5.5468 | 783000 | 2000 | 786000 | 1000 | 1563267 | 4933 | 1566000 | 1558334 | 11.15 | 4.6893 | 1.0107 | 5.452 | 0.25417 | 21.55% | 4.662% | 21.2177 | 32.2 | 2.5802 | 5.5043 | 1573366.9 | 1561800 | 1812802.0608 | 86.15% | 75 | 31009
2024-02-13 | 2024 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 335090.89 | 7:22 | 18:32 | 9574.9 | 9928.7 | 9889 | 9895.9 | 9933.8 | 9992.5 | 9954.7 | 10317.9 | 9954.4 | 9935.6 | 9770.8 | 9932.1 | 9852.2 | 9846.6 | 9857.6 | 9910.7 | 9790.5 | 9860.2 | 9888.8 | 9939 | 9896.5 | 9903.6 | 9723.2 | 9807.6 | 9664.9 | 8613.5 | 9705.9 | 9673.9 | 9915.5 | 9802.4 | 9692.9 | 9879.3 | 10005.7 | 10057.1 | 9993.6 | 9948.4 | 9987 | 9884.9 | 9935.2 | 9840.5 | 10523.1 | 9533.3 | 10375.9 | 9411.3 | 10024 | 11043.2 | 9370 | 10508.8 | 9190.8 | 9413.6 | 9961.8 | 9441.2 | 10260 | 9255.8 | 10233.4 | 9210.8 | 9254.3 | 10478 | 9228.1 | 10314.7 | 10297.6 | 9230.1 | 10085.5 | 9629.6 | 9801.1 | 9225.1 | 9761.4 | 10104.6 | 10400.5 | 9409.2 | 10233.4 | 9092.8 | 9983.9 | 9828 | 9267.4 | 10289.5 | 9173.2 | 10376.1 | 9252.8 | 10275.4 | 9439.9 | 10106.5 | 9561.1 | 10464 | 9419.3 | 10006.5 | 9315.5 | 8347.2 | 10162.4 | 9806.6 | 9163.8 | 10440.4 | 10118.9 | 9407.8 | 9325.8 | 10212.6 | 9224.3 | 9520.7 | 10250.7 | 9118.6 | 10364.1 | 9105.9 | 10075.7 | 9347.4 | 10167.7 | 8872.2 | 10232.2 | 9290.5 | 10117.3 | 9306.4 | 10156.8 | 9414.1 | 9166.7 | 10077.6 | 9302.4 | 9128.3 | 10125.3 | 10232.5 | 10050.1 | 9302 | 10172.6 | 9225.6 | 9868.4 | 9299.9 | 9820.7 | 8673.6 | 9976.8 | 9249.9 | 9403.1 | 9432.6 | 9286.9 | 8082.2 | 9282.4 | 8283.6 | 9435.4 | 9445.9 | 10656.6 | 9418.1 | 10748.2 | 9656.4 | 10617.3 | 9534.8 | 9677.1 | 9561.3 | 10441.4 | 10747.2 | 10608.1 | 10550.5 | 10605.3 | 10646.4 | 9749 | 10655 | 10649.2 | 10704 | 10803.8 | 10759.9 | 10782.8 | 9782.3 | 10729.8 | 9765.9 | 20.3932 | 20.1029 | 20.2389 | 20.0463 | 20.032 | 20.0822 | 0 | 29.5 | 0 | 0 | 29.2 | 29.2 | 3.5995 | 3.5986 | 3.6125 | 3.6973 | 3.5783 | 2.9265 | 6.44 | 6.668 | 6.257 | 6.966 | 6.511 | 6.283 | 4.5258 | 4.5416 | 4.554 | 4.529 | 4.543 | 4.6436 | 0.96608 | 0.93891 | 0.87049 | 1.175 | 1.0554 | 0.94752 | 5.2633 | 5.3058 | 5.2716 | 5.3409 | 5.2384 | 5.268 | 0.24051 | 0.28459 | 0.23312 | 0.27076 | 0.24937 | 0.27846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550857 | 992 | 538740 | 1063 | 500345.506 | 1347.933 | 4.5258 | 4.5416 | 4.554 | 4.529 | 4.543 | 4.6436 | 5.2633 | 5.3058 | 5.2716 | 5.3409 | 5.2384 | 5.268 | 785000 | 2000 | 782000 | 2000 | 1560400 | 5000 | 1563000 | 1555400 | 11.1667 | 4.5562 | 0.99223 | 5.2813 | 0.25947 | 21.78% | 4.913% | 20.1492 | 29.3 | 3.5021 | 6.5208 | 1570744.6 | 1559400 | 1801625.3531 | 86.56% | 55 | 31285
2024-02-14 | 2024 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 335090.89 | 7:22 | 18:39 | 11255.6 | 11617.7 | 11574.8 | 11569.2 | 11636.7 | 11679.7 | 11654 | 11957.4 | 11602.7 | 11560.4 | 11477.6 | 11612.4 | 11579.3 | 11551.3 | 11573.5 | 11637.2 | 11510 | 11591.9 | 11619.1 | 11688.6 | 11612.4 | 11642.9 | 11466.9 | 11551.8 | 11427.2 | 10287.9 | 11472.3 | 11440.1 | 11634.2 | 11517.4 | 11439.3 | 11595.1 | 11941.8 | 11992.7 | 11934.6 | 11889.5 | 11694.9 | 11610.6 | 11641.3 | 11540.3 | 12212.9 | 11366.4 | 12056.6 | 11250.7 | 11800 | 12667.7 | 11166.5 | 12169.3 | 10952.4 | 11185.5 | 11687 | 11212.8 | 11956.5 | 11038.2 | 11907.7 | 10971.3 | 10974.7 | 12087 | 10985.1 | 11994.6 | 11955 | 10974.7 | 11750.3 | 11342.7 | 11480.8 | 10947.9 | 11462 | 11775.3 | 11974.2 | 11143 | 11881.8 | 10824.3 | 11621.6 | 11532.3 | 10955.8 | 11897.1 | 10874.8 | 11953 | 10936.7 | 11861.2 | 11176.6 | 11782.1 | 11288.7 | 12082.3 | 11142.9 | 11688.8 | 11032.7 | 9890.3 | 11826.3 | 11477.6 | 10936.1 | 12100 | 11835.8 | 11217.5 | 11116.1 | 11887.1 | 10984 | 11285.9 | 11905.1 | 10888.8 | 12036.4 | 10876.9 | 11814.5 | 11144.7 | 11856.9 | 10604.1 | 11935.7 | 11079.3 | 11859.6 | 11104.1 | 11889.2 | 11240.3 | 10955.1 | 11796.4 | 11101.5 | 10918.5 | 11814.1 | 11949.7 | 11766.4 | 11094.1 | 11889.7 | 11043.9 | 11618.1 | 11124.4 | 11592.9 | 10379.1 | 11739.8 | 11061.2 | 11189 | 11192.5 | 11082.2 | 9642.8 | 11027.9 | 9846.6 | 11102.2 | 11104.4 | 12160.2 | 11091.6 | 12213.2 | 11297.7 | 12120.1 | 11147.5 | 11297.4 | 11193.5 | 11966.3 | 12208.4 | 12146.6 | 12072.6 | 12141.3 | 12162.9 | 11363.7 | 12127.5 | 12155.7 | 12167.5 | 12239 | 12206.9 | 12243.8 | 11378.8 | 12239.7 | 11388.1 | 21.3731 | 21.1497 | 21.4137 | 21.1292 | 21.1238 | 21.0262 | 0 | 31.2 | 0 | 0 | 31 | 30.8 | 4.0063 | 4.1487 | 4.095 | 4.2082 | 4.1525 | 3.7223 | 7.047 | 8.013 | 6.832 | 8.437 | 8.699 | 7.706 | 5.2654 | 5.3101 | 5.3391 | 5.2676 | 5.3264 | 5.3574 | 1.1305 | 1.1702 | 1.0289 | 1.4075 | 1.3059 | 1.1712 | 6.3632 | 6.467 | 6.3942 | 6.4077 | 6.3806 | 6.3432 | 0.25398 | 0.29483 | 0.24013 | 0.2709 | 0.25457 | 0.28956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 551778 | 993 | 539654 | 1065 | 502172.706 | 1352.8 | 5.2654 | 5.3101 | 5.3391 | 5.2676 | 5.3264 | 5.3574 | 6.3632 | 6.467 | 6.3942 | 6.4077 | 6.3806 | 6.3432 | 921000 | 1000 | 914000 | 2000 | 1827200 | 4867 | 1832000 | 1822333 | 11.2833 | 5.311 | 1.2024 | 6.3927 | 0.26733 | 22.64% | 4.182% | 21.2026 | 31 | 4.0555 | 7.789 | 1841818.6 | 1826467 | 2128676.6982 | 85.8% | 38 | 0
2024-02-15 | 2024 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 335090.89 | 7:20 | 18:40 | 11508.4 | 11907.6 | 11855.5 | 11843.8 | 11916.4 | 11978.1 | 11956.1 | 12252.8 | 11872 | 11826.6 | 11743.1 | 11882.2 | 11845.4 | 11813.4 | 11839 | 11907.3 | 11783.9 | 11875.6 | 11901.2 | 11971.8 | 11894.4 | 11923.3 | 11746.7 | 11831.8 | 11690.3 | 10477.1 | 11732.7 | 11702 | 11915.1 | 11797.9 | 11710.4 | 11868.9 | 12201.2 | 12257.8 | 12154.5 | 12106.2 | 11980.5 | 11892 | 11918.2 | 11806.4 | 12537.7 | 11635.6 | 12366.9 | 11509.6 | 12081.2 | 13016.3 | 11441.2 | 12508.1 | 11165.1 | 11414 | 11959.3 | 11462.1 | 12243.8 | 11260.3 | 12182.6 | 11176.2 | 11182.8 | 12372 | 11190.1 | 12305.2 | 12229.1 | 11181.9 | 12018.5 | 11593.4 | 11742.2 | 11169.3 | 11705.3 | 12032.9 | 12252.6 | 11361.1 | 12154.2 | 10995.4 | 11866.4 | 11773.4 | 11162 | 12164.9 | 11062.2 | 12231.2 | 11141.1 | 12131.1 | 11378.5 | 12035.1 | 11485.5 | 12362.4 | 11363.1 | 11933.3 | 11256.1 | 10041.7 | 12073.9 | 11717.8 | 11112.9 | 12367.4 | 12091.7 | 11435.9 | 11322.1 | 12152.9 | 11195 | 11508.7 | 12183.3 | 11090.5 | 12309.7 | 11060.6 | 12082.4 | 11359.2 | 12130 | 10780 | 12209.2 | 11315.7 | 12123.4 | 11315.7 | 12163.8 | 11483.1 | 11147.4 | 12026.6 | 11309.7 | 11097.4 | 12066.6 | 12193.2 | 12029.3 | 11274.3 | 12133.6 | 11235.2 | 11869.3 | 11354.7 | 11842.7 | 10525.5 | 11971.9 | 11236 | 11366.7 | 11363.7 | 11257.1 | 9754.5 | 11194.5 | 9965.8 | 11247.6 | 11257 | 12409.3 | 11270.5 | 12461.1 | 11482.4 | 12364.3 | 11326.1 | 11490.2 | 11359.3 | 12205.2 | 12464.4 | 12402.6 | 12321 | 12393.4 | 12411 | 11553.7 | 12377.6 | 12406.2 | 12420.8 | 12486.5 | 12456.8 | 12501 | 11575.9 | 12504.7 | 11589.8 | 23.81 | 23.45 | 23.4 | 23.4 | 23.31 | 23.22 | 0 | 36.9 | 0 | 0 | 37.1 | 36.8 | 2.79 | 2.8 | 2.79 | 2.82 | 2.78 | 2.35 | 5.95 | 5.87 | 6.02 | 5.79 | 6.15 | 5.73 | 5.49 | 5.53 | 5.58 | 5.47 | 5.54 | 5.58 | 1.17 | 1.21 | 1.06 | 1.46 | 1.33 | 1.2 | 6.65 | 6.75 | 6.71 | 6.69 | 6.64 | 6.62 | 0.25 | 0.3 | 0.24 | 0.27 | 0.25 | 0.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 552720 | 995 | 540586 | 1067 | 504038.373 | 1357.6 | 5.49 | 5.53 | 5.58 | 5.47 | 5.54 | 5.58 | 6.65 | 6.75 | 6.71 | 6.69 | 6.64 | 6.62 | 942000 | 2000 | 932000 | 2000 | 1865667 | 4800 | 1870000 | 1860867 | 11.3333 | 5.5317 | 1.2383 | 6.6767 | 0.26667 | 22.39% | 3.994% | 23.4317 | 36.9333 | 2.7217 | 5.9183 | 1880460.6 | 1864667 | 2181387.4221 | 85.48% | 37 | 0
2024-02-16 | 2024 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 335090.89 | 7:22 | 18:38 | 10940.8 | 11386.9 | 11345.2 | 11325.2 | 11396.5 | 11465.3 | 11449.8 | 11812.1 | 11374.5 | 11338 | 11231.2 | 11382.8 | 11326.9 | 11313.9 | 11301.2 | 11385.5 | 11265.6 | 11363.3 | 11391.7 | 11452.5 | 11388.9 | 11409.9 | 11208.8 | 11311.4 | 11146.9 | 9840.8 | 11185.7 | 11153.7 | 11394.9 | 11281.4 | 11134.4 | 11325.1 | 11540.9 | 11601.6 | 11538.7 | 11482.5 | 11457.5 | 11361.3 | 11400.3 | 11276.4 | 12098.5 | 11088.3 | 11929.3 | 10934.8 | 11564 | 12562.4 | 10848.1 | 12060.9 | 10511.9 | 10788.4 | 11434.1 | 10859.4 | 11745.9 | 10610.9 | 11676.5 | 10517.3 | 10527.9 | 11876.5 | 10529.7 | 11805.9 | 11722.2 | 10531.7 | 11489.4 | 11013.3 | 11193.9 | 10528.3 | 11147.3 | 11509.2 | 11768.3 | 10751.5 | 11642.6 | 10351.8 | 11340.7 | 11224.4 | 10519.5 | 11671.6 | 10416.8 | 11739.3 | 10494.6 | 11640.9 | 10790 | 11516.2 | 10907.5 | 11865.1 | 10771.1 | 11399.8 | 10683.2 | 9460.8 | 11575.4 | 11169.1 | 10487.1 | 11875.7 | 11572.2 | 10817.7 | 10701.6 | 11647.8 | 10577.3 | 10933.9 | 11697.2 | 10476.6 | 11807.9 | 10451.2 | 11562.2 | 10747.5 | 11621.2 | 10161 | 11701.3 | 10711.8 | 11599.3 | 10720.5 | 11650.6 | 10849.7 | 10510.7 | 11515.6 | 10689 | 10457.7 | 11570.1 | 11704 | 11509.7 | 10657.5 | 11635.1 | 10598.8 | 11331.7 | 10701.4 | 11276.7 | 9913.2 | 11441 | 10597.5 | 10748.2 | 10773.9 | 10614.6 | 9178.2 | 10554.9 | 9358.5 | 10647.6 | 10669 | 11996.7 | 10720.6 | 12061.3 | 10959.1 | 11954.3 | 10786.4 | 10966 | 10809.3 | 11782.7 | 12083.7 | 11985.8 | 11901.3 | 11971.8 | 11997.5 | 11043.7 | 11971.8 | 11996.9 | 12019.4 | 12110.2 | 12076.9 | 12107.7 | 11071.7 | 12086.3 | 11081.2 | 25.5581 | 25.2774 | 25.1197 | 25.1821 | 25.1338 | 25.0541 | 0 | 38.2 | 0 | 0 | 38.3 | 37.9 | 2.7704 | 2.6799 | 2.7322 | 2.7264 | 2.7609 | 2.8244 | 5.942 | 6.129 | 5.996 | 6.33 | 6.187 | 6.092 | 5.2159 | 5.2487 | 5.3024 | 5.2137 | 5.2665 | 5.3208 | 1.0872 | 1.1502 | 1.0068 | 1.3803 | 1.2514 | 1.158 | 6.2738 | 6.351 | 6.3148 | 6.3154 | 6.2706 | 6.268 | 0.24639 | 0.28768 | 0.23711 | 0.2663 | 0.24793 | 0.283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 553619 | 997 | 541475 | 1068 | 505818.973 | 1362.333 | 5.2159 | 5.2487 | 5.3024 | 5.2137 | 5.2665 | 5.3208 | 6.2738 | 6.351 | 6.3148 | 6.3154 | 6.2706 | 6.268 | 899000 | 2000 | 889000 | 1000 | 1780600 | 4733 | 1785000 | 1775867 | 11.2667 | 5.2613 | 1.1723 | 6.2989 | 0.2614 | 22.28% | 4.15% | 25.2209 | 38.1333 | 2.749 | 6.1127 | 1794064.4 | 1779867 | 2054611.4101 | 86.63% | 39 | 0
2024-02-17 | 2024 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 335090.89 | 7:19 | 18:42 | 11345 | 11760.2 | 11715.7 | 11685.4 | 11773.9 | 11831.9 | 11799.7 | 12166.9 | 11751 | 11719.9 | 11613.8 | 11763.5 | 11713.9 | 11698.3 | 11683.3 | 11759.1 | 11642.4 | 11730.7 | 11782.6 | 11850.4 | 11771.4 | 11799.5 | 11597.4 | 11691.7 | 11556 | 10319.5 | 11588.4 | 11550.9 | 11792.3 | 11670.8 | 11578.6 | 11758.7 | 12042.9 | 12093.4 | 12023.4 | 11978.8 | 11883 | 11778.8 | 11796.7 | 11697.9 | 12458.4 | 11454.8 | 12278.5 | 11332.2 | 11928.3 | 12905.1 | 11238 | 12418.4 | 10987.5 | 11241.9 | 11829.6 | 11299.1 | 12143 | 11063.9 | 12097.5 | 11015.1 | 11009.3 | 12300.3 | 11019.5 | 12226.9 | 12135.4 | 11008.2 | 11914.4 | 11428.9 | 11619.9 | 11024.7 | 11581.2 | 11948.2 | 12184.1 | 11224.6 | 12077.6 | 10856 | 11745.1 | 11654.1 | 10991.9 | 12096.6 | 10906.2 | 12147.9 | 10971.5 | 12047.5 | 11243.4 | 11951.6 | 11358.1 | 12309.9 | 11230.5 | 11845.4 | 11135.9 | 9935.5 | 12004.2 | 11598.9 | 10990.4 | 12332.4 | 12024.2 | 11302.8 | 11192 | 12081.5 | 11048.3 | 11395.5 | 12131.5 | 10963.1 | 12245.1 | 10943.4 | 12000 | 11221.7 | 12044.3 | 10657.5 | 12127.7 | 11184 | 12018.3 | 11152 | 12074.7 | 11326.7 | 11000.3 | 11945.3 | 11158 | 10956.8 | 11983.2 | 12117.4 | 11934.9 | 11119.7 | 12056.5 | 11081.3 | 11764 | 11190.2 | 11710.9 | 10396.3 | 11873.5 | 11078.5 | 11200.7 | 11208.1 | 11065.9 | 9602.8 | 11006.8 | 9782.1 | 11133 | 11139.6 | 12410.7 | 11175.3 | 12478.3 | 11391.9 | 12354.3 | 11224.6 | 11390.9 | 11255.2 | 12193.1 | 12469.8 | 12392.8 | 12305 | 12386.1 | 12414.6 | 11479.2 | 12389.7 | 12387.5 | 12407.8 | 12481.8 | 12454.3 | 12495.8 | 11486.8 | 12493.7 | 11504 | 26.3287 | 26.3236 | 26.4689 | 26.1453 | 26.3079 | 26.2779 | 0 | 41.4 | 0 | 0 | 41.2 | 40.9 | 2.1589 | 2.0517 | 2.0081 | 2.0436 | 2.0276 | 2.1327 | 4.575 | 4.779 | 4.546 | 4.687 | 4.288 | 5.702 | 5.4906 | 5.552 | 5.5828 | 5.501 | 5.5647 | 5.6024 | 1.1608 | 1.2063 | 1.0546 | 1.4532 | 1.3098 | 1.206 | 6.6258 | 6.7551 | 6.6746 | 6.7025 | 6.661 | 6.6296 | 0.24303 | 0.28394 | 0.23229 | 0.26005 | 0.24689 | 0.28162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 554550 | 998 | 542399 | 1070 | 507666.906 | 1366.933 | 5.4906 | 5.552 | 5.5828 | 5.501 | 5.5647 | 5.6024 | 6.6258 | 6.7551 | 6.6746 | 6.7025 | 6.661 | 6.6296 | 931000 | 1000 | 924000 | 2000 | 1847933 | 4600 | 1852000 | 1843333 | 11.3833 | 5.5489 | 1.2318 | 6.6748 | 0.25797 | 22.2% | 3.865% | 26.3087 | 41.1667 | 2.0704 | 4.7628 | 1862568.5 | 1846666 | 2154319.4617 | 85.72% | 41 | 0
2024-02-18 | 2024 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 335090.89 | 7:10 | 18:44 | 8498.3 | 8875.4 | 8830.7 | 8803.1 | 8900.4 | 8950.7 | 8919 | 9232.3 | 8864.7 | 8841.8 | 8742.2 | 8878.2 | 8821.8 | 8807.3 | 8814.1 | 8853.8 | 11474.1 | 11547.3 | 11596.9 | 11649.4 | 11603 | 11607.8 | 11403.4 | 11498.4 | 11311.9 | 9967.3 | 11340.8 | 11313.6 | 11582.6 | 11491.8 | 11376 | 11572.7 | 11659.9 | 11695.1 | 11627.8 | 11590 | 11666.9 | 11551.9 | 11620.9 | 11511.9 | 12238.4 | 11215.3 | 12108.7 | 11050.6 | 11774.1 | 12667.1 | 10980.7 | 12214.3 | 10433.2 | 10955.7 | 11608.9 | 11023.5 | 11913.7 | 10748.7 | 11910.2 | 10702.8 | 10702.3 | 12080.1 | 10711.4 | 12001.3 | 11875 | 10695.8 | 11679.7 | 11189.6 | 11443.7 | 10738.4 | 11370.2 | 11752 | 12016.5 | 10939.4 | 11891.4 | 10505 | 11583.9 | 11289.3 | 10704.9 | 11882.6 | 10565.4 | 11965.6 | 10668.5 | 11826.3 | 10968.8 | 11718.1 | 11095.6 | 12089.9 | 10967.9 | 11652.6 | 10894.3 | 9641.7 | 11763.5 | 11409.2 | 10655.6 | 12108.6 | 11819.8 | 11032.2 | 10930.8 | 11903.6 | 10734.5 | 11132.6 | 11931.7 | 10627.6 | 12033.1 | 10614.3 | 11817.9 | 10927.7 | 11872.1 | 10327.5 | 11956.3 | 10893.5 | 11849 | 10886.5 | 11939.6 | 11059.4 | 10670.8 | 11747 | 10867.6 | 10643 | 11817.7 | 11921.4 | 11792.1 | 10828 | 11856.3 | 10769.2 | 11592.4 | 10895.6 | 11482 | 10101.1 | 11715.8 | 10766.6 | 10943.9 | 10951.2 | 10772.3 | 9333.8 | 10768.3 | 9513.5 | 10893.3 | 10879.8 | 12233.2 | 10909.1 | 12318.3 | 11180.4 | 12181.8 | 10992.3 | 11207 | 11019.7 | 10087.8 | 10335.5 | 10272 | 10214.4 | 10246.5 | 10291 | 9412 | 10313.7 | 10239.3 | 10286.3 | 10382.4 | 10341.9 | 10326.3 | 9391.6 | 10396.5 | 9436.4 | 26.5837 | 26.5756 | 26.6637 | 26.2307 | 26.4574 | 26.7593 | 0 | 36.9 | 0 | 0 | 37 | 37.6 | 7.2033 | 7.3798 | 7.0438 | 7.4587 | 7.1407 | 7.667 | 13.974 | 13.461 | 13.617 | 13.46 | 13.233 | 14.12 | 5.3241 | 5.3654 | 5.3845 | 5.3204 | 5.3991 | 5.4242 | 1.1692 | 1.1848 | 1.0522 | 1.4406 | 1.316 | 1.1717 | 6.2805 | 6.3705 | 6.2797 | 6.3426 | 6.3203 | 6.2658 | 0.26479 | 0.31535 | 0.2567 | 0.28878 | 0.27716 | 0.30812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555419 | 1000 | 543274 | 1072 | 509403.173 | 1371.4 | 5.3241 | 5.3654 | 5.3845 | 5.3204 | 5.3991 | 5.4242 | 6.2805 | 6.3705 | 6.2797 | 6.3426 | 6.3203 | 6.2658 | 869000 | 2000 | 875000 | 2000 | 1736267 | 4467 | 1740000 | 1731800 | 11.5667 | 5.3696 | 1.2224 | 6.3099 | 0.28515 | 22.77% | 4.519% | 26.5451 | 37.1667 | 7.3156 | 13.6442 | 1751313 | 1734733 | 2084348.4213 | 83.23% | 44 | 0
2024-02-19 | 2024 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 335090.89 | 7:26 | 18:42 | 9755.5 | 10198.3 | 10221.7 | 10165.2 | 10299.2 | 10365.3 | 10300.3 | 10616.9 | 10122.8 | 10089.2 | 10046.7 | 10153.2 | 10221.2 | 10131.4 | 10215.9 | 10275.1 | 10153.9 | 10218 | 10271.3 | 10323.7 | 10240.3 | 10269 | 10083.9 | 10167.7 | 10062 | 9000.3 | 10068.2 | 10059.8 | 10274.9 | 10153.1 | 10088.5 | 10264 | 10651.4 | 10669 | 10638.1 | 10610 | 10335.6 | 10247.2 | 10273.6 | 10209 | 10671.7 | 9909 | 10575.2 | 9788.9 | 10312.2 | 11054.6 | 9719.6 | 10660.5 | 9510.4 | 9721.1 | 10259.2 | 9763.1 | 10560.3 | 9649.2 | 10440.9 | 9552.2 | 9491.3 | 10592.8 | 9506.5 | 10525.4 | 10437.8 | 9477.1 | 10275.7 | 9853 | 10037.5 | 9554.1 | 10008.5 | 10359.7 | 10533.1 | 9731.6 | 10477.9 | 9433.5 | 10173.3 | 10036.1 | 9522.2 | 10520.3 | 9472 | 10535.3 | 9532.2 | 10477.5 | 9793.1 | 10396.4 | 9910.8 | 10687.9 | 9777.3 | 10325 | 9664.7 | 8704 | 10397.8 | 10089.3 | 9450 | 10587.5 | 10334.3 | 9718.5 | 9646 | 10403.4 | 9542 | 9838.9 | 10475.4 | 9434.7 | 10501.7 | 9409.9 | 10307.8 | 9648.3 | 10358.1 | 9168.1 | 10419.1 | 9593.2 | 10343 | 9601.2 | 10397.8 | 9747.7 | 9497.2 | 10343.8 | 9592.5 | 9438.4 | 10333.8 | 10473 | 10276.5 | 9614.3 | 10393.1 | 9536.6 | 10110.4 | 9602.3 | 10076.7 | 9013.8 | 10232.7 | 9552.1 | 9742.6 | 9759.8 | 9573.9 | 8423.2 | 9632 | 8642.2 | 9749.1 | 9718 | 10739.5 | 9720.2 | 10741.5 | 9890.1 | 10705.6 | 9746.9 | 9919.8 | 9786.7 | 9138.5 | 9329 | 9320.6 | 9271 | 9325.4 | 9366.1 | 8645.9 | 9297.2 | 9456.1 | 9460.6 | 9488 | 9462.6 | 9477 | 8764.2 | 9550.9 | 8818.7 | 27.3194 | 27.0008 | 26.9855 | 27.0026 | 27.0255 | 27.1658 | 0 | 36.7 | 0 | 0 | 36.5 | 36.7 | 9.1283 | 9.2282 | 9.1351 | 9.0471 | 9.117 | 9.0959 | 13.268 | 13.991 | 12.895 | 13.78 | 12.917 | 12.736 | 4.8979 | 4.9631 | 4.9414 | 4.8679 | 4.9441 | 4.9639 | 1.0345 | 1.128 | 0.93529 | 1.3005 | 1.2215 | 1.1131 | 5.7126 | 5.8301 | 5.6779 | 5.7017 | 5.6951 | 5.6907 | 0.23925 | 0.28652 | 0.23266 | 0.25983 | 0.25184 | 0.27847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 556227 | 1001 | 544052 | 1073 | 510984.107 | 1376.067 | 4.8979 | 4.9631 | 4.9414 | 4.8679 | 4.9441 | 4.9639 | 5.7126 | 5.8301 | 5.6779 | 5.7017 | 5.6951 | 5.6907 | 808000 | 1000 | 778000 | 1000 | 1580934 | 4667 | 1584000 | 1576267 | 11.2667 | 4.9297 | 1.1222 | 5.718 | 0.25809 | 22.76% | 4.514% | 27.0832 | 36.6333 | 9.1253 | 13.2645 | 1592645.9 | 1304266 | 1533473.4039 | 85.05% | 47 | 9081
2024-02-20 | 2024 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 335090.89 | 7:25 | 18:42 | 10131.3 | 10619.2 | 10595.3 | 10528 | 10684.6 | 10704.3 | 10664.5 | 11146 | 10608.8 | 10600.2 | 10426.6 | 10620.6 | 10545.2 | 10535.4 | 10585.9 | 10642.6 | 10531.5 | 10631 | 10663.2 | 10700.8 | 10669 | 10662.3 | 10417.1 | 10538 | 10366.5 | 9101.1 | 10384.8 | 10348.1 | 10650.1 | 10537.8 | 10398 | 10632.5 | 10690.3 | 10736.9 | 10663.2 | 10610.3 | 10747.9 | 10610.8 | 10666.6 | 10573.5 | 11580.7 | 10304.4 | 11409.4 | 10152.9 | 10814.7 | 12122.5 | 10052.2 | 11549.6 | 9744.5 | 10000.8 | 10709.1 | 10054.1 | 11093.2 | 9799.2 | 11032.9 | 9769.6 | 9749.5 | 11291.1 | 9766.2 | 11183.8 | 11067.5 | 9756.3 | 10786.3 | 10188.8 | 10414.7 | 9750.1 | 10363.5 | 10849.5 | 11180.2 | 9973.6 | 10994.2 | 9592.6 | 10614.2 | 10462 | 9741.9 | 11037.4 | 9631.2 | 11128.9 | 9708.3 | 10956.4 | 10010.7 | 10850.3 | 10146.1 | 11308.3 | 9992.6 | 10717.4 | 9898.2 | 8775.9 | 10890.4 | 10457.2 | 9715.9 | 11329.5 | 10959.6 | 10078 | 9975.7 | 11035.6 | 9782.7 | 10175.7 | 11153.2 | 9717.9 | 11262.6 | 9730.9 | 10929.4 | 9991.5 | 11059 | 9464.4 | 11128.9 | 9986 | 10959.6 | 9959.7 | 11045.9 | 10133.1 | 9780 | 10884.9 | 9951.9 | 9719.1 | 10965.1 | 11129.9 | 10881.9 | 9938.1 | 11061.8 | 9863.9 | 10664.8 | 9971.2 | 10585.4 | 9240.3 | 10782 | 9869.5 | 10005.8 | 10008.9 | 9867 | 8553.1 | 9785.9 | 8642.1 | 9881.3 | 9890.8 | 11493.7 | 9932.8 | 11602.4 | 10206.1 | 11414.6 | 9987.8 | 10183 | 10034.4 | 11128.4 | 11574.6 | 11380 | 11327.3 | 11401.7 | 11457.8 | 10290.1 | 11458.3 | 11375.2 | 11446.5 | 11540.3 | 11506.8 | 11568.2 | 10265 | 11481.5 | 10264.5 | 25.2914 | 25.1111 | 25.0575 | 25.1804 | 25.3754 | 25.1876 | 0 | 38.3 | 0 | 0 | 38.6 | 38.1274 | 2.7285 | 2.8143 | 2.7886 | 2.8823 | 2.8256 | 2.7466 | 5.457 | 6.206 | 5.496 | 6.367 | 5.457 | 5.037 | 4.9521 | 4.9912 | 4.9987 | 4.9531 | 5.0213 | 5.0195 | 1.05 | 1.1316 | 0.95555 | 1.3341 | 1.2435 | 1.1294 | 5.7695 | 5.8494 | 5.7615 | 5.8001 | 5.784 | 5.7405 | 0.2585 | 0.3096 | 0.25822 | 0.28907 | 0.27643 | 0.30315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 557067 | 1003 | 544888 | 1075 | 512653.773 | 1380.8 | 4.9521 | 4.9912 | 4.9987 | 4.9531 | 5.0213 | 5.0195 | 5.7695 | 5.8494 | 5.7615 | 5.8001 | 5.784 | 5.7405 | 840000 | 2000 | 836000 | 2000 | 1669666 | 4733 | 1672000 | 1664933 | 11.2833 | 4.9893 | 1.1407 | 5.7841 | 0.2825 | 22.86% | 4.884% | 25.2006 | 38.3425 | 2.7976 | 5.67 | 1681415.4 | 1668667 | 1895642.5384 | 88.03% | 35 | 0
2024-02-21 | 2024 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 335090.89 | 7:20 | 18:42 | 10679.2 | 11130.4 | 10979.6 | 10936.8 | 11032.7 | 11114.2 | 11162 | 11477.9 | 11105.9 | 11087.3 | 10929.6 | 11110 | 11010.4 | 11012.9 | 11032.1 | 11089.4 | 10983.7 | 11082.4 | 11127.2 | 11180.8 | 11129.4 | 11144.2 | 10938.1 | 11041.4 | 10920.3 | 9609.3 | 10903.7 | 10879.6 | 11133 | 11030.2 | 10963.1 | 11148.7 | 11332.6 | 11381.2 | 11275.1 | 11233.2 | 11266.7 | 11162.4 | 11224.6 | 11132 | 11865.3 | 10860.9 | 11735.1 | 10713.5 | 11364.2 | 12336.3 | 10638.5 | 11824.2 | 10270.9 | 10546.9 | 11201.6 | 10643.5 | 11503.5 | 10281.7 | 11468.3 | 10311.7 | 10309 | 11705.2 | 10314.2 | 11606.8 | 11517.8 | 10304.6 | 11306.2 | 10793.2 | 11099 | 10451.2 | 11033.8 | 11491.6 | 11662.1 | 10698.6 | 11562.1 | 10282.5 | 11213.5 | 11155.6 | 10363.5 | 11590.6 | 10287.8 | 11594.3 | 10332.3 | 11488.5 | 10770.3 | 11515.5 | 10910.2 | 11865.6 | 10753.1 | 11428.9 | 10656.8 | 9446.7 | 11506 | 11177.6 | 10414.4 | 11841.7 | 11552.4 | 10755.8 | 10644 | 11634.1 | 10560.5 | 10932.4 | 11765.8 | 10448 | 11828.8 | 10445.7 | 11610.6 | 10728.7 | 11678.9 | 10173 | 11742 | 10732.6 | 11634.4 | 10696.6 | 11699.3 | 10876.9 | 10463.3 | 11515.5 | 10698 | 10426.7 | 11593 | 11757.1 | 11526.4 | 10697.2 | 11695.5 | 10616.3 | 11367.4 | 10716.1 | 11285.4 | 9943.3 | 11492 | 10625.5 | 10763.9 | 10774.2 | 10589.4 | 9193.3 | 10443.8 | 9349.6 | 10571.4 | 10582.4 | 12019.6 | 10702.7 | 12118.6 | 11010.9 | 11960.4 | 10793 | 10988.2 | 10751.6 | 11801.9 | 12111.2 | 11994 | 11928.8 | 11966.2 | 12014.3 | 11095.8 | 12021 | 11976.7 | 12013.5 | 12081.3 | 12060.3 | 12127.3 | 11075.8 | 12088 | 11081.2 | 25.3398 | 25.17 | 25.1552 | 25.2843 | 25.6054 | 25.2105 | 0 | 38.5 | 0 | 0 | 39.2 | 38.9715 | 3.1034 | 3.0694 | 3.0617 | 3.0992 | 2.9968 | 3.0307 | 6.992 | 7.459 | 8.122 | 8.268 | 7.582 | 7.232 | 5.2314 | 5.2978 | 5.2687 | 5.2916 | 5.418 | 5.4411 | 1.1362 | 1.1886 | 1.0298 | 1.449 | 1.3433 | 1.2003 | 6.1142 | 6.2505 | 6.123 | 6.261 | 6.2751 | 6.2338 | 0.26755 | 0.31962 | 0.26612 | 0.29764 | 0.28825 | 0.31678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 557948 | 1004 | 545778 | 1077 | 514417.174 | 1385.4 | 5.2314 | 5.2978 | 5.2687 | 5.2916 | 5.418 | 5.4411 | 6.1142 | 6.2505 | 6.123 | 6.261 | 6.2751 | 6.2338 | 881000 | 1000 | 890000 | 2000 | 1763401 | 4600 | 1768000 | 1758801 | 11.3667 | 5.3247 | 1.2245 | 6.2096 | 0.29266 | 23% | 4.713% | 25.2942 | 38.8905 | 3.0602 | 7.6092 | 1776739.7 | 1762067 | 2024067.5711 | 87.06% | 38 | 0
2024-02-22 | 2024 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 335090.89 | 7:24 | 18:45 | 11041 | 11529.8 | 11592 | 11548.7 | 11620.6 | 11679.4 | 11608.8 | 11892.3 | 11399.3 | 11452 | 11177.1 | 11361.3 | 11299.1 | 11249.4 | 11397.1 | 11432.4 | 11317.7 | 11386.5 | 11418.8 | 11474.6 | 11396.2 | 11430.1 | 11226.8 | 11312.5 | 11155.1 | 9960.7 | 11153.7 | 11125 | 11365.9 | 11281.6 | 11212.7 | 11372 | 11599.6 | 11639.6 | 11589.1 | 11555.2 | 11469.7 | 11359.6 | 11391.6 | 11298.5 | 12185.6 | 11277.6 | 12019.5 | 11122.2 | 11669.5 | 12534.6 | 10990 | 12127.5 | 10620 | 10861.3 | 11424.9 | 10931.8 | 11730.7 | 10665.9 | 11714.3 | 10675.9 | 10690 | 11933.8 | 10629.4 | 11841.8 | 11744.1 | 10617.4 | 11578.3 | 11131.5 | 11287.9 | 10667.2 | 11244.8 | 11568.2 | 11850.2 | 10873.2 | 11724.5 | 10503.7 | 11450.6 | 11322.9 | 10703.6 | 11724.2 | 10592.8 | 11847.5 | 10696.4 | 11734 | 10933.4 | 11570.4 | 11093.7 | 11936.3 | 10951.9 | 11556.9 | 10835.4 | 9708.1 | 11646.2 | 11298.7 | 10649.7 | 11933.8 | 11663.8 | 10959.5 | 10851.6 | 11700.4 | 10733.4 | 11025.2 | 11773.9 | 10593.1 | 11840.8 | 10629.8 | 11654.4 | 10903 | 11697.1 | 10361.7 | 11772.4 | 10873.2 | 11683.4 | 10874.2 | 11749.5 | 11057.3 | 10627.7 | 11505.2 | 10828.2 | 10591 | 11633.4 | 11682.4 | 11562.1 | 10744.7 | 11600.9 | 10680.3 | 11441.3 | 10881 | 11384.3 | 9985.7 | 11437 | 10690.2 | 10850.3 | 10849.3 | 10746.5 | 9304.5 | 10652.6 | 9465.5 | 10690.4 | 10692.5 | 11875.4 | 10679.1 | 11919.2 | 10934.2 | 11836.6 | 10813.2 | 10962.4 | 10804.6 | 11710.6 | 11949.4 | 11865.5 | 11770.2 | 11834.1 | 11874.6 | 11005.7 | 11844.8 | 11863.5 | 11848.7 | 11922.8 | 11901.6 | 11969.3 | 11032 | 12010 | 11006.3 | 23.5404 | 23.278 | 23.1549 | 23.2949 | 23.5398 | 23.2193 | 0 | 37.1 | 0 | 0 | 37.2 | 36.6 | 2.449 | 2.451 | 2.3756 | 2.5451 | 2.5084 | 2.5124 | 6.148 | 6.189 | 5.356 | 6.232 | 5.79 | 5.481 | 5.4021 | 5.4229 | 5.4383 | 5.3832 | 5.4063 | 5.4023 | 1.151 | 1.2466 | 1.047 | 1.4525 | 1.3516 | 1.2312 | 6.346 | 6.436 | 6.3487 | 6.3955 | 6.2931 | 6.2356 | 0.26721 | 0.31392 | 0.26128 | 0.28807 | 0.27263 | 0.30244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 558852 | 1006 | 546670 | 1078 | 516206.307 | 1390 | 5.4021 | 5.4229 | 5.4383 | 5.3832 | 5.4063 | 5.4023 | 6.346 | 6.436 | 6.3487 | 6.3955 | 6.2931 | 6.2356 | 904000 | 2000 | 892000 | 1000 | 1789133 | 4600 | 1793000 | 1784533 | 11.35 | 5.4092 | 1.2466 | 6.3425 | 0.28426 | 23.05% | 4.482% | 23.3379 | 36.9667 | 2.4736 | 5.866 | 1803555.4 | 1787867 | 2080158.3809 | 85.95% | 39 | 904
2024-02-23 | 2024 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 335090.89 | 7:14 | 18:45 | 11818.8 | 12214.2 | 12154.1 | 12138.7 | 12213.1 | 12263.1 | 12240.5 | 12562.9 | 12146.4 | 12140.2 | 11994.2 | 12138.2 | 12120.3 | 12058.8 | 12158.8 | 12207.7 | 12081.7 | 12167.9 | 12219.2 | 12297 | 12212.5 | 12242.5 | 12074.1 | 12148.3 | 12002.8 | 10802.2 | 12022.9 | 11984.8 | 12186.3 | 12085.7 | 12037.7 | 12188 | 12579.9 | 12622.2 | 12462.4 | 12427.7 | 12279.8 | 12190.4 | 12227 | 12136.2 | 12876.4 | 12009.7 | 12705.8 | 11866.8 | 12391.8 | 13285.5 | 11759.9 | 12828.8 | 11502.3 | 11736.2 | 12262.3 | 11783.4 | 12538.8 | 11502.8 | 12497.2 | 11526.5 | 11525.3 | 12672.5 | 11539.4 | 12611.9 | 12534.9 | 11509 | 12312.3 | 11870.3 | 12067.9 | 11517.7 | 12040 | 12376.4 | 12567.9 | 11711.9 | 12467.6 | 11365 | 12186.7 | 12105.3 | 11492.6 | 12468.6 | 11414.7 | 12540.6 | 11479.8 | 12439.8 | 11744.6 | 12341.4 | 11878.8 | 12700.4 | 11743.9 | 12310.4 | 11639.5 | 10421.7 | 12402.3 | 12072.9 | 11491.7 | 12704.8 | 12429.5 | 11784.9 | 11693.4 | 12459.8 | 11557.7 | 11864 | 12537.8 | 11457.7 | 12632.5 | 11500 | 12455.3 | 11757.8 | 12467.4 | 11222.3 | 12574.3 | 11725.8 | 12495 | 11736.5 | 12529.9 | 11893 | 11509.6 | 12344.2 | 11681.5 | 11476.5 | 12418.2 | 12562.6 | 12358.8 | 11665.5 | 12487.8 | 11624.2 | 12232 | 11722.9 | 12132 | 10934.6 | 12362.2 | 11653.8 | 11770.1 | 11759.3 | 11629.4 | 10141.2 | 11567.2 | 10290.9 | 11666.5 | 11662.7 | 12790.9 | 11663.9 | 12883.9 | 11930 | 12755.8 | 11749 | 11890.4 | 11755.6 | 12623.1 | 12893.7 | 12772.6 | 12699.1 | 12757.3 | 12793 | 12003.7 | 12809.4 | 12759.7 | 12781.7 | 12830.7 | 12815.4 | 12908.6 | 11987.1 | 12861.9 | 11995.1 | 23.2114 | 22.9007 | 22.976 | 22.9303 | 23.0823 | 22.9446 | 0 | 38.9 | 0 | 0 | 39 | 38.6 | 2.5692 | 2.4773 | 2.5199 | 2.5692 | 2.5149 | 2.4891 | 5.691 | 5.98 | 5.814 | 5.873 | 5.624 | 6.251 | 5.8281 | 5.8715 | 5.939 | 5.8394 | 5.8901 | 5.9123 | 1.2709 | 1.3357 | 1.1547 | 1.5825 | 1.4582 | 1.3239 | 6.8984 | 7.0197 | 6.9071 | 6.9812 | 6.9043 | 6.8549 | 0.27234 | 0.31929 | 0.26665 | 0.2902 | 0.27906 | 0.3106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 559818 | 1008 | 547632 | 1080 | 518126.44 | 1394.6 | 5.8281 | 5.8715 | 5.939 | 5.8394 | 5.8901 | 5.9123 | 6.8984 | 7.0197 | 6.9071 | 6.9812 | 6.9043 | 6.8549 | 966000 | 2000 | 962000 | 2000 | 1920133 | 4600 | 1924000 | 1915533 | 11.5167 | 5.8801 | 1.3543 | 6.9276 | 0.28969 | 23.03% | 4.182% | 23.0075 | 38.8333 | 2.5233 | 5.8722 | 1935733.8 | 1918667 | 2260356.3307 | 84.88% | 39 | 215
2024-02-24 | 2024 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 335090.89 | 7:13 | 18:46 | 12014.5 | 12361.9 | 12306 | 12298.8 | 12378.4 | 12433.5 | 12424.7 | 12676.4 | 12313.1 | 12274.3 | 12183.9 | 12308.7 | 12311.5 | 12257.5 | 12340 | 12373.1 | 12295.7 | 12338.6 | 12380.9 | 12462.5 | 12369 | 12405.3 | 12244.9 | 12310.9 | 12164.4 | 11111.1 | 12221.8 | 12180.9 | 12368.4 | 12260.1 | 12204.9 | 12338.2 | 12781.1 | 12813.5 | 12684.3 | 12654.2 | 12433.5 | 12339 | 12375.7 | 12273.2 | 12980.8 | 12196.8 | 12809.4 | 12069.8 | 12564.5 | 13385.7 | 11964.6 | 12928.1 | 11732.5 | 11940.5 | 12426.3 | 11981.2 | 12689.1 | 11763.5 | 12631.2 | 11758.9 | 11756.9 | 12803.3 | 11780.2 | 12740.4 | 12663 | 11729.2 | 12462.9 | 12045.5 | 12236 | 11724.3 | 12205.3 | 12526.6 | 12685.9 | 11907.8 | 12603.7 | 11612.5 | 12334.7 | 12268.9 | 11701.3 | 12591.6 | 11635.2 | 12656.7 | 11698.6 | 12570.6 | 11930.8 | 12486.3 | 12068.4 | 12827.4 | 11937.3 | 12472 | 11825.7 | 10747.8 | 12532.3 | 12235.5 | 11709.8 | 12818.4 | 12564.3 | 11982.6 | 11893.6 | 12612.8 | 11778.6 | 12070.5 | 12663.5 | 11659.2 | 12742.7 | 11705.1 | 12588.5 | 11951.9 | 12594.3 | 11479.8 | 12697.2 | 11917.3 | 12628.4 | 11924.2 | 12662 | 12086.8 | 11704.5 | 12493.9 | 11872 | 11706.3 | 12546 | 12701.4 | 12513 | 11874.1 | 12628.5 | 11838.4 | 12380.2 | 11946 | 12355.1 | 11239 | 12424.8 | 11858.2 | 11958.1 | 11930.4 | 11822.2 | 10398.2 | 11788.1 | 10597.2 | 11847.3 | 11842.9 | 12893.9 | 11850.3 | 12970.1 | 12084.9 | 12848.5 | 11925.2 | 12066 | 11931.7 | 12744.8 | 12976.8 | 12897 | 12817.3 | 12872.9 | 12896.4 | 12163.2 | 12903.9 | 12874.3 | 12909.7 | 12939.6 | 12929.2 | 12996.5 | 12159 | 12987.2 | 12164.6 | 23.3932 | 23.2179 | 23.2349 | 23.3879 | 23.8348 | 23.28 | 0 | 37.4 | 0 | 0 | 37.7 | 37.5 | 3.031 | 3.0828 | 3.0006 | 3.1144 | 3.1525 | 2.9725 | 7.13 | 7.612 | 7.733 | 7.178 | 6.964 | 6.577 | 5.9528 | 6.0086 | 6.0525 | 5.961 | 6.0172 | 6.0496 | 1.3093 | 1.375 | 1.1836 | 1.6259 | 1.5035 | 1.3737 | 7.0574 | 7.1702 | 7.1184 | 7.1158 | 7.0463 | 7.0025 | 0.28143 | 0.33174 | 0.27468 | 0.29678 | 0.2902 | 0.32034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560798 | 1009 | 548607 | 1081 | 520073.107 | 1399.2 | 5.9528 | 6.0086 | 6.0525 | 5.961 | 6.0172 | 6.0496 | 7.0574 | 7.1702 | 7.1184 | 7.1158 | 7.0463 | 7.0025 | 980000 | 1000 | 975000 | 1000 | 1946667 | 4600 | 1953000 | 1942067 | 11.55 | 6.0069 | 1.3952 | 7.0851 | 0.29919 | 23.23% | 4.223% | 23.3914 | 37.5333 | 3.059 | 7.199 | 1962896.2 | 1945267 | 2311104.2742 | 84.17% | 46 | 2610
2024-02-25 | 2024 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 335090.89 | 7:14 | 18:40 | 10644.6 | 11015.2 | 10951.4 | 10964.1 | 10998 | 11062.1 | 11070 | 11426.2 | 11027.7 | 10974.2 | 10848.7 | 11005.2 | 10955.7 | 10918 | 10943.5 | 11006.6 | 10915.1 | 10956.4 | 10995.8 | 11072.1 | 10981.1 | 11004.7 | 10808.5 | 10892.3 | 10786.9 | 9688.7 | 10834.8 | 10783.7 | 11007.2 | 10879.5 | 10808.1 | 10997.4 | 11207.3 | 11253.7 | 11105.3 | 11078.8 | 11091.6 | 10990.5 | 11008.3 | 10921 | 11617.4 | 10687.8 | 11453.7 | 10533.2 | 11097.3 | 12083.8 | 10481.4 | 11608.2 | 10279.2 | 10503.7 | 11064.8 | 10573.1 | 11364.4 | 10334.4 | 11352.6 | 10317.7 | 10333.9 | 11561.4 | 10327.8 | 11489.4 | 11404.7 | 10308.4 | 11175.8 | 10695.5 | 10917.3 | 10358.2 | 10874.9 | 11302.7 | 11478.3 | 10573.2 | 11353.4 | 10235.6 | 11050.5 | 10964 | 10319.5 | 11398.4 | 10258 | 11450.1 | 10316.6 | 11377.5 | 10617.6 | 11277 | 10806.6 | 11673.8 | 10631.3 | 11268.1 | 10527.2 | 9474.5 | 11389.9 | 11011 | 10350.7 | 11664.4 | 11333.4 | 10584.2 | 10485.6 | 11436.6 | 10469.8 | 10796.5 | 11534 | 10345.3 | 11602.2 | 10383.3 | 11380.9 | 10620.3 | 11428.6 | 10130.3 | 11520.8 | 10607.2 | 11403.3 | 10583.9 | 11456.2 | 10752.6 | 10450.9 | 11371.8 | 10580.4 | 10408.8 | 11421.6 | 11564 | 11371.3 | 10616.8 | 11492.9 | 10548.1 | 11179 | 10636.3 | 11132.9 | 9952.7 | 11280.4 | 10569.1 | 10710.2 | 10714.6 | 10566.3 | 9266.5 | 10539.9 | 9450.3 | 10598 | 10601.4 | 11841.5 | 10619.8 | 11910.8 | 10872.8 | 11800.9 | 10707.6 | 10853.6 | 10710.2 | 11619.8 | 11907.3 | 11789.6 | 11737.7 | 11791 | 11822.6 | 10948.9 | 11815.6 | 11796.5 | 11840.2 | 11917 | 11879.5 | 11924.4 | 10935.9 | 11908.6 | 10930.9 | 24.0025 | 23.6474 | 23.7736 | 23.6467 | 23.6115 | 23.5314 | 0 | 35 | 0 | 0 | 35.3 | 35.3 | 3.3448 | 3.3996 | 3.3211 | 3.3998 | 3.3616 | 3.3968 | 7.29 | 7.587 | 6.782 | 7.501 | 7.817 | 7.359 | 5.2795 | 5.2854 | 5.2912 | 5.2817 | 5.3509 | 5.3881 | 1.181 | 1.1641 | 1.0518 | 1.4703 | 1.3115 | 1.1715 | 6.0963 | 6.1307 | 6.0597 | 6.1538 | 6.1151 | 6.0638 | 0.28317 | 0.33161 | 0.27698 | 0.31191 | 0.29704 | 0.32436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 561670 | 1011 | 549486 | 1083 | 521817.374 | 1404 | 5.2795 | 5.2854 | 5.2912 | 5.2817 | 5.3509 | 5.3881 | 6.0963 | 6.1307 | 6.0597 | 6.1538 | 6.1151 | 6.0638 | 872000 | 2000 | 879000 | 2000 | 1744267 | 4800 | 1747000 | 1739467 | 11.4333 | 5.3128 | 1.225 | 6.1032 | 0.30418 | 23.06% | 4.984% | 23.7022 | 35.2 | 3.3706 | 7.3893 | 1757211.8 | 1741733 | 2010696.0366 | 86.62% | 45 | 11258
2024-02-26 | 2024 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 335090.89 | 7:22 | 18:44 | 8143.4 | 8436.3 | 8390.6 | 8345.8 | 8433.7 | 8483.6 | 8496.6 | 8738.1 | 8405.5 | 8369.7 | 8321.6 | 8415.7 | 8421.7 | 8373.8 | 8446.9 | 8474 | 8416.9 | 8448.6 | 8440.6 | 8491.7 | 8455.3 | 8466.3 | 8339.9 | 8393 | 8308.5 | 7486.3 | 8315.4 | 8291.9 | 8461.4 | 8383 | 8349.3 | 8474.2 | 8631.7 | 8658.6 | 8610.2 | 8589.2 | 8536 | 8472.3 | 8500.7 | 8437.8 | 8984.5 | 8329.6 | 8882.4 | 8216.8 | 8603 | 9322.1 | 8152.6 | 8969.1 | 7906.6 | 8090.9 | 8477.1 | 8145.1 | 8688.3 | 7955.2 | 8689.4 | 7955.2 | 7954.9 | 8843.3 | 7927.5 | 8776.5 | 8712.4 | 7912.8 | 8549 | 8230.6 | 8359 | 7945.6 | 8358.9 | 8591.3 | 8789.8 | 8104.9 | 8707.2 | 7866.7 | 8491.3 | 8424.9 | 7961.4 | 8703.2 | 7891.4 | 8760.3 | 7949.9 | 8693 | 8062 | 8546.8 | 8155.7 | 8800.4 | 8058.5 | 8491.3 | 8022.1 | 7213.6 | 8627.5 | 8338.5 | 7903.6 | 8843 | 8652 | 8165.1 | 8084.9 | 8668.7 | 7942.4 | 8171.5 | 8683.1 | 7833.4 | 8781.2 | 7876.6 | 8615.2 | 8055.2 | 8644.8 | 7688.5 | 8701.9 | 8020.9 | 8635.3 | 8032.6 | 8666.6 | 8140.6 | 7909.6 | 8580.7 | 8000.6 | 7879.5 | 8618.6 | 8703 | 8565.8 | 8032 | 8649.6 | 7987.8 | 8448 | 8043.8 | 8413.5 | 7548.4 | 8530.2 | 7984 | 8113.4 | 8123.8 | 8011.3 | 7038.4 | 7948.9 | 7147.6 | 7999.3 | 8018.9 | 8895.7 | 8053.2 | 8924.2 | 8176.1 | 8867 | 8072.7 | 8179.1 | 8098.1 | 8718.3 | 8928 | 8895.8 | 8832.9 | 8865.4 | 8893.1 | 8235.9 | 8866.9 | 8893.7 | 8918.4 | 8920.2 | 8898.9 | 8931.8 | 8230.4 | 8943.7 | 8259.2 | 23.5921 | 23.4488 | 23.0308 | 23.2398 | 23.1591 | 23.2225 | 0 | 33.8 | 0 | 0 | 33.6 | 33.1 | 3.6133 | 3.4379 | 3.4865 | 3.4673 | 3.4648 | 3.4566 | 7.926 | 7.495 | 7.547 | 7.473 | 7.165 | 7.364 | 4.1455 | 4.1731 | 4.2395 | 4.1612 | 4.1289 | 4.1039 | 0.7593 | 0.93122 | 0.70487 | 0.97938 | 0.97439 | 0.93319 | 4.7189 | 4.7748 | 4.7407 | 4.733 | 4.6561 | 4.6289 | 0.20722 | 0.24281 | 0.2047 | 0.22853 | 0.21326 | 0.22957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 562341 | 1012 | 550151 | 1085 | 523147.041 | 1408.733 | 4.1455 | 4.1731 | 4.2395 | 4.1612 | 4.1289 | 4.1039 | 4.7189 | 4.7748 | 4.7407 | 4.733 | 4.6561 | 4.6289 | 671000 | 1000 | 665000 | 2000 | 1329667 | 4733 | 1333000 | 1324934 | 11.3667 | 4.1587 | 0.88039 | 4.7087 | 0.22102 | 21.17% | 4.694% | 23.2822 | 33.5 | 3.4877 | 7.495 | 1339448.4 | 1327667 | 1551862.5939 | 85.55% | 77 | 28218
2024-02-27 | 2024 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 335090.89 | 7:18 | 18:45 | 11375.3 | 11751 | 11718.2 | 11697.7 | 11769 | 11837.7 | 11843.7 | 12115.4 | 11728.6 | 11654 | 11593.2 | 11738.3 | 11695.8 | 11676.9 | 11724.7 | 11762.5 | 11695.5 | 11729.5 | 11743.9 | 11819.5 | 11751.1 | 11771.4 | 11593 | 11670.2 | 11541.5 | 10344 | 11585.8 | 11542.6 | 11661.1 | 11528.4 | 11578.3 | 11747.3 | 12072.8 | 12093.2 | 12020 | 12004.3 | 11745.8 | 11655.9 | 11682.7 | 11566.3 | 12384.4 | 11514.4 | 12237.7 | 11359.9 | 11943.1 | 12883.5 | 11313.4 | 12363.9 | 10976.7 | 11204.6 | 11811.5 | 11337.9 | 12097.5 | 11086.5 | 12060.8 | 11076.5 | 11082.7 | 12250.3 | 11077.3 | 12176.5 | 12095.5 | 11060.4 | 11877.8 | 11445.5 | 11633.3 | 11061 | 11592.8 | 11923.1 | 12146.2 | 11262.3 | 12046.1 | 10922.6 | 11710 | 11622.7 | 11059.8 | 12068.2 | 10972.8 | 12119.2 | 11037.3 | 12043.2 | 11258.1 | 11882.8 | 11423.8 | 12224.7 | 11267.3 | 11844.9 | 11175.2 | 9977.7 | 11985.9 | 11619.7 | 11019.2 | 12258.1 | 11987.3 | 11325.8 | 11222.1 | 12046.5 | 11076.6 | 11349.1 | 12080.6 | 10949.5 | 12164.1 | 10989.1 | 11962.8 | 11261 | 11995.9 | 10726.3 | 12083.6 | 11217.3 | 11987.8 | 11219.5 | 12036.6 | 11361 | 10982.4 | 11935.4 | 10968.5 | 10791.8 | 11977.8 | 12109.6 | 11930.4 | 11208.7 | 12034.9 | 11134.7 | 11762.5 | 11219.6 | 11741.1 | 10468.2 | 11884.2 | 11148.4 | 11302.3 | 11319.3 | 11101.5 | 9662 | 11086.9 | 9905 | 11195.5 | 11205.1 | 12294.3 | 11123.7 | 12418.1 | 11430 | 12307.9 | 11307.3 | 11370.6 | 11207.9 | 12138.9 | 12423.3 | 12324.1 | 12259.6 | 12241.8 | 12240.5 | 11505.3 | 12332.9 | 12351.5 | 12396.2 | 12428.3 | 12407.4 | 12442.2 | 11519.1 | 12426.8 | 11521.9 | 22.7105 | 22.4895 | 22.6918 | 22.4557 | 22.4542 | 22.517 | 0 | 32 | 0 | 0 | 31.8 | 31.9 | 5.741 | 5.6134 | 5.5281 | 5.8155 | 5.5492 | 5.6717 | 10.109 | 9.645 | 9.511 | 10.153 | 10.264 | 9.373 | 5.5088 | 5.5514 | 5.4834 | 5.5131 | 5.5107 | 5.2713 | 1.1814 | 1.283 | 1.0851 | 1.5152 | 1.3765 | 1.2534 | 6.4084 | 6.4559 | 6.3361 | 6.3986 | 6.2636 | 0 | 0.27874 | 0.32479 | 0.27377 | 0.29722 | 0.28587 | 0.31309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 563272 | 1014 | 551076 | 1087 | 524995.908 | 1413.733 | 5.5088 | 5.5514 | 5.4834 | 5.5131 | 5.5107 | 5.2713 | 6.4084 | 6.4559 | 6.3361 | 6.3986 | 6.2636 | 0 | 931000 | 2000 | 925000 | 2000 | 1848867 | 5000 | 1852000 | 1843867 | 11.45 | 5.4731 | 1.2824 | 6.3725 | 0.29558 | 23.43% | 4.638% | 22.5531 | 31.9 | 5.6531 | 9.8425 | 1861240.3 | 1848467 | 2126922.2094 | 86.91% | 47 | 0
2024-02-28 | 2024 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 335090.89 | 7:13 | 18:48 | 11748.7 | 12122 | 12079.2 | 12073.4 | 12120.2 | 12204.6 | 12213.2 | 12523 | 12116.6 | 12051 | 11985.4 | 12120.5 | 12084.5 | 12057.5 | 12077.8 | 12138.9 | 12043.6 | 12098 | 12116.5 | 12193.2 | 12118.7 | 12144.9 | 11977.8 | 12054.1 | 11919.3 | 10723.1 | 11963.1 | 11921.1 | 12123.4 | 12019.1 | 11951.6 | 12116.7 | 12490.9 | 12522.6 | 12450 | 12429.5 | 12215.9 | 12117.3 | 12161.1 | 12036.3 | 12818.2 | 11955.9 | 12631.7 | 11801.8 | 12315.3 | 13247.5 | 11714.3 | 12777.4 | 11422.9 | 11647.8 | 12185.6 | 11719.5 | 12463.8 | 11504.7 | 12422.2 | 11451.2 | 11455.1 | 12608.9 | 11463.3 | 12542.3 | 12463.6 | 11434.3 | 12250.5 | 11819 | 11997.8 | 11442.2 | 11958.9 | 12311.5 | 12495.8 | 11647 | 12397.6 | 11316.6 | 12110.7 | 12037.6 | 11422.3 | 12414.4 | 11343.2 | 12471 | 11412.2 | 12404.1 | 11660.5 | 12284.3 | 11819.3 | 12616.4 | 11673.9 | 12247.5 | 11567.2 | 10362.3 | 12367.6 | 12003.8 | 11422.8 | 12636 | 12340.4 | 11682.9 | 11569.3 | 12417.1 | 11498.2 | 11798.9 | 12461 | 11347 | 12545 | 11410.3 | 12351.9 | 11658.3 | 12378.5 | 11133 | 12473.8 | 11626.3 | 12388.6 | 11629 | 12438 | 11795.8 | 11361.5 | 12318.2 | 11585.9 | 11430 | 12340.3 | 12491.1 | 12302.1 | 11614 | 12429.5 | 11549.9 | 12155.2 | 11655.6 | 12109.6 | 10877.9 | 12279.4 | 11570.1 | 11677.7 | 11663.6 | 11551.1 | 10057.2 | 11505.1 | 10294.5 | 11555.6 | 11564.5 | 12732.8 | 11610.3 | 12798.9 | 11839 | 12694.3 | 11677.8 | 11832.2 | 11652.6 | 12536.7 | 12812 | 12723.4 | 12658.5 | 12702.9 | 12732.7 | 11912.4 | 12722.5 | 12711.2 | 12767.3 | 12827.1 | 12800 | 12845.3 | 11934.7 | 12801.1 | 11929.7 | 24.0642 | 23.597 | 23.6726 | 23.6269 | 23.6577 | 23.6382 | 0 | 36.7 | 0 | 0 | 37 | 37.1 | 3.1588 | 3.1044 | 3.04 | 3.3062 | 3.1628 | 3.0157 | 5.605 | 6.342 | 6.595 | 6.216 | 6.077 | 5.582 | 5.8123 | 5.8261 | 5.7571 | 5.7801 | 5.7831 | 5.5583 | 1.2293 | 1.3184 | 1.1283 | 1.5756 | 1.4047 | 1.2779 | 6.7411 | 6.8068 | 6.6929 | 6.764 | 6.6648 | 6.6472 | 0.26857 | 0.31557 | 0.26479 | 0.28454 | 0.27579 | 0.3018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 564234 | 1016 | 552032 | 1089 | 526905.641 | 1418.6 | 5.8123 | 5.8261 | 5.7571 | 5.7801 | 5.7831 | 5.5583 | 6.7411 | 6.8068 | 6.6929 | 6.764 | 6.6648 | 6.6472 | 962000 | 2000 | 956000 | 2000 | 1909733 | 4867 | 1914000 | 1904866 | 11.5833 | 5.7528 | 1.3224 | 6.7195 | 0.28517 | 22.99% | 4.244% | 23.7094 | 36.9333 | 3.1313 | 6.0695 | 1924723.9 | 1909000 | 2204805.4209 | 86.58% | 50 | 0
2024-02-29 | 2024 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 335090.89 | 7:10 | 18:44 | 11507.9 | 11926.7 | 11901.9 | 11885.6 | 11967.4 | 12023.4 | 12014.6 | 12378.5 | 11934.8 | 11868.1 | 11808.4 | 11947.3 | 11908.7 | 11884.8 | 11926.1 | 11969 | 11899.8 | 11961 | 11970.4 | 12042.4 | 11981.8 | 11999.1 | 11805.2 | 11898.7 | 11744.3 | 10388 | 11775.8 | 11744.4 | 11983.5 | 11872.1 | 11793.8 | 11974.4 | 12220.5 | 12257.2 | 12183.5 | 12148.5 | 12074.4 | 11987.6 | 12032.5 | 11900.8 | 12728.1 | 11770.2 | 12552.9 | 11590 | 12162.6 | 13146.9 | 11515.9 | 12693.4 | 11088.7 | 11363.6 | 12018.2 | 11487.7 | 12335.4 | 11206.6 | 12276.1 | 11128.9 | 11132.6 | 12486.9 | 11119 | 12406.5 | 12311.4 | 11104.9 | 12115.7 | 11617.5 | 11832.6 | 11142.6 | 11774 | 12168.9 | 12377.7 | 11386.6 | 12261.7 | 10952.8 | 11944.1 | 11851.7 | 11120 | 12279.5 | 11006.4 | 12342.4 | 11106 | 12271.4 | 11434 | 12170.3 | 11602.5 | 12520.3 | 11448.8 | 12096.6 | 11359.8 | 10058.5 | 12216.3 | 11821.6 | 11114.3 | 12529.8 | 12225.3 | 11478.9 | 11351.3 | 12281.6 | 11179.6 | 11593.7 | 12342.7 | 11027.1 | 12420.1 | 11083.2 | 12186.1 | 11362.8 | 12229.5 | 10770.6 | 12318.5 | 11353.6 | 12213.3 | 11334.3 | 12285.7 | 11525.1 | 11115.3 | 12131.2 | 11291.3 | 11078.8 | 12174.8 | 12318.1 | 12131.1 | 11300.2 | 12264.3 | 11210.5 | 11959.9 | 11346.6 | 11921.8 | 10492.7 | 12087.3 | 11208.4 | 11374.2 | 11393.3 | 11188.4 | 9690.8 | 11160.4 | 9885.9 | 11260.6 | 11266.2 | 12589.7 | 11333.7 | 12668.6 | 11596.6 | 12542.7 | 11410.2 | 11590 | 11419 | 12392.8 | 12693.4 | 12581.1 | 12520.2 | 12559.6 | 12586.6 | 11687.6 | 12590.7 | 12593.9 | 12652.9 | 12726.9 | 12695.6 | 12726.2 | 11707.9 | 12667.8 | 11723 | 27.1782 | 26.9104 | 26.8705 | 26.9553 | 27.0623 | 26.9083 | 0 | 41.7 | 0 | 0 | 41.6 | 41.3 | 3.1145 | 3.087 | 3.1298 | 3.088 | 3.0221 | 2.9879 | 6.349 | 6.575 | 6.641 | 6.262 | 6.096 | 6.712 | 5.7534 | 5.8115 | 5.7188 | 5.7556 | 5.7272 | 5.5148 | 1.2261 | 1.3024 | 1.1254 | 1.5679 | 1.3963 | 1.2633 | 6.6336 | 6.7169 | 6.5928 | 6.6667 | 6.6013 | 6.6311 | 0.26324 | 0.31086 | 0.26394 | 0.28271 | 0.27446 | 0.29801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 565180 | 1017 | 552971 | 1090 | 528783.908 | 1423.4 | 5.7534 | 5.8115 | 5.7188 | 5.7556 | 5.7272 | 5.5148 | 6.6336 | 6.7169 | 6.5928 | 6.6667 | 6.6013 | 6.6311 | 946000 | 1000 | 939000 | 1000 | 1878267 | 4800 | 1883000 | 1873467 | 11.5667 | 5.7136 | 1.3136 | 6.6404 | 0.2822 | 22.99% | 4.25% | 26.9808 | 41.5333 | 3.0716 | 6.4392 | 1892115.6 | 1876934 | 2150848.2224 | 87.26% | 47 | 20
2024-03-01 | 2024 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 335090.89 | 7:13 | 18:36 | 8182.2 | 8540.7 | 8515.6 | 8505.8 | 8570.8 | 8604.6 | 8620.1 | 8935.9 | 8572.6 | 8507.6 | 8437.2 | 8565.3 | 8494.4 | 8492.2 | 8524.2 | 8533.4 | 8479 | 8497.8 | 8525.1 | 8574.7 | 8540 | 8540.1 | 8369.7 | 8444.6 | 8330.6 | 7379.4 | 8354.7 | 8323.5 | 8548 | 8456.3 | 8361.2 | 8538.9 | 8585 | 8618 | 8583.2 | 8535.1 | 8595.1 | 8503.1 | 8548.5 | 8462.4 | 9062.5 | 8179.9 | 8944.7 | 8037.4 | 8579.3 | 9507.5 | 8026.7 | 9085 | 7775.9 | 8082.8 | 8594.4 | 8157.6 | 8871.7 | 7936.3 | 8845.2 | 7930.5 | 7923.2 | 9034.8 | 7927.8 | 8960.3 | 8874.2 | 7906.8 | 8678.8 | 8236.7 | 8468.5 | 7969.7 | 8407.3 | 8786.1 | 8979.2 | 8135 | 8853.2 | 7841.2 | 8588.5 | 8491.9 | 7944 | 8896.1 | 7875.1 | 8947 | 7947.9 | 8880 | 8162.4 | 8780 | 8285.6 | 9099.4 | 8170.9 | 8719.6 | 8118.8 | 7231.5 | 8819.4 | 8519.1 | 7918.8 | 9082.7 | 8813.5 | 8166.2 | 8084.2 | 8879.2 | 7999.3 | 8283 | 8967.8 | 7891.3 | 9003.8 | 7913 | 8786.3 | 8115.8 | 8848.1 | 7703.1 | 8902.7 | 8077.1 | 8786.3 | 8065.1 | 8842.8 | 8197.9 | 7963.4 | 8788.4 | 8065 | 7936.4 | 8836.3 | 8955.9 | 8767.7 | 8129.4 | 8907.7 | 8033.2 | 8603.5 | 8077.3 | 8551.5 | 7546.5 | 8720.4 | 8058.2 | 8191 | 8211.5 | 8044.7 | 7018.9 | 8058.1 | 7165.2 | 8199.4 | 8203 | 9340.2 | 8240.9 | 9401.8 | 8433.2 | 9300.3 | 8299.7 | 8434 | 8311.9 | 9115.4 | 9399.6 | 9273.8 | 9241.3 | 9257.8 | 9301.3 | 8486.6 | 9309.8 | 9305.4 | 9360.7 | 9437.1 | 9401.3 | 9421.5 | 8509.6 | 9348.5 | 8516.4 | 27.2946 | 27.0582 | 26.9307 | 27.058 | 27.0982 | 27.2929 | 0 | 36 | 0 | 0 | 36.3 | 36.6133 | 5.6989 | 5.7959 | 5.5673 | 5.771 | 5.682 | 5.6605 | 12.731 | 12.601 | 12.716 | 11.858 | 12.004 | 12.138 | 4.1963 | 4.2031 | 4.1851 | 4.1911 | 4.2056 | 4.0951 | 0.94662 | 0.92359 | 0.84037 | 1.1864 | 1.0308 | 0.90628 | 4.5462 | 4.5288 | 4.508 | 4.5781 | 4.5568 | 4.6146 | 0.23231 | 0.27034 | 0.23149 | 0.2596 | 0.24238 | 0.26085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 565856 | 1019 | 553652 | 1092 | 530135.975 | 1428.2 | 4.1963 | 4.2031 | 4.1851 | 4.1911 | 4.2056 | 4.0951 | 4.5462 | 4.5288 | 4.508 | 4.5781 | 4.5568 | 4.6146 | 676000 | 2000 | 681000 | 2000 | 1352067 | 4800 | 1353000 | 1347267 | 11.3833 | 4.1794 | 0.97235 | 4.5554 | 0.2495 | 23.27% | 5.477% | 27.1221 | 36.3044 | 5.6959 | 12.3413 | 1360182.7 | 1350667 | 1541470 | 87.62% | 66 | 73011
2024-03-02 | 2024 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 335090.89 | 7:16 | 18:49 | 10343.3 | 10770.5 | 10764.1 | 10700.3 | 10862.3 | 10916.4 | 10843.1 | 11146.6 | 10682 | 10669.4 | 10630.2 | 10705.4 | 10779.5 | 10722 | 10836.5 | 10846.3 | 10797.4 | 10808.5 | 10818.2 | 10867.5 | 10804.3 | 10822.5 | 10646.2 | 10715.1 | 10610.2 | 9603.7 | 10634.4 | 10623.6 | 10791.7 | 10697.5 | 10585.5 | 10768.4 | 10760.5 | 10798.9 | 10791.1 | 10750.1 | 10849.3 | 10722 | 10751.9 | 10682.7 | 11120.8 | 10377.9 | 11031.5 | 10291.2 | 10752.1 | 11521.6 | 10153.3 | 11088.5 | 10134.1 | 10317.7 | 10834.5 | 10360.3 | 11111.8 | 10270.3 | 10996.9 | 10170.4 | 10024.6 | 11098.4 | 10098.7 | 11030 | 10956.6 | 10049.8 | 10781 | 10346.8 | 10458.2 | 9915.9 | 10411.2 | 10669.3 | 10963.7 | 10038.6 | 10801.6 | 9724.3 | 10613.1 | 10405.2 | 9948.7 | 10761.6 | 9759.7 | 10932.9 | 9907.6 | 10755 | 9992 | 10573.8 | 10026.2 | 10921.4 | 9990.4 | 10523 | 9988.1 | 9000.5 | 10779.8 | 10426.3 | 9911.7 | 11050.8 | 10820.1 | 10258.3 | 10223.7 | 10875 | 10010.5 | 10237.7 | 10889.7 | 9853.8 | 11025.8 | 9906.8 | 10836.4 | 10151.9 | 10900.1 | 9744.5 | 10963.5 | 10135.1 | 10879.4 | 10176.1 | 10910.9 | 10286.4 | 9886.2 | 10691.6 | 10055.5 | 9903 | 10793.7 | 10829.8 | 10740.8 | 10012.8 | 10798 | 9998.3 | 10629.4 | 10127.2 | 10600.1 | 9557 | 10687.1 | 10013.3 | 10085.9 | 10101.6 | 10025.9 | 8781.7 | 9938.7 | 8880 | 9736.9 | 9712.2 | 10729 | 9673 | 10736.7 | 9815.1 | 10688.5 | 9689.9 | 9847.6 | 9752.3 | 10621.2 | 10824.1 | 10734.7 | 10670.4 | 10675.9 | 10707.7 | 9875.1 | 10706.9 | 10827.2 | 10871.4 | 10951.5 | 10932.2 | 10921.1 | 10038.2 | 10846.3 | 10026 | 23.2753 | 23.0264 | 22.9001 | 22.9112 | 22.8855 | 23.0993 | 0 | 32.9 | 0 | 0 | 32.3 | 31.9 | 9.0316 | 9.1394 | 8.8725 | 8.9145 | 8.8589 | 8.9285 | 14.279 | 13.892 | 14.561 | 13.805 | 14.095 | 13.385 | 5.2989 | 5.3655 | 5.2985 | 5.1901 | 5.24 | 5.0624 | 1.0152 | 1.1412 | 0.91618 | 1.2809 | 1.2014 | 1.0462 | 6.0084 | 6.0971 | 5.8968 | 5.896 | 5.8604 | 5.6274 | 0.27477 | 0.32425 | 0.26919 | 0.28934 | 0.28372 | 0.29172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 566703 | 1020 | 554475 | 1094 | 531799.975 | 1433.133 | 5.2989 | 5.3655 | 5.2985 | 5.1901 | 5.24 | 5.0624 | 6.0084 | 6.0971 | 5.8968 | 5.896 | 5.8604 | 5.6274 | 847000 | 1000 | 823000 | 2000 | 1664000 | 4933 | 1667000 | 1659067 | 11.55 | 5.2426 | 1.1002 | 5.8977 | 0.28883 | 20.99% | 4.897% | 23.0163 | 32.3667 | 8.9576 | 14.0028 | 1675922.9 | 1663267 | 2041563.7865 | 81.47% | 94 | 38525
2024-03-03 | 2024 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 335090.89 | 7:05 | 18:51 | 12586.7 | 12924.8 | 12840.6 | 12836.1 | 12902.4 | 12950 | 12934.4 | 13181.9 | 12883.8 | 12888.8 | 12778.1 | 12902.9 | 12874.7 | 12844 | 12900 | 12933.9 | 12841.3 | 12875.7 | 12903.8 | 12984.6 | 12895.7 | 12934.8 | 12787.4 | 12843.8 | 12734.6 | 11801.9 | 12785.2 | 12742.8 | 12911.2 | 12806.5 | 12743.2 | 12871.7 | 13414.5 | 13446.9 | 13339.6 | 13296.8 | 12973.7 | 12896 | 12915.5 | 12828.1 | 13397.4 | 12688.3 | 13247.9 | 12569.1 | 13062.4 | 13843.3 | 12503.4 | 13359 | 12368 | 12573.4 | 12996 | 12589.9 | 13234.5 | 12412.7 | 13193.3 | 12387.7 | 12387.5 | 13350.8 | 12429.3 | 13298 | 13230.3 | 12369.5 | 13063.2 | 12684.6 | 12811.4 | 12364.1 | 12806.4 | 13053.2 | 13233.6 | 12504.7 | 13161.9 | 12264.5 | 12925 | 12860.9 | 12361.7 | 13159.4 | 12287.3 | 13241.1 | 12376 | 13148.2 | 12532.1 | 13060 | 12618.8 | 13323.7 | 12504.3 | 12977.5 | 12401.4 | 11432.7 | 13091 | 12770 | 12315.8 | 13319.3 | 13077.9 | 12535.3 | 12432.1 | 13126.6 | 12369.8 | 12616.2 | 13166.2 | 12257.5 | 13259.2 | 12272.2 | 13089.9 | 12518.9 | 13083.5 | 12063 | 13170.8 | 12446.6 | 13105.2 | 12441.6 | 13132.9 | 12601.1 | 12324.4 | 13047.3 | 12448.9 | 12322 | 13071.8 | 13189.4 | 13032.7 | 12423.8 | 13114.1 | 12373.2 | 12803.9 | 11213.2 | 12860.3 | 11868.5 | 12996.8 | 12397.7 | 12538.1 | 12530 | 12421.4 | 11118.9 | 12389.1 | 11351.4 | 12447.9 | 12435.8 | 13377.7 | 12433.5 | 13416.1 | 12596.9 | 13318.6 | 12474.7 | 12614 | 12505.5 | 13211.1 | 13423.7 | 13396.1 | 13316.2 | 13363 | 13374.9 | 12674.9 | 13367.3 | 13405.1 | 13422.9 | 13437 | 13418.5 | 13467.5 | 12709 | 13489.5 | 12728.6 | 18.48 | 18.39 | 18.52 | 18.38 | 18.77 | 18.52 | 0 | 34.7 | 0 | 0 | 34.9 | 34.74 | 2.93 | 2.95 | 2.87 | 2.8 | 2.88 | 2.78 | 7.31 | 6.67 | 7.3 | 6.71 | 7.33 | 7.54 | 6.45 | 6.53 | 6.54 | 6.45 | 6.53 | 6.57 | 1.33 | 1.42 | 1.22 | 1.69 | 1.54 | 1.38 | 7.48 | 7.6 | 7.5 | 7.53 | 7.49 | 7.44 | 0.3 | 0.35 | 0.3 | 0.31 | 0.31 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 567729 | 1022 | 555491 | 1096 | 533832.908 | 1437.867 | 6.45 | 6.53 | 6.54 | 6.45 | 6.53 | 6.57 | 7.48 | 7.6 | 7.5 | 7.53 | 7.49 | 7.44 | 1026000 | 2000 | 1016000 | 2000 | 2032933 | 4734 | 2038000 | 2028199 | 11.7667 | 6.5117 | 1.43 | 7.5067 | 0.31667 | 21.96% | 4.218% | 18.51 | 34.78 | 2.8683 | 7.1433 | 2050313.3 | 2031933 | 2546610.8949 | 79.79% | 45 | 7199
2024-03-04 | 2024 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 335090.89 | 7:04 | 18:50 | 12610.6 | 12937.9 | 12855.6 | 12858.7 | 12908.9 | 12951.5 | 12929.4 | 13165.4 | 12902.6 | 12887.1 | 12788.5 | 12910.6 | 12890.7 | 12848.8 | 12911.1 | 12954.8 | 12854.5 | 12887.2 | 12914.9 | 13002.5 | 12905.4 | 12951.5 | 12801.5 | 12857.5 | 12754 | 11851.2 | 12805.7 | 12761 | 12928.8 | 12819.5 | 12767 | 12898.1 | 13447.4 | 13492.2 | 13295.3 | 13248.6 | 12989.8 | 12911.1 | 12930.9 | 12840.2 | 13426.7 | 12732.2 | 13279.1 | 12604.6 | 13092.8 | 13850.4 | 12535.5 | 13386 | 12392.9 | 12597.2 | 13009.2 | 12604.9 | 13232.1 | 12422.9 | 13202.1 | 12418.1 | 12406.1 | 13349.7 | 12454.2 | 13309.2 | 13248.4 | 12400.8 | 13050.8 | 12693.7 | 12814.1 | 12367.1 | 12813.2 | 13058.1 | 13235 | 12516.2 | 13166 | 12288.3 | 12936.8 | 12874.9 | 12380.7 | 13167.6 | 12318.6 | 13245.8 | 12393.7 | 13161.9 | 12544.7 | 13060.9 | 12647.6 | 13327.6 | 12528.1 | 12992.4 | 12401 | 11493.3 | 13087.7 | 12787.7 | 12342.8 | 13334.6 | 13101.2 | 12555.9 | 12440.4 | 13140.8 | 12419.9 | 12658.8 | 13199.7 | 12316.4 | 13289.6 | 12331.3 | 13127.7 | 12551.4 | 13126.1 | 12133.3 | 13214.5 | 12502.9 | 13140.7 | 12480.5 | 13170.2 | 12628.2 | 12377.1 | 13093.2 | 12495.1 | 12365.6 | 13109.9 | 13222.8 | 13064.5 | 12483.1 | 13162.9 | 12432.4 | 12946.2 | 12518.8 | 12909.9 | 11932.7 | 13043.1 | 12452.6 | 12565 | 12560 | 12457.1 | 11183.7 | 12421.3 | 11439.5 | 12463.8 | 12460 | 13407.8 | 12484.6 | 13451.9 | 12640 | 13347.5 | 12520.8 | 12651.3 | 12529.6 | 13223.6 | 13448.2 | 13409 | 13338.8 | 13390.8 | 13400.8 | 12712.7 | 13391.2 | 13409.7 | 13439 | 13457.9 | 13435.3 | 13486.9 | 12734.8 | 13484 | 12748.2 | 19.4984 | 19.2114 | 19.3785 | 19.1542 | 19.1579 | 19.0139 | 0 | 32.9 | 0 | 0 | 32.8 | 32.7 | 3.3167 | 3.3317 | 3.3279 | 3.3679 | 3.256 | 3.1122 | 6.446 | 6.998 | 5.89 | 7.115 | 6.166 | 5.9967 | 6.4617 | 6.5299 | 6.5426 | 6.4571 | 6.5275 | 5.4927 | 1.3396 | 1.4363 | 1.225 | 1.7056 | 1.5369 | 1.1505 | 7.4789 | 7.5852 | 7.492 | 7.5316 | 7.4774 | 7.444 | 0.31583 | 0.35928 | 0.31323 | 0.32692 | 0.31334 | 0.34054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 568755 | 1024 | 556511 | 1097 | 535869.975 | 1442.533 | 6.4617 | 6.5299 | 6.5426 | 6.4571 | 6.5275 | 5.4927 | 7.4789 | 7.5852 | 7.492 | 7.5316 | 7.4774 | 7.444 | 1026000 | 2000 | 1020000 | 1000 | 2037067 | 4666 | 2043000 | 2032401 | 11.7667 | 6.3352 | 1.399 | 7.5015 | 0.32819 | 22.08% | 4.375% | 19.2357 | 32.8 | 3.2854 | 6.4353 | 2055448.2 | 2036200 | 2543368.2814 | 80.06% | 48 | 0
2024-03-05 | 2024 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 335090.89 | 6:50 | 18:35 | 11821.5 | 12144.6 | 12050.9 | 12065.6 | 12100.6 | 12140.1 | 12125.2 | 12399.9 | 12143.1 | 12130 | 12011 | 12146.5 | 12104.1 | 12069.5 | 12106.7 | 12153.3 | 12052.9 | 12083.8 | 12127.5 | 12205.4 | 12123 | 12165.5 | 12016 | 12073.3 | 11976.3 | 11093.2 | 12014.2 | 11969.7 | 12162.8 | 12050.7 | 11989.6 | 12133.3 | 12589.2 | 12625.8 | 12490.9 | 12451.1 | 12221.3 | 12133.9 | 12160.3 | 12073.9 | 12616.5 | 11910.7 | 12490.3 | 11790.7 | 12283.5 | 13053.4 | 11720.5 | 12591 | 11607.6 | 11810.8 | 12233 | 11826.1 | 12464.2 | 11627.3 | 12445.6 | 11647.5 | 11638.7 | 12594.5 | 11682.2 | 12557.7 | 12494.1 | 11625.9 | 12297.5 | 11917.7 | 12066.7 | 11612.4 | 12049.6 | 12299.7 | 12491.3 | 11752.4 | 12406.2 | 11517.5 | 12187.2 | 12105.5 | 11627.4 | 12414.2 | 11558.6 | 12505.5 | 11632.2 | 12413.7 | 11787.3 | 12309.4 | 11892.5 | 12580 | 11774.3 | 12243.7 | 11652.7 | 10792.2 | 12343.2 | 12045.9 | 11581.8 | 12566.9 | 12329.9 | 11779.7 | 11665.1 | 12372.3 | 11652.9 | 11891.7 | 12434.7 | 11543.4 | 12492.5 | 11554.8 | 12341.3 | 11783.7 | 12326.6 | 11366.4 | 12388.3 | 11710.2 | 12352.1 | 11693.9 | 12369.3 | 11854 | 11614.7 | 12324.1 | 11728 | 11605.3 | 12351.2 | 12458.4 | 12307.9 | 11729.2 | 12386.6 | 11667 | 12173 | 11742 | 12125.7 | 11203.4 | 12279.1 | 11689.5 | 11820.3 | 11810.3 | 11706.5 | 10512.5 | 11676.3 | 10766.2 | 11763.4 | 11758.5 | 12710.2 | 11767.7 | 12773.9 | 11956.6 | 12663.2 | 11823 | 11947.5 | 11824.1 | 12562 | 12767.3 | 12745.1 | 12678.8 | 12707.1 | 12711.9 | 12030.7 | 12726.7 | 12740.7 | 12765.7 | 12789.5 | 12759.9 | 12815.4 | 12042.3 | 12815.2 | 12066.7 | 20.8651 | 20.3488 | 20.4868 | 20.4389 | 20.3239 | 20.3091 | 0 | 32.6 | 0 | 0 | 32.6 | 32.6 | 3.9896 | 3.9922 | 3.8862 | 4.1307 | 4.067 | 3.9635 | 7.439 | 7.377 | 7.043 | 7.698 | 7.604 | 7.698 | 6.1083 | 6.1675 | 6.167 | 6.1275 | 6.2009 | 6.2561 | 1.2876 | 1.3381 | 1.1799 | 1.65 | 1.4557 | 1.3022 | 6.9146 | 6.9942 | 6.9129 | 7.0008 | 6.9601 | 6.8265 | 0.31751 | 0.36556 | 0.31721 | 0.33791 | 0.32132 | 0.34617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 569719 | 1025 | 557472 | 1099 | 537786.642 | 1447.133 | 6.1083 | 6.1675 | 6.167 | 6.1275 | 6.2009 | 6.2561 | 6.9146 | 6.9942 | 6.9129 | 7.0008 | 6.9601 | 6.8265 | 964000 | 1000 | 961000 | 2000 | 1916667 | 4600 | 1922000 | 1912067 | 11.75 | 6.1712 | 1.3689 | 6.9349 | 0.33428 | 22.18% | 4.82% | 20.4621 | 32.6 | 4.0049 | 7.4765 | 1934126.3 | 1915933 | 2354932.4444 | 81.36% | 59 | 3245
2024-03-06 | 2024 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 335090.89 | 7:11 | 18:52 | 10537.4 | 10802.5 | 10645.7 | 10589.8 | 10689 | 10746.8 | 10759.1 | 11150.8 | 10934 | 10981.2 | 10814.6 | 10967.3 | 10831.1 | 10890.6 | 10754.4 | 10809.7 | 10735.2 | 10795.4 | 10941.8 | 11008.1 | 10968.3 | 10979.4 | 10859.4 | 10916 | 10880.6 | 9850.8 | 10861.3 | 10845.5 | 11084.8 | 10989.5 | 10941.7 | 11103.2 | 11150.7 | 11184.9 | 11167.7 | 11122.5 | 11191.3 | 11096.7 | 11143.3 | 11024.5 | 11356.3 | 10523.4 | 11337.4 | 10425.6 | 11090.1 | 11986.1 | 10414.2 | 11349.1 | 10347.4 | 10604.7 | 11084.1 | 10647.3 | 11355.1 | 10328 | 11393.4 | 10435.1 | 10417.5 | 11593.2 | 10414.8 | 11504.7 | 11420.2 | 10389 | 11196.6 | 10774.6 | 11029.8 | 10571.2 | 11046.8 | 11369.9 | 11590.8 | 10738.5 | 11511.4 | 10454.6 | 11177.5 | 11161.3 | 10520.7 | 11542.2 | 10501 | 11519.7 | 10525 | 11455.8 | 10744.1 | 11383.4 | 10897.5 | 11696.8 | 10753.8 | 11307.1 | 10652.3 | 9651.5 | 11442.8 | 11071.2 | 10487.5 | 11672.2 | 11399.4 | 10743.3 | 10642.2 | 11428.6 | 10488.3 | 10738.9 | 11434.1 | 10333 | 11493.7 | 10363.9 | 11278 | 10569.6 | 11321.7 | 10145.5 | 11304.3 | 10489.8 | 11294.1 | 10524.2 | 11313.2 | 10632.3 | 10372.1 | 11227.9 | 10487.7 | 10351.4 | 11246.4 | 11375.5 | 11182.9 | 10537.2 | 11308.8 | 10470.3 | 11016.9 | 10456.3 | 10939.1 | 9927.7 | 11156.5 | 10490.1 | 10675.9 | 10666.9 | 10544.5 | 9335.5 | 10481.6 | 9450 | 10430 | 10439.6 | 11506.3 | 10450.6 | 11586.6 | 10649.9 | 11526.5 | 10496.3 | 10649.5 | 10524.7 | 11358.6 | 11559.6 | 11514.4 | 11466.4 | 11466.8 | 11510.6 | 10694 | 11511.6 | 11544 | 11585.4 | 11547.6 | 11536.5 | 11592.7 | 10694 | 11571.5 | 10761.7 | 22.9336 | 22.644 | 22.5438 | 22.6881 | 22.8892 | 22.7653 | 0 | 37.5 | 0 | 0 | 38 | 37.5 | 2.4053 | 2.4308 | 2.442 | 2.4666 | 2.3663 | 2.4321 | 5.44 | 5.692 | 5.053 | 5.163 | 5.151 | 6.454 | 5.4412 | 5.605 | 5.5206 | 5.6321 | 5.6119 | 5.5972 | 1.0702 | 1.2611 | 0.97221 | 1.4251 | 1.327 | 1.2268 | 6.1241 | 6.3342 | 6.112 | 6.3615 | 6.2359 | 6.1906 | 0.27483 | 0.32951 | 0.27993 | 0.31135 | 0.29303 | 0.31167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 570591 | 1027 | 558342 | 1101 | 539522.509 | 1451.933 | 5.4412 | 5.605 | 5.5206 | 5.6321 | 5.6119 | 5.5972 | 6.1241 | 6.3342 | 6.112 | 6.3615 | 6.2359 | 6.1906 | 872000 | 2000 | 870000 | 2000 | 1735867 | 4800 | 1738000 | 1731067 | 11.6833 | 5.568 | 1.2137 | 6.2264 | 0.30005 | 21.8% | 4.819% | 22.744 | 37.6667 | 2.4238 | 5.4922 | 1748425.6 | 1733800 | 2097804.6208 | 82.65% | 66 | 7846
2024-03-07 | 2024 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 335090.89 | 7:04 | 18:52 | 12116.5 | 12496.1 | 12432.5 | 12408.2 | 12500.3 | 12559.1 | 12537.3 | 12824.8 | 12463.2 | 12441.2 | 12355.6 | 12480.1 | 12460.8 | 12425.7 | 12478.9 | 12523.8 | 12436.4 | 12468.3 | 12488.2 | 12561.6 | 12490.6 | 12515.1 | 12357.8 | 12426.8 | 12304.3 | 11159.9 | 12341.7 | 12304.7 | 12514.2 | 12411.2 | 12334.8 | 12483.9 | 12914.6 | 12950 | 12927.3 | 12876.4 | 12593.2 | 12504.8 | 12530.2 | 12423.4 | 13110.5 | 12297.7 | 12959.4 | 12142.9 | 12674.5 | 13557.9 | 12085.8 | 13077.4 | 11854.5 | 12088.5 | 12580.5 | 12120.3 | 12845.1 | 11912.3 | 12805.5 | 11893 | 11871.5 | 12978.5 | 11908.2 | 12925.2 | 12841.7 | 11857.7 | 12630.4 | 12207.5 | 12393.4 | 11885.1 | 12371.3 | 12665 | 12877.7 | 12037.4 | 12792.3 | 11722.7 | 12516.8 | 12447.3 | 11869.6 | 12792.4 | 11773.8 | 12874.7 | 11876.5 | 12771.5 | 12096.2 | 12702.4 | 12183.5 | 12995.1 | 12067.7 | 12592.2 | 11958.2 | 10757.3 | 12681 | 12362.5 | 11819.1 | 12971.9 | 12712.4 | 12087.7 | 11981.9 | 12731.3 | 11839.6 | 12110.1 | 12745.2 | 11706.2 | 12825.5 | 11720.3 | 12630.3 | 11968.8 | 12639.3 | 11466.6 | 12676.6 | 11894.5 | 12644.7 | 11893.1 | 12693.8 | 12048.1 | 11769.3 | 12603.9 | 11912.6 | 11759.8 | 12621.6 | 12761.4 | 12579.7 | 11916.3 | 12683.1 | 11844.8 | 12439.3 | 11928.9 | 12389.4 | 11179.7 | 12546.7 | 11890.1 | 12045 | 12005.1 | 11910.1 | 10416.1 | 11877.4 | 10658.5 | 11914.3 | 11924.1 | 13054.4 | 11969 | 13087 | 12147.5 | 12973.6 | 12003.6 | 12152.4 | 12029.3 | 12869.8 | 13115.6 | 13086.4 | 13004.7 | 13034.3 | 13050.2 | 12243.4 | 13043.6 | 13089.3 | 13120.9 | 13110.3 | 13097.8 | 13156.7 | 12272.7 | 13165.8 | 12307.8 | 24.147 | 23.9718 | 23.9022 | 24.0708 | 24.1519 | 24.0253 | 0 | 37.3 | 0 | 0 | 37.8 | 37.4 | 3.4615 | 3.467 | 3.4088 | 3.6296 | 3.369 | 3.3258 | 7.003 | 7.027 | 6.881 | 7.084 | 7.025 | 6.957 | 6.1165 | 6.1867 | 6.1983 | 6.1176 | 6.1695 | 6.2366 | 1.2635 | 1.3722 | 1.1448 | 1.6061 | 1.4614 | 1.3451 | 7.0318 | 7.1001 | 7.0015 | 7.0659 | 6.9869 | 6.98 | 0.29588 | 0.34007 | 0.29573 | 0.30953 | 0.29693 | 0.3207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 571583 | 1028 | 559324 | 1102 | 541488.776 | 1456.667 | 6.1165 | 6.1867 | 6.1983 | 6.1176 | 6.1695 | 6.2366 | 7.0318 | 7.1001 | 7.0015 | 7.0659 | 6.9869 | 6.98 | 992000 | 1000 | 982000 | 1000 | 1966267 | 4734 | 1972000 | 1961533 | 11.8 | 6.1709 | 1.3655 | 7.0277 | 0.3098 | 22.13% | 4.408% | 24.0448 | 37.5 | 3.4436 | 6.9962 | 1981683.9 | 1964401 | 2350845.2068 | 83.56% | 52 | 0
2024-03-08 | 2024 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 335090.89 | 7:02 | 18:53 | 12437 | 12782.7 | 12708.6 | 12710.2 | 12766.5 | 12822.5 | 12811.3 | 13080.4 | 12757.5 | 12742.5 | 12641.2 | 12758.9 | 12737.2 | 12700.5 | 12739.7 | 12796.7 | 12689.4 | 12736.7 | 12757.2 | 12836 | 12764.2 | 12796.7 | 12656.2 | 12716.4 | 12594.3 | 11641.5 | 12632.9 | 12599.7 | 12788.6 | 12687.9 | 12628.7 | 12760.2 | 13268.7 | 13298.1 | 13276.3 | 13233 | 12859.3 | 12781.7 | 12805.2 | 12704.3 | 13348 | 12618.6 | 13198.7 | 12487.3 | 12975.7 | 13778.9 | 12404.6 | 13306.2 | 12208.6 | 12417 | 12858.3 | 12443.1 | 13092.9 | 12244.2 | 13053.7 | 12238.1 | 12223.9 | 13209.2 | 12278.2 | 13176.2 | 13102.2 | 12216.2 | 12907.9 | 12525.8 | 12666 | 12206.6 | 12647.7 | 12903.9 | 13099.6 | 12342.9 | 13025.5 | 12099.6 | 12791.1 | 12721 | 12213.1 | 13024.1 | 12134.7 | 13113.1 | 12229.2 | 13026.1 | 12407.4 | 12950.7 | 12491.8 | 13213 | 12378.1 | 12858.1 | 12265.9 | 11279 | 12963.5 | 12659.8 | 12193.5 | 13217.8 | 12968.1 | 12398.9 | 12294 | 13021.1 | 12243.5 | 12498.8 | 13065.8 | 12143 | 13163.3 | 12168.2 | 13004.2 | 12397 | 12988.5 | 11962 | 13076.7 | 12315.1 | 13015.7 | 12330.9 | 13047.1 | 12488.3 | 12199.6 | 12918.1 | 12321.5 | 12190.6 | 12950.9 | 13047.4 | 12901.4 | 12297.7 | 12985.1 | 12236.7 | 12797.8 | 12348.1 | 12754.3 | 11728 | 12874.8 | 12271.9 | 12400 | 12322.1 | 12285.4 | 10942.5 | 12238.4 | 11194.5 | 12290 | 12289.2 | 13277.4 | 12310.2 | 13319.6 | 12487.2 | 13232.7 | 12357.6 | 12493.7 | 12362.1 | 13111.9 | 13322.8 | 13300.8 | 13229.8 | 13266.1 | 13275.6 | 12564.4 | 13271.2 | 13290.2 | 13314.8 | 13323.7 | 13306.6 | 13365.9 | 12573.6 | 13367.3 | 12601.1 | 23.4374 | 23.2356 | 23.2587 | 23.3227 | 23.3099 | 23.2704 | 0 | 36.7 | 0 | 0 | 37 | 36.8 | 3.1271 | 3.1889 | 3.197 | 3.2552 | 3.186 | 3.0757 | 6.832 | 6.512 | 5.916 | 6.981 | 6.259 | 7.678 | 6.4444 | 6.518 | 6.5412 | 6.4338 | 6.5374 | 6.5731 | 1.3721 | 1.4573 | 1.248 | 1.7298 | 1.5688 | 1.4247 | 7.3934 | 7.4717 | 7.3878 | 7.4275 | 7.3989 | 7.3347 | 0.31552 | 0.5333 | 0.31422 | 0.32768 | 0.31715 | 0.33953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 572599 | 1030 | 560332 | 1104 | 543503.642 | 1461.4 | 6.4444 | 6.518 | 6.5412 | 6.4338 | 6.5374 | 6.5731 | 7.3934 | 7.4717 | 7.3878 | 7.4275 | 7.3989 | 7.3347 | 1016000 | 2000 | 1008000 | 2000 | 2014866 | 4733 | 2020000 | 2010133 | 11.85 | 6.508 | 1.4668 | 7.4024 | 0.3579 | 22.54% | 4.835% | 23.3058 | 36.8333 | 3.1717 | 6.6963 | 2031645.4 | 2013733 | 2472907.4059 | 81.43% | 43 | 0
2024-03-09 | 2024 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 335090.89 | 7:01 | 18:51 | 11861.8 | 12219.8 | 12157.6 | 12164.2 | 12216.8 | 12256.2 | 12246.6 | 12523.7 | 12206 | 12175.8 | 12076 | 12203.2 | 12171.4 | 12130.2 | 12182.5 | 12232.9 | 12136.4 | 12172.9 | 12189.4 | 12268.3 | 12196.1 | 12219.5 | 12065.5 | 12129.5 | 12013 | 11043.4 | 12049.3 | 12007.6 | 12211.4 | 12111.4 | 12046.9 | 12183.8 | 12609.5 | 12646.1 | 12628.8 | 12580.9 | 12278.9 | 12192.8 | 12214.9 | 12116.5 | 12790.9 | 12039.9 | 12653.9 | 11895.5 | 12400.5 | 13209.8 | 11830 | 12761.2 | 11611.1 | 11825.6 | 12288.9 | 11855.7 | 12530.9 | 11652.9 | 12494.1 | 11635.8 | 11622.3 | 12645.4 | 11672.7 | 12613.3 | 12540.3 | 11624.9 | 12325.6 | 11936.8 | 12073.2 | 11597.8 | 12055 | 12340.6 | 12534 | 11748.5 | 12444.3 | 11485.8 | 12202.5 | 12124.9 | 11603 | 12450.1 | 11520.3 | 12538.8 | 11609.7 | 12444.5 | 11808.4 | 12383.1 | 11900 | 12655.7 | 11786.2 | 12278.1 | 11681.1 | 10707.3 | 12388.8 | 12073.6 | 11596.7 | 12663.2 | 12415.6 | 11829.1 | 11713 | 12442.3 | 11626.2 | 11900.2 | 12487.9 | 11523.9 | 12594.9 | 11543.1 | 12412.6 | 11776.5 | 12421.3 | 11345.7 | 12505.8 | 11710.4 | 12437.8 | 11726.6 | 12459.6 | 11869.1 | 11599.1 | 12359.5 | 11707.8 | 11578.2 | 12383.4 | 12501.8 | 12332.1 | 11718.4 | 12439 | 11652.5 | 12211 | 11736.8 | 12145.5 | 11108.5 | 12314.5 | 11679.1 | 11827 | 11796.4 | 11688.5 | 10404.9 | 11653.4 | 10650.4 | 11727.1 | 11737 | 12768.8 | 11753 | 12816.7 | 11938.7 | 12721.5 | 11803.6 | 11931.9 | 11820.4 | 12584 | 12809.3 | 12784.4 | 12723.1 | 12752.6 | 12761.3 | 12013.1 | 12757.9 | 12788.4 | 12806.8 | 12829.4 | 12803.3 | 12849.6 | 12026.2 | 12855.7 | 12049.4 | 25.2571 | 24.7577 | 24.7858 | 24.7174 | 24.6713 | 24.621 | 0 | 37.1 | 0 | 0 | 36.9 | 36.8 | 3.5385 | 3.5445 | 3.5004 | 3.6584 | 3.6159 | 3.5323 | 7.876 | 7.382 | 7.129 | 7.428 | 7.508 | 7.248 | 6.1529 | 6.1968 | 6.2365 | 6.1278 | 6.2535 | 6.2008 | 1.3143 | 1.3936 | 1.1842 | 1.6565 | 1.3624 | 1.4849 | 7.0055 | 7.0507 | 6.9925 |  | 7.0237 | 6.9674 | 0.29874 | 0.34077 | 0.29651 | 0.31358 | 0.32155 | 0.29952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 573568 | 1031 | 561296 | 1106 | 545427.843 | 1465.867 | 6.1529 | 6.1968 | 6.2365 | 6.1278 | 6.2535 | 6.2008 | 7.0055 | 7.0507 | 6.9925 | 0 | 7.0237 | 6.9674 | 969000 | 1000 | 964000 | 2000 | 1924201 | 4467 | 1930000 | 1919734 | 11.8333 | 6.1947 | 1.3993 | 7.008 | 0.31178 | 22.59% | 4.449% | 24.8017 | 36.9333 | 3.565 | 7.4285 | 1939933.3 | 1922933 | 2343297.4988 | 82.06% | 63 | 4589
2024-03-10 | 2024 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 335090.89 | 7:00 | 18:51 | 10974.5 | 11322.8 | 11242.9 | 11257.5 | 11309 | 11348.2 | 11353.3 | 11621.1 | 11325.5 | 11293.2 | 11198.9 | 11318.4 | 11291.2 | 11252 | 11311.7 | 11341.3 | 11260.4 | 11293.6 | 11310.3 | 11383.6 | 11329 | 11343.5 | 11208.9 | 11268.4 | 11135.5 | 10146.5 | 11167.8 | 11136.8 | 11338.4 | 11251 | 11179.6 | 11313.9 | 11625.4 | 11656.8 | 11647.2 | 11605 | 11397.2 | 11312.6 | 11340.3 | 11249.5 | 11860.7 | 11123.8 | 11763.1 | 10996.8 | 11511.3 | 12274.2 | 10968 | 11859.1 | 10725.3 | 10935.8 | 11399.9 | 10981.9 | 11640.1 | 10795.2 | 11598.2 | 10755.8 | 10752.7 | 11759.6 | 10765.4 | 11717.4 | 11635.2 | 10728.2 | 11447 | 11055 | 11214.8 | 10713.3 | 11171.3 | 11440.1 | 11649.6 | 10852.9 | 11520.4 | 10572.6 | 11330.5 | 11211.4 | 10735.3 | 11539.9 | 10622.3 | 11645.3 | 10723.8 | 11530.6 | 10907 | 11460.7 | 11007.3 | 11730.5 | 10896.6 | 11375.5 | 10796.2 | 9777.4 | 11462.3 | 11188.2 | 10683 | 11733.1 | 11513.2 | 10964.9 | 10875 | 11533.4 | 10730.7 | 10996.1 | 11573.7 | 10613.1 | 11672.2 | 10646.4 | 11498 | 10862.1 | 11513.3 | 10443.3 | 11579.1 | 10791.9 | 11512.5 | 10824.3 | 11543.6 | 10945.2 | 10677.8 | 11406.1 | 10793 | 10663.7 | 11450.9 | 11542.6 | 11401.9 | 10796.3 | 11478.6 | 10716.1 | 11267 | 10797.8 | 11192 | 10145.4 | 11358.4 | 10751.2 | 10899.8 | 10888.4 | 10757.6 | 9464.5 | 10741.8 | 9690.1 | 10802.7 | 10817.5 | 11881.9 | 10866.8 | 11940.7 | 11077.7 | 11819.4 | 10924.2 | 11044.1 | 10918.2 | 11724.1 | 11943.5 | 11910.2 | 11861.2 | 11878.8 | 11880.6 | 11149.1 | 11889.2 | 11919.9 | 11946.7 | 11977.1 | 11950.6 | 11990.1 | 11164.1 | 12003.5 | 11206.3 | 27.0238 | 26.7363 | 26.7299 | 26.7744 | 26.7915 | 26.9127 | 0 | 40.2 | 0 | 0 | 40.1 | 40.6 | 3.2934 | 3.1956 | 3.2109 | 3.2784 | 3.1573 | 3.0744 | 7.01 | 6.384 | 7.01 | 6.771 | 7.445 | 7.841 | 5.8097 | 5.8634 | 5.8905 | 5.7994 | 5.907 | 5.8428 | 1.2771 | 1.2839 | 1.1443 | 1.6017 | 1.2445 | 1.3691 | 6.4632 | 6.5147 | 6.4531 | 6.4109 | 6.4872 | 6.4297 | 0.30449 | 0.35531 | 0.30982 | 0.32936 | 0.33261 | 0.31147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 574466 | 1033 | 562187 | 1108 | 547210.909 | 1470.467 | 5.8097 | 5.8634 | 5.8905 | 5.7994 | 5.907 | 5.8428 | 6.4632 | 6.5147 | 6.4531 | 6.4109 | 6.4872 | 6.4297 | 898000 | 2000 | 891000 | 2000 | 1783066 | 4600 | 1785000 | 1778466 | 11.85 | 5.8521 | 1.3201 | 6.4598 | 0.32384 | 22.56% | 5.013% | 26.8281 | 40.3 | 3.2017 | 7.0768 | 1796205.5 | 1780933 | 2141465.7347 | 83.16% | 78 | 26863
2024-03-11 | 2024 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 335090.89 | 7:01 | 18:54 | 12052.7 | 12425.5 | 12315.4 | 12323.7 | 12362.7 | 12458.1 | 12475.5 | 12800.2 | 12418.7 | 12423.3 | 12298.6 | 12428.7 | 12402.4 | 12362.3 | 12403 | 12454.9 | 12371.5 | 12409 | 12427.6 | 12496.9 | 12431.7 | 12448.9 | 12294.3 | 12368.6 | 12219.3 | 11053.5 | 12257.2 | 12231.2 | 12455.1 | 12351.6 | 12280.6 | 12437.2 | 12825.4 | 12859.1 | 12841.2 | 12803.1 | 12544.5 | 12441.7 | 12465.3 | 12360.4 | 13094.8 | 12232.3 | 12935.7 | 12090.5 | 12619.8 | 13512.9 | 12013.7 | 13059.8 | 11761 | 12000.5 | 12524.6 | 12065.2 | 12797.7 | 11832.3 | 12749.7 | 11798.9 | 11774.8 | 12924.6 | 11796.5 | 12879 | 12786.6 | 11761.8 | 12581.8 | 12159.4 | 12323.3 | 11785 | 12285.9 | 12609 | 12819.1 | 11951.4 | 12723.9 | 11619.1 | 12450.7 | 12368.8 | 11778.4 | 12726.9 | 11674 | 12820.9 | 11772.7 | 12704.8 | 12020.4 | 12653.7 | 12110.2 | 12949.2 | 11993.7 | 12536.2 | 11896.7 | 10668.6 | 12644.7 | 12308.2 | 11755.9 | 12942.9 | 12666.1 | 12011.1 | 11897.1 | 12724.6 | 11813 | 12120.4 | 12788.8 | 11684.2 | 12870.9 | 11717.8 | 12671 | 11973.5 | 12688 | 11465.6 | 12775.2 | 11917.7 | 12689.6 | 11913.8 | 12732.4 | 12087.9 | 11753.9 | 12604 | 11905.1 | 11735.6 | 12648.2 | 12759.8 | 12597.1 | 11887.4 | 12704.9 | 11818.8 | 12470.9 | 11931.6 | 12408.8 | 11116.2 | 12563.5 | 11838.8 | 11996.7 | 11985.8 | 11859.3 | 10325 | 11814.4 | 10553.4 | 11885.5 | 11885.8 | 13046.5 | 11930 | 13084.2 | 12084.9 | 12999.5 | 11996.3 | 12150.9 | 11987.3 | 12821.1 | 13080.7 | 13033.1 | 12965.6 | 13012.1 | 13028.3 | 12202.3 | 13021.9 | 13034.8 | 13067.4 | 13085.5 | 13069.2 | 13112.8 | 12214.3 | 13119.2 | 12243.4 | 28.4247 | 28.3664 | 28.5972 | 28.3241 | 28.5833 | 28.5201 | 0 | 43.9 | 0 | 0 | 43.9 | 44.2 | 3.2753 | 3.2674 | 3.0111 | 3.2706 | 3.0158 | 3.1203 | 7.275 | 7.193 | 7.24 | 7.715 | 7.034 | 6.992 | 6.273 | 6.3664 | 6.3583 | 6.2695 | 6.3878 | 6.3497 | 1.3294 | 1.4173 | 1.1865 | 1.6874 | 1.3688 | 1.4713 | 7.1336 | 7.1869 | 7.0962 | 7.0007 | 7.1599 | 7.1162 | 0.29211 | 0.33504 | 0.29106 | 0.3049 | 0.31882 | 0.2963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575452 | 1034 | 563167 | 1109 | 549170.176 | 1475.133 | 6.273 | 6.3664 | 6.3583 | 6.2695 | 6.3878 | 6.3497 | 7.1336 | 7.1869 | 7.0962 | 7.0007 | 7.1599 | 7.1162 | 986000 | 1000 | 980000 | 1000 | 1959267 | 4666 | 1964000 | 1954601 | 11.8833 | 6.3341 | 1.4101 | 7.1156 | 0.30637 | 22.26% | 4.306% | 28.4693 | 44 | 3.1601 | 7.2415 | 1974379.3 | 1957801 | 2343413.312 | 83.54% | 61 | 0
2024-03-12 | 2024 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 335090.89 | 7:00 | 18:53 | 12071.4 | 12461.9 | 12383.3 | 12341.6 | 12466.6 | 12518.3 | 12504 | 12827.5 | 12461.1 | 12435.7 | 12348.3 | 12467 | 12459.7 | 12410.5 | 12469.3 | 12512.9 | 12422.2 | 12451.9 | 12467.2 | 12542 | 12474.4 | 12491.6 | 12330.1 | 12402.9 | 12230.3 | 11134.8 | 12303.7 | 12267.7 | 12495.2 | 12383.9 | 12313.2 | 12469.3 | 12863.2 | 12897.6 | 12888.1 | 12839.6 | 12564.2 | 12463.3 | 12483.3 | 12380.8 | 13093.5 | 12262.5 | 12939.3 | 12116.7 | 12634.9 | 13510 | 12036 | 13065.6 | 11808.1 | 12045.6 | 12565.2 | 12100.6 | 12829.4 | 11881.3 | 12782.4 | 11845.6 | 11824.1 | 12951.5 | 11843.2 | 12905.7 | 12819.8 | 11806.5 | 12617.6 | 12192.5 | 12335.4 | 11811.9 | 12307.2 | 12627 | 12833.4 | 11977.3 | 12735.7 | 11668.4 | 12476.5 | 12390.5 | 11818.4 | 12747.2 | 11720 | 12838 | 11804.9 | 12723.8 | 12059.1 | 12684.2 | 12148.9 | 12964.9 | 12034.7 | 12569.3 | 11926.3 | 10743.9 | 12670.2 | 12338.3 | 11798 | 12969 | 12704.5 | 12061.6 | 11941 | 12735.9 | 11841.6 | 12141.1 | 12808 | 11728.3 | 12893.9 | 11765.9 | 12703.6 | 12018.2 | 12712 | 11517.4 | 12805.7 | 11957.3 | 12722.7 | 11951.9 | 12764.5 | 12138 | 11805.4 | 12633.8 | 11954.7 | 11772.9 | 12675.2 | 12790.4 | 12628.8 | 11931.8 | 12725.7 | 11860.9 | 12505.6 | 11977.3 | 12445.7 | 11150.8 | 12590.1 | 11887.2 | 12054.4 | 12042.8 | 11916.7 | 10402 | 11858.7 | 10594.8 | 11931.4 | 11937.4 | 13041.9 | 11944.1 | 13085.8 | 12111.1 | 13005.3 | 12015.8 | 12159.5 | 12037.2 | 12836.4 | 13082.2 | 13031.1 | 12973.7 | 13017.5 | 13030.7 | 12218.8 | 13022.3 | 13063.2 | 13080.7 | 13100.6 | 13079.6 | 13118.6 | 12234.9 | 13130.7 | 12257.4 | 27.6495 | 27.3482 | 27.4568 | 27.4251 | 27.392 | 27.5353 | 0 | 42.1 | 0 | 0 | 41.9 | 42.2 | 2.6413 | 2.6776 | 2.5341 | 2.7194 | 2.6606 | 2.5524 | 5.506 | 8.558 | 6.143 | 6.676 | 6.579 | 5.857 | 6.3136 | 6.3757 | 6.3711 | 6.2796 | 6.3949 | 6.3474 | 1.3439 | 1.4318 | 1.1986 | 1.7069 | 1.3907 | 1.4902 | 7.1351 | 7.174 | 7.097 | 7.1784 | 7.1409 | 7.0979 | 0.30536 | 0.35055 | 0.30651 | 0.32256 | 0.33368 | 0.30982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576442 | 1036 | 564150 | 1111 | 551135.043 | 1479.933 | 6.3136 | 6.3757 | 6.3711 | 6.2796 | 6.3949 | 6.3474 | 7.1351 | 7.174 | 7.097 | 7.1784 | 7.1409 | 7.0979 | 990000 | 2000 | 983000 | 2000 | 1964867 | 4800 | 1969000 | 1960067 | 11.8833 | 6.347 | 1.427 | 7.1372 | 0.32141 | 22.48% | 4.503% | 27.4678 | 42.0667 | 2.6309 | 6.5532 | 1979566.3 | 1963266 | 2350505.5034 | 83.53% | 57 | 0
2024-03-13 | 2024 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 335090.89 | 7:00 | 18:54 | 11799.6 | 12195.3 | 12130.3 | 12100.1 | 12205.9 | 12270.5 | 12280.4 | 12559.2 | 12178 | 12156.4 | 12074.9 | 12191.9 | 12180.9 | 12136.1 | 12219.4 | 12240.6 | 12164.4 | 12184 | 12197.8 | 12268.1 | 12208.4 | 12225.2 | 12071.6 | 12139.2 | 11988.6 | 10864.9 | 12026.2 | 11999 | 12226.8 | 12126.2 | 12051.5 | 12193.7 | 12573 | 12599.7 | 12592.2 | 12547.8 | 12283.7 | 12189.9 | 12214.6 | 12114.9 | 12822.6 | 12038.6 | 12679.9 | 11875.3 | 12409 | 13263.1 | 11798.6 | 12791.9 | 11539.1 | 11770.8 | 12285.6 | 11834.8 | 12552.2 | 11634.5 | 12494.7 | 11583 | 11556.7 | 12673.3 | 11577.8 | 12615.8 | 12531 | 11539.4 | 12337.8 | 11919 | 12090.1 | 11563.2 | 12048.5 | 12366.6 | 12565.6 | 11719.2 | 12465.2 | 11403.7 | 12216.6 | 12120.3 | 11567.6 | 12462.9 | 11452.8 | 12565.7 | 11568.8 | 12456.3 | 11805.7 | 12419.9 | 11905 | 12706.2 | 11794.7 | 12327.1 | 11682.1 | 10521.2 | 12412 | 12117.9 | 11555.3 | 12709.4 | 12452.2 | 11824.1 | 11730.7 | 12504.9 | 11634.4 | 11907 | 12570.8 | 11504.9 | 12640.3 | 11538.1 | 12456.5 | 11775.8 | 12471.4 | 11302.3 | 12549.8 | 11716.4 | 12471.7 | 11717.5 | 12514 | 11874.8 | 11562.7 | 12357.1 | 11707.3 | 11534.8 | 12419 | 12502.3 | 12354.8 | 11663.3 | 12439.9 | 11598.7 | 12246.1 | 11725 | 12155 | 10961.4 | 12307.6 | 11618.1 | 11764.9 | 11750.4 | 11641.5 | 10182.8 | 11610.5 | 10412.3 | 11648 | 11651.6 | 12774.2 | 11702.7 | 12808.1 | 11892.7 | 12711.5 | 11753.2 | 11898.6 | 11753.8 | 12556.3 | 12806.9 | 12764.3 | 12707.4 | 12740.4 | 12748.8 | 11964.3 | 12744 | 12762.9 | 12794.5 | 12809.1 | 12796.1 | 12837.1 | 11977.2 | 12831.1 | 11999.5 | 27.0286 | 26.7209 | 26.822 | 26.9189 | 26.8567 | 27.4803 | 0 | 39.3 | 0 | 0 | 39.1 | 39.9 | 4.3317 | 4.2704 | 4.2287 | 4.2284 | 4.2086 | 4.2811 | 8.562 | 8.019 | 9.642 | 8.269 | 7.825 | 8.902 | 6.1424 | 6.2095 | 6.2065 | 6.1197 | 6.2277 | 6.2268 | 1.3186 | 1.3972 | 1.1762 | 1.6769 | 1.358 | 1.465 | 6.879 | 6.9296 | 6.8412 | 6.9202 | 6.8915 | 6.8998 | 0.32176 | 0.37357 | 0.32383 | 0.34367 | 0.35659 | 0.33108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577410 | 1038 | 565113 | 1113 | 553058.31 | 1484.6 | 6.1424 | 6.2095 | 6.2065 | 6.1197 | 6.2277 | 6.2268 | 6.879 | 6.9296 | 6.8412 | 6.9202 | 6.8915 | 6.8998 | 968000 | 2000 | 963000 | 2000 | 1923267 | 4667 | 1927000 | 1918600 | 11.9 | 6.1888 | 1.3987 | 6.8936 | 0.34175 | 22.6% | 4.958% | 26.9712 | 39.4333 | 4.2581 | 8.5365 | 1937792.4 | 1921600 | 2300153.2166 | 83.54% | 52 | 0
2024-03-14 | 2024 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 335090.89 | 6:59 | 18:56 | 12175.6 | 12560.7 | 12483.9 | 12457.2 | 12530 | 12621.3 | 12634.3 | 12947.5 | 12555.7 | 12537.1 | 12447.5 | 12564 | 12566.2 | 12497.9 | 12561 | 12614.7 | 12519.8 | 12549.9 | 12574.4 | 12646 | 12573.8 | 12611.8 | 12442.6 | 12515.6 | 12396 | 11265.2 | 12415.5 | 12385.2 | 12598.8 | 12478.2 | 12421.8 | 12576.4 | 12996.8 | 13027.8 | 13015.2 | 12969.9 | 12667 | 12558.8 | 12584.6 | 12486.1 | 11778.1 | 11142.2 | 11559.4 | 10912.5 | 11341.5 | 12000.5 | 10869.5 | 11652.9 | 11913.6 | 12155.3 | 12658.3 | 12208.4 | 12911.5 | 11999.2 | 12863.8 | 11950.6 | 11931.5 | 13028.4 | 11957 | 12989.3 | 12905.8 | 11916.3 | 12691.5 | 12277.5 | 12440.9 | 11923.4 | 12418.5 | 12730.4 | 12926.4 | 12094.9 | 12838.3 | 11793.9 | 12579.6 | 12498 | 11942.5 | 12843.5 | 11837.8 | 12931.1 | 11943.5 | 12839.4 | 12185.9 | 12781.2 | 12282 | 13064.6 | 12173.7 | 12687.5 | 12056.4 | 10910.1 | 12782 | 12470 | 11942.5 | 13054.6 | 12793 | 12163 | 12030.1 | 12838.6 | 11982.6 | 12262 | 12914.4 | 11855.9 | 12991.3 | 11872 | 12803.3 | 12118 | 12805.4 | 11625.1 | 12891.6 | 12035.1 | 12816.8 | 12038.8 | 12838.5 | 12207.7 | 11925 | 12748.1 | 12054.9 | 11887.2 | 12781.7 | 12889.1 | 12729.9 | 12049.9 | 12830.2 | 11985.8 | 12607.7 | 12063.1 | 12553.4 | 11369.1 | 12706.4 | 12014.7 | 12125.5 | 12111.9 | 12022.3 | 10545.2 | 11960.8 | 10802.4 | 12032.3 | 12036.2 | 13142.2 | 12093 | 13183 | 12278.7 | 13090.3 | 12135.5 | 12281 | 12123.2 | 12942.1 | 13171.6 | 13141 | 13080.7 | 13112.3 | 13117.3 | 12354.2 | 13120.1 | 13096 | 13146.1 | 13179.4 | 13160.8 | 13203.8 | 12360.8 | 13176.2 | 12376.6 | 27.07 | 26.79 | 26.84 | 26.78 | 26.81 | 26.95 | 0 | 42.3 | 0 | 0 | 42.4 | 42.5 | 2.39 | 2.28 | 2.18 | 2.38 | 2.29 | 2.34 | 5.34 | 4.56 | 5.11 | 5.68 | 5.87 | 5.14 | 6.47 | 6.56 | 6.53 | 6.52 | 6.57 | 6.57 | 1.39 | 1.52 | 1.24 | 1.77 | 1.48 | 1.59 | 7.26 | 7.32 | 7.21 | 7.3 | 7.29 | 7.29 | 0.34 | 0.39 | 0.34 | 0.37 | 0.38 | 0.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578397 | 1039 | 566104 | 1114 | 555028.643 | 1489.333 | 6.47 | 6.56 | 6.53 | 6.52 | 6.57 | 6.57 | 7.26 | 7.32 | 7.21 | 7.3 | 7.29 | 7.29 | 987000 | 1000 | 991000 | 1000 | 1970333 | 4733 | 1976000 | 1965600 | 11.95 | 6.5367 | 1.4983 | 7.2783 | 0.36167 | 22.92% | 4.969% | 26.8733 | 42.4 | 2.31 | 5.2833 | 1985400.9 | 1969133 | 2396797 | 82.16% | 56 | 0
2024-03-15 | 2024 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 335090.89 | 6:58 | 18:51 | 12059.8 | 12453.1 | 12397.3 | 12376.1 | 12476.2 | 12516.3 | 12513.2 | 12843.1 | 12456 | 12428 | 12326.3 | 12454.9 | 12454.8 | 12392.3 | 12471.3 | 12505.9 | 12421.3 | 12448.9 | 12467.8 | 12545.6 | 12477.5 | 12511.5 | 12340.8 | 12410.9 | 12292.5 | 11120.7 | 12307.2 | 12271.5 | 12504.9 | 12397.3 | 12333.2 | 12471.7 | 12883.7 | 12916.9 | 12902.5 | 12856.2 | 12583.7 | 12476.6 | 12508.3 | 12408.5 | 13140.7 | 12334.5 | 12979.9 | 12167.3 | 12691.4 | 13559 | 12078.9 | 13113.1 | 11784 | 12034.2 | 12544 | 12090.5 | 12805.9 | 11864.1 | 12762.8 | 11823.5 | 11809.4 | 12940.3 | 11817.6 | 12891.2 | 12799.8 | 11783.4 | 12586 | 12169.8 | 12330 | 11800.2 | 12305.7 | 12647.4 | 12832.4 | 11991.5 | 12733.8 | 11655.8 | 12473.1 | 12389.2 | 11819.7 | 12741.9 | 11718.6 | 12827.2 | 11811.6 | 12725.7 | 12076.2 | 12686 | 12189.1 | 12987.9 | 12080.5 | 12600.6 | 11959 | 10777.2 | 12703.9 | 12382.5 | 11844.7 | 13001.6 | 12744.5 | 12108 | 11983.9 | 12767.1 | 11881.5 | 12189.7 | 12863.1 | 11807.4 | 12937.6 | 11813.5 | 12746.5 | 12058.3 | 12754.4 | 11562.8 | 12847 | 11996.7 | 12768.7 | 12001.4 | 12777.9 | 12162.2 | 11854.8 | 12683.7 | 11998.1 | 11822.4 | 12725 | 12838.8 | 12667.2 | 11993.1 | 12781.1 | 11920.1 | 12541.7 | 12015 | 12461.8 | 11234.2 | 12645.7 | 11931.4 | 12078.2 | 12077.5 | 11931.6 | 10435.5 | 11867.1 | 10644.7 | 11952.7 | 11965.9 | 13112.9 | 12023.4 | 13145.7 | 12201.7 | 13034.3 | 12048.4 | 12187.6 | 12072.7 | 12898.2 | 13158.2 | 13109.5 | 13053.7 | 13089.8 | 13087 | 12299.6 | 13089.6 | 13081.9 | 13130.7 | 13161.5 | 13136.6 | 13179.5 | 12316.7 | 13159.5 | 12335.2 | 27.9866 | 27.3982 | 27.2374 | 27.4004 | 27.2337 | 27.3828 | 0 | 41.2 | 0 | 0 | 41 | 41.4 | 3.2624 | 3.2829 | 3.1747 | 3.3841 | 3.1894 | 3.3473 | 6.829 | 6.547 | 7.327 | 6.955 | 6.38 | 6.427 | 6.3373 | 6.4211 | 6.4151 | 6.387 | 6.4306 | 6.4374 | 1.3715 | 1.4771 | 1.2262 | 1.7529 | 1.4372 | 1.5433 | 7.0995 | 7.1378 | 7.0672 | 7.1465 | 7.1024 | 7.1232 | 0.33253 | 0.3819 | 0.33498 | 0.35839 | 0.36842 | 0.34018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579387 | 1041 | 567090 | 1116 | 556996.91 | 1494.067 | 6.3373 | 6.4211 | 6.4151 | 6.387 | 6.4306 | 6.4374 | 7.0995 | 7.1378 | 7.0672 | 7.1465 | 7.1024 | 7.1232 | 990000 | 2000 | 986000 | 2000 | 1968267 | 4734 | 1972000 | 1963533 | 11.8833 | 6.4047 | 1.468 | 7.1128 | 0.35273 | 22.92% | 4.959% | 27.4399 | 41.2 | 3.2735 | 6.7442 | 1983602 | 1966801 | 2351332.0038 | 83.65% | 51 | 0
2024-03-16 | 2024 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 335090.89 | 6:59 | 18:52 | 12132.6 | 12527.1 | 12477.4 | 12458.4 | 12558.2 | 12617.8 | 12629.3 | 12910.9 | 12512.2 | 12470.3 | 12404.5 | 12526.9 | 12518.3 | 12474 | 12553.3 | 12572.2 | 12492.1 | 12511.9 | 12533.3 | 12615.2 | 12540.6 | 12579 | 12408 | 12475.6 | 12353.6 | 11236.2 | 12376.3 | 12338.2 | 12565.9 | 12462.6 | 12398.3 | 12544.2 | 12973.7 | 13011 | 12991.3 | 12943.8 | 12637.5 | 12534.1 | 12562.4 | 12464.3 | 13199.4 | 12404.8 | 13029.9 | 12225.4 | 12746.3 | 13622.9 | 12164.5 | 13169.9 | 11886.2 | 12127.5 | 12621.6 | 12181.5 | 12881.8 | 11977.8 | 12828.7 | 11905.3 | 11906 | 13008 | 11930.3 | 12958.4 | 12865.7 | 11877.3 | 12664.1 | 12246.6 | 12405.5 | 11883.2 | 12369.5 | 12703.7 | 12884.3 | 12062.8 | 12786.3 | 11753.9 | 12533.1 | 12446.3 | 11894.5 | 12790.8 | 11794.5 | 12883.4 | 11899.8 | 12788.6 | 12141.5 | 12734.9 | 12239.2 | 13028.3 | 12132.3 | 12635.9 | 12029.7 | 10862 | 12730.8 | 12432.4 | 11915.4 | 13047.1 | 12801.2 | 12179.4 | 12056.4 | 12825 | 11967.2 | 12253.7 | 12904 | 11869.1 | 12983.6 | 11892.5 | 12796.3 | 12119.4 | 12796.3 | 11645.4 | 12887.7 | 12053.8 | 12806 | 12047.8 | 12838.2 | 12220.1 | 11913.2 | 12734 | 12065.5 | 11908.6 | 12772.1 | 12885.7 | 12715.3 | 12072.9 | 12824 | 11992.6 | 12602 | 12082.3 | 12531.2 | 11319.5 | 12686.6 | 12007.5 | 12139.9 | 12129.8 | 11996.9 | 10497.7 | 11959.8 | 10752.6 | 12003.1 | 12018.8 | 13144.4 | 12097.2 | 13169.9 | 12266.9 | 13079 | 12124.7 | 12255.3 | 12125.4 | 12926.2 | 13168 | 13137.5 | 13077.8 | 13111.3 | 13118.4 | 12341.6 | 13109.4 | 13113.2 | 13154.8 | 13174.1 | 13147.9 | 13204.7 | 12349.9 | 13202.1 | 12369.7 | 28.9004 | 28.4788 | 28.3742 | 28.4382 | 28.4866 | 28.4441 | 0 | 42.5 | 0 | 0 | 43.1 | 43.3 | 3.1863 | 3.1519 | 3.1761 | 3.1426 | 3.1293 | 3.083 | 7.057 | 6.855 | 6.435 | 8.03 | 7.031 | 6.503 | 6.4657 | 6.5197 | 6.5871 | 6.4839 | 6.5288 | 6.5353 | 1.404 | 1.5077 | 1.2518 | 1.7847 | 1.4588 | 1.5907 | 7.2102 | 7.2389 | 7.1718 | 7.2498 | 7.1996 | 7.2238 | 0.33459 | 0.38143 | 0.33515 | 0.35909 | 0.36544 | 0.33525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580383 | 1042 | 568080 | 1118 | 558975.11 | 1498.867 | 6.4657 | 6.5197 | 6.5871 | 6.4839 | 6.5288 | 6.5353 | 7.2102 | 7.2389 | 7.1718 | 7.2498 | 7.1996 | 7.2238 | 996000 | 1000 | 990000 | 2000 | 1978200 | 4800 | 1983000 | 1973400 | 11.8833 | 6.5201 | 1.4996 | 7.2157 | 0.35182 | 23% | 4.876% | 28.5204 | 42.9667 | 3.1449 | 6.9852 | 1993656.2 | 1976000 | 2370626.556 | 83.35% | 50 | 0
2024-03-17 | 2024 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 335090.89 | 6:54 | 18:56 | 9939.1 | 10409.5 | 10413.1 | 10370.1 | 10481.3 | 10538 | 10560.2 | 10986 | 10445.6 | 10420.1 | 10280.4 | 10449.3 | 10379.3 | 10369.6 | 10427.4 | 10452.5 | 10382.4 | 10386.8 | 10418.1 | 10461 | 10447.6 | 10432.5 | 10223.7 | 10325 | 10176.8 | 8953 | 10196.3 | 10156.5 | 10471.9 | 10361.4 | 10234 | 10450.5 | 10465.7 | 10518.3 | 10524.5 | 10465.4 | 10544.1 | 10409.2 | 10463.5 | 10342.7 | 11302.3 | 10173.7 | 11112.9 | 9960.1 | 10650.6 | 11870.5 | 9931.9 | 11297.4 | 9582.1 | 9844.7 | 10491.4 | 9919.7 | 10856.2 | 9698.3 | 10801 | 9600.8 | 9589.5 | 11026.8 | 9597 | 10946.4 | 10838.2 | 9588.7 | 10555.7 | 10008.7 | 10228.5 | 9597.2 | 10155 | 10645.4 | 10925.6 | 9799 | 10752.2 | 9418.3 | 10430.8 | 10260.9 | 9606.7 | 10799.4 | 9475.7 | 10910.9 | 9605.4 | 10761.8 | 9852.2 | 10650.6 | 9966.5 | 11038.4 | 9847.6 | 10501.9 | 9810.5 | 8665 | 10647.6 | 10294 | 9572.1 | 11061.2 | 10740.3 | 9896 | 9785.1 | 10797.7 | 9653 | 9998.9 | 10909.7 | 9553.3 | 11008.5 | 9557.1 | 10689.7 | 9818.2 | 10787.8 | 9322 | 10860.4 | 9765.5 | 10748.7 | 9761.8 | 10759.8 | 9894.6 | 9615.4 | 10665.2 | 9761.5 | 9558.1 | 10755.1 | 10852.2 | 10661.5 | 9758.2 | 10793.1 | 9650.2 | 10481.8 | 9765.7 | 10356.4 | 9026.5 | 10537.2 | 9650.6 | 9790.2 | 9810.2 | 9665.6 | 8358.3 | 9628.2 | 8552.5 | 9767.8 | 9784.9 | 11289.4 | 9828.7 | 11346.9 | 10052.1 | 11219.7 | 9907.7 | 10079.3 | 9922.1 | 10910.2 | 11318.8 | 11165.4 | 11134.6 | 11161.2 | 11221.4 | 10142.6 | 11225 | 11154.9 | 11240.5 | 11332.6 | 11281.9 | 11319.2 | 10117.7 | 11239.6 | 10111.6 | 28.6176 | 28.096 | 28.1665 | 28.1311 | 27.9856 | 28.0278 | 0 | 36.9 | 0 | 0 | 37 | 37.1 | 3.648 | 3.6938 | 3.6445 | 3.6162 | 3.2057 | 3.3942 | 7.603 | 7.097 | 6.916 | 7.203 | 8.552 | 6.54 | 5.1891 | 5.2087 | 5.2657 | 5.1806 | 5.207 | 5.2045 | 1.1468 | 1.1872 | 1.0125 | 1.4386 | 1.1451 | 1.2503 | 5.5774 | 5.5519 | 5.5135 | 5.5654 | 5.485 | 5.5167 | 0.32449 | 0.38157 | 0.3319 | 0.36891 | 0.36456 | 0.34118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 581209 | 1044 | 568902 | 1119 | 560617.044 | 1503.467 | 5.1891 | 5.2087 | 5.2657 | 5.1806 | 5.207 | 5.2045 | 5.5774 | 5.5519 | 5.5135 | 5.5654 | 5.485 | 5.5167 | 826000 | 2000 | 822000 | 1000 | 1641934 | 4600 | 1645000 | 1637334 | 12.0333 | 5.2093 | 1.1967 | 5.535 | 0.3521 | 22.97% | 6.361% | 28.1708 | 37 | 3.5337 | 7.3185 | 1650535 | 1641134 | 1864457.6574 | 88.02% | 57 | 3950
2024-03-18 | 2024 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 335090.89 | 6:53 | 18:57 | 12325.4 | 12710.9 | 12671.2 | 12660.2 | 12750.7 | 12794.5 | 12800.6 | 13105.2 | 12716.3 | 12680.9 | 12591.8 | 12723.2 | 12706.3 | 12653.1 | 12730.4 | 12764.7 | 12673.5 | 12689.7 | 12721 | 12795.1 | 12725.3 | 12762.1 | 12575 | 12654.6 | 12523.6 | 11367.8 | 12554.2 | 12517.1 | 12749.2 | 12632.5 | 12560.4 | 12706.2 | 13111.1 | 13163.4 | 13165.1 | 13120.1 | 12815.6 | 12710.2 | 12734.9 | 12625.2 | 13363.5 | 12558.4 | 13201.9 | 12376.6 | 12918.4 | 13788.8 | 12317.5 | 13333.5 | 12031.6 | 12281.5 | 12803.7 | 12337 | 13068.9 | 12131.5 | 13020.4 | 12062.6 | 12045.6 | 13193.6 | 12077.4 | 13150.6 | 13055.8 | 12033.4 | 12836.8 | 12413 | 12591.8 | 12058.2 | 12558.1 | 12911.3 | 13082.4 | 12247.2 | 12996.2 | 11922 | 12716.5 | 12652.1 | 12064.2 | 13003 | 11966.7 | 13088.4 | 12075.1 | 12984.7 | 12330.1 | 12947.6 | 12407.6 | 13237.4 | 12300.4 | 12830.2 | 12195.7 | 11001.8 | 12886.4 | 12603.7 | 12041.6 | 13218.9 | 12971 | 12325.6 | 12202.7 | 12984.9 | 12096.2 | 12419.4 | 13081.9 | 12028.9 | 13163.9 | 12030.9 | 12971 | 12266.7 | 12971.9 | 11757.7 | 13062.6 | 12202 | 12997 | 12183.9 | 13012.4 | 12374.5 | 12073.3 | 12918.6 | 12219.1 | 12048.1 | 12957.4 | 13065.5 | 12900.6 | 12220.7 | 13016 | 12139.8 | 12783.1 | 12247.8 | 12708.6 | 11479 | 12871.3 | 12152.8 | 12289.3 | 12271.6 | 12147.3 | 10618 | 12099.8 | 10852.4 | 12181.4 | 12189.1 | 13363.3 | 12268.1 | 13391.5 | 12444.4 | 13280.8 | 12278.5 | 12425.6 | 12290.3 | 13145.9 | 13398.3 | 13362.6 | 13294.7 | 13322.4 | 13343.8 | 12536.2 | 13335.2 | 13328.9 | 13362.6 | 13391.1 | 13366.8 | 13418.1 | 12531.7 | 13411.1 | 12574.8 | 29.4107 | 29.1905 | 29.1911 | 29.1685 | 29.1695 | 29.3213 | 0 | 43.9 | 0 | 0 | 44.1 | 44.2 | 2.6189 | 2.6487 | 2.6088 | 2.6878 | 2.4 | 2.5603 | 5.917 | 6.339 | 5.96 | 7.658 | 6.619 | 6.434 | 6.5919 | 6.6514 | 6.7699 | 6.6862 | 6.823 | 6.7645 | 1.4425 | 1.54 | 1.287 | 1.8337 | 1.5443 | 1.6332 | 7.3502 | 7.3508 | 7.4316 | 7.4553 | 7.4472 | 7.4531 | 0.3324 | 0.37917 | 0.33471 | 0.35981 | 0.36765 | 0.33658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 582218 | 1046 | 569906 | 1121 | 562623.111 | 1508.2 | 6.5919 | 6.6514 | 6.7699 | 6.6862 | 6.823 | 6.7645 | 7.3502 | 7.3508 | 7.4316 | 7.4553 | 7.4472 | 7.4531 | 1009000 | 2000 | 1004000 | 2000 | 2006067 | 4733 | 2009000 | 2001334 | 12.0667 | 6.7145 | 1.5468 | 7.4147 | 0.35172 | 23.04% | 4.744% | 29.2419 | 44.0667 | 2.5874 | 6.4878 | 2021782 | 1995201 | 2418189.6531 | 82.51% | 44 | 26
2024-03-19 | 2024 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 335090.89 | 6:56 | 18:56 | 11956.1 | 12361.2 | 12324.7 | 12302 | 12407.3 | 12460.2 | 12459.1 | 12754.9 | 12362.8 | 12321.5 | 12246.5 | 12373.9 | 12359.1 | 12306.7 | 12378.5 | 12413.2 | 12329.3 | 12353.8 | 12377.7 | 12449.7 | 12388.9 | 12413.6 | 12237.3 | 12316 | 12188.2 | 10960.8 | 12204.6 | 12173.4 | 12412.9 | 12312.8 | 12241.8 | 12389.6 | 12731.2 | 12762.8 | 12767.7 | 12724.4 | 12486.1 | 12379.9 | 12408.8 | 12303.1 | 13038.1 | 12224.5 | 12897 | 12053.5 | 12601.4 | 13448.7 | 11994.1 | 13011 | 9785.5 | 11760.8 | 12462.1 | 11985.2 | 12731.1 | 11782.2 | 12670.6 | 11702 | 11670.8 | 12852.9 | 11692.5 | 12796 | 12700.1 | 11655.8 | 12500.2 | 12059.3 | 12252.5 | 11687.3 | 12204.7 | 12564.1 | 12734.3 | 11871.5 | 12646.8 | 11512.5 | 12370.1 | 12297.8 | 11696.4 | 12652.5 | 11572.7 | 12740.3 | 11698.8 | 12636.9 | 11965.5 | 12601.7 | 12051.5 | 12893.2 | 11947.9 | 12498.3 | 11858.9 | 10612.8 | 12545.4 | 12279.2 | 11666.3 | 12883.6 | 12637 | 11991.9 | 11879.2 | 12667.7 | 11743 | 12064 | 12757 | 11648.9 | 12842.4 | 11659 | 12643.9 | 11900.8 | 12648.5 | 11374.2 | 12729.9 | 11842.4 | 12643.5 | 11838.2 | 12682.9 | 12011.4 | 11692.3 | 12573.3 | 11857.5 | 11671.4 | 12623.1 | 12719.1 | 12568.2 | 11845.2 | 12669.3 | 11757.3 | 12450.4 | 11878.3 | 12381.5 | 11057.8 | 12871 | 11772 | 11913.8 | 11901.8 | 11775.1 | 10235.4 | 11754.2 | 10477.2 | 11802 | 11807.9 | 13012.3 | 11898.8 | 13053.7 | 12096 | 12942.5 | 11938.5 | 12094.6 | 11930.5 | 12803.3 | 13057.6 | 13010 | 12946.8 | 12974.2 | 12993.5 | 12183.1 | 12996.8 | 12973.3 | 13017.3 | 13046.6 | 13029.7 | 13070.3 | 12187.7 | 13069.5 | 12207.3 | 32.1094 | 31.9545 | 32.0529 | 32.112 | 32.1397 | 32.4855 | 0 | 44.2 | 0 | 0 | 44.3 | 44.6 | 3.6798 | 3.6487 | 3.5919 | 3.5894 | 3.5741 | 3.7361 | 8.135 | 8.254 | 7.776 | 8.101 | 7.822 | 8.355 | 6.3626 | 6.4225 | 6.5361 | 6.4337 | 6.566 | 6.5187 | 1.3995 | 1.4823 | 1.2505 | 1.7792 | 1.47 | 1.5799 | 7.0647 | 7.0689 | 7.1448 | 7.1494 | 7.1403 | 7.1498 | 0.32671 | 0.3751 | 0.32998 | 0.35447 | 0.36493 | 0.33482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583198 | 1047 | 570882 | 1123 | 564572.244 | 1513 | 6.3626 | 6.4225 | 6.5361 | 6.4337 | 6.566 | 6.5187 | 7.0647 | 7.0689 | 7.1448 | 7.1494 | 7.1403 | 7.1498 | 980000 | 1000 | 976000 | 2000 | 1949133 | 4800 | 1953000 | 1944333 | 12 | 6.4733 | 1.4936 | 7.1197 | 0.34767 | 23.07% | 4.883% | 32.1423 | 44.3667 | 3.6367 | 8.0738 | 1963915.8 | 1948333 | 2317829.7162 | 84.06% | 41 | 0
2024-03-20 | 2024 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 335090.89 | 6:56 | 18:56 | 12289.6 | 12656.6 | 12620.1 | 12621.6 | 12683.8 | 12729.3 | 12730.2 | 13021.7 | 12673.1 | 12637.2 | 12541.8 | 12665.2 | 12652.9 | 12590.2 | 12677.5 | 12708.8 | 12613.6 | 12639.3 | 12663 | 12741.5 | 12668 | 12700.3 | 12520.2 | 12595.1 | 12467.3 | 11416.2 | 12499.6 | 12457.8 | 12677.3 | 12574 | 12499.1 | 12649.4 | 13049.9 | 13097.3 | 13108.7 | 13063.2 | 12734.1 | 12629.9 | 12645 | 12535.3 | 13255.5 | 12473.6 | 13101.6 | 12291.6 | 12831.4 | 13665.6 | 12271.5 | 13242 | 11870.5 | 12227.1 | 12754.4 | 12301.7 | 13006.9 | 12100.1 | 12944 | 12035.3 | 12019.6 | 13107.7 | 12067.2 | 13071.4 | 12987.7 | 12020.7 | 12781.4 | 12368.4 | 12514.3 | 11987.3 | 12484.8 | 12790.2 | 12979.5 | 12166.9 | 12897.3 | 11877.8 | 12650.1 | 12568.9 | 12039.9 | 12905.9 | 11941.9 | 13002.7 | 12045.1 | 12915.3 | 12240.1 | 12841.6 | 12307.6 | 13102.8 | 12205.5 | 12704.9 | 12110.7 | 11026.7 | 12778.5 | 12496.7 | 11959.8 | 13078 | 12831 | 12225.2 | 12102 | 12855 | 12015.6 | 12301.9 | 12936.7 | 11921.8 | 13023.1 | 11935.5 | 12838.8 | 12157.1 | 12838.2 | 11687.7 | 12922.1 | 12104.7 | 12839.9 | 12085.7 | 12873 | 12277.6 | 11969.8 | 12786.3 | 12122.1 | 11960.6 | 12822.8 | 12927.6 | 12773.3 | 12122.7 | 12869.4 | 12037.3 | 12659.1 | 12141.8 | 12590.1 | 11465.9 | 12742 | 12065.7 | 12195.3 | 12176.6 | 12075.4 | 10641.2 | 12013.6 | 10887.3 | 12069.2 | 12076.6 | 13183.4 | 12141.6 | 13228.8 | 12329.6 | 13129.6 | 12182.3 | 12318.6 | 12174.1 | 12982.5 | 13222.1 | 13181.4 | 13126.1 | 13155 | 13173 | 12418.8 | 13169.1 | 13158.4 | 13195.2 | 13228.1 | 13200.6 | 13244.5 | 12411.8 | 13245.9 | 12432.6 | 31.6194 | 31.0642 | 31.1004 | 31.0822 | 30.9361 | 30.8817 | 0 | 43.7 | 0 | 0 | 43.2 | 43.4 | 3.7682 | 3.6678 | 3.6204 | 3.8187 | 3.4223 | 3.5655 | 7.077 | 6.699 | 6.46 | 6.596 | 6.766 | 6.753 | 6.8245 | 6.7429 | 6.8432 | 6.5825 | 6.5383 | 6.6874 | 1.4807 | 1.568 | 1.3189 | 1.8966 | 1.4942 | 1.6678 | 7.3123 | 7.0992 | 7.4421 | 7.0612 | 7.126 | 7.215 | 0.34405 | 0.39297 | 0.34761 | 0.37619 | 0.381 | 0.34759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 584203 | 1049 | 571877 | 1124 | 566564.778 | 1516.467 | 6.8245 | 6.7429 | 6.8432 | 6.5825 | 6.5383 | 6.6874 | 7.3123 | 7.0992 | 7.4421 | 7.0612 | 7.126 | 7.215 | 1005000 | 2000 | 995000 | 1000 | 1992534 | 3467 | 1997000 | 1989067 | 12 | 6.7031 | 1.571 | 7.2093 | 0.3649 | 23.44% | 5.062% | 31.114 | 43.4333 | 3.6438 | 6.7252 | 2007359.8 | 1991600 | 2355261.8106 | 84.56% | 52 | 4300
2024-03-21 | 2024 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 335090.89 | 6:59 | 18:58 | 11388.8 | 11751 | 11761.8 | 11730.2 | 11850.2 | 11864 | 11843.8 | 12103.1 | 11718 | 11698.4 | 11638.9 | 11740.9 | 11736.4 | 11682 | 11757.5 | 11780 | 11700.1 | 11699.4 | 11729.3 | 11789.8 | 11742.5 | 11765.4 | 11599.4 | 11672.1 | 11516.2 | 10474.2 | 11539.5 | 11512.4 | 11729.7 | 11635.1 | 11557 | 11705.1 | 12056.2 | 12048.6 | 12064.2 | 12025.4 | 11793.3 | 11689.4 | 11724.3 | 11670.8 | 12308.1 | 11554.1 | 12159.3 | 11375.3 | 11854.9 | 12657.4 | 11359.2 | 12296.3 | 8424.8 | 11071.7 | 11793.6 | 11346.9 | 12043.4 | 11192.7 | 11958.3 | 11121.8 | 11090.8 | 12125.9 | 11157.5 | 12077.6 | 11993.7 | 11116.1 | 11800.8 | 11411.1 | 11585 | 11141.1 | 11570 | 11898.8 | 12060.8 | 11305 | 11999.9 | 11030.8 | 11700.2 | 11667.9 | 11121.6 | 11984 | 11048.3 | 12018.3 | 11113.6 | 11933.7 | 11367.4 | 11938.4 | 11472.4 | 12203.5 | 11377 | 11864.3 | 11249.9 | 10183.3 | 11958.6 | 11666.2 | 11186.4 | 12244.5 | 12005.3 | 11431.6 | 11319.5 | 12039.9 | 11250.8 | 11526.2 | 12128.8 | 11194.2 | 12200.8 | 11209.5 | 12024.3 | 11408.4 | 12034.8 | 10953.3 | 12109.5 | 11355.4 | 12024.9 | 11349 | 12056.3 | 11521.3 | 11216.6 | 11981.9 | 11380.2 | 11240.2 | 12040.9 | 12139.6 | 11996.4 | 11398.2 | 12096.6 | 11331.4 | 11883.6 | 11415.1 | 11816.4 | 10708.1 | 11971 | 11350.8 | 11470.5 | 11448.8 | 11364.5 | 9930.7 | 11275.4 | 10111.7 | 11263 | 11268.1 | 12353.3 | 11386.7 | 12384.5 | 11535.9 | 12282.9 | 11353.2 | 11483.4 | 11334.6 | 12187.6 | 12397.7 | 12380.7 | 12300.8 | 12313.9 | 12338.7 | 11627 | 12342.2 | 12362.5 | 12374.1 | 12386 | 12370.6 | 12394.9 | 11631.6 | 12457.2 | 11671 | 32.63 | 32.5838 | 32.8109 | 32.4608 | 32.7654 | 32.5909 | 0 | 46.8 | 0 | 0 | 47.5 | 47.2 | 2.9157 | 3.0791 | 2.8883 | 3.112 | 2.9335 | 3.0006 | 7.086 | 6.227 | 7.278 | 6.605 | 7.11 | 8.677 | 6.3178 | 6.2517 | 6.3519 | 6.1012 | 6.1516 | 6.3355 | 1.3327 | 1.504 | 1.1687 | 1.6891 | 1.4793 | 1.6076 | 6.8004 | 6.5744 | 6.8743 | 6.5021 | 6.7885 | 6.8253 | 0.30834 | 0.35595 | 0.31487 | 0.33939 | 0.353 | 0.32469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 585142 | 1061 | 572820 | 1136 | 568417.711 | 1521.2 | 6.3178 | 6.2517 | 6.3519 | 6.1012 | 6.1516 | 6.3355 | 6.8004 | 6.5744 | 6.8743 | 6.5021 | 6.7885 | 6.8253 | 939000 | 12000 | 943000 | 12000 | 1852933 | 4733 | 1858000 | 1848200 | 11.9833 | 6.2516 | 1.4636 | 6.7275 | 0.33271 | 23.41% | 4.945% | 32.6403 | 47.1667 | 2.9882 | 7.1638 | 1866561.1 | 1851533 | 2182875.897 | 84.82% | 61 | 1649
2024-03-22 | 2024 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 335090.89 | 6:52 | 18:58 | 12231.9 | 12641.1 | 12606.2 | 12594.2 | 12680.7 | 12724.6 | 12706 | 13018.6 | 12649.9 | 12599.2 | 12535.5 | 12662.5 | 12644.1 | 12596.5 | 12646.9 | 12693.3 | 12599.1 | 12622.2 | 12647.1 | 12714.2 | 12659.5 | 12686 | 12497 | 12580.7 | 12451.5 | 11188.8 | 12450.6 | 12424.4 | 12673.6 | 12573.6 | 12493.7 | 12658.4 | 13004.7 | 13031.9 | 13038 | 12981.2 | 12748.2 | 12638.3 | 12669.2 | 12572.1 | 13312.1 | 12443.2 | 13167.8 | 12258.1 | 12838.3 | 13763.1 | 12225.9 | 13287.3 | 11841.1 | 12082.6 | 12738.8 | 12213.9 | 13012.3 | 11983.6 | 12951.2 | 11929.7 | 11909.2 | 13126.8 | 11951.5 | 13084.7 | 12988.1 | 11919.5 | 12789.6 | 12330.2 | 12474.7 | 11914.1 | 12443 | 12818.7 | 13012.1 | 12100.4 | 12913.8 | 11732.5 | 12629.1 | 12528.5 | 11938 | 12912.7 | 11812 | 13017.8 | 11931.3 | 12902.8 | 12182.5 | 12851.4 | 12259.1 | 13163.9 | 12154.2 | 12713.1 | 12073.8 | 10774.1 | 12825.4 | 12503.5 | 11905.1 | 13161.7 | 12884 | 12198.4 | 12074.7 | 12937.3 | 11986.4 | 12303.8 | 13035.6 | 11890.7 | 13101.4 | 11891.7 | 12897.9 | 12149.3 | 12917.8 | 11604.5 | 12996.4 | 12081.4 | 12899.3 | 12075.1 | 12934.4 | 12234 | 11920.1 | 12828.5 | 12107.4 | 11913.1 | 12866.2 | 12988.4 | 12811.8 | 12069.6 | 12919 | 11985.7 | 12682.6 | 12096.9 | 12588.6 | 11265.1 | 12745.8 | 11988.4 | 12161.2 | 12143 | 12005.2 | 10446.4 | 11975.7 | 10679.1 | 12032.6 | 12047.7 | 13320.4 | 12146 | 13370.5 | 12367 | 13256.2 | 12194.7 | 12359.4 | 12178.5 | 13098 | 13377.6 | 13310.4 | 13250.4 | 13281.4 | 13297.5 | 12446.9 | 13308.9 | 13293.1 | 13342.4 | 13352.8 | 13342.1 | 13396.5 | 12455.1 | 13375.7 | 12492.6 | 32.2848 | 32.2445 | 32.442 | 32.2405 | 32.5323 | 32.3692 | 0 | 48.6 | 0 | 0 | 49.2 | 49.2 | 2.1381 | 2.21 | 2.201 | 2.1757 | 1.9228 | 2.2849 | 5.419 | 5.63 | 5.491 | 5.168 | 5.411 | 5.587 | 6.7595 | 6.7125 | 6.8006 | 6.5658 | 6.6783 | 6.7533 | 1.4696 | 1.5426 | 1.2908 | 1.8552 | 1.4894 | 1.6748 | 7.295 | 7.1514 | 7.36 | 7.1408 | 7.2605 | 7.2477 | 0.32949 | 0.38225 | 0.34072 | 0.36234 | 0.37522 | 0.33813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586145 | 1062 | 573817 | 1138 | 570409.978 | 1525.933 | 6.7595 | 6.7125 | 6.8006 | 6.5658 | 6.6783 | 6.7533 | 7.295 | 7.1514 | 7.36 | 7.1408 | 7.2605 | 7.2477 | 1003000 | 1000 | 997000 | 2000 | 1992267 | 4733 | 1997000 | 1987534 | 12.1 | 6.7117 | 1.5537 | 7.2426 | 0.35469 | 23.15% | 4.897% | 32.3522 | 49 | 2.1554 | 5.451 | 2006609.4 | 1991201 | 2345806.0824 | 84.88% | 43 | 2190
2024-03-23 | 2024 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 335090.89 | 6:53 | 18:53 | 11277.7 | 11736.3 | 11591.4 | 11602.2 | 11635.2 | 11718 | 11787.8 | 12173.8 | 11780.5 | 11608.2 | 11690.9 | 11813.6 | 11750.2 | 11776.4 | 11603.2 | 11694.3 | 11561.1 | 11574.8 | 11649.6 | 11757.9 | 11614.9 | 11657.3 | 11350.3 | 11485.3 | 11483.6 | 10295.6 | 11579.7 | 11460.9 | 11602.3 | 11411.5 | 11313.2 | 11610.6 | 11708.1 | 11805.2 | 11951.1 | 11822.6 | 11707.7 | 11493.5 | 11480.8 | 11383.2 | 12194.7 | 11305.1 | 12048.4 | 11100.9 | 11646.5 | 12502.8 | 11055.3 | 12128.5 | 10973.4 | 11225.3 | 11948.6 | 11409.5 | 12179.9 | 11069.2 | 12201.9 | 11041.9 | 11022.5 | 12345.3 | 11068.9 | 12297.1 | 12141.4 | 11023.3 | 11875.9 | 11369.2 | 11567.8 | 10897.7 | 11522.2 | 11876.7 | 12151.6 | 11126.8 | 12019.9 | 10683.5 | 11747.8 | 11574.4 | 10970 | 11977.3 | 10795.9 | 12125.5 | 10931.3 | 11975.9 | 11166.6 | 11873.1 | 11219 | 12196.1 | 11123.1 | 11707.4 | 11060.9 | 9802.9 | 11845.9 | 11491.2 | 10795.4 | 12139.5 | 11850.1 | 11125.3 | 10992.6 | 11909.9 | 10902 | 11214.4 | 12077.2 | 10830.6 | 12078.3 | 10828.5 | 11862.6 | 11092.2 | 11885 | 10528.5 | 11936.4 | 10998.8 | 11767.9 | 10901.2 | 11740.7 | 11048.5 | 10806.6 | 11816.7 | 11079 | 10853.5 | 11878.5 | 11952.6 | 11820.5 | 10977.1 | 11878.1 | 10853.6 | 11667.9 | 10995.9 | 11495 | 10141.1 | 11676.9 | 10796.6 | 11051.6 | 11017.1 | 10818.8 | 9439.4 | 10791.4 | 9534.5 | 10675.4 | 10672.6 | 11853.5 | 10674.9 | 11975.6 | 10919.7 | 11821.3 | 10762.7 | 10926.5 | 10771.4 | 11836.1 | 12085.7 | 12093.3 | 12009.7 | 11938.7 | 11894.8 | 11088.9 | 12013.8 | 12094.5 | 12122.6 | 12143.8 | 12101.9 | 12126.5 | 11178.3 | 12224.5 | 11259.3 | 33.4956 | 33.2908 | 33.3673 | 33.2821 | 33.4365 | 33.4203 | 0 | 48.2 | 0 | 0 | 48 | 48.0359 | 3.0311 | 3.0488 | 3.0488 | 3.0016 | 3.0024 | 3.1248 | 6.812 | 6.921 | 7.533 | 7.696 | 7.082 | 7.168 | 6.2974 | 6.1677 | 6.1802 | 6.1148 | 5.9974 | 6.2187 | 1.4054 | 1.4005 | 1.203 | 1.7546 | 1.3179 | 1.547 | 6.7148 | 6.4663 | 6.5685 | 6.5509 | 6.3841 | 6.5668 | 0.34056 | 0.39618 | 0.34824 | 0.38226 | 0.37837 | 0.35619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 587069 | 1064 | 574722 | 1139 | 572232.911 | 1530.6 | 6.2974 | 6.1677 | 6.1802 | 6.1148 | 5.9974 | 6.2187 | 6.7148 | 6.4663 | 6.5685 | 6.5509 | 6.3841 | 6.5668 | 924000 | 2000 | 905000 | 1000 | 1822933 | 4667 | 1826000 | 1818266 | 12 | 6.1627 | 1.438 | 6.5419 | 0.36697 | 23.33% | 5.609% | 33.3821 | 48.0786 | 3.0429 | 7.202 | 1835720.5 | 1821400 | 2121636.2901 | 85.85% | 44 | 468
2024-03-24 | 2024 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 335090.89 | 6:53 | 18:53 | 11910.7 | 12350.9 | 12317.5 | 12286.8 | 12405.7 | 12423.9 | 12421.4 | 12804.4 | 12347.8 | 12324 | 12242.2 | 12363.7 | 12338.6 | 12308 | 12364.4 | 12402.4 | 12311.5 | 12332.3 | 12351.3 | 12420 | 12363.9 | 12384.4 | 12173.8 | 12269.5 | 12154.6 | 10833.4 | 12151.7 | 12117.2 | 12383 | 12276.8 | 12181.2 | 12367.3 | 12671.1 | 12673.8 | 12701 | 12652.4 | 12482.4 | 12350.6 | 12380.3 | 12287.6 | 13062.8 | 12132.7 | 12927.5 | 11936.3 | 12541.1 | 13488.8 | 11911.8 | 13033.7 | 11436.2 | 11712.4 | 12451.8 | 11908.1 | 12750.7 | 11686.4 | 12683.9 | 11586.6 | 11559 | 12872.1 | 11568.7 | 12817.5 | 12716.8 | 11553.7 | 12505.6 | 12029.2 | 12178 | 11571.7 | 12141.9 | 12528.6 | 12753.9 | 11776.9 | 12650.7 | 11363.6 | 12339.5 | 12242.6 | 11584.1 | 12659.2 | 11448.4 | 12754.5 | 11574 | 12635 | 11875 | 12577 | 11963.4 | 12905.5 | 11849.4 | 12433.4 | 11762.7 | 10445.2 | 12580.1 | 12208.6 | 11549.3 | 12925.8 | 12630.3 | 11907.1 | 11784 | 12692.5 | 11675.2 | 12005.7 | 12805.7 | 11548.5 | 12849.2 | 11534.3 | 12619.4 | 11818.7 | 12659.4 | 11229.2 | 12734.5 | 11732.8 | 12619.9 | 11742.2 | 12669.4 | 11889.3 | 11576.3 | 12561.7 | 11777.1 | 11552.1 | 12608.6 | 12722.3 | 12559.6 | 11736.3 | 12666.5 | 11637.2 | 12400.1 | 11757.3 | 12276.6 | 10876.5 | 12473.8 | 11629.5 | 11862.4 | 11881.7 | 11687.9 | 10140.2 | 11653 | 10343.8 | 11746.7 | 11756.8 | 13061.6 | 11830.7 | 13109.6 | 12047.4 | 13013.9 | 11890.6 | 12055.9 | 11901.1 | 12818.5 | 13115.6 | 13054.7 | 12987.7 | 13007 | 13030.9 | 12135.3 | 13038 | 13046.2 | 13080.3 | 13123.6 | 13102.5 | 13126 | 12143.6 | 13134 | 12174.4 | 32.6938 | 32.533 | 32.5483 | 32.4676 | 32.6765 | 32.4438 | 0 | 48.5 | 0 | 0 | 48.6 | 48.7 | 2.9175 | 3.0793 | 3.0363 | 2.9535 | 3.0256 | 3.0333 | 5.949 | 6.461 | 6.695 | 6.313 | 6.072 | 6.313 | 6.5353 | 6.5177 | 6.5979 | 6.4048 | 6.4647 | 6.5474 | 1.3998 | 1.5132 | 1.2333 | 1.7723 | 1.4554 | 1.636 | 7.0505 | 6.9372 | 7.088 | 6.9143 | 6.9842 | 6.9947 | 0.31998 | 0.3766 | 0.33494 | 0.35665 | 0.36931 | 0.3347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 588047 | 1065 | 575695 | 1141 | 574177.978 | 1535.2 | 6.5353 | 6.5177 | 6.5979 | 6.4048 | 6.4647 | 6.5474 | 7.0505 | 6.9372 | 7.088 | 6.9143 | 6.9842 | 6.9947 | 978000 | 1000 | 973000 | 2000 | 1945067 | 4600 | 1948000 | 1940467 | 12 | 6.5113 | 1.5017 | 6.9948 | 0.3487 | 23.06% | 4.985% | 32.5605 | 48.6 | 3.0076 | 6.3005 | 1959095.3 | 1944334 | 2272535.8954 | 85.56% | 56 | 3749
2024-03-25 | 2024 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 335090.89 | 6:49 | 18:58 | 9925.8 | 10371.9 | 10385.7 | 10353.8 | 10487.8 | 10431.5 | 10415.5 | 10799.3 | 10374 | 10361.8 | 10213.5 | 10353.5 | 10283.8 | 10285.1 | 10357.6 | 10373.4 | 10310.1 | 10300.5 | 10327.4 | 10373.8 | 10356.5 | 10354.1 | 10166.8 | 10248.4 | 10141.1 | 8976.2 | 10126.5 | 10096.5 | 10399.2 | 10312.2 | 10190 | 10380.4 | 10535.2 | 10540.4 | 10541.9 | 10504 | 10522.3 | 10392.1 | 10418.8 | 10327.1 | 11034.8 | 10045.1 | 10890.1 | 9856.9 | 10436.8 | 11471.7 | 9850.1 | 11031 | 9521.4 | 9765.9 | 10420.9 | 9898.9 | 10722.8 | 9649.5 | 10721.6 | 9607.7 | 9628.9 | 10935.8 | 9587.5 | 10862.7 | 10755.9 | 9579.1 | 10538.6 | 10042.9 | 10218.7 | 9665.4 | 10171.7 | 10628.5 | 10826.5 | 9867.8 | 10699 | 9506.1 | 10396.6 | 10283.5 | 9656.2 | 10747 | 9546.4 | 10830.1 | 9641.8 | 10714.1 | 9991 | 10694.3 | 10105 | 11044.2 | 9978.2 | 10581.3 | 9886.6 | 8803.9 | 10748.2 | 10364.5 | 9686.7 | 11062.6 | 10752.7 | 9998.2 | 9886.3 | 10817.4 | 9805.1 | 10108.3 | 10956.2 | 9703.9 | 10958.4 | 9669.6 | 10689.7 | 9913.9 | 10770.5 | 9409.2 | 10848.4 | 9841.2 | 10715.7 | 9855.3 | 10752.9 | 9979.5 | 9763.3 | 10763.2 | 9926.7 | 9735 | 10825.9 | 10963.9 | 10768.8 | 10002.7 | 10940.1 | 9895.7 | 10560.9 | 9909 | 10414 | 9241.1 | 10723.6 | 9937.7 | 10136.1 | 10173.9 | 10008.8 | 8672.3 | 9961 | 8848.9 | 10045.4 | 10065 | 11403.9 | 10091.4 | 11406.1 | 10300.7 | 11347 | 10173.3 | 10328 | 10211.7 | 10970.8 | 11301.3 | 11252 | 11219.1 | 11283.6 | 11318.4 | 10324.6 | 11251.8 | 11233.8 | 11234.2 | 11222.4 | 11191 | 11221.1 | 10183 | 11360.1 | 10253.3 | 32.9379 | 32.7961 | 32.658 | 32.6277 | 32.7713 | 32.7647 | 0 | 45.4 | 0 | 0 | 45.9 | 47.8 | 2.1601 | 2.0042 | 2.0807 | 1.9818 | 1.9228 | 2.1016 | 5.049 | 4.361 | 4.998 | 4.559 | 4.867 | 4.839 | 5.4195 | 5.4269 | 5.4797 | 5.3803 | 5.4928 | 5.5674 | 1.2079 | 1.2092 | 1.063 | 1.5352 | 1.1732 | 1.3623 | 5.7301 | 5.6243 | 5.7636 | 5.7311 | 5.7655 | 5.8236 | 0.30521 | 0.36786 | 0.32577 | 0.35665 | 0.36304 | 0.33366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 588868 | 1067 | 576525 | 1143 | 575823.712 | 1539.2 | 5.4195 | 5.4269 | 5.4797 | 5.3803 | 5.4928 | 5.5674 | 5.7301 | 5.6243 | 5.7636 | 5.7311 | 5.7655 | 5.8236 | 821000 | 2000 | 830000 | 2000 | 1645734 | 4000 | 1647000 | 1641734 | 12.15 | 5.4611 | 1.2585 | 5.7397 | 0.34203 | 23.04% | 5.959% | 32.7593 | 46.3667 | 2.0419 | 4.7788 | 1655616 | 1645000 | 1882033.73 | 87.41% | 52 | 18423
2024-03-26 | 2024 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 335090.89 | 6:50 | 19:02 | 11390.4 | 11880.5 | 11842.9 | 11801.6 | 11951.1 | 12003 | 11979.1 | 12337.6 | 11857.5 | 11813.9 | 11737.8 | 11873.5 | 11856.3 | 11816.7 | 11877.6 | 11911.9 | 11833.5 | 11843.4 | 11869.9 | 11927.7 | 11884.4 | 11894.6 | 11651.4 | 11766.8 | 11537.5 | 10261.3 | 11596 | 11565 | 11842.2 | 11745.7 | 11604.1 | 11785.4 | 11867.5 | 11863.6 | 11942.2 | 11874.1 | 11885.5 | 11759.5 | 11804.1 | 11703.2 | 12489.8 | 11500.4 | 12362.9 | 11314.2 | 11942.4 | 12870.2 | 11299.7 | 12465.9 | 10788.7 | 11046.7 | 11895.9 | 11284.1 | 12225.4 | 11112.5 | 12081.6 | 10951 | 10872.6 | 12220.6 | 10994.3 | 12228 | 12167.5 | 10981.2 | 11885.2 | 11388.6 | 11469 | 10793.3 | 11406.8 | 11789.1 | 12081.7 | 11001.7 | 11934.1 | 10612.7 | 11664.7 | 11493.3 | 10870 | 11951.8 | 10728.8 | 12086.3 | 10872.7 | 11963.5 | 11110.8 | 11852.9 | 11227 | 12197.2 | 11096.7 | 11725.4 | 11010.1 | 9795.3 | 11838.3 | 11484.7 | 10826.9 | 12241.7 | 11968 | 11181.9 | 11074.8 | 11991.1 | 10889.5 | 11208.1 | 12043.9 | 10757 | 12183 | 10784.2 | 11907.1 | 11039.1 | 11970.9 | 10497.5 | 12024.9 | 10971.5 | 11933.4 | 11031.5 | 12018.4 | 11159.2 | 10806.4 | 11827.7 | 10999 | 10799.5 | 11858.1 | 11966.4 | 11804.2 | 10979.5 | 11887.6 | 10874.2 | 11659.9 | 11008.5 | 11553.3 | 10184.1 | 11716.4 | 10873.7 | 11047.8 | 11039.4 | 10894.6 | 9463.5 | 10810.4 | 9619.2 | 10938.3 | 10953.7 | 12299.2 | 11036.9 | 12423.6 | 11297.6 | 12287.9 | 11161.4 | 11326.9 | 11149.5 | 12199.3 | 12504.5 | 12383.2 | 12314.8 | 12302.6 | 12308.2 | 11435.1 | 12401.1 | 12390.5 | 12452.4 | 12600.3 | 12547.1 | 12519.2 | 11507.4 | 12491 | 11489.6 | 35.3068 | 35.1701 | 35.247 | 35.0799 | 35.4356 | 35.3735 | 0 | 49.5334 | 0 | 0 | 49.2 | 49.3 | 3.0389 | 2.9937 | 2.8867 | 2.9481 | 2.9477 | 2.957 | 7.607 | 7.238 | 7.847 | 8.869 | 8.157 | 7.477 | 6.3227 | 6.2705 | 6.3277 | 6.0815 | 6.1481 | 6.2131 | 1.3531 | 1.4572 | 1.1861 | 1.6909 | 1.3723 | 1.5485 | 6.7691 | 6.6214 | 6.714 | 6.521 | 6.5699 | 6.5746 | 0.33502 | 0.39758 | 0.34961 | 0.37031 | 0.38426 | 0.34988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 589799 | 1068 | 577441 | 1144 | 577664.245 | 1543.667 | 6.3227 | 6.2705 | 6.3277 | 6.0815 | 6.1481 | 6.2131 | 6.7691 | 6.6214 | 6.714 | 6.521 | 6.5699 | 6.5746 | 931000 | 1000 | 916000 | 1000 | 1840533 | 4467 | 1845000 | 1836066 | 12.2 | 6.2273 | 1.4347 | 6.6283 | 0.36444 | 23.04% | 5.498% | 35.2688 | 49.3445 | 2.962 | 7.8658 | 1853765.6 | 1838800 | 2139497.2099 | 85.95% | 52 | 396
2024-03-27 | 2024 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 335090.89 | 6:49 | 18:55 | 11145.8 | 11563.1 | 11533.1 | 11525.6 | 11618.7 | 11656.3 | 11651.2 | 11965.9 | 11554.6 | 11521.1 | 11439 | 11554.6 | 11543.3 | 11489.3 | 11561.3 | 11582.4 | 11506.7 | 11521.9 | 11533.1 | 11606.3 | 11538.2 | 11553.8 | 11383.8 | 11456.7 | 11313.8 | 10215.9 | 11313.4 | 11283.5 | 11532.8 | 11452.7 | 11368.8 | 11516.3 | 11664.2 | 11662.2 | 11727 | 11682.2 | 11615.1 | 11493.6 | 11532.6 | 11442.1 | 12195.9 | 11361.2 | 12069.3 | 11209 | 11725.4 | 12599.4 | 11171.5 | 12171 | 10646.1 | 10865.7 | 11590.4 | 11139.5 | 11867.5 | 10945.5 | 11817.9 | 10878.1 | 10843.5 | 11984.9 | 10878.5 | 11933.1 | 11834.6 | 10831.1 | 11645.6 | 11211 | 11376.8 | 10825.4 | 11316.6 | 11662.3 | 11879.3 | 10996.8 | 11746.7 | 10661.8 | 11510.9 | 11381.2 | 10858.1 | 11756.7 | 10731.6 | 11879.9 | 10858.7 | 11759.3 | 11091.1 | 11712.8 | 11144.4 | 12016 | 11052.7 | 11579.9 | 10984.9 | 9887.5 | 11678.8 | 11387.9 | 10805 | 12001.4 | 11731.3 | 11080.8 | 10981.2 | 11789.1 | 10893.2 | 11163.2 | 11889.9 | 10763.1 | 11957.8 | 10797.9 | 11747.3 | 11033.4 | 11771.6 | 10549.3 | 11848.6 | 10952.1 | 11746.2 | 10969.9 | 11808 | 11112.8 | 10780.3 | 11645.7 | 10951.1 | 10782.2 | 11699.2 | 11808.5 | 11648.6 | 10933.7 | 11737 | 10841.8 | 11513.7 | 10955 | 11424.6 | 10232.9 | 11523.1 | 10802.4 | 10979.6 | 10972.9 | 10872.2 | 9495.8 | 10802.5 | 9690.8 | 10868.7 | 10863.8 | 12112.1 | 10947.6 | 12161.8 | 11152.4 | 12041.9 | 10996.1 | 11153 | 10970.7 | 11884.4 | 12149.2 | 12096.4 | 12039.8 | 12060.1 | 12076.9 | 11252.6 | 12095.8 | 12069.4 | 12114.4 | 12161.5 | 12135.3 | 12165 | 11243.1 | 12174.6 | 11277.1 | 36.1064 | 35.9894 | 36.1124 | 35.8494 | 36.2925 | 35.9079 | 0 | 49.322 | 0 | 0 | 49.2 | 49.1 | 4.5527 | 4.5805 | 4.6168 | 4.696 | 4.6749 | 4.647 | 10.557 | 8.574 | 11.171 | 10.133 | 9.932 | 9.059 | 6.2831 | 6.2343 | 6.3318 | 6.1288 | 6.1067 | 6.2162 | 1.4065 | 1.4421 | 1.2346 | 1.7657 | 1.3543 | 1.5543 | 6.7036 | 6.5308 | 6.7023 | 6.5572 | 6.484 | 6.5477 | 0.33039 | 0.39457 | 0.34756 | 0.37038 | 0.37955 | 0.34789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 590712 | 1070 | 578346 | 1146 | 579477 | 1548.333 | 6.2831 | 6.2343 | 6.3318 | 6.1288 | 6.1067 | 6.2162 | 6.7036 | 6.5308 | 6.7023 | 6.5572 | 6.484 | 6.5477 | 913000 | 2000 | 905000 | 2000 | 1812755 | 4666 | 1814000 | 1808089 | 12.1 | 6.2168 | 1.4596 | 6.5876 | 0.36172 | 23.48% | 5.491% | 36.043 | 49.2073 | 4.628 | 9.9043 | 1824726.2 | 1811800 | 2136194.9956 | 84.81% | 55 | 624
2024-03-28 | 2024 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 335090.89 | 6:53 | 19:00 | 11383.1 | 11867.4 | 11841.6 | 11794.8 | 11938.1 | 11941.1 | 11960.3 | 12328.4 | 11865.5 | 11826.4 | 11751.5 | 11878.4 | 11849.3 | 11824.2 | 11855.4 | 11893.4 | 11800 | 11824.1 | 11871.4 | 11945.3 | 11884.7 | 11900.1 | 11685.3 | 11779.4 | 11653.1 | 10449.7 | 11647.2 | 11608.2 | 11898 | 11799.7 | 11692.3 | 11889.3 | 12053.6 | 12060.3 | 12118.1 | 12056.7 | 11984.8 | 11850.8 | 11886 | 11764.1 | 12611.2 | 11632.9 | 12475.2 | 11444.5 | 12059.6 | 13074.5 | 11404.7 | 12589.3 | 11030.3 | 11267.1 | 11943.6 | 11416.5 | 12266.1 | 11183.1 | 12204.5 | 11101.3 | 11081.5 | 12411.5 | 11102.1 | 12336.7 | 12226 | 11060.7 | 12035.3 | 11533.7 | 11701.7 | 11054 | 11633.2 | 12042.5 | 12290.7 | 11262 | 12155 | 10903.4 | 11860.4 | 11714.1 | 11098.8 | 12166.7 | 10968.4 | 12297.7 | 11093.9 | 12156.3 | 11358.6 | 12098.9 | 11423.3 | 12446.5 | 11322 | 11928.5 | 11266 | 10099 | 12074.4 | 11718.6 | 11068.7 | 12458.1 | 12180.7 | 11441.9 | 11337.8 | 12194.2 | 11158.1 | 11491.2 | 12323.1 | 11049.9 | 12384.6 | 11068.6 | 12132.9 | 11341.2 | 12185.6 | 10815.5 | 12263.4 | 11253.6 | 12140.9 | 11259 | 12212.5 | 11414.6 | 11093.3 | 12102.7 | 11271.4 | 11080.8 | 12159 | 12282.3 | 12101.7 | 11279.4 | 12202.3 | 11172.1 | 11941.1 | 11276.9 | 11845.7 | 10548.5 | 12008.2 | 11183 | 11366 | 11383.2 | 11215.4 | 9806.6 | 11146.3 | 9969.4 | 11250.1 | 11262.9 | 12646.4 | 11322.6 | 12706.9 | 11566.5 | 12579.8 | 11385.6 | 11553.7 | 11407.9 | 12376.5 | 12692.6 | 12627 | 12560.8 | 12592.5 | 12613.2 | 11665 | 12628.3 | 12609.3 | 12668.9 | 12676.5 | 12652.1 | 12693 | 11637.1 | 12671.1 | 11675.3 | 33.7498 | 33.4212 | 33.4975 | 33.4192 | 33.6029 | 33.763 | 0 | 47.1 | 0 | 0 | 47.2 | 47.4 | 3.6117 | 3.6299 | 3.563 | 3.619 | 3.5239 | 3.5516 | 8.962 | 7.948 | 7.202 | 8.174 | 7.77 | 7.704 | 6.4367 | 6.4065 | 6.5007 | 6.323 | 6.3622 | 6.4103 | 1.4121 | 1.5139 | 1.252 | 1.7832 | 1.4544 | 1.6292 | 6.8456 | 6.7927 | 6.8663 | 6.7374 | 6.7333 | 6.7408 | 0.35653 | 0.42806 | 0.37946 | 0.40112 | 0.41494 | 0.37842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 591652 | 1071 | 579282 | 1148 | 581347.245 | 1552.933 | 6.4367 | 6.4065 | 6.5007 | 6.323 | 6.3622 | 6.4103 | 6.8456 | 6.7927 | 6.8663 | 6.7374 | 6.7333 | 6.7408 | 940000 | 1000 | 936000 | 2000 | 1870245 | 4600 | 1873000 | 1865645 | 12.1167 | 6.4066 | 1.5075 | 6.786 | 0.39309 | 23.53% | 5.793% | 33.5756 | 47.2333 | 3.5832 | 7.96 | 1882860.6 | 1869600 | 2209051.8041 | 84.63% | 53 | 0
2024-03-29 | 2024 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 335090.89 | 6:53 | 19:02 | 10405.5 | 10877.2 | 10880.7 | 10837.3 | 10978.4 | 11025.1 | 11025.7 | 11342.4 | 10851 | 10738.3 | 10771.3 | 10861.7 | 10932.4 | 10854.6 | 10961.1 | 10981.8 | 10921.4 | 10956.1 | 10966.1 | 11025 | 11008.4 | 11002.8 | 10868.2 | 10927.8 | 10745.7 | 9692.5 | 10731.1 | 10703.2 | 10993.6 | 10942.7 | 10849.3 | 10984.2 | 11048.9 | 11069.1 | 11098.4 | 11040.1 | 11042.5 | 10933.8 | 10976.5 | 10883.2 | 11653.5 | 10786 | 11551.4 | 10627.1 | 11210.3 | 12151.8 | 10622 | 11634.1 | 10189.7 | 10399.3 | 10977.6 | 10481.2 | 11298.3 | 10353.3 | 11191.6 | 10244.8 | 10146.9 | 11330.3 | 10201.2 | 11261 | 11136.7 | 10129.9 | 10921.8 | 10460.8 | 10666.7 | 10099.2 | 10608.2 | 11009.1 | 11219.7 | 10302.7 | 11092.4 | 9974.1 | 10817.3 | 10684.8 | 10130.4 | 11080.7 | 10012.9 | 11202.6 | 10126.9 | 11068.6 | 10382.2 | 11021.2 | 10452 | 11364.3 | 10358.3 | 10898.1 | 10318.1 | 9327.6 | 11003.8 | 10743.5 | 10109.2 | 11350.2 | 11120.4 | 10492.6 | 10417.2 | 11128.5 | 10214.4 | 10489.9 | 11241.3 | 10135.3 | 11362 | 10150.4 | 11152.2 | 10385.7 | 11219.8 | 9982.1 | 11291.7 | 10348.9 | 11219.9 | 10425.7 | 11280 | 10556.8 | 10176.4 | 11057.2 | 10334.1 | 10174.1 | 11146.8 | 11228.9 | 11085 | 10379.4 | 11177.8 | 10292.7 | 10977.4 | 10420.9 | 10886 | 9786.7 | 11030 | 10330.7 | 10421.7 | 10401.5 | 10332.6 | 9078.9 | 10228.2 | 9221.3 | 10201 | 10208.8 | 11419.1 | 10280.9 | 11447.7 | 10453.2 | 11402.3 | 10319.9 | 10494.9 | 10321.8 | 11096.9 | 11366.6 | 11310.9 | 11248 | 11309.2 | 11360.3 | 10478.5 | 11328.4 | 11242.6 | 11296.4 | 11329.5 | 11305.5 | 11355.4 | 10391.1 | 11339.4 | 10430.9 | 32.7229 | 32.4939 | 32.5274 | 32.4169 | 32.6558 | 32.473 | 0 | 46.6493 | 0 | 0 | 46.1 | 46.7 | 3.5329 | 3.6102 | 3.6548 | 3.4858 | 3.2917 | 3.4506 | 8.356 | 7.933 | 8.697 | 7.389 | 8.391 | 8.02 | 5.9065 | 5.9224 | 6.0192 | 5.7668 | 5.7131 | 5.9312 | 1.2903 | 1.3942 | 1.1635 | 1.6061 | 1.2931 | 1.4957 | 6.285 | 6.2729 | 6.3567 | 6.1377 | 6.0196 | 6.1913 | 0.31728 | 0.38412 | 0.33701 | 0.35489 | 0.36115 | 0.34047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 592516 | 1073 | 580136 | 1149 | 583059.512 | 1557.6 | 5.9065 | 5.9224 | 6.0192 | 5.7668 | 5.7131 | 5.9312 | 6.285 | 6.2729 | 6.3567 | 6.1377 | 6.0196 | 6.1913 | 864000 | 2000 | 854000 | 1000 | 1712267 | 4667 | 1715000 | 1707600 | 12.15 | 5.8765 | 1.3738 | 6.2105 | 0.34915 | 23.38% | 5.622% | 32.5483 | 46.4831 | 3.5043 | 8.131 | 1723642.8 | 1712267 | 2035202.3945 | 84.13% | 68 | 37101
2024-03-30 | 2024 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 335090.89 | 6:44 | 19:02 | 12551.2 | 12950 | 12901.6 | 12883.2 | 12982.2 | 13028.6 | 13027.3 | 13345.7 | 12941.2 | 12903.7 | 12829.8 | 12946 | 12946.7 | 12884 | 12961.5 | 12992.2 | 12893.3 | 12931.5 | 12942.7 | 13031 | 12951 | 12983.3 | 12824.4 | 12887.5 | 12765.2 | 11678.1 | 12754.5 | 12729.3 | 12962.4 | 12867.8 | 12809.5 | 12955.9 | 13378 | 13387.2 | 13424.9 | 13376.3 | 13032.9 | 12922.8 | 12943.9 | 12880 | 13566.8 | 12770.4 | 13426.6 | 12618 | 13164.9 | 14032.4 | 12571 | 13541.3 | 12303.9 | 12521.2 | 13036.6 | 12595.7 | 13305.8 | 12403.4 | 13251.3 | 12349 | 12321.9 | 13420.4 | 12363.4 | 13373.4 | 13273.1 | 12293.4 | 13092.6 | 12668.1 | 12837.4 | 12305.8 | 12791 | 13123.1 | 13304 | 12471.5 | 13199.6 | 12166.3 | 12959.6 | 12862.3 | 12318.5 | 13200.2 | 12213.3 | 13313 | 12325.7 | 13196.8 | 12575.8 | 13173.1 | 12636.6 | 13464.4 | 12542 | 13051.2 | 12455.1 | 11340.1 | 13128 | 12858.1 | 12304.8 | 13457.2 | 13193.6 | 12582.5 | 12478.5 | 13228.7 | 12385.4 | 12659.8 | 13316.7 | 12281.8 | 13404.2 | 12291.5 | 13222.5 | 12541.2 | 13216 | 12071.1 | 13296.1 | 12463.9 | 13205.5 | 12448.3 | 13252.7 | 12644.4 | 12329.9 | 13136.7 | 12475.1 | 12324 | 13183.8 | 13307.4 | 13133.8 | 12492.9 | 13238.7 | 12396.8 | 13015.3 | 12500.2 | 12935.3 | 11853.6 | 13103 | 12438.9 | 12555.4 | 12525.9 | 12438.6 | 10988.6 | 12386.4 | 11226.4 | 12454.2 | 12445.7 | 13609.4 | 12529.2 | 13639 | 12722.4 | 13533 | 12553.3 | 12709.2 | 12539.6 | 13407 | 13637.7 | 13621.7 | 13544.8 | 13565.1 | 13588.4 | 12810.9 | 13585.6 | 13562.6 | 13603.6 | 13636.6 | 13615.6 | 13672.6 | 12821.9 | 13651.8 | 12842.9 | 31.3711 | 31.0132 | 31.0239 | 31.0449 | 31.3238 | 30.9462 | 0 | 42.8 | 0 | 0 | 42.9 | 42.8 | 7.2091 | 7.2101 | 7.0934 | 7.1133 | 7.0056 | 7.2319 | 12.66 | 12.811 | 12.469 | 14.516 | 12.748 | 13.24 | 7.037 | 7.014 | 7.1039 | 7.1306 | 7.007 | 7.1937 | 1.6126 | 1.6826 | 1.4356 | 2.0142 | 1.6125 | 1.8346 | 7.5074 | 7.4396 | 7.5302 | 7.4114 | 7.3988 | 7.6509 | 0.38252 | 0.45744 | 0.40001 | 0.42001 | 0.44648 | 0.40581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 593544 | 1074 | 581160 | 1151 | 585104.579 | 1562.133 | 7.037 | 7.014 | 7.1039 | 7.1306 | 7.007 | 7.1937 | 7.5074 | 7.4396 | 7.5302 | 7.4114 | 7.3988 | 7.6509 | 1028000 | 1000 | 1024000 | 2000 | 2045067 | 4533 | 2049000 | 2040534 | 12.3 | 7.081 | 1.6987 | 7.4897 | 0.41871 | 23.99% | 5.59% | 31.1205 | 42.8333 | 7.1439 | 13.074 | 2061302.3 | 2043933 | 2484346.7216 | 82.27% | 47 | 5111
2024-03-31 | 2024 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 335090.89 | 6:45 | 18:59 | 11829.3 | 12281.7 | 12263.5 | 12224.6 | 12368.7 | 12379.7 | 12369.8 | 12753.8 | 12301.8 | 12241.2 | 12198.9 | 12321.9 | 12310.4 | 12275.8 | 12330.9 | 12364.7 | 12278.2 | 12310.1 | 12332.4 | 12412.2 | 12347 | 12368.9 | 12159.1 | 12250.3 | 12129.1 | 10784.5 | 12112.3 | 12088.7 | 12368.4 | 12255.8 | 12158.6 | 12345.7 | 12594 | 12619 | 12662.4 | 12595.8 | 12444.7 | 12316.2 | 12351.4 | 12240 | 13056.6 | 12115.3 | 12928.7 | 11932.4 | 12520.4 | 13496.2 | 11899.6 | 13038 | 11519.1 | 11791.3 | 12416.8 | 11886.6 | 12721.7 | 11625.2 | 12661.3 | 11555 | 11529.3 | 12848.5 | 11543.4 | 12804.2 | 12696.8 | 11511.5 | 12478.8 | 11988.2 | 12137.9 | 11488.3 | 12094.7 | 12469.5 | 12722.3 | 11740.9 | 12594.2 | 11328.5 | 12320.5 | 12184.1 | 11565.1 | 12606.9 | 11416.8 | 12743.5 | 11571.5 | 12598.7 | 11836.9 | 12541 | 11907.1 | 12849.4 | 11795.9 | 12371.3 | 11705.9 | 10403.1 | 12461 | 12155.3 | 11468.8 | 12820.4 | 12537.6 | 11811.4 | 11691.1 | 12575.6 | 11534.9 | 11872.3 | 12651.8 | 11421 | 12750.7 | 11444.6 | 12517.7 | 11720.8 | 12569.5 | 11143.8 | 12645.4 | 11663.9 | 12544.3 | 11676 | 12607.3 | 11838 | 11475.8 | 12415.2 | 11658.9 | 11426.5 | 12482 | 12617 | 12423.8 | 11674 | 12551.9 | 11557.3 | 12298.1 | 11678.8 | 12212.8 | 10830.5 | 12372.5 | 11569.1 | 11796.2 | 11814 | 11644.3 | 10075.8 | 11624.2 | 10302 | 11716 | 11742.6 | 13065.4 | 11853.7 | 13135.5 | 12066 | 13010.4 | 11878.4 | 12040.8 | 11884.2 | 12807.8 | 13121.4 | 13024.6 | 12964.5 | 12988.9 | 13031.6 | 12168.2 | 13060.2 | 12977.9 | 13033.1 | 13100.5 | 13073.7 | 13108 | 12127.4 | 13073.8 | 12131.3 | 31.3641 | 31.0793 | 31.0731 | 31.1525 | 31.236 | 31.342 | 0 | 45 | 0 | 0 | 45 | 45 | 3.0239 | 2.9557 | 2.8817 | 3.0347 | 2.4673 | 2.9759 | 6.951 | 5.947 | 5.637 | 6.529 | 5.863 | 6.095 | 6.5234 | 6.527 | 6.5822 | 6.5812 | 6.4974 | 6.5734 | 1.4654 | 1.5797 | 1.3104 | 1.8467 | 1.5285 | 1.6893 | 6.9172 | 6.8611 | 6.9525 | 6.8221 | 6.8566 | 6.9686 | 0.36674 | 0.44382 | 0.39184 | 0.4128 | 0.42915 | 0.39047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 594520 | 1075 | 582129 | 1153 | 587042.046 | 1566.667 | 6.5234 | 6.527 | 6.5822 | 6.5812 | 6.4974 | 6.5734 | 6.9172 | 6.8611 | 6.9525 | 6.8221 | 6.8566 | 6.9686 | 976000 | 1000 | 969000 | 2000 | 1937467 | 4534 | 1942000 | 1932933 | 12.2333 | 6.5474 | 1.57 | 6.8963 | 0.40581 | 23.98% | 5.884% | 31.2078 | 45 | 2.8899 | 6.1703 | 1951710.2 | 1935934 | 2253803.5249 | 85.9% | 53 | 0
2024-04-01 | 2025 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 335090.89 | 6:41 | 18:56 | 11610.9 | 12008.6 | 11955.9 | 11937.8 | 12028.6 | 12071.3 | 12085.2 | 12385.7 | 12029.5 | 12004 | 11900.6 | 12027.6 | 11989.3 | 11959.6 | 12019.5 | 12040.2 | 11949.5 | 11971.2 | 11995.9 | 12079.1 | 12012.7 | 12035.9 | 11864.4 | 11934.2 | 11858.4 | 10706.4 | 11838.9 | 11808.8 | 12064.8 | 11959 | 11898.5 | 12062.9 | 12359 | 12377.7 | 12421.1 | 12361.4 | 12150.8 | 12032 | 12066.1 | 11974.3 | 12640.4 | 11816.1 | 12537.7 | 11658 | 12202.2 | 13077.8 | 11625 | 12627.3 | 11349.2 | 11577 | 12119.8 | 11669.6 | 12382.3 | 11396.7 | 12362.7 | 11399.8 | 11368.3 | 12525.3 | 11393.2 | 12492.7 | 12400.3 | 11348.1 | 12179.3 | 11750.8 | 11932.3 | 11381.5 | 11894.9 | 12244.6 | 12438.2 | 11570.2 | 12330.9 | 11219.9 | 12070.5 | 11964.5 | 11410.7 | 12344.8 | 11292.8 | 12447.6 | 11406.3 | 12338.6 | 11669.5 | 12302.9 | 11747 | 12593.5 | 11640.8 | 12179.8 | 11565.3 | 10398.9 | 12253.2 | 11974.6 | 11373.1 | 12578.8 | 12321.8 | 11649.4 | 11534.6 | 12347.8 | 11431.9 | 11756.3 | 12470.8 | 11380.7 | 12531 | 11377.8 | 12336 | 11615.5 | 12348.5 | 11101.2 | 12431.2 | 11544.8 | 12327.5 | 11542.8 | 12384.3 | 11702.2 | 11448.3 | 12336.1 | 11592.6 | 11425.3 | 12366.2 | 12505.2 | 12316.7 | 11638 | 12435.6 | 11528.4 | 12168.5 | 11603.2 | 12087.3 | 10898.9 | 12275.2 | 11551.3 | 11715.6 | 11716.5 | 11562.8 | 10119.9 | 11580 | 10404 | 11629.5 | 11653.7 | 12878.3 | 11790.2 | 12924.3 | 11976.7 | 12813.2 | 11814.2 | 11961.8 | 11793.4 | 12679.4 | 12928.5 | 12891.2 | 12831.5 | 12845.4 | 12858.1 | 12079 | 12881.1 | 12828.3 | 12883.7 | 12936.1 | 12910.3 | 12932.4 | 12068.1 | 12925.1 | 12098.3 | 31.022 | 30.6945 | 30.7527 | 30.7814 | 30.7337 | 31.0402 | 0 | 44.4 | 0 | 0 | 44.8 | 45.1 | 3.1923 | 3.1816 | 3.1427 | 3.2711 | 2.8173 | 3.1686 | 6.902 | 6.765 | 6.989 | 7.555 | 7.803 | 7.501 | 6.4605 | 6.4823 | 6.501 | 6.5666 | 6.5726 | 6.6637 | 1.4788 | 1.5331 | 1.3222 | 1.8689 | 1.5069 | 1.6909 | 6.7979 | 6.7295 | 6.8191 | 6.7533 | 6.8609 | 6.9955 | 0.37199 | 0.45132 | 0.39515 | 0.4223 | 0.44164 | 0.40495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 595474 | 1077 | 583087 | 1154 | 588948.513 | 1571.333 | 6.4605 | 6.4823 | 6.501 | 6.5666 | 6.5726 | 6.6637 | 6.7979 | 6.7295 | 6.8191 | 6.7533 | 6.8609 | 6.9955 | 954000 | 2000 | 958000 | 1000 | 1906467 | 4666 | 1909000 | 1901801 | 12.25 | 6.5411 | 1.5668 | 6.826 | 0.41456 | 23.95% | 6.073% | 30.8374 | 44.7667 | 3.1289 | 7.2525 | 1920526.1 | 1905333 | 2276701.673 | 83.69% | 57 | 0
2024-04-02 | 2025 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 335090.89 | 6:45 | 18:57 | 11209.3 | 11647.5 | 11612.7 | 11578.4 | 11674.9 | 11732.2 | 11742.4 | 12130.3 | 11662.2 | 11613 | 11526.7 | 11658.6 | 11624.9 | 11592.3 | 11653.3 | 11699 | 11614.1 | 11635.4 | 11642.7 | 11706.8 | 11677 | 11680.2 | 11487.5 | 11573.3 | 11443.3 | 10167 | 11414.6 | 11397.5 | 11698.7 | 11585.4 | 11487.2 | 11680.5 | 11874.6 | 11883.9 | 11909.5 | 11861.6 | 11777.7 | 11633.9 | 11682.6 | 11583.3 | 12460.1 | 11469.4 | 12338.2 | 11283.8 | 11875.1 | 12934.6 | 11252.9 | 12444.2 | 10843.5 | 11093.5 | 11728 | 11185.2 | 12035.2 | 10933.9 | 11992 | 10881 | 10854.1 | 12195.7 | 10884.6 | 12144 | 12036.1 | 10845.3 | 11803.1 | 11305.9 | 11480.8 | 10881.5 | 11454.8 | 11892.3 | 12106.3 | 11112.4 | 11968.8 | 10701.8 | 11671.4 | 11543.3 | 10905.1 | 11999.3 | 10774.1 | 12121.6 | 10903.2 | 11981.7 | 11222.3 | 11945 | 11313.3 | 12291.7 | 11199.2 | 11805.1 | 11119.7 | 9879.8 | 11900 | 11572.5 | 10880.3 | 12268.4 | 11924.6 | 11143 | 11014.7 | 11996.2 | 10912.8 | 11294.6 | 12143.7 | 10887.9 | 12195 | 10878.4 | 11952.9 | 11129.2 | 11996.1 | 10588.5 | 12066.4 | 11081.5 | 11944.8 | 11055.3 | 11992 | 11220.3 | 10914 | 11926.4 | 11100.9 | 10892.2 | 11977 | 12126.9 | 11923 | 11104.8 | 12059.1 | 11008 | 11767.5 | 11103.3 | 11669.5 | 10322.4 | 11842.2 | 10999.2 | 11157 | 11142.7 | 11022.9 | 9542.3 | 10948.5 | 9730.9 | 10987.8 | 11007 | 12450 | 11146.9 | 12476.9 | 11339.8 | 12371.1 | 11163.9 | 11343 | 11143.6 | 12127.5 | 12465.8 | 12399.5 | 12337 | 12379 | 12403.3 | 11417.8 | 12392.3 | 12370.8 | 12411.4 | 12470 | 12436.3 | 12461.1 | 11415 | 12446.8 | 11447 | 32.8618 | 32.7387 | 32.9381 | 32.5936 | 32.9502 | 32.7254 | 0 | 47.5 | 0 | 0 | 47.6 | 48 | 2.4864 | 2.5189 | 2.423 | 2.4956 | 2.4879 | 2.3843 | 6.443 | 7.686 | 6.613 | 7.338 | 6.421 | 6.259 | 6.2182 | 6.23 | 6.2966 | 6.2722 | 6.1841 | 6.3662 | 1.4393 | 1.4723 | 1.2889 | 1.8023 | 1.402 | 1.6218 | 6.5355 | 6.4729 | 6.5842 | 6.4506 | 6.4326 | 6.6699 | 0.35482 | 0.42939 | 0.37945 | 0.40067 | 0.41331 | 0.38245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 596398 | 1079 | 584007 | 1156 | 590786.646 | 1575.933 | 6.2182 | 6.23 | 6.2966 | 6.2722 | 6.1841 | 6.3662 | 6.5355 | 6.4729 | 6.5842 | 6.4506 | 6.4326 | 6.6699 | 924000 | 2000 | 920000 | 2000 | 1838133 | 4600 | 1840000 | 1833533 | 12.2 | 6.2612 | 1.5044 | 6.5243 | 0.39335 | 24.03% | 6.029% | 32.8013 | 47.7 | 2.466 | 6.7933 | 1850680.3 | 1837267 | 2163953.278 | 84.9% | 56 | 2576
2024-04-03 | 2025 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 335090.89 | 6:45 | 19:03 | 10593.8 | 11058.1 | 11047 | 10999 | 11119.9 | 11165.3 | 11153.4 | 11584.1 | 11073.8 | 11017.6 | 10948.9 | 11080.4 | 11042 | 11020.7 | 11076.6 | 11120.4 | 11049.1 | 11061.1 | 11089.3 | 11134.8 | 11124.7 | 11119.5 | 10907.3 | 10999.9 | 10873.1 | 9583.4 | 10835.1 | 10813.9 | 11138.3 | 11022.9 | 10929.5 | 11147.6 | 11225.9 | 11238.2 | 11260.3 | 11201.2 | 11220.6 | 11071.2 | 11126.5 | 11044.8 | 11887.8 | 10792.3 | 11782.1 | 10616.4 | 11250 | 12411.8 | 10580.8 | 11889.6 | 10212.5 | 10459.6 | 11154.3 | 10580.9 | 11514.3 | 10301.2 | 11449 | 10273.5 | 10237.4 | 11684.1 | 10245.3 | 11594.8 | 11475.5 | 10216.7 | 11239.4 | 10686.5 | 10852.8 | 10264.2 | 10846.9 | 11313.6 | 11585.5 | 10481.2 | 11417 | 10077.2 | 11108.4 | 10929.2 | 10283.6 | 11443.1 | 10144.6 | 11575.4 | 10292.8 | 11429.6 | 10600.6 | 11373.9 | 10714.5 | 11758.7 | 10581.3 | 11238.1 | 10504.5 | 9321.2 | 11348.2 | 10997.1 | 10277.2 | 11776.3 | 11440.8 | 10610.1 | 10510.1 | 11473.7 | 10321.3 | 10711.7 | 11647.7 | 10302.1 | 11685.6 | 10281.5 | 11407.3 | 10540.5 | 11487.4 | 10004.5 | 11539.9 | 10479.2 | 11404.8 | 10455.8 | 11482.4 | 10614.1 | 10322.5 | 11396.8 | 10503.2 | 10291.9 | 11452.9 | 11607.2 | 11383.2 | 10521.3 | 11543.3 | 10406.3 | 11209.8 | 10491.6 | 11090.4 | 9765.7 | 11290.5 | 10410.4 | 10589.9 | 10536.9 | 10436.3 | 9048.5 | 10407.6 | 9214.9 | 10463.8 | 10464 | 12060.1 | 10638.4 | 12105 | 10852.5 | 11959.8 | 10640.2 | 10829.5 | 10613.6 | 11718.4 | 12081.3 | 11989.7 | 11951.9 | 11965.7 | 11997 | 10941.4 | 12012.5 | 11964.9 | 12015.9 | 12080.3 | 12052.6 | 12077.5 | 10934.8 | 12026.6 | 10969.1 | 31.0127 | 30.9535 | 31.009 | 30.7964 | 31.0111 | 30.8074 | 0 | 44.5 | 0 | 0 | 44.8 | 44.6 | 3.2628 | 3.4891 | 3.3548 | 3.3344 | 3.3715 | 3.3671 | 6.808 | 6.935 | 6.101 | 6.652 | 7.574 | 6.031 | 5.7954 | 5.8164 | 5.8363 | 5.8439 | 5.8276 | 5.9468 | 1.327 | 1.36 | 1.1903 | 1.6456 | 1.327 | 1.5212 | 6.0242 | 5.7267 | 6.0071 | 5.7849 | 6.011 | 6.1433 | 0.3541 | 0.4336 | 0.37732 | 0.40616 | 0.42178 | 0.39722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 597275 | 1080 | 584886 | 1158 | 592537.18 | 1580.6 | 5.7954 | 5.8164 | 5.8363 | 5.8439 | 5.8276 | 5.9468 | 6.0242 | 5.7267 | 6.0071 | 5.7849 | 6.011 | 6.1433 | 877000 | 1000 | 879000 | 2000 | 1750534 | 4667 | 1753000 | 1745867 | 12.3 | 5.8444 | 1.3952 | 5.9496 | 0.39836 | 23.87% | 6.696% | 30.9317 | 44.6333 | 3.3633 | 6.6835 | 1762119.8 | 1749267 | 2006662.9398 | 87.17% | 53 | 2530
2024-04-04 | 2025 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 335090.89 | 6:43 | 18:59 | 9549.5 | 9927 | 9895.3 | 9871.5 | 9965.2 | 10056.7 | 10007.7 | 10365.1 | 9960.2 | 9878.9 | 9836.9 | 9953 | 9935 | 9896.1 | 9966.7 | 10002.1 | 9924.5 | 9914.7 | 9898 | 9955.3 | 9906.4 | 9911.7 | 9710.1 | 9799.1 | 9691.6 | 8660.5 | 9684.9 | 9647.2 | 9899.7 | 9794.8 | 9739.5 | 9913.8 | 10005.9 | 10034.6 | 10072.8 | 10013.3 | 9997.1 | 9873.8 | 9908.9 | 9823.1 | 10518.1 | 9602.5 | 10395.8 | 9444.7 | 9980.1 | 10957.7 | 9434.6 | 10522.5 | 9220.7 | 9419.8 | 9988.8 | 9496.3 | 10264.4 | 9280 | 10244.2 | 9253.8 | 9260.9 | 10475.2 | 9268.8 | 10380.8 | 10284.7 | 9250.3 | 10093.5 | 9628.8 | 9820.4 | 9260 | 9768.4 | 10137.4 | 10380.8 | 9431.1 | 10206.8 | 9097.4 | 9998.7 | 9816.8 | 9307.9 | 10251.6 | 9186.4 | 10386 | 9321.5 | 10274.2 | 9511.3 | 10176.4 | 9573.5 | 10485 | 9469.2 | 10012.7 | 9427.7 | 8420.3 | 10067.1 | 9819.3 | 9170.6 | 10423.7 | 10161.3 | 9477.3 | 9394.7 | 10182.5 | 9188 | 9473.8 | 10242.7 | 9115.3 | 10297.4 | 9113.3 | 10068.6 | 9329.7 | 10131.2 | 8890.4 | 10184.3 | 9275.2 | 10087.7 | 9280.3 | 10133.9 | 9412.4 | 9116.4 | 9998.2 | 9280 | 9094.2 | 10067.5 | 10197.6 | 10019.6 | 9300 | 10146.2 | 9216.2 | 9851.6 | 9255.7 | 9771 | 8695.5 | 9958.6 | 9207.7 | 9339 | 9322.8 | 9222.4 | 8054.7 | 9202.2 | 8238.5 | 9304.9 | 9311.1 | 10649.9 | 9429.3 | 10742.3 | 9642.2 | 10556.5 | 9468.4 | 9624.2 | 9436.2 | 10451.1 | 10790.8 | 10648.9 | 10601.3 | 10603.1 | 10617.7 | 9790.3 | 10692.5 | 10646.9 | 10699.4 | 10811.7 | 10763.9 | 10797.3 | 9796.1 | 10686.2 | 9796.8 | 33.4095 | 33.1622 | 33.2157 | 33.2415 | 33.291 | 33.2704 | 0 | 44.8 | 0 | 0 | 44.7 | 44.8 | 3.0589 | 3.1365 | 2.921 | 3.1274 | 3.1389 | 3.003 | 6.812 | 6.888 | 6.429 | 6.955 | 6.667 | 6.215 | 5.3367 | 5.2757 | 5.2664 | 5.3519 | 5.262 | 5.3053 | 1.2715 | 1.212 | 1.1276 | 1.568 | 1.1578 | 1.3416 | 5.5402 | 5.2315 | 5.4254 | 5.3794 | 5.3878 | 5.4824 | 0.32768 | 0.39891 | 0.34839 | 0.37861 | 0.38797 | 0.36051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 598061 | 1082 | 585667 | 1160 | 594099.313 | 1585.267 | 5.3367 | 5.2757 | 5.2664 | 5.3519 | 5.262 | 5.3053 | 5.5402 | 5.2315 | 5.4254 | 5.3794 | 5.3878 | 5.4824 | 786000 | 2000 | 781000 | 2000 | 1562133 | 4667 | 1563000 | 1557466 | 12.2667 | 5.2997 | 1.2797 | 5.4078 | 0.36701 | 24.15% | 6.787% | 33.265 | 44.7667 | 3.0643 | 6.661 | 1571072 | 1560866 | 1808435.0584 | 86.31% | 65 | 30895
2024-04-05 | 2025 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 335090.89 | 6:47 | 19:06 | 7458.3 | 7830.3 | 7856.7 | 7789.9 | 7940.3 | 7979.4 | 7939.9 | 8208.3 | 7846.8 | 7826.1 | 7742.1 | 7859 | 7846.6 | 7810.2 | 7888 | 7901.4 | 7840.3 | 7832.1 | 7850.5 | 7880.8 | 7907.4 | 7890.6 | 7769.6 | 7842 | 7724.6 | 6825.9 | 7714 | 7691.3 | 7903.6 | 7819.1 | 7748.4 | 7888.5 | 8029.7 | 8020.9 | 8000.3 | 7979.1 | 7971.9 | 7865.3 | 7902.5 | 7878.2 | 8696.3 | 8022.4 | 8573 | 7919.8 | 8180.5 | 8893.6 | 7661.1 | 8586 | 7301.3 | 7476.2 | 7939.2 | 7533.6 | 8165.7 | 7323.2 | 8105.5 | 7304.2 | 7297 | 8284.2 | 7305.8 | 8247.3 | 8160.3 | 7260.8 | 7979.4 | 7592.2 | 7811.9 | 7403.4 | 7777.7 | 8161.4 | 8263.6 | 7597.3 | 8190.9 | 7314.6 | 7968.7 | 7884.6 | 7396.5 | 8203.7 | 7297.5 | 8266.8 | 7369.4 | 8161.9 | 7727.9 | 8235.4 | 7813.2 | 8510.7 | 7727.2 | 8198.3 | 7638.6 | 6840.5 | 8381.8 | 8066.7 | 7592.2 | 8605.4 | 8327.4 | 7720.3 | 7592.5 | 8356.5 | 7639 | 7981.5 | 8606.2 | 7721.4 | 8515 | 7631.1 | 8347.2 | 7810.4 | 8429.6 | 7387.6 | 8507.5 | 7816.8 | 8406.6 | 7765.7 | 8478.3 | 7959.6 | 7793.1 | 8606.8 | 7884.5 | 7765.3 | 8594 | 8743.6 | 8544 | 7989.5 | 8670.6 | 7857.9 | 8398.7 | 7875.5 | 8300.7 | 7354.6 | 8498.7 | 7866.8 | 8038.2 | 8069.5 | 7916.9 | 6856.3 | 7920.3 | 7104.3 | 8162.5 | 8168.2 | 9338.1 | 8359.4 | 9382.2 | 8538.7 | 9293.5 | 8354.3 | 8491.9 | 8269.3 | 9105.6 | 9362.8 | 9294.8 | 9270.1 | 9267 | 9289.3 | 8603.6 | 9328.1 | 9178.7 | 9249.4 | 9272.7 | 9260.9 | 9330.1 | 8538.7 | 9297.1 | 8557.8 | 31.021 | 30.8613 | 30.8657 | 30.9179 | 31.0108 | 31.0807 | 0 | 40.1 | 0 | 0 | 41.7 | 41.5 | 3.3716 | 3.2365 | 3.3178 | 3.4041 | 2.9883 | 3.4563 | 9.091 | 8.112 | 8.292 | 8.706 | 10.692 | 9.249 | 4.092 | 4.1341 | 4.247 | 4.1281 | 4.5792 | 4.4768 | 0.90495 | 0.97518 | 0.85322 | 1.1605 | 1.0838 | 1.1449 | 4.2267 | 4.2494 | 4.3114 | 4.296 | 4.6957 | 4.5823 | 0.25089 | 0.30918 | 0.27331 | 0.2972 | 0.32707 | 0.29867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 598688 | 1083 | 586331 | 1161 | 595385.713 | 1589.933 | 4.092 | 4.1341 | 4.247 | 4.1281 | 4.5792 | 4.4768 | 4.2267 | 4.2494 | 4.3114 | 4.296 | 4.6957 | 4.5823 | 627000 | 1000 | 664000 | 1000 | 1286400 | 4666 | 1289000 | 1281734 | 12.3167 | 4.2762 | 1.0204 | 4.3936 | 0.29272 | 23.86% | 6.662% | 30.9596 | 41.1 | 3.2958 | 9.0237 | 1293931.1 | 1285533 | 1487954.4145 | 86.4% | 72 | 145605
2024-04-06 | 2025 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 335090.89 | 6:41 | 19:05 | 11203.1 | 11671.5 | 11527.1 | 11513.1 | 11666.7 | 11730.3 | 11680.2 | 12050.2 | 11683.3 | 11546.2 | 11606 | 11658.3 | 11889.6 | 11710.1 | 11949.7 | 11915 | 11899.4 | 11946.9 | 11945.2 | 12017.8 | 12036.5 | 11962.8 | 11833.9 | 11873.4 | 11681 | 10472.7 | 11701 | 11651 | 11913.6 | 11930.3 | 11863.8 | 11901.4 | 12121.5 | 11997.1 | 12075.7 | 11997.5 | 11935.6 | 11910.8 | 11981.7 | 11883.3 | 13153.4 | 12346.6 | 13022.2 | 12170.4 | 12751.8 | 13436.7 | 12111.5 | 13152.5 | 11151.6 | 11259.4 | 11918.5 | 11327.1 | 12228.6 | 11355.7 | 11949.9 | 11140.2 | 10913.6 | 12018.4 | 11013 | 12048.6 | 11845.1 | 10927.1 | 11597.4 | 11209.3 | 11380.9 | 10822.6 | 11331.2 | 11624.5 | 11861.4 | 10948.9 | 11713.3 | 10552 | 11581.1 | 11267.3 | 10818.6 | 11690.9 | 10609.3 | 11802 | 10771.1 | 11653.6 | 10994.1 | 11555.1 | 11118.8 | 11877.8 | 11035.1 | 11625 | 11082.4 | 9876.4 | 11924.5 | 11486.5 | 11144.9 | 12321.4 | 12134 | 11585.8 | 11514.1 | 12091.8 | 11124.6 | 11411.6 | 12033.6 | 10989.5 | 12256 | 11044.7 | 12035.6 | 11284.1 | 12071 | 10811 | 12129 | 11251.8 | 12109.4 | 11337.6 | 12202.4 | 11484.7 | 10911.8 | 11604.4 | 11139.8 | 10949.3 | 11872.8 | 11755.1 | 11836.1 | 11017.3 | 11912.6 | 11116.3 | 11835.6 | 11383.8 | 11820.7 | 10586.5 | 11965.6 | 11180.7 | 11100.2 | 10982.8 | 11185 | 9497 | 10757.8 | 9588.3 | 10308.3 | 10267.9 | 11683.5 | 10533.4 | 11561.3 | 10578.6 | 11355.7 | 10345.5 | 10469.3 | 10368.8 | 11442.8 | 11704 | 11678.6 | 11603.7 | 11658.1 | 11684.8 | 10828.1 | 11596.8 | 11787 | 11723.3 | 11834 | 11702.7 | 11720.6 | 10859.5 | 11757.9 | 10932.7 | 32.7841 | 32.4785 | 32.527 | 32.4832 | 32.4081 | 32.547 | 0 | 45.8 | 0 | 0 | 45 | 45.7 | 2.6549 | 2.7233 | 2.6462 | 2.6015 | 2.501 | 2.6088 | 6.156 | 5.814 | 6.263 | 7.101 | 6.697 | 6.553 | 6.3133 | 6.3886 | 6.9267 | 6.1579 | 6.0286 | 6.3827 | 1.3452 | 1.5231 | 1.423 | 1.7747 | 1.3717 | 1.6307 | 6.6524 | 6.5409 |  | 6.2892 | 6.2088 | 6.6477 | 0.35217 | 0.43895 | 0.41186 | 0.39702 | 0.4023 | 0.38003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 599623 | 1085 | 587234 | 1163 | 597217.78 | 1594.467 | 6.3133 | 6.3886 | 6.9267 | 6.1579 | 6.0286 | 6.3827 | 6.6524 | 6.5409 | 0 | 6.2892 | 6.2088 | 6.6477 | 935000 | 2000 | 903000 | 2000 | 1832067 | 4534 | 1834000 | 1827533 | 12.4 | 6.3663 | 1.5114 | 6.4678 | 0.39705 | 23.74% | 6.139% | 32.538 | 45.5 | 2.6226 | 6.4307 | 1844942.3 | 1830733 | 2151020.2823 | 85.11% | 72 | 54683
2024-04-07 | 2025 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 335090.89 | 6:36 | 19:05 | 10854.7 | 11162.7 | 11169.1 | 11100.7 | 11179.3 | 11200 | 11211.3 | 11445.3 | 11156.2 | 11146.4 | 11072.3 | 11229.5 | 11239.2 | 11119.8 | 11206.3 | 11213.1 | 11123 | 11200.7 | 11156 | 11303.5 | 11155.2 | 11179.5 | 11087.5 | 11091.3 | 10977.5 | 10269.4 | 11008.7 | 10961.5 | 11206.8 | 11040.9 | 10999.7 | 11105.8 | 12949.7 | 12944.5 | 12977.5 | 12904.5 | 11176.5 | 11157.3 | 11172.7 | 11110.6 | 11601.2 | 10969 | 11512.2 | 10844.4 | 11236.9 | 11979.5 | 10788.4 | 11570.3 | 10706.1 | 10855.7 | 11259.4 | 10949.6 | 11529.2 | 10823.9 | 11392.8 | 10701.9 | 10682.6 | 11553.2 | 10817.6 | 11583.7 | 11447.5 | 10747.7 | 11270.5 | 11015.4 | 11091.4 | 10729.3 | 11079.9 | 11382.4 | 11554.5 | 10858.4 | 11495.3 | 10729.6 | 11184.8 | 11161.5 | 10709.3 | 11425.2 | 10670.5 | 11473.8 | 10730.9 | 11459 | 10948.4 | 11425 | 10974.2 | 11656.7 | 10968.4 | 11300.8 | 10828.2 | 10228.5 | 11433.6 | 11134.7 | 10803.3 | 11651.8 | 11442.5 | 10939.9 | 10834.8 | 11453.5 | 10866.8 | 11042.9 | 11575.1 | 10754.2 | 11669.3 | 10813.8 | 11447 | 10989.4 | 11499.1 | 10576.1 | 11511.6 | 10914.6 | 11436.8 | 10859.1 | 11535.1 | 11019.1 | 10765.7 | 11398.4 | 10864.1 | 10761.3 | 11420 | 11529.6 | 11446.3 | 10899 | 11474.6 | 10870.1 | 11291.5 | 10885 | 11299.7 | 10520.7 | 11369.8 | 10858.8 | 10934.2 | 10900.8 | 10836.7 | 10031.1 | 10769.3 | 10188.7 | 10864.6 | 10810.2 | 11807.2 | 10900.9 | 11829.3 | 11100.4 | 11777.3 | 10876.8 | 10990 | 10879.5 | 11611.8 | 11912.1 | 11882.5 | 11757.3 | 11783.7 | 11798.7 | 11132.2 | 11852.7 | 11753.5 | 11774.6 | 11768.8 | 11810.8 | 11835.8 | 11165.9 | 11829 | 11146.2 | 34.259 | 34.1501 | 34.119 | 33.9904 | 34.2136 | 34.2555 | 0 | 49.1 | 0 | 0 | 49.6 | 49.3 | 2.7802 | 2.6382 | 2.6037 | 2.6243 | 2.6949 | 2.1773 | 6.539 | 6.605 | 6.681 | 6.438 | 6.38 | 7.121 | 6.9721 | 6.7771 | 6.982 | 7.1239 | 6.9132 | 6.9667 | 1.5088 | 1.6647 | 1.4603 | 1.981 | 1.8479 | 1.6284 | 7.3342 | 6.2905 | 7.2686 | 7.3057 | 7.3339 | 7.1758 | 0.37325 | 0.45545 | 0.40788 | 0.41838 | 0.40257 | 0.44095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600518 | 1086 | 588128 | 1165 | 599002.113 | 1599 | 6.9721 | 6.7771 | 6.982 | 7.1239 | 6.9132 | 6.9667 | 7.3342 | 6.2905 | 7.2686 | 7.3057 | 7.3339 | 7.1758 | 895000 | 1000 | 894000 | 2000 | 1784333 | 4533 | 1786000 | 1779800 | 12.4833 | 6.9558 | 1.6818 | 7.1181 | 0.41641 | 24.18% | 5.85% | 34.1646 | 49.3333 | 2.5864 | 6.6273 | 1794042.2 | 873600 | 1033806.461 | 84.5% | 64 | 2484
2024-04-08 | 2025 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 335090.89 | 6:38 | 19:05 | 11054.3 | 11347 | 11291.5 | 11296 | 11352 | 11387.6 | 11407.7 | 11637.4 | 11335.6 | 11324.9 | 11248.9 | 11340.6 | 11352.2 | 11286.7 | 11381.7 | 11392.7 | 11294.6 | 11302.4 | 11320.9 | 11410.8 | 11320.2 | 11352.4 | 11224.4 | 11271.8 | 11166.9 | 10485.3 | 11183.6 | 11141.7 | 11314.7 | 11223.8 | 11199.5 | 11295.9 | 13170.4 | 13160.9 | 13237.2 | 13176.5 | 11359.5 | 11281.3 | 11291.2 | 11232 | 11799.9 | 11208.1 | 11703.1 | 11095.8 | 11474.7 | 12161 | 11010.7 | 11763.7 | 10913.4 | 11052.2 | 11439.9 | 11074.2 | 11621.3 | 10955.9 | 11558.2 | 10907.7 | 10876.3 | 11685.1 | 10973.9 | 11662.1 | 11592 | 10891.4 | 11398.9 | 11100.8 | 11209 | 10843.9 | 11196.8 | 11449.3 | 11584.4 | 10960.6 | 11501.7 | 10797.6 | 11315.3 | 11249 | 10867.1 | 11491.6 | 10802.8 | 11593.1 | 10888.7 | 11491.4 | 11053.4 | 11498 | 11080.4 | 11712.9 | 11022.4 | 11390.9 | 10929.6 | 10380.2 | 11447.5 | 11229.4 | 10877.2 | 11711.3 | 11512.4 | 11048.1 | 10950.9 | 11526.8 | 10913.4 | 11124.1 | 11626.3 | 10872.8 | 11670.1 | 10880.4 | 11549.8 | 11051 | 11524.2 | 10716.5 | 11599.2 | 10968 | 11541.8 | 10980.9 | 11546.4 | 11129.5 | 10868.3 | 11464.4 | 10983.9 | 10889.9 | 11494.2 | 11583.7 | 11460.2 | 11000.3 | 11495.2 | 10930.5 | 11377.2 | 11006.1 | 11339.8 | 10656 | 11446.6 | 10967.9 | 11036.6 | 10982.9 | 10946 | 10186.1 | 10867.9 | 10266.4 | 10923.3 | 10920.1 | 11849.3 | 11006.9 | 11868.6 | 11139.6 | 11758.8 | 10984.1 | 11097.6 | 10972.6 | 11683.5 | 11885 | 11871.7 | 11807.2 | 11833.2 | 11843.3 | 11226.1 | 11824.8 | 11787 | 11816.5 | 11850.7 | 11831.6 | 11887.5 | 11215.2 | 11870.9 | 11241.7 | 35.2825 | 35.0804 | 35.1223 | 35.0514 | 35.2918 | 35.1524 | 0 | 50.4 | 0 | 0 | 50.9 | 50.4 | 2.3365 | 2.4276 | 2.3517 | 2.3788 | 2.3981 | 2.2262 | 7.001 | 6.134 | 5.446 | 6.19 | 7.288 | 7.011 | 7.1352 | 7.2729 | 7.1247 | 6.6302 | 7.0757 | 7.0275 | 1.5418 | 1.7121 | 1.483 | 2.0105 | 1.8768 | 1.6516 | 7.3438 | 7.5453 | 7.4681 | 7.3323 | 7.3388 | 7.6636 | 0.38533 | 0.47327 | 0.41995 | 0.43097 | 0.42006 | 0.46024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 601426 | 1088 | 589028 | 1166 | 600804.98 | 1603.533 | 7.1352 | 7.2729 | 7.1247 | 6.6302 | 7.0757 | 7.0275 | 7.3438 | 7.5453 | 7.4681 | 7.3323 | 7.3388 | 7.6636 | 908000 | 2000 | 900000 | 1000 | 1802867 | 4533 | 1805000 | 1798334 | 12.45 | 7.0444 | 1.7126 | 7.4486 | 0.43164 | 24.31% | 5.795% | 35.1635 | 50.5667 | 2.3532 | 6.5117 | 1812330 | 832667 | 980492.2873 | 84.92% | 60 | 298
2024-04-09 | 2025 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 335090.89 | 6:40 | 18:59 | 10360.4 | 10754.5 | 10727.8 | 10714.2 | 10803.8 | 10842.1 | 10824.9 | 11137 | 10766.6 | 10747.5 | 10662.3 | 10778.2 | 10764.5 | 10727.4 | 10805.5 | 10807.7 | 10744.6 | 10760.4 | 10802 | 10858.4 | 10812.3 | 10815.8 | 10625.2 | 10713.2 | 10544.7 | 9511.6 | 10573.2 | 10524.6 | 10771.9 | 10677.2 | 10616.3 | 10755.2 | 10804.9 | 10815.1 | 10925.1 | 10870.3 | 10823 | 10711.8 | 10729.2 | 10610.5 | 11406.4 | 10594.6 | 11277 | 10421.7 | 10902.3 | 11738.4 | 10367.4 | 11392.3 | 10116.2 | 10310.5 | 10861.7 | 10350.6 | 11111.9 | 10228.8 | 11028.8 | 10114 | 10075.5 | 11185.7 | 10151.4 | 11143.9 | 11048.6 | 10107.6 | 10828.2 | 10419.7 | 10540 | 10023.3 | 10496.1 | 10847.4 | 11066.5 | 10187.5 | 10914.7 | 9896 | 10720.5 | 10555.1 | 10078.7 | 10924.1 | 9942.2 | 11079.4 | 10086.1 | 10941.2 | 10295.3 | 10897 | 10343.7 | 11181.8 | 10267.2 | 10769.9 | 10203.7 | 9203.5 | 10898.5 | 10604.2 | 10082.6 | 11230.9 | 10991.6 | 10359.2 | 10267.2 | 10998.6 | 10083.2 | 10351.2 | 11048 | 10010.1 | 11105.3 | 10030.7 | 10907.9 | 10221.2 | 10938 | 9787.4 | 10998.8 | 10152.3 | 10915.7 | 10161.2 | 10943.8 | 10291.9 | 10002.2 | 10808.9 | 10146.6 | 9987.8 | 10865.1 | 10954.2 | 10810.1 | 10119.8 | 10865.8 | 10052.9 | 10691.9 | 10157.5 | 10597.6 | 9532.8 | 10737.8 | 10043 | 10184.8 | 10171.7 | 10066.9 | 8835.8 | 9934.6 | 8894.5 | 9724.1 | 9776 | 11156.3 | 10029.9 | 11116.1 | 10136.3 | 10950.5 | 9874.3 | 10023.5 | 9854.8 | 10892.8 | 11120.7 | 11170.2 | 11099.7 | 11122.1 | 11129.4 | 10256.2 | 11060.9 | 11119.4 | 11138.1 | 11156.6 | 11114.1 | 11143.9 | 10248 | 11239.8 | 10345.9 | 36.4416 | 36.2043 | 36.1625 | 36.3015 | 36.554 | 36.3035 | 0 | 47.7 | 0 | 0 | 47.7 | 47.4 | 3.6094 | 3.6453 | 3.5672 | 3.6895 | 3.5311 | 2.8646 | 6.988 | 7.565 | 7.255 | 7.916 | 6.697 | 6.844 | 5.81 | 5.9422 | 5.8748 | 5.5274 | 5.7822 | 5.6573 | 1.2876 | 1.4005 | 1.2358 | 1.6719 | 1.5193 | 1.3115 | 6.0733 | 5.8306 | 6.1365 | 6.059 | 5.9282 | 6.0534 | 0.33548 | 0.41321 | 0.36521 | 0.38489 | 0.37541 | 0.39642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 602277 | 1089 | 589864 | 1168 | 602487.38 | 1607.933 | 5.81 | 5.9422 | 5.8748 | 5.5274 | 5.7822 | 5.6573 | 6.0733 | 5.8306 | 6.1365 | 6.059 | 5.9282 | 6.0534 | 851000 | 1000 | 836000 | 2000 | 1682400 | 4400 | 1684000 | 1678000 | 12.3167 | 5.7657 | 1.4044 | 6.0135 | 0.37844 | 24.36% | 6.293% | 36.3279 | 47.6 | 3.4845 | 7.2108 | 1693106.4 | 1681934 | 1979101.9393 | 84.98% | 84 | 25033
2024-04-10 | 2025 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 335090.89 | 6:56 | 19:04 | 9324.3 | 9717.8 | 9794.6 | 9787.2 | 9897.8 | 9912.5 | 9822.9 | 10015.8 | 9603.3 | 9544.4 | 9489.4 | 9563.1 | 9670.5 | 9530.4 | 9806.7 | 9774 | 9721.2 | 9667.8 | 9613.7 | 9664.8 | 9629.3 | 9626.8 | 9481 | 9547.3 | 9306.5 | 8312.1 | 9406.6 | 9355.2 | 9532.9 | 9460.1 | 9338.8 | 9450 | 9349 | 9343.1 | 9515.8 | 9446.5 | 9435.4 | 9361.9 | 9373.9 | 9258.7 | 10048 | 9413.6 | 9951.9 | 9264.2 | 9672 | 10340.6 | 9276.8 | 10053.7 | 8917.1 | 9107.6 | 9627.2 | 9146.6 | 9801.6 | 9106.5 | 9663.5 | 8875.6 | 8745.6 | 9680.8 | 8882.6 | 9727 | 9640.8 | 8840 | 9401.9 | 9067.6 | 9135.2 | 8642.9 | 9073.4 | 9358.2 | 9504.6 | 8782.9 | 9373.1 | 8436.3 | 9257.4 | 9088 | 8676.1 | 9372.5 | 8509 | 9559.2 | 8703.4 | 9449.6 | 8866.7 | 9339.9 | 8947 | 9606.3 | 8889.2 | 9313.1 | 8867.1 | 7860.9 | 9381.3 | 9203.1 | 8688.2 | 9631.9 | 9455.6 | 8964.7 | 8877.8 | 9451.2 | 8720 | 8976.4 | 9496.3 | 8661.7 | 9535.6 | 8644 | 9400.3 | 8840.9 | 9409.8 | 8367.6 | 9446.9 | 8796.6 | 9381.7 | 8753 | 9401.2 | 8911.1 | 8678.3 | 9375.1 | 8833.5 | 8657.1 | 9423.4 | 9494.3 | 9392.2 | 8833.8 | 9450.9 | 8750.9 | 9297.8 | 8825.9 | 9204.6 | 8182.8 | 9355.8 | 8715.4 | 8860.4 | 8859.3 | 8722.2 | 7552.8 | 8692.3 | 7696 | 8564.2 | 8631.3 | 9619.9 | 8776.9 | 9617.5 | 8893.9 | 9507.9 | 8728.5 | 8854.7 | 8728 | 9412.4 | 9581.1 | 9593.5 | 9562.8 | 9589.4 | 9609.6 | 8977.5 | 9553.3 | 9514.3 | 9554.6 | 9601.4 | 9566.4 | 9588.3 | 8926.5 | 9601.8 | 8979.3 | 37.1835 | 36.9518 | 36.9462 | 37.0139 | 37.0992 | 36.9431 | 0 | 47.4 | 0 | 0 | 47.3 | 46.5 | 3.3858 | 3.4596 | 3.4894 | 3.294 | 3.3175 | 2.8204 | 11.162 | 10.631 | 14.883 | 13.011 | 14.086 | 11.897 | 5.2506 | 5.1608 | 5.1886 | 4.9193 | 4.985 | 4.836 | 1.1546 | 1.2405 | 1.1016 | 1.434 | 1.3158 | 1.1304 | 5.4962 | 5.4135 | 5.4022 | 5.2354 | 5.0911 | 5.2084 | 0.29579 | 0.36412 | 0.32334 | 0.32849 | 0.3228 | 0.33925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 603027 | 1090 | 590588 | 1170 | 603956.581 | 1612.467 | 5.2506 | 5.1608 | 5.1886 | 4.9193 | 4.985 | 4.836 | 5.4962 | 5.4135 | 5.4022 | 5.2354 | 5.0911 | 5.2084 | 750000 | 1000 | 724000 | 2000 | 1469201 | 4534 | 1471000 | 1464667 | 12.1333 | 5.0567 | 1.2295 | 5.3078 | 0.32897 | 24.31% | 6.198% | 37.0229 | 47.0667 | 3.2945 | 12.6117 | 1478704.6 | 1468601 | 1739541.9573 | 84.42% | 82 | 41576
2024-04-11 | 2025 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 335090.89 | 6:35 | 19:04 | 10029.1 | 10313.4 | 10255.4 | 10324.3 | 10303.5 | 10316.1 | 10302.2 | 10566.5 | 10293.6 | 10346.7 | 10088 | 10208.6 | 10229.3 | 10148 | 10263.2 | 10281.7 | 10143.2 | 10095.9 | 10106.8 | 10223.4 | 10068 | 10115.9 | 9932.2 | 9989.8 | 9881.7 | 8859.7 | 10011.9 | 9898.1 | 10076 | 10002.8 | 9931.8 | 10050.7 | 10110.5 | 10134.8 | 10191.7 | 10138.1 | 10115.8 | 10013.2 | 10025.3 | 9937.6 | 10498.6 | 9837.7 | 10412.1 | 9701.1 | 10120.7 | 10833.4 | 9631.3 | 10510.3 | 9568.5 | 9770 | 10308.2 | 9807.2 | 10525.7 | 9684.8 | 10412.8 | 9504.2 | 9540.8 | 10614 | 9586 | 10547.1 | 10483.7 | 9566.6 | 10283.3 | 9967.2 | 10110.7 | 9673.8 | 10069.4 | 10507.9 | 10549.4 | 9859.6 | 10431.3 | 9512.6 | 10253.2 | 10133.6 | 9655.4 | 10481.5 | 9541.9 | 10617.9 | 9710.3 | 10552.3 | 9994.1 | 10544.5 | 10014.7 | 10806.9 | 9963 | 10436.7 | 9885.8 | 8827.9 | 10477.8 | 10251.9 | 9635 | 10656.9 | 10317.1 | 9671 | 9514.1 | 10388.7 | 9498 | 9785.5 | 10336.1 | 9419.9 | 10322.5 | 9349.5 | 10141 | 9526.6 | 10150.1 | 9063 | 10188.3 | 9444.9 | 10087.4 | 9411.6 | 10103.2 | 9571.7 | 9463.4 | 10165.3 | 9540.5 | 9396.1 | 10174.2 | 10308.2 | 10123.4 | 9564.3 | 10208.1 | 9441.6 | 9983.2 | 9470.2 | 9907.1 | 8869.5 | 10099.8 | 9485.7 | 9636.3 | 9638.3 | 9517.5 | 8239.4 | 9461.2 | 8371 | 9288 | 9278.2 | 10386.5 | 9471.4 | 10361.2 | 9592.4 | 10235 | 9355.6 | 9488.5 | 9347.5 | 10141.7 | 10328.2 | 10362.1 | 10320.1 | 10324.8 | 10348.5 | 9652.3 | 10291 | 10279.3 | 10286.1 | 10367.5 | 10323 | 10333 | 9597.5 | 10392.7 | 9666.4 | 35.723 | 35.4937 | 35.5778 | 35.5885 | 35.7241 | 35.4916 | 0 | 45.6 | 0 | 0 | 46 | 45.4 | 3.5765 | 3.538 | 3.4374 | 3.5917 | 3.5314 | 3.0666 | 9.595 | 9.391 | 11.341 | 10.024 | 9.049 | 8.582 | 5.622 | 5.5054 | 5.4389 | 5.588 | 5.4735 | 5.2075 | 1.2933 | 1.2882 | 1.2083 | 1.6737 | 1.4434 | 1.1959 | 5.8769 | 5.7018 | 5.642 | 5.8734 | 5.5464 | 5.621 | 0.3306 | 0.38289 | 0.33931 | 0.36327 | 0.34631 | 0.36393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 603832 | 1092 | 591373 | 1171 | 605541.914 | 1616.867 | 5.622 | 5.5054 | 5.4389 | 5.588 | 5.4735 | 5.2075 | 5.8769 | 5.7018 | 5.642 | 5.8734 | 5.5464 | 5.621 | 805000 | 2000 | 785000 | 1000 | 1585333 | 4400 | 1587000 | 1580933 | 12.4833 | 5.4726 | 1.3505 | 5.7102 | 0.35439 | 24.68% | 6.206% | 35.5998 | 45.6667 | 3.4569 | 9.6637 | 1596368.8 | 1584067 | 1880001.1614 | 84.26% | 61 | 87084
2024-04-12 | 2025 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 335090.89 | 6:30 | 19:01 | 10241.3 | 10789.9 | 10836.3 | 10803.6 | 10946.9 | 10965.8 | 10909.9 | 11242.7 | 10732.6 | 10636.3 | 10651.8 | 10757.9 | 10801.1 | 10706.5 | 10851.4 | 10889.7 | 10790 | 10785.2 | 10783.1 | 10837 | 10785.7 | 10790.2 | 10560.9 | 10659.4 | 10457.7 | 9193.3 | 10512.2 | 10449.8 | 10736.4 | 10638.3 | 10517.3 | 10695.8 | 10741.6 | 10756.3 | 10784 | 10736.5 | 10752.5 | 10631.5 | 10669.4 | 10572.5 | 11412 | 10461 | 11319.8 | 10259.4 | 10916.1 | 11798 | 10293.6 | 11431.2 | 9857.4 | 10101.9 | 10805 | 10165.9 | 11103.9 | 10056.6 | 10950.6 | 9846.4 | 9772.3 | 11090.9 | 9872.6 | 11052.7 | 10934.9 | 9826.4 | 10647.2 | 10140.1 | 10370.2 | 9695.3 | 10287.1 | 10703.9 | 10922 | 9909.2 | 10772.8 | 9501.9 | 10507.2 | 10331.5 | 9704 | 10766.1 | 9532.4 | 10883.4 | 9689.3 | 10754 | 10007.4 | 10725.1 | 10095.4 | 11057.6 | 9999.9 | 10624.7 | 9928.5 | 8781.2 | 10743.1 | 10339.5 | 9752.8 | 11122.3 | 10898.9 | 10138.8 | 10030.8 | 10934.9 | 9814 | 10232.1 | 11038.1 | 9790 | 11065.5 | 9789.5 | 10858.9 | 10026.9 | 10919 | 9507.2 | 10982.5 | 9963.5 | 10883.9 | 9974 | 10919.4 | 10125 | 9810.2 | 10783.3 | 9885 | 9702 | 10752.9 | 10869.7 | 10787.3 | 9964.9 | 10889.2 | 9840.5 | 10648.6 | 9940.3 | 10535.1 | 9210.8 | 10699.8 | 9821.7 | 10016.7 | 10024 | 9845.8 | 8532 | 9783.8 | 8633.7 | 9714.7 | 9707.1 | 11124.2 | 9882 | 11171.9 | 10107.8 | 10990.8 | 9863.8 | 10032.4 | 9886.5 | 10850.5 | 11124.8 | 11067.1 | 11008.9 | 11020.4 | 11075.7 | 10183.2 | 11044 | 11013.1 | 11049.7 | 11131.5 | 11096.8 | 11114.7 | 10167.1 | 11117.8 | 10195.9 | 34.346 | 34.117 | 34.3595 | 34.0232 | 34.0809 | 34.2412 | 0 | 45.452 | 0 | 0 | 45.3 | 45.5 | 5.0614 | 5.3576 | 4.8003 | 5.4508 | 5.3417 | 5.1177 | 10.544 | 10.743 | 10.279 | 10.062 | 11.006 | 9.94 | 5.7573 | 5.626 | 5.6468 | 5.6008 | 5.5934 | 5.3558 | 1.3212 | 1.3826 | 1.2403 | 1.645 | 1.4981 | 1.2894 | 6.0315 | 5.9332 | 5.899 | 5.8878 | 5.6984 | 5.7748 | 0.32222 | 0.37611 | 0.33506 | 0.34351 | 0.33611 | 0.35568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 604674 | 1093 | 592198 | 1173 | 607204.714 | 1621.267 | 5.7573 | 5.626 | 5.6468 | 5.6008 | 5.5934 | 5.3558 | 6.0315 | 5.9332 | 5.899 | 5.8878 | 5.6984 | 5.7748 | 842000 | 1000 | 825000 | 2000 | 1662800 | 4400 | 1664000 | 1658400 | 12.5167 | 5.5967 | 1.3961 | 5.8708 | 0.34478 | 24.95% | 5.873% | 34.1946 | 45.4173 | 5.1882 | 10.429 | 1674836.6 | 1661466 | 1956743.8076 | 84.91% | 62 | 19388
2024-04-13 | 2025 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 335090.89 | 6:30 | 19:01 | 10029.7 | 10534 | 10613.9 | 10568.4 | 10698.6 | 10755.1 | 10694.2 | 11046.5 | 10518.6 | 10433.2 | 10418.9 | 10541.5 | 10590 | 10500.9 | 10633.8 | 10686 | 10609.5 | 10636.2 | 10662.1 | 10696.9 | 10698.1 | 10682.3 | 10491.6 | 10583.3 | 10372.4 | 9128.9 | 10378.6 | 10368.6 | 10700.2 | 10604.6 | 10502.9 | 10671.9 | 10700.1 | 10703.1 | 10684.1 | 10647.1 | 10733.1 | 10613.7 | 10678.4 | 10612.1 | 11305.6 | 10288.4 | 11249.4 | 10136.5 | 10801.7 | 11843.3 | 10112.5 | 11309.3 | 9710.7 | 9941.9 | 10638.9 | 10049.7 | 10986.7 | 9881.2 | 10870.4 | 9760.4 | 9663.5 | 11075.4 | 9716.9 | 10977.7 | 10852.2 | 9685.5 | 10600.8 | 10050.1 | 10388.5 | 9768.1 | 10301.5 | 10779.2 | 11006.6 | 9938 | 10853.2 | 9545.7 | 10521.5 | 10347.8 | 9712.6 | 10835.9 | 9552.4 | 10949.6 | 9570.8 | 10770.5 | 8721.1 | 9377.9 | 8774.7 | 9714.5 | 8713.5 | 9260.2 | 8718.3 | 7716.6 | 9515.8 | 9213.2 | 8619.8 | 9876.5 | 9623.7 | 8919.7 | 8843.2 | 9701.8 | 7878.3 | 8109.4 | 8846.4 | 7784.4 | 8903 | 7835 | 8692.7 | 8023.9 | 8769.1 | 7624.7 | 8828.7 | 7984.7 | 8759 | 8025.1 | 8852.3 | 8130 | 8224 | 9080.7 | 8427 | 8245.4 | 9227.4 | 9264.8 | 9183.2 | 8397.8 | 8707.5 | 7869.2 | 8555 | 8017.3 | 8510.7 | 7433.1 | 8561.7 | 7844.3 | 8028.5 | 8038.9 | 7920.3 | 6852.5 | 7903.1 | 6975.1 | 7875.2 | 7870.8 | 9034.7 | 7989.7 | 9051.9 | 8138.8 | 8931.3 | 7947 | 8105.4 | 7956.2 | 8775.1 | 9015.3 | 8991.5 | 8943.6 | 8939.1 | 8972.7 | 8195.4 | 8963 | 9014.9 | 9023.2 | 9023 | 8992.5 | 9007.6 | 8181.7 | 9101.2 | 8250.1 | 34.3784 | 34.2755 | 34.4344 | 34.1149 | 34.1789 | 34.289 | 0 | 46.9 | 0 | 0 | 47.5 | 47.3 | 4.4765 | 4.5664 | 4.5542 | 4.4892 | 4.4121 | 4.4205 | 10.031 | 10.494 | 10.206 | 9.731 | 9.7 | 11.137 | 5.691 | 5.6986 | 5.6593 | 5.6853 | 5.7424 | 5.4948 | 1.2339 | 1.351 | 1.177 | 1.5719 | 1.4634 | 1.2088 | 5.9292 | 5.9245 | 5.8426 | 5.8863 | 5.9455 | 5.8304 | 0.35766 | 0.42447 | 0.36895 | 0.39145 | 0.38725 | 0.3997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 605531 | 1095 | 592897 | 1175 | 608717.914 | 1625.467 | 5.691 | 5.6986 | 5.6593 | 5.6853 | 5.7424 | 5.4948 | 5.9292 | 5.9245 | 5.8426 | 5.8863 | 5.9455 | 5.8304 | 857000 | 2000 | 699000 | 2000 | 1513200 | 4200 | 1552000 | 1509000 | 12.5167 | 5.6619 | 1.3343 | 5.8931 | 0.38825 | 23.57% | 6.588% | 34.2785 | 47.2333 | 4.4865 | 10.2165 | 1522689.3 | 1511601 | 1970116.7933 | 76.73% | 63 | 51668
2024-04-14 | 2025 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 335090.89 | 6:36 | 18:59 | 9949.4 | 10404.4 | 10378 | 10350.7 | 10441.8 | 10470.1 | 10475.4 | 10838.5 | 10423.2 | 10444.9 | 10269.6 | 10422.4 | 10360.4 | 10352.7 | 10400.4 | 10437.2 | 10355.8 | 10364.9 | 10388.1 | 10437.5 | 10414.7 | 10406.3 | 10198.6 | 10290.6 | 10146.9 | 8971.1 | 10178 | 10132.6 | 10419.5 | 10321.9 | 10199 | 10368.9 | 10491.4 | 10493.7 | 10572 | 10489.1 | 10469 | 10348.6 | 10386.9 | 10300.3 | 11023.5 | 9990.9 | 10900.1 | 9827.3 | 10497.8 | 11583 | 9846.1 | 11040.4 | 9609.9 | 9837.8 | 10485.4 | 9918.1 | 10797.2 | 9729.8 | 10739.8 | 9635.9 | 9602.8 | 10930.5 | 9630.3 | 10877.8 | 10777.2 | 9613.2 | 10551.7 | 10032.9 | 10168.9 | 9567.7 | 10138.7 | 10530.1 | 10818.3 | 9763.9 | 10653.8 | 9396.6 | 10399.3 | 10211 | 9627.1 | 10691.9 | 9479.9 | 10836.2 | 9470.5 | 10685.9 | 9727.1 | 10535 | 9924.9 | 10863.6 | 9801.3 | 10412.7 | 9769.4 | 8642.2 | 10564.5 | 9877.6 | 9537.4 | 10932 | 10620.6 | 9854.4 | 9749.9 | 10711.7 | 9691.8 | 10005.2 | 10817.2 | 9573.9 | 10933.8 | 9569.5 | 10664.2 | 9823.1 | 10732.4 | 9318.9 | 10792.6 | 9755.3 | 10647.5 | 9739 | 10701 | 9878.8 | 9612.8 | 10596.3 | 9717.8 | 9509.5 | 10659.9 | 10731 | 10612.1 | 9714.3 | 10692.8 | 9593.1 | 10437.7 | 9723.5 | 10321.9 | 8997.6 | 10444.9 | 9595.4 | 9764.3 | 9819.9 | 9623.5 | 8344.2 | 9634.1 | 8551.8 | 9634.2 | 9647.3 | 10996.9 | 9714.5 | 11035 | 9915.7 | 10938.5 | 9782.2 | 9940.8 | 9788.9 | 10706.1 | 11042.8 | 10953.2 | 10915.7 | 10924.4 | 10951.2 | 10019.8 | 10958.3 | 11012.7 | 11025.8 | 11073 | 11031.1 | 11051.3 | 10006.5 | 11075.3 | 10046.1 | 28.5943 | 28.3383 | 28.212 | 28.4161 | 28.6855 | 28.6002 | 0 | 40.1 | 0 | 0 | 40.6 | 40.7 | 3.2947 | 3.3545 | 3.2447 | 3.3879 | 3.4364 | 3.3666 | 7.469 | 7.357 | 7.39 | 7.69 | 7.926 | 7.484 | 5.4489 | 5.4879 | 5.481 | 5.4396 | 5.4779 | 5.4781 | 1.0749 | 1.0297 | 0.94633 | 1.306 | 1.1649 | 0.9793 | 5.5499 | 5.5874 | 5.5286 | 5.5685 | 5.5615 | 5.4978 | 0.30909 | 0.35771 | 0.29075 | 0.33807 | 0.32813 | 0.3495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 606362 | 1098 | 593613 | 1175 | 610346.448 | 1628.867 | 5.4489 | 5.4879 | 5.481 | 5.4396 | 5.4779 | 5.4781 | 5.5499 | 5.5874 | 5.5286 | 5.5685 | 5.5615 | 5.4978 | 831000 | 3000 | 716000 | 0 | 1628534 | 3400 | 1544000 | 1625134 | 12.3833 | 5.4689 | 1.0835 | 5.5489 | 0.32887 | 19.81% | 5.927% | 28.4744 | 40.4667 | 3.3475 | 7.5527 | 1638537.9 | 1627933 | 1889518.0942 | 86.16% | 83 | 21383
2024-04-15 | 2025 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 335090.89 | 6:32 | 19:01 | 7851.2 | 8234.5 | 8200.7 | 8165.9 | 8255.8 | 8276.1 | 8299.1 | 8624.4 | 8242.5 | 8278.5 | 8119.1 | 8245.7 | 8192.2 | 8189.3 | 8222 | 8252.9 | 8179.8 | 8173.9 | 8202.9 | 8240.3 | 8221.6 | 8212.6 | 8037.6 | 8115.8 | 8003.1 | 7063.1 | 8032.2 | 7993.9 | 8246.6 | 8159.5 | 8056.7 | 8226.5 | 8246.7 | 8251.2 | 8291.3 | 8224.2 | 8274.5 | 8168.3 | 8206.6 | 8154.6 | 8764.4 | 7871.9 | 8667.5 | 7742.9 | 8300.1 | 9283.6 | 7743.6 | 8788.8 | 7576.5 | 7767 | 8294.2 | 7825 | 8580.9 | 7679.3 | 8521.8 | 7609.9 | 7577.2 | 8701.2 | 7594.4 | 8636.4 | 8544.4 | 7579 | 8347 | 7919.9 | 8063.9 | 7585.4 | 8017.2 | 8347.7 | 8621 | 7714.8 | 8471 | 7430.1 | 8256.2 | 8089.7 | 7613.2 | 8493.2 | 7484.8 | 8631.3 | 7614.6 | 8480.7 | 7715 | 8345 | 7844 | 8635.6 | 7743 | 8250.9 | 7723.1 | 6830.8 | 8437.8 | 8079.2 | 7533.7 | 8705.1 | 8427.3 | 7795.9 | 7724 | 8512.5 | 7648.9 | 7899.3 | 8598.2 | 7556.8 | 8650.9 | 7545.9 | 8413.8 | 7747.9 | 8484.7 | 7353.9 | 8528.7 | 7685.4 | 8408.1 | 7679.9 | 8451.5 | 7788.9 | 7609.5 | 8393.2 | 7711.6 | 7554.2 | 8476.2 | 8531.6 | 8390.8 | 7704.6 | 8480.4 | 7606.5 | 8237.2 | 7675 | 8150.8 | 7146.4 | 8272.9 | 7613.1 | 7762.3 | 7803.8 | 7653.3 | 6643.2 | 7660.3 | 6798.4 | 7731.9 | 7735.4 | 8878.3 | 7751.7 | 8920.5 | 7918 | 8830.7 | 7822 | 7959.9 | 7850.9 | 8601.1 | 8920.3 | 8809.5 | 8781.9 | 8780.6 | 8821.8 | 8001.2 | 8836 | 8861.3 | 8890 | 8960.9 | 8930.4 | 8932 | 8013.5 | 8898.5 | 8018.3 | 29.8929 | 29.7963 | 29.5688 | 29.7758 | 29.8382 | 30.0161 | 0 | 37.9 | 0 | 0 | 38.2 | 38.1 | 4.448 | 4.4554 | 4.4924 | 4.3825 | 4.3878 | 4.4344 | 8.587 | 8.46 | 8.786 | 8.164 | 8.169 | 9.062 | 4.2185 | 4.2403 | 4.2437 | 4.2258 | 4.275 | 4.2676 | 0.84566 | 0.86016 | 0.74222 | 1.014 | 0.93813 | 0.82379 | 4.2393 | 4.2668 | 4.1889 | 4.2413 | 4.2615 | 4.2539 | 0.26555 | 0.30437 | 0.25266 | 0.29299 | 0.28788 | 0.29957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 607002 | 1099 | 594321 | 1176 | 611640.581 | 1633.333 | 4.2185 | 4.2403 | 4.2437 | 4.2258 | 4.275 | 4.2676 | 4.2393 | 4.2668 | 4.1889 | 4.2413 | 4.2615 | 4.2539 | 640000 | 1000 | 708000 | 1000 | 1294133 | 4466 | 1346000 | 1289667 | 12.4833 | 4.2452 | 0.87067 | 4.242 | 0.28384 | 20.51% | 6.691% | 29.8147 | 38.0667 | 4.4334 | 8.538 | 1300542.7 | 1292133 | 1460338.2848 | 88.48% | 91 | 40775
2024-04-16 | 2025 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 335090.89 | 6:35 | 19:08 | 11850.8 | 12299.3 | 12229.3 | 12177.7 | 12295.3 | 12345.5 | 12386.1 | 12720.2 | 12307.8 | 12357.6 | 12202.6 | 12341.9 | 12314.1 | 12281.6 | 12336 | 12379 | 12274.8 | 12294.5 | 12327.6 | 12403.3 | 12341.4 | 12354.8 | 12145 | 12238.3 | 12114.2 | 10854.8 | 12140.5 | 12092.3 | 12374.5 | 12265.8 | 12161.8 | 12347.8 | 12605.8 | 12616.4 | 12666.7 | 12585.5 | 12440.1 | 12316.4 | 12337 | 12264.9 | 12946.9 | 12024.7 | 12840.8 | 11841.9 | 12491.3 | 13450.7 | 11839.7 | 12946.4 | 11571.4 | 11820.7 | 12455.1 | 11891.7 | 12693.7 | 11644.3 | 12676 | 11588.2 | 11540.7 | 12846.3 | 11586.8 | 12810.6 | 12712.3 | 11552.6 | 12481.5 | 12011 | 12123.8 | 11534.2 | 12103.3 | 12475.4 | 12737.2 | 11732.5 | 12630.2 | 11364.9 | 12336.3 | 12225.2 | 11593.8 | 12633.3 | 11440.8 | 12772.1 | 11597.8 | 12618 | 11789.4 | 12519 | 11905.5 | 12815 | 11785.4 | 12384.5 | 11719.4 | 10455.2 | 12556.2 | 12133.1 | 11517.2 | 12867.5 | 12564.8 | 11825.5 | 11695.5 | 12635.5 | 11644.4 | 11970.8 | 12757.4 | 11531.2 | 12809.7 | 11538.9 | 12583.1 | 11795.3 | 12600.4 | 11238 | 12682 | 11705.6 | 12556.6 | 11686.4 | 12602.1 | 11861.5 | 11574.9 | 12520.7 | 11735.2 | 11522.9 | 12585.7 | 12691 | 12511.5 | 11733.8 | 12621.4 | 11610.6 | 12368.3 | 11707.5 | 12255.2 | 10920.6 | 12419.8 | 11626.5 | 11820.9 | 11853.9 | 11671.3 | 10158.4 | 11650.1 | 10411.6 | 11705.9 | 11734 | 13036.7 | 11818.9 | 13087.4 | 12026.4 | 13004.2 | 11889.5 | 12057 | 11889 | 12800.4 | 13091.2 | 13060.9 | 12984.3 | 12991.3 | 13011.6 | 12132.4 | 13022.5 | 13027.1 | 13042.8 | 13086.1 | 13059.2 | 13077.6 | 12116.3 | 13112.9 | 12141.7 | 33.1187 | 32.9592 | 32.8937 | 32.9516 | 33.1155 | 33.0458 | 0 | 45.4 | 0 | 0 | 46 | 45.6 | 3.455 | 3.3507 | 3.2871 | 3.435 | 3.4196 | 3.2653 | 6.287 | 6.173 | 6.673 | 6.177 | 6.854 | 6.201 | 6.8 | 6.8359 | 6.8781 | 6.8018 | 6.8915 | 6.9072 | 1.3828 | 1.5171 | 1.2251 | 1.6507 | 1.6158 | 1.4716 | 7.0172 | 7.0743 | 6.9948 | 7.0066 | 7.0597 | 7.0542 | 0.39631 | 0.44964 | 0.38076 | 0.41431 | 0.40174 | 0.4314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 607978 | 1101 | 595292 | 1177 | 613580.448 | 1637.8 | 6.8 | 6.8359 | 6.8781 | 6.8018 | 6.8915 | 6.9072 | 7.0172 | 7.0743 | 6.9948 | 7.0066 | 7.0597 | 7.0542 | 976000 | 2000 | 971000 | 1000 | 1939867 | 4467 | 1944000 | 1935400 | 12.55 | 6.8524 | 1.4772 | 7.0345 | 0.41236 | 21.56% | 5.862% | 33.0141 | 45.6667 | 3.3688 | 6.3942 | 1954284.3 | 1939067 | 2325785.7864 | 83.37% | 76 | 4881
2024-04-17 | 2025 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 335090.89 | 6:32 | 19:04 | 9059.8 | 9508.5 | 9486.7 | 9457.8 | 9543.7 | 9582.5 | 9599.5 | 9990.3 | 9530 | 9564.4 | 9367.2 | 9521.5 | 9477 | 9456 | 9531 | 9568.7 | 9485.4 | 9492.5 | 9514.9 | 9546.3 | 9547.3 | 9521.8 | 9306.3 | 9411.6 | 9255.9 | 8103.7 | 9286.4 | 9244.2 | 9559.4 | 9450.8 | 9308.5 | 9525.5 | 9501.8 | 9522.9 | 9573.1 | 9483.6 | 9585.5 | 9451.3 | 9497.4 | 9426.1 | 10296.1 | 9185.5 | 10151.8 | 9013.6 | 9644.6 | 10865.4 | 8994.7 | 10318.8 | 8706.9 | 8932.9 | 9582.3 | 9017.5 | 9828.7 | 8752.1 | 9867.7 | 8739 | 8699.3 | 10072.1 | 8721.7 | 10006.9 | 9894.6 | 8712.4 | 9636.4 | 9105 | 9253.7 | 8665 | 9217.7 | 9642.1 | 9966.9 | 8860.7 | 9775.1 | 8503.1 | 9507 | 9299.6 | 8727.6 | 9820.8 | 8576.5 | 9982.5 | 8722.2 | 9803.3 | 8896.9 | 9655.1 | 9005.5 | 10020.1 | 8889.7 | 9511.9 | 8873.4 | 7809.3 | 9710.8 | 9301 | 8630.1 | 10066.4 | 9722.8 | 8932.1 | 8831.9 | 9822.2 | 8744.4 | 9060.7 | 9947.3 | 8635.8 | 9999.3 | 8635.1 | 9699.1 | 8861.3 | 9797.1 | 8401.8 | 9845.8 | 8800.2 | 9693 | 8790.5 | 9735.3 | 8908.1 | 8688.8 | 9643.4 | 8808.4 | 8607.3 | 9754.8 | 9830.8 | 9648.2 | 8813.1 | 9771 | 8685.5 | 9468.9 | 8771.3 | 9332 | 8121.9 | 9499.3 | 8696.8 | 8857.4 | 8894 | 8728.7 | 7541.5 | 8704.5 | 7713.2 | 8730.2 | 8749.9 | 10222.6 | 8819.1 | 10270.8 | 9023.6 | 10140.3 | 8884.5 | 9037.9 | 8889.4 | 9842.4 | 10254.9 | 10140.7 | 10096.2 | 10105.1 | 10146.6 | 9122.7 | 10146 | 10180.7 | 10212.7 | 10260 | 10214.1 | 10250.4 | 9092.9 | 10247.6 | 9124.4 | 33.2758 | 33.1203 | 33.0003 | 32.8688 | 33.0129 | 33.1002 | 0 | 44.1 | 0 | 0 | 44.6 | 44.2 | 2.3417 | 2.2664 | 2.1182 | 2.3371 | 2.3494 | 2.2419 | 4.824 | 5.096 | 5.005 | 5.252 | 4.622 | 4.493 | 4.9676 | 4.9869 | 5.0253 | 4.949 | 4.9714 | 4.9747 | 1.0553 | 1.0497 | 0.93824 | 1.2597 | 1.1328 | 0.99033 | 4.9861 | 5.0091 | 4.9805 | 4.9824 | 4.957 | 4.9027 | 0.33811 | 0.38725 | 0.32977 | 0.374 | 0.35516 | 0.37009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 608730 | 1103 | 596035 | 1179 | 615071.448 | 1642.333 | 4.9676 | 4.9869 | 5.0253 | 4.949 | 4.9714 | 4.9747 | 4.9861 | 5.0091 | 4.9805 | 4.9824 | 4.957 | 4.9027 | 752000 | 2000 | 743000 | 2000 | 1491000 | 4533 | 1491000 | 1486467 | 12.5333 | 4.9791 | 1.071 | 4.9696 | 0.35907 | 21.51% | 7.225% | 33.0631 | 44.3 | 2.2758 | 4.882 | 1496937.1 | 1489334 | 1681076.2329 | 88.59% | 63 | 10944
2024-04-18 | 2025 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 335090.89 | 6:29 | 19:03 | 5758.7 | 6025.5 | 5989.5 | 5969.1 | 6031.5 | 6054.3 | 6074.6 | 6336.1 | 6058.2 | 6099.2 | 5955.1 | 6053.5 | 6016.2 | 6005.3 | 6042.8 | 6067.9 | 6006.2 | 6013.5 | 6037.2 | 6061.8 | 6059.8 | 6048.1 | 5936.2 | 5986.6 | 5909.3 | 5197.8 | 5915.3 | 5891.6 | 6087.2 | 6032.9 | 5956 | 6074.7 | 6116.1 | 6119.8 | 6135.4 | 6085.5 | 6134.5 | 6051.5 | 6088.2 | 6072 | 6511.4 | 5843.7 | 6440.3 | 5748.2 | 6168.3 | 6905.6 | 5727.7 | 6525.7 | 5579.7 | 5733.5 | 6107.3 | 5791.3 | 6313.9 | 5638.6 | 6329 | 5639.2 | 5622.2 | 6466.2 | 5603 | 6410 | 6335.7 | 5598.1 | 6168.1 | 5843 | 6009.3 | 5674.2 | 5976.6 | 6261.6 | 6423.2 | 5773.8 | 6318.4 | 5551.5 | 6145.8 | 6039.2 | 5654.3 | 6343.5 | 5571.8 | 6413.9 | 5649.4 | 6312 | 5789.1 | 6250.9 | 5856 | 6476.2 | 5792 | 6184.3 | 5781.5 | 5123.4 | 6272.3 | 5604.6 | 5647.1 | 6530.7 | 6317.8 | 5828 | 5769.9 | 6391.1 | 5741.7 | 5934 | 6474.8 | 5675.5 | 6508.8 | 5671.3 | 6340 | 5822.6 | 6394.1 | 5533.1 | 6426.2 | 5784.2 | 6335 | 5781.5 | 6369.1 | 5868.1 | 5714.2 | 6309 | 5509.8 | 5485.8 | 6042.1 | 6206.3 | 6317.2 | 5813.5 | 6390.8 | 5724.2 | 6200.7 | 5774 | 6108 | 5365 | 6233.7 | 5737.5 | 5858.9 | 5885.2 | 5768.8 | 5011.3 | 5792.5 | 5154.1 | 5891 | 5901.4 | 6771 | 5897.9 | 6813.8 | 6029.4 | 6729.9 | 5954.4 | 6056.5 | 5980.4 | 6546.8 | 6794.9 | 6714.6 | 6691.9 | 6688.3 | 6722.5 | 6098.8 | 6733.4 | 6727.4 | 6748.5 | 6803.5 | 6777.2 | 6785.7 | 6072.3 | 6777.5 | 6092 | 31.2671 | 31.16 | 31.0426 | 31.1071 | 31.153 | 31.4107 | 0 | 35.8 | 0 | 0 | 36.1 | 36.2 | 5.2809 | 5.3803 | 5.3287 | 5.352 | 5.4309 | 5.3145 | 12.387 | 12.957 | 12.725 | 12.065 | 12.327 | 12.128 | 3.1263 | 3.1619 | 3.1818 | 3.1798 | 3.2267 | 3.304 | 0.64416 | 0.65172 | 0.57744 | 0.78846 | 0.71288 | 0.64715 | 3.1041 | 3.1462 | 3.1089 | 3.1614 | 3.1793 | 3.2407 | 0.19907 | 0.22824 | 0.19328 | 0.22472 | 0.21803 | 0.22765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 609211 | 1104 | 596523 | 1180 | 616037.981 | 1646.733 | 3.1263 | 3.1619 | 3.1818 | 3.1798 | 3.2267 | 3.304 | 3.1041 | 3.1462 | 3.1089 | 3.1614 | 3.1793 | 3.2407 | 481000 | 1000 | 488000 | 1000 | 966533 | 4400 | 967000 | 962133 | 12.5667 | 3.1967 | 0.6703 | 3.1568 | 0.21517 | 20.97% | 6.816% | 31.1901 | 36.0333 | 5.3479 | 12.4315 | 970201.4 | 965800 | 1096862.6766 | 88.05% | 90 | 107210
2024-04-19 | 2025 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 335090.89 | 6:32 | 19:11 | 11128.8 | 11465.3 | 11427.5 | 11416 | 11507.6 | 11520.6 | 11509.6 | 11766.5 | 11452.5 | 11471.5 | 11346.7 | 11458.3 | 11460.7 | 11392.6 | 11513.4 | 11515.1 | 11434.7 | 11449.1 | 11446.6 | 11530.9 | 11460.2 | 11478.4 | 11348.7 | 11393.6 | 11280.4 | 10540.3 | 11303.4 | 11272.1 | 11471.9 | 11394.4 | 11323.8 | 11434.7 | 12977.7 | 12982 | 13063.5 | 13005.8 | 11506.2 | 11416.5 | 11433 | 11392.7 | 11966 | 11314 | 11848.6 | 11202.3 | 11612 | 12339.8 | 11120.2 | 11939.6 | 10989.2 | 11151.2 | 11548.7 | 11184.1 | 11706.1 | 11000.4 | 11720.5 | 11024.6 | 10986.2 | 11852 | 11050.2 | 11825.3 | 11739.4 | 10983.4 | 11569 | 11222.4 | 11323.4 | 10946.6 | 11296.2 | 11533.7 | 11731.7 | 11032.2 | 11623.4 | 10840.6 | 11445.1 | 11345.5 | 10960.4 | 11618.7 | 10872.8 | 11750.6 | 10969.4 | 11624.1 | 11059.9 | 11528.6 | 11119.1 | 11773.1 | 11052.4 | 11455 | 10982.9 | 10342.8 | 11572.8 | 11294.3 | 10914.4 | 11834 | 11614.1 | 11134.2 | 11052.8 | 11650.9 | 10986 | 11198.6 | 11739.8 | 10907.9 | 11771.2 | 10917.5 | 11629.3 | 11113.4 | 11615 | 10753.3 | 11688.2 | 11023.9 | 11616.9 | 11024.7 | 11643.5 | 11171.9 | 10930.9 | 11558.1 | 11035.3 | 10930.3 | 11609.9 | 11683.2 | 11560.4 | 11042 | 11627.5 | 10965.2 | 11457.4 | 11037.6 | 11400 | 10660.5 | 11508.2 | 11006.7 | 11099.3 | 11090.6 | 10992 | 10162.3 | 10972.8 | 10283.7 | 11010.9 | 11009.1 | 11896 | 11020.3 | 11933.1 | 11167.1 | 11848.9 | 11053.8 | 11169.8 | 11080 | 11717.2 | 11927.8 | 11917.2 | 11862.5 | 11867.2 | 11881.3 | 11240.3 | 11883.7 | 11911.8 | 11911.6 | 11940.8 | 11924.2 | 11952 | 11250 | 11987.7 | 11282.9 | 32.1908 | 31.7442 | 31.7278 | 31.8245 | 31.6778 | 32.0328 | 0 | 43.2 | 0 | 0 | 43.1 | 43.1 | 8.4467 | 8.4939 | 8.5388 | 8.5038 | 8.445 | 8.3362 | 13.547 | 13.297 | 13.294 | 13.278 | 13.683 | 14.851 | 7.0915 | 7.1484 | 7.1294 | 7.0714 | 7.1584 | 7.1896 | 1.5554 | 1.5888 | 1.3952 | 1.8381 | 1.7169 | 1.5041 | 7.3069 | 7.3615 | 7.2304 | 7.2748 | 7.298 | 7.2478 | 0.43398 | 0.49329 | 0.42677 | 0.45405 | 0.44621 | 0.47682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 610126 | 1106 | 597427 | 1181 | 617851.715 | 1651 | 7.0915 | 7.1484 | 7.1294 | 7.0714 | 7.1584 | 7.1896 | 7.3069 | 7.3615 | 7.2304 | 7.2748 | 7.298 | 7.2478 | 915000 | 2000 | 904000 | 1000 | 1813734 | 4267 | 1816000 | 1809467 | 12.65 | 7.1314 | 1.5997 | 7.2866 | 0.45519 | 22.43% | 6.247% | 31.8663 | 43.1333 | 8.4607 | 13.6583 | 1825946.4 | 866866 | 1026510.8371 | 84.45% | 63 | 201
2024-04-20 | 2025 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 335090.89 | 6:25 | 19:08 | 11362.2 | 11721.3 | 11583 | 11563.3 | 11625.8 | 11643.2 | 11692.8 | 11938.9 | 11728.2 | 11874.4 | 11349.4 | 11562 | 11438.2 | 11388.8 | 11442.6 | 11523.5 | 11394.7 | 11443.3 | 11403.5 | 11493 | 11473.9 | 11435.1 | 11315.8 | 11317.3 | 10940 | 9758.3 | 11138.1 | 10996.5 | 11354.4 | 11427.2 | 11225.6 | 11351.4 | 11480.4 | 11484.5 | 11243.9 | 11264.5 | 11464.4 | 11334.7 | 11377 | 11304.5 | 12376.7 | 11256.5 | 12118.9 | 10975 | 11550.1 | 12683.8 | 11063.5 | 12403.2 | 10610.3 | 10855.1 | 11542.3 | 10903.4 | 11878.6 | 10818.8 | 11698.8 | 10519.7 | 10540.1 | 11926.3 | 10677.3 | 11848.5 | 11712.2 | 10623.8 | 11417 | 10991.7 | 11222.1 | 10660.5 | 11181.5 | 11695.8 | 11824.1 | 10853.7 | 11710.4 | 10463 | 11315.1 | 11273.1 | 10532.1 | 11701.1 | 10494.1 | 11795.7 | 10721.5 | 11861.1 | 10885.3 | 11691 | 10979.6 | 12030.6 | 10851.2 | 11480.3 | 10823.3 | 9629.7 | 11717.5 | 11319.5 | 10574.1 | 12011.2 | 11710.1 | 10907.8 | 10795.3 | 11798.7 | 10740 | 11136.7 | 11971.2 | 10581.5 | 11879 | 10539.6 | 11579.2 | 10737.6 | 11597.7 | 10176.4 | 11659.9 | 10544.4 | 11463 | 10471.4 | 11416.9 | 10605.9 | 10664.6 | 11714.1 | 10683.1 | 10534.9 | 11628 | 11892.1 | 11561 | 10836.7 | 11742.9 | 10626.3 | 11280 | 10535.9 | 11173.4 | 9964.6 | 11487 | 10678.2 | 10935.8 | 10990.1 | 10729.2 | 9349.4 | 10830.6 | 9703.7 | 10914.2 | 10982.6 | 12613 | 11308.5 | 12639.2 | 11500.4 | 12540.5 | 11283.3 | 11440.4 | 11193.1 | 12313.3 | 12614.5 | 12572.8 | 12496.7 | 12431.2 | 12460 | 11555.5 | 12489.7 | 12475.8 | 12527.4 | 12631.6 | 12596.9 | 12610.1 | 11568.8 | 12650.5 | 11646.5 | 30.5082 | 30.2836 | 30.3131 | 30.2549 | 30.3794 | 30.4073 | 0 | 44.6 | 0 | 0 | 45.2 | 46 | 2.7775 | 2.7312 | 2.607 | 2.7837 | 2.7586 | 2.604 | 6.671 | 6.175 | 5.892 | 6.724 | 6.726 | 6.553 | 6.3836 | 6.2423 | 6.3728 | 6.3167 | 6.3204 | 6.6799 | 1.3868 | 1.361 | 1.2551 | 1.65 | 1.5049 | 1.3845 | 6.4867 | 6.36 | 6.389 | 6.4377 | 6.3818 | 6.6718 | 0.40694 | 0.44904 | 0.40436 | 0.43084 | 0.41507 | 0.45751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 611031 | 1108 | 598334 | 1183 | 619657.782 | 1655.467 | 6.3836 | 6.2423 | 6.3728 | 6.3167 | 6.3204 | 6.6799 | 6.4867 | 6.36 | 6.389 | 6.4377 | 6.3818 | 6.6718 | 905000 | 2000 | 907000 | 2000 | 1806067 | 4467 | 1808000 | 1801600 | 12.7167 | 6.386 | 1.4237 | 6.4545 | 0.4273 | 22.29% | 6.62% | 30.3577 | 45.2667 | 2.7103 | 6.4568 | 1818059.8 | 1805133 | 2168402.9201 | 83.25% | 82 | 15556
2024-04-21 | 2025 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 335090.89 | 6:24 | 19:14 | 11688.1 | 12197.7 | 12238.4 | 12197 | 12301.6 | 12358.1 | 12361.8 | 12660.9 | 12164.7 | 11857.3 | 11952.9 | 12121.7 | 12223.6 | 11990.7 | 12310.7 | 12306.9 | 12285.6 | 12333.8 | 12234.8 | 12258.9 | 12313.7 | 12282.7 | 12176.3 | 12208.9 | 11958.9 | 10749.3 | 11958.1 | 11977.7 | 12241.1 | 12235.1 | 12108.8 | 12165.8 | 12082.7 | 12129.5 | 12247.6 | 12184.8 | 12244.3 | 12163 | 12202.4 | 11992.3 | 12374 | 11418.1 | 12165.6 | 11223.8 | 11685.9 | 12718.9 | 11261.4 | 12478.3 | 11315.7 | 11506.2 | 12249.7 | 11692.3 | 12522 | 11573.5 | 12444.8 | 11439.3 | 11171.5 | 12397.1 | 11338 | 12417.2 | 12326.9 | 11350.9 | 11943.2 | 11394.7 | 11342.8 | 10696.9 | 11347.5 | 11622.2 | 12020.3 | 10952.6 | 11730.8 | 10556.8 | 11628.2 | 11288 | 10855.7 | 11699.7 | 10638.5 | 11917.9 | 10838.5 | 11697 | 10885.1 | 11585.9 | 10792.2 | 11863.7 | 10774.1 | 11235.9 | 10880.9 | 9615.8 | 11602.5 | 11254.8 | 10816.6 | 12079.8 | 11927.3 | 11268.3 | 11145.3 | 11878.4 | 10754.9 | 11032.1 | 11724.6 | 10570.1 | 11736.9 | 10613.1 | 11492.4 | 10798.9 | 11419.3 | 10261.7 | 11446.4 | 10556.3 | 11296.3 | 10479.2 | 11281.9 | 10581 | 10534.1 | 11255.6 | 10638 | 10406.7 | 11295.4 | 11300.6 | 11196 | 10522.1 | 11174.7 | 10367.3 | 11063.6 | 10472.9 | 10865.9 | 9734.6 | 11044.8 | 10340.8 | 10630.9 | 10607.8 | 10393.3 | 9154.7 | 10448.9 | 9303.4 | 10347.4 | 10348.3 | 11670.4 | 10664.2 | 11743.7 | 10825.5 | 11624.3 | 10589.7 | 10678.2 | 10522.3 | 11550 | 11796.6 | 11742.2 | 11705.5 | 11610 | 11637.3 | 10925.1 | 11756.5 | 11714.1 | 11708.7 | 11919.8 | 11805.2 | 11665.6 | 10768.9 | 11756 | 10854.1 | 32.7971 | 32.5357 | 32.4308 | 32.3897 | 32.4426 | 32.4603 | 0 | 47.6 | 0 | 0 | 46.5 | 46.4 | 2.409 | 2.5848 | 2.4772 | 2.5471 | 2.4199 | 2.2822 | 6.016 | 5.953 | 6.975 | 6.269 | 5.957 | 5.952 | 6.8985 | 6.9474 | 6.5828 | 6.6138 | 6.3362 | 6.4168 | 1.4664 | 1.5838 | 1.2618 | 1.7027 | 1.5237 | 1.3669 | 7.0401 | 7.1147 | 6.6259 | 6.7309 | 6.4163 | 6.447 | 0.41746 | 0.47849 | 0.39988 | 0.4311 | 0.39546 | 0.42197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 611979 | 1110 | 599213 | 1184 | 621478.449 | 1659.933 | 6.8985 | 6.9474 | 6.5828 | 6.6138 | 6.3362 | 6.4168 | 7.0401 | 7.1147 | 6.6259 | 6.7309 | 6.4163 | 6.447 | 948000 | 2000 | 879000 | 1000 | 1820667 | 4466 | 1824000 | 1816201 | 12.8333 | 6.6326 | 1.4842 | 6.7292 | 0.42406 | 22.38% | 6.302% | 32.5094 | 46.8333 | 2.4534 | 6.187 | 1833244 | 1819333 | 2233458.0962 | 81.46% | 90 | 12343
2024-04-22 | 2025 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 335090.89 | 6:23 | 19:13 | 11948.7 | 12384.7 | 12342.8 | 12349 | 12408.4 | 12430.8 | 12470.7 | 12754.6 | 12363 | 12346.7 | 12177.9 | 12324.9 | 12294.7 | 12193.2 | 12338.9 | 12366.1 | 12247.7 | 12234.2 | 12233.3 | 12313.2 | 12204.8 | 12238.6 | 11999.2 | 12085.8 | 11999 | 10836.7 | 12020 | 11982.1 | 12199.3 | 12090.2 | 11999.2 | 12203 | 12395.6 | 12433.7 | 12469.6 | 12388.9 | 12293.1 | 12131.7 | 12121.2 | 12071.9 | 12369.4 | 11414 | 12148.2 | 11140.4 | 11730.8 | 12727.8 | 11356.8 | 12525 | 11580 | 11833.8 | 12330.8 | 11895.7 | 12568.6 | 11675.2 | 12627.8 | 11608.6 | 11615.7 | 12829.9 | 11671.8 | 12732.1 | 12612.2 | 11611.9 | 12409.7 | 12005.9 | 12324.6 | 11901 | 12433.9 | 12899.1 | 12912.6 | 12257.1 | 12919.2 | 11902.8 | 12482.6 | 12612.3 | 11845.1 | 12941.8 | 11835.7 | 12864.3 | 11869.2 | 12827 | 12365.5 | 12998.3 | 12405.5 | 13222.8 | 12288.1 | 12786.2 | 12235.6 | 10976.3 | 12759.9 | 12577.3 | 11835.3 | 13033.9 | 12660.9 | 11934.9 | 11777.8 | 12627.7 | 11645.1 | 12045.3 | 12759 | 11622.6 | 12692 | 11588.9 | 12552.3 | 11812.1 | 12588 | 11273.3 | 12681 | 11737.8 | 12585.8 | 11741.2 | 12639.3 | 11944.9 | 11677 | 12533.7 | 11822.7 | 11617.9 | 12591.2 | 12713.8 | 12563.6 | 11889 | 12722.3 | 11825.8 | 12439.8 | 11826.6 | 12367.6 | 11274.6 | 12641.9 | 11939.2 | 11998.8 | 11976.4 | 11973.2 | 10362.4 | 11747.6 | 10538.1 | 11928 | 11942.3 | 13242.1 | 12108.8 | 13162.2 | 12211.3 | 13075.6 | 12058.2 | 12203 | 12129.7 | 13142.3 | 13307.9 | 13318.6 | 13188.8 | 13167.8 | 13182.7 | 12294.8 | 13110.5 | 13450.8 | 13466.6 | 13620.4 | 13565.1 | 13478.6 | 12553.7 | 13521.3 | 12630.1 | 34.3765 | 34.0597 | 34.0341 | 34.1615 | 34.2619 | 34.1959 | 0 | 47.5 | 0 | 0 | 47.5 | 47.6 | 2.7989 | 2.7053 | 2.6593 | 2.795 | 2.7912 | 2.7285 | 5.808 | 6.127 | 6.373 | 6.719 | 7.35 | 6.814 | 6.9878 | 6.9964 | 6.5655 | 7.2525 | 7.1105 | 7.271 | 1.5535 | 1.5981 | 1.2984 | 1.9104 | 1.7306 | 1.5703 | 6.8022 | 7.1447 | 6.5738 | 7.3942 | 7.1776 | 7.286 | 0.44344 | 0.49848 | 0.41874 | 0.47927 | 0.45279 | 0.494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 612952 | 1111 | 600200 | 1185 | 623431.515 | 1664.4 | 6.9878 | 6.9964 | 6.5655 | 7.2525 | 7.1105 | 7.271 | 6.8022 | 7.1447 | 6.5738 | 7.3942 | 7.1776 | 7.286 | 973000 | 1000 | 987000 | 1000 | 1953066 | 4467 | 1958000 | 1948599 | 12.8333 | 7.0306 | 1.6102 | 7.0631 | 0.46445 | 22.9% | 6.576% | 34.1816 | 47.5333 | 2.7463 | 6.5318 | 1967036.5 | 1952200 | 2331177.3755 | 83.74% | 74 | 2151
2024-04-23 | 2025 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 335090.89 | 6:23 | 19:13 | 12693.3 | 13137.8 | 13053.3 | 13041.4 | 13121 | 13195.2 | 13207.1 | 13533.7 | 13136.4 | 13114.6 | 12994.6 | 13119.2 | 13136.5 | 13057.4 | 13160 | 13200.2 | 13083 | 13097.3 | 13112.7 | 13194.1 | 13116.2 | 13140.7 | 12923.5 | 13013.6 | 12854.5 | 11547.7 | 12916.7 | 12871.4 | 13066.3 | 12939.8 | 12851.4 | 13030.1 | 13283.4 | 13297 | 13425.4 | 13329.9 | 13089.7 | 12961.1 | 12960.7 | 12900.3 | 13751.1 | 12854.3 | 13562.6 | 12634.6 | 13162.2 | 14071.5 | 12607.3 | 13747.2 | 12349.5 | 12607.4 | 13223.6 | 12686.5 | 13494.5 | 12483.5 | 13404.4 | 12350.9 | 12285.1 | 13543.9 | 12354.5 | 13555.5 | 13452 | 12297.8 | 13191.5 | 12746 | 12831.2 | 12189.6 | 12807.1 | 13135.8 | 13412.9 | 12430.4 | 13260.6 | 12002.3 | 13051.4 | 12887.3 | 12334 | 13273.5 | 12135 | 13479.9 | 12339.1 | 13316.7 | 12519.5 | 13206.4 | 12570.6 | 13479 | 12477.3 | 13029.8 | 12395.8 | 11040.5 | 13094.2 | 12783.1 | 12143.1 | 13420.3 | 13152 | 12466.4 | 12334.4 | 13182 | 12245.3 | 12635 | 13369.8 | 12207.7 | 13378.8 | 12212.3 | 13216.5 | 12463 | 13213.4 | 11878.2 | 13313.2 | 12401.9 | 13186.3 | 12352.6 | 13215.3 | 12561.9 | 12222.4 | 13130.1 | 12399.1 | 12176.6 | 13208.5 | 13356.1 | 13153.8 | 12476.9 | 13307.1 | 12339.6 | 13016.5 | 12375.6 | 12913.9 | 11598.9 | 13130.6 | 12368 | 12533.9 | 12535.1 | 12358 | 10742.6 | 12330.7 | 10989.6 | 12295.2 | 12303.8 | 13657.1 | 12481.3 | 13651.6 | 12641.3 | 13540.8 | 12450.6 | 12612 | 12438.5 | 13430.9 | 13701.7 | 13644.8 | 13573.8 | 13579.5 | 13599.4 | 12757.9 | 13605.7 | 13572.3 | 13631.4 | 13690.4 | 13667.2 | 13714.6 | 12791 | 13693.8 | 12812.3 | 34.3753 | 34.0994 | 34.0557 | 34.0766 | 34.2863 | 34.1514 | 0 | 49.1 | 0 | 0 | 49.3 | 48.8 | 2.7877 | 2.8391 | 2.7616 | 2.9258 | 2.8496 | 2.6619 | 7.13 | 7.491 | 7.648 | 7.206 | 8.03 | 6.638 | 7.3695 | 7.4712 | 7.4134 | 7.429 | 7.4736 | 7.4802 | 1.6526 | 1.7371 | 1.4916 | 1.9766 | 1.8344 | 1.6271 | 7.3031 | 7.6383 | 7.4496 | 7.5494 | 7.5452 | 7.4849 | 0.45446 | 0.51392 | 0.45179 | 0.47429 | 0.45723 | 0.48873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 613987 | 1113 | 601221 | 1187 | 625480.716 | 1668.733 | 7.3695 | 7.4712 | 7.4134 | 7.429 | 7.4736 | 7.4802 | 7.3031 | 7.6383 | 7.4496 | 7.5494 | 7.5452 | 7.4849 | 1035000 | 2000 | 1021000 | 2000 | 2049201 | 4333 | 2052000 | 2044868 | 12.8333 | 7.4395 | 1.7199 | 7.4951 | 0.4734 | 23.12% | 6.316% | 34.1741 | 49.0667 | 2.8043 | 7.3572 | 2064560.5 | 2047601 | 2459334.0765 | 83.26% | 60 | 128
2024-04-24 | 2025 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 335090.89 | 6:23 | 19:10 | 11497.2 | 11844.1 | 11711.8 | 11720.4 | 11823.5 | 11773.1 | 11770.6 | 12089.8 | 11951.2 | 12005.2 | 11724.9 | 11929 | 11712.5 | 11793 | 11603.8 | 11639.2 | 11540.8 | 11533.1 | 11659.1 | 11828.1 | 11588.5 | 11618.2 | 11450.2 | 11504.2 | 11473.5 | 10340.9 | 11613 | 11460.7 | 11660.1 | 11594.9 | 11510.2 | 11681.6 | 11750.4 | 11770.8 | 11796.7 | 11737.5 | 11787.6 | 11671.7 | 11726.5 | 11647.4 | 11517.5 | 10787.8 | 11355.4 | 10617.9 | 10917.1 | 11600.1 | 10406.5 | 11397.6 | 11150.3 | 11386.1 | 12004.4 | 11450.2 | 12251.6 | 11149.1 | 12199.7 | 11125.8 | 11055.2 | 12342 | 11191.7 | 12354.5 | 12275.4 | 11195.1 | 12041.5 | 11596.6 | 11568.9 | 10851.7 | 11557.7 | 11839.6 | 12235.2 | 11098 | 11994.6 | 10691.5 | 11853.9 | 11555.5 | 11126.9 | 12001.5 | 10887.1 | 12302.5 | 11113.5 | 12062.2 | 11083.6 | 11809.8 | 11050.5 | 12130.7 | 11028.8 | 11590.4 | 11118.6 | 9841.4 | 11879.4 | 11505.4 | 10900.8 | 12256 | 11944.7 | 11203.2 | 11109.1 | 12014.2 | 10920.8 | 11226.5 | 12095.4 | 10834.6 | 12229.4 | 10900.2 | 12068.2 | 11192.7 | 12162.6 | 10743.2 | 12256.4 | 11278 | 12163.6 | 11309.2 | 12292.1 | 11502.8 | 10869.4 | 11859.6 | 11143.2 | 10893.2 | 12095.7 | 12155.1 | 12072.2 | 11204.5 | 12175.9 | 11156.4 | 11966.9 | 11286.1 | 11868.2 | 10617.7 | 12039.3 | 11186.6 | 11130.6 | 11059.7 | 11124.1 | 9611.4 | 10769.1 | 9502.2 | 10356 | 10354.3 | 11718.7 | 10513.4 | 11792.5 | 10683.6 | 11643.9 | 10524.7 | 10705.5 | 10539.3 | 11719.1 | 11968.1 | 11824.8 | 11721.9 | 11629.6 | 11644.2 | 10803.6 | 11767.7 | 11896.7 | 11896.8 | 11995.8 | 11960.5 | 11970.6 | 11020.2 | 12011.9 | 11070.9 | 35.0308 | 34.8011 | 35.0948 | 34.7279 | 34.9601 | 35.0167 | 0 | 49.4 | 0 | 0 | 49.5 | 48.5 | 2.527 | 2.5976 | 2.5552 | 2.4857 | 2.5218 | 2.2436 | 7.264 | 7.737 | 7.18 | 7.033 | 7.643 | 6.465 | 6.7308 | 6.6723 | 10.9528 | 6.7828 | 6.7154 | 6.3569 | 1.5326 | 1.5239 | 1.7669 | 1.8541 | 1.6414 | 1.3363 | 6.7239 | 6.7876 | 6.8546 | 6.9048 | 6.748 | 6.3015 | 0.43176 | 0.48354 | 0.58254 | 0.45759 | 0.4372 | 0.44165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 614919 | 1115 | 602129 | 1189 | 627315.382 | 1673.133 | 6.7308 | 6.6723 | 10.9528 | 6.7828 | 6.7154 | 6.3569 | 6.7239 | 6.7876 | 6.8546 | 6.9048 | 6.748 | 6.3015 | 932000 | 2000 | 908000 | 2000 | 1834666 | 4400 | 1836000 | 1830266 | 12.7833 | 7.3685 | 1.6092 | 6.7201 | 0.47238 | 21.84% | 7.029% | 34.9386 | 49.1333 | 2.4885 | 7.2203 | 1837808.1 | 1832933 | 2209393 | 82.96% | 66 | 49384
2024-04-25 | 2025 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 335090.89 | 6:33 | 19:00 | 12341 | 12817 | 12718.2 | 12684.8 | 12821.3 | 12823.9 | 12865.1 | 13208.7 | 12824.7 | 12771.5 | 12723.7 | 12843.4 | 12837.8 | 12790.5 | 12811.8 | 12875.9 | 12750.1 | 12754.6 | 12800 | 12897.3 | 12783.2 | 12812.6 | 12580.9 | 12678.6 | 12594.2 | 11253.1 | 12630.2 | 12571 | 12669.8 | 12548.6 | 12547.8 | 12755.1 | 12930.9 | 12940.3 | 13044.4 | 12953.2 | 12833.9 | 12676.8 | 12692.7 | 12612.1 | 13358.8 | 12418.6 | 13184.5 | 12206.1 | 12797.2 | 13707.5 | 12198.2 | 13344.4 | 12047 | 12293.4 | 12965 | 12386.9 | 13225.1 | 12153.1 | 13170.5 | 12063.2 | 12025.2 | 13331.6 | 12058.4 | 13292.7 | 13171.3 | 12011.2 | 12959.1 | 12496.8 | 12733.2 | 12095.9 | 12642.2 | 13050.7 | 13259 | 12290.1 | 13125.5 | 11855.7 | 12852.2 | 12724.9 | 12102.9 | 13117.6 | 11927.1 | 13287.4 | 12113.3 | 13121.9 | 12401.5 | 13104.6 | 12475.6 | 13426.5 | 12396.4 | 12973.9 | 12298.4 | 10957.1 | 13028.4 | 12714.9 | 12026.2 | 13364 | 13079.9 | 12330.3 | 12195.1 | 13100.8 | 11997.9 | 12415 | 13152 | 11929 | 13118.7 | 11865.2 | 12893.9 | 12091.5 | 12885.3 | 11492.6 | 12933.5 | 11966.9 | 12812.4 | 11943.1 | 12856 | 12116.1 | 11980.9 | 12912.5 | 12062.3 | 11851.4 | 12883 | 13069.5 | 12801.4 | 12096.1 | 12937.2 | 11918.3 | 12625.1 | 11931.6 | 12470.2 | 11167.2 | 12708.5 | 11943 | 12189.8 | 12214 | 11956.6 | 10413.8 | 12015 | 10703.9 | 12177.9 | 12184.7 | 13661.4 | 12441.2 | 13656.8 | 12613.8 | 13562.5 | 12409.6 | 12567 | 12336.8 | 13310.2 | 13607.5 | 13541.3 | 13493.3 | 13528.1 | 13568.9 | 12693.2 | 13553.2 | 13323.1 | 13372.6 | 13448.7 | 13441.2 | 13484.4 | 12553.3 | 13526.4 | 12585.8 | 36.4044 | 36.1417 | 36.1916 | 36.1896 | 36.2956 | 36.3673 | 0 | 51.7 | 0 | 0 | 51.6 | 52 | 3.1876 | 3.3736 | 3.2625 | 3.4966 | 3.5798 | 3.0424 | 7.925 | 8.084 | 7.86 | 8.193 | 7.707 | 7.872 | 7.3265 | 7.3295 | 5.5433 | 7.4102 | 7.3538 | 7.4969 | 1.6194 | 1.7104 | 1.0499 | 1.9721 | 1.8066 | 1.6439 | 7.2824 | 7.4514 | 7.2394 | 7.5202 | 7.3856 | 7.4649 | 0.451 | 0.51047 | 0.32257 | 0.47507 | 0.45604 | 0.49211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 615931 | 1116 | 603132 | 1190 | 629324.582 | 1677.533 | 7.3265 | 7.3295 | 5.5433 | 7.4102 | 7.3538 | 7.4969 | 7.2824 | 7.4514 | 7.2394 | 7.5202 | 7.3856 | 7.4649 | 1012000 | 1000 | 1003000 | 1000 | 2009200 | 4400 | 2013000 | 2004800 | 12.45 | 7.0767 | 1.6337 | 7.3907 | 0.45121 | 23.09% | 6.105% | 36.265 | 51.7667 | 3.3238 | 7.9402 | 2024073 | 2007200 | 2410796.2543 | 83.26% | 54 | 0
2024-04-26 | 2025 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 335090.89 | 6:24 | 19:14 | 12134.7 | 12482.3 | 12427.3 | 12439.2 | 12519.5 | 12533.5 | 12547.9 | 12825.8 | 12530.2 | 12502.2 | 12374.4 | 12511.9 | 12501 | 12422.4 | 12507.1 | 12537 | 12442.1 | 12470.5 | 12488.5 | 12571.3 | 12519.9 | 12528.9 | 12400.8 | 12451.6 | 12316 | 11153.1 | 12346.5 | 12309.9 | 12531.2 | 12461.5 | 12376.4 | 12498.3 | 12887.4 | 12885.8 | 12946 | 12889.9 | 12590.6 | 12486.9 | 12513.3 | 12477.3 | 13096.4 | 12362.2 | 12976.8 | 12225.4 | 12709.9 | 13489.8 | 12135.7 | 13079.6 | 11873 | 12087.3 | 12620.4 | 12173.6 | 12865.3 | 11947.2 | 12825.8 | 11927.3 | 11875.6 | 12966.5 | 11930 | 12934.7 | 12818.1 | 11873.7 | 12629.2 | 12237.1 | 12345.4 | 11809.6 | 12370.5 | 12709.5 | 12871.8 | 12064.4 | 12738.2 | 11722.6 | 12546.9 | 12438.9 | 11922.5 | 12755.1 | 11765.7 | 12906.8 | 11939.8 | 12761 | 12179.9 | 12778 | 12257.8 | 13024 | 12156.3 | 12651.2 | 12074.2 | 10854.7 | 12690.9 | 12448.1 | 11903.6 | 13028.2 | 12772.6 | 12163.4 | 12060.5 | 12825.8 | 11973.1 | 12286.2 | 12932.6 | 11905.4 | 12970 | 11920.1 | 12836.4 | 12159.1 | 12821.3 | 11648.9 | 12914.3 | 12091.8 | 12825.9 | 12071.2 | 12835.3 | 12254 | 11929.4 | 12716.3 | 12084.6 | 11905.1 | 12793.1 | 12894.1 | 12738.1 | 12125.9 | 12830.9 | 12010.4 | 12631.3 | 12079.5 | 12531.5 | 11375.1 | 12712.4 | 12055.6 | 12187.9 | 12175.9 | 12028.7 | 10520.4 | 12036.7 | 10783.2 | 12073.6 | 12077.7 | 13235 | 12216.7 | 13243.1 | 12362.3 | 13139.6 | 12201 | 12350.4 | 12201.2 | 13018.8 | 13249 | 13228 | 13169.3 | 13172.4 | 13190.6 | 12449 | 13178.4 | 13167.1 | 13184.5 | 13281.3 | 13249.1 | 13271.8 | 12455.4 | 13286.1 | 12494.1 | 33.64 | 33.28 | 33.29 | 33.29 | 33.2 | 33.52 | 0 | 45.8 | 0 | 0 | 45.8 | 45.9 | 6.73 | 6.75 | 6.59 | 6.71 | 6.78 | 6.64 | 11.19 | 11.54 | 11.52 | 10.9 | 11.8 | 10.91 | 7.09 | 7.14 | 7.1 | 7.18 | 7.21 | 7.29 | 1.62 | 1.63 | 1.49 | 1.97 | 1.76 | 1.56 | 7.07 | 7.24 | 7.09 | 7.26 | 7.23 | 7.25 | 0.45 | 0.52 | 0.46 | 0.48 | 0.47 | 0.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 616923 | 1118 | 604126 | 1191 | 631304.4 | 1681.933 | 7.09 | 7.14 | 7.1 | 7.18 | 7.21 | 7.29 | 7.07 | 7.24 | 7.09 | 7.26 | 7.23 | 7.25 | 992000 | 2000 | 994000 | 1000 | 1979818 | 4400 | 1983000 | 1975418 | 12.8333 | 7.1683 | 1.6717 | 7.19 | 0.48167 | 23.32% | 6.699% | 33.37 | 45.8333 | 6.7 | 11.31 | 1994275.8 | 1978401 | 2409419.1578 | 82.11% | 61 | 6494
2024-04-27 | 2025 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 335090.89 | 6:22 | 19:15 | 11407.3 | 11992.1 | 11972 | 11901.2 | 12077.8 | 12115.8 | 12138.6 | 12681.7 | 12040.4 | 12139.2 | 11835.9 | 12012.2 | 11944.9 | 11923.4 | 11945.2 | 12006.4 | 11922.6 | 11934.6 | 11966.9 | 12001.4 | 11994.2 | 11961.7 | 11701 | 11833 | 11713.6 | 10252 | 11698.8 | 11660 | 11965.4 | 11833.5 | 11743.3 | 12015.6 | 12120.2 | 12089.3 | 12123.6 | 12058.1 | 12179.4 | 11993.5 | 12054.1 | 11988.1 | 12869.3 | 11586.9 | 12726.6 | 11371.3 | 12109.5 | 13393 | 11325.6 | 12881.1 | 10954 | 11221.7 | 12057.3 | 11360.2 | 12467.8 | 11080.4 | 12404.3 | 11016.4 | 10981.4 | 12680.3 | 10958.3 | 12554.9 | 12404.7 | 10935 | 12201 | 11564.9 | 11493.2 | 10757.4 | 11666.3 | 12252.2 | 12579.6 | 11259.2 | 12369.6 | 10831.2 | 12007.5 | 11805.6 | 11059.2 | 12418.5 | 10872.9 | 12623.5 | 11081.5 | 12425 | 11396.4 | 12358.8 | 11517 | 12769.4 | 11372.6 | 12150.4 | 11303 | 9978.3 | 12387.1 | 11850.7 | 11011.6 | 12791.3 | 12385.4 | 11392.9 | 11277.1 | 12489.5 | 11137.3 | 11615.3 | 12698.8 | 11101.7 | 12711.4 | 11070.3 | 12374.4 | 11347.4 | 12496.9 | 10756.7 | 12578.7 | 11305.1 | 12367.6 | 11259.7 | 12449.1 | 11471.6 | 11163.2 | 12409.3 | 11322.4 | 11072 | 12482.2 | 12638 | 12371.9 | 11361.7 | 12568 | 11222.9 | 12169.2 | 11272.8 | 12009.8 | 10521.7 | 12260.3 | 11226.6 | 11422.3 | 11444.3 | 11283.4 | 9753.1 | 11197.8 | 9919 | 11350 | 11350.4 | 13071.7 | 11447.7 | 13132.1 | 11702.4 | 13048.1 | 11506.3 | 11736.6 | 11519.9 | 12641.1 | 13060.8 | 12971.4 | 12919.2 | 12917.4 | 12980 | 11797.4 | 12985.2 | 12864 | 12911 | 13072 | 13023.7 | 13018.5 | 11728.9 | 12988.3 | 11735.8 | 32.37 | 32.06 | 31.97 | 32.03 | 32.26 | 32.23 | 0 | 45.4 | 0 | 0 | 45.5 | 45.4 | 4.22 | 4.17 | 4.13 | 4.26 | 4.14 | 3.8 | 8.35 | 8.6 | 8.21 | 8.35 | 8.68 | 9.69 | 6.55 | 6.59 | 6.57 | 6.63 | 6.7 | 6.73 | 1.47 | 1.62 | 1.35 | 1.82 | 1.7 | 1.56 | 6.61 | 6.69 | 6.57 | 6.69 | 6.7 | 6.74 | 0.47 | 0.53 | 0.47 | 0.5 | 0.48 | 0.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 617870 | 1120 | 605076 | 1192 | 633195.049 | 1686.333 | 6.55 | 6.59 | 6.57 | 6.63 | 6.7 | 6.73 | 6.61 | 6.69 | 6.57 | 6.69 | 6.7 | 6.74 | 947000 | 2000 | 950000 | 1000 | 1890649 | 4400 | 1894000 | 1886249 | 12.8833 | 6.6283 | 1.5867 | 6.6667 | 0.49333 | 23.94% | 7.4% | 32.1533 | 45.4333 | 4.12 | 8.6467 | 1903291.6 | 1889134 | 2229553.979 | 84.73% | 54 | 0
2024-04-28 | 2025 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 335090.89 | 6:26 | 19:17 | 11492.1 | 11925 | 11916.4 | 11874 | 12034.7 | 12089.3 | 12041.6 | 12486.5 | 12020.2 | 11936.7 | 12003.2 | 12045.2 | 12137.8 | 12077.5 | 12118 | 12139.1 | 12043.3 | 12040.8 | 12134.7 | 12199.7 | 12113.3 | 12135.6 | 11887.7 | 11976.3 | 11870.6 | 10664.2 | 11944.9 | 11890.6 | 12093.7 | 11985.1 | 11954.8 | 12102.1 | 12291.4 | 12292.8 | 12308.1 | 12261.6 | 12220.2 | 12092.2 | 12124.3 | 12075.1 | 12730 | 11845.7 | 12578.1 | 11666.7 | 12173.7 | 13080 | 11604.1 | 12737 | 11413.1 | 11624.6 | 12263.1 | 11698.2 | 12521.4 | 11480 | 12445.2 | 11407 | 11429.5 | 12709.8 | 11408.7 | 12606 | 12464 | 11318 | 12295.3 | 11832.3 | 12031.7 | 11400.1 | 11958.3 | 12346.9 | 12601.7 | 11568.7 | 12391.7 | 11156.8 | 12201.3 | 11962.2 | 11461.2 | 12362 | 11193.9 | 12633.8 | 11404.3 | 12367.1 | 11704.5 | 12398.5 | 11801.4 | 12747.4 | 11695.1 | 12283.2 | 11589.7 | 10387.8 | 12290.4 | 12025.6 | 11286.3 | 12582.8 | 12310.7 | 11620.1 | 11521.5 | 12290.5 | 11294.7 | 11722.2 | 12510.9 | 11375.5 | 12490.9 | 11320.1 | 12290 | 11578.2 | 12331.9 | 11017.3 | 12434.5 | 11559 | 12298.4 | 11476.6 | 12360.1 | 11711.7 | 11478.5 | 12463.6 | 11623 | 11433.6 | 12485 | 12616.3 | 12422.8 | 11666.6 | 12522.3 | 11526.4 | 12263.1 | 11632.7 | 12100.8 | 10846.5 | 12324.8 | 11538.3 | 11714.2 | 11706.2 | 11524.7 | 10041.6 | 11444.3 | 10167.8 | 11297.7 | 11293.7 | 12722.2 | 11501.1 | 12734.8 | 11645.2 | 12621.1 | 11368.7 | 11557.1 | 11418.5 | 12430.1 | 12724.4 | 12708.5 | 12613.8 | 12611 | 12635.9 | 11717.4 | 12620.7 | 12704.3 | 12724.1 | 12797.7 | 12749 | 12748.6 | 11731.7 | 12765.3 | 11797.8 | 34.91 | 34.67 | 34.76 | 34.7 | 34.97 | 34.81 | 0 | 49.9 | 0 | 0 | 50.3 | 49.6 | 2.79 | 2.81 | 2.71 | 2.8 | 2.75 | 2 | 6.32 | 6.98 | 7.86 | 6.88 | 6.33 | 6.1 | 6.92 | 6.97 | 6.9 | 7.03 | 7.15 | 6.93 | 1.56 | 1.64 | 1.43 | 1.93 | 1.71 | 1.51 | 6.93 | 7.02 | 6.84 | 7.05 | 6.99 | 6.82 | 0.47 | 0.54 | 0.47 | 0.51 | 0.49 | 0.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618828 | 1121 | 606029 | 1194 | 635099.25 | 1690.733 | 6.92 | 6.97 | 6.9 | 7.03 | 7.15 | 6.93 | 6.93 | 7.02 | 6.84 | 7.05 | 6.99 | 6.82 | 958000 | 1000 | 953000 | 2000 | 1904201 | 4400 | 1908000 | 1899801 | 12.85 | 6.9833 | 1.63 | 6.9417 | 0.49833 | 23.34% | 7.179% | 34.8033 | 49.9333 | 2.6433 | 6.745 | 1917504.6 | 1902867 | 2288277.8149 | 83.16% | 66 | 4143
2024-04-29 | 2025 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 335090.89 | 6:22 | 19:15 | 12612 | 13052.9 | 13037.2 | 13000.6 | 13137.6 | 13159.4 | 13192.4 | 13495.9 | 13059.4 | 13066 | 12938.3 | 13051.5 | 13053.9 | 12990.9 | 13099.2 | 13114.1 | 13015.4 | 13030.8 | 13042.4 | 13118 | 13066.2 | 13080.1 | 12912 | 12982.7 | 12834 | 11545.3 | 12853.4 | 12826.1 | 12924.4 | 12824.4 | 12918.1 | 13055.8 | 13390.3 | 13388 | 13480.8 | 13409.2 | 13148.6 | 13035.3 | 13057.6 | 12986.5 | 13753.7 | 12906.8 | 13609.6 | 12729 | 13291.7 | 14157.5 | 12663 | 13734.5 | 12302.3 | 12539.5 | 13152 | 12652.2 | 13425.2 | 12423 | 13371.2 | 12359.8 | 12302.8 | 13526.3 | 12324 | 13482.7 | 13372.6 | 12276.7 | 13150.1 | 12696.5 | 12886.4 | 12311.7 | 12826.5 | 13249 | 13405.4 | 12521.7 | 13288.6 | 12138.5 | 13043.2 | 12928.2 | 12340.6 | 13291.4 | 12164.6 | 13444.2 | 12339.8 | 13296.9 | 12652.1 | 13317.9 | 12706.6 | 13601.8 | 12621.8 | 13169.6 | 12555.5 | 11245 | 13248.9 | 12965.7 | 12340.1 | 13606.2 | 13368.1 | 12696.5 | 12581.5 | 13381.7 | 12434.6 | 12789.5 | 13509.7 | 12374.4 | 13553.6 | 12379.8 | 13375 | 12627.7 | 13374.7 | 12064.6 | 13461.2 | 12555.3 | 13356.2 | 12539.5 | 13391.2 | 12728.6 | 12410.2 | 13307.6 | 12571.4 | 12359.6 | 13359.2 | 13486.2 | 13299 | 12611.3 | 13415.8 | 12492 | 13167.3 | 12555.9 | 13071.1 | 11792 | 13259.8 | 12523.6 | 12645.1 | 12625.7 | 12508.4 | 10897 | 12473.8 | 11140.5 | 12488.7 | 12503.8 | 13777 | 12636.5 | 13816.1 | 12818.5 | 13695.5 | 12647.6 | 12813.5 | 12656.2 | 13546.4 | 13822.2 | 13799.5 | 13676.6 | 13724.6 | 13745.1 | 12937 | 13760.4 | 13720.2 | 13741 | 13797.3 | 13780.1 | 13819 | 12911.9 | 13809.6 | 12933.3 | 33.6802 | 33.2901 | 33.3313 | 33.5079 | 33.9116 | 33.526 | 0 | 44.2 | 0 | 0 | 44.7 | 44.4 | 5.7512 | 5.7936 | 5.5835 | 5.9004 | 5.7521 | 5.4407 | 11.095 | 10.235 | 11.179 | 10.423 | 11.738 | 10.754 | 7.315 | 7.0544 | 7.3306 | 7.351 | 7.5037 | 7.5095 | 1.6585 | 1.7257 | 1.528 | 2.0336 | 1.8931 | 1.7252 | 7.4081 | 7.4396 | 7.3035 | 7.431 | 7.4083 | 7.4707 | 0.50778 | 0.57992 | 0.50728 | 0.53819 | 0.52197 | 0.56025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 619862 | 1123 | 607062 | 1195 | 637160.25 | 1695.2 | 7.315 | 7.0544 | 7.3306 | 7.351 | 7.5037 | 7.5095 | 7.4081 | 7.4396 | 7.3035 | 7.431 | 7.4083 | 7.4707 | 1034000 | 2000 | 1033000 | 1000 | 2061000 | 4467 | 2064000 | 2056533 | 12.8833 | 7.344 | 1.7607 | 7.4102 | 0.5359 | 23.97% | 7.232% | 33.5412 | 44.4333 | 5.7036 | 10.904 | 2076590.8 | 2059333 | 2469204.7554 | 83.4% | 57 | 0
2024-04-30 | 2025 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 335090.89 | 6:12 | 19:17 | 12912.7 | 13352 | 13315.2 | 13296.2 | 13395.4 | 13438.5 | 13469.9 | 13817.6 | 13365.6 | 13327.6 | 13236.8 | 13359.9 | 13357.4 | 13284.5 | 13374.9 | 13416.6 | 13304.2 | 13324.4 | 13336 | 13407.2 | 13351.1 | 13370.3 | 13201.1 | 13276.3 | 13143 | 11904.4 | 13159.5 | 13134.2 | 13402.3 | 13289.7 | 13202.4 | 13357.4 | 13662.4 | 13652.1 | 13804.6 | 13754 | 13463.5 | 13339.4 | 13355.4 | 13287.6 | 14065.1 | 13185.9 | 13885 | 13006.1 | 13559.1 | 14467.9 | 12932.6 | 14051.4 | 12619.3 | 12847 | 13448.2 | 12959.9 | 13726.9 | 12738.6 | 13669.5 | 12672.6 | 12633.8 | 13850.4 | 12640 | 13794.2 | 13675.5 | 12575.6 | 13490.7 | 13042.7 | 13188.3 | 12626.4 | 13135.6 | 13544.3 | 13719.3 | 12833.2 | 13571.3 | 12459.8 | 13344.9 | 13231.4 | 12661.2 | 13601.8 | 12501.6 | 13754.1 | 12654.6 | 13600.1 | 12954 | 13621.6 | 12984.1 | 13915.4 | 12917 | 13444 | 12835.9 | 11530.8 | 13557 | 13237.4 | 12651.7 | 13900.4 | 13632.8 | 12947.2 | 12817.7 | 13646.3 | 12703.7 | 13081 | 13805.2 | 12658.6 | 13864.3 | 12665.3 | 13672 | 12901.5 | 13660 | 12376.1 | 13748.8 | 12833.6 | 13628.6 | 12811.2 | 13642.4 | 13001.9 | 12696.9 | 13577.3 | 12847 | 12649.6 | 13635.4 | 13771.8 | 13576.6 | 12889.4 | 13699.9 | 12769.6 | 13441.3 | 12830.1 | 13325.7 | 12092.3 | 13528 | 12795.2 | 12893.4 | 12864.8 | 12775.5 | 11148.8 | 12689.7 | 11402.5 | 12746.4 | 12759.1 | 14081.3 | 12911.7 | 14114.5 | 13096.9 | 13992.1 | 12904.9 | 13062.3 | 12887.9 | 13823.5 | 14117.2 | 14086.7 | 14012.5 | 14016.8 | 14028.1 | 13210 | 14056.3 | 13978.6 | 14005 | 14099.5 | 14073.9 | 14107.6 | 13191 | 14108.7 | 13206.9 | 33.26 | 33.13 | 33.24 | 33.06 | 33.4 | 33.29 | 0 | 47.2 | 0 | 0 | 47.5 | 47.3 | 4 | 3.9 | 3.91 | 3.91 | 3.9 | 3.22 | 9.37 | 9.62 | 9.54 | 9.47 | 9.18 | 9.27 | 7.73 | 7.72 | 7.7 | 7.76 | 7.89 | 7.88 | 1.79 | 1.91 | 1.65 | 2.19 | 2.01 | 1.82 | 7.82 | 7.79 | 7.64 | 7.81 | 7.76 | 7.81 | 0.53 | 0.61 | 0.53 | 0.56 | 0.55 | 0.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 620921 | 1125 | 608118 | 1197 | 639267.517 | 1699.467 | 7.73 | 7.72 | 7.7 | 7.76 | 7.89 | 7.88 | 7.82 | 7.79 | 7.64 | 7.81 | 7.76 | 7.81 | 1059000 | 2000 | 1056000 | 2000 | 2107267 | 4267 | 2111000 | 2103000 | 13.0833 | 7.78 | 1.895 | 7.7717 | 0.56167 | 24.36% | 7.227% | 33.23 | 47.3333 | 3.8067 | 9.4083 | 2123396.9 | 2106334 | 2562719 | 82.19% | 53 | 0
2024-05-01 | 2025 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 335090.89 | 6:12 | 19:17 | 12958 | 13374 | 13317 | 13306 | 13387 | 13432 | 13445 | 13773 | 13374 | 13332 | 13243 | 13356 | 13360 | 13298 | 13375 | 13436 | 13304 | 13325 | 13365 | 13429 | 13375 | 13396 | 13217 | 13297 | 13158 | 11994 | 13186 | 13156 | 13412 | 13292 | 13199 | 13361 | 13830 | 13823 | 13853 | 13813 | 13482 | 13369 | 13382 | 13317 | 14038 | 13190 | 13856 | 13016 | 13553 | 14423 | 12917 | 14011 | 12663 | 12886 | 13469 | 12956 | 13724 | 12749 | 13688 | 12697 | 12679 | 13855 | 12707 | 13800 | 13680 | 12630 | 13493 | 13045 | 13190 | 12650 | 13154 | 13550 | 13730 | 12849 | 13611 | 12531 | 13372 | 13260 | 12707 | 13624 | 12555 | 13770 | 12691 | 13615 | 12955 | 13607 | 12996 | 13896 | 12927 | 13457 | 12840 | 11617 | 13578 | 13259 | 12671 | 13903 | 13625 | 12949 | 12824 | 13703 | 12776 | 13119 | 13811 | 12709 | 13845 | 12708 | 13668 | 12943 | 13666 | 12425 | 13751 | 12861 | 13640 | 12844 | 13673 | 13046 | 12730 | 13594 | 12898 | 12698 | 13652 | 13777 | 13586 | 12914 | 13707 | 12800 | 13460 | 12866 | 13351 | 12190 | 13550 | 12825 | 12942 | 12926 | 12813 | 11266 | 12726 | 11470 | 12815 | 12827 | 14077 | 12942 | 14121 | 13121 | 13983 | 12924 | 13078 | 12954 | 13838 | 14124 | 14091 | 14026 | 14014 | 14036 | 13241 | 14067 | 14018 | 14030 | 14099 | 14075 | 14128 | 13208 | 14126 | 13239 | 31.3586 | 31.1335 | 31.2903 | 31.1792 | 31.6333 | 31.3984 | 0 | 45.243 | 0 | 0 | 45.6 | 45.5 | 3.0593 | 3.0061 | 2.9501 | 3.1194 | 3.1819 | 2.3831 | 7.877 | 8.43 | 7.594 | 8.049 | 8.3 | 7.873 | 7.8965 | 7.9067 | 7.9821 | 7.8918 | 7.9897 | 8.0099 | 1.7932 | 1.9119 | 1.6566 | 2.1856 | 2.0183 | 1.82 | 7.9114 | 7.9499 | 7.874 | 7.9013 | 7.9495 | 7.9561 | 0.54047 | 0.61115 | 0.53784 | 0.56846 | 0.55031 | 0.58809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 621981 | 1126 | 609176 | 1198 | 641378.3 | 1703.8 | 7.8965 | 7.9067 | 7.9821 | 7.8918 | 7.9897 | 8.0099 | 7.9114 | 7.9499 | 7.874 | 7.9013 | 7.9495 | 7.9561 | 1060000 | 1000 | 1058000 | 1000 | 2110783 | 4333 | 2116000 | 2106450 | 13.0833 | 7.9461 | 1.8976 | 7.9237 | 0.56605 | 23.88% | 7.144% | 31.3322 | 45.4477 | 2.95 | 8.0205 | 2126920 | 2108933 | 2648524.3146 | 79.63% | 61 | 0
2024-05-02 | 2025 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 335090.89 | 6:11 | 19:14 | 12864.6 | 13286.1 | 13196.1 | 13200.9 | 13245.9 | 13326.3 | 13363.3 | 13653.2 | 13288 | 13238.8 | 13148.4 | 13268.5 | 13259.2 | 13208.2 | 13254.8 | 13315.9 | 13188 | 13226.8 | 13279.1 | 13339.5 | 13292.4 | 13310.6 | 13140.1 | 13216.9 | 13093.5 | 11856.2 | 13108.9 | 13084.5 | 13344.2 | 13222.7 | 13142.3 | 13300.1 | 13609.1 | 13592.5 | 13752.4 | 13684.1 | 13423.5 | 13307.3 | 13324.6 | 13259 | 13958 | 13111.1 | 13801.5 | 12941.8 | 13475 | 14350.1 | 12846.2 | 13942.3 | 12559.9 | 12801.3 | 13386.2 | 12898.2 | 13650 | 12635.2 | 13615.7 | 12605.6 | 12574.9 | 13776.9 | 12594.6 | 13734.6 | 13620.2 | 12531.8 | 13377.1 | 12967.4 | 13139 | 12588.7 | 13088.4 | 13506.5 | 13665.9 | 12797.4 | 13545.3 | 12430 | 13301.6 | 13201.2 | 12632.7 | 13570.3 | 12471.3 | 13712.5 | 12611.4 | 13555.1 | 12925.4 | 13569.9 | 12953.5 | 13864.4 | 12887.6 | 13409.6 | 12790.8 | 11502.2 | 13560.6 | 13219.4 | 12622 | 13867.1 | 13572.8 | 12882.5 | 12738.1 | 13641.1 | 12722.9 | 13072.6 | 13784.9 | 12666.4 | 13807.1 | 12646.3 | 13625.4 | 12894.9 | 13625.4 | 12339.5 | 13716.4 | 12822.5 | 13602.6 | 12797.8 | 13627.3 | 12989 | 12663.1 | 13552.9 | 12840 | 12631.7 | 13617.2 | 13734.9 | 13555 | 12875 | 13659.5 | 12733.2 | 13421.7 | 12813.6 | 13301 | 12047.8 | 13482.5 | 12752.7 | 12864.7 | 12860.4 | 12714.1 | 11109.1 | 12682.6 | 11389.3 | 12707.5 | 12735.1 | 14039.3 | 12905.9 | 14076.5 | 13094.1 | 13940 | 12903.4 | 13040.5 | 12887.9 | 13804.1 | 14085 | 14053.4 | 13986.6 | 13976.3 | 13993.8 | 13199.6 | 14020.9 | 13992.9 | 14004.1 | 14054.3 | 14023.4 | 14070.8 | 13171.6 | 14094 | 13204.7 | 33.2744 | 32.935 | 32.8151 | 32.8289 | 32.8817 | 32.9621 | 0 | 47.5 | 0 | 0 | 47.2643 | 47.7 | 2.7984 | 2.9025 | 2.8197 | 2.8606 | 2.7812 | 1.8556 | 6.701 | 6.783 | 6.686 | 6.386 | 6.559 | 6.469 | 7.8892 | 7.8898 | 7.9516 | 7.9066 | 7.9881 | 8.0001 | 1.8068 | 1.8902 | 1.6708 | 2.2031 | 1.9978 | 1.797 | 7.8349 | 7.8713 | 7.791 | 7.8554 | 7.8743 | 7.8716 | 0.54688 | 0.61963 | 0.54377 | 0.58049 | 0.55814 | 0.59494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 623034 | 1128 | 610229 | 1199 | 643477.717 | 1708.133 | 7.8892 | 7.8898 | 7.9516 | 7.9066 | 7.9881 | 8.0001 | 7.8349 | 7.8713 | 7.791 | 7.8554 | 7.8743 | 7.8716 | 1053000 | 2000 | 1053000 | 1000 | 2099417 | 4333 | 2103000 | 2095084 | 13.05 | 7.9376 | 1.8943 | 7.8498 | 0.57398 | 23.86% | 7.312% | 32.9495 | 47.4881 | 2.6697 | 6.5973 | 2115905.1 | 2097733 | 2604713.9074 | 80.54% | 62 | 975
2024-05-03 | 2025 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 335090.89 | 6:14 | 19:12 | 10604.5 | 11027.8 | 10963.3 | 10962.4 | 11015.6 | 11087.8 | 11118.9 | 11438.2 | 11037 | 11015.3 | 10895.1 | 11018.3 | 10990.9 | 10939.3 | 10991.1 | 11056.8 | 10957.4 | 10975.7 | 11015.9 | 11050.1 | 11025.1 | 11019.3 | 10843.6 | 10940.7 | 10765.9 | 9679.2 | 10802.7 | 10776 | 11043.2 | 10948.7 | 10840.8 | 10994.5 | 11090.6 | 11081.1 | 11141.7 | 11090.1 | 11082.9 | 10966.6 | 11001.4 | 10924.6 | 11694.2 | 10814.4 | 11544.9 | 10642.5 | 11170.4 | 12056.6 | 10577.3 | 11696.7 | 10263.2 | 10485.5 | 11055.5 | 10579 | 11339.2 | 10362.3 | 11285.2 | 10306.4 | 10268.2 | 11452.3 | 10301.3 | 11396.7 | 11268.3 | 10239.9 | 11086.3 | 10631.8 | 10808.4 | 10274.7 | 10743.4 | 11173.5 | 11350.7 | 10472.8 | 11211.6 | 10146.3 | 10972.1 | 10852 | 10297.2 | 11247.7 | 10159.7 | 11372.8 | 10276.9 | 11225.1 | 10583.7 | 11232.3 | 10631.3 | 11521.5 | 10548.8 | 11089.5 | 10466.9 | 9448.4 | 11236.4 | 10900.1 | 10290.3 | 11534 | 11239.9 | 10541.7 | 10421.4 | 11303.1 | 10386.3 | 10719.7 | 11448.5 | 10347.6 | 11470.3 | 10320.2 | 11263.4 | 10537.5 | 11297.1 | 10052.2 | 11366.2 | 10485.8 | 11244.1 | 10453.5 | 11280.4 | 10626.2 | 10357.1 | 11231.5 | 10509.3 | 10332.4 | 11295.8 | 11397.5 | 11240.8 | 10553 | 11342.5 | 10427.9 | 11092.5 | 10474.3 | 10958.6 | 9881.3 | 11166.5 | 10446.1 | 10575.2 | 10588.3 | 10444.9 | 9169.8 | 10407.5 | 9372.9 | 10450.3 | 10460.3 | 11711.9 | 10576.5 | 11743 | 10749.8 | 11626.7 | 10601.4 | 10745.5 | 10580 | 11439.2 | 11701.8 | 11669.5 | 11614.1 | 11420.7 | 11578.9 | 10845 | 11644.1 | 11592.3 | 11625.3 | 11716.7 | 11677 | 11687.4 | 10805.9 | 11729.4 | 10848.3 | 35.69 | 35.64 | 35.88 | 35.46 | 35.65 | 35.85 | 0 | 47.6 | 0 | 0 | 47.9 | 48.4 | 3.43 | 3.81 | 3.41 | 3.78 | 3.71 | 2.81 | 8.73 | 8.57 | 8.77 | 8.48 | 9.26 | 8.34 | 6.37 | 6.31 | 6.39 | 6.26 | 6.33 | 6.34 | 1.43 | 1.51 | 1.33 | 1.75 | 1.58 | 1.43 | 6.33 | 6.31 | 6.21 | 6.25 | 6.32 | 6.32 | 0.44 | 0.5 | 0.44 | 0.47 | 0.46 | 0.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 623904 | 1130 | 611099 | 1201 | 645212.05 | 1712.533 | 6.37 | 6.31 | 6.39 | 6.26 | 6.33 | 6.34 | 6.33 | 6.31 | 6.21 | 6.25 | 6.32 | 6.32 | 870000 | 2000 | 870000 | 2000 | 1734333 | 4400 | 1736000 | 1729933 | 12.9667 | 6.3333 | 1.505 | 6.29 | 0.465 | 23.76% | 7.393% | 35.695 | 47.9667 | 3.4917 | 8.6917 | 1745718.1 | 1732600 | 2098737.5741 | 82.55% | 74 | 67228
2024-05-04 | 2025 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 335090.89 | 6:25 | 19:22 | 10842.2 | 11300 | 11249.8 | 11197.9 | 11319.5 | 11389.5 | 11419.9 | 11792.8 | 11301.5 | 11311.3 | 11169.9 | 11301.7 | 11262.5 | 11235 | 11297.4 | 11332.6 | 11247.7 | 11249.7 | 11293.9 | 11329.7 | 11304.3 | 11286.9 | 11093.9 | 11199.8 | 11034.4 | 9846.8 | 11058 | 11026.9 | 11335.3 | 11235.2 | 11111.7 | 11296.1 | 11381.8 | 11373.4 | 11485.7 | 11431.6 | 11406.4 | 11261.8 | 11295.3 | 11246.1 | 12059 | 11063.3 | 11909.6 | 10868.5 | 11448.7 | 12516.5 | 10793.1 | 12067.4 | 10478.6 | 10717.6 | 11353.4 | 10819.8 | 11671.6 | 10580.4 | 11631.5 | 10534.3 | 10503.4 | 11832.3 | 10513.4 | 11755.2 | 11625 | 10462.3 | 11399.3 | 10903 | 11092.8 | 10518.7 | 11039.9 | 11497.5 | 11729.4 | 10723.6 | 11581.5 | 10387 | 11297.7 | 11159 | 10554.2 | 11598.7 | 10394.4 | 11757.1 | 10535.2 | 11576.1 | 10811.6 | 11550.2 | 10875.7 | 11871.6 | 10785.8 | 11385.5 | 10724.2 | 9629 | 11559.5 | 11190.4 | 10541.7 | 11921.1 | 11620.8 | 10876 | 10770.2 | 11663.3 | 10645 | 11001.5 | 11819.5 | 10589.9 | 11833 | 10562.1 | 11583.1 | 10797.5 | 11644 | 10292.9 | 11715.2 | 10749.1 | 11569.2 | 10706.1 | 11623.4 | 10899.8 | 10601.7 | 11575.2 | 10760.8 | 10564.1 | 11643.1 | 11765.4 | 11569.8 | 10806.4 | 11698.5 | 10685.7 | 11402 | 10722.5 | 11277.8 | 10091 | 11486.3 | 10706.5 | 10834.6 | 10856.7 | 10704.5 | 9381.7 | 10673.4 | 9582.9 | 10780 | 10785.8 | 12190.7 | 10909.1 | 12227 | 11076.5 | 12108.3 | 10913.7 | 11086.5 | 10925.1 | 11883.8 | 12226.7 | 12150.2 | 12090.6 | 12089.5 | 12129.6 | 11193.9 | 12136.4 | 12084.5 | 12115.2 | 12210.2 | 12181.6 | 12204 | 11162.9 | 12190.9 | 11190.7 | 34.971 | 34.6555 | 34.5276 | 34.7189 | 34.864 | 34.9717 | 0 | 45.1 | 0 | 0 | 45.5 | 45.4 | 6.301 | 6.2282 | 6.1947 | 6.1547 | 6.2171 | 5.9491 | 10.447 | 10.756 | 10.309 | 10.636 | 11.208 | 10.819 | 6.3818 | 6.2872 | 6.3957 | 6.3409 | 6.3654 | 6.4314 | 1.3411 | 1.5819 | 1.2333 | 1.6754 | 1.6128 | 1.5303 | 6.406 | 6.331 | 6.2351 | 6.2995 | 6.3658 | 6.4798 | 0.44191 | 0.50392 | 0.42626 | 0.47189 | 0.46588 | 0.49765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 624798 | 1131 | 611995 | 1202 | 646996.784 | 1716.8 | 6.3818 | 6.2872 | 6.3957 | 6.3409 | 6.3654 | 6.4314 | 6.406 | 6.331 | 6.2351 | 6.2995 | 6.3658 | 6.4798 | 894000 | 1000 | 896000 | 1000 | 1784734 | 4267 | 1788000 | 1780467 | 12.95 | 6.3671 | 1.4958 | 6.3529 | 0.46792 | 23.49% | 7.365% | 34.7848 | 45.3333 | 6.1741 | 10.6958 | 1795947.8 | 1784201 | 2150801.5068 | 82.96% | 70 | 10539
2024-05-05 | 2025 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 335090.89 | 6:25 | 19:18 | 11957.3 | 12449.4 | 12396.1 | 12374.6 | 12476.1 | 12545.4 | 12565.2 | 12985.7 | 12497.1 | 12453.4 | 12342.4 | 12486.7 | 12442.1 | 12408.5 | 12475.5 | 12514.6 | 12417.1 | 12425.3 | 12484.4 | 12549.1 | 12493.7 | 12480.4 | 12237.3 | 12366.8 | 12186.2 | 10771.9 | 12227.5 | 12187.3 | 12503.1 | 12385.6 | 12227.3 | 12447.7 | 12513.2 | 12539.1 | 12666.6 | 12582.2 | 12553.3 | 12397.2 | 12418.9 | 12322.5 | 13271.4 | 12189.8 | 13097.7 | 11977.8 | 12635.5 | 13685.4 | 11946.8 | 13275.1 | 11545.6 | 11819.6 | 12551.3 | 11940.1 | 12882.9 | 11712.3 | 12823.1 | 11586.3 | 11546.2 | 13030.3 | 11566.6 | 12965.6 | 12829.8 | 11523.2 | 12588.8 | 12042 | 12249.9 | 11538.3 | 12171 | 12638.4 | 12897.8 | 11790.3 | 12724.8 | 11337.3 | 12462.3 | 12279.2 | 11627.6 | 12762.1 | 11414.5 | 12968.6 | 11633.3 | 12788.6 | 11896.3 | 12694.2 | 11946.8 | 13015.6 | 11858.1 | 12509.8 | 11821.6 | 10470.8 | 12665.3 | 12289 | 11550.2 | 13035.4 | 12698.3 | 11866 | 11736.5 | 12773.8 | 11635.8 | 12045.7 | 12886.9 | 11565.3 | 12868.8 | 11516.3 | 12632.3 | 11767.8 | 12669.1 | 11160.6 | 12754.4 | 11708.4 | 12590.5 | 11646.6 | 12654.3 | 11861.3 | 11557.9 | 12636.8 | 11750.2 | 11494.8 | 12689.9 | 12838 | 12627.1 | 11771.9 | 12754.6 | 11631.2 | 12453.6 | 11693.3 | 12291 | 10904.4 | 12535.3 | 11659.9 | 11811.8 | 11825.8 | 11662.3 | 10080.9 | 11648 | 10339.1 | 11677.9 | 11697.8 | 13237.8 | 11888.8 | 13288.4 | 12101.8 | 13162.1 | 11934.2 | 12123.8 | 11880.5 | 12959.2 | 13301.6 | 13220 | 13160.7 | 13156.6 | 13187.5 | 12246 | 13226.2 | 13112.5 | 13164 | 13275.3 | 13232.5 | 13251.6 | 12185.7 | 13256.8 | 12229.5 | 36.2505 | 35.9461 | 35.9163 | 36.0649 | 36.2849 | 36.0854 | 0 | 49.3 | 0 | 0 | 49.4 | 49.3 | 3.3874 | 3.3178 | 3.2905 | 3.3737 | 3.4565 | 2.5371 | 6.385 | 7.188 | 6.165 | 6.513 | 7.271 | 6.029 | 7.1791 | 7.0496 | 7.1628 | 7.0802 | 7.0323 | 7.12 | 1.6152 | 1.7357 | 1.4776 | 1.974 | 1.798 | 1.6374 | 7.1173 | 7.0106 | 6.9535 | 6.9955 | 7.0546 | 7.0784 | 0.48714 | 0.55336 | 0.47501 | 0.51197 | 0.49655 | 0.53237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 625782 | 1133 | 612972 | 1204 | 648951.717 | 1721.133 | 7.1791 | 7.0496 | 7.1628 | 7.0802 | 7.0323 | 7.12 | 7.1173 | 7.0106 | 6.9535 | 6.9955 | 7.0546 | 7.0784 | 984000 | 2000 | 977000 | 2000 | 1954933 | 4333 | 1957000 | 1950600 | 12.8833 | 7.104 | 1.7063 | 7.035 | 0.5094 | 24.02% | 7.241% | 36.0913 | 49.3333 | 3.2272 | 6.5918 | 1968679.4 | 1953666 | 2335094.2093 | 83.67% | 62 | 0
2024-05-06 | 2025 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 335090.89 | 6:19 | 19:18 | 10118.6 | 10665.7 | 10808.2 | 10709.8 | 11026.2 | 11067.2 | 10841.7 | 11180.2 | 10676.5 | 10538.3 | 10517.6 | 10623.3 | 10637.9 | 10522.8 | 10832.2 | 10802.9 | 10778.6 | 10795.7 | 10675.4 | 10677.7 | 10732 | 10684.3 | 10535.7 | 10594.2 | 10123.1 | 8907 | 10276.6 | 10205.3 | 10538.7 | 10563.6 | 10416.5 | 10444.5 | 10756 | 10559.7 | 10458.1 | 10432.9 | 10606.8 | 10562.5 | 10673.8 | 10724.7 | 11942 | 11097.9 | 11776.1 | 10934.5 | 11274.5 | 12106.2 | 10646.7 | 11807.5 | 9720 | 9940.4 | 10586.3 | 9974.3 | 10845.4 | 9940.6 | 10664.8 | 9596.8 | 9652.8 | 10931.4 | 9789.2 | 10881.8 | 10840.3 | 9744.1 | 10643.7 | 10222.6 | 10238 | 9605.7 | 10165 | 10612.3 | 10853 | 9861.3 | 10669.9 | 9495.4 | 10521.3 | 10332.8 | 9818.4 | 10794.3 | 9649.4 | 10975.7 | 9842.6 | 10854.2 | 9948.8 | 10677.4 | 9935.2 | 11018.4 | 9908.5 | 10555.1 | 9963.5 | 8859.2 | 11158.7 | 10550.9 | 9985.7 | 11468.8 | 11105.9 | 10367.9 | 10301.2 | 11301.9 | 10362.7 | 10788.5 | 11672.3 | 10448.8 | 11850.5 | 10462.4 | 11736.6 | 10771.2 | 11905.7 | 10361.2 | 11956.3 | 10903.9 | 11772.8 | 10900.9 | 11888.5 | 11222 | 10468.9 | 11711.3 | 10824.5 | 10628.2 | 11859.8 | 12131.4 | 11845.5 | 11181 | 12065.5 | 11027.8 | 11703.3 | 11063.1 | 11613.7 | 10384 | 11889.5 | 11141.9 | 11236.3 | 11220.9 | 11174.2 | 9623.7 | 11005.4 | 9792.9 | 11184.8 | 11152.9 | 12207.2 | 10956.8 | 12340.1 | 11194.8 | 12325.6 | 11220 | 11451 | 11299.4 | 11780.7 | 12206.1 | 11865.7 | 11918.3 | 11520.4 | 12095.4 | 11261.8 | 12155.6 | 11693.5 | 11725 | 11926.8 | 11928 | 11948.8 | 10980.4 | 11829.9 | 10913.9 | 37.6663 | 37.4043 | 37.5224 | 37.4239 | 37.8351 | 37.6014 | 0 | 48.6 | 0 | 0 | 50.9 | 50.6 | 2.8478 | 2.9504 | 2.9643 | 2.8475 | 3.0338 | 1.829 | 5.866 | 5.794 | 5.673 | 5.815 | 6.293 | 7.288 | 6.1672 | 5.9374 | 6.4784 | 5.9336 | 6.6166 | 6.5024 | 1.4144 | 1.4102 | 1.3666 | 1.6817 | 1.6828 | 1.4606 | 6.0832 | 5.8545 | 6.2917 | 5.8568 | 6.6086 | 6.4215 | 0.43541 | 0.48999 | 0.45055 | 0.45615 | 0.4845 | 0.50338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 626622 | 1134 | 613864 | 1205 | 650678.984 | 1725.467 | 6.1672 | 5.9374 | 6.4784 | 5.9336 | 6.6166 | 6.5024 | 6.0832 | 5.8545 | 6.2917 | 5.8568 | 6.6086 | 6.4215 | 840000 | 1000 | 892000 | 1000 | 1727267 | 4334 | 1730000 | 1722933 | 12.9833 | 6.2726 | 1.5027 | 6.186 | 0.47 | 23.96% | 7.598% | 37.5756 | 50.0333 | 2.7455 | 6.1215 | 1737928.8 | 1726734 | 2059206.1003 | 83.85% | 70 | 30994
2024-05-07 | 2025 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 335090.89 | 6:23 | 19:18 | 10423.1 | 10668.2 | 10541.1 | 10568 | 10653.7 | 10549.2 | 10397.2 | 10665.6 | 10672.2 | 10886.5 | 10258.2 | 10402.5 | 10104 | 10255.4 | 9912.9 | 10030 | 9747.8 | 9707.3 | 9808.2 | 9868.3 | 9751.8 | 9774.2 | 9753.7 | 9694.7 | 9900 | 8704 | 9717.5 | 9651.2 | 10043.2 | 10069.9 | 10030 | 10275.8 | 10569.5 | 10482.5 | 10351.8 | 10388.8 | 10514 | 10374.6 | 10414.8 | 10569.8 | 10696.5 | 9967.8 | 10534.5 | 9784.1 | 10155.3 | 11025.6 | 9658.1 | 10591.6 | 9552.4 | 9819.2 | 10211.2 | 9825.5 | 10253.5 | 9357.7 | 10525.3 | 9426.1 | 9768.8 | 10999.6 | 9639.8 | 10986.8 | 10802.4 | 9634.7 | 10883.1 | 10550.4 | 10798 | 10528.2 | 10864.1 | 11547.9 | 11385.4 | 10879 | 11390 | 10455.1 | 10962.4 | 11283.7 | 10308.5 | 11675.4 | 10457.1 | 11380.1 | 10352.3 | 11407.7 | 11048.6 | 11719.7 | 10935.8 | 11857.8 | 10781.6 | 11320.6 | 10696.7 | 9562.7 | 11382.8 | 11140.6 | 10385.5 | 11528.5 | 11250.3 | 10614.3 | 10416.3 | 11324.4 | 10451.1 | 10741 | 11373.6 | 10290.7 | 11206.2 | 10187.4 | 11058.3 | 10339.9 | 11095.9 | 9841.5 | 11136.7 | 10313.5 | 11113.3 | 10443.6 | 11311.5 | 10667.9 | 10306.2 | 11058.9 | 10304.5 | 10135.8 | 11018.8 | 11230.9 | 11027.5 | 10498.5 | 11226.8 | 10403.4 | 10953.8 | 10432.3 | 10818.8 | 9824.6 | 11136.7 | 10493.4 | 10526.8 | 10599.5 | 10490.8 | 9029.9 | 10438.7 | 9358.9 | 10658.3 | 10702.5 | 11866.4 | 10806.2 | 11794.2 | 10913.9 | 11641 | 10845.7 | 11011.9 | 10855.8 | 11627.7 | 11847.1 | 11577.2 | 11586.9 | 6678.1 | 11703.4 | 11036.5 | 11753.7 | 11585.6 | 11591 | 11855.1 | 11771.9 | 11629.9 | 10906.8 | 11762.2 | 10898.2 | 38.95 | 38.59 | 38.55 | 38.73 | 38.98 | 38.91 | 0 | 49.1 | 0 | 0 | 50.9 | 51.1 | 3.58 | 3.54 | 3.47 | 3.65 | 3.64 | 2.91 | 6.41 | 6.34 | 6.04 | 6.52 | 7.92 | 6.6 | 6 | 5.71 | 5.85 | 6.35 | 6.3 | 6.5 | 1.33 | 1.41 | 1.18 | 1.76 | 1.62 | 1.54 | 5.95 | 5.7 | 5.69 | 6.31 | 6.32 | 6.5 | 0.41 | 0.46 | 0.4 | 0.47 | 0.45 | 0.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 627447 | 1136 | 614731 | 1206 | 652365.718 | 1729.733 | 6 | 5.71 | 5.85 | 6.35 | 6.3 | 6.5 | 5.95 | 5.7 | 5.69 | 6.31 | 6.32 | 6.5 | 825000 | 2000 | 867000 | 1000 | 1686734 | 4266 | 1689000 | 1682468 | 12.9167 | 6.1183 | 1.4733 | 6.0783 | 0.44667 | 24.08% | 7.349% | 38.785 | 50.3667 | 3.465 | 6.6383 | 1697237.1 | 1685600 | 2008318.0881 | 83.93% | 70 | 20230
2024-05-08 | 2025 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 335090.89 | 6:18 | 19:20 | 12321.5 | 12893 | 12802.4 | 12777.4 | 12894.2 | 13000.2 | 13034.4 | 13336.8 | 12861.5 | 12785.9 | 12799.7 | 12870.7 | 12977.9 | 12862.4 | 12969.4 | 13056.8 | 12976.6 | 12987.6 | 13039.5 | 13096.8 | 13073.2 | 13066.8 | 12809.6 | 12927.5 | 12774 | 11295.3 | 12793.5 | 12785.1 | 13016.7 | 12925.8 | 12831.4 | 12955.5 | 12946.7 | 12913.6 | 13170 | 13066.2 | 13084.2 | 12956.5 | 13003 | 12926.3 | 13776.7 | 12865.2 | 13590.8 | 12626 | 13125.7 | 13942.6 | 12525.2 | 13727.2 | 11997.4 | 12304.3 | 13050.4 | 12477.3 | 13348.5 | 12208.5 | 13341.3 | 12108.5 | 12048 | 13507.6 | 12009.5 | 13431.2 | 13270.6 | 11956.9 | 13061.3 | 12524.7 | 12829.9 | 12127.2 | 12751.4 | 13196.3 | 13369.2 | 12359.8 | 13089.1 | 11729.9 | 12977.8 | 12854.5 | 12096.2 | 13242.8 | 11875.3 | 13390 | 12064.6 | 13196.8 | 12520.4 | 13280.4 | 12573.1 | 13575.2 | 12509.9 | 13086.7 | 12476.6 | 11025.5 | 13257.1 | 12934.5 | 12163.3 | 13632 | 13323.3 | 12559.6 | 12424.6 | 13411.9 | 12311.6 | 12744.2 | 13541.6 | 12207.5 | 13579.8 | 12196.7 | 13395 | 12482 | 13408 | 11838.1 | 13498.1 | 12441.8 | 13360 | 12383.9 | 13444.8 | 12604.6 | 12167.4 | 13267.8 | 12412.6 | 12137.2 | 13362.5 | 13459.8 | 13312.5 | 12447.8 | 13397.1 | 12271.7 | 13175 | 12365.5 | 12862.5 | 11444.8 | 13201.6 | 12231.9 | 12462.6 | 12495.2 | 12211.4 | 10602.8 | 12269.7 | 10878 | 12347.6 | 12377.6 | 13815.9 | 12575.2 | 13729.5 | 12685 | 13765.5 | 12666.6 | 12852.6 | 12608.7 | 13630.9 | 13895 | 13857.1 | 13787.2 | 11335.2 | 13285.5 | 12978.2 | 13843.6 | 13492.3 | 13597.8 | 13871.5 | 13812.8 | 13677.8 | 12759.2 | 13903.1 | 12953.6 | 40.9464 | 40.6425 | 40.6582 | 40.696 | 41.0853 | 40.795 | 0 | 53.3 | 0 | 0 | 53.8 | 53.6 | 3.8568 | 3.8833 | 3.5695 | 3.9515 | 3.9618 | 3.0053 | 7.72 | 7.659 | 7.707 | 7.827 | 7.341 | 8.127 | 7.5852 | 7.6209 | 7.6632 | 7.5645 | 7.593 | 7.6972 | 1.725 | 1.8688 | 1.5915 | 2.1233 | 1.9474 | 1.7754 | 7.4897 | 7.5702 | 7.4009 | 7.4114 | 7.5542 | 7.6154 | 0.52264 | 0.59915 | 0.51792 | 0.55337 | 0.53941 | 0.58262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 628470 | 1138 | 615755 | 1208 | 654408.051 | 1734 | 7.5852 | 7.6209 | 7.6632 | 7.5645 | 7.593 | 7.6972 | 7.4897 | 7.5702 | 7.4009 | 7.4114 | 7.5542 | 7.6154 | 1023000 | 2000 | 1024000 | 2000 | 2042333 | 4267 | 2043000 | 2038066 | 13.0333 | 7.6207 | 1.8386 | 7.507 | 0.55252 | 24.13% | 7.36% | 40.8039 | 53.5667 | 3.7047 | 7.7302 | 2056376 | 2041667 | 2444412.9483 | 83.52% | 61 | 0
2024-05-09 | 2025 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 335090.89 | 6:17 | 19:20 | 11329.9 | 11760.1 | 11700.1 | 11731.1 | 11817.9 | 11877.5 | 11891.2 | 12203.5 | 11795.2 | 11772.5 | 11729.3 | 11799.9 | 11865.9 | 11741.7 | 11963.3 | 11998.7 | 11955.1 | 12036.6 | 12168.8 | 12159 | 12358.5 | 12273.9 | 12319.4 | 12366.6 | 12211.6 | 10810.7 | 11995.1 | 12119.2 | 12461.8 | 12417.6 | 12276 | 12434.3 | 12336.8 | 12382.7 | 12631.3 | 12549.7 | 12527.9 | 12313.6 | 12271.4 | 12175.4 | 13032.4 | 12248.9 | 12957.7 | 12093.9 | 12560.8 | 13301.7 | 11947.3 | 12910.6 | 11118 | 11420.5 | 12039.5 | 11743.6 | 12333.8 | 11282.6 | 12544.4 | 11524.7 | 11432 | 12708.7 | 11157.6 | 12540.4 | 12359.1 | 11097.2 | 12279 | 11843.6 | 12187.2 | 11490.8 | 12070.1 | 12422.2 | 12597.4 | 11693.8 | 12341.3 | 11152.1 | 12228.9 | 12089.3 | 11457.4 | 12441.2 | 11275.4 | 12572.6 | 11435.9 | 12391.5 | 11821.6 | 12488.8 | 11858.6 | 12758.8 | 11797.1 | 12316.5 | 11772.1 | 10414 | 12556.2 | 12175.9 | 11567.4 | 12864 | 12567.1 | 11865.6 | 11752.6 | 12662.6 | 11736.4 | 12205.7 | 12927 | 11721.2 | 12907.2 | 11704.8 | 12822.8 | 12003.9 | 12910.5 | 11441 | 13021.2 | 12043 | 12949.6 | 12064.7 | 13031.9 | 12242.3 | 11662.1 | 12630.7 | 11947.2 | 11661.7 | 12794 | 12818.4 | 12751.1 | 11943.8 | 12815.6 | 11829.4 | 12681.9 | 11940 | 12327.5 | 11022.9 | 12664.8 | 11787.5 | 11978.3 | 11989.9 | 11797 | 10225.2 | 11704.3 | 10338.9 | 11757.5 | 11764.9 | 13026.7 | 11882.6 | 12991.2 | 12050.7 | 12986.9 | 11970.5 | 12139.1 | 11960 | 12809.1 | 13078.4 | 13119.7 | 13042.4 | 13018 | 13002.3 | 12219.8 | 13053.8 | 12725.6 | 12742.1 | 12927.5 | 12885.1 | 12809.5 | 11972.7 | 13114 | 12247.8 | 40.1983 | 40.0486 | 40.055 | 39.961 | 40.2788 | 40.208 | 0 | 53.2 | 0 | 0 | 53 | 53.3 | 4.2806 | 4.4085 | 4.3579 | 4.3694 | 4.415 | 3.8881 | 7.542 | 7.588 | 8.468 | 7.034 | 7.853 | 8.22 | 6.9864 | 7.4287 | 7.3892 | 7.2157 | 7.3191 | 7.3342 | 1.6177 | 1.7893 | 1.572 | 2.0721 | 1.8701 | 1.6653 | 6.8864 | 7.3655 | 7.1101 | 7.1059 | 7.2478 | 7.2243 | 0.4774 | 0.57305 | 0.49283 | 0.52685 | 0.5181 | 0.55184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 629431 | 1139 | 616733 | 1209 | 656340.5 | 1738.267 | 6.9864 | 7.4287 | 7.3892 | 7.2157 | 7.3191 | 7.3342 | 6.8864 | 7.3655 | 7.1101 | 7.1059 | 7.2478 | 7.2243 | 961000 | 1000 | 978000 | 1000 | 1932449 | 4267 | 1937000 | 1928182 | 13.05 | 7.2789 | 1.7644 | 7.1567 | 0.52335 | 24.24% | 7.313% | 40.1249 | 53.1667 | 4.2866 | 7.7842 | 1946438.1 | 1931600 | 2339433.0551 | 82.57% | 63 | 2961
2024-05-10 | 2025 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 335090.89 | 6:17 | 19:20 | 11936.2 | 12434 | 12405.2 | 12368.5 | 12539 | 12549.5 | 12561.4 | 12930.9 | 12463.8 | 12456.7 | 12343 | 12434.1 | 12508.9 | 12417.7 | 12489.7 | 12523.4 | 12393.2 | 12405.2 | 12482.5 | 12533.1 | 12520.9 | 12480.9 | 12248.6 | 12349.4 | 12195.6 | 10766.2 | 12203.7 | 12207.1 | 12485 | 12409.8 | 12286 | 12473.7 | 12549.9 | 12532.8 | 12647.7 | 12568.9 | 12579.7 | 12435.8 | 12467 | 12406.7 | 13250.8 | 12252 | 13099.9 | 12057.2 | 12694.1 | 13641.7 | 12021.9 | 13296.8 | 11500 | 11794.7 | 12510.7 | 11897.2 | 12787.3 | 11619.2 | 12769.9 | 11541.8 | 11508.4 | 12948.6 | 11523 | 12916.4 | 12747.1 | 11460.2 | 12512.6 | 12002.9 | 12200.8 | 11487.6 | 12129.6 | 12577.9 | 12852.7 | 11757 | 12622 | 11249.7 | 12431.7 | 12276.5 | 11544.8 | 12722.8 | 11342.2 | 12857.7 | 11565 | 12722.2 | 11866.7 | 12691.5 | 11962.8 | 12970.3 | 12417 | 12017 | 11830.6 | 10493.4 | 12739.4 | 12355.3 | 11606.9 | 13083.8 | 12760.5 | 12001.4 | 11883.9 | 12809.3 | 11769.7 | 12165.5 | 12979.7 | 11648.8 | 12959.4 | 11609.5 | 12717.2 | 11834.9 | 12723.7 | 11208.8 | 12811.9 | 11760.2 | 12707.1 | 11769.3 | 12847.8 | 11991.1 | 11602.1 | 12645.1 | 11752.1 | 11520.8 | 12686.6 | 12805.8 | 12641.5 | 11820.3 | 12770.9 | 11662.7 | 12536.4 | 11746.2 | 12369.9 | 10964.3 | 12616.8 | 11707.6 | 11866.9 | 11897.6 | 11710.6 | 10112 | 11649.2 | 10267.7 | 11726.7 | 11732.1 | 13316.9 | 11991.2 | 13334.6 | 12177.8 | 13216.4 | 11979.3 | 12176.1 | 11941.1 | 13131.3 | 13407.4 | 13367.1 | 13304.9 | 13283.2 | 13299.9 | 12405.9 | 13344.9 | 13090.9 | 13182.5 | 13405.9 | 13359.5 | 13362.3 | 12357.8 | 13374 | 12420.9 | 38.8414 | 38.5254 | 38.5105 | 38.428 | 38.5916 | 35.5258 | 0 | 51.1 | 0 | 0 | 49.3 | 47.9 | 4.9962 | 5.0922 | 5.1432 | 5.0679 | 5.0148 | 4.2813 | 8.481 | 8.706 | 9.1 | 8.573 | 8.85 | 8.329 | 7.2245 | 7.2172 | 7.2837 | 7.1751 | 7.1102 | 7.2876 | 1.6358 | 1.7683 | 1.5042 | 1.9915 | 1.8189 | 1.6554 | 7.1309 | 7.1527 | 7.0088 | 6.9011 | 7.0387 | 7.1264 | 0.50434 | 0.58081 | 0.49937 | 0.5327 | 0.5259 | 0.56081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 630413 | 1141 | 617715 | 1211 | 658299.251 | 1742.467 | 7.2245 | 7.2172 | 7.2837 | 7.1751 | 7.1102 | 7.2876 | 7.1309 | 7.1527 | 7.0088 | 6.9011 | 7.0387 | 7.1264 | 982000 | 2000 | 982000 | 2000 | 1958751 | 4200 | 1960000 | 1954551 | 13.05 | 7.2164 | 1.729 | 7.0598 | 0.53399 | 23.96% | 7.564% | 38.0705 | 49.4333 | 4.9326 | 8.6732 | 1972724.1 | 1958067 | 2346314.6775 | 83.45% | 55 | 0
2024-05-11 | 2025 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 335090.89 | 6:20 | 19:19 | 11193.1 | 11651.3 | 11638.7 | 11660.9 | 11694.2 | 11668.1 | 11751.7 | 12025.6 | 11696.8 | 11791.2 | 11430.3 | 11616.2 | 11470.7 | 11472.5 | 11526 | 11548.3 | 11412.6 | 11406.2 | 11488.7 | 11521.1 | 11475.8 | 11484 | 11191 | 11317.8 | 11189.5 | 9806.1 | 11198.3 | 11176.9 | 11458 | 11365.5 | 11214.9 | 11432.8 | 11417.6 | 11439.8 | 11575.2 | 11478.7 | 11530.4 | 11391 | 11420 | 11322.2 | 12336.8 | 11326.1 | 12223.6 | 11115.1 | 11810.2 | 12788.5 | 11097.3 | 12365 | 10520.1 | 10818.1 | 11538.8 | 10947 | 11844.3 | 10717.9 | 11796.2 | 10503.7 | 10564.3 | 12045.7 | 10591.6 | 12029 | 11915.1 | 10586.5 | 11757.7 | 11252.9 | 11258.8 | 10561.2 | 11213.3 | 11711.1 | 11972.7 | 10844.4 | 11657.1 | 10265.1 | 11549.9 | 11389.5 | 10710.9 | 11900.2 | 10520.2 | 12105.1 | 10748.8 | 11972 | 10950.2 | 11833.7 | 10999.9 | 12070.4 | 10844.2 | 11542.7 | 10828.7 | 9500.5 | 11654.7 | 11268.3 | 10474.9 | 11985.2 | 11703.7 | 10874 | 10727.7 | 11754.1 | 10674.3 | 11026.8 | 11928.3 | 10549.3 | 11969.9 | 10543.9 | 11714.3 | 10800.4 | 11848.3 | 10257.3 | 11933.6 | 10781 | 11811.8 | 10797.8 | 11899.1 | 10966.9 | 10532.9 | 11677.7 | 10735 | 10490.9 | 11762.6 | 11862.9 | 11706.8 | 10805.7 | 11828.9 | 10649.9 | 11557.5 | 10724.2 | 11413.5 | 9996 | 11594.2 | 10663 | 10835.1 | 10877.6 | 10683.2 | 9226.6 | 10510.1 | 9486.9 | 10682.9 | 10691.9 | 12163.5 | 10836.9 | 12185.7 | 11066.8 | 12142.4 | 10947.8 | 11134.6 | 10891.3 | 11994.2 | 12256.6 | 12252.5 | 12166.1 | 12090.5 | 12085.7 | 11160.4 | 12162.3 | 12272.5 | 12287.1 | 12455.7 | 12359.8 | 12315.1 | 11275.1 | 12330.9 | 11305.6 | 36.93 | 36.75 | 36.67 | 36.58 | 36.56 | 22.49 | 0 | 49.4 | 0 | 0 | 40.1 | 30.09 | 5.35 | 5.4 | 5.28 | 5.44 | 5.55 | 2.45 | 10.06 | 10.45 | 9.66 | 10.41 | 10.81 | 8.48 | 6.64 | 6.61 | 6.63 | 6.56 | 6.46 | 3.9 | 1.53 | 1.63 | 1.39 | 1.87 | 1.68 | 0.99 | 6.55 | 6.51 | 6.42 | 6.32 | 6.43 | 3.89 | 0.46 | 0.52 | 0.46 | 0.49 | 0.47 | 0.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 631323 | 1142 | 618615 | 1212 | 660103.5 | 1746.667 | 6.64 | 6.61 | 6.63 | 6.56 | 6.46 | 3.9 | 6.55 | 6.51 | 6.42 | 6.32 | 6.43 | 3.89 | 910000 | 1000 | 900000 | 1000 | 1804249 | 4200 | 1808000 | 1800049 | 12.9833 | 6.1333 | 1.515 | 6.02 | 0.44833 | 24.7% | 7.447% | 34.33 | 39.8633 | 4.9117 | 9.9783 | 1816072.5 | 1803600 | 2160089.8351 | 83.5% | 71 | 2655
2024-05-12 | 2025 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 335090.89 | 6:12 | 19:23 | 12385.7 | 12881.1 | 12860.2 | 12815.8 | 12993.4 | 13053.8 | 13057.8 | 13548.1 | 12964.5 | 12956 | 12858.3 | 12939.1 | 12987.7 | 12935.1 | 12980.5 | 12995.9 | 12964.8 | 12993.5 | 13027 | 13042.7 | 13048.6 | 13037.7 | 12823.9 | 12922.4 | 12761.7 | 11242.9 | 12741.1 | 12751.1 | 13055.4 | 12948.4 | 12822.2 | 13021.2 | 13055.8 | 13050.3 | 13218.6 | 13142 | 13118 | 12950 | 12979.6 | 12885.9 | 13977.5 | 12912.7 | 13769.8 | 12649.8 | 13328.6 | 14343.7 | 12625.9 | 13958.6 | 12000.5 | 12277.9 | 13096.2 | 12479.8 | 13406.1 | 12209.5 | 13366.4 | 12070.9 | 11985.1 | 13532.9 | 11978.2 | 13474.1 | 13317.6 | 11934.4 | 13133.7 | 12556.6 | 12687.3 | 11856.1 | 12595.6 | 13010.2 | 13366.3 | 12125.6 | 13086.7 | 11612.8 | 12925.7 | 12694.1 | 12033 | 13159.2 | 11753.7 | 13439.3 | 12002.4 | 13157.7 | 12259.4 | 13118.6 | 12311.5 | 13380.5 | 12188.6 | 12855.8 | 12166.9 | 10725.3 | 13029.7 | 12640.7 | 11912.2 | 13434.9 | 13112.5 | 12273.1 | 12163 | 13201 | 11959.2 | 12386.1 | 13320.6 | 11936 | 13447.8 | 11910.7 | 13202.9 | 12213.2 | 13283.7 | 11604.2 | 13355.6 | 12179.1 | 13183.8 | 12173.7 | 13259.1 | 12399.8 | 11929.2 | 13130.3 | 12144.8 | 11902.4 | 13130.1 | 13348.5 | 13084.5 | 12279.2 | 13255 | 12073 | 12906.9 | 12116.3 | 12758.1 | 11308.6 | 13041.1 | 12120.7 | 12271.2 | 12290.6 | 12166 | 10494.4 | 12024.1 | 10705 | 12274.9 | 12267.3 | 13929.3 | 12563.1 | 13967.9 | 12776.1 | 13837.9 | 12591.6 | 12785.8 | 12493.1 | 13676.5 | 13972.4 | 13922.8 | 13856.4 | 13841.8 | 13864.4 | 12956.7 | 13927.6 | 13732.9 | 13789.8 | 13997.2 | 13933.8 | 13929.9 | 12892 | 13930.8 | 12913.6 | 37.064 | 36.7278 | 36.9417 | 36.6884 | 36.8567 | 37.0282 | 0 | 51.8 | 0 | 0 | 51.7 | 52.1 | 3.5702 | 3.5578 | 3.4397 | 3.4861 | 3.5566 | 2.7834 | 9.612 | 9.074 | 9.352 | 8.89 | 8.596 | 9.6 | 7.6359 | 7.7035 | 7.6978 | 7.5403 | 7.4739 | 7.7985 | 1.7371 | 1.8701 | 1.611 | 2.1171 | 1.9074 | 1.7671 | 7.4898 | 7.5139 | 7.4066 | 7.2348 | 7.3898 | 7.579 | 0.52662 | 0.60612 | 0.52095 | 0.55485 | 0.5454 | 0.59151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 632347 | 1144 | 619632 | 1213 | 662139.252 | 1750.933 | 7.6359 | 7.7035 | 7.6978 | 7.5403 | 7.4739 | 7.7985 | 7.4898 | 7.5139 | 7.4066 | 7.2348 | 7.3898 | 7.579 | 1024000 | 2000 | 1017000 | 1000 | 2035752 | 4266 | 2038000 | 2031486 | 13.1833 | 7.6417 | 1.835 | 7.4356 | 0.55758 | 24.01% | 7.499% | 36.8844 | 51.8667 | 3.399 | 9.1873 | 2050404.8 | 2034267 | 2461839.0021 | 82.63% | 68 | 0
2024-05-13 | 2025 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 335090.89 | 6:15 | 19:21 | 11963.5 | 12232.4 | 12095.2 | 12120.3 | 12121.2 | 12109.6 | 12175.1 | 12567.6 | 12384.1 | 12561.5 | 12119.7 | 12280.7 | 12114.9 | 12143.3 | 11838.2 | 11941.8 | 11769.8 | 11822.4 | 12005.4 | 12121.5 | 11988.4 | 12018 | 11817.4 | 11879.9 | 12175.1 | 10811 | 12077.4 | 11969.7 | 12182.9 | 12105.2 | 12120.9 | 12325.1 | 12624.2 | 12608.2 | 12642.9 | 12572.5 | 12559.7 | 12374.6 | 12391.1 | 12402.4 | 12520.3 | 11600.1 | 12417.7 | 11423 | 12152.8 | 13087 | 11533.1 | 12573.7 | 11491.1 | 11784.7 | 12473.7 | 12083.5 | 12682.9 | 11450 | 12890 | 11704.9 | 11666.7 | 13133.1 | 11512.5 | 12998 | 12862.3 | 11508.7 | 12758.6 | 12318.2 | 12544 | 11932.7 | 12488.4 | 13042.3 | 13091.3 | 12213.3 | 12830.2 | 11627 | 12703.6 | 12649.2 | 11896.5 | 13038.1 | 11733.8 | 13157.4 | 11897.2 | 12989.4 | 12475.7 | 13206.2 | 12545.1 | 13466.1 | 12444.4 | 13061.1 | 12385.1 | 10975.1 | 13180.2 | 12854.8 | 12020.3 | 13404.3 | 13061.1 | 12284.1 | 12110.2 | 13176.2 | 12214.6 | 12637.8 | 13349.7 | 12041.5 | 13269 | 11992.4 | 12999.9 | 12214.5 | 12909.4 | 11466.6 | 12961.4 | 11958.9 | 12728.1 | 11792.8 | 12731.2 | 11998.2 | 12029.2 | 13015.3 | 12106.7 | 11861.7 | 12950.8 | 13161.2 | 12890.1 | 12205.4 | 13118.9 | 12022.8 | 12655 | 11872.9 | 12465 | 11220.2 | 12945.8 | 12026.3 | 12233.1 | 12260.6 | 12029.6 | 10417.4 | 12021 | 10638.7 | 12061.8 | 12065.7 | 13543.1 | 12348.3 | 13443.4 | 12450.7 | 13428.8 | 12307.3 | 12469.9 | 12259.4 | 13319.8 | 13539.1 | 13578.3 | 13515.4 | 13527.6 | 13506.4 | 12632.2 | 13503.8 | 13245.9 | 13332.3 | 13535.5 | 13457.2 | 13445.7 | 12541 | 13538.2 | 12666.5 | 38.4 | 38.11 | 38.06 | 38.13 | 38.45 | 38.27 | 0 | 52 | 0 | 0 | 52.3 | 53.16 | 3.61 | 3.52 | 3.47 | 3.76 | 3.67 | 2.56 | 6.67 | 6.87 | 6.35 | 7.22 | 6.42 | 7.17 | 7.17 | 7.25 | 6.97 | 7.47 | 7.49 | 7.63 | 1.65 | 1.74 | 1.48 | 2.13 | 1.91 | 1.72 | 7.02 | 7.09 | 6.74 | 7.2 | 7.38 | 7.43 | 0.5 | 0.58 | 0.48 | 0.55 | 0.54 | 0.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 633321 | 1146 | 620637 | 1215 | 664113 | 1755.267 | 7.17 | 7.25 | 6.97 | 7.47 | 7.49 | 7.63 | 7.02 | 7.09 | 6.74 | 7.2 | 7.38 | 7.43 | 974000 | 2000 | 1005000 | 2000 | 1973748 | 4334 | 1975000 | 1969414 | 13.1 | 7.33 | 1.7717 | 7.1433 | 0.53667 | 24.17% | 7.513% | 38.2367 | 52.4867 | 3.4317 | 6.7833 | 1987922.8 | 1971800 | 2347876.7908 | 83.98% | 66 | 700
2024-05-14 | 2025 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 335090.89 | 6:11 | 19:23 | 10461.4 | 11001.1 | 11020.3 | 11025.9 | 11061.3 | 11120 | 11185.7 | 11480.1 | 11032.1 | 11000.7 | 10925.2 | 11031.2 | 10989.6 | 10968.4 | 11072.4 | 11060.5 | 11030.1 | 11114.6 | 11101.4 | 11131.6 | 11171.7 | 11143.7 | 10888.5 | 11015.6 | 10856.5 | 9503.2 | 10849.1 | 10839 | 11152.4 | 11029 | 10846.9 | 11063.8 | 11064.8 | 11072.6 | 11217 | 11113.7 | 11148.1 | 11024.2 | 11054.4 | 10979 | 11829.4 | 10839.6 | 11683.5 | 10678.3 | 11389.1 | 12143.1 | 10663.1 | 11829 | 10103.2 | 10351.1 | 11123.5 | 10560.3 | 11411.4 | 10299.8 | 11401.3 | 10197 | 10172.9 | 11585.4 | 10104.5 | 11490.9 | 11360.9 | 10086.3 | 11250.7 | 10704.9 | 10931.8 | 10117.3 | 10812.6 | 11155.5 | 11488.7 | 10315.3 | 11127.1 | 9739.9 | 11133.7 | 10800.1 | 10265.4 | 11261.3 | 10004.1 | 11539.1 | 10248.2 | 11335.2 | 10365 | 11191.7 | 10364.5 | 11421.7 | 10297.2 | 10955.5 | 10351.9 | 9083.9 | 11163 | 10801.6 | 10055.9 | 11479.7 | 11252.3 | 10447.6 | 10346.7 | 11339.4 | 10249.7 | 10597.5 | 11418.4 | 10115.8 | 11444.2 | 10121.4 | 11263.2 | 10376.9 | 11296.5 | 9831.6 | 11346 | 10288.4 | 11225.7 | 10278.6 | 11300.1 | 10426.4 | 10062.9 | 11081.7 | 10190.3 | 9993 | 11112 | 11147.8 | 11139.2 | 10221.7 | 11214.9 | 10166.4 | 11007.4 | 10259.2 | 10962.2 | 9574.7 | 11097.7 | 10162.7 | 10326.9 | 10354.6 | 10195 | 8810.6 | 10266.3 | 9046 | 10043.8 | 10022.7 | 11284.8 | 10168.5 | 11102.1 | 10213.6 | 11280.6 | 10165.3 | 10394.9 | 10143 | 10844.5 | 11082.9 | 11116.1 | 11113.4 | 11154.4 | 11201 | 10323.3 | 11108.6 | 11001.1 | 10990.2 | 10991.4 | 10931.7 | 10923.6 | 10060.8 | 11178.1 | 10171.7 | 34.842 | 34.5655 | 34.5006 | 34.5106 | 34.7871 | 34.5759 | 0 | 45.9 | 0 | 0 | 45.5 | 45.5 | 4.9219 | 4.8559 | 4.6881 | 4.9362 | 4.9889 | 4.1847 | 12.317 | 13.892 | 13.979 | 13.608 | 13.854 | 14.193 | 6.2647 | 6.3464 | 6.3551 | 6.2942 | 6.2138 | 6.0622 | 1.4812 | 1.4652 | 1.3508 | 1.8249 | 1.5132 | 1.2146 | 6.1368 | 6.2516 | 6.1805 | 6.2339 | 6.0923 | 5.8718 | 0.43074 | 0.49757 | 0.42962 | 0.46208 | 0.43869 | 0.44894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 634193 | 1147 | 621484 | 1216 | 665825.852 | 1759.533 | 6.2647 | 6.3464 | 6.3551 | 6.2942 | 6.2138 | 6.0622 | 6.1368 | 6.2516 | 6.1805 | 6.2339 | 6.0923 | 5.8718 | 872000 | 1000 | 847000 | 1000 | 1712852 | 4266 | 1717000 | 1708586 | 13.2 | 6.2561 | 1.475 | 6.1278 | 0.45127 | 23.58% | 7.364% | 34.6303 | 45.6333 | 4.7626 | 13.6405 | 1725284.6 | 1711400 | 2037823.7972 | 83.98% | 55 | 95049
2024-05-15 | 2025 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 335090.89 | 6:15 | 19:23 | 12110.7 | 12667.5 | 12653.3 | 12598.9 | 12784.6 | 12841.7 | 12818 | 13280.4 | 12739.4 | 12795.1 | 12593.4 | 12725.7 | 12692.3 | 12660.2 | 12694.6 | 12759.7 | 12608.2 | 12555 | 12643.4 | 12706.6 | 12621.1 | 12593.6 | 12382.2 | 12490.8 | 12376.8 | 10792.1 | 12357.8 | 12296.2 | 12699.1 | 12573.6 | 12348.4 | 12658.2 | 12608.5 | 12638.5 | 12830.1 | 12702.6 | 12755.1 | 12497.5 | 12482.8 | 12455.4 | 13040.7 | 11923.9 | 12845.8 | 11709.9 | 12322 | 13352.4 | 11634.7 | 13072.2 | 11611.8 | 11903.8 | 12788.3 | 12043.3 | 13104.1 | 11799.8 | 13044.6 | 11619.5 | 11603.7 | 13244 | 11625.8 | 13270.5 | 13135.1 | 11610.5 | 12876.8 | 12202.5 | 12328.8 | 11553 | 12249.2 | 12817.8 | 13136.6 | 11795.2 | 12942.4 | 11332.5 | 12675.9 | 12382.3 | 11706 | 13003.3 | 11479.8 | 13251 | 11713.4 | 13061.8 | 11959.5 | 12910.7 | 12049.3 | 13272.2 | 11942.4 | 12748.5 | 11918.1 | 10515.1 | 12871.8 | 12465.9 | 11568.6 | 13226.1 | 12902.1 | 11908.5 | 11738.5 | 12838.2 | 11382 | 11821.8 | 12760.7 | 11256 | 12747.4 | 11211.9 | 12498.2 | 11476.8 | 12629.4 | 10896 | 12715.2 | 11473.7 | 12556.5 | 11463.6 | 12622.8 | 11674 | 11304.5 | 12581.4 | 11492.4 | 11264.1 | 12626.5 | 12843.5 | 12578.3 | 11703 | 12840.7 | 11556.6 | 12422.2 | 11540.1 | 12340.9 | 10800 | 12607.3 | 11600.1 | 11737 | 11780.3 | 11662.6 | 10048 | 11578.8 | 10291 | 11787.7 | 11804.7 | 13538 | 12005.3 | 13533.4 | 12215.7 | 13464.7 | 12074.5 | 12297.9 | 12012.3 | 13336.5 | 13669.1 | 13448.6 | 13523.5 | 13506.5 | 13504.5 | 12462.4 | 13598 | 13391.2 | 13486.6 | 13699.5 | 13643.5 | 13619.7 | 12463.9 | 13549.8 | 12457.5 | 38.1475 | 38.0397 | 37.9601 | 37.9037 | 37.9895 | 38.2138 | 0 | 52.3 | 0 | 0 | 52.2 | 52.7 | 3.8168 | 3.908 | 3.7605 | 3.9367 | 3.9529 | 3.1608 | 7.132 | 7.86 | 9.112 | 7.804 | 8.466 | 7.612 | 7.3752 | 7.4295 | 7.24 | 7.29 | 7.2039 | 7.4941 | 1.6079 | 1.6714 | 1.385 | 1.9204 | 1.7042 | 1.6427 | 7.1861 | 7.2697 | 6.9527 | 7.2123 | 6.968 | 7.3214 | 0.52633 | 0.59212 | 0.48896 | 0.55584 | 0.52526 | 0.5814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 635186 | 1149 | 622465 | 1217 | 667795.586 | 1763.933 | 7.3752 | 7.4295 | 7.24 | 7.29 | 7.2039 | 7.4941 | 7.1861 | 7.2697 | 6.9527 | 7.2123 | 6.968 | 7.3214 | 993000 | 2000 | 981000 | 1000 | 1969734 | 4400 | 1971000 | 1965334 | 13.1333 | 7.3388 | 1.6553 | 7.1517 | 0.54498 | 22.56% | 7.62% | 38.0424 | 52.4 | 3.7559 | 7.9977 | 1983219.6 | 1968667 | 2357001.3654 | 83.52% | 66 | 0
2024-05-16 | 2025 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 335090.89 | 6:15 | 19:23 | 11734.1 | 12209.8 | 12223.2 | 12184.1 | 12400.3 | 12379.5 | 12317.7 | 12694.8 | 12246.9 | 12205.5 | 12135.8 | 12210.4 | 12392.2 | 12199.3 | 12531.3 | 12501.3 | 12477 | 12454.1 | 12431.9 | 12486.9 | 12499.9 | 12465.4 | 12300.1 | 12388.6 | 12095.1 | 10704.1 | 12151 | 12124.2 | 12452.8 | 12348.4 | 12194.4 | 12358 | 12223.8 | 12230.7 | 12391.5 | 12314 | 12402.3 | 12269.1 | 12294.1 | 12173.9 | 13257.2 | 12287.3 | 13087.3 | 12036.3 | 12557.8 | 13502.1 | 12001.4 | 13255.5 | 11364.1 | 11608.6 | 12403.7 | 11776.5 | 12708.5 | 11682.2 | 12527 | 11456.3 | 11208.2 | 12514.2 | 11264.9 | 12527.4 | 12379.5 | 11238.6 | 12114.1 | 11608.2 | 11768.6 | 11073.4 | 11684.4 | 12062.7 | 12286.8 | 11280.3 | 12083 | 10778.5 | 11924.2 | 11648.9 | 11115.2 | 12033.2 | 10812.1 | 12361.4 | 11092.1 | 12119.7 | 11365.1 | 12113.8 | 11316.9 | 12371.3 | 11304.3 | 11916 | 11366.7 | 10012 | 12235.9 | 11867.1 | 11231.1 | 12689.7 | 12472.8 | 11753.7 | 11607.3 | 12465.3 | 11436 | 11857.7 | 12726.8 | 11447.9 | 12848.8 | 11515.1 | 12702.4 | 11794.8 | 12770.8 | 11211.3 | 12863.7 | 11875.9 | 12729.5 | 11787.1 | 12899.1 | 12042.6 | 11378.8 | 12578.8 | 11752.2 | 11487 | 12786.6 | 13003.2 | 12811.7 | 12132.5 | 13133.2 | 11997.7 | 12699.3 | 11931.4 | 12411.5 | 11149.1 | 12971.5 | 11985.6 | 12164.7 | 12177.4 | 11989.3 | 10373.6 | 11892.5 | 10489.1 | 11883.2 | 11920.2 | 13370 | 12149.9 | 13207.8 | 12166.4 | 13351 | 12181.1 | 12383.7 | 12146.5 | 13133.6 | 13427.8 | 13244.5 | 13258.6 | 13257.7 | 13307.1 | 12483.7 | 13332.3 | 12742.6 | 12884.6 | 13245.6 | 13219.2 | 13167.8 | 12279.7 | 13101.9 | 12245.5 | 40.9967 | 40.686 | 40.6262 | 40.66 | 40.8874 | 40.8806 | 0 | 54.1 | 0 | 0 | 54.1 | 54.4 | 3.4296 | 3.3563 | 3.1034 | 3.4319 | 3.214 | 1.9689 | 8.265 | 7.47 | 7.919 | 8.003 | 8.502 | 6.912 | 7.2562 | 7.4723 | 7.554 | 7.0862 | 7.3284 | 7.5019 | 1.6059 | 1.7035 | 1.4619 | 1.8923 | 1.8088 | 1.6633 | 7.0517 | 7.3062 | 7.2512 | 6.9679 | 7.1249 | 7.2984 | 0.52972 | 0.60755 | 0.51742 | 0.55551 | 0.54608 | 0.59173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 636151 | 1151 | 623443 | 1219 | 669732.986 | 1768.2 | 7.2562 | 7.4723 | 7.554 | 7.0862 | 7.3284 | 7.5019 | 7.0517 | 7.3062 | 7.2512 | 6.9679 | 7.1249 | 7.2984 | 965000 | 2000 | 978000 | 2000 | 1937400 | 4267 | 1939000 | 1933133 | 13.1333 | 7.3665 | 1.6893 | 7.1667 | 0.558 | 22.93% | 7.786% | 40.7895 | 54.2 | 3.084 | 7.8452 | 1950276.1 | 1936134 | 2335599.5332 | 82.9% | 75 | 6793
2024-05-17 | 2025 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 335090.89 | 6:17 | 19:22 | 11946.9 | 12528.8 | 12423.2 | 12324.2 | 12574.8 | 12622.7 | 12671.5 | 12984.6 | 12580.1 | 12417.7 | 12480.3 | 12603.8 | 12586.2 | 12483.5 | 12629.9 | 12616.5 | 12617 | 12623.6 | 12671.3 | 12695.9 | 12737.3 | 12724.5 | 12580.4 | 12651.1 | 12553.7 | 11017.4 | 12474.6 | 12469.3 | 12810 | 12695.4 | 12566.9 | 12722.7 | 12686.9 | 12687 | 12909.1 | 12781.3 | 12770.1 | 12654.7 | 12716.8 | 12647.6 | 13444.6 | 12529.8 | 13312.4 | 12282.6 | 12843.1 | 13621.5 | 12335.8 | 13474.6 | 11624.4 | 11934.1 | 12719.9 | 12096.6 | 12955 | 11767.2 | 12999.3 | 11765.8 | 11630 | 13074.2 | 11634.7 | 13082 | 12932.9 | 11592.7 | 12721.7 | 12100.2 | 12405.5 | 11615.4 | 12377.5 | 12701.7 | 12993.2 | 11883.4 | 12852.3 | 11366.3 | 12668.6 | 12398.3 | 11750.9 | 12839.2 | 11482.1 | 13010.5 | 11576.7 | 12675 | 11943.2 | 12770.5 | 11866.8 | 13006.9 | 11797.2 | 12452.5 | 11882.7 | 10420.5 | 12787.4 | 12438.5 | 11695.9 | 13179.7 | 12930 | 12142.7 | 12038.6 | 12968.9 | 11812.2 | 12240.6 | 13044.6 | 11694 | 13155.9 | 11722.7 | 13005.7 | 11998.1 | 13046.6 | 11400.2 | 13098 | 11970.1 | 12989.8 | 11939.7 | 13037.5 | 12100.4 | 11645.1 | 12796.5 | 11928.2 | 11657.2 | 12909.9 | 12963.5 | 12857.3 | 11932.7 | 12916.4 | 11749.3 | 12743.4 | 11873.7 | 12388.8 | 10955.5 | 12750.8 | 11713.1 | 11937.6 | 11940.3 | 11708 | 10156.3 | 11690.3 | 10286.7 | 11178.2 | 11212.4 | 12372.3 | 11297.6 | 12241.7 | 11351.1 | 12401.1 | 11347.5 | 11573.8 | 11360.3 | 12094.5 | 12342 | 12415.1 | 12352 | 12303.1 | 12290.2 | 11509.7 | 12324.1 | 12211.3 | 12333.1 | 12522.2 | 12453.5 | 12241 | 11295.4 | 12519.4 | 11543.2 | 41.1437 | 40.8531 | 40.8191 | 40.8759 | 41.0633 | 40.8319 | 0 | 52.9 | 0 | 0 | 52.2 | 51.8 | 3.9976 | 3.9957 | 3.8101 | 4.0432 | 3.9662 | 2.6484 | 7.493 | 7.483 | 6.625 | 7.723 | 7.757 | 7.374 | 7.318 | 7.532 | 7.6107 | 7.3637 | 7.3395 | 6.8322 | 1.6227 | 1.7606 | 1.4918 | 1.9919 | 1.8178 | 1.5004 | 7.1299 | 7.4043 | 7.3451 | 7.2897 | 7.1881 | 6.6497 | 0.53293 | 0.6163 | 0.51936 | 0.57075 | 0.53816 | 0.53907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 637147 | 1152 | 624408 | 1220 | 671688.5 | 1772.533 | 7.318 | 7.532 | 7.6107 | 7.3637 | 7.3395 | 6.8322 | 7.1299 | 7.4043 | 7.3451 | 7.2897 | 7.1881 | 6.6497 | 996000 | 1000 | 965000 | 1000 | 1955514 | 4333 | 1959000 | 1951181 | 13.0833 | 7.3327 | 1.6975 | 7.1678 | 0.55276 | 23.15% | 7.712% | 40.9312 | 52.3 | 3.7435 | 7.4092 | 1969175.5 | 1954800 | 2335828.9603 | 83.69% | 67 | 0
2024-05-18 | 2025 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 335090.89 | 6:15 | 19:24 | 11772.1 | 12377.9 | 12342.4 | 12306.9 | 12501.7 | 12546.3 | 12539.3 | 12884.3 | 12391.6 | 12301.5 | 12296.2 | 12385 | 12523.5 | 12348 | 12508.1 | 12549.1 | 12462.1 | 12466.3 | 12543.3 | 12550.9 | 12627.9 | 12599.8 | 12435.7 | 12493.9 | 12284.1 | 10783.4 | 12281 | 12274.6 | 12602.7 | 12634.6 | 12529.1 | 12590 | 12650.2 | 12592.3 | 12652.1 | 12613.5 | 12752.8 | 12656.7 | 12703.8 | 12604.2 | 13277.6 | 12346 | 13176 | 12119.5 | 12711.5 | 13535.2 | 12140.9 | 13244.5 | 11439.1 | 11737.1 | 12551.4 | 11920.4 | 12850.8 | 11689.3 | 12841.3 | 11573.4 | 11515 | 12965.1 | 11410.9 | 12935.7 | 12744.5 | 11390.3 | 12537.9 | 12003.8 | 12290 | 11521.6 | 12212.3 | 12603.5 | 12884.5 | 11766.4 | 12736.1 | 11284.8 | 12501.9 | 12300.2 | 11611.9 | 12723.6 | 11354.5 | 12902.3 | 11493.5 | 12608.7 | 11879.2 | 12677.2 | 11925.2 | 12910.2 | 11820.6 | 12489.8 | 11851.1 | 10356.3 | 12739 | 12358.4 | 11705.7 | 13227.1 | 12962.2 | 12159.8 | 12054.6 | 13027 | 11830.7 | 12229.5 | 13069.9 | 11699.1 | 13208.8 | 11745.7 | 13034.4 | 12012 | 13087.5 | 11443.4 | 13147.6 | 12027.1 | 13031.8 | 12000.1 | 13121.7 | 12180.5 | 11623.4 | 12710 | 11929.5 | 11624.2 | 12925.4 | 12901.3 | 12880.6 | 11890.2 | 12875.4 | 11742.9 | 12801 | 11965.9 | 12419.4 | 10998 | 12734.8 | 11720.5 | 11890.5 | 11926.6 | 11746 | 10136.3 | 11688.3 | 10306.5 | 11510.6 | 11522.9 | 12804.2 | 11635.6 | 12795.8 | 11747.2 | 12824.7 | 11745.6 | 11960.9 | 11727.3 | 12740.4 | 12965.3 | 12821.1 | 12763.7 | 12716.4 | 12754.4 | 12039.5 | 12877 | 12603.2 | 12653 | 13144.2 | 13058.8 | 12846.9 | 11966.3 | 12934.4 | 12033.9 | 41.84 | 41.49 | 41.52 | 41.57 | 41.91 | 41.63 | 0 | 53.9 | 0 | 0 | 53.4 | 53.2 | 4.06 | 4.12 | 4.03 | 4.13 | 4.05 | 2.55 | 7.57 | 7.98 | 7.88 | 7.51 | 8.41 | 6.69 | 7.28 | 7.46 | 7.56 | 7.35 | 7.42 | 7.18 | 1.63 | 1.74 | 1.52 | 2.01 | 1.84 | 1.58 | 7.09 | 7.31 | 7.25 | 7.21 | 7.21 | 6.96 | 0.53 | 0.62 | 0.52 | 0.58 | 0.55 | 0.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 638131 | 1154 | 625386 | 1221 | 673645.8 | 1774.933 | 7.28 | 7.46 | 7.56 | 7.35 | 7.42 | 7.18 | 7.09 | 7.31 | 7.25 | 7.21 | 7.21 | 6.96 | 984000 | 2000 | 978000 | 1000 | 1957300 | 2400 | 1959000 | 1954900 | 13.15 | 7.375 | 1.72 | 7.1717 | 0.56333 | 23.32% | 7.855% | 41.66 | 53.5 | 3.8233 | 7.6733 | 1971055.1 | 1956534 | 2335992 | 83.76% | 66 | 0
2024-05-19 | 2025 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 335090.89 | 6:11 | 19:24 | 11150.4 | 11534.3 | 11534.7 | 11516.6 | 11677.8 | 11666 | 11650.8 | 12018.1 | 11626.1 | 11719.3 | 11446.6 | 11547.6 | 11624.7 | 11508.4 | 11653.9 | 11670.4 | 11596.9 | 11625.9 | 11659.9 | 11695.3 | 11747 | 11711.2 | 11507 | 11601 | 11381.7 | 10062.4 | 11408.7 | 11381.9 | 11716.1 | 11646.9 | 11518.4 | 11656.8 | 11686.3 | 11662.2 | 11763.8 | 11682.3 | 11766.1 | 11629.9 | 11714.1 | 11635.5 | 12485.1 | 11500.1 | 12381.2 | 11316.8 | 11970.3 | 12871.7 | 11286 | 12483.7 | 10707.3 | 10984.2 | 11667.2 | 11112.1 | 11986.6 | 10876.3 | 11987.2 | 10830.2 | 10754.4 | 12139.8 | 10731.8 | 12091 | 11933.4 | 10683.8 | 11766.2 | 11269.7 | 11435.3 | 10859.6 | 11408.7 | 11926.8 | 12097.1 | 11127.1 | 11958.1 | 10692.6 | 11687.7 | 11540.8 | 10917 | 12003.4 | 10736.4 | 12166.7 | 10913.9 | 12010.3 | 11259.3 | 12049.6 | 11315.4 | 12306.6 | 11207.6 | 11852.5 | 11151.2 | 9868.8 | 12030.7 | 11634.2 | 10907.8 | 12356.3 | 12052.7 | 11251.5 | 11127.3 | 12121.5 | 11028.4 | 11440.8 | 12256.3 | 10918 | 12278.7 | 10916.6 | 12030.6 | 11144.3 | 12125.9 | 10592.4 | 12191 | 11107.7 | 12054.8 | 11096.7 | 12122.8 | 11273.3 | 10917 | 11941.6 | 11067 | 10821.6 | 12011 | 12092 | 11942.3 | 11040.7 | 12019.3 | 10900.2 | 11818 | 11092.1 | 11583.5 | 10234.9 | 11813.6 | 10878.6 | 11015.6 | 11066.6 | 10872.9 | 9416.1 | 10799 | 9548 | 10763.1 | 10810.3 | 12364.1 | 11045.4 | 12213.2 | 11091.8 | 12272.8 | 11020.9 | 11207.4 | 10996.6 | 12026 | 12289.7 | 12279.2 | 12255.6 | 12256.7 | 12299.6 | 11361.9 | 12277.7 | 11957.4 | 12027.2 | 12329.9 | 12258.1 | 12100.6 | 11148.9 | 12304 | 11298.1 | 41.3185 | 41.0121 | 41.0759 | 41.0175 | 41.3288 | 41.1639 | 0 | 52.9715 | 0 | 0 | 52.5 | 52.6 | 4.0491 | 4.004 | 4.0155 | 4.0621 | 4.0575 | 2.4906 | 9.522 | 9.402 | 8.889 | 9.357 | 9.484 | 8.717 | 6.7453 | 6.8905 | 7.0686 | 6.8192 | 6.8502 | 6.77 | 1.5465 | 1.6206 | 1.4613 | 1.895 | 1.7118 | 1.4826 | 6.6061 | 6.7538 | 6.7792 | 6.6998 | 6.6421 | 6.5471 | 0.5192 | 0.59913 | 0.51444 | 0.56792 | 0.54679 | 0.57134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 639052 | 1155 | 626303 | 1222 | 675478.786 | 1779.067 | 6.7453 | 6.8905 | 7.0686 | 6.8192 | 6.8502 | 6.77 | 6.6061 | 6.7538 | 6.7792 | 6.6998 | 6.6421 | 6.5471 | 921000 | 1000 | 917000 | 1000 | 1832986 | 4134 | 1836000 | 1828852 | 13.2167 | 6.8573 | 1.6196 | 6.6713 | 0.55314 | 23.62% | 8.291% | 41.1528 | 52.6905 | 3.7798 | 9.2285 | 1844519.7 | 1832133 | 2182907.3088 | 83.93% | 67 | 7063
2024-05-20 | 2025 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 335090.89 | 6:12 | 19:26 | 11924 | 12479 | 12475 | 12430 | 12645 | 12685 | 12661 | 13012 | 12521 | 12542 | 12392 | 12500 | 12583 | 12454 | 12666 | 12641 | 12588 | 12567 | 12653 | 12676 | 12683 | 12664 | 12391 | 12510 | 12304 | 10762 | 12329 | 12329 | 12646 | 12540 | 12367 | 12580 | 12572 | 12561 | 12711 | 12627 | 12689 | 12518 | 12570 | 12508 | 13365 | 12265 | 13239 | 12028 | 12795 | 13742 | 12051 | 13375 | 11490 | 11786 | 12622 | 11969 | 12960 | 11711 | 12914 | 11590 | 11486 | 13043 | 11482 | 13012 | 12839 | 11439 | 12575 | 12002 | 12328 | 11529 | 12206 | 12706 | 12982 | 11765 | 12802 | 11279 | 12498 | 12271 | 11552 | 12769 | 11302 | 12987 | 11560 | 12772 | 11886 | 12777 | 11947 | 13097 | 11856 | 12598 | 11840 | 10434 | 12731 | 12379 | 11529 | 13139 | 12794 | 11925 | 11854 | 12930 | 11661 | 12121 | 13050 | 11564 | 13119 | 11570 | 12887 | 11847 | 12931 | 11234 | 13007 | 11803 | 12859 | 11753 | 12941 | 11970 | 11533 | 12725 | 11780 | 11524 | 12849 | 12937 | 12789 | 11782 | 12873 | 11633 | 12645 | 11759 | 12403 | 10920 | 12686 | 11650 | 11786 | 11811 | 11645 | 10051 | 11630 | 10290 | 11679 | 11693 | 13351 | 11929 | 13384 | 12172 | 13261 | 11946 | 12202 | 11901 | 12997 | 13286 | 13285 | 13237 | 13183 | 13236 | 12292 | 13304 | 13049 | 13119 | 13286 | 13229 | 13192 | 12176 | 13355 | 12281 | 39.6 | 39.37 | 39.45 | 39.14 | 39.06 | 39.57 | 0 | 51.6 | 0 | 0 | 51.2 | 52.14 | 5.61 | 5.69 | 5.6 | 5.8 | 5.71 | 4.97 | 10.57 | 11.72 | 11.58 | 10.68 | 10.21 | 10.22 | 7.23 | 7.39 | 7.43 | 7.27 | 7.27 | 7.32 | 1.62 | 1.77 | 1.5 | 1.97 | 1.84 | 1.69 | 7.08 | 7.19 | 7.12 | 7.08 | 7.04 | 6.92 | 0.53 | 0.61 | 0.51 | 0.56 | 0.55 | 0.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 640040 | 1156 | 627284 | 1223 | 677443.6 | 1783.3 | 7.23 | 7.39 | 7.43 | 7.27 | 7.27 | 7.32 | 7.08 | 7.19 | 7.12 | 7.08 | 7.04 | 6.92 | 988000 | 1000 | 981000 | 1000 | 1964814 | 4233 | 1967000 | 1960581 | 13.2333 | 7.3183 | 1.7317 | 7.0717 | 0.55833 | 23.66% | 7.895% | 39.365 | 51.6467 | 5.5633 | 10.83 | 1978802 | 1963800 | 2339117 | 83.95% | 68 | 0
2024-05-21 | 2025 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 335090.89 | 6:09 | 19:26 | 12280.6 | 12863.3 | 12858.3 | 12821.7 | 13006.6 | 13033.9 | 13030.8 | 13470.6 | 12933.7 | 12887 | 12787.6 | 12907.1 | 12943.8 | 12859 | 12967.5 | 12986.7 | 12874.6 | 12880.1 | 12958.9 | 13005.7 | 12984.6 | 12982.6 | 12683.3 | 12815.1 | 12553.1 | 10982.3 | 12679.1 | 12647.7 | 12987.6 | 12861.2 | 12682.2 | 12915.6 | 12943.8 | 12942.6 | 13087 | 12991.3 | 13047.2 | 12865.8 | 12890.4 | 12826.3 | 13762 | 12618.1 | 13597 | 12367 | 13094.2 | 14127.9 | 12358.3 | 13761.1 | 11832.4 | 12147.8 | 13021.1 | 12336.5 | 13336.8 | 12030.2 | 13305 | 11907.6 | 11856 | 13467.3 | 11843.2 | 13449.2 | 13277.1 | 11806.3 | 12997.1 | 12362 | 12669.1 | 11852 | 12577.5 | 13107.3 | 13369.4 | 12131.4 | 13174.8 | 11621.3 | 12877.5 | 12650.8 | 11916.7 | 13182.5 | 11679.7 | 13402.9 | 11933.4 | 13214.9 | 12248.8 | 13200.8 | 12302.7 | 13514.9 | 12209.5 | 12975.9 | 12192.3 | 10743.6 | 13218.8 | 12751.9 | 11908.3 | 13591.4 | 13152.2 | 12199.2 | 12119.6 | 13315.5 | 11994.4 | 12503.9 | 13475.3 | 11934.8 | 13516.2 | 11918.1 | 13243.6 | 12182.1 | 13307.9 | 11547 | 13377.6 | 12135.1 | 13208.1 | 12063.5 | 13275 | 12288.8 | 11923.5 | 13174.1 | 12146.6 | 11886.9 | 13241.7 | 13372.4 | 13161.7 | 12157.5 | 13293.4 | 11974.2 | 12995.9 | 12080.5 | 12775.6 | 11206.1 | 13045 | 11989.6 | 12162.2 | 12190.2 | 12000.7 | 10369 | 11931.4 | 10572.7 | 12015.5 | 12050.7 | 13797.3 | 12306.8 | 13847.7 | 12574.4 | 13701.3 | 12323.8 | 12564.3 | 12271.8 | 13482.4 | 13807.7 | 13749.6 | 13691.6 | 13661.8 | 13694.5 | 12720.9 | 13755.6 | 13551.6 | 13650.4 | 13813.5 | 13760.1 | 13715.7 | 12643.4 | 13771.6 | 12678.9 | 39.2238 | 39.0256 | 39.3125 | 38.8456 | 39.0248 | 39.2127 | 0 | 55 | 0 | 0 | 55.2 | 55.5 | 2.5572 | 2.551 | 2.4752 | 2.5996 | 2.5527 | 0.50855 | 6.069 | 6.512 | 8.044 | 6.057 | 6.16 | 6.35 | 7.7564 | 7.773 | 7.8195 | 7.7033 | 7.6531 | 7.7612 | 1.7038 | 1.8484 | 1.5817 | 2.0849 | 1.9241 | 1.7811 | 7.3918 | 7.4921 | 7.4221 | 7.421 | 7.3253 | 7.4544 | 0.54736 | 0.62738 | 0.53591 | 0.58415 | 0.57315 | 0.60918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 641058 | 1158 | 628297 | 1224 | 679467.986 | 1787.467 | 7.7564 | 7.773 | 7.8195 | 7.7033 | 7.6531 | 7.7612 | 7.3918 | 7.4921 | 7.4221 | 7.421 | 7.3253 | 7.4544 | 1018000 | 2000 | 1013000 | 1000 | 2024386 | 4167 | 2028000 | 2020219 | 13.2833 | 7.7444 | 1.8207 | 7.4178 | 0.57952 | 23.51% | 7.813% | 39.1075 | 55.2333 | 2.2074 | 6.532 | 2038619.3 | 2023400 | 2425378.3706 | 83.43% | 54 | 0
2024-05-22 | 2025 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 335090.89 | 6:13 | 19:26 | 10667.1 | 10987.7 | 10957.8 | 11068.8 | 11028.5 | 10914.3 | 10911.7 | 11240.8 | 10971.8 | 11038.1 | 10718.6 | 10839 | 10857.1 | 10759.8 | 10893.6 | 10885.6 | 10807.6 | 10764.5 | 10764.9 | 10822.5 | 10810.6 | 10782.5 | 10654.3 | 10695.2 | 10561.6 | 9343.2 | 10578.4 | 10589 | 10846.1 | 10750.9 | 10607.3 | 10766.1 | 10837.9 | 10811.9 | 10942.2 | 10901.2 | 10906.6 | 10684.8 | 10700.2 | 10663.4 | 10981.2 | 10040.4 | 10642.5 | 9713.3 | 10222.1 | 11126.9 | 10088.6 | 11156.7 | 10117.9 | 10360.9 | 10986.2 | 10427.7 | 11135.3 | 10232.1 | 11126.2 | 10079.1 | 10131.8 | 11313.5 | 10147.5 | 11350.5 | 11251.9 | 10124.6 | 10991.2 | 10534.6 | 10765.2 | 10190.1 | 10689.7 | 11090.9 | 11233 | 10431.8 | 11126.2 | 10036.7 | 10898 | 10813.4 | 10161.9 | 11167.4 | 10021.6 | 11303.5 | 10237.7 | 11214.3 | 10527.9 | 11280.3 | 10615.8 | 11394.4 | 10522.1 | 11040.6 | 10475.1 | 9303.5 | 11146.1 | 10864.5 | 10162.3 | 11445.4 | 11193 | 10546.1 | 10430 | 11190.2 | 10197.7 | 10596.9 | 11223.7 | 10142.8 | 11094.8 | 10081.1 | 10922.9 | 10298.6 | 10924 | 9715.8 | 10966.9 | 10189.7 | 10785.1 | 10039.7 | 10865.2 | 10244.7 | 10149 | 11026.1 | 10275.1 | 10076.4 | 11019.1 | 11176.7 | 10972.6 | 10248.6 | 11068.2 | 10057.7 | 10816.7 | 10171.4 | 10465.5 | 9341 | 10796.5 | 9951.4 | 10206.8 | 10245.6 | 9899.1 | 8670 | 10026.7 | 8920.3 | 10360.9 | 10402 | 11918.4 | 10730.7 | 12003.1 | 10964.6 | 11669.2 | 10648.3 | 10754.1 | 10591.4 | 11968.5 | 12153.7 | 12140.1 | 12069.5 | 12031.7 | 11999.5 | 11299.3 | 12062.7 | 11668.3 | 11818 | 12175 | 12088.1 | 11840.8 | 11076 | 12069.9 | 11294.9 | 42.3079 | 42.0761 | 42.0046 | 42.0537 | 42.2192 | 42.226 | 0 | 51 | 0 | 0 | 51.4 | 52 | 3.6603 | 3.7969 | 3.7486 | 3.7594 | 3.703 | 1.4861 | 6.803 | 7.484 | 7.118 | 7.804 | 7.155 | 7.089 | 6.4874 | 6.4335 | 6.1822 | 6.4886 | 6.4189 | 6.9041 | 1.4977 | 1.5277 | 1.3085 | 1.8383 | 1.6196 | 1.5561 | 6.1856 | 6.225 | 5.8951 | 6.2765 | 6.1882 | 6.614 | 0.50067 | 0.57219 | 0.47053 | 0.54483 | 0.52336 | 0.57801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 641911 | 1160 | 629159 | 1226 | 681179.787 | 1791.8 | 6.4874 | 6.4335 | 6.1822 | 6.4886 | 6.4189 | 6.9041 | 6.1856 | 6.225 | 5.8951 | 6.2765 | 6.1882 | 6.614 | 853000 | 2000 | 862000 | 2000 | 1711801 | 4333 | 1711000 | 1707468 | 13.2167 | 6.4858 | 1.558 | 6.2307 | 0.5316 | 24.02% | 8.532% | 42.1479 | 51.4667 | 3.3591 | 7.2422 | 1722803.4 | 1711401 | 2043431.7628 | 83.75% | 68 | 13614
2024-05-23 | 2025 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 335090.89 | 6:09 | 19:26 | 11843.4 | 12438.8 | 12440.8 | 12435.2 | 12601.2 | 12670.3 | 12640 | 13009.5 | 12449.6 | 12328 | 12295.2 | 12362.1 | 12568.8 | 12394.1 | 12617.9 | 12604.6 | 12514.2 | 12510 | 12602.4 | 12638.2 | 12680.5 | 12650.6 | 12440 | 12522.5 | 12335.5 | 10868.2 | 12404.2 | 12383.9 | 12698.4 | 12594.7 | 12435.2 | 12603 | 12614.1 | 12617.8 | 12754.3 | 12663.2 | 12747.9 | 12574.4 | 12607.3 | 12507.1 | 13361.4 | 12357.3 | 13226.9 | 12114.9 | 12775 | 13717.8 | 12096.3 | 13345.4 | 11518.4 | 11786 | 12709.7 | 12034.9 | 13004.1 | 11765.2 | 12928.4 | 11637.3 | 11443.1 | 12973.3 | 11432.5 | 12930.2 | 12768.2 | 11380 | 12430.4 | 11843.6 | 12266 | 11517.4 | 12136.3 | 12679.1 | 12836.7 | 11769.5 | 12668.1 | 11287.5 | 12342.5 | 12219.3 | 11429.6 | 12664.5 | 11226.4 | 12820 | 11468.6 | 12660.4 | 11943.2 | 12822.3 | 12030 | 13083.9 | 11951.8 | 12614.6 | 11933.6 | 10510.7 | 12876.9 | 12444.1 | 11668.9 | 13226.6 | 12883 | 12045.2 | 11950.5 | 12948.1 | 11820 | 12279.5 | 13174.2 | 11788 | 13202.7 | 11763.2 | 12992.5 | 12016.1 | 13067.6 | 11393.9 | 13100.3 | 11945.2 | 12973.9 | 11913.8 | 13064.8 | 12077 | 11715.8 | 12881.9 | 11965.6 | 11704.6 | 12961.6 | 13038.1 | 12891.9 | 11922.3 | 12992.4 | 11742.5 | 12733.6 | 11859.7 | 12316.1 | 10952.6 | 12741.9 | 11697.9 | 11902.2 | 11942.3 | 11684.2 | 10121.6 | 11698.6 | 10373.3 | 11607.9 | 11676.1 | 13392.5 | 12083.7 | 13479.6 | 12323 | 13275.8 | 12054 | 12210.3 | 11892.1 | 13191.9 | 13458.8 | 13451.3 | 13366.9 | 13350.5 | 13394.2 | 12532.4 | 13424.5 | 12837.7 | 13052.8 | 13398.6 | 13337.5 | 13046.3 | 12148.4 | 13315.9 | 12382.8 | 42.844 | 42.6525 | 42.8929 | 42.528 | 42.8145 | 42.766 | 0 | 55.9 | 0 | 0 | 56.1 | 56.3 | 2.3801 | 2.4734 | 2.3979 | 2.3776 | 2.3799 | 0.65303 | 7.49 | 6.246 | 9.66 | 6.13 | 5.844 | 7.465 | 7.473 | 7.5832 | 7.6304 | 7.4531 | 7.5287 | 7.6369 | 1.7009 | 1.8571 | 1.5849 | 2.0769 | 1.9277 | 1.7696 | 7.1487 | 7.3599 | 7.3191 | 7.1918 | 7.1901 | 7.3187 | 0.55753 | 0.64665 | 0.55518 | 0.59732 | 0.5873 | 0.62393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 642898 | 1161 | 630148 | 1227 | 683150.587 | 1796 | 7.473 | 7.5832 | 7.6304 | 7.4531 | 7.5287 | 7.6369 | 7.1487 | 7.3599 | 7.3191 | 7.1918 | 7.1901 | 7.3187 | 987000 | 1000 | 989000 | 1000 | 1970800 | 4200 | 1974000 | 1966600 | 13.2833 | 7.5509 | 1.8195 | 7.2547 | 0.59465 | 24.1% | 8.197% | 42.7496 | 56.1 | 2.1103 | 7.1392 | 1984271.6 | 1969534 | 2338825.5912 | 84.21% | 61 | 0
2024-05-24 | 2025 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 335090.89 | 6:11 | 19:26 | 11664 | 12186.7 | 12095.4 | 12116.9 | 12220.7 | 12313 | 12350.2 | 12736.2 | 12206 | 12194.7 | 12070.8 | 12156.7 | 12272.7 | 12142.4 | 12267.2 | 12295.1 | 12173.4 | 12184.4 | 12315.4 | 12345.1 | 12353.6 | 12361.4 | 12078.7 | 12165.8 | 12119.5 | 10684.7 | 12111.5 | 12119.4 | 12384.4 | 12277.4 | 12144.5 | 12334.4 | 12374.9 | 12376.1 | 12524.9 | 12422.1 | 12479.3 | 12303.7 | 12330.8 | 12227.3 | 13125.2 | 12193.4 | 12967.6 | 11979.3 | 12515.3 | 13401.9 | 11800.4 | 12995.4 | 11332.7 | 11614.1 | 12421.3 | 11829.4 | 12667.6 | 11512.2 | 12693.4 | 11427.2 | 11341.6 | 12814 | 11290.2 | 12780.5 | 12618.6 | 11254.7 | 12349.4 | 11790.3 | 12092.8 | 11410.4 | 12006.6 | 12475.9 | 12713.4 | 11672.7 | 12540.2 | 11232.2 | 12303 | 12160.3 | 11426.2 | 12619.8 | 11277 | 12775.7 | 11500.2 | 12676.5 | 11789.1 | 12645.9 | 11888.3 | 12817.3 | 11738.3 | 12346.3 | 11704.8 | 10336.3 | 12551.1 | 12142.7 | 11439.6 | 12833 | 12395.1 | 11618 | 11617.6 | 12552.4 | 11555.1 | 11979.1 | 12762.9 | 11529.9 | 12800.3 | 11523.9 | 12618.7 | 11761.4 | 12693.8 | 11177.7 | 12715 | 11737.3 | 12593.3 | 11687.7 | 12641.8 | 11871.7 | 11464.5 | 12510.6 | 11704.5 | 11457.5 | 12581.7 | 12671.2 | 12533.1 | 11771.6 | 12672.2 | 11634.4 | 12385.2 | 11682.9 | 12013.3 | 10895.4 | 12564 | 11679 | 11766 | 11775 | 11673.9 | 10058.3 | 11522 | 10222.4 | 11552.9 | 11595 | 13021.5 | 11820.6 | 13094.1 | 12060.5 | 13045 | 11909.1 | 12096.4 | 11827.7 | 12824 | 13047.8 | 13058.5 | 12972 | 12966.6 | 13014.8 | 12133.9 | 13018.6 | 12478.8 | 12732.7 | 13065.8 | 12995.2 | 12663.6 | 11779.8 | 13070.6 | 12085.8 | 42.8391 | 42.6501 | 42.8037 | 42.5878 | 42.8644 | 42.8501 | 0 | 55.7 | 0 | 0 | 55.9 | 56.66 | 2.4597 | 2.6187 | 2.6276 | 2.5481 | 2.6512 | 0.91729 | 7.2 | 7.121 | 6.508 | 8.292 | 7.774 | 6.108 | 7.3278 | 7.4168 | 7.5113 | 7.3565 | 7.3681 | 6.8277 | 1.67 | 1.824 | 1.5702 | 2.0562 | 1.8939 | 1.7281 | 7.0202 | 7.195 | 7.1968 | 7.1067 | 7.0329 | 6.6803 | 0.55191 | 0.63858 | 0.55415 | 0.59259 | 0.58075 | 0.61306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 643867 | 1163 | 631116 | 1228 | 685083.054 | 1800.133 | 7.3278 | 7.4168 | 7.5113 | 7.3565 | 7.3681 | 6.8277 | 7.0202 | 7.195 | 7.1968 | 7.1067 | 7.0329 | 6.6803 | 969000 | 2000 | 968000 | 1000 | 1932467 | 4133 | 1934000 | 1928334 | 13.25 | 7.3014 | 1.7904 | 7.0386 | 0.58851 | 24.52% | 8.361% | 42.7659 | 56.0867 | 2.3038 | 7.1672 | 1945315.4 | 1931267 | 2276046.6801 | 84.85% | 47 | 0
2024-05-25 | 2025 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 335090.89 | 6:13 | 19:26 | 10761.6 | 11307.4 | 11425 | 11407.8 | 11585.5 | 11560.9 | 11511.2 | 11825.2 | 11326.2 | 11326.5 | 11138.1 | 11259.1 | 11273.7 | 11201.7 | 11391.5 | 11366.6 | 11316 | 11265.9 | 11304.7 | 11365.3 | 11354.1 | 11327.3 | 11087.3 | 11186.9 | 11036.4 | 9648.4 | 11079.8 | 11071.2 | 11423.6 | 11314.4 | 11169.4 | 11374.6 | 11378.5 | 11390.8 | 11524.1 | 11404.5 | 11518.6 | 11357.6 | 11414.8 | 11271.3 | 11918.5 | 10805.2 | 11806.5 | 10601.9 | 11345.5 | 12354.3 | 10646 | 11959.1 | 10341.3 | 10603.3 | 11405.2 | 10726.3 | 11697.4 | 10516.8 | 11653.8 | 10375.9 | 10321.7 | 11797.9 | 10352.6 | 11839.6 | 11749.7 | 10357.9 | 11493.2 | 10870.6 | 11100.8 | 10383.2 | 10989.5 | 11530.8 | 11736.9 | 10659.6 | 11550 | 10220.7 | 11279.9 | 11073.3 | 10445.1 | 11589.4 | 10251 | 11829.2 | 10448.1 | 11668.1 | 10739.5 | 11707.3 | 10811.2 | 11890.1 | 10697.7 | 11390 | 10670.2 | 9404.4 | 11647.9 | 11197.2 | 10392.7 | 11963.9 | 11586.1 | 10700.5 | 10611.9 | 11728.6 | 10403.2 | 10772.7 | 11666.4 | 10191.2 | 11736.3 | 10204.8 | 11434.7 | 10398.5 | 11508.7 | 9859.9 | 11533.4 | 10340.7 | 11389.1 | 10365.8 | 11488.7 | 10475.9 | 10120.5 | 11267.9 | 10276 | 10073.5 | 11340.6 | 11485.9 | 11260.2 | 10389 | 11441.4 | 10230.2 | 11092.3 | 10274.2 | 10820.1 | 9560.8 | 11168.9 | 10250.4 | 10447.2 | 10490.3 | 10246.5 | 8885.9 | 10250.4 | 9069.6 | 10332.1 | 10371.7 | 11926.2 | 10549.1 | 11942.7 | 10788 | 11827.9 | 10583.5 | 10735.7 | 10525.8 | 11652.2 | 11924.4 | 11883.2 | 11817.3 | 11820.5 | 11858.9 | 10892.7 | 11865.1 | 11606.7 | 11725.4 | 11928.6 | 11861.5 | 11615.3 | 10710.7 | 11929.2 | 10884.1 | 42.6882 | 42.2805 | 42.47 | 42.2885 | 42.4816 | 42.3965 | 0 | 53.9968 | 0 | 0 | 53.8 | 54 | 2.9598 | 3.0103 | 2.9277 | 3.1422 | 2.9312 | 1.6206 | 6.776 | 7.309 | 7.318 | 6.857 | 6.815 | 6.386 | 6.6299 | 6.6424 | 6.6109 | 6.6959 | 6.4053 | 6.1528 | 1.5519 | 1.6068 | 1.4124 | 1.8961 | 1.6374 | 1.4755 | 6.346 | 6.4736 | 6.3223 | 6.3993 | 6.1227 | 6.0518 | 0.50143 | 0.57937 | 0.49562 | 0.54164 | 0.51555 | 0.54899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 644759 | 1165 | 631990 | 1230 | 686844.92 | 1804.333 | 6.6299 | 6.6424 | 6.6109 | 6.6959 | 6.4053 | 6.1528 | 6.346 | 6.4736 | 6.3223 | 6.3993 | 6.1227 | 6.0518 | 892000 | 2000 | 874000 | 2000 | 1761866 | 4200 | 1762000 | 1757666 | 13.2167 | 6.5229 | 1.5967 | 6.286 | 0.53043 | 24.48% | 8.438% | 42.4342 | 53.9323 | 2.7653 | 6.9102 | 1772458.8 | 1761400 | 2050754.8076 | 85.89% | 67 | 46879
2024-05-26 | 2025 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 335090.89 | 6:18 | 19:22 | 10727.9 | 11232.2 | 11057.3 | 11088 | 11188.4 | 11313.2 | 11330.3 | 11715.9 | 11236 | 11126.9 | 11206.5 | 11227.6 | 11411.6 | 11263 | 11453.1 | 11423.5 | 11351.4 | 11327 | 11495.4 | 11483.7 | 11599.9 | 11548.1 | 11421.4 | 11479.4 | 11287.8 | 9976.9 | 11334.5 | 11364.3 | 11622.6 | 11582.1 | 11419.2 | 11556.3 | 11647 | 11644.1 | 11757.5 | 11680.9 | 11724.9 | 11596 | 11613.1 | 11582.6 | 12310.7 | 11466.5 | 12269.2 | 11356.6 | 11901.5 | 12593 | 11187.5 | 12152.1 | 10578.5 | 10854.4 | 11535 | 11071 | 11778.8 | 10766.1 | 11842.4 | 10746.5 | 10649.2 | 11972 | 10538.2 | 11918.4 | 11709.8 | 10507.9 | 11470.2 | 11001.1 | 11404.6 | 10777.9 | 11291.5 | 11738.1 | 11864.3 | 10972.4 | 11684.7 | 10496.4 | 11500.6 | 11345 | 10706 | 11728.3 | 10511.6 | 11835.3 | 10658.1 | 11634.9 | 11119.6 | 11844.1 | 11227 | 12109.8 | 11129.8 | 11742.2 | 11150.3 | 9834.3 | 11964.7 | 11602.8 | 10919.1 | 12296.3 | 12008.6 | 11309.8 | 11181.5 | 12062.5 | 11164.1 | 11555.8 | 12341.8 | 11138.9 | 12406.1 | 11126.2 | 12219.7 | 11396.4 | 12253 | 10803.9 | 12320.5 | 11366.2 | 12241.6 | 11311.7 | 12373.3 | 11518.3 | 11111.3 | 12168.2 | 11353.4 | 11127.9 | 12215 | 12331.4 | 12165.9 | 11427.6 | 12266.1 | 11261.7 | 12024 | 11332.8 | 11386.6 | 10493.1 | 12169.2 | 11252.1 | 11448 | 11453.6 | 11244.2 | 9755 | 11281.4 | 9996.9 | 11290.9 | 11321.3 | 12614.1 | 11482 | 12743.9 | 11745.1 | 12606 | 11560.3 | 11736.6 | 11506.5 | 12447.2 | 12694.5 | 12626.3 | 12600.5 | 12573.5 | 12671.3 | 11908.7 | 12706.2 | 11669.7 | 11907.9 | 12631.1 | 12543.9 | 12118.7 | 11244.9 | 12671.5 | 11758.2 | 43.5641 | 43.2429 | 43.3173 | 43.403 | 43.855 | 43.4277 | 0 | 53.4 | 0 | 0 | 53.6 | 53.9 | 5.1461 | 5.2485 | 5.1714 | 5.2372 | 5.251 | 4.3778 | 9.006 | 8.571 | 7.953 | 8.252 | 8.707 | 8.826 | 6.6767 | 6.8319 | 6.9652 | 6.8717 | 7.1971 | 6.7458 | 1.5521 | 1.6899 | 1.4772 | 1.9282 | 1.8342 | 1.6795 | 6.4243 | 6.7105 | 6.6715 | 6.5556 | 6.9091 | 6.6662 | 0.5228 | 0.6128 | 0.53158 | 0.57014 | 0.57554 | 0.60937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 645665 | 1166 | 632924 | 1231 | 688679.787 | 1808.533 | 6.6767 | 6.8319 | 6.9652 | 6.8717 | 7.1971 | 6.7458 | 6.4243 | 6.7105 | 6.6715 | 6.5556 | 6.9091 | 6.6662 | 906000 | 1000 | 934000 | 1000 | 1834867 | 4200 | 1838000 | 1830667 | 13.0667 | 6.8814 | 1.6935 | 6.6562 | 0.57037 | 24.61% | 8.569% | 43.4683 | 53.6333 | 5.072 | 8.5525 | 1847109.9 | 1834067 | 2171218.9714 | 84.47% | 49 | 823
2024-05-27 | 2025 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 335090.89 | 6:10 | 19:28 | 12241.3 | 12732.2 | 12577 | 12614.3 | 12727.3 | 12819 | 12764.6 | 13148.4 | 12708.5 | 12566.7 | 12597.8 | 12623 | 12787.9 | 12584.1 | 12781.6 | 12741 | 12668.6 | 12571.4 | 12750.8 | 12737.9 | 12780.1 | 12729.1 | 12591.3 | 12600.7 | 12431.1 | 11340.6 | 12537.2 | 12534.4 | 12745.1 | 12733.1 | 12528.5 | 12645.8 | 12742.6 | 12764 | 12949.5 | 12881.1 | 12836.2 | 12705.9 | 12659.6 | 12606.1 | 13363.9 | 12544.4 | 13288.1 | 12396.8 | 12941.5 | 13633.7 | 12316.1 | 13214.1 | 11989.7 | 12277.6 | 12815 | 12384.5 | 13020.1 | 12211.4 | 13017 | 12106.5 | 12037.2 | 13155.9 | 12075.7 | 13171.3 | 12991.2 | 11998 | 12721 | 12362.8 | 12552.9 | 12021 | 12487.5 | 12801.1 | 13043.9 | 12184 | 12856.6 | 11779.9 | 12684.4 | 12525.7 | 12104 | 12867.5 | 11875.4 | 13086.6 | 12009.9 | 12875.5 | 12246.5 | 12934.9 | 12348.7 | 13160.7 | 12244.6 | 12785.6 | 12267.9 | 11044.4 | 12911 | 12595.3 | 12103.7 | 13270.2 | 12977.2 | 12367.9 | 12234.2 | 12998.8 | 12156.2 | 12451.2 | 13126.3 | 12135 | 13212.8 | 12177.2 | 13003.1 | 12352.6 | 13034.4 | 11850.5 | 13101.4 | 12292.3 | 13026.3 | 12322.9 | 13139 | 12452.7 | 12063 | 12905.4 | 12265.5 | 12095.8 | 12968.6 | 13052 | 12893.4 | 12298.9 | 13004.6 | 12217.9 | 12814.5 | 12292.6 | 12056.3 | 11355 | 12941 | 12271.8 | 12333 | 12355.3 | 12256.1 | 10700.1 | 12185.9 | 10926.7 | 12253.4 | 12188 | 13330.7 | 12196 | 13430.4 | 12450.2 | 13314.4 | 12315.4 | 12458.4 | 12247.2 | 13168.8 | 13381.7 | 13377.7 | 13329.1 | 13287 | 13352.1 | 12646 | 13379.2 | 12315.8 | 12463.8 | 13391.9 | 13275 | 12734.3 | 11763.3 | 13429 | 12561.6 | 43.0143 | 42.5956 | 42.6123 | 42.7098 | 43.1547 | 42.8409 | 0 | 52.6756 | 0 | 0 | 52.5 | 52.9 | 6.2712 | 6.3251 | 6.2572 | 6.3031 | 6.3642 | 5.0263 | 12.852 | 11.483 | 10.94 | 11.691 | 11.799 | 11.282 | 7.8501 | 7.8345 | 7.9488 | 7.9127 | 7.9493 | 7.5285 | 1.8348 | 1.9722 | 1.7015 | 2.2287 | 2.0563 | 1.8901 | 7.546 | 7.6505 | 7.5675 | 7.4696 | 7.5839 | 7.4864 | 0.61127 | 0.70106 | 0.6037 | 0.65001 | 0.64019 | 0.68132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 646670 | 1168 | 633926 | 1232 | 690682.121 | 1812.667 | 7.8501 | 7.8345 | 7.9488 | 7.9127 | 7.9493 | 7.5285 | 7.546 | 7.6505 | 7.5675 | 7.4696 | 7.5839 | 7.4864 | 1005000 | 2000 | 1002000 | 1000 | 2002334 | 4134 | 2004000 | 1998200 | 13.3 | 7.8373 | 1.9473 | 7.5506 | 0.64792 | 24.85% | 8.581% | 42.8213 | 52.6919 | 6.0912 | 11.6745 | 2016494.1 | 2000933 | 2461035.9827 | 81.3% | 53 | 560
2024-05-28 | 2025 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 335090.89 | 6:09 | 19:29 | 12112 | 12676 | 12624 | 12623 | 12783 | 12831 | 12790 | 13211 | 12720 | 12677 | 12585 | 12693 | 12726 | 12642 | 12790 | 12771 | 12735 | 12683 | 12755 | 12816 | 12806 | 12777 | 12551 | 12639 | 12434 | 10927 | 12486 | 12472 | 12786 | 12710 | 12540 | 12741 | 12697 | 12705 | 12857 | 12791 | 12854 | 12702 | 12720 | 12665 | 13500 | 12446 | 13420 | 12223 | 12954 | 13863 | 12204 | 13459 | 11677 | 11967 | 12804 | 12159 | 13103 | 11875 | 13083 | 12286 | 11678 | 13243 | 11673 | 13207 | 13033 | 11633 | 12763 | 12230 | 12536 | 11737 | 12414 | 12898 | 13173 | 11961 | 12974 | 11464 | 12700 | 12470 | 11745 | 12957 | 11515 | 13174 | 11748 | 12977 | 12078 | 12958 | 12177 | 13272 | 12076 | 12797 | 12079 | 10609 | 12967 | 12590 | 11755 | 13379 | 13066 | 12210 | 12102 | 13136 | 11915 | 12374 | 13230 | 11805 | 13311 | 11811 | 13069 | 12090 | 13107 | 11447 | 13196 | 12020 | 13064 | 11983 | 13150 | 12195 | 11773 | 12966 | 12008 | 11760 | 13047 | 13165 | 12977 | 12052 | 13096 | 11891 | 12835 | 11973 | 12548 | 11171 | 12920 | 11913 | 12102 | 12148 | 11936 | 10316 | 11928 | 10522 | 11973 | 11983 | 13567 | 12208 | 13629 | 12453 | 13500 | 12221 | 12374 | 12132 | 13237 | 13501 | 13490 | 13453 | 13408 | 13484 | 12573 | 13506 | 13199 | 13240 | 13579 | 13493 | 13348 | 12379 | 13582 | 12551 | 41.07 | 40.67 | 40.76 | 40.66 | 40.76 | 40.92 | 0 | 52.4 | 0 | 0 | 52.1 | 52.3 | 6.76 | 6.76 | 6.82 | 6.74 | 6.84 | 6.46 | 11.25 | 11 | 10.56 | 10.72 | 10.68 | 10.23 | 7.47 | 7.46 | 7.56 | 7.53 | 7.57 | 7.24 | 1.75 | 1.88 | 1.61 | 2.11 | 1.96 | 1.81 | 7.21 | 7.33 | 7.2 | 7.12 | 7.23 | 7.18 | 0.58 | 0.66 | 0.57 | 0.61 | 0.61 | 0.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 647672 | 1170 | 634926 | 1234 | 692679.5 | 1816.6 | 7.47 | 7.46 | 7.56 | 7.53 | 7.57 | 7.24 | 7.21 | 7.33 | 7.2 | 7.12 | 7.23 | 7.18 | 1002000 | 2000 | 1000000 | 2000 | 1997379 | 3933 | 1998000 | 1993446 | 13.3333 | 7.4717 | 1.8533 | 7.2117 | 0.61333 | 24.8% | 8.505% | 40.8067 | 52.2667 | 6.73 | 10.74 | 2011157 | 1996933 | 2379662 | 83.92% | 51 | 0
2024-05-29 | 2025 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 335090.89 | 6:05 | 19:30 | 12355 | 12905 | 12893 | 12848 | 13002 | 13076 | 13088 | 13471 | 12917 | 12946 | 12796 | 12919 | 12931 | 12874 | 12997 | 13009 | 12921 | 12910 | 12953 | 13025 | 12999 | 12996 | 12761 | 12853 | 12637 | 11068 | 12693 | 12679 | 13034 | 12912 | 12758 | 12979 | 13034 | 13009 | 13152 | 13074 | 13085 | 12929 | 12958 | 12899 | 13781 | 12672 | 13655 | 12461 | 13176 | 14223 | 12378 | 13747 | 11900 | 12213 | 13035 | 12391 | 13396 | 12101 | 13327 | 12907 | 11904 | 13510 | 11914 | 13466 | 13305 | 11858 | 13076 | 12451 | 12739 | 11952 | 12638 | 13119 | 13408 | 12164 | 13195 | 11652 | 12913 | 12666 | 11959 | 13171 | 11701 | 13393 | 11943 | 13207 | 12276 | 13166 | 12382 | 13535 | 12289 | 13033 | 12288 | 10819 | 13236 | 12828 | 11947 | 13609 | 13289 | 12397 | 12266 | 13375 | 12130 | 12585 | 13480 | 11996 | 13557 | 12008 | 13282 | 12293 | 13356 | 11655 | 13432 | 12231 | 13263 | 12181 | 13328 | 12416 | 11980 | 13213 | 12206 | 11971 | 13311 | 13434 | 13207 | 12258 | 13360 | 12083 | 13042 | 12175 | 12930 | 11362 | 9660 | 9455 | 12310 | 12342 | 12107 | 10479 | 12154 | 10747 | 12150 | 12165 | 13834 | 12384 | 13891 | 12624 | 13757 | 12446 | 12606 | 12344 | 13504 | 13834 | 13799 | 13751 | 13732 | 13769 | 12757 | 13804 | 13707 | 13752 | 13847 | 13819 | 13835 | 12700 | 13824 | 12734 | 37.74 | 37.57 | 37.82 | 37.27 | 37.35 | 37.8 | 0 | 50.7 | 0 | 0 | 50.5 | 50.9 | 6.85 | 7.04 | 6.82 | 7.24 | 6.81 | 7.23 | 10.68 | 10.6 | 11.35 | 11.01 | 10.58 | 11.73 | 7.6 | 7.63 | 7.67 | 7.63 | 7.68 | 7.37 | 1.78 | 1.92 | 1.64 | 2.15 | 1.98 | 1.83 | 7.33 | 7.41 | 7.31 | 7.17 | 7.28 | 7.24 | 0.59 | 0.68 | 0.58 | 0.62 | 0.62 | 0.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 648694 | 1171 | 635939 | 1235 | 694708.7 | 1820.5 | 7.6 | 7.63 | 7.67 | 7.63 | 7.68 | 7.37 | 7.33 | 7.41 | 7.31 | 7.17 | 7.28 | 7.24 | 1022000 | 1000 | 1013000 | 1000 | 2029200 | 3900 | 2033000 | 2025300 | 13.4167 | 7.5967 | 1.8833 | 7.29 | 0.625 | 24.79% | 8.573% | 37.5917 | 50.7 | 6.9983 | 10.9917 | 2043095 | 2028600 | 2438085.3232 | 83.2% | 51 | 433
2024-05-30 | 2025 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 335090.89 | 6:08 | 19:31 | 12537.9 | 13041.5 | 13018.9 | 12988.7 | 13130.1 | 13196.8 | 13192.3 | 13616 | 13079.1 | 13103.9 | 12969 | 13080.5 | 13083.7 | 13035.6 | 13124.8 | 13136.7 | 13053.6 | 13058.7 | 13095.3 | 13162.5 | 13139.5 | 13143.8 | 12932.5 | 13017.2 | 12848.9 | 11334.2 | 12863.1 | 12854.7 | 13176.5 | 13060.6 | 12915.1 | 13125.5 | 13231 | 13190.8 | 13333.9 | 13272.2 | 13236.3 | 13078.7 | 13107 | 13060.6 | 13836 | 12820.6 | 13723.5 | 12638 | 13293.7 | 14242.1 | 12586 | 13836.6 | 12125 | 12428.6 | 13190.8 | 12597.7 | 13519.2 | 12309 | 13473.9 | 13351.2 | 12117.4 | 13640.8 | 12119.1 | 13589.7 | 13431.1 | 12063.5 | 13209.9 | 12653.8 | 12911.3 | 12177.7 | 12831.2 | 13271 | 13542.1 | 12384.8 | 13355.6 | 11866.1 | 13085.8 | 12866.4 | 12195.1 | 13332.7 | 11935.8 | 13543.8 | 12176.6 | 13358.7 | 12478.5 | 13308.5 | 12569 | 13643.7 | 12488.2 | 13178.9 | 12465.3 | 11003.3 | 13376.3 | 12972.8 | 12153.8 | 13699.4 | 13379.3 | 12550.4 | 12421 | 13470.9 | 12308.5 | 12748 | 13564.5 | 12201.2 | 13643.3 | 12200.2 | 13407.2 | 12486 | 13436 | 11828.1 | 13514.6 | 12409.7 | 13363.8 | 12350.8 | 13425.5 | 12593.1 | 12181.5 | 13326.5 | 12410.3 | 12163.9 | 13412 | 13531.4 | 13313.2 | 12452.6 | 13436.5 | 12269 | 13165.4 | 12368.8 | 13019.1 | 11554.9 | 13245.4 | 12318.3 | 12519.9 | 12547.6 | 12353.6 | 10671.9 | 12340 | 10906.5 | 12402.8 | 12408.5 | 13914.7 | 12582.8 | 13968.1 | 12801.7 | 13855.1 | 12629.3 | 12645.1 | 12423.7 | 13621 | 13907.8 | 13887.5 | 13839 | 13811.8 | 13845 | 12929.3 | 13890.6 | 13747.4 | 13791.3 | 13926 | 13897.9 | 13875 | 12885.8 | 13924 | 12918.8 | 38.7329 | 38.5445 | 38.6957 | 38.2999 | 38.2977 | 38.7914 | 0 | 51.7 | 0 | 0 | 51.4 | 51.8 | 6.1972 | 6.2713 | 6.1965 | 6.3556 | 6.1483 | 6.4932 | 10.002 | 10.231 | 10.647 | 9.696 | 9.809 | 9.482 | 7.7685 | 7.7997 | 7.8473 | 7.8193 | 7.8448 | 7.5465 | 1.8422 | 1.9819 | 1.6852 | 2.2112 | 2.0474 | 1.8985 | 7.4858 | 7.6038 | 7.463 | 7.3422 | 7.4379 | 7.4017 | 0.59238 | 0.68577 | 0.59104 | 0.63171 | 0.63516 | 0.67338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 649728 | 1173 | 636969 | 1236 | 696767.588 | 1824.6 | 7.7685 | 7.7997 | 7.8473 | 7.8193 | 7.8448 | 7.5465 | 7.4858 | 7.6038 | 7.463 | 7.3422 | 7.4379 | 7.4017 | 1034000 | 2000 | 1030000 | 1000 | 2058888 | 4100 | 2061000 | 2054788 | 13.3833 | 7.771 | 1.9444 | 7.4557 | 0.63491 | 25.02% | 8.516% | 38.5603 | 51.6333 | 6.277 | 9.9778 | 2073737.7 | 2058200 | 2476927.6664 | 83.09% | 44 | 0
2024-05-31 | 2025 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 335090.89 | 6:09 | 19:33 | 12645.3 | 13101.9 | 13079.3 | 13051.4 | 13206.7 | 13239.5 | 13222.9 | 13611.6 | 13152.6 | 13143.6 | 13043.1 | 13142.6 | 13171.1 | 13080.8 | 13217.8 | 13205.4 | 13131.8 | 13112.2 | 13161.6 | 13230.2 | 13213.9 | 13219.3 | 13025.4 | 13089.3 | 12907.2 | 11451.4 | 12931.2 | 12930.7 | 13206 | 13114.9 | 12995.2 | 13158.8 | 13355.5 | 13316 | 13451 | 13394.8 | 13256.1 | 13115.4 | 13148 | 13097.1 | 13884.6 | 12955.6 | 13783.2 | 12773.8 | 13387.4 | 14260.4 | 12686.2 | 13841 | 12433.4 | 12556.8 | 13237.4 | 12723.6 | 13519.8 | 12455.3 | 13492.4 | 13485.6 | 12246.5 | 13644.1 | 12247.8 | 13604 | 13461.9 | 12192.2 | 13243.8 | 12758.8 | 12981.1 | 12297 | 12919.9 | 13310.5 | 13554.6 | 12519.7 | 13388.3 | 12016.7 | 13138 | 12970.9 | 12321.6 | 13364.2 | 12060.9 | 13561.5 | 12304.3 | 13368.8 | 12610.6 | 13365.1 | 12686.4 | 13669.1 | 12608.1 | 13226.7 | 12584.2 | 11117.2 | 13358.7 | 13005.1 | 12275.5 | 13704.9 | 13429.5 | 12724.8 | 12606.1 | 13485.6 | 12428.1 | 12860.3 | 13599.7 | 12356.4 | 13672.1 | 12371.9 | 13490.1 | 12652.6 | 13498.4 | 11996.8 | 13586.2 | 12577 | 13456.7 | 12530.2 | 13519 | 12766.7 | 12293.8 | 13347.5 | 12544.6 | 12306.2 | 13449.2 | 13557.7 | 13375.9 | 12593.5 | 13489.1 | 12443.3 | 13251.1 | 12530.3 | 13091.8 | 11694.6 | 13338.5 | 12472.5 | 12657 | 12681.8 | 12474.9 | 10786.2 | 12458.7 | 10993.7 | 12511.8 | 12521.1 | 13943.3 | 12701.2 | 13994.9 | 12904.6 | 13863.9 | 12721.3 | 12829 | 12653.4 | 13648.1 | 13915 | 13923.1 | 13871.9 | 13836.4 | 13874.7 | 13033.6 | 13921.4 | 13791.5 | 13804.9 | 13958.5 | 13910.7 | 13907.5 | 12957.5 | 13954 | 13012.7 | 37.0102 | 37.8158 | 38.0165 | 37.564 | 37.5642 | 38.0307 | 0 | 50.3 | 0 | 0 | 50.5 | 51.229 | 6.6628 | 7.1533 | 6.8649 | 7.0926 | 6.9919 | 7.2404 | 10.597 | 10.653 | 11.598 | 11.668 | 11.015 | 12.061 | 7.8346 | 7.8393 | 7.9006 | 7.8488 | 7.918 | 7.6144 | 1.8533 | 2.0056 | 1.6999 | 2.2272 | 2.0745 | 1.9169 | 7.5091 | 7.6248 | 7.4992 | 7.3582 | 7.4815 | 7.4176 | 0.61171 | 0.70633 | 0.60947 | 0.65116 | 0.65038 | 0.68999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 650769 | 1174 | 638006 | 1237 | 698838.188 | 1828.8 | 7.8346 | 7.8393 | 7.9006 | 7.8488 | 7.918 | 7.6144 | 7.5091 | 7.6248 | 7.4992 | 7.3582 | 7.4815 | 7.4176 | 1041000 | 1000 | 1037000 | 1000 | 2070600 | 4200 | 2076000 | 2066400 | 13.4 | 7.826 | 1.9629 | 7.4817 | 0.65317 | 25.08% | 8.73% | 37.6669 | 50.6763 | 7.001 | 11.2653 | 2086899.9 | 2069867 | 2501385.1022 | 82.75% | 48 | 206
2024-06-01 | 2025 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 335090.89 | 6:06 | 19:32 | 12482.3 | 13035.4 | 12966.1 | 12985.9 | 13081.3 | 13119.3 | 13214.4 | 13492.5 | 13000.9 | 13062.3 | 12880.3 | 12999.2 | 13003.2 | 12943.2 | 13061.6 | 13056.3 | 13039 | 12984.1 | 13006.1 | 13078.5 | 13123.9 | 13132 | 12847 | 12994.1 | 12771.9 | 11241.2 | 12774.5 | 12761.5 | 13146.5 | 12972.5 | 12844.1 | 13025.9 | 13213.1 | 13118 | 13246.4 | 13246.1 | 13131.9 | 12987.2 | 13023.6 | 12965.9 | 13775.8 | 12832.8 | 13660.4 | 12576.9 | 13241.9 | 14272.7 | 12562.6 | 13776.8 | 12588 | 12439.8 | 13090.7 | 12531.3 | 13473.9 | 12326.8 | 13431 | 13429.6 | 12130.5 | 13593.2 | 12134.1 | 13493.7 | 13410.1 | 12070.6 | 13131.5 | 12589.7 | 12825.5 | 12088.9 | 12733.2 | 13248.3 | 13494.1 | 12320.2 | 13307.8 | 11882.5 | 12983.2 | 12783.4 | 12118.8 | 13230 | 11865.4 | 13494.8 | 12105.8 | 13246 | 12424.3 | 13230 | 12560.3 | 13551.6 | 12411.9 | 13148.1 | 12454.1 | 10942.9 | 13254.8 | 12947.5 | 12078.5 | 13600.1 | 13321.1 | 12521.7 | 12455.8 | 13390.2 | 12326.5 | 12688.9 | 13492 | 12148 | 13625.4 | 12224 | 13411.4 | 12447.9 | 13371.5 | 11846.1 | 13519.4 | 12360.9 | 13304.1 | 12303.1 | 13347.7 | 12604.5 | 12176.1 | 13252.8 | 12329.1 | 12116.9 | 13317.9 | 13508.8 | 13322.3 | 12464.6 | 13372.4 | 12286 | 13089.9 | 12300.6 | 12956.6 | 11541.7 | 13166.7 | 12306.7 | 12509.2 | 12534.5 | 12250.3 | 10598 | 12347.4 | 10856.1 | 12351.1 | 12308.7 | 13830.8 | 12496.1 | 13883 | 12721.1 | 13754.7 | 12550.2 | 12700.6 | 12549.9 | 13600.5 | 13825 | 13809.9 | 13753.3 | 13790.3 | 13824.4 | 12845.1 | 13862.8 | 13772.2 | 13740.6 | 13847.4 | 13877.7 | 13824.8 | 12805.7 | 13837.8 | 12906.9 | 36.4546 | 36.4818 | 36.7832 | 36.1921 | 36.22 | 36.6565 | 0 | 50.3 | 0 | 0 | 50.2 | 50.6 | 5.5578 | 6.0266 | 5.6252 | 6.1437 | 5.8247 | 5.8231 | 10.316 | 10.033 | 10.506 | 10.41 | 9.427 | 10.181 | 7.7239 | 7.8274 | 7.7576 | 7.7601 | 7.7994 | 7.5349 | 1.8364 | 1.959 | 1.683 | 2.2091 | 2.0484 | 1.8754 | 7.4234 | 7.5305 | 7.3738 | 7.3783 | 7.3993 | 7.2893 | 0.59982 | 0.69038 | 0.59799 | 0.63442 | 0.63596 | 0.67353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 651799 | 1176 | 639032 | 1239 | 700889.055 | 1832.933 | 7.7239 | 7.8274 | 7.7576 | 7.7601 | 7.7994 | 7.5349 | 7.4234 | 7.5305 | 7.3738 | 7.3783 | 7.3993 | 7.2893 | 1030000 | 2000 | 1026000 | 2000 | 2050867 | 4133 | 2052000 | 2046734 | 13.4333 | 7.7339 | 1.9352 | 7.3991 | 0.63868 | 25.02% | 8.632% | 36.4647 | 50.3667 | 5.8335 | 10.1455 | 2066341 | 2049933 | 2469550.4402 | 83.01% | 53 | 0
2024-06-02 | 2025 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 335090.89 | 6:10 | 19:34 | 12452.9 | 12955.6 | 12919.7 | 12877.3 | 13031.1 | 13072.8 | 13121 | 13531.9 | 13007.4 | 13069.7 | 12859.3 | 12999.2 | 12945.6 | 12913.9 | 13014.2 | 13005.9 | 12935.9 | 12948.9 | 12952.3 | 13027 | 13026.6 | 13017.8 | 12799.1 | 12889.8 | 12711.7 | 11135 | 12693.8 | 12690.2 | 13054.2 | 12936.8 | 12787.8 | 12989.1 | 13071.4 | 13033.6 | 13142.7 | 13096.1 | 13120.3 | 12973.7 | 13007.9 | 12935.6 | 13731.2 | 12650.4 | 13617.8 | 12436.2 | 13144.1 | 14171.1 | 12464.2 | 13751.7 | 12644.5 | 12273.7 | 13039.4 | 12438.3 | 13369.8 | 12184.4 | 13334.4 | 13318.6 | 11969.5 | 13541.3 | 11958.2 | 13501.8 | 13352.3 | 11918.3 | 13141.1 | 12552.9 | 12794.4 | 12015.5 | 12697.9 | 13193 | 13451.6 | 12255.4 | 13253.6 | 11758.2 | 12903.8 | 12693.9 | 11977.3 | 13167.7 | 11786.3 | 13440.2 | 12021.7 | 13253.1 | 12372.3 | 13248.5 | 12442.3 | 13583.9 | 12355.6 | 13074.8 | 12345.7 | 10885.7 | 13298.6 | 12868.8 | 12024.8 | 13623.7 | 13307.4 | 12423.5 | 12277.6 | 13388.1 | 12182.7 | 12645.7 | 13491 | 12075.5 | 13541.8 | 12067.1 | 13315.5 | 12350.4 | 13356.8 | 11702 | 13431.6 | 12275.5 | 13268.7 | 12210.3 | 13315 | 12443.1 | 12048 | 13250.4 | 12275.4 | 12035.6 | 13331.9 | 13448.9 | 13228.8 | 12320.5 | 13345.7 | 12123.9 | 13058.5 | 12225.1 | 12922 | 11405.5 | 13134.3 | 12161.8 | 12378.9 | 12414.6 | 12170.3 | 10539 | 12205.4 | 10798.2 | 12258.6 | 12268.7 | 13819 | 12444.6 | 13857.2 | 12672.6 | 13769.7 | 12494.8 | 12594.8 | 12367.2 | 13497.4 | 13791.8 | 13763.3 | 13706.9 | 13689.8 | 13733.3 | 12770.8 | 13751.5 | 13694.9 | 13743.7 | 13864.4 | 13828.6 | 13828.9 | 12760.3 | 13780.8 | 12769.9 | 36.7531 | 36.83 | 37.0848 | 36.6148 | 36.6272 | 37.0454 | 0 | 50.6 | 0 | 0 | 50.5 | 50.7 | 5.3695 | 5.619 | 5.3216 | 5.8628 | 5.5311 | 5.3769 | 10.365 | 10.218 | 9.942 | 9.574 | 10.286 | 10.63 | 7.5937 | 7.7031 | 7.6064 | 7.6655 | 7.6567 | 7.3846 | 1.7946 | 1.9474 | 1.6357 | 2.1661 | 2.0297 | 1.8588 | 7.3334 | 7.4382 | 7.2364 | 7.3177 | 7.2865 | 7.1729 | 0.58818 | 0.67659 | 0.58242 | 0.62448 | 0.62386 | 0.65855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 652824 | 1177 | 640054 | 1240 | 702930.055 | 1837.133 | 7.5937 | 7.7031 | 7.6064 | 7.6655 | 7.6567 | 7.3846 | 7.3334 | 7.4382 | 7.2364 | 7.3177 | 7.2865 | 7.1729 | 1025000 | 1000 | 1022000 | 1000 | 2041000 | 4200 | 2045000 | 2036800 | 13.4 | 7.6017 | 1.9054 | 7.2975 | 0.62568 | 25.07% | 8.574% | 36.8259 | 50.6 | 5.5135 | 10.1692 | 2055463.8 | 2040267 | 2434165.2098 | 83.82% | 53 | 138
2024-06-03 | 2025 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 335090.89 | 6:11 | 19:33 | 12093.5 | 12677.1 | 12684.2 | 12617.1 | 12833.9 | 12836.8 | 12852.1 | 13277.6 | 12737.7 | 12760.5 | 12588.5 | 12728.6 | 12709.2 | 12635.6 | 12779.9 | 12752.6 | 12689.3 | 12665.9 | 12720.5 | 12799.7 | 12780.5 | 12755.4 | 12493.1 | 12602.9 | 12411.4 | 10852.7 | 12419.8 | 12402.9 | 12763.2 | 12672.6 | 12490.9 | 12720.7 | 12790.1 | 12758.2 | 12876.6 | 12808.7 | 12834.5 | 12660.1 | 12702.3 | 12644.5 | 13544.1 | 12405.1 | 13456.2 | 12189 | 12935.9 | 13942.1 | 12131.8 | 13489.8 | 12656 | 11935 | 12779.4 | 12099.7 | 13103.4 | 11862.2 | 13098.3 | 13076.9 | 11634.7 | 13258.3 | 11626.5 | 13208.7 | 13036.5 | 11581.9 | 12793.7 | 12195.6 | 12477.6 | 11671.5 | 12347.6 | 12894.4 | 13160.3 | 11903 | 12967.3 | 11420.6 | 12600.5 | 12368.6 | 11624.1 | 12906.8 | 11462.1 | 13169.8 | 11679 | 12960.3 | 12025.4 | 12969.3 | 12107.6 | 13296.4 | 12013.8 | 12796.3 | 11999.6 | 10572.4 | 12985.6 | 12581.6 | 11686.5 | 13370.4 | 13072.9 | 12157.3 | 12023.4 | 13142.5 | 11853.9 | 12315.9 | 13231 | 11758.8 | 13295.9 | 11758.4 | 13068.2 | 12027.7 | 13098.2 | 11383.4 | 13189.4 | 11935.8 | 13027.9 | 11890.7 | 13125.1 | 12117.9 | 11702.9 | 12969.3 | 11948.3 | 11705.2 | 13064.7 | 13183.6 | 12981.2 | 11978.4 | 13028.6 | 11767.2 | 12796.4 | 11882.8 | 12623.4 | 11090.6 | 12880.6 | 11825.4 | 12025.8 | 12077.7 | 11825.5 | 10237.6 | 11880 | 10480.7 | 11924.7 | 11934.8 | 13639 | 12142.9 | 13691.7 | 12409.9 | 13555.4 | 12184.4 | 12407.2 | 12168.1 | 13281.8 | 13593 | 13575.5 | 13528.7 | 13485 | 13532 | 12553.4 | 13589.2 | 13441.9 | 13487 | 13657.4 | 13586 | 13567.4 | 12475.9 | 13627.5 | 12526.7 | 37.9307 | 38.1679 | 38.2604 | 38.0598 | 38.0204 | 38.4552 | 0 | 50.7 | 0 | 0 | 50.7 | 50.9 | 6.0741 | 6.1893 | 6.1865 | 6.0269 | 5.9686 | 5.5957 | 10.424 | 10.073 | 10.77 | 10.159 | 10.217 | 11.175 | 7.4036 | 7.477 | 7.4305 | 7.4495 | 7.4468 | 7.2954 | 1.7655 | 1.8983 | 1.6117 | 2.1238 | 1.9768 | 1.8145 | 7.1718 | 7.2523 | 7.0643 | 7.1145 | 7.0927 | 7.1808 | 0.58793 | 0.67744 | 0.58496 | 0.6238 | 0.62766 | 0.66299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 653827 | 1179 | 641053 | 1241 | 704926.655 | 1841.267 | 7.4036 | 7.477 | 7.4305 | 7.4495 | 7.4468 | 7.2954 | 7.1718 | 7.2523 | 7.0643 | 7.1145 | 7.0927 | 7.1808 | 1003000 | 2000 | 999000 | 1000 | 1996600 | 4134 | 1999000 | 1992466 | 13.3667 | 7.4171 | 1.8651 | 7.1461 | 0.62746 | 25.15% | 8.781% | 38.1491 | 50.7667 | 6.0069 | 10.4697 | 2010937.3 | 1995867 | 2375581.4509 | 84.02% | 48 | 1440
2024-06-04 | 2025 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 335090.89 | 6:08 | 19:34 | 12393 | 12918 | 12886 | 12779 | 13030 | 13012 | 13095 | 13439 | 12961 | 12948 | 12775 | 12880 | 12983 | 12794 | 12959 | 12996 | 12939 | 12896 | 12971 | 13028 | 12956 | 13003 | 12809 | 12807 | 12571 | 11218 | 12693 | 12621 | 12967 | 12836 | 12764 | 12875 | 13168 | 13144 | 13209 | 13211 | 13019 | 12869 | 12913 | 12787 | 13660 | 12687 | 13580 | 12509 | 13158 | 14003 | 12465 | 13594 | 13041 | 12300 | 13024 | 12403 | 13289 | 12252 | 13241 | 13227 | 12007 | 13430 | 11967 | 13390 | 13212 | 11951 | 12979 | 12484 | 12785 | 12053 | 12674 | 13085 | 13348 | 12267 | 13172 | 11766 | 12837 | 12624 | 11976 | 13042 | 11806 | 13337 | 11910 | 13115 | 12349 | 13049 | 12445 | 13431 | 12354 | 12925 | 12382 | 10906 | 13097 | 12698 | 12043 | 13408 | 13137 | 12416 | 12362 | 13230 | 12248 | 12613 | 13312 | 12128 | 13357 | 12137 | 13204 | 12359 | 13192 | 11758 | 13353 | 12262 | 13224 | 12285 | 13321 | 12510 | 12069 | 13126 | 12315 | 12087 | 13228 | 13323 | 13102 | 12289 | 13166 | 12132 | 13011 | 12194 | 12825 | 11456 | 13056 | 12149 | 12350 | 12462 | 12201 | 10507 | 12297 | 10851 | 12210 | 12217 | 13753 | 12475 | 13736 | 12606 | 13678 | 12529 | 12456 | 12253 | 13316 | 13643 | 13607 | 13558 | 13520 | 13569 | 12791 | 13622 | 13530 | 13579 | 13678 | 13595 | 13637 | 12661 | 13747 | 12783 | 37.33 | 37.43 | 37.55 | 37.18 | 37.14 | 37.62 | 0 | 49.1 | 0 | 0 | 49 | 49.3 | 7.67 | 7.83 | 7.72 | 7.9 | 7.64 | 8 | 12.33 | 11.82 | 12.37 | 12.83 | 12.03 | 12.14 | 7.61 | 7.7 | 7.65 | 7.68 | 7.66 | 7.49 | 1.85 | 1.97 | 1.68 | 2.21 | 2.05 | 1.86 | 7.35 | 7.45 | 7.29 | 7.29 | 7.28 | 7.36 | 0.61 | 0.71 | 0.61 | 0.65 | 0.65 | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 654849 | 1180 | 642069 | 1242 | 706958.5 | 1845.2 | 7.61 | 7.7 | 7.65 | 7.68 | 7.66 | 7.49 | 7.35 | 7.45 | 7.29 | 7.29 | 7.28 | 7.36 | 1022000 | 1000 | 1016000 | 1000 | 2031845 | 3933 | 2036000 | 2027912 | 13.4333 | 7.6317 | 1.9367 | 7.3367 | 0.65333 | 25.38% | 8.905% | 37.375 | 49.1333 | 7.7933 | 12.2533 | 2047212 | 2030900 | 2457013 | 82.66% | 55 | 2473
2024-06-05 | 2025 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 335090.89 | 6:06 | 19:28 | 12338.6 | 12891 | 12886.2 | 12827 | 13001.4 | 13034.7 | 13063.8 | 13504.5 | 12907.5 | 12961.8 | 12779.6 | 12915.7 | 12897.7 | 12823.4 | 12957.1 | 12960.5 | 12867.4 | 12878.7 | 12904.7 | 12967.9 | 12951.2 | 12947.5 | 12714.9 | 12806.8 | 12647.8 | 11080.3 | 12644.6 | 12627 | 12986 | 12872.4 | 12718.6 | 12936.3 | 13086.5 | 13039.1 | 13126.6 | 13057.2 | 13042.4 | 12876 | 12921 | 12869.9 | 13723.7 | 12580.8 | 13605.8 | 12360.7 | 13124.5 | 14206.7 | 12309.6 | 13645.8 | 13126.8 | 12187.7 | 13007.7 | 12352.4 | 13351.8 | 12096 | 13310 | 13307.9 | 11884.2 | 13484.7 | 11852.6 | 13436.2 | 13262.8 | 11825.9 | 13061.7 | 12442.2 | 12705.2 | 11915.2 | 12608 | 13092.4 | 13371.2 | 12138.1 | 13094 | 11634.7 | 12804.1 | 12628.1 | 11859.9 | 13075.4 | 11686.5 | 13371.5 | 11907.5 | 13166.8 | 12212.1 | 13102.9 | 12319.6 | 13461.4 | 12219.1 | 12976.5 | 12237.5 | 10767.4 | 13186.8 | 12771.6 | 11881 | 13531.4 | 13222 | 12345.6 | 12207.9 | 13298.6 | 12082.4 | 12524.9 | 13406.2 | 11959.5 | 13465.8 | 11954.9 | 13231.3 | 12261 | 13271.2 | 11594.4 | 13347.4 | 12163.6 | 13205.1 | 12127.7 | 13272.7 | 12349.1 | 11936.4 | 13149.3 | 12168.2 | 11927.4 | 13247.7 | 13351.2 | 13157.3 | 12214.8 | 13251.1 | 12014.2 | 12980 | 12102.3 | 12859.4 | 11313 | 13056.2 | 12056.6 | 12276.7 | 12332.2 | 12084.1 | 10454.3 | 12129.8 | 10711.3 | 12178.1 | 12185.8 | 13764.9 | 12322.7 | 13828 | 12568.7 | 13708.5 | 12409.4 | 12423.3 | 12207.1 | 13427.3 | 13743.1 | 13724.3 | 13673 | 13656.4 | 13693.9 | 12703.8 | 13733.3 | 13640.6 | 13683.6 | 13780.3 | 13733.2 | 13747.3 | 12649 | 13769.7 | 12686.8 | 34.8163 | 34.9737 | 35.0893 | 34.6584 | 34.7218 | 35.1778 | 0 | 46.8 | 0 | 0 | 46.6 | 47 | 7.8031 | 8.1009 | 7.9622 | 8.3273 | 7.8366 | 8.3312 | 12.561 | 12.212 | 13.033 | 11.893 | 11.495 | 12.205 | 7.4796 | 7.464 | 7.428 | 7.4701 | 7.4454 | 7.2961 | 1.8086 | 1.9124 | 1.6469 | 2.1629 | 2.001 | 1.8111 | 7.1554 | 7.243 | 7.1216 | 7.099 | 7.0872 | 7.1972 | 0.6002 | 0.69037 | 0.59982 | 0.63706 | 0.63978 | 0.67261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 655870 | 1182 | 643083 | 1244 | 708986.922 | 1849.267 | 7.4796 | 7.464 | 7.428 | 7.4701 | 7.4454 | 7.2961 | 7.1554 | 7.243 | 7.1216 | 7.099 | 7.0872 | 7.1972 | 1021000 | 2000 | 1014000 | 2000 | 2028422 | 4067 | 2031000 | 2024355 | 13.3667 | 7.4305 | 1.8905 | 7.1506 | 0.63998 | 25.44% | 8.95% | 34.9062 | 46.8 | 8.0602 | 12.2332 | 2043302.3 | 2027867 | 2421659.68 | 83.74% | 49 | 0
2024-06-06 | 2025 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 335090.89 | 6:07 | 19:29 | 11638.8 | 12256.9 | 12298.5 | 12233.5 | 12431.7 | 12387.4 | 12409.8 | 12801.2 | 12218.5 | 12198.8 | 12131.9 | 12240.1 | 12252.5 | 12190.3 | 12338.7 | 12297.2 | 12259.4 | 12255.8 | 12263.7 | 12312.2 | 12333 | 12309.4 | 12088.3 | 12191.5 | 11976 | 10485.9 | 11976.3 | 11955.7 | 12347.7 | 12226.2 | 12073.2 | 12285.7 | 12285 | 12276.4 | 12357.4 | 12294 | 12378.3 | 12220.7 | 12259 | 12178.4 | 12953 | 11797.7 | 12838.9 | 11563.9 | 12384.9 | 13483.6 | 11703.4 | 12994.3 | 12450.4 | 11504.4 | 12365.2 | 11673.4 | 12680.6 | 11483.9 | 12595.3 | 12633.6 | 11187.2 | 12729.7 | 11208.1 | 12694.6 | 12551 | 11158.2 | 12278.9 | 11685.7 | 11958.6 | 11161 | 11828.7 | 12327.7 | 12588.8 | 11399.1 | 12287 | 10960.9 | 12127.9 | 11940.7 | 11207.2 | 12459.6 | 11025.3 | 12605.5 | 11265.2 | 12472.2 | 11497.2 | 12411.8 | 11623.4 | 12730.3 | 11470 | 12214 | 11474.6 | 10089.6 | 12474.5 | 12039.7 | 11220.3 | 12843 | 12543.8 | 11684.9 | 11542.2 | 12570.4 | 11343.2 | 11770.5 | 12634.1 | 11216.8 | 12719.8 | 11222.4 | 12480.1 | 11528.2 | 12567.3 | 10899.8 | 12676.3 | 11431.9 | 12556.1 | 11467.1 | 12648.7 | 11668.1 | 11190.1 | 12376.2 | 11410.2 | 11158.2 | 12465.3 | 12559.7 | 12368.9 | 11397.8 | 12479 | 11255.8 | 12234.7 | 11401.5 | 12164.8 | 10610.1 | 12273.9 | 11265.7 | 11438.6 | 11516.2 | 11263.7 | 9723.9 | 11305.5 | 9968.8 | 11374.6 | 11450.9 | 13068.9 | 11662.9 | 13111 | 11909.1 | 13047.3 | 11770.3 | 11795.4 | 11601.5 | 12706.3 | 13054.4 | 13027 | 12974.9 | 12953.1 | 13006 | 12008.4 | 13030.3 | 12862.4 | 12860.9 | 12946.7 | 12887.7 | 12915.8 | 11846.7 | 13052.3 | 11932.6 | 34.2321 | 34.4409 | 34.7431 | 34.2503 | 34.1946 | 34.7076 | 0 | 49 | 0 | 0 | 48.2 | 48.6 | 4.7626 | 5.0847 | 4.7819 | 5.1829 | 4.9377 | 5.0463 | 8.887 | 8.582 | 8.623 | 8.688 | 8.659 | 8.834 | 7.1682 | 7.1628 | 7.1071 | 7.0896 | 7.0145 | 7.2103 | 1.6787 | 1.8712 | 1.5189 | 1.9981 | 1.9002 | 1.7799 | 6.8999 | 6.9626 | 6.8621 | 6.7677 | 6.7211 | 6.9479 | 0.57534 | 0.66191 | 0.57064 | 0.60364 | 0.60639 | 0.64056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 656836 | 1183 | 644040 | 1245 | 710904.456 | 1853.533 | 7.1682 | 7.1628 | 7.1071 | 7.0896 | 7.0145 | 7.2103 | 6.8999 | 6.9626 | 6.8621 | 6.7677 | 6.7211 | 6.9479 | 966000 | 1000 | 957000 | 1000 | 1917534 | 4266 | 1921000 | 1913268 | 13.3667 | 7.1254 | 1.7912 | 6.8602 | 0.60975 | 25.14% | 8.888% | 34.4281 | 48.6 | 4.966 | 8.7122 | 1930076.4 | 1916734 | 2309480.9062 | 82.99% | 49 | 0
2024-06-07 | 2025 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 335090.89 | 6:13 | 19:32 | 11237.4 | 11873.8 | 11918.4 | 11822.2 | 12032.2 | 12077 | 12159.1 | 12613.4 | 11864.1 | 11884.3 | 11753.2 | 11901.8 | 11846.4 | 11847.6 | 11905.6 | 11946.7 | 11847.4 | 11838.9 | 11873.8 | 11951.4 | 11929.7 | 11896.5 | 11617.3 | 11744.9 | 11572.3 | 10117 | 11570.2 | 11544.2 | 11955.5 | 11839.3 | 11646.2 | 11905 | 11902.5 | 11880.7 | 12002.6 | 11915.1 | 12044.1 | 11857.9 | 11910.6 | 11828 | 12852.6 | 11467.9 | 12701.4 | 11263.8 | 12013 | 13390.7 | 11145.3 | 12754.1 | 12119.3 | 11121.6 | 11961.3 | 11283.3 | 12392.4 | 11063.8 | 12289.3 | 12305.2 | 10822.3 | 12526.2 | 10854.3 | 12473.3 | 12275.2 | 10811.1 | 11985.8 | 11296.3 | 11549.5 | 10786.9 | 11430 | 12016.9 | 12376 | 11025.1 | 12119.3 | 10576.7 | 11771.2 | 11521.8 | 10814.6 | 12123.1 | 10591.2 | 12368 | 10816.9 | 12082 | 11135.6 | 12101.8 | 11247.2 | 12555 | 11099.6 | 11874.3 | 11120.3 | 9783.6 | 12227.5 | 11673.2 | 10838.7 | 12645.6 | 12213.2 | 11240.4 | 11120.5 | 12375.5 | 11060.6 | 11435.1 | 12485.9 | 10888.1 | 12528.7 | 10871.9 | 12145 | 11153.5 | 12282.5 | 10544.3 | 12353.3 | 11069.4 | 12126.5 | 11011.9 | 12224 | 11208 | 10873.4 | 12122.6 | 11072.6 | 10826.1 | 12247.7 | 12391 | 12102.4 | 11092.9 | 12255.9 | 10887 | 11899 | 11010.5 | 11743.9 | 10248.6 | 11942.7 | 10943.6 | 11102 | 11150.9 | 10986 | 9474.3 | 10990.1 | 9714.8 | 10952.6 | 10972.1 | 12784.3 | 11126.8 | 12817.5 | 11341.6 | 12771.6 | 11206.2 | 11231.2 | 10959.7 | 12311.8 | 12751.7 | 12700.4 | 12662.1 | 12637.5 | 12675 | 11407.9 | 12694.5 | 12687.4 | 12740.2 | 12811.4 | 12763.5 | 12732.7 | 11354.2 | 12779 | 11415.4 | 37.0329 | 37.3329 | 37.5286 | 37.2383 | 37.3012 | 37.5414 | 0 | 51.3 | 0 | 0 | 51.1 | 51.3 | 4.0612 | 4.1026 | 3.9335 | 4.1814 | 4.1554 | 2.7832 | 9.635 | 8.179 | 7.897 | 8.717 | 7.608 | 8.393 | 6.963 | 6.9086 | 6.8537 | 6.8661 | 6.8074 | 6.8685 | 1.6677 | 1.812 | 1.5001 | 1.9885 | 1.8694 | 1.7066 | 6.6839 | 6.7366 | 6.6323 | 6.569 | 6.5507 | 6.6486 | 0.56287 | 0.64361 | 0.55239 | 0.58873 | 0.58859 | 0.61166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 657775 | 1185 | 644970 | 1247 | 712768.456 | 1857.733 | 6.963 | 6.9086 | 6.8537 | 6.8661 | 6.8074 | 6.8685 | 6.6839 | 6.7366 | 6.6323 | 6.569 | 6.5507 | 6.6486 | 939000 | 2000 | 930000 | 2000 | 1864000 | 4200 | 1865000 | 1859800 | 13.3167 | 6.8779 | 1.7574 | 6.6368 | 0.59131 | 25.55% | 8.909% | 37.3292 | 51.2333 | 3.8695 | 8.4048 | 1875020 | 1863333 | 2205350.0725 | 84.49% | 55 | 0
2024-06-08 | 2025 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 335090.89 | 6:08 | 19:33 | 11149.4 | 11683.5 | 11737.1 | 11690.3 | 11830.7 | 11834.3 | 11840.3 | 12288.3 | 11686.7 | 11778.5 | 11482 | 11610.7 | 11158.5 | 10639.5 | 11607.7 | 11640.1 | 11513.6 | 11467.9 | 11500.5 | 11592.7 | 11522.3 | 11520.9 | 11280.8 | 11372.2 | 11225.3 | 9861.2 | 11277.4 | 11245 | 11589.8 | 11444 | 11189.2 | 11478 | 11636.9 | 11591.7 | 11620.2 | 11519.9 | 11581 | 11397.5 | 11470.9 | 11492.9 | 12337.9 | 11121.1 | 12181.7 | 10941.9 | 11600.2 | 12798.5 | 10812.1 | 12257.8 | 11461 | 10852.9 | 11615 | 11027.3 | 11971.9 | 10766 | 11985.2 | 11933 | 10595.9 | 12178.9 | 10580.6 | 12085.9 | 11924.7 | 10564.5 | 11677.6 | 11080 | 11343 | 10683.5 | 11256.2 | 11892.9 | 12073 | 10933.4 | 11900.4 | 10501.7 | 11562.5 | 11396.8 | 10669 | 11957.5 | 10516.9 | 12084 | 10710.5 | 11948.4 | 11091.3 | 11989.4 | 11247.6 | 12362.2 | 11089.4 | 11824.7 | 11069.5 | 9760.1 | 12168.8 | 11564.5 | 10811.8 | 12453 | 12069 | 11163.9 | 11014.9 | 12203 | 11048.9 | 11478.5 | 12374.7 | 11006 | 12448.9 | 10960.2 | 12166.8 | 11240.9 | 12268.2 | 10649.5 | 12350.6 | 11177.1 | 12175.5 | 11136.2 | 12225.9 | 11353.7 | 11024.4 | 12172.5 | 11189.2 | 10962.7 | 12257.9 | 12342.3 | 12134.2 | 11216.4 | 12237.9 | 11020.4 | 11960.5 | 11113.2 | 11782.2 | 10297.1 | 11972.3 | 11057.6 | 11262 | 11333.8 | 11065.3 | 9602.3 | 11111.8 | 9875.5 | 11225.9 | 11248.6 | 12814.1 | 11402.5 | 12857.6 | 11608.6 | 12738.5 | 11449 | 11230.6 | 11094.4 | 12454.8 | 12769.4 | 12773.2 | 12698 | 12683.4 | 12716.9 | 11729.1 | 12730.6 | 12747.1 | 12743.2 | 12865.8 | 12784.7 | 12749.3 | 11646.5 | 12883.4 | 11724.4 | 33.923 | 34.1162 | 34.0598 | 34.0136 | 34.0804 | 34.3055 | 0 | 47 | 0 | 0 | 47.5 | 47.6 | 4.5008 | 4.4085 | 4.3468 | 4.4475 | 4.4204 | 3.4387 | 8.749 | 7.863 | 8.646 | 8.143 | 8.963 | 7.797 | 6.733 | 6.5775 | 6.5904 | 6.6888 | 6.8251 | 7.1119 | 1.5556 | 1.6662 | 1.4139 | 1.8937 | 1.7822 | 1.5723 | 6.4871 | 6.3815 | 6.3437 | 6.4082 | 6.5904 | 6.8211 | 0.55786 | 0.63497 | 0.54455 | 0.59543 | 0.6049 | 0.62285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 658689 | 1186 | 645905 | 1248 | 714612.456 | 1861.8 | 6.733 | 6.5775 | 6.5904 | 6.6888 | 6.8251 | 7.1119 | 6.4871 | 6.3815 | 6.3437 | 6.4082 | 6.5904 | 6.8211 | 914000 | 1000 | 935000 | 1000 | 1844000 | 4067 | 1847000 | 1839933 | 13.4167 | 6.7544 | 1.6473 | 6.5053 | 0.59343 | 24.39% | 9.122% | 34.0831 | 47.3667 | 4.2604 | 8.3602 | 1854136.5 | 1842600 | 2197564.1976 | 83.85% | 55 | 7771
2024-06-09 | 2025 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 335090.89 | 6:08 | 19:33 | 11901 | 12504 | 12446 | 12391 | 12593 | 12594 | 12599 | 12982 | 12512 | 12523 | 12390 | 12512 | 12525 | 12411 | 12530 | 12568 | 12463 | 12428 | 12509 | 12556 | 12555 | 12525 | 12271 | 12384 | 12232 | 10687 | 12204 | 12190 | 12529 | 12449 | 12283 | 12504 | 12716 | 12644 | 12760 | 12647 | 12586 | 12422 | 12478 | 12405 | 13183 | 12056 | 13077 | 11834 | 12539 | 13692 | 11826 | 13111 | 12489 | 11724 | 12585 | 11929 | 12906 | 11659 | 12893 | 12590 | 11424 | 13066 | 11404 | 13014 | 12851 | 11411 | 12635 | 12052 | 12242 | 11428 | 12154 | 12607 | 12970 | 11660 | 12807 | 11202 | 12477 | 12233 | 11525 | 12832 | 11354 | 13041 | 11590 | 12829 | 11728 | 12650 | 11851 | 12985 | 11761 | 12508 | 11683 | 10271 | 12726 | 12213 | 11367 | 13091 | 12788 | 11879 | 11728 | 12839 | 11617 | 12041 | 12947 | 11524 | 13038 | 11507 | 12746 | 11774 | 12790 | 11095 | 12862 | 11609 | 12685 | 11544 | 12770 | 11819 | 11480 | 12693 | 11686 | 11415 | 12786 | 12868 | 12675 | 11592 | 12783 | 11468 | 12501 | 11569 | 12301 | 10728 | 12499 | 11448 | 11713 | 11797 | 11515 | 9954 | 11600 | 10235 | 11587 | 11696 | 13329 | 11938 | 13383 | 12155 | 13297 | 12036 | 12242 | 11973 | 12986 | 13314 | 13279 | 13223 | 13214 | 13248 | 12282 | 13285 | 13196 | 13217 | 13373 | 13287 | 13256 | 12179 | 13416 | 12289 | 36.27 | 36.01 | 36.47 | 35.94 | 36 | 36.12 | 0 | 51.3 | 0 | 0 | 50.5 | 50.4 | 3.17 | 3.14 | 3.1 | 3.05 | 2.96 | 1.11 | 6.11 | 6.09 | 6.88 | 5.78 | 5.59 | 5.77 | 7.53 | 7.56 | 7.61 | 7.53 | 7.45 | 7.63 | 1.62 | 1.73 | 1.45 | 1.89 | 1.9 | 1.6 | 7.16 | 7.27 | 7.17 | 7.17 | 7.14 | 7.31 | 0.54 | 0.61 | 0.51 | 0.55 | 0.55 | 0.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 659675 | 1188 | 646881 | 1250 | 716568.1 | 1865.7 | 7.53 | 7.56 | 7.61 | 7.53 | 7.45 | 7.63 | 7.16 | 7.27 | 7.17 | 7.17 | 7.14 | 7.31 | 986000 | 2000 | 976000 | 2000 | 1955644 | 3900 | 1958000 | 1951744 | 13.4167 | 7.5517 | 1.6983 | 7.2033 | 0.55667 | 22.49% | 7.728% | 36.135 | 50.7333 | 2.755 | 6.0367 | 1970731 | 1955000 | 2385318.2245 | 81.96% | 57 | 134
2024-06-10 | 2025 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 335090.89 | 6:09 | 19:34 | 12286.6 | 12949 | 12919.4 | 12832.2 | 13027.3 | 13074.8 | 13089 | 13494.8 | 12968.5 | 13012.8 | 12804 | 12969.3 | 12913.2 | 12886.8 | 12948.7 | 13007.7 | 12890.5 | 12874.1 | 12928.2 | 12985.3 | 12953.1 | 12933.8 | 12619.8 | 12760 | 12653.3 | 11067.5 | 12628.4 | 12603.5 | 12984.7 | 12864.5 | 12685.1 | 12964.8 | 12970.9 | 12974.6 | 13107.6 | 12986.3 | 13061.9 | 12873.8 | 12922.5 | 12840.7 | 13670.4 | 12390 | 13543.6 | 12153 | 13018.5 | 14204.6 | 12208.2 | 13647 | 12887.2 | 12155.6 | 13051.7 | 12307.1 | 13413.5 | 12037.1 | 13368.6 | 12751.9 | 11846.2 | 13560.6 | 11849.3 | 13511.1 | 13368.8 | 11829.7 | 13136.1 | 12460.8 | 12651.9 | 11840 | 12566.5 | 13073.7 | 13446.7 | 12062.6 | 13273.1 | 11580.4 | 12941.7 | 12683.8 | 11922.1 | 13282.8 | 11714.6 | 13509.3 | 11948.1 | 13293.8 | 12110.5 | 13105.7 | 12246.1 | 13483.5 | 12123.1 | 12944.9 | 12104.1 | 10636.3 | 13214.3 | 12629.5 | 11769.8 | 13579.7 | 13239.9 | 12226.3 | 12084.7 | 13336.5 | 11963.6 | 12377.4 | 13385.3 | 11806.8 | 13484.6 | 11804.9 | 13176.1 | 12090.1 | 13242 | 11417.5 | 13301.3 | 11962.8 | 13116.5 | 11923.9 | 13189.8 | 12121.3 | 11825 | 13128.8 | 12026.5 | 11749.9 | 13223.1 | 13313.2 | 13107.3 | 11999.3 | 13233 | 11826.4 | 12906.2 | 11933.2 | 12722.8 | 11077.6 | 12921.9 | 11829.1 | 12076.9 | 12162 | 11882.2 | 10277.5 | 11938.6 | 10554.5 | 11976.8 | 12008.5 | 13775.5 | 12184.4 | 13832.8 | 12438.9 | 13737.2 | 12305.1 | 12537.8 | 12261.6 | 13425.1 | 13784.9 | 13707.8 | 13664.5 | 13665.6 | 13699.6 | 12566 | 13736 | 13664.3 | 13691.5 | 13825.3 | 13762 | 13730.3 | 12505.7 | 13829.5 | 12547.6 | 37.0492 | 36.8568 | 37.1729 | 36.5338 | 36.7881 | 36.7777 | 0 | 51.6 | 0 | 0 | 51,4 | 51.4 | 3.4208 | 3.4136 | 3.4643 | 3.3947 | 3.3882 | 1.8707 | 6.277 | 6.441 | 6.575 | 6.584 | 6.095 | 6.382 | 7.7073 | 7.7463 | 7.7657 | 7.6924 | 7.5466 | 7.7706 | 1.6991 | 1.7514 | 1.4672 | 1.8944 | 1.8889 | 1.61 | 7.3563 | 7.4424 | 7.314 | 7.3032 | 7.2624 | 7.4039 | 0.55166 | 0.61741 | 0.51183 | 0.54576 | 0.55419 | 0.57894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 660696 | 1189 | 647889 | 1251 | 718590.056 | 1869.867 | 7.7073 | 7.7463 | 7.7657 | 7.6924 | 7.5466 | 7.7706 | 7.3563 | 7.4424 | 7.314 | 7.3032 | 7.2624 | 7.4039 | 1021000 | 1000 | 1008000 | 1000 | 2021956 | 4167 | 2027000 | 2017789 | 13.4167 | 7.7048 | 1.7185 | 7.347 | 0.55997 | 22.3% | 7.622% | 36.8631 | 51.5 | 3.1587 | 6.3923 | 2036258.8 | 2020400 | 2420256 | 83.48% | 45 | 715
2024-06-11 | 2025 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 335090.89 | 6:10 | 19:35 | 12181.4 | 12832.3 | 12813.3 | 12745.2 | 12922 | 12968.5 | 12966.4 | 13437.2 | 12891.1 | 12929.1 | 12712.9 | 12883.4 | 12832.5 | 12779.3 | 12844.3 | 12902 | 12801.7 | 12782 | 12817.2 | 12865.9 | 12846.3 | 12819.8 | 12528.7 | 12658.8 | 12504.6 | 10948.5 | 12510.5 | 12485.2 | 12862.8 | 12766.7 | 12580.6 | 12831.5 | 12851.7 | 12829.2 | 12967.9 | 12856.1 | 12929.9 | 12749.9 | 12814.5 | 12731.6 | 13608.4 | 12352.4 | 13497 | 12131 | 12933.8 | 14077.2 | 12048.5 | 13492.2 | 12781.1 | 12044.5 | 12923.2 | 12185.9 | 13274.5 | 11930.7 | 13231.6 | 12957.8 | 11755.6 | 13444.7 | 11751.3 | 13403.5 | 13256.8 | 11731.5 | 13026.4 | 12373 | 12557.3 | 11754.9 | 12471.2 | 12989.6 | 13350.8 | 11981.5 | 13173.8 | 11497.5 | 12854.4 | 12586 | 11843 | 13171.6 | 11618.8 | 13410 | 11848.4 | 13169.6 | 12040.6 | 13008.4 | 12172.8 | 13400.3 | 12056.1 | 12864.8 | 12038.5 | 10577.4 | 13066.6 | 12549 | 11671.6 | 13438.3 | 13088.9 | 12085.7 | 11951.5 | 13230.3 | 11872.5 | 12305 | 13305.6 | 11733.8 | 13399.2 | 11750.9 | 13106.5 | 12036 | 13169.2 | 11369.7 | 13239.4 | 11925.1 | 13068.2 | 11887 | 13166.4 | 12086.4 | 11735 | 13022.9 | 11959.1 | 11686 | 13138.9 | 13226.9 | 13025.8 | 11943.4 | 13144.3 | 11775.3 | 12839.6 | 11881.9 | 12658.2 | 11042.7 | 12871.8 | 11798 | 11983.2 | 12055.2 | 11801.6 | 10201.8 | 11817.8 | 10453.2 | 11908.8 | 11920.7 | 13722.3 | 12121.9 | 13772.2 | 12381.6 | 13635 | 12187.4 | 12423.9 | 12150.8 | 13340.2 | 13687.5 | 13633.4 | 13584.7 | 13570.2 | 13611 | 12510.9 | 13655.7 | 13549.2 | 13577.6 | 13744.2 | 13666.4 | 13639.4 | 12442.2 | 13741.9 | 12478.3 | 37.9367 | 37.6034 | 37.9939 | 37.4814 | 37.5065 | 37.7554 | 0 | 51.9 | 0 | 0 | 51.6 | 51.7 | 4.1893 | 4.3297 | 4.2172 | 4.1916 | 4.2895 | 3.5491 | 7.482 | 8.235 | 7.384 | 7.603 | 8.42 | 7.497 | 7.699 | 7.7094 | 7.7678 | 7.6737 | 7.5307 | 7.7241 | 1.7678 | 1.8298 | 1.5049 | 2.044 | 1.9243 | 1.7083 | 7.3359 | 7.4019 | 7.2966 | 7.2794 | 7.2371 | 7.3609 | 0.57158 | 0.64548 | 0.53002 | 0.59181 | 0.57344 | 0.61374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 661708 | 1191 | 648890 | 1252 | 720597.923 | 1874 | 7.699 | 7.7094 | 7.7678 | 7.6737 | 7.5307 | 7.7241 | 7.3359 | 7.4019 | 7.2966 | 7.2794 | 7.2371 | 7.3609 | 1012000 | 2000 | 1001000 | 1000 | 2007867 | 4133 | 2010000 | 2003734 | 13.4167 | 7.6841 | 1.7965 | 7.3186 | 0.58768 | 23.38% | 8.03% | 37.7129 | 51.7333 | 4.1277 | 7.7702 | 2021855.2 | 2007000 | 2414863.589 | 83.11% | 57 | 35
2024-06-12 | 2025 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 335090.89 | 6:09 | 19:37 | 12289 | 12853 | 12885 | 12822 | 13007 | 12993 | 12946 | 13400 | 12904 | 12938 | 12723 | 12899 | 12844 | 12801 | 12851 | 12928 | 12806 | 12825 | 12846 | 12911 | 12878 | 12875 | 12624 | 12722 | 12577 | 11010 | 12568 | 12555 | 12912 | 12783 | 12652 | 12870 | 12945 | 12944 | 13060 | 12943 | 12985 | 12814 | 12868 | 12826 | 13749 | 12535 | 13617 | 12321 | 13045 | 14197 | 12180 | 13639 | 12778 | 12115 | 12960 | 12257 | 13326 | 11959 | 13267 | 13196 | 11825 | 13500 | 11834 | 13447 | 13317 | 11811 | 13070 | 12432 | 12682 | 11899 | 12603 | 13119 | 13343 | 12095 | 13258 | 11643 | 12919 | 12718 | 11940 | 13264 | 11742 | 13464 | 11951 | 13251 | 12200 | 13118 | 12337 | 13531 | 12218 | 12999 | 12168 | 10722 | 13151 | 12696 | 11823 | 13554 | 13227 | 12282 | 12169 | 13295 | 11973 | 12501 | 13454 | 11881 | 13517 | 11912 | 13222 | 12186 | 13287 | 11533 | 13369 | 12118 | 13190 | 12053 | 13247 | 12285 | 11879 | 13140 | 12093 | 11855 | 13231 | 13381 | 13126 | 12150 | 13308 | 11973 | 12934 | 12029 | 12815 | 11239 | 13037 | 11995 | 12115 | 12148 | 11942 | 10313 | 11928 | 10540 | 12039 | 12044 | 13875 | 12315 | 13916 | 12577 | 13734 | 12293 | 12525 | 12311 | 13492 | 13862 | 13805 | 13757 | 13746 | 13780 | 12712 | 13817 | 13692 | 13736 | 13864 | 13832 | 13853 | 12647 | 13810 | 12659 | 36.18 | 36.37 | 36.69 | 36.23 | 36.17 | 36.61 | 0 | 50 | 0 | 0 | 49.6 | 50 | 5.15 | 5.44 | 5.39 | 5.3 | 5.25 | 5.33 | 8.88 | 8.85 | 10.07 | 8.73 | 8.69 | 8.54 | 7.65 | 7.65 | 7.75 | 7.65 | 7.52 | 7.72 | 1.78 | 1.84 | 1.53 | 2.11 | 1.95 | 1.74 | 7.29 | 7.35 | 7.28 | 7.25 | 7.22 | 7.36 | 0.58 | 0.66 | 0.54 | 0.62 | 0.59 | 0.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 662726 | 1192 | 649903 | 1254 | 722623.4 | 1878.1 | 7.65 | 7.65 | 7.75 | 7.65 | 7.52 | 7.72 | 7.29 | 7.35 | 7.28 | 7.25 | 7.22 | 7.36 | 1018000 | 1000 | 1013000 | 2000 | 2025477 | 4100 | 2028000 | 2021377 | 13.4667 | 7.6567 | 1.825 | 7.2917 | 0.60333 | 23.84% | 8.274% | 36.375 | 49.8667 | 5.31 | 8.96 | 2039232 | 2024300 | 2432234 | 83.23% | 54 | 0
2024-06-13 | 2025 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 335090.89 | 6:18 | 19:37 | 11446.4 | 11957.2 | 11971.2 | 11899.8 | 12066.6 | 12094.4 | 12110.9 | 12477.2 | 12004.5 | 12049.5 | 11851.2 | 12002.6 | 11954.5 | 11902.6 | 11978.5 | 12035.2 | 11934.6 | 11946.3 | 11956 | 12022.5 | 11993.4 | 11991.4 | 11742.3 | 11842.6 | 11693 | 10254.8 | 11704.4 | 11677.3 | 11988.5 | 11866.8 | 11728.7 | 11941.5 | 12003.2 | 12000.9 | 12120.7 | 12004.5 | 12033.6 | 11891.6 | 11940.8 | 11870.2 | 12566.9 | 11503.9 | 12485.7 | 11324.3 | 12064.1 | 13074.7 | 11256.5 | 12511.3 | 12058.3 | 11285.9 | 12059.9 | 11418.3 | 12390.6 | 11218 | 12305.7 | 12279.9 | 10973.9 | 12496.2 | 11019.4 | 12443.3 | 12332.9 | 10992.7 | 12099.1 | 11559.2 | 11773.8 | 10984 | 11694.2 | 12065.4 | 12429.2 | 11211.5 | 12276.1 | 10784.6 | 11995.6 | 11791.1 | 11115.2 | 12265 | 10904.1 | 12469.9 | 11153.8 | 12333.5 | 11217.2 | 12092.1 | 11337.7 | 12395.3 | 11222.6 | 11914.6 | 11216.9 | 9846.9 | 12031.8 | 11693.8 | 10835.4 | 12371.9 | 12109.4 | 11287.1 | 11178.1 | 12175.2 | 10998.4 | 11441.9 | 12262.7 | 10900 | 12319.9 | 10901.1 | 12073.9 | 11163.1 | 12129.2 | 10562.9 | 12207.4 | 11071.7 | 12058.6 | 11036 | 12121.1 | 11242.1 | 10918.6 | 12040.4 | 11062.3 | 10874.1 | 12095.7 | 12239.3 | 12014 | 11132.2 | 12167.9 | 10970.8 | 11830.6 | 11015.4 | 11705.2 | 10271.3 | 11903.3 | 10932.4 | 11042.2 | 11071.2 | 10880.2 | 9404.2 | 10863.4 | 9612.5 | 10886.9 | 10906.6 | 12463.1 | 11107.3 | 12504.9 | 11319.4 | 12379.7 | 11153.9 | 11361.7 | 11143.7 | 12188.5 | 12492.6 | 12460.2 | 12388.6 | 12368.6 | 12405.9 | 11449 | 12432.7 | 12444 | 12443.4 | 12562.3 | 12526.9 | 12519.4 | 11460.9 | 12521.5 | 11460 | 33.44 | 35.31 | 35.5 | 35.16 | 35.07 | 35.47 | 0 | 47.2 | 0 | 0 | 46.8 | 47 | 6.57 | 6.66 | 6.57 | 6.75 | 6.57 | 6.53 | 10.59 | 11.63 | 10.57 | 10.87 | 10.89 | 10.66 | 7.01 | 7.01 | 7.01 | 6.99 | 6.75 | 6.86 | 1.61 | 1.77 | 1.36 | 1.91 | 1.8 | 1.66 | 6.74 | 6.78 | 6.61 | 6.64 | 6.52 | 6.61 | 0.54 | 0.61 | 0.5 | 0.58 | 0.54 | 0.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 663672 | 1194 | 650826 | 1255 | 724486.6 | 1882.133 | 7.01 | 7.01 | 7.01 | 6.99 | 6.75 | 6.86 | 6.74 | 6.78 | 6.61 | 6.64 | 6.52 | 6.61 | 946000 | 2000 | 923000 | 1000 | 1863200 | 4033 | 1866000 | 1859167 | 13.3167 | 6.9383 | 1.685 | 6.65 | 0.55667 | 24.29% | 8.371% | 34.9917 | 47 | 6.6083 | 10.8683 | 1875734.5 | 1862067 | 2239752 | 83.14% | 59 | 52803
2024-06-14 | 2025 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 335090.89 | 6:15 | 19:35 | 12272.5 | 12790.4 | 12794.8 | 12734.5 | 12891.4 | 12930.5 | 12936.1 | 13329.9 | 12817.9 | 12868.7 | 12672.9 | 12827.6 | 12792.9 | 12723.8 | 12855.2 | 12906.1 | 12822 | 12849 | 12859.8 | 12899.7 | 12906.3 | 12902 | 12702.4 | 12780.3 | 12606.5 | 11036.8 | 12558.3 | 12584.7 | 12950.1 | 12837.5 | 12720.4 | 12896.8 | 13017.2 | 12989.9 | 13101.5 | 13027.3 | 13010.6 | 12870.3 | 12920.9 | 12847.2 | 13804.1 | 12692.7 | 13669.1 | 12488.3 | 13197.9 | 14280.7 | 12356.6 | 13727.3 | 12975.5 | 12109.8 | 12878.4 | 12239.7 | 13253.1 | 12029.6 | 13157 | 13131.7 | 11808.2 | 13373.9 | 11833 | 13338.6 | 13212.6 | 11809.2 | 12970.2 | 12390.1 | 12637.9 | 11870.4 | 12551.6 | 13012.2 | 13293.1 | 12097.8 | 13141.2 | 11595.4 | 12838.2 | 12640.2 | 11913.9 | 13105.8 | 11683.1 | 13314 | 11919 | 13108 | 12147.9 | 12999.6 | 12285.1 | 13392.1 | 12181.6 | 12911.9 | 12175.1 | 10715 | 13053.8 | 12654.2 | 11770.6 | 13390.5 | 13094.1 | 12253.3 | 12132.4 | 13174.1 | 11967.1 | 12403.5 | 13283.5 | 11828.4 | 13399 | 11868.8 | 13141.1 | 12168.6 | 13176.2 | 11515.3 | 13277.9 | 12095 | 13148.6 | 12075.5 | 13198 | 12293.5 | 11826 | 13014.9 | 12082.9 | 11830.8 | 13144.1 | 13241 | 13034.1 | 12098.7 | 13177.3 | 11946.7 | 12888.3 | 12029.1 | 12736.3 | 11193.8 | 12949.1 | 11944.5 | 12091.6 | 12126 | 11935 | 10314.9 | 11912.3 | 10561.9 | 12111.9 | 12123.9 | 13739.4 | 12314.5 | 13808.6 | 12558.8 | 13674.4 | 12378.6 | 12595.1 | 12367.9 | 13521 | 13865 | 13775.8 | 13703 | 13656 | 13678.8 | 12719.9 | 13775 | 13780.5 | 13820.6 | 13920.3 | 13903.9 | 13922 | 12789.2 | 13824.6 | 12788 | 33.9614 | 35.1454 | 35.5259 | 34.9471 | 34.9495 | 35.4252 | 0 | 48.2 | 0 | 0 | 48 | 48.4 | 6.1736 | 6.5912 | 6.2946 | 6.5744 | 6.2987 | 6.2777 | 11.086 | 11.174 | 12.047 | 10.301 | 10.579 | 11.342 | 7.5555 | 7.7216 | 7.7262 | 7.5299 | 7.4049 | 7.6973 | 1.7719 | 1.8889 | 1.5797 | 2.124 | 1.9851 | 1.8029 | 7.2265 | 7.3401 | 7.278 | 7.1579 | 7.1042 | 7.3385 | 0.57852 | 0.66369 | 0.55891 | 0.62503 | 0.58497 | 0.63502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 664689 | 1195 | 651837 | 1257 | 726507.723 | 1886.333 | 7.5555 | 7.7216 | 7.7262 | 7.5299 | 7.4049 | 7.6973 | 7.2265 | 7.3401 | 7.278 | 7.1579 | 7.1042 | 7.3385 | 1017000 | 1000 | 1011000 | 2000 | 2021123 | 4200 | 2025000 | 2016923 | 13.3333 | 7.6059 | 1.8587 | 7.2409 | 0.60769 | 24.44% | 8.393% | 34.9924 | 48.2 | 6.3684 | 11.0882 | 2035659.1 | 2020000 | 2439313.2751 | 82.81% | 51 | 0
2024-06-15 | 2025 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 335090.89 | 6:17 | 19:35 | 12244.3 | 12872.6 | 12928.6 | 12838.5 | 13083.2 | 13126.5 | 13086.9 | 13552.6 | 12908.4 | 12826.3 | 12852.5 | 12967.9 | 13010.1 | 12914.9 | 13022.4 | 13072.6 | 12975.7 | 13002.4 | 13048.6 | 13118.5 | 13066.6 | 13080.5 | 12790.8 | 12904.6 | 12793.5 | 11204.2 | 12773.7 | 12765.2 | 13105.8 | 12950.9 | 12801.6 | 13056.2 | 13112.4 | 13125.1 | 13273.6 | 13164.7 | 13184.1 | 13000.2 | 13037.6 | 12963.6 | 13759.4 | 12576.2 | 13640.1 | 12355.9 | 13151.1 | 14265.8 | 12310.8 | 13708.3 | 13187.7 | 12233.7 | 13103.1 | 12406.7 | 13486.3 | 12148.9 | 13410.8 | 13397.4 | 11901.6 | 13532 | 11929.6 | 13488.2 | 13315.5 | 11878.8 | 13036.1 | 12372.6 | 12703.6 | 11903.7 | 12567.3 | 13063.4 | 13335 | 12061.7 | 13116.5 | 11535.7 | 12723.5 | 12417.9 | 11750.8 | 12901 | 11603 | 13314.4 | 11834.3 | 13049.1 | 12109.5 | 13007.6 | 12240.5 | 13437.1 | 12147.7 | 12911.5 | 12207.6 | 10692.4 | 13222.7 | 12726.6 | 11893.5 | 13635.4 | 13360.7 | 12453.2 | 12331.3 | 13415.9 | 12047.1 | 12478.4 | 13419.7 | 11881.8 | 13520.3 | 11905.1 | 13257.7 | 12210.7 | 13341.4 | 11580.9 | 13434.3 | 12170.6 | 13262.8 | 12119.7 | 13303.1 | 12337 | 11882.8 | 13186.2 | 12173.1 | 11915 | 13319.5 | 13436 | 13204.7 | 12213.9 | 13371.1 | 12037.1 | 13042.1 | 12097.1 | 12847.2 | 11241.5 | 13093.1 | 12015.1 | 12267.5 | 12335.4 | 12037.3 | 10443.1 | 12076.5 | 10636.6 | 11986.2 | 12009.8 | 13671.8 | 12157 | 13757.5 | 12432.1 | 13612.3 | 12256 | 12479 | 12258.1 | 13413 | 13757.9 | 13691.7 | 13666.1 | 13629.7 | 13644.7 | 12618.2 | 13731.6 | 13571.7 | 13587.7 | 13719.4 | 13685 | 13701.7 | 12575.2 | 13714.4 | 12576.4 | 34.18 | 35.81 | 36.22 | 35.69 | 35.63 | 36.09 | 0 | 50.9 | 0 | 0 | 50.4 | 50.8 | 4.78 | 5.07 | 4.89 | 4.92 | 4.93 | 4.67 | 8.67 | 8.78 | 8.69 | 9.08 | 8.67 | 8.8 | 7.78 | 7.89 | 7.77 | 7.65 | 7.59 | 7.75 | 1.84 | 1.93 | 1.62 | 2.19 | 2.03 | 1.81 | 7.38 | 7.48 | 7.32 | 7.27 | 7.28 | 7.35 | 0.6 | 0.68 | 0.56 | 0.65 | 0.61 | 0.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 665713 | 1197 | 652849 | 1258 | 728538.4 | 1890.467 | 7.78 | 7.89 | 7.77 | 7.65 | 7.59 | 7.75 | 7.38 | 7.48 | 7.32 | 7.27 | 7.28 | 7.35 | 1024000 | 2000 | 1012000 | 1000 | 2030677 | 4134 | 2033000 | 2026543 | 13.3 | 7.7383 | 1.9033 | 7.3467 | 0.625 | 24.6% | 8.507% | 35.6033 | 50.7 | 4.8767 | 8.7817 | 2044925.8 | 2029601 | 2450651 | 82.82% | 48 | 750
2024-06-16 | 2025 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 335090.89 | 6:18 | 19:36 | 12189.6 | 12800.3 | 12885.4 | 12796.8 | 12983.6 | 13047 | 13058.5 | 13488 | 12813.1 | 12832.5 | 12758.8 | 12846.5 | 12922 | 12877.3 | 12915.5 | 12989.5 | 12847.3 | 12870 | 12905.4 | 12992.8 | 12963.2 | 12955.1 | 12694.3 | 12796.7 | 12679.3 | 11089.4 | 12654.6 | 12644.1 | 13016.2 | 12867 | 12710.8 | 12972.9 | 13041.3 | 13064.7 | 13183.7 | 13088.9 | 13107 | 12916.4 | 12951.6 | 12898.6 | 13485.5 | 12269.5 | 13321 | 11992.7 | 12801 | 14009.9 | 12009.5 | 13426.5 | 13120.5 | 12154.5 | 13050.6 | 12324.5 | 13434 | 12053.2 | 13360.5 | 13320.2 | 11867.3 | 13561.3 | 11843.7 | 13471.5 | 13273.4 | 11770.8 | 12997.3 | 12291.6 | 12715 | 11904.8 | 12579.9 | 13119.4 | 13412.3 | 12076.7 | 13162.6 | 11540.7 | 12851.4 | 12568.4 | 11836.9 | 13107.8 | 11572.7 | 13318.2 | 11817.2 | 13089.7 | 12151.8 | 13048.4 | 12298.1 | 13489.4 | 12187.8 | 13011.9 | 12250.6 | 10771.6 | 13246.1 | 12775.7 | 11913.4 | 13646.4 | 13336.8 | 12386.1 | 12258.7 | 13423.4 | 12064.1 | 12548.3 | 13464.9 | 11929.5 | 13500.6 | 11894.2 | 13212.4 | 12164.7 | 13226 | 11480.5 | 13304.1 | 12018.8 | 13114.3 | 11938.4 | 13151.7 | 12172 | 11896.2 | 13122.5 | 12067.6 | 11799.6 | 13166.8 | 13271.1 | 13018.6 | 12025 | 13183.3 | 11858.7 | 12834.3 | 11900.5 | 12693.8 | 11077.5 | 12911.9 | 11832.9 | 12083.3 | 12167.2 | 11859.2 | 10291.8 | 11969.8 | 10602.8 | 12066.8 | 12087.5 | 13848.8 | 12239.2 | 13842.6 | 12481.3 | 13702.8 | 12317.3 | 12581.9 | 12330.1 | 13407.3 | 13755.1 | 13712.2 | 13636.3 | 13640.9 | 13725.7 | 12641.6 | 13703.3 | 13563.4 | 13600.1 | 13688.9 | 13670.4 | 13722.6 | 12550.8 | 13706.5 | 12576.8 | 35.4376 | 37.2755 | 37.5428 | 37.1939 | 37.0933 | 37.5235 | 0 | 52.1 | 0 | 0 | 51.9 | 52.3 | 4.8981 | 5.0432 | 4.8817 | 5.0779 | 5.0094 | 4.765 | 8.379 | 8.898 | 8.305 | 8.047 | 8.353 | 8.258 | 7.7509 | 7.8218 | 7.5433 | 7.6766 | 7.5568 | 7.7178 | 1.8322 | 1.921 | 1.5756 | 2.196 | 2.0176 | 1.8015 | 7.3564 | 7.4302 | 7.1576 | 7.2871 | 7.2231 | 7.366 | 0.59047 | 0.67741 | 0.5494 | 0.64856 | 0.60283 | 0.64789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 666731 | 1198 | 653859 | 1259 | 730560.79 | 1894.667 | 7.7509 | 7.8218 | 7.5433 | 7.6766 | 7.5568 | 7.7178 | 7.3564 | 7.4302 | 7.1576 | 7.2871 | 7.2231 | 7.366 | 1018000 | 1000 | 1010000 | 1000 | 2022390 | 4200 | 2026000 | 2018190 | 13.3 | 7.6778 | 1.8906 | 7.3034 | 0.61943 | 24.62% | 8.481% | 37.0111 | 52.1 | 4.9459 | 8.3733 | 2035815.2 | 2021400 | 2423183.4342 | 83.42% | 59 | 0
2024-06-17 | 2025 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 335090.89 | 6:15 | 19:38 | 12174.3 | 12790.1 | 12811.9 | 12741.4 | 12930.3 | 12983.4 | 12981.3 | 13441.3 | 12839.2 | 12806.6 | 12701.1 | 12838.9 | 12831.9 | 12771.7 | 12884.2 | 12923.3 | 12825.2 | 12849 | 12876.7 | 12938 | 12929.8 | 12909.8 | 12668.1 | 12773.4 | 12606 | 11012.1 | 12569.4 | 12578.7 | 12967.5 | 12840.3 | 12691.3 | 12910.2 | 12969.8 | 12946.5 | 13069.2 | 12977.2 | 13051.3 | 12867.5 | 12924.9 | 12861.7 | 13705.9 | 12506.5 | 13580.3 | 12278 | 13056.4 | 14177.8 | 12193.7 | 13607.8 | 13031.6 | 12057.2 | 12943.4 | 12200.2 | 13339.4 | 11961.4 | 13238.4 | 13221.4 | 11721.7 | 13412.8 | 11763.3 | 13367 | 13207.5 | 11714.7 | 12936.5 | 12248.6 | 12591.6 | 11774.2 | 12457.4 | 12989.8 | 13307.3 | 11964.6 | 13096.7 | 11463.7 | 12781.4 | 12522.9 | 11790.2 | 13086.1 | 11541.5 | 13312.5 | 11796.9 | 13100.2 | 12038 | 12991.8 | 12136.7 | 13388.7 | 12049.5 | 12863.2 | 12100.9 | 10624.9 | 13097.2 | 12617.4 | 11733.9 | 13498.9 | 13193.9 | 12245.9 | 12122.2 | 13276.8 | 11894.3 | 12383.3 | 13358.4 | 11796.2 | 13451.5 | 11813.1 | 13164.4 | 12112.8 | 13251 | 11460.9 | 13341.6 | 12035.6 | 13167.9 | 12008.2 | 13217.1 | 12233.2 | 11743.4 | 13045 | 12010.5 | 11749.7 | 13178.6 | 13287.9 | 13054.3 | 12035.6 | 13229.3 | 11880.5 | 12895.7 | 11912.8 | 12762.1 | 11169.5 | 12960.7 | 11922.4 | 12053 | 12089.3 | 11923.8 | 10285.2 | 11886.5 | 10514.5 | 11922.2 | 11926.9 | 13664.5 | 12112.4 | 13711.5 | 12378.1 | 13587.9 | 12185.5 | 12431.9 | 12156.3 | 13286.6 | 13606.8 | 13579.4 | 13531.7 | 13525.2 | 13573.2 | 12509.4 | 13596.3 | 13483.7 | 13520.7 | 13649.7 | 13611.2 | 13613.4 | 12435.7 | 13608.7 | 12457.4 | 36.5601 | 37.6406 | 38.0018 | 37.496 | 37.4827 | 37.9102 | 0 | 51.7 | 0 | 0 | 51.3 | 51.7 | 5.7064 | 5.872 | 5.7693 | 5.9658 | 5.7476 | 5.7654 | 9.547 | 9.305 | 9.904 | 9.444 | 9.52 | 10.067 | 7.6458 | 7.7452 | 7.6462 | 7.5473 | 7.4582 | 7.5891 | 1.8046 | 1.9102 | 1.6025 | 2.1632 | 2.0074 | 1.7781 | 7.1812 | 7.2705 | 7.1366 | 7.0275 | 7.1455 | 7.1499 | 0.57779 | 0.66309 | 0.54955 | 0.63013 | 0.58997 | 0.63282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 667746 | 1200 | 654863 | 1261 | 732574.124 | 1898.933 | 7.6458 | 7.7452 | 7.6462 | 7.5473 | 7.4582 | 7.5891 | 7.1812 | 7.2705 | 7.1366 | 7.0275 | 7.1455 | 7.1499 | 1015000 | 2000 | 1004000 | 2000 | 2013334 | 4266 | 2015000 | 2009068 | 13.3833 | 7.6053 | 1.8777 | 7.1519 | 0.60723 | 24.69% | 8.49% | 37.5152 | 51.5667 | 5.8044 | 9.6312 | 2027039 | 2012200 | 2383193.6232 | 84.43% | 43 | 425
2024-06-18 | 2025 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 335090.89 | 6:18 | 19:38 | 12305 | 12890.2 | 12851.6 | 12796.3 | 12970.6 | 13012.5 | 13012.9 | 13414.6 | 12932.9 | 12927.3 | 12776.1 | 12919.8 | 12892.9 | 12830.5 | 12934.5 | 12948.5 | 12845.6 | 12850.5 | 12887 | 12953.1 | 12936.2 | 12920.8 | 12692.4 | 12784.1 | 12622.1 | 11077 | 12619.2 | 12611.2 | 12942.7 | 12835.3 | 12697.6 | 12875.4 | 12981.3 | 12966.9 | 13105.5 | 13012.1 | 13012.4 | 12835.6 | 12889 | 12835.9 | 13649.1 | 12547.2 | 13535.5 | 12343.7 | 13069.8 | 14099.5 | 12213.6 | 13541.8 | 13037.2 | 12169.3 | 12993.2 | 12321.8 | 13325.1 | 12046.6 | 13282.8 | 13240.2 | 11849.3 | 13449.9 | 11885 | 13408.4 | 13255.2 | 11843.5 | 13002.8 | 12403 | 12715.6 | 11903.2 | 12591.6 | 13060.6 | 13363.9 | 12114.2 | 13197.2 | 11617 | 12903.8 | 12686.2 | 11946 | 13189.4 | 11722.3 | 13396.8 | 11970.7 | 13204.8 | 12187.3 | 13089.7 | 12316.4 | 13441.8 | 12205.9 | 12973 | 12219.5 | 10731.3 | 13129.9 | 12720.5 | 11845.5 | 13511.8 | 13228.4 | 12357.8 | 12237.7 | 13302.2 | 12022.8 | 12495.9 | 13381.7 | 11925.7 | 13445 | 11911.4 | 13201 | 12211.9 | 13224.2 | 11535.9 | 13314.1 | 12097.7 | 13164.5 | 12048.4 | 13235.9 | 12282.9 | 11884.3 | 13112.8 | 12132.8 | 11873.1 | 13217.4 | 13331.3 | 13115.8 | 12159.5 | 13240.3 | 11977 | 12942.9 | 12031.4 | 12801 | 11249.7 | 13030.3 | 12011.6 | 12194.9 | 12243.4 | 12011.9 | 10380.9 | 12033.4 | 10628.9 | 12120.5 | 12131.8 | 13771.3 | 12302.4 | 13817.6 | 12560.1 | 13684.4 | 12364.5 | 12605 | 12369.7 | 13422.9 | 13723.4 | 13717.2 | 13664.7 | 13639.6 | 13678.8 | 12691.8 | 13720.5 | 13606.4 | 13645.4 | 13788.7 | 13732.5 | 13720.4 | 12622.1 | 13747.1 | 12646.4 | 35.4204 | 36.8806 | 37.1207 | 36.7736 | 36.6685 | 37.1973 | 0 | 49.4 | 0 | 0 | 49 | 49.3 | 7.4739 | 7.6145 | 7.6178 | 7.6451 | 7.4039 | 7.6776 | 11.4 | 11.758 | 12.394 | 11.29 | 11.028 | 11.523 | 7.6711 | 7.6909 | 7.5991 | 7.5636 | 7.4652 | 7.6405 | 1.8237 | 1.904 | 1.6145 | 2.1929 | 2.0247 | 1.81 | 7.202 | 7.2665 | 7.1206 | 7.0852 | 7.1486 | 7.2252 | 0.58631 | 0.67298 | 0.5573 | 0.64329 | 0.61092 | 0.6558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 668766 | 1201 | 655874 | 1262 | 734598.324 | 1902.867 | 7.6711 | 7.6909 | 7.5991 | 7.5636 | 7.4652 | 7.6405 | 7.202 | 7.2665 | 7.1206 | 7.0852 | 7.1486 | 7.2252 | 1020000 | 1000 | 1011000 | 1000 | 2024200 | 3934 | 2029000 | 2020266 | 13.3333 | 7.6051 | 1.895 | 7.1747 | 0.6211 | 24.92% | 8.657% | 36.6769 | 49.2333 | 7.5721 | 11.5655 | 2039399.4 | 2023100 | 2411873.4393 | 83.88% | 58 | 505
2024-06-19 | 2025 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 335090.89 | 6:15 | 19:36 | 12028.6 | 12629.8 | 12595.6 | 12531.6 | 12696.7 | 12750.3 | 12768.8 | 13186.4 | 12651.9 | 12691.6 | 12483.9 | 12646.5 | 12581.3 | 12547.7 | 12664 | 12686.4 | 12564.3 | 12573.8 | 12614.4 | 12675.5 | 12632.7 | 12633.2 | 12352.2 | 12467.4 | 12331.6 | 10774.9 | 12298.3 | 12300.4 | 12664.8 | 12532.2 | 12379.1 | 12606.8 | 12664.5 | 12665.7 | 12775.3 | 12673.2 | 12728.1 | 12541.3 | 12589.2 | 12521 | 13388.4 | 12159.7 | 13250.5 | 11935.7 | 12732.7 | 13864.6 | 11819.8 | 13238.6 | 12805.5 | 11854 | 12693.3 | 11985.8 | 13084.6 | 11770.6 | 12994.2 | 12961.6 | 11547.2 | 13231.1 | 11579.1 | 13169.9 | 13027.8 | 11550.2 | 12816.1 | 12160.3 | 12398.7 | 11606.9 | 12290.3 | 12833.8 | 13141.7 | 11839.3 | 12968.2 | 11355.7 | 12633.6 | 12412.4 | 11666.6 | 12979.6 | 11458.8 | 13196.6 | 11697.8 | 13000.6 | 11910.9 | 12854.1 | 12055.2 | 13251.9 | 11936.5 | 12734.2 | 11921.5 | 10493.2 | 12892.1 | 12466.7 | 11507 | 13231.2 | 12935.7 | 11999.9 | 11856.2 | 13015.8 | 11711 | 12144.5 | 13125.5 | 11578.4 | 13170.3 | 11569.8 | 12848 | 11857.7 | 12892 | 11185.6 | 12969 | 11713.8 | 12787.6 | 11670.3 | 12829.8 | 11882.6 | 11586.8 | 12833.6 | 11789.9 | 11533.5 | 12920.5 | 13039.3 | 12781.9 | 11795.8 | 12941 | 11607.1 | 12574.3 | 11666.8 | 12445.5 | 10877.6 | 12653.1 | 11625.8 | 11887.3 | 11947.7 | 11622.3 | 10087.1 | 11741.8 | 10384.2 | 11827.6 | 11858.3 | 13579.7 | 12019.2 | 13643.7 | 12274.6 | 13514.8 | 12110 | 12349.6 | 12123.3 | 13218.3 | 13589.8 | 13543.3 | 13484.8 | 13465.8 | 13505.7 | 12414.1 | 13550 | 13410.8 | 13452.8 | 13521.5 | 13496.8 | 13526.5 | 12322.4 | 13570.9 | 12378.1 | 32.2769 | 36.1217 | 36.4965 | 35.9051 | 36.0324 | 36.4161 | 0 | 48.9 | 0 | 0 | 48.8 | 49.2 | 6.9204 | 7.5338 | 7.0757 | 7.6819 | 7.1619 | 7.6612 | 11.506 | 11.774 | 12.319 | 11.347 | 11.031 | 11.728 | 7.4342 | 7.4555 | 7.3469 | 7.3402 | 7.257 | 7.4457 | 1.7902 | 1.8856 | 1.5807 | 2.1597 | 1.9968 | 1.8095 | 7.0352 | 7.104 | 6.9259 | 6.9306 | 6.9802 | 7.0814 | 0.58141 | 0.66164 | 0.5566 | 0.63659 | 0.60173 | 0.64873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 669763 | 1203 | 656863 | 1263 | 736578.658 | 1906.8 | 7.4342 | 7.4555 | 7.3469 | 7.3402 | 7.257 | 7.4457 | 7.0352 | 7.104 | 6.9259 | 6.9306 | 6.9802 | 7.0814 | 997000 | 2000 | 989000 | 1000 | 1980334 | 3933 | 1983000 | 1976401 | 13.35 | 7.3799 | 1.8704 | 7.0096 | 0.61445 | 25.34% | 8.766% | 35.5415 | 48.9667 | 7.3391 | 11.6175 | 1993896.2 | 1979133 | 2361656.468 | 83.8% | 44 | 0
2024-06-20 | 2025 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 335090.89 | 6:16 | 19:36 | 11931 | 12545.4 | 12525.1 | 12461 | 12609.6 | 12652.7 | 12699.3 | 13187.7 | 12577.3 | 12610.7 | 12404.4 | 12580 | 12474.6 | 12470.7 | 12507 | 12549 | 12418.9 | 12445 | 12475.6 | 12540.8 | 12538.5 | 12499.2 | 12262.8 | 12366.7 | 12205.1 | 10673.1 | 12182.8 | 12160.3 | 12608 | 12509 | 12330.8 | 12540.6 | 12586.9 | 12572.4 | 12658 | 12581.5 | 12716.7 | 12542.6 | 12612.9 | 12513.3 | 13449.7 | 12125 | 13326.2 | 11920.3 | 12741.4 | 14026.2 | 11740.1 | 13248.5 | 12743.9 | 11764.1 | 12590.9 | 11877.9 | 13021.2 | 11641.3 | 12952 | 12902.7 | 11461.1 | 13215 | 11483.3 | 13150 | 13009.2 | 11457.2 | 12765.3 | 12052 | 12285.9 | 11514.2 | 12200.5 | 12775.8 | 13128.3 | 11741.8 | 12932.9 | 11272.4 | 12560.8 | 12316.8 | 11571 | 12946.9 | 11369.1 | 13162.7 | 11593.4 | 12957.7 | 11821.4 | 12802.7 | 11959.5 | 13218.9 | 11825.8 | 12653.7 | 11817.9 | 10395.3 | 12903.5 | 12371.3 | 11449.2 | 13242 | 12882.5 | 11875.7 | 11713.5 | 12978.8 | 11613.2 | 12048.3 | 13079.5 | 11488.6 | 13191.3 | 11487.5 | 12866.7 | 11787.2 | 12988.8 | 11164.5 | 13074.2 | 11720.7 | 12903.5 | 11735.3 | 12961 | 11930.5 | 11511.8 | 12788.4 | 11726.3 | 11450.2 | 12940.3 | 13027.1 | 12815.9 | 11743.8 | 12985.6 | 11601.9 | 12620.2 | 11685.4 | 12515.3 | 10919.3 | 12695.2 | 11637.4 | 11791.7 | 11840.2 | 11659.9 | 10046.6 | 11602.6 | 10277 | 11671.6 | 11715.5 | 13561.2 | 11868.5 | 13643.4 | 12159.6 | 13480.1 | 11974.4 | 12189.8 | 11979.2 | 13175.1 | 13579.5 | 13509.8 | 13455.9 | 13430.1 | 13468.7 | 12311.4 | 13525 | 13369.8 | 13428.5 | 13533.5 | 13507.9 | 13523.7 | 12231.8 | 13548.1 | 12263.2 | 33.0699 | 36.0317 | 36.524 | 35.9833 | 36.0655 | 36.304 | 0 | 49.2 | 0 | 0 | 49.4 | 49.9 | 6.0063 | 6.5826 | 5.9013 | 6.7294 | 6.3437 | 6.3956 | 10.317 | 10.003 | 11.997 | 10.974 | 10.874 | 11.115 | 7.3314 | 7.3235 | 7.3222 | 7.2359 | 7.142 | 7.3056 | 1.7791 | 1.8818 | 1.5743 | 2.1398 | 1.9886 | 1.804 | 6.9515 | 7.0076 | 6.885 | 6.8486 | 6.8768 | 6.9849 | 0.58806 | 0.6629 | 0.56374 | 0.64112 | 0.60699 | 0.65006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 670755 | 1204 | 657850 | 1265 | 738550.858 | 1910.867 | 7.3314 | 7.3235 | 7.3222 | 7.2359 | 7.142 | 7.3056 | 6.9515 | 7.0076 | 6.885 | 6.8486 | 6.8768 | 6.9849 | 992000 | 1000 | 987000 | 2000 | 1972200 | 4067 | 1976000 | 1968133 | 13.3333 | 7.2768 | 1.8613 | 6.9257 | 0.61881 | 25.58% | 8.935% | 35.6631 | 49.5 | 6.3265 | 10.88 | 1985261.6 | 1971066 | 2328309.7954 | 84.66% | 46 | 0
2024-06-21 | 2025 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 335090.89 | 6:18 | 19:35 | 11076.7 | 11671.7 | 11673.5 | 11538.5 | 11830.1 | 11840.1 | 11823.1 | 12369.1 | 11695.4 | 11728.8 | 11613.7 | 11734.8 | 11715.3 | 11722.5 | 11672.9 | 11788.5 | 11586.8 | 11597 | 11687.6 | 11786.6 | 11726.5 | 11712.2 | 11420 | 11570.5 | 11455.8 | 10049.1 | 11490.1 | 11437.9 | 11800.1 | 11667.3 | 11456.3 | 11640.5 | 11677.4 | 11718.9 | 11879.8 | 11754 | 11876.3 | 11682.2 | 11706.4 | 11619.9 | 12607.8 | 11303.7 | 12504.8 | 11088.2 | 11827.6 | 13109.3 | 10990.8 | 12556 | 11976.9 | 11039.3 | 11864 | 11161.3 | 12290.6 | 10936 | 12217.1 | 12146.7 | 10758.8 | 12456.8 | 10780.2 | 12371.3 | 12162.3 | 10720.9 | 11910 | 11200.5 | 11501.9 | 10834.9 | 11433 | 12061.9 | 12337.7 | 11111.7 | 12179.4 | 10683.6 | 11717.2 | 11614 | 10785.8 | 12220.5 | 10659.9 | 12312.1 | 10802.5 | 12171.7 | 11197.2 | 12179.2 | 11300.6 | 12580.6 | 11172.7 | 11945.9 | 11106.8 | 9790.5 | 12152.5 | 11638.7 | 10754 | 12538.1 | 12156.1 | 11150.6 | 10978.4 | 12195.1 | 10878.3 | 11344 | 12361.3 | 10817.8 | 12361.3 | 10755.5 | 11993.9 | 11012.5 | 12137.8 | 10403.9 | 12188.6 | 10891 | 11988.3 | 10899.4 | 12108 | 11085.2 | 10845.5 | 12039.6 | 10958 | 10692.4 | 12087.2 | 12242.5 | 11916.8 | 10995.2 | 12140 | 10818.4 | 11665.6 | 10829.9 | 11567.5 | 10109.8 | 11808.9 | 10861 | 11133.9 | 11209.9 | 10924.7 | 9473.8 | 10971.7 | 9715.3 | 10937.1 | 10988 | 12869.7 | 11181.5 | 12870.4 | 11404.8 | 12772.1 | 11172.3 | 11393.9 | 11197.8 | 12290.4 | 12710.3 | 12643.8 | 12617.7 | 12678.6 | 12699.2 | 11472.5 | 12661.6 | 12521.2 | 12570 | 12700.5 | 12659.1 | 12649.9 | 11344.4 | 12643.2 | 11355.6 | 35.5953 | 35.9467 | 36.1298 | 35.904 | 35.9542 | 36.1893 | 0 | 50.4 | 0 | 0 | 50.4 | 50.5 | 3.8424 | 3.7724 | 3.6123 | 3.958 | 3.7615 | 3.4892 | 9.357 | 8.913 | 8.806 | 8.523 | 8.269 | 8.836 | 6.8647 | 6.8824 | 6.8104 | 6.8043 | 6.6848 | 6.7526 | 1.6562 | 1.7777 | 1.4624 | 2.0043 | 1.8658 | 1.6952 | 6.5676 | 6.6174 | 6.4337 | 6.4659 | 6.494 | 6.5312 | 0.54637 | 0.62033 | 0.5229 | 0.59714 | 0.567 | 0.59733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 671684 | 1206 | 658774 | 1266 | 740398.858 | 1915 | 6.8647 | 6.8824 | 6.8104 | 6.8043 | 6.6848 | 6.7526 | 6.5676 | 6.6174 | 6.4337 | 6.4659 | 6.494 | 6.5312 | 929000 | 2000 | 924000 | 1000 | 1848000 | 4133 | 1850000 | 1843867 | 13.2833 | 6.7999 | 1.7436 | 6.5183 | 0.57518 | 25.64% | 8.824% | 35.9532 | 50.4333 | 3.7393 | 8.784 | 1859979.6 | 1846933 | 2172965.0898 | 85% | 54 | 7793
2024-06-22 | 2025 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 335090.89 | 6:20 | 19:40 | 7326.4 | 7759.7 | 7711.5 | 7693.9 | 7772.5 | 7802.2 | 7830.2 | 8114.6 | 7766.7 | 7708.8 | 7650 | 7750.4 | 7737.7 | 7719.3 | 7785.4 | 7799.7 | 7751.5 | 7779.7 | 7816.7 | 7867.6 | 7820.9 | 7815.1 | 7633.9 | 7695.6 | 7609.4 | 6690.9 | 7619.7 | 7587.6 | 7841.4 | 7764.8 | 7668.8 | 7820.1 | 7835.6 | 7829.1 | 7878.4 | 7819.2 | 7893.6 | 7787.6 | 7829.3 | 7813.5 | 8286.6 | 7448 | 8238.8 | 7330.2 | 7913.2 | 8796.5 | 7314.8 | 8233.8 | 7975.5 | 7388.2 | 7908.4 | 7475.6 | 8166.6 | 7297.3 | 8131.7 | 8068 | 7214.5 | 8288.5 | 7197.3 | 8230.7 | 8127.1 | 7143.8 | 7934.4 | 7539.5 | 7736.1 | 7259.2 | 7676.7 | 8020.3 | 8211.8 | 7423.2 | 8115.8 | 7132 | 7784.7 | 7753.8 | 7195.4 | 8078.4 | 7145.6 | 8231.7 | 7270.2 | 8086.4 | 7413.5 | 8023.1 | 7491.5 | 8272.8 | 7406.1 | 7887.7 | 7388 | 6492.6 | 7956.9 | 7692.3 | 6780.3 | 8077.6 | 7997.3 | 7402.6 | 7326.8 | 8029.1 | 7166.1 | 7375.6 | 8048.3 | 7001.8 | 8097.6 | 7037.5 | 7907.2 | 7217.9 | 7987.8 | 6849.2 | 8016.5 | 7122.1 | 7916 | 7163.5 | 7938.8 | 7220.9 | 6972.6 | 7728.7 | 7081.9 | 6909.6 | 7833.7 | 7903.3 | 7747.5 | 7111.8 | 7860 | 6999 | 7627.1 | 7066 | 7551.3 | 6552.1 | 7647.2 | 6957.7 | 7112.4 | 7153.7 | 6948.5 | 6040 | 6940.3 | 6143.4 | 6781.9 | 6846.4 | 8158.8 | 7063.2 | 8106.1 | 7163.2 | 8031.9 | 7079 | 7192.8 | 7064.2 | 7772.4 | 8034.4 | 8023.1 | 7995.1 | 8045.1 | 8066.3 | 7236.2 | 8013.7 | 8110.1 | 8026.4 | 8033.8 | 8001.4 | 8012 | 7159.7 | 8188.9 | 7216.4 | 30.7625 | 31.2745 | 31.2372 | 31.355 | 31.3709 | 31.3099 | 0 | 39.5 | 0 | 0 | 39.4 | 39.4 | 4.1724 | 4.1584 | 4.0475 | 4.1334 | 4.1761 | 2.499 | 16.691 | 15.359 | 14.137 | 14.718 | 16.325 | 15.077 | 4.3884 | 4.4709 | 4.4584 | 4.4862 | 4.3029 | 4.2764 | 0.98518 | 0.94433 | 0.89152 | 1.2289 | 1.0128 | 0.81679 | 4.2208 | 4.3186 | 4.2369 | 4.3054 | 4.1281 | 4.0071 | 0.28478 | 0.32776 | 0.2761 | 0.31785 | 0.29508 | 0.29616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 672302 | 1207 | 659372 | 1267 | 741610.791 | 1919.2 | 4.3884 | 4.4709 | 4.4584 | 4.4862 | 4.3029 | 4.2764 | 4.2208 | 4.3186 | 4.2369 | 4.3054 | 4.1281 | 4.0071 | 618000 | 1000 | 598000 | 1000 | 1211933 | 4200 | 1214000 | 1207733 | 13.3333 | 4.3972 | 0.97991 | 4.2028 | 0.29962 | 22.28% | 7.129% | 31.2183 | 39.4333 | 3.8644 | 15.3845 | 1219184.6 | 1210933 | 1430307.601 | 84.66% | 63 | 215709
2024-06-23 | 2025 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 335090.89 | 6:21 | 19:38 | 11541 | 12186 | 12177 | 12132 | 12268 | 12282 | 12320 | 12757 | 12218 | 12231 | 12016 | 12201 | 12139 | 12098 | 12255 | 12273 | 12157 | 12133 | 11997 | 12200 | 12173 | 12153 | 11823 | 11959 | 11853 | 10399 | 11821 | 11781 | 12182 | 12056 | 11887 | 12164 | 12218 | 12202 | 12320 | 12188 | 12278 | 12086 | 12156 | 12142 | 13047 | 11820 | 12889 | 11601 | 12274 | 13425 | 11441 | 12947 | 12407 | 11418 | 12279 | 11561 | 12681 | 11328 | 12597 | 12568 | 11149 | 12824 | 11140 | 12805 | 12690 | 11141 | 12343 | 11638 | 11823 | 11041 | 11755 | 12248 | 12653 | 11240 | 12410 | 10783 | 12118 | 11808 | 11154 | 12432 | 10926 | 12697 | 11135 | 12459 | 11264 | 12221 | 11393 | 12609 | 11290 | 12055 | 11319 | 9918 | 12437 | 11836 | 11060 | 12838 | 12523 | 11531 | 11378 | 12629 | 11304 | 11669 | 12717 | 11152 | 12809 | 11166 | 12460 | 11425 | 12553 | 10801 | 12640 | 11328 | 12459 | 11335 | 12479 | 11533 | 11154 | 12420 | 11392 | 11104 | 12568 | 12647 | 12029 | 11378 | 12588 | 11225 | 12246 | 11340 | 12129 | 10546 | 12280 | 11260 | 11426 | 11487 | 11314 | 9745 | 11241 | 9948 | 11201 | 11258 | 12982 | 11420 | 13087 | 11698 | 12914 | 11560 | 11727 | 11518 | 12814 | 13163 | 13117 | 13020 | 12964 | 12966 | 11877 | 13035 | 13128 | 13158 | 13301 | 13238 | 13158 | 11921 | 13212 | 11947 | 36.29 | 36.91 | 37.06 | 36.96 | 36.98 | 37.01 | 0 | 48.4 | 0 | 0 | 48.3 | 48.7 | 3.14 | 3.16 | 3.12 | 3.24 | 3.12 | 0.5 | 6.09 | 6.69 | 7 | 6.96 | 6.15 | 6.48 | 7.1 | 7.1 | 7.2 | 7.08 | 7.05 | 7.22 | 1.66 | 1.7 | 1.41 | 1.92 | 1.85 | 1.67 | 6.81 | 6.84 | 6.81 | 6.74 | 6.77 | 6.9 | 0.55 | 0.62 | 0.5 | 0.57 | 0.54 | 0.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 673263 | 1209 | 660325 | 1269 | 743519.1 | 1923.3 | 7.1 | 7.1 | 7.2 | 7.08 | 7.05 | 7.22 | 6.81 | 6.84 | 6.81 | 6.74 | 6.77 | 6.9 | 961000 | 2000 | 953000 | 2000 | 1908309 | 4100 | 1910000 | 1904209 | 13.2833 | 7.125 | 1.7017 | 6.8117 | 0.56 | 23.88% | 8.221% | 36.8683 | 48.4667 | 2.7133 | 6.5617 | 1921099 | 1907700 | 2253004.2075 | 84.67% | 55 | 8789
2024-06-24 | 2025 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 335090.89 | 6:19 | 19:37 | 9919.9 | 10305.6 | 10235.7 | 10275.8 | 10243.5 | 10222.9 | 10286 | 10640.5 | 10324.9 | 10464.8 | 10065.9 | 10230.8 | 10122.6 | 10116.4 | 10198.2 | 10176.6 | 10069.1 | 10054.7 | 10085.5 | 10164 | 10053.2 | 10088.1 | 9671.1 | 9854.5 | 9701.5 | 8662.3 | 9893.6 | 9785.9 | 9948.3 | 9653.1 | 9368.4 | 9734.8 | 9428.2 | 9612 | 9999.8 | 9738.8 | 9697.5 | 9442.5 | 9430.5 | 9320.4 | 10736 | 9785 | 10510.5 | 9551.5 | 9879 | 10836.8 | 9242.4 | 10527.4 | 10332.1 | 9594.2 | 10239.3 | 9712.4 | 10540.6 | 9475.9 | 10477.7 | 10448.7 | 9350.5 | 10689 | 9389.3 | 10653.4 | 10577.7 | 9389.8 | 10372.3 | 9866.9 | 9899.2 | 9286.3 | 9883.6 | 10219.9 | 10621.4 | 9514.8 | 10448.6 | 9183.4 | 10257.6 | 10040.3 | 9496 | 10566.6 | 9363.2 | 10724.6 | 9558 | 10608.6 | 9566 | 10350 | 9619.2 | 10571.9 | 9484.4 | 10048 | 9430.3 | 8269.9 | 9825.3 | 9666 | 8663.9 | 10043.7 | 9693.7 | 8873.4 | 8753.6 | 9658.1 | 8554.6 | 8889.7 | 9692.9 | 8533.2 | 9778.1 | 8526.1 | 9521.4 | 8766.8 | 9635.5 | 8329.1 | 9710 | 8713.2 | 9520.2 | 8661.5 | 9474.3 | 8747.7 | 8583.5 | 9526.4 | 8744.1 | 8517.6 | 9648.6 | 9716.1 | 9509.5 | 8743.3 | 9629.4 | 8557.3 | 9305.3 | 8613.5 | 9171.5 | 7969.5 | 9328.1 | 8528.6 | 8782.4 | 8843.5 | 8578.3 | 7456.9 | 8703.9 | 7730.9 | 9046 | 9098.5 | 10533.8 | 9157.6 | 10641.1 | 9419.4 | 10497.3 | 9310.5 | 9432 | 9303.1 | 10596.1 | 10948.7 | 10823.9 | 10716.7 | 10578.6 | 10510.4 | 9622.4 | 10713.7 | 11147.1 | 11105 | 11243.6 | 11145 | 11040.1 | 9948.1 | 11028.2 | 9960.1 | 39.4959 | 39.2014 | 39.3179 | 39.1747 | 39.1656 | 39.3031 | 0 | 50.8 | 0 | 0 | 50.1 | 50.8 | 2.449 | 2.4014 | 2.334 | 2.503 | 2.4043 | 0.74793 | 7.04 | 6.676 | 7.157 | 6.469 | 6.776 | 6.201 | 6.0662 | 5.9079 | 5.9548 | 6.0298 | 5.4466 | 6.0117 | 1.4868 | 1.3722 | 1.2537 | 1.7141 | 1.4022 | 1.2826 | 5.7791 | 5.6487 | 5.6115 | 5.7643 | 5.2364 | 5.6576 | 0.48283 | 0.53781 | 0.43982 | 0.50806 | 0.45178 | 0.50158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 674060 | 1210 | 661083 | 1270 | 745069.925 | 1927.467 | 6.0662 | 5.9079 | 5.9548 | 6.0298 | 5.4466 | 6.0117 | 5.7791 | 5.6487 | 5.6115 | 5.7643 | 5.2364 | 5.6576 | 797000 | 1000 | 758000 | 1000 | 1550825 | 4167 | 1553000 | 1546658 | 13.3 | 5.9028 | 1.4186 | 5.6163 | 0.48698 | 24.03% | 8.671% | 39.2764 | 50.5667 | 2.1399 | 6.7198 | 1558465.3 | 1549800 | 1860967.8804 | 83.28% | 60 | 132459
2024-06-25 | 2025 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 335090.89 | 6:15 | 19:47 | 9927.9 | 10538.7 | 10595.6 | 10489.6 | 10749.3 | 10851.1 | 10764.5 | 11276.8 | 10571.2 | 10416.9 | 10529.3 | 10619.1 | 10763.1 | 10663 | 10838.8 | 10871.8 | 10776.1 | 10742.3 | 10827.3 | 10881.5 | 10760.3 | 10792.3 | 10491.1 | 10587.2 | 10540.6 | 9150.6 | 10459.7 | 10457 | 10843 | 10706.7 | 10533 | 10803.4 | 10710 | 10745.5 | 10887.6 | 10784.9 | 10890.1 | 10703.3 | 10739.5 | 10678.4 | 11433.1 | 10177.5 | 11288.3 | 9958.2 | 10728.6 | 11986.3 | 9985.6 | 11389.3 | 10889 | 10004.7 | 10786.4 | 10127.4 | 11169.8 | 10011.6 | 10979.5 | 10918.9 | 9596.3 | 11075.2 | 9725.2 | 11083.2 | 10943.3 | 9671.3 | 10660.8 | 10083.8 | 10075.9 | 9318.7 | 10005.7 | 10313.7 | 10848.3 | 9555.2 | 10593 | 9200.2 | 10429 | 10115.4 | 9609.5 | 10668.1 | 9348.7 | 10969 | 9560.5 | 10682 | 9535.3 | 10395.3 | 9694.9 | 10680.2 | 9550.8 | 10206 | 9471.6 | 8352.8 | 10569.8 | 10011 | 9456.1 | 11069.1 | 10864.4 | 10072.4 | 9983.1 | 11004.9 | 9865.2 | 10226.1 | 11189.9 | 9741.2 | 11311.5 | 9797.5 | 10952.2 | 10026.9 | 11006.1 | 9463.9 | 11051.7 | 9862.5 | 10853.2 | 9827.7 | 10780.8 | 9978 | 9749.2 | 10818.3 | 9900.1 | 9657 | 10931.8 | 11080.6 | 10789.7 | 9983.7 | 10981.6 | 9781.9 | 10550.3 | 9774.8 | 10457.1 | 9189.5 | 10698.6 | 9834.1 | 10020.5 | 10036.1 | 9864.9 | 8525.5 | 9803.7 | 8645.4 | 9412.2 | 9498.4 | 11133 | 9654.3 | 11224.3 | 9883.1 | 11061.8 | 9776.5 | 9958.7 | 9701.7 | 10758.9 | 11216.2 | 11033.6 | 11040.6 | 11066.5 | 11072.3 | 10072.3 | 11194.3 | 10712.8 | 10790.2 | 10890.7 | 10902.8 | 10983.4 | 9867 | 10946.5 | 9874 | 36.8528 | 36.908 | 36.9771 | 36.8777 | 36.7494 | 37.1025 | 0 | 49.6 | 0 | 0 | 49.3 | 49.4 | 4.0162 | 4.1062 | 3.803 | 4.2711 | 4.1236 | 3.1501 | 14.324 | 17.198 | 18.61 | 17.448 | 15.858 | 14.674 | 6.2396 | 6.3538 | 6.2578 | 6.0135 | 6.2281 | 6.0505 | 1.479 | 1.535 | 1.271 | 1.6613 | 1.6043 | 1.3834 | 6.0477 | 6.1747 | 5.9654 | 5.7949 | 6.0002 | 5.8347 | 0.47675 | 0.54775 | 0.43807 | 0.48945 | 0.47413 | 0.49082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 674899 | 1212 | 661902 | 1271 | 746724.058 | 1931.533 | 6.2396 | 6.3538 | 6.2578 | 6.0135 | 6.2281 | 6.0505 | 6.0477 | 6.1747 | 5.9654 | 5.7949 | 6.0002 | 5.8347 | 839000 | 2000 | 819000 | 1000 | 1654133 | 4066 | 1655000 | 1650067 | 13.5333 | 6.1906 | 1.489 | 5.9696 | 0.48616 | 24.05% | 8.144% | 36.9112 | 49.4333 | 3.9117 | 16.352 | 1663576.9 | 1654000 | 1975958.114 | 83.71% | 67 | 14209
2024-06-26 | 2025 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 335090.89 | 6:25 | 19:42 | 8791.3 | 9201.1 | 9168.8 | 9121.9 | 9232.4 | 9288.5 | 9269.9 | 9650.8 | 9239.3 | 9238.1 | 9069.5 | 9201.2 | 9144.5 | 9121.3 | 9256.8 | 9253.3 | 9208.4 | 9194.2 | 9200.1 | 9209.2 | 9217.4 | 9205.7 | 8998.4 | 9080.8 | 8935.7 | 7841.2 | 8951.6 | 8919.8 | 9216.5 | 9144.5 | 9013.8 | 9160.5 | 9119.4 | 9158.6 | 9267.9 | 9176.9 | 9279.2 | 9143.6 | 9183.3 | 9104.4 | 9928.2 | 8874.9 | 9798.3 | 8718.2 | 9338.2 | 10493.5 | 8654.1 | 9881.8 | 9282.2 | 8602.1 | 9215.9 | 8680.4 | 9569.6 | 8528.2 | 9445.4 | 9457.5 | 8303.8 | 9577.9 | 8395.6 | 9559.7 | 9471.5 | 8376.6 | 9191.8 | 8728.7 | 8808.8 | 8272.7 | 8779.8 | 9152.5 | 9492.7 | 8458.2 | 9333.1 | 8143.6 | 9098.1 | 8905.2 | 8383.5 | 9387.9 | 8253.1 | 9578.7 | 8433.3 | 9436.7 | 8491.4 | 9189.5 | 8612.6 | 9512.7 | 8488.3 | 9057.1 | 8437.6 | 7443.5 | 9299.8 | 8855.6 | 8230 | 9594.1 | 9282.2 | 8572.2 | 8489.6 | 9373.8 | 8340.5 | 8600.3 | 9382.4 | 8217.9 | 9561.8 | 8245.1 | 9281.4 | 8475.3 | 9403.3 | 8055.2 | 9472.8 | 8451.1 | 9361.1 | 8521 | 9382.2 | 8645.9 | 8217.3 | 9135.3 | 8411.1 | 8202.4 | 9319.2 | 9353.9 | 9223 | 8423.6 | 9350.1 | 8366.2 | 9116.2 | 8482.1 | 9063.2 | 7897.9 | 9162.1 | 8431 | 8498.4 | 8531.7 | 8511.9 | 7296.6 | 8389 | 7366.1 | 8350 | 8368.3 | 9609.3 | 8354.7 | 9664.3 | 8564.1 | 9613.1 | 8489.1 | 8626.9 | 8509.2 | 9214.7 | 9603.2 | 9517.3 | 9492.5 | 9487.4 | 9521.6 | 8630.3 | 9555 | 9486.2 | 9522.3 | 9522.7 | 9495 | 9490.2 | 8490.4 | 9621.4 | 8544.3 | 35.5956 | 36.1956 | 36.2164 | 36.3566 | 36.2705 | 36.2988 | 0 | 46.4 | 0 | 0 | 45.5 | 46.2 | 2.9654 | 2.9811 | 2.8313 | 2.97 | 3.0009 | 1.1724 | 10.205 | 8.365 | 8.415 | 8.162 | 6.636 | 6.799 | 5.1867 | 5.1893 | 5.3065 | 5.0867 | 5.108 | 5.0916 | 1.2248 | 1.2098 | 1.0043 | 1.4256 | 1.2505 | 1.0695 | 5.0413 | 5.068 | 5.0703 | 4.9592 | 4.9549 | 4.8955 | 0.41043 | 0.45829 | 0.36132 | 0.43241 | 0.38229 | 0.41393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 675625 | 1213 | 662609 | 1273 | 748153.392 | 1935.733 | 5.1867 | 5.1893 | 5.3065 | 5.0867 | 5.108 | 5.0916 | 5.0413 | 5.068 | 5.0703 | 4.9592 | 4.9549 | 4.8955 | 726000 | 1000 | 707000 | 2000 | 1429334 | 4200 | 1430000 | 1425134 | 13.2833 | 5.1615 | 1.1974 | 4.9982 | 0.40978 | 23.2% | 8.199% | 36.1556 | 46.0333 | 2.6535 | 8.097 | 1435590.9 | 1428300 | 1683503.864 | 84.84% | 60 | 75821
2024-06-27 | 2025 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 335090.89 | 6:23 | 19:28 | 10829.5 | 11462.5 | 11355 | 11284.6 | 11490.2 | 11421.2 | 11511.5 | 11886.7 | 11414.4 | 11384.2 | 11265.6 | 11420.4 | 11281 | 11318.8 | 11345.6 | 11290.3 | 11213.1 | 11141 | 11165 | 11230.2 | 11207.4 | 11188.4 | 10951.4 | 11049.6 | 10910.4 | 9614.4 | 10938.7 | 10875.2 | 11257.2 | 11170.7 | 10962.8 | 11192.4 | 11212.9 | 11238.2 | 11297 | 11173.4 | 11291.2 | 11119.6 | 11155.1 | 11162.5 | 11814.2 | 10626.2 | 11692 | 10416.2 | 11133.6 | 12439.8 | 10426.8 | 11853.1 | 11502.9 | 10783.1 | 11414 | 10868.6 | 11721 | 10511.7 | 11749.3 | 11622.7 | 10498.8 | 12009.9 | 10549.8 | 12014.8 | 11890.3 | 10518.6 | 11599.2 | 11039.5 | 10872.9 | 10304.7 | 10879.2 | 11352.6 | 11793 | 10423.7 | 11477.9 | 9973.4 | 11392.3 | 10947.2 | 10601.9 | 11548.1 | 10340.6 | 11959.2 | 10604 | 11739.1 | 10497.5 | 11257.9 | 10580 | 11732.2 | 10573.3 | 11227.3 | 10707.9 | 9406.8 | 11578.7 | 11155.5 | 10353.7 | 11903.1 | 11591.7 | 10732.7 | 10581.3 | 11571.2 | 10405.5 | 10809.2 | 11641.1 | 10250.5 | 11738.4 | 10288.7 | 11441 | 10480.2 | 11545.6 | 9992.3 | 11603.2 | 10455 | 11415.9 | 10427.2 | 11404.7 | 10615.5 | 10218.4 | 11163.1 | 10345.5 | 10068.4 | 11328.5 | 11324.7 | 11158.7 | 10217.4 | 11262.6 | 10095.6 | 11054.5 | 10300.2 | 10861.2 | 9475.8 | 10992.3 | 10042.8 | 10248.1 | 10329.6 | 10033.1 | 8736.2 | 9955.3 | 8817.3 | 9905.2 | 10040.2 | 11847.1 | 10351.3 | 11826.3 | 10505.1 | 11625.8 | 10232.4 | 10340.6 | 10308.2 | 11405 | 11845.3 | 11664.9 | 11674.8 | 11686.8 | 11724.6 | 10676.2 | 11748.2 | 11783.5 | 11696.8 | 11825.1 | 11750.4 | 11766.1 | 10551 | 11770.3 | 10584.6 | 33.5208 | 34.6732 | 34.2835 | 34.6403 | 34.4524 | 34.5836 | 0 | 47.997 | 0 | 0 | 47.3 | 47.5 | 4.2367 | 4.093 | 3.9579 | 4.206 | 4.2177 | 2.9795 | 15.992 | 12.833 | 13.393 | 12.725 | 13.391 | 12.28 | 6.6998 | 6.6416 | 6.5319 | 6.6576 | 6.4516 | 6.4775 | 1.5925 | 1.5763 | 1.3542 | 1.9214 | 1.6525 | 1.3859 | 6.4584 | 6.4182 | 6.2102 | 6.4466 | 6.2678 | 6.1397 | 0.53297 | 0.596 | 0.49194 | 0.58969 | 0.52946 | 0.5489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 676516 | 1215 | 663475 | 1274 | 749906.059 | 1939.8 | 6.6998 | 6.6416 | 6.5319 | 6.6576 | 6.4516 | 6.4775 | 6.4584 | 6.4182 | 6.2102 | 6.4466 | 6.2678 | 6.1397 | 891000 | 2000 | 866000 | 1000 | 1752667 | 4067 | 1754000 | 1748600 | 13.0833 | 6.5767 | 1.5805 | 6.3235 | 0.54816 | 24.03% | 8.669% | 34.359 | 47.599 | 3.9485 | 13.4357 | 1763715.1 | 1751801 | 2115420.3193 | 82.81% | 58 | 6693
2024-06-28 | 2025 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 335090.89 | 6:17 | 19:31 | 6700.6 | 7035.9 | 6882.1 | 6884.8 | 6931.2 | 6963.1 | 7045.6 | 7358 | 7084.7 | 7026.4 | 6965.5 | 7072.4 | 7028.6 | 7000 | 7048.5 | 7062.9 | 6998.7 | 7009.7 | 7090.1 | 7141.6 | 7177.5 | 7154.9 | 7064.6 | 7124.1 | 7080.6 | 6273.5 | 7015.4 | 7016.1 | 7242.6 | 7111.2 | 7028.1 | 7191.4 | 7229.1 | 7228.9 | 7312.5 | 7194.9 | 7227.3 | 7125.7 | 7189.9 | 7216.9 | 7514.9 | 6790.4 | 7498.2 | 6755.5 | 7272 | 7970.8 | 6761.9 | 7519.2 | 7171 | 6755.2 | 7179 | 6892.7 | 7418.9 | 6579.4 | 7497.7 | 7452.9 | 6705.3 | 7691.6 | 6601 | 7570.8 | 7458.6 | 6584.5 | 7295.8 | 6863.7 | 7270.3 | 6851.3 | 7177 | 7436.3 | 7656.7 | 6834.4 | 7463 | 6498 | 7305.2 | 7043.5 | 6681.6 | 7327.1 | 6452.7 | 7466.5 | 6561.3 | 7248.5 | 6897.3 | 7320.6 | 7020 | 7679.4 | 7019.2 | 7473 | 7058.1 | 6279.1 | 7687.2 | 7421.8 | 6874.4 | 7801.6 | 7581.5 | 7082.6 | 7008.2 | 7728.8 | 7170.3 | 7373.6 | 7903.7 | 7063.2 | 7929.4 | 7096.1 | 7783.4 | 7263.7 | 7798.4 | 6902.8 | 7859 | 7240.2 | 7790.1 | 7242.8 | 7955.9 | 7438 | 7039.1 | 7710.3 | 7207.8 | 7037.8 | 7859 | 7907 | 7803.1 | 7245.7 | 7891 | 7185.5 | 7746.9 | 7308.6 | 7697.7 | 6788.6 | 7785.3 | 7230.5 | 7291.4 | 7294 | 7214.4 | 6263.3 | 7150.4 | 6291.7 | 6938.4 | 6917.2 | 7744.9 | 6874.1 | 7779.3 | 7033.7 | 7806.1 | 6987.7 | 7099.3 | 7001.3 | 7341 | 7570 | 7563.8 | 7525.4 | 7554.9 | 7641.2 | 6943.1 | 7587.9 | 7438.9 | 7424.7 | 7457.4 | 7472.9 | 7494 | 6780.3 | 7607.3 | 6836.9 | 27.5713 | 31.6129 | 31.8231 | 31.6038 | 31.6203 | 31.8076 | 0 | 44.1 | 0 | 0 | 43.9 | 43.7 | 3.7095 | 3.8961 | 3.7091 | 3.9858 | 3.9009 | 2.5808 | 8.981 | 9.634 | 9.297 | 9.038 | 8.816 | 8.352 | 3.9084 | 4.0932 | 3.9927 | 4.1657 | 4.3695 | 4.0157 | 0.91663 | 0.94809 | 0.8333 | 1.1251 | 1.069 | 0.78912 | 3.8356 | 4.0263 | 3.8803 | 4.078 | 4.2742 | 3.8892 | 0.29076 | 0.33871 | 0.27901 | 0.33355 | 0.31861 | 0.30101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 677082 | 1216 | 664061 | 1276 | 751053.259 | 1944.067 | 3.9084 | 4.0932 | 3.9927 | 4.1657 | 4.3695 | 4.0157 | 3.8356 | 4.0263 | 3.8803 | 4.078 | 4.2742 | 3.8892 | 566000 | 1000 | 586000 | 2000 | 1147200 | 4267 | 1149000 | 1142933 | 13.2333 | 4.0909 | 0.94689 | 3.9973 | 0.31028 | 23.15% | 7.762% | 31.0065 | 43.9 | 3.6304 | 9.0197 | 1154724.2 | 1139600 | 1343320.2664 | 84.83% | 60 | 7179
2024-06-29 | 2025 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 335090.89 | 6:29 | 19:30 | 9303 | 9827.3 | 9871.1 | 9706.9 | 10032.6 | 10072.6 | 10055.9 | 10432.9 | 9787 | 9825.6 | 9737.4 | 9812.1 | 9810.4 | 9788.9 | 9978.8 | 9915.1 | 9941.9 | 9987.9 | 9984 | 9994.7 | 10060.6 | 10054.3 | 9743.5 | 9879.8 | 9757.3 | 8441.4 | 9644.4 | 9703.5 | 10086.1 | 9923.9 | 9817.9 | 10047.9 | 9986.8 | 10057 | 9981.9 | 10041.2 | 10156.3 | 9966.2 | 9978.9 | 9870.2 | 10589.7 | 9524.4 | 10544.2 | 9415 | 10086.4 | 11275.2 | 9314.4 | 10589 | 9957.5 | 9197.5 | 9843 | 9259.4 | 10272.3 | 9179 | 10081.7 | 10091.5 | 8889.6 | 10310.4 | 8995.9 | 10243.5 | 10147.3 | 8928.1 | 9913.5 | 9438 | 9459.3 | 8869.9 | 9429.8 | 9863.8 | 10164.8 | 9126.1 | 10101.3 | 8789.3 | 9676.5 | 9239.5 | 8983.7 | 10070.6 | 8797.3 | 10275.5 | 8976.4 | 10013.1 | 9204.7 | 9967 | 9375.3 | 10303.9 | 9195 | 9823.8 | 9129.1 | 8045 | 10085.3 | 9518.1 | 8940.6 | 10453.2 | 10194 | 9407.4 | 9284.4 | 10243.4 | 9151.2 | 9351.7 | 10223 | 8880.3 | 10262 | 8859.7 | 9878.5 | 9039.3 | 9919.4 | 8513.6 | 9948.4 | 8881.2 | 9837 | 8947.4 | 9901.1 | 9079.6 | 8909 | 9858.9 | 8988.2 | 8770.4 | 9916.1 | 9999.9 | 9778.1 | 8956.4 | 9905.8 | 8816.8 | 9614.6 | 8883.9 | 9590.1 | 8342.3 | 9675.6 | 8848 | 9025.3 | 9118.4 | 8877.1 | 7672.1 | 8884.1 | 7909.6 | 8780.6 | 8833.7 | 10348 | 8948.6 | 10322.8 | 9074.4 | 10223 | 8965.9 | 9137.7 | 8971.5 | 9919.4 | 10304.1 | 10277.9 | 10211.4 | 10195.2 | 10256.8 | 9214.1 | 10251.9 | 10357 | 10345.7 | 10297.1 | 10289.1 | 10308 | 9183.5 | 10408.8 | 9228.7 | 31.3931 | 32.6624 | 33.0205 | 32.5595 | 32.6918 | 32.8076 | 0 | 45 | 0 | 0 | 44.7 | 44.9 | 3.7133 | 4.0667 | 3.3965 | 4.207 | 3.9865 | 3.2751 | 6.951 | 7.379 | 6.878 | 7.4 | 7.192 | 7.865 | 5.5611 | 5.6991 | 5.6044 | 5.4498 | 5.3628 | 5.4217 | 1.157 | 1.2515 | 0.99161 | 1.2806 | 1.263 | 1.1007 | 5.3898 | 5.5335 | 5.3106 | 5.2691 | 5.2328 | 5.2098 | 0.37276 | 0.42032 | 0.3543 | 0.35432 | 0.37781 | 0.38282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 677863 | 1218 | 664818 | 1278 | 752586.592 | 1948.533 | 5.5611 | 5.6991 | 5.6044 | 5.4498 | 5.3628 | 5.4217 | 5.3898 | 5.5335 | 5.3106 | 5.2691 | 5.2328 | 5.2098 | 781000 | 2000 | 757000 | 2000 | 1533333 | 4466 | 1534000 | 1528867 | 13.0167 | 5.5165 | 1.1741 | 5.3243 | 0.37706 | 21.28% | 7.082% | 32.5225 | 44.8667 | 3.7742 | 7.2775 | 1541827.8 | 1532466 | 1822642.0132 | 84.08% | 57 | 29338
2024-06-30 | 2025 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 335090.89 | 6:21 | 19:41 | 9470.7 | 10001.4 | 9853.6 | 9802.8 | 9922.6 | 10000.6 | 10098.6 | 10359.4 | 9962.9 | 9910.3 | 9769.6 | 9895.6 | 9755.9 | 9731.8 | 9825.1 | 9751.4 | 9789.9 | 9802.2 | 9854.8 | 9874.6 | 9942 | 9933.8 | 9719.2 | 9743.4 | 9580.9 | 8483.8 | 9598.6 | 9566.3 | 9836.6 | 10017.1 | 9986.7 | 9877.6 | 10294.8 | 10070.5 | 9864 | 9886.9 | 10127.1 | 10117.8 | 10282.9 | 10228.8 | 11246.5 | 10274.4 | 11190.5 | 10168.7 | 10814.4 | 11883 | 10321.3 | 11371.6 | 9933.3 | 9267.9 | 9792.1 | 9410.9 | 10170.2 | 9066.4 | 10091.4 | 10083.5 | 9137.1 | 10371.2 | 9101.1 | 10266.3 | 10190.4 | 9091.7 | 10115.1 | 9749.3 | 9784 | 9224.9 | 9782.2 | 10146.1 | 10472.3 | 9549.2 | 10388.9 | 9164.7 | 10086.3 | 9987 | 9432.7 | 10393.9 | 9280.8 | 10536.3 | 9393.4 | 10327.1 | 9602 | 10281.6 | 9672.4 | 10494.6 | 9552 | 10076 | 9378 | 8319.3 | 10406 | 9798.2 | 9321.1 | 10687.2 | 10356.3 | 9726.6 | 9707.1 | 10534.9 | 9797.6 | 10101 | 10950.7 | 9749.4 | 11139.8 | 9825.3 | 10905.8 | 9995.4 | 10941.8 | 9449.9 | 10946.9 | 9773.1 | 10963.5 | 10072.1 | 11171 | 10233.3 | 9711.6 | 10692.5 | 9870.4 | 9690.3 | 10741.7 | 10857.7 | 10628.4 | 10010.5 | 10843.7 | 9826 | 10518.3 | 9988.4 | 10623 | 9346.4 | 10653.5 | 9941.6 | 10026.6 | 10056.4 | 10019.8 | 8563.4 | 9841.8 | 8697.4 | 9828.9 | 9914.7 | 11265.9 | 10009.1 | 11170.5 | 10093 | 11116.6 | 10117.9 | 10337.7 | 10185.5 | 10683.3 | 10891.3 | 10956.4 | 10869.7 | 10930.7 | 11086.1 | 10196 | 10932.1 | 11045.5 | 11013.9 | 11214.4 | 11067.4 | 10928.1 | 9959 | 11010.5 | 10074.8 | 34.2193 | 34.439 | 34.8834 | 34.3414 | 34.4527 | 34.704 | 0 | 47.1 | 0 | 0 | 48.2 | 48.4 | 3.7239 | 3.8595 | 3.6847 | 3.9179 | 3.8926 | 3.0377 | 6.587 | 6.386 | 7.573 | 6.487 | 6.192 | 6.744 | 5.8061 | 5.7654 | 6.3995 | 5.8667 | 6.2157 | 6.1376 | 1.3296 | 1.3053 | 1.2512 | 1.5903 | 1.5105 | 1.2591 | 5.6025 | 5.5687 | 6.0404 | 5.6558 | 6.0519 | 5.8841 | 0.41638 | 0.46391 | 0.42354 | 0.4309 | 0.45692 | 0.45234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 678656 | 1219 | 665637 | 1279 | 754194.926 | 1951 | 5.8061 | 5.7654 | 6.3995 | 5.8667 | 6.2157 | 6.1376 | 5.6025 | 5.5687 | 6.0404 | 5.6558 | 6.0519 | 5.8841 | 793000 | 1000 | 819000 | 1000 | 1608334 | 2467 | 1610000 | 1605867 | 13.3333 | 6.0318 | 1.3743 | 5.8006 | 0.44066 | 22.78% | 7.597% | 34.5067 | 47.9 | 3.686 | 6.6615 | 1617629 | 1607800 | 1961921.3942 | 81.95% | 65 | 6451
2024-07-01 | 2025 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 335090.89 | 6:21 | 19:43 | 8487.6 | 8921.6 | 8888 | 8817 | 8971.7 | 9006 | 9049.4 | 9345.5 | 8940.6 | 8970.2 | 8872 | 8958.4 | 8924.3 | 8911.2 | 8964.6 | 8978.4 | 8850.9 | 8865.2 | 8887.9 | 8906.8 | 8908.9 | 8901.9 | 8709.6 | 8791.9 | 8679.5 | 7602.1 | 8668.8 | 8637.5 | 8924.7 | 8864.5 | 8746.6 | 8908.9 | 8843.1 | 8824 | 8914.7 | 8834.7 | 8885.8 | 8768.3 | 8803.8 | 8771.4 | 9425.6 | 8576 | 9354.8 | 8415.5 | 8966.1 | 9840.1 | 8445.7 | 9439.4 | 8862 | 8190.1 | 8746.1 | 8288.5 | 9019.8 | 8133.1 | 8940.2 | 8923.6 | 7968.7 | 9113.4 | 7982.4 | 9074.5 | 8987.6 | 7957.6 | 8837.3 | 8417.7 | 8416 | 7864.1 | 8369.8 | 8664.6 | 8975.5 | 8031 | 8862.7 | 7724 | 8623.8 | 8460.4 | 7979.1 | 8853.3 | 7838.1 | 9005 | 7985.3 | 8882.9 | 8180.6 | 8839.1 | 8265.3 | 9092.6 | 8155.8 | 8694.3 | 8161.8 | 7167.2 | 8931.9 | 8519.2 | 7964.1 | 9176.2 | 8940.3 | 8302.7 | 8211.8 | 9009.9 | 8175.6 | 8443.8 | 9132.7 | 8064.7 | 9231.4 | 8079.9 | 9003.3 | 8287.4 | 9051.1 | 7832.4 | 9092.3 | 8190.6 | 8986.5 | 8203.9 | 9038.7 | 8330.7 | 8150.3 | 9019.4 | 8303.7 | 8111.2 | 9121.1 | 9162 | 9024.8 | 8285.5 | 9107.6 | 8165 | 8902.5 | 8254.9 | 8796.5 | 7654.2 | 8903.9 | 8176.4 | 8499 | 8573.8 | 8365.2 | 7217.7 | 8389 | 7451.5 | 8418.2 | 8455.9 | 9656.1 | 8524.8 | 9708.3 | 8712.2 | 9688.7 | 8642.2 | 8763.7 | 8619.3 | 9429.1 | 9753.6 | 9692.5 | 9619.3 | 9616.9 | 9671.4 | 8842.2 | 9701.4 | 9755.5 | 9753.7 | 9784.8 | 9747.6 | 9748.1 | 8799.1 | 9786.1 | 8825.8 | 32.7262 | 34.2895 | 34.7549 | 34.2573 | 34.4038 | 34.5057 | 0 | 48.3 | 0 | 0 | 48.3 | 48.7 | 4.7969 | 5.4565 | 4.511 | 5.6182 | 5.5003 | 5.0212 | 8.832 | 9.102 | 7.713 | 8.327 | 8.577 | 8.602 | 6.6496 | 6.6552 | 6.7517 | 6.6321 | 6.5204 | 6.6269 | 1.5299 | 1.5772 | 1.3373 | 1.8028 | 1.6221 | 1.4324 | 6.4576 | 6.4791 | 6.4239 | 6.4046 | 6.3273 | 6.4075 | 0.47052 | 0.52184 | 0.44756 | 0.49669 | 0.46537 | 0.48612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 679352 | 1219 | 666335 | 1279 | 1371.666 | 0.333 | 6.6496 | 6.6552 | 6.7517 | 6.6321 | 6.5204 | 6.6269 | 6.4576 | 6.4791 | 6.4239 | 6.4046 | 6.3273 | 6.4075 | 696000 | 0 | 698000 | 0 | 1371666 | 333 | 1394000 | 1371333 | 13.3667 | 6.6393 | 1.5503 | 6.4167 | 0.48135 | 23.35% | 7.502% | 34.1562 | 48.4333 | 5.1507 | 8.5255 | 1398058.9 | 1370600 | 2138894 | 64.08% | 47 | 136100
2024-07-02 | 2025 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 335090.89 | 6:13 | 19:40 | 11355.1 | 11875 | 11875.2 | 11849 | 11914.7 | 11933.7 | 11936.6 | 12307.6 | 11911.9 | 12003.5 | 11649.2 | 11830.2 | 11842.1 | 11730.6 | 11939.6 | 11940.5 | 11851.4 | 11873.6 | 11868.3 | 11867.6 | 12004.7 | 11918.6 | 11783.5 | 11884.5 | 11690.5 | 10129 | 11532.5 | 11577.8 | 12069.4 | 11967.3 | 11818.9 | 12030.9 | 12055.6 | 12012 | 12080.1 | 12007.5 | 12118 | 11974.1 | 12016.4 | 11982.5 | 12511.1 | 11391 | 12447.2 | 11214.6 | 11945.3 | 13003.6 | 11171.3 | 12518 | 12000.5 | 11078.5 | 11891.7 | 11216.1 | 12263.7 | 11052 | 12146.1 | 12123.7 | 10748.7 | 12330 | 10801.7 | 12300.2 | 12214.6 | 10785 | 12030.5 | 11499.9 | 11482.5 | 10744.5 | 11421.5 | 11844 | 12262.6 | 10950.4 | 12073.3 | 10527.1 | 11805.8 | 11536.7 | 10904 | 12118.7 | 10742.4 | 12428.1 | 11007.2 | 12212.3 | 11020.2 | 11892.8 | 11129.1 | 12216 | 10939.8 | 11656.3 | 10927.9 | 9588.8 | 12170.6 | 11481.5 | 10881.8 | 12582.5 | 12329.8 | 11410.5 | 11289.1 | 12484.1 | 11218.9 | 11623 | 12559.1 | 11094.1 | 12584.8 | 11089.9 | 12322.4 | 11374 | 12354.4 | 10713.9 | 12360.6 | 11149.9 | 12107.7 | 11027.9 | 12127.6 | 11178.7 | 11097.3 | 12298 | 11306.5 | 11061.5 | 12376.5 | 12463.7 | 12207.7 | 11252.3 | 12311.7 | 10996.3 | 11974.6 | 11012.4 | 11695.8 | 10180.1 | 11931.5 | 10914 | 11383.9 | 11491.3 | 10980.7 | 9633.7 | 11226.2 | 9959.8 | 11167.4 | 11150.3 | 12624.3 | 11213.9 | 12629.8 | 11451 | 12677 | 11326.9 | 11535.6 | 11329.6 | 12063.8 | 12362.8 | 12287.7 | 12300.7 | 12374.2 | 12458.9 | 11413.7 | 12412.8 | 12205.4 | 12223.9 | 12350.3 | 12315.4 | 12282.6 | 11195.5 | 12344.9 | 11213.7 | 33.8712 | 34.624 | 35.0911 | 34.4781 | 34.6795 | 34.7916 | 0 | 48.7 | 0 | 0 | 48.7 | 48.08 | 4.6161 | 5.5047 | 4.3876 | 5.5037 | 5.3356 | 4.8244 | 10.013 | 9.244 | 8.351 | 9.327 | 8.575 | 9.23 | 6.8905 | 7.0959 | 6.9837 | 6.8838 | 7.0584 | 6.9079 | 1.5925 | 1.7086 | 1.3899 | 1.8834 | 1.797 | 1.5298 | 6.6307 | 6.8533 | 6.5694 | 6.5793 | 6.8135 | 6.6431 | 0.52895 | 0.60795 | 0.50765 | 0.56729 | 0.55298 | 0.54253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 680289 | 1220 | 667264 | 1280 | 3208.8 | 2.733 | 6.8905 | 7.0959 | 6.9837 | 6.8838 | 7.0584 | 6.9079 | 6.6307 | 6.8533 | 6.5694 | 6.5793 | 6.8135 | 6.6431 | 937000 | 1000 | 929000 | 1000 | 1837134 | 2400 | 1864000 | 1834734 | 13.45 | 6.97 | 1.6502 | 6.6815 | 0.55122 | 23.68% | 8.25% | 34.5892 | 48.4933 | 5.0287 | 9.1233 | 1872310.6 | 1859600 | 2225783 | 83.55% | 66 | 40643
2024-07-03 | 2025 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 335090.89 | 6:27 | 19:37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12378.6 | 12480.8 | 12237.8 | 12377 | 12376.1 | 12331.9 | 12456.5 | 12465.1 | 12468.5 | 12486.8 | 12533.7 | 12552.1 | 12536.3 | 12524.8 | 12188.3 | 12337.3 | 12219.8 | 10704.8 | 12210.1 | 12163.4 | 12554.1 | 12464.4 | 12260.2 | 12429 | 12498.2 | 12505.8 | 12640.6 | 12528.6 | 12668.3 | 12455.3 | 12492.2 | 12449.2 | 13445.7 | 12067 | 13344.2 | 11841.9 | 12724.1 | 14051.4 | 11906.6 | 13475.5 | 12713.6 | 11695.9 | 12544.6 | 11845.8 | 13053.3 | 11616.5 | 12920.9 | 12922.9 | 11346 | 13121 | 11400 | 13060.2 | 12892.9 | 11330 | 12657.3 | 11968.2 | 12148.9 | 11370.9 | 12049 | 12574.1 | 12997.5 | 11555.9 | 12774.3 | 11086.5 | 12390.8 | 12094.4 | 11401.7 | 12734.4 | 11179.7 | 13030.7 | 11441 | 12817.8 | 11638.5 | 12571.9 | 11758.6 | 13066.5 | 11639.2 | 12458.7 | 11634.6 | 10263.9 | 12897.1 | 12237.9 | 11448 | 13290.9 | 12882.9 | 11845.4 | 11725.7 | 13033.6 | 11588.8 | 11989.5 | 13100.2 | 11432.7 | 13218.8 | 11454.1 | 12850.9 | 11762.2 | 12982.5 | 11134.4 | 13041.4 | 11654.4 | 12852.6 | 11675.3 | 12773.4 | 11868.5 | 11437.3 | 12737.3 | 11688.1 | 11427.2 | 12961.3 | 13012.6 | 12790.9 | 11669 | 12943.4 | 11527.6 | 12594.7 | 11637.4 | 12461.9 | 10813.2 | 12601.5 | 11524.5 | 11789.4 | 11869.5 | 11573.8 | 10021.9 | 11637.2 | 10292.7 | 11654.9 | 11686.8 | 13550.5 | 11792.8 | 13616.5 | 12064.1 | 13491.5 | 11914.4 | 12148.1 | 11935.9 | 13001.6 | 13425.3 | 13359.9 | 13321 | 13337.3 | 13409.2 | 12152.3 | 13408.1 | 13302.9 | 13357.9 | 13514.4 | 13449.9 | 13396.2 | 12004.3 | 13473.4 | 12064.4 | 33.1 | 35.39 | 35.89 | 35.26 | 35.38 | 35.67 | 0 | 49.5 | 0 | 0 | 49.7 | 50.2 | 4.98 | 5.87 | 5.03 | 5.84 | 5.59 | 5.54 | 9.27 | 9.34 | 9.75 | 9.2 | 8.9 | 9.29 | 7.29 | 7.36 | 7.44 | 7.27 | 7.28 | 7.37 | 1.72 | 1.78 | 1.52 | 2.03 | 1.87 | 1.63 | 7 | 7.09 | 7 | 6.96 | 7.01 | 7.07 | 0.56 | 0.63 | 0.54 | 0.6 | 0.57 | 0.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 681176 | 1221 | 668245 | 1281 | 5071.4 | 6.333 | 7.29 | 7.36 | 7.44 | 7.27 | 7.28 | 7.37 | 7 | 7.09 | 7 | 6.96 | 7.01 | 7.07 | 887000 | 1000 | 981000 | 1000 | 1862600 | 3600 | 1866000 | 1859000 | 13.1667 | 7.335 | 1.7583 | 7.0217 | 0.57833 | 23.97% | 8.236% | 35.115 | 49.8 | 5.475 | 9.2917 | 1874187.8 | 1861800 | 2332850 | 79.81% | 48 | 74
2024-07-04 | 2025 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 335090.89 | 6:22 | 19:31 | 10610.5 | 10610.5 | 10811.6 | 10811.6 | 10972.3 | 10972.3 | 11157.45 | 11157.45 | 10877.2 | 10904.3 | 10750 | 10877 | 10868.1 | 10820.1 | 10944.7 | 10954.2 | 10883.8 | 10886.3 | 10893.6 | 10929.8 | 10954.9 | 10925.4 | 10746.5 | 10833.2 | 10661.7 | 9339.8 | 10640.1 | 10628.1 | 10967.2 | 10897.6 | 10767.7 | 10948.5 | 10972 | 10951.5 | 11020.3 | 10952.2 | 11038.3 | 10900.4 | 10941.2 | 10916.1 | 11658.9 | 10630.2 | 11588.3 | 10446.7 | 11134.2 | 12127.6 | 10452.1 | 11671.6 | 11076.4 | 10270.3 | 10958.2 | 10400.3 | 11312.2 | 10173.5 | 11222.5 | 11190.6 | 10017.1 | 11459.2 | 9948 | 11373.3 | 11241.1 | 9974.6 | 11092.8 | 10572.6 | 10771.1 | 10117.7 | 10678.2 | 11094.7 | 11388.6 | 10284 | 11238.6 | 9879.4 | 10961.5 | 10766.7 | 10139.8 | 11239.1 | 9961.6 | 11393.6 | 10151 | 11241.4 | 10319.8 | 11101.8 | 10439.9 | 11440.6 | 10322.3 | 10996.1 | 10316.9 | 9087.7 | 11266.1 | 10827.9 | 10111.1 | 11565.9 | 11268.4 | 10457.5 | 10334.2 | 11384.3 | 10297.9 | 10655.3 | 11491.7 | 10181.9 | 11529.1 | 10183.2 | 11279.3 | 10444.1 | 11347.2 | 9870 | 11406.3 | 10329.1 | 11258.5 | 10311.1 | 11340.8 | 10485.9 | 10197.4 | 11234 | 10382.5 | 10158 | 11368 | 11416 | 11238.4 | 10354 | 11344.7 | 10230.5 | 11086 | 10303.1 | 10987.4 | 9621.7 | 11124.3 | 10139.8 | 10466.6 | 10527 | 10315.5 | 8922.5 | 10364.9 | 9180.2 | 10361.1 | 10384.3 | 11796.4 | 10480.2 | 11860.6 | 10711.1 | 11798.8 | 10617.5 | 10808.7 | 10584.7 | 11409.5 | 11733.2 | 11714.9 | 11677.3 | 11672 | 11716.8 | 10776.8 | 11713.1 | 11635.9 | 11649.5 | 11712.2 | 11683.8 | 11688.8 | 10636.7 | 11794.9 | 10679.9 | 35.0524 | 34.9529 | 35.3792 | 34.8758 | 34.956 | 35.231 | 0 | 48 | 0 | 0 | 48.2 | 48.4 | 4.6853 | 5.1996 | 4.4992 | 5.1683 | 4.9813 | 4.9729 | 9.001 | 9.418 | 9.247 | 9.354 | 8.763 | 8.584 | 6.175 | 6.2596 | 6.3069 | 6.2194 | 6.362 | 6.3276 | 1.4534 | 1.5132 | 1.2812 | 1.7427 | 1.6298 | 1.3876 | 6.0522 | 6.1571 | 6.0591 | 6.0782 | 6.2036 | 6.1866 | 0.44012 | 0.50128 | 0.42463 | 0.47944 | 0.45832 | 0.46873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 682040 | 1223 | 669110 | 1282 | 6795.801 | 10.8 | 6.175 | 6.2596 | 6.3069 | 6.2194 | 6.362 | 6.3276 | 6.0522 | 6.1571 | 6.0591 | 6.0782 | 6.2036 | 6.1866 | 864000 | 2000 | 865000 | 1000 | 1724401 | 4467 | 1726000 | 1719934 | 13.15 | 6.2751 | 1.5013 | 6.1228 | 0.46208 | 23.93% | 7.547% | 35.0746 | 48.2 | 4.9178 | 9.0612 | 1734907.9 | 1723201 | 2037877 | 84.56% | 48 | 12293
2024-07-05 | 2025 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 335090.89 | 6:19 | 19:39 | 10837.6 | 11419.3 | 11388.5 | 11273.4 | 11554.6 | 11616.3 | 11553.2 | 12122 | 10288.4 | 8241.5 | 11301.5 | 11440.5 | 11461.2 | 11390.5 | 11541.7 | 11567.2 | 11481.4 | 11515.1 | 11510.1 | 11538.7 | 11563.7 | 11522.9 | 11334.2 | 11418.3 | 11236.2 | 9827.7 | 11228.8 | 11190 | 11594.7 | 11534.1 | 11351.9 | 11577.9 | 11552.8 | 11550.2 | 11644.5 | 11536.2 | 11669 | 11483.7 | 11547.2 | 11528.4 | 12455.7 | 11179.2 | 12352.9 | 11011.6 | 11756.4 | 13034 | 10991.8 | 12507.7 | 11689.7 | 10730.6 | 11552.3 | 10881.5 | 12053.7 | 10691.6 | 11851.3 | 11887.4 | 10364.1 | 12015.8 | 10436.3 | 11960.5 | 11784.7 | 10399 | 11535 | 10918.8 | 11075.8 | 10379.8 | 10973.9 | 11485.7 | 11878.3 | 10583.8 | 11708.2 | 10175.8 | 11337.9 | 11138.8 | 10474.4 | 11766.1 | 10315.4 | 12008.6 | 10548.2 | 11811.8 | 10645.9 | 11529.9 | 10811.5 | 11964.2 | 10661 | 11418.3 | 10608.8 | 9355 | 11747.1 | 11175 | 10430.4 | 12189.4 | 11816.6 | 10879.5 | 10780.3 | 11935.2 | 10618.4 | 11006.6 | 12051.4 | 10523.9 | 12193.4 | 10542.2 | 11811.4 | 10833.9 | 11900.6 | 10241.3 | 11948.1 | 10706.7 | 11731.9 | 10664.5 | 11819.8 | 10849.2 | 10525.3 | 11733.1 | 10765.1 | 10506.6 | 11930.4 | 11985.3 | 11766 | 10743.4 | 11918.4 | 10604.2 | 11550 | 10646.5 | 11415.7 | 9955.7 | 11588.9 | 10579.7 | 10833.9 | 10866.2 | 10690.4 | 9226.9 | 10671.5 | 9379.3 | 10501.3 | 10497.4 | 12151.5 | 10581.9 | 12238.1 | 10794 | 12142.2 | 10692.2 | 10908.7 | 10657.8 | 11802.2 | 12209 | 12119.8 | 12071.6 | 12022.1 | 12057.4 | 10928 | 12125.3 | 12139.4 | 12185.6 | 12323.3 | 12262.8 | 12206.9 | 10925 | 12227 | 10956.2 | 35.84 | 36.07 | 36.3 | 35.96 | 35.96 | 36.36 | 0 | 48.4 | 0 | 0 | 48 | 48.1 | 5.83 | 6.02 | 6.02 | 5.97 | 5.84 | 5.78 | 9.62 | 9.46 | 10.44 | 10.6 | 8.96 | 9.67 | 6.57 | 6.65 | 6.71 | 6.45 | 6.63 | 6.5 | 1.56 | 1.64 | 1.37 | 1.82 | 1.72 | 1.46 | 6.37 | 6.48 | 6.37 | 6.23 | 6.41 | 6.31 | 0.51 | 0.59 | 0.49 | 0.56 | 0.54 | 0.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 682944 | 1224 | 670007 | 1283 | 8591.067 | 13.667 | 6.57 | 6.65 | 6.71 | 6.45 | 6.63 | 6.5 | 6.37 | 6.48 | 6.37 | 6.23 | 6.41 | 6.31 | 904000 | 1000 | 897000 | 1000 | 1795266 | 2867 | 1799000 | 1792399 | 13.3333 | 6.585 | 1.595 | 6.3617 | 0.53833 | 24.22% | 8.462% | 36.0817 | 48.1667 | 5.91 | 9.7917 | 1805639.8 | 1795134 | 2118158 | 84.75% | 53 | 10059
2024-07-06 | 2025 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 335090.89 | 6:17 | 19:38 | 11223.4 | 11851.6 | 11843 | 11736.3 | 11975.4 | 12039.6 | 11979.3 | 12492.4 | 10638.9 | 8384.8 | 11744.8 | 11886 | 11894.7 | 11835.5 | 11922.4 | 11960.9 | 11885.7 | 11895 | 11908 | 11935.1 | 11957.1 | 11914.5 | 11649.2 | 11775.2 | 11622 | 10169.7 | 11590.9 | 11575.3 | 11969.9 | 11843.3 | 11646.5 | 11873.9 | 11934.3 | 11922 | 12004.4 | 11916 | 12050.8 | 11825.9 | 11871.8 | 11851.3 | 12764 | 11531.3 | 12662.6 | 11334.1 | 12090.5 | 13216.5 | 11305.8 | 12771.3 | 12135.2 | 11189.6 | 12008.6 | 11325.5 | 12436.7 | 11103.3 | 11215.2 | 10142.9 | 10857.3 | 12505.4 | 10905.7 | 12438.5 | 12251.1 | 10853.7 | 12061.5 | 11411.5 | 11607.4 | 10849.1 | 11493.4 | 11974.2 | 12392.3 | 11038.4 | 12192.8 | 10590.9 | 11853.5 | 11583.9 | 10917.8 | 12214.2 | 10732.2 | 12429 | 10954 | 12253.3 | 11084.4 | 11989.4 | 11235.5 | 12418 | 11105.7 | 11876.3 | 11081.2 | 9763.4 | 12241.4 | 11671 | 10872.3 | 12627.1 | 12268.5 | 11302.4 | 11184.4 | 12367.8 | 11019.3 | 11424.7 | 12446.2 | 10884.2 | 12485.2 | 10874.8 | 12125.6 | 11153.1 | 12206.6 | 10514.7 | 12245.1 | 10967.3 | 12033.1 | 10933.1 | 11974.9 | 11104.5 | 10906.1 | 12117.6 | 11084.8 | 10844.4 | 12236.6 | 12321.6 | 12078.8 | 11041.5 | 12198.3 | 10857 | 11840.3 | 10936.6 | 11692.8 | 10175.8 | 11853.5 | 10869.7 | 11182.8 | 11277.6 | 10938.4 | 9494.7 | 11085.8 | 9827.1 | 11169.2 | 11164.9 | 12818.5 | 11228.3 | 12899 | 11461.3 | 12811.4 | 11365.6 | 11588.8 | 11367.2 | 12481 | 12831.6 | 12780.6 | 12729.4 | 12702.9 | 12724.6 | 11612 | 12787.4 | 12826.7 | 12847.6 | 12988.9 | 12923.1 | 12869.4 | 11592 | 12963.5 | 11634.5 | 34.5555 | 35.3478 | 35.6892 | 35.1374 | 35.3142 | 35.5842 | 0 | 47 | 0 | 0 | 46.8 | 47.2 | 7.356 | 8.398 | 7.4963 | 8.5602 | 8.2682 | 8.4891 | 11.876 | 12.267 | 12.343 | 12.541 | 11.798 | 13.381 | 6.2359 | 6.8352 | 6.8801 | 6.7174 | 6.7789 | 6.8316 | 1.509 | 1.6878 | 1.4468 | 1.9375 | 1.7712 | 1.5504 | 6.6051 | 6.6901 | 6.5612 | 6.5306 | 6.5859 | 6.6563 | 0.52519 | 0.59192 | 0.49332 | 0.56418 | 0.53409 | 0.55111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 683876 | 1225 | 670939 | 1284 | 10449.201 | 16.6 | 6.2359 | 6.8352 | 6.8801 | 6.7174 | 6.7789 | 6.8316 | 6.6051 | 6.6901 | 6.5612 | 6.5306 | 6.5859 | 6.6563 | 932000 | 1000 | 932000 | 1000 | 1858134 | 2933 | 1862000 | 1855201 | 13.35 | 6.7132 | 1.6504 | 6.6048 | 0.5433 | 24.59% | 8.226% | 35.2714 | 47 | 8.0946 | 12.3677 | 1871103.4 | 1857734 | 2215678 | 83.84% | 53 | 0
2024-07-07 | 2025 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 335090.89 | 6:29 | 19:40 | 6456.3 | 6866.8 | 6849.4 | 6767.8 | 6933 | 6980.4 | 7017.3 | 7312.9 | 6872.5 | 6819.1 | 6830.7 | 6909.2 | 6932.1 | 6906.3 | 7050.6 | 7030.6 | 7026.9 | 7058.8 | 7040 | 7056.5 | 7126.8 | 7091.4 | 6963.3 | 7027.6 | 2081.1 | 1811.6 | 2072.9 | 2071.9 | 2161.5 | 2155.3 | 2120.4 | 2154 | 7120.6 | 7069.7 | 7082.7 | 7038.5 | 7156 | 7089.8 | 7134.4 | 7131.3 | 7963.1 | 7140.8 | 7891.1 | 7012.2 | 7489.1 | 8395.4 | 6923.6 | 7936.4 | 7135.3 | 6562.6 | 7047.4 | 6642.1 | 7365.4 | 6521.3 | 7260.9 | 7243.7 | 6382.4 | 7408.2 | 6382.3 | 7324.7 | 7195.8 | 6350.8 | 7010.9 | 6603.3 | 6839.8 | 6431.8 | 6784 | 7137.2 | 6956.5 | 6469.8 | 7203.6 | 6244 | 6821.1 | 6406.7 | 6230 | 6746.7 | 6223.3 | 7248 | 6317.7 | 7085.5 | 6573.7 | 7105.1 | 6704.4 | 7420.9 | 6625.5 | 7120.8 | 6620.3 | 5836.7 | 7356 | 7015.4 | 6472.4 | 7592.9 | 7342.4 | 6769.2 | 6706.5 | 7500.4 | 6762.7 | 6963.3 | 7620.4 | 6653.1 | 7686.2 | 6625.8 | 7456.5 | 6810.8 | 7556.1 | 6467.2 | 7588.2 | 6760.7 | 7463.9 | 6766.1 | 7512.4 | 6857.4 | 6679.4 | 7409.4 | 6767.5 | 6606.2 | 7511.4 | 7566.2 | 7409.8 | 6782.4 | 7509.6 | 6688.5 | 7274.4 | 6729.4 | 7166.7 | 6252.8 | 7304.3 | 6699.3 | 6833.8 | 6864.6 | 6754.1 | 5826.4 | 6774 | 6002.1 | 6794.8 | 6918.2 | 7927.3 | 6857 | 7993.3 | 7026.2 | 7953.4 | 6997.7 | 7106.4 | 7056.8 | 7595.8 | 7931.7 | 7788.2 | 7769.3 | 7766.3 | 7846.9 | 7089.5 | 7871.1 | 7806.5 | 7849.3 | 7900.3 | 7880.5 | 7892.8 | 7025.9 | 7859.3 | 7015 | 29.0067 | 32.4938 | 32.8691 | 32.4191 | 32.5303 | 32.6744 | 0 | 43.5 | 0 | 0 | 41.5 | 41.5 | 3.8093 | 4.3477 | 3.5236 | 4.3753 | 4.2513 | 3.6679 | 10.86 | 8.473 | 7.739 | 8.295 | 8.106 | 8.15 | 3.7915 | 3.9042 | 4.1129 | 3.8088 | 3.9739 | 3.9991 | 0.89558 | 0.98183 | 0.84421 | 1.0751 | 1.0411 | 0.93387 | 3.8976 | 3.8429 | 3.9415 | 3.7229 | 3.8754 | 3.9199 | 0.31594 | 0.35276 | 0.31051 | 0.3372 | 0.33144 | 0.33064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 684394 | 1226 | 671510 | 1285 | 11535.07 | 20.933 | 3.7915 | 3.9042 | 4.1129 | 3.8088 | 3.9739 | 3.9991 | 3.8976 | 3.8429 | 3.9415 | 3.7229 | 3.8754 | 3.9199 | 518000 | 1000 | 571000 | 1000 | 1085869 | 4333 | 1087000 | 1081536 | 13.1833 | 3.9317 | 0.96195 | 3.8667 | 0.32975 | 24.47% | 8.528% | 31.9989 | 42.1667 | 3.9958 | 8.6038 | 1089957.7 | 1085200 | 1317218 | 82.39% | 48 | 28973
2024-07-08 | 2025 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 335090.89 | 6:23 | 19:07 | 7112.9 | 7563.6 | 7656.5 | 7597.3 | 7754.7 | 7791 | 7694.2 | 8065.6 | 7538.8 | 7462.7 | 7531.6 | 7592.9 | 7661.6 | 7613.2 | 7784.7 | 7816.1 | 7785.9 | 7845.7 | 7765.6 | 7759.8 | 7940.4 | 7856.4 | 7874.4 | 7903.1 | 7681.5 | 6645.9 | 7528.1 | 7623.2 | 8024.7 | 8010.3 | 7888 | 8001.7 | 7987 | 7958.2 | 7902.8 | 7892.9 | 8028.4 | 7947.1 | 8017.7 | 8037.1 | 8707 | 7797.1 | 8621.8 | 7660.6 | 8184.1 | 9194.6 | 7679.2 | 8714.3 | 7791 | 7166.6 | 7731.6 | 7257.5 | 8035.3 | 7167.5 | 7889.3 | 7906.8 | 6886.8 | 7943.8 | 6964.5 | 7905.3 | 7757.4 | 6906.8 | 7536 | 7129.2 | 7386.7 | 6948.7 | 7315.8 | 7657.3 | 7858.2 | 7020.2 | 7742.9 | 6726.9 | 7387.6 | 7217.9 | 6809 | 7522.2 | 6811 | 7878.5 | 6931.3 | 7775.3 | 7106.4 | 7661.7 | 7261.3 | 7996 | 7166.1 | 7696.3 | 7114.9 | 6305.1 | 8094.6 | 7588.2 | 7076.7 | 8331.2 | 8075.1 | 7491.9 | 7453.2 | 8305.8 | 7504.6 | 7733 | 8439.8 | 7423.4 | 8511.2 | 7405.9 | 8294 | 7622.1 | 8410.7 | 7231.8 | 8471.2 | 7586.7 | 8392.4 | 7652.1 | 8426.9 | 7785.9 | 7492.2 | 8403.6 | 7614.6 | 7474.9 | 8460.7 | 8633.5 | 8411.2 | 7765 | 8571.5 | 7683.3 | 8271.7 | 7643.6 | 8292.2 | 7227.2 | 8380.2 | 7703.2 | 7852.3 | 7894.7 | 7805.4 | 6693.1 | 7774.1 | 6887.7 | 7909.4 | 7947.9 | 9108.4 | 8023.1 | 9213.4 | 8233.4 | 9191.6 | 8228.1 | 8344.1 | 8141.4 | 8809.3 | 9146.7 | 8889.7 | 8878.5 | 8901.7 | 8998.4 | 8248.8 | 9055.4 | 8787.8 | 8885.4 | 9078.5 | 9081.4 | 9091.7 | 8220 | 8904.6 | 8118.7 | 29.6024 | 33.1114 | 33.3161 | 33.1357 | 33.2597 | 33.3172 | 0 | 43.7 | 0 | 0 | 43.7 | 43.08 | 3.1564 | 3.013 | 2.8845 | 3.0551 | 3.1791 | 1.6266 | 10.86 | 10.962 | 11.17 | 10.932 | 11.451 | 10.223 | 4.2618 | 4.4664 | 4.6362 | 4.1727 | 4.671 | 4.7336 | 1.0207 | 1.0774 | 0.96154 | 1.184 | 1.1916 | 1.0304 | 4.236 | 4.4596 | 4.4932 | 4.1401 | 4.6026 | 4.6664 | 0.31886 | 0.37625 | 0.32092 | 0.33943 | 0.35251 | 0.36069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 685006.9 | 1228.995 | 672154.4 | 1287.835 | 12787.601 | 25.333 | 4.2618 | 4.4664 | 4.6362 | 4.1727 | 4.671 | 4.7336 | 4.236 | 4.4596 | 4.4932 | 4.1401 | 4.6026 | 4.6664 | 612900 | 2995 | 644400 | 2835 | 1252531 | 4400 | 1251470 | 1248131 | 12.7333 | 4.4903 | 1.0776 | 4.433 | 0.34478 | 24% | 7.778% | 32.6238 | 43.4933 | 2.8191 | 10.933 | 1259656.4 | 1249933 | 1479656 | 84.47% | 49 | 66113
2024-07-09 | 2025 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 335090.89 | 6:22 | 19:36 | 9647.4 | 10194.3 | 10197.8 | 10142.8 | 10293.4 | 10299.7 | 10324.6 | 10735.1 | 10203 | 10231.9 | 10038.6 | 10175.8 | 10147.6 | 10108.4 | 10232.1 | 10241.4 | 10161 | 10164.2 | 10186.1 | 10221 | 10215.5 | 10194.9 | 9932.3 | 10047.3 | 9876.3 | 8647.8 | 9908.4 | 9866.1 | 10196.6 | 10115.9 | 9808 | 0 | 10060.1 | 10081.6 | 10205.3 | 10111.2 | 10212.9 | 10051.2 | 10079.3 | 9984 | 10875.7 | 9723.9 | 10733.6 | 9531.5 | 10213.8 | 11443.2 | 9616.7 | 10936.2 | 10356.4 | 9527.4 | 10240.6 | 9626.4 | 10619.4 | 9505 | 10466.2 | 10433.4 | 9240.3 | 10649.6 | 9298.5 | 10620.7 | 10488.5 | 9275.1 | 10238.9 | 9696 | 9806.3 | 9117.5 | 9726.6 | 10068.8 | 10487 | 9285.7 | 10276 | 8909.6 | 10047.9 | 9762.3 | 9244.6 | 10296.8 | 9043.8 | 10555.6 | 9252 | 10353 | 9294.8 | 10068.3 | 9420.2 | 10413.9 | 9292 | 9920.5 | 9237.7 | 0 | 10167.1 | 9714.2 | 9032.9 | 10521.8 | 10219.7 | 9442.2 | 9336.7 | 10284.1 | 9153.4 | 9425.7 | 10265.9 | 8984.8 | 10427.4 | 8991.1 | 10095.5 | 9219.7 | 10190.8 | 8736.2 | 10219.8 | 9116.3 | 10072.3 | 9121.4 | 0 | 9210.2 | 8989.2 | 9972.3 | 9150.5 | 8928 | 10106.3 | 10132.1 | 9985.3 | 9081.8 | 10069 | 8967.6 | 9755.7 | 0 | 9722.3 | 8423.2 | 9804.4 | 8973.8 | 9159.4 | 9239.7 | 9032.2 | 7785.2 | 9036.8 | 8019.9 | 9118.7 | 9143.7 | 10600.4 | 9198.8 | 10602 | 9390.7 | 10526.8 | 9307.4 | 9459.5 | 9304.6 | 10215.8 | 10573.2 | 10525.9 | 10491.8 | 10488.6 | 10519.7 | 9485.6 | 10494.1 | 10618.7 | 10607.4 | 10639.9 | 10581.6 | 10562.6 | 9456.6 | 10663.9 | 9509.5 | 33.1371 | 33.8227 | 33.8318 | 33.6996 | 33.8005 | 33.8912 | 0 | 45.8 | 0 | 0 | 45.2 | 45.3 | 2.957 | 2.7156 | 2.7445 | 2.6127 | 2.7255 | 1.4536 | 10.86 | 8.577 | 7.633 | 7.821 | 7.834 | 8.222 | 5.772 | 5.7841 | 5.8093 | 5.6647 | 5.5492 | 5.6258 | 1.1478 | 1.0951 | 1.0845 | 1.4284 | 1.3106 | 1.0412 | 5.9006 | 5.6446 | 5.5839 | 5.5478 | 5.4289 | 5.4067 | 0.31297 | 0.3726 | 0.31622 | 0.35096 | 0.33697 | 0.35747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 685797 | 1230 | 672898 | 1298 | 14318.334 | 29.6 | 5.772 | 5.7841 | 5.8093 | 5.6647 | 5.5492 | 5.6258 | 5.9006 | 5.6446 | 5.5839 | 5.5478 | 5.4289 | 5.4067 | 790100 | 1005 | 743600 | 10165 | 1530733 | 4267 | 1522530 | 1526466 | 13.2333 | 5.7009 | 1.1846 | 5.5854 | 0.3412 | 20.78% | 6.109% | 33.6972 | 45.4333 | 2.5348 | 8.4912 | 1539150.2 | 1529333 | 1846670 | 82.82% | 48 | 130011
2024-07-10 | 2025 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 335090.89 | 6:19 | 19:45 | 10475 | 11058 | 11120.1 | 11073.4 | 11190.7 | 11266.6 | 11184.6 | 11620.7 | 11159.8 | 11125.2 | 11037.7 | 11134.4 | 11356.7 | 11215.1 | 11591.3 | 11518.7 | 11586 | 11558.2 | 11440.6 | 11515.2 | 11477.8 | 11463.9 | 11155.2 | 11306.2 | 11272.2 | 9876.1 | 11205.6 | 11210.5 | 11504.7 | 11461.2 | 11459.7 | 11548.3 | 11796.4 | 11724.3 | 11676.4 | 11619.3 | 11743.9 | 11667.3 | 11736.6 | 11683.3 | 11864.4 | 10769.1 | 11799.8 | 10557.1 | 11386.5 | 12593.2 | 10821 | 12046.9 | 11574.7 | 10682.8 | 11515.5 | 10878.6 | 11840.3 | 10708 | 11800.6 | 11796.5 | 10478.9 | 11934.9 | 10339.9 | 11869.3 | 11692.5 | 10246.6 | 11513.8 | 10875.8 | 11198.3 | 10499 | 11081.8 | 11593.9 | 11828.2 | 10649.9 | 11677 | 10191.8 | 11397.9 | 11167.2 | 10543.3 | 11756.4 | 10429.8 | 11862.9 | 10544 | 11715 | 10702.5 | 11569.8 | 10817.8 | 11931.7 | 10693.8 | 11423.9 | 10725.9 | 9409.7 | 11976.4 | 11270.1 | 10677 | 12359.7 | 12109.5 | 11240.3 | 11100.1 | 12199 | 10891.4 | 11198.2 | 12065.9 | 10554.5 | 12107.6 | 10529.6 | 11692.9 | 10693 | 11696.3 | 10068 | 11683.8 | 10437.7 | 11527.9 | 10474.2 | 11484 | 10574.9 | 10514.2 | 11552.9 | 10543.7 | 10305 | 11526.4 | 11638.4 | 11384.5 | 10463.5 | 11539.3 | 10301.6 | 11198.9 | 10385.6 | 11071.3 | 9640.8 | 11243.6 | 10297 | 10568 | 10718.4 | 10378.9 | 8950.7 | 10456.2 | 9265.6 | 10341 | 10340.4 | 11980.8 | 10547.3 | 11837.9 | 10684.6 | 11762.8 | 10483.6 | 10692.9 | 10476.7 | 11477.8 | 11743.3 | 11799 | 11736.2 | 11731.2 | 11824.4 | 10665.4 | 11640.1 | 11663.7 | 11645.5 | 11541.5 | 11501.8 | 11545.9 | 10569.3 | 11915.6 | 10689.5 | 34.22 | 35.81 | 36.21 | 35.87 | 36.04 | 36.27 | 0 | 50.8 | 0 | 0 | 50.4 | 50.5 | 2.74 | 2.5 | 2.36 | 2.54 | 2.59 | 0.99 | 10.86 | 7.21 | 7.53 | 7.24 | 6.67 | 6.78 | 6.52 | 6.76 | 6.67 | 6.66 | 6.58 | 6.53 | 1.49 | 1.54 | 1.37 | 1.89 | 1.7 | 1.36 | 6.41 | 6.59 | 6.37 | 6.46 | 6.42 | 6.3 | 0.4 | 0.53 | 0.42 | 0.49 | 0.46 | 0.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 686698 | 1231 | 673780 | 1290 | 16095.8 | 33.8 | 6.52 | 6.76 | 6.67 | 6.66 | 6.58 | 6.53 | 6.41 | 6.59 | 6.37 | 6.46 | 6.42 | 6.3 | 901000 | 1000 | 882000 | -8000 | 1777466 | 4200 | 1790000 | 1773266 | 13.4333 | 6.62 | 1.5583 | 6.425 | 0.46167 | 23.54% | 7.185% | 35.7367 | 50.5667 | 2.2867 | 7.715 | 1788209.8 | 1776867 | 2116527 | 83.95% | 54 | 6451
2024-07-11 | 2025 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 335090.89 | 6:25 | 19:40 | 11807 | 12363 | 12384.2 | 12248.9 | 12529.8 | 12556.3 | 12524.1 | 12967.7 | 12381.6 | 12572.7 | 12208.2 | 12354.6 | 12321.1 | 12273.2 | 12301.8 | 12362.7 | 12238.2 | 12228.1 | 12239.4 | 12246.6 | 12348.3 | 12280.9 | 12053.9 | 12178.6 | 12046.4 | 10491 | 11932.5 | 11957 | 12404.8 | 12296.2 | 12101.9 | 12427.8 | 12406 | 12395 | 12475.3 | 12382 | 12519.5 | 12292.4 | 12335.9 | 12349.5 | 12991.8 | 11770.7 | 12900.2 | 11611 | 12341.6 | 13525.1 | 11557 | 13054.6 | 12539.1 | 11578.6 | 12389.5 | 11683.7 | 12769.1 | 11428.2 | 12705.4 | 12669 | 11271.5 | 12974.3 | 11287 | 12934.8 | 12762.2 | 11274.7 | 12603.4 | 11969.8 | 12039.4 | 11281.1 | 11980.3 | 12473.1 | 12923.3 | 11514.8 | 12771 | 11108.9 | 12405.3 | 12181.1 | 11446.9 | 12848.1 | 11281.5 | 13061.8 | 11504.8 | 12851.9 | 11536.1 | 12559.4 | 11694.3 | 12891.6 | 11523.5 | 12359.4 | 11496.3 | 10158.5 | 12646.2 | 12076.3 | 11221.2 | 13079.6 | 12744.7 | 11764.8 | 11665.2 | 12908.8 | 11526.3 | 11951.6 | 13027.4 | 11410.3 | 13067.1 | 11411.6 | 12730.9 | 11687.7 | 12792.2 | 11045.5 | 12844 | 11555.4 | 12612.7 | 11455.2 | 12605.8 | 11674.5 | 11399.8 | 12675.1 | 11618.8 | 11363.6 | 12832.7 | 12917.5 | 12696.4 | 11589.8 | 12812.1 | 11397.8 | 12462.5 | 11479.4 | 12256.4 | 10686.6 | 12430.2 | 11414.3 | 11679.9 | 11756.7 | 11453 | 9917.4 | 11544.8 | 10164.3 | 11437.2 | 11454.9 | 13274.9 | 11625.5 | 13348.4 | 11884 | 13224 | 11739.5 | 11955.6 | 11679 | 12840.5 | 13182.5 | 13111.3 | 13118.1 | 13113.6 | 13179.9 | 11999.8 | 13181.5 | 13198.3 | 13215.3 | 13333.5 | 13317.6 | 13258.6 | 11940.6 | 13301.9 | 11951.4 | 35.7216 | 36.4114 | 36.6427 | 36.3456 | 36.3792 | 36.8098 | 0 | 49.6 | 0 | 0 | 49.5 | 49.7 | 5.5111 | 5.7968 | 5.6929 | 5.8323 | 5.6844 | 5.2415 | 8.8833 | 9.0167 | 9.3867 | 9.05 | 8.9817 | 9.615 | 7.233 | 7.2534 | 7.2125 | 7.1928 | 7.291 | 7.3049 | 1.7072 | 1.7456 | 1.496 | 2.0694 | 1.9211 | 1.6006 | 6.9881 | 7.0329 | 6.8379 | 6.9001 | 7.0013 | 7.0248 | 0.50377 | 0.62159 | 0.47832 | 0.59249 | 0.54784 | 0.56472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 687673 | 1232 | 674750 | 1291 | 18035.27 | 37.933 | 7.233 | 7.2534 | 7.2125 | 7.1928 | 7.291 | 7.3049 | 6.9881 | 7.0329 | 6.8379 | 6.9001 | 7.0013 | 7.0248 | 975000 | 1000 | 970000 | 1000 | 1939470 | 4133 | 1943000 | 1935337 | 13.25 | 7.2479 | 1.7567 | 6.9642 | 0.55145 | 24.24% | 7.918% | 36.3851 | 49.6 | 5.6265 | 9.1556 | 1952190.3 | 1938870 | 2304422.041 | 84.14% | 50 | 2649
2024-07-12 | 2025 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 335090.89 | 6:37 | 19:36 | 10434 | 10900.1 | 10841.2 | 10759.8 | 10914.8 | 10995.5 | 10937.1 | 11383 | 10974.7 | 10934.9 | 10754.7 | 10892.8 | 10874.3 | 10810.2 | 10891.3 | 10855.8 | 10816.4 | 10788.6 | 10832.8 | 10863.2 | 10858.9 | 10850.8 | 10666.9 | 10721.3 | 10580.2 | 9350.6 | 10574.9 | 10564 | 10865 | 10835.9 | 10719.6 | 10871.2 | 10828.7 | 10820 | 10910.6 | 10834.3 | 10927.8 | 10763.1 | 10848.9 | 10799.3 | 11582.4 | 10503.8 | 11466.7 | 10332.5 | 11058 | 12225.9 | 10443.5 | 11672.6 | 11028.7 | 10325.4 | 10940.5 | 10410.4 | 11274.5 | 10188 | 11225.8 | 11175.6 | 10065.3 | 11453.7 | 10119.8 | 11381.2 | 11233.9 | 10084.7 | 11004.6 | 10466.3 | 10681.7 | 10012.8 | 10574.5 | 10935.3 | 11321.2 | 10161.3 | 11097.1 | 9740.7 | 10880.3 | 10578.4 | 10087.8 | 11044.9 | 9846.5 | 11291.9 | 10032.2 | 11077.6 | 10155.5 | 10860.5 | 10281.9 | 11283.3 | 10195.7 | 10834 | 10200.8 | 9027.4 | 11199.4 | 10704.5 | 10051.8 | 11500.5 | 11186.2 | 10381.9 | 10252.3 | 11295.5 | 10238.5 | 10568.4 | 11394.6 | 10118.1 | 11355.5 | 10091.7 | 11071.1 | 10319 | 11128 | 9720.2 | 11221.1 | 10138.5 | 11116.2 | 10167.6 | 11219.5 | 10335.7 | 10125.2 | 11108.9 | 10269.2 | 10080.2 | 11201.1 | 11263.7 | 11071.2 | 10240.1 | 11151.4 | 10080.4 | 10872.9 | 10122.4 | 10751.5 | 9473 | 10938.7 | 10123.9 | 10372.4 | 10454.9 | 10178.6 | 8827.6 | 10278.4 | 9082.9 | 10216.9 | 10234.2 | 11616.8 | 10300.8 | 11703.7 | 10498.5 | 11595.6 | 10409 | 10584.6 | 10425.3 | 11246.9 | 11568.5 | 11555.9 | 11537.2 | 11537.2 | 11494.7 | 10610 | 11580.6 | 11446.3 | 11474.3 | 11545.1 | 11510.4 | 11502.3 | 10422.9 | 11634.7 | 10509.1 | 31.4031 | 34.9664 | 35.064 | 34.8704 | 34.9891 | 35.3579 | 0 | 45.4 | 0 | 0 | 45.4 | 45.6 | 8.1986 | 8.4359 | 8.6034 | 8.7628 | 8.2376 | 8.8804 | 12.725 | 13.0083 | 12.6233 | 13.02 | 11.57 | 13.7217 | 6.3009 | 6.2937 | 6.3715 | 6.2839 | 6.3707 | 6.3806 | 1.5413 | 1.5322 | 1.3634 | 1.8536 | 1.7004 | 1.4383 | 6.117 | 6.1331 | 6.0868 | 6.0737 | 6.1562 | 6.1621 | 0.49464 | 0.59271 | 0.46896 | 0.57444 | 0.52457 | 0.53517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 688534 | 1234 | 675604 | 1292 | 19744.87 | 42 | 6.3009 | 6.2937 | 6.3715 | 6.2839 | 6.3707 | 6.3806 | 6.117 | 6.1331 | 6.0868 | 6.0737 | 6.1562 | 6.1621 | 861000 | 2000 | 854000 | 1000 | 1709600 | 4067 | 1712000 | 1705533 | 12.9833 | 6.3336 | 1.5715 | 6.1215 | 0.53175 | 24.81% | 8.687% | 34.4418 | 45.4667 | 8.5198 | 12.7781 | 1719120.2 | 1709130 | 2071946.2171 | 82.49% | 43 | 2731
2024-07-13 | 2025 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 335090.89 | 6:28 | 19:38 | 9496 | 10048.2 | 10137.5 | 10035.4 | 10350.5 | 10476.2 | 10203.8 | 10700.4 | 10037.4 | 9924.1 | 10004.9 | 10031.5 | 10385.4 | 10155.5 | 10585.1 | 10561.1 | 10523.9 | 10530.8 | 10515.7 | 10552.5 | 10566.9 | 10541 | 10397.3 | 10462.9 | 10275.6 | 8988.6 | 10235.2 | 10241.1 | 10585.1 | 10513.3 | 10408.3 | 10623.3 | 10491.5 | 10500.4 | 10568.2 | 10525.4 | 10645.8 | 10498 | 10524.7 | 10446.5 | 11140.1 | 10060.2 | 11075.4 | 9869.6 | 10697.4 | 11726.5 | 9976.4 | 11175.6 | 10370.7 | 9569.9 | 10357.6 | 9719.3 | 10780.3 | 9756 | 10498 | 10573.9 | 9194 | 10514.1 | 9254.9 | 10430.8 | 10287.5 | 9175.6 | 9985.1 | 9484.3 | 9728.3 | 9105.3 | 9647 | 9933.8 | 10320.7 | 9166.2 | 10094.7 | 8778.4 | 9888 | 9600.6 | 9123.9 | 10058 | 8912.7 | 10269.9 | 9101.5 | 10086.5 | 9163.9 | 9892.5 | 9263 | 10169.4 | 9154 | 9765.4 | 9226.1 | 8116.6 | 10282 | 9777.2 | 9256.4 | 10640 | 10393.5 | 9691.7 | 9647.4 | 10449.7 | 9458.3 | 9800.9 | 10540.3 | 9333.6 | 10646.5 | 9326.2 | 10423.3 | 9574.6 | 10477.7 | 9076.9 | 10539.2 | 9491.3 | 10508.6 | 9582.6 | 10675.8 | 9716.3 | 9374.4 | 10321.6 | 9504.9 | 9289.7 | 10431.8 | 10442.3 | 10173.6 | 9476.8 | 10399.6 | 9403.5 | 10215.2 | 9546.7 | 10148 | 8915 | 10261 | 9443.2 | 9628.3 | 9764.2 | 9437.6 | 8150.9 | 9626.4 | 8501.2 | 9395.8 | 9361.1 | 10587.4 | 9354.5 | 10646.6 | 9543.1 | 10597.8 | 9481 | 9662.5 | 9505.9 | 10143.8 | 10433.8 | 10448 | 10456.3 | 10492 | 10500 | 9620.8 | 10471.8 | 10342.7 | 10355.1 | 10396.3 | 10337.2 | 10311.8 | 9361.5 | 10487.9 | 9463.4 | 31.8296 | 34.5943 | 34.8133 | 34.467 | 34.4882 | 34.7727 | 0 | 46.8 | 0 | 0 | 46.1 | 46.2 | 5.155 | 5.4623 | 5.1768 | 5.4269 | 5.282 | 5.0889 | 8.4383 | 8.7167 | 8.1967 | 8.225 | 8.5467 | 8.3983 | 5.8304 | 6.095 | 6.0789 | 5.676 | 5.8638 | 5.678 | 1.4225 | 1.5176 | 1.306 | 1.6676 | 1.5856 | 1.322 | 5.6745 | 5.9867 | 5.8492 | 5.5092 | 5.6853 | 5.5494 | 0.45439 | 0.55612 | 0.43432 | 0.50627 | 0.46971 | 0.46499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 689344 | 1235 | 676390 | 1294 | 21337.268 | 46.267 | 5.8304 | 6.095 | 6.0789 | 5.676 | 5.8638 | 5.678 | 5.6745 | 5.9867 | 5.8492 | 5.5092 | 5.6853 | 5.5494 | 810000 | 1000 | 786000 | 2000 | 1592398 | 4267 | 1593000 | 1588131 | 13.1667 | 5.8704 | 1.4702 | 5.709 | 0.48097 | 25.04% | 8.425% | 34.1608 | 46.3667 | 5.2653 | 8.4203 | 1601058.6 | 1592067 | 1920200.7647 | 82.91% | 64 | 17384
2024-07-14 | 2025 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 335090.89 | 6:23 | 19:27 | 10946.4 | 11663.3 | 11496 | 11311.1 | 11755.1 | 11867.2 | 11772.6 | 12172.5 | 11538.8 | 11450.2 | 11420.5 | 11637.3 | 11505.4 | 11460.7 | 11562.8 | 11577.6 | 11439.4 | 11422.7 | 11470.8 | 11488.4 | 11584.2 | 11525.2 | 11403.4 | 11495.1 | 11364.5 | 9899.2 | 11222.2 | 11293.6 | 11706.6 | 11584.6 | 11501.7 | 11733.9 | 11723.2 | 11729.6 | 11710.4 | 11658.5 | 11820.8 | 11665 | 11671.4 | 11689.3 | 12107.5 | 10861.1 | 12046.8 | 10749.6 | 11506.1 | 12728 | 10809.3 | 12272.1 | 11612.1 | 10746.9 | 11500.5 | 10813.2 | 11901.9 | 10656.4 | 11827.5 | 11804 | 10556.2 | 12144.2 | 10532.4 | 12053.1 | 11953.8 | 10582.8 | 11689.2 | 11092.7 | 11311.5 | 10590.1 | 11249.5 | 11729.3 | 12101.7 | 10897 | 11998 | 10481.8 | 11570.3 | 11457.6 | 10745.2 | 12054 | 10612.8 | 12217.8 | 10731.2 | 12012.5 | 10788.6 | 11733.7 | 10759.9 | 12061.4 | 10669.8 | 11381.5 | 10735.3 | 9378.7 | 11696.3 | 11197.8 | 10508.9 | 12164.3 | 11937.7 | 11057.6 | 10948.7 | 11965.4 | 10550 | 10927.3 | 11942.1 | 10486.5 | 12353.9 | 10614 | 11991.6 | 10930.6 | 12079.9 | 10389.9 | 12111.2 | 10903.6 | 11887.6 | 10765.8 | 11812.2 | 10950.2 | 10528.1 | 11756.3 | 10934.3 | 10644.9 | 12094 | 12129.9 | 11965.9 | 10941 | 12099.7 | 10789.4 | 11761.4 | 10868.9 | 11549.7 | 10044.1 | 11755.9 | 10672.6 | 10985.7 | 11094.6 | 10652.4 | 9283.4 | 10786.7 | 9443.4 | 10540.5 | 10517.6 | 11907.3 | 10451.2 | 11966.9 | 10646.2 | 11965.6 | 10616.9 | 10858.5 | 10740.2 | 11585.4 | 11940.7 | 11828.6 | 11812.9 | 11795.3 | 11820.3 | 10712.1 | 11876.8 | 11930.6 | 11994.5 | 12114.7 | 12058.5 | 11986.1 | 10777.8 | 11933.5 | 10768.4 | 34.5779 | 35.6435 | 35.9248 | 35.6616 | 35.7702 | 35.918 | 0 | 51.3 | 0 | 0 | 50.6 | 50.5 | 3.7303 | 3.8137 | 3.7074 | 3.7483 | 3.9357 | 3.6838 | 7.7967 | 7.7167 | 7.7917 | 9.4117 | 7.15 | 7.2183 | 6.7722 | 6.8003 | 6.6045 | 6.7174 | 6.815 | 6.433 | 1.6582 | 1.6813 | 1.4338 | 1.9843 | 1.8412 | 1.4631 | 6.5704 | 6.6769 | 6.3366 | 6.5091 | 6.5449 | 6.2717 | 0.52557 | 0.61088 | 0.46986 | 0.58175 | 0.53817 | 0.52629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690259 | 1237 | 677287 | 1295 | 23143.602 | 50.6 | 6.7722 | 6.8003 | 6.6045 | 6.7174 | 6.815 | 6.433 | 6.5704 | 6.6769 | 6.3366 | 6.5091 | 6.5449 | 6.2717 | 915000 | 2000 | 897000 | 1000 | 1806334 | 4333 | 1809000 | 1802001 | 13.0667 | 6.6904 | 1.677 | 6.4849 | 0.54209 | 25.07% | 8.359% | 35.5827 | 50.8 | 3.7699 | 7.8475 | 1816860.3 | 1804334 | 2141926.3901 | 84.24% | 54 | 5439
2024-07-15 | 2025 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 335090.89 | 6:27 | 19:37 | 10152.1 | 10448.6 | 10192.9 | 10205.3 | 10340.6 | 10403.8 | 10424.5 | 10644.7 | 10414.4 | 10749 | 10284.8 | 10410.4 | 10265.5 | 10324.9 | 10302.1 | 10308.3 | 10381 | 10521.3 | 10306.9 | 10334.4 | 10547.3 | 10485.9 | 10462.6 | 10440.5 | 10230.4 | 8973 | 10141 | 10144.7 | 10534.7 | 10703.6 | 10639.9 | 10578.3 | 10882.3 | 10810.6 | 10654.5 | 10622.2 | 10765.6 | 10709.5 | 10823.7 | 10847.1 | 11777.2 | 10793.4 | 11822.3 | 10599.7 | 11473.9 | 12515.1 | 10770.8 | 11867.5 | 10557.7 | 9829.5 | 10454.7 | 9834.5 | 10765.3 | 9659.8 | 10630.6 | 10597.9 | 9550 | 10848.7 | 9593 | 10855.6 | 10779.4 | 9594.3 | 10554.5 | 10205.7 | 10146.5 | 9640.6 | 10197.4 | 10657.7 | 10872.7 | 9946.9 | 10831.1 | 9596.1 | 10518.6 | 10480.9 | 9845 | 10989.1 | 9769 | 11127 | 9999.4 | 11124 | 10021.1 | 10842.4 | 10141.9 | 11097.2 | 10062.6 | 10775.5 | 9953.3 | 8895.3 | 10989.4 | 10488.7 | 9877.6 | 11345.7 | 11163.8 | 10424.7 | 10259.7 | 11227 | 10107.4 | 10361.4 | 11106.7 | 9847.6 | 11311.3 | 9847.1 | 11076.7 | 10128.9 | 11151.6 | 9699.4 | 11210.2 | 10128.1 | 11130.4 | 10195.7 | 11301.8 | 10426.1 | 9861.4 | 10790.4 | 10102.6 | 9814 | 11072.3 | 10966.8 | 10887.4 | 10006.1 | 11087.5 | 10042.7 | 10829.7 | 10178.2 | 10820.4 | 9557.6 | 10991.5 | 10143.2 | 10168.3 | 10304.6 | 10150.4 | 8694 | 10219.6 | 8968.2 | 10247.8 | 10234.3 | 11867.2 | 10527.7 | 11974.4 | 10764.9 | 11694.8 | 10526.5 | 10641.7 | 10405.3 | 11302.2 | 11639.4 | 11473.9 | 11525.9 | 11644.9 | 11766.2 | 10939.2 | 11742.9 | 11355.8 | 11377.4 | 11473.4 | 11430.8 | 11394.7 | 10536.9 | 11466.2 | 10477.8 | 33.3598 | 36.0745 | 36.2848 | 36.1151 | 36.2626 | 36.1215 | 0 | 47 | 0 | 0 | 47.1 | 47.4 | 3.8789 | 3.8645 | 3.8586 | 3.9071 | 3.932 | 3.8461 | 8.3033 | 8.595 | 8.8983 | 8.315 | 9.105 | 9.3767 | 6.1496 | 6.1709 | 6.7429 | 6.0715 | 6.2975 | 6.4991 | 1.4596 | 1.4848 | 1.3664 | 1.7509 | 1.6016 | 1.3797 | 6.0044 | 6.0564 | 6.4957 | 5.9196 | 6.0903 | 6.3018 | 0.47844 | 0.54558 | 0.45059 | 0.51731 | 0.46863 | 0.48516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 691096 | 1238 | 678137 | 1297 | 24825.669 | 55 | 6.1496 | 6.1709 | 6.7429 | 6.0715 | 6.2975 | 6.4991 | 6.0044 | 6.0564 | 6.4957 | 5.9196 | 6.0903 | 6.3018 | 837000 | 1000 | 850000 | 2000 | 1682067 | 4400 | 1684000 | 1677667 | 13.1667 | 6.3219 | 1.5072 | 6.1447 | 0.49095 | 23.84% | 7.99% | 35.7031 | 47.1667 | 3.8812 | 8.7656 | 1691771.4 | 1623934 | 2034617.3141 | 79.82% | 53 | 15944
2024-07-16 | 2025 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 335090.89 | 6:26 | 19:46 | 10475.8 | 10914.3 | 10593.4 | 10649.1 | 10858.4 | 11007 | 10941.2 | 11380.2 | 11003 | 10984.1 | 10779.3 | 10957 | 10920.1 | 10863 | 10883.8 | 10966.7 | 10836 | 10862.3 | 10959.4 | 11012.1 | 10976.7 | 10993.9 | 10800.8 | 10876.3 | 10807.7 | 9495.2 | 10776.6 | 10749.8 | 11022.9 | 10885.6 | 10808.8 | 11035.2 | 11124.9 | 11138.5 | 11217.2 | 11100.6 | 11182.6 | 10980.9 | 10997.4 | 11023 | 11573.7 | 10519.5 | 11497.8 | 10345.9 | 10992.1 | 12047.9 | 10301.9 | 11567.4 | 11157.6 | 10393.6 | 11111.5 | 10540.4 | 11425.5 | 10215.8 | 11442.8 | 11334.9 | 10150.5 | 11612.8 | 10138.4 | 11565.1 | 11385.6 | 10114.3 | 11071.9 | 10564.6 | 10868.8 | 10243.6 | 10818.8 | 11254.3 | 11565.9 | 10405.5 | 11385 | 9943.7 | 11121.1 | 10851 | 10284.7 | 11388.4 | 10064 | 11606.6 | 10296.9 | 11444.3 | 10435.4 | 11283.1 | 10558.5 | 11628.8 | 10443.3 | 11158 | 10451.5 | 9222.5 | 11511.8 | 10998.7 | 10290.2 | 11793 | 11448 | 10570.9 | 10386.3 | 11553.1 | 10432.4 | 10811.9 | 11617.7 | 10319.1 | 11619.4 | 10259.4 | 11336.5 | 10476.7 | 11430.9 | 9903.4 | 11501.2 | 10371.1 | 11345.6 | 10363.9 | 11389.4 | 10549 | 10356.4 | 11405.7 | 10494.3 | 10239.8 | 11472.3 | 11552.7 | 11173.7 | 10491.8 | 11438.7 | 10287.1 | 11108 | 10332.5 | 10931.2 | 9612.4 | 11176.9 | 10328.5 | 10536.3 | 10612.9 | 10323.4 | 8954.4 | 10381.8 | 9196 | 10343.4 | 10408.6 | 11934.7 | 10548.8 | 11966.7 | 10782.3 | 11899 | 10666.8 | 10838.1 | 10608.7 | 11614.4 | 11923 | 11881.7 | 11827.8 | 11824.6 | 11853.4 | 10871.5 | 11852.4 | 11803.2 | 11848.6 | 11948.9 | 11888.2 | 11868.8 | 10808.1 | 11969.7 | 10837.9 | 37.3143 | 37.3253 | 37.4797 | 37.3914 | 37.4968 | 37.3502 | 0 | 48.2 | 0 | 0 | 48.1423 | 48.3 | 4.1654 | 4.1875 | 4.076 | 4.2473 | 4.1926 | 4.0153 | 9.8967 | 10.015 | 10.2 | 11.1183 | 10.5117 | 9.5333 | 6.4211 | 6.3935 | 6.3901 | 6.4881 | 6.5466 | 6.5427 | 1.5886 | 1.5393 | 1.3609 | 1.9417 | 1.6939 | 1.3875 | 6.2674 | 6.2752 | 6.1622 | 6.3327 | 6.3645 | 6.301 | 0.49447 | 0.56299 | 0.43753 | 0.54916 | 0.4869 | 0.49439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 691966 | 1240 | 679011 | 1298 | 26564.74 | 59.267 | 6.4211 | 6.3935 | 6.3901 | 6.4881 | 6.5466 | 6.5427 | 6.2674 | 6.2752 | 6.1622 | 6.3327 | 6.3645 | 6.301 | 870000 | 2000 | 874000 | 1000 | 1739071 | 4267 | 1741000 | 1734804 | 13.3333 | 6.4637 | 1.5853 | 6.2838 | 0.50424 | 24.53% | 8.024% | 37.393 | 48.2141 | 4.1474 | 10.2125 | 1748941.7 | 1738534 | 2073853.4866 | 83.83% | 48 | 22084
2024-07-17 | 2025 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 335090.89 | 6:35 | 18:36 | 9526.5 | 9895.7 | 9431.6 | 9475.6 | 9683.5 | 9805.4 | 9786.7 | 10136 | 9934.7 | 9934.8 | 9666.7 | 9861 | 9764.5 | 9711.8 | 9755.7 | 9839.5 | 9699.7 | 9688.7 | 9879.3 | 9927.3 | 9842.3 | 9870.8 | 9674.2 | 9752.3 | 9602.7 | 8441.3 | 9628.6 | 9640.2 | 9870.4 | 9728.7 | 9610.1 | 9817.6 | 9754.7 | 9776 | 9870.4 | 9769.7 | 9869.3 | 9707.9 | 9735.6 | 9659.6 | 10252.8 | 9334.3 | 10218.9 | 9203.1 | 9813.6 | 10826.2 | 9242.6 | 10321.7 | 9942.9 | 9279.6 | 9872.7 | 9369.9 | 10164.7 | 9175.5 | 10059.2 | 9997.5 | 8985.2 | 10210.1 | 9075.3 | 10155.2 | 10012.5 | 9038.1 | 9759 | 9440.4 | 9599.1 | 9064.4 | 9582.1 | 9962.7 | 10209.2 | 9271.2 | 10095.3 | 8912.2 | 9848.6 | 9695.9 | 9162 | 10133.8 | 9015.3 | 10307.7 | 9212.5 | 10193.7 | 9318 | 10042.5 | 9414.3 | 10284.8 | 9300.9 | 9890.9 | 9275.7 | 8224.4 | 10141.7 | 9751.3 | 9122.2 | 10401.6 | 10102.2 | 9412.4 | 9301.9 | 10178.5 | 9277.6 | 9606 | 10287.6 | 9226.3 | 10212.9 | 9128.2 | 9973.3 | 9332.1 | 10001.8 | 8802.3 | 10064.6 | 9201 | 9902.2 | 9104 | 9938.6 | 9294.6 | 9251.5 | 10135.5 | 9389.8 | 9173.8 | 10207.5 | 10310 | 9941.2 | 9420.8 | 10223.7 | 9251.3 | 9858.8 | 9200.5 | 9678.5 | 8639.6 | 10000.8 | 9271.4 | 9412.1 | 9463.3 | 9232.5 | 8018.2 | 9234.9 | 8196.5 | 9120.7 | 9184.5 | 10522 | 9349.1 | 10538.2 | 9519.1 | 10477 | 9400.1 | 9540.3 | 9379.4 | 10187 | 10408.2 | 10522.4 | 10460.4 | 10462.3 | 10475 | 9548.6 | 10371.7 | 10418.7 | 10416.2 | 10527.8 | 10454.6 | 10405 | 9453.7 | 10645.5 | 9526.1 | 35.759 | 36.0479 | 35.8441 | 36.0542 | 36.0646 | 34.3449 | 0 | 47.7473 | 0 | 0 | 46.8 | 46.6 | 4.7812 | 4.617 | 4.4428 | 4.5769 | 4.6462 | 5.2982 | 11.522 | 12.972 | 11.503 | 11.925 | 12.445 | 8.577 | 5.6561 | 5.6954 | 5.6057 | 5.6655 | 5.6319 | 5.6536 | 1.3368 | 1.4085 | 1.1323 | 1.6282 | 1.5164 | 1.2826 | 5.5052 | 5.6124 | 5.4301 | 5.5419 | 5.5341 | 5.5449 | 0.42891 | 0.48391 | 0.36855 | 0.46254 | 0.41669 | 0.43757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 692741 | 1241 | 679786 | 1300 | 28109.802 | 63.6 | 5.6561 | 5.6954 | 5.6057 | 5.6655 | 5.6319 | 5.6536 | 5.5052 | 5.6124 | 5.4301 | 5.5419 | 5.5341 | 5.5449 | 775000 | 1000 | 775000 | 2000 | 1545062 | 4333 | 1547000 | 1540729 | 12.0167 | 5.6514 | 1.3841 | 5.5281 | 0.43303 | 24.49% | 7.833% | 35.6858 | 47.0491 | 4.7271 | 11.4907 | 1553386 | 1494267 | 1837525 | 81.32% | 68 | 6379
2024-07-18 | 2025 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 335090.89 | 6:26 | 19:17 | 11278.2 | 11973 | 11797.5 | 11689.3 | 12104.1 | 12155.8 | 12225.7 | 12650.8 | 11949.9 | 11937.3 | 11907.2 | 11976.8 | 12021.9 | 12005.5 | 11914.9 | 12000.4 | 11795.1 | 11773 | 11835.2 | 11903.7 | 11755.1 | 11832.3 | 11454.1 | 11609.7 | 11495 | 10152 | 11602.1 | 11500.4 | 11802.3 | 11713.8 | 11552.7 | 11757.5 | 11670 | 11644.6 | 11907.8 | 11754.5 | 11877.5 | 11704.8 | 11709.3 | 11611.8 | 12387.2 | 11149.1 | 12266.6 | 10939.5 | 11696.1 | 13086.9 | 11085.6 | 12513.9 | 12285.4 | 11341.8 | 12160.9 | 11484.3 | 12474.4 | 11225.7 | 12427.4 | 12328.5 | 10997.2 | 12603.8 | 11014.1 | 12534.8 | 12307.9 | 10914.4 | 12034.9 | 11440.4 | 11615.4 | 10804.4 | 11488.6 | 11904.2 | 12330.8 | 10950.2 | 12102.8 | 10540.2 | 11829.4 | 11562 | 10933.3 | 12168.9 | 10737.9 | 12408.2 | 10967.4 | 12233.1 | 10991.2 | 11916.9 | 11110.7 | 12312.3 | 11031.3 | 11780.3 | 11062.3 | 9655.5 | 12045.8 | 11493.5 | 10659.6 | 12296.4 | 11876.7 | 10960.3 | 10820.8 | 11906 | 10580.2 | 10854.1 | 11725.7 | 10200 | 11895.8 | 10191.8 | 11489.5 | 10414 | 11564.7 | 9887.1 | 11574.6 | 10288.7 | 11435.6 | 10377.8 | 11452.6 | 10488.8 | 10239.5 | 11292.5 | 10307 | 10054.2 | 11340 | 11385.2 | 11217.6 | 10272.9 | 11356.5 | 10155.5 | 11080.8 | 10326.6 | 11056.8 | 9605.6 | 11141.3 | 10257.4 | 10519.2 | 10646.2 | 10377.6 | 8913.2 | 10496.8 | 9319 | 10501.8 | 10495.3 | 12023.4 | 10389.9 | 11978.3 | 10636.5 | 11947.3 | 10611.4 | 10796.1 | 10669.5 | 11828.5 | 12139.1 | 12196.2 | 12118.6 | 12084.2 | 12009.3 | 10801.3 | 11989.5 | 12243.4 | 12278.9 | 12360.4 | 12291.3 | 12227.8 | 10986.3 | 12374 | 11074.7 | 33.8686 | 34.8042 | 35.0761 | 34.8345 | 34.8784 | 34.357 | 0 | 50.7 | 0 | 0 | 48.1 | 46.4 | 3.3866 | 3.0775 | 2.7766 | 3.2184 | 3.1745 | 5.2912 | 10.86 | 11.642 | 11.303 | 10.763 | 11.371 | 8.577 | 7.0148 | 6.8591 | 6.8335 | 6.9027 | 6.3842 | 6.6541 | 1.4906 | 1.398 | 1.2834 | 1.7914 | 1.5747 | 1.3858 | 6.8559 | 6.7186 | 6.5657 | 6.7147 | 6.1441 | 6.4399 | 0.43693 | 0.504 | 0.39561 | 0.47137 | 0.42643 | 0.45574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 693679 | 1243 | 680672 | 1301 | 29927.669 | 67.933 | 7.0148 | 6.8591 | 6.8335 | 6.9027 | 6.3842 | 6.6541 | 6.8559 | 6.7186 | 6.5657 | 6.7147 | 6.1441 | 6.4399 | 938000 | 2000 | 886000 | 1000 | 1817867 | 4333 | 1821000 | 1813534 | 12.85 | 6.7747 | 1.4873 | 6.5731 | 0.44835 | 21.95% | 6.821% | 34.6365 | 48.4 | 3.4875 | 10.7527 | 1829035.2 | 1816066 | 2170400 | 83.67% | 49 | 11064
2024-07-19 | 2025 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 335090.89 | 6:37 | 19:44 | 11492.6 | 12202.8 | 11978.9 | 11893.6 | 12300.6 | 12349.6 | 12387.9 | 12802.6 | 12235.8 | 12189.8 | 12136.1 | 12298.3 | 12236.5 | 12251.4 | 12254.6 | 12289.9 | 12168.6 | 12184.5 | 12291.1 | 12334.4 | 12231.5 | 12291 | 11997.8 | 12134 | 12026 | 10548.8 | 12018.9 | 11991.3 | 12389.5 | 12277.4 | 12130.5 | 12365.2 | 12392.7 | 12423.5 | 12507.6 | 12429.1 | 12542.6 | 12347.4 | 12365 | 12285.1 | 13109.1 | 11895.3 | 13067.2 | 11710.6 | 12498.2 | 13688.1 | 11710.7 | 13112.2 | 12554.9 | 11576.1 | 12447.5 | 11721.4 | 12840.9 | 11476.5 | 12751.6 | 12693.9 | 11312.8 | 13014.6 | 11290.4 | 12924.5 | 12762.5 | 11270.2 | 12601.2 | 11952.2 | 12115.1 | 11312.2 | 12060.5 | 12506.4 | 12929.5 | 11560.4 | 12797.5 | 11106.8 | 12393.4 | 12190.2 | 11439.1 | 12811.8 | 11282.2 | 12964.4 | 11427.8 | 12793.4 | 11584.2 | 12556.4 | 11693.8 | 12923.3 | 11553.3 | 12307.3 | 11529.1 | 10099 | 12409.1 | 11956.7 | 11142.4 | 12876.8 | 12557.2 | 11628.5 | 11473.2 | 12527.7 | 11204.9 | 11630 | 12614.9 | 11179.8 | 12637.4 | 11106.8 | 12325.6 | 11391.5 | 12385.7 | 10742.6 | 12463.1 | 11233.9 | 12293.1 | 11185.5 | 12347.7 | 11319.6 | 11293.8 | 12493.8 | 11390.2 | 11138 | 12478.9 | 12550.5 | 12358.2 | 11282.1 | 12439.5 | 11109.1 | 12148.9 | 11249.4 | 11947.7 | 10356.4 | 12107.7 | 11060.4 | 11346 | 11450.1 | 11094.7 | 9627.1 | 11076.2 | 9803.5 | 10821.6 | 10881.4 | 12814.8 | 11223.3 | 12695.4 | 11411.4 | 12541.4 | 11169.5 | 11357.4 | 11077.5 | 12477.2 | 12775.5 | 12882.3 | 12806.1 | 12802.3 | 12793.9 | 11551.4 | 12674.9 | 12848.5 | 12824.1 | 12788 | 12745.8 | 12745.1 | 11568.3 | 12990.9 | 11730.9 | 31.66 | 34.51 | 34.59 | 34.57 | 34.74 | 34.55 | 0 | 49.7 | 0 | 0 | 48.1 | 46.2 | 3.13 | 2.74 | 2.8 | 2.86 | 2.93 | 5.29 | 10.86 | 7.07 | 7.58 | 9.9 | 7.32 | 8.58 | 7.07 | 7.14 | 7.26 | 7.15 | 7.11 | 7.08 | 1.62 | 1.64 | 1.47 | 2.01 | 1.85 | 1.56 | 6.9502 | 7.0315 | 7.0119 | 6.9794 | 6.9099 | 6.8792 | 0.45 | 0.54 | 0.43 | 0.51 | 0.47 | 0.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 694653 | 1245 | 681616 | 1303 | 31840.736 | 72.4 | 7.07 | 7.14 | 7.26 | 7.15 | 7.11 | 7.08 | 6.9502 | 7.0315 | 7.0119 | 6.9794 | 6.9099 | 6.8792 | 974000 | 2000 | 944000 | 2000 | 1913067 | 4467 | 1914000 | 1908600 | 13.1167 | 7.135 | 1.6917 | 6.9604 | 0.47667 | 23.71% | 6.848% | 34.1033 | 48 | 3.2917 | 8.5517 | 1925329 | 1912066 | 2295824 | 83.28% | 45 | 17706
2024-07-20 | 2025 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 335090.89 | 6:59 | 19:05 | 8723.9 | 9233.1 | 9050.4 | 9033.6 | 9430.2 | 9355.1 | 9320.7 | 9618 | 9203 | 9222.9 | 9050.7 | 9194.2 | 9136.9 | 9106.3 | 9265.7 | 9237.2 | 9230.1 | 9246 | 9267 | 9285.5 | 9323.3 | 9318.5 | 9215.8 | 9281.8 | 9236.2 | 8074.6 | 9106.3 | 9120 | 9477.7 | 9441 | 9355.3 | 9495.6 | 9638.4 | 9616.3 | 9593.2 | 9543.4 | 9655.8 | 9526.1 | 9573.6 | 9541.1 | 10131.4 | 9226.2 | 10148.4 | 9131.1 | 9770.1 | 10667.4 | 9119.1 | 10132.5 | 9381.6 | 8687 | 9310.2 | 8909.2 | 9622.2 | 8590.2 | 9687.7 | 9650.3 | 8606.1 | 9856.4 | 8453 | 9711 | 9533.6 | 8433.8 | 9431.9 | 8935 | 9212.9 | 8642.2 | 9134.1 | 9530.6 | 9753.9 | 8804.8 | 9607.2 | 8441.6 | 9366.1 | 9186.8 | 8653.1 | 9612.4 | 8461.9 | 9749.2 | 8610.7 | 9562 | 8885.4 | 9576.2 | 9073.9 | 9861.3 | 8922.7 | 9517.7 | 8848.6 | 7782.1 | 9764.5 | 9327.8 | 8722 | 10036.2 | 9764.6 | 9050.8 | 8947.2 | 9830.5 | 8839.1 | 9084.7 | 9829.6 | 8675.3 | 9999 | 8709 | 9730.4 | 8920.2 | 9795.6 | 8456.2 | 9817.5 | 8813.9 | 9700 | 8836.1 | 9717.6 | 8951.3 | 8648.6 | 9591.1 | 8829 | 8624.7 | 9706 | 9772.9 | 9621 | 8835.3 | 9722.6 | 8711.9 | 9509.4 | 8831.3 | 9404.3 | 8178.5 | 9501.5 | 8758.4 | 8962.1 | 9031.9 | 8814.1 | 7610 | 8830.9 | 7822.5 | 8490.3 | 8516.1 | 9870.2 | 8680.6 | 9780.5 | 8810.1 | 9768.2 | 8698.4 | 8855 | 8674.5 | 9405.8 | 9610.3 | 9792.7 | 9734.2 | 9764.8 | 9788.7 | 8788.3 | 9604.7 | 9848.3 | 9759 | 9578.4 | 9523.3 | 9538.7 | 8634.5 | 9986 | 8837.3 | 32.5785 | 34.0191 | 34.0873 | 34.1108 | 34.1625 | 34.4926 | 0 | 46.2 | 0 | 0 | 46.3 | 46.4 | 3.2344 | 3.1824 | 2.9482 | 3.2509 | 3.2803 | 5.2801 | 18.682 | 17.859 | 15.478 | 18.161 | 18.474 | 8.577 | 5.0639 | 5.278 | 5.61 | 5.3283 | 5.4747 | 5.306 | 1.2229 | 1.2034 | 1.1713 | 1.5574 | 1.3733 | 1.097 | 5.0019 | 5.171 | 5.4283 | 5.1916 | 5.3609 | 5.1183 | 0.3699 | 0.44787 | 0.36425 | 0.42625 | 0.38902 | 0.40482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 695394 | 1246 | 682350 | 1304 | 33310.536 | 76.8 | 5.0639 | 5.278 | 5.61 | 5.3283 | 5.4747 | 5.306 | 5.0019 | 5.171 | 5.4283 | 5.1916 | 5.3609 | 5.1183 | 741000 | 1000 | 734000 | 1000 | 1469800 | 4400 | 1473000 | 1465400 | 12.1 | 5.3435 | 1.2709 | 5.212 | 0.40035 | 23.78% | 7.681% | 33.9085 | 46.3 | 3.5294 | 16.2052 | 1478243.3 | 1469333 | 1732504 | 84.81% | 48 | 74581
2024-07-21 | 2025 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 335090.89 | 6:28 | 19:03 | 11162.2 | 11838.8 | 11424.9 | 11375.8 | 11868.3 | 11877.5 | 11960.8 | 12441.6 | 11824.5 | 11833.4 | 11634.9 | 11813.3 | 11749.9 | 11736.3 | 11851.1 | 11856.6 | 11804.8 | 11841 | 11860.8 | 11860 | 11852 | 11872.3 | 11657.9 | 11758.1 | 11618.4 | 10171.7 | 11557.4 | 11569.5 | 12012.7 | 11938.6 | 11737.5 | 11968.2 | 11940.1 | 11910.4 | 12052.8 | 11966.5 | 12106.2 | 11914.6 | 11979.3 | 11883.3 | 13012.6 | 11603.4 | 12862.5 | 11372.7 | 12170.4 | 13680.3 | 11463.7 | 13060.4 | 12002.4 | 11088.7 | 11873.3 | 11300.2 | 12333.6 | 10969.4 | 12356.9 | 12299.2 | 10900.5 | 12577.9 | 10827.1 | 12548.4 | 12365.1 | 10809.2 | 12018.7 | 11318 | 11413.7 | 10557.2 | 11300.1 | 11676.2 | 12234.9 | 10741.6 | 11936.7 | 10306.4 | 11688.6 | 11297.3 | 10728.5 | 11921.1 | 10451.1 | 12297.8 | 10726.8 | 11977.7 | 10738.9 | 11654.4 | 10871.2 | 12105.9 | 10765.7 | 11501.8 | 10803 | 9458.5 | 11988.8 | 11344.2 | 10647.4 | 12461.1 | 12085.9 | 11140.2 | 11020.9 | 12129.4 | 10792.6 | 11119.9 | 12144.7 | 10590.4 | 12297.8 | 10585.8 | 11883.2 | 10839.1 | 11993.1 | 10255 | 12003.3 | 10682.9 | 11792.4 | 10675.7 | 11818.5 | 10808.6 | 10570.9 | 11687.4 | 10732.1 | 10460.6 | 11825 | 11830.5 | 11667.8 | 10545.5 | 11708.8 | 10374.6 | 11476.8 | 10557.9 | 11247.5 | 9672 | 11309.4 | 10293.9 | 10583.1 | 10666.7 | 10351.3 | 8980 | 10399.1 | 9228.6 | 10334.9 | 10369.5 | 12173.1 | 10537.4 | 12199.4 | 10773.9 | 12079 | 10639.2 | 10815.1 | 10558.7 | 11503.5 | 11931.3 | 11869.3 | 11851.7 | 11961.2 | 12059.2 | 10810.6 | 11913.1 | 12073.5 | 12002.1 | 11965.4 | 11884.6 | 11850.7 | 10596 | 12067.1 | 10687.2 | 34.88 | 35.64 | 35.93 | 35.68 | 35.81 | 35.92 | 0 | 50.4 | 0 | 0 | 49.6 | 49.8 | 2.49 | 2.54 | 2.34 | 2.65 | 2.6 | 2.47 | 7.52 | 7.36 | 8.69 | 8.12 | 7.75 | 8.47 | 6.75 | 6.88 | 7.03 | 6.68 | 6.62 | 6.42 | 1.46 | 1.32 | 1.32 | 1.8 | 1.64 | 1.39 | 6.6385 | 6.7948 | 6.8096 | 6.5489 | 6.473 | 6.2468 | 0.39 | 0.5 | 0.39 | 0.46 | 0.42 | 0.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 696331 | 1248 | 683242 | 1306 | 35133.74 | 81.067 | 6.75 | 6.88 | 7.03 | 6.68 | 6.62 | 6.42 | 6.6385 | 6.7948 | 6.8096 | 6.5489 | 6.473 | 6.2468 | 937000 | 2000 | 892000 | 2000 | 1823204 | 4267 | 1825000 | 1818937 | 12.5833 | 6.73 | 1.4883 | 6.5853 | 0.43333 | 22.11% | 6.58% | 35.6433 | 49.9333 | 2.515 | 7.985 | 1833830.8 | 1822067 | 2161714 | 84.29% | 48 | 3083
2024-07-22 | 2025 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 335090.89 | 6:25 | 18:48 | 8945.5 | 9463.7 | 9421.6 | 9427.6 | 9508.8 | 9504.8 | 9506.2 | 9808.3 | 9437.6 | 9516.7 | 9271.6 | 9392.7 | 9352.6 | 9354.2 | 9361.4 | 9373.2 | 9310.5 | 9305.6 | 9374.2 | 9406.1 | 9359.4 | 9378.1 | 9216.4 | 9296.7 | 9236.4 | 8079.8 | 9169.4 | 9171.2 | 9494.3 | 9419.2 | 9276.3 | 9486.5 | 9500.2 | 9465.4 | 9545.8 | 9472.2 | 9566.4 | 9430.9 | 9461.4 | 9433.4 | 9978.2 | 9098.9 | 9922.4 | 8965.5 | 9563.5 | 10327.5 | 8949.3 | 9953 | 9514.1 | 8797.8 | 9453.9 | 8942.4 | 9720 | 8725 | 9700.9 | 9680.3 | 8586.6 | 9830.5 | 8573.2 | 9768.7 | 9636.7 | 8540.8 | 9500.3 | 9014.3 | 9262.9 | 8658.7 | 9177 | 9509 | 9736.4 | 8791.4 | 9632.6 | 8424.9 | 9381.6 | 9230.4 | 8662.7 | 9650.5 | 8533.9 | 9752.2 | 8666 | 9599.5 | 8828 | 9524 | 8970 | 9765 | 8858 | 9441 | 8415 | 8215 | 9676 | 9266.9 | 8640 | 9903.3 | 9645.8 | 8929.5 | 8845.1 | 9738.4 | 8780 | 9029.9 | 9771.4 | 8618.3 | 9794.7 | 8607.1 | 9582.8 | 8815.7 | 9619.2 | 8324.4 | 9654 | 8694.6 | 9574.2 | 8725.5 | 9664.3 | 8811.1 | 8600.7 | 9506.5 | 8767.2 | 8549.4 | 9578.9 | 9582.5 | 9464.9 | 8660.4 | 9531.8 | 8548 | 9304.1 | 8575.3 | 9162.7 | 8029.7 | 9344.3 | 8613.9 | 8775.1 | 8835.6 | 8652.2 | 7469 | 8614 | 7584.7 | 8431.9 | 8444.1 | 9601.2 | 8486.3 | 9701.4 | 8765.5 | 9616.3 | 8650 | 8803.9 | 8628.6 | 9338.1 | 9598.6 | 9595.9 | 9561.2 | 9560.4 | 9595.1 | 8819.2 | 9602.2 | 9560.1 | 9568.7 | 9588.9 | 9532.1 | 9498.3 | 8660.3 | 9729.1 | 8793.5 | 31.4391 | 34.5663 | 34.7519 | 34.6037 | 34.7338 | 34.8158 | 0 | 47.2 | 0 | 0 | 46.4 | 46.6 | 3.9027 | 3.8698 | 3.8408 | 4.0682 | 4.1109 | 4.1513 | 9.4383 | 9.595 | 10.2533 | 9.955 | 9.6133 | 9.3633 | 5.3832 | 5.4519 | 5.4881 | 5.4034 | 5.423 | 5.252 | 1.2981 | 1.1796 | 1.1896 | 1.576 | 1.3733 | 1.1005 | 5.2747 | 5.3818 | 5.3227 | 5.301 | 5.3281 | 5.0915 | 0.32279 | 0.41775 | 0.31202 | 0.37351 | 0.35662 | 0.36425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 697074 | 1249 | 683965 | 1307 | 36595.536 | 85.6 | 5.3832 | 5.4519 | 5.4881 | 5.4034 | 5.423 | 5.252 | 5.2747 | 5.3818 | 5.3227 | 5.301 | 5.3281 | 5.0915 | 743000 | 1000 | 723000 | 1000 | 1461796 | 4533 | 1464000 | 1457263 | 12.3833 | 5.4003 | 1.2862 | 5.2833 | 0.35782 | 23.82% | 6.773% | 34.1518 | 46.7333 | 3.9906 | 9.7031 | 1472125.8 | 1460133 | 1735633.3163 | 84.13% | 45 | 215174
2024-07-23 | 2025 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 335090.89 | 6:26 | 19:35 | 11490.8 | 12054.9 | 11931.9 | 11908.9 | 12092 | 12139.2 | 12118.6 | 12547 | 12073.5 | 12134.2 | 11799.5 | 11979.4 | 11965.5 | 11870.5 | 12046.3 | 12063.8 | 11928.7 | 11843 | 11943.8 | 12008.9 | 11833 | 11895.7 | 11575.1 | 11716.3 | 11603.2 | 10199.5 | 11620.9 | 11585.7 | 11872.4 | 11729.2 | 11564.9 | 11847.2 | 11812.6 | 11818.8 | 11948.8 | 11842.3 | 11907.7 | 11679.8 | 11710.1 | 11638.5 | 12722.6 | 11588.6 | 12611.5 | 11378.4 | 12100.4 | 13285.1 | 11432.4 | 12745.9 | 12074.1 | 11215 | 11960.4 | 11324.7 | 12354.2 | 11196.4 | 12244.4 | 12224.3 | 11003.3 | 12542.5 | 11008.7 | 12430.2 | 12290.5 | 10982.1 | 12145 | 11619.6 | 11737.1 | 11053.1 | 11689.6 | 12134.2 | 12466.1 | 11216.5 | 12282.7 | 10781.9 | 12000.2 | 11785.1 | 11122.4 | 12346.1 | 10996 | 12555.4 | 11258.1 | 12497.8 | 11242.8 | 12093.1 | 11396.6 | 12497.6 | 11301.7 | 11997.6 | 11306 | 9909 | 12340.1 | 11843.8 | 10948.6 | 12544 | 12162 | 11270 | 11138.8 | 12265 | 11061 | 11373.3 | 12294.8 | 10877.6 | 12317.5 | 10851.8 | 11972.8 | 11123.2 | 11933.7 | 10468.8 | 11992.1 | 10859.2 | 11841 | 10833.4 | 12009.6 | 11042.7 | 10911 | 12086.5 | 11085.8 | 10864.8 | 12121.9 | 12173.4 | 11956.2 | 11001.5 | 12088.7 | 10865.4 | 11697.6 | 10872.5 | 11541 | 10135.5 | 11843.3 | 10919.5 | 11103.3 | 11223 | 11002.2 | 9479.1 | 11012.9 | 9804.2 | 10966.3 | 11026.5 | 12615.3 | 11097.5 | 12660.8 | 11316.3 | 12580.7 | 11235.7 | 11437.3 | 11250.7 | 12178.8 | 12528 | 12453.6 | 12399.8 | 12444.1 | 12534.8 | 11371.2 | 12472.4 | 12581 | 12598.9 | 12669.8 | 12623.1 | 12573 | 11375.4 | 12626.8 | 11429.2 | 30.8787 | 33.1819 | 33.6214 | 33.0797 | 33.0677 | 33.3961 | 0 | 47.6 | 0 | 0 | 47.6 | 47.8 | 3.6186 | 3.9471 | 3.4748 | 3.9495 | 3.8357 | 3.89 | 6.8 | 6.5633 | 7.0483 | 6.4933 | 6.2367 | 6.8383 | 6.8635 | 6.9203 | 7.0306 | 6.9424 | 6.9114 | 6.8461 | 1.4116 | 1.2898 | 1.2787 | 1.7512 | 1.6068 | 1.3657 | 6.7155 | 6.7918 | 6.7649 | 6.7546 | 6.7183 | 6.6358 | 0.40441 | 0.5052 | 0.41461 | 0.46739 | 0.45326 | 0.45796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 698019 | 1251 | 684890 | 1309 | 38459.74 | 89.867 | 6.8635 | 6.9203 | 7.0306 | 6.9424 | 6.9114 | 6.8461 | 6.7155 | 6.7918 | 6.7649 | 6.7546 | 6.7183 | 6.6358 | 945000 | 2000 | 925000 | 2000 | 1864204 | 4267 | 1866000 | 1859937 | 13.15 | 6.9191 | 1.4506 | 6.7301 | 0.45047 | 20.97% | 6.693% | 32.8709 | 47.6667 | 3.786 | 6.6633 | 1875690.2 | 1863867 | 2252024.4989 | 82.76% | 50 | 22313
2024-07-24 | 2025 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 335090.89 | 6:45 | 19:40 | 11539.3 | 12333.4 | 12143 | 12044.9 | 12196.4 | 12253.2 | 12436.1 | 12749.7 | 12366.7 | 12127.2 | 12127.6 | 12379.4 | 12016.2 | 12036.9 | 12011.5 | 12032.8 | 11943.9 | 11954.7 | 11975.5 | 12007.2 | 11965.7 | 12001.3 | 11696.2 | 11878.6 | 11685.5 | 10309.5 | 11713 | 11695.3 | 11943.4 | 11770.3 | 11628 | 11866 | 11783.6 | 11791.9 | 12005.2 | 11847.9 | 11876.6 | 11699.5 | 11720.2 | 11661.7 | 12702.6 | 11628.1 | 12646.8 | 11497 | 12180.9 | 13187.5 | 11366.2 | 12709 | 12130 | 11351.8 | 12065.5 | 11426.2 | 12417.7 | 11225.6 | 12327.5 | 12285.2 | 11218.3 | 12762 | 11164.8 | 12707.2 | 12713 | 11350.3 | 12572.7 | 11996.4 | 12039.3 | 11259.2 | 12000.7 | 12384.7 | 12814.4 | 11567.8 | 12668.6 | 11110.2 | 12387.7 | 12108.2 | 11479.2 | 12611.7 | 11205.4 | 12876.4 | 11414.1 | 12556.1 | 11511.3 | 12455.5 | 11649.1 | 12700.8 | 11491.5 | 12208.6 | 11456.8 | 10028.5 | 12466.8 | 11913.5 | 11094.8 | 12588.9 | 12165.2 | 11266.5 | 11118.8 | 12300.4 | 11217.2 | 11620.9 | 12447.6 | 11070 | 12419.2 | 11005.6 | 12147.5 | 11281.1 | 12197.4 | 10614.3 | 12271.9 | 11065.7 | 12162.1 | 11109.6 | 12268.9 | 11284.2 | 11093.5 | 12297.9 | 11257.7 | 11037.6 | 12295.8 | 12351.9 | 12173.9 | 11192 | 12256.9 | 10974.9 | 11938.4 | 11057.5 | 11788.3 | 10300.9 | 11950 | 11008.5 | 11335.9 | 11474.6 | 11110.6 | 9586.4 | 11254.3 | 9996.2 | 11411.2 | 11466.4 | 13037.5 | 11530.1 | 13050.9 | 11791.3 | 13067.1 | 11778.2 | 12000.1 | 11737 | 12332.7 | 12746.2 | 12691.8 | 12675.4 | 12755.9 | 12895 | 11792.9 | 12806 | 12811.9 | 12760.8 | 12882.6 | 12758.7 | 12639 | 11444.3 | 12917 | 11575.3 | 32.642 | 34.2931 | 34.6531 | 34.1802 | 34.1875 | 34.6657 | 0 | 49.4 | 0 | 0 | 49.5 | 49.7 | 4.0287 | 4.1057 | 3.885 | 4.2124 | 4.1356 | 4.1592 | 7.2233 | 7.6517 | 7.485 | 7.5517 | 7.285 | 8.0183 | 7.0653 | 6.9475 | 6.9946 | 7.0795 | 7.0311 | 7.0087 | 1.6044 | 1.4973 | 1.3901 | 1.9746 | 1.777 | 1.5186 | 6.9509 | 6.8454 | 6.7596 | 6.9261 | 6.8833 | 6.8314 | 0.42159 | 0.52202 | 0.41546 | 0.48681 | 0.46978 | 0.48107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 698975 | 1252 | 685833 | 1310 | 40352.336 | 94.333 | 7.0653 | 6.9475 | 6.9946 | 7.0795 | 7.0311 | 7.0087 | 6.9509 | 6.8454 | 6.7596 | 6.9261 | 6.8833 | 6.8314 | 956000 | 1000 | 943000 | 1000 | 1892596 | 4466 | 1897000 | 1888130 | 12.9167 | 7.0211 | 1.627 | 6.8661 | 0.46612 | 23.17% | 6.789% | 34.1036 | 49.5333 | 4.0877 | 7.5358 | 1905020.2 | 1892133 | 2276133.4933 | 83.13% | 47 | 2009
2024-07-25 | 2025 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 335090.89 | 6:36 | 19:36 | 11147.3 | 11707.1 | 11462 | 11429 | 11561.5 | 11612.5 | 11680.1 | 11983.9 | 11744.3 | 11665 | 11464.1 | 11663.3 | 11559.5 | 11484.6 | 11765.9 | 11703.2 | 11751.6 | 11797.1 | 11783 | 11804.5 | 11792.9 | 11807.3 | 11657.6 | 11733.2 | 11462.6 | 10090.7 | 11468.7 | 11438.8 | 11840 | 11803.9 | 11680.5 | 11831.8 | 11811.8 | 11799.6 | 11820.5 | 11777.4 | 11841.7 | 11745.4 | 11761.8 | 11634.1 | 12227.3 | 11197.6 | 12144.1 | 10960.3 | 11785.1 | 12740.5 | 11159 | 12233.3 | 11748.3 | 10982.4 | 11723.8 | 11169.4 | 12081.8 | 10938.9 | 11978 | 11974.8 | 10722.9 | 12110.1 | 10602.9 | 12002.4 | 11865.1 | 10675 | 11697.3 | 11247.7 | 11388.4 | 10695.4 | 11285.5 | 11646.8 | 11951.6 | 10806.5 | 11801.1 | 10436.8 | 11529.1 | 11385.3 | 10720.6 | 11842 | 10584.4 | 12023 | 10820.2 | 11898.9 | 10849.5 | 11611.4 | 11006.4 | 11984 | 10928.3 | 11600.6 | 10887.4 | 9624 | 11860.9 | 11386.1 | 10623.4 | 11976.8 | 11744.4 | 11043.8 | 10945.2 | 11716.2 | 10612.1 | 10918.7 | 11795.7 | 10571.5 | 12100.2 | 10685.4 | 11945 | 11028.8 | 12052.4 | 10500.9 | 12149.1 | 11035.5 | 12071.4 | 11087.7 | 12225.6 | 11288.9 | 10560.4 | 11715.9 | 10944.5 | 10687.6 | 12042 | 12013 | 11983.7 | 10973.3 | 12048.5 | 10889.8 | 11893.7 | 11098.2 | 11773.4 | 10298.3 | 11866.7 | 10952.7 | 11096 | 11140.7 | 11023.5 | 9470 | 10961.4 | 9629.6 | 10919 | 10913.9 | 12406.7 | 11068.4 | 12386 | 11276.4 | 12383.8 | 11183.8 | 11338.8 | 11121 | 11848.2 | 12098.4 | 12129 | 12095.3 | 12185.3 | 12265.6 | 11268.4 | 12157.1 | 12158.4 | 12139.6 | 12177.4 | 12122.8 | 12083.8 | 11055.5 | 12240 | 11149.4 | 30.64 | 33.68 | 33.95 | 33.58 | 33.6 | 34.04 | 0 | 47.4 | 0 | 0 | 47.5 | 47.8 | 4.62 | 5.03 | 4.63 | 5.17 | 4.92 | 5.04 | 8.3 | 8.38 | 9.01 | 8.38 | 7.99 | 8.6 | 6.61 | 6.79 | 6.76 | 6.6 | 6.69 | 6.66 | 1.51 | 1.54 | 1.36 | 1.86 | 1.72 | 1.48 | 6.53 | 6.74 | 6.58 | 6.5 | 6.59 | 6.54 | 0.41 | 0.53 | 0.42 | 0.48 | 0.46 | 0.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 699896 | 1254 | 686743 | 1312 | 42177.537 | 98.733 | 6.61 | 6.79 | 6.76 | 6.6 | 6.69 | 6.66 | 6.53 | 6.74 | 6.58 | 6.5 | 6.59 | 6.54 | 921000 | 2000 | 910000 | 2000 | 1825201 | 4400 | 1827000 | 1820801 | 13 | 6.685 | 1.5783 | 6.58 | 0.46167 | 23.61% | 7.016% | 33.2483 | 47.5667 | 4.9017 | 8.4433 | 1837445.6 | 1824467 | 2199187.6093 | 82.96% | 44 | 1611
2024-07-26 | 2025 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 335090.89 | 6:43 | 19:38 | 9233.9 | 9681.5 | 9598.2 | 9530.6 | 9690 | 9723.9 | 9768.2 | 10163.9 | 9694.6 | 9769 | 9567.1 | 9711.6 | 9684.6 | 9648.2 | 9717.6 | 9748.2 | 9666.5 | 9664.5 | 9734.6 | 9810.5 | 9650.6 | 9704.9 | 9506.3 | 9585.6 | 9518.3 | 8372.8 | 9530.9 | 9468.6 | 9774.2 | 9724.4 | 9617 | 9768.6 | 9924.2 | 9888.3 | 9870.1 | 9807.5 | 9896.8 | 9756.4 | 9835.1 | 9842.5 | 10343.2 | 9327.9 | 10332.1 | 9193.9 | 9893.7 | 10971.3 | 9220.7 | 10370.8 | 9920.1 | 9262.1 | 9901.9 | 9396.7 | 10223.2 | 9133.1 | 10203.1 | 10151.6 | 9104.7 | 10476.7 | 9012.2 | 10353.8 | 10204.7 | 8975.1 | 10054.7 | 9529.4 | 9809.6 | 9260.4 | 9776.3 | 10197.4 | 10477.2 | 9460.9 | 10351.3 | 9126.3 | 10017.3 | 9903.5 | 9260.3 | 10355.1 | 9114.8 | 10431.8 | 9229.8 | 10255.3 | 9544.6 | 10261.6 | 9733.6 | 10619.9 | 9590 | 10209.4 | 9471.5 | 8352.9 | 10401.5 | 9904.1 | 9254.9 | 10708.8 | 10383.4 | 9585.6 | 9473.7 | 10506.5 | 9419.4 | 9687.7 | 10486.9 | 9215.3 | 10590.1 | 9214.2 | 10249.4 | 9436.6 | 10298.6 | 8931.9 | 10332.8 | 9330.4 | 10168 | 9307.8 | 10225.3 | 9480.3 | 9202.9 | 10129 | 9356 | 9141.1 | 10277.9 | 10291.2 | 10156.9 | 9307.1 | 10260.5 | 9211.2 | 10012.6 | 9312.5 | 9827.5 | 8677.2 | 10025.9 | 9268.2 | 9362.1 | 9409.6 | 9288.5 | 8021.3 | 9249.1 | 8222.6 | 9264.8 | 9278.1 | 10712.6 | 9350.1 | 10717.4 | 9524.4 | 10652.3 | 9456.2 | 9619.2 | 9448.8 | 10346.4 | 10655.1 | 10553.9 | 10564.9 | 10573.4 | 10621.3 | 9612.4 | 10585.2 | 10809.2 | 10758.3 | 10730.5 | 10655.8 | 10646.4 | 9637.2 | 10868.4 | 9729 | 30.35 | 33.55 | 33.79 | 33.48 | 33.61 | 33.94 | 0 | 44.7 | 0 | 0 | 45.3 | 45.6 | 4.44 | 5.01 | 4.59 | 5.07 | 4.89 | 4.98 | 7.28 | 8.29 | 7.84 | 8.02 | 7.56 | 8.16 | 5.39 | 5.47 | 5.53 | 5.61 | 5.62 | 5.67 | 1.17 | 1.28 | 1.05 | 1.52 | 1.47 | 1.32 | 5.33 | 5.43 | 5.35 | 5.52 | 5.51 | 5.58 | 0.35 | 0.45 | 0.36 | 0.43 | 0.4 | 0.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 700673 | 1255 | 687529 | 1313 | 43736.403 | 103.2 | 5.39 | 5.47 | 5.53 | 5.61 | 5.62 | 5.67 | 5.33 | 5.43 | 5.35 | 5.52 | 5.51 | 5.58 | 777000 | 1000 | 786000 | 1000 | 1558866 | 4467 | 1561000 | 1554399 | 12.9167 | 5.5483 | 1.3017 | 5.4533 | 0.40167 | 23.46% | 7.366% | 33.12 | 45.2 | 4.83 | 7.8583 | 1567193.2 | 1558200 | 1836185.1956 | 84.86% | 71 | 43916
2024-07-27 | 2025 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 335090.89 | 7:06 | 19:25 | 11298.3 | 11843.9 | 11733.2 | 11720.9 | 11811.8 | 11840.9 | 11881.1 | 12219.9 | 11831.6 | 11879.9 | 11639.6 | 11802.4 | 11745 | 11705.9 | 11792.3 | 11808.7 | 11725.6 | 11708.2 | 11725 | 11798.4 | 11666.7 | 11725.9 | 11491.9 | 11593.2 | 11448.8 | 10024.2 | 11460.2 | 11418.5 | 11747 | 11651.9 | 11510 | 11758.7 | 11791.9 | 11812.9 | 11832.8 | 11781.6 | 11830.6 | 11634.3 | 11652.6 | 11607.1 | 12259.7 | 11232.5 | 12164.4 | 11075.7 | 11725.3 | 12724.9 | 11022.7 | 12252.3 | 11822.1 | 11082.4 | 11841.1 | 11216.5 | 12162.3 | 10996 | 12092 | 12019 | 10802.2 | 12299.6 | 10815.9 | 12226.1 | 12090.3 | 10795.4 | 11889.8 | 11332.3 | 11518.6 | 10760.3 | 11416.9 | 11815.8 | 12155.7 | 10950.8 | 11998.4 | 10518.4 | 11711.4 | 11500.2 | 10828.4 | 11990.2 | 10616.7 | 12199.3 | 10879.9 | 12028 | 10991.8 | 11848 | 11113.9 | 12189.1 | 10985.2 | 11701 | 10974.1 | 9653.1 | 11969.4 | 11467.8 | 10720 | 12268.3 | 11941 | 11106 | 10966 | 12054.1 | 10880.6 | 11221.4 | 12062.2 | 10695.3 | 12132.9 | 10682.2 | 11838.2 | 10948.7 | 11869.4 | 10337.1 | 11916.9 | 10792.5 | 11792.3 | 10797.2 | 11886.7 | 10971.8 | 10697.6 | 11800 | 10877.3 | 10653.4 | 11892.1 | 11942.2 | 11777.7 | 10801 | 11854.6 | 10667.6 | 11611.8 | 10789.9 | 11490 | 10024.3 | 11611.6 | 10696.7 | 10952.7 | 11050.2 | 10748.9 | 9306.8 | 10867.6 | 9654.7 | 10880.4 | 10889.3 | 12420.1 | 10997.7 | 12485.6 | 11243.6 | 12409.2 | 11178.3 | 11388.6 | 11089.2 | 12120.1 | 12484.7 | 12408.7 | 12345 | 12308.9 | 12349.8 | 11347.8 | 12404 | 12443.6 | 12458.7 | 12524.6 | 12474.1 | 12468.4 | 11353.6 | 12480.1 | 11375 | 31.12 | 34.23 | 34.5 | 34.14 | 34.21 | 34.66 | 0 | 47.7 | 0 | 0 | 47.9 | 48.2 | 5.36 | 5.83 | 5.42 | 5.9 | 5.64 | 5.94 | 9.25 | 9.13 | 9.3 | 9.08 | 8.56 | 9.59 | 6.62 | 6.64 | 6.58 | 6.58 | 6.6 | 6.65 | 1.53 | 1.53 | 1.34 | 1.88 | 1.74 | 1.51 | 6.59 | 6.64 | 6.47 | 6.54 | 6.54 | 6.58 | 0.4 | 0.5 | 0.39 | 0.47 | 0.44 | 0.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 701600 | 1257 | 688441 | 1315 | 45568.47 | 107.8 | 6.62 | 6.64 | 6.58 | 6.58 | 6.6 | 6.65 | 6.59 | 6.64 | 6.47 | 6.54 | 6.54 | 6.58 | 927000 | 2000 | 912000 | 2000 | 1832067 | 4600 | 1835000 | 1827467 | 12.3167 | 6.6117 | 1.5883 | 6.56 | 0.44333 | 24.02% | 6.758% | 33.81 | 47.9333 | 5.6817 | 9.1517 | 1844654.9 | 1831534 | 2189423.2658 | 83.65% | 52 | 10231
2024-07-28 | 2025 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 335090.89 | 6:32 | 19:16 | 9253.1 | 9848.9 | 9798.5 | 9742.9 | 9857.6 | 9927.4 | 9980.2 | 10322.9 | 9818.5 | 9732.7 | 9732.1 | 9855.9 | 9856 | 9820.8 | 9850.6 | 9915.7 | 9797.3 | 9797.8 | 9884.2 | 9940.4 | 9807.8 | 9871.7 | 9593.9 | 9721.5 | 9640.8 | 8442.8 | 9631.7 | 9630.6 | 9917.3 | 9764.8 | 9639.4 | 9902.7 | 9775.3 | 9810.3 | 9947.1 | 9852.5 | 9932.9 | 9765.9 | 9782.7 | 9668.1 | 10277.5 | 9301.7 | 10140.1 | 9119.8 | 9682.3 | 10664.2 | 9131.6 | 10291.2 | 9944.3 | 9258.3 | 9954.2 | 9374.3 | 10268.8 | 9222.8 | 10145.2 | 10090.3 | 8994.9 | 10313.9 | 9020 | 10262.4 | 10136.2 | 9001 | 9901.9 | 9322.8 | 9551.6 | 8955.4 | 9454.2 | 9838.2 | 10114.1 | 9029.6 | 9902.8 | 8624.2 | 9722.9 | 9402.6 | 8923.3 | 9833 | 8640.7 | 10061.9 | 8820.1 | 9770 | 9029.2 | 9714.1 | 9133 | 10079.5 | 9080.8 | 9683.1 | 9143.7 | 8013.8 | 10055.8 | 9579.8 | 8967.1 | 10281.7 | 9969.6 | 9187.9 | 9071.2 | 10060.4 | 9041.7 | 9330.3 | 10063.9 | 8897.1 | 10105 | 8874.2 | 9850.6 | 9093.1 | 9903.5 | 8582.3 | 9947.5 | 8986.7 | 9822.9 | 8956.2 | 9916.8 | 9116.3 | 8884.9 | 9841 | 9053.5 | 8849.1 | 9962.8 | 9990 | 9850 | 8987.5 | 9944 | 8888.6 | 9714.8 | 8990.6 | 9583.5 | 8345.1 | 9720.7 | 8924.2 | 9013.5 | 9061.7 | 8958.4 | 7694 | 8855.4 | 7833 | 8711.3 | 8724.9 | 9916.9 | 8772.6 | 9921.3 | 8968.7 | 9937.3 | 8898 | 9079.3 | 8864.5 | 9536.6 | 9784.8 | 9738.4 | 9726.2 | 9757.1 | 9822.3 | 8950.8 | 9773 | 9694.4 | 9720.9 | 9794.9 | 9745.8 | 9731.7 | 8844 | 9779.7 | 8851.8 | 32.03 | 33.99 | 34.19 | 34.03 | 34.09 | 34.26 | 0 | 48 | 0 | 0 | 47.5 | 47.1 | 3.07 | 3.18 | 3.11 | 3.23 | 3.14 | 3.17 | 9.14 | 8.62 | 8.41 | 9.47 | 8.72 | 8.66 | 5.58 | 5.6 | 5.45 | 5.49 | 5.52 | 5.23 | 1.28 | 1.26 | 1.1 | 1.56 | 1.42 | 1.13 | 5.54 | 5.59 | 5.34 | 5.46 | 5.46 | 5.15 | 0.35 | 0.44 | 0.34 | 0.41 | 0.38 | 0.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 702373 | 1259 | 689186 | 1317 | 47082.07 | 112.267 | 5.58 | 5.6 | 5.45 | 5.49 | 5.52 | 5.23 | 5.54 | 5.59 | 5.34 | 5.46 | 5.46 | 5.15 | 773000 | 2000 | 745000 | 2000 | 1513600 | 4467 | 1514000 | 1509133 | 12.7333 | 5.4783 | 1.2917 | 5.4233 | 0.38167 | 23.58% | 7.037% | 33.765 | 47.5333 | 3.15 | 8.8367 | 1522829.9 | 1512800 | 1798541.1295 | 84.11% | 46 | 33036
2024-07-29 | 2025 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 335090.89 | 6:55 | 19:15 | 9708.2 | 10112 | 10128.1 | 10073.2 | 10227.2 | 10214.5 | 10187.3 | 10484.9 | 10109.4 | 10145.6 | 9923.9 | 10074 | 10021 | 9963.9 | 10101.4 | 10112 | 10013.1 | 9980.6 | 10027.7 | 10092.2 | 10006.3 | 10035.8 | 9837.5 | 9934.4 | 9809.2 | 8746.7 | 9795.9 | 9762.9 | 10065.8 | 9970 | 9892.7 | 10095.5 | 9999.6 | 10017.3 | 10130.4 | 10018.1 | 10122.3 | 9958.3 | 9980.3 | 9847.5 | 10526.8 | 9599 | 10483.2 | 9471.5 | 10081.3 | 11113.3 | 9539.6 | 10603.1 | 10137.8 | 9599.3 | 10160.7 | 9716.9 | 10445.1 | 9547.8 | 10408.1 | 10310.2 | 9384.2 | 10611.1 | 9405.4 | 10544.5 | 10451.1 | 9391.1 | 10187.2 | 9747.4 | 9879.3 | 9357.5 | 9869 | 10159.1 | 10514.2 | 9529.2 | 10388.4 | 9216.4 | 10145.5 | 9976.1 | 9495.1 | 10424.3 | 9378.6 | 10571.7 | 9494.5 | 10426.9 | 9479.8 | 10172.2 | 9558.8 | 10424 | 9447 | 9965.1 | 9493.7 | 8434.9 | 10292.6 | 9825.1 | 9250.9 | 10470 | 10175.6 | 9518.8 | 9402.5 | 10216.7 | 9319.9 | 9521.7 | 10221.4 | 9127.1 | 10331.4 | 9162.8 | 10065.3 | 9346.3 | 10110.9 | 8903.5 | 10154.2 | 9217.8 | 9995.2 | 9221.8 | 10078.3 | 9359.1 | 9149.4 | 9978.5 | 9271.7 | 9085.3 | 10062.9 | 10066.3 | 9692.5 | 9187.9 | 9987 | 9083.4 | 9807.4 | 9169.9 | 9666.2 | 8541.7 | 9765.3 | 9063.4 | 9227.1 | 9274.8 | 9098.9 | 7970.6 | 9022 | 8069 | 8902.8 | 8952.4 | 10199.1 | 9033 | 10195.3 | 9221.1 | 10097.6 | 9136.6 | 9223.9 | 9112.7 | 10018.4 | 10227.3 | 10272.1 | 10191.3 | 10164.4 | 10178 | 9332.3 | 10152.1 | 10345.3 | 10302.5 | 10341.8 | 10257 | 10202.7 | 9353.1 | 10392.9 | 9445.3 | 32.5825 | 35.377 | 35.5097 | 35.4206 | 35.5682 | 35.6264 | 0 | 45.9 | 0 | 0 | 45.6013 | 45.7 | 4.0957 | 4.0845 | 3.9775 | 4.1163 | 4.2376 | 4.2305 | 13.6617 | 13.7083 | 15.2933 | 12.4483 | 12.39 | 11.6583 | 5.8465 | 5.7686 | 5.8491 | 5.856 | 5.6356 | 5.6617 | 1.247 | 1.2992 | 1.1026 | 1.5538 | 1.4571 | 1.2869 | 5.764 | 5.7203 | 5.6632 | 5.742 | 5.5071 | 5.5372 | 0.38973 | 0.48372 | 0.38805 | 0.46172 | 0.42814 | 0.43962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 703171 | 1260 | 689954 | 1318 | 48643.337 | 116.8 | 5.8465 | 5.7686 | 5.8491 | 5.856 | 5.6356 | 5.6617 | 5.764 | 5.7203 | 5.6632 | 5.742 | 5.5071 | 5.5372 | 798000 | 1000 | 768000 | 1000 | 1561267 | 4533 | 1564000 | 1556734 | 12.3333 | 5.7696 | 1.3244 | 5.6556 | 0.43183 | 22.96% | 7.635% | 35.0141 | 45.7338 | 4.1237 | 13.1933 | 1569774.8 | 1559870 | 1889021.1761 | 82.58% | 71 | 53790
2024-07-30 | 2025 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 335090.89 | 6:28 | 19:22 | 9634.8 | 10205.1 | 10418.3 | 10411.5 | 10523.2 | 10489 | 10383.6 | 10532.4 | 9988.3 | 9975.3 | 9757.9 | 9875.2 | 9969.8 | 9795.5 | 10268.2 | 10175.9 | 10148.4 | 10037.8 | 9795.1 | 9856.8 | 9742.6 | 9775.7 | 9518.3 | 9619.1 | 9364 | 8286.9 | 9420.6 | 9383.6 | 9671.4 | 9610.7 | 9487.1 | 9612.6 | 9419.6 | 9417.3 | 9568.6 | 9463.8 | 9575.1 | 9473.3 | 9514.3 | 9390.5 | 10545.1 | 9771.6 | 10460.5 | 9600.7 | 9989.7 | 10851.8 | 9547.4 | 10543.1 | 9751.7 | 9202.7 | 9819.7 | 9207.4 | 10075.9 | 9336.4 | 9805.8 | 9736.9 | 8833.4 | 9950.3 | 9010.3 | 9988.5 | 9917.4 | 9014.2 | 9657.3 | 9241.4 | 9063.3 | 8478.4 | 9018.8 | 9237.5 | 9668.1 | 8605.5 | 9439.6 | 8255.5 | 9404.5 | 9015.1 | 8743.8 | 9446.4 | 8451.3 | 9889.8 | 8816.4 | 9690.6 | 8493.4 | 9161.3 | 8478.4 | 9433.7 | 8421.9 | 8892.9 | 8535.3 | 7371.7 | 9243 | 8863.2 | 8368.1 | 9560.4 | 9397.8 | 8805.4 | 8729.6 | 9344.7 | 8308.2 | 8527.9 | 9196.8 | 8182.3 | 9376.3 | 8221.5 | 9144.7 | 8449.6 | 9223 | 8031.1 | 9259.4 | 8378.9 | 9174.4 | 8433.5 | 9295 | 8545.7 | 8258.5 | 9107.4 | 8437.7 | 8243.5 | 9227 | 9188.2 | 9127.3 | 8451.6 | 9178.8 | 8350.8 | 9028.5 | 8420.1 | 8852.4 | 7822.4 | 9048.6 | 8451.2 | 8709.4 | 8782.6 | 8569.8 | 7425.9 | 8647.2 | 7698.1 | 8803.7 | 8819.4 | 9831.4 | 8787 | 10005.4 | 9034.5 | 9948.2 | 8970.3 | 9092.4 | 8962.1 | 9669.8 | 9983.2 | 9698.3 | 9712.9 | 9688.6 | 9755.9 | 9105.8 | 9908.8 | 9676.1 | 9784.8 | 10032.7 | 9955.1 | 9910.3 | 9051.6 | 9647.4 | 8977.9 | 30.0362 | 34.1666 | 34.2675 | 34.2151 | 34.1202 | 34.0487 | 0 | 44.3 | 0 | 0 | 43.7036 | 43.8 | 4.4229 | 4.6518 | 4.4016 | 4.5517 | 4.5762 | 4.3895 | 11.4133 | 11.9833 | 12.1267 | 11.32 | 15.635 | 19.7317 | 5.7199 | 5.5166 | 5.8969 | 5.237 | 5.1512 | 5.3991 | 1.3389 | 1.1991 | 1.1967 | 1.4956 | 1.2918 | 1.1096 | 5.6566 | 5.4818 | 5.7522 | 5.2064 | 5.0493 | 5.1985 | 0.36149 | 0.44734 | 0.37328 | 0.41264 | 0.37775 | 0.4074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 703940 | 1262 | 690669 | 1320 | 50122.737 | 121.267 | 5.7199 | 5.5166 | 5.8969 | 5.237 | 5.1512 | 5.3991 | 5.6566 | 5.4818 | 5.7522 | 5.2064 | 5.0493 | 5.1985 | 769000 | 2000 | 715000 | 2000 | 1479400 | 4467 | 1480000 | 1474933 | 12.9 | 5.4868 | 1.2719 | 5.3908 | 0.39665 | 23.18% | 7.358% | 33.4757 | 43.9345 | 4.499 | 13.7017 | 1487330.7 | 1479400 | 1806579.5045 | 81.89% | 70 | 36878
2024-07-31 | 2025 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 335090.89 | 6:40 | 19:30 | 10648.9 | 10979.6 | 10792.6 | 10825.2 | 10803.7 | 10788.3 | 10944.1 | 11187.9 | 11051.6 | 11234.9 | 10738 | 10939 | 10582.2 | 10694.6 | 10604.4 | 10573 | 10603.3 | 10633.2 | 10641.9 | 10691.5 | 10709.5 | 10708.2 | 10661.1 | 10690.9 | 10432.9 | 9207.5 | 10355.8 | 10369.6 | 10818.6 | 10823.7 | 10746.3 | 10832.2 | 10662.2 | 10651.2 | 10711.4 | 10678.2 | 10794.3 | 10713.4 | 10838.6 | 10751.3 | 11855.4 | 10956.5 | 11867.3 | 10883.3 | 11495 | 12366 | 10747 | 11742.5 | 10723.4 | 10210.2 | 10720.6 | 10269.8 | 11029.1 | 9967.6 | 10992.6 | 10847.5 | 10044.8 | 11359.5 | 10071.9 | 11309.4 | 11251.6 | 10114.7 | 11084.1 | 10793.8 | 10744.5 | 10176.6 | 10756.9 | 11148.4 | 11415.9 | 10498.8 | 11325.6 | 10205.8 | 11000.8 | 11096.1 | 10371.4 | 11593 | 10376.1 | 11677.5 | 10587.1 | 11606.4 | 10636.5 | 11391.2 | 10773.1 | 11614.4 | 10584.2 | 11141.3 | 10379.5 | 9147.7 | 10994.3 | 10691 | 9682.9 | 10969.9 | 10713 | 10135.9 | 10097.4 | 10838 | 10037.4 | 10276.4 | 11145.2 | 9968 | 11302.9 | 10016.9 | 11142.1 | 10347.5 | 11357.7 | 9864.7 | 11523.8 | 10445.2 | 11588.4 | 10662.2 | 11950.2 | 10970.9 | 9960.6 | 11022.6 | 10293.9 | 10083.9 | 11335.2 | 11334.2 | 11335.4 | 10481.3 | 11498.4 | 10497.3 | 11297.4 | 10702.2 | 11443.2 | 10043.5 | 11434.6 | 10622 | 10585.4 | 10591.1 | 10680.2 | 9145.2 | 10424 | 9012.9 | 10053.4 | 10138.9 | 12008.1 | 10561.6 | 12143.7 | 10841.9 | 11756.2 | 10549.8 | 10616.4 | 10405.5 | 12210.1 | 12483.1 | 12448.3 | 12372.3 | 12107.5 | 12054.4 | 11250.4 | 12353.6 | 12319.2 | 12404.4 | 12406.3 | 12331.9 | 12414.3 | 11453.3 | 12556.5 | 11521.3 | 26.4 | 33.38 | 33.91 | 33.42 | 33.28 | 33.68 | 0 | 47 | 0 | 0 | 47.8 | 48.7 | 4.2 | 4.62 | 4.2 | 4.67 | 4.44 | 4.48 | 8.17 | 8.4 | 8.18 | 8.21 | 8.01 | 8.27 | 6.33 | 6.32 | 6.73 | 6.34 | 6.41 | 7.02 | 1.43 | 1.4 | 1.35 | 1.78 | 1.59 | 1.57 | 6.22 | 6.24 | 6.52 | 6.25 | 6.27 | 6.84 | 0.42 | 0.53 | 0.44 | 0.51 | 0.46 | 0.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 704802 | 1263 | 691547 | 1322 | 51858.071 | 125 | 6.33 | 6.32 | 6.73 | 6.34 | 6.41 | 7.02 | 6.22 | 6.24 | 6.52 | 6.25 | 6.27 | 6.84 | 862000 | 1000 | 878000 | 2000 | 1735334 | 3733 | 1737000 | 1731601 | 12.8333 | 6.525 | 1.52 | 6.39 | 0.47833 | 23.3% | 7.486% | 32.345 | 47.8333 | 4.435 | 8.2067 | 1745376 | 1734860 | 2149338 | 80.72% | 48 | 5403
2024-08-01 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 335090.89 | 6:59 | 19:22 | 6216.5 | 6586.9 | 6544.4 | 6496.9 | 6604.4 | 6622.4 | 6674.6 | 6953.1 | 6589.9 | 6587.3 | 6494.3 | 6594.1 | 6547.8 | 6540.7 | 6617.4 | 6613.8 | 6569.5 | 6573 | 6569 | 6601.6 | 6587.4 | 6586.1 | 6511.4 | 6548 | 6412.7 | 5610.7 | 6400.4 | 6389.6 | 6650.9 | 6650.5 | 6561.9 | 6649.8 | 6617.1 | 6605 | 6642.4 | 6588.1 | 6671.9 | 6601.1 | 6662.8 | 6612.1 | 7205.9 | 6446 | 7165.6 | 6371.6 | 6812.9 | 7675.5 | 6347.8 | 7238.2 | 6599 | 6185.7 | 6635.3 | 6254 | 6895.8 | 6143.6 | 6823.3 | 6743.8 | 6027.5 | 6999.4 | 6041.5 | 6928.8 | 6825 | 6023.1 | 6619.7 | 6243 | 6381.8 | 6040 | 6389.2 | 6698.9 | 6905.9 | 6140.4 | 6777.8 | 5890.2 | 6588.5 | 6423 | 6031.3 | 6765.7 | 5897.5 | 6891.5 | 6010.4 | 6732.7 | 6162.3 | 6665.3 | 6274.5 | 6962.8 | 6193.5 | 6650.6 | 6206.4 | 5458.8 | 6873.2 | 6527.3 | 6063.8 | 7084 | 6852.8 | 6326.7 | 6274 | 6947.7 | 6217.9 | 6406.4 | 7006.3 | 6136.6 | 7089.2 | 6137.7 | 6877.4 | 6321.1 | 6944 | 5969.3 | 6979.7 | 6251.3 | 6897.2 | 6275.5 | 6986.4 | 6379.1 | 6157.7 | 6870.3 | 6285.8 | 6153.8 | 6970.5 | 7017.8 | 6893.1 | 6298.3 | 6977.5 | 6214.1 | 6767.2 | 6267.8 | 6694.6 | 5826.3 | 6793.2 | 6243.8 | 6360.4 | 6391.6 | 6291.2 | 5432 | 6252.6 | 5530.8 | 6250.5 | 6249.7 | 7198.5 | 6211.9 | 7226.3 | 6351.9 | 7172.5 | 6320.7 | 6434.8 | 6343.6 | 6896.5 | 7178.5 | 7103 | 7081.6 | 7096.7 | 7136.3 | 6407 | 7123.4 | 7184.2 | 7185.8 | 7188.4 | 7149.1 | 7149.5 | 6377.7 | 7177.8 | 6383.7 | 26.1 | 31.21 | 31.35 | 31.18 | 31.25 | 31.37 | 0 | 38.2 | 0 | 0 | 38.3 | 38.2 | 6.02 | 6.59 | 6.12 | 6.71 | 6.45 | 6.63 | 10.43 | 10.05 | 10.67 | 10.7 | 9.68 | 10.95 | 3.35 | 3.42 | 3.5 | 3.37 | 3.5 | 3.46 | 0.74 | 0.75 | 0.68 | 0.93 | 0.86 | 0.79 | 3.28 | 3.41 | 3.41 | 3.35 | 3.44 | 3.38 | 0.21 | 0.27 | 0.22 | 0.26 | 0.24 | 0.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 705326 | 1265 | 692074 | 1322 | 52905.337 | 128.667 | 3.35 | 3.42 | 3.5 | 3.37 | 3.5 | 3.46 | 3.28 | 3.41 | 3.41 | 3.35 | 3.44 | 3.38 | 524000 | 2000 | 527000 | 0 | 1047266 | 3667 | 1049000 | 1043599 | 12.3833 | 3.4333 | 0.79167 | 3.3783 | 0.24 | 23.06% | 7.104% | 30.41 | 38.2333 | 6.42 | 10.4133 | 1050643.1 | 1045933 | 1173180.4899 | 89.15% | 55 | 14793
2024-08-02 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 335090.89 | 6:56 | 19:21 | 2646.8 | 2785 | 2788 | 2772.6 | 2812.2 | 2820.1 | 2840.1 | 2958.2 | 2801.6 | 2806.1 | 2755.5 | 2803 | 2783.4 | 2780.4 | 2821.2 | 2820.6 | 2796.9 | 2791.6 | 2790.2 | 2804.2 | 2791.4 | 2800.1 | 2744.2 | 2770.5 | 2720.3 | 2381.4 | 2723.4 | 2715.1 | 2818.1 | 2799.3 | 2752.9 | 2801.8 | 2804.9 | 2803.5 | 2823.8 | 2799 | 2823.6 | 2786.3 | 2802.9 | 2794.7 | 3011.3 | 2689.8 | 2993.2 | 2655.9 | 2846 | 3221.2 | 2649.2 | 3026.7 | 2815.8 | 2635.2 | 2832.4 | 2660 | 2946.3 | 2623.5 | 2907.1 | 2874.2 | 2545 | 2972.4 | 2569.6 | 2947.8 | 2902.6 | 2568.7 | 2784.4 | 2628.6 | 2736.8 | 2571.5 | 2712.9 | 2848 | 2943.1 | 2615.1 | 2867.8 | 2502.6 | 2812.8 | 2721.3 | 2565.7 | 2891 | 2512.4 | 2940.5 | 2560.4 | 2878.9 | 2324.8 | 2584.2 | 2662 | 2932.4 | 2625 | 2826.2 | 2632 | 2310.1 | 2921.1 | 2767.8 | 2560.2 | 3011.8 | 2913.4 | 2680.2 | 2644.8 | 2952 | 2639.5 | 2723.8 | 2971.9 | 2603.3 | 3005.6 | 2588.1 | 2896.6 | 2653.9 | 2924.4 | 2513 | 2938.6 | 2619.6 | 2880.3 | 2616.2 | 2916 | 2656.2 | 2618.2 | 2910.6 | 2168.4 | 2392.3 | 2397.2 | 2773.2 | 2900.9 | 2645.2 | 2936.9 | 2611.8 | 2843.6 | 2618.7 | 2808.6 | 2434.1 | 2847.2 | 2622.2 | 2678.5 | 2696.7 | 2646 | 2282.2 | 2630.4 | 2318.3 | 2639.8 | 2645.4 | 3038.2 | 2616.7 | 3057.3 | 2680 | 3027.7 | 2670.4 | 2711.2 | 2688.2 | 2916.3 | 3044.4 | 2995.9 | 2987.5 | 2989.9 | 3010.8 | 2711.7 | 3016 | 3030.9 | 3034.9 | 3061.4 | 3033.5 | 3024.5 | 2700.4 | 3026.4 | 2692.5 | 28.09 | 28.75 | 28.62 | 28.8 | 28.79 | 28.94 | 0 | 31.52 | 0 | 0 | 31.7 | 31.7 | 5.17 | 5.14 | 5.09 | 5.35 | 5.32 | 4.85 | 7.45 | 7.24 | 7.8 | 8.07 | 7.52 | 7.19 | 1.39 | 1.4 | 1.42 | 1.45 | 1.43 | 1.42 | 0.23 | 0.23 | 0.21 | 0.28 | 0.26 | 0.24 | 1.37 | 1.39 | 1.37 | 1.36 | 1.4 | 1.39 | 0.02 | 0.03 | 0.02 | 0.03 | 0.03 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 705548 | 1266 | 692293 | 1324 | 53345.004 | 132.667 | 1.39 | 1.4 | 1.42 | 1.45 | 1.43 | 1.42 | 1.37 | 1.39 | 1.37 | 1.36 | 1.4 | 1.39 | 222000 | 1000 | 219000 | 2000 | 439667 | 4000 | 438000 | 435667 | 12.4167 | 1.4183 | 0.24167 | 1.38 | 0.026667 | 17.04% | 1.932% | 28.665 | 31.64 | 5.1533 | 7.545 | 442550.7 | 438600 | 489543.5975 | 89.59% | 46 | 3244
2024-08-03 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 335090.89 | 6:59 | 19:13 | 3178 | 3346 | 3392 | 3364 | 3438 | 3436 | 3421 | 3567 | 3352 | 3359 | 3303 | 3350 | 3351 | 3333 | 3442 | 3425 | 3411 | 3400 | 3378 | 3382 | 3382 | 3388 | 3314 | 3350 | 3255 | 2845 | 3268 | 3261 | 3392 | 3365 | 3299 | 3353 | 3326 | 3324 | 3359 | 3333 | 3368 | 3334 | 3350 | 3324 | 3677 | 3280 | 3644 | 3236 | 3479 | 3931 | 3229 | 3691 | 3373 | 3148 | 3384 | 3165 | 3523 | 3148 | 3452 | 3404 | 3031 | 3518 | 3071 | 3501 | 3457 | 3066 | 3308 | 3123 | 3204 | 3008 | 3192 | 3341 | 3453 | 3073 | 3391 | 2955 | 3305 | 3228 | 3021 | 3412 | 2968 | 3470 | 3031 | 3412 | 2944 | 3325 | 3145 | 3465 | 3089 | 3323 | 3051 | 2604 | 3386 | 3221 | 2980 | 3493 | 3394 | 3134 | 3113 | 3421 | 3036 | 3137 | 3419 | 2991 | 3501 | 2991 | 3380 | 3081 | 3432 | 2924 | 3444 | 3066 | 3406 | 3084 | 3434 | 3122 | 3010 | 3343 | 3055 | 2980 | 3394 | 3400 | 3290 | 3037 | 3381 | 3011 | 3296 | 3055 | 3188 | 2828 | 3285 | 3018 | 3051 | 3082 | 3034 | 2606 | 3024 | 2684 | 3119 | 3128 | 3641 | 3129 | 3647 | 3191 | 3603 | 3164 | 3210 | 3174 | 3520 | 3661 | 3632 | 3603 | 3598 | 3617 | 3249 | 3620 | 3691 | 3687 | 3700 | 3663 | 3659 | 3260 | 3683 | 3270 | 25.92 | 26.78 | 26.67 | 26.73 | 26.63 | 26.83 | 0 | 29.57 | 0 | 0 | 29.6 | 29.82 | 4.15 | 4.31 | 4.21 | 4.3 | 4.25 | 2.46 | 7.42 | 9 | 8.76 | 6.97 | 7.32 | 7.97 | 1.72 | 1.74 | 1.78 | 1.8 | 1.68 | 1.76 | 0.2 | 0.21 | 0.21 | 0.24 | 0.24 | 0.21 | 1.67 | 1.7 | 1.69 | 1.62 | 1.62 | 1.69 | 0.03 | 0.04 | 0.04 | 0.03 | 0.04 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 705813 | 1267 | 692554 | 1325 | 53868.9 | 137.3 | 1.72 | 1.74 | 1.78 | 1.8 | 1.68 | 1.76 | 1.67 | 1.7 | 1.69 | 1.62 | 1.62 | 1.69 | 265000 | 1000 | 261000 | 1000 | 523896 | 4633 | 524000 | 519263 | 12.2333 | 1.7467 | 0.21833 | 1.665 | 0.035 | 12.5% | 2.102% | 26.5933 | 29.6633 | 3.9467 | 7.9067 | 526828 | 520410 | 592503.3536 | 87.83% | 51 | 7480
2024-08-04 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 335090.89 | 6:47 | 19:26 | 8557.2 | 8982.1 | 8957.9 | 8900.2 | 8989.5 | 8972.2 | 9047.6 | 9385.4 | 9007.3 | 8983.5 | 8834.2 | 8967.6 | 8990.4 | 8921 | 9212 | 9162.8 | 9137.2 | 9050.2 | 9079.2 | 9182.1 | 8867.2 | 8996.1 | 8528.1 | 8714.2 | 8620.9 | 7704 | 8862.1 | 8687 | 8789.1 | 8581.6 | 8404.4 | 8677 | 8539.9 | 8605.6 | 8859.7 | 8688.7 | 8701.8 | 8508.7 | 8503.5 | 8448.1 | 9168 | 8327.6 | 9122.3 | 8238.8 | 8726.6 | 9670.5 | 8203.3 | 9195.1 | 9029.5 | 8513.6 | 9129.7 | 8664.8 | 9459.1 | 8528.9 | 9379.7 | 9261.3 | 8303.2 | 9551.3 | 8271.1 | 9410.2 | 9289.7 | 8240 | 9080.1 | 8641.1 | 8904.2 | 8393.4 | 8867.9 | 9232.3 | 9499.4 | 8579.6 | 9417.7 | 8287.8 | 9073.4 | 8988.3 | 8354.4 | 9364.5 | 8241.5 | 9434.6 | 8399.4 | 9371.2 | 8581.4 | 9261.6 | 8736.9 | 9567 | 8597.6 | 9148.6 | 8495.1 | 7490.7 | 9199.4 | 8827.9 | 8107.6 | 9180.5 | 8848.3 | 8214.2 | 8082.9 | 8883 | 8023.8 | 8307.1 | 8958.5 | 7965.4 | 9028.9 | 7924.8 | 8738.9 | 8095.2 | 8823.2 | 7642.7 | 8860.5 | 7978.4 | 8760.6 | 8009.9 | 8806.5 | 8119 | 8018.9 | 8743.6 | 7960 | 7846.9 | 8721.9 | 8776.3 | 8622.7 | 7967.5 | 8780.8 | 7881.6 | 8571.6 | 7983.6 | 8431.8 | 7338.3 | 8571.8 | 7849.8 | 8027.5 | 8075.9 | 7905.6 | 6873.9 | 7906.9 | 7077.7 | 8116.1 | 8185.5 | 9642.4 | 8423.2 | 9685.4 | 8585.5 | 9520 | 8474 | 8565 | 8376.5 | 9462.1 | 9713.3 | 9698.7 | 9606.5 | 9622.7 | 9649.4 | 8817.4 | 9664.7 | 9985.8 | 9916.8 | 9940.2 | 9836.4 | 9758.6 | 8808.8 | 9852.3 | 8872.4 | 27.39 | 29.54 | 29.73 | 29.69 | 29.48 | 29.76 | 0 | 39.34 | 0 | 0 | 39.7 | 40.3 | 4.09 | 4.23 | 3.48 | 4.44 | 4.29 | 3.56 | 7.11 | 7.34 | 7.25 | 7.42 | 7.28 | 7.66 | 4.92 | 4.89 | 4.85 | 5.13 | 4.8 | 5.14 | 0.68 | 0.8 | 0.67 | 0.93 | 0.88 | 0.93 | 4.88 | 4.85 | 4.69 | 4.99 | 4.7 | 5.08 | 0.23 | 0.28 | 0.24 | 0.27 | 0.23 | 0.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 706520 | 1269 | 693244 | 1327 | 55261.404 | 141.733 | 4.92 | 4.89 | 4.85 | 5.13 | 4.8 | 5.14 | 4.88 | 4.85 | 4.69 | 4.99 | 4.7 | 5.08 | 707000 | 2000 | 690000 | 2000 | 1392504 | 4433 | 1393000 | 1388071 | 12.65 | 4.955 | 0.815 | 4.865 | 0.255 | 16.45% | 5.242% | 29.265 | 39.78 | 4.015 | 7.3433 | 1400402.8 | 1390734 | 1654416.7233 | 84.06% | 45 | 78864
2024-08-05 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 335090.89 | 8:56 | 18:00 | 2139.9 | 2248.7 | 2269.3 | 2249.5 | 2291.7 | 2292.7 | 2298.4 | 2397.8 | 2257.9 | 2048 | 2231.6 | 2258.2 | 2244.7 | 2241.7 | 2295.1 | 2289.3 | 2262.2 | 2264.2 | 2248.2 | 2254.6 | 2248.1 | 2236 | 2205 | 2227.4 | 2170.3 | 1902.4 | 2181.3 | 2172.4 | 2256 | 2242.1 | 2204.8 | 2250.6 | 2212.6 | 2206.2 | 2246.5 | 2227 | 2248.2 | 2223.1 | 2229.2 | 2212.9 | 2467.1 | 2195.4 | 2443.6 | 2159.1 | 2300.2 | 2616.3 | 2169.6 | 2477.8 | 2263 | 2115.5 | 2273.3 | 2134.5 | 2363.8 | 2111.6 | 2226.5 | 0 | 2045.2 | 2373.9 | 2064.2 | 2363.8 | 2340.2 | 2064.8 | 2241.8 | 2121.2 | 2159.5 | 2024.6 | 2151.7 | 2239.7 | 2331.2 | 2062.7 | 2284.8 | 1977.8 | 2238 | 2168 | 2046.6 | 2297.3 | 2000 | 2353.4 | 2052.2 | 2304.5 | 2046.5 | 2210.9 | 2083.7 | 2306.4 | 2052 | 2206.1 | 2055.4 | 1805.3 | 2275.2 | 2148.8 | 1995.7 | 2342 | 2265.9 | 2087.2 | 2068.3 | 2296.3 | 2041.3 | 2114.9 | 2290.9 | 2003.6 | 2330.8 | 1999.7 | 2248.2 | 2057.1 | 2270.4 | 1946.4 | 2279 | 2034 | 2247.7 | 2031.6 | 2258.4 | 2060.4 | 2029.9 | 2235.9 | 2034.9 | 1987.7 | 2258.8 | 2280.7 | 0 | 2037.1 | 2261.6 | 2007.8 | 2191.4 | 2024.7 | 0 | 1879.8 | 2195.2 | 2006.3 | 2031.9 | 2046.6 | 2006.2 | 1729.5 | 1992.5 | 1767 | 2005.6 | 2013.7 | 2350.5 | 2012.7 | 2355.6 | 2063.6 | 2334.4 | 2054.2 | 2085.1 | 2040.3 | 2247.6 | 2348.2 | 2295.8 | 2306.8 | 143.6 | 2327.5 | 2088 | 2322.2 | 2350.2 | 2343 | 2346.3 | 2324 | 2325.4 | 2055.1 | 2352.4 | 2070.1 | 25.02 | 26.56 | 26.57 | 26.77 | 26.73 | 26.77 | 0 | 30.21 | 0 | 0 | 29.9 | 29.81 | 5.91 | 5.76 | 5.68 | 5.94 | 6.12 | 5.63 | 8.76 | 9.82 | 8.56 | 8.68 | 9.58 | 9.02 | 1.16 | 1.16 | 1.18 | 1.17 | 1.12 | 1.11 | 0.16 | 0.16 | 0.15 | 0.18 | 0.19 | 0.13 | 1.12 | 1.12 | 1.11 | 1.09 | 1.07 | 1.06 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 706696 | 1271 | 693409 | 1329 | 55599.404 | 147.067 | 1.16 | 1.16 | 1.18 | 1.17 | 1.12 | 1.11 | 1.12 | 1.12 | 1.11 | 1.09 | 1.07 | 1.06 | 176000 | 2000 | 165000 | 2000 | 338000 | 5334 | 337000 | 332666 | 9.0667 | 1.15 | 0.16167 | 1.095 | 0.028333 | 14.06% | 2.588% | 26.4033 | 29.9733 | 5.84 | 9.07 | 340837.7 | 333130 | 389905.9172 | 85.44% | 45 | 35868
2024-08-06 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 335090.89 | 6:56 | 19:16 | 1518.6 | 1609.1 | 1635.2 | 1612.5 | 1663 | 1668.9 | 1657.5 | 1740.6 | 1620.3 | 1607.9 | 1617.3 | 1634.7 | 1652.8 | 1641.6 | 1718.7 | 1703 | 1709.8 | 1731.2 | 1708.7 | 1704.5 | 1738.4 | 1732.1 | 1731.8 | 1734.8 | 1690.1 | 1466.1 | 1663 | 1679 | 1766.1 | 1779.6 | 1738.2 | 1318.5 | 1777.3 | 1742.5 | 1751.9 | 1752.3 | 1779.7 | 1777.7 | 0 | 1753.5 | 2118.6 | 1915.9 | 2108.6 | 1908.1 | 2001.1 | 2239.8 | 1825.7 | 2090.7 | 1543.4 | 1578.2 | 1700.2 | 1606.5 | 1784.2 | 1577.5 | 1769.3 | 1759.1 | 1533.6 | 1807.1 | 1515.1 | 1771.6 | 1735.2 | 1521.3 | 1657.9 | 1563.1 | 1688.5 | 1605.5 | 1668.6 | 1783.2 | 1765.6 | 1629.6 | 1773.1 | 1560.3 | 1718.7 | 1686.3 | 1564.6 | 1797.5 | 1548.2 | 1789.4 | 1557.6 | 1761.1 | 1629.3 | 1752.4 | 1658.7 | 1843.7 | 1644.4 | 1772.4 | 1637.2 | 1103.3 | 1563.8 | 1731.2 | 1620.7 | 1907.8 | 1850.5 | 1704.9 | 1693.6 | 1878 | 1653.6 | 1695 | 1852.3 | 1605.3 | 1921.3 | 1623 | 1854 | 1668.8 | 1879 | 1588.1 | 1880.9 | 1657.9 | 1865.4 | 1679.8 | 1872.6 | 1689.3 | 1608 | 1774.6 | 1640.5 | 1590.7 | 1819.4 | 1819.3 | 1411.5 | 1628 | 1819.6 | 1622 | 1775.3 | 1642.5 | 0 | 1515.8 | 1776.7 | 1633 | 1639.1 | 1642.3 | 1648.2 | 1404.6 | 1607 | 1417.7 | 1624.4 | 1623.2 | 1806.4 | 1567.6 | 1813 | 1602.4 | 1822.7 | 1607 | 1638.1 | 1629.7 | 1678.8 | 1755.5 | 0 | 1697.1 | 1755 | 1777.4 | 1594.3 | 1759.7 | 1710.9 | 1713.8 | 1721.3 | 1711.3 | 1715.9 | 1537.7 | 1655.5 | 1537.3 | 25.4166 | 25.447 | 25.4205 | 25.5279 | 25.4363 | 25.4445 | 0 | 26.0804 | 0 | 0 | 26.0804 | 25.9 | 5.3674 | 5.5872 | 5.68 | 5.6081 | 5.7922 | 5.0289 | 9.8217 | 10.3133 | 10.1233 | 9.2683 | 10.2617 | 10.085 | 0.85752 | 0.92069 | 1.0292 | 0.98736 | 0.90893 | 0.86649 | 0.014968 | 0.016742 | 0.01804 | 0.017045 | 0.0186 | 0.012796 | 0.82599 | 0.88371 | 0.97328 | 0.85582 | 0.86805 | 0.82047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 706830 | 1272 | 693540 | 1330 | 55862.738 | 151.467 | 0.85752 | 0.92069 | 1.0292 | 0.98736 | 0.90893 | 0.86649 | 0.82599 | 0.88371 | 0.97328 | 0.85582 | 0.86805 | 0.82047 | 134000 | 1000 | 131000 | 1000 | 263334 | 4400 | 263000 | 258934 | 12.3333 | 0.92837 | 0.016365 | 0.87122 | 0 | 1.763% | 0% | 25.4488 | 26.0203 | 5.5106 | 9.9789 | 266528.1 | 261870 | 316462.4115 | 82.75% | 27 | 45969
2024-08-07 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 335090.89 | 6:55 | 19:26 | 4964 | 5271 | 5288 | 5234.9 | 5348 | 5376.7 | 5398.9 | 5650.9 | 5289.3 | 5194.5 | 5255.6 | 5321.3 | 5336 | 5313.6 | 5436.5 | 5422 | 5366.1 | 5409.7 | 5417.9 | 5435.4 | 5426.7 | 5435.7 | 5363.5 | 5397.2 | 5300 | 4621.9 | 5277.1 | 5282.1 | 5501.5 | 5492.7 | 5400.4 | 5389 | 5509.8 | 5412.5 | 5495.6 | 5469.1 | 5543.3 | 5479 | 5517.4 | 5504.6 | 6045.8 | 5409 | 6000.1 | 5347.7 | 5728.8 | 6470.5 | 5306.3 | 6050.9 | 5369.1 | 5045.8 | 5429.5 | 5111.3 | 5663 | 5038.4 | 5591.4 | 5524.1 | 4899.9 | 5708.3 | 4911.9 | 5625.6 | 5524.1 | 4878.2 | 5356.9 | 5033.2 | 5227.9 | 4945 | 5217.2 | 5484.7 | 5627.1 | 5019 | 5533.2 | 4822.1 | 5367.7 | 5259.5 | 4905.8 | 5544.3 | 4818.2 | 5607.7 | 4885.7 | 5493.6 | 5042.9 | 5407.9 | 5158.5 | 5698.5 | 5083.2 | 5469.8 | 5077.9 | 4482.5 | 5670.6 | 5365.2 | 5000 | 5864.3 | 5686.1 | 5245.6 | 5210 | 5767.8 | 5168 | 5332.7 | 5821.6 | 5095.6 | 5921.5 | 5094.3 | 5743.6 | 5254.3 | 5802.2 | 4969 | 5825.1 | 5199.9 | 5753.7 | 5220.5 | 5813.9 | 5303.9 | 5130 | 5680.3 | 5219 | 5103.2 | 5802.2 | 5832.4 | 5705.5 | 5228.1 | 5798.3 | 5156.7 | 5624.7 | 5204.3 | 5553.9 | 4840.8 | 5643.8 | 5186.3 | 5295 | 5325.9 | 5236.3 | 4520.8 | 5222.7 | 4607.6 | 5257.8 | 5256 | 6010.5 | 5187 | 6037.9 | 5307.6 | 6006.2 | 5278.3 | 5375.2 | 5314.6 | 5748.7 | 5986.6 | 0 | 5729.9 | 5915.2 | 5956.8 | 5356.7 | 5950.3 | 5955.2 | 5960.1 | 5959.6 | 5923.8 | 5924.6 | 5298.2 | 5976.6 | 5320.7 | 27.61 | 28.93 | 28.88 | 28.88 | 28.92 | 29.06 | 0 | 34.2 | 0 | 0 | 34.2 | 34.2 | 6.28 | 6.4 | 6.39 | 6.32 | 6.02 | 6.71 | 9.78 | 9.7 | 9.41 | 9.62 | 9.35 | 9.56 | 2.78 | 2.87 | 2.97 | 2.78 | 2.95 | 2.93 | 0.38 | 0.42 | 0.42 | 0.46 | 0.47 | 0.45 | 2.75 | 2.85 | 2.85 | 2.76 | 2.89 | 2.86 | 0.1 | 0.13 | 0.11 | 0.11 | 0.11 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 707259 | 1274 | 693972 | 1331 | 56721.6 | 155.867 | 2.78 | 2.87 | 2.97 | 2.78 | 2.95 | 2.93 | 2.75 | 2.85 | 2.85 | 2.76 | 2.89 | 2.86 | 429000 | 2000 | 432000 | 1000 | 858862 | 4400 | 858000 | 854462 | 12.5167 | 2.88 | 0.43333 | 2.8267 | 0.11333 | 15.05% | 4.009% | 28.7133 | 34.2 | 6.3533 | 9.57 | 860840.4 | 858600 | 994626.7562 | 86.32% | 35 | 42336
2024-08-08 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 335090.89 | 6:41 | 19:29 | 9145.5 | 9526.2 | 9338.2 | 9342.6 | 9410.5 | 9437.2 | 9570.9 | 9906.1 | 9651.8 | 9664.4 | 9438.8 | 9621.7 | 9340.4 | 9443.4 | 9480.7 | 9395 | 9396.2 | 9525.5 | 9406 | 9413.3 | 9545.8 | 9493.9 | 9492 | 9519.1 | 9227.5 | 8101.8 | 9170.6 | 9182.4 | 9621.9 | 9665 | 9527.8 | 9570.4 | 9543.3 | 9377.3 | 9524.2 | 9488.3 | 9685.7 | 9621 | 9541.9 | 9594.3 | 10377.7 | 9384.9 | 10333.6 | 9286.5 | 9912.4 | 10910.9 | 9294.2 | 10393 | 9450.6 | 9020 | 9509.8 | 9062.7 | 9780.1 | 8781.8 | 9857.1 | 9606.9 | 8893.2 | 10194.2 | 8878 | 10097 | 9971.2 | 8872.6 | 9750.4 | 9281.9 | 9398.1 | 8995.7 | 9424.1 | 9894.4 | 10090.6 | 9188.2 | 10028.2 | 8846.1 | 9691.7 | 9623.2 | 8999.8 | 10040.7 | 8892.6 | 10171.6 | 9051.6 | 10034 | 9215.9 | 9792.5 | 9417.8 | 10233.2 | 9254.1 | 9852.7 | 9197.2 | 8094.9 | 10176.1 | 9619 | 9079.1 | 10417.5 | 10050.3 | 9237.9 | 9131.4 | 10171 | 9246.1 | 9535.5 | 10241.9 | 9112.3 | 10243.2 | 9025.1 | 9982.6 | 9248.3 | 10062.2 | 8763.3 | 10150.7 | 9175.7 | 10030.4 | 9196.3 | 10164.5 | 9383.9 | 9160 | 10016 | 9220.2 | 9067.4 | 10095.1 | 10155.7 | 9920.8 | 9221.3 | 10125.5 | 9131.3 | 9874.9 | 9207.1 | 9690.1 | 8592.1 | 9924.6 | 9183.6 | 9352.3 | 9415.2 | 9266.5 | 8036.2 | 9271.3 | 8139.4 | 9200.8 | 9251.6 | 10616.2 | 9436.9 | 10772.5 | 9681.5 | 10633.9 | 9560.4 | 9662.7 | 9487.4 | 10656.9 | 10916.1 | 8041.3 | 10738.5 | 10622 | 10602.9 | 9878 | 10818.8 | 10918.4 | 10995.8 | 11098.8 | 11033.9 | 11018.7 | 10084.3 | 10817.5 | 9986.7 | 26.74 | 30.16 | 30.34 | 30.02 | 30.07 | 30.5 | 0 | 40.4 | 0 | 0 | 41.06 | 41.6 | 5.12 | 5.19 | 4.71 | 5.35 | 5.07 | 5.55 | 8.22 | 7.81 | 8.13 | 8.05 | 7.91 | 8.2 | 5.29 | 5.33 | 5.53 | 5.38 | 5.59 | 5.81 | 0.81 | 0.89 | 0.99 | 1.04 | 1.11 | 1.21 | 5.26 | 5.32 | 5.33 | 5.35 | 5.52 | 5.74 | 0.25 | 0.32 | 0.3 | 0.29 | 0.31 | 0.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 708019 | 1276 | 694749 | 1333 | 58253.94 | 160.133 | 5.29 | 5.33 | 5.53 | 5.38 | 5.59 | 5.81 | 5.26 | 5.32 | 5.33 | 5.35 | 5.52 | 5.74 | 760000 | 2000 | 777000 | 2000 | 1532340 | 4266 | 1533000 | 1528074 | 12.8 | 5.4883 | 1.0083 | 5.42 | 0.305 | 18.37% | 5.627% | 29.6383 | 41.02 | 5.165 | 8.0533 | 1540321.6 | 1169260 | 1397155.1175 | 83.69% | 43 | 10718
2024-08-09 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 335090.89 | 6:39 | 19:16 | 10706.8 | 11360.7 | 11235.2 | 11152.4 | 11346 | 11402.7 | 11425.8 | 11820 | 11419.2 | 11181.5 | 11157.5 | 11346.1 | 11233.7 | 11202.6 | 11247.2 | 11305 | 11070.7 | 11142.4 | 11201.9 | 11319.1 | 11215.5 | 11187.2 | 10960.3 | 11076.2 | 10824.2 | 9620.1 | 10945.4 | 10900.4 | 11176.2 | 11061.1 | 10845 | 11048.2 | 10989.4 | 10888.6 | 11162.6 | 11055.5 | 11149.4 | 10993.1 | 10999.3 | 10864.5 | 11597.3 | 10565.5 | 11520.5 | 10475.2 | 11086.5 | 12156 | 10353.2 | 11578.1 | 11146.3 | 10589.2 | 11351.6 | 10698.6 | 11706.3 | 10618.5 | 11479.2 | 11325.5 | 10261.3 | 11707.4 | 10378.8 | 11653.3 | 11515.1 | 10356.7 | 11254 | 10661 | 10838 | 10221.3 | 10812.2 | 11281.6 | 11588.1 | 10554.4 | 11486.1 | 10179.9 | 11096.1 | 11048.7 | 10316 | 11560.5 | 10278.7 | 11582.9 | 10344.2 | 11445 | 10599.5 | 11271.6 | 10771.5 | 11697 | 10549.5 | 11185.2 | 10418.6 | 9197.5 | 11331.1 | 10880 | 10075.3 | 11614.7 | 11278.1 | 10429.7 | 10297.6 | 11355.2 | 10263.5 | 10514.6 | 11369.8 | 10069.9 | 11444.6 | 10129.1 | 11200 | 10409.9 | 11191.9 | 9884 | 11278.3 | 10300.5 | 11126.9 | 10182.6 | 11264.1 | 10413.2 | 10016.5 | 10971.8 | 10279.9 | 10048.4 | 11249.9 | 11312.5 | 11071 | 10323.9 | 11382.4 | 10267.7 | 11072.3 | 10351.2 | 10886.6 | 9598.2 | 11137.7 | 10297.4 | 10483.2 | 10506.6 | 10369.3 | 8972.9 | 10230.3 | 8993.5 | 10200.6 | 10213.7 | 11600.6 | 10257 | 11769.8 | 10557.2 | 11688.1 | 10427.9 | 10571 | 10379.2 | 11494.2 | 11824.6 | 10737.4 | 11649.7 | 11592.8 | 11574.9 | 10611 | 11671.4 | 11922.2 | 11983.6 | 12102.6 | 11983.7 | 11921.9 | 10816.3 | 11915.7 | 10817.7 | 32.0842 | 32.1058 | 32.3617 | 32.0483 | 32.3617 | 32.5421 | 0 | 44.8 | 0 | 0 | 44.3514 | 45.1 | 4.7318 | 4.8915 | 3.9317 | 4.9122 | 3.9317 | 4.679 | 7.2833 | 7.4633 | 7.1833 | 7.0367 | 7.1833 | 7.3383 | 6.4445 | 6.3508 | 6.1526 | 6.2236 | 6.1526 | 6.2986 | 1.1306 | 1.133 | 1.221 | 1.418 | 1.221 | 1.2892 | 6.4388 | 6.3619 | 5.9823 | 6.2318 | 5.9823 | 6.185 | 0.2994 | 0.39793 | 0.35442 | 0.3734 | 0.35442 | 0.42985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 708901 | 1277 | 695613 | 1335 | 59994.938 | 164.6 | 6.4445 | 6.3508 | 6.1526 | 6.2236 | 6.1526 | 6.2986 | 6.4388 | 6.3619 | 5.9823 | 6.2318 | 5.9823 | 6.185 | 882000 | 1000 | 864000 | 2000 | 1740998 | 4467 | 1743000 | 1736531 | 12.6167 | 6.2704 | 1.2355 | 6.197 | 0.36824 | 19.7% | 5.942% | 32.2506 | 44.7505 | 4.513 | 7.2481 | 1751010.5 | 1740200 | 2077964.4567 | 83.75% | 38 | 19955
2024-08-10 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 335090.89 | 6:53 | 19:05 | 9036 | 9564 | 9568 | 9491 | 9634 | 9674 | 9742 | 10082 | 9593 | 9503 | 9459 | 9600 | 9615 | 9534 | 9622 | 9622 | 9498 | 9527 | 9607 | 9699 | 9585 | 9601 | 9382 | 9459 | 9396 | 8356 | 9439 | 9401 | 9604 | 9556 | 9404 | 9589 | 9622 | 9527 | 9737 | 9635 | 9710 | 9534 | 9583 | 9470 | 10297 | 9424 | 10273 | 9314 | 9897 | 10938 | 9317 | 10329 | 9521 | 9058 | 9699 | 9150 | 10050 | 9086 | 9891 | 9779 | 8744 | 10063 | 8839 | 9967 | 9827 | 8805 | 9608 | 9108 | 9320 | 8756 | 9242 | 9625 | 9919 | 8914 | 9773 | 8612 | 9520 | 9379 | 8804 | 9860 | 8713 | 9938 | 8825 | 9845 | 8937 | 9560 | 9163 | 9986 | 8986 | 9588 | 8919 | 7862 | 9834 | 9329 | 8779 | 10137 | 9879 | 9195 | 9129 | 9990 | 9044 | 9315 | 10081 | 8914 | 10186 | 8885 | 9931 | 9127 | 9997 | 8688 | 10044 | 9065 | 9898 | 9064 | 10018 | 9211 | 8938 | 9873 | 9083 | 8926 | 10005 | 10017 | 9880 | 9009 | 9991 | 8989 | 9758 | 9066 | 9593 | 8450 | 9772 | 9008 | 9134 | 9259 | 9010 | 7786 | 9097 | 8077 | 9285 | 9279 | 10555 | 9283 | 10515 | 9465 | 10574 | 9431 | 9599 | 9436 | 9998 | 10324 | 10266 | 10255 | 10332 | 10435 | 9401 | 10289 | 10242 | 10261 | 10268 | 10198 | 10196 | 9248 | 10347 | 9283 | 30.88 | 31.28 | 31.47 | 31.24 | 0 | 31.72 | 0 | 41.3 | 0 | 0 | 41.4 | 41.7 | 6.23 | 6.36 | 6.41 | 6.34 | 0 | 6.47 | 9.67 | 9.38 | 10.05 | 9.32 | 0 | 9.83 | 5.32 | 5.36 | 5.49 | 5.24 | 0 | 5.38 | 0.95 | 1.07 | 1.01 | 1.26 | 0 | 1.21 | 5.36 | 5.41 | 5.33 | 5.24 | 0 | 5.37 | 0.26 | 0.35 | 0.31 | 0.33 | 0 | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 709765 | 1280 | 696472 | 1337 | 61510.5 | 169.1 | 5.32 | 5.36 | 5.49 | 5.24 | 0 | 5.38 | 5.36 | 5.41 | 5.33 | 5.24 | 0 | 5.37 | 864000 | 3000 | 859000 | 2000 | 1515562 | 4500 | 1718000 | 1511062 | 12.2 | 5.358 | 1.1 | 5.342 | 0.326 | 20.53% | 6.103% | 31.318 | 41.4667 | 6.362 | 9.65 | 1523516 | 734130 | 852269.6995 | 86.14% | 44 | 24413
2024-08-11 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 335090.89 | 6:49 | 19:26 | 7236.9 | 7478.4 | 7490.1 | 7486.7 | 7526.9 | 7523.4 | 7543.4 | 7668.6 | 7361.6 | 2038.3 | 7429.8 | 7461.3 | 7468.6 | 7448.6 | 7554.2 | 7523 | 7465.7 | 7502.7 | 7486.5 | 7534.3 | 7519.3 | 7530.6 | 7458.6 | 7484.8 | 7385.7 | 6922.4 | 7367 | 7387 | 7536 | 7485.4 | 7430.7 | 7485 | 10030.1 | 9886.1 | 10087.1 | 10010.1 | 7539.5 | 7495.6 | 7452.1 | 7431.4 | 7748.2 | 7307.7 | 7729.9 | 7265.2 | 7574 | 7983.5 | 7279.5 | 7736.9 | 7481.3 | 7312.2 | 7531.2 | 7313.8 | 7642.8 | 7238.7 | 7606.8 | 7528.9 | 7154.2 | 7663.1 | 7219.7 | 7621.3 | 7565.3 | 7156 | 7427.9 | 7223.5 | 7363.9 | 7121 | 7331.5 | 7429.1 | 7579.4 | 7132.4 | 7471.9 | 7001.9 | 7426.8 | 7301.9 | 7131.4 | 7453 | 7016.6 | 7553.8 | 7093.9 | 7445.7 | 7124.6 | 7353.8 | 7177.1 | 7547.3 | 7159.5 | 7397.2 | 7115.3 | 6699 | 7586.5 | 7354.2 | 7154.7 | 7671.5 | 7533.3 | 7259.2 | 7219.9 | 7553.1 | 7177.9 | 7332.6 | 7578.7 | 7162.9 | 7662.9 | 7149.1 | 7599.2 | 7263.3 | 7604.6 | 7072.8 | 7637.2 | 7209.1 | 7576.5 | 7220.8 | 7569 | 7310.2 | 7193.4 | 7535.4 | 7227.2 | 7192.7 | 7576 | 7624.4 | 7474.7 | 7262.3 | 7565.6 | 7196.4 | 7455.8 | 7201.2 | 7357.3 | 6963 | 7492.8 | 7201.5 | 7329.9 | 7288.8 | 7209.9 | 6770.1 | 7209.5 | 6803.6 | 7293 | 7283.6 | 7684.8 | 7214.2 | 7729.2 | 7301.5 | 7731.6 | 7301.4 | 7370 | 7326.9 | 7643.3 | 7747.6 | 7693.3 | 7663.4 | 7637.5 | 7666.1 | 7307.2 | 7689.8 | 7836.5 | 7836.1 | 7942.4 | 7884.8 | 7837.5 | 7410.7 | 7772.2 | 7365.4 | 30.4505 | 30.9676 | 31.2111 | 32.4229 | 30.9538 | 31.3499 | 0 | 41.7 | 0 | 0 | 42.1 | 42.1 | 6.7467 | 6.9841 | 6.8408 | 6.911 | 6.6096 | 7.1192 | 10.2067 | 9.9233 | 11.7033 | 10.1083 | 10.0617 | 10.8067 | 5.6106 | 5.5715 | 5.5199 | 5.4514 | 5.732 | 5.5911 | 1.1118 | 1.1458 | 1.0373 | 1.4147 | 1.5413 | 1.256 | 5.6069 | 5.5804 | 5.3162 | 5.4789 | 5.6706 | 5.5589 | 0.28863 | 0.3977 | 0.33276 | 0.36594 | 0.43078 | 0.40183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 710302 | 1282 | 697004 | 1339 | 62698.738 | 173.467 | 5.6106 | 5.5715 | 5.5199 | 5.4514 | 5.732 | 5.5911 | 5.6069 | 5.5804 | 5.3162 | 5.4789 | 5.6706 | 5.5589 | 537000 | 2000 | 532000 | 2000 | 1188238 | 4367 | 1065000 | 1183871 | 12.6167 | 5.5794 | 1.2511 | 5.5353 | 0.3696 | 22.42% | 6.677% | 31.226 | 41.9667 | 6.8686 | 10.4683 | 1191653.8 | 199266 | 233971.93 | 85.17% | 46 | 12451
2024-08-12 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 335090.89 | 6:41 | 19:25 | 9833.1 | 10303.5 | 10212.4 | 10215 | 10254.3 | 10389.9 | 10467.6 | 10817.5 | 10372.5 | 0 | 10246.4 | 10431.7 | 10171 | 10228.7 | 10330.4 | 10254.2 | 10228.9 | 10412.2 | 10388.1 | 10349.9 | 10632.4 | 10572.8 | 10433.8 | 10506 | 10223.7 | 9050.7 | 10166.8 | 10207.6 | 10568.1 | 10623.8 | 10635.2 | 10560.6 | 10686.4 | 10571.5 | 10524.2 | 10470.6 | 10687.4 | 10692.9 | 10765.7 | 10756 | 11509.4 | 10407.5 | 11450.3 | 10234.5 | 11046.2 | 12220.9 | 10602.3 | 11685.3 | 10067.5 | 9679.8 | 10227.8 | 9785.2 | 10585.5 | 9553.9 | 10583.5 | 10445.8 | 9476.7 | 10873.8 | 9537.2 | 10732.2 | 10646.8 | 9555.1 | 10394.7 | 9858 | 10095.9 | 9483.4 | 10011.2 | 10368.8 | 10780.6 | 9657.4 | 10633.9 | 9413.9 | 10377.7 | 10292.9 | 9652.8 | 10786.6 | 9578.5 | 10841.9 | 9739.1 | 10791.8 | 9634.3 | 10347.5 | 9827.3 | 10729.9 | 9682.7 | 10321.5 | 9658.4 | 8578.2 | 10650 | 10127.1 | 9607.5 | 10998.9 | 10754.9 | 10094.7 | 10052.9 | 10887.6 | 9880 | 10132.1 | 10893.5 | 9706.5 | 11074 | 9749.8 | 10824.4 | 9957 | 10802.1 | 9412.4 | 10792 | 9721.2 | 10682.4 | 9751.4 | 10766 | 9936 | 9704.5 | 10494.5 | 9756 | 9567 | 10568.7 | 10592.1 | 10476.2 | 9745 | 10709.3 | 9702.9 | 10397.1 | 9785 | 10327 | 9195.4 | 10547.9 | 9790.7 | 9805.6 | 9788.2 | 9828.4 | 8461 | 9649.3 | 8523.6 | 9651.9 | 9667 | 10909 | 9712 | 11026.3 | 9938 | 11058.9 | 9856.3 | 9988.1 | 9850.7 | 10547.8 | 10792.9 | 10787.1 | 10728.5 | 10741.3 | 10815.5 | 9880.7 | 10778.9 | 10916.9 | 10905 | 10922.6 | 10842.4 | 10865.5 | 9922.6 | 10965 | 9957.1 | 30.9274 | 31.8609 | 32.3347 | 37.2941 | 31.745 | 32.1239 | 0 | 44.5 | 0 | 0 | 44.7 | 44.7 | 3.8329 | 4.1747 | 2.949 | 4.1593 | 4.0911 | 3.7061 | 6.7633 | 7.29 | 6.905 | 7.09 | 7.1 | 7.6333 | 5.8875 | 6.0141 | 6.2757 | 5.6784 | 5.9494 | 5.826 | 1.266 | 1.208 | 1.2358 | 1.5594 | 1.5903 | 1.2583 | 5.8863 | 6.0397 | 6.1246 | 5.8109 | 5.9169 | 5.7728 | 0.30178 | 0.41637 | 0.36177 | 0.38352 | 0.43683 | 0.41056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 711077 | 1282 | 697780 | 1339 | 64324.472 | 177.867 | 5.8875 | 6.0141 | 6.2757 | 5.6784 | 5.9494 | 5.826 | 5.8863 | 6.0397 | 6.1246 | 5.8109 | 5.9169 | 5.7728 | 775000 | 0 | 776000 | 0 | 1625734 | 4400 | 1551000 | 1621334 | 12.7333 | 5.9385 | 1.353 | 5.9252 | 0.38514 | 22.78% | 6.5% | 32.7143 | 44.6333 | 3.8188 | 7.1303 | 1634387.4 | 1624800 | 1985844.9384 | 81.82% | 33 | 2173
2024-08-13 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 335090.89 | 6:40 | 18:40 | 9855.8 | 10114.4 | 9939.1 | 9968.9 | 9976.5 | 9941 | 9975.5 | 10270.7 | 10167 | 10064.9 | 9714.3 | 9965.7 | 9665.3 | 9664.4 | 9863.9 | 9809.9 | 9721.5 | 9648.6 | 9565.1 | 9654.1 | 9519 | 9541.4 | 9385.8 | 9415.5 | 9194.8 | 8133.8 | 9279.3 | 9220.1 | 9502.2 | 9537.5 | 9402.5 | 9397 | 9498 | 9448.2 | 9444.9 | 9337.3 | 9555.4 | 9470.6 | 9512.7 | 9455 | 10695.4 | 9633.6 | 10675.1 | 9503.3 | 10283.9 | 11502.9 | 9756.6 | 10775.9 | 9622.8 | 9200.3 | 9714.8 | 9253.6 | 9953.9 | 8992.1 | 10044 | 9728.9 | 9096.4 | 10465.2 | 9047.1 | 10331.3 | 10255.9 | 9122.2 | 10241.7 | 9858.4 | 9723 | 9273.8 | 9756.7 | 10378.8 | 10534.7 | 9716.4 | 10552.4 | 9438.6 | 10251.7 | 10291.9 | 9688.9 | 10909.9 | 9732.3 | 10982.2 | 9869.7 | 11049.1 | 9774.8 | 10563.7 | 10085.2 | 10852.8 | 9788.8 | 10419.4 | 9464.4 | 8406.3 | 10131.3 | 9819.8 | 8970.9 | 10265 | 9887 | 9143.7 | 9030.1 | 9939.3 | 9074.8 | 9502.4 | 10219.5 | 9119.8 | 10169.6 | 9056.2 | 9927.8 | 9322.8 | 10030.2 | 8787.1 | 10178.2 | 9345 | 10021.1 | 9291.1 | 10303.8 | 9571.7 | 9307.4 | 10405.2 | 9451.3 | 9340 | 10396.3 | 10696.3 | 10301.7 | 9889.2 | 10698.3 | 9723.7 | 10162 | 9537.7 | 10111.3 | 9100.8 | 10546.8 | 9793.2 | 10209.9 | 10351.1 | 9870.1 | 8657.4 | 10322.2 | 9172.6 | 10521.7 | 10511.9 | 11808.1 | 10448.7 | 11854.3 | 10711.3 | 11854.5 | 10696.5 | 10837.6 | 10680 | 11536.7 | 11845.7 | 11570.4 | 11628.2 | 11647.9 | 11725.8 | 10744.9 | 11793.6 | 11749.5 | 11794.8 | 11852.5 | 11762 | 11775.3 | 10838.1 | 11820.6 | 10761.9 | 31.59 | 33.15 | 33.55 | 38.75 | 33.35 | 33.79 | 0 | 44.9 | 0 | 0 | 47.3 | 48.1 | 4.19 | 4.31 | 2.75 | 4.27 | 4.35 | 3.15 | 7.99 | 8.26 | 8.87 | 8.37 | 7.93 | 8.32 | 5.57 | 5.28 | 5.73 | 5.43 | 5.86 | 6.35 | 1.25 | 1.03 | 1.18 | 1.54 | 1.56 | 1.32 | 5.56 | 5.31 | 5.61 | 5.59 | 5.84 | 6.28 | 0.28 | 0.37 | 0.33 | 0.36 | 0.42 | 0.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 711860 | 1284 | 698600 | 1341 | 65923.272 | 182.533 | 5.57 | 5.28 | 5.73 | 5.43 | 5.86 | 6.35 | 5.56 | 5.31 | 5.61 | 5.59 | 5.84 | 6.28 | 783000 | 2000 | 820000 | 2000 | 1598800 | 4666 | 1599000 | 1594134 | 12 | 5.7033 | 1.3133 | 5.6983 | 0.365 | 23.03% | 6.405% | 34.03 | 46.7667 | 3.8367 | 8.29 | 1607983.6 | 1598060 | 1894102.1801 | 84.37% | 34 | 50599
2024-08-14 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 335090.89 | 6:59 | 19:09 | 4260.4 | 4484.6 | 4511.8 | 4471.1 | 4577.8 | 4601.8 | 4582.8 | 4762.4 | 4529.8 | 4402.3 | 4496 | 4555.4 | 4515.1 | 4502.3 | 4654.2 | 4607.5 | 4601.2 | 4574.6 | 4502.8 | 4544.2 | 4506.6 | 4496.8 | 4352.7 | 4421.5 | 4286.2 | 3802.5 | 4340.5 | 4291.5 | 4446.9 | 4422.1 | 4339.6 | 4448.7 | 4403.4 | 4399.3 | 4485.2 | 4448.7 | 4479.6 | 4397.6 | 4389.8 | 4341.1 | 4850.8 | 4378.2 | 4772.5 | 4283.1 | 4492.8 | 5063.9 | 4245 | 4834.6 | 4585.2 | 4264.2 | 4566.4 | 4296.6 | 4702.7 | 4277.3 | 4608.8 | 4585.5 | 4136.6 | 4722.5 | 4181.9 | 4666.8 | 4617.6 | 4183.6 | 4485.7 | 4262.8 | 4370.1 | 4134.3 | 4351.8 | 4495.4 | 4647.1 | 4185 | 4564.2 | 4038.3 | 4481.1 | 4376.8 | 4154.4 | 4592.3 | 4081.4 | 4653.1 | 4127.2 | 4566.6 | 4203.4 | 4477.1 | 4305 | 4637.9 | 4236.7 | 4496.7 | 4217 | 3768.2 | 4563.2 | 4378.6 | 4080.9 | 4645.8 | 4517.6 | 4204 | 4162.7 | 4554.8 | 4097.8 | 4213.5 | 4527 | 4032.5 | 4563.4 | 3997.7 | 4436 | 4111.8 | 4480.7 | 3917.6 | 4517.1 | 4077.7 | 4431.6 | 4035.5 | 4420.4 | 4059.6 | 4060 | 4410.3 | 4100.5 | 4001.7 | 4458.2 | 4392.3 | 4352.8 | 3908.5 | 4296.3 | 3831.5 | 4273 | 3946.8 | 4138.9 | 3563.1 | 4146.6 | 3778 | 3924.4 | 3974.5 | 3792.7 | 3318.3 | 3829.6 | 3423.4 | 3840.8 | 3851.1 | 4466.1 | 3911.6 | 4471.5 | 3961.4 | 4407.9 | 3912.2 | 3969.2 | 3876.9 | 4237.1 | 4366.1 | 4298.1 | 4358.7 | 4400.2 | 4438 | 4011.9 | 4374.4 | 4578.8 | 4563.8 | 4508.1 | 4427.1 | 4379.6 | 3942.3 | 4553.9 | 4010 | 27.45 | 30.03 | 30.06 | 31.26 | 29.96 | 30.03 | 0 | 35.2 | 0 | 0 | 34.9 | 34.9 | 3.28 | 3.17 | 1.29 | 3.27 | 3.28 | 2.05 | 5.93 | 5.93 | 5.67 | 6.01 | 5.9 | 6.31 | 2.45 | 2.41 | 2.43 | 2.54 | 2.37 | 2.24 | 0.31 | 0.31 | 0.32 | 0.39 | 0.35 | 0.28 | 2.42 | 2.39 | 2.33 | 2.42 | 2.32 | 2.17 | 0.07 | 0.09 | 0.08 | 0.08 | 0.08 | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 712215 | 1285 | 698935 | 1342 | 66610.539 | 187.2 | 2.45 | 2.41 | 2.43 | 2.54 | 2.37 | 2.24 | 2.42 | 2.39 | 2.33 | 2.42 | 2.32 | 2.17 | 355000 | 1000 | 335000 | 1000 | 687267 | 4667 | 688000 | 682600 | 12.1667 | 2.4067 | 0.32667 | 2.3417 | 0.08 | 13.57% | 3.416% | 29.7983 | 35 | 2.7233 | 5.9583 | 691530.3 | 685667 | 804157.3405 | 85.27% | 46 | 219743
2024-08-15 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 335090.89 | 7:06 | 19:18 | 6076.3 | 6420.6 | 6437.1 | 6395.4 | 6499.7 | 6506.4 | 6504.3 | 6763.6 | 6426.7 | 6327.6 | 6298.7 | 6409.3 | 6409.4 | 6353.9 | 6493.2 | 6489.3 | 6416 | 6391.9 | 6375 | 6413 | 6393.1 | 6348.3 | 6285 | 6309.5 | 6204.1 | 5476.3 | 6211.7 | 6190.4 | 6414.4 | 6398.3 | 6290.2 | 6320.3 | 6483.4 | 6422.4 | 6484 | 6428.8 | 6422.8 | 6373 | 5702 | 6185.8 | 6927.8 | 6254.9 | 6892.2 | 6172.1 | 6620.6 | 7398.4 | 6267.9 | 6985.4 | 6157.6 | 5867.9 | 6432.4 | 6051.2 | 6535.7 | 6022 | 6575.6 | 6525.8 | 5831.4 | 6747.2 | 5879.8 | 6687.3 | 6544.3 | 5893.7 | 6423.9 | 6034.6 | 6195.8 | 5801.7 | 6094.3 | 6359.5 | 6637.2 | 5896.1 | 6496.2 | 5610.4 | 6373.2 | 6148.2 | 5853 | 6447.8 | 5676.1 | 6644.3 | 5789.4 | 6483.4 | 5891.2 | 6332.7 | 6003.3 | 6630.5 | 5934.2 | 6350.1 | 5885.4 | 5118.3 | 6510.1 | 6180.6 | 5845.9 | 6804 | 6626.4 | 6140.2 | 6089.7 | 6698.6 | 6018.6 | 6195.3 | 6726.4 | 5926.2 | 6819.7 | 5919.9 | 6594.4 | 6066.3 | 6605.3 | 5626.3 | 6643.7 | 6003.7 | 6541.9 | 5974 | 6583.3 | 6064.4 | 5953.5 | 6529.3 | 6030.7 | 5914.3 | 6634.7 | 6537.1 | 6440.5 | 6007.2 | 6624.8 | 5936.1 | 6445.8 | 5978.3 | 6191.7 | 5546.1 | 6448.8 | 5960.5 | 6117 | 6149.2 | 6015 | 5240.6 | 6051.4 | 5372.2 | 6192.5 | 6184.7 | 7039.5 | 6177.9 | 7137.9 | 6329.3 | 7093.7 | 6308 | 6389.9 | 6302.4 | 6856.7 | 7117.4 | 6620.7 | 6944.9 | 6954 | 6992.4 | 6369.9 | 7040.2 | 7067.7 | 7088.2 | 7119 | 7063.4 | 7055.6 | 6418.1 | 7055.7 | 6372.2 | 26.6902 | 30.2082 | 30.1619 | 31.6014 | 30.11 | 30.5239 | 0 | 36.9 | 0 | 0 | 37.1319 | 37.4 | 4.2437 | 4.2663 | 2.4341 | 4.2657 | 4.2285 | 3.8347 | 6.6517 | 6.3383 | 5.865 | 6.315 | 6.4367 | 6.86 | 3.3286 | 3.4095 | 3.5639 | 3.3455 | 3.3848 | 3.4945 | 0.47965 | 0.50487 | 0.52473 | 0.57955 | 0.58267 | 0.52359 | 3.3672 | 3.4464 | 3.5415 | 3.3088 | 3.3991 | 3.491 | 0.11087 | 0.14162 | 0.13161 | 0.11831 | 0.1211 | 0.13379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 712720 | 1287 | 699444 | 1344 | 67621.139 | 191.8 | 3.3286 | 3.4095 | 3.5639 | 3.3455 | 3.3848 | 3.4945 | 3.3672 | 3.4464 | 3.5415 | 3.3088 | 3.3991 | 3.491 | 505000 | 2000 | 509000 | 2000 | 1010600 | 4600 | 1010000 | 1006000 | 12.2 | 3.4211 | 0.53251 | 3.4257 | 0.12622 | 15.57% | 3.684% | 29.8826 | 37.144 | 3.8788 | 6.4111 | 1014754.8 | 368934 | 416074.74 | 88.67% | 44 | 29324
2024-08-16 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 335090.89 | 7:15 | 18:50 | 3166.3 | 3348.4 | 3406 | 3382 | 3447 | 3439.2 | 3425.1 | 3562.5 | 3344.8 | 3291.9 | 3300.6 | 3344.7 | 3352.7 | 3332 | 3432.2 | 3419 | 3385.7 | 3401.2 | 3382.2 | 3384.1 | 3410.3 | 3391.9 | 3335.6 | 3364.3 | 3266.6 | 2849.4 | 3279.7 | 3271.6 | 3406.8 | 3395.4 | 3313.8 | 3048.5 | 3345 | 3338.3 | 3366.1 | 3340.2 | 3385.9 | 3360.4 | 1049.6 | 3201.4 | 3724.2 | 3337.8 | 3679.1 | 3286.4 | 3496.7 | 3961.7 | 3258.9 | 3731.8 | 2293.9 | 3077.9 | 3387.8 | 3166.2 | 3531.6 | 3150.2 | 3460.8 | 3098.8 | 3031.8 | 3525 | 3068.6 | 3500 | 3446.5 | 3062.8 | 3315.1 | 3121.1 | 3225.7 | 3014.2 | 3203 | 3337.5 | 3468.2 | 3058.5 | 3392.2 | 2937.3 | 3319.9 | 3212.8 | 3031.4 | 3398.9 | 2955.2 | 3477.9 | 3018.9 | 3391.9 | 3034.6 | 3288.3 | 3082.7 | 3431.5 | 3053.1 | 3279.2 | 3054.8 | 2630.9 | 3394.5 | 3215 | 3009 | 3522.2 | 3420.1 | 3156 | 3132.1 | 3453.6 | 3075.5 | 3178.4 | 3472.2 | 3040.9 | 3539.3 | 3039.6 | 3426.1 | 3131.4 | 3464.5 | 2963.2 | 3479.4 | 3105.8 | 3427.1 | 3020.2 | 3461.9 | 3152.3 | 3060.5 | 3379.2 | 3110.6 | 3038.9 | 3458.1 | 3467.8 | 2522.95 | 2480 | 3453.7 | 3069.3 | 3349.9 | 3096.8 | 3146.3 | 2861.1 | 3354.5 | 3079 | 3108 | 3109 | 3096 | 2660 | 3026.9 | 2661 | 3000.7 | 3010 | 3475 | 2989 | 3507.6 | 3068 | 3453.6 | 3043 | 3083.6 | 3053.8 | 3362 | 3512.7 | 3169 | 3414 | 3194 | 3437 | 3110.8 | 3465.9 | 3507.8 | 3514.9 | 3549.5 | 3507.7 | 3494.9 | 3132.6 | 3494.1 | 3113.1 | 25.7111 | 27.0616 | 26.9263 | 27.815 | 0 | 0 | 0 | 29.3765 | 0 | 0 | 0 | 0 | 3.9956 | 4.1674 | 3.5853 | 4.2403 | 0 | 0 | 7.435 | 6.7783 | 7.2833 | 6.4617 | 0 | 0 | 1.7164 | 1.7446 | 1.7874 | 1.8543 | 0 | 0 | 0.17354 | 0.16578 | 0.18626 | 0.20221 | 0 | 0 | 1.6717 | 1.6979 | 1.7143 | 1.6325 | 0 | 0 | 0.025095 | 0.031109 | 0.026653 | 0.027364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 712982 | 1290 | 699701 | 1347 | 68138.539 | 196.667 | 1.7164 | 1.7446 | 1.7874 | 1.8543 | 0 | 0 | 1.6717 | 1.6979 | 1.7143 | 1.6325 | 0 | 0 | 262000 | 3000 | 257000 | 3000 | 517400 | 4867 | 513000 | 512533 | 11.5833 | 1.7757 | 0.18194 | 1.6791 | 0.027555 | 10.25% | 1.641% | 26.8785 | 29.3765 | 3.9971 | 6.9896 | 518815.85 | 516934 | 597120.4716 | 86.57% | 25 | 30871
2024-08-17 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 335090.89 | 6:52 | 19:07 | 5111.9 | 5396.8 | 5388.9 | 5341.8 | 5466.4 | 5497.5 | 5484.8 | 5731.6 | 5416.8 | 5368.7 | 5332.4 | 5423.6 | 5455.8 | 5392.4 | 5586.6 | 5550 | 5518.5 | 5550.3 | 5549.8 | 5562.6 | 5574.4 | 5564.3 | 5425.4 | 5496.7 | 5399.2 | 4731.5 | 5398.5 | 5392.9 | 5578.1 | 5518.1 | 5418 | 5463.4 | 5525.7 | 5523.8 | 5565.5 | 5519.7 | 5580.5 | 5408.2 | 5190.7 | 5492.6 | 5812.2 | 5218.7 | 5716 | 4665.4 | 5497.8 | 6213.6 | 5173.8 | 5860.5 | 5475.6 | 5118.5 | 5519.2 | 5182 | 5759.6 | 5157.7 | 5652.4 | 5692.9 | 4964.3 | 5765.2 | 4984.4 | 5700.3 | 5616.1 | 4979.7 | 5471.2 | 5182 | 5327.4 | 5029.7 | 5321.7 | 5593.5 | 5753.7 | 5163 | 5681.8 | 4977.6 | 5507.8 | 5405.8 | 5072.8 | 5705 | 4987 | 5758.3 | 5065 | 5651.6 | 5165 | 5558.5 | 5277.3 | 5797.6 | 5198.8 | 5561.9 | 5125.6 | 4450.7 | 5635.7 | 5366 | 4997.7 | 5815.3 | 5673.7 | 5261.7 | 5201.5 | 5714 | 5106 | 5252 | 5729 | 5030 | 5804 | 5036 | 5605 | 5171.1 | 5661 | 4876.5 | 5692 | 5085 | 5616 | 5098 | 5675 | 5167 | 5009 | 5550 | 1757.6 | 4976 | 5660 | 5679 | 5511 | 5096 | 5619 | 5006 | 5474 | 5059 | 1766 | 4647 | 5454 | 5018 | 5121 | 5137 | 5056 | 4389 | 5026 | 4451 | 5138 | 5155 | 5316 | 5243 | 5920 | 5251 | 5927 | 5281 | 5926 | 5188 | 5661 | 5867 | 1809 | 5255 | 5812 | 5864 | 5304 | 5847 | 5884 | 5255 | 5779 | 5240 | 5844 | 5785 | 5838 | 5838 | 25.053 | 27.0855 | 27.082 | 28.6795 | 27.0384 | 27.1869 | 0 | 32.0487 | 0 | 0 | 32.1265 | 32.3245 | 5.3331 | 5.7425 | 5.0445 | 5.8284 | 5.5376 | 5.3034 | 10.4567 | 8.8467 | 9.39 | 9.715 | 8.95 | 9.3717 | 2.8472 | 2.9628 | 2.9039 | 2.9997 | 2.9318 | 2.9739 | 0.35315 | 0.41616 | 0.37172 | 0.44088 | 0.45097 | 0.42492 | 2.8275 | 2.9429 | 2.8356 | 2.8363 | 2.8792 | 2.9256 | 0.094 | 0.12337 | 0.10536 | 0.11032 | 0.10274 | 0.11732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 713445 | 1291 | 700152 | 1349 | 68989.01 | 201.267 | 2.8472 | 2.9628 | 2.9039 | 2.9997 | 2.9318 | 2.9739 | 2.8275 | 2.9429 | 2.8356 | 2.8363 | 2.8792 | 2.9256 | 463000 | 1000 | 451000 | 2000 | 850471 | 4600 | 911000 | 845871 | 12.25 | 2.9365 | 0.40963 | 2.8745 | 0.10885 | 13.95% | 3.787% | 27.0209 | 32.1666 | 5.4649 | 9.455 | 853368.4 | 849400 | 1005047.821 | 84.51% | 25 | 56424
2024-08-18 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 335090.89 | 7:07 | 19:09 | 9112.6 | 9499.8 | 9465.6 | 9440.9 | 9523.1 | 9583.3 | 9564.1 | 9945.1 | 9525.7 | 9318.8 | 9303.5 | 9469.8 | 9555.8 | 9407.3 | 9805.8 | 9756.3 | 9720.5 | 9808.1 | 9830.2 | 9824.7 | 9851.1 | 9846 | 9601.2 | 9706.9 | 9571.3 | 8472.7 | 9524.2 | 9572 | 9826.1 | 9745 | 9550.5 | 9582.7 | 9709.1 | 9684.1 | 9832.6 | 9732 | 9830.4 | 9698.5 | 9343.4 | 9711.5 | 10403.1 | 9450.4 | 10304.5 | 9234.7 | 9900.9 | 10986.9 | 9441.6 | 10506.1 | 9658.5 | 8965.7 | 9646.5 | 9134.4 | 9995.1 | 9096.2 | 9870.9 | 9929.4 | 8662.3 | 9963.6 | 8691.1 | 9817.5 | 9684.5 | 8714.8 | 9532 | 9076.8 | 9255.1 | 8739 | 9219.7 | 9592.2 | 9880.9 | 8898.8 | 9716 | 8563.8 | 9461.4 | 9303.4 | 8787.2 | 9811.7 | 8741.6 | 9933.9 | 8910.3 | 9961.4 | 8880.6 | 9495.7 | 9036.6 | 9877.8 | 8902.9 | 9453.9 | 8891.9 | 7670.4 | 9882.7 | 9319.9 | 8930.5 | 10241.2 | 9944.6 | 9241.5 | 9161.6 | 9989 | 9112 | 9368 | 10150 | 9006 | 10351 | 9145 | 10072 | 9399 | 10119.9 | 8856.7 | 10167.8 | 9201.4 | 10000.4 | 9174.9 | 10039.8 | 9312.6 | 9074.5 | 10003.1 | 9164.9 | 9120.6 | 10146.6 | 10192.2 | 9841.4 | 9196 | 10040.4 | 9081 | 9833.7 | 9175.6 | 9516.6 | 8470.6 | 9816.6 | 9090.9 | 9362 | 9445 | 9142 | 7995 | 9243 | 8224 | 9071 | 9021 | 10161.7 | 8971.4 | 10281.5 | 9160 | 10244.3 | 9152.6 | 9276 | 9130.5 | 10061 | 10391 | 10157 | 10246 | 10166 | 10198 | 9325 | 10277 | 10519 | 10537 | 10506 | 10421 | 10408 | 9487.3 | 10483 | 9503 | 28.987 | 30.1238 | 30.455 | 33.151 | 29.9917 | 30.2404 | 0 | 41.4 | 0 | 0 | 41.3 | 41.5 | 4.0972 | 4.9034 | 3.0486 | 4.9014 | 4.7696 | 4.8285 | 8.155 | 7.9933 | 7.7517 | 8.265 | 7.805 | 8.6617 | 5.212 | 5.4639 | 5.4917 | 5.2002 | 5.6006 | 5.4747 | 0.72806 | 0.90267 | 0.87736 | 0.91623 | 1.0521 | 1.0051 | 5.2852 | 5.5369 | 5.5045 | 5.2652 | 5.6184 | 5.5042 | 0.21082 | 0.28145 | 0.24826 | 0.24009 | 0.23768 | 0.28025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 714177 | 1293 | 700884 | 1350 | 70508.339 | 206 | 5.212 | 5.4639 | 5.4917 | 5.2002 | 5.6006 | 5.4747 | 5.2852 | 5.5369 | 5.5045 | 5.2652 | 5.6184 | 5.5042 | 732000 | 2000 | 732000 | 1000 | 1519329 | 4733 | 1461000 | 1514596 | 12.0333 | 5.4072 | 0.91358 | 5.4524 | 0.24976 | 16.9% | 4.581% | 30.4915 | 41.4 | 4.4248 | 8.1053 | 1528024.5 | 1518267 | 1846491.5897 | 82.22% | 29 | 45419
2024-08-19 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 335090.89 | 6:47 | 19:10 | 10465.8 | 11057.2 | 11191.8 | 11096.3 | 11341.7 | 11363.9 | 11331.1 | 11702.3 | 11044.7 | 10852.9 | 11009.4 | 11061.2 | 11331.1 | 11128.7 | 11216.2 | 11295.8 | 11092.8 | 11162.6 | 11272.1 | 11371.6 | 11286.2 | 11270.1 | 11198.2 | 11191.6 | 11066.5 | 9902.5 | 11088.7 | 11059 | 11308.9 | 11306.5 | 11126.5 | 11221.1 | 11264.1 | 11121.9 | 11314.2 | 11246.2 | 11390.8 | 11213.3 | 10846.6 | 11129.4 | 11818.2 | 10875.1 | 11702.6 | 10713.7 | 11278.5 | 12065.3 | 10668 | 11740.2 | 11285.9 | 10575.4 | 11335.4 | 10720.1 | 11639.4 | 10738.9 | 11375 | 11447.7 | 10147 | 11469.3 | 10278.5 | 11346.7 | 11217.9 | 10215.2 | 11055.6 | 10595.2 | 10762.7 | 10131.8 | 10726.5 | 11024 | 11407.2 | 10350.1 | 11196.5 | 9998.7 | 11065.6 | 10768.7 | 10325.1 | 11132.7 | 10106.1 | 11414 | 10275.8 | 11315.3 | 10391.5 | 11062.5 | 10534.4 | 11423 | 10400.2 | 10973.8 | 10297.1 | 8949.6 | 11212.9 | 10699.3 | 10310.5 | 11687.7 | 11435.7 | 10773.2 | 10746.4 | 11522.3 | 10501.9 | 10758.2 | 11524.2 | 10247.9 | 11751.5 | 10399.1 | 11502.4 | 10705.9 | 11466.2 | 10161.2 | 11486.1 | 10621.7 | 11330 | 10442.8 | 11425.8 | 10662 | 10308.5 | 11219.8 | 10509.7 | 10226.1 | 11394 | 11391.2 | 11330.1 | 10486.7 | 11467.2 | 10464.5 | 11293.8 | 10559.9 | 11012.7 | 9782.3 | 11276.2 | 10501.1 | 10549.7 | 10569 | 10515.9 | 9070.5 | 10415.4 | 9171.2 | 10079.6 | 10122.7 | 11745 | 10506 | 11935.5 | 10822 | 11644.5 | 10649.5 | 10667.4 | 10463.4 | 12172.7 | 12435.7 | 11859.9 | 12038.5 | 11799.5 | 11762.6 | 11198.7 | 12192.8 | 12486.8 | 12570.2 | 12685.1 | 12614.6 | 12585.8 | 11738.5 | 12414.1 | 11652.5 | 30.1606 | 31.2846 | 31.5077 | 34.4423 | 31.2623 | 31.599 | 0 | 44.9 | 0 | 0 | 45.4465 | 46.1 | 4.0462 | 4.1505 | 2.4248 | 3.8585 | 4.1043 | 3.6849 | 7.08 | 6.6967 | 7.1083 | 7.085 | 7.615 | 7.65 | 6.3702 | 6.4892 | 6.4169 | 6.1707 | 6.3388 | 6.7419 | 1.0261 | 1.1405 | 1.1522 | 1.2426 | 1.3848 | 1.3308 | 6.4874 | 6.6123 | 6.4323 | 6.3021 | 6.3961 | 6.6849 | 0.26929 | 0.35651 | 0.31479 | 0.31078 | 0.32233 | 0.38713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 715059 | 1293 | 701765 | 1350 | 72265.01 | 208.867 | 6.3702 | 6.4892 | 6.4169 | 6.1707 | 6.3388 | 6.7419 | 6.4874 | 6.6123 | 6.4323 | 6.3021 | 6.3961 | 6.6849 | 882000 | 0 | 881000 | 0 | 1756671 | 2867 | 1763000 | 1753804 | 12.3833 | 6.4213 | 1.2128 | 6.4859 | 0.3268 | 18.89% | 5.039% | 31.7094 | 45.4822 | 3.7116 | 7.2058 | 1768013.2 | 1755260 | 2162696.4665 | 81.16% | 23 | 15025
2024-08-20 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 335090.89 | 6:45 | 19:11 | 11360.3 | 11923 | 11913.1 | 11785.4 | 12066.3 | 12155.1 | 12090 | 12599 | 12014.2 | 11828.5 | 12010.7 | 12068.1 | 12273.5 | 12122 | 12319 | 12322.3 | 12172.2 | 12140.9 | 12259.7 | 12358.7 | 12203.1 | 12215.3 | 11994.5 | 12083.7 | 12035.1 | 10797.8 | 12052.9 | 11997.7 | 12231 | 12107.1 | 11988.1 | 12256.6 | 12388.7 | 12393.6 | 12410.4 | 12347.9 | 12417.8 | 12213 | 11837.8 | 12261.5 | 12340.2 | 11417.3 | 12276.8 | 11303.7 | 11892.8 | 12954 | 11292.2 | 12374.2 | 12301.9 | 11628 | 12378.4 | 11795 | 12714.9 | 11671.3 | 12554.1 | 12588.6 | 11342.9 | 12763.8 | 11318.5 | 12633.1 | 12427 | 11218.3 | 12179.5 | 11612.4 | 12002.7 | 11234.5 | 11856.5 | 12203.8 | 12555.1 | 11340.2 | 12309.4 | 10911.3 | 12143.8 | 11805.5 | 11278.3 | 12261.4 | 10994.2 | 12493.3 | 11178.7 | 12294.9 | 11286.8 | 12034.5 | 11477.5 | 12531.2 | 11445 | 12139 | 11461.2 | 10134.2 | 12618.7 | 11919.3 | 11533 | 12996 | 12672.5 | 11940.9 | 11861.2 | 12778.9 | 11682.4 | 11966.4 | 12778 | 11415 | 12852.3 | 11534.2 | 12610 | 11810 | 12656.2 | 11157.4 | 12723.7 | 11629.8 | 12594 | 11688 | 12702 | 11887 | 11478.3 | 12470.5 | 11714.4 | 11480 | 12631.3 | 12682.2 | 12542.6 | 11684.9 | 12645.9 | 11529.6 | 12347 | 11599.4 | 12277 | 10793.6 | 12418.4 | 11585.6 | 11739.2 | 11770.4 | 11620.5 | 10109.5 | 11546.6 | 10257.8 | 11514.8 | 11479 | 12766 | 11412 | 12642.8 | 10531.9 | 12836.4 | 11648.3 | 11817.9 | 11658.5 | 12360.8 | 12625.6 | 12533.4 | 12641.9 | 12666.7 | 12698.6 | 11727.2 | 12657.3 | 12543 | 12538.7 | 12539.6 | 12423.4 | 12455.3 | 11532.8 | 12712.8 | 11565 | 30.5365 | 31.8883 | 32.1228 | 34.9844 | 31.7644 | 32.1932 | 0 | 45.3 | 0 | 0 | 45.2 | 45.3 | 4.9996 | 5.2564 | 4.138 | 5.2247 | 5.288 | 5.3737 | 8.1783 | 8.545 | 8.1817 | 7.7167 | 7.815 | 8.9383 | 6.8644 | 6.98 | 6.6587 | 6.9385 | 7.0549 | 6.9026 | 1.2243 | 1.3687 | 1.22 | 1.5371 | 1.7707 | 1.4059 | 6.9991 | 7.1152 | 6.6907 | 6.997 | 7.1251 | 6.8242 | 0.29489 | 0.38982 | 0.33306 | 0.35581 | 0.39137 | 0.41015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 716017 | 1293 | 702721 | 1350 | 74173.539 | 210.667 | 6.8644 | 6.98 | 6.6587 | 6.9385 | 7.0549 | 6.9026 | 6.9991 | 7.1152 | 6.6907 | 6.997 | 7.1251 | 6.8242 | 958000 | 0 | 956000 | 0 | 1908529 | 1800 | 1914000 | 1906729 | 12.4333 | 6.8998 | 1.4211 | 6.9586 | 0.36252 | 20.6% | 5.21% | 32.2483 | 45.2667 | 5.0467 | 8.2292 | 1921828.8 | 1908330 | 2322258.8987 | 82.18% | 22 | 3508
2024-08-21 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 335090.89 | 6:44 | 19:17 | 11608 | 12226 | 12110 | 12077 | 12222 | 12303 | 12373 | 12767 | 12238 | 12041 | 12143 | 12275 | 12197 | 12193 | 12306 | 12287 | 12205 | 12278 | 12335 | 12355 | 12354 | 12385 | 12116 | 12233 | 12183 | 10773 | 12107 | 12171 | 12457 | 12374 | 12259 | 12426 | 12477 | 12465 | 12535 | 12432 | 12488 | 12352 | 11962 | 12396 | 13132 | 12130 | 13087 | 11961 | 12578 | 13633 | 11748 | 13077 | 12434 | 11758 | 12392 | 11819 | 12757 | 11574 | 12676 | 12631 | 11524 | 13042 | 11504 | 12926 | 12720 | 11431 | 12527 | 11913 | 12331 | 11587 | 12176 | 12634 | 12912 | 11748 | 12770 | 11356 | 12462 | 12309 | 11617 | 12843 | 11443 | 12944 | 11534 | 12703 | 11809 | 12569 | 12038 | 13016 | 11898 | 12583 | 11841 | 10447 | 12772 | 12195 | 11579 | 13078 | 12747 | 11961 | 11862 | 12910 | 11875 | 12239 | 13099 | 11653 | 13119 | 11721 | 12875 | 12034 | 12889 | 11343 | 12918 | 11810 | 12780 | 11773 | 12881 | 11940 | 11785 | 12820 | 11982 | 11753 | 12961 | 13086 | 12812 | 11955 | 12903 | 11689 | 12567 | 11752 | 12417 | 10838 | 12570 | 11653 | 12077 | 12097 | 11700 | 10289 | 11855 | 10474 | 11973 | 11932 | 13235 | 11860 | 13294 | 12133 | 13300 | 12112 | 12303 | 12119 | 12947 | 13225 | 13180 | 13132 | 13122 | 13129 | 12157 | 13159 | 13382 | 13384 | 13426 | 13284 | 13231 | 12254 | 13281 | 12195 | 30.84 | 32.41 | 32.78 | 36.8 | 32.32 | 32.71 | 0 | 46.5 | 0 | 0 | 47.4 | 47.5 | 4.16 | 4.41 | 2.39 | 4.32 | 4.37 | 4.4 | 8.16 | 7.6 | 7.81 | 7.98 | 7.56 | 8.14 | 6.89 | 6.97 | 7.03 | 6.96 | 7.2 | 7.11 | 1.33 | 1.41 | 1.28 | 1.69 | 1.89 | 1.47 | 7.05 | 7.13 | 7.09 | 7.14 | 7.29 | 7.1 | 0.3 | 0.39 | 0.35 | 0.37 | 0.42 | 0.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 716995 | 1294 | 703707 | 1352 | 76130.9 | 214.5 | 6.89 | 6.97 | 7.03 | 6.96 | 7.2 | 7.11 | 7.05 | 7.13 | 7.09 | 7.14 | 7.29 | 7.1 | 978000 | 1000 | 986000 | 2000 | 1957361 | 3833 | 1961000 | 1953528 | 12.55 | 7.0267 | 1.5117 | 7.1333 | 0.37667 | 21.51% | 5.28% | 32.9767 | 47.1333 | 4.0083 | 7.875 | 1970865 | 1956334 | 2356663.6022 | 83.01% | 18 | 8550
2024-08-22 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 335090.89 | 6:43 | 19:06 | 11154.7 | 11877 | 11732.6 | 11708.4 | 11833.9 | 11896.5 | 11984.4 | 12358.1 | 11903.9 | 11480.1 | 11856 | 11976.8 | 11968.6 | 11948.7 | 11876.8 | 11917.7 | 11729.2 | 11778.9 | 11888.1 | 12025.8 | 11896.7 | 11896.3 | 11714.1 | 11795.3 | 11710.6 | 10421 | 11765.1 | 11683.6 | 11952.6 | 11922.3 | 11826.3 | 11975.6 | 12161.3 | 12084.9 | 12076.8 | 12029.7 | 12188.7 | 12008 | 11634.7 | 12138.5 | 12847.1 | 11704.7 | 12715.2 | 11469.9 | 12358.6 | 13483.8 | 11910.2 | 13023.9 | 12273.9 | 11585.2 | 12280.1 | 11751.7 | 12493.8 | 11375.6 | 12512.3 | 12361.5 | 11245.7 | 12694.1 | 11196.9 | 12530.8 | 12199 | 11062.2 | 11821.5 | 11133.2 | 11873.7 | 11037 | 11660.8 | 11991.1 | 12309.8 | 11167 | 11992.9 | 10755.3 | 11778.3 | 11512.2 | 10834 | 12004.2 | 10701.3 | 12069.1 | 10884.1 | 11972.6 | 11303 | 12023.9 | 11604.9 | 12401.4 | 11376.2 | 12023.6 | 11296.4 | 9892.9 | 12358 | 11779.8 | 11279.1 | 12746.1 | 12427.9 | 11661.1 | 11539.9 | 12615.7 | 11640.2 | 12017.2 | 12866.6 | 11403.5 | 12959.4 | 11464.6 | 12718 | 11764.9 | 12832.3 | 11138.1 | 12879.4 | 11731.8 | 12808 | 11783.8 | 12856.5 | 11916.3 | 11534.6 | 12527.3 | 11643.1 | 11392.3 | 12672.4 | 12734.9 | 12595.8 | 11631.3 | 12677.8 | 11505.2 | 12528.3 | 11729.1 | 12376.6 | 10794 | 12493.8 | 11547.5 | 11841.8 | 11986.2 | 11506.5 | 10032.6 | 11763.2 | 10449.1 | 11960.2 | 11940.2 | 13280.6 | 11869.1 | 13389.4 | 12118 | 13271 | 12036.6 | 12282.7 | 12105.5 | 12960.4 | 13240.8 | 13120.8 | 13086.2 | 13155.9 | 13224 | 12290.9 | 13206.9 | 13256.3 | 13288 | 13225.2 | 13105.1 | 13183.4 | 12200.4 | 13230.5 | 12202.7 | 32.2307 | 33.4534 | 38.3588 | 34.0078 | 33.486 | 33.9302 | 0 | 47.8 | 0 | 0 | 49.1 | 49.5 | 3.3818 | 3.55 | 2.6195 | 1.5904 | 3.6319 | 3.7036 | 7.175 | 7.545 | 6.8983 | 6.5967 | 6.85 | 6.86 | 6.7895 | 6.7837 | 6.7828 | 6.9682 | 7.0728 | 7.1591 | 1.3898 | 1.3626 | 1.6799 | 1.285 | 1.8577 | 1.4698 | 6.9322 | 6.9319 | 6.9653 | 7.0305 | 7.1512 | 7.1688 | 0.29436 | 0.37468 | 0.34891 | 0.33704 | 0.40287 | 0.41837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 717940 | 1297 | 704767 | 1355 | 78041.739 | 218.8 | 6.7895 | 6.7837 | 6.7828 | 6.9682 | 7.0728 | 7.1591 | 6.9322 | 6.9319 | 6.9653 | 7.0305 | 7.1512 | 7.1688 | 945000 | 3000 | 1060000 | 3000 | 1910839 | 4300 | 1999000 | 1906539 | 12.3833 | 6.926 | 1.5075 | 7.03 | 0.3627 | 21.77% | 5.159% | 34.2445 | 48.8 | 3.0796 | 6.9875 | 1923657.3 | 1909800 | 2309568.5412 | 82.69% | 31 | 195
2024-08-23 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 335090.89 | 6:44 | 19:05 | 9483.1 | 10044.4 | 9926 | 9905.8 | 10037.4 | 10103.8 | 10141.4 | 10386 | 9961 | 9752.5 | 9912.7 | 9970.2 | 10061.4 | 9972.7 | 10107.1 | 10132.3 | 9937.2 | 9983.4 | 10002.2 | 10064.4 | 9977.3 | 10024.8 | 9808.2 | 9871.5 | 9800 | 8717.4 | 9824.7 | 9791.4 | 9980.3 | 9920.9 | 9829.4 | 9944.2 | 10028.4 | 10029 | 10155.8 | 10102.6 | 10036.3 | 9888.1 | 9551.2 | 9856 | 10437.1 | 9732.3 | 10297.2 | 9562.7 | 10043.7 | 10785.7 | 9569.6 | 10438.4 | 10416.5 | 9873.6 | 10504.9 | 9955.1 | 10793.5 | 9933.9 | 10549.8 | 10589 | 9545.6 | 10673.3 | 9608.4 | 10626 | 10495.8 | 9549.2 | 10268.5 | 9828.3 | 9901 | 9325.5 | 9830.3 | 10087.3 | 10268 | 9455.2 | 10181.9 | 9131.3 | 9921.2 | 9837.1 | 9277 | 10190.4 | 9182.9 | 10199.6 | 9260 | 10115.9 | 11661.3 | 12337.7 | 11914 | 12732.8 | 11703.3 | 12324.8 | 11608.2 | 10202.9 | 12464.9 | 11902.8 | 11431.7 | 12825.2 | 12572.3 | 11933 | 11876 | 12654.1 | 11520.7 | 11882 | 12584.4 | 11288.7 | 12763.1 | 11361.7 | 12587.8 | 11684.9 | 12718.1 | 11126.1 | 12776.7 | 11689.1 | 12710.4 | 11769 | 12874.7 | 11958.6 | 11391.7 | 12371.9 | 11632.9 | 11412.7 | 12573.8 | 12734.4 | 12488.6 | 11780.5 | 12702.6 | 11617.6 | 12411.5 | 11732.4 | 12292.1 | 10795.4 | 12495.5 | 11653.7 | 11911 | 11986.5 | 11727.9 | 10160.1 | 11860 | 10529.9 | 11831.9 | 11818.5 | 13332.4 | 11998.8 | 13340.5 | 12224.3 | 13227.4 | 12111.8 | 12263.5 | 12039.9 | 12907.5 | 13200.9 | 13173.7 | 13106.5 | 13135 | 13247.4 | 12311 | 13182.1 | 13274.2 | 13319.1 | 13344.8 | 13209.1 | 13174.6 | 12231.9 | 13292.1 | 12240.6 | 33.1749 | 33.603 | 34.0853 | 36.7581 | 33.8753 | 34.5018 | 0 | 49.3 | 0 | 0 | 47.7 | 46.8 | 4.1332 | 3.9856 | 2.3868 | 4.5265 | 4.6867 | 5.2929 | 10.86 | 8.552 | 9.157 | 9.897 | 9.051 | 8.577 | 6.9341 | 6.9887 | 6.9902 | 6.8225 | 6.9818 | 7.1416 | 1.5273 | 1.4001 | 1.3081 | 1.8368 | 1.8004 | 1.4406 | 7.0575 | 7.2087 | 7.1121 | 7.0328 | 7.119 | 7.1897 | 0.3307 | 0.39513 | 0.34786 | 0.39377 | 0.415 | 0.46256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 718735 | 1298 | 705653 | 1355 | 79805.073 | 223.333 | 6.9341 | 6.9887 | 6.9902 | 6.8225 | 6.9818 | 7.1416 | 7.0575 | 7.2087 | 7.1121 | 7.0328 | 7.119 | 7.1897 | 795000 | 1000 | 886000 | 0 | 1763334 | 4533 | 1680000 | 1758801 | 12.35 | 6.9765 | 1.5522 | 7.12 | 0.39084 | 22.25% | 5.489% | 34.3331 | 47.9333 | 4.1686 | 9.349 | 1775508.4 | 1762734 | 2340121.8532 | 75.33% | 31 | 76590
2024-08-24 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 335090.89 | 6:47 | 19:02 | 6257.4 | 6702.1 | 6712.2 | 6688.3 | 6792 | 6789 | 6800.5 | 6990.9 | 6578.2 | 6370.2 | 6485.5 | 6540.4 | 6599.2 | 6511.9 | 6667.4 | 6695.5 | 6532.5 | 6503.4 | 6539.1 | 6629.2 | 6474.2 | 6516 | 6345.9 | 6401.3 | 6424.2 | 5646.4 | 6419 | 6419.9 | 6581.4 | 6517.1 | 6436.3 | 6483.9 | 6599.6 | 6592.7 | 6623.9 | 6586.3 | 6694.2 | 6607.7 | 6352 | 6576.4 | 7076.2 | 6333.4 | 6987.9 | 6218.2 | 6700.1 | 7493 | 6331 | 7134.5 | 6526.1 | 6078 | 6571.3 | 6188.4 | 6816.7 | 6177.1 | 6708.1 | 6666.5 | 5876.9 | 6785.7 | 5847.4 | 6722.1 | 6572 | 5793.1 | 6390.9 | 6090.9 | 6322.8 | 5993.2 | 6263 | 6659.4 | 6682.8 | 6160.5 | 6609.1 | 5954.5 | 6399.6 | 6418.5 | 5943.2 | 6791.6 | 5963.9 | 6798.6 | 6023.4 | 6763.9 | 6216.4 | 6639.4 | 6355.3 | 6918 | 6233.9 | 6625 | 6177.3 | 5432 | 6773.2 | 6419.1 | 6063.5 | 6985.9 | 6744.1 | 6265.9 | 6222.1 | 6875.3 | 6046.4 | 6201.9 | 6747.4 | 5929.2 | 6899.1 | 5949.3 | 6688.7 | 6110.3 | 6725.1 | 5798.8 | 6743.1 | 6018.7 | 6658.8 | 5963.6 | 6602.1 | 6033 | 5941.7 | 6474.1 | 5997.1 | 5847.3 | 6570.7 | 6550.2 | 6454.8 | 5811.1 | 6378.5 | 5660.7 | 6423.8 | 5933.6 | 6216.7 | 5331.3 | 6208.6 | 5671.3 | 5860.8 | 5935.4 | 5663.7 | 4942 | 6039.5 | 5466.9 | 6499.9 | 6446.5 | 7356.4 | 6442.5 | 7347.6 | 6612.6 | 7348.4 | 6538 | 6606 | 6518.4 | 7082.1 | 7319.2 | 7271.9 | 7249 | 7253.2 | 7286 | 6642.2 | 7260.2 | 7228.7 | 7330.8 | 7386.9 | 7290.1 | 7292.3 | 6677 | 7286.3 | 6663.9 | 22.9676 | 29.5615 | 29.8956 | 32.3896 | 29.7844 | 29.7097 | 0 | 37.5135 | 0 | 0 | 37.6 | 38 | 3.2032 | 3.2759 | 1.3156 | 2.4996 | 3.1924 | 3.1376 | 11.2883 | 11.1267 | 9.4067 | 11.1167 | 12.315 | 9.25 | 3.5989 | 3.5921 | 3.5694 | 3.5136 | 3.4601 | 3.8554 | 0.7682 | 0.59124 | 0.6838 | 0.86316 | 0.79885 | 0.63332 | 3.6185 | 3.6213 | 3.5976 | 3.5302 | 3.4886 | 3.7621 | 0.14372 | 0.17811 | 0.16003 | 0.16261 | 0.17845 | 0.19858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 719253 | 1299 | 706170 | 1356 | 80836.073 | 227.8 | 3.5989 | 3.5921 | 3.5694 | 3.5136 | 3.4601 | 3.8554 | 3.6185 | 3.6213 | 3.5976 | 3.5302 | 3.4886 | 3.7621 | 518000 | 1000 | 517000 | 1000 | 1031000 | 4467 | 1033000 | 1026533 | 12.25 | 3.5982 | 0.7231 | 3.6031 | 0.17025 | 20.1% | 4.725% | 29.0514 | 37.7045 | 2.7707 | 10.7506 | 1037194.6 | 1030270 | 1216799.4231 | 84.67% | 33 | 201670
2024-08-25 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 335090.89 | 6:50 | 19:06 | 7698.1 | 8240.8 | 8297 | 8268 | 8403 | 8423 | 8349 | 7357 | 8343.9 | 7907.7 | 8256.6 | 8374.7 | 8419 | 8348.2 | 8609.1 | 8578 | 8529.4 | 8590.2 | 8543 | 8578.3 | 8611.8 | 8597.8 | 8433.6 | 8518.4 | 8127.8 | 7202.3 | 7587.6 | 8156.7 | 8061.8 | 8464.6 | 8211.9 | 8398.6 | 8589 | 8589.7 | 8611.6 | 8571.8 | 8667 | 8535 | 8283.1 | 8503.6 | 9232.5 | 8432.6 | 9158.7 | 8319.1 | 8822.2 | 9676.4 | 8300.8 | 9264.7 | 8165.8 | 7647.2 | 8002.2 | 7527.2 | 8252.2 | 7876.4 | 8473 | 8037.9 | 7135.2 | 8517.3 | 7407.1 | 8369 | 8160 | 7387.9 | 7937.3 | 7628.7 | 7926 | 7462.9 | 7493 | 7797.3 | 7965 | 7583.2 | 8287.5 | 6740.4 | 8153.8 | 7236.6 | 7429.5 | 8211.6 | 7129.2 | 8453.2 | 6799.4 | 8197.6 | 7728.8 | 8237.2 | 7869 | 8657.3 | 7808.1 | 8309 | 7832 | 6906.3 | 8599.7 | 8174.6 | 7773 | 8906.8 | 8705.2 | 8152.9 | 8083.6 | 8790 | 7959.7 | 8137.2 | 8778.5 | 7822.7 | 8940 | 7864.9 | 8724.9 | 8091.7 | 8757.1 | 7672.5 | 8786.7 | 7982.2 | 8689.8 | 7950.9 | 8802.6 | 8114.9 | 7854 | 8588.5 | 8025.9 | 7850.3 | 8756.4 | 8758.2 | 8540.7 | 7945.1 | 8721.2 | 7893.4 | 8553.5 | 7997.1 | 8383 | 7396.4 | 8545.8 | 7906 | 8044.2 | 8104.9 | 7906.6 | 6906.4 | 7926.1 | 7077.8 | 7929.6 | 7885.8 | 8760 | 7752.3 | 8771.7 | 7897.6 | 8803.2 | 7916.1 | 8050.7 | 7974.6 | 8396.2 | 8651.3 | 8594.6 | 8594.8 | 8645.3 | 8694.4 | 7919.7 | 8630.7 | 8574 | 8585.1 | 8588.9 | 8489.3 | 8482.3 | 7753.6 | 8645 | 7768.3 | 29.1239 | 31.8634 | 31.7183 | 35.786 | 32.0695 | 32.0442 | 0 | 40.2191 | 0 | 0 | 39.6532 | 39.6013 | 3.8691 | 3.7765 | 2.0508 | 3.3233 | 3.8197 | 3.5892 | 6.4283 | 8.085 | 7.6017 | 6.535 | 7.15 | 6.2317 | 4.5049 | 4.6564 | 4.7398 | 4.4438 | 4.6381 | 4.4583 | 0.96118 | 0.90462 | 0.88936 | 1.1466 | 1.1979 | 0.84772 | 4.5789 | 4.7515 | 4.7724 | 4.5753 | 4.6964 | 4.4283 | 0.2246 | 0.28458 | 0.25228 | 0.25968 | 0.29156 | 0.2695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 719906 | 1301 | 706826 | 1358 | 82140.273 | 232.533 | 4.5049 | 4.6564 | 4.7398 | 4.4438 | 4.6381 | 4.4583 | 4.5789 | 4.7515 | 4.7724 | 4.5753 | 4.6964 | 4.4283 | 653000 | 2000 | 656000 | 2000 | 1304200 | 4733 | 1305000 | 1299467 | 12.2667 | 4.5735 | 0.99122 | 4.6338 | 0.2637 | 21.67% | 5.691% | 32.1009 | 39.8245 | 3.4048 | 7.0053 | 1311481.7 | 1303800 | 1557009.2874 | 83.74% | 29 | 0
2024-08-26 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 335090.89 | 6:52 | 19:02 | 8374 | 8827 | 8833 | 8795 | 8954 | 8941 | 8903 | 9138 | 8764 | 8604.3 | 8645.8 | 8756.3 | 8783.1 | 8693.5 | 8924.7 | 8891.5 | 8824.4 | 8866.3 | 8831.3 | 8879.8 | 8895.7 | 8877.9 | 8776.3 | 8826.9 | 8571.5 | 7696 | 8587 | 8588.4 | 8907.6 | 8902 | 8769.8 | 8802.5 | 8923.9 | 8925.2 | 8979.8 | 8923.3 | 8846.3 | 8787.4 | 8830.5 | 8696.5 | 9052.5 | 8239.6 | 9030.9 | 8120.5 | 8785.4 | 9715.1 | 8320.4 | 9152.2 | 8797 | 8327.4 | 8824.3 | 8356.1 | 9071.5 | 8350.9 | 8897 | 8875.6 | 8056.3 | 9056.9 | 8149.1 | 9007.1 | 8906.3 | 8119.5 | 8691.2 | 8323.7 | 8473.5 | 8026.6 | 8455.6 | 8779.5 | 8970.9 | 8227.3 | 8854 | 7985.8 | 8679.3 | 8576.9 | 8147.9 | 8946.4 | 8036.7 | 9017.4 | 8153.7 | 8926.7 | 8285.2 | 8783.3 | 8465.9 | 9101.6 | 8339.4 | 8805.2 | 8187.1 | 7342.5 | 8890.4 | 8507.6 | 8032.9 | 9058.6 | 8815.2 | 8291.5 | 8218.4 | 8888.8 | 8162 | 8361.5 | 8945.3 | 8069 | 9022.1 | 8053.1 | 8819 | 8253.8 | 8852.6 | 7869.2 | 8896.8 | 8169.5 | 8838.3 | 8158 | 8917.1 | 8301.1 | 8137.3 | 8830.5 | 8218.9 | 8089.4 | 8921.6 | 8981.3 | 8833.9 | 8254.4 | 8914.6 | 8140.8 | 8702.2 | 8204.7 | 8625.5 | 7670.3 | 8725.9 | 8151.8 | 8387.9 | 8485 | 8174.9 | 7270.3 | 8386.1 | 7663.5 | 8653.8 | 8657.6 | 9624.6 | 8592.3 | 9795.5 | 8846.8 | 9664 | 8829.4 | 8868.6 | 8824.6 | 9622.3 | 9890 | 9725.6 | 9688.3 | 9640.4 | 9642.6 | 9005 | 9765 | 9885.6 | 9906.5 | 10027.7 | 9916.6 | 9842.6 | 9115.8 | 9801.4 | 9064.7 | 28.03 | 31.17 | 31.2 | 36.9 | 31.39 | 31.56 | 0 | 38.92 | 0 | 0 | 38.9 | 39.5 | 6.06 | 6.15 | 5.23 | 6.26 | 6.42 | 6.22 | 12.14 | 12.42 | 12.17 | 12.85 | 14.03 | 11.94 | 4.92 | 4.96 | 4.8 | 4.79 | 4.86 | 5.21 | 1.03 | 0.97 | 0.88 | 1.2 | 1.26 | 1.02 | 5.03 | 5.08 | 4.84 | 4.93 | 4.95 | 5.24 | 0.25 | 0.31 | 0.26 | 0.28 | 0.31 | 0.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720600 | 1303 | 707526 | 1360 | 83529.207 | 237.133 | 4.92 | 4.96 | 4.8 | 4.79 | 4.86 | 5.21 | 5.03 | 5.08 | 4.84 | 4.93 | 4.95 | 5.24 | 694000 | 2000 | 700000 | 2000 | 1388934 | 4600 | 1390000 | 1384334 | 12.1667 | 4.9233 | 1.06 | 5.0117 | 0.28667 | 21.53% | 5.72% | 31.7083 | 39.1067 | 6.0567 | 12.5917 | 1396199.3 | 886733 | 1030349.6342 | 86.06% | 31 | 58550
2024-08-27 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 335090.89 | 7:02 | 19:00 | 4720.9 | 5013.1 | 4998.1 | 4966.4 | 5039.7 | 5037.1 | 5065.1 | 5252.9 | 4996.9 | 4962 | 4905.6 | 4999.7 | 4950.5 | 4939.3 | 5003.7 | 5006.7 | 4922.8 | 4936.3 | 4935.4 | 4966.7 | 4952.4 | 4937.8 | 4832.4 | 4884.1 | 4790.7 | 4203.9 | 4821.4 | 4794.1 | 4968.5 | 4929.6 | 4844.1 | 4949.6 | 4954.8 | 4963.9 | 4977.4 | 4930.5 | 4984.8 | 4907.5 | 4933.9 | 4918.1 | 5266.9 | 4702.4 | 5224.3 | 4620.2 | 4987.3 | 5644.9 | 4628.4 | 5307 | 5028 | 4688 | 5012 | 4712 | 5199.5 | 4642 | 5142 | 5106 | 5304 | 4551 | 4569 | 5242 | 5169 | 4571 | 5002 | 4706 | 4877 | 4555.5 | 4851 | 5087 | 5255 | 4666 | 5160 | 4490.5 | 5036 | 4905.5 | 4608 | 5192.5 | 4517 | 5272 | 4593 | 5166.5 | 4675.9 | 5039.8 | 4784.8 | 5288.3 | 4717.5 | 5063.6 | 4694.2 | 4128.5 | 5176.3 | 4913.2 | 4571.4 | 5339.5 | 5162.9 | 4757.8 | 4705.8 | 5231.7 | 4670.7 | 4806.4 | 5247.1 | 4587.3 | 5320.4 | 4584.7 | 5151.9 | 4726 | 5197.6 | 4462.5 | 5213.6 | 4673.8 | 5141 | 4669.9 | 5193.8 | 4751.1 | 4633 | 5116.7 | 4693.9 | 4585.5 | 5214.5 | 5255.3 | 5110.2 | 4698.6 | 5216.9 | 4642.7 | 5049.4 | 4678.5 | 4968.9 | 4333.2 | 5076.1 | 4675.6 | 4760.4 | 4793 | 4689.4 | 4056.1 | 4664.5 | 4143.2 | 4770.7 | 4775 | 5505.5 | 4744.8 | 5546.5 | 4860.8 | 5493.1 | 4840.7 | 4902.8 | 4859.3 | 5301 | 5529.7 | 5443.7 | 5428.5 | 5431.2 | 5465.8 | 4923.9 | 5474.8 | 5502.7 | 5510.9 | 5561.8 | 5507.7 | 5466.6 | 4906.7 | 5495.1 | 4884.5 | 22.9303 | 28.0286 | 27.8612 | 32.3301 | 28.2115 | 28.3225 | 0 | 31.6 | 0 | 0 | 32 | 32.2 | 8.0611 | 8.3422 | 7.8453 | 8.247 | 8.536 | 7.9329 | 12.99 | 12.365 | 11.985 | 12.72 | 13.47 | 12.2833 | 2.53 | 2.5176 | 2.499 | 2.5469 | 2.5545 | 2.6059 | 0.50547 | 0.48456 | 0.44991 | 0.60259 | 0.64246 | 0.50856 | 2.5032 | 2.4902 | 2.4341 | 2.5028 | 2.5149 | 2.5528 | 0.12299 | 0.14702 | 0.12081 | 0.13854 | 0.14354 | 0.14045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720995 | 1304 | 707924 | 1361 | 84319.007 | 241.733 | 2.53 | 2.5176 | 2.499 | 2.5469 | 2.5545 | 2.6059 | 2.5032 | 2.4902 | 2.4341 | 2.5028 | 2.5149 | 2.5528 | 395000 | 1000 | 398000 | 1000 | 789800 | 4600 | 791000 | 785200 | 11.9667 | 2.5423 | 0.53226 | 2.4997 | 0.13556 | 20.94% | 5.423% | 27.9474 | 31.9333 | 8.1607 | 12.6356 | 792194.2 | 201733 | 236077.4876 | 85.45% | 32 | 111356
2024-08-28 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 335090.89 | 6:42 | 19:05 | 3912 | 4133 | 4094 | 4072 | 4128 | 4125 | 4159 | 4326 | 4151 | 4128 | 4074 | 4157 | 4103 | 4105 | 4138 | 4139 | 4039 | 4067 | 4094 | 4121 | 4122 | 4111 | 4059 | 4077 | 4062 | 3549 | 4033 | 4026 | 4196 | 4185 | 4138 | 4213 | 4114 | 4068 | 4141 | 4108 | 4148 | 4043 | 4126 | 4103 | 4373 | 3926 | 4401 | 3904 | 4224 | 4755 | 3867 | 4378 | 4113 | 3850 | 4115 | 3903 | 4273 | 3792 | 4275 | 4237 | 3789 | 4416 | 3746 | 4342 | 4267 | 3743 | 4167 | 3930 | 4049 | 3767 | 4024 | 4206 | 4339 | 3853 | 4279 | 3722 | 4161 | 4064 | 3814 | 4299 | 3755 | 4354 | 3803 | 4280 | 3959 | 4273 | 4061 | 4474 | 4001 | 4296 | 3949 | 3467 | 4416 | 4161 | 3891 | 4541 | 4382 | 4040 | 4001 | 4470 | 4071 | 4248 | 4630 | 4104 | 4635 | 4072 | 4525 | 4215 | 4570 | 3969 | 4620 | 4209 | 4538 | 4050 | 4629 | 4306 | 4162 | 4621 | 4239 | 4155 | 4716 | 4753 | 4600 | 4257 | 4724 | 4208 | 4582 | 4254 | 4441 | 3902 | 4595 | 4236 | 4312 | 4349 | 4244 | 3680 | 4227 | 3741 | 4163 | 4165 | 4859 | 4196 | 4871 | 4283 | 4834 | 4245 | 4302 | 4246 | 4757 | 4944 | 4884 | 4865 | 4885 | 4919 | 4419 | 4907 | 4952 | 4936 | 4964 | 4935 | 4916 | 4391 | 4948 | 4380 | 26.47 | 29.64 | 29.27 | 31.14 | 29.62 | 29.77 | 0 | 38.4 | 0 | 0 | 38.9 | 38.41 | 6.05 | 6.13 | 5.34 | 6.07 | 6.23 | 6.14 | 12.43 | 12.26 | 11.35 | 11.21 | 11.74 | 11.14 | 4.34 | 4.48 | 4.54 | 4.59 | 4.69 | 4.64 | 0.83 | 0.79 | 0.82 | 1.03 | 1.05 | 0.85 | 4.4 | 4.53 | 4.54 | 4.58 | 4.7 | 4.6 | 0.23 | 0.28 | 0.24 | 0.26 | 0.27 | 0.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 721322 | 1305 | 708276 | 1363 | 84996.14 | 246.267 | 4.34 | 4.48 | 4.54 | 4.59 | 4.69 | 4.64 | 4.4 | 4.53 | 4.54 | 4.58 | 4.7 | 4.6 | 327000 | 1000 | 352000 | 2000 | 677133 | 4534 | 676000 | 672599 | 12.3833 | 4.5467 | 0.895 | 4.5583 | 0.26 | 19.68% | 5.704% | 29.3183 | 38.57 | 5.9933 | 11.6883 | 679379 | 650200 | 764435.9156 | 85.06% | 24 | 35410
2024-08-29 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 335090.89 | 6:45 | 19:01 | 8402 | 8816 | 8655 | 8644 | 8712 | 8736 | 8862 | 9094 | 8853.6 | 8725.1 | 8663.2 | 8809.7 | 8682.3 | 8642.6 | 8699.5 | 8705.2 | 8550.2 | 8540.3 | 8496.9 | 8602.6 | 8434.8 | 8473 | 8223.7 | 8296.7 | 8112.2 | 7333.9 | 8250.3 | 8166.5 | 8382.4 | 8297.2 | 8056.3 | 8293 | 8368 | 8407.4 | 8660.2 | 8532 | 8261.8 | 8067.7 | 8039 | 7964.1 | 8553.3 | 7800.4 | 8477.6 | 7664.7 | 8157.1 | 8994.8 | 7751.3 | 8663.4 | 8609.3 | 8198.8 | 8606.8 | 8121.5 | 8828.8 | 8163.4 | 8634.7 | 8570.5 | 8170 | 9211 | 8345 | 9224 | 9173 | 8354.9 | 8914 | 8550 | 8454.9 | 7875.1 | 8443 | 8626.7 | 9046.4 | 8043 | 8829.5 | 7796 | 8780.7 | 8464 | 8218 | 8872 | 8015.7 | 9190.5 | 8247.5 | 9051.8 | 7681.3 | 8182.9 | 7811 | 8501.9 | 7735.5 | 8169.5 | 7666.6 | 6880.1 | 8421.3 | 7971.4 | 7573.7 | 8594 | 8362.4 | 7846.4 | 7772.2 | 8475.3 | 7846.2 | 8062.5 | 8643.4 | 7729.1 | 8780.8 | 7747.7 | 8553.3 | 7931.7 | 8603.8 | 7550.3 | 8656 | 7829.3 | 8547.3 | 7836.3 | 8570.6 | 7944.2 | 7764.5 | 8436.8 | 7871.3 | 7709.6 | 8570.5 | 8645.4 | 8434.8 | 7933.7 | 8624.1 | 7859.7 | 8369.8 | 7875 | 8322.3 | 7375.4 | 8446.4 | 7782 | 8209 | 8270 | 7732.2 | 6894.4 | 7783.1 | 7049.3 | 7865.8 | 7898.1 | 8923.8 | 7913.7 | 8923.1 | 8047.8 | 8898.6 | 8041 | 8122.7 | 8012.2 | 8805.5 | 8998.2 | 8958.4 | 8918.5 | 8905.3 | 8926.8 | 8154.8 | 8905.9 | 9009.7 | 9054.7 | 9064.7 | 9079.5 | 9050.7 | 8265.2 | 9018.8 | 8221.2 | 27.6124 | 30.1375 | 29.9343 | 31.8042 | 29.9827 | 30.2537 | 0 | 39.9 | 0 | 0 | 39.9 | 39.9 | 6.0359 | 5.7427 | 5.4191 | 5.7462 | 6.2255 | 5.617 | 9.0467 | 9 | 8.7883 | 9.0033 | 9.5267 | 9.3683 | 5.173 | 4.9245 | 4.7309 | 4.8015 | 4.7332 | 4.8397 | 1.0361 | 0.93189 | 0.86429 | 1.1469 | 1.2215 | 0.96263 | 5.2728 | 5.0013 | 4.7309 | 4.9246 | 4.7655 | 4.8629 | 0.25892 | 0.29137 | 0.24317 | 0.26344 | 0.27144 | 0.27965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 721999 | 1307 | 708933 | 1364 | 86326.34 | 250.6 | 5.173 | 4.9245 | 4.7309 | 4.8015 | 4.7332 | 4.8397 | 5.2728 | 5.0013 | 4.7309 | 4.9246 | 4.7655 | 4.8629 | 677000 | 2000 | 657000 | 1000 | 1330200 | 4333 | 1331000 | 1325867 | 12.2667 | 4.8671 | 1.0272 | 4.9263 | 0.268 | 21.1% | 5.44% | 29.9541 | 39.9 | 5.7977 | 9.1222 | 1336627.5 | 536133 | 642213.3992 | 83.48% | 28 | 54518
2024-08-30 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 335090.89 | 6:39 | 19:04 | 9144 | 9548 | 9334 | 9337 | 9380 | 9447 | 9526 | 7977 | 9363 | 9391 | 9389 | 9347 | 9384 | 9556 | 9320 | 9410 | 9147 | 9235 | 9340 | 9362 | 9300 | 9387 | 9228 | 9283 | 9086 | 8192 | 9149 | 9113 | 9316 | 9280 | 9102 | 9216 | 9266 | 8332 | 9357 | 9336 | 9413 | 9335 | 9414 | 9416 | 10073 | 9473 | 10211 | 9458 | 9953 | 10605 | 9164 | 9996 | 9426 | 9012 | 9410 | 9018 | 9510 | 9011 | 9518 | 9451 | 8733 | 9704 | 8831 | 9688 | 9602 | 9591 | 9424 | 9123 | 9217 | 8713 | 9201 | 9468 | 9670 | 8888 | 9581 | 8642 | 9427 | 9298 | 8911 | 9670 | 8794 | 9681 | 8884 | 9649 | 8937 | 9426 | 9093 | 9773 | 8990 | 9490 | 8860 | 7289 | 9749 | 9275 | 8797 | 9945 | 9783 | 9204 | 9149 | 9935 | 9382 | 9636 | 10269 | 9333 | 10387 | 9360 | 10202 | 9579 | 10245 | 9118 | 10287 | 9435 | 10183 | 9444 | 10171 | 9527 | 9361 | 10058 | 9438 | 9298 | 10142 | 10127 | 10002 | 9432 | 10157 | 9320 | 9923 | 9450 | 9945 | 9105 | 9903 | 9287 | 9486 | 9546 | 9345 | 8131 | 9408 | 8424 | 9485 | 9510 | 10456 | 9446 | 10449 | 9562 | 10393 | 9559 | 9676 | 9637 | 10275 | 10453 | 10363 | 10353 | 10349 | 10398 | 9649 | 10387 | 10116 | 10188 | 10251 | 10337 | 10361 | 9637 | 10203 | 9536 | 25.88 | 30.26 | 30.31 | 31.75 | 30.24 | 30.44 | 0 | 40.9 | 0 | 0 | 42.3 | 42.31 | 5.3 | 4.62 | 4.1 | 4.96 | 5.28 | 4.39 | 10.08 | 8.27 | 8.29 | 8.55 | 9.46 | 8.92 | 5.31 | 5.14 | 5.39 | 5.19 | 5.52 | 5.52 | 1.1 | 1.01 | 1.02 | 1.26 | 1.43 | 1.13 | 5.49 | 5.31 | 5.47 | 5.37 | 5.65 | 5.63 | 0.28 | 0.34 | 0.29 | 0.3 | 0.32 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 722746 | 1308 | 709707 | 1366 | 87839.8 | 261.5 | 5.31 | 5.14 | 5.39 | 5.19 | 5.52 | 5.52 | 5.49 | 5.31 | 5.47 | 5.37 | 5.65 | 5.63 | 747000 | 1000 | 774000 | 2000 | 1513460 | 10900 | 1518000 | 1502560 | 12.4167 | 5.345 | 1.1583 | 5.4867 | 0.31 | 21.67% | 5.65% | 29.8133 | 41.8367 | 4.775 | 8.9283 | 1519707 | 1513134 | 1858173.0271 | 81.43% | 34 | 63831
2024-08-31 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 335090.89 | 6:35 | 19:01 | 7700 | 8167 | 8311 | 8326 | 8439 | 8237 | 8065 | 8038 | 7938 | 7911 | 7680 | 7580 | 7575 | 7818 | 7980 | 7914 | 8085 | 8130 | 8193 | 8211 | 8134 | 8115 | 7888 | 8092 | 8059 | 7060 | 7092 | 7176 | 8387 | 8443 | 8519 | 8363 | 8760 | 8515 | 8181 | 8284 | 8536 | 8668 | 8968 | 9060 | 9007 | 8240 | 9226 | 8376 | 8527 | 9245 | 8217 | 8979 | 7810 | 7450 | 7988 | 7722 | 8282 | 7390 | 8304 | 8272 | 7356 | 8290 | 7196 | 8284 | 8138 | 7140 | 7906 | 7469 | 7836 | 7573 | 7784 | 8281 | 8165 | 7462 | 8000 | 7065 | 7748 | 7584 | 7088 | 7900 | 6948 | 8006 | 7013 | 7713 | 7617 | 7908 | 8067 | 8604 | 7894 | 8384 | 7693 | 6748 | 8438 | 7923 | 7468 | 8505 | 8247 | 7777 | 7770 | 8401 | 8232 | 8675 | 9258 | 8430 | 9202 | 8290 | 8988 | 8429 | 9077 | 7905 | 9108 | 8444 | 9062 | 8409 | 9296 | 8807 | 8606 | 9383 | 8745 | 8612 | 9432 | 9211 | 9266 | 8289 | 9030 | 8155 | 9128 | 8591 | 8729 | 7499 | 8731 | 8039 | 8157 | 8227 | 7928 | 6936 | 7945 | 7127 | 8145 | 8288 | 9488 | 8595 | 9712 | 8954 | 9749 | 8865 | 8865 | 8506 | 9499 | 9686 | 9507 | 9509 | 9561 | 9574 | 9002 | 9677 | 9692 | 9680 | 9802 | 9804 | 9750 | 9053 | 9706 | 8839 | 24.08 | 29.77 | 30.27 | 30.82 | 30.35 | 30.34 | 0 | 41.39 | 0 | 0 | 44.3 | 43.9 | 2.52 | 2.11 | 0.83 | 1.1 | 2.59 | 2.34 | 8.8 | 9.57 | 9.62 | 10.08 | 9.19 | 8.57 | 4.1 | 4.56 | 4.72 | 4.35 | 5.17 | 5.14 | 0.85 | 0.84 | 0.94 | 1.04 | 1.28 | 0.96 | 4.23 | 4.73 | 4.81 | 4.37 | 5.33 | 5.22 | 0.23 | 0.31 | 0.26 | 0.25 | 0.31 | 0.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 723388 | 1310 | 710398 | 1367 | 89128.8 | 261.5 | 4.1 | 4.56 | 4.72 | 4.35 | 5.17 | 5.14 | 4.23 | 4.73 | 4.81 | 4.37 | 5.33 | 5.22 | 642000 | 2000 | 691000 | 1000 | 1289000 | 0 | 1330000 | 1289000 | 12.4333 | 4.6733 | 0.985 | 4.7817 | 0.27833 | 21.08% | 5.821% | 29.2717 | 43.1967 | 1.915 | 9.305 | 1335908 | 1287003 | 1604196.6841 | 80.23% | 35 | NA
2024-09-01 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 335090.89 | 6:41 | 19:06 | 7998 | 8439 | 8737 | 8765 | 8869 | 8739 | 8549 | 8782 | 8370 | 8268 | 8167 | 8128 | 8107 | 8738 | 8549 | 8742 | 8251 | 8328 | 8230 | 8236 | 8426 | 8345 | 8528 | 8451 | 8527 | 8451 | 8425 | 8344 | 8229 | 8236 | 8250 | 8327 | 8523 | 8420 | 8342 | 8397 | 8641 | 8593 | 8644 | 8550 | 9781 | 9080 | 9854 | 9134 | 9593 | 10229 | 8727 | 9770 | 8192 | 7734 | 8257 | 7821 | 8514 | 7707 | 8366 | 8353 | 7482 | 8485 | 7468 | 8500 | 8348 | 7420 | 8330 | 7634 | 8016 | 7458 | 7897 | 8137 | 8392 | 7521 | 8223 | 7217 | 8044 | 7833 | 7442 | 8230 | 7359 | 8254 | 7338 | 8124 | 7400 | 7923 | 7337 | 8288 | 7322 | 7747 | 7319 | 6339 | 8098 | 7529 | 7387 | 8517 | 8394 | 7961 | 7962 | 8408 | 7438 | 7663 | 8339 | 7405 | 8494 | 7425 | 8253 | 7649 | 8332 | 7067 | 8379 | 7539 | 8335 | 7513 | 8420 | 7703 | 7363 | 8094 | 7589 | 7405 | 8380 | 8378 | 8304 | 7670 | 8448 | 7645 | 8208 | 7484 | 8138 | 7223 | 8357 | 7819 | 7651 | 7663 | 7863 | 6647 | 7589 | 6746 | 7502 | 7462 | 8161 | 7162 | 8310 | 7335 | 8290 | 7468 | 7599 | 7616 | 8055 | 8340 | 8144 | 8178 | 8171 | 8190 | 7528 | 8237 | 8143 | 7979 | 8198 | 8278 | 8331 | 7536 | 8063 | 7474 | 23.97 | 30.19 | 30.6 | 30.83 | 30.74 | 30.43 | 0 | 39.5 | 0 | 0 | 38.9 | 38.6 | 3.45 | 3.42 | 1.75 | 3.14 | 3.64 | 2.18 | 7.71 | 7.5 | 6.2 | 6.59 | 8.1 | 9.09 | 4.51 | 4.59 | 4.97 | 4.36 | 4.37 | 4.24 | 0.73 | 0.64 | 0.85 | 0.85 | 1.01 | 0.72 | 4.67 | 4.76 | 5.11 | 4.54 | 4.48 | 4.26 | 0.14 | 0.19 | 0.18 | 0.16 | 0.18 | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 724051 | 1311 | 711024 | 1369 | 90454.54 | 263 | 4.51 | 4.59 | 4.97 | 4.36 | 4.37 | 4.24 | 4.67 | 4.76 | 5.11 | 4.54 | 4.48 | 4.26 | 663000 | 1000 | 626000 | 2000 | 1325740 | 1500 | 1286000 | 1324240 | 12.4167 | 4.5067 | 0.8 | 4.6367 | 0.17333 | 17.75% | 3.738% | 29.46 | 39 | 2.93 | 7.5317 | 1294204 | 1287000 | 1585513.4717 | 81.17% | 33 | NA
2024-09-02 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 335090.89 | 6:55 | 19:01 | 9189.7 | 9773.3 | 9733.4 | 9672.8 | 9809.4 | 9823.9 | 9877.5 | 10214.5 | 9735.6 | 9622.1 | 9612.4 | 9775 | 9719.8 | 9719.2 | 9771.6 | 9794.2 | 9662.8 | 9704.4 | 9759.6 | 9837.8 | 9736 | 9758.8 | 9493.5 | 9622.7 | 9535.8 | 8385.7 | 9580.8 | 9537.9 | 9811 | 9676.7 | 9546.5 | 9776.9 | 9858.6 | 9871.7 | 9889.3 | 9806.8 | 9889.2 | 9717.4 | 9757.3 | 9702 | 10319.3 | 9314.5 | 10244.9 | 9180.5 | 9810.4 | 10885.2 | 9183.8 | 10349.7 | 9887.1 | 9234.9 | 9890.9 | 9326.8 | 10228.2 | 9154 | 10091 | 10032.7 | 8971 | 10360.6 | 8989.5 | 10283.7 | 10121.4 | 8967.8 | 9834.4 | 9272.7 | 9653.7 | 9037.1 | 9599.1 | 10015.9 | 10268 | 9239.7 | 10149 | 8884.1 | 9816.1 | 9633.6 | 9052.2 | 10117.1 | 8903.5 | 10237.2 | 8966 | 9988.3 | 9258.4 | 9883.5 | 9467.6 | 10410 | 9379.6 | 9994.7 | 9290.6 | 8157.7 | 10179.4 | 9641.8 | 9117.7 | 10505 | 10171.9 | 9403.7 | 9287.2 | 10270.8 | 9197 | 9491.2 | 10275.4 | 9097 | 10349.1 | 9070.8 | 10044.9 | 9297.9 | 10066.5 | 8733.5 | 10075.6 | 9083.8 | 9942.2 | 9004.5 | 10001.4 | 9154.3 | 9143 | 10013.4 | 9221.5 | 9022.4 | 10027.4 | 10032.2 | 9824.2 | 8973.2 | 9856 | 8859.2 | 9672.9 | 9000.1 | 9435.2 | 8288.8 | 9631.3 | 8942.4 | 9107.7 | 9219.8 | 8953.6 | 7761.3 | 9063 | 8091.4 | 9171.2 | 9194.2 | 10733.1 | 9312.8 | 10741 | 9530.1 | 10528.4 | 9387.8 | 9505.1 | 9337 | 10299 | 10643 | 10600 | 10555 | 10604 | 9487 | 9669 | 10618 | 10651 | 10468.9 | 10475.8 | 10551.4 | 10567.7 | 9523.3 | 10679.6 | 9596.2 | 29.11 | 31.34 | 31.68 | 32.68 | 31.87 | 31.83 | 0 | 43.8 | 0 | 0 | 45 | 44.9 | 2.41 | 2.14 | 0.35 | 1.12 | 2.56 | 0.93 | 5.72 | 5.5 | 3.73 | 7.08 | 7.24 | 6.86 | 5.12 | 5.17 | 5.11 | 5.16 | 5.25 | 5.32 | 0.82 | 0.82 | 0.85 | 1.07 | 1.31 | 1.05 | 5.33 | 5.4 | 5.25 | 5.4 | 5.42 | 5.47 | 0.21 | 0.28 | 0.25 | 0.25 | 0.29 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 724825 | 1313 | 711795 | 1370 | 91993.94 | 267.733 | 5.12 | 5.17 | 5.11 | 5.16 | 5.25 | 5.32 | 5.33 | 5.4 | 5.25 | 5.4 | 5.42 | 5.47 | 774000 | 2000 | 771000 | 1000 | 1539400 | 4733 | 1542000 | 1534667 | 12.1 | 5.1883 | 0.98667 | 5.3783 | 0.26333 | 19.02% | 4.896% | 31.4183 | 44.5667 | 1.585 | 6.0217 | 1547133.5 | 1506200 | 1803677.8802 | 83.51% | 35 | 43624
2024-09-03 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 335090.89 | 7:01 | 17:02 | 8116.3 | 8615.1 | 8719.6 | 8715.4 | 8801 | 8777.3 | 8723.2 | 8938.8 | 8523.8 | 8446.3 | 8369.3 | 8517.2 | 8496.7 | 8402.3 | 8588.8 | 8571.8 | 8579.9 | 8665.6 | 8653.2 | 8661.1 | 8743.9 | 8702.2 | 8527.2 | 8635.4 | 8353 | 7303.3 | 8349.9 | 8414.4 | 8694.8 | 8669.6 | 8521.2 | 8623.9 | 8630.7 | 8571 | 8548.6 | 8535.1 | 8681.5 | 8585.3 | 8633.7 | 8566.4 | 9398 | 8634.2 | 9358.7 | 8524 | 9009.5 | 9771.8 | 8431.8 | 9384.1 | 8481.7 | 8208.9 | 8522.9 | 8036.9 | 8814.9 | 8009 | 8620.9 | 8585.2 | 7650.5 | 8806 | 7739.8 | 8767.7 | 8626.1 | 7751.2 | 8451.6 | 8003.5 | 8071.9 | 7457.5 | 7986.8 | 8222.6 | 8642.7 | 7566.7 | 8379.2 | 7216.5 | 8333.6 | 7894.4 | 7666.6 | 8345.9 | 7401.3 | 8667.9 | 7598.9 | 8428.8 | 7472.6 | 8004.2 | 7524.5 | 8421.7 | 7515.7 | 7993 | 7606.2 | 6578.7 | 8294.9 | 7843.6 | 7523.5 | 8708.9 | 8596.7 | 8065.3 | 8025.5 | 8599.8 | 7675 | 7893.3 | 8624.8 | 7649.1 | 8840.5 | 7702.4 | 8637.2 | 7947.7 | 8729.8 | 7550.5 | 8778 | 7973.5 | 8697.2 | 7963.6 | 8824.4 | 8149.1 | 7679.2 | 8553 | 7961.8 | 7776.5 | 8814.1 | 8853.1 | 8733.3 | 7976.6 | 8846.6 | 7938 | 8652.3 | 8060.9 | 8654.5 | 7452.8 | 8672.7 | 7949.9 | 7941.6 | 7952.8 | 7885.2 | 6814.3 | 7642.1 | 6735.3 | 7212.6 | 7201.3 | 8106.6 | 7154.4 | 8127.7 | 7280 | 8181.1 | 7263.8 | 7410.6 | 7274.2 | 7658.6 | 7934.5 | 7892.9 | 7871.3 | 7932.2 | 7975.5 | 7228.1 | 7929.4 | 7892.9 | 7754.1 | 7786 | 7847.9 | 7869.5 | 7060.1 | 7958.2 | 7114.4 | 25.16 | 31.46 | 31.71 | 32.9 | 31.63 | 31.42 | 0 | 46.54 | 0 | 0 | 46.1 | 44.45 | 2.9 | 2.73 | 0.83 | 2.16 | 3.02 | 1.35 | 10.61 | 9.96 | 11.15 | 10.45 | 11.9 | 10.17 | 4.56 | 4.64 | 4.82 | 4.37 | 4.58 | 3.93 | 0.83 | 0.74 | 0.86 | 1.01 | 1.14 | 0.74 | 4.78 | 4.86 | 4.99 | 4.6 | 4.76 | 4.01 | 0.18 | 0.24 | 0.23 | 0.21 | 0.25 | 0.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 725498 | 1314 | 712428 | 1372 | 93295.141 | 272.733 | 4.56 | 4.64 | 4.82 | 4.37 | 4.58 | 3.93 | 4.78 | 4.86 | 4.99 | 4.6 | 4.76 | 4.01 | 673000 | 1000 | 633000 | 2000 | 1301201 | 5000 | 1303000 | 1296201 | 10.0167 | 4.4833 | 0.88667 | 4.6667 | 0.22167 | 19.78% | 4.75% | 30.7133 | 45.6967 | 2.165 | 10.7067 | 1310519.4 | 1299330 | 1560373 | 83.27% | 28 | 65899
2024-09-04 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 335090.89 | 7:52 | 19:02 | 5950.1 | 6269.2 | 6262.8 | 6244.2 | 6285.3 | 6232 | 6311.7 | 6483.2 | 6233.4 | 6288.2 | 6064.6 | 6202.4 | 6084.5 | 6107.4 | 6125.4 | 6128 | 6078 | 6168 | 6189.8 | 6193.1 | 6244.8 | 6236.6 | 6039.4 | 6144.7 | 5985.8 | 5239.3 | 6020.9 | 6022.7 | 6229.5 | 6132.3 | 6045.3 | 6184 | 6282.4 | 6217.5 | 6189.4 | 6147.9 | 6234 | 6138 | 6186.7 | 6227.3 | 6825.7 | 6090.7 | 6771.6 | 6000 | 6460.8 | 7301.7 | 5971.3 | 6821.2 | 6233.2 | 5940.6 | 6222.7 | 5849.6 | 6465.6 | 5739.7 | 6397.8 | 6377.9 | 5635.8 | 6585.9 | 5648 | 6509.5 | 6427.3 | 5660.7 | 6227.6 | 5916.9 | 6064.9 | 5718.7 | 6067 | 6408.7 | 6548.7 | 5898.1 | 6498.6 | 5694.9 | 6243 | 6162 | 5739.1 | 6493.4 | 5651.8 | 6575.2 | 5731.2 | 6453.8 | 5916.1 | 6371.7 | 6054.1 | 6697.4 | 5963 | 6394 | 5905 | 5187.3 | 6470.3 | 6145.7 | 5760.5 | 6754.2 | 6548.4 | 6057.8 | 6017.6 | 6683.7 | 6037.3 | 6231.7 | 6814.5 | 5990.1 | 6884.4 | 5975.6 | 6624 | 6105.3 | 6603.6 | 5695.9 | 6586.1 | 5876 | 6447.1 | 5767.5 | 6476.5 | 5907.9 | 6040.6 | 6602.3 | 5883 | 5854.6 | 6544.4 | 6549.8 | 6359.9 | 5811.3 | 6392.9 | 5686.8 | 6256.7 | 5803.7 | 5992.2 | 5312.5 | 6229 | 5733.9 | 5864.1 | 5942.7 | 5747.6 | 4984 | 5801.3 | 5209.6 | 6025.4 | 6031.8 | 6702.9 | 5818.8 | 6678.3 | 5919.4 | 6779.6 | 5998.1 | 6148.3 | 6100.4 | 6442.4 | 6675.6 | 6693.8 | 6622 | 6593.4 | 6624.4 | 5929.9 | 6605.9 | 6912.3 | 6561 | 6718.5 | 6752.9 | 6727.2 | 5953 | 6927.6 | 6062.8 | 23.3441 | 28.1528 | 28.3349 | 29.311 | 28.3738 | 28.3694 | 0 | 36.3 | 0 | 0 | 37.1 | 36.7384 | 2.1259 | 2.0141 | 0.1152 | 2.0695 | 2.1211 | 1.555 | 4.5283 | 3.98 | 3.71 | 3.9967 | 3.76 | 3.445 | 3.1839 | 3.2345 | 3.3044 | 3.2547 | 3.3779 | 3.2471 | 0.41052 | 0.4805 | 0.40815 | 0.5181 | 0.61319 | 0.53352 | 3.2002 | 3.2551 | 3.2567 | 3.2112 | 3.3452 | 3.2408 | 0.10122 | 0.12769 | 0.1183 | 0.11491 | 0.12544 | 0.12742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 725992 | 1316 | 712924 | 1373 | 94282.27 | 277.467 | 3.1839 | 3.2345 | 3.3044 | 3.2547 | 3.3779 | 3.2471 | 3.2002 | 3.2551 | 3.2567 | 3.2112 | 3.3452 | 3.2408 | 494000 | 2000 | 496000 | 1000 | 987129 | 4734 | 987000 | 982395 | 11.1667 | 3.2671 | 0.494 | 3.2515 | 0.11916 | 15.12% | 3.665% | 27.6477 | 36.7128 | 1.6668 | 3.9033 | 990639.6 | 986200 | 1137648 | 86.69% | 37 | 21613
2024-09-05 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 335090.89 | 6:51 | 19:04 | 8343 | 8945 | 9272 | 9279 | 9299 | 9200 | 9095 | 9271 | 8634 | 8565 | 8598 | 8603 | 8646 | 8572 | 8787 | 8716 | 8669 | 8539 | 8469 | 8641 | 8430 | 8495 | 8339 | 8339 | 8458 | 7706 | 8469 | 8457 | 8549 | 8539 | 8638 | 8613 | 9214 | 9146 | 9226 | 9121 | 8683 | 8677 | 8798 | 8725 | 9631 | 9131 | 9642 | 9036 | 9411 | 10183 | 8883 | 9677 | 8462 | 8646 | 8485 | 8055 | 8814 | 8206 | 8564 | 8716 | 7590 | 8673 | 7765 | 8462 | 8353 | 7661 | 7954 | 7475 | 8143 | 7850 | 8078 | 8456 | 8465 | 7743 | 8198 | 7357 | 7920 | 7766 | 7246 | 8068 | 7185 | 8052 | 7179 | 8013 | 8040 | 8248 | 8191 | 8825 | 8192 | 8589 | 8043 | 7382 | 8634 | 8275 | 7885 | 8812 | 8654 | 8120 | 8086 | 8750 | 7991 | 8082 | 8553 | 7709 | 8766 | 7733 | 8508 | 7865 | 8440 | 7555 | 8389 | 7787 | 8161 | 7677 | 8412 | 7953 | 7758 | 8532 | 7894 | 7840 | 8556 | 8858 | 8474 | 8313 | 8790 | 8150 | 8332 | 7894 | 8309 | 7712 | 8709 | 8421 | 8687 | 8761 | 8569 | 7715 | 8622 | 7815 | 8382 | 8388 | 10147 | 9110 | 10040 | 9170 | 9703 | 8705 | 8724 | 8515 | 9996 | 10201 | 10177 | 10210 | 10266 | 10260 | 9505 | 10184 | 9623 | 9640 | 9721 | 9800 | 9883 | 9239 | 9898 | 9280 | 27.57 | 30.61 | 31.01 | 32.08 | 30.75 | 30.98 | 0 | 43.8 | 0 | 0 | 45.6 | 46.7 | 2.26 | 2.17 | 1.51 | 1.96 | 2.21 | 1.45 | 4.37 | 4.57 | 4.8 | 4.69 | 4.53 | 4.42 | 5.1 | 4.95 | 5.43 | 4.77 | 4.94 | 5.91 | 0.78 | 0.73 | 0.84 | 0.94 | 1.09 | 1.01 | 5.35 | 5.19 | 5.61 | 5.03 | 5.15 | 6.11 | 0.17 | 0.21 | 0.23 | 0.19 | 0.22 | 0.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 726672 | 1318 | 713616 | 1375 | 95650.7 | 282.1 | 5.1 | 4.95 | 5.43 | 4.77 | 4.94 | 5.91 | 5.35 | 5.19 | 5.61 | 5.03 | 5.15 | 6.11 | 680000 | 2000 | 692000 | 2000 | 1368430 | 4633 | 1368000 | 1363797 | 12.2167 | 5.1833 | 0.89833 | 5.4067 | 0.21333 | 17.33% | 3.946% | 30.5 | 45.3667 | 1.9267 | 4.5633 | 1375744 | 704530 | 835401.4117 | 84.33% | 36 | 41631
2024-09-06 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 335090.89 | 7:09 | 19:01 | 10881.5 | 11511.3 | 11406.6 | 11365.6 | 11506.6 | 11553.7 | 11609.8 | 11813.4 | 11425.7 | 11190.8 | 11215.7 | 11394.9 | 11291.9 | 11231.8 | 11435.9 | 11471.2 | 11288.9 | 11299 | 11303 | 11434.9 | 11295.8 | 11331.6 | 11192.3 | 11257.4 | 11072.7 | 9754 | 11145.3 | 11075.3 | 11377.7 | 11316.7 | 11114.8 | 11341.3 | 11562.8 | 11590.7 | 11577.9 | 11466.5 | 11379.1 | 11205.1 | 11205.5 | 11213.1 | 12241.4 | 11337.3 | 12245.4 | 11107.3 | 11896 | 12904 | 11191.8 | 12193.8 | 11366.6 | 11617.1 | 11413.9 | 10796.4 | 11773.1 | 11150.2 | 11475.3 | 11499.3 | 10400.6 | 11699.8 | 10482.1 | 11676.4 | 11661.9 | 10566.4 | 11427.4 | 11064.6 | 10917.8 | 10452.4 | 10923 | 11487.3 | 11514 | 10706.6 | 11496.8 | 10330.3 | 11193.8 | 11173.8 | 10497 | 11603.6 | 10404.1 | 11746.8 | 10560.9 | 11597.8 | 10713.3 | 11380.1 | 10915.8 | 11835 | 10827.8 | 11417.8 | 10707.3 | 9349.7 | 11546.8 | 10995.6 | 10503.8 | 11934.1 | 11714.9 | 11024.9 | 10902.3 | 11754.3 | 10855.3 | 11191.1 | 11868.4 | 10737.8 | 11961.3 | 10702.6 | 11732.8 | 10984.6 | 11674.3 | 10291 | 11721.4 | 10808.8 | 11530.7 | 10799.9 | 11823.5 | 11039.4 | 10734.7 | 11639.3 | 10927.2 | 10674.3 | 11841.6 | 11895.2 | 11740.1 | 10828.4 | 11892.1 | 10723.7 | 11614.7 | 10907 | 11527 | 9978.7 | 11620 | 10747.5 | 10937.6 | 10961.6 | 10724.1 | 9325.5 | 10704.7 | 9445.2 | 10622.5 | 10632.6 | 12052 | 10846.1 | 12072.6 | 10989.8 | 12024.5 | 10814.3 | 10977.1 | 10750.8 | 11832 | 12028.4 | 12140.9 | 12041.6 | 11982 | 11986.1 | 11060.1 | 12014.4 | 12205.5 | 11960.1 | 12070.3 | 12120 | 12185 | 11154.1 | 12301.7 | 11273.7 | 29.1787 | 31.4997 | 31.7632 | 32.7196 | 31.5329 | 31.815 | 0 | 46.9 | 0 | 0 | 48 | 47.7 | 3.3262 | 3.4219 | 1.5413 | 3.2172 | 3.4605 | 3.2855 | 5.5333 | 5.8933 | 5.3883 | 5.305 | 5.35 | 5.99 | 6.1999 | 6.1982 | 6.4262 | 6.0485 | 6.355 | 6.3134 | 1.0563 | 1.067 | 0.99538 | 1.2614 | 1.5943 | 1.2365 | 6.5697 | 6.5826 | 6.6859 | 6.3697 | 6.6486 | 6.6242 | 0.24163 | 0.27388 | 0.26569 | 0.23186 | 0.28412 | 0.29169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 727573 | 1320 | 714514 | 1376 | 97442.608 | 286.8 | 6.1999 | 6.1982 | 6.4262 | 6.0485 | 6.355 | 6.3134 | 6.5697 | 6.5826 | 6.6859 | 6.3697 | 6.6486 | 6.6242 | 901000 | 2000 | 898000 | 1000 | 1791908 | 4700 | 1796000 | 1787208 | 11.8667 | 6.2568 | 1.2018 | 6.5801 | 0.26481 | 19.21% | 4.024% | 31.4182 | 47.5333 | 3.0421 | 5.5767 | 1804676.7 | 1791334 | 2189071.3502 | 81.83% | 28 | 3736
2024-09-07 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 335090.89 | 6:56 | 19:03 | 11586.3 | 12489.9 | 12516.2 | 12384.4 | 12689.3 | 12758.3 | 12734.1 | 13088 | 12307.2 | 11986.8 | 12234 | 12307.9 | 12529.6 | 12337.1 | 12749.5 | 12718.9 | 12698.6 | 12714.7 | 12706.1 | 12782.8 | 12554.7 | 12655.1 | 12264 | 12409.2 | 12253.2 | 10788.8 | 12377.4 | 12292.7 | 12588.2 | 12411.4 | 12236.1 | 12558.2 | 12491.4 | 12464.6 | 12609 | 12502.1 | 12649.3 | 12438.9 | 12455.3 | 12400.7 | 13227 | 12119.5 | 13064.2 | 11880.8 | 12507.1 | 13594.6 | 11753.4 | 13119.1 | 12552 | 12681.5 | 12670.6 | 11732.3 | 13099.5 | 12912.7 | 12598.3 | 12715.5 | 10962.2 | 12430.7 | 11274.8 | 12510.7 | 12252.7 | 11076.6 | 11689.2 | 10985.4 | 11339 | 10489.7 | 11259.4 | 11578.6 | 11982.3 | 10667.7 | 11744.4 | 10187.1 | 11544.1 | 11085.7 | 10591.1 | 11549.1 | 10193.9 | 11805.3 | 10337.4 | 11504.6 | 10484.2 | 11254.6 | 10735.8 | 11814.3 | 10732.6 | 11462.5 | 10769.5 | 9419.5 | 12037.9 | 11300.8 | 10973.1 | 12676.5 | 12461.8 | 11694.2 | 11632.5 | 12590.5 | 11354.4 | 11582.3 | 12672.6 | 11251.5 | 13124.5 | 11430.3 | 12891.6 | 11819.1 | 13014.3 | 11261.5 | 13079.1 | 11899.3 | 12806.7 | 11797 | 13036.9 | 12034.5 | 11206.1 | 12538.4 | 11706.2 | 11448.9 | 12981.3 | 13039.8 | 12915 | 11804.5 | 12975.6 | 11622.9 | 12814.6 | 11892.2 | 12565.9 | 10844.5 | 12663.7 | 11527.8 | 11835.1 | 11862.6 | 11578.7 | 10040.3 | 11517.8 | 10209.7 | 11561.2 | 11565.7 | 12650.3 | 11474.4 | 12869.1 | 11824.8 | 13064.2 | 11836.1 | 12021.2 | 11799.3 | 12398 | 12748.9 | 12437.1 | 12459.9 | 12434.9 | 12524.4 | 11680.4 | 12659.7 | 12419.4 | 12464.9 | 12550.3 | 12664.8 | 12716.8 | 11676.9 | 12452.1 | 11562.4 | 29.3 | 31.6052 | 31.9211 | 33.0178 | 32.2539 | 31.7469 | 0 | 47.3 | 0 | 0 | 47.3 | 47.7184 | 3.0922 | 3.0784 | 2.2749 | 2.9377 | 3.1115 | 1.5864 | 6.7317 | 5.445 | 4.8367 | 5.7367 | 5.1017 | 6.2067 | 6.7359 | 6.77 | 6.6823 | 6.1792 | 6.8546 | 6.4978 | 1.1907 | 1.1088 | 1.0247 | 1.3397 | 1.5725 | 1.1254 | 7.1337 | 7.1902 | 6.9957 | 6.5712 | 7.1939 | 6.7568 | 0.28729 | 0.32216 | 0.29035 | 0.26615 | 0.30727 | 0.30752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 728541 | 1322 | 715468 | 1378 | 99357.741 | 291.467 | 6.7359 | 6.77 | 6.6823 | 6.1792 | 6.8546 | 6.4978 | 7.1337 | 7.1902 | 6.9957 | 6.5712 | 7.1939 | 6.7568 | 968000 | 2000 | 954000 | 2000 | 1915133 | 4667 | 1918000 | 1910466 | 12.1167 | 6.62 | 1.227 | 6.9736 | 0.29679 | 18.53% | 4.256% | 31.6408 | 47.4395 | 2.6802 | 5.6764 | 1928194.5 | 1914466 | 2320880.6261 | 82.49% | 32 | 9793
2024-09-08 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 335090.89 | 6:58 | 19:01 | 9476.9 | 9900.9 | 9777.7 | 9781.2 | 9817.9 | 9836.2 | 9929.2 | 10176.2 | 8845.2 | 8699.3 | 8734.5 | 8840.5 | 8812.2 | 8766.2 | 8806.1 | 8858.6 | 9751.2 | 9818.9 | 9838.3 | 9924.1 | 9829.8 | 9863.2 | 9768.1 | 9804 | 9638.1 | 8899.9 | 9727.5 | 9647.5 | 9907.8 | 9867.2 | 9819.3 | 9867.1 | 11994.3 | 11884.6 | 11846.5 | 11816.5 | 9963.8 | 9932.5 | 9994 | 9907.5 | 10325.7 | 9585.1 | 10200.3 | 9471.6 | 9942.5 | 10736.9 | 9573.8 | 10371 | 9808.9 | 10069.6 | 9985.9 | 9608.7 | 10194.6 | 10064.2 | 10159 | 10065.1 | 9371.7 | 10292.5 | 9381 | 10235.8 | 10138.2 | 9354.4 | 9945.1 | 9590.8 | 9717.1 | 9305.4 | 9681.7 | 9979.3 | 10135.6 | 9420.7 | 10022.4 | 9164.6 | 9868.7 | 9694 | 9373.7 | 10011.4 | 9219.2 | 10177.8 | 9316.2 | 9972.6 | 9428.7 | 9811.2 | 9563.2 | 10216.3 | 9525.4 | 9926.1 | 9430.6 | 8667.8 | 10033.4 | 9663 | 9372.8 | 10273.8 | 9992.5 | 9529.1 | 9472.4 | 10078.3 | 9274.6 | 9399.6 | 9897.7 | 9107.7 | 10109.2 | 9188.1 | 9960.1 | 9364.3 | 9957.3 | 9041.8 | 9962.6 | 9229.6 | 9677.4 | 9200.2 | 9834.1 | 9286.8 | 9099.9 | 9674.3 | 9239.3 | 9080.9 | 9758.3 | 9720.5 | 9650.3 | 9053.3 | 9657.9 | 9014 | 9578.5 | 9148.5 | 9474.8 | 8739 | 9567.4 | 9079.1 | 9085.3 | 9034.9 | 9097.7 | 8283.5 | 8901.2 | 8219.8 | 8902.6 | 8924.2 | 9973.1 | 9115.5 | 9987.4 | 9203.9 | 9844.4 | 9006.9 | 9084.3 | 8984.7 | 9876.7 | 10033.9 | 10035 | 9978.3 | 9971.4 | 9967.2 | 9321 | 9959.1 | 10228.2 | 10187.9 | 10198 | 10148.2 | 10122.5 | 9391.3 | 10241 | 9454.7 | 30.3895 | 32.5487 | 32.8817 | 33.9242 | 33.1873 | 32.7824 | 0 | 46.8918 | 0 | 0 | 46.5 | 46.7893 | 3.0954 | 2.991 | 1.265 | 2.9241 | 3.144 | 2.0153 | 5.3867 | 5.445 | 4.9317 | 6.0883 | 5.6467 | 5.1533 | 6.4225 | 6.3371 | 6.4168 | 6.2547 | 6.2755 | 6.2127 | 1.2251 | 1.0888 | 1.0411 | 1.4305 | 1.5717 | 1.1428 | 6.8426 | 6.7709 | 6.7785 | 6.7295 | 6.6314 | 6.5103 | 0.28109 | 0.30717 | 0.28587 | 0.26756 | 0.30453 | 0.30515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 729325 | 1323 | 716229 | 1380 | 100897.941 | 296 | 6.4225 | 6.3371 | 6.4168 | 6.2547 | 6.2755 | 6.2127 | 6.8426 | 6.7709 | 6.7785 | 6.7295 | 6.6314 | 6.5103 | 784000 | 1000 | 761000 | 2000 | 1540200 | 4533 | 1542000 | 1535667 | 12.05 | 6.3199 | 1.25 | 6.7105 | 0.2919 | 19.78% | 4.35% | 32.619 | 46.727 | 2.5725 | 5.4419 | 1547678.8 | 819200 | 1003539.1544 | 81.63% | 25 | 17556
2024-09-09 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 335090.89 | 6:55 | 18:53 | 11460.5 | 12166.3 | 12059.9 | 12039 | 12109 | 12218.7 | 12285.8 | 12666.2 | 12119.4 | 11925.9 | 11941 | 12104.5 | 12140.3 | 12010.3 | 12263.9 | 12265.2 | 12166.1 | 12167.4 | 12213.2 | 12294 | 12107 | 12164 | 11879.7 | 12000.5 | 11884.3 | 10487.1 | 11930.8 | 11920.1 | 12185.1 | 12060.4 | 11908.7 | 12112.6 | 12137.3 | 12220.9 | 12366.9 | 12221.7 | 12222.2 | 12058.9 | 12101.9 | 11966 | 12924.6 | 11926.7 | 12841.2 | 11716.1 | 12406.2 | 13454.7 | 11643.5 | 12849.4 | 12079.7 | 12287.2 | 12158.1 | 11494.6 | 12545.8 | 12402.1 | 12393.6 | 12331 | 11074.4 | 12536.3 | 11054.2 | 12446.4 | 12337.3 | 11058.7 | 12012.2 | 11466.2 | 11756.3 | 10991.2 | 11657.3 | 12155 | 12326.7 | 11221.1 | 12195.4 | 10793 | 11908.3 | 11710.6 | 11031.4 | 12165.4 | 10808 | 12315.1 | 10934.5 | 12067.9 | 11284.4 | 11995.6 | 11551.4 | 12578.6 | 11456.7 | 12157 | 11374.8 | 9925.5 | 12279.4 | 11679.1 | 11085 | 12599.5 | 12222.9 | 11431.9 | 11310.3 | 12433.9 | 11308.3 | 11628.5 | 12464.2 | 11177.9 | 12632.7 | 11203.2 | 12426.9 | 11544.6 | 12520.2 | 10912.3 | 12599.9 | 11457.2 | 12470.7 | 11496.1 | 12617.3 | 11648.4 | 11204.7 | 12401.1 | 11488 | 11214.3 | 12447.1 | 12555.7 | 12343.6 | 11281.9 | 12378.3 | 11167.4 | 12263.4 | 11475 | 12157.7 | 10507.3 | 12109.7 | 11057.6 | 11386.2 | 11519.8 | 11069.3 | 9612.3 | 11261.8 | 10038.9 | 11338.5 | 11406.8 | 12780.7 | 11490.6 | 12721.9 | 11638.8 | 12778 | 11595.1 | 11809.5 | 11552.8 | 12422.6 | 12686.5 | 12736.3 | 12647.7 | 12674.4 | 12700.7 | 11737.3 | 12676.4 | 12988.7 | 12965.5 | 12945.6 | 12871.9 | 12867.7 | 11740.8 | 13003 | 11847.3 | 30.8583 | 33.266 | 33.7553 | 34.7842 | 34.0578 | 33.6164 | 0 | 47.9 | 0 | 0 | 48.6 | 48.1 | 3.0139 | 2.6043 | 1.2384 | 2.2873 | 3.067 | 1.1132 | 5.32 | 5.5083 | 5.2667 | 5.3267 | 5.7283 | 5.3933 | 6.5445 | 6.5375 | 6.5948 | 6.3748 | 6.6454 | 6.5419 | 1.2585 | 1.1613 | 1.0734 | 1.4643 | 1.6935 | 1.2506 | 6.9834 | 7.0125 | 6.9713 | 6.8695 | 7.0331 | 6.8989 | 0.29342 | 0.31867 | 0.30653 | 0.27318 | 0.31589 | 0.32306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 730292 | 1325 | 717177 | 1382 | 102796.341 | 300.667 | 6.5445 | 6.5375 | 6.5948 | 6.3748 | 6.6454 | 6.5419 | 6.9834 | 7.0125 | 6.9713 | 6.8695 | 7.0331 | 6.8989 | 967000 | 2000 | 948000 | 2000 | 1898400 | 4667 | 1911000 | 1893733 | 11.9667 | 6.5398 | 1.3169 | 6.9615 | 0.30512 | 20.14% | 4.383% | 33.3897 | 48.2 | 2.2207 | 5.4239 | 1911070.7 | 1897333 | 2295878.8327 | 82.64% | 31 | 0
2024-09-10 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 335090.89 | 6:55 | 18:54 | 10786 | 11465 | 11402 | 11336 | 11476 | 11577 | 11628 | 12020 | 11406 | 11280 | 11259 | 11405 | 11491 | 11376 | 11470 | 11533 | 11336 | 11387 | 11398 | 11526 | 11412 | 11406 | 11236 | 11347 | 11199 | 9911 | 11260 | 11203 | 11561 | 11441 | 11296 | 11530 | 11732 | 11791 | 11818 | 11718 | 11648 | 11473 | 11488 | 11370 | 12195 | 11143 | 12081 | 10922 | 11570 | 12621 | 10856 | 12166 | 11515 | 11714 | 11569 | 10933 | 11919 | 11734 | 11850 | 11759 | 10529 | 12024 | 10462 | 11923 | 11810 | 10439 | 11599 | 11052 | 11195 | 10434 | 11120 | 11567 | 11860 | 10656 | 11697 | 10237 | 11439 | 11136 | 10548 | 11677 | 10350 | 11899 | 10505 | 11670 | 10624 | 11349 | 10817 | 11927 | 10734 | 11443 | 10730 | 9377 | 11632 | 11092 | 10241 | 12053 | 11642 | 10830 | 10705 | 11833 | 10651 | 10942 | 11765 | 10475 | 11899 | 10432 | 11639 | 10730 | 11732 | 10130 | 11734 | 10647 | 11567 | 10560 | 11627 | 10723 | 10546 | 11599 | 10718 | 10492 | 11735 | 11815 | 11636 | 10636 | 11720 | 10542 | 11463 | 10674 | 11343 | 9848 | 11435 | 10465 | 10792 | 10861 | 10514 | 9159 | 10688 | 9483 | 10704 | 10717 | 12156 | 10807 | 12193 | 11015 | 12190 | 10943 | 11162 | 10885 | 11781 | 12126 | 12074 | 12008 | 12032 | 12079 | 11097 | 12104 | 12026 | 12089 | 12188 | 12143 | 12133 | 11030 | 12149 | 11038 | 30.52 | 32.92 | 33.36 | 34.6 | 33.48 | 33.24 | 0 | 48.3 | 0 | 0 | 49.3 | 49.2 | 2.65 | 1.93 | 0.71 | 2.02 | 2.76 | 1.67 | 5.59 | 5.49 | 5.11 | 4.72 | 5.23 | 5.31 | 6.2 | 6.23 | 6.22 | 6.16 | 6.22 | 6.22 | 1.17 | 1.12 | 1.01 | 1.4 | 1.58 | 1.2 | 6.66 | 6.71 | 6.6 | 6.66 | 6.6 | 6.6 | 0.28 | 0.3 | 0.3 | 0.26 | 0.3 | 0.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 731189 | 1326 | 718069 | 1382 | 104590.3 | 305.3 | 6.2 | 6.23 | 6.22 | 6.16 | 6.22 | 6.22 | 6.66 | 6.71 | 6.6 | 6.66 | 6.6 | 6.6 | 897000 | 1000 | 892000 | 0 | 1793959 | 4633 | 1788000 | 1789326 | 11.9833 | 6.2083 | 1.2467 | 6.6383 | 0.29167 | 20.08% | 4.394% | 33.02 | 48.9333 | 1.9567 | 5.2417 | 1806087 | 1792800 | 2193832 | 81.72% | 27 | 4768
2024-09-11 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 335090.89 | 6:58 | 18:52 | 9536.7 | 10049.9 | 9975.4 | 9976.3 | 10022.7 | 10087.6 | 10096.7 | 10404.2 | 9999.5 | 9841.4 | 9836.1 | 9968.8 | 10012.3 | 9939.6 | 10108.9 | 10111.6 | 10049.7 | 10121.3 | 10122.4 | 10175.5 | 10164.3 | 10160.1 | 10104.2 | 10130.2 | 9962.3 | 9009.6 | 9951.4 | 9966.7 | 10276.8 | 10293.5 | 10207.6 | 10302 | 10775.5 | 10745 | 10661.3 | 10650.9 | 10423.9 | 10347.5 | 10397.2 | 10346.4 | 10875.3 | 9955.1 | 10706.9 | 9765.3 | 10329.6 | 11273.1 | 9867 | 10865.8 | 10103.9 | 10264.4 | 10076.1 | 9541.7 | 10434.4 | 10272.3 | 10377.1 | 10322 | 9400.3 | 10534 | 9345.5 | 10439.8 | 10331.5 | 9321.2 | 10146.4 | 9686.6 | 9880.2 | 9407.8 | 9863 | 10245 | 10409.5 | 9560.8 | 10282.3 | 9242.2 | 10044.5 | 9842.1 | 9385.5 | 10208.8 | 9228.7 | 10350.2 | 9324 | 10097.4 | 9585 | 10046 | 9764.5 | 10586.4 | 9703.3 | 10203.5 | 9623.1 | 8605.9 | 10383.2 | 9974.3 | 9544 | 10702 | 10425.8 | 9895.7 | 9849.8 | 10580.3 | 9814.5 | 10004.4 | 10718.2 | 9685.6 | 10824.5 | 9707 | 10590.6 | 9900.9 | 10632.2 | 9460.3 | 10643.9 | 9777 | 10538.5 | 9785.9 | 10631.1 | 9927.5 | 9691.1 | 10424.4 | 9795.8 | 9636.1 | 10528.9 | 10597.5 | 10441.5 | 9731 | 10537.7 | 9649.2 | 10342.4 | 9767.9 | 10242.3 | 9177.6 | 10338.1 | 9656.1 | 9816.4 | 9805.9 | 9697.2 | 8537 | 9672.1 | 8751.6 | 9558 | 9539.8 | 10707.2 | 9618.5 | 10709.2 | 9803.7 | 10664.7 | 9718.7 | 9824.2 | 9652.4 | 10416.9 | 10679 | 10661 | 10607.2 | 10635.4 | 10668.7 | 9867.7 | 10644.1 | 10407.9 | 10502.7 | 10455.1 | 10526.5 | 10594 | 9778.5 | 10684.7 | 9816.1 | 31.27 | 31.27 | 31.46 | 31.91 | 31.82 | 31.45 | 0 | 42.8 | 0 | 0 | 43.4 | 43.21 | 3.56 | 3.32 | 2.11 | 3.17 | 3.62 | 2.94 | 9.41 | 9.33 | 8.66 | 9.52 | 10.41 | 9.29 | 5.44 | 5.59 | 5.64 | 5.44 | 5.66 | 5.6 | 1.06 | 1 | 0.95 | 1.25 | 1.42 | 1.06 | 5.82 | 5.99 | 5.95 | 5.87 | 5.99 | 5.89 | 0.25 | 0.28 | 0.27 | 0.24 | 0.28 | 0.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 731994 | 1329 | 718873 | 1384 | 106192.275 | 309.8 | 5.44 | 5.59 | 5.64 | 5.44 | 5.66 | 5.6 | 5.82 | 5.99 | 5.95 | 5.87 | 5.99 | 5.89 | 805000 | 3000 | 804000 | 2000 | 1601975 | 4500 | 1604000 | 1597475 | 11.9 | 5.5617 | 1.1233 | 5.9183 | 0.26667 | 20.2% | 4.506% | 31.53 | 43.1367 | 3.12 | 9.4367 | 1612614.9 | 1148000 | 1366127 | 84.03% | 32 | 90490
2024-09-12 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 335090.89 | 6:51 | 18:55 | 11137 | 11812.5 | 11584.6 | 11551.6 | 11638.6 | 11727 | 11863.2 | 12248.6 | 11791.7 | 11693.6 | 11605.8 | 11790.7 | 11709.4 | 11695.3 | 11708.2 | 11754.4 | 11613.8 | 11705.9 | 11750.1 | 11850.7 | 11771.2 | 11783.3 | 11576 | 11676.3 | 11649.4 | 10260.8 | 11626.8 | 11632 | 11951.4 | 11856.8 | 11735.3 | 11943.1 | 12151.9 | 12139.5 | 12120.7 | 12039.7 | 12137.4 | 11961 | 12002.2 | 11974.3 | 12299.4 | 11238.7 | 12270.8 | 11062.1 | 11881.3 | 13015.7 | 11145 | 12329.2 | 11905.2 | 12146.1 | 11932 | 11400.5 | 12286.7 | 12048.5 | 12369.5 | 12228.1 | 11055.3 | 12633.1 | 10881 | 12523.5 | 12394.3 | 10873.4 | 12243.4 | 11662.3 | 11739.7 | 10901.1 | 11625.6 | 12083.2 | 12430.9 | 11138.3 | 12228.9 | 10687 | 12008.2 | 11634.2 | 11062.7 | 12204.7 | 10804.8 | 12502.2 | 11036.5 | 12209.5 | 11043.6 | 11789.6 | 11202.2 | 12402 | 11127.7 | 11836.4 | 11178.5 | 9683.1 | 12149.9 | 11536.1 | 10986.3 | 12621.1 | 12253 | 11452 | 11352.1 | 12381.8 | 11157.2 | 11472.5 | 12377.7 | 10950.6 | 12506.1 | 10987.7 | 12226.5 | 11276.4 | 12290.8 | 10677.5 | 12361.3 | 11159.9 | 12223.8 | 11186.3 | 12339.8 | 11370.3 | 10948.1 | 12032 | 11157 | 10905.5 | 12179.6 | 12263.5 | 12091.1 | 11047.5 | 12202 | 10963.8 | 11976.5 | 11150.6 | 11858.9 | 10312.2 | 11955.3 | 10942 | 11112 | 11144.6 | 11006.7 | 9486.6 | 10852.5 | 9549 | 10613.1 | 10629.5 | 12065.9 | 10684.4 | 12007.9 | 10868.1 | 12001.6 | 10800.6 | 11000.8 | 10813 | 11681.3 | 11966.4 | 12009.9 | 11945.3 | 12011.8 | 12018.1 | 10921.7 | 11901.1 | 12058 | 12027.5 | 11984.5 | 11955 | 11971.2 | 10894 | 12209.8 | 10995 | 31.2155 | 32.749 | 32.8431 | 33.6634 | 33.2265 | 32.9716 | 0 | 45.4 | 0 | 0 | 45.4 | 44.8 | 5.2847 | 5.3 | 4.6955 | 5.0386 | 5.3268 | 5.1659 | 7.895 | 7.9433 | 7.2533 | 7.815 | 7.9383 | 7.4833 | 6.2069 | 6.3007 | 6.1988 | 6.3011 | 6.3056 | 6.0164 | 1.1681 | 1.1147 | 1.0174 | 1.3935 | 1.5436 | 1.1041 | 6.6945 | 6.7894 | 6.5815 | 6.7869 | 6.701 | 6.3662 | 0.27157 | 0.30252 | 0.28094 | 0.25784 | 0.28722 | 0.27607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 732933 | 1330 | 719789 | 1385 | 108040.742 | 314.267 | 6.2069 | 6.3007 | 6.1988 | 6.3011 | 6.3056 | 6.0164 | 6.6945 | 6.7894 | 6.5815 | 6.7869 | 6.701 | 6.3662 | 939000 | 1000 | 916000 | 1000 | 1848467 | 4467 | 1853000 | 1844000 | 12.0667 | 6.2216 | 1.2235 | 6.6533 | 0.27936 | 19.67% | 4.199% | 32.7782 | 45.2 | 5.1352 | 7.7214 | 1861076.7 | 1848000 | 2222940.2652 | 83.13% | 32 | 0
2024-09-13 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 335090.89 | 6:53 | 18:51 | 10513.4 | 10827.3 | 10723.7 | 10718.1 | 10731.5 | 10734.7 | 10827.3 | 11057.8 | 10810.9 | 10884.2 | 10626 | 10741.7 | 10626.5 | 10651.5 | 10585.1 | 10605.3 | 10458.5 | 10487.3 | 10472.1 | 10605.3 | 10468.9 | 10508.6 | 10386.5 | 10410.2 | 10275.5 | 9532.4 | 10387.9 | 10309 | 10484.3 | 10472.2 | 10383.9 | 10444.8 | 11189.6 | 11216.7 | 11269.8 | 11167.8 | 10530.6 | 10437.8 | 10488.5 | 10411.9 | 11286.1 | 10612.5 | 11212.1 | 10521.6 | 10991.2 | 11708.8 | 10468.6 | 11276.1 | 10748.2 | 10940.8 | 10743.9 | 10405.6 | 10924.8 | 10770 | 10976.8 | 10839.1 | 10228.2 | 11214.3 | 10236.1 | 11115.6 | 11074.9 | 10191.9 | 11042.9 | 10700.9 | 10734.5 | 10343.1 | 10755.2 | 11062.9 | 11222.6 | 10504.9 | 11124.6 | 10288.1 | 10947.4 | 10838.9 | 10408.4 | 11166.6 | 10351.4 | 11248 | 10470.3 | 11204.4 | 10533.2 | 10943.3 | 10663.1 | 11347 | 10592.4 | 11032.9 | 10486.2 | 9587.5 | 11010.5 | 10708.6 | 10157.8 | 11130.1 | 10794.8 | 10262.4 | 10149.9 | 10909.4 | 10166.3 | 10407.7 | 10890.3 | 10036 | 10897.8 | 9988.9 | 10718.5 | 10189.1 | 10715.3 | 9777.7 | 10811.5 | 10066.2 | 10751.6 | 10122.2 | 10833.1 | 10271 | 10109.2 | 10733.8 | 10119.3 | 10016.7 | 10751.7 | 10833.1 | 10687.6 | 10096.2 | 10753 | 10021 | 10575.5 | 10104.4 | 10535.1 | 9622.9 | 10622 | 10047.2 | 10229.8 | 10269 | 10108.3 | 9069.1 | 10178.8 | 9453 | 10677.2 | 10685 | 11597.7 | 10639.9 | 11676.5 | 10796.4 | 11600.7 | 10732 | 10865 | 10774.7 | 11420.7 | 11580.2 | 11609.1 | 11584.6 | 11605.1 | 11615.2 | 10914.5 | 11614.4 | 11601.4 | 11626.1 | 11644.9 | 11620.4 | 11644.1 | 10864.1 | 11674.6 | 10893.4 | 31.25 | 30.35 | 30.51 | 30.51 | 30.21 | 30.7 | 0 | 41.6 | 0 | 0 | 42.9 | 43 | 7.29 | 7.5 | 7.01 | 7.01 | 7.23 | 7.63 | 10.59 | 11.73 | 10.99 | 10.99 | 10.45 | 10.78 | 6.11 | 5.93 | 6.19 | 6.19 | 6.02 | 6.38 | 1.21 | 1.1 | 1.08 | 1.08 | 1.52 | 1.32 | 6.56 | 6.36 | 6.56 | 6.56 | 6.38 | 6.75 | 0.3 | 0.32 | 0.32 | 0.32 | 0.32 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 733788 | 1332 | 720642 | 1387 | 109742.609 | 318.2 | 6.11 | 5.93 | 6.19 | 6.19 | 6.02 | 6.38 | 6.56 | 6.36 | 6.56 | 6.56 | 6.38 | 6.75 | 855000 | 2000 | 853000 | 2000 | 1701867 | 3933 | 1704000 | 1697934 | 11.9667 | 6.1367 | 1.2183 | 6.5283 | 0.31833 | 19.85% | 4.876% | 30.5883 | 42.5 | 7.2783 | 10.9217 | 1712814.3 | 767733 | 924230.8727 | 83.07% | 31 | 2159
2024-09-14 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 335090.89 | 6:57 | 18:48 | 10481 | 11006 | 10948 | 10901 | 10992 | 11011 | 11045 | 11298 | 10919 | 10726 | 10773 | 10897 | 10901 | 10817 | 10829 | 10874 | 10656 | 10647 | 10703 | 10878 | 10621 | 10695 | 10529 | 10553 | 10450 | 9679 | 10615 | 10508 | 10635 | 10590 | 10492 | 10595 | 11096 | 11146 | 11207 | 11098 | 10680 | 10555 | 10600 | 10538 | 11389 | 10688 | 11296 | 10538 | 10998 | 11567 | 10305 | 11218 | 10921 | 11115 | 10960 | 10521 | 11159 | 11022 | 11134 | 11053 | 10245 | 11274 | 10295 | 11224 | 11172 | 10264 | 10941 | 10527 | 10620 | 10063 | 10563 | 10833 | 11112 | 10267 | 10960 | 9986 | 10800 | 10565 | 10199 | 10891 | 10022 | 11065 | 10176 | 10966 | 10236 | 10651 | 10371 | 11106 | 10284 | 10745 | 10228 | 9251 | 11017 | 10529 | 10176 | 11205 | 10878 | 10332 | 10202 | 10955 | 10183 | 10423 | 10926 | 10056 | 10930 | 10049 | 10744 | 10230 | 10727 | 9764 | 10781 | 10037 | 10664 | 10018 | 10686 | 10161 | 10107 | 10780 | 10156 | 10061 | 10785 | 10878 | 10708 | 10100 | 10746 | 9979 | 10532 | 10028 | 10441 | 9515 | 10568 | 9950 | 10242 | 10292 | 9987 | 9006 | 10153 | 9334 | 10327 | 10332 | 11133 | 10240 | 11087 | 10345 | 11156 | 10301 | 10468 | 10376 | 10768 | 10871 | 10987 | 10962 | 11043 | 11102 | 10334 | 10957 | 10884 | 10899 | 10975 | 10947 | 10919 | 10236 | 11002 | 10281 | 31.28 | 29.54 | 29.71 | 30.39 | 29.36 | 29.75 | 0 | 41.55 | 0 | 0 | 42.4 | 42.24 | 6.23 | 6.52 | 5.98 | 6.55 | 6.18 | 6.59 | 10.96 | 10.15 | 10.76 | 10.09 | 10.02 | 10.95 | 6.11 | 5.98 | 6.1 | 6 | 6.03 | 6 | 1.17 | 1.21 | 1.04 | 1.36 | 1.57 | 1.36 | 6.57 | 6.41 | 6.46 | 6.42 | 6.37 | 6.4 | 0.31 | 0.33 | 0.32 | 0.29 | 0.33 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 734646 | 1333 | 721476 | 1388 | 111428.3 | 322.7 | 6.11 | 5.98 | 6.1 | 6 | 6.03 | 6 | 6.57 | 6.41 | 6.46 | 6.42 | 6.37 | 6.4 | 858000 | 1000 | 834000 | 1000 | 1685691 | 4500 | 1690000 | 1681191 | 11.85 | 6.0367 | 1.285 | 6.4383 | 0.31833 | 21.29% | 4.944% | 30.005 | 42.0633 | 6.3417 | 10.4883 | 1698923 | 753200 | 922258.7471 | 81.67% | 25 | 2704
2024-09-15 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 335090.89 | 6:52 | 18:49 | 10252 | 10827.4 | 10829.4 | 10775.5 | 10928.1 | 10997.4 | 10938.8 | 11285.6 | 10698.5 | 10504.6 | 10612 | 10688 | 10979.3 | 10718.8 | 11059.5 | 11030.3 | 10976.8 | 11044.5 | 10983.4 | 11119.9 | 11016.6 | 11059.4 | 10911.6 | 10956.2 | 10822.8 | 9913.4 | 10874.6 | 10851.4 | 11046.6 | 11001.7 | 10909 | 11006.9 | 11500.3 | 11492.2 | 11676.8 | 11555.5 | 11105 | 10971.5 | 11026.8 | 10908.3 | 11186.1 | 10348.2 | 11080.2 | 10200.4 | 10860.9 | 11729.9 | 10429.2 | 11342.6 | 10811 | 10985.3 | 10924.9 | 10382 | 11207.8 | 11137.3 | 10993.6 | 10980.4 | 10446.5 | 11654.8 | 10489.8 | 11581.2 | 11455.2 | 10445.8 | 11264 | 10838.8 | 11063.5 | 10354.4 | 10957.8 | 11279.7 | 11544 | 10586 | 11349.2 | 10185 | 11173 | 10934 | 10436.6 | 11282.9 | 10201.7 | 11496.1 | 10471.5 | 11422.7 | 10237.5 | 10716.6 | 10382.7 | 11151.2 | 10340.1 | 10833.2 | 10195.3 | 9249.4 | 10994.5 | 10545.7 | 10158.8 | 11275.6 | 10962.3 | 10417.6 | 10339.2 | 11062.8 | 10243.1 | 10547.8 | 11093.7 | 10194 | 11130.1 | 10126.5 | 10913.1 | 10322.2 | 10955.7 | 9850.3 | 11017.4 | 10156.8 | 10906.5 | 10183.4 | 10957.7 | 10331.8 | 10277.1 | 10851.9 | 10299.2 | 10218.9 | 10981.5 | 11145.8 | 10901.3 | 10342 | 11006 | 10210.9 | 10710.3 | 10167.9 | 10641 | 9707.6 | 10832 | 10203.4 | 10575.8 | 10666.2 | 10281.1 | 9271.7 | 10527.2 | 9520.3 | 10281.3 | 10267.8 | 11174.6 | 10191.6 | 11088.3 | 10325.5 | 11222 | 10316.4 | 10481 | 10355 | 10511.9 | 10524.2 | 11074.7 | 11011 | 11021.2 | 11070.9 | 10247.1 | 10999.9 | 11132.1 | 11155.6 | 11213.5 | 11190.2 | 11188.7 | 10390.7 | 11133.7 | 10386.6 | 31.25 | 29.39 | 29.7 | 30.44 | 29.27 | 29.62 | 0 | 43.9 | 0 | 0 | 44.3 | 43.7 | 4.05 | 3.86 | 3.64 | 3.89 | 4.12 | 4.05 | 7.14 | 7.35 | 7.14 | 6.71 | 7.02 | 7.08 | 6.14 | 6.27 | 6.09 | 6.03 | 6.22 | 6.01 | 1.2 | 1.28 | 1.05 | 1.39 | 1.61 | 1.33 | 6.62 | 6.73 | 6.44 | 6.49 | 6.6 | 6.4 | 0.31 | 0.35 | 0.32 | 0.3 | 0.35 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 735518 | 1335 | 722314 | 1389 | 113129.342 | 326.667 | 6.14 | 6.27 | 6.09 | 6.03 | 6.22 | 6.01 | 6.62 | 6.73 | 6.44 | 6.49 | 6.6 | 6.4 | 872000 | 2000 | 838000 | 1000 | 1701042 | 3967 | 1707000 | 1697075 | 11.95 | 6.1267 | 1.31 | 6.5467 | 0.32667 | 21.38% | 4.99% | 29.945 | 43.9667 | 3.935 | 7.0733 | 1722457.6 | 470934 | 561185.1318 | 83.92% | 30 | 890
2024-09-16 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 335090.89 | 6:51 | 18:44 | 10967 | 11296 | 11253 | 11185 | 11444 | 11557 | 11378 | 11726 | 11242 | 11261 | 11069 | 11154 | 11529 | 11206 | 11446 | 11605 | 11259 | 11286 | 11351 | 11572 | 11273 | 11353 | 11182 | 11236 | 11184 | 10428 | 11350 | 11219 | 11327 | 11259 | 11190 | 11291 | 12175 | 12256 | 12314 | 12180 | 11387 | 11250 | 11285 | 11215 | 12048 | 11161 | 11920 | 10957 | 11697 | 12460 | 11271 | 12178 | 11342 | 11477 | 11499 | 11012 | 11856 | 11713 | 11595 | 11579 | 10649 | 11610 | 10672 | 11541 | 11505 | 10622 | 11474 | 11168 | 11043 | 10580 | 11050 | 11369 | 11559 | 10860 | 11510 | 10668 | 11296 | 11206 | 10801 | 11561 | 10739 | 11719 | 10904 | 11646 | 10925 | 11507 | 11060 | 11715 | 10911 | 11323 | 10333 | 9473 | 11380 | 11053 | 10720 | 11766 | 11545 | 11024 | 10886 | 11586 | 10763 | 11037 | 11592 | 10707 | 11659 | 10710 | 11454 | 10911 | 11477 | 10397 | 11453 | 10779 | 11513 | 10822 | 11618 | 11039 | 10728 | 11312 | 10639 | 10566 | 11420 | 11517 | 11373 | 10803 | 11476 | 10758 | 11308 | 10859 | 11132 | 10329 | 11353 | 10753 | 10920 | 10953 | 10794 | 9760 | 10875 | 9908 | 10680 | 10875 | 11984 | 11006 | 12034 | 11133 | 11871 | 11017 | 11132 | 11022 | 7279 | 7280 | 11968 | 11946 | 12025 | 12017 | 11316 | 12004 | 11969 | 11996 | 12091 | 12033 | 12010 | 11231 | 11972 | 11233 | 31.24 | 29.52 | 29.94 | 30.37 | 29.3 | 29.76 | 0 | 43.95 | 0 | 0 | 45.2 | 45 | 3.87 | 3.81 | 2.95 | 3.9 | 4.11 | 3.68 | 6.9 | 7.79 | 7.11 | 7.07 | 7.26 | 6.34 | 6.34 | 6.33 | 6.57 | 6.25 | 6.38 | 6.52 | 1.24 | 1.31 | 1.15 | 1.44 | 1.67 | 1.45 | 6.89 | 6.92 | 7.01 | 6.8 | 6.83 | 6.98 | 0.3 | 0.33 | 0.33 | 0.29 | 0.33 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 736423 | 1336 | 723199 | 1391 | 114913.7 | 330.9 | 6.34 | 6.33 | 6.57 | 6.25 | 6.38 | 6.52 | 6.89 | 6.92 | 7.01 | 6.8 | 6.83 | 6.98 | 905000 | 1000 | 885000 | 2000 | 1784358 | 4233 | 1787000 | 1780125 | 11.8833 | 6.3983 | 1.3767 | 6.905 | 0.31833 | 21.52% | 4.61% | 30.0217 | 44.7167 | 3.72 | 7.0783 | 1796455 | 306667 | 386479 | 79.35% | 25 | 0
2024-09-17 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 335090.89 | 6:51 | 18:46 | 11098.9 | 11532.2 | 11436 | 11430.7 | 11492.8 | 11555.8 | 11560.1 | 11786 | 11444.7 | 11301.6 | 11322.2 | 11429.4 | 11500.2 | 11380 | 11538.7 | 11554.3 | 11441.6 | 11497.7 | 11472.7 | 11577.8 | 11476.9 | 11535.7 | 11407.7 | 11452.2 | 11321.4 | 10526.6 | 11343.3 | 11338.9 | 11527.5 | 11447.6 | 11389.1 | 11454.5 | 12542.6 | 12575.5 | 12558.5 | 12471.9 | 11578 | 11470.6 | 11487.6 | 11434.1 | 11988.3 | 11346.6 | 11873.6 | 11235.2 | 11609.4 | 12339.1 | 11160.6 | 11980.5 | 11284.4 | 11606.6 | 11558.7 | 11191.8 | 11657.3 | 11600.8 | 11713.3 | 11516.6 | 11001.9 | 11870.5 | 11006.8 | 11841.3 | 11681.4 | 10954.5 | 11589.8 | 11259.4 | 11334.8 | 10861.4 | 11283.2 | 11541.6 | 11725.7 | 11025.5 | 11625 | 10804.9 | 11459.1 | 11288 | 10977.3 | 11504.6 | 10845.3 | 11768.3 | 10996.4 | 11651.6 | 11134.3 | 11578.8 | 11164.3 | 11840.8 | 11105.3 | 11495.6 | 11053.5 | 10165.9 | 11479.2 | 11334.3 | 10989.6 | 11906.8 | 11655.9 | 11197.1 | 11090.8 | 11717.8 | 10932.6 | 11253.4 | 11741.1 | 10969.2 | 11845.8 | 10986.4 | 11684.6 | 11192.5 | 11659.8 | 10705.8 | 11649.2 | 11075.6 | 11676.3 | 11009.6 | 11733.8 | 11261.9 | 10982 | 11540.3 | 11052.9 | 10946.4 | 11613.7 | 11757.1 | 11617.7 | 11089.9 | 11707.8 | 11047.9 | 11524.7 | 11103 | 11428.4 | 10636 | 11578.3 | 11070.8 | 11175 | 11175.4 | 11063.7 | 9986.4 | 11046.9 | 10208.8 | 11093.1 | 11108.3 | 12001.3 | 11125.9 | 12000.9 | 11252.7 | 11958.2 | 11177.6 | 11287 | 11199.2 | 7817.4 | 7834.5 | 12030.9 | 11959.1 | 11988.7 | 11995.6 | 11319.5 | 11970.3 | 12012.2 | 12031.8 | 12041.7 | 12021.1 | 12040.2 | 11347.1 | 12080.9 | 11375.7 | 31.25 | 30.97 | 31.52 | 32.02 | 30.95 | 31.34 | 0 | 45.91 | 0 | 0 | 47.1 | 46.8 | 3.22 | 2.34 | 1.78 | 3.2 | 3.32 | 2.86 | 6.88 | 6.99 | 6.54 | 6.89 | 7 | 7.64 | 6.48 | 6.49 | 6.54 | 6.45 | 6.55 | 6.58 | 1.28 | 1.33 | 1.14 | 1.49 | 1.69 | 1.45 | 7.07 | 7.08 | 7.03 | 7.04 | 7.06 | 7.11 | 0.29 | 0.32 | 0.31 | 0.28 | 0.32 | 0.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 737338 | 1338 | 724099 | 1393 | 116721.9 | 334.667 | 6.48 | 6.49 | 6.54 | 6.45 | 6.55 | 6.58 | 7.07 | 7.08 | 7.03 | 7.04 | 7.06 | 7.11 | 915000 | 2000 | 900000 | 2000 | 1808200 | 3767 | 1811000 | 1804433 | 11.9167 | 6.515 | 1.3967 | 7.065 | 0.30667 | 21.44% | 4.341% | 31.3417 | 46.6033 | 2.7867 | 6.99 | 1822966.3 | 742600 | 898744 | 82.63% | 28 | 876
2024-09-18 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 335090.89 | 6:53 | 18:44 | 10979.9 | 11851 | 11956.7 | 11869.5 | 12099.7 | 12187.7 | 12093.1 | 12466.6 | 11667.2 | 11399.4 | 11524.6 | 11632.7 | 11894.8 | 11668.2 | 11942.4 | 11997.9 | 11775 | 11770.4 | 11633.8 | 11802.1 | 11561 | 11607.3 | 11375 | 11473.9 | 11462.6 | 10091.6 | 11463.8 | 11416.1 | 11745.8 | 11642 | 11522.5 | 11775.8 | 11943.2 | 11998.7 | 11924.3 | 11844 | 11988.6 | 11760.8 | 11745.8 | 11697.3 | 12773.4 | 11626.5 | 12680.9 | 11431.8 | 12142.4 | 13102.5 | 11293.9 | 12708 | 11579.5 | 11826.6 | 11789 | 11040.6 | 12052.8 | 12035.3 | 12078.7 | 11951 | 10670.5 | 12251 | 10545.2 | 12027.1 | 11906.5 | 10540.3 | 11789.7 | 11246.1 | 11534.6 | 10758.2 | 11383.5 | 12088.2 | 12150.7 | 11037 | 11979.6 | 10575.1 | 11672.1 | 11383.8 | 10766.3 | 11922.3 | 10501.9 | 12155.3 | 10675.8 | 11883 | 11338.7 | 12195.2 | 11409.2 | 12669.3 | 11317.5 | 12052.8 | 11380.4 | 9982.6 | 12302.9 | 11883.2 | 11173.6 | 12777.1 | 12306.7 | 11429.1 | 11275.3 | 12433.9 | 11183.1 | 11608.6 | 12516.5 | 11113.4 | 12626.3 | 11048.6 | 12298.7 | 11334.1 | 12387.5 | 10720 | 12439.8 | 11224.1 | 12259.1 | 11192 | 12379.9 | 11337 | 11160.9 | 12297.4 | 11275.6 | 11062.3 | 12326.8 | 12467.9 | 12181.6 | 11156.3 | 12289.1 | 10996.8 | 11950.9 | 11055.4 | 11717.7 | 10216.8 | 11961.7 | 11017.1 | 11323.4 | 11312.5 | 11098.5 | 9632.1 | 11030.7 | 9686.6 | 10598.5 | 10568.8 | 11604.1 | 10309 | 11579.8 | 10526.7 | 11817 | 10620.6 | 10868.2 | 10690.7 | 11084.1 | 11375.8 | 11496.2 | 11376.6 | 11382.4 | 11463.9 | 10370 | 11311 | 11798.1 | 11746.8 | 11729.6 | 11575.9 | 11547.5 | 10410.1 | 11765.5 | 10535.8 | 31.2548 | 31.9249 | 32.2058 | 33.635 | 32.4764 | 32.0899 | 0 | 46.6 | 0 | 0 | 47.3 | 45.7 | 2.2905 | 1.7466 | 0.44389 | 1.5098 | 2.3332 | 0.46097 | 4.715 | 4.5433 | 4.4117 | 4.5817 | 4.66 | 3.4833 | 6.1809 | 6.1045 | 6.3061 | 6.1593 | 6.3766 | 5.6289 | 1.1727 | 1.2387 | 1.0815 | 1.4037 | 1.6139 | 1.192 | 6.7712 | 6.6891 | 6.8073 | 6.7469 | 6.8938 | 6.0647 | 0.28115 | 0.30061 | 0.29926 | 0.27196 | 0.30375 | 0.27518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 738269 | 1339 | 725011 | 1394 | 118558.609 | 339.533 | 6.1809 | 6.1045 | 6.3061 | 6.1593 | 6.3766 | 5.6289 | 6.7712 | 6.6891 | 6.8073 | 6.7469 | 6.8938 | 6.0647 | 931000 | 1000 | 912000 | 1000 | 1836709 | 4866 | 1841000 | 1831843 | 11.85 | 6.1261 | 1.2837 | 6.6622 | 0.28865 | 20.96% | 4.333% | 32.2645 | 46.5333 | 1.4641 | 4.3992 | 1848776.5 | 1835933 | 2206536.3715 | 83.2% | 28 | 0
2024-09-19 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 335090.89 | 7:00 | 18:42 | 10062.8 | 10641.2 | 10563.7 | 10555 | 10613.3 | 10650.6 | 10686 | 10980.2 | 10540.3 | 10447.3 | 10328.2 | 10481.4 | 10510.6 | 10410.9 | 10632.1 | 10651.6 | 10502.8 | 10577.7 | 10539.9 | 10629.5 | 10644.9 | 10634.4 | 10541.9 | 10596.2 | 10439.5 | 9161 | 10349.2 | 10404.1 | 10779.6 | 10757 | 10631.3 | 10767.7 | 10848 | 10845.2 | 10762.6 | 10731.7 | 10891.3 | 10748 | 10768.5 | 10658.7 | 11313.2 | 10336.4 | 11190.8 | 10179.5 | 10730.3 | 11732 | 10167.1 | 11378.5 | 10366.6 | 10540.1 | 10477.3 | 9921.8 | 10821 | 10567.8 | 10767.2 | 10643.9 | 9577.7 | 10908.9 | 9507.1 | 10809.6 | 10699 | 9496.7 | 10548.2 | 10095.3 | 10149.7 | 9454.5 | 10017.9 | 10527 | 10663.6 | 9668 | 10537.4 | 9271.7 | 10280.4 | 10058.3 | 9544.6 | 10560.6 | 9360.5 | 10751.3 | 9569.6 | 10600.4 | 10056.6 | 10807.2 | 10191.7 | 11187 | 10067.1 | 10703.4 | 10082.3 | 8879.3 | 11076.2 | 10556.9 | 9978.7 | 11446.3 | 11113.3 | 10404 | 10271.5 | 11232 | 10042.5 | 10329.7 | 11064.5 | 9864.7 | 11185.2 | 9869.2 | 10899.9 | 10120.2 | 11008.5 | 9572.6 | 11097.3 | 10059.2 | 10976.3 | 10043.5 | 11123.8 | 10264.3 | 9850.3 | 10833.7 | 10021.5 | 9827 | 10943.5 | 11102.4 | 10907.7 | 10046.3 | 11034.7 | 9942.3 | 10785.8 | 10063.4 | 10635.9 | 9272.9 | 10779.3 | 9904.8 | 10132.3 | 10193.1 | 9919.1 | 8596.6 | 9965.4 | 8853.5 | 9959.4 | 10005.1 | 11219.9 | 9990.7 | 11219.9 | 10184.4 | 11278.3 | 10127 | 10309.2 | 10163.1 | 10965 | 11235.8 | 11221.4 | 11146.9 | 11133.1 | 11134.2 | 10190.1 | 11103.2 | 11136.5 | 11197.8 | 11227.8 | 11205.8 | 11230.8 | 10239.3 | 11239.7 | 10260.1 | 31.31 | 32.02 | 32.25 | 32.82 | 32.44 | 32.33 | 0 | 43.87 | 0 | 0 | 43.43 | 43.47 | 4.66 | 4.4 | 3.54 | 4.63 | 4.55 | 4.45 | 7.25 | 7.35 | 7.4 | 7.87 | 7.42 | 7.39 | 5.85 | 5.96 | 5.98 | 5.84 | 6.02 | 6.01 | 1.15 | 1.24 | 1.04 | 1.35 | 1.55 | 1.33 | 6.4 | 6.51 | 6.44 | 6.4 | 6.5 | 6.5 | 0.28 | 0.3 | 0.29 | 0.28 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 739103 | 1341 | 725842 | 1395 | 120223.2 | 344.2 | 5.85 | 5.96 | 5.98 | 5.84 | 6.02 | 6.01 | 6.4 | 6.51 | 6.44 | 6.4 | 6.5 | 6.5 | 834000 | 2000 | 831000 | 1000 | 1664591 | 4667 | 1662000 | 1659924 | 11.7 | 5.9433 | 1.2767 | 6.4583 | 0.29167 | 21.48% | 4.516% | 32.195 | 43.59 | 4.3717 | 7.4467 | 1676268.3 | 1608500 | 1940271.5421 | 82.9% | 29 | 39843
2024-09-20 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 335090.89 | 6:53 | 18:37 | 7388.4 | 7734.8 | 7650.4 | 7702.5 | 7668.6 | 7702.1 | 7734.4 | 8016.3 | 7685.2 | 7675.5 | 7477.3 | 7585.9 | 7600.2 | 7544.1 | 7644.1 | 7681.6 | 7479.1 | 7467.8 | 7440 | 7549.3 | 7427.3 | 7447.2 | 7281 | 7348 | 7262.8 | 6389 | 7309.8 | 7272.2 | 7493.3 | 7433.4 | 7371.2 | 7495 | 7458.4 | 7345.4 | 7454.1 | 7396.8 | 7533.9 | 7433.8 | 7468.2 | 7382.9 | 8096.7 | 7307.1 | 7763 | 6977.8 | 7616.3 | 8399 | 7081.6 | 8073.1 | 7451.1 | 7633.8 | 7511.1 | 7020.4 | 7739.9 | 7466.6 | 7676.1 | 7528.4 | 6824.8 | 7862 | 6863.7 | 7861.7 | 7699.4 | 6867 | 7658.2 | 7323 | 7181.6 | 6623.1 | 7121.8 | 7473.4 | 7717.9 | 6868.8 | 7581.5 | 6653.3 | 7481.9 | 7261.2 | 6918 | 7611.6 | 6801.3 | 7958.3 | 7028.3 | 7884.3 | 6983.1 | 7641.9 | 7048.7 | 7809.4 | 6959 | 7439.7 | 6953.2 | 6119.1 | 7647.8 | 7273 | 6822.4 | 7904.4 | 7611.1 | 7050.2 | 6972.7 | 7740 | 6934.7 | 7179.3 | 7808.9 | 6877.8 | 7927.9 | 6872.7 | 7730 | 7079 | 7826.9 | 6719.6 | 7874.7 | 7051.9 | 7472.1 | 6813.3 | 7806.4 | 7152.2 | 6909.7 | 7643.9 | 7056.2 | 6899.4 | 7700.4 | 7860.8 | 7746.3 | 7060.7 | 7845 | 6990.6 | 7622.9 | 7067.7 | 7500.6 | 6544.5 | 7637.1 | 6996 | 7191.1 | 7198.4 | 7068 | 6119.6 | 7056.8 | 6228.1 | 7001.8 | 7019.5 | 7963.3 | 6933.9 | 7910.3 | 7072.8 | 7939.3 | 7028.5 | 7201.2 | 7096.1 | 7674.5 | 7912.9 | 7913.2 | 7857.7 | 7905 | 7905 | 7064 | 7801 | 8008 | 8021 | 8029.8 | 7983 | 7980.9 | 7106 | 8078.1 | 7183.3 | 31.2916 | 32.4046 | 32.7558 | 33.5576 | 32.8762 | 32.6342 | 0 | 46.6 | 0 | 0 | 46.1787 | 46.0453 | 2.2039 | 0.79648 | 0.18678 | 1.7566 | 2.2913 | 1.7879 | 4.1017 | 4.46 | 4.405 | 4.5117 | 4.7183 | 4.5083 | 5.6203 | 5.5021 | 5.6261 | 5.5134 | 5.612 | 5.4001 | 1.1306 | 1.0714 | 1.0069 | 1.2919 | 1.4223 | 1.0931 | 6.1029 | 5.9775 | 6.0444 | 6.0189 | 6.0418 | 5.706 | 0.25221 | 0.26833 | 0.26168 | 0.24651 | 0.26474 | 0.25729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 739697 | 1342 | 726435 | 1396 | 121401.009 | 346.4 | 5.6203 | 5.5021 | 5.6261 | 5.5134 | 5.612 | 5.4001 | 6.1029 | 5.9775 | 6.0444 | 6.0189 | 6.0418 | 5.706 | 594000 | 1000 | 593000 | 1000 | 1177809 | 2200 | 1185000 | 1175609 | 11.7333 | 5.5457 | 1.1694 | 5.9819 | 0.25846 | 21.09% | 4.321% | 32.5867 | 46.2746 | 1.5038 | 4.4508 | 1184536.4 | 1172467 | 1389835.6044 | 84.36% | 22 | 106916
2024-09-21 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 335090.89 | 6:50 | 18:38 | 9421.7 | 10048.2 | 10102.2 | 10020.5 | 10228.7 | 10203.5 | 10116.2 | 10496.4 | 10007.2 | 9779.9 | 9748.6 | 9938.7 | 9986.7 | 9826.9 | 10155.6 | 10162.7 | 10090 | 10128.5 | 9972.7 | 10049.5 | 9978.9 | 9995.5 | 9755.3 | 9862.1 | 9718.4 | 8590 | 9763.6 | 9759.6 | 10007.7 | 9933.1 | 9868.4 | 10015 | 10081.1 | 10142.2 | 10067.4 | 10003.6 | 10215 | 10076.2 | 10111.5 | 9965.9 | 11048.2 | 9942.6 | 10827.6 | 9664.5 | 10362.7 | 11385.4 | 9742.5 | 11033.7 | 9886.4 | 10099.6 | 9957.6 | 9451.9 | 10336.3 | 10024.1 | 10397.2 | 10227.4 | 9179.9 | 10615.2 | 8948.3 | 10448.7 | 10280.2 | 8961 | 10152 | 9543.6 | 9529.9 | 8763.1 | 9433.4 | 9840.1 | 10306.2 | 9056.5 | 10106.4 | 8751.3 | 9910.5 | 9587 | 9078.6 | 10134.5 | 8844.4 | 10307.6 | 8982 | 10065.1 | 9104.1 | 9971.1 | 9237.4 | 10283.5 | 9111.8 | 9730.7 | 9120.7 | 7982.4 | 9966.4 | 9482.5 | 8943 | 10364.1 | 9967.4 | 9212.9 | 9127.7 | 10049.5 | 8876.3 | 9125.7 | 9961.2 | 8735.4 | 10083.8 | 8746.2 | 9834 | 8988.9 | 10020.6 | 8553.8 | 10142.9 | 9071.8 | 9265.1 | 8532.4 | 10157.8 | 9240.1 | 8768 | 9753 | 9024.6 | 8815.1 | 9974.3 | 10140.5 | 9923.1 | 9146.6 | 10197.8 | 9067.3 | 9781.3 | 9075.6 | 9684.4 | 8574.4 | 9930.1 | 9086.7 | 9275 | 9298.7 | 9161.8 | 7888.2 | 9166.3 | 8087.5 | 9287.9 | 9307 | 10453.4 | 9240.7 | 10523 | 9452.1 | 10613.5 | 9470.7 | 9670.7 | 9463.6 | 10099 | 10615.2 | 10281.4 | 10206.9 | 10259.7 | 10342 | 9455.8 | 10428.6 | 10071.2 | 10169.4 | 10216.7 | 10186.5 | 10313.6 | 9316.2 | 10345.5 | 9306 | 31.3209 | 33.3968 | 33.7183 | 34.4046 | 33.6216 | 33.6778 | 0 | 47.1 | 0 | 0 | 47.3 | 46.9 | 2.6201 | 1.3631 | 1.0308 | 1.9936 | 2.7514 | 2.8327 | 4.73 | 4.6567 | 4.9633 | 4.89 | 5.5783 | 5.56 | 5.2632 | 5.2235 | 5.4567 | 5.1735 | 5.1034 | 5.0898 | 1.0097 | 1.0797 | 0.93864 | 1.1705 | 1.3327 | 1.1339 | 5.7586 | 5.7101 | 5.8649 | 5.6463 | 5.4765 | 5.5108 | 0.23068 | 0.25158 | 0.24838 | 0.2243 | 0.24051 | 0.2438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 740488 | 1343 | 727196 | 1397 | 122947.676 | 348.467 | 5.2632 | 5.2235 | 5.4567 | 5.1735 | 5.1034 | 5.0898 | 5.7586 | 5.7101 | 5.8649 | 5.6463 | 5.4765 | 5.5108 | 791000 | 1000 | 761000 | 1000 | 1546667 | 2067 | 1550000 | 1544600 | 11.8 | 5.2184 | 1.1108 | 5.6612 | 0.23988 | 21.29% | 4.237% | 33.3567 | 47.1 | 2.0986 | 5.0631 | 1557515.9 | 1542600 | 1862451.532 | 82.83% | 32 | 15795
2024-09-22 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 335090.89 | 6:55 | 18:36 | 10938.3 | 11608.2 | 11507.1 | 11466 | 11610.3 | 11592 | 11646.2 | 12131.6 | 11559.3 | 11283.3 | 11327.7 | 11510.2 | 11510.1 | 11424.8 | 11608.8 | 11670.2 | 11544.6 | 11612.6 | 11561.7 | 11676.8 | 11547.1 | 11574.1 | 11302.4 | 11440.4 | 11149.1 | 9814.2 | 11266.2 | 11239.8 | 11563.6 | 11449.2 | 11255.8 | 11514.7 | 11360.5 | 11440.5 | 11497.1 | 11404.2 | 11611.7 | 11386.8 | 11397.7 | 11162.4 | 12250.9 | 10959.8 | 12013.9 | 10652.3 | 11365 | 12712.8 | 10858.9 | 12381.7 | 11515 | 11782.3 | 11599.1 | 10881.5 | 12000.6 | 11611.1 | 11876.4 | 11668.5 | 10541.1 | 12116.8 | 10530.4 | 12137 | 11983 | 10507 | 11713.9 | 11093.1 | 11071.8 | 10339.4 | 10986.7 | 11592.6 | 11900 | 10642.2 | 11673 | 10230.5 | 11385.6 | 11114.7 | 10504.2 | 11738.7 | 10276.1 | 12003.8 | 10530.4 | 11787.1 | 10824.1 | 11784.3 | 10998.4 | 12153.9 | 10811.2 | 11574.5 | 10739.8 | 9479.1 | 11829 | 11243.6 | 10507.7 | 12167.3 | 11676.2 | 10767.4 | 10599.3 | 11842.5 | 10558.8 | 10948.9 | 11891 | 10473.1 | 11973.6 | 10454.1 | 11673.8 | 10727.4 | 11783.2 | 10150.3 | 11859.3 | 10657.4 | 11700 | 10669.3 | 11857 | 10852.6 | 10457.4 | 11644.3 | 10657.7 | 10456.5 | 11817.4 | 12056 | 11768.3 | 10756.9 | 11976.3 | 10675.4 | 11575.2 | 10754.9 | 11433.8 | 9989.4 | 11663.5 | 10676.5 | 10840.3 | 10871.5 | 10708.3 | 9241.9 | 10630 | 9406.7 | 10520.4 | 10542.3 | 12430.5 | 10785.6 | 12377.7 | 10962.3 | 12224.9 | 10803.2 | 10995.9 | 10739.4 | 12040 | 12437.6 | 12410.1 | 12322.9 | 12354.5 | 12346.2 | 11117 | 12320.4 | 12225.8 | 12394.7 | 12506.9 | 12451.9 | 12462 | 11161 | 12421.5 | 11201.4 | 31.28 | 33.79 | 34.12 | 35.25 | 34.14 | 34.11 | 0 | 49.1 | 0 | 0 | 50 | 49.6 | 2.66 | 1.51 | 0.83 | 1.53 | 2.5 | 2.57 | 4.96 | 4.82 | 4.93 | 5.23 | 4.67 | 5.52 | 6.05 | 5.97 | 5.95 | 5.94 | 6.02 | 6.03 | 1.17 | 1.21 | 1.04 | 1.36 | 1.55 | 1.3 | 6.69 | 6.6 | 6.47 | 6.57 | 6.55 | 6.49 | 0.25 | 0.27 | 0.26 | 0.24 | 0.27 | 0.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 741397 | 1344 | 728097 | 1398 | 124751.476 | 353.267 | 6.05 | 5.97 | 5.95 | 5.94 | 6.02 | 6.03 | 6.69 | 6.6 | 6.47 | 6.57 | 6.55 | 6.49 | 909000 | 1000 | 901000 | 1000 | 1803800 | 4800 | 1808000 | 1799000 | 11.6833 | 5.9933 | 1.2717 | 6.5617 | 0.26 | 21.22% | 3.962% | 33.7817 | 49.5667 | 1.9333 | 5.0217 | 1815538.6 | 1803133 | 2164020.782 | 83.32% | 33 | 3083
2024-09-23 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 335090.89 | 6:56 | 18:39 | 10190.4 | 11014.7 | 11186.9 | 11127.1 | 11309.6 | 11353 | 11209.2 | 11639.1 | 10693 | 10324.9 | 10660.2 | 10687.6 | 11073.3 | 10834.3 | 11351.2 | 11286.4 | 11265.4 | 11248.2 | 11074.6 | 11182.8 | 11133.5 | 11125.9 | 10945.7 | 11028.6 | 10609.2 | 9308.3 | 10735.3 | 10710.4 | 11176.6 | 11078.6 | 10800.5 | 11043 | 10962.5 | 10997.6 | 10870.4 | 10867.5 | 11147.6 | 10961.1 | 11010.7 | 10923.6 | 11851.8 | 10646.8 | 11651.3 | 10412.7 | 11087.5 | 12372.2 | 10520.4 | 11942.7 | 10791 | 11007.5 | 10941 | 10230.7 | 11440.3 | 11106.1 | 11123.3 | 11013.9 | 9695.7 | 11179.1 | 9734.5 | 11112.9 | 10966.9 | 9670.1 | 10693.9 | 10119.7 | 10280.9 | 9722 | 10186.7 | 10881.9 | 10967.1 | 9997.8 | 10884.8 | 9676.4 | 10424.3 | 10495.5 | 9586.3 | 11120.6 | 9674.8 | 10940.7 | 9648.8 | 10904.8 | 10261.9 | 11122.9 | 10360.2 | 11495.2 | 10179.6 | 10819.5 | 10154.4 | 8857.7 | 11033.9 | 10503.4 | 9746.4 | 11374.6 | 10972 | 10179.6 | 10081.5 | 11180.5 | 9921.1 | 10125.1 | 10988.9 | 9592.3 | 11349.9 | 9625.4 | 11002.9 | 9915.7 | 11105.9 | 9489.4 | 11143.3 | 9938.4 | 11055.6 | 10047.6 | 11196.4 | 10140 | 9546.2 | 10468.5 | 9742.8 | 9461.8 | 10731.6 | 10756.2 | 10670.5 | 9601.7 | 10839.2 | 9693.2 | 10587.8 | 9847.8 | 10541.5 | 9205.8 | 10656.8 | 9756 | 9485.7 | 9543.3 | 9719 | 8149.1 | 9381.8 | 8410.3 | 9362.6 | 9388.9 | 11291.5 | 9832 | 11412.1 | 10105.3 | 11183.9 | 9791.6 | 9898.7 | 9618.5 | 11327.3 | 11779.7 | 11617.9 | 11515.8 | 11454.6 | 11382.6 | 10373.9 | 11547.2 | 11589.5 | 11664.1 | 11860.3 | 11740.8 | 11717.4 | 10497.5 | 11701.7 | 10521.7 | 31.28 | 34.17 | 34.51 | 35.56 | 34.71 | 34.55 | 0 | 48.93 | 0 | 0 | 48.85 | 49.2 | 2.54 | 2.37 | 0.7 | 1.21 | 2.52 | 2.49 | 4.73 | 4.83 | 4.66 | 4.18 | 4.53 | 4.39 | 5.75 | 5.85 | 5.82 | 5.58 | 5.43 | 5.72 | 1.11 | 1.18 | 1.01 | 1.27 | 1.38 | 1.21 | 6.36 | 6.45 | 6.34 | 6.18 | 5.93 | 6.23 | 0.25 | 0.28 | 0.26 | 0.24 | 0.25 | 0.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 742259 | 1346 | 728930 | 1399 | 126442.1 | 357.933 | 5.75 | 5.85 | 5.82 | 5.58 | 5.43 | 5.72 | 6.36 | 6.45 | 6.34 | 6.18 | 5.93 | 6.23 | 862000 | 2000 | 833000 | 1000 | 1690624 | 4666 | 1692000 | 1685958 | 11.7167 | 5.6917 | 1.1933 | 6.2483 | 0.25667 | 20.97% | 4.108% | 34.13 | 48.9933 | 1.9717 | 4.5533 | 1700788.8 | 1689934 | 2063496 | 81.9% | 33 | 15210
2024-09-24 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 335090.89 | 6:54 | 18:35 | 11012.1 | 11684.4 | 11788.1 | 11776.8 | 11908.4 | 11919.3 | 11701 | 11987 | 11552.3 | 11378.5 | 11254.1 | 11449.8 | 11408.7 | 11289.6 | 11589.8 | 11553.3 | 11515.2 | 11493.2 | 11397.3 | 11559.6 | 11365.2 | 11383.8 | 11139.2 | 11252 | 10809.1 | 9612.4 | 11153.1 | 11040.2 | 11288.1 | 11075.9 | 10768.6 | 10977.5 | 10679.8 | 10843.4 | 11129.9 | 10949.8 | 11052 | 10865 | 10876.9 | 10566.9 | 12066.2 | 11130.4 | 12013.3 | 10990 | 11457.8 | 12403.6 | 10794.1 | 12002.8 | 11315.2 | 11567.3 | 11423.2 | 10747.5 | 11810.8 | 11532.2 | 11564.2 | 11403.5 | 10331.2 | 11706.8 | 10394.4 | 11810.3 | 11818.9 | 10453.7 | 11489.9 | 11056.1 | 10538.2 | 9603.4 | 10409.3 | 10618.7 | 11228.2 | 9961 | 10927.2 | 9689.7 | 10932.9 | 10628.8 | 10216.1 | 11301.5 | 10156.7 | 11763.7 | 10464.6 | 11633.5 | 10075.2 | 10983.6 | 10219.6 | 10994.2 | 9979.3 | 10625.2 | 9801.7 | 8703.1 | 10625 | 10204.7 | 9521.4 | 10875.8 | 10551.1 | 9788 | 9654.1 | 10595.1 | 9544 | 9886.7 | 10792 | 9597.6 | 10922.3 | 9669.1 | 10786.9 | 9959.6 | 10981.8 | 9484.2 | 11131.4 | 10080.5 | 10869.7 | 10044.3 | 11539.1 | 10646.4 | 9599.9 | 10648.9 | 9881.5 | 9649.5 | 10924.6 | 11079.3 | 10954.7 | 10158.4 | 11228.5 | 10199.2 | 10990.6 | 10388.5 | 11151.1 | 9710 | 11227.8 | 10428.2 | 10601.7 | 10565.5 | 10583.8 | 9049.1 | 10414 | 9163.6 | 10472.8 | 10417.2 | 11609.1 | 10326.9 | 11758.5 | 10646.7 | 11651.5 | 10553.2 | 10732.5 | 10562.8 | 11531.6 | 11996.1 | 11486.2 | 11486.4 | 11470.2 | 11517.9 | 10728 | 11683.4 | 11442.3 | 11561.5 | 11739.3 | 11671.4 | 11723 | 10676.1 | 11390.9 | 10565 | 31.2763 | 34.738 | 34.9717 | 35.9635 | 35.1705 | 34.9934 | 0 | 48.3 | 0 | 0 | 48.6 | 48.9 | 2.6463 | 2.44 | 1.1887 | 1.5539 | 2.6122 | 2.5246 | 5.6383 | 5.4417 | 5.3783 | 5.2183 | 5.4317 | 5.525 | 6.0238 | 5.901 | 5.9985 | 5.6967 | 5.5573 | 5.788 | 1.163 | 1.1894 | 1.0536 | 1.3076 | 1.4262 | 1.2239 | 6.7297 | 6.5573 | 6.6094 | 6.3773 | 6.108 | 6.3277 | 0.23373 | 0.25 | 0.24553 | 0.21837 | 0.22187 | 0.23707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 743231 | 1350 | 729854 | 1402 | 128172.677 | 362.467 | 6.0238 | 5.901 | 5.9985 | 5.6967 | 5.5573 | 5.788 | 6.7297 | 6.5573 | 6.6094 | 6.3773 | 6.108 | 6.3277 | 972000 | 4000 | 924000 | 3000 | 1730577 | 4534 | 1889000 | 1726043 | 11.6833 | 5.8275 | 1.2273 | 6.4516 | 0.23443 | 21.06% | 3.634% | 34.5189 | 48.6 | 2.1609 | 5.4389 | 1742535.8 | 1729800 | 2123591.0817 | 81.46% | 28 | 12746
2024-09-25 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 335090.89 | 6:55 | 18:34 | 10666.6 | 11400.1 | 11295.1 | 11213 | 11392.4 | 11515.2 | 11496.3 | 11990.2 | 11342.9 | 11029.2 | 11264 | 11364.9 | 11503.8 | 11455 | 11480 | 11559.6 | 11352.8 | 11356.7 | 11319.7 | 11482.8 | 11251 | 11310.2 | 10907.7 | 11090.2 | 10854.9 | 9601.8 | 11045 | 10967.3 | 11230.9 | 10976.5 | 10735.9 | 11112.1 | 10990.6 | 11033.9 | 11185.6 | 11033.8 | 11151.8 | 10909.3 | 10950 | 10835.3 | 12027.6 | 10840.8 | 11847.9 | 10632.2 | 11293.7 | 12388.5 | 10552 | 11969.1 | 11419.8 | 11706.1 | 11518.9 | 10819 | 11864 | 11546.3 | 11773.5 | 11471.7 | 10521.1 | 12088 | 10444.1 | 12030.2 | 11842 | 10389.3 | 11638.3 | 11008.5 | 10907.3 | 10154.3 | 10872.5 | 11355.2 | 11823.1 | 10516 | 11599.1 | 10132.9 | 11324.9 | 10998.1 | 10413.3 | 11587.6 | 10163.7 | 11871.7 | 10402.7 | 11638.5 | 10644.6 | 11600.5 | 10766.7 | 11877.7 | 10554.3 | 11294.2 | 10410.3 | 9202.1 | 11317.1 | 10886.7 | 10009.2 | 11550.9 | 11146.2 | 10352.7 | 10237.8 | 11278.4 | 10026.3 | 10387.4 | 11303.1 | 9980.3 | 11486.5 | 10022.6 | 11240.5 | 10298.3 | 11363.6 | 9752.4 | 11410.1 | 10211.2 | 11007.2 | 10041.6 | 11438.2 | 10458.9 | 9994.1 | 11035.3 | 10211.1 | 9966.5 | 11230.3 | 11347.7 | 11184.4 | 10195.2 | 11338.9 | 10136.5 | 11028.8 | 10267.1 | 10966.3 | 9559.7 | 11122.6 | 10217.4 | 10409.8 | 10452.2 | 10364.1 | 8891.5 | 10201.3 | 9007.7 | 10266.6 | 10327.2 | 11962.2 | 10425.8 | 12073 | 10765.1 | 11962 | 10625.1 | 10791.2 | 10536.1 | 11737.1 | 12136.1 | 12057.4 | 11948.7 | 11928.2 | 11953.9 | 10861 | 11972.8 | 12134.6 | 12094.3 | 12052.5 | 12029.7 | 12086.5 | 10871.2 | 12298.7 | 10968.4 | 31.2686 | 34.6823 | 34.9858 | 35.8637 | 35.216 | 35.0781 | 0 | 47.4 | 0 | 0 | 47.6729 | 47.681 | 1.5535 | 2.0615 | 1.5535 | 2.4674 | 3.0887 | 3.1013 | 5.7017 | 5.7967 | 5.7017 | 5.61 | 6.18 | 5.9417 | 5.8362 | 5.8233 | 5.8362 | 5.8542 | 5.6781 | 5.8645 | 1.0287 | 1.1864 | 1.0287 | 1.3424 | 1.4717 | 1.2546 | 6.3851 | 6.4469 | 6.3851 | 6.5231 | 6.2244 | 6.3901 | 0.27808 | 0.29279 | 0.27808 | 0.26416 | 0.27319 | 0.28093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 744051 | 1351 | 730654 | 1403 | 129929.077 | 366.867 | 5.8362 | 5.8233 | 5.8362 | 5.8542 | 5.6781 | 5.8645 | 6.3851 | 6.4469 | 6.3851 | 6.5231 | 6.2244 | 6.3901 | 820000 | 1000 | 800000 | 1000 | 1756400 | 4400 | 1618000 | 1752000 | 11.65 | 5.8154 | 1.2188 | 6.3925 | 0.27787 | 20.96% | 4.347% | 34.5157 | 47.5846 | 2.3043 | 5.8219 | 1767599.1 | 1755800 | 2107771.1679 | 83.3% | 27 | 0
2024-09-26 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 335090.89 | 7:01 | 18:35 | 10736.9 | 11367 | 11291.3 | 11216.5 | 11374.7 | 11464.1 | 11454.6 | 11831.5 | 11285.8 | 11125.5 | 11111.6 | 11256.9 | 11306.4 | 11248.2 | 11328.5 | 11376.8 | 11247.4 | 11348.1 | 11248.5 | 11368.9 | 11301.3 | 11312.6 | 11077.9 | 11192.7 | 10963.7 | 9671.6 | 11005.6 | 10987.5 | 11373.1 | 11274 | 11136.3 | 11353.4 | 11259.4 | 11295 | 11383.4 | 11265 | 11465.4 | 11302.9 | 11339.7 | 11130.1 | 12233.7 | 11114.7 | 12099.1 | 10905.9 | 11582.6 | 12670.4 | 10861.9 | 12231.3 | 11234.9 | 11513.6 | 11336.2 | 10696 | 11704.2 | 11339.6 | 11686.2 | 11446.6 | 10341.2 | 11893.1 | 10275.9 | 11819.2 | 11674.5 | 10266.2 | 11482.4 | 10891.1 | 10964.5 | 10302 | 10881.1 | 11517.8 | 11701.6 | 10574.1 | 11557.2 | 10168.6 | 11201.5 | 11011.5 | 10307.3 | 11608.2 | 10177.2 | 11754.7 | 10370.1 | 11641.6 | 10763.2 | 11695.7 | 10901.8 | 12021.6 | 10738.2 | 11501.5 | 10665.4 | 9413.4 | 11746 | 11173.2 | 10412.2 | 12015.3 | 11610.6 | 10743.9 | 10570.6 | 11769.9 | 10488.7 | 10880.8 | 11774.1 | 10383.6 | 11928.3 | 10381.6 | 11615.7 | 10637.2 | 11726.5 | 10080.4 | 11767.9 | 10567.2 | 11313.2 | 10346.1 | 11694.8 | 10745.4 | 10409 | 11486.6 | 10557.4 | 10325.3 | 11599 | 11695.8 | 11528 | 10486.8 | 11642.7 | 10395.1 | 11390.5 | 10599.8 | 11265.5 | 9754.2 | 11384.5 | 10408.5 | 10611.7 | 10669.7 | 10496.9 | 9042.6 | 10453.9 | 9243.2 | 10459.1 | 10513.9 | 11984.6 | 10556.3 | 11970.1 | 10797.9 | 11941.7 | 10690.2 | 10916.6 | 10661.7 | 11758.8 | 12173.9 | 12027.3 | 11939.1 | 11952.8 | 11965.5 | 10856.1 | 11943.7 | 12047.1 | 12043.8 | 12034.3 | 11954.5 | 11987.9 | 10854 | 12109.7 | 10916.7 | 31.3 | 35.49 | 35.75 | 36.58 | 35.87 | 35.8 | 0 | 46.5 | 0 | 0 | 47.1 | 46.7 | 3.79 | 3.25 | 2.58 | 3.44 | 3.81 | 3.66 | 7.61 | 6 | 6.23 | 6.43 | 6.37 | 6.28 | 5.81 | 5.84 | 5.91 | 5.81 | 5.83 | 5.83 | 1.13 | 1.23 | 1.05 | 1.35 | 1.55 | 1.27 | 6.49 | 6.5 | 6.45 | 6.51 | 6.41 | 6.39 | 0.28 | 0.3 | 0.29 | 0.27 | 0.29 | 0.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 744938 | 1352 | 731531 | 1403 | 131704.41 | 371.4 | 5.81 | 5.84 | 5.91 | 5.81 | 5.83 | 5.83 | 6.49 | 6.5 | 6.45 | 6.51 | 6.41 | 6.39 | 887000 | 1000 | 877000 | 0 | 1775333 | 4533 | 1763000 | 1770800 | 11.5667 | 5.8383 | 1.2633 | 6.4583 | 0.28667 | 21.64% | 4.439% | 35.1317 | 46.7667 | 3.4217 | 6.4867 | 1786697.3 | 1774900 | 2137983 | 83.02% | 31 | 551
2024-09-27 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 335090.89 | 7:00 | 18:40 | 9820.1 | 10522.9 | 10524.3 | 10432.9 | 10678.1 | 10749.6 | 10648.5 | 11009.8 | 10384.6 | 10074.8 | 10224.7 | 10340.9 | 10483.5 | 10358.8 | 10647.3 | 10669.7 | 10645.3 | 10785.3 | 10667.5 | 10723.1 | 10781.5 | 10765.6 | 10550.4 | 10694.3 | 10516.2 | 9165.4 | 10369.1 | 10447.2 | 10842.3 | 10665.7 | 10529.9 | 10865.1 | 10712 | 10810.5 | 10898.1 | 10803.8 | 10974.9 | 10713.2 | 10700.9 | 10534.9 | 11562.5 | 10328.5 | 11463.7 | 10201.9 | 10831.2 | 12254.9 | 10142.1 | 11603.8 | 10347.5 | 10600 | 10487.6 | 9839.2 | 10925 | 10553.4 | 10785.5 | 10649.2 | 9471.2 | 10928.1 | 9444.7 | 10864 | 10663.3 | 9408.3 | 10389.8 | 9779.4 | 9961.1 | 9297.6 | 9780.3 | 10331.7 | 10538.1 | 9357.2 | 10226.5 | 8961.2 | 10028.6 | 9707 | 9187 | 10247.2 | 9008.7 | 10553.8 | 9227.4 | 10334.1 | 9552.4 | 10357.7 | 9740.6 | 10829 | 9630.9 | 10339.6 | 9681.1 | 8550.7 | 10889.8 | 10265.4 | 9756.6 | 11375.3 | 10993 | 10078.5 | 9917.5 | 11022.8 | 9684.3 | 10021 | 10934.5 | 9587.3 | 11172.9 | 9626.9 | 10776.8 | 9853.4 | 10917.6 | 9323.9 | 10958.2 | 9747.4 | 10774.5 | 9781.3 | 10872.7 | 9939 | 9591.9 | 10612.3 | 9766.2 | 9550.9 | 10772.6 | 10899.9 | 10685.9 | 9713.3 | 10827.7 | 9613.8 | 10507.6 | 9788.1 | 10406.8 | 9031.1 | 10539.5 | 9590.7 | 9792.2 | 9818.6 | 9610.5 | 8335 | 9605.5 | 8502.5 | 9456.5 | 9506.4 | 11268.1 | 9729.6 | 11252 | 9948.8 | 11190.6 | 9785.5 | 9944.7 | 9647.7 | 10654.3 | 11092.7 | 10946.1 | 10920.8 | 11086.2 | 11181.5 | 9964.1 | 11037.1 | 11126.3 | 11105.6 | 11136 | 11049.3 | 11034 | 9789.8 | 11119.8 | 9851.8 | 31.31 | 33.95 | 34.27 | 35.37 | 34.04 | 34.01 | 0 | 49.5 | 0 | 0 | 49.9 | 48.7 | 2.31 | 2.32 | 0.85 | 1.86 | 2.38 | 2.26 | 7.93 | 7.18 | 6.18 | 6.64 | 6.57 | 6.93 | 5.44 | 5.65 | 5.6 | 5.33 | 5.46 | 5.32 | 1.06 | 1.19 | 1 | 1.24 | 1.44 | 1.15 | 6.06 | 6.28 | 6.16 | 5.94 | 5.99 | 5.8 | 0.25 | 0.28 | 0.27 | 0.24 | 0.26 | 0.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 745769 | 1353 | 732349 | 1405 | 133347.344 | 376.133 | 5.44 | 5.65 | 5.6 | 5.33 | 5.46 | 5.32 | 6.06 | 6.28 | 6.16 | 5.94 | 5.99 | 5.8 | 831000 | 1000 | 818000 | 2000 | 1642934 | 4733 | 1646000 | 1638201 | 11.6667 | 5.4667 | 1.18 | 6.0383 | 0.26 | 21.59% | 4.306% | 33.825 | 49.3667 | 1.9967 | 6.905 | 1652345.5 | 1641300 | 1997283 | 82.18% | 27 | 1248
2024-09-28 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 335090.89 | 6:55 | 18:28 | 10023.3 | 10628.5 | 10534.2 | 10487.9 | 10589.7 | 10686.8 | 10670.2 | 11050.9 | 10584.7 | 10304.1 | 10408.3 | 10590.4 | 10581.8 | 10557.7 | 10588.1 | 10675 | 10579.9 | 10726.3 | 10704.9 | 10820.9 | 10777.1 | 10761.3 | 10593.6 | 10714.7 | 10560.2 | 9248.6 | 10497.4 | 10522.9 | 10868.7 | 10740.4 | 10628.2 | 10890.6 | 10757 | 10800.8 | 10921.1 | 10788.3 | 11003.5 | 10803.6 | 10774.5 | 10610.8 | 11876.1 | 10598.8 | 11730.1 | 10378.9 | 11054.2 | 12506.7 | 10389.8 | 11902.7 | 10593.8 | 10863.1 | 10722.1 | 10107.5 | 11137 | 10670.5 | 11123.7 | 10909.1 | 9759.5 | 11295.2 | 9683.2 | 11151.9 | 10987.6 | 9652.9 | 10820.2 | 10255.2 | 10426.7 | 9845.2 | 10349.1 | 10985.9 | 11139.9 | 10114.1 | 11020.7 | 9722.1 | 10600.3 | 10489.6 | 9777.2 | 11042.3 | 9666.5 | 11185.4 | 9815.3 | 11010.1 | 10326.2 | 11231.2 | 10508.2 | 11630.3 | 10338.4 | 11115.9 | 10264.3 | 9109.8 | 11390.9 | 10836.7 | 10062.1 | 11689.8 | 11205.1 | 10236 | 10096.5 | 11424.6 | 10171.7 | 10603.8 | 11560.3 | 10171.7 | 11695.3 | 10144.8 | 11331.2 | 10413.8 | 11471.6 | 9862.7 | 11553.2 | 10344.5 | 11340.9 | 10302.9 | 11463.9 | 10497.1 | 10219.3 | 11318.4 | 10391.8 | 10169.7 | 11449.5 | 11603.3 | 11364.9 | 10347.8 | 11524.7 | 10224.1 | 11173.6 | 10376.8 | 10976.6 | 9549.5 | 11193.9 | 10173.1 | 10452.2 | 10501.5 | 10230.6 | 8889.4 | 10294.8 | 9140.3 | 10179.6 | 10234.1 | 12027.9 | 10347.2 | 12195.4 | 10723.1 | 12060.2 | 10532.1 | 10703.4 | 10408.4 | 11748 | 12225.6 | 12104 | 12021.1 | 12090.3 | 12125.6 | 10840.4 | 12097.6 | 12125.8 | 12151.1 | 12249.4 | 12186.4 | 12203.2 | 10843.6 | 12154.8 | 10851 | 31.2792 | 33.1693 | 33.5077 | 34.7507 | 33.2145 | 33.3653 | 0 | 48.6794 | 0 | 0 | 50 | 49.7043 | 2.7351 | 2.0895 | 1.3837 | 2.4975 | 2.8309 | 2.5975 | 5.5783 | 5.615 | 5.4333 | 6.005 | 5.5817 | 4.7233 | 5.4937 | 5.6547 | 5.7232 | 5.583 | 5.7924 | 5.8285 | 1.0701 | 1.2075 | 1.0272 | 1.3064 | 1.5519 | 1.2983 | 6.1241 | 6.2708 | 6.2838 | 6.2331 | 6.3647 | 6.4026 | 0.23836 | 0.26812 | 0.25769 | 0.23495 | 0.26313 | 0.26293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 746618 | 1355 | 733222 | 1406 | 135064.677 | 380.867 | 5.4937 | 5.6547 | 5.7232 | 5.583 | 5.7924 | 5.8285 | 6.1241 | 6.2708 | 6.2838 | 6.2331 | 6.3647 | 6.4026 | 849000 | 2000 | 873000 | 1000 | 1717333 | 4734 | 1719000 | 1712599 | 11.55 | 5.6793 | 1.2436 | 6.2799 | 0.2542 | 21.9% | 4.048% | 33.2144 | 49.4612 | 2.3557 | 5.4894 | 1727807.6 | 1716867 | 2081001.1058 | 82.5% | 24 | 1
2024-09-29 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 335090.89 | 6:52 | 18:31 | 11026.5 | 11724.2 | 11425.3 | 11614.5 | 11718.8 | 11786.3 | 11813.9 | 12213.3 | 11678.6 | 11563.8 | 11508.7 | 11703.8 | 11620.6 | 11613.7 | 11668.2 | 11729.7 | 11582.2 | 11669.2 | 11614.7 | 11725.1 | 11658.4 | 11649.4 | 11425 | 11557.1 | 11372.7 | 9985.7 | 11376.2 | 11351.3 | 11733.7 | 11629.8 | 11463.7 | 11696.2 | 11731.3 | 11724.7 | 11784.7 | 11697.2 | 11850.9 | 11679.7 | 11724.7 | 11568.1 | 12462.3 | 11305.3 | 12355 | 11108.7 | 11810.1 | 12873.4 | 11119.3 | 12470 | 11643.3 | 11900.6 | 11759.1 | 11044.8 | 12075.7 | 11737.2 | 12035 | 11818.6 | 10695.5 | 12264 | 10704.7 | 12190 | 12071.4 | 10688.2 | 11862.1 | 11309.3 | 11360.9 | 10681.3 | 11326.6 | 11770.6 | 12112.4 | 10912 | 11976.6 | 10478.6 | 11627.4 | 11429.2 | 10719.4 | 11904.8 | 10554.6 | 12157.1 | 10723.1 | 11974.8 | 11004 | 11889.3 | 11139.6 | 12249.5 | 10887.4 | 11741.1 | 10935.7 | 9623.3 | 11922.7 | 11443 | 10702.7 | 12352.7 | 11985.7 | 11061.9 | 10921.7 | 12094.6 | 10793 | 11176.7 | 12105.9 | 10714.7 | 12243.4 | 10697.4 | 11934.5 | 10976.5 | 12008.1 | 10316.6 | 12022.3 | 10866.8 | 11942.4 | 10881.7 | 12034.6 | 11036.9 | 10763.4 | 11860.4 | 10926.4 | 10695 | 11967.2 | 12091.9 | 11908.5 | 10845.9 | 12029.4 | 10731.5 | 11727.3 | 10917.8 | 11623 | 10074.3 | 11753.7 | 10725.4 | 10986.5 | 11068.2 | 10834.1 | 9360.1 | 10835.1 | 9591.2 | 10847.7 | 10871.8 | 12500.7 | 10968.1 | 12526.8 | 11217.4 | 12318.9 | 11101.3 | 11303.1 | 11054.7 | 12178.6 | 12552.6 | 12455.5 | 12391.5 | 12434.5 | 12462.3 | 11334.2 | 12446.6 | 12519.8 | 12536.9 | 12584.4 | 12543.9 | 12547.3 | 11336.5 | 12590.6 | 11329.6 | 31.2521 | 31.5824 | 31.8699 | 32.9781 | 32.0979 | 31.89 | 0 | 47 | 0 | 0 | 47.3 | 47.2152 | 1.982 | 1.9082 | 0.35378 | 1.3642 | 2.0085 | 1.73 | 4.0717 | 4.445 | 3.555 | 3.985 | 4.0783 | 4.2667 | 5.886 | 5.9204 | 5.9826 | 5.8815 | 5.9622 | 5.9868 | 1.0607 | 1.1027 | 0.96434 | 1.2585 | 1.3739 | 1.0972 | 6.6391 | 6.6563 | 6.6325 | 6.6395 | 6.6088 | 6.6073 | 0.21978 | 0.24414 | 0.21904 | 0.2127 | 0.21755 | 0.23311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 747542 | 1357 | 734136 | 1408 | 136896.477 | 385.667 | 5.886 | 5.9204 | 5.9826 | 5.8815 | 5.9622 | 5.9868 | 6.6391 | 6.6563 | 6.6325 | 6.6395 | 6.6088 | 6.6073 | 924000 | 2000 | 914000 | 2000 | 1831800 | 4800 | 1834000 | 1827000 | 11.65 | 5.9366 | 1.1429 | 6.6306 | 0.22439 | 19.25% | 3.384% | 31.9451 | 47.1717 | 1.5578 | 4.0669 | 1844652.6 | 1831266 | 2198390 | 83.3% | 25 | 0
2024-09-30 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 335090.89 | 7:01 | 18:29 | 10307.9 | 10942.6 | 10814.5 | 10788.4 | 10845.9 | 10917.3 | 10957.2 | 11390.9 | 10919.1 | 10784.4 | 10803.8 | 10978.5 | 10880.5 | 10923.6 | 10870.2 | 10932 | 10887.1 | 11057.5 | 11143.1 | 11207 | 11221.4 | 11204.9 | 10946.4 | 11068.9 | 10963 | 9683.2 | 10981.9 | 10972.1 | 11291.6 | 11199.6 | 11054.6 | 11269.1 | 11257.5 | 11190.9 | 11361.8 | 11232.4 | 11399.7 | 11246.2 | 11257.1 | 11148.4 | 11927.1 | 10934.6 | 12004.5 | 10784.1 | 11423.9 | 12443.7 | 10765.4 | 12046.3 | 11063.1 | 11308.8 | 11199.4 | 10562.2 | 11549.7 | 11139.1 | 11543.4 | 11321.5 | 10228.1 | 11745.8 | 10169.6 | 11673.8 | 11530.6 | 10137 | 11392.5 | 10843 | 10796.3 | 10167.5 | 10792.5 | 11219.9 | 11619.1 | 10413.4 | 11448.5 | 10026.9 | 11180.2 | 10935.9 | 10323.4 | 11508.2 | 10142 | 11725.4 | 10327.6 | 11499.8 | 10453.9 | 11359.5 | 10609.7 | 11668 | 10364.5 | 11165 | 10435.6 | 9177.4 | 11417.3 | 10912.2 | 10220.3 | 11809.4 | 11501.9 | 10614.5 | 10487.9 | 11598.6 | 10239.3 | 10571.1 | 11455.2 | 10116.2 | 11577.3 | 10086.5 | 11261.1 | 10307 | 11356.1 | 9701.7 | 11321.6 | 10061.2 | 11134.9 | 10061.7 | 11153.2 | 10122.2 | 10138.6 | 11110.7 | 10185 | 9964.4 | 11094.3 | 11183.6 | 11011.4 | 9966.9 | 11049.4 | 9858.8 | 10806.8 | 9965.3 | 10603.6 | 9267.5 | 10808.2 | 9892.9 | 10126.2 | 10147.6 | 10003.4 | 8696.4 | 10028.6 | 8802.2 | 10037.8 | 10065.8 | 11652.9 | 10179.8 | 11670.4 | 10375.3 | 11372.9 | 10219.3 | 10381.2 | 10223.1 | 11404.5 | 11782.6 | 11570.9 | 11503.9 | 11580 | 11599.3 | 10501.5 | 11566 | 11684 | 11727.4 | 11850.8 | 11736.3 | 11714.4 | 10583.2 | 11736 | 10548.1 | 31.3195 | 33.3328 | 33.6576 | 34.684 | 34.1773 | 33.5896 | 0 | 47.2 | 0 | 0 | 46.9 | 46.6999 | 2.8166 | 2.8522 | 0.90047 | 2.847 | 2.887 | 2.4051 | 6.2317 | 5.265 | 5.3683 | 6.065 | 5.2367 | 5.1083 | 5.5709 | 5.7617 | 5.8147 | 5.6747 | 5.5703 | 5.5646 | 1.0302 | 1.1192 | 0.96488 | 1.2426 | 1.3988 | 1.0482 | 6.2307 | 6.4367 | 6.4106 | 6.3626 | 6.1487 | 6.1214 | 0.24178 | 0.27351 | 0.24674 | 0.23482 | 0.24527 | 0.25145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 748423 | 1359 | 734993 | 1410 | 138627.277 | 390.333 | 5.5709 | 5.7617 | 5.8147 | 5.6747 | 5.5703 | 5.5646 | 6.2307 | 6.4367 | 6.4106 | 6.3626 | 6.1487 | 6.1214 | 881000 | 2000 | 857000 | 2000 | 1730800 | 4666 | 1734000 | 1726134 | 11.4667 | 5.6595 | 1.134 | 6.2851 | 0.24893 | 20.04% | 3.961% | 33.4601 | 46.9333 | 2.4514 | 5.5458 | 1742467.2 | 1730300 | 2085425.7874 | 82.97% | 26 | 0
2024-10-01 | 2025 | 2024 | Year_3 | Year_3 | 2024-10-01 | 31 | 335090.89 | 6:57 | 18:30 | 10872 | 11556.6 | 11486.4 | 11427.8 | 11561.2 | 11641.7 | 11654.9 | 12093 | 11495.4 | 11378 | 11316.8 | 11534.3 | 11437.2 | 11441.2 | 11487.9 | 11545.1 | 11420.4 | 11504.4 | 11432.9 | 11550.2 | 11472.7 | 11454 | 11249.9 | 11373.8 | 11189.1 | 9828.8 | 11183.8 | 11175.9 | 11555.3 | 11462.7 | 11269.4 | 11497.2 | 11549.6 | 11575.1 | 11606.5 | 11536.4 | 11694.7 | 11494.9 | 11470.1 | 11390.5 | 12356.4 | 11179.4 | 12262.1 | 10993.6 | 11673.6 | 12824.8 | 10973.1 | 12339.2 | 11445.2 | 11736.8 | 11585 | 10858.5 | 11982.1 | 11591.9 | 11895.8 | 11653.7 | 10523.2 | 12146.3 | 10525.3 | 12066.3 | 11929.1 | 10513.8 | 11732.2 | 11139.5 | 11176.1 | 10506.9 | 11130.1 | 11686.3 | 11992.5 | 10740.2 | 11832.2 | 10319.8 | 11444.3 | 11231.7 | 10543.7 | 11833.6 | 10376.4 | 12042.2 | 10550.9 | 11831.2 | 10838.1 | 11727.6 | 10971.7 | 12124.7 | 10788.6 | 11580.2 | 10786.9 | 9494.5 | 11881.7 | 11305.7 | 10578.8 | 12233.2 | 11870.3 | 10911.6 | 10782 | 11992.5 | 10700.3 | 11054.6 | 12006.3 | 10583.3 | 12153.1 | 10575.8 | 11818.5 | 10844.8 | 11931.6 | 10255.7 | 11984 | 10748.2 | 11823.2 | 10748 | 11940.6 | 10918.5 | 10645.2 | 11745.2 | 10817 | 10580.5 | 11885.6 | 12020.9 | 11808.3 | 10736.5 | 11950.3 | 10633.3 | 11617.3 | 10819.1 | 11522 | 10005.6 | 11652.5 | 10626.8 | 10856.9 | 10925.5 | 10712.3 | 9261.4 | 10724.5 | 9488.6 | 10704.5 | 10733.8 | 12382 | 10842.3 | 12402.4 | 11070.6 | 12206.8 | 10954 | 11159.2 | 10902.6 | 12071 | 12482.4 | 12334.6 | 12273.5 | 12311.9 | 12341 | 11172.6 | 12321.1 | 12375 | 12387.3 | 12446.5 | 12389.9 | 12418.6 | 11192 | 12466 | 11177.4 | 31.2966 | 33.9744 | 34.1576 | 34.853 | 34.6259 | 34.3613 | 0 | 46.3915 | 0 | 0 | 47.3 | 47 | 4.5248 | 4.5077 | 3.6201 | 4.2564 | 4.4592 | 4.2661 | 6.6833 | 7.0983 | 6.8117 | 7.19 | 6.9217 | 6.655 | 5.8144 | 5.853 | 5.8873 | 5.7944 | 5.877 | 5.8786 | 1.0935 | 1.1655 | 0.9938 | 1.293 | 1.5075 | 1.1463 | 6.5721 | 6.5871 | 6.5286 | 6.5535 | 6.5293 | 6.549 | 0.24866 | 0.27193 | 0.24824 | 0.23341 | 0.26183 | 0.26425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 749333 | 1360 | 735897 | 1411 | 140437.078 | 395 | 5.8144 | 5.853 | 5.8873 | 5.7944 | 5.877 | 5.8786 | 6.5721 | 6.5871 | 6.5286 | 6.5535 | 6.5293 | 6.549 | 910000 | 1000 | 904000 | 1000 | 1809801 | 4667 | 1812000 | 1805134 | 11.55 | 5.8508 | 1.1999 | 6.5533 | 0.25472 | 20.51% | 3.887% | 33.8781 | 46.8972 | 4.2724 | 6.8933 | 1822541.7 | 1809667 | 2160632.5392 | 83.76% | 29 | 0
2024-10-02 | 2025 | 2024 | Year_3 | Year_3 | 2024-10-01 | 31 | 335090.89 | 6:56 | 18:31 | 11359.1 | 11928.6 | 11851.3 | 11820.7 | 11910.4 | 11986.5 | 11977.7 | 12314.2 | 11855.1 | 11743.7 | 11721.3 | 11893.5 | 11851.2 | 11816.6 | 11882.1 | 11922.3 | 11810.5 | 11885.7 | 11833.4 | 11946.3 | 11861.7 | 11872.1 | 11709 | 11797.3 | 11633.6 | 10275.7 | 11626.6 | 11621.7 | 11911.8 | 11827.9 | 11701.1 | 11821.9 | 12078.6 | 12091.2 | 12121.7 | 12053.4 | 12021.1 | 11864.8 | 11843.9 | 11783.9 | 12602.2 | 11637.8 | 12496.6 | 11484.2 | 12038.9 | 13051.5 | 11442.6 | 12587.5 | 11825.5 | 12061.1 | 11946 | 11340.7 | 12252.6 | 11934.2 | 12173.6 | 11975.8 | 10993.2 | 12383.1 | 10988.3 | 12316.1 | 12209.6 | 10979.3 | 12050.1 | 11588.7 | 11631.7 | 10998 | 11591 | 12020.5 | 12235.7 | 11227.1 | 12118.1 | 10784 | 11829.4 | 11681.3 | 11007.8 | 12116.4 | 10838.9 | 12280.9 | 11017.8 | 12118.5 | 11322.7 | 12050.3 | 11457 | 12388.9 | 11285.1 | 11959.3 | 11247.4 | 9920.4 | 12167.6 | 11718.6 | 11049.4 | 12482.7 | 12165 | 11386.9 | 11257.3 | 12269.8 | 11180.9 | 11526.2 | 12273.1 | 11057.2 | 12407 | 11044.1 | 12150.7 | 11335.2 | 12206.4 | 10709.1 | 12264.8 | 11227.5 | 12151.5 | 11203.7 | 12247.1 | 11409.8 | 11137.8 | 12078.6 | 11303.1 | 11072.8 | 12176.2 | 12303.9 | 12115 | 11232.5 | 12236.8 | 11126.4 | 11977.7 | 11315.6 | 11916.7 | 10476.1 | 12028.5 | 11117.4 | 11361.3 | 11413.9 | 11227.6 | 9703.6 | 11220.1 | 9936.3 | 11237.6 | 11250.2 | 12641.2 | 11353.4 | 12648.1 | 11557 | 12472.1 | 11442.8 | 11625.4 | 11399.9 | 12371.5 | 12681.9 | 12607.9 | 12538 | 12592.3 | 12612.6 | 11641.2 | 12584 | 12626.8 | 12633 | 12698 | 12658.1 | 12674.3 | 11675.7 | 12709.9 | 11648.1 | 31.2962 | 34.3285 | 34.5013 | 34.949 | 34.5417 | 34.526 | 0 | 46.3 | 0 | 0 | 46.9 | 46.7 | 5.1188 | 5.0448 | 4.4025 | 4.5767 | 5.2089 | 4.9985 | 8.1617 | 8.2267 | 8.08 | 8.0783 | 8.11 | 7.5867 | 6.0371 | 6.0803 | 6.1166 | 6.0208 | 6.1132 | 6.11 | 1.1519 | 1.2343 | 1.0539 | 1.3692 | 1.591 | 1.2131 | 6.8712 | 6.8837 | 6.8245 | 6.8511 | 6.8277 | 6.8489 | 0.25885 | 0.28387 | 0.2585 | 0.24041 | 0.2775 | 0.27791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 750275 | 1362 | 736834 | 1412 | 142309.078 | 399.8 | 6.0371 | 6.0803 | 6.1166 | 6.0208 | 6.1132 | 6.11 | 6.8712 | 6.8837 | 6.8245 | 6.8511 | 6.8277 | 6.8489 | 942000 | 2000 | 937000 | 1000 | 1872000 | 4800 | 1876000 | 1867200 | 11.5833 | 6.0797 | 1.2689 | 6.8512 | 0.26617 | 20.87% | 3.885% | 34.0238 | 46.6333 | 4.8917 | 8.0406 | 1884267.1 | 1871200 | 2257122.3585 | 82.9% | 30 | 0
2024-10-03 | 2025 | 2024 | Year_3 | Year_3 | 2024-10-01 | 31 | 335090.89 | 6:55 | 18:30 | 11479.3 | 12025.6 | 11957.6 | 11931.2 | 12033.8 | 12082 | 12068.3 | 12408.4 | 11957.4 | 11821.1 | 11824.8 | 12000 | 11967 | 11916.4 | 11982.8 | 12039.1 | 11914.1 | 11999.6 | 11976.9 | 12072.2 | 11981.8 | 11991.3 | 11819.4 | 11905.3 | 11746.5 | 10385.2 | 11743.9 | 11736.7 | 12016.9 | 11928 | 11799.2 | 11863.1 | 12194.1 | 12207.9 | 12238.2 | 12180.6 | 12122 | 11969.2 | 11945.4 | 11881.4 | 12695.4 | 11735.1 | 12575.3 | 11583.5 | 12138.1 | 13148.1 | 11543.2 | 12678.5 | 11913.7 | 12163.3 | 12050.8 | 11457 | 12358.7 | 12026.4 | 12273 | 12055.7 | 11113.8 | 12486.4 | 11123.1 | 12417.6 | 12308.1 | 11105.2 | 12156.6 | 11702.3 | 11726 | 11108.5 | 11692.9 | 12110.9 | 12326.2 | 11337.3 | 12212.5 | 10891.9 | 11923.2 | 11777.8 | 11119.3 | 12205 | 10945.8 | 12363.5 | 11128.3 | 12211 | 11434.9 | 12138.3 | 11560.7 | 12490.7 | 11391.2 | 12058 | 11333.1 | 10016.6 | 12251.8 | 11803.9 | 11153.4 | 12577.2 | 12272 | 11521.1 | 11397.9 | 12359.3 | 11271.4 | 11611.3 | 12360.8 | 11145.1 | 12503.9 | 11143.1 | 12246 | 11441.8 | 12293.8 | 10816.9 | 12360.9 | 11334.8 | 12246.5 | 11274.3 | 12336.4 | 11526.4 | 11232.4 | 12162.8 | 11407.5 | 11193.8 | 12267.7 | 12392.2 | 12209.8 | 11333.9 | 12334.3 | 11232.9 | 12068.9 | 11438.1 | 12020.5 | 10575.7 | 12124.8 | 11219.7 | 11482.8 | 11530 | 11328.7 | 9799.3 | 11326.2 | 10027.3 | 11365.9 | 11371.8 | 12728.4 | 11458.3 | 12742.1 | 11658.2 | 12637.2 | 11542.8 | 11720.5 | 11522.7 | 12459.5 | 12767.1 | 12700.5 | 12622.5 | 12686 | 12710.4 | 11741.9 | 12672 | 12735.4 | 12734.2 | 12787.9 | 12760.8 | 12765.7 | 11775.8 | 12811.6 | 11780.6 | 31.2966 | 32.6604 | 32.8281 | 33.1703 | 32.448 | 32.9151 | 0 | 45.9271 | 0 | 0 | 46.4157 | 46.438 | 5.4345 | 5.7057 | 4.7775 | 5.6359 | 5.6408 | 5.7009 | 8.8067 | 9.085 | 9.02 | 9.6133 | 9.3217 | 9.0483 | 6.0688 | 6.1239 | 6.1465 | 6.0512 | 6.1483 | 6.1519 | 1.1633 | 1.2461 | 1.0731 | 1.3932 | 1.5991 | 1.2226 | 6.9317 | 6.9506 | 6.8896 | 6.9206 | 6.9005 | 6.9132 | 0.25129 | 0.2769 | 0.25219 | 0.23382 | 0.26732 | 0.26937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 751225 | 1364 | 737778 | 1413 | 144197.145 | 404.6 | 6.0688 | 6.1239 | 6.1465 | 6.0512 | 6.1483 | 6.1519 | 6.9317 | 6.9506 | 6.8896 | 6.9206 | 6.9005 | 6.9132 | 950000 | 2000 | 944000 | 1000 | 1888067 | 4800 | 1891000 | 1883267 | 11.5833 | 6.1151 | 1.2829 | 6.9177 | 0.25848 | 20.98% | 3.737% | 32.5531 | 46.2603 | 5.4825 | 9.1492 | 1900645.3 | 1886467 | 2288583.8628 | 82.43% | 27 | 0
2024-10-04 | 2025 | 2024 | Year_3 | Year_3 | 2024-10-01 | 31 | 335090.89 | 7:05 | 18:27 | 10970.7 | 11428.2 | 11372.6 | 11319.8 | 11446.9 | 11480.7 | 11462.7 | 11740.5 | 11340.3 | 11298.7 | 11233.5 | 11384.9 | 11349.4 | 11303.7 | 11338.2 | 11405.2 | 11286 | 11388 | 11332.7 | 11411.6 | 11376.3 | 11371 | 11288.6 | 11335.4 | 11124.8 | 9892.2 | 11106.7 | 11108 | 11421.4 | 11393.4 | 11302.5 | 11377.1 | 11657.3 | 11634.2 | 11628.1 | 11603.3 | 11512.3 | 11415.2 | 11411.3 | 11339.6 | 12178.4 | 11348.6 | 12086.9 | 11187.8 | 11679.6 | 12590.4 | 11115.5 | 12158.3 | 11303 | 11526.7 | 11412 | 10888.6 | 11674.1 | 11387.9 | 11602.7 | 11419.4 | 10593.5 | 11790.7 | 10618.9 | 11739.3 | 11657.1 | 10607 | 11509.2 | 11134.7 | 11102.8 | 10578 | 11093.1 | 11463.1 | 11656.8 | 10815.8 | 11587.8 | 10439.8 | 11307 | 11222.8 | 10624.3 | 11610.5 | 10488.8 | 11728.3 | 10678.9 | 11658.9 | 10909.5 | 11538 | 11020.2 | 11830.5 | 10864.3 | 11428 | 10773.4 | 9569.9 | 11551.5 | 11180.5 | 10617.8 | 11833.3 | 11556.8 | 10908.3 | 10812.8 | 11595.6 | 10663.5 | 10954.7 | 11594.9 | 10561.1 | 11805.4 | 10616 | 11560.5 | 10875.4 | 11615 | 10313.2 | 11684.2 | 10771.7 | 11630 | 10838.2 | 11736.5 | 11002.6 | 10640.7 | 11440.1 | 10818.2 | 10631 | 11556 | 11665.8 | 11507.7 | 10756.7 | 11615.5 | 10712.2 | 11404.1 | 10883.6 | 11391.6 | 10116.6 | 11466.5 | 10715.5 | 10885.8 | 10899.7 | 10775.3 | 9303.8 | 10717 | 9504.8 | 10734.4 | 10745.5 | 11972.6 | 10840 | 12010.7 | 10999.8 | 11864 | 10873.4 | 11026.5 | 10867.5 | 11891.8 | 12172.7 | 12138.7 | 12021.9 | 12025 | 12018.8 | 11179.6 | 12039.5 | 12200.1 | 12185.9 | 12229.4 | 12193.8 | 12191 | 11287.8 | 12237.4 | 11315.8 | 31.36 | 30.68 | 30.92 | 31.32 | 30.49 | 30.95 | 0 | 44.01 | 0 | 0 | 44.7 | 44.64 | 5.84 | 6.3 | 5.2 | 6.36 | 5.93 | 6.21 | 9.47 | 9.27 | 10.12 | 9.38 | 9.02 | 10.05 | 5.77 | 5.83 | 5.93 | 5.76 | 5.83 | 5.89 | 1.07 | 1.24 | 1.01 | 1.29 | 1.55 | 1.23 | 6.59 | 6.62 | 6.62 | 6.55 | 6.51 | 6.64 | 0.25 | 0.27 | 0.25 | 0.23 | 0.26 | 0.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 752129 | 1366 | 738674 | 1415 | 145989.9 | 409.333 | 5.77 | 5.83 | 5.93 | 5.76 | 5.83 | 5.89 | 6.59 | 6.62 | 6.62 | 6.55 | 6.51 | 6.64 | 904000 | 2000 | 896000 | 2000 | 1792755 | 4733 | 1796000 | 1788022 | 11.3667 | 5.835 | 1.2317 | 6.5883 | 0.255 | 21.11% | 3.87% | 30.9533 | 44.45 | 5.9733 | 9.5517 | 1805745.1 | 1792200 | 2197421.8626 | 81.56% | 27 | 2473
2024-10-05 | 2025 | 2024 | Year_3 | Year_3 | 2024-10-01 | 31 | 335090.89 | 6:56 | 18:24 | 9301.3 | 9772.2 | 9660 | 9588.2 | 9739.7 | 9830 | 9809 | 10129.4 | 9696.4 | 9510.9 | 9625.7 | 9718.5 | 9851.3 | 9748.2 | 10003.8 | 10037.1 | 9928.9 | 9999.6 | 9977.8 | 10033.7 | 9981.2 | 9983.8 | 9690.4 | 9851.5 | 9734.2 | 8712.2 | 9762 | 9731.4 | 9901.5 | 9638.2 | 9462.9 | 9801.6 | 9822.3 | 9914.2 | 9996 | 9942.2 | 9974.5 | 9702.7 | 9599.3 | 9600.9 | 10294.6 | 9483.5 | 10188.4 | 9354.2 | 9738.9 | 10525.2 | 9223.2 | 10234.7 | 9786.9 | 10041.9 | 9898.2 | 9409.2 | 10111.4 | 9955.7 | 10125.4 | 10012 | 9128.7 | 10247.6 | 9067 | 9893.9 | 10015.6 | 9027.7 | 9879.1 | 9492.8 | 9507.5 | 8954 | 9477 | 9832.8 | 10070.9 | 9190.4 | 9956.1 | 8865.6 | 9770.4 | 9514.9 | 9094.3 | 9752.2 | 8773.9 | 10081.5 | 9027 | 9829.4 | 9264.4 | 9883.8 | 9363 | 10145.2 | 9164.6 | 9706.5 | 9146.9 | 8193.8 | 9960.1 | 9626.7 | 9166.7 | 10358 | 10153.6 | 9536.6 | 9372.6 | 10224.9 | 9236.2 | 9550.8 | 10093.6 | 9157.5 | 10132 | 9156.5 | 9944.9 | 9332 | 9998.1 | 8745.1 | 9921.2 | 9209.6 | 9842.3 | 9004.3 | 9862.7 | 9263.4 | 9261 | 10106 | 9322.8 | 9199 | 10043 | 10213 | 10048 | 9395 | 10142 | 9200 | 9871 | 9201 | 9672 | 8549 | 9859 | 9060 | 9483 | 9553 | 9160 | 8066 | 9378 | 8287 | 9179 | 9408 | 10491 | 9377 | 10471 | 9558 | 10504 | 9477 | 9636 | 9550 | 10138 | 10390 | 10330 | 10314 | 10418 | 10460 | 10355 | 10525 | 10126 | 10137 | 10227 | 10127 | 10196 | 9385 | 10186 | 9342 | 31.3024 | 29.6307 | 29.8971 | 30.8899 | 29.5187 | 29.8513 | 0 | 43.2 | 0 | 0 | 43.7 | 43.1036 | 3.4761 | 3.8125 | 2.6937 | 3.9038 | 3.7136 | 3.426 | 6.5617 | 6.2483 | 6.43 | 6.3233 | 7.0917 | 6.2733 | 5.0658 | 5.2452 | 5.0515 | 5.0825 | 5.2041 | 5.0939 | 0.92095 | 1.127 | 0.84561 | 1.1193 | 1.3702 | 1.075 | 5.7052 | 5.8749 | 5.5263 | 5.671 | 5.7301 | 5.66 | 0.23169 | 0.2605 | 0.23016 | 0.21933 | 0.24747 | 0.24403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 752904 | 1368 | 739444 | 1416 | 147530.412 | 414.2 | 5.0658 | 5.2452 | 5.0515 | 5.0825 | 5.2041 | 5.0939 | 5.7052 | 5.8749 | 5.5263 | 5.671 | 5.7301 | 5.66 | 775000 | 2000 | 770000 | 1000 | 1540512 | 4867 | 1542000 | 1535645 | 11.4667 | 5.1238 | 1.0763 | 5.6946 | 0.23886 | 21.01% | 4.195% | 30.1817 | 43.3345 | 3.5043 | 6.4881 | 1550691.8 | 1539267 | 1901873.8367 | 80.93% | 26 | 24196
2024-10-06 | 2025 | 2024 | Year_3 | Year_3 | 2024-10-01 | 31 | 335090.89 | 7:03 | 18:27 | 9773.9 | 10635.8 | 10794.5 | 10794.2 | 10810.1 | 10767.9 | 10782.3 | 11057.5 | 10413.7 | 9821.9 | 10298 | 10534.2 | 10153.4 | 10158.8 | 10129.8 | 10222.8 | 10025.9 | 9876.1 | 9697.9 | 9776.7 | 9667.4 | 9729.9 | 9398.3 | 9533.8 | 9307 | 8277.9 | 9425.8 | 9430.5 | 9567.8 | 9539.4 | 9570.7 | 9517.9 | 10176.9 | 10113.4 | 9727.7 | 9787.9 | 9938.9 | 9833.5 | 9925.8 | 10022.4 | 11042.7 | 10033.2 | 10975.5 | 9946 | 10371.8 | 11293.5 | 9610.8 | 10877.9 | 9837.8 | 10135.5 | 9868.7 | 9331.6 | 10052.7 | 9835.1 | 10302.4 | 9795.3 | 9575.8 | 11107.6 | 9293.8 | 10709.4 | 10651.5 | 9423.9 | 10965.7 | 10409.3 | 10887 | 10509 | 10866.2 | 11683.3 | 11487.4 | 10747.6 | 11562.7 | 10318.3 | 10928.9 | 11131.6 | 10140.5 | 11632 | 10139.5 | 11395.4 | 10079.5 | 11268.8 | 11016.1 | 11764.6 | 11095.6 | 12221.9 | 11054.3 | 11723.7 | 11080.7 | 9772.3 | 11786.1 | 11556 | 10521.6 | 11898.1 | 11412.3 | 10451.4 | 10235.5 | 11610.8 | 10574.7 | 10837.8 | 11423.7 | 10172.1 | 11293.4 | 10065.9 | 10869.8 | 10215.2 | 10788.6 | 9498.2 | 10848.4 | 10021.1 | 10663.1 | 9857.3 | 10862.3 | 10216.2 | 10281.8 | 11255.4 | 10328.7 | 10201 | 11232 | 11660.8 | 11233 | 10645 | 11630.3 | 10546.4 | 10976.4 | 10440.5 | 11207.4 | 9866.8 | 11459.3 | 10507.4 | 10776.7 | 10892 | 10628.5 | 9154 | 10758 | 9573.2 | 10955.3 | 10879.9 | 11864.7 | 10617 | 11834 | 10779.9 | 12219.6 | 10810.3 | 11138.7 | 10860.1 | 11101.5 | 11427.8 | 11543.3 | 11486.9 | 11610.8 | 11684.7 | 10493.8 | 11461.9 | 11551.6 | 11345.2 | 11057.6 | 11021.4 | 11127.1 | 10076.6 | 11639.3 | 10301.1 | 31.36 | 31.09 | 31.34 | 33.3 | 31.46 | 31.32 | 0 | 44.69 | 0 | 0 | 47.5 | 46.68 | 1.85 | 1.58 | 0.38 | 1.85 | 1.88 | 1.43 | 4.14 | 4.64 | 4.96 | 5.82 | 5.78 | 4.31 | 5.35 | 4.81 | 5.2 | 5.65 | 5.71 | 5.47 | 1 | 0.98 | 0.9 | 1.29 | 1.48 | 1.09 | 6.13 | 5.45 | 5.82 | 6.45 | 6.39 | 6.15 | 0.23 | 0.23 | 0.23 | 0.23 | 0.26 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 753722 | 1370 | 740316 | 1418 | 149213.345 | 419.067 | 5.35 | 4.81 | 5.2 | 5.65 | 5.71 | 5.47 | 6.13 | 5.45 | 5.82 | 6.45 | 6.39 | 6.15 | 818000 | 2000 | 872000 | 2000 | 1682933 | 4867 | 1686000 | 1678066 | 11.4 | 5.365 | 1.1233 | 6.065 | 0.23833 | 20.94% | 3.93% | 31.645 | 46.29 | 1.495 | 4.9417 | 1692797 | 1682500 | 2010168 | 83.7% | 30 | 17644
2024-10-07 | 2025 | 2024 | Year_3 | Year_3 | 2024-10-01 | 31 | 335090.89 | 6:57 | 18:25 | 10177 | 10782.1 | 10446.2 | 10416.5 | 10481.1 | 10614.5 | 10773.2 | 11237.6 | 10811.6 | 10490.1 | 10733.1 | 10941 | 10837 | 10867.1 | 10673 | 10864.3 | 10712.2 | 10742 | 10986 | 11077.7 | 11027.6 | 10960.9 | 10873.4 | 10972.6 | 10792 | 9463.8 | 10760.8 | 10782.9 | 11168.1 | 11086 | 10865.9 | 11096.4 | 10905 | 11025 | 11185.8 | 11033.8 | 11195.2 | 10994.3 | 10904.8 | 10607.7 | 12102.3 | 10767.9 | 11964.7 | 10556.9 | 11231.1 | 12412.4 | 10591.1 | 12139.1 | 10877.6 | 11165.8 | 11010.9 | 10325.9 | 11399.7 | 10959.1 | 11376.4 | 10972.9 | 10093.2 | 11683.7 | 10032.2 | 11377 | 11270.8 | 10026.2 | 11207.2 | 10627.5 | 10743.1 | 10080.7 | 10689.8 | 11277.7 | 11443.3 | 10401.9 | 11393.8 | 9995.8 | 10972.9 | 10740.4 | 10091.3 | 11480.1 | 9994.9 | 11505 | 9989.7 | 11349.7 | 10573.5 | 11516.8 | 10560.7 | 11662.7 | 10395.1 | 10941 | 10318.8 | 8978.4 | 11162.9 | 10657.6 | 9975.3 | 11570.7 | 11242.9 | 10341.3 | 10188.5 | 11327.8 | 10127.7 | 10433.8 | 11369.6 | 9990.7 | 11532 | 10025 | 11271.4 | 10288.5 | 11444.9 | 9808 | 11525.7 | 10276.9 | 11387.1 | 10322.3 | 11493.3 | 10325.4 | 10129.7 | 11228.2 | 10268 | 10065.8 | 11354.2 | 11538.3 | 11304.1 | 10311.1 | 11491.4 | 10261.6 | 11092 | 10211.5 | 11034.3 | 9577.4 | 11251.1 | 10260.9 | 10277.3 | 10478.7 | 10324.1 | 8869.1 | 10349.5 | 9223.2 | 10650.8 | 10675.2 | 12339.5 | 10753 | 12400.9 | 11034.8 | 12282.7 | 10896.2 | 11061.8 | 10859.8 | 11983.6 | 12470.9 | 12147.8 | 12180.1 | 12259 | 12290.9 | 11086.5 | 12291.7 | 11997.4 | 12206.4 | 12328.9 | 12210 | 12335.5 | 11049.6 | 12091.3 | 11040.2 | 31.31 | 32.99 | 33.28 | 34.5 | 33.25 | 33.21 | 0 | 46.7 | 0 | 0 | 47.55 | 47.3 | 2.3 | 2.07 | 0.48 | 2.31 | 2.39 | 1.61 | 6.86 | 5.63 | 4.13 | 5.06 | 4.97 | 5.21 | 5.44 | 5.56 | 5.61 | 5.54 | 5.53 | 5.74 | 1.04 | 1.13 | 1 | 1.28 | 1.44 | 1.13 | 6.24 | 6.34 | 6.34 | 6.37 | 6.24 | 6.46 | 0.23 | 0.26 | 0.25 | 0.22 | 0.25 | 0.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 754590 | 1372 | 741192 | 1419 | 150951.9 | 423.933 | 5.44 | 5.56 | 5.61 | 5.54 | 5.53 | 5.74 | 6.24 | 6.34 | 6.34 | 6.37 | 6.24 | 6.46 | 868000 | 2000 | 876000 | 1000 | 1738555 | 4866 | 1741000 | 1733689 | 11.4667 | 5.57 | 1.17 | 6.3317 | 0.245 | 21.01% | 3.869% | 33.09 | 47.1833 | 1.86 | 5.31 | 1749549.3 | 1737533 | 2077719 | 83.63% | 29 | 4139
2024-10-08 | 2025 | 2024 | Year_3 | Year_3 | 2024-10-01 | 31 | 335090.89 | 7:03 | 18:22 | 9146 | 9522 | 9378 | 9394 | 9366 | 9367 | 9479 | 9758 | 9490 | 9577 | 9293 | 9518 | 9275 | 9355 | 9070 | 9229 | 9028 | 9086 | 9178 | 9330 | 9054 | 9101 | 8897 | 8959 | 9056 | 8046 | 9118 | 8962 | 9172 | 9083 | 8875 | 9216 | 9469 | 9508 | 9531 | 9360 | 9408 | 9166 | 9087 | 9211 | 9321 | 8422 | 9231 | 8236 | 8769 | 9701 | 8251 | 9344 | 9447 | 9720 | 9548 | 9111 | 9778 | 9323 | 10013 | 9639 | 8994 | 10382 | 8755 | 10083 | 10107 | 8776 | 10125 | 9622 | 9598 | 9040 | 9561 | 10118 | 10313 | 9342 | 10211 | 9038 | 9896 | 9790 | 9174 | 10319 | 9022 | 10494 | 9186 | 10321 | 9634 | 10400 | 9881 | 10769 | 9678 | 10358 | 9518 | 8449 | 10544 | 9997 | 9369 | 10844 | 10398 | 9467 | 9254 | 10569 | 9370 | 9656 | 10364 | 9042 | 10413 | 9083 | 10073 | 9277 | 10091 | 8769 | 10118 | 9173 | 9913 | 9021 | 9948 | 9203 | 9088 | 9998 | 9214 | 9033 | 10195 | 10331 | 10139 | 9328 | 10347 | 9225 | 9920 | 9252 | 9823 | 8563 | 10031 | 9133 | 9478 | 9553 | 9227 | 8022 | 9369 | 8316 | 9403 | 9461 | 10994 | 9585 | 11077 | 9846 | 10977 | 9696 | 9840 | 9643 | 10939 | 11291 | 11213 | 11108 | 11070 | 11019 | 9977 | 11096 | 11377 | 11415 | 11476 | 11395 | 11372 | 10159 | 11373 | 10238 | 31.39 | 32.74 | 32.92 | 34.13 | 33.08 | 33.16 | 0 | 44.7 | 0 | 0 | 47.11 | 47.01 | 2.84 | 2.55 | 1.23 | 2.56 | 2.76 | 2.62 | 8.08 | 8.07 | 8.23 | 8.87 | 9 | 9.48 | 4.78 | 4.65 | 4.4 | 5.05 | 5.03 | 5.3 | 0.93 | 0.94 | 0.8 | 1.18 | 1.31 | 1.07 | 5.43 | 5.24 | 4.9 | 5.74 | 5.6 | 5.92 | 0.21 | 0.22 | 0.2 | 0.2 | 0.23 | 0.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755337 | 1373 | 741987 | 1421 | 152488.5 | 428.7 | 4.78 | 4.65 | 4.4 | 5.05 | 5.03 | 5.3 | 5.43 | 5.24 | 4.9 | 5.74 | 5.6 | 5.92 | 747000 | 1000 | 795000 | 2000 | 1536600 | 4767 | 1539000 | 1531833 | 11.3167 | 4.8683 | 1.0383 | 5.4717 | 0.215 | 21.33% | 3.929% | 32.9033 | 46.2733 | 2.4267 | 8.6217 | 1546507 | 1531000 | 1798136.8197 | 85.14% | 25 | 14245
2024-10-09 | 2025 | 2024 | Year_3 | Year_3 | 2024-10-01 | 31 | 335090.89 | 7:05 | 18:20 | 9164.6 | 9751.7 | 9834.8 | 9761.3 | 10010.7 | 10081.3 | 9898.3 | 10418.8 | 9690.9 | 9538.9 | 9715.6 | 9821.2 | 9909.5 | 9859.4 | 9957.2 | 10126.9 | 9920.6 | 9924.2 | 9942.6 | 10020.8 | 9999.5 | 9927.9 | 9917 | 9979.7 | 9820.1 | 8543.6 | 9677 | 9732.8 | 10203.4 | 10188.4 | 10070.2 | 10226.2 | 10247.4 | 10233.6 | 10185.8 | 10157.2 | 10388.4 | 10269.9 | 10259.2 | 10118.7 | 11300.5 | 10122.6 | 11243.5 | 10013 | 10563.6 | 11765.3 | 9775.2 | 11260.6 | 9803.1 | 10072.2 | 9924.7 | 9326.6 | 10271.5 | 9968.6 | 10226 | 9972.6 | 9029.8 | 10449.8 | 9055 | 10337 | 10179.3 | 9038.2 | 10057.7 | 9571.4 | 9648.1 | 9089.4 | 9602.3 | 10126.8 | 10371 | 9324 | 10237.1 | 8944.7 | 9889.5 | 9697.9 | 9097.3 | 10257.8 | 8967.7 | 10420.7 | 9097.4 | 10220.6 | 9528.8 | 10312.6 | 9657.5 | 10688.8 | 9476.9 | 10126.6 | 9370.3 | 8267 | 10262.1 | 9829.1 | 9091.6 | 10537.7 | 10199.6 | 9396.9 | 9284.6 | 10197.7 | 9015.4 | 9332.5 | 10200.4 | 8913.7 | 10574.9 | 9044.2 | 10236 | 9275 | 10390.8 | 8848 | 10428.7 | 9245.1 | 10334.7 | 9350.8 | 10485.7 | 9486.4 | 8967.9 | 9870.1 | 9145 | 8918.8 | 10077.1 | 10175.5 | 10046.6 | 9152.8 | 10252.5 | 9171.8 | 9950.2 | 9332 | 9950.2 | 8695.1 | 10088.1 | 9280.4 | 9297.9 | 9277.1 | 9383.8 | 7988.4 | 9129.1 | 8001.8 | 8963.7 | 8954.2 | 10412 | 8966.9 | 10432.5 | 9172.3 | 10340.3 | 9053.7 | 9221.2 | 9035.9 | 9964.5 | 10377.7 | 9974.7 | 10119.7 | 10298.1 | 10338.7 | 9224.5 | 10287.8 | 10210.7 | 10264 | 10208.6 | 10205 | 10298.2 | 9142.4 | 10354.2 | 9182.4 | 31.3901 | 32.7718 | 33.172 | 33.8751 | 33.0268 | 32.9044 | 0 | 46.3202 | 0 | 0 | 45.5 | 44.9 | 2.0335 | 1.8652 | 0.12469 | 0.73645 | 1.9614 | 1.4957 | 4.365 | 3.86 | 3.755 | 3.4733 | 4.5417 | 4.0883 | 4.912 | 5.0486 | 5.1651 | 4.966 | 4.8351 | 4.7619 | 0.95717 | 1.0408 | 0.93744 | 1.166 | 1.2663 | 0.93275 | 5.6281 | 5.7664 | 5.8397 | 5.7092 | 5.4465 | 5.3274 | 0.21816 | 0.241 | 0.22651 | 0.20273 | 0.21707 | 0.21716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756130 | 1375 | 742757 | 1422 | 154047.279 | 433.6 | 4.912 | 5.0486 | 5.1651 | 4.966 | 4.8351 | 4.7619 | 5.6281 | 5.7664 | 5.8397 | 5.7092 | 5.4465 | 5.3274 | 793000 | 2000 | 770000 | 1000 | 1558779 | 4900 | 1560000 | 1553879 | 11.25 | 4.9481 | 1.0501 | 5.6195 | 0.22044 | 21.22% | 3.923% | 32.8567 | 45.5734 | 1.3695 | 4.0139 | 1568361.6 | 1557000 | 1849627.1693 | 84.18% | 25 | 2308
2024-10-10 | 2025 | 2024 | Year_3 | Year_3 | 2024-10-01 | 31 | 335090.89 | 7:00 | 18:21 | 10636.9 | 11208.1 | 11160.3 | 11133.1 | 11230.7 | 11252.5 | 11252.8 | 11721 | 11160.7 | 11111.7 | 11079.5 | 11250 | 11311.9 | 11229.5 | 11166.4 | 11390.4 | 11242.1 | 11406.6 | 11409.2 | 11477.2 | 11375.8 | 11386.4 | 11036.3 | 11212.1 | 11030.1 | 9724.4 | 11147 | 11061.4 | 11312.5 | 11158.1 | 10967.7 | 11245 | 11366.8 | 11373.8 | 11420.2 | 11271.3 | 11390.9 | 11229.2 | 11222.8 | 11197.5 | 12131.8 | 11037.9 | 12053.3 | 10847.9 | 11506.4 | 12558 | 10753.3 | 12137.7 | 11213.1 | 11521.4 | 11436.8 | 10774.1 | 11820 | 11394.3 | 11785.7 | 11422.7 | 10433.9 | 11960 | 10363.7 | 11858.9 | 11707 | 10347.8 | 11524.6 | 10984.5 | 10863.1 | 10189.1 | 10776.9 | 11311.2 | 11601.1 | 10336 | 11346 | 9891.5 | 11147.1 | 10737 | 10263.8 | 11285.7 | 9978.7 | 11742.8 | 10303 | 11483.2 | 10528.3 | 11347.6 | 10515.3 | 11851.2 | 10490.6 | 11199.7 | 10578.5 | 9265.4 | 11511.8 | 11005.2 | 10396.3 | 11996.1 | 11691.5 | 10786.9 | 10640.4 | 11732 | 10510.8 | 10874.3 | 11795.6 | 10394.2 | 11952.8 | 10422.4 | 11646.4 | 10673.2 | 11769.9 | 10130.1 | 11849.2 | 10663.5 | 11707.5 | 10631 | 11836.2 | 10852.5 | 10491.3 | 11516.7 | 10651.6 | 10416.1 | 11699.2 | 11795.4 | 11623.3 | 10531.9 | 11689 | 10418.6 | 11449.4 | 10680.4 | 11248.3 | 9755.5 | 11376.8 | 10406.6 | 10650.4 | 10718.2 | 10451.7 | 9040.1 | 10497.8 | 9272.8 | 10287.3 | 10284.8 | 11618.7 | 10153.4 | 11611.1 | 10462.9 | 11683.2 | 10343.4 | 10554.1 | 10358.1 | 11160.5 | 11483 | 11306.6 | 11312 | 11463 | 11524.2 | 10306.6 | 11346.8 | 11545.1 | 11582.9 | 11550.7 | 11476.5 | 11493.8 | 10316.8 | 11597.3 | 10395.2 | 31.34 | 32.62 | 33 | 33.89 | 32.93 | 32.73 | 0 | 46.4 | 0 | 0 | 46.5 | 45.3 | 2.36 | 1.69 | 0.66 | 1 | 2.35 | 1.62 | 5.46 | 6.16 | 5.69 | 5.49 | 4.9 | 5.25 | 5.63 | 5.62 | 5.71 | 5.58 | 5.63 | 5.25 | 1.07 | 1.18 | 1.04 | 1.32 | 1.49 | 1.06 | 6.52 | 6.48 | 6.51 | 6.49 | 6.41 | 5.97 | 0.25 | 0.27 | 0.26 | 0.23 | 0.26 | 0.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 757022 | 1377 | 743632 | 1424 | 155807.4 | 438.333 | 5.63 | 5.62 | 5.71 | 5.58 | 5.63 | 5.25 | 6.52 | 6.48 | 6.51 | 6.49 | 6.41 | 5.97 | 892000 | 2000 | 875000 | 2000 | 1760121 | 4733 | 1763000 | 1755388 | 11.35 | 5.57 | 1.1933 | 6.3967 | 0.25167 | 21.42% | 3.934% | 32.7517 | 46.0667 | 1.6133 | 5.4917 | 1771636.4 | 1759600 | 2096078 | 83.95% | 24 | 319
2024-10-11 | 2025 | 2024 | Year_3 | Year_3 | 2024-10-01 | 31 | 335090.89 | 6:55 | 18:22 | 11520.8 | 11992.3 | 11941.3 | 11920.7 | 12005.8 | 12059.8 | 12026.6 | 12292.7 | 11938 | 11921.5 | 11777.3 | 11960 | 11939.6 | 11883.4 | 11859.6 | 12018.4 | 11865.9 | 11994.5 | 11968.9 | 12044.1 | 11959.2 | 11980.7 | 11801.3 | 11898.1 | 11718.3 | 10419 | 11746.5 | 11717.8 | 12006.7 | 11913.1 | 11790.3 | 11892.5 | 12223.6 | 12240.9 | 12277.6 | 12187.7 | 12118.1 | 11979 | 11943.5 | 11840.1 | 12749.8 | 11813.3 | 12642.9 | 11648 | 12177.7 | 13130.2 | 11503.2 | 12732 | 11826.5 | 12101.2 | 12002 | 11458.1 | 12284.5 | 11941.1 | 12279.4 | 11958.5 | 11181 | 12493.5 | 11113.3 | 12033.5 | 12306.4 | 11143.9 | 12112.2 | 11672 | 11631.8 | 10978.6 | 11592.8 | 12062.5 | 12248.4 | 11261.7 | 12097.8 | 10829.4 | 11874.7 | 11638.6 | 11072.6 | 12089.8 | 10835.3 | 12318.1 | 11078 | 12129.9 | 11503.9 | 12207.5 | 11591 | 12549 | 11467.5 | 12072.6 | 11424.1 | 10133 | 12290.8 | 11865.8 | 11255.4 | 12625.2 | 12321.2 | 11585.4 | 11421 | 12386 | 11361.6 | 11696.1 | 12384.9 | 11235.3 | 12541.7 | 11263.5 | 12296.2 | 11508.3 | 12354.8 | 10948.3 | 12436.6 | 11458.6 | 12303 | 11254 | 12396.4 | 11628.5 | 11329.5 | 12244.3 | 11470.4 | 11275.1 | 12312.9 | 12473.8 | 12266.5 | 11445.9 | 12407.1 | 11377.8 | 12128.9 | 11537.7 | 12057.5 | 10679.1 | 12199.8 | 11369.8 | 11556.8 | 11569.7 | 11422.2 | 9855.3 | 11361 | 10084.6 | 11302.6 | 11329.8 | 12629 | 11375 | 12656.7 | 11590.7 | 12550.1 | 11439.4 | 11590.2 | 11462.3 | 12434.4 | 12745 | 12515.4 | 12553.2 | 12603.6 | 12614.5 | 11698.8 | 12620.1 | 12644.3 | 12689.8 | 12768.2 | 12718.1 | 12741 | 11757 | 12720.9 | 11757.1 | 31.3167 | 32.6527 | 33.0718 | 34.1127 | 32.7851 | 32.5943 | 0 | 45.5 | 0 | 0 | 46.1 | 45.4 | 2.9458 | 2.1319 | 1.4454 | 1.0358 | 3.0182 | 2.6253 | 7.3817 | 7.9517 | 6.3683 | 6.9867 | 6.905 | 7.5867 | 5.982 | 6.0025 | 6.0525 | 5.9541 | 5.9554 | 6.0219 | 1.1586 | 1.2934 | 1.1236 | 1.4249 | 1.6238 | 1.2387 | 7.0107 | 6.9856 | 6.9918 | 7.0068 | 6.9631 | 6.92 | 0.26264 | 0.28311 | 0.26748 | 0.23909 | 0.26709 | 0.27262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 757970 | 1379 | 744578 | 1425 | 157694.746 | 443.067 | 5.982 | 6.0025 | 6.0525 | 5.9541 | 5.9554 | 6.0219 | 7.0107 | 6.9856 | 6.9918 | 7.0068 | 6.9631 | 6.92 | 948000 | 2000 | 946000 | 1000 | 1887346 | 4734 | 1891000 | 1882612 | 11.45 | 5.9947 | 1.3105 | 6.9797 | 0.26534 | 21.86% | 3.802% | 32.7555 | 45.6667 | 2.2004 | 7.1967 | 1900329.5 | 1886133 | 2279999.4219 | 82.73% | 27 | 0
2024-10-12 | 2025 | 2024 | Year_3 | Year_3 | 2024-10-01 | 31 | 335090.89 | 6:58 | 18:20 | 10975.7 | 11501.5 | 11465.6 | 11421.7 | 11516.6 | 11609.9 | 11579.9 | 11963.4 | 11454.4 | 11404.8 | 11250.4 | 11474.3 | 11451.4 | 11378.5 | 11370.9 | 11541.3 | 11382 | 11514.9 | 11518.2 | 11569.1 | 11503.7 | 11501.7 | 11258.6 | 11388.6 | 11164.2 | 9797.3 | 11187.3 | 11153.8 | 11541 | 11430.4 | 11242.6 | 11491 | 11568.2 | 11597.8 | 11628.9 | 11538.5 | 11689 | 11503.1 | 11457.9 | 11353 | 12358.7 | 11170.6 | 12241.3 | 10981.7 | 11639.1 | 12736.5 | 10856.1 | 12354.5 | 11230.7 | 11578.6 | 11459.4 | 10777.1 | 11833.9 | 11433.7 | 11795.7 | 11429.4 | 10502 | 12065 | 10433.5 | 11933.5 | 11831.6 | 10432.1 | 11665.7 | 11087.6 | 11017.7 | 10320.4 | 10955.3 | 11568.1 | 11830.2 | 10603.5 | 11605.7 | 10190.6 | 11321.7 | 11017 | 10413 | 11626.3 | 10194.5 | 11902.4 | 10423.5 | 11689 | 10855.5 | 11757.2 | 10975.8 | 12173.4 | 10835.3 | 11600.4 | 10790.6 | 9543.1 | 11866.5 | 11297.5 | 10563.7 | 12218.6 | 11859.6 | 10911.2 | 10740.3 | 11932.7 | 10613.6 | 10987.8 | 11887.8 | 10461 | 12055.1 | 10491.7 | 11725.5 | 10736.3 | 11841.3 | 10187.6 | 11905.4 | 10686.2 | 11753.2 | 10639.8 | 11830.6 | 10835.7 | 10553.9 | 11640.1 | 10687.6 | 10483 | 11753.2 | 11896.4 | 11694.4 | 10633.9 | 11825.8 | 10565 | 11491.6 | 10741.4 | 11405.3 | 9879.4 | 11538.2 | 10540.8 | 10746.2 | 10773.6 | 10586.4 | 9143.8 | 10534 | 9354.3 | 10545.6 | 10585.2 | 12300.6 | 10766.7 | 12303.9 | 10998.6 | 12180.5 | 10787.4 | 10966.1 | 10771.5 | 11985 | 12295.9 | 12273.6 | 12184.8 | 12261.9 | 12275.2 | 11088.8 | 12196.3 | 12335.6 | 12361 | 12383.3 | 12342.8 | 12375.8 | 11145.5 | 12432.9 | 11192.5 | 31.329 | 32.0846 | 32.4651 | 33.851 | 32.2691 | 32.1567 | 0 | 46.8 | 0 | 0 | 47.0505 | 47.0505 | 2.175 | 1.3918 | 0.50728 | 0.4259 | 2.1514 | 1.8396 | 4.995 | 4.6317 | 4.1467 | 4.5017 | 5.1933 | 5.49 | 5.6425 | 5.6743 | 5.6998 | 5.6448 | 5.656 | 5.673 | 1.0961 | 1.2119 | 1.0679 | 1.3567 | 1.4992 | 1.1525 | 6.6213 | 6.6057 | 6.5783 | 6.6557 | 6.51 | 6.512 | 0.23389 | 0.25318 | 0.24217 | 0.21235 | 0.23691 | 0.2407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 758876 | 1380 | 745478 | 1427 | 159493.879 | 447.8 | 5.6425 | 5.6743 | 5.6998 | 5.6448 | 5.656 | 5.673 | 6.6213 | 6.6057 | 6.5783 | 6.6557 | 6.51 | 6.512 | 906000 | 1000 | 900000 | 2000 | 1799133 | 4733 | 1803000 | 1794400 | 11.3667 | 5.6651 | 1.2307 | 6.5805 | 0.23653 | 21.72% | 3.594% | 32.3593 | 46.967 | 1.4152 | 4.8264 | 1811213.3 | 1798534 | 2152670.0193 | 83.55% | 26 | 0
2024-10-13 | 2025 | 2024 | Year_3 | Year_3 | 2024-10-01 | 31 | 335090.89 | 7:14 | 18:15 | 6308.8 | 6626.7 | 6658.2 | 6624.8 | 6701.1 | 6731.9 | 6717.3 | 6965 | 6625.1 | 6579.3 | 6508.1 | 6618.8 | 6626.5 | 6549.1 | 6664.7 | 6725 | 6630.1 | 6670.4 | 6677.1 | 6708.1 | 6680.6 | 6662.4 | 6548.4 | 6610.9 | 6462.4 | 5649.6 | 6470.5 | 6460.5 | 6689.1 | 6650.8 | 6558.4 | 6673.5 | 6683.7 | 6689 | 6728.9 | 6670.3 | 6778.7 | 6678.9 | 6671.8 | 6607.7 | 7355.9 | 6584.2 | 7282.5 | 6447 | 6869.8 | 7689.7 | 6337.7 | 7370.3 | 6536.2 | 6706.6 | 6542.7 | 6200 | 6833 | 6662.2 | 6811.9 | 6650.6 | 6018.6 | 6945.6 | 6031.5 | 6883.8 | 6740.1 | 6020 | 6594.3 | 6253.2 | 6258.4 | 5878.7 | 6174.1 | 6579 | 6761.9 | 6053.9 | 6610.1 | 5783.3 | 6480.7 | 6262.5 | 5928.3 | 6624.1 | 5783.6 | 6811.9 | 5942.5 | 6668.3 | 6232.8 | 6755.1 | 6305.1 | 6976.3 | 6221.1 | 6641.8 | 6211.6 | 5460.5 | 6817.2 | 6548.8 | 6040.7 | 7046.6 | 6844.4 | 6307.2 | 6224.4 | 6879.1 | 6141.6 | 6354.7 | 6909.1 | 6054 | 7048.4 | 6075 | 6821.5 | 6230.6 | 6933.8 | 5918.5 | 6966.3 | 6208.1 | 6878 | 6161.4 | 6959.2 | 6333.1 | 6131 | 6764.1 | 6207.8 | 6086.9 | 6879.8 | 6951.5 | 6823.7 | 6216.9 | 6854.3 | 6159.4 | 6700.8 | 6211.2 | 6658.8 | 5699.7 | 6724.7 | 6165.4 | 6251.7 | 6314.8 | 6200.8 | 5344.1 | 6190.4 | 5476.3 | 6209.5 | 6218.2 | 7217.2 | 6241.8 | 7216.9 | 6352 | 7135.4 | 6281.6 | 6389.2 | 6300.1 | 6947 | 7215.8 | 7050.7 | 7076.3 | 7120.7 | 7158 | 6421.8 | 7131.4 | 7157.6 | 7188.1 | 7277.4 | 7210.8 | 7198.1 | 6420 | 7197.2 | 6421.8 | 31.44 | 30.69 | 30.97 | 32.41 | 30.8 | 30.8 | 0 | 40.13 | 0 | 0 | 39.87 | 40.08 | 1.81 | 0.91 | 0.3 | 0.05 | 1.46 | 1.46 | 3.85 | 3.58 | 3.57 | 2.41 | 3.4 | 3.4 | 3.15 | 3.43 | 3.45 | 3.31 | 3.32 | 3.4 | 0.63 | 0.73 | 0.64 | 0.79 | 0.62 | 0.72 | 3.33 | 3.63 | 3.61 | 3.52 | 0 | 3.53 | 0.19 | 0.21 | 0.18 | 0.18 | 0 | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 759401 | 1382 | 746002 | 1428 | 160540.279 | 452.6 | 3.15 | 3.43 | 3.45 | 3.31 | 3.32 | 3.4 | 3.33 | 3.63 | 3.61 | 3.52 | 0 | 3.53 | 525000 | 2000 | 524000 | 1000 | 1046400 | 4800 | 1046000 | 1041600 | 11.0167 | 3.3433 | 0.68833 | 3.524 | 0.19 | 20.59% | 5.392% | 31.185 | 40.0267 | 0.99833 | 3.3683 | 1049785.6 | 1046333 | 1202970.7589 | 86.98% | 28 | 76301
2024-10-14 | 2025 | 2024 | Year_3 | Year_3 | 2024-10-01 | 31 | 335090.89 | 6:55 | 18:18 | 6504 | 6776 | 6775 | 6760 | 6802 | 6841 | 6833 | 7659 | 6778 | 6778 | 6648 | 6767 | 6721 | 6682 | 6732 | 6866 | 6625 | 6690 | 6757 | 6749 | 6750 | 6794 | 6708 | 6746 | 6533 | 5769 | 6572 | 6539 | 6699 | 6746 | 6734 | 6601 | 6726 | 6749 | 6807 | 6732 | 6790 | 6691 | 6686 | 6632 | 7315 | 6594 | 7248 | 6499 | 6890 | 7663 | 6406 | 7350 | 6835 | 6669 | 6655 | 6357 | 6966 | 6743 | 6939 | 6782 | 6200 | 7076 | 6212 | 7020 | 6947 | 6204 | 6767 | 6451 | 6420 | 6013 | 6375 | 6699 | 6877 | 6173 | 6715 | 5916 | 6626 | 6325 | 6115 | 6725 | 5931 | 6963 | 6134 | 6808 | 6327 | 6825 | 6405 | 7044 | 6311 | 6734 | 6300 | 5558 | 6885 | 6614 | 6159 | 7113 | 6896 | 6384 | 6303 | 6954 | 6229 | 6416 | 6932 | 6123 | 7046 | 6139 | 6838 | 6289 | 6914 | 5977 | 6944 | 6245 | 6856 | 6248 | 6908 | 6325 | 6190 | 6777 | 6254 | 6136 | 6872 | 6929 | 6813 | 6225 | 6886 | 6181 | 6694 | 6248 | 6756 | 6640 | 6720 | 6179 | 6267 | 6317 | 6211 | 5369 | 6185 | 5466 | 6289 | 6304 | 7486 | 6405 | 7334 | 6443 | 7228 | 6405 | 7297 | 6334 | 7102 | 7366 | 7207 | 7223 | 7249 | 7197 | 6568 | 7277 | 7305 | 7348 | 7434 | 7345 | 7323 | 6583 | 7360 | 6547 | 31.3525 | 29.8932 | 30.3422 | 31.0466 | 30.6708 | 29.965 | 0 | 37.9 | 0 | 0 | 38.8 | 37.217 | 2.5323 | 1.7559 | 1.0886 | 1.0108 | 1.462 | 2.3634 | 6.9533 | 6.7683 | 4.9967 | 5.6633 | 3.3983 | 6.1017 | 3.4001 | 3.4005 | 3.4337 | 3.3436 | 3.3326 | 3.4086 | 0.68479 | 0.69636 | 0.65833 | 0.80733 | 0.84549 | 0.67854 | 3.7063 | 3.6821 | 3.6948 | 3.6584 | 3.5876 | 3.6214 | 0.18134 | 0.19886 | 0.17999 | 0.17371 | 0 | 0.18614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 759935 | 1385 | 746531 | 1431 | 161599.3 | 457.6 | 3.4001 | 3.4005 | 3.4337 | 3.3436 | 3.3326 | 3.4086 | 3.7063 | 3.6821 | 3.6948 | 3.6584 | 3.5876 | 3.6214 | 534000 | 3000 | 529000 | 3000 | 1059021 | 5000 | 1057000 | 1054021 | 11.3833 | 3.3865 | 0.72847 | 3.6584 | 0.18401 | 21.51% | 5.03% | 30.545 | 37.9723 | 1.7022 | 5.6469 | 1065865 | 1059021 | 1242718.951 | 85.22% | 28 | 55614
2024-10-15 | 2025 | 2024 | Year_3 | Year_3 | 2024-10-01 | 31 | 335090.89 | 6:55 | 18:15 | 10332 | 10786 | 10796 | 10732 | 10846 | 10334 | 10885 | 11195 | 10773 | 10774 | 10615 | 10703 | 10670 | 10678 | 10740 | 10808 | 10579 | 10711 | 10792 | 10804 | 10801 | 10869 | 10720 | 10798 | 10513 | 9243 | 10551 | 10522 | 10834 | 10729 | 10604 | 10816 | 10872 | 10906 | 10924 | 10827 | 10959 | 10819 | 10798 | 10717 | 11553 | 10539 | 11441 | 10374 | 10971 | 11964 | 10216 | 11557 | 10592 | 10903 | 10800 | 10167 | 11105 | 10695 | 11089 | 10777 | 9894 | 11308 | 9856 | 11227 | 11113 | 9850 | 10921 | 10447 | 10405 | 9767 | 10340 | 10937 | 11113 | 10039 | 10953 | 9659 | 10662 | 10425 | 9826 | 10967 | 9621 | 11163 | 9851 | 11003 | 10311 | 11131 | 10453 | 11482 | 10291 | 11010 | 10246 | 9069 | 11228 | 10757 | 10049 | 11526 | 11219 | 10371 | 10206 | 11293 | 10158 | 10530 | 10912 | 10032 | 11439 | 10046 | 11167 | 10297 | 11250 | 9759 | 11326 | 10240 | 11199 | 10224 | 11295 | 10393 | 10132 | 11166 | 10258 | 10065 | 11237 | 11402 | 11178 | 10234 | 11323 | 10157 | 10990 | 10300 | 10936 | 9513 | 11091 | 10153 | 10389 | 10440 | 10206 | 8826 | 10221 | 9052 | 10291 | 10322 | 11226 | 10491 | 11891 | 10681 | 11803 | 10544 | 11837 | 10434 | 11591 | 11943 | 11782 | 11732 | 11796 | 11820 | 10798 | 11823 | 11822 | 11857 | 11935 | 11899 | 11920 | 10808 | 11891 | 10801 | 31.3508 | 32.5602 | 32.7999 | 34.1287 | 30.6642 | 32.754 | 0 | 44.08 | 0 | 0 | 42.8 | 45.6 | 2.6326 | 1.6598 | 0.77635 | 0.84757 | 1.4481 | 2.3318 | 5.9917 | 5.9667 | 5.6867 | 4.8667 | 3.3983 | 5.975 | 5.2776 | 5.3107 | 5.3358 | 5.2862 | 5.3792 | 5.4441 | 1.0247 | 1.1778 | 0.9771 | 1.2431 | 1.43 | 1.1527 | 6.1898 | 6.1823 | 6.1351 | 6.202 | 6.1668 | 6.2762 | 0.23687 | 0.25721 | 0.23984 | 0.21529 | 0 | 0.24302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760787 | 1386 | 747395 | 1432 | 163307.3 | 462.6 | 5.2776 | 5.3107 | 5.3358 | 5.2862 | 5.3792 | 5.4441 | 6.1898 | 6.1823 | 6.1351 | 6.202 | 6.1668 | 6.2762 | 852000 | 1000 | 864000 | 1000 | 1708000 | 5000 | 1714000 | 1703000 | 11.3333 | 5.3389 | 1.1676 | 6.192 | 0.23845 | 21.87% | 3.851% | 32.3763 | 44.16 | 1.616 | 5.3142 | 1720381 | 1708000 | 2028245.5085 | 84.21% | 24 | 0
2024-10-16 | 2025 | 2024 | Year_3 | Year_3 | 2024-10-01 | 31 | 335090.89 | 6:50 | 18:16 | 10484 | 10888 | 10878 | 10857 | 10916 | 11007 | 10962 | 11293 | 10902 | 10863 | 10749 | 9803 | 10805 | 10803 | 10762 | 10855 | 10707 | 10798 | 10896 | 10975 | 10882 | 10892 | 10704 | 10800 | 10627 | 9398 | 10658 | 10628 | 10924 | 10825 | 10711 | 10911 | 11036 | 11087 | 11089 | 10993 | 11083 | 10936 | 10922 | 10844 | 11790 | 10711 | 11689 | 10569 | 11150 | 12257 | 10467 | 11779 | 10696 | 11009.6 | 10898 | 10317 | 11214.8 | 10776 | 11208 | 10867 | 10066 | 11491 | 10009 | 11104 | 11245 | 10008 | 11074 | 10608 | 10567 | 9927 | 10490 | 11064 | 11264 | 10206 | 11070 | 9806 | 10816 | 10816 | 10008 | 11079 | 9777 | 11341 | 10046 | 11140 | 10457 | 11255 | 10557 | 11643 | 10414 | 11107 | 10382 | 9192 | 11302 | 10861 | 10183 | 11659 | 11313 | 10480 | 10330 | 11397 | 10250 | 10618 | 11419 | 10133 | 11563 | 10150 | 11258 | 10399 | 11365 | 9874 | 11440 | 10362 | 11276 | 10186 | 11400 | 10542 | 10244 | 11233 | 10370 | 10183 | 11329 | 11500 | 11273 | 10337 | 11424 | 10264 | 11095 | 10435 | 11038 | 9632 | 11178 | 10269 | 10460 | 10479 | 10290 | 8892 | 10284 | 9099 | 10284 | 10302 | 11954 | 10486 | 11963 | 10712 | 11869 | 10560 | 10459 | 10744 | 11631 | 12012 | 11633 | 11728 | 11890 | 11915 | 10810 | 11875 | 11877 | 11915 | 11988 | 11949.8 | 11972 | 10810 | 11998 | 10839 | 31.3127 | 33.3866 | 34.1111 | 34.7014 | 33.5934 | 33.6263 | 0 | 47.5 | 0 | 0 | 48.6 | 47.9843 | 2.5218 | 1.7614 | 0.94799 | 0.711 | 2.4385 | 2.0472 | 6.0167 | 6.2017 | 4.7133 | 5.51 | 5.99 | 5.4967 | 5.4466 | 5.4898 | 5.5474 | 5.4711 | 5.5308 | 5.547 | 1.1154 | 1.2004 | 1.0764 | 1.3468 | 1.4654 | 1.1687 | 6.3103 | 6.319 | 6.3134 | 6.3651 | 6.3044 | 6.3249 | 0.26052 | 0.27885 | 0.26267 | 0.2295 | 0.25573 | 0.25922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 761649 | 1388 | 748263 | 1433 | 165030.3 | 467.6 | 5.4466 | 5.4898 | 5.5474 | 5.4711 | 5.5308 | 5.547 | 6.3103 | 6.319 | 6.3134 | 6.3651 | 6.3044 | 6.3249 | 862000 | 2000 | 868000 | 1000 | 1723000 | 5000 | 1727000 | 1718000 | 11.4333 | 5.5054 | 1.2289 | 6.3229 | 0.25775 | 22.32% | 4.076% | 33.4553 | 48.0281 | 1.738 | 5.6547 | 1736824.2 | 1723000 | 2065844.9112 | 83.4% | 24 | 0
2024-10-17 | 2025 | 2024 | Year_3 | Year_3 | 2024-10-01 | 31 | 335090.89 | 6:49 | 18:13 | 9408 | 9876 | 9886 | 9865 | 9931 | 10001 | 9959 | 10337 | 9949.6 | 9815.7 | 9871.1 | 8925.6 | 9915.9 | 9970 | 9840.9 | 9940.9 | 9780.6 | 9897.4 | 9962.4 | 10021.7 | 9892 | 9923.1 | 9636.6 | 9749.3 | 9562 | 8415.7 | 9660.4 | 9602.9 | 9856.8 | 9719.6 | 9570.9 | 9840.6 | 9618.8 | 9683.1 | 9891.7 | 9763.7 | 9899.6 | 9700.6 | 9655.1 | 9542.6 | 10821.3 | 9651.7 | 10672.5 | 9451.3 | 10038.6 | 11267.1 | 9443.2 | 10890 | 9760.8 | 10084.2 | 9949.5 | 9359.7 | 10249.4 | 9877.1 | 10228.4 | 9866.2 | 9087.3 | 10477.7 | 9083.2 | 10321.1 | 10310.8 | 9065.4 | 10059.9 | 9562 | 9413.3 | 8792 | 9316.2 | 9865 | 10155.3 | 8977.7 | 9863 | 8578.1 | 9735 | 9270 | 8934 | 9796 | 8613 | 10256 | 8943 | 9971 | 9254.6 | 9968.3 | 9391 | 10507.2 | 9303.8 | 10016.6 | 9301.5 | 8258.9 | 10072.7 | 9790.2 | 8959.8 | 10394.4 | 10010.4 | 9177.9 | 9049 | 10101 | 8959.4 | 9320.8 | 10079.9 | 8879.3 | 10266.7 | 8858.8 | 9939.9 | 9111.7 | 10124.5 | 8662.6 | 10225.7 | 9172.5 | 10138.1 | 9187.2 | 10346.4 | 9473.5 | 9036.8 | 10065.8 | 9158.7 | 9035.7 | 10228.5 | 10503.9 | 10234.2 | 9401.7 | 10519.1 | 9367 | 10066.7 | 9468.8 | 10102.5 | 8810.1 | 10271.2 | 9352 | 9484.7 | 9480.4 | 9342.7 | 8062.8 | 9297.7 | 8201.9 | 9225.1 | 9208.9 | 10814.5 | 9320.9 | 10815.7 | 9566.8 | 10753.1 | 9404 | 9548.2 | 9341.7 | 10267.6 | 10643.4 | 10645.6 | 10588.9 | 10736.9 | 10782.6 | 9588 | 10612.7 | 10639.2 | 10702 | 10635.4 | 10583.1 | 10609.3 | 9424 | 10814.8 | 9577.2 | 31.3455 | 33.226 | 33.7337 | 34.7369 | 33.3498 | 33.5196 | 0 | 46,7 | 0 | 0 | 47.8 | 47.1561 | 2.7277 | 1.6403 | 0.96357 | 0.8699 | 2.5876 | 2.3691 | 5.6667 | 6.2867 | 4.275 | 4.535 | 5.1333 | 6.0683 | 4.9342 | 4.8784 | 4.9407 | 4.8515 | 4.9378 | 4.9013 | 1.0178 | 1.077 | 0.96042 | 1.195 | 1.3059 | 1.0257 | 5.7245 | 5.616 | 5.618 | 5.6514 | 5.6237 | 5.5762 | 0.23149 | 0.24307 | 0.22992 | 0.20027 | 0.22291 | 0.22628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 762427 | 1390 | 749042 | 1435 | 166585.9 | 471.933 | 4.9342 | 4.8784 | 4.9407 | 4.8515 | 4.9378 | 4.9013 | 5.7245 | 5.616 | 5.618 | 5.6514 | 5.6237 | 5.5762 | 778000 | 2000 | 779000 | 2000 | 1555600 | 4333 | 1553000 | 1551267 | 11.4 | 4.9073 | 1.097 | 5.635 | 0.22566 | 22.35% | 4.005% | 33.3186 | 47.478 | 1.8597 | 5.3275 | 1561043.7 | 1555580 | 1859818.517 | 83.64% | 27 | 0
2024-10-18 | 2025 | 2024 | Year_3 | Year_3 | 2024-10-01 | 31 | 335090.89 | 7:00 | 18:12 | 9130 | 9577 | 9546 | 9506 | 9582 | 9596 | 9600 | 9899 | 9524 | 9390 | 9339 | 8505 | 9269 | 9364 | 9307 | 9344 | 9318 | 9300 | 9382 | 9540 | 9260 | 9201 | 9005 | 9124 | 9050 | 7965 | 9170 | 9043 | 9217 | 9141 | 9038 | 9227 | 9595 | 9633 | 9411 | 9316 | 9464 | 9288 | 9259 | 9251 | 9693 | 8680 | 9580 | 8366 | 9062 | 10087 | 8477 | 9755 | 9279 | 9592 | 9453 | 9060 | 9764 | 9358 | 9900 | 9408 | 8953 | 10306 | 8747 | 10302 | 10076 | 8676 | 9935 | 9396 | 9478 | 8958 | 9314 | 10001 | 10093 | 9122 | 9876 | 8549 | 9642 | 9206 | 8879 | 9900 | 8657 | 10114 | 8780 | 9808 | 9372 | 10118 | 9523 | 10561 | 9409 | 10117 | 9456 | 8362 | 10406 | 9958 | 9309 | 10834 | 10527 | 9642 | 9451 | 10564 | 9402 | 9735 | 10552 | 9291 | 10846 | 9305 | 10530 | 9537 | 10693 | 9100 | 10739 | 9567 | 10645 | 9618 | 10788 | 9804 | 9352 | 10236 | 9462 | 9234 | 10414 | 10389 | 10362 | 9139 | 10274 | 9105 | 10300 | 9634 | 10130 | 8523 | 9948 | 8891 | 9023 | 9026 | 8852 | 7673 | 8765 | 7727 | 8595 | 8535 | 10590 | 9042 | 10491 | 9166 | 10194 | 8908 | 9002 | 8768 | 10357 | 10725 | 10551 | 10514 | 10569 | 10576 | 9495 | 10534 | 10835 | 10788 | 10771 | 10652 | 10671 | 9574 | 10790 | 9631 | 31.3432 | 32.9817 | 33.4336 | 34.6011 | 33.3767 | 33.1482 | 0 | 44.4 | 0 | 0 | 46 | 45.5 | 1.9603 | 0.60312 | 0.39087 | 0.16189 | 1.9119 | 1.3991 | 5.165 | 4.1917 | 4.1 | 3.54 | 4.95 | 4.5467 | 4.6205 | 4.4957 | 4.348 | 4.7913 | 4.9702 | 4.8747 | 0.95175 | 0.96923 | 0.84718 | 1.1839 | 1.327 | 0.99857 | 5.4389 | 5.2411 | 5.0262 | 5.6651 | 5.6251 | 5.5666 | 0.19809 | 0.21205 | 0.18814 | 0.18581 | 0.21903 | 0.22054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 763173 | 1392 | 749824 | 1437 | 168109.1 | 476.7 | 4.6205 | 4.4957 | 4.348 | 4.7913 | 4.9702 | 4.8747 | 5.4389 | 5.2411 | 5.0262 | 5.6651 | 5.6251 | 5.5666 | 746000 | 2000 | 782000 | 2000 | 1523200 | 4767 | 1524000 | 1518433 | 11.2 | 4.6834 | 1.0463 | 5.4272 | 0.20394 | 22.34% | 3.758% | 33.1474 | 45.3 | 1.0712 | 4.4156 | 1532502 | 1522800 | 1795045.3065 | 84.83% | 26 | 20755
2024-10-19 | 2025 | 2024 | Year_3 | Year_3 | 2024-10-01 | 31 | 335090.89 | 6:59 | 18:10 | 8839.6 | 9312.1 | 9200.8 | 9108.6 | 9231 | 9362 | 9409.6 | 9764.2 | 9266.8 | 9227.3 | 9179.7 | 9328.3 | 9311.3 | 9310.2 | 9390 | 9400.4 | 9371.9 | 9519.8 | 9513.2 | 9565.7 | 9587.6 | 9546.8 | 9493.8 | 9562 | 9471.7 | 8205 | 9280.3 | 9377 | 9792.7 | 9678.2 | 9577.6 | 9810.8 | 9811.9 | 9808.4 | 9868.3 | 9770.4 | 9943.4 | 9801.2 | 9770.3 | 9701 | 11024.3 | 9904.4 | 11003.3 | 9851.7 | 10413.3 | 11543 | 9566.8 | 10933 | 9168.1 | 9394.5 | 9447 | 8922.6 | 9799.7 | 9348.4 | 9813.5 | 9510.3 | 8641 | 10016.3 | 8517.8 | 9866 | 9690.4 | 8479.7 | 9550.6 | 9019.8 | 9109.9 | 8582.4 | 9021.5 | 9660.1 | 9773.5 | 8802 | 9581.2 | 8489 | 9320.8 | 9118.4 | 8532 | 9638.1 | 8432.4 | 9744.2 | 8560.4 | 9620.1 | 9081.7 | 9827.6 | 9259.8 | 10260.1 | 9092.8 | 9769.3 | 9068 | 8043.5 | 10127.1 | 9647.6 | 9050.5 | 10505.5 | 10144.1 | 9317.8 | 9163.3 | 10308.2 | 9111.2 | 9436.1 | 10325 | 9090.2 | 10597.6 | 9153.7 | 10292.5 | 9403.9 | 10492.2 | 8961.6 | 10568.5 | 9466.8 | 10406.6 | 9402.8 | 10586.3 | 9727.4 | 9150.8 | 10232.7 | 9418.9 | 9229.7 | 10421.1 | 10634.6 | 10391.4 | 9509.2 | 10636.9 | 9468 | 10249.8 | 9627.2 | 10244 | 8910.1 | 10360 | 9474.5 | 9557.5 | 9526.5 | 9467 | 8172.7 | 9277.6 | 8126.8 | 9290.7 | 9186.1 | 10793.9 | 9412.1 | 10852.8 | 9634.3 | 10793.7 | 9510.2 | 9701.7 | 9415.3 | 10511 | 10954.8 | 10714.6 | 10676.8 | 10742.6 | 10773 | 9736.1 | 10780.7 | 10696.2 | 10767 | 10783.5 | 10746.1 | 10805.4 | 9678.7 | 10820.5 | 9718.6 | 31.3446 | 33.8465 | 34.438 | 35.0394 | 34.1361 | 33.9927 | 0 | 45.8 | 0 | 0 | 47.1 | 46.3103 | 1.771 | 0.79649 | 0.29447 | 0.095579 | 1.837 | 1.2697 | 4.4167 | 7.3133 | 3.3567 | 2.68 | 4.6967 | 5.1783 | 4.5084 | 4.7663 | 4.9605 | 4.5916 | 4.9521 | 4.9178 | 0.92524 | 1.0627 | 0.97138 | 1.1414 | 1.357 | 1.0397 | 5.3397 | 5.6152 | 5.7801 | 5.4662 | 5.7481 | 5.697 | 0.20112 | 0.22606 | 0.21368 | 0.17861 | 0.21501 | 0.2143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 763930 | 1393 | 750612 | 1438 | 169647.88 | 481.467 | 4.5084 | 4.7663 | 4.9605 | 4.5916 | 4.9521 | 4.9178 | 5.3397 | 5.6152 | 5.7801 | 5.4662 | 5.7481 | 5.697 | 757000 | 1000 | 788000 | 1000 | 1538780 | 4767 | 1543000 | 1534013 | 11.1833 | 4.7828 | 1.0829 | 5.6077 | 0.20813 | 22.64% | 3.712% | 33.7995 | 46.4034 | 1.0107 | 4.6069 | 1547155.1 | 1538334 | 1843475.0787 | 83.45% | 29 | 70213
2024-10-20 | 2025 | 2024 | Year_3 | Year_3 | 2024-10-01 | 31 | 335090.89 | 6:58 | 18:11 | 8352.3 | 8771.1 | 8663.6 | 8639.9 | 8693.3 | 8728.5 | 8770.4 | 9071.3 | 8708.3 | 8692.8 | 8535.8 | 8697.5 | 8597 | 8597.6 | 8582.4 | 8652 | 8518.7 | 8570.8 | 8582.3 | 8656.5 | 8556.3 | 8557.1 | 8427.9 | 8501.6 | 8401.7 | 7325.3 | 8381.9 | 8395.2 | 8686 | 8603.2 | 8539.8 | 8688.4 | 8715.7 | 8718 | 8697.8 | 8663.4 | 8841.3 | 8726.1 | 8704.3 | 8639.8 | 9749.8 | 8671.1 | 9606.6 | 8547.4 | 9050.3 | 10117.7 | 8421.8 | 9727.3 | 8449.3 | 8688.3 | 8591.7 | 8070.8 | 8893.6 | 8590.1 | 8823.6 | 8666.2 | 7834.4 | 9042.5 | 7828.8 | 8981.3 | 8884.1 | 7829.4 | 8738.2 | 8272.9 | 8207.6 | 7729.3 | 8119.1 | 8657.9 | 8806.2 | 7904.3 | 8615.7 | 7603.5 | 8413.7 | 8182.7 | 7735 | 8648 | 7559.3 | 8879 | 7753 | 8689.7 | 8141.9 | 8820.7 | 8279.4 | 9198.7 | 8146.6 | 8758.9 | 8107.8 | 7194.9 | 9009.8 | 8576.6 | 8040.9 | 9373 | 9036.7 | 8273.8 | 8172.6 | 9140.9 | 8036.5 | 8270.6 | 8980.1 | 7735.6 | 9169.9 | 7800.9 | 8776.3 | 7906.4 | 8786.2 | 7469.7 | 8752.4 | 7631.5 | 8612 | 7648.7 | 8452.3 | 7582.8 | 7540.3 | 8025.9 | 7520.9 | 7285.8 | 8140.3 | 8022.4 | 7989.9 | 7073.1 | 7914.3 | 6977.6 | 7862.7 | 7271.8 | 7601.3 | 6541.5 | 7640.9 | 6975.3 | 7086.1 | 7093.6 | 7059.7 | 6058 | 7210.1 | 6473.7 | 7220 | 7224 | 8431.5 | 7217.3 | 8438.2 | 7389.4 | 8337.9 | 7360.8 | 7563.1 | 7414.2 | 8276.3 | 8591.1 | 8601.2 | 8475.4 | 8467 | 8436.2 | 7560.5 | 8487 | 9232 | 9028.6 | 8891.6 | 8791 | 8748.2 | 7681.4 | 9242 | 7895.5 | 30.3221 | 32.186 | 32.627 | 32.7723 | 32.0181 | 32.1519 | 0 | 41.8 | 0 | 0 | 40.5229 | 40.2584 | 3.5969 | 3.202 | 2.4687 | 2.2757 | 3.8219 | 3.5974 | 8.0683 | 7.9383 | 8.9183 | 8.0967 | 8.2617 | 9.79 | 4.2619 | 4.2802 | 4.3848 | 4.1791 | 3.858 | 3.8678 | 0.90844 | 0.92559 | 0.8898 | 1.0587 | 1.0193 | 0.78076 | 4.9247 | 4.921 | 5.0003 | 4.8636 | 4.3945 | 4.37 | 0.20093 | 0.21838 | 0.20266 | 0.17724 | 0.18048 | 0.18179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 764613 | 1395 | 751253 | 1439 | 170967.613 | 486.267 | 4.2619 | 4.2802 | 4.3848 | 4.1791 | 3.858 | 3.8678 | 4.9247 | 4.921 | 5.0003 | 4.8636 | 4.3945 | 4.37 | 683000 | 2000 | 641000 | 1000 | 1319733 | 4800 | 1321000 | 1314933 | 11.2167 | 4.1386 | 0.93044 | 4.7457 | 0.19358 | 22.48% | 4.079% | 32.0129 | 40.8604 | 3.1604 | 8.5122 | 1327685.8 | 1319400 | 1579107 | 83.55% | 24 | 88290
2024-10-21 | 2025 | 2024 | Year_3 | Year_3 | 2024-10-01 | 31 | 335090.89 | 7:12 | 18:09 | 8590.5 | 9086 | 9017.3 | 8956.9 | 9065.1 | 9203.6 | 9194.6 | 9563.6 | 9032 | 8881.2 | 9012.3 | 9134 | 9164.1 | 9119.8 | 9202.7 | 9271.5 | 9166.8 | 9241.4 | 9225 | 9283.5 | 9224.4 | 9196.8 | 9024.9 | 9111.3 | 8950.9 | 7857.9 | 8987.5 | 8991 | 9288.5 | 9195.4 | 9063.1 | 9248.3 | 9214.5 | 9251.3 | 9287.2 | 9210.4 | 9374.5 | 9225.4 | 9204.7 | 9086.4 | 10185.2 | 9057.5 | 10046.6 | 8881.6 | 9462.1 | 10643.6 | 8812.7 | 10198.3 | 9066.9 | 9258 | 9177.8 | 8626.3 | 9535.2 | 9222.2 | 9479.1 | 9223.8 | 8360.7 | 9692.2 | 8316.6 | 9576.4 | 9430.1 | 8309.3 | 9219.2 | 8745.4 | 8743.4 | 8175 | 8672.4 | 9169.8 | 9419.6 | 8381.8 | 9202.8 | 8004.5 | 8994 | 8680.2 | 8242.9 | 9211.3 | 8032 | 9443.9 | 8221.2 | 9239.6 | 8533.9 | 9256.3 | 8664.5 | 9465.5 | 8531.7 | 9158.6 | 8546.8 | 7541.2 | 9431.4 | 9021.9 | 8419.8 | 9812.5 | 9461.1 | 8651.7 | 8522.2 | 9568.7 | 8509 | 8802.3 | 9579.4 | 8411 | 9727.2 | 8429.6 | 9450.2 | 8650.7 | 9574.3 | 8203.5 | 9622.2 | 8602.9 | 9456 | 8587.7 | 9571.4 | 8372.1 | 8488.6 | 9406.6 | 8625.1 | 8438 | 9512.2 | 9673 | 9457.1 | 8596.3 | 9622.2 | 8491.1 | 9266.8 | 8598.1 | 9218.5 | 7962.5 | 9346.7 | 8558.7 | 8640.6 | 8787.9 | 8606.8 | 7437.3 | 8605.6 | 7610.9 | 8626.5 | 8628.3 | 9981.3 | 8628.9 | 10018.4 | 8803.6 | 9952.6 | 8727.2 | 8880.4 | 8732.5 | 9566.4 | 9919.7 | 9832.5 | 9788.9 | 9878.5 | 9895 | 8854.4 | 9875.8 | 9796.3 | 9884.7 | 9877.2 | 9825.6 | 9869.9 | 8796 | 9929.2 | 8834.3 | 27.22 | 30.22 | 31.22 | 31.22 | 30.54 | 30.18 | 0 | 41.7 | 0 | 0 | 42 | 41.54 | 3.59 | 3.72 | 2.33 | 2.33 | 3.87 | 3.24 | 13.05 | 12.96 | 12.35 | 12.35 | 12.2 | 12.12 | 4.42 | 4.51 | 4.42 | 4.42 | 4.46 | 4.42 | 0.94 | 1.02 | 1.12 | 1.12 | 1.21 | 0.94 | 5.14 | 5.22 | 5.18 | 5.18 | 5.08 | 5.05 | 0.22 | 0.24 | 0.2 | 0.2 | 0.22 | 0.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 765338 | 1397 | 751976 | 1441 | 172410.613 | 491.267 | 4.42 | 4.51 | 4.42 | 4.42 | 4.46 | 4.42 | 5.14 | 5.22 | 5.18 | 5.18 | 5.08 | 5.05 | 725000 | 2000 | 723000 | 2000 | 1443000 | 5000 | 1444000 | 1438000 | 10.95 | 4.4417 | 1.0583 | 5.1417 | 0.21833 | 23.83% | 4.246% | 30.1 | 41.7467 | 3.18 | 12.505 | 1451259.5 | 1441200 | 1713056.8886 | 84.13% | 24 | 24223
2024-10-22 | 2025 | 2024 | Year_3 | Year_3 | 2024-10-01 | 31 | 335090.89 | 7:02 | 18:06 | 10040.7 | 10561.6 | 10512.7 | 10466.9 | 10526 | 10652.5 | 10646.1 | 11075.1 | 10522.5 | 10428.7 | 10385.9 | 10557.4 | 10478.9 | 10484 | 10470.4 | 10539.1 | 10440.1 | 10503.2 | 10511 | 10582 | 10517.2 | 10481.8 | 10270.5 | 10397.7 | 10192.5 | 8953.8 | 10231.9 | 10206.9 | 10521.6 | 10396.2 | 10274.4 | 10501.2 | 10514.3 | 10566.8 | 10584.3 | 10477.4 | 10663.3 | 10503.6 | 10477.2 | 10363.7 | 11556.6 | 10264.5 | 11401.1 | 10086.9 | 10714.6 | 12074.7 | 10030.3 | 11564 | 10399.8 | 10578.8 | 10473.9 | 9848.9 | 10851.8 | 10464.9 | 10795.8 | 10579.9 | 9538.2 | 11081.7 | 9548.7 | 10955.1 | 10777 | 9545.9 | 10566.9 | 10055.2 | 10003.9 | 9401.9 | 9949.7 | 10568.2 | 10774.9 | 9694.8 | 10615.8 | 9309.6 | 10305.9 | 10063.2 | 9470.1 | 10664.4 | 9299.1 | 10839.8 | 9456.3 | 10647.3 | 9895.1 | 10751.3 | 10018.9 | 11155.8 | 9858.7 | 10557.1 | 9797 | 8674.8 | 10829 | 10344.5 | 9669.5 | 11247.6 | 10824.1 | 9888.9 | 9719.7 | 10961.7 | 9733.8 | 10112.5 | 10969.2 | 9649.2 | 11134.4 | 9658.4 | 10809.9 | 9905.6 | 10948.7 | 9394.8 | 11011.1 | 9871.1 | 10838.4 | 9795.2 | 10960.1 | 10014 | 9734.9 | 10777.7 | 9879.4 | 9676.2 | 10878.4 | 11072.4 | 10825.1 | 9855 | 11007 | 9709.4 | 10603.1 | 9908.2 | 10557.9 | 9163.1 | 10698.1 | 9779.7 | 9940.2 | 9998.4 | 9822.9 | 8479.4 | 9793.8 | 8669.5 | 9811.5 | 9834.9 | 11497.5 | 9919.3 | 11560.7 | 10165.1 | 11444 | 10017.1 | 10188.6 | 9967.6 | 11128.1 | 11573.3 | 11382.6 | 11329.7 | 11428.5 | 11455.3 | 10255.7 | 11440 | 11381.1 | 11472.7 | 11557.3 | 11495 | 11573.6 | 10266 | 11501.9 | 10262.7 | 30.2481 | 30.771 | 31.4179 | 32.2251 | 31.0805 | 30.8444 | 0 | 43.7 | 0 | 0 | 44.7 | 43.3912 | 2.15 | 1.4021 | 0.48551 | 0.46281 | 2.186 | 1.6973 | 5.3133 | 5.3367 | 4.8267 | 4.925 | 5.92 | 5.31 | 5.002 | 5.0284 | 5.0653 | 4.9932 | 5.0247 | 5.015 | 1.0445 | 1.1375 | 1.009 | 1.2613 | 1.3637 | 1.0718 | 5.9757 | 5.9626 | 5.9532 | 5.9824 | 5.8601 | 5.8828 | 0.23398 | 0.25062 | 0.23381 | 0.20377 | 0.22834 | 0.23458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 766168 | 1399 | 752807 | 1443 | 174066.214 | 496.2 | 5.002 | 5.0284 | 5.0653 | 4.9932 | 5.0247 | 5.015 | 5.9757 | 5.9626 | 5.9532 | 5.9824 | 5.8601 | 5.8828 | 830000 | 2000 | 831000 | 2000 | 1655601 | 4933 | 1657000 | 1650668 | 11.0667 | 5.0215 | 1.148 | 5.9361 | 0.23085 | 22.86% | 3.889% | 31.0978 | 43.9304 | 1.3973 | 5.2719 | 1666040.9 | 1654867 | 1963075.3264 | 84.3% | 25 | 0
2024-10-23 | 2025 | 2024 | Year_3 | Year_3 | 2024-10-01 | 31 | 335090.89 | 7:03 | 18:07 | 10223.4 | 10738.8 | 10747.9 | 10700.5 | 10792.2 | 10864.9 | 10837.7 | 11289.2 | 10721.2 | 10617.2 | 10578.4 | 10749.6 | 10679.9 | 10673.7 | 10688.9 | 10768 | 10637.8 | 10739.5 | 10730.7 | 10788.3 | 10726.4 | 10711.3 | 10472.2 | 10604.5 | 10378.5 | 9124.2 | 10425.5 | 10378 | 10683.6 | 10554.9 | 10466 | 10685 | 10726.8 | 10781.2 | 10786.9 | 10677.2 | 10864.5 | 10710.8 | 10681.6 | 10592.4 | 11819.5 | 10523.9 | 11679.7 | 10376.7 | 10978.3 | 12307.4 | 10297.5 | 11827.9 | 10597.5 | 10787.4 | 10708.8 | 10056.4 | 11100.1 | 10663 | 11006.7 | 10778.3 | 9740.1 | 11297.7 | 9749 | 11164 | 11007.3 | 9736 | 10763.4 | 10241.9 | 10229.4 | 9602.6 | 10148.4 | 10799 | 11010.7 | 9898.7 | 10828.2 | 9536.9 | 10503.2 | 10278.6 | 9657.9 | 10887 | 9492.3 | 11041.4 | 9662.5 | 10864.7 | 10120.1 | 10993.4 | 10251.9 | 11422 | 10083.5 | 10816.2 | 10005.9 | 8888.4 | 11072.1 | 10571.6 | 9888.3 | 11493.1 | 11045 | 10089.4 | 9918.9 | 11221.7 | 9962.9 | 10359 | 11220 | 9880.5 | 11397.6 | 9878.6 | 11052.5 | 10134.5 | 11193.2 | 9605.5 | 11260.9 | 10102.2 | 11100.1 | 10058.2 | 11201.9 | 10265.9 | 9961.7 | 11022.2 | 10097.5 | 9901 | 11100.6 | 11323.4 | 11057.2 | 10074.4 | 11246.7 | 9930.1 | 10833.1 | 10153 | 10784 | 9373.8 | 10932.8 | 9996.2 | 10197.8 | 10219.1 | 10055.8 | 8676.2 | 10025.9 | 8883.3 | 10031.8 | 10054.9 | 11744.5 | 10159.8 | 11779 | 10395.8 | 11673.4 | 10233.5 | 10421 | 10179.8 | 11374.3 | 11818.6 | 11663.1 | 11584.3 | 11675.7 | 11706.2 | 10489.2 | 11673.7 | 11589.3 | 11689.3 | 11771.3 | 11723 | 11797.1 | 10495 | 11715.8 | 10490.7 | 32.4091 | 31.8954 | 32.459 | 32.9768 | 32.1417 | 31.9456 | 0 | 44.2 | 0 | 0 | 45.4 | 43.806 | 2.3557 | 1.371 | 0.62988 | 0.37243 | 2.4422 | 2.0597 | 5.4933 | 5.5617 | 3.6633 | 4.69 | 5.325 | 6.17 | 5.0905 | 5.0984 | 5.1636 | 5.2 | 5.1456 | 5.1622 | 1.0713 | 1.1662 | 1.0411 | 1.2975 | 1.3999 | 1.0996 | 6.1166 | 6.0748 | 6.1053 | 6.1289 | 6.0553 | 6.0703 | 0.23874 | 0.2622 | 0.23871 | 0.2077 | 0.23391 | 0.23944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 767015 | 1400 | 753657 | 1444 | 175757.08 | 499.733 | 5.0905 | 5.0984 | 5.1636 | 5.2 | 5.1456 | 5.1622 | 6.1166 | 6.0748 | 6.1053 | 6.1289 | 6.0553 | 6.0703 | 847000 | 1000 | 850000 | 1000 | 1690866 | 3533 | 1695000 | 1687333 | 11.0667 | 5.1434 | 1.1793 | 6.0919 | 0.23678 | 22.93% | 3.887% | 32.3046 | 44.4687 | 1.5385 | 5.1506 | 1701580.2 | 1690067 | 2002337.659 | 84.4% | 28 | 0
2024-10-24 | 2025 | 2024 | Year_3 | Year_3 | 2024-10-01 | 31 | 335090.89 | 6:58 | 18:08 | 10396.1 | 10917.8 | 10933.8 | 10879.3 | 10993.5 | 11057.5 | 11036.2 | 11493.8 | 10898.9 | 10785.5 | 10751.9 | 10931.5 | 10861.1 | 10846.8 | 10870.6 | 10936.5 | 10812.9 | 10911.6 | 10903.9 | 10963.5 | 10890.4 | 10876.8 | 10643.9 | 10774.8 | 10497.5 | 9235.2 | 10587.2 | 10535.6 | 10864.7 | 10741.8 | 10589.1 | 10809.3 | 10881.3 | 10926.1 | 10936.9 | 10835.9 | 11035.6 | 10872.7 | 10913.9 | 10755.9 | 11973.7 | 10672.1 | 11842.4 | 10533.3 | 11145.5 | 12404.4 | 10445.4 | 11958.8 | 10778.8 | 10965.5 | 10893.9 | 10218 | 11293.8 | 10836.2 | 11177.3 | 10941.9 | 9898.1 | 11477.8 | 9914.2 | 11340 | 11177.6 | 9897.8 | 10932.8 | 10403.8 | 10415.2 | 9766.9 | 10314.2 | 10987.1 | 11191.4 | 10053 | 10038.9 | 8515.4 | 10667.7 | 10444.4 | 9811.4 | 11053.3 | 9649.6 | 11217.9 | 9830.1 | 11040.7 | 10300 | 11182.8 | 10435 | 11641 | 10268.7 | 11027.8 | 10187 | 9060 | 11252 | 10772 | 10055.8 | 11701.5 | 11237.4 | 10255 | 10086.7 | 11428.7 | 10127 | 10536 | 11418.5 | 10062.7 | 11607.1 | 10058 | 11259.3 | 10316.7 | 11398 | 9779 | 11467.5 | 10294.7 | 11304.2 | 10228 | 11404.6 | 10460.1 | 10136.4 | 11220 | 10278.7 | 10084 | 11308.8 | 11522.7 | 11267 | 10248 | 11464 | 10197.7 | 11036.4 | 10353.6 | 10985 | 9560 | 11147 | 10191 | 10388.5 | 10394.6 | 10249.1 | 8848.2 | 10189.9 | 9007.5 | 10222.6 | 10233.9 | 11943.4 | 10338.8 | 11977.4 | 10579.3 | 11852 | 10395 | 10598 | 10349 | 11592.2 | 12045.1 | 11878.3 | 11803.2 | 11900.2 | 11924.6 | 10684.7 | 11899.5 | 11840 | 11933.4 | 11965.8 | 11919.4 | 12000.5 | 10686 | 11954 | 10697.3 | 32.5538 | 32.2618 | 32.8663 | 33.0168 | 32.6298 | 32.3805 | 0 | 43.7 | 0 | 0 | 45 | 43.2398 | 2.7745 | 2.1031 | 1.1645 | 1.0574 | 2.8217 | 2.181 | 6.1033 | 6.2933 | 6.76 | 5.1983 | 6.42 | 6.5467 | 5.1434 | 5.1807 | 5.2103 | 5.1 | 5.2118 | 5.2206 | 1.086 | 1.1934 | 1.0574 | 1.3145 | 1.427 | 1.1167 | 6.2043 | 6.192 | 6.1829 | 6.2125 | 6.1505 | 6.1649 | 0.24503 | 0.2768 | 0.24344 | 0.21382 | 0.24162 | 0.24689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 767879 | 1401 | 754515 | 1445 | 177474.481 | 501.667 | 5.1434 | 5.1807 | 5.2103 | 5.1 | 5.2118 | 5.2206 | 6.2043 | 6.192 | 6.1829 | 6.2125 | 6.1505 | 6.1649 | 864000 | 1000 | 858000 | 1000 | 1717401 | 1934 | 1720000 | 1715467 | 11.1667 | 5.1778 | 1.1992 | 6.1845 | 0.2446 | 23.16% | 3.955% | 32.6182 | 43.9799 | 2.017 | 6.2203 | 1728412.1 | 1716400 | 2031217.4204 | 84.5% | 29 | 0
2024-10-25 | 2025 | 2024 | Year_3 | Year_3 | 2024-10-01 | 31 | 335090.89 | 6:59 | 18:08 | 10205 | 10751.2 | 10694.2 | 10649.9 | 10743.2 | 10816.7 | 10807.7 | 11270.8 | 10686.9 | 10556.4 | 10525.7 | 10703.2 | 10617.7 | 10618.4 | 10619.4 | 10695.1 | 10571.2 | 10674.6 | 10670 | 10721.3 | 10647.3 | 10638.3 | 10423.5 | 10542.5 | 10270.8 | 9020.9 | 10372.6 | 10333.9 | 10645.1 | 10520 | 10365.1 | 10577.7 | 10671.3 | 10708.3 | 10708.3 | 10625.2 | 10823 | 10650.7 | 10684.8 | 10537.8 | 11749.9 | 10444.3 | 11609.2 | 10310.4 | 10911.5 | 12181.3 | 10233.3 | 11730.4 | 10561.9 | 10733 | 10671.2 | 9994.6 | 11059.7 | 10590 | 10930.3 | 10696.6 | 9681 | 11224.8 | 9722.5 | 11106.4 | 10954.2 | 9702.1 | 10691.2 | 10163.4 | 10212.6 | 9570.1 | 10122.3 | 10750.2 | 10963.2 | 9844.3 | 10802 | 9494.2 | 10447 | 10233.8 | 9603.9 | 10841 | 9463.6 | 10976.2 | 9620.7 | 10801.4 | 10078.4 | 10951.8 | 10206 | 11383.2 | 10045.9 | 10786.3 | 9951 | 8860 | 11018.4 | 10537.5 | 9843.1 | 11459.4 | 11022.6 | 10081 | 9934 | 11174 | 9880.2 | 10298.8 | 11164.9 | 9841.5 | 11337.7 | 9841.5 | 11007.6 | 10091.5 | 11142.7 | 9561.8 | 11208.2 | 10071.8 | 11017.6 | 9943.8 | 11135.9 | 10238.1 | 9922 | 10980.4 | 10063.4 | 9875.3 | 11074.5 | 11295.7 | 11028.5 | 10027.2 | 11210.3 | 9977.3 | 10802.8 | 10129.2 | 10734.1 | 9225.4 | 10899.2 | 9981 | 10155.7 | 10157.9 | 10019.8 | 8648.1 | 9972.9 | 8824.7 | 9988.1 | 9996.8 | 11715.5 | 10115.2 | 11757.3 | 10349.4 | 11614.9 | 10157.3 | 10358.4 | 10109.6 | 11339.8 | 11787.2 | 11590.7 | 11542.8 | 11651.5 | 11684.8 | 10461.3 | 11656.2 | 11622.1 | 11714.7 | 11746.2 | 11702.8 | 11774.4 | 10455.5 | 11689.9 | 10479.7 | 32.9892 | 32.7099 | 33.2078 | 33.5409 | 33.1545 | 32.846 | 0 | 45 | 0 | 0 | 46 | 44.8 | 2.3423 | 1.164 | 0.57346 | 0.45076 | 2.4365 | 2.0044 | 5.105 | 5.5817 | 4.1317 | 4.525 | 5.25 | 5.26 | 5.0512 | 5.0838 | 5.1039 | 5.2 | 5.1154 | 5.1217 | 1.0681 | 1.1781 | 1.0425 | 1.2917 | 1.4076 | 1.1008 | 6.0985 | 6.0768 | 6.0672 | 6.0984 | 6.0417 | 6.0557 | 0.24081 | 0.27203 | 0.23928 | 0.20936 | 0.23752 | 0.24134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 768715 | 1402 | 755369 | 1446 | 179157.614 | 506.6 | 5.0512 | 5.0838 | 5.1039 | 5.2 | 5.1154 | 5.1217 | 6.0985 | 6.0768 | 6.0672 | 6.0984 | 6.0417 | 6.0557 | 836000 | 1000 | 854000 | 1000 | 1683133 | 4933 | 1688000 | 1678200 | 11.15 | 5.1127 | 1.1815 | 6.0731 | 0.24006 | 23.11% | 3.953% | 33.0747 | 45.2667 | 1.4952 | 4.9756 | 1693949.1 | 1681300 | 1989016 | 84.53% | 26 | 0
2024-10-26 | 2025 | 2024 | Year_3 | Year_3 | 2024-10-01 | 31 | 335090.89 | 7:02 | 18:04 | 10395.7 | 10954.6 | 10891.1 | 10837.3 | 10958.8 | 10998.6 | 10975.4 | 11456.9 | 10871.6 | 10799.1 | 10709.3 | 10887.9 | 10817.9 | 10806.7 | 10803.1 | 10905 | 10773.2 | 10876 | 10866.7 | 10911.7 | 10831.5 | 10825 | 10603.6 | 10736.1 | 10409.5 | 9150.7 | 10559.9 | 10530.5 | 10837.2 | 10695.7 | 10505.6 | 10719.9 | 10866.9 | 10893.9 | 10821.1 | 10733.7 | 11007.7 | 10831.5 | 10882.6 | 10721.3 | 11951.5 | 10620.6 | 11802.4 | 10483.8 | 11089 | 12384.5 | 10394.6 | 11924.3 | 10735.2 | 10908.4 | 10848.3 | 10158.3 | 11250.6 | 10771.4 | 11113.2 | 10847.5 | 9843.3 | 11413.2 | 9887.3 | 11286.2 | 11127.8 | 9870.6 | 10905.8 | 10368.3 | 10390.9 | 9737.7 | 10291.8 | 10931.5 | 11160.3 | 10010.9 | 10990.4 | 9650 | 10624 | 10407.6 | 9765.6 | 11019.6 | 9622 | 11166.4 | 9779 | 10978.4 | 10254.7 | 11136.1 | 10383.1 | 11585 | 10222.7 | 10970.6 | 10165.5 | 9021.6 | 11223.5 | 10729 | 10027 | 11671.1 | 11222.6 | 10265.7 | 10119.8 | 11405.3 | 10114 | 10498.8 | 11392.5 | 10024.2 | 11524.5 | 10022.4 | 11202.7 | 10279.1 | 11341.8 | 9736.9 | 11409.7 | 10247.9 | 11227.9 | 10181.8 | 11351.5 | 10411.5 | 10085.6 | 11165.2 | 10236.2 | 10040.8 | 11255.6 | 11484.7 | 11215.4 | 10199 | 11409.3 | 10151.9 | 10984 | 10304.4 | 10914 | 9328 | 11084.3 | 10155.1 | 10332.7 | 10335.1 | 10178.2 | 8801.9 | 10130.3 | 8968.7 | 10150.9 | 10159.1 | 11911.1 | 10289.1 | 11957.8 | 10529.2 | 11792.2 | 10308.8 | 10512.8 | 10247.3 | 11524.1 | 11973.6 | 11826.5 | 11757.2 | 11854.7 | 11881.2 | 10632 | 11847.6 | 11818.5 | 11917.2 | 11953.2 | 11904.8 | 11971.7 | 10626.4 | 11898.5 | 10661.5 | 34.25 | 33.95 | 34.39 | 34.75 | 34.77 | 34.27 | 0 | 46.5 | 0 | 0 | 47.5 | 46.39 | 2.87 | 1.4 | 0.59 | 0.58 | 2.98 | 2.76 | 5.67 | 5.12 | 4.59 | 4.72 | 5.68 | 5.86 | 5.15 | 5.18 | 5.2 | 5.13 | 5.21 | 5.22 | 1.1 | 1.2 | 1.07 | 1.35 | 1.44 | 1.12 | 6.26 | 6.23 | 6.21 | 6.25 | 6.2 | 6.21 | 0.24 | 0.27 | 0.24 | 0.21 | 0.24 | 0.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 769572 | 1404 | 756231 | 1448 | 180870.1 | 511.667 | 5.15 | 5.18 | 5.2 | 5.13 | 5.21 | 5.22 | 6.26 | 6.23 | 6.21 | 6.25 | 6.2 | 6.21 | 857000 | 2000 | 862000 | 2000 | 1712486 | 5067 | 1715000 | 1707419 | 11.0333 | 5.1817 | 1.2133 | 6.2267 | 0.24 | 23.42% | 3.854% | 34.3967 | 46.7967 | 1.8633 | 5.2733 | 1723210.6 | 1711800 | 2030619 | 84.3% | 31 | 1143
2024-10-27 | 2025 | 2024 | Year_3 | Year_3 | 2024-10-01 | 31 | 335090.89 | 7:05 | 18:07 | 10172.5 | 10707.2 | 10654.1 | 10607 | 10722.5 | 10816.4 | 10803.3 | 11200.4 | 10628.2 | 10571.5 | 10471.7 | 10640.3 | 10576.8 | 10569.4 | 10567.1 | 10676.8 | 10553.4 | 10666.7 | 10647.2 | 10688.4 | 10625 | 10611.5 | 10373.2 | 10518.1 | 10154.1 | 8944 | 10311 | 10289.4 | 10573 | 10411.2 | 10283.9 | 10459.8 | 10618.7 | 10649.1 | 10629.9 | 10555.8 | 10746.1 | 10592.6 | 10648.2 | 10480.8 | 11653.4 | 10406 | 11533.3 | 10277.8 | 10853.9 | 12042.8 | 10172.8 | 11620 | 10496.2 | 10666 | 10616.7 | 9924.1 | 11004.7 | 10512.4 | 10866.8 | 10606.3 | 9624.8 | 11164.9 | 9681.7 | 11032.6 | 10877.3 | 9661.7 | 10653.9 | 10130.4 | 10182.4 | 9546.3 | 10080.3 | 10691.2 | 10930.9 | 9806.6 | 10759.2 | 9439.6 | 10402.3 | 10200.2 | 9556.3 | 10796.5 | 9436.5 | 10921.4 | 9568.5 | 10734.8 | 10035.3 | 10904.7 | 10165.4 | 11341.4 | 10013.4 | 10744.8 | 9962.9 | 8828.2 | 10954.8 | 10506.9 | 9802 | 11408.7 | 11003 | 10080.6 | 9944.7 | 11157 | 9908.7 | 10274.2 | 11147 | 9811.8 | 11268.4 | 9802.9 | 10957.6 | 10055.3 | 11097.8 | 9530.3 | 11168.8 | 10027.8 | 11018.1 | 10005.4 | 11134.9 | 10202.7 | 9870.6 | 10926.8 | 10026 | 9827.6 | 11025.7 | 11252.8 | 10991.2 | 9995.3 | 11188.2 | 9957.2 | 10763 | 10111.5 | 10695.7 | 9321.3 | 10869.6 | 9966.1 | 10136.3 | 10136.7 | 9968.5 | 8632 | 9914.2 | 8767.8 | 9962.5 | 9975.2 | 11673.2 | 10076.7 | 11717.4 | 10306.3 | 11544.4 | 10090.6 | 10287.3 | 10058.3 | 11288.8 | 11719.1 | 11567.8 | 11500.7 | 11609.4 | 11639.7 | 10408.8 | 11598.1 | 11610.6 | 11695.7 | 11699.9 | 11661.7 | 11713.7 | 10396.8 | 11661 | 10441 | 35.22 | 34.86 | 35.25 | 35.77 | 35.77 | 35.13 | 0 | 46.2 | 0 | 0 | 47.1 | 46 | 3.58 | 3.07 | 2.17 | 1.83 | 3.6 | 3.36 | 5.85 | 6.21 | 5.74 | 5.7 | 5.91 | 5.99 | 5.02 | 5.05 | 5.08 | 5.01 | 5.09 | 5.1 | 1.07 | 1.18 | 1.05 | 1.32 | 1.41 | 1.11 | 6.1 | 6.09 | 6.07 | 6.1 | 6.05 | 6.09 | 0.24 | 0.27 | 0.23 | 0.21 | 0.24 | 0.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 770410 | 1406 | 757075 | 1449 | 182547.148 | 516.6 | 5.02 | 5.05 | 5.08 | 5.01 | 5.09 | 5.1 | 6.1 | 6.09 | 6.07 | 6.1 | 6.05 | 6.09 | 838000 | 2000 | 844000 | 1000 | 1677048 | 4933 | 1679000 | 1672115 | 11.0333 | 5.0583 | 1.19 | 6.0833 | 0.23833 | 23.53% | 3.918% | 35.3333 | 46.4333 | 2.935 | 5.9 | 1687064.1 | 1675800 | 1987783 | 84.3% | 26 | 0
2024-10-28 | 2025 | 2024 | Year_3 | Year_3 | 2024-10-01 | 31 | 335090.89 | 7:05 | 18:06 | 10478.2 | 11004.6 | 10957.8 | 10918.1 | 11007.2 | 11125.6 | 11102 | 11556.9 | 10937.2 | 10845 | 10801.2 | 10956.9 | 10924.9 | 10899.5 | 10888.1 | 11020.9 | 10891.1 | 11002 | 10981 | 11009.8 | 10963.9 | 10945 | 10657.6 | 10857.7 | 10505 | 9244.8 | 10642.9 | 10632.6 | 10939.8 | 10829.6 | 10638.1 | 10822.7 | 10930.4 | 10981.3 | 10985.1 | 10890.4 | 11088.1 | 10932 | 10971.3 | 10805.8 | 11997.1 | 10693.1 | 11865.6 | 10561.9 | 11131.4 | 12374.7 | 10465.8 | 11960.8 | 10837.9 | 11001.4 | 10980.3 | 10231.2 | 11370.9 | 10814.2 | 11208.2 | 10933.4 | 9917.5 | 11511.7 | 9998.5 | 11376.4 | 11214.7 | 9975.6 | 10958.5 | 10428.1 | 10508.3 | 9855.7 | 10430.8 | 11034.9 | 11295 | 10126.8 | 11117.3 | 9744.4 | 10739.7 | 10533.4 | 9865.3 | 11157.5 | 9759.9 | 11258.9 | 9867.8 | 11068.9 | 10325.8 | 11207.8 | 10455.7 | 11662.5 | 10295.7 | 11050.4 | 10232.3 | 9070.6 | 11230.5 | 10786.5 | 10080.1 | 11707.9 | 11316 | 10359.9 | 10211.6 | 11451.3 | 10146.6 | 10538.3 | 11430.3 | 10079.6 | 11585.1 | 10069.7 | 11263.8 | 10319.2 | 11408.7 | 9791.1 | 11483.9 | 10306.2 | 11315.3 | 10269 | 11433.3 | 10396.1 | 10149.5 | 11200.1 | 10315.7 | 10084.8 | 11305.5 | 11520.4 | 11261.2 | 10234.9 | 11437.4 | 10182.3 | 11037.7 | 10364.5 | 10939.9 | 9509.3 | 11117.1 | 10212.1 | 10376.5 | 10370.3 | 10197.6 | 8837.9 | 10177 | 9014.6 | 10188.7 | 10205.9 | 11931.4 | 10348.5 | 11972.8 | 10574.5 | 11825.1 | 10375 | 10579.2 | 10304.3 | 11595.8 | 12031 | 11883.1 | 11801.6 | 11879.3 | 11901.5 | 10683.4 | 11867.8 | 11912 | 11974.5 | 11966.7 | 11912.5 | 11987.4 | 10678.2 | 11948.4 | 10576.9 | 35.2526 | 34.9213 | 35.3362 | 36.0669 | 35.4444 | 35.1909 | 0 | 48.2 | 0 | 0 | 49 | 48 | 2.82 | 2.3404 | 1.3237 | 0.83549 | 2.7215 | 2.3697 | 5.5983 | 6.2333 | 4.6633 | 4.54 | 5.43 | 5.8033 | 5.1594 | 5.2016 | 5.2363 | 5.1487 | 5.2368 | 5.2365 | 1.0843 | 1.2215 | 1.0822 | 1.3596 | 1.4463 | 1.1418 | 6.3338 | 6.3275 | 6.3046 | 6.3316 | 6.2577 | 6.3007 | 0.22668 | 0.25846 | 0.22543 | 0.1951 | 0.22825 | 0.23047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 771274 | 1408 | 757941 | 1451 | 184271.681 | 521.533 | 5.1594 | 5.2016 | 5.2363 | 5.1487 | 5.2368 | 5.2365 | 6.3338 | 6.3275 | 6.3046 | 6.3316 | 6.2577 | 6.3007 | 864000 | 2000 | 866000 | 2000 | 1724533 | 4933 | 1726000 | 1719600 | 11.0167 | 5.2032 | 1.2226 | 6.3093 | 0.2274 | 23.5% | 3.604% | 35.3687 | 48.4 | 2.0685 | 5.3781 | 1734778.2 | 1723400 | 2050626.0723 | 84.04% | 30 | 271
2024-10-29 | 2025 | 2024 | Year_3 | Year_3 | 2024-10-01 | 31 | 335090.89 | 7:04 | 18:07 | 10315.2 | 10829.3 | 10779.2 | 10736.4 | 10823 | 10937.6 | 10927 | 11385.4 | 10767.2 | 10673.7 | 10644 | 10791.3 | 10757.5 | 10731.1 | 10709.2 | 10837 | 10706 | 10814.1 | 10815.9 | 10839.3 | 10795.2 | 10776.7 | 10547.3 | 10689.9 | 10346.2 | 9108.9 | 10485.1 | 10476.9 | 10791.9 | 10689.7 | 10489.4 | 10673.7 | 10792.9 | 10814.9 | 10791.7 | 10722.1 | 10917.9 | 10756 | 10804.7 | 10663.5 | 11849.3 | 10568.4 | 11728 | 10440.1 | 11042.3 | 12252.2 | 10352.6 | 11807.7 | 10665.3 | 10828.2 | 10792 | 10061.1 | 11182.8 | 10609.6 | 11029.5 | 10776.8 | 9757.5 | 11350.5 | 9839 | 11197.5 | 11047.2 | 9817.8 | 10841.8 | 10309.8 | 10345.7 | 9706.4 | 10264.5 | 10907.2 | 11126.6 | 10001.5 | 10952.1 | 9621.1 | 10570.3 | 10379.7 | 9707.6 | 10985.8 | 9601.2 | 11088.9 | 9715 | 10909.5 | 10207.1 | 11074.1 | 10326.3 | 11511.2 | 10173.5 | 10916.3 | 10096.8 | 8968.1 | 11087.6 | 10673 | 9951.9 | 11549.5 | 11167.9 | 10224.1 | 10075.6 | 11347.5 | 10053.7 | 10425.4 | 11308.2 | 9968.1 | 11449.1 | 9963.5 | 11140.2 | 10202.8 | 11283.5 | 9683.6 | 11355.6 | 10191.7 | 11180.6 | 10123.8 | 11299.1 | 10313.3 | 10055.8 | 11098.5 | 10206 | 9977.5 | 11186.3 | 11402 | 11036.2 | 10139.5 | 11332.5 | 10098.5 | 10911.2 | 10246.5 | 10813.8 | 9441 | 11025.4 | 10122.3 | 10280.2 | 10266.3 | 10145.9 | 8766 | 10079.1 | 8943.3 | 10060.2 | 10078 | 11779.5 | 10232.3 | 11794.6 | 10443.5 | 11680.8 | 10252.6 | 10448.2 | 10179.1 | 11461.2 | 11898 | 11731.1 | 11656.3 | 11736.5 | 11748.2 | 10546.9 | 11706.7 | 11728.9 | 11790.4 | 11791.2 | 11735.9 | 11816.3 | 10548.8 | 11788.8 | 10438.9 | 34.1603 | 33.8722 | 34.1544 | 34.8214 | 34.732 | 34.2313 | 0 | 45.5 | 0 | 0 | 46.5 | 45.4661 | 3.7326 | 2.813 | 2.1419 | 1.5901 | 3.7383 | 3.3269 | 6.8033 | 6.6967 | 6.1983 | 5.615 | 7.2633 | 6.2767 | 5.0628 | 5.0937 | 5.1259 | 5.0509 | 5.1439 | 5.1382 | 1.1033 | 1.2118 | 1.0757 | 1.3514 | 1.4392 | 1.1383 | 6.1838 | 6.1734 | 6.143 | 6.1836 | 6.1267 | 6.1644 | 0.24402 | 0.27893 | 0.24118 | 0.21299 | 0.24521 | 0.24695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 772126 | 1410 | 758796 | 1452 | 185972.948 | 526.6 | 5.0628 | 5.0937 | 5.1259 | 5.0509 | 5.1439 | 5.1382 | 6.1838 | 6.1734 | 6.143 | 6.1836 | 6.1267 | 6.1644 | 852000 | 2000 | 855000 | 1000 | 1701267 | 5067 | 1704000 | 1696200 | 11.05 | 5.1026 | 1.22 | 6.1625 | 0.24488 | 23.91% | 3.974% | 34.3286 | 45.822 | 2.8905 | 6.4756 | 1711923.5 | 1700134 | 2020304.8046 | 84.15% | 30 | 123
2024-10-30 | 2025 | 2024 | Year_3 | Year_3 | 2024-10-01 | 31 | 335090.89 | 7:05 | 18:06 | 10778.1 | 11305.8 | 11262.3 | 11227.3 | 11279.1 | 11420.9 | 11368.8 | 11772 | 11227.5 | 11113 | 11101.8 | 11255.6 | 11243.7 | 11184.6 | 11201.5 | 11340.1 | 11205.1 | 11332 | 11327.2 | 11355.6 | 11295.4 | 11285.6 | 11045.3 | 11188.6 | 10871.8 | 9554.9 | 10981.3 | 10981.2 | 11290.7 | 11171.1 | 10995 | 11189 | 11294.6 | 11315.2 | 11259.2 | 11196.1 | 11395.2 | 11228.1 | 11274.3 | 11152.4 | 12228.1 | 11020.6 | 12083.7 | 10888 | 11489.9 | 12594.5 | 10796.5 | 12201.8 | 11140.9 | 11202.5 | 11290.3 | 10533.3 | 11678.5 | 11136.8 | 11505.9 | 11256.7 | 10186.2 | 11793.6 | 10285.3 | 11604.9 | 11546 | 10281.4 | 11337.7 | 10787.5 | 10814.7 | 10140.3 | 10733.4 | 11366.6 | 11597.9 | 10430.5 | 11436.5 | 10037.7 | 11046.3 | 10836.1 | 10148.7 | 11459.4 | 10037 | 11551.6 | 10141.5 | 11380.6 | 10665.8 | 11522.4 | 10751.9 | 11865.7 | 10597.1 | 11366.3 | 10491.5 | 9333.9 | 11498.2 | 11112.5 | 10373.8 | 11926.6 | 11595.7 | 10630.1 | 10463.4 | 11748.6 | 10467.1 | 10877.7 | 11712.9 | 10389 | 11854.9 | 10381.6 | 11604.5 | 10626.8 | 11707.2 | 10090.8 | 11771.9 | 10623.1 | 11629 | 10556.1 | 11715.6 | 10791.5 | 10494.6 | 11549 | 10634.4 | 10410.6 | 11625.6 | 11808.8 | 11486.2 | 10553.8 | 11743.1 | 10505.3 | 11378.4 | 10688.7 | 11325 | 9860.4 | 11467.5 | 10525.1 | 10684.8 | 10664 | 10556.5 | 9113.3 | 10452.9 | 9276.3 | 10516.4 | 10516 | 12156.6 | 10681.2 | 12189.9 | 10913 | 12050.3 | 10667.7 | 10867.2 | 10591.7 | 11884.5 | 12243 | 12105.9 | 12025.2 | 12105.1 | 12120.5 | 11015.6 | 12101.5 | 12104.5 | 12177 | 12172 | 12128.4 | 12194.6 | 11004.3 | 12131.3 | 11063.5 | 33.5065 | 33.4074 | 33.8696 | 34.1407 | 33.5291 | 33.7931 | 0 | 47.3983 | 0 | 0 | 48 | 47.1 | 3.2461 | 2.6667 | 1.9494 | 1.2801 | 3.247 | 3.1146 | 7.38 | 7.0967 | 6.3333 | 6.4617 | 6.66 | 6.8433 | 5.2527 | 5.2931 | 5.3204 | 5.2 | 5.3255 | 5.3296 | 1.1497 | 1.2693 | 1.1265 | 1.4113 | 1.502 | 1.19 | 6.4857 | 6.4702 | 6.4428 | 6.4727 | 6.4091 | 6.4512 | 0.23587 | 0.2696 | 0.23427 | 0.20465 | 0.23679 | 0.24081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 773014 | 1411 | 759684 | 1454 | 187744.081 | 531.667 | 5.2527 | 5.2931 | 5.3204 | 5.2 | 5.3255 | 5.3296 | 6.4857 | 6.4702 | 6.4428 | 6.4727 | 6.4091 | 6.4512 | 888000 | 1000 | 888000 | 2000 | 1771133 | 5067 | 1773000 | 1766066 | 11.0167 | 5.2869 | 1.2748 | 6.4553 | 0.237 | 24.11% | 3.671% | 33.7077 | 47.4994 | 2.584 | 6.7958 | 1782570.8 | 1770000 | 2112091.5615 | 83.8% | 31 | 4089
2024-10-31 | 2025 | 2024 | Year_3 | Year_3 | 2024-10-01 | 31 | 335090.89 | 7:04 | 18:07 | 10400.4 | 10900.7 | 10848.1 | 10818.6 | 10847.9 | 10986.2 | 10944.6 | 11425.7 | 10829.4 | 10704.2 | 10709.8 | 10863.4 | 10840.9 | 10798.7 | 10794.5 | 10924.1 | 10782.8 | 10903.3 | 10909.4 | 10939.4 | 10875.4 | 10864 | 10624.1 | 10769.6 | 10480.1 | 9206.1 | 10575 | 10566.8 | 10868 | 10739 | 10601.3 | 10795.1 | 10848 | 10874.9 | 10727.4 | 10648.8 | 10977.6 | 10809.3 | 10857.9 | 10706.2 | 11942.2 | 10618.5 | 11794.6 | 10486.1 | 11065 | 12329.2 | 10397 | 11912.4 | 10742.8 | 10900.2 | 10883.4 | 10159.3 | 11280.3 | 10745.6 | 11102.1 | 10838.1 | 9817.8 | 11401 | 9932.1 | 11275.4 | 11131.6 | 9915.9 | 10907.5 | 10377.8 | 10410.8 | 9770.9 | 10330.4 | 10958.6 | 11202 | 10057.3 | 11017.3 | 9669.2 | 10625.5 | 10434.5 | 9782 | 11041.5 | 9671.5 | 11161.1 | 9791.8 | 10994.9 | 10286.2 | 11128.4 | 10359.2 | 11519 | 10209.8 | 10946.7 | 10125.8 | 8997.8 | 11078.7 | 10720.4 | 9994.9 | 11609 | 11231.4 | 10277.7 | 10128.6 | 11373.7 | 10075 | 10475.7 | 11357.4 | 10018.1 | 11536.9 | 10016.4 | 11217.8 | 10268.1 | 11361.3 | 9745.9 | 11434.2 | 10256.1 | 11265.7 | 10211.1 | 11367.8 | 10426 | 10110.1 | 11142.2 | 10256.9 | 10024.4 | 11260 | 11456.5 | 11217.7 | 10172.4 | 11382.2 | 10136.9 | 10992.3 | 10315.1 | 10931.2 | 9506.3 | 11058 | 10154.9 | 10304.1 | 10301.7 | 10172.6 | 8789.8 | 10070.4 | 8911.3 | 10125.5 | 10116.4 | 11890.6 | 10289.2 | 11942.7 | 10521.1 | 11801.8 | 10318.6 | 10525.8 | 10185.9 | 11526.7 | 11979.1 | 11815.9 | 11729.9 | 11835.6 | 11858.9 | 10634.8 | 11846.6 | 11797.8 | 11899.8 | 11894.9 | 11844.2 | 11942.8 | 10608.5 | 11825.1 | 10661.9 | 33.0887 | 32.7292 | 33.3098 | 33.823 | 33.3197 | 33.0266 | 0 | 46.6 | 0 | 0 | 47.6 | 46.5 | 2.176 | 0.70087 | 1.009 | 0.64639 | 2.2086 | 1.8077 | 5.3767 | 4.6183 | 4.8133 | 4.23 | 4.9283 | 4.93 | 5.0596 | 5.0895 | 5.1218 | 5.2 | 5.1076 | 5.1176 | 1.1099 | 1.2079 | 1.085 | 1.3437 | 1.4323 | 1.1282 | 6.2237 | 6.2192 | 6.1963 | 6.2087 | 6.1471 | 6.1813 | 0.23268 | 0.26563 | 0.23078 | 0.20158 | 0.2325 | 0.2348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 773871 | 1413 | 760545 | 1456 | 189455.881 | 536.667 | 5.0596 | 5.0895 | 5.1218 | 5.2 | 5.1076 | 5.1176 | 6.2237 | 6.2192 | 6.1963 | 6.2087 | 6.1471 | 6.1813 | 857000 | 2000 | 861000 | 2000 | 1711800 | 5000 | 1714000 | 1706800 | 11.05 | 5.116 | 1.2178 | 6.196 | 0.23299 | 23.8% | 3.76% | 33.2162 | 46.9 | 1.4248 | 4.8161 | 1722569.8 | 1710800 | 2025366.3179 | 84.47% | 37 | 110
2024-11-01 | 2025 | 2024 | Year_3 | Year_3 | 2024-11-01 | 30 | 335090.89 | 7:07 | 18:00 | 10027.2 | 10501.4 | 10456 | 10425.2 | 10454.3 | 10579.9 | 10542.2 | 11019.4 | 10437.6 | 10308.3 | 10329.7 | 10476.7 | 10458.1 | 10416.6 | 10416.9 | 10546.4 | 10398.2 | 10519 | 10517.3 | 10544.3 | 10485.5 | 10476.6 | 10249.2 | 10390.6 | 10114.8 | 8873.7 | 10199.3 | 10188.7 | 10471.1 | 10348.8 | 10226.5 | 10417 | 10459.5 | 10490.5 | 10482.6 | 10397.3 | 10588.9 | 10430.7 | 10471.1 | 10338 | 11538.5 | 10254.4 | 11382.7 | 10123.3 | 10684.2 | 11930.7 | 10023.6 | 11511.5 | 10373.3 | 10522.4 | 10501.5 | 9793.5 | 10890.6 | 10363.7 | 10713.5 | 10467.4 | 9463.2 | 11003 | 9558.7 | 10847.8 | 10746.3 | 9560.9 | 10515.1 | 9999.7 | 10040.4 | 9446.9 | 9981.2 | 10599.5 | 10822.5 | 9721.8 | 10643.6 | 9341.8 | 10261.8 | 10085.9 | 9433.5 | 10672 | 9335.4 | 10770.8 | 9449 | 10616.3 | 9925.6 | 10745.1 | 9986.3 | 11196 | 9845.3 | 10566.5 | 9783.7 | 8689.2 | 10685.2 | 10358.9 | 9651.4 | 11216.7 | 10863.1 | 9942.8 | 9805.7 | 10975.8 | 9721.9 | 10112.6 | 10966 | 9665.8 | 11153.3 | 9665.2 | 10825.5 | 9909.1 | 10955.4 | 9396.7 | 11016.5 | 9880.9 | 10865.2 | 9857.5 | 10961.1 | 10046.3 | 9754.3 | 10757.1 | 9888.5 | 9662.1 | 10827.6 | 11073.1 | 10814.6 | 9805.3 | 10988.8 | 9778.9 | 10586.8 | 9931.1 | 10526.9 | 9157.2 | 10670.1 | 9781.5 | 9931.1 | 9936.9 | 9782.5 | 8467.7 | 9697.5 | 8564.7 | 9748.9 | 9743.4 | 11481.3 | 9924.4 | 11543.5 | 10142.9 | 11392.7 | 9956.9 | 10161.6 | 9815.3 | 11116.6 | 11549.8 | 11371.3 | 11319.4 | 11422.3 | 11452.8 | 10257.7 | 11431.4 | 11372.5 | 11467.9 | 11485 | 11439.9 | 11534.7 | 10232.2 | 11401.2 | 10277.3 | 33.04 | 32.83 | 33.22 | 33.81 | 33.25 | 32.86 | 0 | 45.8 | 0 | 0 | 46.5 | 45.4 | 2.72 | 1.16 | 0.7 | 0.74 | 2.66 | 1.81 | 5.26 | 5.49 | 4.88 | 5.22 | 5.39 | 5.27 | 4.88 | 4.9 | 4.94 | 4.92 | 4.92 | 4.92 | 1.07 | 1.18 | 1.05 | 1.25 | 1.39 | 1.1 | 5.98 | 5.97 | 5.95 | 5.96 | 5.9 | 5.94 | 0.23 | 0.27 | 0.23 | 0.2 | 0.23 | 0.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 774698 | 1415 | 761375 | 1457 | 191107.948 | 541.667 | 4.88 | 4.9 | 4.94 | 4.92 | 4.92 | 4.92 | 5.98 | 5.97 | 5.95 | 5.96 | 5.9 | 5.94 | 827000 | 2000 | 830000 | 1000 | 1652067 | 5000 | 1654000 | 1647067 | 10.8833 | 4.9133 | 1.1733 | 5.95 | 0.23333 | 23.88% | 3.922% | 33.1683 | 45.9 | 1.6317 | 5.2517 | 1662130.5 | 1651300 | 1899777 | 86.92% | 35 | 0
2024-11-02 | 2025 | 2024 | Year_3 | Year_3 | 2024-11-01 | 30 | 335090.89 | 7:06 | 18:01 | 10094.4 | 10543.9 | 10508.9 | 10486 | 10501.2 | 10642.3 | 10571.2 | 11050.4 | 10482.9 | 10344.6 | 10377.2 | 10527 | 10519.3 | 10461.1 | 10474.1 | 10609.6 | 10467.1 | 10594.7 | 10592.3 | 10619.6 | 10558.7 | 10550.2 | 10329.6 | 10470.7 | 10178.8 | 8927.4 | 10263.9 | 10256.2 | 10536.7 | 10407 | 10294.9 | 10486.6 | 10500.6 | 10551.2 | 10537.3 | 10447.5 | 10644.8 | 10492 | 10527.8 | 10398.9 | 11639.8 | 10333.9 | 11463.8 | 10203.8 | 10743.6 | 12020.6 | 10085.1 | 11615.4 | 10429.3 | 10581.6 | 10560.1 | 9837.6 | 10959.7 | 10416.8 | 10760.1 | 10522.4 | 9503 | 11041.4 | 9639.9 | 10946.1 | 10816.8 | 9623.4 | 10555.9 | 10039.6 | 10097 | 9532.2 | 10050 | 10668.2 | 10889.8 | 9792.1 | 10719.8 | 9407.3 | 10317.2 | 10146.4 | 9483.8 | 10736.7 | 9387.1 | 10823.5 | 9498.6 | 10673 | 9989.9 | 10807.2 | 10046.2 | 11270.3 | 9901.9 | 10630.7 | 9830.2 | 8739.2 | 10722.9 | 10408.8 | 9700.2 | 11258.9 | 10902.4 | 9974.1 | 9832.8 | 11018.2 | 9757.2 | 10172.1 | 11023.9 | 9723.6 | 11206.5 | 9714.3 | 10875 | 9959.6 | 11006.9 | 9443.5 | 11076.9 | 9932.1 | 10916 | 9904.9 | 11016.7 | 10100.2 | 9824.2 | 10819.6 | 9951.6 | 9727 | 10890 | 11134.5 | 10881.5 | 9870.9 | 11057.3 | 9839.6 | 10644.4 | 9993.4 | 10587.5 | 9224.8 | 10736.2 | 9848.5 | 9993.2 | 9987.6 | 9841.4 | 8522 | 9745.2 | 8609.4 | 9799.1 | 9790.8 | 11558.6 | 9986 | 11630.1 | 10211.2 | 11455.8 | 10006.5 | 10220.1 | 9868.8 | 11209.3 | 11640.8 | 11452 | 11397 | 11501 | 11530.9 | 10325.5 | 11520.5 | 11459.5 | 11554.2 | 11564.7 | 11521 | 11624.2 | 10309.4 | 11482 | 10357 | 32.5972 | 32.5037 | 32.9262 | 33.8123 | 32.6977 | 32.9354 | 0 | 45.4901 | 0 | 0 | 46.1 | 45.3 | 3.1222 | 1.9058 | 1.3028 | 0.74312 | 3.2061 | 3.218 | 6.745 | 6.4533 | 6.1133 | 5.219 | 6.63 | 6.3267 | 4.8622 | 4.8998 | 4.9355 | 4.923 | 4.9175 | 4.9315 | 1.0839 | 1.1888 | 1.0616 | 1.2452 | 1.4033 | 1.1133 | 6.0045 | 5.991 | 5.9736 | 5.958 | 5.9308 | 5.9724 | 0.23024 | 0.26379 | 0.228 | 0.20364 | 0.23206 | 0.23322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 775531 | 1417 | 762211 | 1459 | 192769.682 | 546.667 | 4.8622 | 4.8998 | 4.9355 | 4.923 | 4.9175 | 4.9315 | 6.0045 | 5.991 | 5.9736 | 5.958 | 5.9308 | 5.9724 | 833000 | 2000 | 836000 | 2000 | 1661734 | 5000 | 1665000 | 1656734 | 10.9167 | 4.9116 | 1.1827 | 5.9717 | 0.23183 | 24.08% | 3.882% | 32.9121 | 45.63 | 2.2497 | 6.2479 | 1671960.1 | 1661067 | 1913733.0399 | 86.8% | 34 | 0
2024-11-03 | 2025 | 2024 | Year_3 | Year_3 | 2024-11-01 | 30 | 335090.89 | 7:08 | 18:00 | 10049.9 | 10497.6 | 10470.2 | 10450.3 | 10450.4 | 10596 | 10501.6 | 10983.5 | 10452.1 | 10380.5 | 10339.9 | 10492 | 10467.6 | 10424.8 | 10503.2 | 10571.1 | 10450.9 | 10546.4 | 10546 | 10585.6 | 10522.7 | 10510.5 | 10271.9 | 10409.1 | 10102 | 8867.6 | 10206.5 | 10191 | 10469.9 | 10336.7 | 10236.1 | 10415.9 | 10437.3 | 10493.4 | 9468.8 | 9417.6 | 10562.6 | 10423.2 | 10463.7 | 10339.9 | 11599.7 | 10283.1 | 11411.3 | 10157.3 | 10680.6 | 11947.5 | 10035 | 11567.4 | 10394.7 | 10541.1 | 10529 | 9804.4 | 10910.5 | 10371.3 | 10724.5 | 10472.8 | 9467.5 | 10997.9 | 9609 | 10898.2 | 10768.1 | 9589 | 10493.6 | 9980.4 | 10063.9 | 9497.4 | 10012.8 | 10628.6 | 10844.6 | 9754.6 | 10672.3 | 9379.5 | 10272.3 | 10103.5 | 9439.6 | 10700.3 | 9351.7 | 10767.4 | 9444.7 | 10615.9 | 9958.1 | 10778.1 | 10008.6 | 11234 | 9868 | 10587.8 | 9796.4 | 8709.2 | 10775.1 | 10375.2 | 9691.9 | 11257.2 | 10842.8 | 9903.1 | 9737.5 | 10979.1 | 9702.5 | 10124.7 | 10971.1 | 9691.7 | 11151.8 | 9676.8 | 10831.9 | 9919 | 10958.8 | 9406.1 | 11028.9 | 9895.7 | 10866.1 | 9858.5 | 10962.3 | 10055.5 | 9779.9 | 10784.9 | 9910.9 | 9687.3 | 10847.9 | 11099.4 | 10838.3 | 9831.7 | 11013.9 | 9803.7 | 10600.2 | 9956.4 | 10549.3 | 9194 | 10691.6 | 9811.8 | 9944.5 | 9928.7 | 9801.3 | 8481.5 | 9739.2 | 8617 | 9778.2 | 9773.8 | 11510.1 | 9936.6 | 11582.2 | 10167 | 11401.6 | 9966.1 | 10179 | 9878.8 | 11165.6 | 11589.6 | 11404 | 11346.7 | 11454.3 | 11481.4 | 10286.5 | 11473.2 | 11411.9 | 11494.5 | 11519.3 | 11488.3 | 11576.4 | 10266.7 | 11436.6 | 10307.2 | 32.18 | 32 | 32.36 | 33.81 | 32.42 | 32.16 | 0 | 46.4 | 0 | 0 | 46.2 | 45.1 | 2.61 | 1.16 | 0.63 | 0.74 | 2.57 | 2.52 | 5.73 | 5.46 | 5.91 | 5.22 | 6.28 | 5.46 | 4.82 | 4.85 | 4.89 | 4.92 | 4.87 | 4.89 | 1.07 | 1.17 | 1.05 | 1.24 | 1.38 | 1.09 | 5.97 | 5.95 | 5.94 | 5.96 | 5.89 | 5.93 | 0.22 | 0.25 | 0.22 | 0.2 | 0.23 | 0.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 776357 | 1419 | 763043 | 1460 | 194422.882 | 551.8 | 4.82 | 4.85 | 4.89 | 4.92 | 4.87 | 4.89 | 5.97 | 5.95 | 5.94 | 5.96 | 5.89 | 5.93 | 826000 | 2000 | 832000 | 1000 | 1653200 | 5133 | 1655000 | 1648067 | 10.8667 | 4.8733 | 1.1667 | 5.94 | 0.225 | 23.94% | 3.788% | 32.4883 | 45.9 | 1.705 | 5.6767 | 1663081.5 | 1652500 | 1904213 | 86.78% | 40 | 0
2024-11-04 | 2025 | 2024 | Year_3 | Year_3 | 2024-11-01 | 30 | 335090.89 | 7:09 | 18:02 | 10035.9 | 10472.7 | 10450.4 | 10435.9 | 10419.3 | 10639.5 | 10564.8 | 11000.2 | 10441 | 10386.8 | 10330 | 10483 | 10476.2 | 10425.3 | 10512.9 | 10577.3 | 10460.5 | 10557.6 | 10569.8 | 10615.8 | 10547.4 | 10533.7 | 10290.8 | 10434.9 | 10139.5 | 8890.9 | 10217.8 | 10211.2 | 10488.5 | 10348.7 | 10259.3 | 10444.7 | 10457.8 | 10514.1 | 10459.7 | 10362.6 | 10556.7 | 10420.3 | 10475.2 | 10354.6 | 11615.5 | 10299.8 | 11428.6 | 10182.3 | 10687.5 | 11946.6 | 10034.4 | 11577.3 | 10389.6 | 10536.1 | 10541.4 | 9814 | 10916.5 | 10369 | 10736.7 | 10474.8 | 9476.7 | 11022.2 | 9613.9 | 10899 | 10766.7 | 9596 | 10497.5 | 9993.4 | 10063.2 | 9510.3 | 10018.4 | 10658.5 | 10835.8 | 9764.9 | 10673.9 | 9387.3 | 10266.2 | 10110.5 | 9435.4 | 10708.3 | 9356.7 | 10758.5 | 9437.5 | 10611.8 | 9983.2 | 10801.1 | 10045.1 | 11263.9 | 9898.7 | 10630.2 | 9812.4 | 8735.8 | 10834.8 | 10396.4 | 9720.1 | 11288.7 | 10852.6 | 9905.2 | 9724.5 | 11048.8 | 9767.5 | 10159.7 | 11003.1 | 9724.9 | 11189.2 | 9701.1 | 10863.7 | 9944.1 | 10988.7 | 9429.7 | 11066.3 | 9933.8 | 10879 | 9857.7 | 10999.2 | 10091.4 | 9803.7 | 10825.4 | 9942.1 | 9719.7 | 10878.5 | 11118.5 | 10872.1 | 9837.2 | 11030.6 | 9818.9 | 10642 | 9995.2 | 10591.4 | 9205.9 | 10714.9 | 9826.3 | 9953.8 | 9935.7 | 9848.6 | 8499.9 | 9754 | 8646 | 9790.2 | 9788.4 | 11529.7 | 9943.3 | 11599.5 | 10174 | 11402.2 | 9973.5 | 10180.2 | 9914.7 | 11188.7 | 11626.8 | 11402.5 | 11310.8 | 11469.5 | 11499.6 | 10307.2 | 11499.3 | 11418 | 11501.6 | 11536.5 | 11507.2 | 11595.4 | 10280.1 | 11445.6 | 10313.9 | 32.1106 | 31.8008 | 32.2805 | 33.8343 | 32.6035 | 32.0451 | 0 | 44.8 | 0 | 0 | 45.2841 | 45 | 2.4542 | 1.1194 | 0.42371 | 0.74547 | 2.5063 | 2.3056 | 5.265 | 4.5783 | 3.875 | 5.219 | 4.87 | 4.3317 | 4.8067 | 4.8364 | 4.8646 | 4.9227 | 4.8575 | 4.8691 | 1.0624 | 1.1619 | 1.0408 | 1.2444 | 1.3771 | 1.0899 | 5.969 | 5.9556 | 5.9387 | 5.9573 | 5.9054 | 5.9339 | 0.22603 | 0.25737 | 0.22224 | 0.20181 | 0.22458 | 0.22665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 777186 | 1421 | 763877 | 1462 | 196080.282 | 556.867 | 4.8067 | 4.8364 | 4.8646 | 4.9227 | 4.8575 | 4.8691 | 5.969 | 5.9556 | 5.9387 | 5.9573 | 5.9054 | 5.9339 | 829000 | 2000 | 834000 | 2000 | 1657400 | 5067 | 1659000 | 1652333 | 10.8833 | 4.8595 | 1.1628 | 5.9433 | 0.22645 | 23.93% | 3.81% | 32.4458 | 45.028 | 1.5924 | 4.6898 | 1667475.4 | 1657000 | 1902849.6004 | 87.08% | 37 | 0
2024-11-05 | 2025 | 2024 | Year_3 | Year_3 | 2024-11-01 | 30 | 335090.89 | 7:10 | 18:02 | 9827.6 | 10269.8 | 10269 | 10230.9 | 10280.4 | 10426.2 | 10390.2 | 10777.6 | 10206.8 | 10147 | 10141.8 | 10313.9 | 10259.1 | 10255 | 10290.3 | 10366.1 | 10247 | 10343.6 | 10352.4 | 10399.7 | 10326.7 | 10316.1 | 10088.2 | 10225.4 | 9940.6 | 8715.8 | 10011.6 | 9988.1 | 10266.3 | 10120.9 | 10052.1 | 10240.8 | 10242.2 | 10247.3 | 10226.8 | 10109 | 10370.2 | 10226 | 10259.1 | 10120.8 | 11402.1 | 10099.3 | 11223.6 | 9983.8 | 10461.2 | 11718.1 | 9821.6 | 11375.7 | 10188.3 | 10328.5 | 10329.9 | 9614.5 | 10692.5 | 10152.1 | 10522.4 | 10254.7 | 9292.6 | 10798.7 | 9422.5 | 10689.1 | 10557.5 | 9395.5 | 10281.3 | 9791.5 | 9854.8 | 9317.6 | 9817.2 | 10444 | 10610.2 | 9578.7 | 10457.7 | 9206.7 | 10056.5 | 9904.3 | 9242.7 | 10485.1 | 9161.4 | 10535.5 | 9237.7 | 10387.9 | 9773.7 | 10574.7 | 9843.5 | 11024.1 | 9694.9 | 10412 | 9597.3 | 8551.4 | 10591.7 | 10174.4 | 9511.3 | 11054.4 | 10661 | 9744.4 | 9583.9 | 10795.2 | 9555.3 | 9937 | 10765.8 | 9524.5 | 10936.2 | 9500.7 | 10630.9 | 9731.1 | 10767.1 | 9240 | 10839.7 | 9732.2 | 10685.4 | 9670.5 | 10768.4 | 9896.4 | 9603.8 | 10590.9 | 9736.7 | 9514.8 | 10670 | 10891.6 | 10656.9 | 9662.1 | 10829.5 | 9640 | 10424.8 | 9811.1 | 10368.9 | 9038.5 | 10526.5 | 9632.5 | 9793.4 | 9784.9 | 9646.3 | 8351 | 9528.5 | 8446.5 | 9571.5 | 9572.2 | 11339.7 | 9788.1 | 11402.3 | 10005.6 | 11249.8 | 9828.6 | 10023.5 | 9729.2 | 10990.9 | 11418.6 | 11251.6 | 11172.9 | 11283.6 | 11310.4 | 10126.2 | 11287.1 | 11281.1 | 11324.2 | 11389.4 | 11359.5 | 11395 | 10123.6 | 11334.2 | 10140.6 | 31.75 | 31.4 | 31.87 | 33.84 | 31.92 | 31.63 | 0 | 45.64 | 0 | 0 | 46.2 | 45.9 | 2.08 | 1.19 | 0.12 | 0.75 | 1.96 | 1.94 | 4.77 | 4.3 | 2.61 | 5.22 | 3.95 | 4.25 | 4.71 | 4.74 | 4.75 | 4.92 | 4.78 | 4.77 | 1.04 | 1.14 | 1.02 | 1.24 | 1.35 | 1.08 | 5.88 | 5.86 | 5.81 | 5.96 | 5.81 | 5.81 | 0.22 | 0.25 | 0.22 | 0.2 | 0.22 | 0.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 777998 | 1423 | 764695 | 1464 | 197705.815 | 561.8 | 4.71 | 4.74 | 4.75 | 4.92 | 4.78 | 4.77 | 5.88 | 5.86 | 5.81 | 5.96 | 5.81 | 5.81 | 812000 | 2000 | 818000 | 2000 | 1625533 | 4933 | 1626000 | 1620600 | 10.8667 | 4.7783 | 1.145 | 5.855 | 0.22167 | 23.96% | 3.786% | 32.0683 | 45.9133 | 1.34 | 4.1833 | 1635201.1 | 1624400 | 1874854 | 86.64% | 22 | 0
2024-11-06 | 2025 | 2024 | Year_3 | Year_3 | 2024-11-01 | 30 | 335090.89 | 7:08 | 18:00 | 9820.1 | 10281.4 | 10284.5 | 10245.4 | 10294.6 | 10429.7 | 10399 | 10872.9 | 10268.3 | 10129.5 | 10148.7 | 10346.9 | 10248.5 | 10244.2 | 10263.9 | 10352 | 10223.5 | 10334.2 | 10339.8 | 10386.6 | 10306.2 | 10297.8 | 10074.7 | 10208.6 | 9919.6 | 8703.9 | 9995.5 | 9981.3 | 10258.2 | 10142 | 10053.5 | 10216.9 | 10190.9 | 10213.5 | 10305.2 | 10217.7 | 10396.5 | 10258.2 | 10287.2 | 10090.4 | 11402.6 | 10094.5 | 11220.9 | 9989.2 | 10509.7 | 11805.6 | 9862.6 | 11378.3 | 10161.3 | 10296.2 | 10298.1 | 9587.8 | 10667.9 | 10124.2 | 10489.2 | 10239.5 | 9259 | 10759.7 | 9384.6 | 10625.7 | 10529.5 | 9373.1 | 10232.2 | 9754.6 | 9839.4 | 9279 | 9772.9 | 10411.4 | 10562.3 | 9538 | 10407.4 | 9172.2 | 10002.8 | 9857.9 | 9192.3 | 10435.5 | 9120.3 | 10491.1 | 9215.5 | 10359.2 | 9759.5 | 10561.5 | 9826.9 | 11007 | 9685.4 | 10410 | 9613.8 | 8559.8 | 10613.1 | 10178.7 | 9527.7 | 11071.4 | 10684.8 | 9786.9 | 9649.1 | 10825.2 | 9554 | 9969 | 10780.4 | 9524.6 | 10935 | 9514 | 10631.1 | 9742.9 | 10766.5 | 9244.3 | 10838.5 | 9735.7 | 10687.7 | 9693.4 | 10775.9 | 9904.7 | 9614.4 | 10589.4 | 9739.8 | 9504.7 | 10676.6 | 10880.2 | 10645.1 | 9655.4 | 10808.1 | 9623.7 | 10413.1 | 9809.2 | 10351.9 | 9036.2 | 10514.9 | 9634.8 | 9773.9 | 9771.2 | 9618.8 | 8331.9 | 9558.1 | 8443.8 | 9560.5 | 9547.2 | 11315.3 | 9756.4 | 11361 | 9977.6 | 11223.1 | 9808.5 | 10002.4 | 9715.4 | 10963.6 | 11387.4 | 11245.6 | 11151.9 | 11257.6 | 11279.5 | 10094.8 | 11249.7 | 11267.7 | 11333.4 | 11379.1 | 11344.7 | 11383.1 | 10108.9 | 11334.2 | 10140.3 | 32.17 | 31.81 | 32.37 | 33.86 | 32.47 | 31.92 | 0 | 44.3 | 0 | 0 | 45.4 | 44.1 | 2.46 | 1.52 | 0.31 | 0.75 | 2.5 | 2 | 5.04 | 4.55 | 3.99 | 5.22 | 5.24 | 4.95 | 4.68 | 4.72 | 4.73 | 4.92 | 4.76 | 4.74 | 1.05 | 1.14 | 1.02 | 1.24 | 1.36 | 1.08 | 5.87 | 5.84 | 5.8 | 5.96 | 5.79 | 5.82 | 0.23 | 0.25 | 0.22 | 0.2 | 0.22 | 0.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 778810 | 1425 | 765514 | 1466 | 199330.3 | 566.733 | 4.68 | 4.72 | 4.73 | 4.92 | 4.76 | 4.74 | 5.87 | 5.84 | 5.8 | 5.96 | 5.79 | 5.82 | 812000 | 2000 | 819000 | 2000 | 1624485 | 4933 | 1627000 | 1619552 | 10.8667 | 4.7583 | 1.1483 | 5.8467 | 0.225 | 24.13% | 3.848% | 32.4333 | 44.6 | 1.59 | 4.8317 | 1633977.3 | 1623601 | 1873169 | 86.68% | 20 | 0
2024-11-07 | 2025 | 2024 | Year_3 | Year_3 | 2024-11-01 | 30 | 335090.89 | 7:09 | 18:04 | 10085 | 10531.4 | 10513.4 | 10467.9 | 10522.3 | 10676.9 | 10625 | 11133.1 | 10557.1 | 10420 | 10417.5 | 10626.5 | 10528.8 | 10527.3 | 10594.7 | 10641.9 | 10532.2 | 10616.6 | 10638.8 | 10689.3 | 10619.4 | 10606.8 | 10361.1 | 10508.1 | 10237.2 | 8981.8 | 10301.3 | 10281.9 | 10556.2 | 10428.1 | 10328.9 | 10544.6 | 10490.9 | 10524.7 | 10616.9 | 10523.1 | 10702.9 | 10551.9 | 10570.6 | 10389.5 | 11684.7 | 10329.8 | 11493.9 | 10216.5 | 10756.8 | 12078.6 | 10124.6 | 11666 | 10442.4 | 10582.2 | 10578.8 | 9863.5 | 10978.6 | 10395.6 | 10813.2 | 10539.6 | 9551.4 | 11098.1 | 9654.6 | 10989 | 10850.4 | 9634.2 | 10579.5 | 10070.2 | 10174.6 | 9555.9 | 10081.6 | 10698.7 | 10901.6 | 9799.2 | 10723.7 | 9429.6 | 10319.6 | 10155.1 | 9474.7 | 10752.6 | 9400.1 | 10800.8 | 9484.9 | 10655.2 | 10027.7 | 10850.2 | 10090.7 | 11308.3 | 9939.1 | 10682.2 | 9876.6 | 8773.7 | 10900.5 | 10435.3 | 9776.3 | 11356.4 | 10940.5 | 10003.2 | 9848.7 | 11122.1 | 9821.7 | 10235.3 | 11062.3 | 9771.9 | 11203.1 | 9765.7 | 10874.1 | 10009.1 | 11057.2 | 9494.8 | 11138.4 | 10000.5 | 10978.4 | 9950.1 | 11064.8 | 10160.6 | 9869.2 | 10865.7 | 9991.9 | 9749.8 | 10963.4 | 11153.1 | 10931.5 | 9901.8 | 11090.6 | 9877.8 | 10685.7 | 10062.3 | 10642.1 | 9268 | 10784.4 | 9883.4 | 10018.8 | 10011 | 9853.3 | 8541.2 | 9826.5 | 8693.6 | 9848.5 | 9823.9 | 11623.2 | 10026.7 | 11664.7 | 10249.7 | 11527.2 | 10055.3 | 10253.3 | 9971.8 | 11266.1 | 11699.2 | 11561.1 | 11458.5 | 11575.1 | 11597.4 | 10367.5 | 11562.5 | 11578.5 | 11651.6 | 11692.7 | 11652.7 | 11703 | 10381.8 | 11636.2 | 10429 | 31.82 | 31.48 | 32.23 | 33.86 | 31.93 | 31.74 | 0 | 46.5 | 0 | 0 | 46.4 | 45.4 | 2.41 | 1.55 | 0.74 | 0.75 | 2.36 | 2.08 | 5.82 | 6.29 | 5.1 | 5.22 | 5.66 | 5.44 | 4.8 | 4.84 | 4.85 | 4.92 | 4.87 | 4.85 | 1.08 | 1.18 | 1.06 | 1.24 | 1.39 | 1.11 | 6.07 | 6.04 | 5.98 | 5.96 | 5.97 | 6.01 | 0.22 | 0.25 | 0.22 | 0.2 | 0.22 | 0.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 779644 | 1427 | 766354 | 1467 | 200999.3 | 571.733 | 4.8 | 4.84 | 4.85 | 4.92 | 4.87 | 4.85 | 6.07 | 6.04 | 5.98 | 5.96 | 5.97 | 6.01 | 834000 | 2000 | 840000 | 1000 | 1669000 | 5000 | 1671000 | 1664000 | 10.9167 | 4.855 | 1.1767 | 6.005 | 0.22167 | 24.24% | 3.691% | 32.1767 | 46.1 | 1.6483 | 5.5883 | 1678893.5 | 1668000 | 1921366.2477 | 86.81% | 23 | 0
2024-11-08 | 2025 | 2024 | Year_3 | Year_3 | 2024-11-01 | 30 | 335090.89 | 7:10 | 18:01 | 10271.2 | 10714.5 | 10744.8 | 10720.6 | 10792 | 10880 | 10790.9 | 11297.2 | 10741.7 | 10625.7 | 10590.5 | 10806.2 | 10706.1 | 10699.6 | 10782.6 | 10829.6 | 10718.8 | 10800 | 10821.3 | 10866.8 | 10803.8 | 10791.6 | 10548.6 | 10693.3 | 10425.9 | 9150.9 | 10474.7 | 10474.8 | 10748.9 | 10609.4 | 10521.4 | 10732.2 | 10702.3 | 10707.9 | 10742.9 | 10641.2 | 10916.5 | 10753.8 | 10770.6 | 10573.7 | 11895 | 10520.8 | 11706.4 | 10406.2 | 10932.7 | 12243.3 | 10307.5 | 11857.9 | 10611 | 10752.9 | 10772.3 | 10063.8 | 11179.8 | 10605.7 | 10995.1 | 10712.5 | 9709.3 | 11289.5 | 9808.3 | 11108.7 | 11013.1 | 9792.9 | 10783.1 | 10272.3 | 10345.1 | 9701.8 | 10255.1 | 10872.7 | 11078.4 | 9965.4 | 10893.2 | 9583.8 | 10491 | 10267 | 9638 | 10931 | 9560 | 10971 | 9633 | 10824 | 10199.4 | 11039.4 | 10278.4 | 11504.7 | 10132 | 10885.6 | 10032.8 | 8932.7 | 11083.4 | 10622.3 | 9951.2 | 11560.5 | 11158.5 | 10212.8 | 10070.4 | 11313.5 | 10002.8 | 10424.6 | 11266 | 9962 | 11452.5 | 9956.4 | 11112.3 | 10202.2 | 11260.2 | 9674.1 | 11340.6 | 10177.9 | 11168.2 | 10114.6 | 11267.7 | 10342.5 | 10056.6 | 11088.9 | 10178.9 | 9960.7 | 11167.6 | 11359.7 | 11144.4 | 10074.1 | 11284.6 | 10055.8 | 10870 | 10239.4 | 10826.1 | 9433.2 | 10968.7 | 10067.6 | 10200 | 10193.5 | 10023.7 | 8698.6 | 9990.5 | 8832.6 | 10032.9 | 10021.3 | 11812.7 | 10191.5 | 11860.7 | 10435.1 | 11714.8 | 10227.4 | 10427.9 | 10170.4 | 11447.8 | 11897.8 | 11738.9 | 11647.8 | 11769.4 | 11792.5 | 10545.9 | 11754.9 | 11772.2 | 11838.3 | 11880.6 | 11833.5 | 11897.9 | 10555.1 | 11834.8 | 10600.7 | 31.5264 | 31.2046 | 31.942 | 33.8564 | 31.8654 | 31.2556 | 0 | 44.2 | 0 | 0 | 45.3 | 44.1 | 2.7096 | 1.8018 | 0.87804 | 0.74783 | 2.5856 | 2.0889 | 6.6283 | 6.2583 | 4.9967 | 5.219 | 5.9133 | 5.4467 | 4.8464 | 4.8941 | 4.9128 | 4.9212 | 4.9244 | 4.9081 | 1.1009 | 1.1947 | 1.0743 | 1.2442 | 1.4152 | 1.1166 | 6.1504 | 6.1252 | 6.0976 | 5.9566 | 6.066 | 6.0889 | 0.22814 | 0.25783 | 0.22223 | 0.20177 | 0.22857 | 0.22777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 780493 | 1429 | 767208 | 1468 | 202697.416 | 576.8 | 4.8464 | 4.8941 | 4.9128 | 4.9212 | 4.9244 | 4.9081 | 6.1504 | 6.1252 | 6.0976 | 5.9566 | 6.066 | 6.0889 | 849000 | 2000 | 854000 | 1000 | 1698116 | 5067 | 1700000 | 1693049 | 10.85 | 4.9012 | 1.191 | 6.0808 | 0.22772 | 24.3% | 3.745% | 31.9417 | 44.5333 | 1.802 | 5.7437 | 1708455.3 | 1697067 | 1948583.513 | 87.09% | 21 | 215
2024-11-09 | 2025 | 2024 | Year_3 | Year_3 | 2024-11-01 | 30 | 335090.89 | 7:09 | 18:00 | 10328.2 | 10798.6 | 10844.3 | 10805.8 | 10873.2 | 11005.7 | 10950.8 | 11384.5 | 10783.2 | 10667.4 | 10640.7 | 10855.4 | 10765.9 | 10754.2 | 10839.2 | 10893.2 | 10788.7 | 10866.5 | 10882.5 | 10925.3 | 10868.3 | 10853 | 10612.2 | 10758.7 | 10490.5 | 9203 | 10531.9 | 10528.7 | 10806.5 | 10668.7 | 10587.8 | 10801.5 | 10791.8 | 10783.5 | 8446.1 | 8415.9 | 10991.3 | 10827.6 | 10820.7 | 10648.2 | 11976.2 | 10603.4 | 11790.7 | 10493.9 | 11031 | 12336.9 | 10397.6 | 11935.9 | 10672 | 10806.9 | 10843.1 | 10128 | 11257.8 | 10695.5 | 11064 | 10761.3 | 9779.1 | 11378.2 | 9873.9 | 11231.6 | 11062.1 | 9846.2 | 10881.4 | 10368.3 | 10437.7 | 9785.7 | 10344.4 | 10952.4 | 11174.9 | 10044.9 | 11001.3 | 9653 | 10571 | 10331 | 9712 | 11022 | 9641 | 11036 | 9701 | 10916 | 10266 | 11114.8 | 10344.2 | 11575.5 | 10199.9 | 10958.2 | 10105.8 | 8983.8 | 11207 | 10685.2 | 10029.8 | 11677.6 | 11243.8 | 10294.9 | 10153 | 11396.5 | 10047.8 | 10407.7 | 11330.6 | 10033.7 | 11545.6 | 10028.3 | 11207.5 | 10270.7 | 11345.8 | 9744.1 | 11423.8 | 10262.4 | 11250.5 | 10183.4 | 11345.2 | 10422.2 | 10126.5 | 11170.4 | 10260.9 | 10037.4 | 11244.8 | 11464.6 | 11220 | 10150.7 | 11362.7 | 10129.2 | 10947.3 | 10308.8 | 10870.7 | 9491.9 | 11045.3 | 10146.7 | 10269 | 10259.3 | 10096.1 | 8761 | 10092.2 | 8898.3 | 10091.7 | 10084.4 | 11879.7 | 10255.1 | 11927.9 | 10499.5 | 11800.6 | 10317.4 | 10512.9 | 10242 | 11536.9 | 11978.7 | 11818.5 | 11716.3 | 11848.3 | 11867.6 | 10615.7 | 11832.4 | 11850.1 | 11916.8 | 11962 | 11919.1 | 11987.1 | 10636.9 | 11916.5 | 10670.7 | 30.9117 | 30.5929 | 31.0548 | 33.8564 | 31.3828 | 30.7389 | 0 | 43.7116 | 0 | 0 | 44.1 | 42.9 | 3.0636 | 2.0456 | 1.5571 | 0.74783 | 3.0274 | 2.5586 | 5.91 | 6.2083 | 6.1417 | 5.219 | 6.05 | 6.2967 | 4.8429 | 4.8837 | 4.907 | 4.9212 | 4.9127 | 4.9034 | 1.0948 | 1.1972 | 1.0721 | 1.2443 | 1.4175 | 1.1261 | 6.1633 | 6.134 | 6.1077 | 5.9566 | 6.0708 | 6.0995 | 0.22939 | 0.25843 | 0.22225 | 0.20238 | 0.22927 | 0.22944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 781344 | 1432 | 768069 | 1471 | 204402.683 | 581.8 | 4.8429 | 4.8837 | 4.907 | 4.9212 | 4.9127 | 4.9034 | 6.1633 | 6.134 | 6.1077 | 5.9566 | 6.0708 | 6.0995 | 851000 | 3000 | 861000 | 3000 | 1705267 | 5000 | 1706000 | 1700267 | 10.85 | 4.8952 | 1.192 | 6.0887 | 0.22853 | 24.35% | 3.753% | 31.4229 | 43.5705 | 2.1667 | 5.9709 | 1715752.4 | 1704300 | 1958290.1294 | 87.03% | 23 | 0
2024-11-10 | 2025 | 2024 | Year_3 | Year_3 | 2024-11-01 | 30 | 335090.89 | 7:09 | 18:04 | 10343.9 | 10795.4 | 10841.2 | 10809.7 | 10849.1 | 11006.4 | 10977.1 | 11462.8 | 10823.3 | 10749.3 | 10674.5 | 10874.2 | 10798.7 | 10776.3 | 10829.9 | 10892.6 | 10786.1 | 10883.4 | 10889.8 | 10933.7 | 10876.2 | 10862.1 | 10628 | 10773.8 | 10497.6 | 9213.8 | 10541.1 | 10531.5 | 10832 | 10704.4 | 10586.2 | 10805.6 | 10791.4 | 10813.3 | 10896.4 | 10812.7 | 10996.7 | 10827.6 | 10775.5 | 10646.4 | 11966.1 | 10603.4 | 11778.5 | 10497.4 | 11022.4 | 12305.9 | 10395.5 | 11923.6 | 10667.4 | 10794 | 10848.8 | 10087.4 | 11258.5 | 10691.8 | 11033.2 | 10737.3 | 9768.5 | 11369.9 | 9880.2 | 11182 | 11016.4 | 9850.4 | 10893.1 | 10389.8 | 10432.7 | 9783.3 | 10333.4 | 10958.9 | 11165.5 | 10046.6 | 10988.4 | 9655.8 | 10575.5 | 10327.8 | 9693.2 | 11017.5 | 9636.2 | 11026.8 | 9697.4 | 10916.9 | 10281 | 11120.9 | 10338.3 | 11587.2 | 10205.2 | 10946.6 | 10122.8 | 8978.3 | 11222 | 10709.7 | 10028.7 | 11683.2 | 11224.5 | 10271.3 | 10123.6 | 11416.9 | 10056.2 | 10433.6 | 11342.7 | 10025.6 | 11548.2 | 10015.6 | 11196.9 | 10276.8 | 11328.7 | 9740 | 11403.2 | 10254.4 | 11231.3 | 10181.8 | 11338.8 | 10399 | 10108.2 | 11152.7 | 10250.6 | 10019.8 | 11239.3 | 11449.5 | 11197.5 | 10136.7 | 11345.7 | 10113.8 | 10925 | 10288.6 | 10853.9 | 9458.8 | 11024.4 | 10124.1 | 10259.8 | 10252.2 | 10114.9 | 8752.9 | 10092.9 | 8907.3 | 10061.8 | 10058.9 | 11867.9 | 10248.8 | 11923.1 | 10496.6 | 11798.2 | 10313.3 | 10506.1 | 10223.1 | 11506.3 | 11961.9 | 11800.9 | 11700 | 11834.4 | 11854.3 | 10605.3 | 11820.4 | 11842.9 | 11906.3 | 11944 | 11903 | 11968.5 | 10617 | 11902.4 | 10651 | 30.41 | 30.22 | 30.72 | 33.86 | 30.85 | 30.28 | 0 | 43.1 | 0 | 0 | 44.4 | 43 | 2.52 | 1.35 | 1.06 | 0.75 | 2.49 | 1.6 | 5.18 | 5.32 | 5.28 | 5.22 | 5.17 | 5.4 | 4.82 | 4.87 | 4.89 | 4.92 | 4.9 | 4.87 | 1.1 | 1.2 | 1.07 | 1.24 | 1.41 | 1.12 | 6.15 | 6.15 | 6.11 | 5.96 | 6.07 | 6.09 | 0.23 | 0.26 | 0.22 | 0.2 | 0.23 | 0.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 782199 | 1433 | 768929 | 1472 | 206112.016 | 586.733 | 4.82 | 4.87 | 4.89 | 4.92 | 4.9 | 4.87 | 6.15 | 6.15 | 6.11 | 5.96 | 6.07 | 6.09 | 855000 | 1000 | 860000 | 1000 | 1709333 | 4933 | 1713000 | 1704400 | 10.9167 | 4.8783 | 1.19 | 6.0883 | 0.22833 | 24.39% | 3.75% | 31.0567 | 43.5 | 1.6283 | 5.2617 | 1720045.1 | 1708400 | 1955553.2677 | 87.36% | 24 | 0
2024-11-11 | 2025 | 2024 | Year_3 | Year_3 | 2024-11-01 | 30 | 335090.89 | 7:11 | 18:00 | 9996.1 | 10425.3 | 10504.7 | 10453.9 | 10546.2 | 10630 | 10590.3 | 11064.3 | 10463.6 | 10405.9 | 10320.6 | 10501.9 | 10441.4 | 10411.5 | 10501.1 | 10533.3 | 10440.5 | 10521.8 | 10526.7 | 10569.5 | 10518.5 | 10499.7 | 10264.8 | 10404.6 | 10130.8 | 8896.5 | 10166.3 | 10171.8 | 10458.9 | 10344.6 | 10232 | 10437.2 | 10430.4 | 10455 | 10533.6 | 10447.7 | 10622.8 | 10464.5 | 10396.2 | 10300.2 | 11589.8 | 10253.3 | 11413.2 | 10147 | 10655.1 | 11956.4 | 10044.1 | 11572.3 | 10308.6 | 10431.1 | 10473 | 9731.6 | 10868 | 10316.3 | 10644 | 10386.7 | 9435.4 | 10967.4 | 9548.8 | 10811.5 | 10654.5 | 9516.8 | 10518.7 | 10024.8 | 10076 | 9473.6 | 9984.4 | 10596 | 10789.6 | 9727.5 | 10624.6 | 9343 | 10215.2 | 9982.4 | 9366.4 | 10640 | 9300.8 | 10647.4 | 9363.5 | 10536.3 | 9945.6 | 10757.6 | 10006.8 | 11205.1 | 9873.1 | 10593.1 | 9787.5 | 8695 | 10831.7 | 10379.6 | 9694.7 | 11287.7 | 10880.1 | 9963.3 | 9827.6 | 11021.7 | 9724 | 10144.6 | 10983.7 | 9695.1 | 11182.9 | 9685.9 | 10828.2 | 9940.6 | 10957.3 | 9411.5 | 11022.7 | 9907.6 | 10858 | 9852.2 | 10958.3 | 10050.3 | 9774.4 | 10785.1 | 9907.5 | 9698 | 10907 | 11044.4 | 10830.1 | 9799.6 | 10962.4 | 9771.9 | 10570.3 | 9953.8 | 10538.7 | 9150 | 10655.6 | 9778.1 | 9930.4 | 9927.2 | 9771.2 | 8469.8 | 9654.8 | 8583.6 | 9699.6 | 9698.9 | 11461.5 | 9894.7 | 11509.3 | 10132.8 | 11378.9 | 9946.5 | 10140.4 | 9862.3 | 11120.7 | 11550.7 | 11401.9 | 11304.9 | 11420 | 11433.8 | 10235.6 | 11409.3 | 11436.9 | 11497.2 | 11539.6 | 11502.5 | 11558.5 | 10259.5 | 11504.3 | 10297.4 | 30.1221 | 29.853 | 30.2731 | 33.8801 | 30.5289 | 30.1214 | 0 | 43.5398 | 0 | 0 | 42.8845 | 42.2965 | 2.7304 | 1.4386 | 0.69333 | 0.7514 | 2.7255 | 2.5203 | 6.91 | 6.1 | 5.1067 | 5.219 | 7.1033 | 5.9433 | 4.6693 | 4.7147 | 4.7276 | 4.9204 | 4.7278 | 4.703 | 1.0666 | 1.1593 | 1.0447 | 1.2438 | 1.3702 | 1.0886 | 5.9211 | 5.9247 | 5.895 | 5.9555 | 5.8469 | 5.858 | 0.21994 | 0.25126 | 0.21678 | 0.20104 | 0.22304 | 0.22311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 782985 | 1435 | 769801 | 1474 | 207764.483 | 590.267 | 4.6693 | 4.7147 | 4.7276 | 4.9204 | 4.7278 | 4.703 | 5.9211 | 5.9247 | 5.895 | 5.9555 | 5.8469 | 5.858 | 786000 | 2000 | 872000 | 2000 | 1652467 | 3534 | 1654000 | 1648933 | 10.8167 | 4.7438 | 1.1622 | 5.9002 | 0.22253 | 24.5% | 3.772% | 30.7964 | 42.9069 | 1.8099 | 6.0637 | 1662574.5 | 1651734 | 1902011.6856 | 86.84% | 23 | 0
2024-11-12 | 2025 | 2024 | Year_3 | Year_3 | 2024-11-01 | 30 | 335090.89 | 7:10 | 17:58 | 9739.4 | 10181.3 | 10216 | 10168.8 | 10254.2 | 10359.7 | 10341.2 | 10762.3 | 10170 | 10337 | 10033 | 10210.6 | 10154.8 | 10128 | 10221 | 10257 | 10158.6 | 10247.4 | 10251.4 | 10299.3 | 10239.9 | 10225.2 | 9986.1 | 10129.8 | 9855 | 8897 | 9909.3 | 9899.2 | 10170 | 10027 | 9910.3 | 10140.1 | 10168.3 | 10206.2 | 10246.1 | 10169 | 10332.7 | 10178.8 | 10210.9 | 10034.3 | 11269.4 | 9968 | 11102.1 | 9858.3 | 10379.1 | 11690 | 9768 | 11247.9 | 10038.8 | 10171.2 | 10211.2 | 9516 | 10592.2 | 10032.1 | 10399.4 | 10124.9 | 9188.3 | 10667.9 | 9298.3 | 10551 | 10407.3 | 9279 | 10224.5 | 9744 | 9814.1 | 9202.2 | 9711.4 | 10309.9 | 10495 | 9459.2 | 10331.2 | 9072.9 | 9940.7 | 9704.6 | 9123.9 | 10340.8 | 9050.2 | 10356.1 | 9109.1 | 10264.5 | 9659 | 10452 | 9719 | 10883.7 | 9583.7 | 10290.5 | 9515.9 | 8447.9 | 10522.9 | 10090.8 | 9401.4 | 10955.9 | 10568 | 9685.6 | 9551.8 | 10683.8 | 9433.8 | 9849.1 | 10667.8 | 9426.4 | 10866.5 | 9412.4 | 10529.4 | 9658.4 | 10660.1 | 9152.1 | 10721.8 | 9632.8 | 10563.2 | 9567 | 10648.9 | 9772.7 | 9508.1 | 10494.4 | 9635.7 | 9439.3 | 10618 | 10746.9 | 10542.1 | 9541 | 10671.2 | 9513.6 | 10282.8 | 9684.7 | 10246.5 | 8903.2 | 10378.7 | 9378.3 | 9657 | 9654.3 | 9496.9 | 8228.7 | 9350.5 | 8333.3 | 9412.7 | 9416.3 | 11150.1 | 9605 | 11196.4 | 9847.2 | 11071.5 | 9686.7 | 9871.2 | 9585.5 | 10805.4 | 11226.3 | 11085.8 | 10990.5 | 11102 | 11118.9 | 9949.9 | 11089.3 | 11152.5 | 11206.5 | 11231.4 | 11189.7 | 11235.7 | 9957.3 | 11203.1 | 10014.5 | 29.0788 | 28.9334 | 29.4008 | 33.9019 | 29.3228 | 29.0869 | 0 | 42.6581 | 0 | 0 | 42.614 | 42.1 | 2.1794 | 0.9677 | 0.23683 | 0.7538 | 2.2858 | 1.6837 | 4.7533 | 6.2283 | 4.035 | 5.219 | 4.6217 | 5.5817 | 4.5257 | 4.5673 | 4.5907 | 4.9191 | 4.581 | 4.5751 | 1.0316 | 1.1239 | 1.0157 | 1.2415 | 1.3276 | 1.0588 | 5.7248 | 5.7191 | 5.7056 | 5.9546 | 5.6524 | 5.6756 | 0.21487 | 0.24606 | 0.21254 | 0.19696 | 0.21677 | 0.21584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 783831 | 1435 | 770569 | 1474 | 209372.283 | 594.733 | 4.5257 | 4.5673 | 4.5907 | 4.9191 | 4.581 | 4.5751 | 5.7248 | 5.7191 | 5.7056 | 5.9546 | 5.6524 | 5.6756 | 846000 | 0 | 768000 | 0 | 1607800 | 4466 | 1614000 | 1603334 | 10.8 | 4.6265 | 1.1332 | 5.7387 | 0.21717 | 24.49% | 3.784% | 29.9541 | 42.4574 | 1.3512 | 5.0732 | 1617721.8 | 1606133 | 1841053.6523 | 87.24% | 24 | 0
2024-11-13 | 2025 | 2024 | Year_3 | Year_3 | 2024-11-01 | 30 | 335090.89 | 7:14 | 17:57 | 9304 | 9721.2 | 9731.8 | 9695.8 | 9762.7 | 9872.1 | 9852.6 | 10306.2 | 9714.1 | 9686.9 | 9574.9 | 9738.8 | 9673.6 | 9641.6 | 9714.2 | 9769.6 | 9659.4 | 9743.8 | 9749.4 | 9796.9 | 9738.1 | 9730.6 | 9503.8 | 9633.3 | 9377.2 | 8228.8 | 9422.3 | 9419.1 | 9679.7 | 9577.6 | 9449.2 | 9662.9 | 9704.6 | 9755.2 | 9751 | 9682.8 | 9846.2 | 9697.6 | 9720.9 | 9574.2 | 10672.6 | 9429 | 10523.8 | 9334.5 | 9839.8 | 11081.9 | 9259.7 | 10663.2 | 9582.3 | 9713.4 | 9723.4 | 9076.6 | 10066.7 | 9540.6 | 9918.4 | 9652.8 | 8766.8 | 10168.1 | 8880.9 | 10090.2 | 9970.7 | 8882.3 | 9736.7 | 9286 | 9336.6 | 8740 | 9253.4 | 9807.7 | 10008.3 | 8994.6 | 9839.5 | 8628.5 | 9492.1 | 9240.4 | 8711.6 | 9863.7 | 8645.8 | 9897.5 | 8708 | 9820.2 | 9180.3 | 9963.5 | 9234.4 | 10354.3 | 9115.2 | 9800.1 | 9053.1 | 8045.9 | 9997.6 | 9607.4 | 8879.3 | 10405 | 10050.3 | 9197.5 | 9061.4 | 10175.9 | 9016.5 | 9383.5 | 10162.1 | 8959 | 10362.1 | 8953.6 | 10018.2 | 9186 | 10140.3 | 8702.5 | 10197.3 | 9148.9 | 10047.4 | 9098.7 | 10121.2 | 9277.5 | 9045 | 9981.5 | 9149.2 | 8968.5 | 10087.7 | 10202.6 | 10010.2 | 9069.2 | 10135.1 | 9036.7 | 9771.3 | 9194.9 | 9727.2 | 8464.7 | 9856.6 | 8905.8 | 9161.6 | 9171.3 | 9005.9 | 7801.7 | 8952.2 | 7914.5 | 9005.3 | 9012.4 | 10640 | 9177.5 | 10684.5 | 9400.6 | 10572.2 | 9228.5 | 9396.3 | 9139.1 | 10268.7 | 10674.1 | 10548.2 | 10462.1 | 10574 | 10599.4 | 9477.7 | 10557.8 | 10618.4 | 10648 | 10691.4 | 10637.7 | 10672.2 | 9457.1 | 10653 | 9518.6 | 28.6881 | 28.5758 | 28.8999 | 33.9453 | 28.6715 | 28.4882 | 0 | 42.5284 | 0 | 0 | 42.8 | 41.6 | 2.3438 | 1.5217 | 0.53256 | 0.75865 | 2.2081 | 1.4977 | 4.6583 | 4.7667 | 3.5783 | 5.219 | 4.5933 | 4.3967 | 4.3493 | 4.374 | 4.3879 | 4.9175 | 4.3851 | 4.3759 | 1.0016 | 1.0881 | 0.98122 | 1.2394 | 1.278 | 1.0263 | 5.4685 | 5.4311 | 5.4086 | 5.9526 | 5.3751 | 5.3877 | 0.21275 | 0.23932 | 0.21018 | 0.19673 | 0.21008 | 0.21415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 784598 | 1437 | 771338 | 1476 | 210903.416 | 599.733 | 4.3493 | 4.374 | 4.3879 | 4.9175 | 4.3851 | 4.3759 | 5.4685 | 5.4311 | 5.4086 | 5.9526 | 5.3751 | 5.3877 | 767000 | 2000 | 769000 | 2000 | 1531133 | 5000 | 1532000 | 1526133 | 10.7167 | 4.4649 | 1.1025 | 5.5039 | 0.21387 | 24.69% | 3.886% | 29.5448 | 42.3095 | 1.4771 | 4.5354 | 1539537.2 | 1514800 | 1746917.2236 | 86.71% | 24 | 0
2024-11-14 | 2025 | 2024 | Year_3 | Year_3 | 2024-11-01 | 30 | 335090.89 | 7:13 | 17:55 | 9436.9 | 9894.2 | 9866.9 | 9817 | 9916 | 10000.7 | 9957.1 | 10444.6 | 9824.8 | 9812.6 | 9719 | 9898.5 | 9818.2 | 9813.9 | 9852 | 9919.1 | 9800.9 | 9897 | 9899.4 | 9950 | 9881.7 | 9875.2 | 9644 | 9780.2 | 9518.5 | 8351.6 | 9559.2 | 9547.9 | 9814.6 | 9707.2 | 9596.3 | 9801.6 | 9847.8 | 9901.8 | 9897.1 | 9814.2 | 9985.6 | 9844.6 | 9867.6 | 9718.1 | 10882.2 | 9626.1 | 10735.6 | 9525.6 | 10017.5 | 11268.2 | 9427.1 | 10862.8 | 9703.9 | 9833 | 9858.8 | 9196 | 10219 | 9671.7 | 10058.1 | 9780.6 | 8884.8 | 10325.4 | 8974.7 | 10219.4 | 10078.2 | 8972.1 | 9868.4 | 9391.3 | 9474.7 | 8878.9 | 9388.3 | 9968.4 | 10156.1 | 9131.4 | 9979 | 8765 | 9633.6 | 9369.8 | 8847 | 9999 | 8749.7 | 10045.9 | 8811 | 9935.9 | 9354.7 | 10140.1 | 9385 | 10544.7 | 9268 | 9957.3 | 9197.9 | 8177.9 | 10127.3 | 9770.5 | 9063.2 | 10558.9 | 10198.3 | 9343.3 | 9210.7 | 10319.8 | 9167.3 | 9522.9 | 10313.7 | 9095.5 | 10507.9 | 9083 | 10160 | 9325.3 | 10299.3 | 8834.4 | 10366.3 | 9308.1 | 10226.2 | 9271.1 | 10313.6 | 9445.3 | 9187.6 | 10152.9 | 9304.2 | 9123.2 | 10254.6 | 10393.9 | 10192.8 | 9237.2 | 10323.1 | 9209.6 | 9945.8 | 9367 | 9912.9 | 8620 | 10041 | 9080.6 | 9304.6 | 9295.3 | 9162.3 | 7933 | 9115.5 | 8039.1 | 9178.5 | 9171.2 | 10815.6 | 9332.8 | 10863.6 | 9553.4 | 10740.9 | 9378.4 | 9548.5 | 9297 | 10454 | 10867 | 10724.3 | 10633.6 | 10750.6 | 10782.9 | 9645.8 | 10740 | 10799.7 | 10837.1 | 10908 | 10858 | 10880.1 | 9647.2 | 10826.5 | 9686.7 | 28.7239 | 28.6062 | 28.926 | 29.3195 | 28.7058 | 28.5209 | 0 | 42.6432 | 0 | 0 | 42.2588 | 41.8 | 2.347 | 1.5291 | 0.53514 | 0.76233 | 2.2144 | 1.5049 | 4.6583 | 4.7667 | 3.5783 | 5.219 | 4.5933 | 4.3967 | 4.3493 | 4.374 | 4.3879 | 4.9175 | 4.3851 | 4.3759 | 1.0016 | 1.0881 | 0.98122 | 1.2394 | 1.278 | 1.0263 | 5.4676 | 5.4302 | 5.4077 | 5.5403 | 5.3741 | 5.3868 | 0.21275 | 0.23932 | 0.21018 | 0.19673 | 0.21008 | 0.21415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 785376 | 1439 | 772120 | 1477 | 212458.75 | 604.733 | 4.3493 | 4.374 | 4.3879 | 4.9175 | 4.3851 | 4.3759 | 5.4676 | 5.4302 | 5.4077 | 5.5403 | 5.3741 | 5.3868 | 778000 | 2000 | 782000 | 1000 | 1555334 | 5000 | 1557000 | 1550334 | 10.7 | 4.4649 | 1.1025 | 5.4344 | 0.21387 | 24.69% | 3.935% | 28.8004 | 42.234 | 1.4821 | 4.5354 | 1563982.9 | 1538400 | 1770040.3297 | 86.91% | 24 | 0
2024-11-15 | 2025 | 2024 | Year_3 | Year_3 | 2024-11-01 | 30 | 335090.89 | 7:14 | 17:56 | 8320 | 8767.2 | 8741.8 | 8692.2 | 8775.8 | 8863.1 | 8839.9 | 9234.6 | 8667.5 | 8644.1 | 8596.7 | 8760.5 | 8671.3 | 8686.4 | 8682.3 | 8748.1 | 8605.7 | 8669 | 8670.8 | 8728.4 | 8631.9 | 8632.1 | 8416.7 | 8536.3 | 8326.6 | 7321 | 8359 | 8343.9 | 8566.4 | 8451.2 | 8399.1 | 8570.7 | 8695.5 | 8749.4 | 8726.4 | 8650.1 | 8786.9 | 8659.2 | 8675.8 | 8566.6 | 9689.1 | 8602.4 | 9559.7 | 8485.5 | 8909.3 | 9955.5 | 8317 | 9608.3 | 8589.2 | 8699.9 | 8712.4 | 8137.8 | 9010.6 | 8565.2 | 8902.1 | 8633.8 | 7907.7 | 9190.9 | 7912.2 | 9019.9 | 8899.9 | 7920.9 | 8754.6 | 8308.6 | 8429.7 | 7868.7 | 8335 | 8834.8 | 9003.6 | 8100.8 | 8809.1 | 7744.2 | 8510.2 | 8263.9 | 7795.7 | 8821.2 | 7685.9 | 8841.8 | 7737.7 | 8712.6 | 8223.6 | 8913.8 | 8189.8 | 9263.2 | 8076.8 | 8651 | 8042.8 | 7096.5 | 8890.9 | 8538.1 | 8007 | 9363.1 | 9091.3 | 8329.3 | 8230.4 | 9157 | 8119.8 | 8438 | 9157.3 | 8058.3 | 9320.3 | 8053.1 | 9015.2 | 8264.3 | 9126.1 | 7828.3 | 9188.6 | 8246.2 | 9069.1 | 8214.9 | 9130.9 | 8365.2 | 8133.3 | 8968.5 | 8205.3 | 8047.4 | 9065.5 | 9166.8 | 9006.8 | 8125.6 | 9076.9 | 8088.9 | 8789 | 8264.4 | 8722.4 | 7578.9 | 8837.2 | 7963.3 | 8126.7 | 8129.8 | 8006.3 | 6914.9 | 8003.6 | 7168.2 | 8086.5 | 8118.3 | 9614.6 | 8288.9 | 9641.1 | 8485.1 | 9550.4 | 8335.2 | 8484.5 | 8271.3 | 9346 | 9710.6 | 9550.8 | 9474.7 | 9554.4 | 9585.9 | 8557.8 | 9549.6 | 9638.1 | 9657.2 | 9794.8 | 9738.8 | 9741.1 | 8667.4 | 9635.5 | 8638.1 | 28.27 | 28 | 28.56 | 28.37 | 28.4 | 28.17 | 0 | 40.08 | 0 | 0 | 40.8 | 40 | 2.14 | 1.31 | 0.42 | 0.77 | 2.15 | 1.36 | 5.52 | 5.37 | 4.62 | 5.22 | 4.74 | 5 | 3.95 | 3.94 | 4.03 | 4.92 | 4 | 4.03 | 0.92 | 0.99 | 0.91 | 1.24 | 1.17 | 0.95 | 4.92 | 4.83 | 4.89 | 4.9 | 4.84 | 4.87 | 0.21 | 0.24 | 0.21 | 0.2 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 786063 | 1441 | 772813 | 1479 | 213834.55 | 609.733 | 3.95 | 3.94 | 4.03 | 4.92 | 4 | 4.03 | 4.92 | 4.83 | 4.89 | 4.9 | 4.84 | 4.87 | 687000 | 2000 | 693000 | 2000 | 1375800 | 5000 | 1376000 | 1370800 | 10.7 | 4.145 | 1.03 | 4.875 | 0.21333 | 24.85% | 4.376% | 28.295 | 40.2933 | 1.3583 | 5.0783 | 1381984.2 | 1374700 | 1600345 | 85.9% | 26 | 491
2024-11-16 | 2025 | 2024 | Year_3 | Year_3 | 2024-11-01 | 30 | 335090.89 | 7:15 | 17:55 | 8311 | 8745.8 | 8699.4 | 8640.2 | 8744.8 | 8831.2 | 8699 | 8813.1 | 8333.6 | 8311.5 | 8253 | 8403.9 | 8328.2 | 8324.8 | 8401.8 | 8441 | 8649.8 | 8721.9 | 8729.6 | 8762.5 | 8715.7 | 8704.6 | 8506.9 | 8619.1 | 8386.1 | 7358.7 | 8395.7 | 8402.6 | 8629.2 | 8528.8 | 8475.6 | 8644.5 | 9186.3 | 9258.4 | 9268.8 | 9204.9 | 9002.5 | 8867.8 | 9029.5 | 8877.9 | 9597.7 | 8495.4 | 9466.7 | 8401.1 | 8818.3 | 9903.7 | 8297.3 | 9582.8 | 8563.4 | 8673.9 | 8688.8 | 8102.2 | 9020.9 | 8568.9 | 8860.3 | 8616.9 | 7909.8 | 9208.7 | 8009.3 | 9096.1 | 8967.1 | 8001.1 | 8826.6 | 8381.5 | 8377.9 | 7836.8 | 8297.7 | 8804 | 8987.1 | 8070.3 | 8775.2 | 7731.2 | 8502.6 | 8280.3 | 7805 | 8828.9 | 7712.3 | 8861.5 | 7763.9 | 8762.7 | 8239.7 | 8937.4 | 8299.6 | 9280.6 | 8183.4 | 8768.5 | 8079.6 | 7184.2 | 8867.8 | 8593.6 | 7959.6 | 9277 | 8988.8 | 8224.4 | 8110.9 | 9040.6 | 8034.7 | 8388.8 | 9077 | 8022.5 | 9236.3 | 8005.2 | 8943.7 | 8209.5 | 9053.8 | 7777.9 | 9111.1 | 8196.1 | 8984.5 | 8151.3 | 9054.9 | 8307.5 | 8097 | 8943.6 | 8185.9 | 8032.7 | 9025.5 | 9192 | 8981 | 8185.9 | 9113 | 8137 | 8750.6 | 8239.5 | 8707 | 7608.4 | 8875.7 | 8010.8 | 8198.4 | 8175.1 | 8136.2 | 7002.4 | 8060.5 | 7155.6 | 8085 | 8077.5 | 9563 | 8257.4 | 9617.9 | 8453 | 9504.9 | 8308 | 8464.5 | 8215.1 | 9273.4 | 9639.3 | 9501.1 | 9425.2 | 9514.4 | 9538.5 | 8541.8 | 9519.2 | 9563 | 9604.1 | 9668.4 | 9638 | 9649.5 | 8567 | 9600.2 | 8589.8 | 28.038 | 27.6068 | 28.2204 | 27.9873 | 28.181 | 27.8969 | 0 | 40.8118 | 0 | 0 | 40.6085 | 40.13 | 2.203 | 1.2299 | 0.52515 | 0.21047 | 2.1778 | 1.5653 | 5.5933 | 5.6867 | 5.7367 | 3.5333 | 5.735 | 5.75 | 4.1194 | 4.1528 | 4.1674 | 4.0943 | 4.1768 | 4.1935 | 0.95993 | 1.0451 | 0.94451 | 1.1956 | 1.2282 | 0.99026 | 5.1854 | 5.1512 | 5.1178 | 5.144 | 5.1092 | 5.1479 | 0.21229 | 0.24061 | 0.20879 | 0.1903 | 0.21306 | 0.21427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 786750 | 1443 | 773503 | 1480 | 215207.55 | 614.733 | 4.1194 | 4.1528 | 4.1674 | 4.0943 | 4.1768 | 4.1935 | 5.1854 | 5.1512 | 5.1178 | 5.144 | 5.1092 | 5.1479 | 687000 | 2000 | 690000 | 1000 | 1373000 | 5000 | 1374000 | 1368000 | 10.6667 | 4.1507 | 1.0606 | 5.1426 | 0.21322 | 25.55% | 4.146% | 27.9884 | 40.5168 | 1.3186 | 5.3392 | 1380449.1 | 1372600 | 1684606.4036 | 81.48% | 24 | 7540
2024-11-17 | 2025 | 2024 | Year_3 | Year_3 | 2024-11-01 | 30 | 335090.89 | 7:17 | 17:56 | 9069.9 | 9524.6 | 9521.2 | 9481.9 | 9557.2 | 9623.6 | 9563.9 | 9953.7 | 9423.7 | 9382.8 | 9328.7 | 9500.8 | 9416.7 | 9421.6 | 9450.2 | 9512.8 | 9401.5 | 9487.6 | 9518 | 9560.3 | 9501.7 | 9487.7 | 9285.8 | 9406.9 | 9168.7 | 8055.5 | 9174.8 | 9175.2 | 9419.3 | 9304.4 | 9259.5 | 9437.7 | 9428.4 | 9509.9 | 9524.3 | 9442.1 | 9584.5 | 9451.9 | 9488.8 | 9338.4 | 10450.3 | 9257.2 | 10314.3 | 9163.8 | 9655.2 | 10884.1 | 9047.7 | 10441.4 | 9368.3 | 9491.5 | 9509.8 | 8870.2 | 9848.5 | 9347.6 | 9683.3 | 9391.2 | 8525.8 | 9932.8 | 8654.3 | 9798.8 | 9683.2 | 8651.7 | 9479.8 | 9012.4 | 9094.7 | 8507.5 | 9017.9 | 9557 | 9761.4 | 8758.9 | 9565 | 8428.3 | 9274.1 | 9017.4 | 8505.7 | 9622.1 | 8406.7 | 9648 | 8459.7 | 9551.8 | 8983.8 | 9732.8 | 9091 | 10114.1 | 8946.3 | 9587.2 | 8824.4 | 7851.7 | 9727.9 | 9388.6 | 8693.2 | 10122.2 | 9775.6 | 8926.4 | 8789 | 9861.7 | 8765.8 | 9153.6 | 9916.3 | 8758.1 | 10084.4 | 8743.7 | 9772.6 | 8974.5 | 9892.1 | 8508.6 | 9962.4 | 8959 | 9813.6 | 8907 | 9894.9 | 9087.4 | 8840.7 | 9768 | 8943.2 | 8761.7 | 9854.1 | 10027.5 | 9800.6 | 8926.7 | 9940.9 | 8869.8 | 9551.2 | 8995 | 9512.4 | 8307.1 | 9676.3 | 8741.7 | 8967.6 | 8968.2 | 8888 | 7662.1 | 8748.3 | 7768 | 8743.1 | 8773 | 10380.1 | 8954.9 | 10430 | 9172.7 | 10324.1 | 9030.7 | 9184.7 | 8947.4 | 10048.2 | 10445.3 | 10280.9 | 10212.2 | 10319.2 | 10349.5 | 9258.5 | 10316.3 | 10384.1 | 10431.7 | 10472.4 | 10419.4 | 10442.8 | 9275 | 10416.4 | 9313.3 | 26.65 | 26.07 | 26.47 | 26.37 | 26.23 | 25.93 | 0 | 37.88 | 0 | 0 | 38.1 | 37 | 2.56 | 2.44 | 0.32 | 0.14 | 2.56 | 1.59 | 4.63 | 4.99 | 4.08 | 2.82 | 4.63 | 4.38 | 4.19 | 4.25 | 4.23 | 4.15 | 4.24 | 4.24 | 0.98 | 1.08 | 0.96 | 1.22 | 1.26 | 1.02 | 5.3 | 5.24 | 5.25 | 5.24 | 5.21 | 5.22 | 0.22 | 0.25 | 0.22 | 0.2 | 0.23 | 0.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 787499 | 1444 | 774255 | 1482 | 216702.3 | 619.933 | 4.19 | 4.25 | 4.23 | 4.15 | 4.24 | 4.24 | 5.3 | 5.24 | 5.25 | 5.24 | 5.21 | 5.22 | 749000 | 1000 | 752000 | 2000 | 1494750 | 5200 | 1498000 | 1489550 | 10.65 | 4.2167 | 1.0867 | 5.2433 | 0.225 | 25.77% | 4.291% | 26.2867 | 37.66 | 1.6017 | 4.255 | 1503240.5 | 1477500 | 1706496.1635 | 86.58% | 28 | 0
2024-11-18 | 2025 | 2024 | Year_3 | Year_3 | 2024-11-01 | 30 | 335090.89 | 7:16 | 17:55 | 9702 | 10198.8 | 10170.3 | 10115.2 | 10203.4 | 10298.6 | 10250.7 | 10719.8 | 10113.4 | 10010.9 | 9989.2 | 10186.2 | 10082.9 | 10086 | 10126.6 | 10200 | 10092 | 10187.8 | 10206.5 | 10250.4 | 10185.4 | 10174.8 | 9945.3 | 10084.5 | 9830.8 | 8624.2 | 9820.7 | 9835.5 | 10103.8 | 9964.2 | 9922.9 | 10121.9 | 10139.4 | 10211.8 | 10212.2 | 10150.7 | 10312.8 | 10169.2 | 10209.9 | 10025.7 | 11199.7 | 9895.6 | 11050 | 9802.7 | 10328.5 | 11664.6 | 9707.5 | 11178.1 | 10000.2 | 10131.1 | 10164.4 | 9476 | 10532.4 | 9995.1 | 10319.4 | 9996.7 | 9082.5 | 10609.9 | 9252.1 | 10477.9 | 10351.1 | 9244.9 | 10121.6 | 9630.4 | 9738.8 | 9091.1 | 9642 | 10227.7 | 10430.6 | 9364.9 | 10219.7 | 9000.5 | 9901.5 | 9614.3 | 9077.8 | 10253.1 | 8964.9 | 10288.9 | 9029.8 | 10198.6 | 9617.9 | 10413.3 | 9705.1 | 10832.6 | 9564.3 | 10237 | 9445.6 | 8394.1 | 10415.1 | 10023.4 | 9311 | 10846.9 | 10461.5 | 9560.9 | 9421.3 | 10586.7 | 9390.3 | 9791.1 | 10599.8 | 9357.3 | 10782.3 | 9344.6 | 10447.9 | 9590 | 10590.3 | 9097.7 | 10672.9 | 9587.6 | 10509.7 | 9551.3 | 10606 | 9721.2 | 9444.9 | 10423.2 | 9557.9 | 9362.6 | 10539 | 10710.9 | 10483.9 | 9522.1 | 10612.8 | 9471.6 | 10217.7 | 9624.3 | 10173.8 | 8860.3 | 10326.6 | 9321.4 | 9577.3 | 9592.3 | 9459.3 | 8175.1 | 9374.5 | 8315.1 | 9327.8 | 9348.9 | 11080.4 | 9560.7 | 11123.1 | 9778.7 | 10999.6 | 9610.2 | 9793.5 | 9522.9 | 10728.2 | 11139.1 | 10978.2 | 10897.4 | 11017.3 | 11051.7 | 9868.8 | 10995.8 | 11097.7 | 11160.6 | 11201.3 | 11149.9 | 11172.4 | 9913.6 | 11104.6 | 9956.2 | 25.537 | 24.983 | 25.3187 | 25.3072 | 25.1462 | 24.8571 | 0 | 38.5954 | 0 | 0 | 38.9 | 37.7 | 2.1881 | 1.0725 | 0.17499 | 0.11998 | 2.1263 | 1.5454 | 4.7467 | 5.0283 | 3.88 | 2.8417 | 4.1633 | 4.745 | 4.4317 | 4.4621 | 4.459 | 4.3973 | 4.4562 | 4.4441 | 1.0283 | 1.1362 | 1.0156 | 1.2858 | 1.3195 | 1.0603 | 5.7117 | 5.6458 | 5.6191 | 5.6572 | 5.5616 | 5.5635 | 0.2241 | 0.25481 | 0.21963 | 0.20076 | 0.22261 | 0.2247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 788299 | 1446 | 775059 | 1484 | 218300.2 | 625.067 | 4.4317 | 4.4621 | 4.459 | 4.3973 | 4.4562 | 4.4441 | 5.7117 | 5.6458 | 5.6191 | 5.6572 | 5.5616 | 5.5635 | 800000 | 2000 | 804000 | 2000 | 1597900 | 5134 | 1600000 | 1592766 | 10.65 | 4.4417 | 1.141 | 5.6265 | 0.22443 | 25.69% | 3.989% | 25.1915 | 38.3985 | 1.2045 | 4.2342 | 1607694.9 | 1581800 | 1829144.8 | 86.48% | 28 | 0
2024-11-19 | 2025 | 2024 | Year_3 | Year_3 | 2024-11-01 | 30 | 335090.89 | 7:15 | 17:55 | 9712.4 | 10197.9 | 10140.4 | 10087 | 10175.3 | 10279.7 | 10217.5 | 10702.2 | 10103.9 | 9984.7 | 9959.9 | 10164 | 10068.8 | 10059.9 | 10147.9 | 10196 | 10104.3 | 10205.7 | 10221.1 | 10262.1 | 10205.9 | 10195.3 | 9962.4 | 10104 | 9819.8 | 8616.7 | 9831.1 | 9837.4 | 10124.3 | 9992.5 | 9946.4 | 10128.5 | 10166.8 | 10213.6 | 10210.6 | 10153.2 | 10330.3 | 10186.8 | 10230.2 | 10037.4 | 11252 | 9936.1 | 11096.6 | 9844.8 | 10356 | 11695.3 | 9740.2 | 11228.8 | 9967.1 | 10099.9 | 10131.5 | 9451.6 | 10508.5 | 9966.8 | 10305.3 | 9976.1 | 9078.3 | 10606.7 | 9220.4 | 10452.3 | 10325.3 | 9214.9 | 10126.7 | 9632.8 | 9735.7 | 9109.9 | 9637.7 | 10249.2 | 10439.3 | 9369.8 | 10231.1 | 9012.9 | 9913.3 | 9625.3 | 9096.5 | 10265.7 | 8975.7 | 10318 | 9037.7 | 10211 | 9650 | 10440.5 | 9731.4 | 10867.4 | 9588.1 | 10258.8 | 9470.1 | 8416.9 | 10417.1 | 10055.8 | 9334 | 10870.3 | 10496.4 | 9591.5 | 9450.3 | 10612.1 | 9403.1 | 9819.7 | 10625.5 | 9392.5 | 10818.4 | 9375.3 | 10484.3 | 9619.8 | 10626.6 | 9125.4 | 10707.3 | 9624.2 | 10545.8 | 9584.6 | 10639.6 | 9761.5 | 9481.3 | 10464.7 | 9601.3 | 9405.2 | 10584.9 | 10757.8 | 10539.4 | 9565.8 | 10666.1 | 9519.1 | 10261 | 9669.3 | 10221.2 | 8901.5 | 10370.6 | 9359.5 | 9617.5 | 9615 | 9520.1 | 8204.8 | 9418.5 | 8357.6 | 9368.6 | 9403.1 | 11072.7 | 9542.1 | 11190.2 | 9837 | 11049.3 | 9657.7 | 9839.3 | 9582.2 | 10808 | 11224.1 | 11055.8 | 10980.7 | 11098.1 | 11121.5 | 9936.2 | 11077.5 | 11160.2 | 11237.2 | 11279.5 | 11224.9 | 11248.8 | 9982.8 | 11173.3 | 10026.5 | 25.8182 | 25.3437 | 25.7106 | 25.7776 | 25.5973 | 25.2951 | 0 | 39.1908 | 0 | 0 | 39.6 | 38.5 | 1.991 | 0.65579 | 0.054535 | 0.05919 | 1.9168 | 1.3166 | 4.2683 | 4.1367 | 2.62 | 2.2517 | 4.03 | 4.3133 | 4.409 | 4.4514 | 4.4535 | 4.3597 | 4.46 | 4.457 | 1.0338 | 1.1257 | 1.0229 | 1.2958 | 1.3145 | 1.0526 | 5.698 | 5.65 | 5.6408 | 5.6772 | 5.5896 | 5.5952 | 0.22183 | 0.25195 | 0.21759 | 0.19782 | 0.22052 | 0.22358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 789100 | 1448 | 775865 | 1486 | 219902.017 | 630.2 | 4.409 | 4.4514 | 4.4535 | 4.3597 | 4.46 | 4.457 | 5.698 | 5.65 | 5.6408 | 5.6772 | 5.5896 | 5.5952 | 801000 | 2000 | 806000 | 2000 | 1601817 | 5133 | 1603000 | 1596684 | 10.6667 | 4.4318 | 1.1409 | 5.6418 | 0.22221 | 25.74% | 3.939% | 25.5904 | 39.0969 | 0.99899 | 3.6033 | 1611410.5 | 1588067 | 1835753.7807 | 86.51% | 30 | 0
2024-11-20 | 2025 | 2024 | Year_3 | Year_3 | 2024-11-01 | 30 | 335090.89 | 7:15 | 17:56 | 9725 | 10208 | 10130 | 10089 | 10154 | 10295 | 10234 | 10686 | 10100 | 9987 | 9974 | 10162 | 10077 | 10073 | 10130 | 10176 | 10077 | 10170 | 10198 | 10246 | 10171 | 10167 | 9920 | 10062 | 9803 | 8604 | 9814 | 9814 | 10107 | 9985 | 9897 | 10093 | 10135 | 10190 | 10190 | 10127 | 10292 | 10142 | 10192 | 10002 | 11211 | 9908 | 11064 | 9815 | 10345 | 11677 | 9711 | 11181 | 9977 | 10118 | 10140 | 9463 | 10492 | 9948 | 10317 | 9978 | 9116 | 10634 | 9249 | 10499 | 10363 | 9233 | 10174 | 9675 | 9757 | 9129 | 9653 | 10279 | 10436 | 9407 | 10260 | 9049 | 9930 | 9657 | 9119 | 10296 | 9002 | 10339 | 9075 | 10243 | 9673 | 10469 | 9751 | 10894 | 9606 | 10278 | 9496 | 8435 | 10407 | 10063 | 9338 | 10870 | 10524 | 9623 | 9486 | 10612 | 9411 | 9841 | 10649 | 9409 | 10853 | 9391 | 10499 | 9647 | 10647 | 9145 | 10724 | 9650 | 10553 | 9600 | 10646 | 9786 | 9500 | 10481 | 9621 | 9419 | 10600 | 10783 | 10557 | 9588 | 10690 | 9534 | 10282 | 9690 | 10229 | 8912 | 10392 | 9379 | 9651 | 9649 | 9550 | 8233 | 9431 | 8366 | 9383 | 9421 | 11161 | 9624 | 11214 | 9859 | 11073 | 9674 | 9859 | 9608 | 10813 | 11224 | 11067 | 10991 | 11107 | 11137 | 9946 | 11082 | 11174 | 11255 | 11281 | 11229 | 11256 | 9989 | 11186 | 10041 | 25.23 | 24.95 | 25.48 | 25.34 | 25.23 | 24.88 | 0 | 39.42 | 0 | 0 | 39.8 | 38.7 | 1.91 | 0.59 | 0.16 | 0.09 | 1.72 | 1.34 | 3.95 | 4.3 | 3.7 | 1.82 | 3.76 | 4.46 | 4.4 | 4.43 | 4.44 | 4.13 | 4.47 | 4.45 | 1.04 | 1.13 | 1.03 | 1.3 | 1.32 | 1.06 | 5.7 | 5.63 | 5.62 | 5.68 | 5.6 | 5.6 | 0.22 | 0.25 | 0.22 | 0.2 | 0.22 | 0.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 789901 | 1450 | 776674 | 1487 | 221505 | 635.3 | 4.4 | 4.43 | 4.44 | 4.13 | 4.47 | 4.45 | 5.7 | 5.63 | 5.62 | 5.68 | 5.6 | 5.6 | 801000 | 2000 | 809000 | 1000 | 1602983 | 5100 | 1607000 | 1597883 | 10.6833 | 4.3867 | 1.1467 | 5.6383 | 0.22167 | 26.14% | 3.931% | 25.185 | 39.3067 | 0.96833 | 3.665 | 1612684 | 1587333 | 1830392.8 | 86.72% | 28 | 0
2024-11-21 | 2025 | 2024 | Year_3 | Year_3 | 2024-11-01 | 30 | 335090.89 | 7:17 | 17:57 | 9738.2 | 10204.9 | 10134.1 | 10101.9 | 10156.1 | 10307.2 | 10215.5 | 10659.5 | 10106.6 | 10051.1 | 9976.4 | 10151.9 | 10101.2 | 10083.6 | 10139.2 | 10200.5 | 10102.4 | 10199.1 | 10225.6 | 10265.9 | 10195.6 | 10191 | 9961.1 | 10095.6 | 9832.2 | 8618.5 | 9829.9 | 9834.1 | 10130 | 10035.1 | 9939.5 | 10131.5 | 10167.5 | 10224.8 | 10203.7 | 10164 | 10339 | 10176.1 | 10207.5 | 10007.7 | 11236.1 | 9932.8 | 11081.8 | 9850.9 | 10356.9 | 11682.1 | 9728.3 | 11209.7 | 9974 | 10119.1 | 10145.1 | 9471 | 10509.3 | 9987.3 | 10350.3 | 10057.8 | 9132.8 | 10602.9 | 9254.6 | 10522.3 | 10382.7 | 9245.4 | 10147.2 | 9652.3 | 9793.9 | 9144.3 | 9680.3 | 10289.4 | 10462.7 | 9417.5 | 10270.7 | 9056 | 9917.4 | 9701 | 9112.1 | 10308 | 9015.5 | 10322.2 | 9067.6 | 10229.8 | 9672.7 | 10471.7 | 9750.9 | 10898.6 | 9612 | 10281.6 | 9510.8 | 8438.1 | 10453.7 | 10068.1 | 9365.3 | 10908 | 10530.6 | 9629 | 9490.1 | 10641.7 | 9396.7 | 9841.9 | 10643.4 | 9402 | 10842.9 | 9376.7 | 10485.3 | 9636.9 | 10631 | 9133.6 | 10709 | 9631.2 | 10537.4 | 9566.1 | 10636.1 | 9765.4 | 9495.1 | 10481.6 | 9612.1 | 9420.5 | 10587.5 | 10758.1 | 10542 | 9555.5 | 10677.8 | 9505.5 | 10259.5 | 9661.4 | 10224.7 | 8890.4 | 10359.4 | 9344.3 | 9610.6 | 9605.5 | 9495.1 | 8195.1 | 9397 | 8316.9 | 9397.5 | 9429.7 | 11173.6 | 9634.6 | 11222.2 | 9865.8 | 11060.3 | 9653.5 | 9845.3 | 9580.8 | 10809.5 | 11218.9 | 11062.8 | 10992.3 | 11118.9 | 11149.7 | 9951.3 | 11084.8 | 11153.3 | 11246.6 | 11257.6 | 11214.7 | 11240.2 | 9979.7 | 11180.5 | 10035.1 | 25.636 | 25.2894 | 25.962 | 25.6054 | 25.5039 | 25.3645 | 0 | 39.9182 | 0 | 0 | 40.4 | 39.3 | 1.78 | 0.41916 | 0.098813 | 0.064547 | 1.642 | 1.3627 | 3.7883 | 4.1317 | 3.32 | 1.6767 | 3.9033 | 6.3183 | 4.3936 | 4.4291 | 4.4242 | 3.9022 | 4.4528 | 4.45 | 1.0337 | 1.1305 | 1.0219 | 1.3069 | 1.3224 | 1.0639 | 5.7097 | 5.6534 | 5.6295 | 5.6936 | 5.598 | 5.6176 | 0.21497 | 0.24637 | 0.21283 | 0.19486 | 0.21735 | 0.22057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 790703 | 1452 | 777481 | 1489 | 223108.417 | 640.2 | 4.3936 | 4.4291 | 4.4242 | 3.9022 | 4.4528 | 4.45 | 5.7097 | 5.6534 | 5.6295 | 5.6936 | 5.598 | 5.6176 | 802000 | 2000 | 807000 | 2000 | 1603417 | 4900 | 1605000 | 1598517 | 10.6667 | 4.342 | 1.1466 | 5.6503 | 0.21783 | 26.41% | 3.855% | 25.5602 | 39.8727 | 0.89453 | 3.8564 | 1613339.7 | 1587266 | 1832522.4424 | 86.62% | 22 | 0
2024-11-22 | 2025 | 2024 | Year_3 | Year_3 | 2024-11-01 | 30 | 335090.89 | 7:17 | 17:55 | 9601 | 10083 | 10005 | 9944 | 10045 | 10149 | 10073 | 10497 | 9952 | 9940 | 9836 | 10025 | 9950 | 9946 | 9968 | 10045 | 9937 | 10042 | 10070 | 10115 | 10033 | 10035 | 9791 | 9934 | 9682 | 8493 | 9694 | 9693 | 9967 | 9856 | 9759 | 9957 | 9988 | 10044 | 10041 | 9991 | 10150 | 9987 | 10017 | 9837 | 10994 | 9708 | 10843 | 9630 | 10123 | 11426 | 9517 | 10974 | 9828 | 9966 | 10001 | 9339 | 10361 | 9847 | 10208 | 9931 | 8996 | 10449 | 9102 | 10355 | 10210 | 9088 | 10026 | 9511 | 9592 | 9005 | 9508 | 10131 | 10285 | 9273 | 10108 | 8917 | 9730 | 9566 | 8941 | 10129 | 8859 | 10131 | 8908 | 10053 | 9515 | 10300 | 9597 | 10720 | 9455 | 10116 | 9343 | 8297 | 10296 | 9911 | 9203 | 10717 | 10332 | 9438 | 9303 | 10483 | 9258 | 9678 | 10468 | 9244 | 10650 | 9218 | 10300 | 9467 | 10443 | 8972 | 10518 | 9466 | 10339 | 9378 | 10427 | 9589 | 9337 | 10323 | 9448 | 9271 | 10405 | 10572 | 10357 | 9401 | 10493 | 9340 | 10075 | 9492 | 10048 | 8734 | 10178 | 9184 | 9454 | 9456 | 9335 | 8061 | 9253 | 8186 | 9296 | 9314 | 10981 | 9474 | 11031 | 9701 | 10875 | 9482 | 9677 | 9449 | 10635 | 11038 | 10883 | 10810 | 10926 | 10960 | 9781 | 10903 | 10990 | 11081 | 11111 | 11059 | 11074 | 9832 | 10997 | 9873 | 25.66 | 25.48 | 26.03 | 25.73 | 25.61 | 25.57 | 0 | 38.9 | 0 | 0 | 40.1 | 39.1 | 2.22 | 0.76 | 0.23 | 0.08 | 2.21 | 1.57 | 4.5 | 4.72 | 4.09 | 1.91 | 4.45 | 4.22 | 4.34 | 4.37 | 4.37 | 4.33 | 4.4 | 4.39 | 1.02 | 1.13 | 1.01 | 1.29 | 1.31 | 1.06 | 5.64 | 5.58 | 5.54 | 5.61 | 5.52 | 5.56 | 0.22 | 0.25 | 0.21 | 0.19 | 0.22 | 0.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 791492 | 1454 | 778275 | 1490 | 224686 | 645.1 | 4.34 | 4.37 | 4.37 | 4.33 | 4.4 | 4.39 | 5.64 | 5.58 | 5.54 | 5.61 | 5.52 | 5.56 | 789000 | 2000 | 794000 | 1000 | 1577583 | 4900 | 1580000 | 1572683 | 10.6333 | 4.3667 | 1.1367 | 5.575 | 0.21833 | 26.03% | 3.916% | 25.68 | 39.3667 | 1.1783 | 3.9817 | 1586818 | 1562000 | 1808813.1 | 86.35% | 26 | 0
2024-11-23 | 2025 | 2024 | Year_3 | Year_3 | 2024-11-01 | 30 | 335090.89 | 7:18 | 17:52 | 9205 | 9668 | 9577 | 9530 | 9616 | 9698 | 9682 | 10035 | 9523 | 9494 | 9416 | 9604 | 9516 | 9519 | 9524 | 9609 | 9497 | 9608 | 9631 | 9676 | 9596 | 9599 | 9386 | 9516 | 9263 | 8121 | 9288 | 9277 | 9551 | 9448 | 9377 | 9552 | 9589 | 9634 | 9613 | 9571 | 9728 | 9582 | 9614 | 9464 | 10576 | 9344 | 10435 | 9274 | 9776 | 11031 | 9169 | 10547 | 9419 | 9554 | 9577 | 8965 | 9931 | 9416 | 9784 | 9501 | 8626 | 10043 | 8743 | 9953 | 9811 | 8733 | 9611 | 9107 | 9206 | 8641 | 9111 | 9723 | 9884 | 8894 | 9700 | 8557 | 9364 | 9195 | 8593 | 9730 | 8511 | 9728 | 8541 | 9643 | 9116 | 9867 | 9196 | 10274 | 9057 | 9696 | 8946 | 7951 | 9856 | 9504 | 8819 | 10262 | 9907 | 9059 | 8935 | 10045 | 8888 | 9288 | 10050 | 8866 | 10227 | 8850 | 9894 | 9092 | 10025 | 8613 | 10093 | 9074 | 9936 | 9026 | 10022 | 9194 | 8947 | 9889 | 9056 | 8888 | 9968 | 10143 | 9927 | 9020 | 10061 | 8957 | 9656 | 9096 | 9629 | 8387 | 9773 | 8815 | 9060 | 9050 | 8956 | 7732 | 8836 | 7805 | 8890 | 8901 | 10534 | 9077 | 10568 | 9285 | 10416 | 9088 | 9292 | 9036 | 10204 | 10591 | 10453 | 10381 | 10486 | 10517 | 9375 | 10457 | 10533 | 10617 | 10640 | 10594 | 10610 | 9422 | 10545 | 9472 | 25.7 | 25.42 | 26.05 | 25.76 | 25.42 | 25.55 | 0 | 39.06 | 0 | 0 | 39.27 | 38.7 | 1.96 | 0.51 | 0.24 | 0.1 | 1.87 | 1.44 | 4.42 | 4.36 | 2.84 | 2.44 | 4.48 | 4.06 | 4.16 | 4.19 | 4.21 | 4.14 | 4.22 | 4.22 | 0.99 | 1.09 | 0.98 | 1.25 | 1.27 | 1.03 | 5.38 | 5.32 | 5.31 | 5.35 | 5.28 | 5.32 | 0.21 | 0.24 | 0.21 | 0.2 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 792249 | 1456 | 779037 | 1492 | 226199.6 | 650.3 | 4.16 | 4.19 | 4.21 | 4.14 | 4.22 | 4.22 | 5.38 | 5.32 | 5.31 | 5.35 | 5.28 | 5.32 | 757000 | 2000 | 762000 | 2000 | 1513600 | 5200 | 1515000 | 1508400 | 10.5667 | 4.19 | 1.1017 | 5.3267 | 0.21333 | 26.29% | 4.005% | 25.65 | 39.01 | 1.02 | 3.7667 | 1521607 | 1500000 | 1734553.8 | 86.48% | 27 | 0
2024-11-24 | 2025 | 2024 | Year_3 | Year_3 | 2024-11-01 | 30 | 335090.89 | 7:16 | 17:53 | 8951.4 | 9388.5 | 9310.6 | 9260.4 | 9337.9 | 9433.9 | 9408 | 9805.9 | 9296.2 | 9247.8 | 9166 | 9356.5 | 9289.4 | 9268.6 | 9276 | 9380.4 | 9252.1 | 9366.2 | 9384.4 | 9423.5 | 9345.7 | 9348.2 | 9139.2 | 9261.4 | 9034.6 | 7916 | 9057 | 9046.5 | 9307 | 9197.3 | 9133.1 | 9311.8 | 9330.3 | 9373 | 9361.8 | 9314.2 | 9466.9 | 9325.2 | 9347.9 | 9211.4 | 10310 | 9117 | 10177.5 | 9045.8 | 9549.4 | 10750.8 | 8958.6 | 10296.1 | 9160.6 | 9287.1 | 9325.9 | 8723.4 | 9674.8 | 9169.3 | 9512.4 | 9245.6 | 8372.3 | 9746.6 | 8490.5 | 9643.1 | 9523.6 | 8481.6 | 9322.4 | 8827.1 | 8943.2 | 8381.7 | 8835 | 9439.7 | 9592.8 | 8631.4 | 9414.8 | 8308.8 | 9086.7 | 8933.8 | 8342 | 9442 | 8257.3 | 9447.9 | 8313.5 | 9379.4 | 8856.8 | 9581.2 | 8932.6 | 9977.8 | 8800.4 | 9412.3 | 8694.3 | 7727.7 | 9559.8 | 9250.4 | 8582 | 9991.1 | 9671.5 | 8840.4 | 8718.5 | 9758.6 | 8625.8 | 9019.3 | 9757.5 | 8615.6 | 9936.7 | 8598.1 | 9622.6 | 8838.2 | 9747.3 | 8377.4 | 9815.5 | 8837.5 | 9666.5 | 8768.7 | 9756.5 | 8966.4 | 8690.2 | 9612.8 | 8799.9 | 8643.5 | 9703.4 | 9878.4 | 9671.6 | 8788.7 | 9795.1 | 8727.2 | 9418.5 | 8862.9 | 9383.5 | 8156.5 | 9511.5 | 8587.6 | 8826.3 | 8812.1 | 8711.6 | 7529.2 | 8595.5 | 7574.1 | 8606.6 | 8621.9 | 10193.7 | 8799.9 | 10243.8 | 9014.5 | 10114.7 | 8840.7 | 9022.5 | 8763.9 | 9863.8 | 10223 | 10109.8 | 10039.8 | 10144.9 | 10176 | 9097.1 | 10113.8 | 10190.3 | 10269.1 | 10268.5 | 10226.6 | 10242.4 | 9104.4 | 10200.8 | 9165.2 | 24.96 | 24.78 | 25.53 | 25.21 | 25.12 | 24.7 | 0 | 38.12 | 0 | 0 | 37.91 | 37.4 | 1.53 | 0.19 | 0.01 | 0.04 | 1.35 | 0.94 | 3.41 | 3.11 | 1.23 | 1.87 | 3.38 | 3.16 | 4.03 | 4.05 | 4.08 | 4.01 | 4.08 | 4.06 | 0.96 | 1.06 | 0.95 | 1.2 | 1.22 | 0.98 | 5.19 | 5.15 | 5.15 | 5.16 | 5.09 | 5.11 | 0.21 | 0.24 | 0.2 | 0.2 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 792985 | 1458 | 779777 | 1494 | 227670.884 | 655.333 | 4.03 | 4.05 | 4.08 | 4.01 | 4.08 | 4.06 | 5.19 | 5.15 | 5.15 | 5.16 | 5.09 | 5.11 | 736000 | 2000 | 740000 | 2000 | 1471284 | 5033 | 1472000 | 1466251 | 10.6167 | 4.0517 | 1.0617 | 5.1417 | 0.21167 | 26.2% | 4.117% | 25.05 | 37.81 | 0.67667 | 2.6933 | 1479136.5 | 1508552 | 1681676.4956 | 89.71% | 22 | 0
2024-11-25 | 2025 | 2024 | Year_3 | Year_3 | 2024-11-01 | 30 | 335090.89 | 7:20 | 17:50 | 8613.9 | 9031.6 | 8988.7 | 8949.9 | 9019 | 9082 | 9042.1 | 9456.5 | 8963.7 | 8914.2 | 8838.2 | 9027.2 | 8952.6 | 8929.2 | 8965.3 | 9048.7 | 8941.9 | 9027 | 9043.8 | 9074.9 | 9012.5 | 9012.4 | 8808.1 | 8933.5 | 8740.9 | 7656.8 | 8743.8 | 8748.9 | 8989.8 | 8855.1 | 8802.5 | 8987.2 | 8974 | 9031.4 | 9028.1 | 8976.9 | 9115 | 8978.5 | 9017.5 | 8881.5 | 9899.1 | 8748.5 | 9780 | 8667.2 | 9168.5 | 10361.8 | 8612.4 | 9891.2 | 8844.6 | 8963.5 | 8989.9 | 8395.8 | 9313.2 | 8830.6 | 9181.3 | 8941.9 | 8084.2 | 9400.3 | 8200.5 | 9302.1 | 9174.1 | 8192 | 8983.5 | 8525.3 | 8636.9 | 8072.6 | 8505.7 | 9081.2 | 9235.6 | 8311.3 | 9068.3 | 8028.5 | 8712.2 | 8628.2 | 8017.9 | 9128.4 | 7987.7 | 9097.5 | 8016.6 | 9057.3 | 8528.5 | 9201 | 8620.8 | 9613.5 | 8484.8 | 9086.1 | 8368.9 | 7452.5 | 9257.9 | 8919.5 | 8285.4 | 9651.8 | 9314.2 | 8501.7 | 8379 | 9423.7 | 8316 | 8703.5 | 9408.8 | 8308.6 | 9581.4 | 8290.9 | 9275.4 | 8517.7 | 9398.9 | 8072 | 9464.1 | 8514.1 | 9311.1 | 8397.1 | 9404.7 | 8626.6 | 8371.8 | 9250.3 | 8451 | 8319.3 | 9347.8 | 9496.4 | 9304.4 | 8434.7 | 9400 | 8377.2 | 9048.1 | 8430.4 | 9037 | 7843.3 | 9142.3 | 8249.4 | 8497.4 | 8491.7 | 8362 | 7237.2 | 8308.3 | 7339.7 | 8358.5 | 8369.3 | 9844.3 | 8498.8 | 9883.6 | 8700 | 9785 | 8545 | 8718.6 | 8485.1 | 9529.6 | 9877.2 | 9756 | 9689.1 | 9792.2 | 9816.4 | 8768.9 | 9762 | 9846.9 | 9932.2 | 9932.4 | 9885.7 | 9895.4 | 8788.7 | 9860.6 | 8847.4 | 25.73 | 25.31 | 25.58 | 25.75 | 25.42 | 25.18 | 0 | 37.81 | 0 | 0 | 38.1 | 37 | 1.98 | 0.8 | 0.09 | 0.07 | 1.93 | 1.2 | 4.05 | 4.14 | 2.63 | 2.64 | 4.17 | 4.01 | 3.91 | 3.93 | 3.96 | 3.88 | 3.95 | 3.94 | 0.92 | 1.03 | 0.91 | 1.16 | 1.18 | 0.96 | 5.01 | 4.96 | 4.96 | 4.96 | 4.91 | 4.94 | 0.21 | 0.23 | 0.2 | 0.19 | 0.2 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 793695 | 1460 | 780490 | 1495 | 229089.351 | 660.467 | 3.91 | 3.93 | 3.96 | 3.88 | 3.95 | 3.94 | 5.01 | 4.96 | 4.96 | 4.96 | 4.91 | 4.94 | 710000 | 2000 | 713000 | 1000 | 1418467 | 5134 | 1420000 | 1413333 | 10.5 | 3.9283 | 1.0267 | 4.9567 | 0.20667 | 26.13% | 4.169% | 25.495 | 37.6367 | 1.0117 | 3.6067 | 1425831 | 1444436.65 | 1617785.9604 | 89.28% | 25 | 0
2024-11-26 | 2025 | 2024 | Year_3 | Year_3 | 2024-11-01 | 30 | 335090.89 | 7:20 | 17:51 | 8858.6 | 9260.9 | 9199.2 | 9174 | 9231.9 | 9314.5 | 9270.3 | 9707.9 | 9196 | 9160.8 | 9073.5 | 9271.8 | 9183.5 | 9166.1 | 9192.5 | 9282.1 | 9177.2 | 9261.5 | 9279.8 | 9308.9 | 9256.9 | 9254.8 | 9052 | 9171.7 | 8975.6 | 7873.9 | 8987.8 | 8984.6 | 9229.4 | 9098.3 | 9051.7 | 9241 | 9245.2 | 9290.3 | 9293.2 | 9246.2 | 9393 | 9249.4 | 9284.2 | 9137.2 | 10179.7 | 8991.9 | 10050 | 8920.9 | 9413.2 | 10613.8 | 8832.5 | 10164.7 | 9094.3 | 9215.5 | 9254.5 | 8657.8 | 9591.9 | 9073.6 | 9452.8 | 9186.2 | 8342.4 | 9694.7 | 8430 | 9571.6 | 9467.5 | 8440 | 9280.1 | 8799.9 | 8912.9 | 8342.3 | 8798.7 | 9375.5 | 9551.9 | 8582.5 | 9364.8 | 8278.5 | 9041.8 | 8914 | 8291.8 | 9418.6 | 8228.2 | 9362.9 | 8245.6 | 9317.9 | 8360.1 | 8944.7 | 8434.4 | 9436.8 | 8300.2 | 8893.6 | 8199.1 | 7295.6 | 8747.4 | 8431.8 | 7837.9 | 9126.9 | 8798.2 | 8032 | 7921.8 | 8919 | 8456.6 | 8866.3 | 9584.8 | 8463.5 | 9758.5 | 8455.5 | 9459.5 | 8685 | 8624.3 | 7417.6 | 8686 | 7815.8 | 8553.3 | 7764 | 8629.4 | 7926.4 | 8525.4 | 9429.8 | 8637.4 | 8491.4 | 9533.9 | 9699.3 | 9496.3 | 8620.2 | 9611 | 8567.2 | 9248.2 | 8707.7 | 9216.4 | 8014.1 | 9340.5 | 8429.5 | 8660 | 8640.5 | 8560.4 | 7388.4 | 8454.9 | 7488.5 | 8496.2 | 8506.6 | 10004.8 | 8626.2 | 10063.9 | 8847.5 | 9930.2 | 8676.7 | 8850.7 | 8636.5 | 9706.2 | 10067.3 | 9901.3 | 9838.2 | 9951.3 | 9981.8 | 8927.4 | 9940.3 | 9171.8 | 9257.7 | 9276.1 | 9232.2 | 9239.1 | 8206.3 | 9185.5 | 8244.8 | 26.3408 | 26.1191 | 26.7933 | 26.3883 | 26.4119 | 26.3932 | 0 | 39.0113 | 0 | 0 | 39.6 | 38.6 | 2.4721 | 1.4903 | 0.71203 | 0.24451 | 2.2546 | 1.9018 | 7.015 | 5.82 | 6.31 | 4.3683 | 5.6933 | 5.1517 | 3.992 | 4.0291 | 4.038 | 4.0008 | 4.0513 | 4.0324 | 0.95166 | 1.0532 | 0.9384 | 1.2022 | 1.2002 | 0.97385 | 5.1519 | 5.1281 | 5.0895 | 5.1486 | 5.074 | 5.0747 | 0.20672 | 0.23048 | 0.19786 | 0.19271 | 0.20464 | 0.20541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 794425 | 1462 | 781196 | 1497 | 230520.018 | 665.6 | 3.992 | 4.0291 | 4.038 | 4.0008 | 4.0513 | 4.0324 | 5.1519 | 5.1281 | 5.0895 | 5.1486 | 5.074 | 5.0747 | 730000 | 2000 | 706000 | 2000 | 1430667 | 5133 | 1432000 | 1425534 | 10.5167 | 4.0239 | 1.0533 | 5.1111 | 0.2063 | 26.17% | 4.036% | 26.4078 | 39.0704 | 1.5125 | 5.7264 | 1437988.4 | 1415733 | 1666040.6688 | 84.98% | 25 | 534
2024-11-27 | 2025 | 2024 | Year_3 | Year_3 | 2024-11-01 | 30 | 335090.89 | 7:22 | 17:54 | 9367 | 9796.2 | 9744.5 | 9722.2 | 9773.4 | 9863.9 | 9795.5 | 10309.8 | 9754.2 | 9714.7 | 9626.7 | 9822.4 | 9754.3 | 9735.5 | 9733.3 | 9843.2 | 9724.6 | 9825.4 | 9840.3 | 9868.4 | 9801.1 | 9804.5 | 9579.4 | 9718.7 | 9492.2 | 8323.2 | 9516.6 | 9514.1 | 9779.2 | 9663.5 | 9572.8 | 9769.9 | 9733.1 | 9786.1 | 9824.3 | 9759.9 | 9921.3 | 9750.5 | 9804.6 | 9611.6 | 10827.6 | 9546.4 | 10668.1 | 9470.3 | 9983.9 | 11250.7 | 9368.4 | 10797.1 | 9615 | 9744 | 9805.4 | 9147.5 | 10157 | 9615.1 | 9990.9 | 9694.8 | 8815.4 | 10236.6 | 8944.7 | 10150.8 | 10002.3 | 8929.6 | 9792.7 | 9284.8 | 9421.4 | 8812.8 | 9299.7 | 9910.9 | 10071.9 | 9067.9 | 9887.2 | 8745.4 | 9536.9 | 9407.2 | 8753.5 | 9938.4 | 8690.9 | 9896.7 | 8718.7 | 9843.1 | 9268.4 | 9916.9 | 9352.4 | 10463.9 | 9205.4 | 9851.7 | 9104.7 | 8079.2 | 10001.3 | 9654.4 | 8967.1 | 10445.5 | 10077.3 | 9202.3 | 9076.2 | 10195.6 | 8984.5 | 9438.9 | 10191.4 | 9017.1 | 10373 | 9001 | 10063.2 | 9251 | 10199 | 8770.6 | 10262.4 | 9246.5 | 10112.8 | 9188.1 | 10185.6 | 9378.3 | 9086.1 | 10078.3 | 9216.5 | 9058.7 | 10161.1 | 10348.2 | 10126.2 | 9198.1 | 10251.5 | 9137.4 | 9854.1 | 9285.7 | 9806.8 | 8526.8 | 9957.8 | 9000.3 | 9273.3 | 9254.6 | 9145.8 | 7908.6 | 9021.7 | 7988.2 | 9065.4 | 9086.5 | 10730.8 | 9240.6 | 10771.4 | 9475.3 | 10642.6 | 9304.8 | 9494.2 | 9227.8 | 10391.6 | 10766.4 | 10621.6 | 10559.5 | 10682.6 | 10711.4 | 9556 | 10638.4 | 10730.3 | 10828.5 | 10824.8 | 10785.7 | 10788.6 | 9574.1 | 10743.2 | 9638.3 | 26.8317 | 26.4183 | 27.0798 | 26.971 | 26.9346 | 26.5611 | 0 | 40.415 | 0 | 0 | 40.9 | 39.7 | 2.0609 | 0.70726 | 0.279 | 0.11134 | 1.9288 | 1.2437 | 4.9417 | 4.8017 | 3.6983 | 2.935 | 5.0083 | 4.605 | 4.1821 | 4.2181 | 4.2396 | 4.1714 | 4.2436 | 4.2355 | 0.97734 | 1.1021 | 0.98349 | 1.2608 | 1.2635 | 1.0196 | 5.4824 | 5.4533 | 5.4273 | 5.4528 | 5.3939 | 5.4132 | 0.21292 | 0.23874 | 0.20341 | 0.19602 | 0.21068 | 0.21181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 795198 | 1464 | 781971 | 1499 | 232062.218 | 670.8 | 4.1821 | 4.2181 | 4.2396 | 4.1714 | 4.2436 | 4.2355 | 5.4824 | 5.4533 | 5.4273 | 5.4528 | 5.3939 | 5.4132 | 773000 | 2000 | 775000 | 2000 | 1542200 | 5200 | 1544000 | 1537000 | 10.5333 | 4.2151 | 1.1011 | 5.4371 | 0.21226 | 26.12% | 3.904% | 26.7994 | 40.3383 | 1.0552 | 4.3317 | 1551275.7 | 1528533 | 1764902.8211 | 86.61% | 26 | 0
2024-11-28 | 2025 | 2024 | Year_3 | Year_3 | 2024-11-01 | 30 | 335090.89 | 7:21 | 17:55 | 9509.2 | 9906.4 | 9890.6 | 9855.2 | 9942.3 | 9968.9 | 9883.9 | 10390.1 | 9882 | 9859.1 | 9746.9 | 9954.8 | 9862.2 | 9857.6 | 9838 | 9958.6 | 9827.3 | 9938 | 9959.3 | 10005.6 | 9926.8 | 9928.8 | 9680.5 | 9824.6 | 9591.9 | 8427.1 | 9638 | 9619.9 | 9883.3 | 9752.6 | 9665.7 | 9866.3 | 9864 | 9929 | 9947.8 | 9876.2 | 10032.3 | 9867.3 | 9911.1 | 9735.7 | 10956.4 | 9657.4 | 10794.8 | 9580.8 | 10078.2 | 11356.6 | 9470.9 | 10931 | 9713.1 | 9849.3 | 9899 | 9257.3 | 10255.4 | 9704 | 10113.9 | 9798.4 | 8951.3 | 10390.2 | 9040.6 | 10271.2 | 10120 | 9027 | 9990.5 | 9472.2 | 9586.8 | 8964.5 | 9483 | 10084.5 | 10238.6 | 9238.8 | 10063.3 | 8893.4 | 9684 | 9569.8 | 8890.8 | 10102.6 | 8828.5 | 10039.6 | 8850.9 | 9996.4 | 9436.3 | 10235.1 | 9515 | 10653.5 | 9360.5 | 10014.9 | 9283.3 | 8173.4 | 10195.4 | 9812.5 | 9130.1 | 10626.7 | 10246.9 | 9355.7 | 9214.7 | 10376.1 | 9105 | 9581.9 | 10339.2 | 9156.7 | 10526.8 | 9151.7 | 10215.6 | 9389.1 | 10350.4 | 8906.8 | 10427.6 | 9386.7 | 10255.1 | 9320.6 | 10330.7 | 9508.9 | 9216.9 | 10208.8 | 9346.3 | 9185.5 | 10301.2 | 10479.7 | 10263.1 | 9304.7 | 10381.1 | 9252 | 9991.5 | 9413.7 | 9936.7 | 8633.5 | 10078.4 | 9101.5 | 9370.6 | 9362.9 | 9225.8 | 7983.3 | 9148.7 | 8089.4 | 9185.4 | 9211.3 | 10868.5 | 9375 | 10918.6 | 9606.1 | 10799.6 | 9433.1 | 9614.2 | 9357.7 | 10542.6 | 10931.4 | 10781.9 | 10709.1 | 10820.9 | 10851.6 | 9690.9 | 10791.7 | 10912.4 | 11002 | 11015.8 | 10956.7 | 10958.1 | 9728.9 | 10904.2 | 9789.9 | 26.8832 | 26.5413 | 26.9152 | 26.8213 | 26.6404 | 26.41 | 0 | 40.141 | 0 | 0 | 40.1227 | 39.4 | 2.2739 | 1.1039 | 0.31469 | 0.14835 | 2.1346 | 1.7692 | 4.5067 | 4.65 | 3.5917 | 4.3833 | 5.0267 | 5.135 | 4.2188 | 4.2379 | 4.276 | 4.2316 | 4.2808 | 4.2771 | 1.0098 | 1.1125 | 1.0006 | 1.2884 | 1.2793 | 1.0287 | 5.5522 | 5.4935 | 5.5017 | 5.562 | 5.4691 | 5.4757 | 0.21944 | 0.24465 | 0.2082 | 0.20483 | 0.21217 | 0.21467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 795980 | 1466 | 782758 | 1500 | 233626.018 | 675.933 | 4.2188 | 4.2379 | 4.276 | 4.2316 | 4.2808 | 4.2771 | 5.5522 | 5.4935 | 5.5017 | 5.562 | 5.4691 | 5.4757 | 782000 | 2000 | 787000 | 1000 | 1563800 | 5133 | 1566000 | 1558667 | 10.5667 | 4.2537 | 1.1199 | 5.509 | 0.21733 | 26.33% | 3.945% | 26.7019 | 39.8879 | 1.2908 | 4.5489 | 1572815.7 | 1550533 | 1785928.8808 | 86.82% | 22 | 0
2024-11-29 | 2025 | 2024 | Year_3 | Year_3 | 2024-11-01 | 30 | 335090.89 | 7:20 | 17:53 | 9618.7 | 10016.1 | 10006.3 | 9969.4 | 10063.7 | 10126.9 | 10054.6 | 10493.4 | 10000 | 9940.5 | 9873.6 | 10083.5 | 9987 | 9983.7 | 9927.1 | 10069.9 | 9927.5 | 10047.4 | 10073.7 | 10116.5 | 10043.3 | 10040.3 | 9810.4 | 9948.9 | 9718.4 | 8537.9 | 9752.9 | 9747 | 10021 | 9884.8 | 9819.8 | 10017 | 10041.8 | 10093.6 | 10085.4 | 10035.9 | 10201.5 | 10015.7 | 10054.4 | 9883.6 | 11083.8 | 9770.2 | 10912.1 | 9683.4 | 10226.9 | 11539.4 | 9611 | 11061.9 | 9809.3 | 9949 | 10007.1 | 9373.9 | 10374.8 | 9837.7 | 10241 | 9899.1 | 9072.9 | 10505.5 | 9134.3 | 10384.9 | 10238.2 | 9122.7 | 10125.7 | 9614.4 | 9686.6 | 9060.4 | 9587.9 | 10192.6 | 10356.4 | 9331.7 | 10165.9 | 8994.7 | 9790.1 | 9666.4 | 8989.4 | 10204.8 | 8918.9 | 10150.6 | 8946.1 | 10123.9 | 9560.8 | 10374.1 | 9640.1 | 10788.7 | 9475.6 | 10138.6 | 9381.9 | 8322.1 | 10326.3 | 9919.2 | 9241.3 | 10738.8 | 10340.5 | 9428.7 | 9282.2 | 10495.1 | 9237.3 | 9698.1 | 10443.8 | 9258.1 | 10637.3 | 9246.1 | 10319.1 | 9488.1 | 10461.1 | 8999.2 | 10542.7 | 9494.1 | 10369.7 | 9419 | 10444.9 | 9620.9 | 9331.3 | 10335.5 | 9445.9 | 9279.6 | 10403.1 | 10606.7 | 10372.8 | 9441.2 | 10510.4 | 9380.7 | 10102.7 | 9517.6 | 10055.4 | 8765.9 | 10221 | 9236.8 | 9484.8 | 9472.2 | 9339.4 | 8086.3 | 9289.2 | 8241.9 | 9326 | 9351.8 | 11005.9 | 9490.4 | 11043.3 | 9711.7 | 10923.9 | 9541 | 9721.5 | 9501.9 | 10661.8 | 11053.4 | 10918.5 | 10832.5 | 10961.2 | 10997.4 | 9798 | 10915.1 | 11039.8 | 11118.8 | 11125.9 | 11066.7 | 11073.2 | 9843.5 | 11019.8 | 9896.6 | 25.571 | 25.2235 | 25.4796 | 25.6863 | 25.3596 | 25.0551 | 0 | 39.0168 | 0 | 0 | 39.1 | 37.1852 | 2.5823 | 1.2528 | 0.80802 | 0.16717 | 2.4655 | 1.9431 | 5.2583 | 5.1367 | 5.2 | 3.3667 | 5.3717 | 5.5817 | 4.2569 | 4.2725 | 4.3125 | 4.2454 | 4.2951 | 4.2908 | 1.0149 | 1.1281 | 1.0036 | 1.2923 | 1.2897 | 1.0418 | 5.6374 | 5.5431 | 5.5784 | 5.6123 | 5.5044 | 5.5304 | 0.2188 | 0.24184 | 0.20602 | 0.20254 | 0.2104 | 0.21274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 796773 | 1467 | 783554 | 1502 | 235208.618 | 680.867 | 4.2569 | 4.2725 | 4.3125 | 4.2454 | 4.2951 | 4.2908 | 5.6374 | 5.5431 | 5.5784 | 5.6123 | 5.5044 | 5.5304 | 793000 | 1000 | 796000 | 2000 | 1582600 | 4934 | 1586000 | 1577666 | 10.55 | 4.2788 | 1.1284 | 5.5677 | 0.21539 | 26.37% | 3.869% | 25.3958 | 38.434 | 1.5365 | 4.9858 | 1591872.2 | 1568333 | 1815412.8191 | 86.39% | 20 | 0
2024-11-30 | 2025 | 2024 | Year_3 | Year_3 | 2024-11-01 | 30 | 335090.89 | 7:22 | 17:51 | 8885.3 | 9266.8 | 9264.9 | 9231.5 | 9290.2 | 9381.4 | 9340.8 | 9781.1 | 9260.5 | 9204.4 | 9132.1 | 9323 | 9231.6 | 9230.7 | 9174.9 | 9300.8 | 9176.5 | 9296 | 9312 | 9345.2 | 9282.5 | 9280.1 | 9066.1 | 9192 | 8977.1 | 7889.5 | 9007.4 | 8999.9 | 9256.2 | 9144.8 | 9072.9 | 9255.1 | 9280.5 | 9311.1 | 9318.6 | 9257.2 | 9408 | 9259.2 | 9306.9 | 9141 | 10268.7 | 9063.6 | 10114.3 | 8981.9 | 9500.3 | 10711.5 | 8905.9 | 10255.6 | 9082.5 | 9207.5 | 9258.2 | 8672.1 | 9600.9 | 9108.8 | 9502.1 | 9173.4 | 8422.8 | 9730.5 | 8449.4 | 9617.2 | 9467.6 | 8443 | 9347.9 | 8868.4 | 8922.7 | 8362 | 8859.6 | 9421.3 | 9573.3 | 8623.9 | 9407.7 | 8316.9 | 9055.6 | 8950.2 | 8302.3 | 9449.4 | 8257.1 | 9378.5 | 8275.5 | 9358.2 | 8835.6 | 9597.5 | 8927.8 | 9975.3 | 8776.4 | 9388.7 | 8666.2 | 7709.5 | 9543.2 | 9204 | 8552 | 9942.9 | 9596.3 | 8767 | 8638.2 | 9708.7 | 8573.6 | 8991.5 | 9692.4 | 8577.3 | 9853.7 | 8566.1 | 9570.4 | 8797.6 | 9696.3 | 8343.3 | 9776.5 | 8801.8 | 9626.7 | 8752 | 9712.5 | 8923.7 | 8649.3 | 9578.7 | 8756.2 | 8604.6 | 9661.5 | 9852.6 | 9632.2 | 8762.1 | 9750.7 | 8695.5 | 9379.2 | 8827.2 | 9342.5 | 8126 | 9482 | 8568 | 8775.4 | 8753.8 | 8697 | 7491.8 | 8598.2 | 7626.3 | 8655.3 | 8678.3 | 10183 | 8774.8 | 10227.3 | 8994.6 | 10126 | 8844.8 | 9020.6 | 8812.8 | 9873.1 | 10234 | 10099.1 | 10028.1 | 10140.8 | 10168.5 | 9071.9 | 10109.3 | 10225.8 | 10297.6 | 10300.7 | 10251.9 | 10254.8 | 9113.9 | 10213.6 | 9155.1 | 25.33 | 24.88 | 25.26 | 25.24 | 24.95 | 24.64 | 0 | 36.71 | 0 | 0 | 36.7 | 35.6 | 2.58 | 1.42 | 0.71 | 0.14 | 2.67 | 1.96 | 5.32 | 5.58 | 4.35 | 3.39 | 6.28 | 5.65 | 3.95 | 3.97 | 4 | 3.73 | 3.98 | 3.99 | 0.95 | 1.05 | 0.94 | 1.4 | 1.2 | 0.96 | 5.15 | 5.08 | 5.11 | 5.14 | 5.05 | 5.07 | 0.22 | 0.24 | 0.2 | 0.2 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 797506 | 1469 | 784292 | 1504 | 236674.818 | 686 | 3.95 | 3.97 | 4 | 3.73 | 3.98 | 3.99 | 5.15 | 5.08 | 5.11 | 5.14 | 5.05 | 5.07 | 733000 | 2000 | 738000 | 2000 | 1466200 | 5133 | 1467000 | 1461067 | 10.4833 | 3.9367 | 1.0833 | 5.1 | 0.21333 | 27.52% | 4.183% | 25.05 | 36.3367 | 1.58 | 5.095 | 1473955.3 | 1452000 | 1673202.8 | 86.78% | 21 | 0
2024-12-01 | 2025 | 2024 | Year_3 | Year_3 | 2024-12-01 | 31 | 335090.89 | 7:24 | 17:54 | 8634.9 | 8994.9 | 9012.7 | 8990.6 | 9044.2 | 9117.3 | 9050.9 | 9456.7 | 8997.8 | 8929.5 | 8878.6 | 9057.4 | 8972.6 | 8975.8 | 8957.4 | 9052.2 | 8936.1 | 9028.3 | 9060.8 | 9103.8 | 9033.8 | 9030.7 | 8812.5 | 8939.6 | 8728.1 | 7671.8 | 8764.8 | 8750.9 | 8993.2 | 8880 | 8815.2 | 8998.1 | 9011.5 | 9054.5 | 9055.3 | 8991.6 | 9131.7 | 8992.8 | 9032.8 | 8883.5 | 9967.7 | 8802.4 | 9823.1 | 8720.4 | 9211.3 | 10385.3 | 8640.7 | 9952.7 | 8839.5 | 8967.5 | 9006.8 | 8441.2 | 9334.9 | 8851.9 | 9249.6 | 8924.1 | 8193.2 | 9448.5 | 8221.6 | 9381.8 | 9239.4 | 8217.5 | 9072.6 | 8601.3 | 8631.8 | 8125.7 | 8614.3 | 9154.4 | 9309.1 | 8381 | 9167.2 | 8080.2 | 8811.1 | 8709.2 | 8075.7 | 9199.1 | 8040.8 | 9122 | 8038.7 | 9100.7 | 8590.9 | 9331.8 | 8676.1 | 9692.7 | 8521.9 | 9121.9 | 8429.3 | 7499.3 | 9254.3 | 8943.1 | 8319.1 | 9660.8 | 9338.4 | 8524.2 | 8399.5 | 9432.2 | 8329 | 8749.1 | 9439.1 | 8354 | 9581.7 | 8342.1 | 9299.1 | 8568.2 | 9405.4 | 8125.9 | 9498.7 | 8568.1 | 9335.9 | 8516.1 | 9445 | 8688.3 | 8418.3 | 9308.4 | 8535.5 | 8372 | 9422.1 | 9573.6 | 9369.3 | 8518.8 | 9475.6 | 8451.1 | 9130.4 | 8582.9 | 9097.9 | 7892.9 | 9212.9 | 8327 | 8542.9 | 8529.2 | 8461.2 | 7295.1 | 8323.3 | 7386.2 | 8405.4 | 8427.3 | 9897 | 8511.1 | 9933.1 | 8730.7 | 9831.4 | 8594.3 | 8764.6 | 8552.6 | 9594.1 | 9945.8 | 9838 | 9750 | 9861.4 | 9883.4 | 8813.2 | 9813.5 | 9949.3 | 10011.6 | 10014.8 | 9957.1 | 9969.5 | 8857.5 | 9932.9 | 8903.3 | 25.34 | 24.95 | 25.1 | 25.22 | 24.91 | 24.64 | 0 | 36.72 | 0 | 0 | 36.5 | 35.8 | 2.71 | 1.54 | 0.67 | 0.1 | 2.73 | 2.06 | 4.88 | 4.89 | 4.6 | 2.36 | 5.14 | 5.2 | 3.86 | 3.88 | 3.92 | 4 | 3.91 | 3.91 | 0.93 | 1.03 | 0.91 | 1.48 | 1.17 | 0.95 | 5.02 | 4.94 | 4.98 | 4.99 | 4.93 | 4.94 | 0.21 | 0.23 | 0.2 | 0.2 | 0.2 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 798219 | 1471 | 785010 | 1505 | 238100.285 | 691.133 | 3.86 | 3.88 | 3.92 | 4 | 3.91 | 3.91 | 5.02 | 4.94 | 4.98 | 4.99 | 4.93 | 4.94 | 713000 | 2000 | 718000 | 1000 | 1425467 | 5133 | 1428000 | 1420334 | 10.5 | 3.9133 | 1.0783 | 4.9667 | 0.20833 | 27.56% | 4.195% | 25.0267 | 36.34 | 1.635 | 4.5117 | 1432831.6 | 1412334 | 1597914.4657 | 88.39% | 22 | 0
2024-12-02 | 2025 | 2024 | Year_3 | Year_3 | 2024-12-01 | 31 | 335090.89 | 7:25 | 17:53 | 8888 | 9277.9 | 9281.2 | 9264.5 | 9304.4 | 9417.7 | 9344.4 | 9766.9 | 9271.8 | 9173 | 9146.3 | 9330.2 | 9249 | 9250.5 | 9251.7 | 9334.8 | 9219.1 | 9311.4 | 9339.4 | 9380.5 | 9309.1 | 9305.5 | 9090.6 | 9218.3 | 9020.2 | 7919.8 | 9036.6 | 9027 | 9272.8 | 9148 | 9095.1 | 9290.7 | 9307.6 | 9345.5 | 9347.1 | 9285.3 | 9429.5 | 9285.7 | 9326.8 | 9160.9 | 10264.9 | 9057.5 | 10111.9 | 8976.4 | 9506.6 | 10727.3 | 8891.3 | 10251.8 | 9119 | 9265.6 | 9297.3 | 8725.4 | 9630 | 9108.6 | 9566.7 | 9207.9 | 8477 | 9764.3 | 8495.2 | 9719.3 | 9598.7 | 8499.6 | 9374.3 | 8895.9 | 8996.4 | 8432.2 | 8944.3 | 9498 | 9654.2 | 8697.6 | 9506.9 | 8387.6 | 9136.3 | 9040.5 | 8379.9 | 9550 | 8346.3 | 9476.8 | 8342.5 | 9461.5 | 8911.2 | 9677.6 | 8997.9 | 10053.2 | 8846.6 | 9467.6 | 8743.2 | 7768.4 | 9571.7 | 9258.9 | 8625.2 | 9997.9 | 9653.3 | 8799.4 | 8661.1 | 9754.5 | 8576.6 | 9035.8 | 9733.9 | 8638.2 | 9905.4 | 8599.5 | 9577 | 8829.7 | 9680.8 | 8359.2 | 9775.7 | 8837.2 | 9600.9 | 8735.4 | 9696.9 | 8957.1 | 8707.1 | 9623.1 | 8822.2 | 8654.2 | 9732.2 | 9906.4 | 9678 | 8810.1 | 9796.3 | 8739.1 | 9418.6 | 8868.8 | 9384.1 | 8163.1 | 9524.3 | 8616.5 | 8871.5 | 8866.5 | 8750.5 | 7570.4 | 8643.4 | 7654.6 | 8707.3 | 8726 | 10248.8 | 8815.4 | 10278.5 | 9039.1 | 10175.6 | 8903 | 9071.5 | 8866 | 9922.4 | 10288.8 | 10163.7 | 10076.1 | 10202.4 | 10228.3 | 9117.9 | 10152 | 10284.3 | 10356.1 | 10356.9 | 10296.7 | 10314.7 | 9161.2 | 10279.2 | 9210.1 | 25.5031 | 24.9291 | 25.1276 | 25.3025 | 24.9393 | 24.7292 | 0 | 35.5 | 0 | 0 | 36.5 | 35.3 | 3.3124 | 2.5304 | 1.5916 | 0.72892 | 3.2256 | 2.9117 | 6.5167 | 7.6967 | 6.0917 | 6.8567 | 6.525 | 6.6283 | 3.9347 | 3.9479 | 3.9845 | 3.9386 | 3.9984 | 3.9989 | 0.94381 | 1.0462 | 0.9267 | 1.1971 | 1.1982 | 0.96553 | 5.1538 | 5.0769 | 5.1097 | 5.1638 | 5.0839 | 5.109 | 0.21266 | 0.23644 | 0.19843 | 0.1995 | 0.20589 | 0.21483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 798955 | 1473 | 785752 | 1507 | 239573.152 | 696.133 | 3.9347 | 3.9479 | 3.9845 | 3.9386 | 3.9984 | 3.9989 | 5.1538 | 5.0769 | 5.1097 | 5.1638 | 5.0839 | 5.109 | 736000 | 2000 | 742000 | 2000 | 1472867 | 5000 | 1474000 | 1467867 | 10.4667 | 3.9672 | 1.0463 | 5.1162 | 0.21129 | 26.37% | 4.13% | 25.0885 | 35.7667 | 2.3834 | 6.7192 | 1480778.3 | 1459200 | 1645898.7847 | 88.66% | 20 | 0
2024-12-03 | 2025 | 2024 | Year_3 | Year_3 | 2024-12-01 | 31 | 335090.89 | 7:26 | 17:53 | 9245.5 | 9638.7 | 9654.9 | 9642.6 | 9669.3 | 9805.4 | 9695.3 | 10166.7 | 9624.2 | 9512.9 | 9497.9 | 9685.6 | 9607.5 | 9605.2 | 9590.9 | 9694 | 9580 | 9683.2 | 9699.8 | 9735.7 | 9667.9 | 9663.7 | 9456.4 | 9582.5 | 9400.3 | 8256.6 | 9391.9 | 9380 | 9635.7 | 9521.7 | 9471.4 | 9673.1 | 9702.2 | 9735.3 | 9717.2 | 9662.7 | 9818.6 | 9674.5 | 9720 | 9553.6 | 10619.5 | 9363.1 | 10469.6 | 9283.9 | 9845.3 | 11112.3 | 9205.8 | 10606.9 | 9471 | 9634.3 | 9669.2 | 9096.1 | 10023.5 | 9486.7 | 9967.5 | 9584.2 | 8827.2 | 10164 | 8842.5 | 10131 | 10000.2 | 8847.1 | 9722.2 | 9218.3 | 9369.4 | 8730.4 | 9298.7 | 9830.4 | 10045.5 | 9000.4 | 9864.1 | 8690.4 | 9499.6 | 9388.7 | 8707.1 | 9919.2 | 8675 | 9843.7 | 8652.4 | 9813.1 | 9237.4 | 10023.6 | 9335.8 | 10415.9 | 9178.8 | 9824 | 9046.4 | 8047.9 | 9922.2 | 9605.2 | 8942.2 | 10359 | 10005.2 | 9120.8 | 8976.5 | 10146.5 | 8927.3 | 9367.8 | 10073.2 | 8948.9 | 10293.4 | 8906.5 | 9962.6 | 9125.1 | 10080.9 | 8654.5 | 10149.1 | 9146.4 | 9973.3 | 9053.1 | 10033.1 | 9273.3 | 9045.1 | 9987 | 9151 | 8965.3 | 10080.2 | 10274.8 | 10026.9 | 9139.3 | 10157.4 | 9061.5 | 9756.2 | 9193.7 | 9729 | 8481.4 | 9877.5 | 8933.1 | 9201.6 | 9194.6 | 9088 | 7847.4 | 9011 | 7996.6 | 9012.7 | 9032.8 | 10626.8 | 9142.4 | 10661.1 | 9373.4 | 10545.8 | 9231.2 | 9402.2 | 9192.5 | 10291.5 | 10666.5 | 10541.1 | 10450.6 | 10583.4 | 10612.4 | 9459.3 | 10527.1 | 10666 | 10738.8 | 10746.5 | 10691.2 | 10699.1 | 9504 | 10726.6 | 9552.1 | 25.9139 | 25.2213 | 25.7245 | 25.511 | 25.3415 | 25.097 | 0 | 35.8668 | 0 | 0 | 35.8 | 34.6 | 3.9108 | 3.3389 | 2.1424 | 1.2818 | 3.9525 | 3.3674 | 7.055 | 7.1817 | 6.4983 | 6.6133 | 7.565 | 6.45 | 4.0415 | 4.0608 | 4.0745 | 4.0384 | 4.0954 | 4.1075 | 0.9788 | 1.0852 | 0.95506 | 1.2409 | 1.2382 | 0.9974 | 5.3218 | 5.2516 | 5.2554 | 5.3314 | 5.2447 | 5.2659 | 0.22397 | 0.24894 | 0.20705 | 0.21024 | 0.21781 | 0.22692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 799719 | 1475 | 786522 | 1509 | 241101.619 | 701.2 | 4.0415 | 4.0608 | 4.0745 | 4.0384 | 4.0954 | 4.1075 | 5.3218 | 5.2516 | 5.2554 | 5.3314 | 5.2447 | 5.2659 | 764000 | 2000 | 770000 | 2000 | 1528467 | 5067 | 1530000 | 1523400 | 10.45 | 4.0697 | 1.0826 | 5.2785 | 0.22249 | 26.6% | 4.215% | 25.4682 | 35.4223 | 2.999 | 6.8939 | 1537271.7 | 1514467 | 1696143.4493 | 89.29% | 36 | 0
2024-12-04 | 2025 | 2024 | Year_3 | Year_3 | 2024-12-01 | 31 | 335090.89 | 7:27 | 17:54 | 8751 | 9155.3 | 9167.6 | 9133.4 | 9206.1 | 9292.8 | 9183.7 | 9650.6 | 9108.6 | 8967.7 | 9006.8 | 9180.3 | 9113.9 | 9109.8 | 9129.3 | 9205.6 | 9095.9 | 9176.9 | 9189.1 | 9224.5 | 9159.3 | 9155.6 | 8970.2 | 9082.1 | 8915.2 | 7834.6 | 8903.2 | 8891.5 | 9137.2 | 9025.9 | 8998.4 | 9182.4 | 9189.4 | 9221.4 | 9217 | 9155.3 | 9303.8 | 9174 | 9217 | 9075.2 | 10122.8 | 8937.2 | 9977.3 | 8856.9 | 9369.3 | 10559 | 8749.1 | 10105.4 | 8992.4 | 9148 | 9176.3 | 8639.3 | 9518 | 9020.1 | 9468.7 | 9124.8 | 8372.6 | 9656.6 | 8376.5 | 9594.3 | 9467.6 | 8373.7 | 9180.7 | 8703 | 8875.1 | 8260.5 | 8795.5 | 9287.7 | 9505.7 | 8505.2 | 9328.9 | 8216.5 | 9001.8 | 8879.3 | 8241.3 | 9377.7 | 8194.2 | 9317.3 | 8189.5 | 9274.2 | 8712 | 9454.5 | 8797.4 | 9826.3 | 8657.2 | 9268.9 | 8541.1 | 7606.5 | 9344.7 | 9091.4 | 8428.8 | 9772.4 | 9456.4 | 8633.5 | 8510.7 | 9576.9 | 8477.4 | 8825.9 | 9524.6 | 8419.3 | 9735 | 8396.9 | 9423.2 | 8618.5 | 9539.8 | 8174 | 9593.7 | 8592.6 | 9452.8 | 8572.4 | 9533.7 | 8718.4 | 8532.6 | 9414.8 | 8623.7 | 8446.4 | 9501.9 | 9683.7 | 9445.5 | 8620.4 | 9586.3 | 8555.6 | 9205.4 | 8687.2 | 9191.2 | 8022.4 | 9340.2 | 8439.7 | 8661.5 | 8645.4 | 8603.8 | 7394.1 | 8489.8 | 7547.9 | 8496.3 | 8514.1 | 10019.1 | 8627.4 | 10047.1 | 8835.3 | 9940.4 | 8697 | 8864.3 | 8670.7 | 9696.1 | 10052.5 | 9926.1 | 9846.6 | 9962.3 | 9992 | 8909.3 | 9919 | 10052.4 | 10122.2 | 10134.1 | 10076.4 | 10081.6 | 8956.6 | 10085.3 | 8997.4 | 24.2533 | 23.8407 | 24.1753 | 24.1591 | 23.9726 | 23.8333 | 0 | 33.4 | 0 | 0 | 34.1104 | 33.3 | 3.3964 | 2.89 | 1.5027 | 0.31289 | 3.313 | 2.8285 | 6.01 | 5.6917 | 5.4217 | 5.0667 | 5.855 | 5.9967 | 3.856 | 3.8768 | 3.9128 | 3.8526 | 3.899 | 3.9074 | 0.93437 | 1.0517 | 0.91841 | 1.1845 | 1.19 | 0.9654 | 5.0318 | 4.9712 | 4.9993 | 5.0313 | 4.9386 | 4.9595 | 0.21882 | 0.24288 | 0.2026 | 0.20537 | 0.21197 | 0.22048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800445 | 1477 | 787248 | 1510 | 242548.086 | 706.467 | 3.856 | 3.8768 | 3.9128 | 3.8526 | 3.899 | 3.9074 | 5.0318 | 4.9712 | 4.9993 | 5.0313 | 4.9386 | 4.9595 | 726000 | 2000 | 726000 | 1000 | 1446467 | 5267 | 1449000 | 1441200 | 10.45 | 3.8841 | 1.0407 | 4.9886 | 0.21702 | 26.79% | 4.35% | 24.0391 | 33.6035 | 2.3739 | 5.6736 | 1454035.6 | 1423667 | 1600507.8197 | 88.95% | 23 | 0
2024-12-05 | 2025 | 2024 | Year_3 | Year_3 | 2024-12-01 | 31 | 335090.89 | 7:24 | 17:55 | 9364 | 9795.6 | 9780.2 | 9752.9 | 9830.5 | 9924.2 | 9783 | 10267.9 | 9733.2 | 9635.8 | 9618.4 | 9804.2 | 9734.6 | 9733.7 | 9758.3 | 9843.6 | 9734.6 | 9824.3 | 9829.9 | 9860.7 | 9795.8 | 9791.1 | 9587 | 9714.8 | 9534 | 8372.7 | 9505.9 | 9505.8 | 9757.6 | 9625.3 | 9596.8 | 9810.3 | 9803.7 | 9841.3 | 9846.6 | 9778.1 | 9937.1 | 9797.9 | 9832.2 | 9660 | 10787.9 | 9502.2 | 10625.2 | 9423.5 | 9949.9 | 11223.4 | 9322.9 | 10767.2 | 9590.7 | 9752.6 | 9793.3 | 9217.4 | 10151.3 | 9607.7 | 10094.3 | 9707.9 | 8950 | 10316.3 | 8941.8 | 10237 | 10125 | 8945.2 | 9842 | 9340 | 9488.9 | 8831.5 | 9404.4 | 9937.3 | 10167.1 | 9102.5 | 9976.2 | 8791.2 | 9627.2 | 9490.1 | 8821.6 | 10036 | 8772.5 | 9999.7 | 8792.1 | 9964.5 | 9329.2 | 10118 | 9421.2 | 10520.7 | 9263.3 | 9916.9 | 9117.1 | 8129.9 | 10020.4 | 9694.6 | 9014.4 | 10459.8 | 10092.1 | 9204.7 | 9074.2 | 10224.6 | 9011.1 | 9415 | 10135.9 | 8953.3 | 10403.5 | 8947 | 10054.4 | 9196.8 | 10181.5 | 8734 | 10244.6 | 9183.7 | 10081.2 | 9132 | 10173.5 | 9299.2 | 9101.2 | 10061.3 | 9184.6 | 9032.8 | 10135.3 | 10339 | 10089.6 | 9196.5 | 10231 | 9120.5 | 9792.8 | 9258.4 | 9793.8 | 8527.5 | 9951.6 | 8989.5 | 9241.3 | 9213.1 | 9137.4 | 7884.8 | 9012.2 | 7998.3 | 9043.8 | 9071.3 | 10715.6 | 9213.3 | 10695.6 | 9436.9 | 10604.9 | 9260.6 | 9441 | 9211.1 | 10366.3 | 10739.4 | 10629.4 | 10531.6 | 10663.2 | 10698.1 | 9518.8 | 10599.9 | 10730.3 | 10815 | 10815.2 | 10759.5 | 10773.6 | 9567.9 | 10794.5 | 9623.1 | 23.5737 | 23.4508 | 23.7977 | 23.7728 | 23.6648 | 23.4661 | 0 | 37.8306 | 0 | 0 | 38.1 | 37 | 2.3515 | 0.90581 | 0.36523 | 0.59632 | 2.2088 | 1.6254 | 4.7417 | 4.8817 | 4.8683 | 4.6583 | 4.8533 | 4.3483 | 4.0844 | 4.1111 | 4.1426 | 4.079 | 4.1528 | 4.1468 | 0.98771 | 1.0987 | 0.97439 | 1.2596 | 1.2523 | 1.008 | 5.4293 | 5.3573 | 5.3804 | 5.4255 | 5.3447 | 5.3563 | 0.21862 | 0.24112 | 0.20198 | 0.20488 | 0.20939 | 0.21891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 801220 | 1479 | 788023 | 1512 | 244092.019 | 711.133 | 4.0844 | 4.1111 | 4.1426 | 4.079 | 4.1528 | 4.1468 | 5.4293 | 5.3573 | 5.3804 | 5.4255 | 5.3447 | 5.3563 | 775000 | 2000 | 775000 | 2000 | 1543933 | 4666 | 1546000 | 1539267 | 10.5167 | 4.1195 | 1.0968 | 5.3822 | 0.21582 | 26.62% | 4.01% | 23.621 | 37.6435 | 1.3422 | 4.7253 | 1552481.3 | 1531133 | 1735119.1931 | 88.24% | 22 | 0
2024-12-06 | 2025 | 2024 | Year_3 | Year_3 | 2024-12-01 | 31 | 335090.89 | 7:25 | 17:52 | 9210.2 | 9633.1 | 9621.3 | 9581.5 | 9656.9 | 9776.6 | 9611.1 | 10078 | 9576.2 | 9547.7 | 9476.7 | 9641.9 | 9589.9 | 9591.7 | 9579 | 9675.5 | 9563.4 | 9658.9 | 9670.9 | 9694.9 | 9630 | 9621 | 9429.3 | 9555.4 | 9375.2 | 8234.8 | 9345.5 | 9346.2 | 9597.4 | 9493.8 | 9440 | 9647.1 | 9644.7 | 9668.9 | 9685.3 | 9617.5 | 9775 | 9639.6 | 9683.6 | 9511.1 | 10588.1 | 9330.3 | 10440 | 9265.5 | 9777.2 | 11016.1 | 9148.1 | 10566.9 | 9437.4 | 9597.3 | 9631.4 | 9063.1 | 9989.9 | 9430.9 | 9940.7 | 9568 | 8804.7 | 10147.8 | 8804.7 | 10088.1 | 9955.7 | 8799.3 | 9656.8 | 9145 | 9307.7 | 8668.5 | 9227.8 | 9750.1 | 9983.1 | 8926.4 | 9786 | 8624.3 | 9455.4 | 9321.2 | 8657.6 | 9840.4 | 8593 | 9829.1 | 8628 | 9764.2 | 9149.1 | 9914.5 | 9217 | 10314.2 | 9074.5 | 9705.4 | 8938.9 | 7965.2 | 9859.1 | 9505.4 | 8837 | 10279.3 | 9889.6 | 9015.7 | 8889.5 | 10044.3 | 8829.3 | 9228.6 | 9960 | 8815.1 | 10216.4 | 8824.1 | 9891 | 9055.5 | 10008.6 | 8586.8 | 10067.6 | 9043.4 | 9921 | 9007.1 | 9996.1 | 9164.8 | 8891.9 | 9852.5 | 9028.3 | 8867.5 | 9949.5 | 10108.3 | 9907.8 | 8979.2 | 9996.4 | 8914.6 | 9631.3 | 9089.7 | 9608.8 | 8338.2 | 9723.9 | 8781 | 9037.8 | 9020.6 | 8924.5 | 7709.6 | 8829.7 | 7828.9 | 8893.8 | 8905 | 10493.9 | 9023.2 | 10445.5 | 9248.2 | 10383.5 | 9069.2 | 9254.5 | 9024.8 | 10161.3 | 10523.9 | 10407.6 | 10315.3 | 10448.5 | 10470 | 9321.9 | 10382.6 | 10500.6 | 10586.3 | 10590.2 | 10548.8 | 10554.2 | 9383.2 | 10581.8 | 9422.6 | 23.9552 | 23.6967 | 23.9456 | 24.1807 | 24.0767 | 23.6687 | 0 | 36.9 | 0 | 0 | 38 | 36.0964 | 2.1006 | 0.3539 | 0.073014 | 0.16919 | 2.0058 | 1.0962 | 4.2567 | 4.16 | 3.9983 | 3.6933 | 4.2267 | 4.5683 | 4.0262 | 4.0465 | 4.0748 | 4.0087 | 4.0742 | 4.0652 | 0.96481 | 1.0888 | 0.94408 | 1.2307 | 1.2345 | 0.99599 | 5.3447 | 5.2738 | 5.2986 | 5.3246 | 5.2313 | 5.2519 | 0.21559 | 0.24151 | 0.19981 | 0.20236 | 0.20913 | 0.21826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 801981 | 1481 | 788783 | 1514 | 245607.019 | 715.933 | 4.0262 | 4.0465 | 4.0748 | 4.0087 | 4.0742 | 4.0652 | 5.3447 | 5.2738 | 5.2986 | 5.3246 | 5.2313 | 5.2519 | 761000 | 2000 | 760000 | 2000 | 1515000 | 4800 | 1517000 | 1510200 | 10.45 | 4.0493 | 1.0765 | 5.2875 | 0.21444 | 26.58% | 4.056% | 23.9206 | 36.9988 | 0.96645 | 4.1506 | 1524107.1 | 1496467 | 1689497.7597 | 88.57% | 22 | 0
2024-12-07 | 2025 | 2024 | Year_3 | Year_3 | 2024-12-01 | 31 | 335090.89 | 7:26 | 18:01 | 10412.8 | 10869 | 10868.8 | 10830.6 | 10920.1 | 11032.1 | 10825.4 | 11278.5 | 10797.5 | 10766.6 | 10706.3 | 10871.5 | 10848.8 | 10845.7 | 10843.9 | 10933.3 | 10821.6 | 10925.1 | 10924.5 | 10971.3 | 10891 | 10886.9 | 10662.8 | 10808.3 | 10619.7 | 9319.7 | 10574.2 | 10583.5 | 10861.8 | 10754.8 | 10699.3 | 10910.7 | 10928.4 | 10955.2 | 10962.2 | 10891.2 | 11042 | 10911.8 | 10953.8 | 10741.3 | 11811 | 10586.8 | 11654.8 | 10529.4 | 11065.4 | 12143.3 | 10379.6 | 11769.4 | 10650.6 | 10813.1 | 10879.7 | 10247.5 | 11246.9 | 10671.1 | 11190 | 10786.7 | 9953.7 | 11403.1 | 9942.6 | 11315.8 | 11196.5 | 9933.5 | 10933.9 | 10370.3 | 10554.7 | 9855.7 | 10469 | 11044.7 | 11239.9 | 10143.9 | 11078.7 | 9790.7 | 10696.8 | 10574 | 9815.9 | 11119.3 | 9743.1 | 11099.2 | 9778.7 | 11033.6 | 10375.1 | 11202.3 | 10449.8 | 11569.1 | 10300.2 | 11000 | 10138.4 | 9046.7 | 11125.6 | 10781.5 | 10025.2 | 11528.3 | 11186.6 | 10258.4 | 10123.2 | 11303.9 | 10015.1 | 10480.7 | 11285.4 | 10026.5 | 11459.9 | 10022.3 | 11186.9 | 10284.9 | 11277.8 | 9763.8 | 11341.8 | 10286.2 | 11210.3 | 10224.1 | 11295.2 | 10442 | 10133 | 11172.6 | 10276.9 | 10091.4 | 11175.2 | 11424.3 | 11211.6 | 10231.2 | 11299 | 10171.4 | 10946.8 | 10370.6 | 10941.3 | 9500 | 11057.4 | 10018.1 | 10306.5 | 10277 | 10170.6 | 8800.9 | 10093.2 | 8951.4 | 10097.3 | 10102.2 | 11724.7 | 10262.4 | 11684.4 | 10514.1 | 11618.6 | 10323.8 | 10547.1 | 10231.2 | 11435.8 | 11743.4 | 11652.7 | 11561.5 | 11696.4 | 11716.3 | 10606.9 | 11626.3 | 11721.9 | 11806.4 | 11792.3 | 11754.3 | 11774.4 | 10658.6 | 11805.3 | 10699 | 23.4062 | 23.0771 | 23.4089 | 23.5542 | 23.7262 | 23.1157 | 0 | 36.3491 | 0 | 0 | 35.3595 | 34.7 | 3.1587 | 1.6456 | 1.2483 | 1.4299 | 3.2692 | 2.7533 | 5.8933 | 5.7367 | 5.13 | 5.6933 | 6.4517 | 6.1733 | 4.4557 | 4.49 | 4.5388 | 4.4533 | 4.5447 | 4.5297 | 1.085 | 1.2267 | 1.0722 | 1.39 | 1.4066 | 1.1345 | 6.02 | 5.9492 | 6.0004 | 6.0216 | 5.94 | 5.9743 | 0.24867 | 0.27845 | 0.22669 | 0.23402 | 0.24416 | 0.25381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 802840 | 1482 | 789641 | 1515 | 247317.286 | 720.6 | 4.4557 | 4.49 | 4.5388 | 4.4533 | 4.5447 | 4.5297 | 6.02 | 5.9492 | 6.0004 | 6.0216 | 5.94 | 5.9743 | 859000 | 1000 | 858000 | 1000 | 1710267 | 4667 | 1715000 | 1705600 | 10.5833 | 4.502 | 1.2191 | 5.9842 | 0.24763 | 27.08% | 4.138% | 23.3814 | 35.4695 | 2.2508 | 5.8464 | 1722559.5 | 1693133 | 1918037.7648 | 88.27% | 27 | 2014
2024-12-08 | 2025 | 2024 | Year_3 | Year_3 | 2024-12-01 | 31 | 335090.89 | 7:23 | 17:57 | 9275.1 | 9654.9 | 9643.3 | 9641.2 | 9682 | 9763.7 | 9595.4 | 9961.2 | 9579.8 | 9507.7 | 9501.8 | 9624.7 | 9613.6 | 9602.8 | 9628.2 | 9702.6 | 9594.4 | 9674.8 | 9627.6 | 9710 | 9649.7 | 9631.2 | 9468.7 | 9575.5 | 9408.7 | 8419.3 | 9404.1 | 9385.3 | 9640.2 | 9533.9 | 9490.7 | 9663.2 | 9913.3 | 9960.6 | 9962.6 | 9899.6 | 9779.8 | 9665 | 9707 | 9538.3 | 10498 | 9411.4 | 10338.8 | 9362.2 | 9822.5 | 10906.7 | 9242.5 | 10379.2 | 9510.6 | 9621.1 | 9664.3 | 9168.7 | 9967.1 | 9484.2 | 9911.1 | 9587.2 | 8926.1 | 10134.4 | 8958.8 | 10041 | 9967.7 | 8939.8 | 9690.5 | 9238 | 9410.2 | 8855.1 | 9351.7 | 9790.7 | 9999.5 | 9043.8 | 9829.3 | 8794.1 | 9568.2 | 9424 | 8850.3 | 9884.8 | 8795 | 9881.5 | 8798.9 | 9818.8 | 9239.5 | 9912.3 | 9320.3 | 10268.5 | 9162 | 9756.2 | 9055.1 | 8204.9 | 9848.7 | 9608.3 | 8959.3 | 10249.3 | 9934.9 | 9173.9 | 9069.3 | 9961.2 | 8964.5 | 9346.5 | 10059.4 | 8982 | 10188 | 8943.4 | 9920.7 | 9124.9 | 10013.8 | 8726.3 | 10017.9 | 9178 | 9949.8 | 9154.6 | 10010.5 | 9313.5 | 9047.4 | 9894.7 | 9155.8 | 9018.8 | 9952 | 10080.9 | 9929.3 | 9130.8 | 9982.7 | 9061 | 9687.1 | 9218.5 | 9681.9 | 8547.1 | 9794.8 | 8956.4 | 9175.5 | 9109.2 | 9092.9 | 7924 | 9006.2 | 8104.6 | 9058.9 | 9046.7 | 10427.5 | 9122.3 | 10455.3 | 9337.8 | 10303.2 | 9179.2 | 9349.2 | 9143.5 | 10131.8 | 10449.3 | 10335.2 | 10268 | 10368.5 | 10401.3 | 9394.4 | 10339.5 | 10454.4 | 10516.1 | 10510 | 10460.6 | 10466 | 9435.5 | 10512.3 | 9483.6 | 21.6499 | 21.4166 | 21.7891 | 21.6754 | 21.9281 | 21.4956 | 0 | 29.8011 | 0 | 0 | 28.999 | 28.2572 | 6.368 | 5.9819 | 5.3919 | 5.423 | 6.3177 | 5.6459 | 11.89 | 11.5383 | 11.135 | 11.9867 | 11.5717 | 10.7433 | 4.1135 | 4.1603 | 4.1883 | 4.1138 | 4.1826 | 4.1784 | 1.0819 | 1.1259 | 1.0617 | 1.3473 | 1.3006 | 1.0185 | 5.3617 | 5.322 | 5.3697 | 5.4006 | 5.3204 | 5.3002 | 0.2707 | 0.2997 | 0.24881 | 0.26022 | 0.26315 | 0.27083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 803605 | 1485 | 790405 | 1517 | 248841.019 | 725.333 | 4.1135 | 4.1603 | 4.1883 | 4.1138 | 4.1826 | 4.1784 | 5.3617 | 5.322 | 5.3697 | 5.4006 | 5.3204 | 5.3002 | 765000 | 3000 | 764000 | 2000 | 1523733 | 4733 | 1524000 | 1519000 | 10.5667 | 4.1562 | 1.156 | 5.3458 | 0.2689 | 27.81% | 5.03% | 21.6591 | 29.0191 | 5.8547 | 11.4775 | 1533268.5 | 1540602.9706 | 1761021.5285 | 87.48% | 20 | 1229
2024-12-09 | 2025 | 2024 | Year_3 | Year_3 | 2024-12-01 | 31 | 335090.89 | 7:26 | 17:58 | 9341 | 9714.4 | 9745.8 | 9724.6 | 9747.1 | 9868.9 | 9651.3 | 10246.2 | 9687.4 | 9685.2 | 9591.8 | 9739.2 | 9693 | 9691.2 | 9675.2 | 9792.7 | 9673.8 | 9779.3 | 9789.6 | 9813.5 | 9757.3 | 9735.1 | 9550.4 | 9680.6 | 9530.9 | 8370.8 | 9482.3 | 9485.4 | 9772 | 9687.4 | 9593.8 | 9778.8 | 9768.4 | 9813.7 | 9812.4 | 9735.7 | 9898.2 | 9785.8 | 9831.2 | 9661.8 | 10778.5 | 9507.4 | 10618.1 | 9436.8 | 9986.8 | 11260.1 | 9311.9 | 10736.5 | 9623.3 | 9794.8 | 9777.5 | 9162.6 | 10125.8 | 9541.7 | 10081 | 9711.2 | 8941.6 | 10305.7 | 8964.5 | 10252.5 | 10137 | 8951.3 | 9762.6 | 9257.5 | 9440.2 | 8817.1 | 9413.2 | 9894.8 | 10180.4 | 9090 | 10000.7 | 8788.5 | 9654.1 | 9530.4 | 8855.8 | 10081.5 | 8793.8 | 10054.5 | 8790.8 | 9973.1 | 9258.9 | 10032.9 | 9325.4 | 10435.4 | 9184.4 | 9826.9 | 9073.2 | 8068 | 10016.8 | 9626.4 | 8980.4 | 10448.4 | 10022.8 | 9136.5 | 9003.7 | 10188.9 | 8928.5 | 9413.7 | 10212.3 | 9003 | 10345.1 | 8992.3 | 10054.4 | 9245.6 | 10193.2 | 8771.1 | 10266.4 | 9235.6 | 10106.6 | 9177.7 | 10199.5 | 9328.1 | 9068 | 10000.1 | 9175.1 | 9000.7 | 10114.7 | 10326.7 | 10071.4 | 9170.4 | 10217.8 | 9114 | 9785.6 | 9240.7 | 9749.9 | 8522.1 | 9947.8 | 8968.1 | 9252.8 | 9232.2 | 9143.9 | 7918.9 | 9002.4 | 7992.2 | 9020.2 | 9035.9 | 10626.4 | 9144.2 | 10681.4 | 9402.5 | 10578.4 | 9253.7 | 9446.4 | 9190.5 | 10304 | 10676.6 | 10528.3 | 10431 | 10566.5 | 10599.1 | 9457.4 | 10545.4 | 10663.2 | 10749.3 | 10782.2 | 10721.4 | 10737.4 | 9534.5 | 10713.1 | 9550.5 | 18.74 | 18.68 | 18.94 | 18.94 | 18.87 | 18.75 | 0 | 29.81 | 0 | 0 | 29.9 | 28.6 | 3.05 | 2.16 | 1.2 | 1.39 | 2.99 | 2.15 | 5.31 | 5.63 | 5.21 | 4.88 | 5.7 | 5.64 | 4.03 | 4.05 | 4.13 | 4.03 | 4.1 | 4.09 | 1 | 1.15 | 0.99 | 1.27 | 1.28 | 1.03 | 5.31 | 5.22 | 5.33 | 5.33 | 5.27 | 5.28 | 0.25 | 0.28 | 0.23 | 0.24 | 0.24 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 804378 | 1486 | 791177 | 1518 | 250379.953 | 728.6 | 4.03 | 4.05 | 4.13 | 4.03 | 4.1 | 4.09 | 5.31 | 5.22 | 5.33 | 5.33 | 5.27 | 5.28 | 773000 | 1000 | 772000 | 1000 | 1538934 | 3267 | 1543000 | 1535667 | 10.5333 | 4.0717 | 1.12 | 5.29 | 0.24833 | 27.51% | 4.694% | 18.82 | 29.4367 | 2.1567 | 5.395 | 1548825.9 | 1523867 | 1737212.5255 | 87.72% | 24 | 0
2024-12-10 | 2025 | 2024 | Year_3 | Year_3 | 2024-12-01 | 31 | 335090.89 | 7:28 | 17:57 | 9464.9 | 9805.8 | 9897.7 | 9863 | 9927.7 | 9981.4 | 9709.9 | 10336.6 | 9816.5 | 9798.6 | 9720 | 9857.8 | 9828.8 | 9808.3 | 9841.9 | 9947.3 | 9840 | 9959.6 | 9935.5 | 9968.5 | 9912.6 | 9889.2 | 9691.1 | 9815.6 | 9687.4 | 8501.7 | 9627.9 | 9635.8 | 9923.8 | 9820.4 | 9729.7 | 9945.3 | 9902.3 | 9992.6 | 9982.5 | 9890 | 10044.8 | 9917.8 | 9963.5 | 9806.1 | 10902.6 | 9611.4 | 10766.3 | 9559 | 10071.1 | 11337.4 | 9418.5 | 10882.9 | 9760.4 | 9925.3 | 9923.6 | 9287.4 | 10268.4 | 9601.6 | 10259.5 | 9858.3 | 9099.4 | 10492.1 | 9086 | 10399.7 | 10283.1 | 9081.4 | 9876.1 | 9367.8 | 9604.7 | 9001.3 | 9583.2 | 10110.9 | 10353.6 | 9280.6 | 10177.8 | 8974.3 | 9808.4 | 9709.4 | 9012.3 | 10271.5 | 8946.8 | 10256.4 | 8936.7 | 10107.5 | 9472.6 | 10254.7 | 9525.5 | 10679.5 | 9379.1 | 10041.4 | 9259.5 | 8234.2 | 10182.7 | 9818.4 | 9190.8 | 10649.9 | 10193.8 | 9253 | 9091.8 | 10413.6 | 9104.9 | 9552.2 | 10355.4 | 9142.5 | 10507.1 | 9127.4 | 10215.8 | 9393 | 10341.5 | 8904.5 | 10426.8 | 9383.6 | 10259.2 | 9332.4 | 10341.9 | 9513.7 | 9179.1 | 10186.3 | 9309 | 9153.4 | 10290.1 | 10528.5 | 10246.6 | 9335.4 | 10404.2 | 9273.7 | 9943.8 | 9390.2 | 9941.7 | 8689 | 10125 | 9128.6 | 9428.8 | 9426.7 | 9250.8 | 8056.3 | 9104.7 | 8079 | 9169.5 | 9186.3 | 10826.9 | 9299.5 | 10860.6 | 9558.3 | 10738.9 | 9394.9 | 9588.3 | 9322.6 | 10491 | 10875 | 10736.7 | 10646 | 10767 | 10796 | 9628 | 10729 | 10889.5 | 10975.3 | 10973.6 | 10904.3 | 10916.2 | 9698.4 | 10946.9 | 9738.5 | 20.05 | 19.33 | 19.52 | 19.49 | 19.24 | 19 | 0 | 30.87 | 0 | 0 | 30.9 | 29.6 | 3.28 | 2.35 | 1.44 | 1.97 | 2.99 | 2.48 | 6.82 | 6.61 | 6.57 | 6.07 | 6.41 | 6.75 | 4.07 | 4.08 | 4.15 | 4.09 | 4.14 | 4.14 | 1.01 | 1.15 | 0.99 | 1.28 | 1.28 | 1.04 | 5.39 | 5.29 | 5.41 | 5.45 | 5.35 | 5.38 | 0.24 | 0.27 | 0.22 | 0.23 | 0.23 | 0.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 805163 | 1488 | 791963 | 1520 | 251942.42 | 733.2 | 4.07 | 4.08 | 4.15 | 4.09 | 4.14 | 4.14 | 5.39 | 5.29 | 5.41 | 5.45 | 5.35 | 5.38 | 785000 | 2000 | 786000 | 2000 | 1562467 | 4600 | 1567000 | 1557867 | 10.4833 | 4.1117 | 1.125 | 5.3783 | 0.23833 | 27.36% | 4.431% | 19.4383 | 30.4567 | 2.4183 | 6.5383 | 1573915.1 | 1543734 | 1754351.3564 | 87.99% | 28 | 0
2024-12-11 | 2025 | 2024 | Year_3 | Year_3 | 2024-12-01 | 31 | 335090.89 | 7:28 | 17:56 | 4599.3 | 4764.1 | 4815.9 | 4816.8 | 4830.2 | 4870.4 | 4720.4 | 5022.8 | 4787.8 | 4744.7 | 4726.8 | 4796.7 | 4791.3 | 4768.2 | 4814.1 | 4854.1 | 4777.4 | 4834.4 | 4825.4 | 4845.9 | 4816.5 | 4806.6 | 4708.9 | 4761.6 | 4704.4 | 4132 | 4675.7 | 4679.8 | 4815.1 | 4757.1 | 4720.2 | 4827.9 | 4790.5 | 4842.2 | 4843.6 | 4801.5 | 4870.5 | 4815.7 | 4833.4 | 4741.9 | 5301.1 | 4652.6 | 5230.1 | 4644.3 | 4899.7 | 5518.1 | 4557.7 | 5296.6 | 4659.3 | 4749 | 4763 | 4472.4 | 4927 | 4605.9 | 4927.1 | 4691.4 | 4379.3 | 5039 | 4366.9 | 4993.5 | 4937.1 | 4365.2 | 4747.7 | 4496.7 | 4788 | 4745 | 4727 | 4797 | 4791 | 4768 | 4814 | 4854 | 4715.6 | 4648 | 4326.5 | 4919.3 | 4293.5 | 4927.9 | 4289.7 | 4850.4 | 4313.4 | 4662.9 | 4343 | 4870.4 | 4273 | 4576.9 | 4216.8 | 3763.6 | 4620.9 | 4495.9 | 4178.5 | 4842.8 | 4633.9 | 4203.2 | 4136.9 | 4741.8 | 4148.4 | 4347.7 | 4718 | 4162.2 | 4781.1 | 4145.1 | 4656.1 | 4273.6 | 4707.2 | 4057.1 | 4746.9 | 4276.4 | 4679.8 | 4258.6 | 4709.1 | 4334.8 | 4170.2 | 4640.7 | 4238.1 | 4171 | 4683.9 | 4795.4 | 4671.2 | 4257.7 | 4745.2 | 4219.2 | 4527 | 4281.6 | 4533 | 3958.4 | 4615.5 | 4162 | 4302.3 | 4288 | 4209.9 | 3670.6 | 4144.7 | 3653 | 4193 | 4183.5 | 4945.8 | 4228.6 | 4959.1 | 4363.1 | 4886.3 | 4274.8 | 4362.4 | 4255.7 | 4784 | 4952.7 | 4880.7 | 4852.3 | 4917.2 | 4926.2 | 4389.4 | 4894.4 | 4960.3 | 5005.8 | 5016.6 | 4981.5 | 4986.7 | 4423.9 | 4989.8 | 4446.2 | 20.15 | 19.66 | 19.99 | 19.82 | 19.8 | 19.51 | 0 | 34.74 | 0 | 0 | 34.9 | 33 | 2.73 | 1.41 | 0.96 | 1.15 | 2.69 | 1.85 | 5.23 | 4.97 | 4.7 | 4.78 | 4.82 | 4.89 | 4.16 | 4.18 | 4.26 | 4.19 | 4.23 | 4.24 | 1.04 | 1.19 | 1.02 | 1.32 | 1.29 | 1.05 | 5.57 | 5.47 | 5.6 | 5.61 | 5.51 | 5.53 | 0.25 | 0.27 | 0.22 | 0.23 | 0.24 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 805542 | 1490 | 792321 | 1521 | 252676.62 | 740.133 | 4.16 | 4.18 | 4.26 | 4.19 | 4.23 | 4.24 | 5.57 | 5.47 | 5.6 | 5.61 | 5.51 | 5.53 | 379000 | 2000 | 358000 | 1000 | 734200 | 6933 | 734000 | 727267 | 10.4667 | 4.21 | 1.1517 | 5.5483 | 0.24333 | 27.36% | 4.386% | 19.8217 | 34.2133 | 1.7983 | 4.8983 | 740302 | 703400 | 791330.0088 | 88.89% | 20 | 825
2024-12-12 | 2025 | 2024 | Year_3 | Year_3 | 2024-12-01 | 31 | 335090.89 | 7:28 | 17:57 | 9888.5 | 10286.2 | 10329.9 | 10280.9 | 10379.2 | 10508.8 | 10245.9 | 10848.9 | 10232.6 | 10257.1 | 10142.5 | 10274.1 | 10284.3 | 10237.9 | 10313.4 | 10415.5 | 10305.2 | 10422.2 | 10412.8 | 10440.4 | 10373.8 | 10356 | 10137 | 10273.2 | 10132.4 | 8892.8 | 10069 | 10078.2 | 10368 | 10243 | 10178.8 | 10400.4 | 10400.9 | 10439.1 | 10447.4 | 10367.9 | 10544.2 | 10407.3 | 10465 | 10253 | 11460.9 | 10086.5 | 11288.1 | 10037.6 | 10597.8 | 11919.3 | 9836.8 | 11422 | 10181.1 | 10351.5 | 10377.1 | 9770.3 | 10760.8 | 10110.2 | 10731 | 10289.5 | 9513.2 | 10964 | 9474.1 | 10869.2 | 10706.2 | 9456.4 | 10308.6 | 9765.7 | 10061 | 9387 | 9992 | 10565 | 10805 | 9690 | 10629 | 9358 | 10233.5 | 10123.8 | 9395.2 | 10697.5 | 9316.9 | 10686.7 | 9347.3 | 10550.6 | 9883.7 | 10699.5 | 9939 | 11157 | 9794 | 10482.8 | 9688.8 | 8630.4 | 10622.4 | 10270.4 | 9589.9 | 11140.6 | 10712.3 | 9770.4 | 9630.4 | 10872.5 | 9513.2 | 9996.1 | 10838.4 | 9560.4 | 10983.3 | 9533.5 | 10685.2 | 9807.7 | 10806.3 | 9309.9 | 10888.5 | 9804.1 | 10728 | 9756.3 | 10801.1 | 9935.4 | 9602.7 | 10652.3 | 9753.4 | 9591.1 | 10746.4 | 10966.9 | 10687.6 | 9709.3 | 10856.4 | 9686.6 | 10408.3 | 9833.9 | 10389.2 | 9068 | 10557.3 | 9527.5 | 9804.9 | 9756.4 | 9629.3 | 8373.7 | 9547.1 | 8423.9 | 9633.8 | 9634.9 | 11323.4 | 9715.5 | 11354.8 | 9979 | 11187 | 9796 | 9996.3 | 9795.1 | 10962.9 | 11364 | 11199.7 | 11115.5 | 11256.9 | 11284.7 | 10082.5 | 11237.2 | 11334 | 11429.9 | 11424.6 | 11397.5 | 11391.5 | 10132.4 | 11416.2 | 10150.5 | 19.99 | 19.93 | 20.2 | 20.37 | 20.21 | 19.88 | 0 | 31.9 | 0 | 0 | 32.9 | 31.3 | 2.64 | 1.55 | 0.71 | 1.38 | 2.34 | 1.77 | 5.21 | 5.03 | 5.31 | 4.74 | 5.91 | 4.93 | 4.21 | 4.24 | 4.31 | 4.25 | 4.3 | 4.3 | 1.04 | 1.21 | 1.02 | 1.32 | 1.33 | 1.08 | 5.66 | 5.6 | 5.69 | 5.72 | 5.61 | 5.66 | 0.25 | 0.28 | 0.23 | 0.24 | 0.24 | 0.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 806363 | 1491 | 793142 | 1523 | 254311.353 | 745.133 | 4.21 | 4.24 | 4.31 | 4.25 | 4.3 | 4.3 | 5.66 | 5.6 | 5.69 | 5.72 | 5.61 | 5.66 | 821000 | 1000 | 821000 | 2000 | 1634733 | 5000 | 1639000 | 1629733 | 10.4833 | 4.2683 | 1.1667 | 5.6567 | 0.25 | 27.33% | 4.42% | 20.0967 | 32.0333 | 1.7317 | 5.1883 | 1645449.6 | 1627267 | 1844160.4173 | 88.24% | 27 | 1954
2024-12-13 | 2025 | 2024 | Year_3 | Year_3 | 2024-12-01 | 31 | 335090.89 | 7:30 | 17:58 | 10079 | 10445 | 10538.2 | 10504.8 | 10613.3 | 10667 | 10364.8 | 10920.3 | 10413.3 | 10464.8 | 10318 | 10479.5 | 10440.4 | 10421.1 | 10497.7 | 10584.5 | 10471 | 10580.5 | 10579.9 | 10614.5 | 10544.4 | 10529.9 | 10320.1 | 10458.4 | 10308.5 | 9054.2 | 10248.5 | 10251.2 | 10550.5 | 10429.3 | 10348.8 | 10578.7 | 10573.7 | 10640.1 | 10628.6 | 10550.1 | 10703.7 | 10571.7 | 10610.1 | 10412.9 | 11499.4 | 10231.1 | 11344.1 | 10156.1 | 10744.3 | 11914.5 | 9962 | 11463 | 10344.2 | 10542.9 | 10550.5 | 9925.8 | 10915.2 | 10257.8 | 10887.6 | 10457.5 | 9687.1 | 11130.8 | 9653.8 | 11040.1 | 10915.4 | 9653.5 | 10559.7 | 10028.3 | 10242.6 | 9569.8 | 10197.3 | 10747.4 | 10974.7 | 9862.1 | 10812.5 | 9519.1 | 10449.1 | 10312.9 | 9601 | 10893.6 | 9523.3 | 10899 | 9542.7 | 10771.8 | 10029.3 | 10851.4 | 10092.9 | 11256.3 | 9947.5 | 10643 | 9838.7 | 8767.8 | 10831 | 10454.4 | 9755.8 | 11246 | 10855.3 | 9906.5 | 9744.1 | 11016.7 | 9715.6 | 10190.4 | 10997.8 | 9732.8 | 11136.6 | 9690.6 | 10853.1 | 9960.6 | 10956.9 | 9457.3 | 11044 | 9973 | 10898.7 | 9917.4 | 10966.4 | 10108.1 | 9794.7 | 10861.7 | 9929.7 | 9770.1 | 10921.3 | 11113 | 10875.3 | 9879.7 | 11001.1 | 9849.7 | 10578.8 | 10013 | 10592.2 | 9207.5 | 10721.4 | 9691.8 | 9962.3 | 9925.7 | 9836.5 | 8505 | 9734.6 | 8651.7 | 9753.2 | 9770.5 | 11416.4 | 9899.6 | 11436 | 10164.4 | 11296.3 | 9947.3 | 10138.9 | 9946 | 11089.3 | 11428.6 | 11307.9 | 11229.7 | 11363.9 | 11384 | 10243.8 | 11181.6 | 11402.6 | 11512.3 | 11489.1 | 11463.2 | 11468.9 | 10295.7 | 11460.7 | 10321.3 | 19.2603 | 18.6777 | 19.2294 | 18.8661 | 18.7573 | 18.5337 | 0 | 29.5483 | 0 | 0 | 29.2 | 27.7 | 4.2572 | 3.4888 | 2.4525 | 3.5284 | 4.0367 | 3.7765 | 7.36 | 7.5183 | 7.25 | 7.33 | 7.2217 | 7.2367 | 4.2272 | 4.2507 | 4.3145 | 4.2584 | 4.3079 | 4.3027 | 1.1095 | 1.2118 | 1.0378 | 1.3456 | 1.3416 | 1.0778 | 5.6737 | 5.5984 | 5.6909 | 5.7291 | 5.619 | 5.6559 | 0.26104 | 0.28396 | 0.23188 | 0.24449 | 0.24833 | 0.26501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 807197 | 1494 | 793974 | 1525 | 255970.687 | 750.2 | 4.2272 | 4.2507 | 4.3145 | 4.2584 | 4.3079 | 4.3027 | 5.6737 | 5.5984 | 5.6909 | 5.7291 | 5.619 | 5.6559 | 834000 | 3000 | 832000 | 2000 | 1659334 | 5067 | 1661000 | 1654267 | 10.4667 | 4.2769 | 1.1873 | 5.6612 | 0.25579 | 27.76% | 4.518% | 18.8874 | 28.8161 | 3.59 | 7.3194 | 1670758.6 | 1648467 | 1865278.0447 | 88.38% | 27 | 0
2024-12-14 | 2025 | 2024 | Year_3 | Year_3 | 2024-12-01 | 31 | 335090.89 | 7:29 | 17:59 | 10442 | 10801.8 | 10880.9 | 10853.8 | 10937.6 | 11004.1 | 10807.3 | 11197 | 10734.9 | 10776.8 | 10695.8 | 10855.9 | 10795.1 | 10800 | 10828.1 | 10919 | 10806.9 | 10907.4 | 10902.6 | 10946.8 | 10866.2 | 10865.4 | 10688.1 | 10810.4 | 10678.5 | 9398.7 | 10625.5 | 10622.8 | 10874.7 | 10768.5 | 10713.9 | 10903.6 | 10960.4 | 11055.8 | 11023.6 | 10939.8 | 11012.9 | 10900 | 10931.7 | 10755.9 | 11730.5 | 10606.8 | 11575.3 | 10555.4 | 11091.7 | 12134.6 | 10412 | 11691 | 10686.1 | 10875.8 | 10887.3 | 10295.4 | 11198.4 | 10642.2 | 11181.2 | 10775.3 | 10053 | 11600 | 10011 | 11492 | 11339 | 9998 | 11046 | 10484 | 10609 | 9938 | 10584 | 11171 | 11422 | 10246 | 11238 | 9887.3 | 10837 | 10701 | 9953 | 11320 | 9873 | 11333 | 9889 | 11178 | 10424.5 | 11163.2 | 10485 | 11531.9 | 10326.9 | 10983.1 | 10195.4 | 9093.7 | 11103.1 | 10803 | 10112.7 | 11502.8 | 11167.5 | 10307.2 | 10148 | 11288.5 | 10101.3 | 10574.2 | 11282 | 10112.7 | 11396.4 | 10065.7 | 11157.1 | 10342.8 | 11235.1 | 9822.2 | 11329.2 | 10364.4 | 11204.4 | 10296.4 | 11248.2 | 10499.4 | 10189.7 | 11173.2 | 10337.9 | 10156.2 | 11219.8 | 11392.2 | 11186.5 | 10273.9 | 11284.3 | 10226 | 10934.9 | 10407.5 | 10952.3 | 9567.3 | 11054.9 | 10069.7 | 10347.8 | 10305.9 | 10240.7 | 8837.5 | 10075.2 | 8945 | 10140.2 | 10151.5 | 11644.6 | 10288.1 | 11671.3 | 10545.5 | 11529 | 10314.3 | 10521.2 | 10304.4 | 11378.8 | 11687 | 11573.6 | 11493.2 | 11608.8 | 11632.4 | 10632.1 | 11343.3 | 11650.7 | 11759 | 11709.8 | 11701.2 | 11718.2 | 10693.3 | 11681.9 | 10728.4 | 20.3985 | 19.6282 | 20.0048 | 19.9829 | 19.6487 | 19.3193 | 0 | 32.3078 | 0 | 0 | 32.1 | 30.4 | 3.2736 | 2.3088 | 1.3049 | 2.0229 | 2.9603 | 2.595 | 6.25 | 5.6233 | 5.42 | 5.025 | 6.195 | 5.9417 | 4.3943 | 4.4115 | 4.4864 | 4.4267 | 4.4888 | 4.4858 | 1.1875 | 1.2554 | 1.0821 | 1.4026 | 1.3896 | 1.12 | 5.9578 | 5.8311 | 5.98 | 6.028 | 5.9164 | 5.9338 | 0.26315 | 0.28659 | 0.2337 | 0.24549 | 0.24929 | 0.26868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 808059 | 1496 | 794832 | 1526 | 257684.553 | 755.333 | 4.3943 | 4.4115 | 4.4864 | 4.4267 | 4.4888 | 4.4858 | 5.9578 | 5.8311 | 5.98 | 6.028 | 5.9164 | 5.9338 | 862000 | 2000 | 858000 | 1000 | 1713866 | 5133 | 1717000 | 1708733 | 10.5 | 4.4489 | 1.2395 | 5.9412 | 0.25782 | 27.86% | 4.339% | 19.8304 | 31.6026 | 2.4109 | 5.7425 | 1725779.7 | 1694666 | 1926942.2723 | 87.95% | 26 | 0
2024-12-15 | 2025 | 2024 | Year_3 | Year_3 | 2024-12-01 | 31 | 335090.89 | 7:28 | 17:57 | 10418.9 | 10814.3 | 10916.9 | 10890.4 | 10958.8 | 11059.9 | 10819 | 11225.5 | 10816.2 | 10757.2 | 10697.1 | 10915.5 | 10806.5 | 10829 | 10814.4 | 10955.9 | 10820.4 | 10940.8 | 10948.2 | 10988.1 | 10899.4 | 10895.1 | 10674.2 | 10828.9 | 10672 | 9369.9 | 10612.9 | 10609.9 | 10898.8 | 10772.8 | 10714.7 | 10947.2 | 10948.4 | 11027.9 | 10992.1 | 10917.7 | 11080.3 | 10948.4 | 10988.2 | 10773.7 | 11843.1 | 10584.4 | 11679.6 | 10517 | 11129.1 | 12273.3 | 10403.6 | 11808.1 | 10698.3 | 10909.6 | 10917.8 | 10264.3 | 11261.3 | 10637.9 | 11245.5 | 10783.9 | 10016 | 11551 | 9993 | 11457 | 11306 | 9986 | 11004 | 10452 | 10604 | 9909 | 10553 | 11143 | 11397 | 10225 | 11206 | 9866 | 10806 | 10666 | 9936 | 11280 | 9841 | 11321 | 9981 | 11169 | 10423.9 | 11251.2 | 10482.9 | 11630.9 | 10324.6 | 11020.8 | 10183.4 | 9077.7 | 11164.6 | 10787.1 | 10084.9 | 11588.5 | 11238.7 | 10293 | 10149.3 | 11356.1 | 10032.4 | 10522.2 | 11335.6 | 10068.8 | 11486.9 | 10039.2 | 11211.7 | 10321 | 11310.8 | 9796.1 | 11395.1 | 10328.2 | 11262.4 | 10276.7 | 11318.7 | 10458.1 | 10127.8 | 11209.1 | 10286.6 | 10113.7 | 11272.2 | 11457.7 | 11238.7 | 10233.9 | 11344.3 | 10185.4 | 10949.3 | 10363.3 | 10953.3 | 9520.4 | 11072.9 | 10030.6 | 10173.4 | 10285.4 | 10171.7 | 8819.6 | 10006.2 | 8872.1 | 10127.4 | 10135.2 | 11753.7 | 10266.4 | 11764.4 | 10510.7 | 11641.2 | 10314.5 | 10518.9 | 10290.2 | 11453 | 11793.6 | 11661.4 | 11580.8 | 11712.2 | 11740.7 | 10603.4 | 11411.2 | 11746.5 | 11872.7 | 11718.3 | 11812.4 | 11823 | 10676.7 | 11844.6 | 10705.5 | 21.4111 | 20.8193 | 21.1782 | 21.3003 | 20.8347 | 20.4157 | 0 | 33.8 | 0 | 0 | 34.4113 | 33.3 | 2.6147 | 1.2649 | 0.21129 | 0.61504 | 2.2089 | 1.6115 | 4.9767 | 4.4717 | 3.4983 | 4.2783 | 4.4017 | 4.3383 | 4.4174 | 4.4754 | 4.5143 | 4.4551 | 4.5135 | 4.5093 | 1.1944 | 1.2605 | 1.0896 | 1.4135 | 1.3662 | 1.125 | 6.0039 | 5.9905 | 6.0337 | 6.0827 | 5.9574 | 5.98 | 0.2613 | 0.28365 | 0.23139 | 0.24168 | 0.24242 | 0.2665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 808923 | 1497 | 795692 | 1528 | 259400.554 | 760.467 | 4.4174 | 4.4754 | 4.5143 | 4.4551 | 4.5135 | 4.5093 | 6.0039 | 5.9905 | 6.0337 | 6.0827 | 5.9574 | 5.98 | 864000 | 1000 | 860000 | 2000 | 1716001 | 5134 | 1721000 | 1710867 | 10.4833 | 4.4808 | 1.2415 | 6.008 | 0.25449 | 27.71% | 4.236% | 20.9932 | 33.8371 | 1.4211 | 4.3275 | 1727978 | 1705134 | 1943333.6537 | 87.74% | 30 | 0
2024-12-16 | 2025 | 2024 | Year_3 | Year_3 | 2024-12-01 | 31 | 335090.89 | 7:30 | 17:58 | 10228.2 | 10659.7 | 10696.1 | 10676 | 10743.8 | 10834.2 | 10610.4 | 11000.7 | 10610.4 | 10489.8 | 10505 | 10695 | 10631.6 | 10631.6 | 10605.8 | 10748.7 | 10612.9 | 10730.8 | 10741.3 | 10790.5 | 10701.3 | 10698.3 | 10469.5 | 10616 | 10457.7 | 9184 | 10398.5 | 10395.4 | 10689.3 | 10578.5 | 10495.7 | 10727.8 | 10738.5 | 10801.5 | 10753.7 | 10698.9 | 10861.1 | 10721.7 | 10769.3 | 10553 | 11632.8 | 10392.6 | 11473.9 | 10323.5 | 10928.1 | 12050.5 | 10196.8 | 11586.6 | 10470.6 | 10684.9 | 10695.2 | 10058.3 | 11046.8 | 10424.8 | 11021.2 | 10568.2 | 9803.8 | 11302.6 | 9786.5 | 11215.4 | 11078.5 | 9787.8 | 10746.7 | 10207.6 | 10390.8 | 9699.7 | 10326.5 | 10905.7 | 11153.7 | 9992.4 | 10952.6 | 9646.1 | 10584.3 | 10432.8 | 9726.4 | 11034.5 | 9626.6 | 11086.7 | 9678.9 | 10946.1 | 10181 | 10995.6 | 10271.8 | 11374.4 | 10105.4 | 10797.7 | 9977 | 8882.3 | 10973.6 | 10568.1 | 9876.9 | 11361.8 | 11008 | 10081.7 | 9933.2 | 11125.8 | 9813.6 | 10311.6 | 11102.5 | 9869.5 | 11251.2 | 9837.8 | 10987.1 | 10119.3 | 11085.4 | 9605.9 | 11176 | 10117.6 | 11050.7 | 10080.9 | 11120.1 | 10258.5 | 9928.9 | 10989.6 | 10076.9 | 9902.9 | 11050.3 | 11233.5 | 11018.8 | 10034.1 | 11122.5 | 9988.1 | 10736.2 | 10153.1 | 10748 | 9346 | 10871.2 | 9829.9 | 10134.6 | 10116.3 | 9967.9 | 8646.9 | 9854.8 | 8704.3 | 9910.6 | 9926.1 | 11484.8 | 10023.1 | 11497.9 | 10267.4 | 11397.4 | 10094.8 | 10282.3 | 10093.7 | 11181.5 | 11502.9 | 11384.5 | 11310.7 | 11438.2 | 11464.4 | 10341.5 | 11140.7 | 11479.7 | 11596.3 | 11534.5 | 11532.2 | 11543.8 | 10408.7 | 11572.6 | 10444 | 20.3389 | 19.9607 | 20.517 | 20.1938 | 20.2517 | 20.0646 | 0 | 32.4612 | 0 | 0 | 32.0202 | 30.9 | 2.8915 | 2.3059 | 2.0821 | 1.4635 | 2.6313 | 2.4243 | 5.3667 | 5.565 | 5.3267 | 5.7433 | 5.605 | 5.47 | 4.329 | 4.3602 | 4.3858 | 4.3112 | 2.4592 | 4.3652 | 1.1632 | 1.2335 | 1.0618 | 1.3718 | 1.3485 | 1.0947 | 5.8868 | 5.7983 | 5.8245 | 5.8528 | 5.7449 | 5.7557 | 0.25772 | 0.28294 | 0.23084 | 0.24333 | 0.24435 | 0.26595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 809769 | 1499 | 796534 | 1530 | 261082.154 | 765.667 | 4.329 | 4.3602 | 4.3858 | 4.3112 | 2.4592 | 4.3652 | 5.8868 | 5.7983 | 5.8245 | 5.8528 | 5.7449 | 5.7557 | 846000 | 2000 | 842000 | 2000 | 1681600 | 5200 | 1684000 | 1676400 | 10.4667 | 4.0351 | 1.2122 | 5.8105 | 0.25419 | 30.04% | 4.375% | 20.2211 | 31.7938 | 2.2997 | 5.5128 | 1692830.8 | 1669933 | 1893557.1737 | 88.19% | 21 | 1194
2024-12-17 | 2025 | 2024 | Year_3 | Year_3 | 2024-12-01 | 31 | 335090.89 | 7:32 | 17:59 | 10163 | 10613 | 10596 | 10577 | 10639 | 10724 | 10637 | 10911 | 10527.5 | 10498.5 | 10415.3 | 10586.8 | 10551.3 | 10538.7 | 10539.7 | 10663 | 10547.8 | 10662.3 | 10657.8 | 10700.9 | 10632.1 | 10628.4 | 10419.1 | 10557.9 | 10390.1 | 9123.2 | 10342.2 | 10343.6 | 10631.6 | 10522.8 | 10440.4 | 10651.3 | 10670.3 | 10736.4 | 10689.2 | 10639.7 | 10768.5 | 10650.9 | 10691.6 | 10499.7 | 11489.7 | 10328 | 11334 | 10258.1 | 10849.2 | 11911.6 | 10129.7 | 11452.7 | 10390.7 | 10592.1 | 10601.4 | 9983.2 | 10936.8 | 10348 | 10910.2 | 10496.7 | 9733 | 11112 | 9709 | 11034 | 10931 | 9715 | 10625 | 10107 | 10315 | 9628 | 10258 | 10790 | 10981 | 9928 | 10829 | 9590 | 10439 | 10443 | 9667 | 10898 | 9570 | 10939 | 9632 | 10838 | 10118 | 10903 | 10209 | 11258 | 10043 | 10726 | 9922 | 8837 | 10868 | 10532.4 | 9810.4 | 11241.5 | 10908.6 | 10018.6 | 9875.1 | 11036.4 | 9767.9 | 10287.5 | 11023 | 9824.8 | 11148.6 | 9799.3 | 10910.4 | 10088.9 | 11001.7 | 9569.8 | 11092.2 | 10082.6 | 10972.9 | 10038.8 | 11037 | 10221.9 | 9912.2 | 10907.5 | 10050.8 | 9870 | 10973.2 | 11139.9 | 10938.5 | 9990.1 | 11034.7 | 9950.7 | 10682.3 | 10109.4 | 10705.1 | 9311.7 | 10812.7 | 9805.7 | 10091 | 10069.1 | 9928.8 | 8614.4 | 9865.4 | 8719.7 | 9894.4 | 9914.6 | 11395.8 | 9995.7 | 11411.4 | 10238.3 | 11305.6 | 10057.7 | 10258.2 | 10065.4 | 11099 | 11413 | 11311 | 11239 | 11356 | 11379 | 10313 | 11067 | 11376.9 | 11485.1 | 11476 | 11439.1 | 11450.1 | 10362.8 | 11471.8 | 10400.2 | 19.58 | 19.39 | 19.7 | 19.62 | 19.54 | 19.35 | 0 | 30 | 0 | 0 | 30 | 28.8 | 3.94 | 2.99 | 2.96 | 2.91 | 3.59 | 3.29 | 7.07 | 7.33 | 7.75 | 6.82 | 7.2 | 6.83 | 4.31 | 4.35 | 4.38 | 4.3 | 3.95 | 4.36 | 1.17 | 1.25 | 1.07 | 1.38 | 1.39 | 1.11 | 5.82 | 5.75 | 5.78 | 5.8 | 5.71 | 5.72 | 0.27 | 0.3 | 0.24 | 0.25 | 0.26 | 0.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 810608 | 1501 | 797372 | 1531 | 262752.087 | 770.933 | 4.31 | 4.35 | 4.38 | 4.3 | 3.95 | 4.36 | 5.82 | 5.75 | 5.78 | 5.8 | 5.71 | 5.72 | 839000 | 2000 | 838000 | 1000 | 1669933 | 5266 | 1674000 | 1664667 | 10.45 | 4.275 | 1.2283 | 5.7633 | 0.26667 | 28.73% | 4.627% | 19.53 | 29.6 | 3.28 | 7.1667 | 1681335 | 1658601 | 1892723.2034 | 87.63% | 28 | 208
2024-12-18 | 2025 | 2024 | Year_3 | Year_3 | 2024-12-01 | 31 | 335090.89 | 7:29 | 18:00 | 10074.6 | 10488.6 | 10452.7 | 10440.3 | 10486.7 | 10570.8 | 10517.1 | 10773.5 | 10412.6 | 10412.9 | 10292.7 | 10436.4 | 10424.1 | 10398.4 | 10397.9 | 10523.9 | 10397.4 | 10506.1 | 10514.5 | 10562.3 | 10483.3 | 10487.5 | 10296.6 | 10423.5 | 10267.2 | 9045.9 | 10249.5 | 10270.8 | 10508.6 | 10393.4 | 10316.4 | 10498.8 | 10551.7 | 10631.3 | 10586.4 | 10540.9 | 10608.8 | 10498 | 10532.8 | 10351.6 | 11280.1 | 10195.8 | 11141.3 | 10131.9 | 10677.8 | 11703.8 | 10010.8 | 11250.4 | 10275.8 | 10455.5 | 10472.5 | 9899.6 | 10781.7 | 10249.8 | 10741.6 | 10365.9 | 9617.9 | 10917.5 | 9613 | 10860.7 | 10756.3 | 9614 | 10448.3 | 9970.8 | 10176.7 | 9523.4 | 10137.8 | 10591.6 | 10794.3 | 9814.4 | 10646.3 | 9482.1 | 10359 | 10227.7 | 9571.4 | 10694 | 9461.9 | 10758.9 | 9542.3 | 10639.6 | 9997.3 | 10697.9 | 10099.9 | 11035.9 | 9926.3 | 10530 | 9794.9 | 8729.8 | 10655.5 | 10355.5 | 9685.7 | 11009.9 | 10688.7 | 9854.9 | 9709.7 | 10810 | 9626.6 | 10128.5 | 10798.6 | 9684.2 | 10921.7 | 9660.7 | 10697.8 | 9939 | 10788.2 | 9424.2 | 10876.2 | 9929.5 | 10767 | 9895.4 | 10825 | 10068 | 9770.3 | 10670.3 | 9896.4 | 9724.6 | 10753.8 | 10890.2 | 10708.7 | 9861.4 | 10793.4 | 9814.2 | 10486 | 9969.5 | 10493.7 | 9186.4 | 10600.8 | 9685.2 | 9945.1 | 9920.4 | 9825.3 | 8492.9 | 9747.8 | 8648.7 | 9783 | 9805.8 | 11175.2 | 9867.1 | 11199.1 | 10111.6 | 11095.8 | 9928.5 | 10111.4 | 9950.5 | 10878.4 | 11181.3 | 11089.2 | 11018.4 | 11130 | 11149 | 10185.1 | 10861.6 | 11156.2 | 11248.5 | 11238.1 | 11199.1 | 11209.1 | 10208.4 | 11249.9 | 10251.7 | 19.1 | 18.58 | 19.14 | 18.92 | 18.74 | 18.64 | 0 | 29.93 | 0 | 0 | 29.9 | 28.5 | 3.83 | 3.67 | 2.67 | 3.1 | 3.76 | 3.39 | 5.88 | 6.59 | 6.25 | 6.21 | 6.07 | 5.94 | 4.26 | 4.33 | 4.35 | 4.27 | 3.4 | 4.3 | 1.16 | 1.25 | 1.06 | 1.36 | 1.37 | 1.11 | 5.79 | 5.69 | 5.73 | 5.73 | 5.64 | 5.66 | 0.27 | 0.29 | 0.24 | 0.25 | 0.25 | 0.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 811437 | 1503 | 798196 | 1533 | 264396.954 | 776 | 4.26 | 4.33 | 4.35 | 4.27 | 3.4 | 4.3 | 5.79 | 5.69 | 5.73 | 5.73 | 5.64 | 5.66 | 829000 | 2000 | 824000 | 2000 | 1644867 | 5067 | 1649000 | 1639800 | 10.5167 | 4.1517 | 1.2183 | 5.7067 | 0.26333 | 29.35% | 4.614% | 18.8533 | 29.4433 | 3.4033 | 6.1567 | 1656260.3 | 1621999 | 1859739.5544 | 87.22% | 21 | 1944
2024-12-19 | 2025 | 2024 | Year_3 | Year_3 | 2024-12-01 | 31 | 335090.89 | 7:33 | 18:00 | 10069.5 | 10550.6 | 10530.9 | 10490.7 | 10582.6 | 10634.4 | 10565 | 10912.8 | 10478.4 | 10440.4 | 10334.4 | 10522.9 | 10446.7 | 10459 | 10472.4 | 10573.5 | 10463.5 | 10584.4 | 10580.4 | 10618.3 | 10566.6 | 10553.2 | 10324.6 | 10471.8 | 10292.1 | 9037.1 | 10284.8 | 10288.4 | 10588.3 | 10470.6 | 10352.4 | 10577.2 | 10546.4 | 10629.6 | 10580 | 10540.5 | 10716.1 | 10569.9 | 10623.4 | 10403.8 | 11636.4 | 10262.5 | 11477.4 | 10195.5 | 10800.4 | 12038 | 10047.6 | 11587.8 | 10292.1 | 10505.6 | 10512.4 | 9910 | 10897 | 10244 | 10876.8 | 10407.5 | 9630.3 | 11121.5 | 9616.3 | 11031.6 | 10899.2 | 9615.7 | 10553.9 | 10011 | 10174.6 | 9510 | 10143 | 10695 | 10950.4 | 9817.6 | 10765.8 | 9482 | 10398.3 | 10252.5 | 9555.2 | 10845.1 | 9450.3 | 10908.8 | 9522.7 | 10756.5 | 9995 | 10825.6 | 10087.8 | 11268.9 | 9919.5 | 10618.9 | 9773.8 | 8708.1 | 10770.6 | 10392.7 | 9683.9 | 11243.4 | 10865.7 | 9898.1 | 9767.4 | 10984.5 | 9689.8 | 10150.7 | 11022.6 | 9702.7 | 11137.8 | 9690.2 | 10840.6 | 9964.9 | 10982.1 | 9453.9 | 11079.7 | 9957 | 10920.3 | 9925.4 | 11005.9 | 10103.9 | 9791.8 | 10817.8 | 9932.1 | 9737.1 | 10942.9 | 11111.8 | 10882.8 | 9871.3 | 10990.6 | 9822.8 | 10591.6 | 10005.4 | 10594.8 | 9215 | 10711.9 | 9696.6 | 9940.2 | 9909.2 | 9832.6 | 8497.5 | 9704 | 8608.3 | 9755.6 | 9775.5 | 11437.5 | 9848.3 | 11470.1 | 10098.4 | 11321.3 | 9895.1 | 10087 | 9928.9 | 11050.6 | 11470.3 | 11311.9 | 11234.3 | 11375 | 11414.9 | 10180.1 | 11023.1 | 11407 | 11548.4 | 11526.7 | 11479.1 | 11487.6 | 10212.6 | 11525.7 | 10267.2 | 19.18 | 18.93 | 19.59 | 19.15 | 18.97 | 18.79 | 0 | 29.5 | 0 | 0 | 29.4 | 26.9 | 3.95 | 3.45 | 2.99 | 3.07 | 3.76 | 2.91 | 7.53 | 7.23 | 6.98 | 6.91 | 7.43 | 6.82 | 4.23 | 4.3 | 4.33 | 4.23 | 4.29 | 4.26 | 1.15 | 1.24 | 1.06 | 1.36 | 1.37 | 1.1 | 5.74 | 5.65 | 5.72 | 5.69 | 5.61 | 5.61 | 0.26 | 0.29 | 0.24 | 0.25 | 0.25 | 0.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 812271 | 1505 | 799027 | 1535 | 266055.287 | 781.2 | 4.23 | 4.3 | 4.33 | 4.23 | 4.29 | 4.26 | 5.74 | 5.65 | 5.72 | 5.69 | 5.61 | 5.61 | 834000 | 2000 | 831000 | 2000 | 1658333 | 5200 | 1661000 | 1653133 | 10.45 | 4.2733 | 1.2133 | 5.67 | 0.26 | 28.39% | 4.586% | 19.1017 | 28.6 | 3.355 | 7.15 | 1669897.6 | 1647000 | 1870792.1 | 88.04% | 28 | 923
2024-12-20 | 2025 | 2024 | Year_3 | Year_3 | 2024-12-01 | 31 | 335090.89 | 7:34 | 17:56 | 8568.3 | 8996.4 | 8983.3 | 8937.9 | 9028.3 | 9101.4 | 9021 | 9314.2 | 8946.9 | 8887 | 8831.1 | 8997.6 | 8927.1 | 8931.1 | 8985.3 | 9047 | 8942.9 | 9036.4 | 9036.4 | 9070.8 | 9030.6 | 9015.5 | 8834.1 | 8943.7 | 8794.4 | 7723.7 | 8785.5 | 8785.7 | 9051.8 | 8951.5 | 8854.6 | 9048 | 9011.7 | 9074.1 | 9043.3 | 9002.6 | 9147.5 | 9025.2 | 9069.9 | 8911.8 | 9954.1 | 8797.6 | 9808.8 | 8724.1 | 9260 | 10448 | 8599.1 | 9917.6 | 8822.9 | 8994.4 | 8991.8 | 8469.9 | 9331 | 8778.4 | 9311.3 | 8945.7 | 8231.2 | 9519.8 | 8217 | 9421.5 | 9308.7 | 8211.5 | 9026.4 | 8553 | 8704.5 | 8133.8 | 8671.8 | 9149 | 9376.7 | 8385.3 | 9202 | 8093.6 | 8905.9 | 8759.2 | 8160.4 | 9267.3 | 8060 | 9316.3 | 8127.7 | 9180.1 | 8536.5 | 9245.6 | 8616.1 | 9631.3 | 8479.4 | 9093 | 8395.7 | 7468.8 | 9235.1 | 8952.8 | 8286.7 | 9636.4 | 9322.9 | 8512.2 | 8404.1 | 9436.8 | 8335.5 | 8716.9 | 9476.1 | 8322.7 | 9572.2 | 8312.9 | 9304.4 | 8554.4 | 9428.2 | 8113.7 | 9502.4 | 8533.1 | 9359.3 | 8501 | 9447.6 | 8669.3 | 8416 | 9294.6 | 8520.8 | 8360.7 | 9404 | 9555.6 | 9350.6 | 8498.1 | 9454.2 | 8434.6 | 9100.8 | 8570.8 | 9088.5 | 7917.4 | 9226.8 | 8331.1 | 8558 | 8541.1 | 8454.6 | 7319.2 | 8340.8 | 7384.4 | 8375.8 | 8393.5 | 9828.8 | 8458.6 | 9862.9 | 8667.4 | 9731.5 | 8502.9 | 8673.6 | 8532.3 | 9467.2 | 9823.5 | 9700.8 | 9634.5 | 9750.2 | 9794.5 | 8734.4 | 9454 | 9747.4 | 9874.3 | 9866.5 | 9821.6 | 9824.7 | 8731.6 | 9857 | 8778.9 | 17.7293 | 17.6583 | 17.7292 | 17.8452 | 17.7314 | 17.6531 | 0 | 25.1686 | 0 | 0 | 25 | 24 | 5.427 | 5.1208 | 4.9777 | 4.7608 | 5.2475 | 5.1178 | 8.975 | 8.6 | 8.9133 | 8.605 | 9.1333 | 9.47 | 3.6915 | 3.7693 | 3.787 | 3.6987 | 3.7606 | 3.7388 | 1.0237 | 1.0992 | 0.93709 | 1.197 | 1.2187 | 0.98576 | 4.8227 | 4.7724 | 4.814 | 4.7931 | 4.7467 | 4.7466 | 0.24601 | 0.26952 | 0.22183 | 0.23675 | 0.23875 | 0.25467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 812985 | 1507 | 799741 | 1536 | 267477.554 | 786.4 | 3.6915 | 3.7693 | 3.787 | 3.6987 | 3.7606 | 3.7388 | 4.8227 | 4.7724 | 4.814 | 4.7931 | 4.7467 | 4.7466 | 714000 | 2000 | 714000 | 1000 | 1422267 | 5200 | 1425000 | 1417067 | 10.3667 | 3.741 | 1.0769 | 4.7826 | 0.24459 | 28.79% | 5.114% | 17.7245 | 24.7229 | 5.1086 | 8.9494 | 1430247.2 | 1404001 | 1596401.2439 | 87.95% | 34 | 0
2024-12-21 | 2025 | 2024 | Year_3 | Year_3 | 2024-12-01 | 31 | 335090.89 | 7:39 | 17:59 | 7353.5 | 7707.1 | 7701.1 | 7678.3 | 7723.5 | 7788.1 | 7712 | 8017.1 | 7668.9 | 7614.7 | 7556.4 | 7698.9 | 7643.2 | 7639.1 | 7694.9 | 7752.8 | 7645.5 | 7716.1 | 7719.3 | 7749.7 | 7712.3 | 7706.2 | 7553.2 | 7642.1 | 7525.5 | 6612.8 | 7520.5 | 7516.4 | 7739.2 | 7654.7 | 7574.3 | 7736.1 | 7715.6 | 7769.7 | 7743.2 | 7695.5 | 7811.3 | 7704.9 | 7747.4 | 7646.6 | 8482.7 | 7509.5 | 8361.6 | 7426.2 | 7903 | 8919.9 | 7346 | 8472.6 | 7588.8 | 7732.8 | 7704.7 | 7258.6 | 7984.9 | 7531.6 | 7987.4 | 7708.2 | 7063.2 | 8172.5 | 7048.3 | 8095.6 | 8008.7 | 7057 | 7736.9 | 7332.9 | 7472.3 | 6993.9 | 7454.6 | 7848.3 | 8059.1 | 7198.8 | 7917.4 | 6951.6 | 7670 | 7540.6 | 7031.2 | 7989.6 | 6948 | 8032.6 | 7002 | 7910.4 | 7310.6 | 7921.7 | 7382.7 | 8248.6 | 7267.9 | 7792.6 | 7198.2 | 6398.3 | 7888.1 | 7665.5 | 7072.1 | 8215.9 | 7949.8 | 7257.9 | 7166.9 | 8058.8 | 7124.3 | 7448.1 | 8114.6 | 7111.5 | 8194.1 | 7102.2 | 7951.3 | 7304.9 | 8050.9 | 6927.6 | 8110 | 7283.5 | 7982 | 7250.3 | 8054.3 | 7392.7 | 7195.7 | 7943.4 | 7280.4 | 7136.6 | 8049.6 | 8173 | 7997.3 | 7291.8 | 8092 | 7225.6 | 7786.9 | 7316.2 | 7762.8 | 6777.5 | 7907.6 | 7142.7 | 7329.2 | 7324.7 | 7252.4 | 6269.6 | 7166.7 | 6350.8 | 7230.7 | 7245.8 | 8458.9 | 7288.4 | 8505.7 | 7473.3 | 8395.4 | 7341.2 | 7479 | 7366.5 | 8156.4 | 8466.6 | 8367.6 | 8312.5 | 8396 | 8433.8 | 7536.3 | 8156.6 | 8399.4 | 8501.3 | 8514.7 | 8469.7 | 8466.3 | 7523.7 | 8494.5 | 7561.5 | 18.5832 | 18.4067 | 18.7424 | 18.5631 | 18.5598 | 18.4399 | 0 | 27.1551 | 0 | 0 | 27 | 26.1 | 3.2513 | 2.4201 | 0.87814 | 1.8077 | 3.0985 | 2.4626 | 5.635 | 5.315 | 4.75 | 4.9983 | 5.4217 | 6.0167 | 3.3136 | 3.3646 | 3.3818 | 3.3194 | 3.3691 | 3.3761 | 0.92528 | 0.98483 | 0.8355 | 1.0754 | 1.0825 | 0.89343 | 4.1647 | 4.1311 | 4.1531 | 4.1536 | 4.1119 | 4.1411 | 0.22437 | 0.24461 | 0.20433 | 0.21887 | 0.21592 | 0.23039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 813597 | 1509 | 800354 | 1538 | 268697.954 | 790.4 | 3.3136 | 3.3646 | 3.3818 | 3.3194 | 3.3691 | 3.3761 | 4.1647 | 4.1311 | 4.1531 | 4.1536 | 4.1119 | 4.1411 | 612000 | 2000 | 613000 | 2000 | 1220400 | 4000 | 1221000 | 1216400 | 10.3333 | 3.3541 | 0.96615 | 4.1426 | 0.22308 | 28.81% | 5.385% | 18.5492 | 26.7517 | 2.3197 | 5.3561 | 1226073.9 | 1196400 | 1365269.3803 | 87.63% | 31 | 0
2024-12-22 | 2025 | 2024 | Year_3 | Year_3 | 2024-12-01 | 31 | 335090.89 | 7:38 | 17:45 | 5793.9 | 6094.6 | 6097.9 | 6069.6 | 6127.1 | 6153.3 | 6100 | 6350.8 | 6075.6 | 6023.5 | 5981.5 | 6096.1 | 6049 | 6038.3 | 6099.5 | 6136.3 | 6049.7 | 6104.5 | 6094.8 | 6118 | 6116.7 | 6094.8 | 5983.2 | 6052 | 5931.6 | 5202.8 | 5930.1 | 5921.4 | 6125 | 6056.3 | 5982.4 | 6118.5 | 6085 | 6110.2 | 6108.4 | 6072.9 | 6164.4 | 6077.5 | 6105.4 | 6035.5 | 6637.3 | 5871.6 | 6536.5 | 5803.1 | 6176.1 | 6982.9 | 5763.5 | 6662.9 | 6017.4 | 6130 | 6098.3 | 5739.4 | 6324.5 | 5983.8 | 6308.6 | 6114.5 | 5578.1 | 6447 | 5573.9 | 6400.6 | 6325.3 | 5578 | 6104.8 | 5762.4 | 5912.1 | 5515.4 | 5873.3 | 6190.4 | 6360.2 | 5674.4 | 6240 | 5463.2 | 6060.6 | 5922 | 5545.9 | 6262.8 | 5448 | 6317.3 | 5501.1 | 6215.2 | 5760.5 | 6230 | 5813.4 | 6498.7 | 5726.8 | 6139.8 | 5677 | 5039.1 | 6203.7 | 6048.9 | 5563.1 | 6470.8 | 6252.8 | 5715 | 5651.9 | 6340 | 5606.6 | 5860.1 | 6408.8 | 5606.2 | 6465.5 | 5591.7 | 6270.3 | 5751.7 | 6341.2 | 5454.9 | 6384.6 | 5733.2 | 6284.1 | 5704.8 | 6349.1 | 5819.8 | 5663.9 | 6248.2 | 5729.6 | 5614.9 | 6343.4 | 6427.5 | 6295.4 | 5740 | 6367.1 | 5682.6 | 6142.5 | 5750.3 | 6103.1 | 5326.4 | 6226.3 | 5619.3 | 5752.3 | 5740.1 | 5697.3 | 4916.6 | 5624.7 | 4968.7 | 5688.4 | 5701.3 | 6665.5 | 5744.6 | 6678.6 | 5875.6 | 6608.7 | 5778.7 | 5886 | 5793.3 | 6401.2 | 6648.5 | 6570.3 | 6530 | 6586 | 6621.3 | 5913.6 | 6394 | 6561.8 | 6645.1 | 6647 | 6628.9 | 6641.8 | 5904.8 | 6654.6 | 5931.3 | 20.48 | 20.25 | 20.45 | 20.6 | 20.27 | 20.21 | 0 | 29.9 | 0 | 0 | 29.62 | 29.21 | 2.24 | 1.09 | 0.47 | 0.44 | 2.11 | 1.36 | 5.35 | 4.88 | 5.44 | 4.92 | 5.29 | 5.23 | 2.8 | 2.84 | 2.83 | 2.8 | 2.82 | 2.82 | 0.79 | 0.81 | 0.7 | 0.9 | 0.88 | 0.72 | 3.31 | 3.31 | 3.28 | 3.3 | 3.27 | 3.27 | 0.2 | 0.21 | 0.18 | 0.19 | 0.19 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 814080 | 1511 | 800837 | 1539 | 269660.221 | 795.733 | 2.8 | 2.84 | 2.83 | 2.8 | 2.82 | 2.82 | 3.31 | 3.31 | 3.28 | 3.3 | 3.27 | 3.27 | 483000 | 2000 | 483000 | 1000 | 962267 | 5333 | 963000 | 956934 | 10.1167 | 2.8183 | 0.8 | 3.29 | 0.195 | 28.39% | 5.927% | 20.3767 | 29.5767 | 1.285 | 5.185 | 965795.7 | 960134 | 1103694 | 86.99% | 27 | 1008
2024-12-23 | 2025 | 2024 | Year_3 | Year_3 | 2024-12-01 | 31 | 335090.89 | 7:42 | 18:00 | 6686.1 | 7018.4 | 7015.5 | 6970.2 | 7049.8 | 7087.2 | 7064.5 | 7310.6 | 6973.2 | 6949.3 | 6868.4 | 6997.1 | 6931.8 | 6931.1 | 6999.6 | 7039.5 | 6948.9 | 7016.7 | 7015.8 | 7034.9 | 7032.1 | 7013.3 | 6873 | 6959.8 | 6832.1 | 6005.3 | 6833.5 | 6828.8 | 7038.5 | 6961.1 | 6886.3 | 7025.2 | 7009.1 | 7039.4 | 7022.3 | 6976.5 | 7085.2 | 6995.5 | 7041.1 | 6957.9 | 7706 | 6843.1 | 7598.6 | 6768.3 | 7210.4 | 8110.2 | 6660.6 | 7696.2 | 6899.7 | 7031.2 | 6992.8 | 6586.7 | 7257.8 | 6842.7 | 7256.6 | 7029.5 | 6407.4 | 7408.7 | 6402.5 | 7344.8 | 7268.4 | 6410 | 7019.5 | 6642.6 | 6800.8 | 6349.8 | 6759.8 | 7114 | 7303.8 | 6518.1 | 7173.5 | 6293 | 6950.9 | 6831.7 | 6362.5 | 7230.8 | 6293.3 | 7280.4 | 6352.4 | 7177.6 | 6612.8 | 7169.8 | 6683.5 | 7464.1 | 6574.9 | 7049.2 | 6524.1 | 5787.8 | 7157 | 6953.8 | 6410.4 | 7460.3 | 7215.7 | 6599.1 | 6526.2 | 7308 | 6450 | 6744.6 | 7356.9 | 6454.5 | 7434 | 6437.4 | 7210.3 | 6618.4 | 7300.4 | 6273.7 | 7350.9 | 6596.4 | 7227.5 | 6559.4 | 7321.5 | 6714.4 | 6524 | 7197 | 6596.1 | 6465.7 | 7296.7 | 7409.5 | 7244.4 | 6614.1 | 7338.9 | 6559.6 | 7071.5 | 6638.9 | 7043.6 | 6137.1 | 7183.2 | 6481.7 | 6647 | 6628.7 | 6590.4 | 5690.9 | 6505.4 | 5743.9 | 6586.4 | 6595.4 | 7653.7 | 6602.9 | 7683.1 | 6750.9 | 7593.2 | 6649.2 | 6779.3 | 6692.4 | 7378.6 | 7666.1 | 7563.3 | 7512.7 | 7581 | 7617.6 | 6807.5 | 7367.4 | 7586.7 | 7630.8 | 7692.8 | 7659.5 | 7655 | 6804.7 | 7675.6 | 6828.4 | 17.49 | 17.38 | 17.47 | 17.7 | 17.51 | 17.51 | 0 | 24.58 | 0 | 0 | 24.6 | 24 | 4.03 | 3.47 | 3.14 | 2.98 | 3.97 | 3.16 | 6.28 | 6.87 | 6.11 | 6.33 | 6.32 | 5.67 | 3.08 | 3.13 | 3.14 | 3.08 | 3.13 | 3.13 | 0.85 | 0.93 | 0.77 | 0.98 | 1.01 | 0.85 | 3.77 | 3.75 | 3.76 | 3.75 | 3.72 | 3.75 | 0.22 | 0.24 | 0.2 | 0.21 | 0.21 | 0.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 814636 | 1513 | 801392 | 1541 | 270767.754 | 800.933 | 3.08 | 3.13 | 3.14 | 3.08 | 3.13 | 3.13 | 3.77 | 3.75 | 3.76 | 3.75 | 3.72 | 3.75 | 556000 | 2000 | 555000 | 2000 | 1107533 | 5200 | 1107000 | 1102333 | 10.3 | 3.115 | 0.89833 | 3.75 | 0.21833 | 28.84% | 5.822% | 17.51 | 24.3933 | 3.4583 | 6.2633 | 1112280.8 | 1082667 | 1245091.0301 | 86.95% | 33 | 0
2024-12-24 | 2025 | 2024 | Year_3 | Year_3 | 2024-12-01 | 31 | 335090.89 | 7:43 | 17:59 | 7078 | 7431.1 | 7415.8 | 7381.3 | 7438.2 | 7489.2 | 7461 | 7767.5 | 7376.7 | 7367.8 | 7267.7 | 7402.3 | 7360.2 | 7344.2 | 7413.6 | 7474.5 | 7347.3 | 7413.4 | 7438.9 | 7464.1 | 7448.6 | 7431.1 | 7293.2 | 7378.1 | 7241.6 | 6360.6 | 7249.9 | 7234.2 | 7466.5 | 7386.9 | 7312.2 | 7463.2 | 7396.6 | 7462.6 | 7453.3 | 7404.2 | 7522.3 | 7433.2 | 7472.1 | 7377.4 | 8189.1 | 7262.1 | 8073.6 | 7180.7 | 7649.9 | 8583.4 | 7074.2 | 8179.1 | 7317 | 7463.3 | 7313.5 | 6581.8 | 7651.3 | 7232.5 | 7690.5 | 7425.6 | 6792.7 | 7847.8 | 6800.6 | 7796.3 | 7704.8 | 6798.1 | 7424.5 | 7027.7 | 7186.6 | 6719.9 | 7161.9 | 7532.1 | 7746.5 | 6911.5 | 7605.7 | 6675.4 | 7371.2 | 7244.1 | 6667.3 | 7395.8 | 6665.7 | 7717.2 | 6717.7 | 7587 | 6999.7 | 7562.3 | 7082.4 | 7897.6 | 6964.3 | 7473.5 | 6894.6 | 6134.6 | 7534.8 | 7351.3 | 6796.9 | 7904.7 | 7644.6 | 6984.5 | 6899.8 | 7741.5 | 6558.2 | 7065.7 | 7801.7 | 6849 | 7888.2 | 6836.9 | 7655.2 | 7035.4 | 7737.9 | 6599.6 | 7737.5 | 7004.5 | 7685.8 | 6920.1 | 7763.4 | 7120.4 | 6879.5 | 7592.7 | 6893.6 | 6803.2 | 7645.2 | 7829.9 | 7696.5 | 7014 | 7785.7 | 6951 | 7506.7 | 7049 | 7269.8 | 6479.7 | 7610 | 6865.8 | 7054.2 | 7020.3 | 6983.7 | 6034.1 | 6858.6 | 6024.3 | 6653.6 | 6863.2 | 8085.2 | 6974.8 | 8105 | 7124 | 8022.2 | 7025.9 | 7137.5 | 6982.1 | 7787.4 | 8091.5 | 7987.9 | 7929.4 | 8013.7 | 8052.1 | 7180.4 | 7774 | 8004.3 | 8080.7 | 8122.6 | 8091.9 | 8087.4 | 7182.5 | 7943.9 | 7183.8 | 16.07 | 15.94 | 16.02 | 16.17 | 16.01 | 15.99 | 0 | 22.49 | 0 | 0 | 22.2 | 21.3 | 4.81 | 4.76 | 4.36 | 4.06 | 4.76 | 4.65 | 7.79 | 7.81 | 7.67 | 7.35 | 7.98 | 8.48 | 3.19 | 3.25 | 3.27 | 3.19 | 3.25 | 3.2 | 0.86 | 0.95 | 0.78 | 0.99 | 1.04 | 0.86 | 3.97 | 3.94 | 3.95 | 3.93 | 3.89 | 3.91 | 0.22 | 0.24 | 0.2 | 0.22 | 0.21 | 0.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 815225 | 1514 | 801979 | 1543 | 271937.755 | 806.067 | 3.19 | 3.25 | 3.27 | 3.19 | 3.25 | 3.2 | 3.97 | 3.94 | 3.95 | 3.93 | 3.89 | 3.91 | 589000 | 1000 | 587000 | 2000 | 1170001 | 5134 | 1173000 | 1164867 | 10.2667 | 3.225 | 0.91333 | 3.9317 | 0.22 | 28.32% | 5.596% | 16.0333 | 21.9967 | 4.5667 | 7.8467 | 1175347.4 | 1149200 | 1321543.624 | 86.96% | 26 | 0
2024-12-25 | 2025 | 2024 | Year_3 | Year_3 | 2024-12-01 | 31 | 335090.89 | 7:39 | 18:01 | 8459.3 | 8850.7 | 8820.3 | 8792.5 | 8846.8 | 8905.9 | 8857.2 | 9259.3 | 8845.9 | 8836.8 | 8666.2 | 8850.6 | 8763.2 | 8751.9 | 8812.6 | 8888.8 | 8773.2 | 8849.4 | 8859.6 | 8897.1 | 8850.8 | 8838.1 | 8657.4 | 8769 | 8625.5 | 7583.3 | 8642 | 8616 | 8868.6 | 8761.2 | 8676.3 | 8865.6 | 8859.8 | 8936 | 8878.1 | 8821.8 | 8961.9 | 8845.2 | 8894.4 | 8758.4 | 9677.8 | 8560.2 | 9536.6 | 8483 | 9036 | 10179.8 | 8365.5 | 9662.5 | 8697.4 | 8874.6 | 8851.2 | 8339.4 | 9175.5 | 8623.2 | 9175.3 | 8812.8 | 8112.8 | 9372.2 | 8115.3 | 9312.9 | 9209 | 8120 | 8884 | 8412.1 | 8580.2 | 8009.5 | 8550.4 | 8959.3 | 9241.6 | 8234.4 | 9062.3 | 7943.9 | 8789.8 | 8622.3 | 8052.2 | 9136.3 | 7943.1 | 9206.7 | 8010.2 | 9055.1 | 8329.2 | 9026.5 | 8424.5 | 9382.4 | 8276.2 | 8872.3 | 8190.2 | 7285 | 9070.2 | 8723 | 8107.7 | 9426.8 | 9089.3 | 8302.3 | 8195 | 9230.5 | 8174.5 | 8507.8 | 9271.6 | 8132.3 | 9357.3 | 8118.8 | 9079.1 | 8364.3 | 9190.7 | 7920.4 | 9262.9 | 8321.9 | 9110.7 | 8278.9 | 9203.8 | 8436.1 | 8227.3 | 9086.8 | 8330.4 | 8164.8 | 9202.2 | 9318.9 | 9139.9 | 8298.9 | 9223.5 | 8233.7 | 8896.2 | 8362.7 | 8862.9 | 7708.3 | 9001 | 8123.4 | 8385.4 | 8411.4 | 8269.2 | 7164.9 | 8178.4 | 7210 | 8217.4 | 8235 | 9592 | 8264.5 | 9634.2 | 8458.8 | 9533.4 | 8356.1 | 8511.1 | 8353.3 | 9292.7 | 9648.8 | 9516.2 | 9440 | 9541.3 | 9572 | 8540.7 | 9257.3 | 9573.8 | 9703.1 | 9716.6 | 9678 | 9671.2 | 8583.1 | 9671.8 | 8620 | 17.64 | 17.38 | 17.74 | 17.57 | 17.47 | 17.36 | 0 | 25.91 | 0 | 0 | 25.6 | 24.7 | 4.74 | 4.58 | 3.47 | 4.37 | 4.78 | 4.49 | 7.21 | 7.48 | 6.59 | 7.67 | 8.33 | 7.31 | 3.65 | 3.71 | 3.72 | 3.66 | 3.71 | 3.66 | 0.99 | 1.06 | 0.89 | 1.16 | 1.17 | 0.96 | 4.75 | 4.69 | 4.68 | 4.72 | 4.63 | 4.66 | 0.24 | 0.26 | 0.21 | 0.23 | 0.23 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 815926 | 1516 | 802677 | 1544 | 273331.555 | 811.133 | 3.65 | 3.71 | 3.72 | 3.66 | 3.71 | 3.66 | 4.75 | 4.69 | 4.68 | 4.72 | 4.63 | 4.66 | 701000 | 2000 | 698000 | 1000 | 1393800 | 5066 | 1396000 | 1388734 | 10.3667 | 3.685 | 1.0383 | 4.6883 | 0.23667 | 28.18% | 5.048% | 17.5267 | 25.4033 | 4.405 | 7.4317 | 1401927.9 | 1377267 | 1563384.4 | 88.1% | 26 | 0
2024-12-26 | 2025 | 2024 | Year_3 | Year_3 | 2024-12-01 | 31 | 335090.89 | 7:42 | 17:55 | 4804.9 | 5029 | 5035.3 | 5019.3 | 5057.2 | 5088 | 5068.7 | 5284.1 | 5044 | 5024.5 | 4958.2 | 5043.1 | 5025.4 | 5002.3 | 5068.9 | 5101.7 | 5027.6 | 5073.9 | 5083.2 | 5097.6 | 5108.8 | 5093.2 | 5011.8 | 5054.2 | 4973.9 | 4352.9 | 4957.4 | 4952.9 | 5124.7 | 5086.2 | 5047.8 | 5136 | 5106.8 | 5138.4 | 5124.2 | 5088.6 | 5164.8 | 5112.1 | 5143.5 | 5086.5 | 5639.9 | 5026.2 | 5582.5 | 4966.7 | 5292 | 5950.3 | 4877.7 | 5633.7 | 5022.2 | 5109.7 | 5079.6 | 4779.5 | 5269.5 | 4978.2 | 5260.6 | 5104.2 | 4630.3 | 5347.3 | 4643 | 5322.5 | 5255.9 | 4641 | 5036.3 | 4761.5 | 4908.2 | 4581.2 | 4875.4 | 5126.4 | 5279.4 | 4694.2 | 5171.4 | 4523.5 | 5039.1 | 4918.6 | 4610 | 5206.8 | 4527.4 | 5274.7 | 4587.9 | 5172.1 | 4754.5 | 5144.3 | 4819 | 5365.8 | 4746.1 | 5097.5 | 4709 | 4189.2 | 5228.5 | 5030 | 4659.1 | 5432.7 | 5242 | 4790.8 | 4733.8 | 5321.6 | 4718.8 | 4918.5 | 5376.4 | 4693.4 | 5423.1 | 4686.7 | 5264.1 | 4821.9 | 5325.3 | 4567.9 | 5356.9 | 4788.7 | 5275.9 | 4782.8 | 5307.1 | 4856.5 | 4744.5 | 5218.9 | 4789.9 | 4687.2 | 5301.7 | 5345.3 | 5248.8 | 4782.3 | 5296.3 | 4719.2 | 5122.6 | 4783.1 | 5067.6 | 4417.2 | 5172.1 | 4657.5 | 4806.3 | 4818.2 | 4736.3 | 4100.4 | 4709.8 | 4159.6 | 4791.8 | 4799.9 | 5581.5 | 4804.5 | 5611.8 | 4916.8 | 5534.2 | 4849.7 | 4933.8 | 4865.6 | 5408.5 | 5627.4 | 5545.4 | 5510.1 | 5541.3 | 5561.3 | 4986.3 | 5402.3 | 5572 | 5635.1 | 5665.9 | 5641.2 | 5637.1 | 5001.8 | 5629.2 | 5014.1 | 18.0287 | 17.8772 | 18.091 | 18.0574 | 17.9167 | 17.9527 | 0 | 23.3987 | 0 | 0 | 23.2065 | 22.9 | 3.8404 | 3.725 | 2.8493 | 2.4714 | 3.708 | 3.5388 | 6.7117 | 6.3417 | 6.2867 | 6.365 | 6.425 | 5.9 | 2.3691 | 2.4173 | 2.4504 | 2.3591 | 2.3971 | 2.4319 | 0.65582 | 0.67591 | 0.5903 | 0.73644 | 0.73884 | 0.61326 | 2.6811 | 2.6985 | 2.724 | 2.6607 | 2.6591 | 2.6933 | 0.15776 | 0.17332 | 0.14643 | 0.15867 | 0.15308 | 0.16682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 816330 | 1518 | 803081 | 1546 | 274136.155 | 816.333 | 2.3691 | 2.4173 | 2.4504 | 2.3591 | 2.3971 | 2.4319 | 2.6811 | 2.6985 | 2.724 | 2.6607 | 2.6591 | 2.6933 | 404000 | 2000 | 404000 | 2000 | 804600 | 5200 | 804000 | 799400 | 10.2167 | 2.4041 | 0.66843 | 2.6861 | 0.15935 | 27.8% | 5.932% | 17.9873 | 23.1684 | 3.3555 | 6.3383 | 807689.5 | 759800 | 865957.2587 | 87.74% | 30 | 24246
2024-12-27 | 2025 | 2024 | Year_3 | Year_3 | 2024-12-01 | 31 | 335090.89 | 7:46 | 18:02 | 5867 | 6207.4 | 6229.7 | 6173.2 | 6276.3 | 6337.9 | 6307.9 | 6594 | 6170 | 6107.7 | 6127.8 | 6206.2 | 6238 | 6201.5 | 6315.4 | 6339.8 | 6280 | 6345.5 | 6330.8 | 6338.7 | 6369.8 | 6342.6 | 6258.7 | 6313.3 | 6142.8 | 5396.7 | 6145.9 | 6151.2 | 6386 | 6350 | 6286.8 | 6389.4 | 6350.6 | 6383.9 | 6358.5 | 6325.6 | 6436.1 | 6376.2 | 6412.7 | 6326.9 | 7063.1 | 6277.9 | 6981.3 | 6207.4 | 6624 | 7441.2 | 6113.2 | 7050.4 | 6182.5 | 6289.1 | 6274 | 5900.6 | 6530.1 | 6163 | 6492.9 | 6295.1 | 5692.3 | 6577.2 | 5710.9 | 6535.1 | 6436.8 | 5685 | 6167.2 | 5808.6 | 6035.1 | 5638.9 | 5996.2 | 6310 | 6482.2 | 5774.4 | 6351.1 | 5558.5 | 6166.3 | 6024.6 | 5625.2 | 6356.5 | 5515.9 | 6416.8 | 5576.2 | 6285.8 | 5836.1 | 6308.7 | 5903.8 | 6602.6 | 5831.6 | 6262.3 | 5806.1 | 5154.2 | 6462.1 | 6201.1 | 5770.4 | 6739.7 | 6508.8 | 5951.4 | 5886.2 | 6605.7 | 5862.7 | 6115.3 | 6687.9 | 5846.9 | 6772.9 | 5852.1 | 6581.9 | 6032.8 | 6677.5 | 5730.2 | 6724 | 6025.5 | 6623.1 | 6017.5 | 6704.8 | 6134 | 5913.9 | 6537.8 | 6000.7 | 5882.2 | 6658.6 | 6720.9 | 6606.3 | 6005.4 | 6674.9 | 5960 | 6465.7 | 6058.4 | 6428.9 | 5595.7 | 6536 | 5891.7 | 6033.1 | 6024 | 6006.5 | 5169.4 | 5885 | 5188.3 | 5856.3 | 5859.9 | 6746.2 | 5830.1 | 6745.5 | 5938.3 | 6710.8 | 5877.1 | 5998.7 | 5919.3 | 6456.4 | 6715.1 | 6635.5 | 6589.7 | 6656 | 6697.5 | 5970.9 | 6455.1 | 6624.2 | 6694 | 6691.2 | 6675.6 | 6685.1 | 5946.6 | 6720.2 | 5969 | 18.6965 | 18.6005 | 18.6545 | 18.8004 | 18.6855 | 18.6623 | 0 | 24.2011 | 0 | 0 | 23.503 | 23.3 | 4.7991 | 4.6492 | 4.1119 | 3.2348 | 4.5122 | 4.4536 | 8.65 | 8.2467 | 8.21 | 7.8017 | 8.8867 | 8.055 | 2.8208 | 2.8902 | 2.9426 | 2.7904 | 2.9022 | 2.7822 | 0.73727 | 0.84379 | 0.67754 | 0.84576 | 0.92142 | 0.74785 | 3.3413 | 3.385 | 3.4237 | 3.2923 | 3.3491 | 3.2577 | 0.21066 | 0.23341 | 0.19562 | 0.21026 | 0.20932 | 0.21712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 816829 | 1520 | 803580 | 1548 | 275130.155 | 821.4 | 2.8208 | 2.8902 | 2.9426 | 2.7904 | 2.9022 | 2.7822 | 3.3413 | 3.385 | 3.4237 | 3.2923 | 3.3491 | 3.2577 | 499000 | 2000 | 499000 | 2000 | 994000 | 5067 | 994000 | 988933 | 10.2667 | 2.8547 | 0.79561 | 3.3415 | 0.21273 | 27.87% | 6.366% | 18.6833 | 23.6681 | 4.2935 | 8.3083 | 997238.7 | 974733 | 1120403.5774 | 87% | 27 | 11889
2024-12-28 | 2025 | 2024 | Year_3 | Year_3 | 2024-12-01 | 31 | 335090.89 | 7:34 | 18:08 | 9469 | 9914.4 | 9881 | 9851.4 | 9915.6 | 10033.6 | 9961.7 | 10403.2 | 9861.3 | 9806.5 | 9729.7 | 9900.1 | 9847.6 | 9835 | 9862 | 9955.3 | 9825.3 | 9926.5 | 9934.2 | 9986.8 | 9893.6 | 9896.1 | 9690.7 | 9821 | 9583.6 | 8484 | 9677.6 | 9647.8 | 9943.6 | 9830.1 | 9716.4 | 9930 | 9899.4 | 9993.4 | 9928.2 | 9874.9 | 10043.3 | 9919.3 | 9968 | 9791.3 | 10831.4 | 9547.2 | 10680.2 | 9472.5 | 10090.8 | 11357.5 | 9402 | 10817.1 | 9692.9 | 9884.3 | 9888.5 | 9332 | 10259.5 | 9647.7 | 10239.6 | 9804 | 9058.9 | 10461.7 | 9057.3 | 10392.2 | 10271.1 | 9052.7 | 9913.4 | 9394.5 | 9604.7 | 8988.8 | 9561 | 10056.1 | 10317 | 9236 | 10128.9 | 8897.8 | 9797.7 | 9634.5 | 8995.4 | 10202.5 | 8881.6 | 10271.4 | 8959.8 | 10110.7 | 9343.2 | 10117.5 | 9452 | 10535.8 | 9293.5 | 9944.5 | 9180.5 | 8162.4 | 10148.3 | 9730.7 | 9074.6 | 10551.3 | 10185.9 | 9296.8 | 9165.3 | 10290.2 | 9082.3 | 9505 | 10341.2 | 9092.8 | 10486.5 | 9077.8 | 10148.7 | 9336.4 | 10291.1 | 8854.5 | 10358.9 | 9302 | 10190.4 | 9258.8 | 10282.3 | 9430.1 | 9178.3 | 10150.4 | 9301.3 | 9123.4 | 10256.8 | 10400.2 | 10199.7 | 9233 | 10275.4 | 9183.7 | 9932.1 | 9349.4 | 9906.7 | 8596.3 | 10024.6 | 9045.9 | 9329.1 | 9335.8 | 9225.1 | 7973.2 | 9123 | 8082.5 | 9177.1 | 9198.1 | 10719.6 | 9230.3 | 10744.4 | 9451.5 | 10650.7 | 9314.9 | 9485.6 | 9321 | 10381 | 10772.3 | 10618.4 | 10523.2 | 10656.7 | 10697.8 | 9514.4 | 10328.1 | 10768.8 | 10828.3 | 10864 | 10812.9 | 10801 | 9581.8 | 10826.8 | 9615.9 | 18.55 | 18.25 | 18.56 | 18.48 | 18.47 | 18.2 | 0 | 29.6 | 0 | 0 | 30.6 | 29 | 2.58 | 2.41 | 1.59 | 0.74 | 2.49 | 1.79 | 4.73 | 4.99 | 4.27 | 4.6 | 4.84 | 4.92 | 4.05 | 4.08 | 4.08 | 4.02 | 4.08 | 3.99 | 1.09 | 1.17 | 0.97 | 1.27 | 1.29 | 1.04 | 5.37 | 5.31 | 5.29 | 5.35 | 5.23 | 5.24 | 0.25 | 0.27 | 0.22 | 0.24 | 0.24 | 0.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 817613 | 1522 | 804360 | 1549 | 276687.7 | 826.533 | 4.05 | 4.08 | 4.08 | 4.02 | 4.08 | 3.99 | 5.37 | 5.31 | 5.29 | 5.35 | 5.23 | 5.24 | 784000 | 2000 | 780000 | 1000 | 1557545 | 5133 | 1561000 | 1552412 | 10.5667 | 4.05 | 1.1383 | 5.2983 | 0.24667 | 28.11% | 4.656% | 18.4183 | 29.7333 | 1.9333 | 4.725 | 1567247.2 | 1544100 | 1739033.5518 | 88.79% | 24 | 0
2024-12-29 | 2025 | 2024 | Year_3 | Year_3 | 2024-12-01 | 31 | 335090.89 | 7:35 | 18:09 | 9738.4 | 10196.6 | 10153.3 | 10137.4 | 10169.1 | 10281.8 | 10224.5 | 10658.9 | 10134 | 10094.1 | 10001.5 | 10183.8 | 10102.6 | 10115.9 | 10112.6 | 10193.9 | 10077.4 | 10176.1 | 10176 | 10233.8 | 10150.7 | 10142.7 | 9931.9 | 10065.2 | 9895.8 | 8710.7 | 9932.1 | 9897.4 | 10190.1 | 10074.3 | 9957.9 | 10179 | 7706.9 | 7782.2 | 7725.9 | 7681.5 | 7804.6 | 7704.4 | 7742.1 | 7605.1 | 6479.8 | 5706.6 | 6383.1 | 5677.7 | 6034.2 | 6724.4 | 5614.8 | 6469.3 | 9951.9 | 10156.1 | 10163.2 | 9594.4 | 10541.4 | 9909 | 10522.7 | 10063.6 | 9326.3 | 10787.9 | 9307.9 | 10691.7 | 10574.3 | 9310.4 | 10259.2 | 9736.4 | 9894.3 | 9277.1 | 9854.5 | 10382.4 | 10635.9 | 9531.3 | 10453.1 | 9192.2 | 10103.2 | 9949.8 | 9279.5 | 10531.5 | 9159.5 | 10603.5 | 9245.4 | 10463.8 | 9659.1 | 10463.1 | 9772.4 | 10889.9 | 9603.9 | 10285.7 | 9474.9 | 8425.2 | 10455.6 | 10042 | 9347.9 | 10855.9 | 10484.6 | 9581.3 | 9454.4 | 10592.8 | 9367.4 | 9800.4 | 10650 | 9375.3 | 10793.8 | 9345.6 | 10457.6 | 9617.6 | 10589.5 | 9111.9 | 10668.1 | 9587 | 10502.6 | 9542.1 | 10603 | 9725.9 | 9479.2 | 10484.5 | 9590.8 | 9414.3 | 10575.8 | 10749.8 | 10513.6 | 9545 | 10610.1 | 9475.4 | 10237.4 | 9652.3 | 10220.5 | 8869 | 10339.7 | 9351.2 | 9648.5 | 9658 | 9521.4 | 8240.2 | 9427.7 | 8343.8 | 9473.1 | 9496.4 | 11071.7 | 9535.1 | 11112.5 | 9770 | 11023.2 | 9654.4 | 9832.2 | 9645.1 | 10730.8 | 11129.9 | 10972.1 | 10872.9 | 11017.7 | 11056.1 | 9851.2 | 10675 | 11141 | 11196.6 | 11220.2 | 11172.2 | 11166.8 | 9909 | 11186.7 | 9943.3 | 18.73 | 18.27 | 18.7 | 18.55 | 18.38 | 18.15 | 0 | 28.3 | 0 | 0 | 28.9 | 27.5 | 3.65 | 3.02 | 2.79 | 2.4 | 3.71 | 3.09 | 7.81 | 7.1 | 6.98 | 6.72 | 7.46 | 6.98 | 4.13 | 4.14 | 4.16 | 4.1 | 4.16 | 4.08 | 1.11 | 1.18 | 0.99 | 1.29 | 1.31 | 1.07 | 5.49 | 5.4 | 5.42 | 5.47 | 5.35 | 5.37 | 0.25 | 0.27 | 0.22 | 0.24 | 0.24 | 0.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 818364 | 1524 | 805165 | 1551 | 278237.155 | 831.8 | 4.13 | 4.14 | 4.16 | 4.1 | 4.16 | 4.08 | 5.49 | 5.4 | 5.42 | 5.47 | 5.35 | 5.37 | 751000 | 2000 | 805000 | 2000 | 1549455 | 5267 | 1552000 | 1544188 | 10.5667 | 4.1283 | 1.1583 | 5.4167 | 0.24833 | 28.06% | 4.585% | 18.4633 | 28.2333 | 3.11 | 7.175 | 1559515.4 | 1528067 | 1776684.7862 | 86.01% | 20 | 0
2024-12-30 | 2025 | 2024 | Year_3 | Year_3 | 2024-12-01 | 31 | 335090.89 | 7:36 | 18:07 | 10641.2 | 11064.7 | 11036.4 | 11021.4 | 11050.1 | 11150.8 | 11060.1 | 11367.7 | 11016.4 | 10995.1 | 10900.3 | 11065.5 | 10993.6 | 11002.8 | 10986.9 | 11074.5 | 10959.9 | 10987.9 | 11050.8 | 11109.7 | 11025.8 | 11022.8 | 10814.7 | 10952 | 10804 | 9526.8 | 10831 | 10794.5 | 11051.7 | 10937.6 | 10829.6 | 11027.8 | 11159.3 | 11237 | 11160.4 | 11097.6 | 11161 | 11040.2 | 11076.4 | 10873.5 | 11846.6 | 10701 | 11700.7 | 10651.2 | 11243.6 | 12277.7 | 10537.5 | 11808.9 | 10836.5 | 11038.9 | 11007.9 | 10308.1 | 11069.8 | 10702.2 | 11355.5 | 10917.3 | 10215.8 | 11583.9 | 10202.1 | 11511.1 | 11402.6 | 10211.2 | 11152.4 | 10671.4 | 10800.5 | 10155.4 | 10779.1 | 11217.9 | 11387.1 | 10424.2 | 11301.7 | 10053.4 | 10954.1 | 10616 | 10109.6 | 11137.4 | 9998.1 | 11398.4 | 10112.2 | 11294.1 | 10531.3 | 11278.5 | 10643.7 | 11636.9 | 10473.9 | 11121.4 | 10328.4 | 9185.7 | 10873.4 | 10818.5 | 10175.4 | 11578.9 | 11254 | 10410.6 | 10269.7 | 11364.8 | 9806.2 | 10596.3 | 11388.8 | 10201.4 | 11525.3 | 10160.6 | 11248.9 | 10461.9 | 11255 | 9496 | 10962.8 | 10380.9 | 11282.5 | 10386 | 11381.8 | 10578.2 | 10254.8 | 10791.9 | 10175.9 | 10123 | 10896 | 11342.1 | 11269.1 | 10349.2 | 11337.5 | 10278.4 | 11031.5 | 10486.2 | 11041.9 | 9631.8 | 11120.9 | 10152.3 | 10493.6 | 10489 | 10341.4 | 8952 | 10225.4 | 8631.1 | 9729.8 | 9807.1 | 11769.2 | 10399.9 | 11796.8 | 10656.4 | 11720.1 | 10522.8 | 10701.6 | 10502.7 | 11504.5 | 11815.6 | 11703.1 | 11612.9 | 11742 | 11769.3 | 10733.6 | 11458 | 11825.5 | 11870.9 | 11875.9 | 11847.5 | 11857.3 | 10792 | 11502.3 | 10822.6 | 16.4 | 15.88 | 16.49 | 16.25 | 16.23 | 16.03 | 0 | 30.17 | 0 | 0 | 29.5 | 28.3 | 2.69 | 1.45 | 2.61 | 1.29 | 2.69 | 1.99 | 4.6 | 4.67 | 4.65 | 4.55 | 5.03 | 4.96 | 4.42 | 4.43 | 4.44 | 4.37 | 4.45 | 4.37 | 1.15 | 1.24 | 1.08 | 1.35 | 1.37 | 1.12 | 5.96 | 5.84 | 5.86 | 5.92 | 5.77 | 5.82 | 0.26 | 0.28 | 0.23 | 0.24 | 0.25 | 0.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 819238 | 1526 | 806027 | 1553 | 279964.955 | 835.933 | 4.42 | 4.43 | 4.44 | 4.37 | 4.45 | 4.37 | 5.96 | 5.84 | 5.86 | 5.92 | 5.77 | 5.82 | 874000 | 2000 | 862000 | 2000 | 1727800 | 4133 | 1732000 | 1723667 | 10.5167 | 4.4133 | 1.2183 | 5.8617 | 0.25667 | 27.61% | 4.379% | 16.2133 | 29.3233 | 2.12 | 4.7433 | 1740464.7 | 1700333 | 1909447.838 | 89.05% | 22 | 1833
2024-12-31 | 2025 | 2024 | Year_3 | Year_3 | 2024-12-01 | 31 | 335090.89 | 7:35 | 18:04 | 10195.5 | 10623.2 | 10589.2 | 10586.6 | 10611.5 | 10683.6 | 10604 | 10972.7 | 10567.2 | 10562.2 | 10430.5 | 10601.8 | 10536.1 | 10536.8 | 10529.7 | 10624.8 | 10506.2 | 10600.9 | 10608.4 | 10667.5 | 10576.7 | 10576.7 | 10378 | 10505.2 | 10356.9 | 9138.1 | 10384.8 | 10349.6 | 10615 | 10514.9 | 10400.3 | 10595.3 | 10675 | 10755.8 | 10679.1 | 10625.5 | 10727 | 10604.1 | 10650.7 | 10445.8 | 11402.4 | 10253 | 11261.2 | 10194.1 | 10788.2 | 11837.7 | 10095.9 | 11373.1 | 10385.5 | 10583 | 10601.6 | 10052.9 | 10926.1 | 10364.1 | 10915 | 10483 | 9773.9 | 11126.4 | 9764.1 | 11056.2 | 10954.8 | 9768.5 | 10691.2 | 10202.6 | 10331.6 | 9711 | 10304 | 10753.8 | 10864.7 | 9949.8 | 10828.7 | 9612.5 | 10531.3 | 10378.2 | 9724.8 | 10895.9 | 9601.6 | 10961.2 | 9688.1 | 10857.2 | 10064.2 | 10818.2 | 10169.3 | 11168.4 | 10006.7 | 10655.2 | 9866.8 | 8792 | 10812.8 | 10418.2 | 9752.6 | 11145.9 | 10817 | 9978.8 | 9849 | 10914.9 | 9792.4 | 10205.8 | 10980.7 | 9776.6 | 11082.3 | 9747.4 | 10823.3 | 10034.9 | 10919.1 | 9514.3 | 10999.3 | 9994.8 | 10871.9 | 9968.6 | 10952.3 | 10140.2 | 9871.8 | 10825.1 | 9994.7 | 9817.5 | 10892.8 | 11049.8 | 10857 | 9921.1 | 10924.7 | 9852.3 | 10612.2 | 10053.2 | 10619.4 | 9243.3 | 10694 | 9728.2 | 10045.9 | 10055.6 | 9892.4 | 8582.2 | 9868.1 | 8736.8 | 9916.8 | 9928.3 | 11338.6 | 9952.2 | 11362.6 | 10199 | 11278.8 | 10053.1 | 10234.3 | 10047.7 | 11072.8 | 11380.7 | 11272.3 | 11186.7 | 11304.9 | 11329 | 10276 | 11018 | 11396.1 | 11438.5 | 11455.3 | 11415.8 | 11422.2 | 10332.4 | 11441.5 | 10382.4 | 19.7713 | 19.364 | 19.8485 | 19.5482 | 19.5322 | 19.3528 | 0 | 32.9067 | 0 | 0 | 32.8 | 31.2 | 2.5189 | 1.8678 | 1.8824 | 0.8491 | 2.5914 | 1.7988 | 5.1667 | 5.1817 | 4.9133 | 5.5067 | 6.005 | 4.9717 | 4.3047 | 4.3285 | 4.3179 | 4.2598 | 4.3283 | 4.2692 | 1.1367 | 1.1926 | 1.0623 | 1.3256 | 1.3124 | 1.0703 | 5.714 | 5.6253 | 5.6313 | 5.6947 | 5.5666 | 5.5859 | 0.25965 | 0.28243 | 0.22959 | 0.24902 | 0.248 | 0.27698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 820076 | 1528 | 806861 | 1554 | 281630.222 | 841.133 | 4.3047 | 4.3285 | 4.3179 | 4.2598 | 4.3283 | 4.2692 | 5.714 | 5.6253 | 5.6313 | 5.6947 | 5.5666 | 5.5859 | 838000 | 2000 | 834000 | 1000 | 1665267 | 5200 | 1669000 | 1660067 | 10.4833 | 4.3014 | 1.1833 | 5.6363 | 0.25761 | 27.51% | 4.571% | 19.5695 | 32.3022 | 1.9181 | 5.2908 | 1676649.8 | 1650000 | 1836959.0219 | 89.82% | 18 | 831
2025-01-01 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 335090.89 | 7:33 | 18:05 | 9971.1 | 10453.3 | 10412.5 | 10387.5 | 10443 | 10536.4 | 10442.7 | 10860.1 | 10374.5 | 10375.4 | 10240.5 | 10422.6 | 10353.2 | 10362.6 | 10323.8 | 10442.1 | 10315.8 | 10428.3 | 10449.5 | 10505.9 | 10406.9 | 10401.9 | 10177.3 | 10326.3 | 10154.2 | 8920.7 | 10185 | 10152.6 | 10455.7 | 10336.3 | 10198.1 | 10426.3 | 10454.6 | 10533.3 | 10456.1 | 10402.8 | 10581.4 | 10432.9 | 10487.6 | 10292.6 | 11382.7 | 10040.8 | 11224.5 | 9976.2 | 10615.8 | 11866.7 | 9887.9 | 11354 | 9523.8 | 9726.1 | 9743.7 | 9203.8 | 10102.6 | 9516 | 10089 | 9626 | 9559.4 | 11048.8 | 9542.7 | 10958.2 | 10839 | 9546.1 | 10543.5 | 10008.6 | 10127.4 | 9488.3 | 10085.1 | 10591.1 | 10881.2 | 9731.2 | 10690.6 | 9388.8 | 10333.8 | 10169.7 | 9494.2 | 10768 | 9382.2 | 10840 | 9450.5 | 10699.5 | 9844.4 | 10669.8 | 9948.8 | 11092.6 | 9788.3 | 10479.3 | 9651.6 | 8581.8 | 10647.4 | 10213.2 | 9521.8 | 11063.7 | 10686.1 | 9777.8 | 9652.9 | 10795.1 | 9554.6 | 9974 | 10857 | 9536.6 | 10974.4 | 9514.1 | 10644.7 | 9793 | 10785.9 | 9277.8 | 10863.2 | 9753.4 | 10695.9 | 9715.1 | 10794 | 9891.1 | 9637.9 | 10641.5 | 9748.6 | 9569.1 | 10739.8 | 10900.4 | 10680.4 | 9661.1 | 10760.4 | 9601.6 | 10397.8 | 9798.5 | 10401.9 | 9000.3 | 10483.2 | 9476.1 | 9790.7 | 9807 | 9631.9 | 8360.6 | 9608.1 | 8494.4 | 9685.2 | 9703 | 11281.2 | 9724.3 | 11321.4 | 9975.9 | 11221.5 | 9834.6 | 10016.4 | 9834.3 | 10947.5 | 11345.5 | 11189 | 11093.1 | 11235.9 | 11270.4 | 10057.3 | 10898.9 | 11339.7 | 11399.5 | 11425.4 | 11377.6 | 11382.1 | 10114.4 | 11394.9 | 10156.5 | 20.85 | 20.2 | 20.47 | 20.42 | 20.31 | 19.99 | 0 | 32.2 | 0 | 0 | 32.76 | 31.3 | 2.62 | 1.78 | 2.03 | 0.67 | 2.3 | 1.87 | 4.79 | 5.22 | 4.74 | 4.26 | 5.09 | 5.1 | 4.19 | 4.23 | 4.21 | 4.18 | 4.24 | 4.23 | 1.1 | 1.17 | 1.03 | 1.28 | 1.28 | 1.05 | 5.63 | 5.56 | 5.53 | 5.63 | 5.51 | 5.53 | 0.24 | 0.26 | 0.21 | 0.23 | 0.22 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 820896 | 1529 | 807680 | 1556 | 283262.755 | 846.2 | 4.19 | 4.23 | 4.21 | 4.18 | 4.24 | 4.23 | 5.63 | 5.56 | 5.53 | 5.63 | 5.51 | 5.53 | 820000 | 1000 | 819000 | 2000 | 1632533 | 5067 | 1636000 | 1627466 | 10.5333 | 4.2133 | 1.1517 | 5.565 | 0.235 | 27.33% | 4.223% | 20.3733 | 32.0867 | 1.8783 | 4.8667 | 1643387.1 | 1631500 | 1820110 | 89.64% | 22 | 0
2025-01-02 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 335090.89 | 7:34 | 18:10 | 9059.7 | 9478.7 | 9421.6 | 9403.5 | 9448.3 | 9531.5 | 9469.5 | 9832.6 | 9411.9 | 9414.7 | 9298.5 | 9446.6 | 9389.9 | 9385.4 | 9364.8 | 9468.5 | 9346.2 | 9444.9 | 9457.8 | 9510.1 | 9432 | 9430.8 | 9255.6 | 9365.5 | 9216 | 8132.8 | 9239.4 | 9209.4 | 9474.8 | 9372.8 | 9262.4 | 9446.4 | 9491.1 | 9552.3 | 9513.5 | 9459.4 | 9562.1 | 9438.3 | 9478 | 9336.4 | 10225.9 | 9143.7 | 10098.9 | 9072.4 | 9611.7 | 10652.7 | 8994.7 | 10204 | 9266.4 | 9446.2 | 9434.1 | 8699.4 | 9764.7 | 9245.6 | 9745.8 | 9361 | 8708.4 | 9962.3 | 8698.5 | 9888.7 | 9786.6 | 8699.8 | 9543.2 | 9085.8 | 9219.7 | 8661 | 9175.5 | 9606.3 | 9832.1 | 8879.4 | 9677.3 | 8582.4 | 9394.9 | 9259.1 | 8676 | 9746.3 | 8573.7 | 9810.1 | 8649.8 | 9700.1 | 8993.1 | 9690 | 9087.4 | 10032.8 | 8950.6 | 9537.9 | 8833.8 | 7872.8 | 9657.3 | 9330.2 | 8689.5 | 9988.7 | 9670.2 | 8904.6 | 8793.8 | 9775 | 8740.7 | 9107.5 | 9850.7 | 8729.9 | 9929.6 | 8707.1 | 9667.1 | 8951.9 | 9775.2 | 8484.8 | 9840.3 | 8912.7 | 9705.5 | 8880.9 | 9788.8 | 9043.2 | 8810.3 | 9661.4 | 8915 | 8754.2 | 9759.6 | 9890.5 | 9705.4 | 8866.1 | 9778.4 | 8801 | 9474.2 | 8956.4 | 9469 | 8245.6 | 9562.1 | 8692.5 | 8978.1 | 8985.2 | 8813.9 | 7669.4 | 8806.8 | 7785.3 | 8889.7 | 8899.1 | 10242.3 | 8938.8 | 10265.2 | 9146.5 | 10180.2 | 9014.5 | 9180.1 | 9006.3 | 9948.1 | 10271.6 | 10168.2 | 10093.5 | 10195.7 | 10224.9 | 9219.1 | 9911.5 | 10282.1 | 10320.1 | 10324.2 | 10287 | 10290.7 | 9245 | 10327.7 | 9297 | 22.06 | 21.62 | 22.13 | 22.14 | 21.96 | 21.72 | 0 | 34.99 | 0 | 0 | 34.84 | 34.1 | 1.86 | 1.2 | 1.74 | 0.17 | 1.66 | 0.87 | 3.51 | 3.53 | 3.91 | 3.59 | 3.62 | 3.66 | 4.01 | 4.05 | 4.03 | 4.01 | 4.08 | 4.08 | 1.08 | 1.14 | 1 | 1.24 | 1.23 | 1 | 5.1 | 5.05 | 5.03 | 5.13 | 5.06 | 5.06 | 0.25 | 0.28 | 0.23 | 0.25 | 0.24 | 0.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 821645 | 1531 | 808427 | 1558 | 284752.4 | 851.2 | 4.01 | 4.05 | 4.03 | 4.01 | 4.08 | 4.08 | 5.1 | 5.05 | 5.03 | 5.13 | 5.06 | 5.06 | 749000 | 2000 | 747000 | 2000 | 1489645 | 5000 | 1492000 | 1484645 | 10.6 | 4.0433 | 1.115 | 5.0717 | 0.25333 | 27.58% | 4.995% | 21.9383 | 34.6433 | 1.25 | 3.6367 | 1498511 | 1479734 | 1643311.5 | 90.05% | 21 | 6789
2025-01-03 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 335090.89 | 7:36 | 18:08 | 9598.5 | 10062 | 9993.8 | 9968.9 | 10021.7 | 10128.4 | 10033.8 | 10494.1 | 9975.2 | 10011.7 | 9852.6 | 10021.2 | 9954.2 | 9961 | 9932.2 | 10048.5 | 9925.6 | 10040.7 | 10064.9 | 10113.7 | 10025.8 | 10019.3 | 9798.2 | 9945.8 | 9772 | 8579.7 | 9803.8 | 9775.6 | 10070.4 | 9942.6 | 9806.4 | 10036.1 | 10061.9 | 10134.5 | 10070.3 | 10016.4 | 10194 | 10037.6 | 10088.6 | 9906 | 10964.9 | 9650.7 | 10803.8 | 9590.1 | 10189.5 | 11473.7 | 9506.5 | 10936.6 | 9804.7 | 10015.3 | 9979.6 | 9342.5 | 10403.7 | 9786.6 | 10381 | 9913.2 | 9197.4 | 10643 | 9181 | 10554.8 | 10434.7 | 9182.9 | 10159.3 | 9625.1 | 9775 | 9176.8 | 9740.3 | 10232.5 | 10498.7 | 9399.8 | 10327.6 | 9064.7 | 9970 | 9814.3 | 9163.5 | 10386.9 | 9047.7 | 10477.3 | 9139.3 | 10334.3 | 9493.4 | 10283.5 | 9591.1 | 10708.5 | 9450.9 | 10114.8 | 9311.4 | 8280.3 | 10254.2 | 9847.4 | 9169.2 | 10661.4 | 10298.1 | 9418.1 | 9297.7 | 10401.6 | 9201.7 | 9611.9 | 10480 | 9197.1 | 10587.3 | 9170.7 | 10258.2 | 9432.9 | 10391.8 | 8937.2 | 10466.1 | 9404.5 | 10300.7 | 9368.6 | 10400.4 | 9532.8 | 9282.8 | 10245 | 9397.7 | 9219.7 | 10354.9 | 10508 | 10296.5 | 9323.6 | 10376.1 | 9259.9 | 10029.7 | 9451 | 10021.4 | 8671.8 | 10108.5 | 9139.2 | 9442.9 | 9444.4 | 9265.1 | 8052.4 | 9254 | 8155.8 | 9326.8 | 9333.5 | 10883.7 | 9367.8 | 10927.6 | 9608 | 10811.2 | 9453.9 | 9640.1 | 9446 | 10544.5 | 10943.9 | 10790.1 | 10696.4 | 10833.3 | 10865.6 | 9688.1 | 10503.3 | 10928.2 | 10994.2 | 11005.6 | 10963.7 | 10972.8 | 9731.8 | 10988.6 | 9785.7 | 23.58 | 23.4 | 23.86 | 23.88 | 23.61 | 23.38 | 0 | 38.05 | 0 | 0 | 38.6 | 37.3 | 2.01 | 1.15 | 1.52 | 0.54 | 1.52 | 0.74 | 4.7 | 5.07 | 4.61 | 4.56 | 4.59 | 4.13 | 4.12 | 4.17 | 4.14 | 4.12 | 4.19 | 4.18 | 1.09 | 1.17 | 1.02 | 1.28 | 1.27 | 1.04 | 5.5 | 5.46 | 5.41 | 5.53 | 5.43 | 5.44 | 0.23 | 0.25 | 0.2 | 0.22 | 0.22 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 822440 | 1534 | 809217 | 1560 | 286331.422 | 856.267 | 4.12 | 4.17 | 4.14 | 4.12 | 4.19 | 4.18 | 5.5 | 5.46 | 5.41 | 5.53 | 5.43 | 5.44 | 795000 | 3000 | 790000 | 2000 | 1579022 | 5067 | 1580000 | 1573955 | 10.5333 | 4.1533 | 1.145 | 5.4617 | 0.22833 | 27.57% | 4.181% | 23.6183 | 37.9833 | 1.2467 | 4.61 | 1588215.3 | 1563000 | 1739412.6124 | 89.86% | 21 | 0
2025-01-04 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 335090.89 | 7:41 | 18:06 | 9027.3 | 9491.2 | 9431.5 | 9399.2 | 9446.6 | 9545.4 | 9502 | 9894.9 | 9391.5 | 9417.7 | 9295.8 | 9439.3 | 9401.2 | 9400.4 | 9389.9 | 9477.5 | 9367.6 | 9461.3 | 9486 | 9527.9 | 9453.7 | 9446.3 | 9244.8 | 9371 | 9206.7 | 8082.7 | 9231.6 | 9204.7 | 9491.6 | 9383.1 | 9260.8 | 9464.4 | 9481.1 | 9534.7 | 9483.9 | 9436.6 | 9600.5 | 9452 | 9503.2 | 9353.1 | 10393.3 | 9171.8 | 10248.5 | 9109.9 | 9676.8 | 10884.8 | 9007.8 | 10361 | 9256.5 | 9450.8 | 9440.9 | 8908.9 | 9818.1 | 9247.3 | 9784 | 9370 | 8661.4 | 10022.3 | 8653.3 | 9938 | 9821.5 | 8650.5 | 9560.1 | 9055.4 | 9212 | 8636.8 | 9163.6 | 9638 | 9891.2 | 8848.8 | 9721.3 | 8538.3 | 9390.4 | 9247.8 | 8626.8 | 9768.6 | 8517.7 | 9862.2 | 8606.4 | 9730.6 | 8948.5 | 9695.6 | 9045.2 | 10092.1 | 8906.7 | 9536.2 | 8783.9 | 7811.5 | 9671 | 9307.9 | 8649.3 | 10055.4 | 9722.9 | 8890.8 | 8788.9 | 9826 | 8707.4 | 9083.4 | 9906.8 | 8685 | 9985.6 | 8658.8 | 9677.2 | 8908.7 | 9803.6 | 8431.1 | 9872.9 | 8876.9 | 9726.6 | 8837.6 | 9819.1 | 9010.8 | 8766.2 | 9685.1 | 8875.1 | 8705.8 | 9788 | 9921.4 | 9725.6 | 8811.2 | 9796.7 | 8748 | 9478.3 | 8919.3 | 9466.4 | 8173.4 | 9548.6 | 8639.6 | 8924.5 | 8931.5 | 8764.3 | 7616.5 | 8783 | 7745 | 8823.4 | 8827.5 | 10276.6 | 8855.1 | 10309.3 | 9073.4 | 10217.7 | 8936.8 | 9118.3 | 8935.7 | 9942.2 | 10325.9 | 10186.1 | 10100.8 | 10220.6 | 10254.3 | 9140.6 | 9907.4 | 10309.4 | 10366.4 | 10374.5 | 10343.6 | 10339.4 | 9180.2 | 10377.5 | 9227.5 | 23.16 | 22.83 | 23.44 | 23.09 | 23.47 | 23.09 | 0 | 35.2 | 0 | 0 | 34.6 | 34.07 | 2.92 | 1.63 | 3.03 | 1.57 | 2.71 | 2.32 | 5.98 | 6.09 | 5.99 | 5.55 | 5.78 | 5.76 | 3.93 | 3.97 | 3.98 | 4.1 | 3.99 | 3.97 | 1.04 | 1.14 | 0.98 | 1.27 | 1.22 | 1.01 | 5.14 | 5.11 | 5.07 | 5.14 | 5.07 | 5.1 | 0.23 | 0.25 | 0.2 | 0.22 | 0.22 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 823190 | 1535 | 809963 | 1561 | 287821.822 | 861.467 | 3.93 | 3.97 | 3.98 | 4.1 | 3.99 | 3.97 | 5.14 | 5.11 | 5.07 | 5.14 | 5.07 | 5.1 | 750000 | 1000 | 746000 | 1000 | 1490400 | 5200 | 1494000 | 1485200 | 10.4167 | 3.99 | 1.11 | 5.105 | 0.22833 | 27.82% | 4.473% | 23.18 | 34.6233 | 2.3633 | 5.8583 | 1498881.2 | 1474600 | 1642797.1483 | 89.76% | 17 | 0
2025-01-05 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 335090.89 | 7:43 | 18:08 | 8567.3 | 8962.9 | 8925.7 | 8904 | 8926 | 9024.7 | 8979.7 | 9345.1 | 8902.7 | 8959 | 8792.3 | 8920.7 | 8934.3 | 8902.5 | 8913.4 | 9008.8 | 8864 | 8942.5 | 8963.7 | 9020.2 | 8926.2 | 8926.7 | 8708.6 | 8837.3 | 8695.2 | 7657.5 | 8752.1 | 8704.1 | 8947.8 | 8841.5 | 8729.5 | 8919.1 | 8915.4 | 8979.2 | 8954.9 | 8885.5 | 9024.7 | 8896.9 | 8944.8 | 8811.1 | 9784.2 | 8663.7 | 9663.4 | 8597.6 | 9154 | 10293.3 | 8482.5 | 9758.1 | 8811.7 | 8994.5 | 8983.6 | 8467.8 | 9323.7 | 8788.3 | 9301.6 | 8921.5 | 8232.5 | 9523.4 | 8202.4 | 9431.6 | 9310.3 | 8191.5 | 9026.8 | 8545.1 | 8745.8 | 8190.6 | 8707.5 | 9132.1 | 9385.9 | 8390.7 | 9216.2 | 8085.5 | 8907.3 | 8758.9 | 8161.1 | 9231.9 | 8049.8 | 9322.8 | 8134.1 | 9209.9 | 8479.2 | 9184.3 | 8579.8 | 9560.5 | 8442.1 | 9048.6 | 8338.1 | 7409.4 | 9048 | 8744 | 8147 | 9463 | 9137 | 8348 | 8241 | 9262 | 8231.2 | 8575.3 | 9356.1 | 8203.5 | 9456.4 | 8200 | 9176.9 | 8446.4 | 9311.1 | 8004.7 | 9371.8 | 8414.1 | 9223.7 | 8377.8 | 9331.1 | 8555.9 | 8296.1 | 9193 | 8421.6 | 8262.8 | 9301.4 | 9437.3 | 9241.5 | 8398.3 | 9329.7 | 8335.6 | 9005.6 | 8474.6 | 9011.4 | 7801.4 | 9111.7 | 8234.9 | 8494.6 | 8499.2 | 8385 | 7260.5 | 8371 | 7405 | 8406.8 | 8412.1 | 9706 | 8366 | 9747.8 | 8576.3 | 9680.7 | 8493.4 | 8665 | 8524.1 | 9418.1 | 9774.5 | 9646.9 | 9562.5 | 9659.8 | 9691.5 | 8644 | 9373.4 | 9789.9 | 9834.1 | 9853 | 9816.9 | 9808.1 | 8704.4 | 9840.6 | 8737.5 | 19.06 | 18.91 | 18.92 | 19.25 | 18.97 | 18.92 | 0 | 29.16 | 0 | 0 | 28.8 | 27.5 | 3.08 | 2.47 | 2.72 | 1.48 | 3.05 | 2.48 | 5.75 | 5.7 | 5.43 | 5.28 | 6.02 | 5.61 | 3.73 | 3.76 | 3.79 | 3.5 | 3.8 | 3.78 | 1.01 | 1.09 | 0.94 | 1.24 | 1.2 | 1 | 4.77 | 4.73 | 4.71 | 4.8 | 4.73 | 4.75 | 0.24 | 0.26 | 0.21 | 0.24 | 0.23 | 0.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 823899 | 1538 | 810671 | 1563 | 289233.089 | 866.6 | 3.73 | 3.76 | 3.79 | 3.5 | 3.8 | 3.78 | 4.77 | 4.73 | 4.71 | 4.8 | 4.73 | 4.75 | 709000 | 3000 | 708000 | 2000 | 1411267 | 5133 | 1412000 | 1406134 | 10.4167 | 3.7267 | 1.08 | 4.7483 | 0.24 | 28.98% | 5.054% | 19.005 | 28.4867 | 2.5467 | 5.6317 | 1419574.4 | 1391867 | 1554575.6482 | 89.53% | 13 | 0
2025-01-06 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 335090.89 | 7:39 | 18:11 | 10438.8 | 10884.3 | 10838.2 | 10810.6 | 10844.1 | 10932.9 | 10874.9 | 11219.9 | 10833.2 | 10879.2 | 10707.3 | 10867 | 10814.6 | 10807.7 | 10800.4 | 10904 | 10766.7 | 10867.6 | 10886.5 | 10955.8 | 10850.4 | 10854.3 | 10635.1 | 10779.2 | 10616.7 | 9339.7 | 10662.9 | 10615 | 10893 | 10779 | 10661.5 | 10864.3 | 10947.7 | 11015.7 | 10940.1 | 10881.3 | 10997.4 | 10872.9 | 10918.2 | 10758.2 | 11681.7 | 10516.9 | 11539.9 | 10463.4 | 11070.7 | 12124.6 | 10357 | 11655.7 | 10647.7 | 10862.1 | 10883.4 | 10302.5 | 11218.6 | 10648.2 | 11199 | 10760 | 10016.4 | 11420.4 | 9989.3 | 11335.7 | 11244.9 | 9995.6 | 10995.9 | 10520.4 | 10632.9 | 9966.3 | 10605.5 | 11048 | 11277 | 10231.2 | 11148.3 | 9875.9 | 10823.5 | 10695.6 | 9973.9 | 11177.5 | 9864.8 | 11264.4 | 9944.2 | 11145.6 | 10343.9 | 11124.9 | 10454.9 | 11472 | 10278.8 | 10952.8 | 10159.2 | 9019.7 | 11098.2 | 10716 | 10003.2 | 11432.6 | 11107.6 | 10244.8 | 10111.6 | 11198.4 | 10044.6 | 10480.2 | 11255.1 | 10013.8 | 11374 | 9997.6 | 11107.3 | 10291.9 | 11207.2 | 9752.8 | 11282 | 10245.5 | 11146.1 | 10205.4 | 11234.7 | 10398.5 | 10122.4 | 11093 | 10240.7 | 10051.5 | 11161.8 | 11310.2 | 11117.4 | 10171.1 | 11184 | 10097 | 10881.4 | 10300.4 | 10899.6 | 9452.2 | 10975.5 | 9967.6 | 10280.2 | 10284.5 | 10172.9 | 8778.6 | 10118.3 | 8964.9 | 10167.6 | 10181.3 | 11592.8 | 10198.8 | 11630.3 | 10464.1 | 11538.9 | 10320.2 | 10515.8 | 10318 | 11325 | 11646.3 | 11530.4 | 11436 | 11557.2 | 11578.4 | 10539.7 | 11281.2 | 11663.5 | 11701.8 | 11712.4 | 11673.8 | 11677.5 | 10601.9 | 11704.9 | 10636.5 | 18.13 | 17.98 | 18.14 | 18.16 | 18.02 | 17.97 | 0 | 29.71 | 0 | 0 | 29.6 | 28 | 3.34 | 2.56 | 3.17 | 2.07 | 3.27 | 3.13 | 5.96 | 5.74 | 5.84 | 5.66 | 5.95 | 6.45 | 4.36 | 4.41 | 4.41 | 4.33 | 4.43 | 4.41 | 1.17 | 1.26 | 1.1 | 1.45 | 1.39 | 1.14 | 5.82 | 5.75 | 5.73 | 5.83 | 5.73 | 5.75 | 0.26 | 0.29 | 0.23 | 0.25 | 0.25 | 0.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 824760 | 1539 | 811525 | 1564 | 290940.356 | 871.8 | 4.36 | 4.41 | 4.41 | 4.33 | 4.43 | 4.41 | 5.82 | 5.75 | 5.73 | 5.83 | 5.73 | 5.75 | 861000 | 1000 | 854000 | 1000 | 1707267 | 5200 | 1713000 | 1702067 | 10.5333 | 4.3917 | 1.2517 | 5.7683 | 0.26 | 28.5% | 4.507% | 18.0667 | 29.1033 | 2.9233 | 5.9333 | 1719515.7 | 1693666 | 1889208.1972 | 89.65% | 16 | 1043
2025-01-07 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 335090.89 | 7:37 | 18:13 | 10561.9 | 10970.6 | 10930.8 | 10906 | 10942.6 | 11036.2 | 10977.7 | 11273.8 | 10921.3 | 10943.3 | 10805.3 | 10953 | 10907 | 10897.2 | 10902.5 | 10992.4 | 10859.3 | 10957.6 | 10974.5 | 11046.4 | 10948.9 | 10955.8 | 10762.3 | 10884.4 | 10737.6 | 9469.9 | 10777.6 | 10730.2 | 10986.5 | 10869.4 | 10773.3 | 10960.2 | 11102.2 | 11178 | 11090.2 | 11032.8 | 11083.9 | 10969.8 | 11008.7 | 10863.4 | 11723.1 | 10649.3 | 11590.5 | 10595.7 | 11163.6 | 12156.9 | 10491.9 | 11688.1 | 10745.4 | 10947.3 | 10972.2 | 10434.6 | 11286.8 | 10746 | 11271 | 10848 | 10153.9 | 11482.4 | 10122.2 | 11410.6 | 11328.3 | 10138 | 11082.4 | 10643.8 | 10760.5 | 10102.8 | 10736.6 | 11136.1 | 11354.1 | 10362.7 | 11228.5 | 9995.8 | 10927.9 | 10806.6 | 10107.4 | 11257.3 | 9986.2 | 11341.6 | 10066.6 | 11231 | 10463.1 | 11198.8 | 10579.2 | 11525.2 | 10404.9 | 11040.2 | 10273.3 | 9125.4 | 11162.5 | 10814.3 | 10134.1 | 11489.2 | 11192.4 | 10387.4 | 10248.6 | 11261 | 10166.2 | 10602.6 | 11312.5 | 10139.7 | 11425.6 | 10108.1 | 11179.1 | 10409 | 11265.6 | 9860.8 | 11346.3 | 10367.4 | 11220 | 10327.6 | 11299.8 | 10517.4 | 10249 | 11177.9 | 10358.4 | 10173.6 | 11224.6 | 11374.6 | 11187.6 | 10309.7 | 11246.9 | 10220.5 | 10961.6 | 10419.6 | 10974 | 9575.3 | 11054.5 | 10088.9 | 10414.3 | 10428 | 10284.2 | 8887.3 | 10230.1 | 9070.1 | 10307.6 | 10316.3 | 11635.9 | 10314.1 | 11671.9 | 10579.4 | 11578.2 | 10436 | 10617.6 | 10444.4 | 11388.1 | 11683.2 | 11580.6 | 11498.2 | 11610.7 | 11632.6 | 10655.2 | 11352.4 | 11706.2 | 11738.3 | 11754 | 11718.9 | 11729.4 | 10718.6 | 11739.3 | 10751.3 | 18.1748 | 17.839 | 18.4265 | 18.0509 | 17.9991 | 17.7166 | 0 | 28.3 | 0 | 0 | 28.6418 | 27.6 | 3.5428 | 2.464 | 3.3189 | 1.6137 | 3.457 | 2.9327 | 6.5067 | 6.425 | 6.0567 | 6.2967 | 6.75 | 6.83 | 4.416 | 4.4664 | 4.4736 | 4.414 | 4.4834 | 4.4625 | 1.1998 | 1.3069 | 1.1261 | 1.4803 | 1.4061 | 1.1531 | 5.8878 | 5.8309 | 5.8999 | 5.9151 | 5.8074 | 5.8155 | 0.26667 | 0.28955 | 0.23275 | 0.25578 | 0.25469 | 0.28647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 825629 | 1541 | 812386 | 1566 | 292662.89 | 876.933 | 4.416 | 4.4664 | 4.4736 | 4.414 | 4.4834 | 4.4625 | 5.8878 | 5.8309 | 5.8999 | 5.9151 | 5.8074 | 5.8155 | 869000 | 2000 | 861000 | 2000 | 1722534 | 5133 | 1726000 | 1717401 | 10.6 | 4.4527 | 1.2787 | 5.8594 | 0.26432 | 28.72% | 4.511% | 18.0345 | 28.1806 | 2.8882 | 6.4775 | 1734934.6 | 1708067 | 1916712.3349 | 89.11% | 25 | 3189
2025-01-08 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 335090.89 | 7:38 | 18:12 | 10402.8 | 10892.8 | 10835.9 | 10789 | 10839.5 | 10976.9 | 10923.1 | 11348.7 | 10858 | 10856.1 | 10703.1 | 10892.2 | 10813.5 | 10822.2 | 10781.5 | 10907.1 | 10773.9 | 10900.8 | 10929.8 | 10980.2 | 10895.4 | 10894.8 | 10641.8 | 10797.1 | 10635.9 | 9332.1 | 10660.1 | 10618.9 | 10945.4 | 10803.2 | 10665.8 | 10920.2 | 10949.7 | 11032.6 | 10947.8 | 10895.5 | 11076.1 | 10910.2 | 10962.3 | 10763.3 | 11868 | 10512.2 | 11712.1 | 10456.7 | 11101.3 | 12331.9 | 10361.9 | 11838.5 | 10642.4 | 10869.2 | 10894.6 | 10282.2 | 11298.7 | 10616.9 | 11268 | 10753.7 | 9982.7 | 11525 | 9952.7 | 11442.1 | 11325.9 | 9961.6 | 11035.9 | 10496.8 | 10625.1 | 9974 | 10596.1 | 11121.6 | 11405 | 10227.8 | 11238.1 | 9862.2 | 10828.9 | 10683.1 | 9966.6 | 11272.5 | 9856.9 | 11384.6 | 9938.1 | 11235.3 | 10326.1 | 11183.4 | 10434.4 | 11610.8 | 10273.1 | 10987.9 | 10137.2 | 9005.8 | 11145.2 | 10707.3 | 9986.6 | 11566.8 | 11181.9 | 10224.2 | 10082.4 | 11304.7 | 10007.3 | 10451.7 | 11367.5 | 10003.4 | 11492 | 9973.2 | 11163.6 | 10272 | 11306.8 | 9729.6 | 11389 | 10237.9 | 11219 | 10199.8 | 11325.5 | 10387.6 | 10089.3 | 11164.5 | 10219.6 | 10034.2 | 11257.3 | 11435.6 | 11203.5 | 10164.7 | 11286.9 | 10080.9 | 10907.4 | 10290.2 | 10917.6 | 9433 | 11003.1 | 9952 | 10265.1 | 10267.2 | 10117.7 | 8753.7 | 10073.2 | 8903.5 | 10131.3 | 10133.6 | 11782.1 | 10204.7 | 11812.8 | 10460 | 11700.5 | 10292.2 | 10494.1 | 10268 | 11460.5 | 11833.1 | 11691.3 | 11594.4 | 11735.9 | 11767.3 | 10540.9 | 11410.4 | 11836.8 | 11890.8 | 11893.6 | 11858.9 | 11874.2 | 10608.4 | 11886.8 | 10652.4 | 20.2793 | 19.9657 | 20.6429 | 20.4689 | 20.0219 | 19.9462 | 0 | 37.0981 | 0 | 0 | 37 | 35.9 | 1.7418 | 0.52801 | 1.3046 | 0.019774 | 1.5446 | 1.0647 | 3.8117 | 3.0733 | 3.3217 | 1.435 | 3.2917 | 3.5633 | 4.4368 | 4.4953 | 4.4972 | 4.4413 | 4.5238 | 4.5075 | 1.1844 | 1.2808 | 1.1072 | 1.4665 | 1.3974 | 1.1476 | 5.9351 | 5.8941 | 5.9498 | 5.9708 | 5.8779 | 5.8927 | 0.24486 | 0.26704 | 0.2159 | 0.23193 | 0.23338 | 0.26522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 826492 | 1543 | 813244 | 1567 | 294376.623 | 880.8 | 4.4368 | 4.4953 | 4.4972 | 4.4413 | 4.5238 | 4.5075 | 5.9351 | 5.8941 | 5.9498 | 5.9708 | 5.8779 | 5.8927 | 863000 | 2000 | 858000 | 1000 | 1713733 | 3867 | 1718000 | 1709866 | 10.5667 | 4.4836 | 1.264 | 5.92 | 0.24305 | 28.19% | 4.106% | 20.2208 | 36.666 | 1.0339 | 3.0828 | 1725641.1 | 1700866 | 1906043.0998 | 89.24% | 24 | 0
2025-01-09 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 335090.89 | 7:36 | 18:13 | 10337.5 | 10826.2 | 10705 | 10660.2 | 10815.1 | 10899.8 | 10850.8 | 11284.2 | 10812.5 | 10791 | 10648.1 | 10837.4 | 10768.4 | 10764.6 | 10736.1 | 10862.6 | 10716.1 | 10839.2 | 10872.6 | 10934 | 10839.9 | 10841.3 | 10584.6 | 10741.9 | 10576.4 | 9289.8 | 10610.5 | 10568.7 | 10887.4 | 10748 | 10610.2 | 10863.2 | 10897.6 | 10977 | 10891.5 | 10837.6 | 11015.9 | 10863.2 | 10914.3 | 10722.7 | 11794 | 10451.3 | 11647.9 | 10385.7 | 11032.9 | 12256.7 | 10306.9 | 11768.9 | 10591.3 | 10823.5 | 10849.8 | 10246.1 | 11231.2 | 10587.1 | 11222.7 | 10721.2 | 9962.3 | 11490.9 | 9924.6 | 11399.2 | 11279.7 | 9929.4 | 10982.1 | 10434.1 | 10591.3 | 9935.3 | 10560.2 | 11073.2 | 11350 | 10186.8 | 11183.5 | 9817.8 | 10787.1 | 10644.1 | 9920.6 | 11222.6 | 9808.8 | 11313.9 | 9880.4 | 11170.8 | 10282.9 | 11127.2 | 10402.9 | 11551.2 | 10229.3 | 10941.6 | 10089.7 | 8969.5 | 11110.2 | 10670.6 | 9961.6 | 11531.9 | 11155.1 | 10215 | 10071.7 | 11262.6 | 9975.5 | 10421.3 | 11326.6 | 9970.5 | 11448 | 9949.2 | 11123.9 | 10237.3 | 11259.9 | 9698.7 | 11340.4 | 10208.1 | 11178.9 | 10180.5 | 11281.6 | 10363.9 | 10065.5 | 11114.5 | 10192.2 | 10000.1 | 11219.3 | 11384.9 | 11168.2 | 10130.7 | 11240.9 | 10051.1 | 10887.8 | 10268.1 | 10895.7 | 9408.9 | 10967.4 | 9926.2 | 10238.5 | 10254.7 | 10083 | 8730.9 | 10050.6 | 8889.1 | 10110.1 | 10124.5 | 11749.8 | 10186.7 | 11791.3 | 10447 | 11686.2 | 10297 | 10492 | 10265.8 | 11433.3 | 11810.2 | 11673.9 | 11584.1 | 11713.3 | 11739.2 | 10536.3 | 11396.6 | 11811.3 | 11851.6 | 11859.8 | 11819.4 | 11834.4 | 10577.6 | 11861.5 | 10635 | 22.6952 | 22.1778 | 22.4186 | 22.5631 | 22.0649 | 21.8309 | 0 | 36.2485 | 0 | 0 | 36.1 | 34.7 | 2.6439 | 1.2232 | 2.3932 | 0.0076536 | 2.1979 | 2.0493 | 4.8517 | 4.6767 | 4.8233 | 0.95 | 5.3167 | 4.7983 | 4.4467 | 4.4791 | 4.4953 | 4.4476 | 4.5143 | 4.5076 | 1.1919 | 1.265 | 1.1124 | 1.4748 | 1.4008 | 1.1454 | 5.892 | 5.8296 | 5.9007 | 5.9419 | 5.8257 | 5.8438 | 0.26009 | 0.28232 | 0.22906 | 0.25083 | 0.24667 | 0.2794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 827350 | 1545 | 814099 | 1569 | 296084.423 | 885.933 | 4.4467 | 4.4791 | 4.4953 | 4.4476 | 4.5143 | 4.5076 | 5.892 | 5.8296 | 5.9007 | 5.9419 | 5.8257 | 5.8438 | 858000 | 2000 | 855000 | 2000 | 1707800 | 5133 | 1709000 | 1702667 | 10.6167 | 4.4818 | 1.2651 | 5.8723 | 0.25806 | 28.23% | 4.395% | 22.2917 | 35.6828 | 1.7525 | 4.2361 | 1719002.5 | 1695067 | 1888669.145 | 89.75% | 23 | 0
2025-01-10 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 335090.89 | 7:40 | 18:11 | 9316.7 | 9663 | 9631.2 | 9620.8 | 9662.7 | 9703.4 | 9657.2 | 9913.6 | 9623.3 | 9593.3 | 9515.3 | 9640.6 | 9616.9 | 9585.2 | 9618.6 | 9686.7 | 9578.4 | 9653.6 | 9675.2 | 9732.8 | 9648.1 | 9668.9 | 9512.4 | 9598.5 | 9470.4 | 8430.2 | 9504.3 | 9460.9 | 9668.9 | 9569.9 | 9503.8 | 9648.3 | 9882.3 | 9953.8 | 9890.5 | 9833.8 | 9742.6 | 9649.6 | 9680.1 | 9571.7 | 10233.3 | 9411 | 10120.3 | 9366.4 | 9792.7 | 10590.7 | 9275.6 | 10206.8 | 9512.3 | 9664.6 | 9676.9 | 9286.9 | 9926.7 | 9510.1 | 9904.3 | 9607.6 | 9050.5 | 10076.3 | 9026.2 | 10017.3 | 9940.1 | 9026.4 | 9714.6 | 9365.7 | 9494.2 | 9005.8 | 9483.2 | 9791 | 9961.1 | 9211.3 | 9857.4 | 8905.2 | 9631.4 | 9540.5 | 9010.9 | 9881.1 | 8911.7 | 9950 | 8978.1 | 9864.5 | 9289.4 | 9827.4 | 9371.3 | 10098.2 | 9249.1 | 9719 | 9115.6 | 8128.3 | 9789.2 | 9542.9 | 8999.4 | 10052.4 | 9818.2 | 9222.3 | 9114 | 9871.3 | 9021.4 | 9357.8 | 9914.3 | 9009 | 9989.3 | 8990.7 | 9809.1 | 9231 | 9865.1 | 8763.6 | 9928.5 | 9189.5 | 9839.2 | 9167.9 | 9898.4 | 9323.7 | 9087.1 | 9779 | 9176.1 | 9031.2 | 9834.3 | 9954.1 | 9807.7 | 9145.9 | 9853 | 9073.5 | 9637.8 | 9233.1 | 9642.1 | 8500.8 | 9709.3 | 8957.4 | 9234.8 | 9231.9 | 9098.7 | 7893.8 | 9065.2 | 8016.3 | 9140.7 | 9145.6 | 10200.4 | 9192 | 10224.3 | 9378.7 | 10150.8 | 9268.8 | 9407 | 9246.5 | 10009.4 | 10241.1 | 10168.9 | 10101.3 | 10179.9 | 10190.3 | 9441.5 | 9971.7 | 10251.9 | 10275.8 | 10281.8 | 10259.8 | 10277.9 | 9495.7 | 10299.8 | 9527.6 | 21.1445 | 20.7369 | 21.0042 | 21.1767 | 20.7245 | 20.6764 | 0 | 35.4971 | 0 | 0 | 35.5 | 34.3 | 2.1666 | 0.90865 | 2.0975 | 0.0019265 | 1.633 | 0.95289 | 4.69 | 4.2283 | 5.425 | 0.12667 | 3.815 | 4.6567 | 4.0845 | 4.122 | 4.126 | 4.0791 | 4.1338 | 4.1411 | 1.1018 | 1.1986 | 1.0282 | 1.3639 | 1.2913 | 1.0606 | 5.3189 | 5.2751 | 5.3244 | 5.3535 | 5.2462 | 5.2794 | 0.2329 | 0.2526 | 0.20623 | 0.225 | 0.22112 | 0.2507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 828117 | 1547 | 814860 | 1571 | 297605.623 | 890.933 | 4.0845 | 4.122 | 4.126 | 4.0791 | 4.1338 | 4.1411 | 5.3189 | 5.2751 | 5.3244 | 5.3535 | 5.2462 | 5.2794 | 767000 | 2000 | 761000 | 2000 | 1521200 | 5000 | 1524000 | 1516200 | 10.5167 | 4.1144 | 1.1741 | 5.2996 | 0.23142 | 28.54% | 4.367% | 20.9105 | 35.099 | 1.2934 | 3.8236 | 1530157 | 1574355.2336 | 1712791.361 | 91.92% | 22 | 0
2025-01-11 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 335090.89 | 7:55 | 18:13 | 8615 | 9053.2 | 8984.6 | 8955.6 | 9025.9 | 9090.1 | 9059.1 | 9439 | 8997.9 | 9040.9 | 8862.4 | 9025.6 | 8947.3 | 8964.2 | 8965.7 | 9018.6 | 8922.2 | 8995.9 | 9014.4 | 9049.7 | 8991.6 | 8985.7 | 8783 | 8896.7 | 8743.3 | 7677.8 | 8773.3 | 8733.2 | 9016.7 | 8923.9 | 8789.1 | 8990.2 | 9003.9 | 9049.4 | 9005.3 | 8959.1 | 9108.5 | 8972.5 | 9017.8 | 8890.6 | 9786.1 | 8645.1 | 9639.7 | 8565.7 | 9152.1 | 10283.9 | 8515.8 | 9772.8 | 8919.1 | 9104.6 | 9018.5 | 8497.6 | 9321.4 | 8931.5 | 9309.8 | 9063.6 | 8245.3 | 9544.9 | 8250.7 | 9466 | 9362.4 | 8246.9 | 9169.6 | 8695.1 | 8773.3 | 8233.6 | 8745.9 | 9157.8 | 9409 | 8358.1 | 9299.9 | 8122.8 | 8970.3 | 8827.2 | 8241.9 | 9324 | 8142.1 | 9440.4 | 8237.1 | 9298 | 8474.7 | 9187.3 | 8598.9 | 9556.5 | 8458.7 | 9060.3 | 8380.5 | 7406 | 9250.4 | 8836.8 | 8225.9 | 9587.6 | 9228.4 | 8454.2 | 8362.2 | 9351.3 | 8261.5 | 8602.5 | 9406 | 8226.9 | 9485 | 8215.5 | 9185.2 | 8454.7 | 9287.6 | 7941.3 | 9344.7 | 8391.2 | 9220.4 | 8380.4 | 9254.8 | 8506.4 | 8051 | 9067.3 | 8408.4 | 8224.6 | 9293.2 | 9408.9 | 9223.1 | 8355.3 | 9318.9 | 8303.8 | 8995.6 | 8430.1 | 8974.8 | 7775.8 | 9057.2 | 8176.6 | 8481.8 | 8524.1 | 8371.6 | 7236.6 | 8362.3 | 7370.3 | 8344.8 | 8374.8 | 9719.7 | 8379 | 9766.7 | 8583.4 | 9680.7 | 8480.7 | 8643.7 | 8494.7 | 9413.4 | 9782.2 | 9643.4 | 9568.5 | 9664.3 | 9696.6 | 8655.8 | 9386.6 | 9750.6 | 9800.7 | 9820.2 | 9791.7 | 9808.8 | 8703.7 | 9812.7 | 8745.7 | 20.2528 | 19.9859 | 20.3152 | 20.3731 | 20.3899 | 20.148 | 0 | 32.7918 | 0 | 0 | 32.9 | 31.9 | 2.7103 | 2.2938 | 2.5519 | 1.3749 | 2.3612 | 2.1773 | 5.6833 | 5.53 | 5.6717 | 5.2617 | 5.395 | 5.2933 | 3.783 | 3.8398 | 3.8476 | 3.7828 | 3.8518 | 3.825 | 0.91118 | 1.0078 | 0.87126 | 1.129 | 1.0573 | 0.90188 | 4.8164 | 4.8071 | 4.7964 | 4.8177 | 4.7635 | 4.7881 | 0.21207 | 0.23383 | 0.19202 | 0.20788 | 0.20371 | 0.22928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 828831 | 1549 | 815567 | 1572 | 299021.69 | 896.333 | 3.783 | 3.8398 | 3.8476 | 3.7828 | 3.8518 | 3.825 | 4.8164 | 4.8071 | 4.7964 | 4.8177 | 4.7635 | 4.7881 | 714000 | 2000 | 707000 | 1000 | 1416067 | 5400 | 1418000 | 1410667 | 10.3 | 3.8217 | 0.97972 | 4.7982 | 0.21313 | 25.64% | 4.442% | 20.2442 | 32.5306 | 2.2449 | 5.4725 | 1423936.7 | 1391600 | 1552479.5823 | 89.64% | 19 | 400
2025-01-12 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 335090.89 | 8:03 | 18:14 | 7299.6 | 7675.9 | 7641.3 | 7609.3 | 7642.1 | 7689.2 | 7683.8 | 7995.4 | 7647.6 | 7639.8 | 7539 | 7679.7 | 7579.2 | 7619.7 | 7562.5 | 7611.1 | 7534.5 | 7620.3 | 7614.2 | 7626.2 | 7652 | 7623.3 | 7506.9 | 7586.9 | 7440.3 | 6516.8 | 7424 | 7405.3 | 7707.1 | 7658.2 | 7558.9 | 7712.2 | 7742.9 | 7744.3 | 7670 | 7656.3 | 7815 | 7724.7 | 7769.2 | 7688.4 | 8432.2 | 7548.4 | 8351.6 | 7506.6 | 7986.5 | 8825 | 7406.6 | 8430 | 7630.9 | 7773.4 | 7684.9 | 7253.8 | 7923.8 | 7561.3 | 7959.3 | 7737.1 | 7061.3 | 8153.3 | 7036.9 | 8082.3 | 8005.7 | 7043.8 | 7783.1 | 7336.8 | 7506.9 | 7024.8 | 7476.2 | 7765.2 | 8015.4 | 7089.2 | 7863.5 | 6809.5 | 7631.9 | 7402.3 | 6962.9 | 7777.1 | 6764.3 | 7922.6 | 6865.2 | 7689.5 | 7091 | 7664 | 7188.9 | 8018.3 | 7124.5 | 7646.4 | 7176.8 | 6325.9 | 7980.2 | 7615.7 | 7130.6 | 8273.4 | 7974.4 | 7285.8 | 7182.1 | 8073.5 | 7181.7 | 7516.2 | 8151.1 | 7164.1 | 8162.9 | 7102.7 | 7935 | 7300.3 | 8053.1 | 6876.8 | 8079.3 | 7262.1 | 8002.7 | 7253.8 | 8125.9 | 7418.1 | 7260.8 | 8026.2 | 7282.4 | 7164.9 | 8047.4 | 8184.3 | 7990 | 7306.9 | 8105.1 | 7249.1 | 7804.4 | 7321.5 | 7808.9 | 6779.7 | 7902.7 | 7150.1 | 7464.3 | 7525.6 | 7336.9 | 6354.9 | 7375.2 | 6492.5 | 7184.9 | 7195.5 | 8308.8 | 7223.3 | 8393.6 | 7405.9 | 8303.4 | 7333.6 | 7466.5 | 7361.9 | 8238 | 8529 | 8386.4 | 8307.3 | 8323.5 | 8324.6 | 7547.3 | 8196.6 | 8462 | 8499.3 | 8509.5 | 8505.2 | 8535.3 | 7657.6 | 8507.1 | 7662.5 | 14.68 | 14.52 | 14.75 | 14.62 | 14.65 | 14.55 | 0 | 23.72 | 0 | 0 | 23.7 | 22.6 | 4.01 | 3.65 | 3.68 | 2.58 | 3.87 | 3.2 | 6.4 | 6.1 | 6.24 | 6.15 | 6.36 | 6.27 | 3.24 | 3.27 | 3.34 | 3.26 | 3.33 | 3.33 | 0.75 | 0.91 | 0.72 | 0.94 | 0.96 | 0.86 | 4.02 | 4.02 | 4.05 | 3.99 | 4.01 | 4.1 | 0.18 | 0.2 | 0.16 | 0.18 | 0.18 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 829439 | 1551 | 816179 | 1574 | 300235.6 | 901.667 | 3.24 | 3.27 | 3.34 | 3.26 | 3.33 | 3.33 | 4.02 | 4.02 | 4.05 | 3.99 | 4.01 | 4.1 | 608000 | 2000 | 612000 | 2000 | 1213910 | 5334 | 1216000 | 1208576 | 10.1833 | 3.295 | 0.85667 | 4.0317 | 0.18333 | 26% | 4.547% | 14.6283 | 23.34 | 3.4983 | 6.2533 | 1222833.9 | 1190200 | 1331492.2 | 89.39% | 29 | 12114
2025-01-13 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 335090.89 | 7:55 | 18:13 | 7332.1 | 7705.5 | 7726.9 | 7683.2 | 7745.2 | 7800.7 | 7784.6 | 8080.2 | 7684.6 | 7711.6 | 7587.2 | 7721.3 | 7665.1 | 7670.6 | 7699.1 | 7746.2 | 7654.4 | 7718.3 | 7723.9 | 7745 | 7727.3 | 7711.1 | 7547.1 | 7645.8 | 7497.4 | 6583.8 | 7520.5 | 7496.1 | 7753 | 7682.6 | 7580.4 | 7735.2 | 7735.7 | 7780 | 7735 | 7687.1 | 7801.8 | 7709.8 | 7760.2 | 7644.7 | 8253.1 | 7346.3 | 8171.2 | 7252.9 | 7826.5 | 8682.3 | 7279.5 | 8280.3 | 7670.6 | 7803 | 7715.2 | 7288.6 | 7996.4 | 7647.6 | 7995.5 | 7798.4 | 7055.7 | 8166.7 | 7054 | 8090.7 | 8008.2 | 7063.6 | 7801 | 7394.8 | 7463.9 | 6961.9 | 7433.4 | 7714.8 | 8011 | 7116 | 7854.3 | 6845.6 | 7638.1 | 7455.1 | 6982.6 | 7858.6 | 6851.9 | 7962.5 | 6932.7 | 7837.2 | 7180.4 | 7786.7 | 7348.6 | 8030.9 | 7185.7 | 7696 | 7092 | 6274.9 | 7924 | 7516.1 | 7050.5 | 8201.3 | 7951.5 | 7284.7 | 7181.5 | 8030.8 | 7124.7 | 7386.3 | 8061.4 | 7049.8 | 8176.3 | 7059.2 | 7916.7 | 7254.5 | 8032.9 | 6872 | 8080.2 | 7211.5 | 7972.4 | 7251.5 | 8062.9 | 7291.5 | 7112.9 | 7866.3 | 7195.3 | 7059.1 | 7964.8 | 8036 | 7892.2 | 7160.6 | 7972.7 | 7113.9 | 7721.7 | 7199.8 | 7710.5 | 6642.8 | 7767 | 7002.3 | 7260 | 7334.4 | 7177.8 | 6198.5 | 7211 | 6427.3 | 7365.4 | 7345.8 | 8334.7 | 7272.6 | 8373.8 | 7402 | 8352.7 | 7354.3 | 7511.8 | 7412 | 8081.1 | 8377.4 | 8197.4 | 8213.1 | 8267.8 | 8251 | 7460.1 | 8090.5 | 8256.3 | 8354.6 | 8369.8 | 8341 | 8369.1 | 7478.2 | 8382 | 7493 | 13.7519 | 13.4288 | 13.6634 | 13.5873 | 13.4875 | 13.5108 | 0 | 23.0956 | 0 | 0 | 23 | 22.1 | 3.9508 | 3.636 | 3.6444 | 1.8403 | 3.7266 | 2.8238 | 6.0417 | 5.9033 | 5.96 | 5.7317 | 6.7683 | 5.8367 | 3.2585 | 3.3109 | 3.305 | 3.248 | 3.3031 | 3.2956 | 0.75915 | 0.91896 | 0.70503 | 0.93951 | 0.94664 | 0.84826 | 4.074 | 4.0252 | 3.9913 | 4.0072 | 3.9709 | 4.0442 | 0.18467 | 0.20418 | 0.16286 | 0.18289 | 0.17694 | 0.19753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 830049 | 1552 | 816786 | 1576 | 301445.957 | 906.933 | 3.2585 | 3.3109 | 3.305 | 3.248 | 3.3031 | 3.2956 | 4.074 | 4.0252 | 3.9913 | 4.0072 | 3.9709 | 4.0442 | 610000 | 1000 | 607000 | 2000 | 1210357 | 5266 | 1214000 | 1205091 | 10.3 | 3.2868 | 0.85292 | 4.0188 | 0.18485 | 25.95% | 4.6% | 13.5716 | 22.7319 | 3.2703 | 6.0403 | 1219355.8 | 1180067 | 1320428.8994 | 89.37% | 22 | 26369
2025-01-14 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 335090.89 | 7:44 | 18:15 | 9730.4 | 10193.3 | 10145.1 | 10118.1 | 10166.1 | 10245.9 | 10211.8 | 10636 | 10152.9 | 10136.4 | 9991.4 | 10181.2 | 10092.1 | 10098.5 | 10104.4 | 10179 | 10052 | 10132 | 10162.2 | 10217.4 | 10127.6 | 10130.6 | 9890 | 10023.7 | 9881 | 8674.2 | 9912 | 9867.6 | 10164.5 | 10046.8 | 9906 | 10144 | 10187 | 10264.4 | 10186.6 | 10129 | 10281.5 | 10131.6 | 10176.3 | 10047.4 | 11014.2 | 9735.9 | 10860.2 | 9652.3 | 10340 | 11587.5 | 9606 | 11005.1 | 10048.3 | 10256.4 | 10170.8 | 9596.4 | 10456.7 | 10025.8 | 10527 | 10183.8 | 9319.1 | 10789.5 | 9320.3 | 10685.3 | 10589.8 | 9323.6 | 10333.9 | 9814 | 9901.8 | 9289.6 | 9891.6 | 10327.5 | 10656.9 | 9513.7 | 10497.6 | 9165.4 | 10129.2 | 9957.9 | 9309 | 10521.8 | 9186 | 10636.3 | 9278.2 | 10476.6 | 9568.3 | 10374.5 | 9720 | 10769 | 9547.5 | 10224 | 9439.6 | 8356.6 | 10397.2 | 9948.7 | 9272.2 | 10789.2 | 10404.6 | 9536.9 | 9422.9 | 10523.2 | 9273.4 | 9684.2 | 10560.6 | 9260.2 | 10681.3 | 9242.6 | 10341.3 | 9514.2 | 10446.1 | 8982.2 | 10542.3 | 9464.1 | 10384.9 | 9411.3 | 10500.8 | 9608.5 | 9361.8 | 10333.6 | 9419.3 | 9246.9 | 10426.4 | 10593.6 | 10383.5 | 9432.8 | 10498.3 | 9363.2 | 10137.2 | 9517.5 | 10126.7 | 8765.1 | 10209.6 | 9218.2 | 9600.1 | 9667.9 | 9445.4 | 8176.3 | 9472.6 | 8401.1 | 9476.3 | 9491 | 10997.6 | 9492.9 | 11053 | 9731.6 | 10963.9 | 9621.9 | 9789.4 | 9643.1 | 10638.4 | 11040.5 | 10901.2 | 10815.2 | 10939.6 | 10978.3 | 9807.9 | 10623.9 | 11023.3 | 11073.9 | 11086.6 | 11042.8 | 11065.7 | 9828.8 | 11086 | 9885.4 | 17.65 | 16.98 | 17.44 | 17.23 | 17.05 | 16.87 | 0 | 28.3 | 0 | 0 | 28 | 26.7 | 3.73 | 3.34 | 3.66 | 2.46 | 3.67 | 3.16 | 7.33 | 6.76 | 6.99 | 6.73 | 7.29 | 7.1 | 4.17 | 4.21 | 4.23 | 4.16 | 4.21 | 4.22 | 1.01 | 1.12 | 0.94 | 1.25 | 1.2 | 1.02 | 5.42 | 5.34 | 5.36 | 5.39 | 5.27 | 5.32 | 0.24 | 0.26 | 0.21 | 0.23 | 0.23 | 0.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 830854 | 1554 | 817584 | 1577 | 303042.357 | 912.133 | 4.17 | 4.21 | 4.23 | 4.16 | 4.21 | 4.22 | 5.42 | 5.34 | 5.36 | 5.39 | 5.27 | 5.32 | 805000 | 2000 | 798000 | 1000 | 1596400 | 5200 | 1600000 | 1591200 | 10.5167 | 4.2 | 1.09 | 5.35 | 0.23833 | 25.95% | 4.455% | 17.2033 | 27.6667 | 3.3367 | 7.0333 | 1607186.7 | 1578200 | 1757976.8 | 89.77% | 23 | 2634
2025-01-15 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 335090.89 | 7:43 | 18:14 | 9584.4 | 10042.4 | 9987.3 | 9960.4 | 10012.9 | 10096.7 | 10055.8 | 10487.1 | 10005.1 | 9981.3 | 9850.2 | 10033.8 | 9950.9 | 9957.2 | 9967.3 | 10045.6 | 9918.7 | 10001.8 | 10022.3 | 10077.6 | 9992 | 9991.5 | 9753.6 | 9890.2 | 9737.7 | 8555.2 | 9778 | 9728.5 | 10021.7 | 9894.7 | 9758.6 | 9997.9 | 10019.2 | 10091.9 | 10030.4 | 9971.8 | 10126.1 | 9975.1 | 10018.6 | 9885.3 | 10820.2 | 9563.1 | 10661.9 | 9473.4 | 10144.4 | 11393.7 | 9416 | 10804.7 | 9905.8 | 10106.9 | 10035.9 | 9452.5 | 10410.8 | 9916.2 | 10377.2 | 10054.4 | 9190.4 | 10642.2 | 9183.1 | 10532.7 | 10443.5 | 9189.7 | 10186.2 | 9672.1 | 9778.4 | 9179.9 | 9766 | 10206.8 | 10521.5 | 9403.5 | 10364.7 | 9060.9 | 9997.7 | 9847.8 | 9185.2 | 10396.3 | 9080.5 | 10510.8 | 9167.8 | 10360.2 | 9460.4 | 10256.5 | 9605.8 | 10650.5 | 9436.3 | 10106 | 9323.5 | 8258.7 | 10314.8 | 9847.1 | 9170.1 | 10669.3 | 10274.1 | 9405 | 9288.9 | 10397 | 9206.5 | 9584.5 | 10452.8 | 9155.7 | 10556.6 | 9143.1 | 10220.6 | 9406.8 | 10342.7 | 8872.9 | 10369.6 | 9327.5 | 10243.5 | 9283.4 | 10355.8 | 9466.8 | 9255.2 | 10233 | 9349.9 | 9178.1 | 10331.7 | 10458.1 | 10256.8 | 9296.8 | 10361.9 | 9232.1 | 9997.4 | 9377.5 | 9973.3 | 8642.6 | 10068.7 | 9084.9 | 9439.9 | 9498.3 | 9300.7 | 8044.6 | 9304.6 | 8242.5 | 9343 | 9358.1 | 10834.4 | 9348.1 | 10895 | 9581.8 | 10800.4 | 9466.4 | 9643.4 | 9492.8 | 10509.4 | 10913.7 | 10757.2 | 10666.9 | 10779.1 | 10814.1 | 9660.4 | 10477.4 | 10901.8 | 10956.6 | 10982.7 | 10935.9 | 10953.9 | 9720.3 | 10958.9 | 9762.3 | 18.25 | 17.96 | 18.35 | 18.24 | 18.1 | 18.03 | 0 | 27.73 | 0 | 0 | 27.4 | 26.2 | 4.11 | 3.6 | 4.03 | 2.93 | 3.98 | 3.58 | 7.74 | 7.68 | 7.57 | 7.62 | 7.6 | 7.43 | 4.13 | 4.17 | 4.17 | 4.12 | 4.17 | 4.17 | 1.02 | 1.14 | 0.96 | 1.27 | 1.21 | 1.02 | 5.32 | 5.26 | 5.25 | 5.29 | 5.21 | 5.25 | 0.24 | 0.27 | 0.21 | 0.24 | 0.23 | 0.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 831648 | 1556 | 818372 | 1579 | 304618 | 917.2 | 4.13 | 4.17 | 4.17 | 4.12 | 4.17 | 4.17 | 5.32 | 5.26 | 5.25 | 5.29 | 5.21 | 5.25 | 794000 | 2000 | 788000 | 2000 | 1575643 | 5067 | 1578000 | 1570576 | 10.5167 | 4.155 | 1.1033 | 5.2633 | 0.24167 | 26.55% | 4.592% | 18.155 | 27.11 | 3.705 | 7.6067 | 1585557.2 | 1559867 | 1735172 | 89.9% | 25 | 0
2025-01-16 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 335090.89 | 7:40 | 18:17 | 9977.6 | 10443 | 10390.6 | 10358 | 10430.7 | 10517.8 | 10461.7 | 10924.1 | 10407.3 | 10439.2 | 10262.3 | 10444.4 | 10365.4 | 10374.9 | 10360.3 | 10446.7 | 10306.7 | 10395.7 | 10420.2 | 10483.9 | 10380.2 | 10383.3 | 10142.3 | 10276 | 10110.5 | 8890.2 | 10170.3 | 10106 | 10408.5 | 10300.9 | 10168.5 | 10392 | 10418.7 | 10489.4 | 10410.6 | 10359.1 | 10535.1 | 10390.9 | 10447.9 | 10297.1 | 11357.2 | 10027.4 | 11180.3 | 9942.3 | 10618.9 | 11934.5 | 9870.6 | 11326.9 | 10298.9 | 10512.1 | 10437.7 | 9836 | 10831.3 | 10311.4 | 10784.6 | 10423.4 | 9554.8 | 11061.6 | 9557.5 | 10966.6 | 10869.2 | 9561.3 | 10597.3 | 10064.2 | 10136.3 | 9514.1 | 10133.7 | 10579 | 10921.1 | 9747.1 | 10758.6 | 9391.5 | 10378.4 | 10211.7 | 9538.4 | 10783.6 | 9423.3 | 10922.2 | 9522.5 | 10758.8 | 9796.3 | 10624.1 | 9934.8 | 11038.3 | 9763.8 | 10454.1 | 9655.9 | 8547.1 | 10697.1 | 10196.8 | 9500.3 | 11065.7 | 10665.9 | 9765 | 9648.8 | 10795 | 9571.6 | 9953.3 | 10855.9 | 9521.3 | 10995.5 | 9520.6 | 10654.1 | 9801.6 | 10800.1 | 9284.8 | 10866.1 | 9746.3 | 10703.6 | 9728.1 | 10817.5 | 9891.3 | 9618.9 | 10651.2 | 9753.2 | 9570.3 | 10763.8 | 10901.9 | 10694.2 | 9682.8 | 10811.2 | 9629.8 | 10428.3 | 9791.3 | 10415.4 | 9011.6 | 10498.2 | 9476.9 | 9821.2 | 9852.1 | 9691.5 | 8380.4 | 9674 | 8561.6 | 9659.4 | 9678.6 | 11249.4 | 9699.5 | 11315 | 9946.3 | 11203.8 | 9808.5 | 9994.6 | 9817.8 | 10900.1 | 11324.2 | 11157.2 | 11058.4 | 11185.6 | 11221 | 10027.4 | 10870.1 | 11303.9 | 11359.1 | 11383.9 | 11343.4 | 11366.6 | 10084.1 | 11361.9 | 10125.5 | 18.9514 | 18.6479 | 19.1008 | 18.8548 | 18.7217 | 18.4856 | 0 | 31.6284 | 0 | 0 | 32 | 29.6 | 2.5621 | 1.8063 | 2.5937 | 0.76502 | 2.4281 | 2.0222 | 6.3383 | 5.1633 | 5.7667 | 5.07 | 6.065 | 5.5517 | 4.2971 | 4.314 | 4.3606 | 4.2688 | 4.3523 | 4.3039 | 1.0672 | 1.1838 | 1.0013 | 1.3221 | 1.2641 | 1.059 | 5.6158 | 5.5228 | 5.5714 | 5.5625 | 5.5014 | 5.5 | 0.24523 | 0.26856 | 0.21819 | 0.2399 | 0.23552 | 0.2657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 832474 | 1558 | 819191 | 1581 | 306256.824 | 922.333 | 4.2971 | 4.314 | 4.3606 | 4.2688 | 4.3523 | 4.3039 | 5.6158 | 5.5228 | 5.5714 | 5.5625 | 5.5014 | 5.5 | 826000 | 2000 | 819000 | 2000 | 1638824 | 5133 | 1641000 | 1633691 | 10.6167 | 4.3161 | 1.1496 | 5.5457 | 0.24552 | 26.63% | 4.427% | 18.7937 | 31.0761 | 2.0296 | 5.6592 | 1648920.1 | 1617401 | 1800443.0424 | 89.83% | 20 | 0
2025-01-17 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 335090.89 | 7:40 | 18:18 | 10620.5 | 10998.1 | 10928.7 | 10925.4 | 10959.1 | 11030.4 | 10986.8 | 11290.3 | 10947.4 | 10959.1 | 10818.6 | 10962.6 | 10907.8 | 10896.1 | 10936.1 | 10990.5 | 10877.8 | 10952 | 10967.8 | 11038.5 | 10944.1 | 10962.3 | 10780.4 | 10880.9 | 10748.4 | 9541 | 10786 | 10744.1 | 10978.6 | 10876.7 | 10787.1 | 10959.5 | 11164.4 | 11237.5 | 11157.9 | 11114.1 | 11071.4 | 10966 | 10993.7 | 10873.4 | 11623.9 | 10675.2 | 11489.3 | 10606.3 | 11154.1 | 12042.8 | 10539.9 | 11593.8 | 10855.6 | 11032 | 10989.6 | 10511.6 | 11269 | 10865.3 | 11246.7 | 10961.8 | 10245.7 | 11436.2 | 10226.3 | 11367.8 | 11300.6 | 10235.4 | 11085.5 | 10694 | 10766 | 10208 | 10761.2 | 11097.7 | 11305.6 | 10443 | 11206.1 | 10072.4 | 10924.8 | 10822.8 | 10217.8 | 11223.3 | 10100.8 | 11304.3 | 10194.8 | 11209.6 | 10505.4 | 11143.4 | 10629.4 | 11430.4 | 10472.1 | 11023.9 | 10344.6 | 9180.3 | 11180.3 | 10804 | 10211.5 | 11437.7 | 11163.9 | 10472.1 | 10342.6 | 11230.4 | 10275.8 | 10629.4 | 11274 | 10212.4 | 11373.2 | 10192.2 | 11152.6 | 10479.5 | 11222.8 | 9932.4 | 11292.5 | 10418.5 | 11194.4 | 10394.9 | 11263.9 | 10560.9 | 10308.8 | 11133.2 | 10427.2 | 10242.2 | 11196.2 | 11311.1 | 11156.8 | 10368.8 | 11232.4 | 10305.8 | 10964.6 | 10465.8 | 10966.7 | 9645.7 | 11033.5 | 10142.8 | 10502.8 | 10538.4 | 10370.4 | 8973 | 10359.2 | 9195.1 | 10364.6 | 10383.9 | 11539.9 | 10383.1 | 11583.1 | 10610.5 | 11496.6 | 10486.5 | 10637.2 | 10509.6 | 11339 | 11600.4 | 11514.2 | 11436.4 | 11521.4 | 11534.5 | 10685 | 11301 | 11619.3 | 11649.3 | 11648.4 | 11622.4 | 11653.1 | 10750.1 | 11663.7 | 10785.3 | 18.13 | 17.6445 | 18.2911 | 17.8029 | 17.7324 | 17.7517 | 0 | 28.2625 | 0 | 0 | 27.9 | 26.7 | 4.9268 | 4.4319 | 4.7717 | 3.887 | 4.8286 | 4.3126 | 9.175 | 8.59 | 8.6183 | 8.7917 | 8.9067 | 8.9067 | 4.5406 | 4.5843 | 4.6156 | 4.5281 | 4.5969 | 4.5602 | 1.1467 | 1.2333 | 1.0767 | 1.4195 | 1.3412 | 1.1212 | 5.9451 | 5.8823 | 5.9163 | 5.9159 | 5.8332 | 5.854 | 0.25909 | 0.28219 | 0.22902 | 0.25211 | 0.24866 | 0.28113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 833344 | 1560 | 820053 | 1583 | 307981.491 | 927.467 | 4.5406 | 4.5843 | 4.6156 | 4.5281 | 4.5969 | 4.5602 | 5.9451 | 5.8823 | 5.9163 | 5.9159 | 5.8332 | 5.854 | 870000 | 2000 | 862000 | 2000 | 1724667 | 5134 | 1728000 | 1719533 | 10.6333 | 4.571 | 1.2231 | 5.8911 | 0.2587 | 26.76% | 4.391% | 17.8921 | 27.6208 | 4.5264 | 8.8314 | 1737068.1 | 1709133 | 1941436.0054 | 88.03% | 27 | 1231
2025-01-18 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 335090.89 | 7:42 | 18:16 | 9541.5 | 9995.6 | 9916.9 | 9901.1 | 9948.2 | 10038.3 | 9983.4 | 10419 | 9950.3 | 9987.2 | 9797.1 | 9964.3 | 9886.1 | 9891.5 | 9871.2 | 9959.1 | 9814.4 | 9898.3 | 9921.3 | 9991.2 | 9887.9 | 9890.6 | 9670.5 | 9792.8 | 9633.6 | 8478 | 9696.7 | 9629.7 | 9927.3 | 9828.4 | 9694.6 | 9906.5 | 9915 | 9989 | 9931 | 9869.5 | 10029.1 | 9894 | 9945.1 | 9809.2 | 10761.2 | 9540.9 | 10606.6 | 9458.6 | 10057.8 | 11305.3 | 9338 | 10720.9 | 9840.1 | 10041.4 | 9975.4 | 9398.5 | 10328.3 | 9829.8 | 10313.1 | 9974.3 | 9137.5 | 10579.2 | 9127.9 | 10480.8 | 10394.3 | 9132.7 | 10134.5 | 9625.8 | 9724.3 | 9127.7 | 9711.8 | 10151 | 10465.4 | 9354.3 | 10304.6 | 9012.4 | 9945.3 | 9789.1 | 9146 | 10339.3 | 9038.4 | 10464.1 | 9129.1 | 10319.9 | 9413.4 | 10208 | 9540.1 | 10593.8 | 9370.7 | 10033.2 | 9266.8 | 8203.3 | 10235.8 | 9784.7 | 9083.3 | 10562.3 | 10168.9 | 9301.9 | 9180.9 | 10274.2 | 9104.8 | 9484.1 | 10342.4 | 9058.6 | 10439.8 | 9044.5 | 10115.4 | 9302.8 | 10259.9 | 8815.8 | 10325 | 9258.2 | 10170.2 | 9235.6 | 10262.7 | 9392.9 | 9146.3 | 10108.4 | 9258 | 9083.9 | 10229 | 10349.2 | 10158.3 | 9203.8 | 10269.9 | 9144.8 | 9912.9 | 9301.6 | 9890.9 | 8566 | 9983 | 9000.3 | 9318.7 | 9355.7 | 9198.9 | 7950 | 9168.1 | 8126.8 | 9236.4 | 9261.9 | 10756.3 | 9278.7 | 10809.3 | 9512.7 | 10705.3 | 9371.3 | 9544.7 | 9388.6 | 10426.6 | 10830.6 | 10673.9 | 10589.3 | 10694.3 | 10731.4 | 9584.6 | 10393.2 | 10831.7 | 10880.3 | 10905.4 | 10859.8 | 10876.2 | 9647.4 | 10876.3 | 9696.2 | 19.347 | 19.006 | 19.5227 | 19.2895 | 19.1944 | 19.0928 | 0 | 31.6574 | 0 | 0 | 31.6 | 30.3 | 2.6561 | 2.4876 | 2.5249 | 0.86486 | 2.581 | 1.8496 | 5.01 | 5.075 | 4.7233 | 4.9667 | 4.6167 | 4.3133 | 4.1699 | 4.1782 | 4.192 | 4.1598 | 4.1934 | 4.1791 | 1.0363 | 1.1067 | 0.96291 | 1.2843 | 1.2054 | 1.0112 | 5.3616 | 5.2727 | 5.2809 | 5.3443 | 5.2298 | 5.257 | 0.23581 | 0.25632 | 0.21005 | 0.23179 | 0.22422 | 0.25244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 834133 | 1562 | 820835 | 1584 | 309545.024 | 932.733 | 4.1699 | 4.1782 | 4.192 | 4.1598 | 4.1934 | 4.1791 | 5.3616 | 5.2727 | 5.2809 | 5.3443 | 5.2298 | 5.257 | 789000 | 2000 | 782000 | 1000 | 1563533 | 5266 | 1568000 | 1558267 | 10.5667 | 4.1787 | 1.1011 | 5.291 | 0.23511 | 26.35% | 4.443% | 19.242 | 31.1858 | 2.1607 | 4.7842 | 1573141 | 1546133 | 1723823.3796 | 89.69% | 28 | 0
2025-01-19 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 335090.89 | 7:41 | 18:18 | 9924.5 | 10397 | 10326.7 | 10293.2 | 10358.3 | 10456.3 | 10380.4 | 10842 | 10335.6 | 10385 | 10190 | 10355.8 | 10297.1 | 10302.3 | 10285.8 | 10373.9 | 10247.8 | 10337.9 | 10367.1 | 10425.7 | 10334.3 | 10333.2 | 10093.1 | 10229.8 | 10063.8 | 8835.7 | 10104.2 | 10059.5 | 10364 | 10242.9 | 10098.5 | 10333 | 10344.5 | 10412.2 | 10354.2 | 10294.4 | 10469.2 | 10317.5 | 10369 | 10215.1 | 11256.7 | 9948.7 | 11089.2 | 9862.8 | 10515.2 | 11788.6 | 9785.7 | 11232.7 | 10233.4 | 10438.1 | 10375.4 | 9758.7 | 10751.2 | 10237.9 | 10702.3 | 10361.9 | 9469.8 | 10953 | 9482 | 10862.4 | 10765.5 | 9478.9 | 10501.9 | 9975.4 | 10068.6 | 9452.4 | 10047.4 | 10506.5 | 10822.8 | 9679.9 | 10665.9 | 9322.6 | 10283.2 | 10130.6 | 9467.6 | 10691.3 | 9351 | 10839.7 | 9460.1 | 10686.8 | 9740 | 10553.7 | 9867.7 | 10974.9 | 9711.9 | 10397.5 | 9605.2 | 8509.5 | 10613.2 | 10148.8 | 9434.2 | 10974.2 | 10568.2 | 9674.3 | 9556.4 | 10692.9 | 9480.5 | 9889 | 10790.3 | 9456.7 | 10882.9 | 9444.7 | 10546.4 | 9709.6 | 10688.9 | 9194.7 | 10756.6 | 9659.3 | 10597.6 | 9624.6 | 10717.2 | 9815.9 | 9542.8 | 10559.3 | 9671.6 | 9491.6 | 10672.6 | 10804.7 | 10605 | 9601.7 | 10718.8 | 9552.8 | 10349.3 | 9718.9 | 10337.1 | 8946.4 | 10419.7 | 9397.9 | 9721.2 | 9750.3 | 9592.3 | 8295 | 9573.1 | 8472.1 | 9598 | 9619.6 | 11198.7 | 9659.6 | 11252.3 | 9902 | 11140.8 | 9752.8 | 9944.4 | 9754.3 | 10842.8 | 11260.3 | 11100.2 | 11013.6 | 11135.5 | 11171.4 | 9983 | 10816.4 | 11201.5 | 11268.3 | 11293.2 | 11263.1 | 11288 | 10022.2 | 11282.5 | 10067.2 | 20.9072 | 20.7458 | 20.8777 | 21.2097 | 20.9673 | 20.8285 | 0 | 34.6429 | 0 | 0 | 34.5 | 33.2 | 2.5872 | 2.1731 | 2.5465 | 0.47371 | 2.5292 | 1.8306 | 4.7733 | 4.63 | 4.59 | 3.5217 | 5.6383 | 5.205 | 4.3569 | 4.4194 | 4.4084 | 4.3296 | 4.4125 | 4.3726 | 1.0777 | 1.1885 | 1.009 | 1.3367 | 1.2809 | 1.075 | 5.6275 | 5.5757 | 5.572 | 5.5857 | 5.5237 | 5.5379 | 0.24181 | 0.26361 | 0.21504 | 0.23459 | 0.23088 | 0.26112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 834953 | 1563 | 821648 | 1586 | 311171.491 | 938 | 4.3569 | 4.4194 | 4.4084 | 4.3296 | 4.4125 | 4.3726 | 5.6275 | 5.5757 | 5.572 | 5.5857 | 5.5237 | 5.5379 | 820000 | 1000 | 813000 | 2000 | 1626467 | 5267 | 1630000 | 1621200 | 10.6167 | 4.3832 | 1.1613 | 5.5704 | 0.24118 | 26.49% | 4.33% | 20.9227 | 34.1143 | 2.0234 | 4.7264 | 1636957.7 | 1604532 | 1788616.1317 | 89.71% | 30 | 0
2025-01-20 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 335090.89 | 7:42 | 18:18 | 9634.6 | 10076.3 | 10016.7 | 9991.4 | 10035.7 | 10132 | 10069.7 | 10455.5 | 10033.7 | 10074.8 | 9869.9 | 10043.1 | 9970.2 | 9971.9 | 9987 | 10064.6 | 9941.7 | 10031.7 | 10048.7 | 10098 | 10027.9 | 10022.8 | 9810.5 | 9934 | 9767.4 | 8575.1 | 9796 | 9747 | 10063.3 | 9959.5 | 9826.2 | 10044.4 | 10049.9 | 10126.4 | 10058.4 | 9995.3 | 10163.7 | 10028 | 10078.8 | 9941.1 | 10969.1 | 9693.9 | 10799.4 | 9592.3 | 10227.7 | 11519.2 | 9524.6 | 10946.4 | 9915.7 | 10125.6 | 10058.3 | 9466.8 | 10424 | 9909.5 | 10395.5 | 10059.8 | 9203.7 | 10659 | 9202.5 | 10565.9 | 10472.7 | 9213.8 | 10211.7 | 9698 | 9808.2 | 9203 | 9787.3 | 10239.6 | 10546.9 | 9428.7 | 10390.9 | 9082.3 | 10021.6 | 9870.4 | 9213.8 | 10416.3 | 9096.9 | 10546.7 | 9195.3 | 10385.1 | 9487.5 | 10288.7 | 9611.7 | 10684 | 9450.8 | 10112.2 | 9346.5 | 8275.2 | 10300 | 9866.3 | 9170.7 | 10665 | 10278.7 | 9410.9 | 9290.1 | 10394.7 | 9152.7 | 9587.4 | 10469.9 | 9171.9 | 10574.8 | 9168.7 | 10244.8 | 9429.7 | 10384.3 | 8928.2 | 10451.7 | 9377.9 | 10294.4 | 9354.2 | 10390.2 | 9517 | 9252 | 10214.2 | 9253.7 | 9110.7 | 10238.9 | 10394 | 10283.6 | 9314.2 | 10386.6 | 9253.7 | 10035.1 | 9415 | 10007 | 8662.3 | 10096.1 | 9102.3 | 9408.9 | 9439.3 | 9285.7 | 8030.5 | 9285.2 | 8219.7 | 9282.5 | 9309.4 | 10854.8 | 9360.2 | 10924.7 | 9602.6 | 10809.4 | 9464.6 | 9637.9 | 9461.2 | 10520.3 | 10930.1 | 10774.9 | 10688.3 | 10798.7 | 10835.5 | 9687.1 | 10501.5 | 10902.7 | 10951.9 | 10978.6 | 10934.9 | 10953.9 | 9723.6 | 10960.4 | 9768.1 | 20.65 | 20.43 | 20.83 | 20.72 | 20.71 | 20.64 | 0 | 32.79 | 0 | 0 | 32.8 | 31.5 | 2.72 | 2.17 | 2.65 | 1.16 | 2.61 | 2 | 4.44 | 4.34 | 4.34 | 4.57 | 4.55 | 4.5 | 4.21 | 4.27 | 4.29 | 4.21 | 4.27 | 4.23 | 1.04 | 1.18 | 0.98 | 1.29 | 1.23 | 1.04 | 5.4 | 5.36 | 5.38 | 5.38 | 5.3 | 5.32 | 0.24 | 0.26 | 0.21 | 0.23 | 0.23 | 0.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 835750 | 1565 | 822436 | 1588 | 312750.624 | 943.267 | 4.21 | 4.27 | 4.29 | 4.21 | 4.27 | 4.23 | 5.4 | 5.36 | 5.38 | 5.38 | 5.3 | 5.32 | 797000 | 2000 | 788000 | 2000 | 1579133 | 5267 | 1581000 | 1573866 | 10.6 | 4.2467 | 1.1267 | 5.3567 | 0.23833 | 26.53% | 4.449% | 20.6633 | 32.3633 | 2.2183 | 4.4567 | 1589088.3 | 1562133 | 1734074.7066 | 90.08% | 29 | 0
2025-01-21 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 335090.89 | 7:43 | 18:17 | 9153.7 | 9587 | 9544 | 9521.7 | 9561.8 | 9664.8 | 9624.1 | 10043.2 | 9553 | 9579.6 | 9404.1 | 9561.6 | 9519.6 | 9502.9 | 9536.4 | 9615.6 | 9494.1 | 9585.6 | 9604 | 9641.2 | 9595.4 | 9582.4 | 9392.4 | 9510.5 | 9350 | 8198.5 | 9356.6 | 9329.1 | 9637.6 | 9544.4 | 9408 | 9611.3 | 9610.2 | 9682.2 | 9624.4 | 9564.2 | 9718 | 9595.1 | 9643 | 9509.8 | 10506.5 | 9296.8 | 10356 | 9199.2 | 9814.6 | 11065.9 | 9130.3 | 10483.2 | 9455.5 | 9650.9 | 9587.1 | 9021.1 | 9954.2 | 9464.1 | 9906.5 | 9611.3 | 8759.6 | 10144.5 | 8758.5 | 10058.7 | 9964.7 | 8760.9 | 9705.8 | 9216.7 | 9344.2 | 8778 | 9322.2 | 9775.1 | 10044.4 | 9000.6 | 9906.7 | 8671.8 | 9543.6 | 9415.9 | 8780.1 | 9935.5 | 8678.5 | 10048.7 | 8768.5 | 9915 | 9062 | 9823 | 9180.7 | 10208.2 | 9027.7 | 9665 | 8939.4 | 7909 | 9863.2 | 9440.3 | 8767.5 | 10194.5 | 9820.4 | 8984.4 | 8873.8 | 9948.2 | 8798.6 | 9191.7 | 10023.5 | 8793.5 | 10118 | 8783.4 | 9816.1 | 9035 | 9962 | 8561.9 | 10034.5 | 9003.1 | 9889.1 | 8983.1 | 9985.7 | 9142.3 | 8877.3 | 9824.4 | 8929 | 8827.4 | 9949.8 | 10076.3 | 9884.6 | 8967.5 | 9996.7 | 8900.7 | 9642.2 | 9043.2 | 9612 | 8330.5 | 9714.6 | 8760.5 | 9062 | 9091.2 | 8933 | 7727.2 | 8934.5 | 7909.4 | 8919.6 | 8942.7 | 10403.6 | 8980.9 | 10455.8 | 9202.9 | 10369.2 | 9074.6 | 9243.9 | 9071.5 | 10074.1 | 10468.8 | 10320.1 | 10233.8 | 10334 | 10374.8 | 9266.4 | 10045 | 10446.4 | 10497.4 | 10513 | 10478.9 | 10505.7 | 9320.6 | 10506 | 9364.1 | 22.1 | 21.6 | 21.87 | 21.91 | 21.68 | 21.48 | 0 | 33.47 | 0 | 0 | 33.3 | 32.1 | 2.75 | 2.54 | 2.71 | 1.08 | 2.74 | 2.23 | 4.73 | 4.9 | 4.66 | 4.88 | 5.61 | 4.58 | 4.08 | 4.15 | 4.16 | 4.06 | 4.15 | 4.11 | 1.03 | 1.15 | 0.96 | 1.27 | 1.21 | 1.02 | 5.18 | 5.15 | 5.18 | 5.16 | 5.11 | 5.11 | 0.23 | 0.26 | 0.21 | 0.23 | 0.23 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 836511 | 1567 | 823193 | 1589 | 314262.825 | 948.4 | 4.08 | 4.15 | 4.16 | 4.06 | 4.15 | 4.11 | 5.18 | 5.15 | 5.18 | 5.16 | 5.11 | 5.11 | 761000 | 2000 | 757000 | 1000 | 1512201 | 5133 | 1515000 | 1507068 | 10.5667 | 4.1183 | 1.1067 | 5.1483 | 0.235 | 26.87% | 4.565% | 21.7733 | 32.9567 | 2.3417 | 4.8933 | 1520799.1 | 1491334 | 1659252.1174 | 89.88% | 27 | 0
2025-01-22 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 335090.89 | 7:46 | 18:19 | 9326.3 | 9767.8 | 9732.9 | 9684.8 | 9765.2 | 9853 | 9789.9 | 10219.3 | 9738.6 | 9779.5 | 9598 | 9762.2 | 9692.3 | 9697.5 | 9712.5 | 9790 | 9678.9 | 9777.3 | 9799.5 | 9835.6 | 9781.7 | 9777.4 | 9566.5 | 9692.1 | 9525 | 8355 | 9545.5 | 9505.7 | 9820.2 | 9721.8 | 9596.9 | 9802.8 | 9828.1 | 9881.9 | 9812.3 | 9765.8 | 9932.2 | 9793.1 | 9844.9 | 9712.9 | 10704.6 | 9466.2 | 10547.3 | 9372.9 | 9986.4 | 11247.7 | 9295.2 | 10683.5 | 9647.4 | 9844.4 | 9785.2 | 9221.7 | 10155.4 | 9637.7 | 10116.3 | 9805.1 | 8953.3 | 10375.5 | 8929.8 | 10267.9 | 10161.4 | 8925.6 | 9916.5 | 9406.1 | 9544.2 | 8983.3 | 9528.8 | 10006.5 | 10266.3 | 9201.6 | 10122.8 | 8862 | 9745.1 | 9616.3 | 8957.7 | 10138.3 | 8854.9 | 10247.8 | 8941 | 10095.1 | 9278.2 | 10043.7 | 9403.3 | 10460.5 | 9261 | 9913.8 | 9161.6 | 8109.1 | 10096.5 | 9681.2 | 8981.4 | 10449.3 | 10059.9 | 9206.9 | 9099.4 | 10207.6 | 9025.2 | 9434.9 | 10278.5 | 9019.2 | 10365.7 | 8998.6 | 10046.7 | 9243.4 | 10175.2 | 8752.6 | 10239.3 | 9193.9 | 10075.1 | 9157.4 | 10168.4 | 9323 | 9092 | 10035.4 | 9194.1 | 9026.2 | 10149.6 | 10276.3 | 10078.6 | 9132.7 | 10185.7 | 9074.6 | 9836.4 | 9225.5 | 9797.4 | 8486.8 | 9899.4 | 8925.1 | 9219.9 | 9238.3 | 9087.9 | 7864.2 | 9093.3 | 8055.6 | 9096.7 | 9122.7 | 10656.9 | 9193.3 | 10716.8 | 9417.2 | 10605.1 | 9282.7 | 9465.6 | 9261.8 | 10340.7 | 10746.4 | 10602.8 | 10508.6 | 10608.6 | 10641.8 | 9511.7 | 10314.6 | 10722.4 | 10774.6 | 10780 | 10750 | 10777.3 | 9563.4 | 10789.3 | 9607.5 | 21.98 | 21.85 | 22.13 | 22.29 | 22.08 | 21.9 | 0 | 34.59 | 0 | 0 | 34.6 | 33.4 | 2.6 | 2.11 | 2.53 | 0.72 | 2.57 | 2.47 | 5.36 | 5.57 | 5.6 | 4.37 | 5.1 | 5.23 | 4.16 | 4.23 | 4.25 | 4.16 | 4.26 | 4.23 | 1.03 | 1.16 | 0.97 | 1.29 | 1.25 | 1.06 | 5.27 | 5.26 | 5.29 | 5.27 | 5.25 | 5.27 | 0.24 | 0.26 | 0.22 | 0.23 | 0.23 | 0.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 837287 | 1570 | 823967 | 1591 | 315807.291 | 953.533 | 4.16 | 4.23 | 4.25 | 4.16 | 4.26 | 4.23 | 5.27 | 5.26 | 5.29 | 5.27 | 5.25 | 5.27 | 776000 | 3000 | 774000 | 2000 | 1544466 | 5133 | 1545000 | 1539333 | 10.55 | 4.215 | 1.1267 | 5.2683 | 0.24 | 26.73% | 4.556% | 22.0383 | 34.1967 | 2.1667 | 5.205 | 1553571.7 | 1527667 | 1697582.1689 | 89.99% | 29 | 0
2025-01-23 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 335090.89 | 7:41 | 18:23 | 10908.9 | 11279.1 | 11216.9 | 11206.1 | 11236.4 | 11323.5 | 11282.3 | 11582 | 11235.8 | 11214.2 | 11109.2 | 11245.5 | 11201.7 | 11191.7 | 11199.6 | 11279.2 | 11156 | 11248.2 | 11260.4 | 11325.3 | 11236.3 | 11251.2 | 11076 | 11177.9 | 11036.3 | 9823.9 | 11070.9 | 11025.9 | 11264.9 | 11156.2 | 11064.5 | 11235.7 | 11480.1 | 11541.5 | 11476.8 | 11433.3 | 11352.7 | 11239.3 | 11265.8 | 11144.3 | 11907.2 | 10952.4 | 11764.2 | 10884.4 | 11405.1 | 12318.9 | 10798.8 | 11872.4 | 11127.1 | 11309.8 | 11282.9 | 10800.2 | 11564.7 | 11122.3 | 11530.9 | 11229.7 | 10542.6 | 11726.8 | 10534.2 | 11658.7 | 11590.5 | 10529.5 | 11378.5 | 10978.4 | 11071.4 | 10533.9 | 11070.2 | 11422.5 | 11611.9 | 10757.2 | 11518.3 | 10403.4 | 11232.2 | 11134.8 | 10535.7 | 11523.8 | 10422.1 | 11617 | 10515.6 | 11510.2 | 10825 | 11456.2 | 10928.8 | 11754.2 | 10785.2 | 11332.5 | 10663.4 | 9484.8 | 11460.1 | 11121 | 10529.7 | 11733.2 | 11434.5 | 10734.2 | 10609.4 | 11522.9 | 10542.8 | 10932.6 | 11556.6 | 10528.2 | 11661.6 | 10513.4 | 11446.5 | 10773.8 | 11511.6 | 10239.7 | 11582.1 | 10723.3 | 11478.6 | 10698.2 | 11544.9 | 10873.2 | 10613.4 | 11412.9 | 10716.2 | 10555 | 11468.7 | 11600.5 | 11441.2 | 10662.7 | 11524.8 | 10609.8 | 11256.2 | 10769.1 | 11251.5 | 9942 | 11327.3 | 10451.7 | 10763.3 | 10772.5 | 10625.7 | 9219.7 | 10622.2 | 9438.8 | 10639.9 | 10671.1 | 11850.5 | 10704 | 11890.3 | 10915.9 | 11802.6 | 10795.1 | 10954 | 10798 | 11654.6 | 11921.5 | 11834.8 | 11752.6 | 11834 | 11848.6 | 10993.6 | 11615.1 | 11924.2 | 11957.6 | 11958.8 | 11932.2 | 11965.3 | 11059.3 | 11980.9 | 11094.1 | 19.82 | 19.74 | 19.84 | 20.01 | 19.72 | 19.7 | 0 | 31.12 | 0 | 0 | 30.8 | 29.4 | 4.05 | 3.9 | 4.04 | 2.45 | 3.84 | 3.83 | 7.32 | 6.98 | 7.3 | 6.83 | 7.19 | 6.73 | 4.72 | 4.8 | 4.8 | 4.71 | 4.79 | 4.78 | 1.19 | 1.33 | 1.12 | 1.48 | 1.41 | 1.2 | 6.13 | 6.07 | 6.1 | 6.11 | 6.04 | 6.04 | 0.26 | 0.28 | 0.23 | 0.25 | 0.25 | 0.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 838181 | 1571 | 824853 | 1593 | 317579.425 | 958.6 | 4.72 | 4.8 | 4.8 | 4.71 | 4.79 | 4.78 | 6.13 | 6.07 | 6.1 | 6.11 | 6.04 | 6.04 | 894000 | 1000 | 886000 | 2000 | 1772134 | 5067 | 1777000 | 1767067 | 10.7 | 4.7667 | 1.2883 | 6.0817 | 0.26 | 27.03% | 4.275% | 19.805 | 30.44 | 3.685 | 7.0583 | 1784121.9 | 1757200 | 1981575.6681 | 88.68% | 29 | 3035
2025-01-24 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 335090.89 | 7:36 | 18:26 | 10812.3 | 11171 | 11396.4 | 11390.5 | 11405.6 | 11509.6 | 11482.5 | 11777.7 | 11418.9 | 11414 | 11296.3 | 11426.8 | 11392 | 11378.3 | 11370.4 | 11464.1 | 11333.1 | 11428 | 11449 | 11523.5 | 11415.7 | 11433.5 | 11251.7 | 11357.9 | 11220.8 | 9982.1 | 11263.9 | 11217.5 | 11449.3 | 11335.2 | 11245.4 | 11413.6 | 11664.6 | 11741.8 | 11667.8 | 11615.5 | 11541.6 | 11427.4 | 11448.9 | 11329.1 | 12113 | 11112.9 | 11967.2 | 11040.4 | 11569.9 | 12532.5 | 10958 | 12079.3 | 11311.4 | 11500.3 | 11480.3 | 10984.8 | 11770.6 | 11321.4 | 11736.8 | 11415.9 | 10701.1 | 11936.9 | 10690.1 | 11872.3 | 11800.2 | 10700.8 | 11562.6 | 11157.2 | 11251.1 | 10687.8 | 11253.8 | 11620.4 | 11820 | 10941 | 11722 | 10556.2 | 11417 | 11322.8 | 10698.3 | 11731 | 10572.5 | 11824.9 | 10664.3 | 11706.8 | 11020.5 | 11666.3 | 11120.8 | 11981 | 10973.3 | 11531.1 | 10833.7 | 9624.4 | 11646.3 | 11301 | 10695.8 | 11936.5 | 11627.5 | 10901.3 | 10762.5 | 11713.4 | 10724.7 | 11107.6 | 11762.9 | 10697.9 | 11877 | 10671 | 11651.8 | 10943.1 | 11720 | 10395.2 | 11793.6 | 10912 | 11687.7 | 10881.8 | 11743.9 | 11065.1 | 10780 | 11623.3 | 10890.9 | 10719.5 | 11676.6 | 11815.2 | 11642.2 | 10856 | 11730.9 | 10786.3 | 11452.8 | 10960.6 | 11446.9 | 10102 | 11524.7 | 10644.2 | 10968.8 | 10985.7 | 10784 | 9372.7 | 10775.3 | 9563 | 10797.8 | 10831.9 | 12070.7 | 10868.6 | 12116.2 | 11091.2 | 12017.2 | 10953.4 | 11109.4 | 10968.5 | 11858.7 | 12141.8 | 12046.4 | 11960.9 | 12052.2 | 12071.7 | 11173.5 | 12045 | 12147.5 | 12180.2 | 12183.2 | 12155.3 | 12191.7 | 11235.7 | 12201.4 | 11271.1 | 21.12 | 20.73 | 21.4 | 20.91 | 20.88 | 20.65 | 0 | 33.33 | 0 | 0 | 33 | 31.4 | 3.7 | 3.51 | 3.73 | 2.12 | 3.71 | 3.36 | 7.14 | 6.56 | 6.83 | 5.89 | 7.36 | 7.05 | 4.83 | 4.9 | 4.89 | 4.82 | 4.9 | 4.87 | 1.23 | 1.34 | 1.14 | 1.52 | 1.44 | 1.22 | 6.28 | 6.22 | 6.24 | 6.26 | 6.18 | 6.16 | 0.27 | 0.29 | 0.24 | 0.26 | 0.26 | 0.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 839088 | 1573 | 825760 | 1594 | 319380.892 | 963.6 | 4.83 | 4.9 | 4.89 | 4.82 | 4.9 | 4.87 | 6.28 | 6.22 | 6.24 | 6.26 | 6.18 | 6.16 | 907000 | 2000 | 907000 | 1000 | 1801467 | 5000 | 1811000 | 1796467 | 10.8333 | 4.8683 | 1.315 | 6.2233 | 0.26833 | 27.01% | 4.312% | 20.9483 | 32.5767 | 3.355 | 6.805 | 1813782.6 | 1790934 | 2018039.9745 | 88.75% | 29 | 3740
2025-01-25 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 335090.89 | 7:35 | 18:28 | 11290.2 | 11670.8 | 11599.9 | 11588.3 | 11611.3 | 11712.4 | 11674.1 | 11966.7 | 11629.1 | 11663.3 | 11509.6 | 11650.1 | 11598.2 | 11591.1 | 11576 | 11666.8 | 11539.8 | 11635.3 | 11661.7 | 11734.8 | 11626 | 11645 | 11451.3 | 11565.9 | 11423.2 | 10159.5 | 11462.6 | 11419.5 | 11654.6 | 11537 | 11446.2 | 11622.4 | 11875.8 | 11945.6 | 11882.7 | 11831.2 | 11755 | 11638.5 | 11659.8 | 11533.1 | 12360.5 | 11363.3 | 12214.7 | 11293.8 | 11802.4 | 12749.5 | 11191.2 | 12319.5 | 11518.6 | 11712.2 | 11686.1 | 11187.4 | 11975.5 | 11530.6 | 11946.4 | 11614.1 | 10895.6 | 12147.8 | 10889 | 12087.9 | 12012 | 10886.5 | 11776.8 | 11362.2 | 11454.4 | 10885.4 | 11462 | 11836.4 | 12030.3 | 11144.5 | 11927.8 | 10753 | 11623.9 | 11528.5 | 10895.7 | 11936.2 | 10766.4 | 12034 | 10869.5 | 11911.8 | 11228 | 11885.1 | 11328.1 | 12197.8 | 11179.2 | 11738.3 | 11035.6 | 9805 | 11851.6 | 11502.1 | 10880.4 | 12145.5 | 11823.7 | 11071.1 | 10924.1 | 11911.9 | 10891 | 11302 | 11963.1 | 10882.3 | 12071.3 | 10857.2 | 11856.7 | 11144.3 | 11926.7 | 10588.1 | 12003.7 | 11111.1 | 11895 | 11070.9 | 11954.1 | 11258.4 | 10956.8 | 11821.3 | 11082.2 | 10907.3 | 11878.8 | 12019.8 | 11851.2 | 11032.4 | 11938.1 | 10973.8 | 11661.3 | 11154.9 | 11652.5 | 10275.3 | 11729.4 | 10965.3 | 11158 | 11176.4 | 10958.5 | 9529 | 10969.2 | 9718.8 | 11017.1 | 11044.4 | 12307.3 | 11100.6 | 12350.3 | 11327.2 | 12236.8 | 11165.4 | 11330.7 | 11176.5 | 12100.5 | 12385.6 | 12285.2 | 12202.1 | 12290.1 | 12306.9 | 11416.8 | 12285.5 | 12374.8 | 12413.4 | 12416.5 | 12392.1 | 12430.1 | 11480.4 | 12436.3 | 11518.5 | 21.2276 | 20.9262 | 21.3862 | 21.31 | 20.9864 | 20.7601 | 0 | 36.4356 | 0 | 0 | 36.4 | 34.6 | 2.2735 | 1.4633 | 2.0963 | 0.38365 | 2.1752 | 1.5971 | 4.6067 | 4.48 | 4.1483 | 3.6617 | 4.84 | 5.8483 | 4.9845 | 5.0473 | 5.0537 | 4.9586 | 5.0466 | 5.0403 | 1.2699 | 1.4004 | 1.1795 | 1.5605 | 1.4843 | 1.2608 | 6.5443 | 6.417 | 6.4674 | 6.4705 | 6.39 | 6.3856 | 0.27358 | 0.29402 | 0.24027 | 0.26173 | 0.25885 | 0.29764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 840013 | 1575 | 826673 | 1596 | 321216.158 | 968.6 | 4.9845 | 5.0473 | 5.0537 | 4.9586 | 5.0466 | 5.0403 | 6.5443 | 6.417 | 6.4674 | 6.4705 | 6.39 | 6.3856 | 925000 | 2000 | 913000 | 2000 | 1835266 | 5000 | 1834000 | 1830266 | 10.8833 | 5.0218 | 1.3592 | 6.4458 | 0.27102 | 27.07% | 4.205% | 21.0994 | 35.8119 | 1.6648 | 4.5975 | 1847772.6 | 1825333 | 2072027.0238 | 88.09% | 32 | 4581
2025-01-26 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 335090.89 | 7:36 | 18:28 | 11457.9 | 11815.7 | 11748.9 | 11741.1 | 11765.4 | 11857.1 | 11808.5 | 12075.2 | 11779.9 | 11805.4 | 11659.6 | 11792.8 | 11762.5 | 11737.4 | 11753.3 | 11833 | 11709 | 11795.4 | 11815.7 | 11896.8 | 11780.3 | 11807.2 | 11620.2 | 11728 | 11588.5 | 10348.1 | 11637.2 | 11588.2 | 11807.3 | 11689 | 11609.5 | 11774.9 | 12065.7 | 12145.1 | 12084.5 | 12027.3 | 11905.8 | 11791.4 | 11808.4 | 11694 | 12460.2 | 11511.8 | 12317.7 | 11449.4 | 11931.9 | 12829.2 | 11346.4 | 12421.3 | 11676 | 11863.7 | 11841.1 | 11363.7 | 12117.7 | 11686.7 | 12091.3 | 11766.3 | 11094.5 | 12279 | 11091.9 | 12224.9 | 12158.8 | 11097.2 | 11921.5 | 11527.8 | 11626.8 | 11087.3 | 11642.7 | 11993.2 | 12171 | 11338.5 | 12084.4 | 10951.3 | 11787.7 | 11709.2 | 11098.5 | 12086.9 | 10966.5 | 12179.8 | 11066.8 | 12063.5 | 11416.8 | 12043.3 | 11510.4 | 12336.1 | 11361.7 | 11901.9 | 11229.8 | 9989.5 | 12012.1 | 11674.9 | 11076.3 | 12278.5 | 11970.2 | 11253.2 | 11108.3 | 12050.8 | 11088.5 | 11494.8 | 12117.4 | 11080.5 | 12214.4 | 11064.5 | 12015.2 | 11338.7 | 12068.7 | 10778.7 | 12146.8 | 11296.7 | 12044.7 | 11265.1 | 12100.7 | 11437.4 | 11154.2 | 11981.5 | 11273.1 | 11107.1 | 12028.4 | 12170.5 | 12002.9 | 11226.3 | 12087.7 | 11165.1 | 11821.8 | 11338.2 | 11808.2 | 10456.2 | 11893.1 | 11154.1 | 11333.7 | 11349.2 | 11133 | 9683.1 | 11161.2 | 9878.5 | 11175.7 | 11205.5 | 12427.1 | 11269.1 | 12464.8 | 11488.6 | 12355.1 | 11322.5 | 11487.6 | 11337.1 | 12224.2 | 12489.6 | 12403.6 | 12321.6 | 12406.9 | 12425.5 | 11569.4 | 12401 | 12484.9 | 12518.6 | 12514.4 | 12492.5 | 12531.5 | 11627.7 | 12542.7 | 11663.8 | 21.7967 | 21.5746 | 22.1532 | 21.8173 | 21.7831 | 21.5955 | 0 | 36.5304 | 0 | 0 | 36.6 | 34.9 | 2.6182 | 1.88 | 2.3535 | 0.41613 | 2.5341 | 1.5818 | 4.4983 | 4.5883 | 4.3267 | 3.3017 | 5.0167 | 4.625 | 5.0892 | 5.1508 | 5.1534 | 5.0664 | 5.151 | 5.1373 | 1.3006 | 1.4047 | 1.2047 | 1.5972 | 1.518 | 1.2869 | 6.6703 | 6.5469 | 6.5888 | 6.5996 | 6.5159 | 6.5005 | 0.28148 | 0.30002 | 0.24487 | 0.26927 | 0.2657 | 0.30313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 840950 | 1577 | 827603 | 1598 | 323076.425 | 973.667 | 5.0892 | 5.1508 | 5.1534 | 5.0664 | 5.151 | 5.1373 | 6.6703 | 6.5469 | 6.5888 | 6.5996 | 6.5159 | 6.5005 | 937000 | 2000 | 930000 | 2000 | 1860267 | 5067 | 1863000 | 1855200 | 10.8667 | 5.1247 | 1.3854 | 6.5703 | 0.27741 | 27.03% | 4.222% | 21.7867 | 36.0101 | 1.8973 | 4.3928 | 1873160 | 1849600 | 2103411.3434 | 87.93% | 25 | 0
2025-01-27 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 335090.89 | 7:36 | 18:29 | 11426.6 | 11782.8 | 11724.2 | 11719.6 | 11735.9 | 11832.2 | 11773.1 | 12091.2 | 11768.7 | 11789.1 | 11638.7 | 11777.7 | 11740.5 | 11718.3 | 11726.5 | 11822.1 | 11692.5 | 11787.2 | 11795.5 | 11876 | 11764.4 | 11784.4 | 11603.1 | 11710 | 11561.2 | 10316.2 | 11616.7 | 11564.5 | 11790.9 | 11669.8 | 11594.2 | 11755 | 12040.4 | 12122.7 | 12057.8 | 12002.1 | 11886.9 | 11777.8 | 11793.5 | 11679.9 | 12482.1 | 11520.3 | 12338.7 | 11456.9 | 11943.4 | 12861.3 | 11354.7 | 12443.3 | 11656.6 | 11845.2 | 11830.7 | 11338.5 | 12099.3 | 11658.3 | 12074.1 | 11746 | 11064.2 | 12271.5 | 11059.8 | 12213.5 | 12143.9 | 11064.8 | 11900.6 | 11496.6 | 11594.1 | 11064.9 | 11615.8 | 11978.2 | 12156.8 | 11308.3 | 12066 | 10928.1 | 11765.3 | 11675.4 | 11073.8 | 12065.9 | 10945.2 | 12164.6 | 11040.3 | 12037 | 11388.4 | 12021.3 | 11475.8 | 12328.1 | 11334 | 11880.8 | 11194.8 | 9979.2 | 11979.2 | 11652 | 11052.2 | 12264.2 | 11963.7 | 11254.8 | 11119 | 12023.3 | 11039.5 | 11456.3 | 12098.3 | 11050.3 | 12198.9 | 11042.9 | 11994.3 | 11310.6 | 12055.5 | 10753 | 12136.9 | 11266.8 | 12033 | 11238.4 | 12086.3 | 11413.7 | 11120.9 | 11955.7 | 11242.7 | 11075.2 | 12006.1 | 12150.1 | 11976.3 | 11193.3 | 12069.6 | 11134 | 11796.2 | 11312.5 | 11782.2 | 10432.7 | 11869 | 11125.2 | 11296 | 11304.3 | 11100.8 | 9652.2 | 11130.1 | 9877.1 | 11139.8 | 11171.1 | 12417 | 11249.7 | 12459.7 | 11468.3 | 12352.9 | 11313.1 | 11474 | 11303.5 | 12215.8 | 12492.8 | 12401.5 | 12323.4 | 12400.7 | 12419.4 | 11554.8 | 12402.7 | 12481.7 | 12519.7 | 12520.4 | 12499.3 | 12537.2 | 11615.4 | 12543 | 11649.8 | 23.06 | 22.67 | 23.25 | 22.97 | 22.74 | 22.44 | 0 | 37.83 | 0 | 0 | 36.84 | 35.7 | 2.54 | 1.72 | 2.37 | 0.43 | 2.25 | 2.06 | 5.18 | 4.68 | 4.19 | 4.69 | 4.69 | 4.7 | 5.11 | 5.17 | 5.19 | 5.09 | 5.18 | 5.17 | 1.31 | 1.41 | 1.21 | 1.61 | 1.52 | 1.29 | 6.68 | 6.56 | 6.61 | 6.62 | 6.53 | 6.52 | 0.28 | 0.3 | 0.25 | 0.27 | 0.27 | 0.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 841886 | 1579 | 828532 | 1599 | 324933.225 | 978.6 | 5.11 | 5.17 | 5.19 | 5.09 | 5.18 | 5.17 | 6.68 | 6.56 | 6.61 | 6.62 | 6.53 | 6.52 | 936000 | 2000 | 929000 | 1000 | 1856800 | 4933 | 1862000 | 1851867 | 10.8833 | 5.1517 | 1.3917 | 6.5867 | 0.28 | 27.01% | 4.251% | 22.855 | 36.79 | 1.895 | 4.6883 | 1870268.3 | 1845600 | 2099329.2298 | 87.91% | 28 | 0
2025-01-28 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 335090.89 | 7:37 | 18:30 | 11256.5 | 11616.3 | 11562.1 | 11551.1 | 11574.9 | 11660.7 | 11592 | 11946.3 | 11625.3 | 11638.2 | 11487.3 | 11637.8 | 11580 | 11571.5 | 11545.2 | 11654.6 | 11521.4 | 11616.7 | 11635 | 11715.2 | 11588.8 | 11619.1 | 11410.7 | 11526.3 | 11373.7 | 10105.4 | 11444.1 | 11384.3 | 11603 | 11471.2 | 11397.6 | 11565.7 | 11838.7 | 11933.2 | 11856.1 | 11796.7 | 11707.2 | 11590.4 | 11613 | 11497.2 | 12291.6 | 11295.3 | 12148.6 | 11224.4 | 11739 | 12679.2 | 11131.5 | 12251.4 | 11504.4 | 11692.3 | 11680.2 | 11168.1 | 11953.4 | 11509 | 11918 | 11585.2 | 10866.1 | 12120 | 10857.3 | 12069.8 | 11990.9 | 10859.7 | 11738.1 | 11314.9 | 11431.6 | 10865 | 11439.5 | 11814.5 | 12001.8 | 11123.7 | 11906.2 | 10724.9 | 11598.9 | 11506.7 | 10870.2 | 11909.1 | 10743.9 | 12010 | 10837.4 | 11892 | 11201 | 11858.6 | 11284.4 | 12169.2 | 11138 | 11704 | 11004 | 9778.2 | 11786.6 | 11470.4 | 10815.7 | 12090.3 | 11804.7 | 11069.3 | 10928.3 | 11848.6 | 10808.8 | 11262.4 | 11929.6 | 10833.6 | 12021.8 | 10817.3 | 11814.3 | 11089.1 | 11873.1 | 10525.3 | 11950.9 | 11052.7 | 11837.8 | 11011.8 | 11897.9 | 11194.8 | 10894.7 | 11769.3 | 11027.9 | 10846.2 | 11825.9 | 11965.5 | 11796.4 | 10964.6 | 11888.7 | 10907.2 | 11615.5 | 11096.7 | 11593.9 | 10212.9 | 11685.9 | 10885.3 | 11060.6 | 11064.3 | 10884.7 | 9438.7 | 10889.1 | 9656 | 10877.7 | 10913.8 | 12266 | 11058.6 | 12301.2 | 11278.1 | 12190.2 | 11113.4 | 11284.2 | 11073.7 | 12050.8 | 12332.8 | 12241.6 | 12160.3 | 12247.3 | 12261.8 | 11372.7 | 12237.5 | 12322.1 | 12363.7 | 12360.2 | 12337.9 | 12378.2 | 11431 | 12390.2 | 11470.9 | 23.96 | 23.92 | 24.59 | 24.27 | 23.89 | 23.67 | 0 | 40.96 | 0 | 0 | 40.6 | 39 | 1.8 | 0.96 | 1.59 | 0.09 | 1.49 | 1.03 | 4.03 | 4.58 | 3.49 | 2.6 | 3.73 | 3.89 | 5.07 | 5.14 | 5.12 | 5.06 | 5.12 | 5.13 | 1.28 | 1.41 | 1.19 | 1.58 | 1.49 | 1.27 | 6.6 | 6.48 | 6.5 | 6.53 | 6.45 | 6.44 | 0.27 | 0.28 | 0.23 | 0.25 | 0.25 | 0.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 842808 | 1581 | 829445 | 1601 | 326762 | 983.533 | 5.07 | 5.14 | 5.12 | 5.06 | 5.12 | 5.13 | 6.6 | 6.48 | 6.5 | 6.53 | 6.45 | 6.44 | 922000 | 2000 | 913000 | 2000 | 1828775 | 4933 | 1831000 | 1823842 | 10.8833 | 5.1067 | 1.37 | 6.5 | 0.26167 | 26.83% | 4.026% | 24.05 | 40.1867 | 1.16 | 3.72 | 1840732.7 | 1817800 | 2057883.5521 | 88.33% | 28 | 0
2025-01-29 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 335090.89 | 7:35 | 18:30 | 11120.7 | 11487.3 | 11443.8 | 11424 | 11472 | 11571.2 | 11484.8 | 11823.9 | 11487.4 | 11499.6 | 11359.1 | 11509.4 | 11458.5 | 11442 | 11458.7 | 11546.5 | 11422.1 | 11516.1 | 11528.8 | 11594.8 | 11491.1 | 11518 | 11327.5 | 11434.9 | 11281.1 | 9985 | 11320.1 | 11280.1 | 11513.4 | 11381.3 | 11322.4 | 11490.5 | 11697.6 | 11783.5 | 11718.8 | 11654 | 11604.1 | 11487 | 11509.1 | 11410.4 | 12205.6 | 11207.7 | 12063.9 | 11129.3 | 11653.3 | 12582.8 | 11032.5 | 12166.7 | 11384.5 | 11571.6 | 11551.3 | 11036.7 | 11848.5 | 11404.8 | 11791.3 | 11491.8 | 10708.9 | 11990.9 | 10718.8 | 11928.6 | 11856.6 | 10710.4 | 11605 | 11174.4 | 11323.9 | 10736.2 | 11313.7 | 11690.6 | 11882.8 | 10979.1 | 11790 | 10574.6 | 11473.9 | 11378.3 | 10714.6 | 11775.7 | 10584.6 | 11881.5 | 10697.1 | 11755.3 | 11050.5 | 11718.9 | 11146.5 | 12043.2 | 11001.2 | 11585.8 | 10867.4 | 9647.8 | 11669.7 | 11358.4 | 10683.5 | 11983.7 | 11693.4 | 10937.6 | 10816.4 | 11771.4 | 10700.3 | 11159.9 | 11842.7 | 10708 | 11917.7 | 10690.2 | 11712.3 | 10967 | 11770.9 | 10407 | 11854.8 | 10934.2 | 11743 | 10891.8 | 11815 | 11088.4 | 10781.8 | 11668.8 | 10918 | 10733.7 | 11740.6 | 11870.1 | 11703.6 | 10847.9 | 11794.3 | 10790.8 | 11514.5 | 10979.3 | 11503.1 | 10113.9 | 11591.1 | 10784.8 | 10955.4 | 10956.5 | 10803.9 | 9349.1 | 10779.2 | 9540.6 | 10793.9 | 10808.2 | 12165.4 | 10946.8 | 12205 | 11177.2 | 12102.6 | 11011 | 11199.2 | 10975.2 | 11944.8 | 12229 | 12141.4 | 12056.9 | 12138.2 | 12161.8 | 11261.9 | 12140.6 | 12207.3 | 12245.9 | 12250.6 | 12235.2 | 12267.7 | 11317.9 | 12278.1 | 11358.1 | 25.7933 | 25.6798 | 26.4022 | 25.7965 | 25.7698 | 25.9832 | 0 | 39.3623 | 0 | 0 | 39.5 | 38.5 | 4.1972 | 3.9063 | 3.862 | 2.8653 | 3.9545 | 4.0163 | 8.28 | 8.0633 | 8.695 | 6.9867 | 8.6067 | 7.7333 | 5.0249 | 5.1142 | 5.091 | 5.0118 | 5.0914 | 5.0958 | 1.2817 | 1.42 | 1.1893 | 1.5739 | 1.4804 | 1.284 | 6.465 | 6.3859 | 6.3907 | 6.3978 | 6.3389 | 6.3577 | 0.27046 | 0.29001 | 0.23428 | 0.25477 | 0.2594 | 0.29654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 843721 | 1582 | 830350 | 1603 | 328572.692 | 988.6 | 5.0249 | 5.1142 | 5.091 | 5.0118 | 5.0914 | 5.0958 | 6.465 | 6.3859 | 6.3907 | 6.3978 | 6.3389 | 6.3577 | 913000 | 1000 | 905000 | 2000 | 1810692 | 5067 | 1815000 | 1805625 | 10.9167 | 5.0715 | 1.3716 | 6.3893 | 0.26758 | 27.04% | 4.188% | 25.9041 | 39.1208 | 3.8003 | 8.0608 | 1822747.9 | 1799333 | 2036729.8863 | 88.34% | 24 | 0
2025-01-30 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 335090.89 | 7:39 | 18:28 | 10378.7 | 10835.9 | 10784 | 10757.7 | 10797.5 | 10921.2 | 10866.1 | 11208.4 | 10832.4 | 10829.2 | 10694.2 | 10856.1 | 10805 | 10803.5 | 10836.4 | 10905.5 | 10788.1 | 10870 | 10890.2 | 10953.4 | 10852.2 | 10866.1 | 10628 | 10765.7 | 10624.7 | 9344.8 | 10672.7 | 10616.2 | 10861.1 | 10684 | 10614.8 | 10841.9 | 10904 | 11001.4 | 10949.6 | 10866.8 | 10944.3 | 10803.4 | 10832.5 | 10727.3 | 11603.5 | 10473 | 11456 | 10385.6 | 10979.3 | 12021.3 | 10257.4 | 11563.7 | 10749.4 | 10947.3 | 10914 | 10311.1 | 11236.1 | 10753.1 | 11200.7 | 10900.9 | 9999.9 | 11397.4 | 10004.4 | 11332 | 11249.1 | 10003.4 | 10949.5 | 10441.6 | 10647.1 | 10012.3 | 10629.7 | 11064.2 | 11286.7 | 10239.3 | 11162.9 | 9850.4 | 10829.7 | 10685.9 | 9995.3 | 11173 | 9875.1 | 11290.5 | 9972.1 | 11147.3 | 10316 | 11077.3 | 10453.8 | 11451.4 | 10307 | 10978 | 10184 | 9027.6 | 11068.6 | 10745.7 | 9985 | 11384.1 | 11051.9 | 10188.6 | 10047.3 | 11150.1 | 9942.8 | 10411.1 | 11189.8 | 9943.6 | 11262.9 | 9929 | 11018.5 | 10185.8 | 11119.2 | 9655.5 | 11193.6 | 10145.3 | 11055.3 | 10093.3 | 11147.6 | 10296.6 | 10030 | 10992.2 | 10146.8 | 9954.8 | 11078.7 | 11223.9 | 11037.2 | 10092.1 | 11141.1 | 10021.6 | 10814.3 | 10192.5 | 10803.3 | 9395.2 | 10919 | 10042.7 | 10201.5 | 10221.8 | 10067.9 | 8705.1 | 10005.6 | 8851.6 | 10013.8 | 10051 | 11573.3 | 10203 | 11627.7 | 10458.5 | 11487.3 | 10261.1 | 10451.6 | 10239.1 | 11331.6 | 11656.3 | 11541.3 | 11460.5 | 11543 | 11565.7 | 10569.2 | 11551.5 | 11634 | 11672.9 | 11690.4 | 11661.9 | 11691.5 | 10620.2 | 11701.2 | 10663.6 | 22.1502 | 21.9048 | 22.1278 | 22.3461 | 22.0854 | 22.0743 | 0 | 34.4728 | 0 | 0 | 34.4 | 33.2 | 3.0208 | 2.4593 | 2.9595 | 1.5651 | 2.8705 | 2.4206 | 5.0517 | 5.63 | 5.7133 | 5.305 | 4.9883 | 5.1933 | 4.6396 | 4.727 | 4.6802 | 4.6265 | 4.6788 | 4.7188 | 1.2089 | 1.3059 | 1.1188 | 1.4863 | 1.3688 | 1.197 | 5.8771 | 5.8086 | 5.796 | 5.8354 | 5.7496 | 5.79 | 0.26699 | 0.28632 | 0.23514 | 0.2586 | 0.25264 | 0.28846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 844581 | 1585 | 831201 | 1605 | 330276.759 | 993.8 | 4.6396 | 4.727 | 4.6802 | 4.6265 | 4.6788 | 4.7188 | 5.8771 | 5.8086 | 5.796 | 5.8354 | 5.7496 | 5.79 | 860000 | 3000 | 851000 | 2000 | 1704067 | 5200 | 1706000 | 1698867 | 10.8167 | 4.6785 | 1.2809 | 5.8094 | 0.26469 | 27.38% | 4.556% | 22.1148 | 34.0243 | 2.5493 | 5.3136 | 1714872.6 | 1687934 | 1871860.5677 | 90.17% | 17 | 0
2025-01-31 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 335090.89 | 7:39 | 18:27 | 8784.8 | 9167.8 | 9107 | 9081.1 | 9103 | 9209.1 | 9154.4 | 9508.8 | 9137.8 | 9226.6 | 8951.1 | 9127.3 | 9035.6 | 9031 | 9100.9 | 9155.1 | 9046.2 | 9108.2 | 9104.6 | 9139.7 | 9092.3 | 9087 | 8893.3 | 9003.6 | 8861.2 | 7772.3 | 8876.2 | 8833.6 | 9102.9 | 8971.2 | 8920.6 | 9106.3 | 9163.2 | 9213.1 | 9129.7 | 9085.3 | 9232 | 9109.3 | 9156.4 | 9084.4 | 10029.3 | 8875.4 | 9883.4 | 8773.2 | 9346.5 | 10501.4 | 8692.5 | 10012.1 | 8986.6 | 9171.1 | 9105.2 | 8578.4 | 9438.1 | 8980.1 | 9427 | 9161.9 | 8327.1 | 9644.4 | 8327.6 | 9572.7 | 9491.7 | 8354.3 | 9183.9 | 8731.8 | 8926.8 | 8419.1 | 8920.3 | 9385.8 | 9594.5 | 8631.7 | 9467.2 | 8311.2 | 9105.6 | 9007 | 8382.1 | 9510.2 | 8306.7 | 9604.9 | 8387.9 | 9480.2 | 8709.4 | 9425.9 | 8839.7 | 9817.5 | 8691.6 | 9302.8 | 8572.1 | 7598.6 | 9408.2 | 9079.4 | 8402 | 9740.2 | 9383.3 | 8557.6 | 8443.1 | 9515.3 | 8444.9 | 8830.9 | 9650.3 | 8453.7 | 9726.7 | 8455.5 | 9464.5 | 8687.4 | 9605.4 | 8243.8 | 9676.4 | 8682.5 | 9540.1 | 8667.6 | 9633.3 | 8833.2 | 8532.6 | 9436.7 | 8655.3 | 8489.2 | 9570.4 | 9699.3 | 9513.6 | 8633.1 | 9628.1 | 8580.4 | 9296.8 | 8730.8 | 9268.6 | 8060.6 | 9399.6 | 8590.9 | 8689.3 | 8711.2 | 8580.9 | 7416.8 | 8500.3 | 7506.7 | 8505.4 | 8546.6 | 10048.3 | 8660.7 | 10099.3 | 8868.7 | 9958 | 8703.6 | 8863.8 | 8703.3 | 9705.7 | 10088.3 | 9981.5 | 9911.2 | 9995.7 | 10026.6 | 8950.5 | 9981.1 | 10056.2 | 10091.9 | 10077.4 | 10048.5 | 10088.6 | 8954.8 | 10138 | 9024.9 | 21.54 | 21.19 | 21.56 | 21.53 | 21.36 | 21.24 | 0 | 33.73 | 0 | 0 | 34 | 33.1 | 2.12 | 0.6 | 2.04 | 0.51 | 1.9 | 0.9 | 5.09 | 4.4 | 6.39 | 4.39 | 4.23 | 4.58 | 4.05 | 4.09 | 4.12 | 4.03 | 4.15 | 4.15 | 1.06 | 1.17 | 0.99 | 1.3 | 1.22 | 1.07 | 4.96 | 4.9 | 4.95 | 4.92 | 4.94 | 4.94 | 0.25 | 0.27 | 0.22 | 0.24 | 0.24 | 0.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 845306 | 1587 | 831930 | 1606 | 331725.026 | 999 | 4.05 | 4.09 | 4.12 | 4.03 | 4.15 | 4.15 | 4.96 | 4.9 | 4.95 | 4.92 | 4.94 | 4.94 | 725000 | 2000 | 729000 | 1000 | 1448267 | 5200 | 1451000 | 1443067 | 10.8 | 4.0983 | 1.135 | 4.935 | 0.24833 | 27.69% | 5.032% | 21.4033 | 33.61 | 1.345 | 4.8467 | 1455663.6 | 1431934 | 1599113.9167 | 89.55% | 24 | 0
2025-02-01 | 2025 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 335090.89 | 7:40 | 18:26 | 8964.2 | 9382 | 9319.2 | 9293.1 | 9322 | 9411.8 | 9370.7 | 9778.8 | 9371.9 | 9375.3 | 9220.3 | 9381.7 | 9306.3 | 9315.9 | 9346.6 | 9410.5 | 9291.6 | 9371.1 | 9400.8 | 9440.3 | 9380.9 | 9381.5 | 9164.1 | 9281.9 | 9133.5 | 8003.6 | 9157.3 | 9114.4 | 9391.7 | 9242 | 9179.1 | 9393.7 | 9378.4 | 9446.6 | 9390 | 9337.6 | 9482.5 | 9353.5 | 9391.5 | 9293.6 | 10279.4 | 9117.4 | 10129.8 | 9012.1 | 9536.5 | 10722.1 | 8893.3 | 10257.6 | 9279.1 | 9470 | 9412.7 | 8846.8 | 9740.7 | 9274.9 | 9708.5 | 9421.1 | 8594.6 | 9938.1 | 8592.2 | 9870.2 | 9763.4 | 8595.3 | 9426 | 8922.8 | 9110.5 | 8573 | 9107.5 | 9552.5 | 9816.8 | 8783.1 | 9666.1 | 8444.8 | 9329 | 9164.4 | 8571 | 9668.9 | 8454.1 | 9801 | 8544.3 | 9659.6 | 8826.7 | 9551 | 8949.8 | 9952.6 | 8813.1 | 9443.8 | 8714.5 | 7727.6 | 9553.9 | 9235.2 | 8587.2 | 9959.1 | 9619.7 | 8780 | 8652.6 | 9705 | 8601.7 | 8952.9 | 9797.1 | 8571.2 | 9882 | 8590.7 | 9600.2 | 8815 | 9725.3 | 8356.5 | 9795.2 | 8796.7 | 9631.4 | 8749.2 | 9693.3 | 8912.1 | 8644.5 | 9557.5 | 8761.5 | 8590.4 | 9691.9 | 9807.2 | 9638.9 | 8731.9 | 9740.1 | 8675.3 | 9417 | 8834.3 | 9361.1 | 8135.6 | 9488.2 | 8665.1 | 8797.7 | 8833.1 | 8670.1 | 7498.3 | 8662.2 | 7671.1 | 8649.4 | 8683.8 | 10128.2 | 8737.1 | 10200 | 8962.4 | 10069.3 | 8815.2 | 8971.8 | 8839.1 | 9723.8 | 10120.7 | 9994.6 | 9938.9 | 10048 | 10088.2 | 9027.8 | 10038 | 10063.2 | 10084.4 | 10057.7 | 10030.5 | 10065.1 | 8945.1 | 10152.7 | 9012.7 | 22.1597 | 21.6941 | 22.0144 | 21.8782 | 21.6493 | 21.3868 | 0 | 32.164 | 0 | 0 | 32 | 31.1 | 3.546 | 2.6996 | 3.3683 | 2.3771 | 3.2914 | 2.7546 | 6.7433 | 6.19 | 5.9333 | 6.0067 | 6.6783 | 5.76 | 4.1497 | 4.1991 | 4.2214 | 4.122 | 4.1834 | 4.1662 | 1.0981 | 1.1686 | 1.0155 | 1.3312 | 1.2267 | 1.0648 | 5.0725 | 5.0255 | 5.0583 | 5.0309 | 4.9771 | 4.9613 | 0.26199 | 0.28142 | 0.23589 | 0.25934 | 0.24774 | 0.27692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 846050 | 1588 | 832667 | 1608 | 333199.959 | 1004.067 | 4.1497 | 4.1991 | 4.2214 | 4.122 | 4.1834 | 4.1662 | 5.0725 | 5.0255 | 5.0583 | 5.0309 | 4.9771 | 4.9613 | 744000 | 1000 | 737000 | 2000 | 1474933 | 5067 | 1478000 | 1469866 | 10.7667 | 4.1736 | 1.1508 | 5.0209 | 0.26055 | 27.57% | 5.189% | 21.7971 | 31.7547 | 3.0061 | 6.2186 | 1482885.7 | 1453300 | 1656552.8 | 87.73% | 20 | 2961
2025-02-02 | 2025 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 335090.89 | 7:39 | 18:30 | 10802.1 | 11180 | 11128.1 | 11105.1 | 11146.8 | 11227.8 | 11202.1 | 11486.7 | 11145.2 | 11168.4 | 11024 | 11166 | 11113.3 | 11107.8 | 11142.1 | 11201.5 | 11079 | 11150.6 | 11182.3 | 11246.9 | 11151.8 | 11171.7 | 10982 | 11083.3 | 10949.7 | 9732.4 | 10987.4 | 10934.9 | 11176.3 | 11047.4 | 10977.3 | 11148.2 | 11375.9 | 11459.3 | 11383.2 | 11331.2 | 11258.5 | 11147.1 | 11166.8 | 11074.5 | 11850.3 | 10903.3 | 11721.3 | 10816.7 | 11329.9 | 12251.9 | 10731.8 | 11824.9 | 11050.1 | 11235.3 | 11201.9 | 10688.1 | 11478.2 | 11062.1 | 11446.4 | 11169.3 | 10423.2 | 11639.2 | 10418.1 | 11583 | 11512.6 | 10431.9 | 11256.6 | 10841.4 | 10960.8 | 10415.6 | 10970 | 11344.6 | 11530.7 | 10669.1 | 11433.5 | 10299.2 | 11141.4 | 11042.8 | 10425.1 | 11442.3 | 10303.6 | 11540.6 | 10401.4 | 11422.7 | 10744.2 | 11391.3 | 10855.3 | 11693.4 | 10705.7 | 11267.3 | 10554 | 9397.3 | 11331.3 | 11047.9 | 10428.1 | 11644.2 | 11388.4 | 10665.5 | 10527.7 | 11419 | 10438.4 | 10844.9 | 11505.3 | 10437.6 | 11593.9 | 10422.1 | 11381.5 | 10674.1 | 11452.1 | 10146 | 11526.5 | 10644.3 | 11414.6 | 10611.3 | 11467.9 | 10787.7 | 10520.7 | 11365.5 | 10632 | 10459.5 | 11417.2 | 11552.9 | 11376.6 | 10597.4 | 11462.1 | 10520.9 | 11190.5 | 10689.5 | 11152.6 | 9859.7 | 11272.8 | 10519.8 | 10687.1 | 10707.2 | 10555.8 | 9136.6 | 10498.4 | 9313.5 | 10498 | 10527.4 | 11784.5 | 10611.2 | 11835 | 10822.6 | 11718.7 | 10659.8 | 10813 | 10681.5 | 11580.1 | 11862.6 | 11768.9 | 11687.4 | 11758.3 | 11782.3 | 10914.8 | 11767.3 | 11868.7 | 11895.4 | 11896.7 | 11868.9 | 11903.9 | 10971.2 | 11917.6 | 11006.9 | 21.27 | 20.86 | 21.37 | 21.18 | 21 | 20.83 | 0 | 32.45 | 0 | 0 | 32.4 | 31.1 | 4.06 | 3.3 | 3.86 | 2.83 | 4.01 | 3.39 | 7.87 | 6.83 | 7.56 | 6.63 | 7.22 | 7.12 | 4.88 | 4.94 | 4.95 | 4.87 | 4.93 | 4.92 | 1.26 | 1.41 | 1.17 | 1.55 | 1.49 | 1.27 | 6.16 | 6.1 | 6.1 | 6.12 | 6.03 | 6.06 | 0.29 | 0.3 | 0.25 | 0.28 | 0.27 | 0.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 846936 | 1590 | 833547 | 1609 | 334959.226 | 1009.067 | 4.88 | 4.94 | 4.95 | 4.87 | 4.93 | 4.92 | 6.16 | 6.1 | 6.1 | 6.12 | 6.03 | 6.06 | 886000 | 2000 | 880000 | 1000 | 1759267 | 5000 | 1763000 | 1754267 | 10.85 | 4.915 | 1.3583 | 6.095 | 0.28333 | 27.64% | 4.649% | 21.085 | 31.9833 | 3.575 | 7.205 | 1771055.4 | 1745267 | 2018444.2964 | 86.47% | 25 | 10831
2025-02-03 | 2025 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 335090.89 | 7:40 | 18:27 | 9919.6 | 10381.1 | 10360.4 | 10322.6 | 10393.1 | 10481.2 | 10448.6 | 10889.2 | 10374.4 | 10393 | 10218.4 | 10404.9 | 10327.4 | 10335.1 | 10347.6 | 10435.7 | 10303.3 | 10407 | 10436.4 | 10483.5 | 10414.2 | 10411.5 | 10184.6 | 10310.9 | 10160.3 | 8911.8 | 10179.6 | 10129.9 | 10461.3 | 10325.6 | 10193.9 | 10432 | 10426.4 | 10515.1 | 10451.8 | 10390.6 | 10546.1 | 10399.3 | 10439.2 | 10329 | 11318.4 | 10056.1 | 11167 | 9941.8 | 10584.3 | 11811.1 | 9864.5 | 11302.4 | 10280.3 | 10489.8 | 10401.6 | 9815.4 | 10807.9 | 10269.7 | 10767.2 | 10449.6 | 9529.5 | 11014.9 | 9527 | 10932.1 | 10825.9 | 9523 | 10499.3 | 9951 | 10134.7 | 9536.9 | 10137.3 | 10622.8 | 10916.3 | 9775.8 | 10753.2 | 9407.3 | 10371.3 | 10207 | 9540.3 | 10761.7 | 9413.1 | 10909.1 | 9504.3 | 10721.3 | 9841.2 | 10653.5 | 9960.4 | 11079.1 | 9811.4 | 10503.7 | 9674.5 | 8591.6 | 10623.8 | 10254.4 | 9523.6 | 11051.7 | 10681.3 | 9764.5 | 9631.2 | 10744.9 | 9543.2 | 9986.9 | 10895.3 | 9555.2 | 11012.7 | 9552.5 | 10681.6 | 9807.3 | 10828.3 | 9299.5 | 10897.9 | 9778.2 | 10721 | 9739.9 | 10807 | 9918.6 | 9633 | 10655.2 | 9760.3 | 9574 | 10776.7 | 10924.3 | 10707.6 | 9724.7 | 10828.1 | 9648.3 | 10452.3 | 9808.5 | 10396.3 | 9041.9 | 10545 | 9656.4 | 9803.7 | 9830.5 | 9683.7 | 8367.4 | 9601.2 | 8489.9 | 9615.1 | 9639.8 | 11251.4 | 9745.6 | 11322.3 | 9992.6 | 11191.1 | 9802.3 | 9997 | 9811.9 | 10933.6 | 11329.7 | 11178.5 | 11094.2 | 11188 | 11233.4 | 10079 | 11211.9 | 11294.2 | 11336.9 | 11361.7 | 11321.8 | 11355.8 | 10111.5 | 11356.8 | 10156.5 | 21.3643 | 20.8476 | 21.1423 | 21.2982 | 21.0359 | 20.8454 | 0 | 33.6603 | 0 | 0 | 33.5 | 32.3 | 2.7955 | 1.7462 | 2.4231 | 0.92141 | 2.4126 | 2.3148 | 5.6017 | 5.9817 | 5.325 | 4.35 | 4.98 | 4.7733 | 4.5422 | 4.6052 | 4.6039 | 4.5363 | 4.5994 | 4.5833 | 1.174 | 1.2951 | 1.0865 | 1.4395 | 1.3859 | 1.1867 | 5.6334 | 5.6033 | 5.593 | 5.6108 | 5.5485 | 5.5552 | 0.27032 | 0.29011 | 0.24095 | 0.26594 | 0.25684 | 0.29136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 847761 | 1593 | 834367 | 1611 | 336598.56 | 1014.067 | 4.5422 | 4.6052 | 4.6039 | 4.5363 | 4.5994 | 4.5833 | 5.6334 | 5.6033 | 5.593 | 5.6108 | 5.5485 | 5.5552 | 825000 | 3000 | 820000 | 2000 | 1639334 | 5000 | 1640000 | 1634334 | 10.7833 | 4.5784 | 1.2613 | 5.5907 | 0.26925 | 27.55% | 4.816% | 21.089 | 33.1534 | 2.1023 | 5.1686 | 1649355.3 | 1623866 | 1841840.7513 | 88.17% | 24 | 0
2025-02-04 | 2025 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 335090.89 | 7:36 | 18:29 | 11006.5 | 11381.1 | 11344.6 | 11332.6 | 11380.1 | 11445.8 | 11402.5 | 11733.4 | 11380.2 | 11391.7 | 11236.4 | 11406.6 | 11322.6 | 11327.5 | 11339.3 | 11410.2 | 11285.3 | 11374.5 | 11396.5 | 11466.8 | 11364.3 | 11388.2 | 11195.3 | 11294.5 | 11167.5 | 9896.8 | 11199.1 | 11152.7 | 11400.9 | 11280 | 11193 | 11375 | 11572.1 | 11661.7 | 11603.7 | 11544.1 | 11482.2 | 11370.2 | 11394.2 | 11277.5 | 12093.4 | 11119.3 | 11944.4 | 11030.9 | 11545.9 | 12487.5 | 10926.3 | 12053.4 | 11255.7 | 11442.2 | 11422.3 | 10884.8 | 11702.6 | 11248.2 | 11662.4 | 11374 | 10580.4 | 11857.8 | 10596.2 | 11808.9 | 11738 | 10601 | 11469.7 | 11034.5 | 11178.3 | 10624.2 | 11193.9 | 11583.5 | 11762.6 | 10883 | 11664.1 | 10481.4 | 11360.7 | 11263.5 | 10607.6 | 11672.9 | 10483.2 | 11779.5 | 10593 | 11662.1 | 10961 | 11618.9 | 11065.1 | 11942.9 | 10912.9 | 11498.1 | 10748.2 | 9572 | 11554.3 | 11276 | 10584.6 | 11883.6 | 11587.4 | 10826.2 | 10686.9 | 11643.4 | 10617.4 | 11064.8 | 11746 | 10635.4 | 11847 | 10619.2 | 11625.9 | 10894.4 | 11690 | 10332.9 | 11765.4 | 10858.4 | 11644.1 | 10798.3 | 11704 | 11003.1 | 10715.8 | 11585.2 | 10856.1 | 10652.6 | 11660.2 | 11789.4 | 11621.1 | 10793.4 | 11704.1 | 10716.9 | 11428.2 | 10902.3 | 11405.4 | 10028.2 | 11511.2 | 10715.2 | 10872.9 | 10878.1 | 10730.7 | 9285.1 | 10665.3 | 9420.7 | 10677.5 | 10709.8 | 12045.7 | 10840.7 | 12100.4 | 11073.2 | 11797.1 | 10705.4 | 11052.7 | 10873.4 | 11838.1 | 12122.7 | 12018.1 | 11941.4 | 12013.6 | 12041.8 | 11159.1 | 12031.8 | 12116.6 | 12146.4 | 12157 | 12130.5 | 12160.2 | 11212.4 | 12178.1 | 11244.2 | 21.29 | 21.25 | 21.63 | 21.64 | 21.39 | 21.27 | 0 | 35.57 | 0 | 0 | 35.5 | 34 | 2.46 | 1.25 | 2.02 | 0.46 | 1.74 | 2.15 | 5.58 | 4.96 | 5.14 | 4.59 | 4.8 | 5.26 | 5 | 5.09 | 5.07 | 4.99 | 5.08 | 5.07 | 1.3 | 1.41 | 1.2 | 1.59 | 1.52 | 1.3 | 6.29 | 6.26 | 6.24 | 6.28 | 6.21 | 6.22 | 0.29 | 0.3 | 0.25 | 0.28 | 0.27 | 0.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 848665 | 1594 | 835264 | 1612 | 338391.893 | 1019.133 | 5 | 5.09 | 5.07 | 4.99 | 5.08 | 5.07 | 6.29 | 6.26 | 6.24 | 6.28 | 6.21 | 6.22 | 904000 | 1000 | 897000 | 1000 | 1793333 | 5066 | 1799000 | 1788267 | 10.8833 | 5.05 | 1.3867 | 6.25 | 0.28333 | 27.46% | 4.533% | 21.4117 | 35.0233 | 1.68 | 5.055 | 1805384.3 | 1779600 | 2044409.7502 | 87.05% | 32 | 0
2025-02-05 | 2025 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 335090.89 | 7:32 | 18:31 | 10980.6 | 11397.8 | 11345.4 | 11314.9 | 11376.9 | 11446.8 | 11397.8 | 11727 | 11361.4 | 11367 | 11239.2 | 11395.6 | 11336.2 | 11335.4 | 11344.3 | 11418.1 | 11282.7 | 11366.6 | 11391 | 11456.9 | 11350.8 | 11378.3 | 11172 | 11281.7 | 11152.6 | 9856.1 | 11189.7 | 11142.1 | 11386.7 | 11254.5 | 11167.2 | 11359.5 | 11495.9 | 11604.4 | 11565 | 11498.7 | 11469.5 | 11343.9 | 11367.8 | 11243.1 | 12067.3 | 11059 | 11914.3 | 10948.3 | 11481.9 | 12445.4 | 10873.3 | 12039.6 | 11265.1 | 11449.8 | 11423.7 | 10868.1 | 11714.7 | 11238.7 | 11674 | 11378.3 | 10573.5 | 11875.7 | 10558.1 | 11819.5 | 11740.4 | 10557.7 | 11472.2 | 11022.9 | 11138.2 | 10565.4 | 11164 | 11546.9 | 11759.1 | 10828 | 11646.5 | 10419.7 | 11346.3 | 11222.4 | 10577.9 | 11640.4 | 10433.8 | 11766.2 | 10568.8 | 11638.5 | 10896.3 | 11572 | 10993.1 | 11902.2 | 10846.7 | 11439.8 | 10676.4 | 9494.2 | 11487.6 | 11216.1 | 10510.4 | 11838.5 | 11538.3 | 10749.2 | 10601.1 | 11601.9 | 10556.8 | 10990.1 | 11690.5 | 10539.9 | 11787.2 | 10522.3 | 11551.5 | 10789.4 | 11613.6 | 10223.8 | 11685.1 | 10745.7 | 11565.6 | 10685.3 | 11617 | 10878.6 | 10613.7 | 11511 | 10753.3 | 10545.9 | 11583.4 | 11718.3 | 11539 | 10684.2 | 11630.4 | 10605.2 | 11341.5 | 10782.1 | 11306.5 | 9905.7 | 11427.9 | 10603.8 | 10767.5 | 10773 | 10615.2 | 9185.5 | 10590.9 | 9356.6 | 10594.5 | 10633.9 | 11989.7 | 10784.5 | 12045.2 | 11013.7 | 11929.8 | 10832.4 | 11016.5 | 10798.1 | 11783 | 12073 | 11970.1 | 11886.9 | 11956.8 | 11987.3 | 11102.3 | 11979.6 | 12068.9 | 12101.2 | 12106.5 | 12086.1 | 12119.6 | 11159.1 | 12127.2 | 11188.3 | 21.97 | 21.68 | 22.33 | 22.24 | 22.04 | 21.7 | 0 | 37.06 | 0 | 0 | 37.1 | 35.7 | 2.19 | 1.19 | 2 | 0.67 | 1.47 | 1.73 | 5.46 | 5.14 | 4.8 | 4.52 | 5.13 | 4.86 | 5.02 | 5.11 | 5.09 | 5.03 | 5.09 | 5.09 | 1.29 | 1.43 | 1.19 | 1.59 | 1.52 | 1.31 | 6.32 | 6.29 | 6.24 | 6.3 | 6.21 | 6.23 | 0.28 | 0.3 | 0.25 | 0.28 | 0.27 | 0.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 849567 | 1596 | 836155 | 1614 | 340178.293 | 1022.8 | 5.02 | 5.11 | 5.09 | 5.03 | 5.09 | 5.09 | 6.32 | 6.29 | 6.24 | 6.3 | 6.21 | 6.23 | 902000 | 2000 | 891000 | 2000 | 1786400 | 3667 | 1789000 | 1782733 | 10.9833 | 5.0717 | 1.3883 | 6.265 | 0.28167 | 27.37% | 4.496% | 21.9933 | 36.62 | 1.5417 | 4.985 | 1798265.7 | 1775134 | 2047430.4433 | 86.7% | 25 | 0
2025-02-06 | 2025 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 335090.89 | 7:31 | 18:31 | 10071 | 10424 | 10365 | 10359 | 10371 | 10435 | 10394 | 10692 | 10389.4 | 10393.5 | 10271.2 | 10409.5 | 10351.4 | 10343.9 | 10357.6 | 10431.8 | 10272.9 | 10357.5 | 10379.9 | 10450.7 | 10349.2 | 10370.4 | 10191.5 | 10285.7 | 10188.2 | 9116.1 | 10212 | 10166.1 | 10381.2 | 10260 | 10199.8 | 10364.4 | 10539.2 | 10629.3 | 10579.3 | 10528.9 | 10440.1 | 10330.1 | 10351.1 | 10240.9 | 10974.7 | 10085.1 | 10838.7 | 10004.1 | 10478.1 | 11340.9 | 9928.6 | 10946.6 | 10052.2 | 10225.2 | 10204.3 | 9742.4 | 10456.5 | 10053.1 | 10431 | 10147.2 | 9535.8 | 10615.1 | 9549 | 10564.6 | 10497.9 | 9543.4 | 10255.9 | 9872.7 | 10141.6 | 9677.1 | 10154.4 | 10496.7 | 10657.9 | 9868.2 | 10568.3 | 9571.6 | 10295.6 | 10203.3 | 9673 | 10572.8 | 9577.9 | 10660.1 | 9654.4 | 10565.3 | 9940.6 | 10538.9 | 10021.8 | 10827.6 | 9899 | 10415.7 | 9761.2 | 8752.9 | 10474.3 | 10214.8 | 9675.8 | 10770.1 | 10504.5 | 9834.1 | 9701.9 | 10565.8 | 9566.2 | 9896.5 | 10493.6 | 9551.3 | 10585.6 | 9541.7 | 10395.3 | 9761.1 | 10443.8 | 9323 | 10510.6 | 9729.9 | 10422.3 | 9703 | 10456.1 | 9856.8 | 9798 | 10543.3 | 9892.7 | 9743.8 | 10604.5 | 10735.4 | 10571.4 | 9860.6 | 10651.7 | 9798.6 | 10400.9 | 9948.6 | 10372.6 | 9214.3 | 10477.1 | 9808.9 | 9937.1 | 9933.7 | 9812 | 8545.9 | 9782 | 8723.3 | 9752.2 | 9784 | 10982.5 | 9891.7 | 11026.8 | 10092.6 | 10760.8 | 9940 | 10089.8 | 9906 | 10811.1 | 11067.4 | 10957.7 | 10882.9 | 10981.2 | 11006.6 | 10191.8 | 10983.8 | 11062.9 | 11082.2 | 11092.4 | 11066.7 | 11101.4 | 10236.1 | 11119.5 | 10260.6 | 22.75 | 22.21 | 22.67 | 22.47 | 22.2 | 21.99 | 0 | 36.09 | 0 | 0 | 35.8 | 34.3 | 3.75 | 3.31 | 3.63 | 2.21 | 3.24 | 3.48 | 7.14 | 7.45 | 7.43 | 6.45 | 7.09 | 7.57 | 5.29 | 5.38 | 5.38 | 5.97 | 5.37 | 5.36 | 1.38 | 1.5 | 1.28 | 1.69 | 1.61 | 1.38 | 6.68 | 6.62 | 6.61 | 6.66 | 6.56 | 6.57 | 0.3 | 0.32 | 0.27 | 0.29 | 0.29 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 850387 | 1597 | 836971 | 1615 | 341806.693 | 1027.8 | 5.29 | 5.38 | 5.38 | 5.97 | 5.37 | 5.36 | 6.68 | 6.62 | 6.61 | 6.66 | 6.56 | 6.57 | 820000 | 1000 | 816000 | 1000 | 1628400 | 5000 | 1634000 | 1623400 | 11 | 5.4583 | 1.4733 | 6.6167 | 0.3 | 26.99% | 4.534% | 22.3817 | 35.3967 | 3.27 | 7.1883 | 1639348 | 1599667 | 1863095.5544 | 85.86% | 28 | 12176
2025-02-07 | 2025 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 335090.89 | 7:31 | 18:32 | 10817.3 | 11182.8 | 11117.7 | 11108.1 | 11129.7 | 11195.4 | 11153.1 | 11479.8 | 11151.8 | 11164.3 | 11043.5 | 11176.1 | 11126.3 | 11118.7 | 11139.1 | 11209.8 | 11078.3 | 11160.2 | 11189.7 | 11263.8 | 11163.5 | 11188.9 | 11004.4 | 11092.5 | 10995.1 | 9843.8 | 11013.2 | 10968.4 | 11203.9 | 11066.4 | 11016.3 | 11194.2 | 11417.8 | 11513.4 | 11471.4 | 11410.8 | 11295.1 | 11181.4 | 11200.2 | 11098.8 | 11824.3 | 10905 | 11698.4 | 10811.7 | 11305.9 | 12212.8 | 10731.1 | 11806 | 11088.1 | 11261.6 | 11217 | 10723.4 | 11490.3 | 11089.4 | 11471.8 | 11202.8 | 10494.9 | 11654 | 10508.2 | 11601.8 | 11528.4 | 10501.1 | 11262.7 | 10845.2 | 11030.7 | 10531.7 | 11034.7 | 11397.9 | 11562.6 | 10748.1 | 11468.9 | 10398.1 | 11173.4 | 11088.9 | 10506.3 | 11468.9 | 10405.3 | 11556.2 | 10484.1 | 11453.3 | 10826 | 11447.9 | 10912.1 | 11739.9 | 10776.6 | 11309.8 | 10655 | 9543.5 | 11393 | 11119.6 | 10529.5 | 11688.1 | 11393.2 | 10680.4 | 10542.3 | 11478.6 | 10570.9 | 10924.5 | 11572.9 | 10550.6 | 11649.5 | 10537.4 | 11444.6 | 10778.7 | 11507.3 | 10276.4 | 11580.7 | 10738 | 11475.3 | 10705.3 | 11526.2 | 10874.6 | 10632.5 | 11417.3 | 10737.6 | 10575 | 11495.6 | 11623.5 | 11449.6 | 10716.1 | 11533.7 | 10639.3 | 11267.3 | 10783 | 11239.1 | 10011.8 | 11356.3 | 10653.4 | 10792.9 | 10804.4 | 10630.8 | 9276.6 | 10611.5 | 9448 | 10567.4 | 10606.6 | 11877 | 10745.7 | 11922.1 | 10947.1 | 11815.1 | 10785.4 | 10939.9 | 10751.8 | 11668.7 | 11935.8 | 11850.6 | 11779.6 | 11843.5 | 11865 | 11032.3 | 11856.4 | 11936.8 | 11956.8 | 11963.4 | 11934.4 | 11972.9 | 11075.1 | 11994.6 | 11108.7 | 21.9374 | 21.395 | 21.5859 | 21.6154 | 21.3415 | 21.194 | 0 | 34.2609 | 0 | 0 | 34.4 | 33.2 | 3.5521 | 3.1331 | 3.3383 | 2.1367 | 3.3006 | 3.0493 | 6.5583 | 5.8433 | 6.195 | 5.855 | 6.0667 | 6.045 | 5.0396 | 5.1254 | 5.1106 | 5.03 | 5.1445 | 5.1389 | 1.3078 | 1.4233 | 1.2048 | 1.6013 | 1.5325 | 1.3179 | 6.2176 | 6.1728 | 6.1482 | 6.22 | 6.1636 | 6.169 | 0.2918 | 0.31166 | 0.26 | 0.28524 | 0.27554 | 0.31651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 851275 | 1599 | 837857 | 1617 | 343574.827 | 1032.733 | 5.0396 | 5.1254 | 5.1106 | 5.03 | 5.1445 | 5.1389 | 6.2176 | 6.1728 | 6.1482 | 6.22 | 6.1636 | 6.169 | 888000 | 2000 | 886000 | 2000 | 1768134 | 4933 | 1770000 | 1763201 | 11.0167 | 5.0982 | 1.3979 | 6.1819 | 0.29012 | 27.42% | 4.693% | 21.5115 | 33.9536 | 3.085 | 6.0939 | 1780066.4 | 1751066 | 2029995.679 | 86.26% | 28 | 0
2025-02-08 | 2025 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 335090.89 | 7:34 | 18:33 | 10604.8 | 10973.7 | 10926.7 | 10912.6 | 10942.6 | 11004.8 | 10941 | 11270.4 | 10925.4 | 10941.2 | 10819.8 | 10951.5 | 10916.7 | 10896.4 | 10951.2 | 11015.8 | 10895.4 | 10973.3 | 10977.7 | 11054 | 10957.8 | 10978.4 | 10789.7 | 10886.9 | 10754.3 | 9688.4 | 10780.6 | 10735.3 | 10973.4 | 10836.4 | 10785.8 | 10960.4 | 11165.2 | 11257.4 | 11218.5 | 11156.2 | 11063.8 | 10947.4 | 10967.1 | 10864.7 | 11688.3 | 10732.7 | 11551.8 | 10637.2 | 11114.3 | 12046.1 | 10538.4 | 11660.8 | 10852.4 | 11030.3 | 11002.2 | 10496.2 | 11270.3 | 10860.2 | 11237.8 | 10947.4 | 10274.3 | 11430 | 10307.7 | 11377.2 | 11305.7 | 10294.1 | 11027.8 | 10609.8 | 10789 | 10318.3 | 10796.1 | 11175.7 | 11344.6 | 10530.1 | 11253.9 | 10224.2 | 10936.1 | 10869.1 | 10293.2 | 11260 | 10217.7 | 11324.6 | 10271.1 | 11227.9 | 10611.4 | 11242.8 | 10700.5 | 11544.5 | 10561.2 | 11100.2 | 10431.4 | 9406.1 | 11160.1 | 10892.8 | 10315.3 | 11463.3 | 11157.3 | 10436.3 | 10303.4 | 11246.3 | 10357.9 | 10705.7 | 11366.3 | 10348.8 | 11432.1 | 10332.8 | 11223.4 | 10561.9 | 11291.4 | 10095.6 | 11374 | 10532.1 | 11258.8 | 10489.4 | 11316.6 | 10666.6 | 10426.8 | 11218.7 | 10529.5 | 10382.9 | 11300.8 | 11427.9 | 11248.6 | 10509.5 | 11342.2 | 10441.5 | 11071.9 | 10579 | 11035.9 | 9861.6 | 11161.8 | 10465.6 | 10600.5 | 10613 | 10433.2 | 9148.4 | 10421.3 | 9307.1 | 10401.1 | 10438.5 | 11716 | 10581.6 | 11757.7 | 10775.8 | 11650 | 10607.3 | 10763.1 | 10574.9 | 11506.4 | 11781 | 11690.7 | 11617.3 | 11680.3 | 11705.5 | 10858 | 11692.5 | 11761.6 | 11795.2 | 11807.1 | 11777.2 | 11819.3 | 10910.1 | 11823.5 | 10938.7 | 23.97 | 23.56 | 23.6 | 23.92 | 23.46 | 23.26 | 0 | 38.18 | 0 | 0 | 38.2 | 37.2 | 2.9 | 1.95 | 2.7 | 0.97 | 2.11 | 2.41 | 5.7 | 5.04 | 4.92 | 4.78 | 4.77 | 4.76 | 5.01 | 5.08 | 5.1 | 5.91 | 5.1 | 5.13 | 1.29 | 1.43 | 1.2 | 1.58 | 1.52 | 1.32 | 6.22 | 6.16 | 6.17 | 6.2 | 6.15 | 6.2 | 0.29 | 0.3 | 0.26 | 0.28 | 0.27 | 0.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 852147 | 1601 | 838729 | 1619 | 345311.894 | 1037.733 | 5.01 | 5.08 | 5.1 | 5.91 | 5.1 | 5.13 | 6.22 | 6.16 | 6.17 | 6.2 | 6.15 | 6.2 | 872000 | 2000 | 872000 | 2000 | 1737067 | 5000 | 1740000 | 1732067 | 10.9833 | 5.2217 | 1.39 | 6.1833 | 0.285 | 26.62% | 4.609% | 23.6283 | 37.86 | 2.1733 | 4.995 | 1747671.7 | 1725400 | 2018306.4247 | 85.49% | 30 | 120
2025-02-09 | 2025 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 335090.89 | 7:31 | 18:32 | 10742.1 | 11139.5 | 11069.3 | 11046.2 | 11074.1 | 11188.4 | 11127.9 | 11473.3 | 11108 | 11109 | 10987.4 | 11123.9 | 11094.6 | 11079.6 | 11091.4 | 11178.1 | 11047.1 | 11140.7 | 11155.8 | 11222.4 | 11130.5 | 11147 | 10931.7 | 11047.3 | 10884.1 | 9657.4 | 10916.7 | 10864.7 | 11139.4 | 10988.4 | 10918.8 | 11123.8 | 11236.2 | 11337.3 | 11285.4 | 11227.8 | 11259.4 | 11120.1 | 11145.1 | 11050.1 | 11855.5 | 10818.3 | 11728 | 10708.1 | 11253.3 | 12233.9 | 10634.2 | 11838.3 | 11021.4 | 11210.1 | 11158 | 10577.8 | 11462.7 | 11017.8 | 11422.5 | 11130 | 10322.5 | 11628.2 | 10345.7 | 11567.3 | 11486.6 | 10340.4 | 11211.7 | 10731.8 | 10920.6 | 10381.2 | 10926.7 | 11374.1 | 11546.9 | 10625 | 11454.6 | 10262.1 | 11083.7 | 11020.9 | 10345.2 | 11470.4 | 10261 | 11523.9 | 10315.3 | 11413.7 | 10677.7 | 11401.3 | 10763.9 | 11728.8 | 10619.3 | 11229.4 | 10516.1 | 9345.5 | 11301.7 | 11009.3 | 10349.1 | 11664.5 | 11360.4 | 10538.6 | 10394.5 | 11425.3 | 10352.4 | 10777 | 11534.4 | 10391.4 | 11597.6 | 10357.3 | 11363.1 | 10599.1 | 11442.6 | 10055.1 | 11525.9 | 10568.4 | 11404 | 10517.4 | 11460.6 | 10701.1 | 10481.9 | 11401.2 | 10605.7 | 10423.5 | 11494 | 11635.7 | 11396.5 | 10585.8 | 11549.4 | 10510.2 | 11218.7 | 10643.2 | 11176.3 | 9846.2 | 11335.6 | 10512.2 | 10682.7 | 10698.4 | 10486.8 | 9118.7 | 10485.6 | 9269.6 | 10404.8 | 10456.3 | 11896.6 | 10636.3 | 11970.2 | 10879 | 11855.6 | 10690.2 | 10878 | 10641.6 | 11696.8 | 11996.2 | 11869.9 | 11798.9 | 11867 | 11891 | 10984 | 11908.2 | 11942.1 | 11989.3 | 12002 | 11981.4 | 12022.9 | 11006.2 | 12001.4 | 11045.5 | 25.22 | 25.21 | 25.34 | 25.67 | 25.29 | 24.88 | 0 | 40.79 | 0 | 0 | 40.9 | 39.6 | 1.9 | 0.98 | 1.75 | 0.09 | 1.46 | 0.74 | 4.64 | 3.8 | 3.54 | 2.57 | 3.68 | 3.75 | 5.09 | 5.14 | 5.17 | 5.3 | 5.19 | 5.17 | 1.31 | 1.43 | 1.21 | 1.61 | 1.55 | 1.34 | 6.26 | 6.21 | 6.21 | 6.24 | 6.21 | 6.22 | 0.28 | 0.3 | 0.25 | 0.27 | 0.26 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 853030 | 1603 | 839610 | 1620 | 347068.227 | 1042.667 | 5.09 | 5.14 | 5.17 | 5.3 | 5.19 | 5.17 | 6.26 | 6.21 | 6.21 | 6.24 | 6.21 | 6.22 | 883000 | 2000 | 881000 | 1000 | 1756333 | 4934 | 1761000 | 1751399 | 11.0167 | 5.1767 | 1.4083 | 6.225 | 0.27667 | 27.21% | 4.444% | 25.2683 | 40.43 | 1.1533 | 3.6633 | 1768081.5 | 1745734 | 2004804.42 | 87.08% | 29 | 611
2025-02-10 | 2025 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 335090.89 | 7:35 | 18:34 | 10394.9 | 10771.1 | 10730.8 | 10704.1 | 10754 | 10856.3 | 10779.8 | 11138.6 | 10755.8 | 10778.2 | 10648.4 | 10776.1 | 10748.9 | 10725.4 | 10734.3 | 10822.8 | 10693.9 | 10783.6 | 10792.1 | 10857.4 | 10772 | 10788.2 | 10600.5 | 10700.3 | 10578.2 | 9373.2 | 10593.5 | 10552.5 | 10801.7 | 10656.5 | 10616.4 | 10802.8 | 10904.6 | 11003.2 | 10983.7 | 10910.3 | 10896.4 | 10766.7 | 10787.3 | 10703 | 11513 | 10518.6 | 11379.6 | 10400.4 | 10922.5 | 11883.8 | 10312 | 11488.4 | 10692.6 | 10862.1 | 10821.5 | 10266.2 | 11115.3 | 10670.7 | 11065.6 | 10815.4 | 9987.6 | 11249.6 | 10028.2 | 11185.9 | 11123.5 | 10022.3 | 10826.2 | 10365.5 | 10578 | 10044.5 | 10576.1 | 10968.8 | 11171.6 | 10266.4 | 11071.3 | 9906.3 | 10743.1 | 10651.5 | 10024.1 | 11063.9 | 9916.7 | 11161.3 | 9994 | 11026.5 | 10340.8 | 11012.5 | 10437.1 | 11340.1 | 10300.7 | 10876.7 | 10176.1 | 9067.2 | 10941.3 | 10687.3 | 10026.1 | 11292.4 | 11013.2 | 10256 | 10140.9 | 11083.3 | 10085.8 | 10492.2 | 11209 | 10094.4 | 11272.4 | 10076.1 | 11055.7 | 10317.5 | 11132.9 | 9800.3 | 11214.5 | 10296.5 | 11097.8 | 10257.2 | 11167.6 | 10437.6 | 10161.3 | 11009.5 | 10292.7 | 10100.7 | 11119.3 | 11238.6 | 10948 | 10245.6 | 11161.7 | 10173.3 | 10885.9 | 10332.6 | 10834.4 | 9530.9 | 10968 | 10185.2 | 10324.5 | 10332.3 | 10191.4 | 8830.2 | 10164 | 9001.4 | 10158.5 | 10187.1 | 11550.1 | 10334.3 | 11603.7 | 10542.7 | 8815.3 | 9080.4 | 10529.7 | 10351.4 | 11314.2 | 11621.1 | 11513 | 11444.1 | 11504 | 11536.2 | 10626.7 | 11531.8 | 11584.3 | 11624.1 | 11634.2 | 11613.9 | 11647 | 10669.4 | 11648.6 | 10701.7 | 26.4794 | 26.2496 | 26.8773 | 26.4386 | 26.5331 | 26.5763 | 0 | 39.2488 | 0 | 0 | 39.7 | 39 | 3.3103 | 2.6848 | 3.1049 | 1.5786 | 3.0111 | 2.9804 | 6.6633 | 6.4333 | 6.3467 | 5.58 | 6.8083 | 6.875 | 4.9546 | 5.012 | 5.0246 | 4.9565 | 5.0533 | 5.0576 | 1.2739 | 1.4183 | 1.17 | 1.5609 | 1.5132 | 1.3219 | 6.0079 | 6.0077 | 5.9431 | 5.9841 | 5.9753 | 6.0397 | 0.29535 | 0.31924 | 0.26484 | 0.28804 | 0.28595 | 0.32373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 853885 | 1605 | 840460 | 1622 | 348767.827 | 1046.6 | 4.9546 | 5.012 | 5.0246 | 4.9565 | 5.0533 | 5.0576 | 6.0079 | 6.0077 | 5.9431 | 5.9841 | 5.9753 | 6.0397 | 855000 | 2000 | 850000 | 2000 | 1699600 | 3933 | 1701000 | 1695667 | 10.9833 | 5.0098 | 1.3764 | 5.993 | 0.29619 | 27.47% | 4.942% | 26.5257 | 39.3163 | 2.7783 | 6.4511 | 1710116.3 | 1688534 | 1943007.419 | 86.9% | 27 | 0
2025-02-11 | 2025 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 335090.89 | 7:35 | 18:35 | 10795 | 11176 | 11142 | 11111 | 11170 | 11268 | 11161 | 11574 | 11202 | 11221 | 11069 | 11216 | 11171 | 11159 | 11150 | 11256 | 11107 | 11218 | 11244 | 11317 | 11216 | 11239 | 11019 | 11132 | 11014 | 9739 | 11038 | 10984 | 11241 | 11068 | 10916 | 11236 | 11335 | 11452 | 11429 | 11345 | 11350 | 11216 | 11239 | 11110 | 11999 | 10919 | 11844 | 10793 | 11327 | 12372 | 10704 | 11976 | 11125 | 11311 | 11280 | 10682 | 11592 | 11086 | 11539 | 11245 | 10382 | 11733 | 10427 | 11698 | 11596 | 10417 | 11285 | 10797 | 10989 | 10418 | 11002 | 11416 | 11638 | 10668 | 11528 | 10284 | 11179 | 11079 | 10417 | 11535 | 10313 | 11634 | 10391 | 11496 | 10735 | 11466 | 10810 | 11806 | 10676 | 11286 | 10542 | 9382 | 11371 | 11078 | 10370 | 11742 | 11419 | 10601 | 10459 | 11516 | 10411 | 10838 | 11604 | 10422 | 11696 | 10404 | 11446 | 10655 | 11535 | 10116 | 11611 | 10626 | 11479 | 10566 | 11551 | 10763 | 10491 | 11406 | 10629 | 10427 | 11500 | 11617 | 11336 | 10550 | 11530 | 10476 | 11243 | 10654 | 11181 | 9803 | 11310 | 10483 | 10647 | 10656 | 10510 | 9092 | 10449 | 9250 | 10495 | 10528 | 11973 | 10670 | 12027 | 10901 | 11895 | 10694 | 10881 | 10694 | 11727 | 12048 | 11928 | 11848 | 11919 | 11949 | 10994 | 11949 | 12003 | 12053 | 12080 | 12055 | 12087 | 11041 | 12074 | 11073 | 25.724 | 25.5112 | 26.1743 | 25.9101 | 25.9222 | 25.6964 | 0 | 41.6413 | 0 | 0 | 41.7 | 41 | 2.1552 | 1.3474 | 2.2103 | 0.58373 | 1.6522 | 1.1049 | 5.4117 | 5.1683 | 5.0483 | 5.1667 | 5.9617 | 5.5083 | 5.1027 | 5.1829 | 5.1709 | 5.0981 | 5.1887 | 5.2044 | 1.3118 | 1.437 | 1.2098 | 1.6167 | 1.5382 | 1.3282 | 6.2671 | 6.2735 | 6.2147 | 6.2579 | 6.2145 | 6.2701 | 0.27789 | 0.29625 | 0.24775 | 0.26804 | 0.26329 | 0.30462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 854775 | 1607 | 841343 | 1623 | 1493.467 | 2.067 | 5.1027 | 5.1829 | 5.1709 | 5.0981 | 5.1887 | 5.2044 | 6.2671 | 6.2735 | 6.2147 | 6.2579 | 6.2145 | 6.2701 | 890000 | 2000 | 883000 | 1000 | 1493467 | 2067 | 1770000 | 1491400 | 11 | 5.1579 | 1.407 | 6.2496 | 0.27631 | 27.28% | 4.421% | 25.823 | 41.4471 | 1.509 | 5.3775 | 1777969 | 1761000 | 2006956.2211 | 87.74% | 20 | 0
2025-02-12 | 2025 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 335090.89 | 7:32 | 18:34 | 10831 | 11241.2 | 11192.1 | 11160.4 | 11212.9 | 11291.3 | 11228.3 | 11591 | 11240 | 11254.6 | 11111.8 | 11254.1 | 11223.7 | 11202.2 | 11203.5 | 11294 | 11155.3 | 11252.8 | 11274.2 | 11347 | 11245.9 | 11277.1 | 11066.6 | 11171.1 | 11048.4 | 9742.1 | 11078.2 | 11021.7 | 11268.9 | 11102.2 | 11011.9 | 11275.1 | 11325.4 | 11461.4 | 11436.2 | 11348 | 11378.3 | 11243.9 | 11263.4 | 11151.5 | 11977.3 | 10931.2 | 11828.1 | 10797.2 | 11359.7 | 12374.8 | 10723.8 | 11955 | 11157.3 | 11339.5 | 11300.9 | 10690.8 | 11598.6 | 11124.2 | 11558.2 | 11280 | 10385.2 | 11748.3 | 10412.9 | 11706.6 | 11617.1 | 10418 | 11328.4 | 10847.9 | 11038.6 | 10408 | 11043.7 | 11433.1 | 11654.5 | 10663.9 | 11550.1 | 10260.2 | 11211.4 | 11108.6 | 10409.6 | 11547.3 | 10283.7 | 11650.7 | 10364.7 | 11515.2 | 10735.8 | 11477 | 10826.2 | 11812.2 | 10682.8 | 11319.9 | 10550.2 | 9369.2 | 11415.5 | 11121.6 | 10377.7 | 11773.5 | 11472 | 10643.5 | 10488.4 | 11543 | 10407.8 | 10879.2 | 11626.9 | 10406 | 11723.3 | 10404.9 | 11479.8 | 10677.6 | 11549.4 | 10110.9 | 11619.3 | 10630.3 | 11488.4 | 10570.6 | 11546.7 | 10771.7 | 10484.6 | 11474.3 | 10629.8 | 10411.7 | 11516.4 | 11620.9 | 11456.2 | 10551.8 | 11526.6 | 10465.3 | 11267.1 | 10656.9 | 11215.6 | 9781.7 | 11324.4 | 10454.6 | 10635.4 | 10659.8 | 10474.7 | 9067.5 | 10424.3 | 9246.7 | 10438.7 | 10481.5 | 11953.9 | 10658.6 | 12011.9 | 10907.3 | 11863.7 | 10668.5 | 10871.5 | 10669.2 | 11732.8 | 12034.6 | 11933.7 | 11854.7 | 11920.7 | 11945.2 | 11011.6 | 11941.9 | 12003.8 | 12038.9 | 12059.6 | 12033 | 12070 | 11048 | 12073.2 | 11083 | 24.6655 | 24.4406 | 24.7925 | 24.8751 | 24.7544 | 24.5034 | 0 | 38.8449 | 0 | 0 | 38.7 | 37.4 | 2.4984 | 1.8804 | 2.4367 | 0.91581 | 1.8523 | 1.6031 | 5.5383 | 5.36 | 5.2067 | 4.4867 | 5.52 | 4.71 | 5.0657 | 5.1428 | 5.1351 | 5.0608 | 5.1375 | 5.1371 | 1.3206 | 1.4486 | 1.2151 | 1.6235 | 1.54 | 1.3358 | 6.1946 | 6.197 | 6.1464 | 6.1871 | 6.1267 | 6.1587 | 0.29509 | 0.31481 | 0.26391 | 0.28767 | 0.27783 | 0.31948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 855666 | 1609 | 842227 | 1626 | 3261.534 | 7.067 | 5.0657 | 5.1428 | 5.1351 | 5.0608 | 5.1375 | 5.1371 | 6.1946 | 6.197 | 6.1464 | 6.1871 | 6.1267 | 6.1587 | 891000 | 2000 | 884000 | 3000 | 1768067 | 5000 | 1770000 | 1763067 | 11.0333 | 5.1132 | 1.4139 | 6.1684 | 0.29313 | 27.65% | 4.752% | 24.6719 | 38.315 | 1.8644 | 5.1369 | 1780240.1 | 1749867 | 1990811.8316 | 87.9% | 23 | 0
2025-02-13 | 2025 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 335090.89 | 7:30 | 18:36 | 10799.6 | 11279 | 11213.2 | 11190.4 | 11234.3 | 11296.2 | 11261.3 | 11633.8 | 11254.8 | 11281.3 | 11122.4 | 11280.2 | 11232.2 | 11224 | 11191.3 | 11302.3 | 11154.1 | 11262.7 | 11297.8 | 11365.8 | 11268.6 | 11287.2 | 11056 | 11180.2 | 11044.2 | 9696 | 11072.5 | 11017.1 | 11286.6 | 11100 | 11063.3 | 11289.8 | 11304.3 | 11409.7 | 11389.4 | 11309.6 | 11397.4 | 11252.7 | 11277.6 | 11155.5 | 12022.3 | 10937.8 | 11883.6 | 10789.6 | 11392.3 | 12425 | 10728.2 | 12007.2 | 11158.6 | 11350.6 | 11311.5 | 10680.2 | 11619.2 | 11121.2 | 11583.2 | 11291.2 | 10335.4 | 11776.6 | 10361.3 | 11728.6 | 11638.6 | 10354.7 | 11343 | 10798.6 | 11033.1 | 10378.2 | 11021.6 | 11463.1 | 11688.4 | 10646.2 | 11575.7 | 10236.3 | 11220.8 | 11096.9 | 10371.2 | 11580.3 | 10246 | 11687.8 | 10321.6 | 11544.9 | 10719.1 | 11519.2 | 10795.5 | 11853 | 10646.7 | 11334.7 | 10516.3 | 9337.8 | 11435.3 | 11115.2 | 10330.8 | 11818.9 | 11519.1 | 10633.4 | 10497.1 | 11581.6 | 10397.6 | 10851.3 | 11675.5 | 10392.3 | 11756.4 | 10388 | 11506.3 | 10653.9 | 11601.1 | 10101 | 11669.4 | 10616.6 | 11533.1 | 10566.3 | 11590.7 | 10745.8 | 10473.8 | 11518.8 | 10610.8 | 10392 | 11559.7 | 11663.6 | 11498.8 | 10514.8 | 11569.4 | 10425.3 | 11299.6 | 10629.6 | 11228.9 | 9740.1 | 11344.1 | 10409 | 10585.1 | 10611.4 | 10408.3 | 9026.3 | 10367.9 | 9206.8 | 10352.4 | 10394.3 | 11971.5 | 10597.3 | 12022.3 | 10850.3 | 11897.7 | 10626.7 | 10832.4 | 10587.1 | 11733.9 | 12053.2 | 11935.3 | 11860 | 11925.9 | 11952.1 | 10953.8 | 11956.9 | 12020.8 | 12057.3 | 12079.3 | 12046.8 | 12080.3 | 10981.8 | 12083.5 | 11030 | 24.97 | 24.9 | 25.43 | 25.38 | 25.2 | 25.02 | 0 | 40.37 | 0 | 0 | 40.4 | 39.5 | 2.36 | 1.86 | 2.2 | 2.05 | 1.77 | 1.82 | 5.24 | 5.1 | 4.76 | 5.18 | 5.65 | 4.85 | 5.09 | 5.17 | 5.18 | 5.09 | 5.17 | 5.15 | 1.33 | 1.44 | 1.23 | 1.63 | 1.54 | 1.32 | 6.21 | 6.22 | 6.18 | 6.21 | 6.15 | 6.16 | 0.29 | 0.3 | 0.26 | 0.28 | 0.27 | 0.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 856558 | 1611 | 843110 | 1628 | 5030.267 | 11.4 | 5.09 | 5.17 | 5.18 | 5.09 | 5.17 | 5.15 | 6.21 | 6.22 | 6.18 | 6.21 | 6.15 | 6.16 | 892000 | 2000 | 883000 | 2000 | 1768733 | 4333 | 1771000 | 1764400 | 11.1 | 5.1417 | 1.415 | 6.1883 | 0.285 | 27.52% | 4.605% | 25.15 | 40.09 | 2.01 | 5.13 | 1780151 | 1736934 | 1982429.786 | 87.62% | 24 | 0
2025-02-14 | 2025 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 335090.89 | 7:31 | 18:34 | 10479 | 10901.9 | 10856.3 | 10822.2 | 10904 | 10922.2 | 10873.7 | 11269.5 | 10892.1 | 10918 | 10768.6 | 10920.5 | 10848.4 | 10851.7 | 10814.7 | 10917 | 10785 | 10885.9 | 10926 | 10988.8 | 10899.2 | 10913.1 | 10707.2 | 10815.1 | 10693.4 | 9436.5 | 10704.1 | 10657.5 | 10916.4 | 10742 | 10720.6 | 10932.8 | 11023.6 | 11097 | 11079.7 | 11009.9 | 11049.6 | 10894.9 | 10917.2 | 10819.7 | 11699.1 | 10612 | 11561.6 | 10488.4 | 11040 | 12113.7 | 10401.6 | 11681.3 | 10803.4 | 10992.6 | 10944.9 | 10392.2 | 11275 | 10747.6 | 11225.2 | 10951.2 | 10071.2 | 11447.4 | 10103.2 | 11398.8 | 11295.4 | 10096.8 | 10983.1 | 10492.8 | 10713.4 | 10138.6 | 10701.5 | 11144.5 | 11368.5 | 10378.5 | 11246.7 | 9994.6 | 10886.3 | 10778.5 | 10121 | 11250.5 | 10002.7 | 11366.1 | 10087.8 | 11204.7 | 10453.9 | 11195.8 | 10505.4 | 11551.4 | 10377.2 | 10987.8 | 10257.5 | 9121.3 | 11085.6 | 10792.1 | 10106.2 | 11501.2 | 11170.4 | 10360.1 | 10244.2 | 11249.7 | 10129.1 | 10521.7 | 11323.1 | 10100.2 | 11398.4 | 10089.6 | 11132 | 10334.8 | 11229.7 | 9805.7 | 11293.9 | 10299.4 | 11152.2 | 10253.2 | 11214.6 | 10436.8 | 10162.8 | 11130 | 10294.7 | 10097 | 11187.4 | 11288.8 | 11119.5 | 10213.2 | 11202.7 | 10137.4 | 10918.1 | 10323.8 | 10849.7 | 9490.8 | 10972 | 10138 | 10298.2 | 10316.2 | 10125.2 | 8794.2 | 10106.8 | 8954.7 | 10076.7 | 10103.4 | 11626.3 | 10296.5 | 11678.9 | 10515.3 | 11562.9 | 10329.8 | 10520 | 10275 | 11361.5 | 11701.3 | 11579.5 | 11506.6 | 11569.4 | 11602.9 | 10603.4 | 11600.6 | 11678.8 | 11719.1 | 11734 | 11705 | 11734.1 | 10653.9 | 11748.1 | 10700.1 | 27.3343 | 27.1029 | 0 | 27.4145 | 27.4455 | 27.2852 | 0 | 40.8129 | 0 | 0 | 40.8 | 40.1 | 3.5682 | 3.3146 | 0 | 2.9812 | 3.5265 | 3.4268 | 8.9683 | 7.7317 | 0 | 7.6617 | 7.7233 | 7.43 | 5.0449 | 5.1169 | 0 | 5.024 | 5.0759 | 5.0677 | 1.313 | 1.4203 | 0 | 1.6052 | 1.5143 | 1.3022 | 6.0906 | 6.0798 | 0 | 6.0826 | 5.9674 | 5.9901 | 0.29268 | 0.31311 | 0 | 0.2835 | 0.27676 | 0.31463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 857424 | 1612 | 843967 | 1629 | 6747.201 | 16.333 | 5.0449 | 5.1169 | 0 | 5.024 | 5.0759 | 5.0677 | 6.0906 | 6.0798 | 0 | 6.0826 | 5.9674 | 5.9901 | 866000 | 1000 | 857000 | 1000 | 1716934 | 4933 | 1721000 | 1712001 | 11.05 | 5.0659 | 1.431 | 6.0421 | 0.29613 | 28.25% | 4.901% | 27.3165 | 40.571 | 3.3635 | 7.903 | 1727755.9 | 1697334 | 1944145.7398 | 87.3% | 23 | 0
2025-02-15 | 2025 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 335090.89 | 7:34 | 18:37 | 11199.2 | 11597.9 | 11563.3 | 11540.6 | 11609.4 | 11653.9 | 11594.2 | 11930.5 | 11586.9 | 11609.9 | 11472 | 11614.6 | 11567.2 | 11562 | 11532.4 | 11632.9 | 11498.8 | 11600.4 | 11627.5 | 11700.1 | 11605 | 11626.1 | 11428.2 | 11533.7 | 11398 | 10086 | 11413.9 | 11365 | 11618.8 | 11455.8 | 11423.4 | 11612.3 | 11778.6 | 11869.2 | 11843.9 | 11768.8 | 11731.8 | 11592.9 | 11606.9 | 11501.9 | 12345 | 11352 | 12195 | 11224.9 | 11763.3 | 12724.5 | 11131.9 | 12313.7 | 11494.7 | 11678.8 | 11652.1 | 11092.2 | 11956.6 | 11446.3 | 11904.6 | 11619.6 | 10746.6 | 12086.2 | 10776.8 | 12047.9 | 11964.3 | 10782.4 | 11661.9 | 11187 | 11403.1 | 10809 | 11398.9 | 11806.3 | 11993.6 | 11069.3 | 11894.9 | 10653.9 | 11568.6 | 11468.7 | 10789.1 | 11891.7 | 10655.8 | 11994 | 10736.3 | 11853.2 | 11152.6 | 11858.9 | 11212.2 | 12180.4 | 11081.9 | 11684.6 | 10939.3 | 9742.1 | 11771.5 | 11502.3 | 10791.1 | 12148.1 | 11831.4 | 11038.8 | 10904.4 | 11920.6 | 10818.6 | 11256.8 | 11988.9 | 10809.2 | 12068.8 | 10792.7 | 11844.9 | 11047 | 11905.4 | 10470.5 | 11975.1 | 11011.2 | 11845.9 | 10938.4 | 11907.7 | 11170.7 | 10880 | 11834 | 11018.4 | 10784.5 | 11860.5 | 11980.4 | 11808.5 | 10930 | 11896.4 | 10855.2 | 11634.5 | 11051.3 | 11574.6 | 10136.9 | 11700.6 | 10854.5 | 11014.1 | 11032.7 | 10844 | 9398.5 | 10817.4 | 9558.1 | 10791.5 | 10835.1 | 12293 | 11037 | 12343 | 11275 | 12221 | 11071 | 11266 | 11013 | 12074.5 | 12371.1 | 12271.4 | 12196.4 | 12256.5 | 12275.4 | 11372.1 | 12281.7 | 12349.9 | 12388.3 | 12399.1 | 12376 | 12408.2 | 11415.1 | 12424.5 | 11447.1 | 27.45 | 27.11 | 0 | 27.6 | 27.39 | 27.25 | 0 | 40.44 | 0 | 0 | 40.3 | 39.2 | 3.71 | 3.31 | 0 | 3.02 | 3.73 | 3.46 | 6.51 | 6.51 | 0 | 6.29 | 7.37 | 6.19 | 5.32 | 5.39 | 0 | 5.31 | 5.36 | 5.38 | 1.37 | 1.51 | 0 | 1.69 | 1.61 | 1.39 | 6.5 | 6.48 | 0 | 6.49 | 6.41 | 6.44 | 0.3 | 0.32 | 0 | 0.29 | 0.28 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 858344 | 1614 | 844880 | 1630 | 8573.601 | 21.133 | 5.32 | 5.39 | 0 | 5.31 | 5.36 | 5.38 | 6.5 | 6.48 | 0 | 6.49 | 6.41 | 6.44 | 920000 | 2000 | 913000 | 1000 | 1826400 | 4800 | 1830000 | 1821600 | 11.05 | 5.352 | 1.514 | 6.464 | 0.304 | 28.29% | 4.703% | 27.36 | 39.98 | 3.446 | 6.574 | 1838618.6 | 1796400 | 2060155.2498 | 87.2% | 20 | 0
2025-02-16 | 2025 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 335090.89 | 7:29 | 18:34 | 10032.3 | 10429.4 | 10389.4 | 10374.1 | 10427 | 10481.4 | 10465.9 | 10772.4 | 10439.6 | 10464.1 | 10322.5 | 10454.7 | 10424.2 | 10407.2 | 10372.4 | 10482.2 | 10344.1 | 10455.2 | 10473.1 | 10541.8 | 10460.9 | 10475.1 | 10289.8 | 10390 | 10278 | 9051.4 | 10281.9 | 10237.1 | 10510.8 | 10357.9 | 10306.4 | 10503.5 | 10581.4 | 10665.7 | 10640.6 | 10568.4 | 10633.2 | 10495.3 | 10510.6 | 10417.9 | 11211.3 | 10199.8 | 11087 | 10063.3 | 10629.3 | 11614.4 | 10002.7 | 11197.5 | 10378.5 | 10556.5 | 10497.7 | 9959.6 | 10799.6 | 10338.5 | 10773.3 | 10518.2 | 9648.1 | 10966.1 | 9654.6 | 10922.7 | 10827.9 | 9650.7 | 10539.6 | 10058.2 | 10303.3 | 9724.8 | 10294.5 | 10713.2 | 10903.3 | 9964 | 10795.2 | 9584.2 | 10463 | 10361 | 9705 | 10803.4 | 9600.5 | 10887.9 | 9658.3 | 10751.5 | 10065.3 | 10771 | 10138.8 | 11107.8 | 9999.7 | 10622.2 | 9857.9 | 8793.4 | 10746.1 | 10434.4 | 9733.1 | 11075.1 | 10746.1 | 9932.8 | 9797.4 | 10844 | 9766.4 | 10176.5 | 10945 | 9756.9 | 11014.4 | 9751.3 | 10778.3 | 9988.1 | 10863.2 | 9469.1 | 10929.5 | 9953.8 | 10774.9 | 9849.2 | 10843.7 | 10096.7 | 9831 | 10761.7 | 9951.9 | 9738.9 | 10815 | 10917.3 | 10750.4 | 9880 | 10849.7 | 9792.7 | 10571.2 | 9981.1 | 10497.8 | 9153.8 | 10628.2 | 9772.5 | 9897.3 | 9916.6 | 9727.5 | 8440.4 | 9726.2 | 8608.4 | 9714.9 | 9742.9 | 11223 | 9937 | 11249 | 10145 | 11136 | 9940 | 10128 | 9909 | 10959 | 11267.1 | 11190.6 | 11120.3 | 11180.3 | 11205.6 | 10242.2 | 11181.3 | 11258.6 | 11288.2 | 11298 | 11263.5 | 11298.2 | 10273.4 | 11322.4 | 10343 | 27.2468 | 27.3058 | 27.6403 | 27.4828 | 27.2864 | 27.4102 | 0 | 41.2194 | 0 | 0 | 41.4 | 40.7 | 3.1402 | 2.8607 | 2.8555 | 2.0815 | 2.9324 | 2.6235 | 6.765 | 6.88 | 7.6017 | 6.3317 | 6.8217 | 7.4117 | 4.9014 | 4.9719 | 4.8095 | 4.9228 | 4.9607 | 4.9584 | 1.2759 | 1.3716 | 1.1374 | 1.5683 | 1.4676 | 1.2669 | 5.8416 | 5.8412 | 5.628 | 5.8708 | 5.8154 | 5.7949 | 0.29173 | 0.30908 | 0.25712 | 0.28793 | 0.27491 | 0.30882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 859175 | 1616 | 845708 | 1631 | 10226.2 | 26.067 | 4.9014 | 4.9719 | 4.8095 | 4.9228 | 4.9607 | 4.9584 | 5.8416 | 5.8412 | 5.628 | 5.8708 | 5.8154 | 5.7949 | 831000 | 2000 | 828000 | 1000 | 1652599 | 4934 | 1656000 | 1647665 | 11.0833 | 4.9208 | 1.3479 | 5.7986 | 0.28827 | 27.39% | 4.971% | 27.3954 | 41.1065 | 2.749 | 6.9686 | 1662465.3 | 1622996 | 1847978.4 | 87.83% | 23 | 16294
2025-02-17 | 2025 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 335090.89 | 7:30 | 18:34 | 10914.4 | 11288.6 | 11296.3 | 11288 | 11340.8 | 11355.9 | 11317.7 | 11581.3 | 11282.6 | 11319.5 | 11164.3 | 11300.7 | 11267.7 | 11248.9 | 11263.6 | 11336.1 | 11214.1 | 11294.9 | 11330.2 | 11402.4 | 11311 | 11330 | 11143.4 | 11243 | 11114 | 9844.8 | 11128.2 | 11077.2 | 11331.1 | 11192.4 | 11149 | 11331 | 11517.7 | 11612.6 | 11570 | 11491.8 | 11436 | 11303 | 11320.5 | 11235.9 | 12064.2 | 11124.1 | 11923.9 | 10998.5 | 11482.8 | 12419.6 | 10898.9 | 12035.7 | 11197.5 | 11372.3 | 11339.8 | 10805.5 | 11631.5 | 11210.1 | 11586.1 | 11319.9 | 10508.8 | 11774 | 10511.5 | 11730.7 | 11644.5 | 10528.3 | 11374 | 10942.6 | 11128.1 | 10565.2 | 11125.2 | 11527.7 | 11687.4 | 10824.4 | 11596 | 10420.1 | 11281 | 11196.3 | 10556.7 | 11603.1 | 10432.4 | 11696.8 | 10501 | 11562.3 | 10937 | 11599.3 | 11009.6 | 11907 | 10876.5 | 11439.6 | 10713.6 | 9555 | 11578.2 | 11259.5 | 10599.2 | 11889.5 | 11593.2 | 10860.8 | 10719.6 | 11639.5 | 10616.7 | 11055.6 | 11754.9 | 10630.8 | 11810.8 | 10608.7 | 11599.7 | 10863.4 | 11660.5 | 10288.3 | 11730.4 | 10819.6 | 11604.9 | 10754 | 11639.6 | 10949.9 | 10698.1 | 11585.8 | 10829.5 | 10591.1 | 11613.5 | 11735.4 | 11567.3 | 10745.7 | 11649.9 | 10651.9 | 11386.5 | 10838 | 11306.9 | 9939.6 | 11440.8 | 10622.5 | 10781.6 | 10797.5 | 10582 | 9183.1 | 10645.8 | 9446.8 | 10653.7 | 10670.5 | 12027.9 | 10825.9 | 12086.3 | 11054.1 | 11949.5 | 10856.6 | 11030.4 | 10844.5 | 11834.9 | 12121.9 | 12024.3 | 11951 | 12006.5 | 12020.2 | 11161.4 | 12031.4 | 12114.9 | 12144.4 | 12169.8 | 12133 | 12166.2 | 11205.7 | 12163.9 | 11241.7 | 28.19 | 27.86 | 28.25 | 28.17 | 28.1 | 28.03 | 0 | 40.46 | 0 | 0 | 40.4 | 39.2 | 3.18 | 2.36 | 3.11 | 1.49 | 3.08 | 2.57 | 6.59 | 7.35 | 6.63 | 5.84 | 6.26 | 6.37 | 5.24 | 5.31 | 5.33 | 5.23 | 5.28 | 5.31 | 1.36 | 1.45 | 1.26 | 1.67 | 1.57 | 1.34 | 6.34 | 6.31 | 6.33 | 6.35 | 6.28 | 6.28 | 0.3 | 0.31 | 0.27 | 0.29 | 0.28 | 0.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 860073 | 1618 | 846603 | 1633 | 12012.668 | 31.067 | 5.24 | 5.31 | 5.33 | 5.23 | 5.28 | 5.31 | 6.34 | 6.31 | 6.33 | 6.35 | 6.28 | 6.28 | 898000 | 2000 | 895000 | 2000 | 1786468 | 5000 | 1789000 | 1781468 | 11.0667 | 5.2833 | 1.4417 | 6.315 | 0.295 | 27.29% | 4.671% | 28.1 | 40.02 | 2.6317 | 6.5067 | 1798313.9 | 1767930 | 2022128.7 | 87.43% | 23 | 0
2025-02-18 | 2025 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 335090.89 | 7:31 | 18:36 | 10585.7 | 11042.2 | 11012.8 | 10969.2 | 11062.5 | 11117.6 | 11099 | 11414.6 | 11015.9 | 11065 | 10894.1 | 11051.2 | 10991.7 | 11004.9 | 10992.9 | 11071.5 | 10939 | 11043.4 | 11082.7 | 11139.8 | 11076.2 | 11082.2 | 10871 | 10987.5 | 10864.9 | 9542.9 | 10853.5 | 10809.4 | 11126.8 | 10979.2 | 10906.9 | 11130.2 | 11182.8 | 11279.6 | 11240.7 | 11159.7 | 11256.2 | 11101.4 | 11124.2 | 11031.2 | 11957.4 | 10792.8 | 11810.8 | 10638.5 | 11260.8 | 12414.5 | 10581.2 | 11938.5 | 10938.3 | 11138.6 | 11084 | 10472.9 | 11444.5 | 10926 | 11417.3 | 11112.4 | 10181.1 | 11656.1 | 10163.9 | 11580.1 | 11470 | 10175.8 | 11190.5 | 10661.7 | 10852.1 | 10239.7 | 10851.1 | 11339.1 | 11551.1 | 10502.8 | 11438.7 | 10104.7 | 11046.7 | 10936.8 | 10217.5 | 11441.3 | 10098.7 | 11546.1 | 10161.5 | 11378.3 | 10606.6 | 11411.1 | 10699.6 | 11785.6 | 10554.4 | 11217.4 | 10391 | 9255.5 | 11388.9 | 11012.2 | 10269 | 11774.9 | 11433.8 | 10562.9 | 10422.9 | 11473.5 | 10341.5 | 10771.5 | 11628.4 | 10328.3 | 11676.3 | 10307.2 | 11404.1 | 10553.3 | 11512.3 | 9993.2 | 11585.2 | 10523.5 | 11426.6 | 10462.2 | 11484.5 | 10676.5 | 10390.9 | 11433.8 | 10527.5 | 10301.9 | 11486.1 | 11625.6 | 11414.3 | 10478.9 | 11549.2 | 10393.1 | 11199.9 | 10562.1 | 11149.9 | 9718.1 | 11291.8 | 10384.4 | 10518.6 | 10531.3 | 10338.5 | 8959.7 | 10388.7 | 9218.3 | 10375.4 | 10412.3 | 11996.3 | 10564.3 | 12053.4 | 10812.2 | 11917.2 | 10601.7 | 10799.4 | 10613.1 | 11703.8 | 12067.4 | 11951.2 | 11870.4 | 11949.2 | 11977.8 | 10914.1 | 11963.5 | 12042.3 | 12080.7 | 12097.7 | 12061.2 | 12095.4 | 10943.4 | 12104.5 | 10985.2 | 27.51 | 27.09 | 27.39 | 27.56 | 27.35 | 27.19 | 0 | 40.88 | 0 | 0 | 41.2 | 40 | 2.8 | 1.95 | 2.77 | 0.24 | 2.57 | 2.02 | 5.71 | 4.9 | 5.39 | 4.44 | 5.43 | 5.25 | 5.12 | 5.19 | 5.2 | 5.13 | 5.2 | 5.23 | 1.31 | 1.46 | 1.22 | 1.62 | 1.56 | 1.35 | 6.14 | 6.14 | 6.13 | 6.16 | 6.12 | 6.17 | 0.29 | 0.31 | 0.26 | 0.28 | 0.27 | 0.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 860952 | 1620 | 847482 | 1635 | 13764.401 | 35.933 | 5.12 | 5.19 | 5.2 | 5.13 | 5.2 | 5.23 | 6.14 | 6.14 | 6.13 | 6.16 | 6.12 | 6.17 | 879000 | 2000 | 879000 | 2000 | 1751733 | 4866 | 1754000 | 1746867 | 11.0833 | 5.1783 | 1.42 | 6.1433 | 0.28667 | 27.42% | 4.666% | 27.3483 | 40.6933 | 2.0583 | 5.1867 | 1762665.7 | 1738800 | 1977498.1457 | 87.93% | 21 | 0
2025-02-19 | 2025 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 335090.89 | 7:26 | 18:38 | 7430.9 | 7761.8 | 7770.7 | 7738.4 | 7807.3 | 7829.9 | 7826.5 | 8023.6 | 7721.2 | 7771.1 | 7630.5 | 7733.6 | 7706.1 | 7697.9 | 7728.8 | 7777 | 7666.3 | 7723.7 | 7745.4 | 7782.7 | 7742 | 7745.6 | 7600.1 | 7674.2 | 7569.2 | 6655 | 7568.7 | 7529.1 | 7769.9 | 7667.3 | 7617.3 | 7752.3 | 7750.6 | 7821 | 7840.5 | 7774.6 | 7840.3 | 7735.8 | 7744.6 | 7691.7 | 8400.4 | 7581.5 | 8285.3 | 7468 | 7882.7 | 8723 | 7379.1 | 8382.7 | 7684.9 | 7828.4 | 7761.1 | 7339.3 | 8025.1 | 7668.1 | 7989 | 7809.7 | 7109.3 | 8132.7 | 7133.2 | 8105.1 | 8027.7 | 7137.1 | 7777.5 | 7403 | 7492.7 | 7073.4 | 7496.8 | 7824 | 8022.1 | 7238.1 | 7895.8 | 6953.5 | 7681 | 7522.4 | 7090.5 | 7873.1 | 6957.3 | 8026.6 | 7053.4 | 7864.6 | 7323.9 | 7871 | 7419.8 | 8153.3 | 7310.4 | 7792.5 | 7212.6 | 6416.4 | 7894.3 | 7644.2 | 7104.5 | 8167.7 | 7949.2 | 7335.8 | 7241.8 | 7990 | 7226 | 7514.5 | 8146.2 | 7209.5 | 8183.3 | 7211 | 7999.5 | 7395.3 | 8094 | 7017.6 | 8150.3 | 7384.3 | 8029.4 | 7340.6 | 8101.1 | 7497.2 | 7251.5 | 8001.8 | 7351.8 | 7208.9 | 8073.6 | 8161.5 | 8002.5 | 7395.4 | 8118 | 7313.3 | 7864.3 | 7384.2 | 7800.4 | 6829 | 7948.7 | 7334.7 | 7412.5 | 7411.5 | 7343.3 | 6325.9 | 7310.8 | 6484.5 | 7453.2 | 7481.4 | 8573.7 | 7532.5 | 8644.5 | 7723.6 | 8561.4 | 7623 | 7752.3 | 7630.9 | 8331.6 | 8621.4 | 8517.4 | 8474.1 | 8509.5 | 8547.2 | 7780.2 | 8546.9 | 8536.8 | 8572.4 | 8601.4 | 8576.8 | 8609.4 | 7775.3 | 8584.9 | 7793.7 | 27.5716 | 27.4354 | 27.7909 | 27.6336 | 27.5043 | 27.6472 | 0 | 35.9289 | 0 | 0 | 36.4282 | 36.3 | 4.5531 | 4.1982 | 4.2026 | 3.0351 | 4.3598 | 4.0503 | 10.2333 | 10.59 | 11.355 | 9.6717 | 11.1817 | 9.9033 | 3.7029 | 3.7272 | 3.7552 | 3.6534 | 3.7408 | 3.8484 | 0.94314 | 1.0345 | 0.8706 | 1.1337 | 1.1142 | 0.98699 | 4.2078 | 4.1861 | 4.1756 | 4.144 | 4.185 | 4.3035 | 0.23442 | 0.25208 | 0.21556 | 0.23446 | 0.22636 | 0.25572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 861566 | 1621 | 848103 | 1636 | 14995.068 | 40.733 | 3.7029 | 3.7272 | 3.7552 | 3.6534 | 3.7408 | 3.8484 | 4.2078 | 4.1861 | 4.1756 | 4.144 | 4.185 | 4.3035 | 614000 | 1000 | 621000 | 1000 | 1230667 | 4800 | 1233000 | 1225867 | 11.2 | 3.738 | 1.0139 | 4.2003 | 0.23643 | 27.12% | 5.629% | 27.5972 | 36.219 | 4.0665 | 10.4892 | 1236073.2 | 1206934 | 1367278.5214 | 88.27% | 23 | 101096
2025-02-20 | 2025 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 335090.89 | 7:28 | 18:41 | 10894.9 | 11332.7 | 11294.6 | 11271.4 | 11334.3 | 11376.9 | 11359.7 | 11707.9 | 11316.1 | 11374.1 | 11180.4 | 11325 | 11266.5 | 11259.5 | 11257 | 11337 | 11194.9 | 11276.3 | 11311.8 | 11373.4 | 11292.5 | 11304.3 | 11103.9 | 11209.9 | 11069.3 | 9749.9 | 11091.1 | 11036.2 | 11326.4 | 11195.5 | 11098.9 | 11299.4 | 11363.7 | 11469.2 | 11464.3 | 11370.1 | 11400.6 | 11261.1 | 11276.1 | 11191.2 | 12048.7 | 11038 | 11912.1 | 10884.1 | 11454.2 | 12448.3 | 10795.5 | 12025.4 | 11223.3 | 11413.1 | 11352.9 | 10737 | 11667.9 | 11200.9 | 11620.9 | 11352.8 | 10426.1 | 11816.7 | 10447.8 | 11778.3 | 11685.8 | 10447.6 | 11423.4 | 10920.4 | 11095.3 | 10461.2 | 11079 | 11513.2 | 11720.9 | 10727.6 | 11615.6 | 10322.3 | 11284 | 11165.2 | 10467.2 | 11619.3 | 10334.1 | 11740.6 | 10447.8 | 11607.9 | 10823.1 | 11578.1 | 10923.7 | 11896.6 | 10777.8 | 11415.4 | 10673.3 | 9443.5 | 11496.9 | 11203.3 | 10427.6 | 11828.8 | 11527.8 | 10689.1 | 10543.8 | 11592.8 | 10487.1 | 10923.6 | 11695.9 | 10468.2 | 11745.7 | 10441.5 | 11518.2 | 10703.9 | 11599.4 | 10133.1 | 11671.2 | 10662.6 | 11544.2 | 10613.6 | 11612.6 | 10814.1 | 10518.6 | 11535.3 | 10668.8 | 10447 | 11577.4 | 11694.2 | 11518.1 | 10604.5 | 11617.9 | 10519.1 | 11350.4 | 10692.7 | 11262.7 | 9816.3 | 11411.2 | 10513.5 | 10645.9 | 10665.6 | 10554.7 | 9095.2 | 10473.8 | 9130.6 | 10483.4 | 10530.8 | 12053 | 10742.4 | 12103.4 | 10996.7 | 11999.6 | 10831.1 | 11022.8 | 10772.6 | 11810.4 | 12121.9 | 12025.8 | 11954.2 | 12008.9 | 12032.7 | 11093.4 | 12027.3 | 12109.7 | 12136.2 | 12153.5 | 12127.6 | 12153.5 | 11134.6 | 12170.2 | 11165.5 | 25.56 | 25.33 | 25.6 | 25.81 | 25.68 | 25.47 | 0 | 38.61 | 0 | 0 | 38.4 | 37.5 | 3.16 | 1.79 | 3.1 | 0.64 | 3.01 | 2.72 | 6.81 | 6.89 | 7.1 | 4.68 | 6.76 | 6.66 | 5.33 | 5.37 | 5.37 | 5.33 | 5.39 | 5.4 | 1.39 | 1.5 | 1.28 | 1.69 | 1.6 | 1.4 | 6.32 | 6.27 | 6.26 | 6.31 | 6.25 | 6.29 | 0.33 | 0.36 | 0.3 | 0.32 | 0.32 | 0.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 862462 | 1623 | 848992 | 1638 | 16774.068 | 45.467 | 5.33 | 5.37 | 5.37 | 5.33 | 5.39 | 5.4 | 6.32 | 6.27 | 6.26 | 6.31 | 6.25 | 6.29 | 896000 | 2000 | 889000 | 2000 | 1779000 | 4734 | 1781000 | 1774266 | 11.2167 | 5.365 | 1.4767 | 6.2833 | 0.33167 | 27.52% | 5.279% | 25.575 | 38.17 | 2.4033 | 6.4833 | 1790491.6 | 1761933 | 2027795.8494 | 86.89% | 22 | 0
2025-02-21 | 2025 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 335090.89 | 7:24 | 18:42 | 10685.5 | 11038.8 | 11071.1 | 11055.2 | 11118.4 | 11111.3 | 11040.7 | 11408.4 | 11084.1 | 11061.7 | 10928.3 | 11056.3 | 11030.7 | 10981.3 | 11026.7 | 11109.4 | 10971.9 | 11055.5 | 11075.6 | 11144 | 11064.3 | 11083.4 | 10895.8 | 10988 | 10845.8 | 9585.8 | 10868.3 | 10810 | 11082.6 | 10958.7 | 10861.2 | 11042.9 | 11047.2 | 11193.7 | 11228.1 | 11115.9 | 11097 | 10967.4 | 10963.5 | 10871.9 | 11759.6 | 10821.2 | 11636.3 | 10679.7 | 11163.4 | 12100.2 | 10569 | 11755.1 | 10955.7 | 11133.8 | 11087 | 10516.3 | 11373.2 | 10925.2 | 11333.1 | 11067.2 | 10223.7 | 11501.8 | 10249.4 | 11485.4 | 11391.2 | 10248.3 | 11111 | 10674 | 10793.1 | 10175.1 | 10780.6 | 11149.9 | 11366.2 | 10450.6 | 11252.1 | 10059.6 | 10969.6 | 10850.7 | 10216.6 | 11256.8 | 10083.4 | 11405 | 10198.4 | 11276.9 | 10529.1 | 11214.1 | 10591.2 | 11496.7 | 10460.3 | 11028.6 | 10340.2 | 9165.7 | 11037.5 | 10843.5 | 10119 | 11401.4 | 11168.1 | 10422.9 | 10272.9 | 11142.4 | 10075.3 | 10572.2 | 11256.7 | 10166.9 | 11317.5 | 10127.7 | 11121.5 | 10365.8 | 11181.8 | 9824.3 | 11269.6 | 10375.5 | 11141.9 | 10246 | 11185.8 | 10519.2 | 10233.8 | 11145 | 10369.9 | 10145.5 | 11193.6 | 11316.1 | 11144.2 | 10352.5 | 11261.8 | 10259.4 | 10984.3 | 10409.2 | 10894.2 | 9581.2 | 11084.3 | 10266.8 | 10397 | 10419.7 | 10222.5 | 8878 | 10106.2 | 8951 | 10177.9 | 10250.6 | 11665.1 | 10460.6 | 11713.9 | 10700.1 | 11587.2 | 10500.3 | 10677.4 | 10439.6 | 11447.3 | 11731.9 | 11652.7 | 11582.9 | 11635.5 | 11648.7 | 10792.2 | 11645.6 | 11740.3 | 11763.6 | 11777.7 | 11744.5 | 11771 | 10827.5 | 11786.8 | 10866.2 | 24.8 | 24.24 | 24.26 | 24.47 | 24.17 | 24.1 | 0 | 37.71 | 0 | 0 | 37.5 | 36.5 | 3.09 | 1.73 | 2.9 | 0.65 | 2.26 | 2.21 | 6.68 | 6.39 | 6.13 | 6.29 | 6.2 | 6.24 | 5.21 | 5.24 | 5.29 | 5.16 | 5.18 | 5.21 | 1.35 | 1.44 | 1.25 | 1.63 | 1.51 | 1.31 | 6.19 | 6.11 | 6.16 | 6.11 | 6.01 | 6.03 | 0.32 | 0.33 | 0.29 | 0.3 | 0.29 | 0.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 863338 | 1625 | 849854 | 1639 | 18505.268 | 50.133 | 5.21 | 5.24 | 5.29 | 5.16 | 5.18 | 5.21 | 6.19 | 6.11 | 6.16 | 6.11 | 6.01 | 6.03 | 876000 | 2000 | 862000 | 1000 | 1731200 | 4666 | 1735000 | 1726534 | 11.3 | 5.215 | 1.415 | 6.1017 | 0.31167 | 27.13% | 5.108% | 24.34 | 37.2367 | 2.14 | 6.3217 | 1741856.4 | 1703866 | 1979009.1617 | 86.1% | 24 | 3351
2025-02-22 | 2025 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 335090.89 | 7:25 | 18:42 | 11267 | 11620 | 11655 | 11634 | 11716 | 11749 | 11643 | 11971 | 11649 | 11619 | 11522 | 11647 | 11631 | 11594 | 11650 | 11705 | 11585 | 11666 | 11708 | 11782 | 11686 | 11711 | 11528 | 11619 | 11490 | 10174 | 11510 | 11460 | 11715 | 11587 | 11514 | 11690 | 11806 | 11960 | 11956 | 11851 | 11772 | 11646 | 11645 | 11574 | 12418 | 11457 | 12281 | 11317 | 11822 | 12777 | 11226 | 12390 | 11564 | 11749 | 11707 | 11136 | 11998 | 11495 | 11966 | 11688 | 10858 | 12161 | 10867 | 12118 | 12028 | 10867 | 11768 | 11327 | 11487 | 10881 | 11467 | 11871 | 12047 | 11152 | 11963 | 10739 | 11630 | 11550 | 10880 | 11954 | 10758 | 12062 | 10857 | 11941 | 11261 | 11948 | 11347 | 12251 | 11224 | 11797 | 11065 | 9836 | 11796 | 11592 | 10892 | 12179 | 11924 | 11166 | 11014 | 11919 | 10804 | 11341 | 12035 | 10943 | 12107 | 10915 | 11920 | 11174 | 11980 | 10588 | 12069 | 11148 | 11939 | 11076 | 11978 | 11273 | 11003 | 11892 | 11129 | 10895 | 11934 | 12070 | 11888 | 11081 | 11999 | 10999 | 11721 | 11162 | 11623 | 10261 | 11815 | 10997 | 11135 | 11136 | 10916 | 9503 | 10755 | 9545 | 10873 | 10943 | 12394 | 11171 | 12437 | 11398 | 12299 | 11170 | 11358 | 11087 | 12159 | 12453 | 12366 | 12299 | 12359 | 12377 | 11490 | 12372 | 12434 | 12457 | 12470 | 12443 | 12478 | 11526 | 12500 | 11546 | 24.84 | 24.32 | 24.57 | 24.75 | 24.45 | 24.27 | 0 | 39.4 | 0 | 0 | 39.1 | 38.2 | 2.95 | 1.7 | 2.91 | 0.51 | 2.65 | 2.27 | 5.97 | 5.89 | 5.97 | 5.15 | 6.4 | 6.15 | 5.52 | 5.58 | 5.6 | 5.5 | 5.56 | 5.58 | 1.41 | 1.54 | 1.31 | 1.72 | 1.63 | 1.43 | 6.57 | 6.57 | 6.55 | 6.56 | 6.49 | 6.54 | 0.31 | 0.33 | 0.28 | 0.3 | 0.29 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 864265 | 1627 | 850774 | 1641 | 20345.3 | 54.9 | 5.52 | 5.58 | 5.6 | 5.5 | 5.56 | 5.58 | 6.57 | 6.57 | 6.55 | 6.56 | 6.49 | 6.54 | 927000 | 2000 | 920000 | 2000 | 1840032 | 4767 | 1843000 | 1835265 | 11.2833 | 5.5567 | 1.5067 | 6.5467 | 0.30667 | 27.11% | 4.684% | 24.5333 | 38.9 | 2.165 | 5.9217 | 1851950 | 1823533 | 2119110 | 86.05% | 22 | 0
2025-02-23 | 2025 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 335090.89 | 7:23 | 18:43 | 11387.2 | 11745.7 | 11774.7 | 11764.1 | 11822.4 | 11880.2 | 11840 | 12105.5 | 11764.4 | 11709.8 | 11664.5 | 11771.2 | 11792.2 | 11745.3 | 11781.7 | 11848.3 | 11718.1 | 11801.2 | 11835.2 | 11912.4 | 11805 | 11833.9 | 11647.1 | 11742.5 | 11605.2 | 10358.9 | 11635.3 | 11584.8 | 11829.1 | 11679.5 | 11627.5 | 11816.9 | 12052.4 | 12187.1 | 12182.7 | 12105.5 | 11912.7 | 11781.8 | 11791.7 | 11677.7 | 12537.2 | 11586.4 | 12394.4 | 11449 | 11963.4 | 12916.6 | 11382.7 | 12504.6 | 11690.1 | 11875.3 | 11840.9 | 11268.8 | 12129.6 | 11667.7 | 12097.6 | 11801.5 | 11016.8 | 12274.7 | 11035.9 | 12245.8 | 12152.6 | 11028.9 | 11885.9 | 11449.9 | 11596.1 | 11029.5 | 11579.7 | 11971.7 | 12156.9 | 11272.4 | 12073.1 | 10890 | 11739 | 11654.7 | 11031.8 | 12056.7 | 10917 | 12172.3 | 11014.7 | 12054.8 | 11378 | 12053.5 | 11455 | 12360.5 | 11334.3 | 11900.1 | 11162.8 | 10021.5 | 11971.8 | 11685.5 | 11054.3 | 12314.7 | 12023.1 | 11272.8 | 11118.7 | 12036.1 | 10954.4 | 11461.9 | 12158.7 | 11082.2 | 12245.5 | 11069.4 | 12052.2 | 11312.1 | 12108.1 | 10762.3 | 12184.6 | 11279.4 | 12062.5 | 11234.1 | 12117.4 | 11424.6 | 11128.3 | 12000.4 | 11252.1 | 11031.6 | 12041.9 | 12205.5 | 12006.1 | 11227.1 | 12129.7 | 11154.7 | 11848.9 | 11317.5 | 11741.5 | 10468.4 | 11949 | 11166.5 | 11269 | 11265.5 | 11071.6 | 9682.8 | 10960.1 | 9715.9 | 11059.1 | 11107.6 | 12508.4 | 11292 | 12550.3 | 11518.9 | 12403.3 | 11274.2 | 11450.4 | 11255.3 | 12285.2 | 12575 | 12490.2 | 12413.3 | 12476.2 | 12491.7 | 11612.3 | 12486.3 | 12549.2 | 12576.8 | 12597.4 | 12566.7 | 12603.5 | 11650.6 | 12622.3 | 11681.4 | 27.3364 | 26.8995 | 27.0612 | 27.2501 | 26.883 | 26.745 | 0 | 42.0112 | 0 | 0 | 41.8 | 40.7 | 3.088 | 1.1715 | 2.8541 | 0.57961 | 2.6464 | 1.9863 | 6.2117 | 6.335 | 7.4317 | 5.5533 | 5.7183 | 6.5633 | 5.6856 | 5.7485 | 5.7746 | 5.6599 | 5.7534 | 5.7426 | 1.4626 | 1.5829 | 1.3561 | 1.7823 | 1.6731 | 1.4629 | 6.8013 | 6.7597 | 6.7631 | 6.7823 | 6.6888 | 6.7183 | 0.31505 | 0.32926 | 0.28395 | 0.2962 | 0.29303 | 0.33498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 865202 | 1629 | 851705 | 1643 | 22206.202 | 59.733 | 5.6856 | 5.7485 | 5.7746 | 5.6599 | 5.7534 | 5.7426 | 6.8013 | 6.7597 | 6.7631 | 6.7823 | 6.6888 | 6.7183 | 937000 | 2000 | 931000 | 2000 | 1860902 | 4833 | 1864000 | 1856069 | 11.3333 | 5.7274 | 1.5533 | 6.7522 | 0.30874 | 27.12% | 4.572% | 27.0292 | 41.5037 | 2.0543 | 6.3022 | 1873311.9 | 1855840.276 | 2169548.7056 | 85.54% | 21 | 0
2025-02-24 | 2025 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 335090.89 | 7:22 | 18:39 | 9523.3 | 9855.6 | 9918.8 | 9919.1 | 9952.1 | 9995.3 | 9953.8 | 10284.4 | 9899.8 | 9904.2 | 9798.1 | 9912.9 | 9884.5 | 9865.6 | 9880.3 | 9952.5 | 9824.5 | 9899.8 | 9922 | 9986.3 | 9899.4 | 9912.9 | 9729.3 | 9826.4 | 9680.5 | 8549.4 | 9722.9 | 9664.8 | 9907.5 | 9765.9 | 9710.7 | 9887.9 | 9955.2 | 10024.1 | 10039.9 | 9963 | 9983.6 | 9843.1 | 9870.2 | 9754.8 | 10629.6 | 9651.9 | 10488.1 | 9517.8 | 10027.4 | 11019.8 | 9464.5 | 10618.1 | 9795.7 | 9962.2 | 9920.2 | 9357.8 | 10213.4 | 9806 | 10173 | 9898.7 | 9128.9 | 10353.1 | 9167.5 | 10324.1 | 10239.2 | 9165 | 9952.5 | 9510.4 | 9668.4 | 9144.6 | 9650.3 | 10040.8 | 10251.4 | 9347 | 10131.4 | 8995.6 | 9834.9 | 9704.8 | 9142.1 | 10134.4 | 9029.5 | 10258.4 | 9120.5 | 10127.1 | 9438.7 | 10104.5 | 9517.8 | 10424.6 | 9400 | 9955.7 | 9244.1 | 8246.8 | 10066.4 | 9776.7 | 9118.7 | 10359.5 | 10045.5 | 9304.1 | 9176.6 | 10118.7 | 9039.4 | 9517.2 | 10230 | 9139.7 | 10308.2 | 9125.2 | 10071.1 | 9331.8 | 10155.9 | 8862.6 | 10210.9 | 9314 | 10087.9 | 9280.9 | 10132.2 | 9447.5 | 9194.6 | 10046.5 | 9294.3 | 9116.1 | 10097.1 | 10222.2 | 10049.3 | 9269.6 | 10162.9 | 9196.8 | 9884.7 | 9342.9 | 9760.2 | 8603.3 | 9960.2 | 9199.7 | 9286.6 | 9283.2 | 9102.1 | 7917.7 | 9034.5 | 7918.9 | 9139.5 | 9170.7 | 10548.8 | 9306.6 | 10592.7 | 9523.2 | 10445.2 | 9330.5 | 9491.2 | 9336.1 | 10284.6 | 10597.2 | 10496.8 | 10443.1 | 10495.5 | 10523 | 9610 | 10507.4 | 10576.6 | 10609.8 | 10636.2 | 10596.2 | 10628 | 9642.7 | 10643.6 | 9690.5 | 27.94 | 27.88 | 28.49 | 28.07 | 27.82 | 28.08 | 0 | 40.43 | 0 | 0 | 40.6 | 40.1 | 2.74 | 0.63 | 2.47 | 0.27 | 2.03 | 1.94 | 6.13 | 5.83 | 5.89 | 5.75 | 5.87 | 5.83 | 4.7 | 4.75 | 4.75 | 4.66 | 4.71 | 4.72 | 1.25 | 1.26 | 1.15 | 1.5 | 1.36 | 1.15 | 5.56 | 5.51 | 5.51 | 5.52 | 5.45 | 5.42 | 0.26 | 0.27 | 0.24 | 0.25 | 0.24 | 0.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 865987 | 1631 | 852481 | 1645 | 23762.269 | 64.533 | 4.7 | 4.75 | 4.75 | 4.66 | 4.71 | 4.72 | 5.56 | 5.51 | 5.51 | 5.52 | 5.45 | 5.42 | 785000 | 2000 | 776000 | 2000 | 1556067 | 4800 | 1557000 | 1551267 | 11.2833 | 4.715 | 1.2783 | 5.495 | 0.25667 | 27.11% | 4.671% | 28.0467 | 40.3767 | 1.68 | 5.8833 | 1564152.5 | 1539400 | 1771963.2 | 86.88% | 26 | 19006
2025-02-25 | 2025 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 335090.89 | 7:18 | 18:23 | 6815.6 | 7109.6 | 7152.4 | 7129.8 | 7190.9 | 7190.9 | 7169.3 | 7483 | 7180.2 | 7181.3 | 7065.2 | 7182.7 | 7124.8 | 7119.6 | 7128.3 | 7186.7 | 7064.2 | 7123.1 | 7148.3 | 7182.1 | 7148.6 | 7141.8 | 7003.7 | 7075.7 | 6961.9 | 6096.9 | 6985.7 | 6941.2 | 7163 | 7047.5 | 7003.7 | 7159.5 | 7104.6 | 7146.2 | 7192.3 | 7118.5 | 7208.9 | 7088.8 | 7109.8 | 7056.1 | 7697.9 | 6897.3 | 7653 | 6789.5 | 7226.1 | 8119 | 6738.3 | 7768.6 | 7099.2 | 7225 | 7159.1 | 6695.3 | 7423.9 | 7078.5 | 7413.8 | 7222.1 | 6531.4 | 7558.8 | 6557.3 | 7529.5 | 7445.7 | 6554.4 | 7162.7 | 6774.9 | 6965.7 | 6559.7 | 6949.1 | 7305.5 | 7503.4 | 6712.9 | 7380.7 | 6444.7 | 7144.5 | 7004 | 6566.5 | 7387.6 | 6466.3 | 7514.1 | 6552.8 | 7376.3 | 6782 | 7352.4 | 6854.9 | 7643.3 | 6764.1 | 7241.7 | 6667.7 | 5929.8 | 7312.3 | 7114.5 | 6521.5 | 7578.2 | 7306 | 6664.6 | 6583.8 | 7385.4 | 6553.9 | 6861.1 | 7526 | 6567.5 | 7553.3 | 6550.6 | 7336.8 | 6711.4 | 7422.9 | 6357.5 | 7459.4 | 6684.8 | 7332 | 6648.9 | 7368 | 6774.1 | 6614.9 | 7334 | 6689.2 | 6549.8 | 7414.2 | 7470 | 7333.8 | 6684.3 | 7416.3 | 6590.6 | 7186.6 | 6681.9 | 7076.2 | 6168.4 | 7227.4 | 6609.9 | 6662.5 | 6660.3 | 6527.8 | 5671.5 | 6531 | 5717.8 | 6596.3 | 6617.6 | 7790.8 | 6697 | 7833.9 | 6868.9 | 7710.7 | 6748.4 | 6874.8 | 6740.5 | 7519.2 | 7825.2 | 7724.4 | 7690.6 | 7712.1 | 7744.9 | 6950.7 | 7746.3 | 7812.7 | 7824.6 | 7863.7 | 7826.8 | 7834.9 | 6957 | 7847.7 | 6990 | 27.588 | 27.4672 | 27.9397 | 27.4798 | 27.4392 | 27.6858 | 0 | 34.8143 | 0 | 0 | 34.8243 | 34.9 | 3.8015 | 1.9584 | 3.57 | 1.1925 | 3.6734 | 3.4787 | 8.1 | 7.345 | 7.6917 | 6.5817 | 7.2817 | 7.2817 | 3.5256 | 3.5558 | 3.5525 | 3.5039 | 3.5322 | 3.5546 | 0.96012 | 0.95375 | 0.87089 | 1.1319 | 1.0183 | 0.88132 | 3.7234 | 3.7206 | 3.6861 | 3.7104 | 3.6942 | 3.6727 | 0.27005 | 0.29377 | 0.24924 | 0.28023 | 0.26598 | 0.28715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 866555 | 1632 | 853045 | 1646 | 24891.535 | 67.467 | 3.5256 | 3.5558 | 3.5525 | 3.5039 | 3.5322 | 3.5546 | 3.7234 | 3.7206 | 3.6861 | 3.7104 | 3.6942 | 3.6727 | 568000 | 1000 | 564000 | 1000 | 1129266 | 2934 | 1130000 | 1126332 | 11.0833 | 3.5374 | 0.96939 | 3.7013 | 0.2744 | 27.4% | 7.414% | 27.6 | 34.8462 | 2.9457 | 7.3803 | 1132416 | 1101400 | 1209826.4927 | 91.04% | 21 | 30649
2025-02-26 | 2025 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 335090.89 | 7:21 | 18:42 | 9271.6 | 9662.2 | 9660.5 | 9643.2 | 9718.5 | 9739.5 | 9703 | 10045.5 | 9697.2 | 9645.8 | 9581.2 | 9717.2 | 9671.9 | 9654.2 | 9668.5 | 9745.2 | 9624.6 | 9719.3 | 9742.6 | 9784.6 | 9746.5 | 9741.6 | 9583.2 | 9669.8 | 9495.6 | 8337.3 | 9512.3 | 9481.7 | 9750 | 9619.6 | 9574.7 | 9752.2 | 9747.6 | 9806.5 | 9817.8 | 9750.2 | 9828.9 | 9696.4 | 9723 | 9631.6 | 10548.7 | 9576 | 10439.8 | 9450 | 9937.6 | 10906.6 | 9348.5 | 10539.9 | 9576.7 | 9739 | 9697.3 | 9134.6 | 10019.1 | 9587.3 | 9961.7 | 9719.6 | 8882.9 | 10117.1 | 8905.4 | 10083.5 | 9977.4 | 8889.6 | 9672.3 | 9210 | 9412.7 | 8869.5 | 9382.4 | 9774.1 | 10006.2 | 9058.8 | 9860.3 | 8690.3 | 9574.9 | 9413.3 | 8864.1 | 9847.1 | 8735.5 | 9992 | 8832.6 | 9827 | 9146 | 9807.8 | 9219.7 | 10153.8 | 9115.4 | 9689.2 | 9044.8 | 8009 | 9798.6 | 9531.9 | 8856.6 | 10157.9 | 9876.3 | 9133.3 | 9038.2 | 9937.7 | 8933.8 | 9314 | 10104.6 | 8944.3 | 10172.2 | 8935 | 9943.1 | 9155.1 | 10049.4 | 8694.6 | 10107.5 | 9166.6 | 9986.1 | 9141.1 | 10052.6 | 9326.7 | 9002.4 | 9914.2 | 9143.3 | 8958.1 | 10020.9 | 10111.2 | 9956.8 | 9135.8 | 10073.7 | 9065.7 | 9797 | 9206.2 | 9730.2 | 8506.5 | 9880.3 | 9093.6 | 9142.8 | 9132.4 | 9051.2 | 7799.1 | 9028.3 | 7963.5 | 9044.7 | 9052.5 | 10391.9 | 9144.4 | 10446.5 | 9362.4 | 10348.6 | 9210.3 | 9380.3 | 9205.3 | 10074.2 | 10405.5 | 10301.2 | 10251.4 | 10306.9 | 10345.1 | 9426.5 | 10331.1 | 10342.7 | 10374 | 10402.5 | 10374.5 | 10410.8 | 9406.8 | 10410.6 | 9419 | 29.6 | 29.41 | 30.07 | 29.54 | 29.35 | 29.58 | 0 | 41.14 | 0 | 0 | 41.2 | 40.8 | 3.64 | 1.67 | 3.35 | 0.97 | 3.5 | 3.55 | 8.19 | 8.03 | 7.73 | 6.33 | 7.47 | 8.6 | 4.72 | 4.8 | 4.83 | 4.65 | 4.76 | 4.74 | 1.29 | 1.29 | 1.19 | 1.52 | 1.39 | 1.15 | 5.38 | 5.38 | 5.41 | 5.32 | 5.33 | 5.25 | 0.31 | 0.33 | 0.28 | 0.3 | 0.29 | 0.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 867323 | 1633 | 853808 | 1647 | 26418.269 | 70.867 | 4.72 | 4.8 | 4.83 | 4.65 | 4.76 | 4.74 | 5.38 | 5.38 | 5.41 | 5.32 | 5.33 | 5.25 | 768000 | 1000 | 763000 | 1000 | 1526734 | 3400 | 1529000 | 1523334 | 11.35 | 4.75 | 1.305 | 5.345 | 0.305 | 27.47% | 5.706% | 29.5917 | 41.0467 | 2.78 | 7.725 | 1534450 | 1508066 | 1722489.3808 | 87.55% | 20 | 31795
2025-02-27 | 2025 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 335090.89 | 7:28 | 18:36 | 5979.6 | 6247.3 | 6281.6 | 6256.3 | 6319.9 | 6317 | 6316.1 | 6554 | 6294.7 | 6281.4 | 6199 | 6305.3 | 6254.3 | 6251.3 | 6293.5 | 6323.3 | 6221 | 6259.6 | 6278.4 | 6304.1 | 6295.1 | 6281.8 | 6146.3 | 6216.5 | 6097.4 | 5336.4 | 6122.2 | 6081.2 | 6290.5 | 6200.2 | 6147.6 | 6278 | 6215.8 | 6264.7 | 6311.3 | 6240.1 | 6311.7 | 6210.6 | 6221.8 | 6177.9 | 6814.6 | 6067 | 6728.4 | 5963 | 6352.9 | 7148.2 | 5909.3 | 6835 | 6230.2 | 6337.7 | 6283.1 | 5911.9 | 6528.7 | 6206.8 | 6499.4 | 6338.3 | 5731.9 | 6629.1 | 5745.8 | 6596.5 | 6523.8 | 5745.9 | 6271 | 5930.5 | 6092.6 | 5730.3 | 6077.7 | 6391.8 | 6569.1 | 5870.8 | 6458.7 | 5634.8 | 6260.7 | 6127.4 | 5748.2 | 6467.6 | 5657.6 | 6581.7 | 5745.6 | 6473.6 | 5926.9 | 6428.1 | 5994.1 | 6678.4 | 5920.1 | 6335.9 | 5884.8 | 5190.2 | 6380.2 | 6214.5 | 5711.3 | 6644 | 6428.7 | 5887.9 | 5818.2 | 6462.8 | 5745.2 | 6009.6 | 6595.5 | 5754.2 | 6608.1 | 5737.7 | 6430 | 5874.6 | 6506.6 | 5569.3 | 6538.1 | 5855 | 6415.2 | 5810.8 | 6442.2 | 5931.4 | 5791.3 | 6406.9 | 5854.3 | 5724.8 | 6487.1 | 6534.8 | 6416.5 | 5853.9 | 6490.9 | 5772.8 | 6288.1 | 5845.1 | 6192.1 | 5393.1 | 6325.2 | 5784.5 | 5826.2 | 5824.4 | 5784.1 | 4969.3 | 5711.4 | 5050.6 | 5763.7 | 5781.6 | 6808.1 | 5850.5 | 6835.2 | 5989.8 | 6725.7 | 5876.4 | 5983.9 | 5889.2 | 6553.1 | 6822.4 | 6745.5 | 6709.5 | 6730.1 | 6759.2 | 6065.5 | 6755.1 | 6823.7 | 6825 | 6855.8 | 6816.9 | 6832.4 | 6062.1 | 6853.6 | 6084.6 | 27.3647 | 27.1783 | 27.5064 | 27.3172 | 27.1696 | 27.3766 | 0 | 34.1909 | 0 | 0 | 34.2021 | 34.4484 | 3.3802 | 2.2144 | 3.1361 | 1.2883 | 2.8346 | 2.6987 | 8.2 | 8.2783 | 8.455 | 7.2417 | 8.5483 | 8.345 | 3.1121 | 3.1356 | 3.1417 | 3.0893 | 3.1119 | 3.1256 | 0.83371 | 0.84507 | 0.7546 | 0.98138 | 0.89492 | 0.7758 | 3.2065 | 3.2107 | 3.1816 | 3.1848 | 3.1783 | 3.1543 | 0.24249 | 0.26461 | 0.22422 | 0.25233 | 0.23789 | 0.25564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 867821 | 1634 | 854302 | 1648 | 27407.135 | 75.933 | 3.1121 | 3.1356 | 3.1417 | 3.0893 | 3.1119 | 3.1256 | 3.2065 | 3.2107 | 3.1816 | 3.1848 | 3.1783 | 3.1543 | 498000 | 1000 | 494000 | 1000 | 988866 | 5066 | 990000 | 983800 | 11.1333 | 3.1194 | 0.84758 | 3.186 | 0.2462 | 27.17% | 7.727% | 27.3188 | 34.2805 | 2.5921 | 8.1781 | 992057.6 | 955267 | 1036992.1845 | 92.12% | 22 | 11010
2025-02-28 | 2025 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 335090.89 | 7:41 | 18:42 | 6943.2 | 7268.7 | 7323.9 | 7249.4 | 7377.6 | 7393.9 | 7375.9 | 7662.8 | 7264.3 | 7263.2 | 7215.7 | 7311.3 | 7302.9 | 7282.9 | 7370.2 | 7390.4 | 7313.7 | 7367 | 7350.5 | 7371.7 | 7369.3 | 7354.5 | 7230.1 | 7299.5 | 7140.8 | 6279.7 | 7147 | 7132.9 | 7374.1 | 7303.1 | 7221.6 | 7348.1 | 7311.3 | 7347.5 | 7350.8 | 7295.2 | 7403.2 | 7290 | 7314.2 | 7279.7 | 8004.5 | 7232.3 | 7928 | 7131.4 | 7562.2 | 8365.9 | 7069.1 | 8001.4 | 7246.2 | 7374.5 | 7321 | 6911.8 | 7595.7 | 7251.5 | 7531 | 7368.8 | 6700.7 | 7689 | 6696 | 7624.6 | 7541.3 | 6687.3 | 7312 | 6961.7 | 7130 | 6741.3 | 7121 | 7456.3 | 7636.3 | 6896.7 | 7553.8 | 6654.3 | 7277.1 | 7195.7 | 6722.5 | 7533.8 | 6639 | 7615.9 | 6716.7 | 7506.6 | 6960.3 | 7501.3 | 7049.7 | 7769.6 | 6960.4 | 7423.9 | 6921.4 | 6134.4 | 7531.6 | 7273.9 | 6765.6 | 7793.6 | 7542.2 | 6953.5 | 6872.5 | 7603.6 | 6835.5 | 7133.5 | 7746.7 | 6847 | 7773.6 | 6832.9 | 7573.2 | 7000.6 | 7663 | 6648.6 | 7714.4 | 6983.8 | 7600.2 | 6950.5 | 7669.9 | 7088.3 | 6878.2 | 7598.6 | 6971.2 | 6834.9 | 7668.4 | 7745.9 | 7601.4 | 6996.1 | 7696.8 | 6927.6 | 7481.2 | 7003.3 | 7407.1 | 6480.8 | 7537.4 | 6964 | 7063.1 | 7078.6 | 6991.8 | 6057.3 | 6925.6 | 6139.9 | 6900.6 | 6912.9 | 7952.7 | 6977 | 7977 | 7107.9 | 7932.8 | 7029.5 | 7166.8 | 7040 | 7711.9 | 7969.7 | 7886.3 | 7831.7 | 7872.9 | 7915.6 | 7168.3 | 7897.7 | 7928 | 7942.5 | 7982.5 | 7960.9 | 7971.7 | 7180.7 | 7970.6 | 7187.2 | 26.51 | 26.24 | 26.36 | 26.39 | 26.18 | 26.51 | 0 | 34.18 | 0 | 0 | 34.2 | 34.33 | 5.6 | 5.51 | 5.35 | 3.4 | 5.56 | 5.46 | 9.05 | 9.02 | 9.14 | 9.02 | 8.95 | 9.07 | 3.58 | 3.6 | 3.7 | 3.58 | 3.66 | 3.63 | 0.84 | 1.06 | 0.79 | 1.03 | 1.08 | 1.01 | 3.97 | 4.01 | 4.01 | 3.92 | 3.97 | 4.03 | 0.22 | 0.24 | 0.2 | 0.22 | 0.22 | 0.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 868403 | 1636 | 854886 | 1650 | 28568.669 | 81.067 | 3.58 | 3.6 | 3.7 | 3.58 | 3.66 | 3.63 | 3.97 | 4.01 | 4.01 | 3.92 | 3.97 | 4.03 | 582000 | 2000 | 584000 | 2000 | 1161534 | 5134 | 1162000 | 1156400 | 11.0167 | 3.625 | 0.96833 | 3.985 | 0.22333 | 26.71% | 5.604% | 26.365 | 34.2367 | 5.1467 | 9.0417 | 1167240.5 | 1133867 | 1299291.3979 | 87.27% | 19 | 16619
2025-03-01 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 335090.89 | 7:21 | 18:40 | 9777.6 | 10134.6 | 10458.7 | 10455.4 | 10647.8 | 10527 | 10259.8 | 10679.9 | 10143.4 | 10239.7 | 10082 | 10171.6 | 10600.2 | 10353.8 | 10928.8 | 10894 | 10901.1 | 10950.3 | 10836 | 10935 | 10649.9 | 10736.9 | 10114 | 10373.3 | 9763.6 | 8802.2 | 10465 | 10174 | 10196.8 | 9962.7 | 9761.1 | 9848.7 | 10190.2 | 10186.6 | 9967.1 | 9865.4 | 10042.6 | 10014.9 | 10087.8 | 10110.6 | 11234.4 | 10206.9 | 10852.2 | 9964.2 | 10255.5 | 11216.9 | 9701.4 | 11141.3 | 10623.2 | 10784.6 | 10827.1 | 10221.8 | 11204.8 | 10693.9 | 10972.2 | 10572.7 | 9803 | 11148.3 | 9662.5 | 11169.9 | 10971.5 | 9585.6 | 10670.9 | 10038.7 | 10121.2 | 9376 | 10128.2 | 10352 | 10899.5 | 9598.6 | 10620.7 | 9224.8 | 10503.3 | 10059.7 | 9681.7 | 10524.8 | 9355.5 | 10926 | 9555.7 | 10639.6 | 9633.3 | 10361.6 | 9793.7 | 10667.1 | 9650.3 | 10320.8 | 9542.9 | 8494.3 | 10540.4 | 10107 | 9516.9 | 10935.7 | 10643.8 | 9782.3 | 9634.9 | 10782.1 | 9750 | 10175.6 | 11007.9 | 9738.6 | 11065.2 | 9735.1 | 10800.6 | 9928.1 | 10917.3 | 9404.3 | 10975.3 | 9825.6 | 10841.2 | 9840.2 | 10945.8 | 10014.8 | 9723.7 | 10546.6 | 9835.4 | 9569.8 | 10665.2 | 10648.2 | 10260.7 | 9466.3 | 10521.9 | 9418 | 10409.2 | 9724.4 | 10283.1 | 8839.8 | 10303.5 | 9445.4 | 9402.9 | 9443.2 | 9414.7 | 8026.1 | 9141 | 8012 | 9141 | 9157.4 | 10632.6 | 9301.9 | 10719.5 | 9479.7 | 10403.9 | 9293.6 | 9492.9 | 9375.9 | 10416.6 | 10704.8 | 10759.4 | 10712 | 10746.7 | 10730.1 | 9833.8 | 10737.3 | 10765.1 | 10762.4 | 10639.5 | 10644.6 | 10736.5 | 9704 | 10644.4 | 9860.2 | 26.15 | 25.81 | 26.33 | 26.37 | 26.06 | 26.03 | 0 | 40.54 | 0 | 0 | 41 | 40.2 | 2.1 | 0.63 | 2.09 | 0.23 | 2.06 | 1.14 | 5.16 | 5.99 | 5.14 | 4.76 | 6.19 | 5.71 | 4.96 | 5 | 5.03 | 5.08 | 5.12 | 5.02 | 1.31 | 1.34 | 1.21 | 1.61 | 1.47 | 1.27 | 5.72 | 5.64 | 5.66 | 5.83 | 5.76 | 5.61 | 0.31 | 0.33 | 0.28 | 0.3 | 0.29 | 0.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 869227 | 1638 | 855687 | 1652 | 30188.869 | 86 | 4.96 | 5 | 5.03 | 5.08 | 5.12 | 5.02 | 5.72 | 5.64 | 5.66 | 5.83 | 5.76 | 5.61 | 824000 | 2000 | 801000 | 2000 | 1620200 | 4933 | 1621000 | 1615267 | 11.3167 | 5.035 | 1.3683 | 5.7033 | 0.305 | 27.18% | 5.348% | 26.125 | 40.58 | 1.375 | 5.4917 | 1630250.5 | 1602667 | 1890812.5068 | 84.76% | 30 | 16266
2025-03-02 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 335090.89 | 7:20 | 18:47 | 11619.2 | 11976.8 | 11973.2 | 11973 | 12017.4 | 12031.5 | 11984 | 12284 | 11996 | 11952.2 | 11891.3 | 12008.5 | 11993.2 | 11964.5 | 11997 | 12059 | 11915.7 | 11985.3 | 12026.4 | 12102.6 | 12010.6 | 12039.4 | 11861 | 11952.9 | 11822.9 | 10626.8 | 11849 | 11810.6 | 12032.5 | 11895.1 | 11854.9 | 12005 | 12318.9 | 12393.4 | 12382.1 | 12310.9 | 12112.8 | 11993.7 | 11998.1 | 11913.2 | 12653.7 | 11809.2 | 12528.6 | 11677 | 12142.2 | 13021.9 | 11602.7 | 12633.2 | 11901.1 | 12079.9 | 12051.4 | 11563 | 12321.2 | 11866.5 | 12297 | 12019.4 | 11310.6 | 12465.8 | 11309.1 | 12423.7 | 12345.9 | 11299.6 | 12055.4 | 11662.3 | 11822 | 11313.5 | 11828.4 | 12176.3 | 12348.6 | 11519.1 | 12260.8 | 11183.8 | 11974.1 | 11881.5 | 11334.4 | 12243.5 | 11217.4 | 12364.3 | 11311.8 | 12245.2 | 11613.4 | 12231.6 | 11692.3 | 12521 | 11578.1 | 12110.2 | 11476.1 | 10286.2 | 12188.2 | 11927.4 | 11336.9 | 12491.6 | 12228.5 | 11552.2 | 11408.9 | 12256.9 | 11304.4 | 11727.1 | 12362.7 | 11357.1 | 12458 | 11346.5 | 12252.9 | 11551.6 | 12294.9 | 11051 | 12376.5 | 11541.4 | 12263.2 | 11495.2 | 12308.3 | 11687.2 | 11415.2 | 12214.8 | 11524.4 | 11335.9 | 12269.5 | 12384.7 | 12219.9 | 11500.6 | 12307.9 | 11421.4 | 12082.2 | 11565.6 | 12004.3 | 10723.4 | 12148.7 | 11429.8 | 11524.3 | 11509.4 | 11387.2 | 9900.7 | 11316 | 10056.6 | 11383.9 | 11427.2 | 12654.2 | 11544.2 | 12693.4 | 11750.6 | 12589.1 | 11584.3 | 11729 | 11575.2 | 12443.9 | 12705.8 | 12651.3 | 12571 | 12626.9 | 12642.5 | 11840.3 | 12636.1 | 12709.4 | 12716.4 | 12727.6 | 12698.9 | 12743.8 | 11868.2 | 12666.2 | 11902.9 | 26.93 | 26.3 | 26.46 | 26.63 | 26.36 | 26.32 | 0 | 40.48 | 0 | 0 | 40.1 | 39.1 | 3.56 | 2.1 | 3.47 | 0.64 | 3.56 | 3.5 | 6.49 | 6.8 | 6.51 | 6.69 | 6.83 | 6.36 | 5.86 | 5.98 | 6 | 5.91 | 5.97 | 6 | 1.54 | 1.66 | 1.42 | 1.86 | 1.75 | 1.54 | 6.95 | 6.91 | 6.9 | 6.93 | 6.84 | 6.85 | 0.34 | 0.36 | 0.31 | 0.33 | 0.32 | 0.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 870182 | 1639 | 856636 | 1653 | 32084.803 | 90.8 | 5.86 | 5.98 | 6 | 5.91 | 5.97 | 6 | 6.95 | 6.91 | 6.9 | 6.93 | 6.84 | 6.85 | 955000 | 1000 | 949000 | 1000 | 1895934 | 4800 | 1902000 | 1891134 | 11.45 | 5.9533 | 1.6283 | 6.8967 | 0.33667 | 27.35% | 4.882% | 26.5 | 39.8933 | 2.805 | 6.6133 | 1908602 | 1878933 | 2273612.3374 | 82.64% | 25 | 0
2025-03-03 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 335090.89 | 7:18 | 18:50 | 11606.3 | 11961.3 | 11966.5 | 11951.3 | 12034.9 | 12061.4 | 11978.1 | 12253.1 | 11981.7 | 11933.4 | 11882.7 | 11995.2 | 11992.4 | 11957.5 | 11996.6 | 12044.2 | 11925.3 | 11989.5 | 12025.7 | 12103.1 | 12013.4 | 12031.9 | 11870.2 | 11952.5 | 11825.9 | 10623.4 | 11838.8 | 11804.8 | 12022.8 | 11890.1 | 11864.7 | 12019.5 | 12250.4 | 12318.6 | 12325.5 | 12256.7 | 12110.6 | 11977.7 | 11942.4 | 11906.4 | 12671.8 | 11823.5 | 12551.4 | 11691.9 | 12175.1 | 13025.3 | 11594.1 | 12646.5 | 11901.1 | 12080.2 | 12053.8 | 11557.6 | 12319 | 11894.7 | 12300.1 | 12024.7 | 11313.7 | 12464.3 | 11314.8 | 12413.8 | 12324.2 | 11293.6 | 12085.3 | 11668.7 | 11813.9 | 11315.1 | 11804.1 | 12166.5 | 12340.8 | 11525.4 | 12249.1 | 11176.8 | 11968 | 11876.2 | 11317.9 | 12244.1 | 11193.8 | 12361.4 | 11289.9 | 12228.2 | 11609.9 | 12225.4 | 11691.8 | 12500.4 | 11579.4 | 12106.4 | 11473.8 | 10288.3 | 12145.5 | 11917.7 | 11303.4 | 12460.5 | 12219.3 | 11555.5 | 11440.4 | 12222.7 | 11316.7 | 11699 | 12337.6 | 11330.3 | 12412 | 11324.3 | 12227.1 | 11524.1 | 12269.8 | 11032.5 | 12348.1 | 11518.3 | 12235.4 | 11465.9 | 12291.8 | 11665.3 | 11385 | 12194.8 | 11502.3 | 11335.7 | 12238.9 | 12349.7 | 12197.6 | 11474.6 | 12276.3 | 11401.4 | 12065.9 | 11550 | 11990.9 | 10714.2 | 12124 | 11421.6 | 11484.3 | 11461.3 | 11362.6 | 9890.8 | 11343.7 | 10049.3 | 11369.3 | 11392.9 | 12612.2 | 11517.7 | 12647 | 11706.6 | 12541.2 | 11546.9 | 11705.4 | 11543.2 | 12404 | 12662 | 12600.1 | 12524.7 | 12577.3 | 12589.6 | 11797.5 | 12586.4 | 12648.6 | 12666.2 | 12679.3 | 12655.4 | 12697 | 11830.1 | 12724 | 11859.6 | 27.92 | 27.59 | 27.66 | 27.97 | 28.24 | 27.92 | 0 | 38.96 | 0 | 0 | 38.7 | 37.9 | 6.55 | 6.23 | 6.3 | 5.59 | 6.66 | 6.46 | 10.71 | 10.48 | 10.53 | 11.22 | 10.8 | 10.09 | 5.95 | 6.02 | 6.02 | 5.93 | 6 | 6.01 | 1.56 | 1.66 | 1.43 | 1.88 | 1.77 | 1.53 | 6.9 | 6.9 | 6.85 | 6.88 | 6.81 | 6.84 | 0.36 | 0.39 | 0.33 | 0.34 | 0.34 | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 871133 | 1642 | 857583 | 1656 | 33978.269 | 93.667 | 5.95 | 6.02 | 6.02 | 5.93 | 6 | 6.01 | 6.9 | 6.9 | 6.85 | 6.88 | 6.81 | 6.84 | 951000 | 3000 | 947000 | 3000 | 1893466 | 2867 | 1892000 | 1890599 | 11.5333 | 5.9883 | 1.6383 | 6.8633 | 0.35667 | 27.36% | 5.197% | 27.8833 | 38.52 | 6.2983 | 10.6383 | 1906184.6 | 1876400 | 2279972.4742 | 82.3% | 26 | 0
2025-03-04 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 335090.89 | 7:14 | 18:48 | 7354 | 7651 | 7693 | 7668 | 7719 | 7742 | 7704 | 7902 | 7674.5 | 7630.7 | 7588.6 | 7682.3 | 7670.4 | 7656.9 | 7683.5 | 7734.9 | 7614.4 | 7673.4 | 7688 | 7730.9 | 7683 | 7683.9 | 7553.9 | 7624.1 | 7545 | 6670.8 | 7555.9 | 7528.7 | 7707.8 | 7610.1 | 7568.4 | 7712.4 | 7748.2 | 7809.6 | 7802.3 | 7742.6 | 7757.7 | 7660.8 | 7645.1 | 7593.7 | 8222.9 | 7498 | 8108.4 | 7399.6 | 7804.6 | 8541.9 | 7334 | 8205.9 | 7443.2 | 7598.1 | 7574.1 | 7181.3 | 7798.5 | 7468.5 | 7795.1 | 7529.7 | 7006.4 | 7919.5 | 7001.1 | 7872.7 | 7808.9 | 7006.7 | 7628.7 | 7298.9 | 7504.2 | 7107.4 | 7489.1 | 7811.8 | 7991.5 | 7279.1 | 7849.1 | 7009.7 | 7631.1 | 7544.4 | 7106.5 | 7859.7 | 7024.7 | 7940.7 | 7099.3 | 7853.7 | 13135.6 | 13715.1 | 13236 | 13951.7 | 12482.4 | 13015.7 | 13035 | 11651 | 13649.3 | 13458 | 12801.8 | 13915.7 | 13700.1 | 13060.2 | 12928.6 | 13741.6 | 12862 | 13235.8 | 13809.2 | 12849.8 | 13878.5 | 12852.1 | 13710.1 | 13069.4 | 13780.3 | 12516.8 | 13831.4 | 13052.3 | 13716.2 | 13010.1 | 13785.3 | 13170.6 | 12921.5 | 13718.2 | 13042.4 | 12851.3 | 13731.1 | 13833.6 | 13504.9 | 12999.5 | 13778.8 | 12924.4 | 13588.9 | 13070.9 | 13518.8 | 12144.6 | 13638 | 12937.8 | 12992.2 | 12984.4 | 12874.1 | 11204.6 | 12879.9 | 11457.8 | 12885.9 | 12919.1 | 14083.6 | 13061.5 | 14125.1 | 13268.4 | 14012.9 | 13116 | 13262.4 | 13094.2 | 13876.7 | 14119.5 | 14030.4 | 13987.9 | 14040 | 14047.6 | 13343.2 | 14048.9 | 14098.7 | 14127 | 14144.7 | 14110.6 | 14138.4 | 13363.7 | 14147.3 | 13382.2 | 22.6017 | 22.4286 | 22.5939 | 22.8247 | 22.4831 | 22.5057 | 0 | 35.3694 | 0 | 0 | 33.5 | 32.6 | 5.7567 | 5.0875 | 5.4386 | 4.7956 | 5.6339 | 5.3132 | 10.045 | 9.3167 | 9.045 | 9.5817 | 10.2583 | 9.0033 | 6.6771 | 6.7672 | 6.7469 | 6.6564 | 6.7604 | 6.7715 | 1.8072 | 1.9136 | 1.6689 | 2.1657 | 2.0466 | 1.7695 | 7.7836 | 7.7641 | 7.7319 | 7.7562 | 7.711 | 7.7172 | 0.42411 | 0.46006 | 0.38386 | 0.39761 | 0.39509 | 0.44594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 871742 | 1642 | 858646 | 1656 | 35641.736 | 95.8 | 6.6771 | 6.7672 | 6.7469 | 6.6564 | 6.7604 | 6.7715 | 7.7836 | 7.7641 | 7.7319 | 7.7562 | 7.711 | 7.7172 | 609000 | 0 | 1063000 | 0 | 1663467 | 2133 | 1672000 | 1661334 | 11.5667 | 6.7299 | 1.8952 | 7.744 | 0.41778 | 28.16% | 5.395% | 22.5729 | 33.8231 | 5.3376 | 9.5417 | 1676855.5 | 1651267 | 2604857.2878 | 63.39% | 21 | 75243
2025-03-05 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 335090.89 | 7:08 | 18:50 | 12473.7 | 12783.6 | 12805.3 | 12801.9 | 12852.4 | 12890.3 | 12845.6 | 13105.3 | 12838.4 | 12820.7 | 12734.8 | 12853.7 | 12862.2 | 12808 | 12874 | 12959.7 | 12809.5 | 12884.8 | 12900.5 | 12970.8 | 12872.3 | 12906.6 | 12732.7 | 12821 | 12680.3 | 11639.2 | 12716.5 | 12673.1 | 12867.8 | 12731.4 | 12706.5 | 12857.4 | 13258.2 | 13346.3 | 13333.5 | 13259.6 | 12979.5 | 12868.9 | 12861.1 | 12799.8 | 13479 | 12705.3 | 13347.6 | 12588.8 | 13033.1 | 13839.6 | 12495.1 | 13443.2 | 12740.9 | 12919.3 | 12911.1 | 12448.6 | 13155.8 | 12763.4 | 13130.5 | 12845.1 | 12241.5 | 13277.6 | 12264.6 | 13246.1 | 13168.3 | 12231 | 12943.9 | 12563.1 | 12694.8 | 12226.2 | 12688.9 | 13038.8 | 13168.4 | 12437.5 | 13097.8 | 12157 | 12824.1 | 12754.1 | 12244.5 | 13077.7 | 12149 | 13188.5 | 12242.5 | 13083.5 | 12551.8 | 13116.5 | 12609.1 | 13384 | 12506.6 | 12991.2 | 12399.1 | 11303.3 | 13029.1 | 12795.4 | 12273.1 | 13319 | 13059.6 | 12429.8 | 12293.8 | 13094.6 | 12272.1 | 12618.8 | 13200.2 | 12288.8 | 13278.4 | 12291.1 | 13116.4 | 12505 | 13134.1 | 12051.5 | 13220.3 | 12457.9 | 13126.6 | 12417.9 | 13161.7 | 12614.9 | 12343.7 | 13085.1 | 12455.3 | 12314.8 | 13108 | 13222.4 | 13069.5 | 12422.8 | 13158.2 | 12350.6 | 12947.9 | 12491.5 | 12860.6 | 11761.1 | 13017.4 | 12372.5 | 12397.1 | 12336.8 | 12333.8 | 10823.6 | 12254.9 | 11097 | 12313.2 | 12342.5 | 13479.7 | 12450.6 | 13511.3 | 12637.4 | 13394.6 | 12457.9 | 12609.2 | 12464.4 | 13296 | 13532.1 | 13489.9 | 13405.1 | 13460.5 | 13471.8 | 12729.1 | 13465.6 | 13533.9 | 13538.5 | 13546 | 13527.6 | 13576 | 12763.8 | 13599 | 12790.4 | 23.54 | 23.13 | 23.81 | 23.5 | 23.37 | 23.19 | 0 | 38.89 | 0 | 0 | 38.9 | 37.5 | 2.61 | 1.35 | 2.39 | 1.37 | 2.12 | 2.03 | 5.24 | 5.31 | 5.28 | 4.97 | 5.96 | 5.67 | 6.52 | 6.61 | 6.51 | 6.56 | 6.62 | 6.64 | 1.74 | 1.86 | 1.6 | 2.09 | 1.97 | 1.72 | 7.67 | 7.61 | 7.58 | 7.64 | 7.54 | 7.6 | 0.39 | 0.42 | 0.35 | 0.36 | 0.35 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 872766 | 1643 | 859665 | 1657 | 37676.403 | 98 | 6.52 | 6.61 | 6.51 | 6.56 | 6.62 | 6.64 | 7.67 | 7.61 | 7.58 | 7.64 | 7.54 | 7.6 | 1024000 | 1000 | 1019000 | 1000 | 2034667 | 2200 | 2041000 | 2032467 | 11.7 | 6.5767 | 1.83 | 7.6067 | 0.37833 | 27.83% | 4.974% | 23.4233 | 38.43 | 1.9783 | 5.405 | 2049165.1 | 2021200 | 2510982.9711 | 80.49% | 26 | 0
2025-03-06 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 335090.89 | 7:08 | 18:50 | 12231.6 | 12540.4 | 12603.9 | 12588.7 | 12668.3 | 12677.2 | 12579.8 | 12899.1 | 12626.8 | 12623.6 | 12512.3 | 12640.2 | 12626.1 | 12592.7 | 12618.6 | 12718.4 | 12560.6 | 12650.2 | 12669.4 | 12741.6 | 12643.1 | 12671.6 | 12502.5 | 12591.9 | 12456.1 | 11248.8 | 12476.6 | 12445.3 | 12659.3 | 12522.9 | 12499.2 | 12657.4 | 12939.1 | 13037.3 | 13027.2 | 12943.1 | 12741.9 | 12612.6 | 12604.3 | 12554.2 | 13307.8 | 12456 | 13174.4 | 12325.4 | 12781.7 | 13653.5 | 12217.4 | 13278 | 12510.6 | 12698.9 | 12698.6 | 12211.5 | 12967 | 12519.6 | 12931.9 | 12632.4 | 11946.2 | 13097.1 | 11980.6 | 13064.6 | 12974.9 | 11947.8 | 12692.2 | 12278.3 | 12457.9 | 11947 | 12454.1 | 12824.7 | 12988.7 | 12166.5 | 12905.8 | 11838.6 | 12604 | 12534.5 | 11971.8 | 12890 | 11863.2 | 13020.5 | 11963.4 | 12880.3 | 12269.8 | 12888.7 | 12337.5 | 13179.3 | 12229.7 | 12755.6 | 12110.1 | 10883.4 | 12792.7 | 12537 | 11950.8 | 13118 | 12846.2 | 12168.3 | 12043 | 12851.4 | 11943.6 | 12347.7 | 13010.5 | 11995.3 | 13083.5 | 11984 | 12890.5 | 12201.3 | 12916.8 | 11691 | 12997.4 | 12167.7 | 12892.7 | 12114.2 | 12936.9 | 12326.9 | 12039.7 | 12868 | 12169.8 | 12002.2 | 12902.1 | 13021.8 | 12859.5 | 12137.5 | 12953.9 | 12056.4 | 12724.3 | 12200.5 | 12603 | 11328.4 | 12788.4 | 12075.2 | 12137 | 12080.1 | 12060.7 | 10476.3 | 11930.5 | 10645.1 | 11990.4 | 12018.5 | 13304.4 | 12181.7 | 13209 | 12172 | 13209.4 | 12172.3 | 12348.7 | 12178.9 | 13099.5 | 13366.2 | 13305.9 | 13220.3 | 13280.6 | 13292.8 | 12477.8 | 13286.6 | 13346.4 | 13363.3 | 13377.5 | 13361.1 | 13402.7 | 12515.7 | 13425.1 | 12541 | 28.77 | 28.36 | 28.73 | 28.83 | 29.12 | 28.64 | 0 | 43 | 0 | 0 | 42.8 | 41.9 | 3.69 | 2.43 | 3.47 | 2.4 | 3.49 | 2.88 | 6.63 | 6.16 | 6.05 | 6.01 | 6.62 | 6.03 | 6.41 | 6.48 | 6.48 | 6.39 | 6.47 | 6.48 | 1.66 | 1.79 | 1.53 | 2 | 1.91 | 1.66 | 7.44 | 7.44 | 7.37 | 7.4 | 7.34 | 7.4 | 0.36 | 0.39 | 0.32 | 0.33 | 0.33 | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 873771 | 1643 | 860664 | 1657 | 39672.936 | 102.533 | 6.41 | 6.48 | 6.48 | 6.39 | 6.47 | 6.48 | 7.44 | 7.44 | 7.37 | 7.4 | 7.34 | 7.4 | 1005000 | 0 | 999000 | 0 | 1996533 | 4533 | 2004000 | 1992000 | 11.7 | 6.4517 | 1.7583 | 7.3983 | 0.35167 | 27.25% | 4.753% | 28.7417 | 42.5667 | 3.06 | 6.25 | 2009831 | 1982800 | 2414443.3977 | 82.12% | 21 | 0
2025-03-07 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 335090.89 | 7:11 | 18:50 | 11918.2 | 12245.5 | 12306.5 | 12289.3 | 12380.2 | 12395.2 | 12287.3 | 12605.3 | 12326 | 12317.6 | 12208.5 | 12345.3 | 12323.2 | 12296.2 | 12323.7 | 12411.4 | 12255.6 | 12345.1 | 12374 | 12447.8 | 12353.1 | 12377 | 12189.9 | 12286.8 | 12146.9 | 10878.8 | 12169.3 | 12134.5 | 12376.2 | 12250.6 | 12185.5 | 12350.9 | 12563.6 | 12669 | 12671.3 | 12578.7 | 12445.5 | 12304.9 | 12303.3 | 12237.1 | 13022.7 | 12126.4 | 12899.8 | 11983.2 | 12467.5 | 13392.8 | 11890.8 | 13011.9 | 12219.2 | 12409.6 | 12402.2 | 11898.2 | 12690.6 | 12234.5 | 12650.3 | 12347.1 | 11610.7 | 12832.2 | 11622.2 | 12790.6 | 12692.2 | 11604.8 | 12395.2 | 11951 | 12135.6 | 11605.7 | 12141.6 | 12518.5 | 12714.5 | 11832.4 | 12618.8 | 11454.4 | 12313.1 | 12214.3 | 11643.1 | 12601.8 | 11502.9 | 12750.8 | 11621.4 | 12592.2 | 11922.3 | 12576.6 | 12014.5 | 12880 | 11896.3 | 12446.9 | 11763.8 | 10499.3 | 12480.7 | 12215.7 | 11565.2 | 12818.6 | 12552.7 | 11840.4 | 11708.2 | 12530.1 | 11616.1 | 12012.2 | 12715.6 | 11630.7 | 12773.3 | 11611 | 12565.7 | 11830.3 | 12607.9 | 11269 | 12688.6 | 11808.8 | 12565.7 | 11749 | 12618 | 11966.6 | 11675.2 | 12549.1 | 11816.4 | 11614 | 12589.6 | 12709.6 | 12216.8 | 11763.8 | 12640 | 11684.2 | 12407.2 | 11839.3 | 12300.6 | 10913.3 | 12454.9 | 11689.3 | 11803.7 | 11786.5 | 11671.7 | 10112.1 | 11571.6 | 10239.5 | 11604 | 11644.9 | 13021.3 | 11838.5 | 13029 | 12042 | 12943.1 | 11862.8 | 12035.7 | 11837.4 | 12800.4 | 13088.8 | 13011.2 | 12933.3 | 12989.1 | 13005.4 | 12150.5 | 13007.5 | 13068.1 | 13091.7 | 13107.4 | 13081 | 13121.9 | 12182.2 | 13139 | 12210.8 | 30.83 | 30.46 | 31.09 | 31.01 | 31.26 | 30.8 | 0 | 44.26 | 0 | 0 | 43.51 | 43.56 | 3.73 | 2.9 | 3.43 | 2.75 | 3.08 | 2.93 | 9.11 | 8.06 | 7.81 | 7.52 | 8.7 | 8.19 | 6.23 | 6.29 | 6.3 | 6.2 | 6.29 | 6.33 | 1.62 | 1.73 | 1.49 | 1.94 | 1.85 | 1.6 | 7.19 | 7.2 | 7.13 | 7.17 | 7.11 | 7.16 | 0.36 | 0.39 | 0.32 | 0.33 | 0.33 | 0.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 874751 | 1645 | 861637 | 1659 | 41619.27 | 105.6 | 6.23 | 6.29 | 6.3 | 6.2 | 6.29 | 6.33 | 7.19 | 7.2 | 7.13 | 7.17 | 7.11 | 7.16 | 980000 | 2000 | 973000 | 2000 | 1946334 | 3067 | 1949000 | 1943267 | 11.65 | 6.2733 | 1.705 | 7.16 | 0.35 | 27.18% | 4.888% | 30.9083 | 43.7767 | 3.1367 | 8.2317 | 1958916.8 | 1933467 | 2321282.4182 | 83.29% | 22 | 0
2025-03-08 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 335090.89 | 7:08 | 18:49 | 11992.6 | 12357 | 12835 | 12375 | 12458.6 | 12481.6 | 12418 | 12708 | 12413 | 12392 | 12301 | 12450 | 12406 | 12394 | 12397 | 12496 | 12113 | 11389 | 12455 | 12534 | 12434 | 12456 | 12266 | 12367 | 12231 | 10889 | 12253 | 12211 | 12463 | 12240 | 12268 | 12456 | 12635 | 12751 | 12765 | 12671 | 12546 | 12405 | 12403 | 12324 | 13269 | 12270 | 13150 | 12083 | 12687 | 13616 | 12027 | 13233 | 12301 | 12501 | 12488 | 11953 | 12789 | 12331 | 12743 | 12432 | 11623 | 12927 | 11632 | 12894 | 12800.1 | 11631.4 | 12508 | 12046 | 12210 | 11641 | 12215 | 12620 | 12801 | 11873 | 12717.2 | 11462 | 12400.5 | 12292.9 | 11673 | 12701 | 11520 | 12852.4 | 11645.2 | 12690.6 | 11986.7 | 12689.8 | 12079.3 | 12966.2 | 11956 | 12543.7 | 11826.3 | 10518.5 | 12585.4 | 12320.8 | 11601 | 12924.5 | 12642 | 11871.8 | 11730.1 | 12690.7 | 11696.5 | 12108.5 | 12845.9 | 11677.2 | 12889.4 | 11664 | 12674 | 11903.6 | 12724 | 11318.7 | 12798.8 | 11864.6 | 12669 | 11797.7 | 12722.9 | 12025.3 | 11710.8 | 12637.8 | 11865.8 | 11636.8 | 12690.8 | 12819.3 | 12203.4 | 11810 | 12748.1 | 11715.5 | 12506.4 | 11894.2 | 12412.9 | 10931.1 | 12544.6 | 11709.2 | 11851.3 | 11852.6 | 11698.4 | 10116.5 | 11682 | 10301.5 | 11634.7 | 11680.4 | 13138.8 | 11907.1 | 13182 | 12131 | 13075.4 | 11952.2 | 12128.6 | 11890.3 | 12907.5 | 13213.9 | 13123.6 | 13049.1 | 13097.4 | 13118.4 | 12235.3 | 13124.5 | 13186.8 | 13212.5 | 13231 | 13200.8 | 13240 | 12264 | 13251.7 | 12298.8 | 31.1089 | 30.8241 | 31.5995 | 31.2854 | 31.4717 | 31.1686 | 0 | 46.5081 | 0 | 0 | 45.5172 | 45.5659 | 2.8979 | 2.1283 | 2.6768 | 1.7511 | 2.4623 | 2.2164 | 7.7833 | 7.145 | 6.8667 | 7.53 | 7.5583 | 7.325 | 6.3285 | 6.3919 | 6.3948 | 6.2862 | 6.3208 | 6.3984 | 1.6344 | 1.7492 | 1.5016 | 1.9719 | 1.8588 | 1.6111 | 7.2673 | 7.2815 | 7.215 | 7.2489 | 7.2003 | 7.2143 | 0.35405 | 0.38413 | 0.32137 | 0.32878 | 0.32653 | 0.36718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 875733 | 1646 | 862613 | 1661 | 43576.937 | 109.333 | 6.3285 | 6.3919 | 6.3948 | 6.2862 | 6.3208 | 6.3984 | 7.2673 | 7.2815 | 7.215 | 7.2489 | 7.2003 | 7.2143 | 982000 | 1000 | 976000 | 2000 | 1957667 | 3733 | 1955000 | 1953934 | 11.6833 | 6.3534 | 1.7211 | 7.2379 | 0.34701 | 27.09% | 4.794% | 31.2431 | 45.8638 | 2.3555 | 7.3681 | 1971776.8 | 1944267 | 2332645.091 | 83.35% | 23 | 0
2025-03-09 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 335090.89 | 7:07 | 18:48 | 11732.4 | 12097.7 | 12131.6 | 12130.4 | 12206 | 12221.5 | 12153.2 | 12490.4 | 12164.7 | 12151.5 | 12016.4 | 12180.4 | 12119.5 | 12097.1 | 12106.1 | 12207.7 | 12037.6 | 12139.2 | 12146.3 | 12221.8 | 12130.7 | 12155.3 | 11944.8 | 12054.8 | 11886.5 | 10662.7 | 11930.3 | 11887.7 | 12131.6 | 12003.1 | 11927.7 | 12118.8 | 12234.3 | 12353.1 | 12379.8 | 12293.2 | 12197.3 | 12052.5 | 12060.6 | 11945.9 | 12838.8 | 11892.2 | 12684.1 | 11735.2 | 12226.6 | 13200.6 | 11679.4 | 12822.3 | 11994.5 | 12180.7 | 12177.3 | 11619.3 | 12480.3 | 12023.5 | 12407.4 | 12102.5 | 11322 | 12579.7 | 11367.6 | 12564.9 | 12482.5 | 11357.4 | 12181.7 | 11746.2 | 11845.1 | 11301.1 | 11854.6 | 12234 | 12451.7 | 11523 | 12344.1 | 11157.8 | 12041.8 | 11916.5 | 11359 | 12328.8 | 11218.9 | 12511.3 | 11331.5 | 12339 | 11602.9 | 12282.7 | 11668.5 | 12538.7 | 11558.4 | 12123.8 | 11445.4 | 10244.3 | 12185.7 | 11929.1 | 11254.8 | 12534.6 | 12224.7 | 11486 | 11348.2 | 12320.4 | 11299 | 11676 | 12413 | 11281.6 | 12463.4 | 11281.9 | 12245.1 | 11509.9 | 12303.2 | 10976.9 | 12373.9 | 11453.1 | 12245.7 | 11413.7 | 12305.8 | 11611.3 | 11308.5 | 12187.4 | 11451.8 | 11248.5 | 12243.9 | 12359.9 | 8663 | 11289.3 | 12285.1 | 11307.2 | 12052.7 | 11480.2 | 11966.7 | 10596.2 | 12082.3 | 11308.6 | 11423.6 | 11402.9 | 11277.5 | 9802.3 | 11280.1 | 10040.6 | 11239.3 | 11268.9 | 12675.8 | 11456.1 | 12716 | 11676 | 12607.8 | 11492.8 | 11655.7 | 11443.5 | 12450.6 | 12759.4 | 12656.1 | 12586.4 | 12633.4 | 12656.2 | 11782.3 | 12666.3 | 12715.9 | 12738.5 | 12765 | 12735.3 | 12773 | 11800.1 | 12782.9 | 11833.1 | 32.07 | 31.89 | 32.35 | 32.33 | 32.23 | 31.92 | 0 | 46.59 | 0 | 0 | 46.4 | 45.4 | 2.43 | 0.98 | 2.34 | 0.91 | 2.09 | 1.65 | 6.09 | 5.49 | 5.37 | 6.02 | 5.88 | 5.86 | 6.21 | 6.27 | 6.26 | 6.14 | 6.14 | 6.21 | 1.65 | 1.72 | 1.52 | 1.99 | 1.81 | 1.55 | 7.11 | 7.1 | 7.05 | 7.07 | 6.99 | 6.94 | 0.35 | 0.38 | 0.32 | 0.33 | 0.32 | 0.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 876698 | 1646 | 863557 | 1662 | 45473.737 | 112.8 | 6.21 | 6.27 | 6.26 | 6.14 | 6.14 | 6.21 | 7.11 | 7.1 | 7.05 | 7.07 | 6.99 | 6.94 | 965000 | 0 | 944000 | 1000 | 1896800 | 3467 | 1908000 | 1893333 | 11.6833 | 6.205 | 1.7067 | 7.0433 | 0.34333 | 27.5% | 4.875% | 32.1317 | 46.13 | 1.7333 | 5.785 | 1909753.5 | 1886200 | 2257819 | 83.54% | 21 | 8613
2025-03-10 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 335090.89 | 7:15 | 18:48 | 11137.9 | 11473 | 11486.3 | 11465.7 | 11562.9 | 11574.3 | 11523.8 | 11861.6 | 11561.4 | 11557.9 | 11453.9 | 11595.3 | 11553.3 | 11534.8 | 11532.3 | 11627.4 | 11469.2 | 11567.1 | 11604.1 | 11676.5 | 11596.9 | 11616.1 | 11429.4 | 11531.3 | 11392.4 | 10234.1 | 11414 | 11377.9 | 11613 | 11482.3 | 11441.4 | 11612.2 | 11680.7 | 11792.1 | 11842.6 | 11758.6 | 11699.7 | 11553.7 | 11551.1 | 11456.2 | 12273.1 | 11384.2 | 12158.2 | 11233.1 | 11719.7 | 12638.9 | 11173.1 | 12253.5 | 11471.3 | 11655.2 | 11633.3 | 11139 | 11913.2 | 11476 | 11873.9 | 11592.4 | 10838.6 | 12049.4 | 10866.2 | 12016 | 11928 | 10857.7 | 11628.7 | 11222.4 | 11339.1 | 10849.4 | 11363.6 | 11753 | 11940.6 | 11077.3 | 11835.7 | 10716.5 | 11537.9 | 11443.7 | 10879.6 | 11827.6 | 10756.9 | 11969 | 10850.8 | 11817.1 | 11175.1 | 11811.9 | 11262.2 | 12112.3 | 11153 | 11692.1 | 11009.8 | 9899 | 11749.3 | 11475 | 10861.7 | 12076.8 | 11767.3 | 11059.1 | 10903.1 | 11848.9 | 10872.1 | 11275.7 | 11969.5 | 10901.9 | 12024.9 | 10890.8 | 11802.8 | 11111 | 11856.1 | 10595.7 | 11934.3 | 11074.4 | 11819.1 | 11034.7 | 11886 | 11222.4 | 10938.9 | 11787.9 | 11070.5 | 10872.5 | 11848.5 | 11973 | 9864.4 | 9871.4 | 11908.5 | 10976.5 | 11662.2 | 11106.3 | 11568.9 | 10317.1 | 11731.4 | 11000.1 | 11097.6 | 11087.2 | 10992.7 | 9533.6 | 10959.1 | 9807.7 | 10968 | 11001.7 | 12307.8 | 11183.8 | 12340.8 | 11377.8 | 12252.5 | 11228.5 | 11369.3 | 11195.2 | 12134.6 | 12419.9 | 12310.3 | 12046.2 | 12262.4 | 12285.4 | 11468.1 | 12290.7 | 12364.3 | 12385.2 | 12394.8 | 12364.2 | 12405 | 11507.3 | 12419.1 | 11531.3 | 33.1 | 33.02 | 33.62 | 33.22 | 33.12 | 33.31 | 0 | 48.57 | 0 | 0 | 48.77 | 48.52 | 2.45 | 1.37 | 2.25 | 0.6 | 2.05 | 1.7 | 5.08 | 5.33 | 4.75 | 4.19 | 4.62 | 5.26 | 6.07 | 6.13 | 6.17 | 6.06 | 6.17 | 6.22 | 1.54 | 1.71 | 1.44 | 1.89 | 1.81 | 1.6 | 6.85 | 6.86 | 6.82 | 6.82 | 6.82 | 6.88 | 0.35 | 0.39 | 0.33 | 0.34 | 0.33 | 0.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 877617 | 1648 | 864470 | 1663 | 47299.47 | 117.333 | 6.07 | 6.13 | 6.17 | 6.06 | 6.17 | 6.22 | 6.85 | 6.86 | 6.82 | 6.82 | 6.82 | 6.88 | 919000 | 2000 | 913000 | 1000 | 1825733 | 4533 | 1829000 | 1821200 | 11.55 | 6.1367 | 1.665 | 6.8417 | 0.35167 | 27.13% | 5.14% | 33.2317 | 48.62 | 1.7367 | 4.8717 | 1837765.5 | 1813200 | 2191393.8736 | 82.74% | 24 | 13468
2025-03-11 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 335090.89 | 7:13 | 18:50 | 11282.6 | 11655.7 | 11681.7 | 11663.4 | 11767.4 | 11783.1 | 11705.1 | 12022 | 11698.5 | 11706.6 | 11577.2 | 11722.3 | 11686.2 | 11661.7 | 11635.5 | 11783.3 | 11636.6 | 11671.1 | 11727.2 | 11794.4 | 11718.7 | 11720.5 | 11543.6 | 11647.7 | 11502.4 | 10280.7 | 11512.3 | 11483.3 | 11734.6 | 11598.9 | 11549.1 | 11704.1 | 11844.6 | 11937.8 | 11959.9 | 11879.1 | 11825.9 | 11690.2 | 11674.4 | 11578.2 | 12392.3 | 11480.1 | 12271.6 | 11249 | 11844.8 | 12760.6 | 11255.3 | 12375.7 | 11590.5 | 11784 | 11747.8 | 11194.9 | 11939.4 | 11591.9 | 12009.3 | 11713.3 | 10914.8 | 12185.9 | 10932.5 | 12141.8 | 12031.1 | 10925.2 | 11785.3 | 11338.5 | 11468.1 | 10924.2 | 11486.1 | 11878.4 | 12074.2 | 11149.4 | 11974.1 | 10773.5 | 11258.2 | 11224 | 10963.2 | 11966.2 | 10830.1 | 12109.5 | 10928.1 | 11952.8 | 11250.2 | 11949.9 | 11359.6 | 12241.4 | 11240.7 | 11833.7 | 11099.2 | 9939.8 | 11896.3 | 11617.9 | 10928.1 | 12233.8 | 11935.2 | 11176.8 | 11036.6 | 11995.3 | 10956.1 | 11393.1 | 12145.4 | 11000.6 | 12190.5 | 10977.8 | 11968.9 | 11209.3 | 12029.9 | 10677.1 | 12108 | 11169.6 | 11978.6 | 11114.9 | 12053.7 | 11285.9 | 11029 | 11961.1 | 11187.7 | 10974.7 | 12021.2 | 12129.2 | 10910.2 | 11013.7 | 12061 | 11040.9 | 11828.4 | 11120.8 | 11732.1 | 10369.5 | 11869.4 | 11042 | 11129 | 11119.3 | 11046 | 9569.8 | 10959.2 | 9774.1 | 10905.4 | 10940 | 12412.8 | 11183.5 | 12447.3 | 11407.1 | 12335.4 | 11201.2 | 11376.8 | 11157.4 | 12178.1 | 12478.1 | 12374.7 | 12325.2 | 12367.8 | 12376.5 | 11507.3 | 12387.3 | 12456.3 | 12474.5 | 12484.3 | 12449 | 12490 | 11521.3 | 12522.3 | 11568.3 | 31.84 | 31.51 | 31.78 | 32.07 | 31.96 | 31.84 | 0 | 46.1 | 0 | 0 | 46.2 | 45.4 | 2.88 | 1.62 | 2.87 | 1.28 | 2.87 | 2.21 | 7.79 | 7.28 | 7.26 | 5.74 | 6.91 | 6.78 | 6.06 | 6.1 | 6.13 | 6.03 | 6.14 | 6.14 | 1.57 | 1.7 | 1.47 | 1.93 | 1.82 | 1.58 | 6.79 | 6.8 | 6.76 | 6.78 | 6.78 | 6.76 | 0.37 | 0.41 | 0.35 | 0.36 | 0.35 | 0.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 878545 | 1649 | 865393 | 1665 | 49142.671 | 121.867 | 6.06 | 6.1 | 6.13 | 6.03 | 6.14 | 6.14 | 6.79 | 6.8 | 6.76 | 6.78 | 6.78 | 6.76 | 928000 | 1000 | 923000 | 2000 | 1843201 | 4534 | 1848000 | 1838667 | 11.6167 | 6.1 | 1.6783 | 6.7783 | 0.37167 | 27.51% | 5.483% | 31.8333 | 45.9 | 2.2883 | 6.96 | 1855873.4 | 1821067 | 2175264.4401 | 83.72% | 23 | 0
2025-03-12 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 335090.89 | 7:11 | 18:47 | 11167.3 | 11611.8 | 11633.9 | 11608.7 | 11706.9 | 11740.6 | 11684.8 | 12040.6 | 11636.5 | 11656.6 | 11494.9 | 11670.9 | 11606.6 | 11602.6 | 11632.8 | 11716 | 11567.4 | 11654.8 | 11689.2 | 11741.4 | 11675.2 | 11684.5 | 11469.2 | 11584.9 | 11428.8 | 10062.2 | 11440.8 | 11404.5 | 11696 | 11537.6 | 11475.7 | 11688.1 | 11726.3 | 11809.1 | 11829.3 | 11743.7 | 11802.8 | 11638.6 | 11650.4 | 11546.9 | 12502.8 | 11396.4 | 12357.5 | 11207 | 11796.3 | 12914.7 | 11146.5 | 12484.7 | 11515.8 | 11747.2 | 11694.6 | 11061.3 | 12049.4 | 11510.1 | 12004.9 | 11661.9 | 10734.5 | 12204.1 | 10753.5 | 12167.6 | 12053.1 | 10751 | 11758.9 | 11235.2 | 11370.7 | 10741.9 | 11365.1 | 11808.5 | 12082.5 | 10983.1 | 11939.8 | 10565.5 | 11584.6 | 11434.6 | 10772.2 | 11935.8 | 10625.4 | 12115.4 | 10755.9 | 11931.2 | 11055.9 | 11852.5 | 11173.2 | 12222.9 | 11037.5 | 11708.5 | 10931.2 | 9676.7 | 11785.2 | 11470.9 | 10693.9 | 12194.6 | 11864.5 | 10992.8 | 10851.8 | 11929.9 | 10701.7 | 11186.6 | 12074.5 | 10747 | 12135 | 10722.6 | 11845 | 10977 | 11940.5 | 10399.8 | 12012.4 | 10933.7 | 11849.6 | 10866 | 11929.7 | 11075.7 | 10422.4 | 11442.4 | 10574.4 | 10355 | 11503.2 | 11619.4 | 11437.5 | 10525.4 | 11955.9 | 10789.3 | 11666.9 | 10948.1 | 11548.1 | 10073.4 | 11708.8 | 10789.9 | 10932 | 10943.4 | 10793.1 | 9324.2 | 10733.9 | 9514 | 10747.5 | 10788.9 | 12432.8 | 11016 | 12506.9 | 11272.6 | 12383.5 | 11092.7 | 11287.1 | 11044 | 12171.6 | 12553.7 | 12400.9 | 12323.6 | 12371.3 | 12404.5 | 11389.1 | 12431 | 12475.7 | 12518.6 | 12574.6 | 12536.3 | 12573.8 | 11422.9 | 12534.7 | 11448.3 | 32.2 | 31.79 | 32.35 | 32.24 | 32.26 | 32.06 | 0 | 46.82 | 0 | 0 | 46.8 | 46.16 | 2.94 | 1.93 | 2.79 | 0.83 | 2.51 | 2.3 | 7.02 | 6.95 | 6.31 | 5.18 | 6.43 | 6.84 | 5.9 | 5.96 | 5.99 | 5.86 | 5.94 | 5.97 | 1.54 | 1.65 | 1.43 | 1.87 | 1.75 | 1.53 | 6.67 | 6.68 | 6.65 | 6.63 | 6.59 | 6.63 | 0.34 | 0.38 | 0.32 | 0.33 | 0.32 | 0.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 879469 | 1651 | 866302 | 1667 | 50971.071 | 126.467 | 5.9 | 5.96 | 5.99 | 5.86 | 5.94 | 5.97 | 6.67 | 6.68 | 6.65 | 6.63 | 6.59 | 6.63 | 924000 | 2000 | 909000 | 2000 | 1828400 | 4600 | 1829000 | 1823800 | 11.6 | 5.9367 | 1.6283 | 6.6417 | 0.34167 | 27.43% | 5.144% | 32.15 | 46.5933 | 2.2167 | 6.455 | 1839622.2 | 1807733 | 2135625.2954 | 84.65% | 21 | 0
2025-03-13 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 335090.89 | 7:10 | 18:49 | 10779 | 11212.8 | 11218.9 | 11206.7 | 11254.3 | 11304.8 | 11272.8 | 11661.7 | 11328.4 | 11359.5 | 11145 | 11347.4 | 11216.6 | 11256.6 | 11202.5 | 11318.9 | 11132.1 | 11230.1 | 11316.9 | 11376.8 | 11297 | 11303.7 | 11062.2 | 11198.5 | 10998.5 | 9630.1 | 11058.6 | 11003.5 | 11316.3 | 11147.9 | 11036.5 | 11283.7 | 11249.3 | 11323.2 | 11323 | 11229 | 11358.9 | 11197.4 | 11209.9 | 11117.9 | 12095.4 | 10968.2 | 11945.1 | 10760.2 | 11365.7 | 12505.9 | 10685.7 | 12094.3 | 11163.9 | 11398.7 | 11340 | 10613.8 | 11688 | 11167.1 | 11605.9 | 11235.5 | 10300.5 | 11813.9 | 10354.3 | 11784.3 | 11674.1 | 10358.3 | 11377.4 | 10809.6 | 10952.3 | 10264.3 | 10924.7 | 11385.3 | 11683.8 | 10504.9 | 11523.5 | 10083.2 | 11181.2 | 10980.3 | 10327.2 | 11518.4 | 10173.3 | 11724.2 | 10309.4 | 11536.4 | 10543.7 | 11387.5 | 10653.9 | 11758.4 | 10525.9 | 11228.2 | 10472.8 | 9233.3 | 11344.4 | 11022.7 | 10230.4 | 11770.9 | 11468.2 | 10546.8 | 10399.1 | 11528.7 | 10289.2 | 10743.6 | 11682.5 | 10306.9 | 11746.1 | 10291.7 | 11466.2 | 10541 | 11580.5 | 9992.4 | 11644.6 | 10512.4 | 11478.8 | 10465.8 | 11551 | 10657.4 | 10346.4 | 11459.8 | 10498.6 | 10276.5 | 11521.8 | 11643.1 | 11456 | 10443.4 | 11572 | 10342.9 | 11284.5 | 10512.9 | 11140.9 | 9643.6 | 11297.7 | 10305.2 | 10481.1 | 10512.6 | 10301.5 | 8919.1 | 10311.1 | 9125.7 | 10277.6 | 10331 | 12029.5 | 10563.6 | 12066.7 | 10818 | 11953.7 | 10634.3 | 10834.5 | 10556 | 11714.1 | 12079.1 | 11978.1 | 11906.8 | 11966 | 11995.1 | 10940.3 | 11990.3 | 12079.1 | 12103.2 | 12071.5 | 12036.3 | 12083 | 10910.1 | 12130.9 | 10999 | 31.7 | 31.31 | 31.82 | 31.9 | 31.69 | 31.46 | 0 | 45.46 | 0 | 0 | 45.4 | 44.5 | 2.39 | 0.74 | 2.4 | 0.67 | 2.3 | 1.61 | 6.37 | 5.72 | 5.54 | 4.83 | 6.84 | 6.01 | 5.69 | 5.73 | 5.74 | 5.63 | 5.71 | 5.73 | 1.51 | 1.57 | 1.4 | 1.83 | 1.68 | 1.44 | 6.38 | 6.37 | 6.34 | 6.34 | 6.31 | 6.28 | 0.33 | 0.37 | 0.31 | 0.32 | 0.31 | 0.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 880360 | 1652 | 867180 | 1669 | 52734.937 | 131.2 | 5.69 | 5.73 | 5.74 | 5.63 | 5.71 | 5.73 | 6.38 | 6.37 | 6.34 | 6.34 | 6.31 | 6.28 | 891000 | 1000 | 878000 | 2000 | 1763866 | 4733 | 1766000 | 1759133 | 11.65 | 5.705 | 1.5717 | 6.3367 | 0.33167 | 27.55% | 5.234% | 31.6467 | 45.12 | 1.685 | 5.885 | 1775174.3 | 1747934 | 2040984.1383 | 85.64% | 25 | 16486
2025-03-14 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 335090.89 | 7:08 | 18:51 | 10633.6 | 11012.6 | 11022.2 | 10999.6 | 11090.6 | 11111.7 | 11062.4 | 11388 | 11069.6 | 11101.1 | 10921.9 | 11092.8 | 10996 | 10996.6 | 11001.6 | 11089.4 | 10936.6 | 11018.5 | 11067.8 | 11120 | 11047.7 | 11057.9 | 10871 | 10972.1 | 10838.3 | 9628.5 | 10850.7 | 10815 | 11072.4 | 10919.9 | 10881 | 11073.9 | 11183.3 | 11251.4 | 11259.1 | 11178.1 | 11179.8 | 11028.8 | 11041.5 | 10979.3 | 11797.9 | 10806.4 | 11691.9 | 10648.5 | 11180.8 | 12165.4 | 10579.9 | 11795.5 | 10961.1 | 11181.6 | 11105.9 | 10556.1 | 11420.4 | 10965 | 11405.6 | 11099.9 | 10286.1 | 11606.2 | 10292.8 | 11562.4 | 11459.1 | 10282.4 | 11186.3 | 10704.7 | 10880.1 | 10311.6 | 10850 | 11273.2 | 11510.9 | 10524.4 | 11380.4 | 10167.4 | 11052.2 | 10926.8 | 10320.3 | 11367.6 | 10199.1 | 11512.3 | 10306.3 | 11346.7 | 10594.3 | 11304.9 | 10706 | 11657.5 | 10577.2 | 11192.6 | 10491 | 9348 | 11229 | 10977.8 | 10297.8 | 11635.4 | 11339.3 | 10547.3 | 10422 | 11406.3 | 10356.3 | 10770.9 | 11581.7 | 10362.5 | 11625.3 | 10352.6 | 11372.1 | 10590.6 | 11463.8 | 10076.6 | 11532.1 | 10544.6 | 11393.9 | 10507.9 | 11460.9 | 10701.4 | 10395.7 | 11352.2 | 10539.5 | 10351.8 | 11425.2 | 11543.9 | 11359.4 | 10514.1 | 11483.3 | 10425.3 | 11204.6 | 10565.5 | 11102 | 9787.1 | 11266.6 | 10433.9 | 10530.3 | 10531.6 | 10407.9 | 9021.6 | 10368.6 | 9193.2 | 10409.5 | 10432.9 | 11937.7 | 10642 | 11983.4 | 10857.5 | 11875.9 | 10679.2 | 10857.3 | 10625.7 | 11708.6 | 12055.4 | 11921.1 | 11849.3 | 11868.9 | 11902.1 | 10952.8 | 11923.6 | 12019.8 | 12054.2 | 12103.9 | 12067.1 | 12085.6 | 11032.5 | 12048.3 | 11058.7 | 30.9122 | 30.7433 | 31.0955 | 30.8657 | 30.714 | 30.9981 | 0 | 43.8158 | 0 | 0 | 44 | 43.7924 | 4.5524 | 3.1682 | 4.3545 | 3.3849 | 4.42 | 4.3734 | 11.3417 | 9.9367 | 9.3967 | 12.0067 | 13.3267 | 11.0567 | 5.6713 | 5.7221 | 5.7497 | 5.6721 | 5.7741 | 5.8019 | 1.4667 | 1.6024 | 1.3676 | 1.7944 | 1.7269 | 1.5024 | 6.315 | 6.3208 | 6.2782 | 6.3179 | 6.3231 | 6.366 | 0.34755 | 0.38951 | 0.32521 | 0.34179 | 0.33835 | 0.37404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 881238 | 1654 | 868059 | 1670 | 54485.404 | 135.933 | 5.6713 | 5.7221 | 5.7497 | 5.6721 | 5.7741 | 5.8019 | 6.315 | 6.3208 | 6.2782 | 6.3179 | 6.3231 | 6.366 | 878000 | 2000 | 879000 | 1000 | 1750467 | 4733 | 1754000 | 1745734 | 11.7167 | 5.7319 | 1.5767 | 6.3201 | 0.35274 | 27.51% | 5.581% | 30.8881 | 43.8694 | 4.0422 | 11.1775 | 1761709.4 | 1727867 | 2054184.734 | 84.11% | 24 | 2059
2025-03-15 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 335090.89 | 7:06 | 18:54 | 11538.6 | 11940.4 | 12008.5 | 12020.1 | 12064.1 | 12065.9 | 12024.1 | 12283.5 | 11928.7 | 11912.8 | 11820 | 11949.5 | 11945.8 | 11890.9 | 11991.1 | 12057.9 | 11891.8 | 11951.2 | 11974.7 | 12061.5 | 11942.2 | 11978.1 | 11776.2 | 11875.9 | 11818.8 | 10592.7 | 11832.3 | 11785.4 | 11996.2 | 11855.1 | 11908.3 | 12031.6 | 12237.5 | 12366.1 | 12356.2 | 12301.7 | 12205.6 | 12067.6 | 12053.1 | 11953.9 | 12738.5 | 11864.2 | 12613.1 | 11711.8 | 12193.3 | 13051.2 | 11602.8 | 12704.3 | 11882.7 | 12081.4 | 12040.1 | 11520.1 | 12322 | 11897.2 | 12289 | 12036.6 | 11213.7 | 12390.7 | 11228.7 | 12395.7 | 12307 | 11205 | 12001.3 | 11562.7 | 11763.9 | 11175.9 | 11738.5 | 12085.5 | 12256.3 | 11413.7 | 12192.4 | 11044.8 | 11847 | 11797.7 | 11146.3 | 12151.8 | 11005.1 | 12225.9 | 11109.4 | 12065.8 | 11412.1 | 12101.1 | 11485.4 | 12348.6 | 11059.5 | 11657 | 11266.2 | 10011 | 11930.7 | 11684.1 | 11009.7 | 12237.1 | 12001.1 | 11299 | 11165.9 | 11997.9 | 11055.8 | 11448.3 | 12162.1 | 11081.7 | 12263.4 | 11082.4 | 12090 | 11340.6 | 12160.5 | 10820.9 | 12245.2 | 11316.1 | 12146.1 | 11263 | 12210.8 | 11517.9 | 11162.9 | 12102.4 | 11315.1 | 11140.5 | 12149 | 12300.2 | 12123.4 | 11369.6 | 12246 | 11281.9 | 11987.5 | 11403.4 | 11914.8 | 10580.6 | 12093 | 11313.3 | 11374.3 | 11370.2 | 11279.7 | 9760.9 | 11218.6 | 9997.6 | 11296.4 | 11340.5 | 12643.7 | 11467.8 | 12750 | 11728 | 12606 | 11574.4 | 11720.4 | 11566.6 | 12523.3 | 12822.7 | 12680.9 | 12614.8 | 12628.3 | 12635.3 | 11880.9 | 12725.3 | 12696.4 | 12765.9 | 12835 | 12810.4 | 12845.6 | 11920.8 | 12729.2 | 11924.4 | 27.96 | 27.42 | 27.77 | 27.84 | 27.65 | 27.57 | 0 | 41.09 | 0 | 0 | 40.9 | 40 | 3.74 | 2.26 | 3.61 | 1.83 | 3.63 | 3.59 | 7.23 | 8.32 | 7.77 | 8.06 | 8.17 | 7.34 | 6.13 | 6.21 | 6.26 | 6.1 | 6.17 | 6.24 | 1.6 | 1.72 | 1.51 | 1.95 | 1.83 | 1.6 | 6.86 | 6.88 | 6.9 | 6.85 | 6.8 | 6.86 | 0.37 | 0.41 | 0.35 | 0.36 | 0.34 | 0.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 882187 | 1655 | 868997 | 1672 | 56368.671 | 140.6 | 6.13 | 6.21 | 6.26 | 6.1 | 6.17 | 6.24 | 6.86 | 6.88 | 6.9 | 6.85 | 6.8 | 6.86 | 949000 | 1000 | 938000 | 2000 | 1883267 | 4667 | 1884000 | 1878600 | 11.8 | 6.185 | 1.7017 | 6.8583 | 0.37 | 27.51% | 5.395% | 27.7017 | 40.6633 | 3.11 | 7.815 | 1896217.8 | 1867066 | 2246151.5247 | 83.12% | 21 | 6818
2025-03-16 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 335090.89 | 7:06 | 18:53 | 10997.1 | 11218.6 | 11104.2 | 11114.5 | 11162.9 | 11203.8 | 11187.1 | 11471.4 | 11348.1 | 11343.3 | 11230 | 11368.1 | 11281.1 | 11289 | 11233.6 | 11292 | 11129.1 | 11234 | 11318.8 | 11407 | 11299 | 11329.2 | 11180.4 | 11255.9 | 11290.9 | 10149.9 | 11274.8 | 11234.8 | 11405.4 | 11241.9 | 11273.7 | 11449.9 | 11847.2 | 11894.8 | 11790.2 | 11721.6 | 11607.8 | 11473.6 | 11507 | 11561.5 | 11939.2 | 11156.8 | 11838.2 | 11034.2 | 11461.9 | 12225.6 | 10877.1 | 11877.6 | 11328.9 | 11514.3 | 11458.6 | 11056.3 | 11684.9 | 11239.5 | 11787.6 | 11517.9 | 10859.3 | 11930 | 10802 | 11882.8 | 11789.3 | 10791.9 | 11550.5 | 11168.9 | 11432.8 | 11071 | 11434.7 | 11918.4 | 11875 | 11283.4 | 11871.3 | 10915.8 | 11494.6 | 11580.3 | 10903.3 | 11916.4 | 10898.8 | 11865.1 | 10894.9 | 11811.6 | 11427.9 | 12042.1 | 11473.9 | 12328.4 | 11307.9 | 11865.8 | 11279.3 | 10053 | 12011 | 11730.8 | 11083 | 12292.6 | 12007.1 | 11329 | 11196.9 | 12029.2 | 11135.3 | 11546.1 | 12228.1 | 11180.4 | 12235.1 | 11139 | 12017.3 | 11368.5 | 12047.6 | 10801.7 | 12136.7 | 11297.1 | 11989.9 | 11211.5 | 12045.4 | 11428.8 | 11253.8 | 12128.1 | 11350 | 11191.4 | 12126.7 | 12327.6 | 12114.9 | 11418.3 | 12259.7 | 11319.1 | 11935.2 | 11377.7 | 11840.9 | 10581.3 | 12066.7 | 11322.4 | 11358.7 | 11341.8 | 11249.5 | 9734.2 | 11203.1 | 9975.7 | 11220 | 11248.7 | 12494.6 | 11338 | 12602.4 | 11606 | 12501.1 | 11464.9 | 11615.4 | 11437.1 | 12411.4 | 12701.7 | 12516.5 | 12447.2 | 12463 | 12477.1 | 11707.3 | 12566.2 | 12632.1 | 12668.1 | 12807.7 | 12742 | 12760.6 | 11834 | 12661.4 | 11783.1 | 27.39 | 27.02 | 27.35 | 27.45 | 27.24 | 27.2 | 0 | 41.3 | 0 | 0 | 41.9 | 41 | 2.96 | 0.54 | 2.83 | 0.45 | 2.73 | 2.38 | 6.03 | 5.84 | 5.93 | 5.39 | 6.43 | 5.6 | 5.89 | 6 | 5.93 | 5.99 | 6.23 | 6.23 | 1.58 | 1.61 | 1.45 | 1.94 | 1.84 | 1.57 | 6.54 | 6.59 | 6.49 | 6.68 | 6.84 | 6.78 | 0.36 | 0.4 | 0.34 | 0.36 | 0.36 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 883087 | 1657 | 869937 | 1674 | 58205.938 | 145.2 | 5.89 | 6 | 5.93 | 5.99 | 6.23 | 6.23 | 6.54 | 6.59 | 6.49 | 6.68 | 6.84 | 6.78 | 900000 | 2000 | 940000 | 2000 | 1837267 | 4600 | 1836000 | 1832667 | 11.7833 | 6.045 | 1.665 | 6.6533 | 0.37 | 27.54% | 5.561% | 27.275 | 41.4 | 1.9817 | 5.87 | 1850114.7 | 1822400 | 2182237.8878 | 83.51% | 23 | 29943
2025-03-17 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 335090.89 | 7:02 | 18:55 | 12372.1 | 12697 | 12666.6 | 12676.4 | 12718.7 | 12774.4 | 12724 | 12977.9 | 12724 | 12738.5 | 12637.7 | 12758.5 | 12731.8 | 12718.1 | 12734.9 | 12793.8 | 12638.6 | 12712.2 | 12757.4 | 12844.1 | 12717.6 | 12753.1 | 12610.1 | 12686.2 | 12573.3 | 11443.6 | 12601.1 | 12554.1 | 12776.2 | 12658.1 | 12613.8 | 12768.2 | 13067.2 | 13153.5 | 13172 | 13090 | 12854.7 | 12739.1 | 12736.8 | 12655.6 | 13357.5 | 12551.8 | 13226.8 | 12407.5 | 12880.8 | 13736.8 | 12326.2 | 13327.3 | 12662.3 | 12855.7 | 12818.6 | 12319.8 | 13073.4 | 12652.9 | 13054.7 | 12766.3 | 12109 | 13204 | 12121 | 13184.1 | 13094.9 | 12091 | 12834.5 | 12447.1 | 12591 | 12098.3 | 12588.3 | 12930.9 | 13096.3 | 12300.5 | 13013.5 | 11987.1 | 12733.5 | 12657.5 | 12127.5 | 12997.7 | 12017 | 13132.2 | 12118.4 | 13010.5 | 12388.3 | 12994.9 | 12462.9 | 13270.3 | 12357.9 | 12869.6 | 12252.8 | 11049.6 | 12947.8 | 12673.2 | 12105.2 | 13258.7 | 12985 | 12331.7 | 12199.1 | 13012.9 | 12109.8 | 12495.9 | 13137.5 | 12134 | 13176 | 12120.2 | 12996.5 | 12349.9 | 13022 | 11819 | 13104.7 | 12282.2 | 12989.5 | 12226 | 13021.3 | 12442.6 | 12159.7 | 12956.7 | 12282.9 | 12102.4 | 12980.4 | 13125.6 | 12959.5 | 12281.4 | 13066.8 | 12180.7 | 12834.1 | 12314.4 | 12742.1 | 11482.6 | 12910.1 | 12203.4 | 12282.1 | 12256.7 | 12181.9 | 10606.1 | 12112.2 | 10868.3 | 12122.9 | 12159.7 | 13422.4 | 12329 | 13450.1 | 12520.2 | 13358.2 | 12370.2 | 12517.9 | 12345.8 | 13210.7 | 13473.3 | 13419.7 | 13343.8 | 13381.6 | 13402.7 | 12614.1 | 13403.3 | 13480 | 13481.2 | 13498.6 | 13471.4 | 13507.7 | 12645.1 | 13535.7 | 12679.9 | 28.29 | 27.8 | 28.38 | 28.17 | 28.06 | 27.94 | 0 | 43.63 | 0 | 0 | 43.8 | 42.7 | 2.37 | 0.26 | 2.37 | 0.58 | 2.02 | 1.49 | 5.83 | 5.26 | 6.98 | 5.33 | 6.62 | 5.34 | 6.76 | 6.82 | 6.81 | 6.74 | 6.83 | 6.85 | 1.78 | 1.85 | 1.65 | 2.15 | 2.02 | 1.75 | 7.58 | 7.57 | 7.51 | 7.57 | 7.53 | 7.53 | 0.39 | 0.42 | 0.36 | 0.38 | 0.36 | 0.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 884101 | 1659 | 870942 | 1676 | 60221.338 | 149.733 | 6.76 | 6.82 | 6.81 | 6.74 | 6.83 | 6.85 | 7.58 | 7.57 | 7.51 | 7.57 | 7.53 | 7.53 | 1014000 | 2000 | 1005000 | 2000 | 2015400 | 4533 | 2015000 | 2010867 | 11.8833 | 6.8017 | 1.8667 | 7.5483 | 0.38667 | 27.44% | 5.123% | 28.1067 | 43.3767 | 1.515 | 5.8933 | 2029747.5 | 2001400 | 2446098.4723 | 81.82% | 26 | 4540
2025-03-18 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 335090.89 | 7:01 | 18:54 | 12331.4 | 12690.3 | 12663.4 | 12670.6 | 12718 | 12778.3 | 12724.3 | 13041 | 12729.8 | 12758.4 | 12639.6 | 12768.2 | 12732.3 | 12722.5 | 12736 | 12806.9 | 12645.7 | 12737 | 12783.7 | 12873.8 | 12733 | 12769.8 | 12609.4 | 12694.5 | 12562.4 | 11330.9 | 12590.3 | 12549.4 | 12788.5 | 12645.9 | 12597.8 | 12769 | 13044.1 | 13117.4 | 13110.7 | 13046.7 | 12861.9 | 12738.9 | 12746 | 12645.5 | 13447 | 12585.9 | 13318 | 12421.9 | 12923.5 | 13848.7 | 12349.6 | 13420.5 | 12661 | 12864.4 | 12817.4 | 12292 | 13083.2 | 12688.7 | 13070.2 | 12778.1 | 12038.7 | 13227 | 12045.5 | 13203.7 | 13106.1 | 12023.8 | 12837.3 | 12422.9 | 12573.8 | 12045.9 | 12564.3 | 12956.9 | 13113.1 | 12281.4 | 13031.9 | 11927.7 | 12719.3 | 12657.6 | 12065.4 | 13032.9 | 11965.8 | 13146.4 | 12067.2 | 13035.5 | 12379.3 | 13025.8 | 12445.8 | 13317.2 | 12339.5 | 12875 | 12241 | 10982.5 | 12951.7 | 12674.6 | 12055.2 | 13273.5 | 12985.8 | 12291.1 | 12156.2 | 13047.1 | 12125.7 | 12511.9 | 13200.5 | 12119.5 | 13212.9 | 12104.1 | 13021.5 | 12349.1 | 13055.4 | 11803.8 | 13135.9 | 12275.2 | 13005.5 | 12197.7 | 13038.4 | 12421.2 | 12146.1 | 12994.4 | 12280.1 | 12084.3 | 13025.9 | 13170.3 | 12994.9 | 12272.4 | 13108.7 | 12169.8 | 12863.4 | 12302.3 | 12749.1 | 11455 | 12936.7 | 12187.8 | 12317.3 | 12312.4 | 12160 | 10598.7 | 12086.1 | 10830 | 12142.7 | 12179.8 | 13506.3 | 12378.8 | 13538.2 | 12567 | 13441 | 12396.9 | 12543.1 | 12353.3 | 13281.1 | 13566.2 | 13509.7 | 13422.9 | 13459.6 | 13484.8 | 12659.7 | 13485.5 | 13568.8 | 13568.1 | 13577.4 | 13548 | 13590.5 | 12682.9 | 13623.7 | 12728.4 | 29.52 | 29.34 | 29.61 | 29.45 | 29.38 | 29.4 | 0 | 45.76 | 0 | 0 | 45.7 | 45.3 | 2.59 | 0.63 | 2.58 | 0.84 | 2.16 | 1.87 | 5.6 | 5.9 | 6.61 | 5.5 | 6.31 | 6.23 | 6.76 | 6.82 | 6.86 | 6.74 | 6.86 | 6.9 | 1.75 | 1.83 | 1.64 | 2.13 | 2.04 | 1.78 | 7.57 | 7.57 | 7.54 | 7.55 | 7.55 | 7.58 | 0.38 | 0.42 | 0.36 | 0.37 | 0.36 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 885110 | 1660 | 871953 | 1677 | 62238.81 | 154.267 | 6.76 | 6.82 | 6.86 | 6.74 | 6.86 | 6.9 | 7.57 | 7.57 | 7.54 | 7.55 | 7.55 | 7.58 | 1009000 | 1000 | 1011000 | 1000 | 2017472 | 4534 | 2018000 | 2012938 | 11.8833 | 6.8233 | 1.8617 | 7.56 | 0.38167 | 27.28% | 5.049% | 29.45 | 45.5867 | 1.7783 | 6.025 | 2031633.2 | 2000270 | 2437356.7284 | 82.07% | 28 | 0
2025-03-19 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 335090.89 | 7:01 | 18:56 | 12289.1 | 12663.5 | 12644.7 | 12647.2 | 12729.7 | 12745.5 | 12689.1 | 13024.6 | 12712.7 | 12710.5 | 12604.5 | 12751.6 | 12690.5 | 12676.6 | 12711.5 | 12763.6 | 12605.8 | 12682.4 | 12731.4 | 12818.5 | 12702.2 | 12733.8 | 12554 | 12642.4 | 12500.8 | 11218.7 | 12530.8 | 12488.1 | 12728.8 | 12586.2 | 12544.7 | 12706.6 | 12997.1 | 13056.8 | 13045.2 | 12990.8 | 12818.5 | 12691.8 | 12691.1 | 12604.3 | 13383.8 | 12511.7 | 13252.1 | 12348.6 | 12859.2 | 13803.5 | 12283.2 | 13364.1 | 12609.9 | 12810.8 | 12760.8 | 12221.6 | 13029.2 | 12654.7 | 13007.1 | 12724.3 | 11961 | 13177 | 11960.7 | 13146.4 | 13044.6 | 11941.4 | 12812.2 | 12385.3 | 12524 | 11970.6 | 12505.4 | 12876.3 | 13063.3 | 12188.9 | 12965.8 | 11805.4 | 12671 | 12571.2 | 11996.5 | 12950.8 | 11861 | 13098.9 | 11987.1 | 12963.4 | 12276.8 | 12931.8 | 12350.1 | 13228.1 | 12237.5 | 12786.3 | 12143.8 | 10846.3 | 12852.6 | 12588.7 | 11959.9 | 13196.4 | 12924 | 12227.9 | 12092.4 | 12954.1 | 12012 | 12388.8 | 13099.1 | 11989.3 | 13139.8 | 11979.9 | 12938.7 | 12229 | 12978 | 11653.4 | 13052.9 | 12162.6 | 12941.3 | 12104.2 | 12980.3 | 12323.6 | 12016.7 | 12874.4 | 12162 | 11944.8 | 12915.7 | 13053.4 | 12875.9 | 12135 | 12988.2 | 12033.6 | 12751.2 | 12184.8 | 12636 | 11277.3 | 12813.1 | 12050 | 12177.7 | 12173.8 | 12021.1 | 10424.5 | 11926.6 | 10620.7 | 11935.2 | 12016.3 | 13375.5 | 12221.1 | 13403.3 | 12419.2 | 13304 | 12242.5 | 12391.3 | 12198.6 | 13143.3 | 13432.8 | 13369.7 | 13289.5 | 13326.8 | 13350.4 | 12506.3 | 13346.2 | 13431.9 | 13434.8 | 13447.7 | 13414.9 | 13454.7 | 12535.6 | 13493.7 | 12585.2 | 30.51 | 30.33 | 30.72 | 30.45 | 30.44 | 30.52 | 0 | 46.01 | 0 | 0 | 45.76 | 45.47 | 3.14 | 1.18 | 2.98 | 1.28 | 2.88 | 2.45 | 7.65 | 7.13 | 6.44 | 7.09 | 6.98 | 8.03 | 6.71 | 6.79 | 6.81 | 6.7 | 6.79 | 6.81 | 1.76 | 1.83 | 1.64 | 2.14 | 2.02 | 1.76 | 7.47 | 7.51 | 7.46 | 7.48 | 7.45 | 7.45 | 0.39 | 0.42 | 0.36 | 0.38 | 0.36 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 886115 | 1661 | 872954 | 1679 | 64242.405 | 158.8 | 6.71 | 6.79 | 6.81 | 6.7 | 6.79 | 6.81 | 7.47 | 7.51 | 7.46 | 7.48 | 7.45 | 7.45 | 1005000 | 1000 | 1001000 | 2000 | 2003595 | 4533 | 2003000 | 1999062 | 11.9167 | 6.7683 | 1.8583 | 7.47 | 0.385 | 27.46% | 5.154% | 30.495 | 45.7467 | 2.3183 | 7.22 | 2017475.1 | 1988067 | 2412605.0904 | 82.4% | 25 | 0
2025-03-20 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 335090.89 | 7:02 | 18:55 | 11336.5 | 11685.9 | 11709.6 | 11715.7 | 11801.9 | 11790.9 | 11728 | 12039.6 | 11735.8 | 11801.6 | 11625.5 | 11787.7 | 11705.9 | 11707.3 | 11769.2 | 11794.5 | 11646.7 | 11687.7 | 11722.4 | 11808.7 | 11736.9 | 11730.4 | 11591.5 | 11679.4 | 11617.9 | 10298.2 | 11558.5 | 11545.3 | 11797.6 | 11640.6 | 11598 | 11805.9 | 12103.1 | 12138.1 | 12130.5 | 12048.8 | 11928.4 | 11766.8 | 11811.6 | 11818.1 | 12650 | 11730.2 | 12521.9 | 11581 | 12069.4 | 13004.5 | 11461.9 | 12640.3 | 11693.1 | 11897.5 | 11805.7 | 11316.8 | 12079.2 | 11692.8 | 12145.4 | 11864.5 | 11052.1 | 12356.4 | 10960.3 | 12287.7 | 12183 | 10965.9 | 11973.1 | 11529 | 11737.7 | 11126.5 | 11715.3 | 12113.7 | 12306.2 | 11413.3 | 12209.6 | 10991.7 | 11868.1 | 11802.2 | 11157.5 | 12215.2 | 11034.6 | 12347.1 | 11182.4 | 12244.5 | 11494.7 | 12209.4 | 11599.8 | 12508.5 | 11405.3 | 12012 | 11357.3 | 10071 | 12092.5 | 11831.8 | 11042.9 | 12413.9 | 12133.6 | 11408.8 | 11276.4 | 12200 | 11219.6 | 11676.6 | 12488.1 | 11310 | 12560.1 | 11297.5 | 12358.2 | 11575 | 12425.2 | 10978.7 | 12493.8 | 11509.8 | 12342.2 | 11434.1 | 12411.1 | 11692.8 | 11338 | 12318.7 | 11533.4 | 11293.6 | 12379.5 | 12526.1 | 12332.2 | 11519.8 | 12464.3 | 11367.6 | 12191.2 | 11557.4 | 12050.8 | 10576.2 | 12210.4 | 11321.8 | 11522.7 | 11550.8 | 11293 | 9810.6 | 11349.7 | 10041.5 | 11329.7 | 11369.7 | 12755.6 | 11560.4 | 12802.2 | 11776.2 | 12758.6 | 11621.2 | 11793.4 | 11596.9 | 12581 | 12931 | 12718.5 | 12657.9 | 12687.3 | 12718 | 11835.6 | 12774.7 | 12888.4 | 12922.7 | 12962.1 | 12937.3 | 12963.5 | 11963.2 | 12860.6 | 11969.6 | 30.27 | 30.03 | 30.64 | 30.34 | 30.04 | 30.33 | 0 | 45.64 | 0 | 0 | 46.22 | 46.31 | 2.5 | 1.15 | 2.3 | 0.92 | 2.22 | 2.12 | 6.58 | 7.01 | 6.36 | 6.02 | 5.84 | 6.39 | 6.19 | 6.29 | 6.37 | 6.3 | 6.47 | 6.44 | 1.64 | 1.68 | 1.55 | 2.03 | 1.95 | 1.68 | 6.79 | 6.86 | 6.87 | 6.93 | 7.01 | 6.94 | 0.39 | 0.43 | 0.37 | 0.39 | 0.38 | 0.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 887049 | 1663 | 873903 | 1680 | 66124.338 | 162.533 | 6.19 | 6.29 | 6.37 | 6.3 | 6.47 | 6.44 | 6.79 | 6.86 | 6.87 | 6.93 | 7.01 | 6.94 | 934000 | 2000 | 949000 | 1000 | 1881933 | 3733 | 1880000 | 1878200 | 11.8833 | 6.3433 | 1.755 | 6.9 | 0.39667 | 27.67% | 5.749% | 30.275 | 46.0567 | 1.8683 | 6.3667 | 1894989.3 | 1863667 | 2227496.8131 | 83.67% | 27 | 7659
2025-03-21 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 335090.89 | 7:01 | 18:56 | 11585.8 | 12041.2 | 12019.5 | 11982 | 12085.8 | 12130 | 12109.7 | 12470.4 | 12080.4 | 12276.7 | 11891.6 | 12122.7 | 11910.8 | 12007.3 | 11887.3 | 11981.9 | 11829 | 11954.8 | 12025 | 12057.9 | 12000.2 | 11996 | 11736.9 | 11886.1 | 11788.7 | 10330 | 11762.3 | 11731.8 | 12079.3 | 11954 | 11899.8 | 12123.1 | 9639.4 | 9684.2 | 9704.3 | 9606.8 | 9761.7 | 9610.1 | 9601.5 | 9537.8 | 3795.6 | 3374 | 3730.3 | 3317 | 3536.6 | 3995.4 | 3307.9 | 3800.8 | 11901.3 | 12209.7 | 12049.3 | 11452.1 | 12445.7 | 11861.1 | 12553.8 | 12160.9 | 11130.7 | 12791.9 | 11082.7 | 12755.9 | 12699.3 | 11115.1 | 12375.7 | 11808.3 | 11969.7 | 11190.1 | 11959.4 | 12395.7 | 12791.6 | 11437.5 | 12663.6 | 11002.6 | 12244.6 | 12042.6 | 11359.1 | 12663.4 | 11182 | 12923.7 | 11363.5 | 12711.4 | 11548.1 | 12479 | 11724.5 | 12924 | 11523.9 | 12330.8 | 11492.6 | 10183.8 | 12516.4 | 12080.5 | 11193.7 | 12884.2 | 12461.9 | 11413.2 | 11225.9 | 12496 | 11036.5 | 11503.3 | 12510.1 | 10996.6 | 12557.3 | 10968 | 12213.1 | 11215.9 | 12327.8 | 10618.7 | 12374.3 | 11090.6 | 12200.9 | 11079.3 | 12338.1 | 11296.7 | 11044.3 | 12247 | 11173.1 | 10947.8 | 12236.5 | 12424.4 | 12149.9 | 11150 | 12308.8 | 11006.8 | 11956.3 | 11121.6 | 11795.7 | 10332 | 12063.4 | 11077.9 | 11222.9 | 11250.6 | 11098.4 | 9564.8 | 11168.3 | 9876.1 | 11164.7 | 11242.1 | 13102.6 | 11540.8 | 13227.3 | 11857.9 | 13101.6 | 11683.1 | 11878 | 11550 | 12873.5 | 13308.1 | 13079.1 | 12968.3 | 12982.4 | 13023.7 | 12023.6 | 13136.4 | 13257.9 | 13223.9 | 13223.6 | 13185.6 | 13228.5 | 11993.3 | 13277.3 | 11984.5 | 31.4795 | 31.0857 | 31.457 | 31.5107 | 31.2197 | 31.1683 | 0 | 45.6661 | 0 | 0 | 45.5 | 45.1 | 2.4118 | 1.1271 | 2.4516 | 0.43157 | 2.1251 | 1.8069 | 5.17 | 4.7917 | 4.9317 | 4.9067 | 7.585 | 5.6 | 6.2771 | 6.3224 | 6.3885 | 0 | 6.3098 | 6.4682 | 1.6138 | 1.6757 | 1.5125 | 2.0043 | 1.8538 | 1.6736 | 6.9442 | 6.9534 | 6.9519 | 0 | 6.8813 | 7.0238 | 0.37468 | 0.41257 | 0.35473 | 0.37627 | 0.3509 | 0.4031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 887917 | 1664 | 874853 | 1682 | 67938.072 | 165.667 | 6.2771 | 6.3224 | 6.3885 | 0 | 6.3098 | 6.4682 | 6.9442 | 6.9534 | 6.9519 | 0 | 6.8813 | 7.0238 | 868000 | 1000 | 950000 | 2000 | 1813734 | 3134 | 1815000 | 1810600 | 11.9167 | 6.3532 | 1.7223 | 6.9509 | 0.37871 | 27.11% | 5.448% | 31.3201 | 45.422 | 1.7257 | 5.4975 | 1825175.5 | 1796000 | 2238755.7226 | 80.22% | 25 | 1723
2025-03-22 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 335090.89 | 6:56 | 18:57 | 12314.4 | 12694.5 | 12660.5 | 12661.5 | 12719.6 | 12783.6 | 12734.2 | 13060.8 | 12707.7 | 12744.5 | 12628 | 12776.4 | 12700.6 | 12705.1 | 12707.4 | 12785.2 | 12632 | 12716 | 12762.6 | 12820.3 | 12747.1 | 12780.6 | 12603.2 | 12686.5 | 12532.2 | 11296.2 | 12551.7 | 12532.7 | 12777.4 | 12651.1 | 12580.4 | 12744.9 | 13084.9 | 13149.8 | 13158.7 | 13070.2 | 12829.2 | 12696.3 | 12683 | 12651.9 | 13405 | 12536.5 | 13271 | 12390.4 | 12880 | 13807.9 | 12339.4 | 13387 | 12647.5 | 12841.1 | 12806 | 12298.5 | 13083 | 12670.7 | 13029.1 | 12753.3 | 11996.8 | 13178.9 | 12045.4 | 13168.3 | 13090.9 | 12026.5 | 12810.5 | 12386.9 | 12576.9 | 12044.5 | 12543 | 12903.3 | 13093 | 12237.7 | 12988.5 | 11886 | 12695.3 | 12598.3 | 12064.5 | 12966.3 | 11936.6 | 13116.4 | 12062.8 | 12984.1 | 12332.2 | 12961.1 | 12380.2 | 13256.4 | 12273.5 | 12793.9 | 12217.9 | 10941 | 12899.9 | 12622.4 | 12046 | 13245 | 12934.5 | 12239.7 | 12112.6 | 13034.9 | 12051 | 12464.2 | 13156.6 | 12106.5 | 13192.1 | 12089.7 | 13011 | 12319.4 | 13035.6 | 11783.2 | 13119.9 | 12268 | 13007.7 | 12198.7 | 13046.6 | 12426.3 | 12123.3 | 12954.4 | 12269 | 12086 | 13002.9 | 13119.8 | 12963.6 | 12234.1 | 13055.3 | 12134.6 | 12843.5 | 12287.4 | 12753.3 | 11437.8 | 12902 | 12169.3 | 12215 | 12182.5 | 12150.2 | 10521.6 | 12081.3 | 10789.9 | 12085.7 | 12122.7 | 13445.1 | 12304.5 | 13497.1 | 12515.1 | 13405 | 12366 | 12516.2 | 12302 | 13254.3 | 13534 | 13479.4 | 13393.9 | 13430.8 | 13436.3 | 12619 | 13457 | 13522.6 | 13528.9 | 13530.3 | 13514 | 13555 | 12654.3 | 13596.2 | 12690.5 | 33.25 | 32.96 | 33.37 | 33.41 | 33.19 | 32.86 | 0 | 48.65 | 0 | 0 | 48.33 | 48.46 | 2.56 | 1.55 | 2.73 | 0.45 | 1.96 | 1.83 | 6.63 | 6.3 | 7.31 | 6.43 | 6.34 | 6.4 | 6.98 | 7.06 | 7.08 | 0 | 7.09 | 7.13 | 1.8 | 1.87 | 1.68 | 2.12 | 2.08 | 1.84 | 7.71 | 7.77 | 7.68 | 0 | 7.73 | 7.75 | 0.4 | 0.44 | 0.37 | 0.38 | 0.37 | 0.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 888929 | 1664 | 875861 | 1682 | 69952.072 | 168.133 | 6.98 | 7.06 | 7.08 | 0 | 7.09 | 7.13 | 7.71 | 7.77 | 7.68 | 0 | 7.73 | 7.75 | 1012000 | 0 | 1008000 | 0 | 2014000 | 2466 | 2020000 | 2011534 | 12.0167 | 7.068 | 1.8983 | 7.728 | 0.39667 | 26.86% | 5.133% | 33.1733 | 48.48 | 1.8467 | 6.5683 | 2027271.1 | 2002067 | 2462511.3693 | 81.3% | 24 | 0
2025-03-23 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 335090.89 | 6:58 | 18:56 | 12196 | 12615 | 12605 | 12598 | 12688 | 12704 | 12636 | 13018 | 12664 | 12669 | 12568 | 12721 | 12631 | 12651 | 12629 | 12703 | 12545 | 12640 | 12697 | 12758 | 12685 | 12709 | 12494 | 12599 | 12446 | 11032 | 12464 | 12429 | 12710 | 12568 | 12508 | 12698 | 12812 | 12888 | 12914 | 12815 | 12777 | 12628 | 12622 | 12574 | 13404 | 12415 | 13274 | 12245 | 12790 | 13788 | 12191 | 13388 | 12570 | 12774 | 12730 | 12149 | 13044 | 12612 | 12999 | 12693 | 11787 | 13169 | 11799 | 13149 | 13065 | 11807 | 12746 | 12256 | 12455 | 11818 | 12428 | 12835 | 13068 | 12066 | 12943 | 11613 | 0 | 11411 | 11830 | 12929 | 11689 | 13089 | 11840 | 12929 | 12170 | 12903 | 12239 | 13223 | 12121 | 12727 | 12051 | 10668 | 12844 | 12530 | 11794 | 13200 | 12862 | 12041 | 11890 | 12996 | 11865 | 12311 | 13116 | 11888 | 13147 | 11850 | 12928 | 12104 | 12979 | 11478 | 13064 | 12065 | 12933 | 11983 | 12961 | 12231 | 11890 | 12876 | 12070 | 11816 | 12945 | 13069 | 12895 | 12025 | 13003 | 11907 | 12759 | 12086 | 12654 | 11140 | 12806 | 11918 | 12020 | 12008 | 11944 | 10273 | 11812 | 10455 | 11879 | 11910 | 13415 | 12128 | 13471 | 12365 | 13371 | 12190 | 12365 | 12136 | 13196 | 13526 | 13434 | 13351 | 13383 | 13396 | 12478 | 13417 | 13489 | 13501 | 13506 | 13478 | 13528 | 12502 | 13568 | 12557 | 33.2 | 32.75 | 33.39 | 33.2 | 32.99 | 33.03 | 0 | 48.99 | 0 | 0 | 48.7 | 48.34 | 2.4 | 0.96 | 2.36 | 0.41 | 2.04 | 1.7 | 5.97 | 6.14 | 6.8 | 5.51 | 6.2 | 6.77 | 6.84 | 6.9 | 6.93 | 6.81 | 6.92 | 6.93 | 1.76 | 1.83 | 1.64 | 2.2 | 2.02 | 1.78 | 7.54 | 7.56 | 7.5 | 7.52 | 7.52 | 7.51 | 0.39 | 0.43 | 0.37 | 0.38 | 0.37 | 0.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 889918 | 1666 | 876859 | 1684 | 71934.3 | 172.7 | 6.84 | 6.9 | 6.93 | 6.81 | 6.92 | 6.93 | 7.54 | 7.56 | 7.5 | 7.52 | 7.52 | 7.51 | 989000 | 2000 | 998000 | 2000 | 1982228 | 4567 | 1983000 | 1977661 | 11.9667 | 6.8883 | 1.8717 | 7.525 | 0.39333 | 27.17% | 5.227% | 33.0933 | 48.6767 | 1.645 | 6.2317 | 1995168 | 1970260 | 2398792.3132 | 82.14% | 25 | 6
2025-03-24 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 335090.89 | 6:59 | 18:58 | 12304 | 12737 | 12721 | 12699 | 12810 | 12803 | 12779 | 13103 | 12748 | 12746 | 12658 | 12796 | 12744 | 12738 | 12749 | 12805 | 12652 | 12737 | 12794 | 12868 | 12775 | 12803 | 12604 | 12702 | 12560 | 11149 | 12574 | 12540 | 12808 | 12668 | 12609 | 12789 | 12895 | 12957 | 12730 | 12731 | 12873 | 12733 | 12719 | 12660 | 13463 | 12526 | 13337 | 12356 | 12875 | 13819 | 12293 | 13442 | 12663 | 12872 | 12826 | 12245 | 13125 | 12716 | 13081 | 12785 | 11896 | 13259 | 11896 | 13228 | 13138 | 11901 | 12874 | 12407 | 12559 | 11923 | 12536 | 12926 | 13144 | 12159 | 13020 | 11701 | 0 | 12581 | 11925 | 13002 | 11772 | 13166 | 11931 | 13009 | 12262 | 12974 | 12355 | 13288 | 12234 | 12833 | 12145 | 10762 | 12937 | 12621 | 11892 | 13276 | 12983 | 12214 | 12081 | 13063 | 11967 | 12421 | 13197 | 11993 | 13210 | 11961 | 13018 | 12225 | 13055 | 11589 | 13141 | 12170 | 13017 | 12085 | 13062 | 12339 | 11998 | 12978 | 12183 | 11938 | 13030 | 13153 | 12981 | 12127 | 13081 | 12004 | 12855 | 12194 | 12746 | 11229 | 12894 | 12019 | 12173 | 12177 | 12030 | 10394 | 11896 | 10524 | 11983 | 12023 | 13471 | 12232 | 13521 | 12477 | 13426 | 12302 | 12475 | 12265 | 13266 | 13578 | 13495 | 13407 | 13440 | 13457 | 12588 | 13475 | 13547 | 13548 | 13551 | 13528 | 13573 | 12605 | 13625 | 12655 | 35.12 | 34.87 | 35.32 | 35.24 | 35.21 | 35.25 | 0 | 48.99 | 0 | 0 | 48.98 | 49.16 | 3.67 | 2.26 | 3.53 | 1.65 | 2.9 | 3.5 | 8.55 | 6.85 | 6.5 | 8.37 | 6.24 | 7.73 | 6.9 | 6.99 | 7.01 | 6.88 | 6.9 | 7.02 | 1.8 | 1.87 | 1.67 | 2.25 | 1.99 | 1.82 | 7.6 | 7.64 | 7.55 | 7.57 | 7.56 | 7.58 | 0.4 | 0.45 | 0.38 | 0.39 | 0.39 | 0.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 890915 | 1667 | 877863 | 1686 | 73932.1 | 177.3 | 6.9 | 6.99 | 7.01 | 6.88 | 6.9 | 7.02 | 7.6 | 7.64 | 7.55 | 7.57 | 7.56 | 7.58 | 997000 | 1000 | 1004000 | 2000 | 1997800 | 4600 | 1998000 | 1993200 | 11.9833 | 6.95 | 1.9 | 7.5833 | 0.40667 | 27.34% | 5.363% | 35.1683 | 49.0433 | 2.9183 | 7.3733 | 2010734 | 1985667 | 2412403.5 | 82.31% | 23 | 0
2025-03-25 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 335090.89 | 6:55 | 18:59 | 12111 | 12544 | 12516 | 12499 | 12603 | 12620 | 12604 | 12901 | 12556 | 12586 | 12455 | 12600 | 12541 | 12530 | 12537 | 12595 | 12447 | 12533 | 12586 | 12652 | 12570 | 12598 | 12407 | 12499 | 12353 | 10973 | 12372 | 12338 | 12602 | 12459 | 12397 | 12584 | 12775 | 12823 | 12855 | 12773 | 12670 | 12525 | 12526 | 12473 | 13236 | 12309 | 13111 | 12148 | 12668 | 13627 | 12097 | 13223 | 12460 | 12673 | 12617 | 12044 | 12918 | 12515 | 12871 | 12577 | 11719 | 13045 | 11726 | 13017 | 12928 | 11734 | 12706 | 12250 | 12390 | 11771 | 12350 | 12739 | 12955 | 11989 | 12840 | 11545 | 12533 | 12406 | 11787 | 12816 | 11617 | 12975 | 11775 | 12827 | 12083 | 12789 | 12174 | 13095 | 12049 | 12647 | 11986 | 10620 | 12770 | 12446 | 11737 | 13107 | 12816 | 12069 | 11945 | 12861 | 11812 | 12245 | 13019 | 11825 | 13027 | 11790 | 12824 | 12067 | 12867 | 11426 | 12950 | 11994 | 12836 | 11934 | 12883 | 12159 | 11834 | 12793 | 12003 | 11779 | 12840 | 12961 | 12791 | 11957 | 12890 | 11833 | 12653 | 12011 | 12542 | 11070 | 12697 | 11851 | 11999 | 12015 | 11848 | 10241 | 11756 | 10356 | 11832 | 11867 | 13278 | 12042 | 13324 | 12280 | 13235 | 12114 | 12291 | 12079 | 13059 | 13372 | 13288 | 13208 | 13238 | 13256 | 12385 | 13274 | 13348 | 13353 | 13357 | 13335 | 13375 | 12403 | 13421 | 12456 | 33.84 | 33.7 | 34.03 | 33.92 | 33.99 | 34.13 | 0 | 46.28 | 0 | 0 | 46.8 | 46.85 | 5.26 | 4.38 | 5.2 | 4.34 | 5.45 | 5.14 | 9.68 | 11.58 | 9.76 | 10.81 | 10.3 | 9.88 | 6.77 | 6.84 | 6.84 | 6.73 | 6.84 | 6.86 | 1.79 | 1.83 | 1.66 | 2.23 | 2.04 | 1.78 | 7.4 | 7.43 | 7.34 | 7.38 | 7.38 | 7.37 | 0.41 | 0.46 | 0.38 | 0.4 | 0.39 | 0.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 891907 | 1668 | 878854 | 1688 | 75913.1 | 181.8 | 6.77 | 6.84 | 6.84 | 6.73 | 6.84 | 6.86 | 7.4 | 7.43 | 7.34 | 7.38 | 7.38 | 7.37 | 992000 | 1000 | 991000 | 2000 | 1981000 | 4500 | 1980000 | 1976500 | 12.0667 | 6.8133 | 1.8883 | 7.3833 | 0.41333 | 27.72% | 5.598% | 33.935 | 46.6433 | 4.9617 | 10.335 | 1994164 | 1960933 | 2372607.1 | 82.65% | 26 | 0
2025-03-26 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 335090.89 | 6:52 | 18:58 | 12169 | 12583 | 12552 | 12513 | 12635 | 12661 | 12629 | 12968 | 12587 | 12612 | 12491 | 12630 | 12578 | 12557 | 12583 | 12629 | 12485 | 12574 | 12614 | 12677 | 12600 | 12627 | 12457 | 12536 | 12380 | 11063 | 12398 | 12371 | 12624 | 12488 | 12443 | 12603 | 12809 | 12851 | 12900 | 12836 | 12693 | 12558 | 12558 | 12511 | 13263 | 12357 | 13123 | 12196 | 12711 | 13675 | 12150 | 13246 | 12501 | 12717 | 12650 | 12123 | 12950 | 12559 | 12897 | 12620 | 11809 | 13043 | 11847 | 13032 | 12937 | 11824 | 12705 | 12261 | 12427 | 11846 | 12378 | 12729 | 12965 | 12028 | 12840 | 11636 | 12558 | 12418 | 11857 | 12802 | 11698 | 12968 | 11844 | 12820 | 12098 | 12756 | 12181 | 13069 | 12057 | 12617 | 12007 | 10669 | 12775 | 12452 | 11817 | 13120 | 12809 | 12101 | 11981 | 12879 | 11875 | 12268 | 13018 | 11871 | 13043 | 11858 | 12834 | 12117 | 12868 | 11527 | 12946 | 12044 | 12846 | 11995 | 12889 | 12216 | 11880 | 12779 | 12044 | 11858 | 12842 | 12952 | 12794 | 12008 | 12888 | 11900 | 12657 | 12061 | 12592 | 11193 | 12707 | 11933 | 12036 | 12042 | 11904 | 10318 | 11849 | 10454 | 11936 | 11944 | 13261 | 12068 | 13314 | 12288 | 13216 | 12132 | 12297 | 12117 | 13037 | 13336 | 13273 | 13194 | 13228 | 13248 | 12388 | 13254 | 13327 | 13331 | 13328 | 13307 | 13348 | 12405 | 13407 | 12468 | 32.49 | 32.22 | 32.55 | 32.2 | 32.06 | 32.5 | 0 | 44.11 | 0 | 0 | 44.3 | 44.38 | 7.19 | 7.24 | 7.17 | 6.94 | 7.08 | 7.53 | 13.25 | 13.7 | 12.5 | 12.35 | 12.95 | 12.78 | 6.77 | 6.86 | 6.85 | 6.7 | 6.83 | 6.86 | 1.79 | 1.83 | 1.67 | 2.22 | 2.03 | 1.77 | 7.38 | 7.42 | 7.33 | 7.34 | 7.37 | 7.35 | 0.41 | 0.46 | 0.39 | 0.41 | 0.39 | 0.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 892902 | 1670 | 879846 | 1689 | 77898.7 | 186.2 | 6.77 | 6.86 | 6.85 | 6.7 | 6.83 | 6.86 | 7.38 | 7.42 | 7.33 | 7.34 | 7.37 | 7.35 | 995000 | 2000 | 992000 | 1000 | 1985600 | 4400 | 1984000 | 1981200 | 12.1 | 6.8117 | 1.885 | 7.365 | 0.41667 | 27.67% | 5.657% | 32.3367 | 44.2633 | 7.1917 | 12.9217 | 1998789 | 1968667 | 2410399.1118 | 81.67% | 28 | 0
2025-03-27 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 335090.89 | 6:53 | 19:00 | 12673.4 | 13035.8 | 13006.1 | 12960.8 | 13084.1 | 13097.9 | 13066.5 | 13349.8 | 13021.6 | 13039.3 | 12945.8 | 13053.1 | 13031.6 | 13008.2 | 13051.8 | 13093.9 | 12942 | 13019.4 | 13055.1 | 13140.2 | 13037.4 | 13070 | 12925.7 | 12989.2 | 12852.1 | 11790 | 12883 | 12848.4 | 13070.5 | 12951.6 | 12907.3 | 13043.8 | 13416.7 | 13467 | 13482 | 13418 | 13115.7 | 13004.7 | 12985.4 | 12948.7 | 13633.4 | 12858.7 | 13500 | 12722.9 | 13160.1 | 14013.5 | 12638.7 | 13611.8 | 12969.6 | 13170.4 | 13119.1 | 12665.3 | 13373.2 | 13011.9 | 13329.8 | 13063.6 | 12405 | 13460.6 | 12452.9 | 13454 | 13376.6 | 12413 | 13146.6 | 12763.1 | 12883.1 | 12413.7 | 12871.3 | 13175.4 | 13366 | 12572.9 | 13274.5 | 12283.4 | 13025.8 | 12923.6 | 12441.3 | 13247 | 12324.7 | 13400.5 | 12434.9 | 13272.5 | 12639.4 | 13212.8 | 12705.6 | 13480.8 | 12605.5 | 13089 | 12526.1 | 11385.8 | 13199.1 | 12926.3 | 12393.9 | 13495.9 | 13223.6 | 12611.2 | 12497.4 | 13284.1 | 12454.1 | 12769.2 | 13409.5 | 12444.6 | 13440.1 | 12432.8 | 13271.1 | 12648.3 | 13281.9 | 12170.8 | 13366.1 | 12582.5 | 13287 | 12542.3 | 13309.9 | 12749.3 | 12460.3 | 13226.6 | 12581.4 | 12437.7 | 13269.9 | 13386.8 | 13229.7 | 12576.4 | 13314.9 | 12483.9 | 13110.1 | 12612.8 | 13039 | 11917.9 | 13174 | 12532.2 | 12590.3 | 12571.9 | 12494.4 | 11021 | 12437.6 | 11253.8 | 12485.7 | 12507.8 | 13636.2 | 12592.9 | 13686.4 | 12795.4 | 13593.1 | 12648.5 | 12787.3 | 12663.6 | 13455.1 | 13707.7 | 13661.9 | 13583.7 | 13610.7 | 13622.6 | 12889.7 | 13642.4 | 13701.6 | 13699 | 13706.8 | 13697 | 13727.9 | 12908.1 | 13774.3 | 12944.9 | 29.3668 | 28.8091 | 29.0778 | 29.2686 | 29.6542 | 29.044 | 0 | 41.7937 | 0 | 0 | 41.7 | 41.1729 | 5.5163 | 5.463 | 5.3565 | 4.4693 | 5.473 | 5.3465 | 9.5983 | 9.7333 | 9.5533 | 8.9567 | 9.04 | 8.5783 | 7.1995 | 7.2644 | 7.2833 | 7.1691 | 7.2821 | 7.3163 | 1.903 | 1.981 | 1.7819 | 2.3697 | 2.1963 | 1.9263 | 7.8238 | 7.8767 | 7.7909 | 7.7956 | 7.8145 | 7.8329 | 0.4642 | 0.51705 | 0.4392 | 0.46006 | 0.43964 | 0.49265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 893935 | 1671 | 880877 | 1691 | 79960.34 | 190.667 | 7.1995 | 7.2644 | 7.2833 | 7.1691 | 7.2821 | 7.3163 | 7.8238 | 7.8767 | 7.7909 | 7.7956 | 7.8145 | 7.8329 | 1033000 | 1000 | 1031000 | 2000 | 2061640 | 4467 | 2061000 | 2057173 | 12.1167 | 7.2524 | 2.0264 | 7.8224 | 0.4688 | 27.94% | 5.993% | 29.2034 | 41.5555 | 5.2708 | 9.2433 | 2075996.9 | 2046867 | 2557962.2152 | 80.02% | 29 | 305
2025-03-28 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 335090.89 | 6:46 | 18:59 | 13032.7 | 13381.8 | 13342 | 13296.1 | 13419.4 | 13448.6 | 13425.4 | 13671.1 | 13360.1 | 13391.8 | 13291.1 | 13388.5 | 13379.5 | 13344.9 | 13398.8 | 13447.4 | 13280.8 | 13359.7 | 13413.7 | 13502.9 | 13391.2 | 13425.3 | 13286.6 | 13347.6 | 13220.3 | 12222.4 | 13255.8 | 13211.2 | 13433.6 | 13298.6 | 13260.5 | 13363 | 13806 | 13866.2 | 13890.7 | 13827.9 | 13487.7 | 13380.9 | 13354.9 | 13308 | 13990.8 | 13240.4 | 13855.5 | 13102.9 | 13531.9 | 14349.4 | 13007.2 | 13962.3 | 13320.3 | 13515.2 | 13469.7 | 13026.1 | 13711.6 | 13352.3 | 13679.9 | 13425.6 | 12790.2 | 13816.1 | 12837.3 | 13800.1 | 13728.8 | 12796.2 | 13514.2 | 13151 | 13242.5 | 12795.7 | 13254.5 | 13546.2 | 13722 | 12965.2 | 13637.1 | 12701.2 | 13386.8 | 13301.6 | 12834 | 13607.1 | 12729.6 | 13751.6 | 12831.5 | 13632.6 | 13035.1 | 13599 | 13103.8 | 13848.5 | 12999.9 | 13475.4 | 12884.7 | 11863.4 | 13546.1 | 13298.8 | 12792.7 | 13849.4 | 13602.4 | 13006.3 | 12883.4 | 13622.6 | 12824.5 | 13151.3 | 13752.8 | 12830.9 | 13795.7 | 12818 | 13634.2 | 13025.1 | 13634.6 | 12565.6 | 13719.1 | 12961.6 | 13631.9 | 12900.6 | 13642.3 | 13123 | 12852.5 | 13580.6 | 12965 | 12821.3 | 13609.4 | 13740.7 | 13577 | 12960 | 13664.7 | 12861.7 | 13458.6 | 12989.4 | 13361.3 | 12316.3 | 13526.8 | 12908.9 | 12939.9 | 12903.7 | 12878.1 | 11408.8 | 12776.4 | 11667 | 12807.1 | 12846.1 | 13992.4 | 12972.3 | 14042.2 | 13173.7 | 13938.4 | 13027.1 | 13158 | 13011 | 13819.7 | 14063.9 | 14025.3 | 13946.1 | 13969.3 | 13978.4 | 13273.7 | 14002.2 | 14078 | 14062.8 | 14073.3 | 14051.1 | 14091 | 13292.2 | 14135.4 | 13325.7 | 26.68 | 26.51 | 26.86 | 26.91 | 26.71 | 26.57 | 0 | 40.6 | 0 | 0 | 40.8 | 39.84 | 3.38 | 1.03 | 3.25 | 0.69 | 3.28 | 2.67 | 6.26 | 6.72 | 5.96 | 5.89 | 7.6 | 7.79 | 7.52 | 7.59 | 7.6 | 7.49 | 7.6 | 7.63 | 2 | 2.09 | 1.86 | 2.47 | 2.3 | 2.03 | 8.18 | 8.22 | 8.13 | 8.16 | 8.14 | 8.15 | 0.49 | 0.54 | 0.46 | 0.48 | 0.46 | 0.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 895000 | 1673 | 881937 | 1693 | 82079.073 | 195.4 | 7.52 | 7.59 | 7.6 | 7.49 | 7.6 | 7.63 | 8.18 | 8.22 | 8.13 | 8.16 | 8.14 | 8.15 | 1065000 | 2000 | 1060000 | 2000 | 2118733 | 4733 | 2121000 | 2114000 | 12.2167 | 7.5717 | 2.125 | 8.1633 | 0.49 | 28.07% | 6.002% | 26.7067 | 40.4133 | 2.3833 | 6.7033 | 2134476.1 | 2102200 | 2654761 | 79.19% | 26 | 1946
2025-03-29 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 335090.89 | 6:49 | 19:01 | 11405 | 11864.2 | 11835.7 | 11832.4 | 11887 | 11918.9 | 11927.6 | 12225 | 11847.4 | 11910.1 | 11717.5 | 11851.1 | 11819.7 | 11803.1 | 11800.6 | 11891 | 11713.9 | 11823.5 | 11880.4 | 11938.3 | 11881.2 | 11887.1 | 11677.4 | 11778.9 | 11623.4 | 10369.6 | 11645.4 | 11593.6 | 11907.2 | 11743.2 | 11686.9 | 11890 | 11927.7 | 12018.9 | 12040.1 | 11968.5 | 11982 | 11828.7 | 11826.6 | 11751 | 12576.8 | 11542.2 | 12452.3 | 11372.7 | 11980.4 | 13041.7 | 11326.7 | 12591.3 | 11767.4 | 11985.5 | 11908 | 11317 | 12235.8 | 11802.8 | 12208 | 11902 | 11008.5 | 12390.1 | 11043.8 | 12354.8 | 12271.7 | 11036.3 | 11981 | 11473.3 | 11621.4 | 11002 | 11595.4 | 11996.3 | 12279.2 | 11213.6 | 12123.5 | 10841.3 | 11824.3 | 11636.1 | 11064.8 | 12111.6 | 10912.6 | 12296.2 | 11046.5 | 12153.7 | 11269.7 | 12029.2 | 11352.3 | 12366.3 | 11235.6 | 11855.2 | 11185.5 | 9988.5 | 12041.1 | 11653.3 | 10982.1 | 12398.2 | 12088.6 | 11283.9 | 11155.5 | 12094.6 | 11015 | 11421.1 | 12277.7 | 11022.8 | 12314 | 10998.9 | 12061.9 | 11244.1 | 12143.5 | 10712.1 | 12209.9 | 11183 | 12072.7 | 11113.3 | 12085.9 | 11328.8 | 11045.3 | 12005.5 | 11181.6 | 10967.3 | 12089.3 | 12193.6 | 12015 | 11150.4 | 12120.6 | 11026.6 | 11847.3 | 11188.1 | 11707.7 | 10380.2 | 11886.7 | 11028.3 | 11102.2 | 11101.5 | 11030.4 | 9585.4 | 10884.2 | 9738.1 | 10943.8 | 11009.2 | 12487.8 | 11149.7 | 12564.5 | 11424.4 | 12444.5 | 11263.7 | 11422.4 | 11208.6 | 12250.5 | 12593.1 | 12477.7 | 12418.5 | 12435.2 | 12454 | 11538.3 | 12499.6 | 12590.9 | 12583.8 | 12616.9 | 12575.2 | 12610.9 | 11547.8 | 12627.3 | 11599.2 | 27.8967 | 27.2073 | 27.5767 | 27.5325 | 27.2431 | 27.0791 | 0 | 38.1182 | 0 | 0 | 38 | 37.4 | 4.0677 | 1.7364 | 3.7344 | 1.9543 | 3.9618 | 3.4696 | 8.2333 | 7.7417 | 7.3817 | 7.59 | 8.5533 | 7.1983 | 6.2653 | 6.3025 | 6.3111 | 6.2222 | 6.2411 | 6.2665 | 1.6868 | 1.683 | 1.5547 | 2.0711 | 1.8486 | 1.6095 | 6.7001 | 6.6925 | 6.6546 | 6.6738 | 6.6046 | 6.5557 | 0.44734 | 0.49968 | 0.42221 | 0.45585 | 0.42803 | 0.47134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 895938 | 1674 | 882865 | 1694 | 83940.34 | 199.2 | 6.2653 | 6.3025 | 6.3111 | 6.2222 | 6.2411 | 6.2665 | 6.7001 | 6.6925 | 6.6546 | 6.6738 | 6.6046 | 6.5557 | 938000 | 1000 | 928000 | 1000 | 1861267 | 3800 | 1864000 | 1857467 | 12.2 | 6.2681 | 1.7423 | 6.6469 | 0.45407 | 27.8% | 6.831% | 27.4226 | 37.8394 | 3.154 | 7.7831 | 1874005.5 | 1835730 | 2179791.1702 | 84.22% | 24 | 14459
2025-03-30 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 335090.89 | 6:46 | 19:03 | 12862.9 | 13270.4 | 13211.4 | 13208.7 | 13276.1 | 13308 | 13305.5 | 13618.3 | 13242.3 | 13258.8 | 13157.4 | 13257.1 | 13248.2 | 13204.6 | 13181.5 | 13305.7 | 13127.4 | 13224 | 13273.7 | 13345.8 | 13264.6 | 13295.3 | 13115 | 13196.6 | 13070.3 | 11914.6 | 13093.5 | 13049.7 | 13278.4 | 13135.4 | 13113.1 | 13270.6 | 13568 | 13654.3 | 13689 | 13619.9 | 13367.4 | 13236.6 | 13218.6 | 13155.2 | 13917.1 | 13083.3 | 13781.1 | 12934.1 | 13401.1 | 14308.6 | 12858.3 | 13905.3 | 13179.5 | 13380.3 | 13339.5 | 12870.2 | 13599.2 | 13228.1 | 13563.4 | 13296.8 | 12573.7 | 13717 | 12615 | 13700 | 13619.9 | 12584.5 | 13366.9 | 12961.2 | 13104.5 | 12589.1 | 13087.3 | 13423.6 | 13623.5 | 12772.1 | 13528.6 | 12457.1 | 13253.2 | 13150.3 | 12632.2 | 13499.7 | 12507.2 | 13649.8 | 12625.2 | 13519.3 | 12868 | 13484.5 | 12922.4 | 13764.7 | 12827.4 | 13339.9 | 12743.7 | 11509.1 | 13447.5 | 13130 | 12582.4 | 13764.6 | 13467.6 | 12800.4 | 12654.3 | 13526.8 | 12580.4 | 12973.4 | 13669.7 | 12629.2 | 13689.8 | 12617.9 | 13516.9 | 12854.3 | 13534.5 | 12333 | 13613.8 | 12780.7 | 13506.9 | 12715 | 13521.2 | 12947.1 | 12654.5 | 13453.7 | 12795.8 | 12606.5 | 13507.5 | 13630.8 | 13469.1 | 12767.9 | 13558.6 | 12662.2 | 13339.6 | 12808.4 | 13225.6 | 11988.2 | 13396.9 | 12701.5 | 12750.8 | 12723.9 | 12665.9 | 11064 | 12516.1 | 11238.9 | 12619.1 | 12656.9 | 13920.8 | 12804.8 | 13982.7 | 13032.4 | 13869 | 12858.4 | 13009 | 12807.1 | 13730 | 14007.6 | 13951.7 | 13861.7 | 13893.6 | 13906.4 | 13142.3 | 13940.2 | 14000.9 | 13995.9 | 14005.4 | 13983.6 | 14031.3 | 13148.9 | 14065.5 | 13187.4 | 30.54 | 30.26 | 30.83 | 30.85 | 30.48 | 30.32 | 0 | 46.61 | 0 | 0 | 46.8 | 46.12 | 2.14 | 0.03 | 1.93 | 0.04 | 1.27 | 1.79 | 7.92 | 1.88 | 4.33 | 3.23 | 5.49 | 4.18 | 7.46 | 7.53 | 7.53 | 7.42 | 7.53 | 7.56 | 1.97 | 2.04 | 1.82 | 2.43 | 2.25 | 1.97 | 8.07 | 8.12 | 8.02 | 8.04 | 8.04 | 8.04 | 0.46 | 0.5 | 0.43 | 0.45 | 0.42 | 0.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 896989 | 1675 | 883913 | 1695 | 86036.007 | 200.2 | 7.46 | 7.53 | 7.53 | 7.42 | 7.53 | 7.56 | 8.07 | 8.12 | 8.02 | 8.04 | 8.04 | 8.04 | 1051000 | 1000 | 1048000 | 1000 | 2095667 | 1000 | 2097000 | 2094667 | 12.2833 | 7.505 | 2.08 | 8.055 | 0.45667 | 27.71% | 5.669% | 30.5467 | 46.51 | 1.2 | 4.505 | 2110656.8 | 2082533 | 2575642.1657 | 80.85% | 28 | 0
2025-03-31 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 335090.89 | 6:45 | 19:02 | 12745.4 | 13165.1 | 13114.1 | 13102.9 | 13184.5 | 13203.4 | 13186.9 | 13540.4 | 13096.3 | 13090.5 | 13008.8 | 13102 | 13103.7 | 13043.5 | 13008.3 | 13147.6 | 13016.4 | 13123 | 13180.1 | 13245.1 | 13173.3 | 13203.2 | 13019.1 | 13108.3 | 12970.4 | 11729.7 | 12995.6 | 12955.3 | 13189.4 | 13038.5 | 13022.1 | 13186.9 | 13444.7 | 13528.7 | 13574.5 | 13499.5 | 13273.6 | 13131.9 | 13112.6 | 13054.2 | 13844.8 | 12964.1 | 13706.5 | 12797.9 | 13280.4 | 14224.8 | 12728.1 | 13833.8 | 13064.5 | 13277.7 | 13225.8 | 12756.3 | 13510.5 | 13131.2 | 13482.6 | 13209.4 | 12429 | 13625.7 | 12451.1 | 13615.9 | 13527.3 | 12437.1 | 13232.9 | 12809 | 12980.1 | 12453.2 | 12970.9 | 13318.8 | 13514.1 | 12642.6 | 13427.4 | 12308.6 | 13144 | 13037 | 12500 | 13402 | 12366 | 13568 | 12486 | 13425 | 12749.9 | 13387.5 | 12805.5 | 13686.6 | 12702.8 | 13234.1 | 12612.4 | 11325.6 | 13350.5 | 13037 | 12455.8 | 13684 | 13368.6 | 12671.7 | 12524.6 | 13470.3 | 12485.1 | 12875.5 | 13592 | 12509.1 | 13612.4 | 12496.7 | 13424.5 | 12726.6 | 13443.6 | 12170.5 | 13522 | 12646.2 | 13413.5 | 12583.7 | 13428.5 | 12812.9 | 12527.2 | 13357.5 | 12668.5 | 12464.1 | 13425.9 | 13539.8 | 13380.1 | 12630.2 | 13466.2 | 12521.7 | 13250.4 | 12672.6 | 13139.5 | 11791.7 | 13291.3 | 12554.1 | 12631 | 12619.6 | 12504.6 | 10891.5 | 12365.5 | 11038.2 | 12499.3 | 12531.3 | 13853.7 | 12678.4 | 13914.8 | 12911.2 | 13806 | 12731 | 12891.3 | 12694.8 | 13645.4 | 13942.7 | 13875 | 13781.7 | 13818.7 | 13831.9 | 13019.7 | 13862.7 | 13920.9 | 13920.7 | 13942.5 | 13919 | 13965.5 | 13027.7 | 13986.2 | 13068.1 | 32.23 | 31.81 | 32.5 | 32.29 | 32.06 | 31.79 | 0 | 48.09 | 0 | 0 | 48.2 | 48.06 | 2.27 | 0.04 | 2 | 0.14 | 1.87 | 1.84 | 5.35 | 3.88 | 5.24 | 5.08 | 5.81 | 5.79 | 7.4 | 7.46 | 7.48 | 7.38 | 7.5 | 7.52 | 1.94 | 2.04 | 1.8 | 2.41 | 2.24 | 1.96 | 7.98 | 8.04 | 7.94 | 7.97 | 7.97 | 7.97 | 0.45 | 0.49 | 0.42 | 0.44 | 0.42 | 0.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 898030 | 1675 | 884953 | 1695 | 88115.007 | 202.2 | 7.4 | 7.46 | 7.48 | 7.38 | 7.5 | 7.52 | 7.98 | 8.04 | 7.94 | 7.97 | 7.97 | 7.97 | 1041000 | 0 | 1040000 | 0 | 2079000 | 2000 | 2081000 | 2077000 | 12.2833 | 7.4567 | 2.065 | 7.9783 | 0.44833 | 27.69% | 5.619% | 32.1133 | 48.1167 | 1.36 | 5.1917 | 2092910.7 | 2077000 | 2531276.7748 | 82.05% | 27 | 0
2025-04-01 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 335090.89 | 6:44 | 19:03 | 12862.9 | 13270.4 | 13211.4 | 13208.7 | 13276.1 | 13308 | 13305.5 | 13618.3 | 13242.3 | 13258.8 | 13157.4 | 13257.1 | 13248.2 | 13204.6 | 13181.5 | 13305.7 | 13127.4 | 13224 | 13273.7 | 13345.8 | 13264.6 | 13295.3 | 13115 | 13196.6 | 13070.3 | 11914.6 | 13093.5 | 13049.7 | 13278.4 | 13135.4 | 13113.1 | 13270.6 | 13568 | 13654.3 | 13689 | 13619.9 | 13367.4 | 13236.6 | 13218.6 | 13155.2 | 13917.1 | 13083.3 | 13781.1 | 12934.1 | 13401.1 | 14308.6 | 12858.3 | 13905.3 | 13179.5 | 13380.3 | 13339.5 | 12870.2 | 13599.2 | 13228.1 | 13563.4 | 13296.8 | 12573.7 | 13717 | 12374 | 13561 | 13619.9 | 12584.5 | 13366.9 | 12961.2 | 13104.5 | 12589.1 | 13087.3 | 13423.6 | 13623.5 | 12772.1 | 13528.6 | 12457.1 | 13253.2 | 13150.3 | 12632.2 | 13499.7 | 12507.2 | 13649.8 | 12625.2 | 13519.3 | 12868 | 13484.5 | 12922.4 | 13764.7 | 12827.4 | 13339.9 | 12743.7 | 11509.1 | 13447.5 | 13130 | 12582.4 | 13764.6 | 13467.6 | 12800.4 | 12654.3 | 13526.8 | 12580.4 | 12973.4 | 13669.7 | 12629.2 | 13689.8 | 12617.9 | 13516.9 | 12854.3 | 13534.5 | 12333 | 13613.8 | 12780.7 | 13506.9 | 12715 | 13521.2 | 12947.1 | 12654.5 | 13453.7 | 12795.8 | 12606.5 | 13507.5 | 13630.8 | 13469.1 | 12767.9 | 13558.6 | 12662.2 | 13339.6 | 12808.4 | 13225.6 | 11988.2 | 13396.9 | 12701.5 | 12750.8 | 12723.9 | 12665.9 | 11064 | 12516.1 | 11238.9 | 12619.1 | 12656.9 | 13920.8 | 12804.8 | 13982.7 | 13032.4 | 13869 | 12858.4 | 13009 | 12807.1 | 13730 | 14007.6 | 13951.7 | 13861.7 | 13893.6 | 13906.4 | 13142.3 | 13940.2 | 14000.9 | 13995.9 | 14005.4 | 13983.6 | 14031.3 | 13148.9 | 14065.5 | 13187.4 | 33.0599 | 32.6821 | 33.2769 | 32.9932 | 32.8515 | 32.7131 | 0 | 48.3534 | 0 | 0 | 48.4 | 48.1454 | 2.6608 | 0.13551 | 2.3783 | 0.28445 | 2.476 | 2.1976 | 7.2217 | 5.5067 | 5.145 | 5.2683 | 5.8067 | 5.8917 | 7.3232 | 7.3855 | 7.3835 | 7.2819 | 7.4101 | 7.425 | 1.9169 | 2.0032 | 1.787 | 2.3888 | 2.2133 | 1.94 | 7.8845 | 7.9126 | 7.81 | 7.8537 | 7.8532 | 7.8459 | 0.44696 | 0.49158 | 0.42164 | 0.44496 | 0.41819 | 0.47153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 899066 | 1677 | 885986 | 1697 | 90182.34 | 206.667 | 7.3232 | 7.3855 | 7.3835 | 7.2819 | 7.4101 | 7.425 | 7.8845 | 7.9126 | 7.81 | 7.8537 | 7.8532 | 7.8459 | 1036000 | 2000 | 1033000 | 2000 | 2067333 | 4467 | 2065000 | 2062866 | 12.3167 | 7.3682 | 2.0415 | 7.86 | 0.44914 | 27.71% | 5.714% | 32.9295 | 48.2996 | 1.6888 | 5.8067 | 2110276.8 | 2041801 | 2527658.6136 | 80.78% | 29 | 0
2025-04-02 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 335090.89 | 6:45 | 19:03 | 12608.9 | 13011.2 | 12979.5 | 12981.2 | 13047.9 | 13081.2 | 13069.5 | 13373 | 13011.7 | 13017.2 | 12905.4 | 12998.2 | 13018 | 12943.8 | 13023.5 | 13071.8 | 12912.9 | 12978.5 | 13029.8 | 13101.5 | 13039.2 | 13066.2 | 12879.4 | 12963.9 | 12848.3 | 11589.6 | 12859.1 | 12826.4 | 13057.8 | 12913.3 | 12894.6 | 13062.3 | 13283 | 13363.9 | 13434.9 | 13341.8 | 13139.9 | 13001.1 | 12991.8 | 12921.4 | 13700.6 | 12825.3 | 13576.4 | 12673.8 | 13139 | 14042.7 | 12575.7 | 13683.4 | 12930.8 | 13143.6 | 13079.5 | 12600.2 | 13370.1 | 12997.7 | 13350.9 | 13080.5 | 12257.8 | 13491.3 | 12298.6 | 13480 | 13388.3 | 12285.7 | 13124 | 12713.9 | 12849.6 | 12294.4 | 12839.3 | 13180.6 | 13410.2 | 12496.4 | 13309.1 | 12133.9 | 13019.4 | 12901.9 | 12362 | 13284 | 12223.3 | 13453.4 | 12341 | 13303.2 | 12591.9 | 13236.1 | 12650.2 | 13528.2 | 12536.3 | 13078.7 | 12449.8 | 11133.7 | 13200.4 | 12901.2 | 12284.5 | 13541.3 | 13266.9 | 12573 | 12418.6 | 13317.4 | 12347 | 12733.4 | 13442.1 | 12341.1 | 13461 | 12336.8 | 13266.1 | 12560.2 | 13295.5 | 11970.9 | 13371.2 | 12494.4 | 13251.1 | 12413.9 | 13280.1 | 12662.5 | 12371.5 | 13207.8 | 12515.8 | 12289.3 | 13273.7 | 13383.8 | 13227 | 12494.7 | 13321.4 | 12366.9 | 13100.1 | 12513.9 | 12987.3 | 11609.8 | 13144.2 | 12384.3 | 12505.3 | 12498.9 | 12324.6 | 10727.1 | 12314.2 | 10929.4 | 12310.5 | 12370.5 | 13686.3 | 12525.3 | 13765.7 | 12772.4 | 13651.3 | 12603.3 | 12746 | 12579.1 | 13502.8 | 13792.5 | 13729.7 | 13640 | 13666.3 | 13676.9 | 12873.4 | 13704.1 | 13751.9 | 13770.6 | 13790 | 13756.3 | 13798.2 | 12883 | 13817.9 | 12927.2 | 33.87 | 33.73 | 34 | 33.95 | 33.82 | 33.84 | 0 | 47.95 | 0 | 0 | 48.09 | 48.02 | 2.89 | 1.36 | 2.83 | 1.48 | 2.52 | 2.65 | 7.15 | 7.24 | 7.31 | 7.13 | 7.74 | 7.56 | 7.34 | 7.37 | 7.36 | 7.28 | 7.37 | 7.41 | 1.94 | 2.01 | 1.8 | 2.4 | 2.21 | 1.94 | 7.86 | 7.88 | 7.77 | 7.82 | 7.79 | 7.81 | 0.46 | 0.51 | 0.43 | 0.46 | 0.43 | 0.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900096 | 1678 | 887014 | 1698 | 92239.141 | 211.133 | 7.34 | 7.37 | 7.36 | 7.28 | 7.37 | 7.41 | 7.86 | 7.88 | 7.77 | 7.82 | 7.79 | 7.81 | 1030000 | 1000 | 1028000 | 1000 | 2056801 | 4466 | 2056000 | 2052335 | 12.3 | 7.355 | 2.05 | 7.8217 | 0.46167 | 27.87% | 5.902% | 33.8683 | 48.02 | 2.2883 | 7.355 | 2070371.8 | 2036067 | 2529673.4443 | 80.49% | 21 | 0
2025-04-03 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 335090.89 | 6:43 | 19:01 | 12521.3 | 12952.2 | 12894.2 | 12880.2 | 12970.2 | 13008 | 12990.1 | 13310.8 | 12949 | 12951 | 12841 | 12937.9 | 12962.4 | 12885.3 | 12938.7 | 13005.1 | 12844.5 | 12933.8 | 12977.5 | 13044.9 | 12976.7 | 12997.1 | 12807.2 | 12903 | 12760.5 | 11431.9 | 12782.1 | 12745 | 12986.1 | 12830 | 12820.1 | 12987.3 | 13042.1 | 13120 | 13209 | 13125.3 | 13059.4 | 12919 | 12908 | 12858.4 | 13592 | 12712.4 | 13473.7 | 12543.2 | 13032.3 | 13925.8 | 12463.2 | 13577.5 | 12883.7 | 13091 | 13031.9 | 12516.1 | 13310.8 | 12948.1 | 13282.9 | 13022 | 12151.2 | 13427.7 | 12185.4 | 13419.9 | 13317.1 | 12176.7 | 13048.2 | 12611 | 12764.5 | 12195.6 | 12752.3 | 13102.5 | 13338.2 | 12390.1 | 13221 | 11985.6 | 12943.2 | 12814.1 | 12250.5 | 13199.6 | 12079.3 | 13383.6 | 12231.7 | 13208.7 | 12469.5 | 13145.1 | 12525.9 | 13440.6 | 12423.4 | 12986.3 | 12341.2 | 10987.2 | 13088.6 | 12797.9 | 12143.8 | 13449.1 | 13176.1 | 12465.5 | 12315.1 | 13227 | 12204.6 | 12619.4 | 13355.3 | 12214 | 13375.6 | 12204.4 | 13183.9 | 12441.6 | 13212.9 | 11836.4 | 13289.1 | 12387.6 | 13173.1 | 12314.6 | 13203.3 | 12550.9 | 12239.7 | 13124.4 | 12401.5 | 12162.8 | 13194.5 | 13322.5 | 13149.3 | 12377.8 | 13250.7 | 12246.7 | 13017.3 | 12403.5 | 12904.5 | 11490.8 | 13065.8 | 12274.8 | 12375.4 | 12368.6 | 12207.1 | 10603.5 | 12187.1 | 10799.5 | 12199.4 | 12250.6 | 13618.7 | 12442.5 | 13684.1 | 12686.4 | 13564.9 | 12499.5 | 12656.1 | 12463.5 | 13436.9 | 13740.8 | 13649.8 | 13565.4 | 13586 | 13598.2 | 12793.4 | 13630.6 | 13675.9 | 13682.7 | 13694.7 | 13665.1 | 13715.5 | 12799 | 13752.6 | 12840.3 | 35.0185 | 34.7848 | 35.4982 | 35.1734 | 35.1062 | 35.0019 | 0 | 49.3561 | 0 | 0 | 49.1 | 49.3608 | 3.1135 | 1.1454 | 2.8658 | 0.91351 | 3.0526 | 2.8922 | 11.2083 | 6.7367 | 7.9683 | 7.0183 | 6.875 | 6.8583 | 7.2478 | 7.3401 | 7.3561 | 7.2376 | 7.3598 | 7.3831 | 1.9236 | 2.0062 | 1.7799 | 2.3848 | 2.2102 | 1.9381 | 7.7669 | 7.8412 | 7.7262 | 7.753 | 7.7759 | 7.772 | 0.46168 | 0.51007 | 0.43314 | 0.45768 | 0.43879 | 0.49129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 901119 | 1680 | 888033 | 1700 | 94280.274 | 214.733 | 7.2478 | 7.3401 | 7.3561 | 7.2376 | 7.3598 | 7.3831 | 7.7669 | 7.8412 | 7.7262 | 7.753 | 7.7759 | 7.772 | 1023000 | 2000 | 1019000 | 2000 | 2041133 | 3600 | 2038000 | 2037533 | 12.3 | 7.3208 | 2.0405 | 7.7725 | 0.46544 | 27.87% | 5.988% | 35.0972 | 49.2723 | 2.3305 | 7.7775 | 2055280 | 2026934 | 2505864.1004 | 80.89% | 26 | 0
2025-04-04 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 335090.89 | 6:42 | 19:02 | 12407.1 | 12826.3 | 12779.2 | 12768.3 | 12848.2 | 12880.5 | 12858.3 | 13176 | 12818.8 | 12823 | 12711.6 | 12816.3 | 12827.9 | 12763 | 12814.9 | 12882.5 | 12713.5 | 12800.8 | 12846.3 | 12909.5 | 12835 | 12851.5 | 12676.8 | 12761.3 | 12623.3 | 11324 | 12652.6 | 12610.1 | 12860.6 | 12698.9 | 12693.2 | 12859.9 | 13013.8 | 13086 | 13159.2 | 13065.3 | 12928.5 | 12792.5 | 12779.6 | 12726.9 | 13486.4 | 12599.2 | 13359 | 12441.2 | 12917.4 | 13833.4 | 12346.8 | 13468.5 | 12757 | 12972.8 | 12903.5 | 12383.7 | 13186.4 | 12824.8 | 13153.2 | 12894.3 | 12045.9 | 13290.4 | 12086 | 13286.2 | 13193.7 | 12072 | 12907.4 | 12467.9 | 12633.3 | 12077.1 | 12630.2 | 12977.8 | 13203.4 | 12273.7 | 13095.2 | 11890.7 | 12819 | 12694.1 | 12140.1 | 13073 | 11976.7 | 13252.2 | 12120 | 13092.3 | 12357.3 | 13025.5 | 12413.2 | 13319 | 12316.2 | 12872.2 | 12229.3 | 10909.9 | 12968.2 | 12703 | 12045 | 13316.2 | 13038.2 | 12327.9 | 12178.7 | 13096.3 | 12091.4 | 12499.5 | 13222.1 | 12119.9 | 13252.7 | 12094 | 13055.7 | 12318.3 | 13086.4 | 11723.8 | 13161.6 | 12259.3 | 13041.8 | 12183 | 13071.6 | 12424.4 | 12142.7 | 12998 | 12286.9 | 12048.4 | 13058 | 13188.9 | 13009.9 | 12263.3 | 13113.5 | 12134.6 | 12871.6 | 12276.2 | 12759.3 | 11381.2 | 12928.9 | 12169.5 | 12252.1 | 12242.6 | 12112.5 | 10501.3 | 12061.4 | 10709.1 | 12074.9 | 12135.8 | 13492.3 | 12307.8 | 13552.7 | 12553.2 | 13435.2 | 12369.1 | 12523.8 | 12343.2 | 13287.9 | 13591.4 | 13509.8 | 13426.8 | 13452.6 | 13470.8 | 12659.7 | 13495.8 | 13556.6 | 13554.8 | 13568.2 | 13543 | 13578.4 | 12651.6 | 13618.2 | 12687.3 | 32.91 | 32.67 | 32.97 | 33.06 | 32.84 | 32.92 | 0 | 45.05 | 0 | 0 | 45.3 | 44.56 | 3.64 | 3.02 | 3.5 | 1.84 | 3.45 | 3.31 | 6.12 | 7.01 | 6.54 | 6.57 | 6.51 | 6.51 | 7.06 | 7.11 | 7.12 | 7.01 | 7.11 | 7.12 | 1.85 | 1.94 | 1.73 | 2.3 | 2.15 | 1.88 | 7.53 | 7.57 | 7.47 | 7.5 | 7.53 | 7.5 | 0.47 | 0.51 | 0.44 | 0.47 | 0.44 | 0.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 902133 | 1680 | 889043 | 1701 | 96301.941 | 217.8 | 7.06 | 7.11 | 7.12 | 7.01 | 7.11 | 7.12 | 7.53 | 7.57 | 7.47 | 7.5 | 7.53 | 7.5 | 1014000 | 0 | 1010000 | 1000 | 2021667 | 3067 | 2023000 | 2018600 | 12.3333 | 7.0883 | 1.975 | 7.5167 | 0.47 | 27.86% | 6.253% | 32.895 | 44.97 | 3.1267 | 6.5433 | 2035769.3 | 2007934 | 2461278.3152 | 81.58% | 24 | 0
2025-04-05 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 335090.89 | 6:41 | 19:02 | 12069.3 | 12557.2 | 12509.7 | 12495.5 | 12582 | 12618.3 | 12577.5 | 12908 | 12547.6 | 12544.4 | 12436.6 | 12552.5 | 12558.5 | 12498.8 | 12522.1 | 12616.7 | 12440 | 12542.9 | 12588.1 | 12640.3 | 12585 | 12594.2 | 12390.7 | 12499.7 | 12349.8 | 10884.8 | 12365.7 | 12326.1 | 12601.7 | 12430.3 | 12415.8 | 12611.7 | 12583.7 | 12668.6 | 12750.5 | 12660.9 | 12685.6 | 12530.7 | 12516.8 | 12462.6 | 13281.3 | 12281 | 13170.7 | 12088.2 | 12625.6 | 13608.4 | 11999.9 | 13270.3 | 12480.5 | 12708.5 | 12630 | 12022.6 | 12941 | 12553.6 | 12913.4 | 12638.1 | 11575 | 13067 | 11609.5 | 13054.1 | 12958.9 | 11609.5 | 12643.4 | 12134.5 | 12333.7 | 11651.9 | 12322.8 | 12732.7 | 12989.2 | 11894.8 | 12858.9 | 11427.7 | 12548 | 12385.9 | 11707.7 | 12840.3 | 11516 | 13032.6 | 11675.5 | 12848.9 | 11993.9 | 12792.1 | 12062.6 | 13108.3 | 11936.4 | 12601.8 | 11861.3 | 10486.8 | 12710.6 | 12424 | 11596.3 | 13095.4 | 12796.6 | 11935.4 | 11758.3 | 12866.1 | 11626.3 | 12171 | 13013.7 | 11712.5 | 13041.2 | 11665.7 | 12814 | 11918.4 | 12862.7 | 11281.4 | 12942 | 11890.9 | 12809 | 11778.7 | 12818.5 | 12050.1 | 11718.4 | 12767.4 | 11902.1 | 11612.2 | 12842.5 | 12975.4 | 12787 | 11860.8 | 12902.2 | 11720.8 | 12619.8 | 11897.6 | 12491.8 | 10957.9 | 12677.7 | 11725.7 | 11833.7 | 11835.4 | 11665.2 | 10081.7 | 11602.4 | 10261.6 | 11611.2 | 11676.4 | 13311.6 | 11971.2 | 13381.2 | 12264.2 | 13253.5 | 12041.9 | 12231.6 | 11984.6 | 13099.8 | 13458.9 | 13320.9 | 13241.6 | 13251.2 | 13271.3 | 12380.5 | 13305.5 | 13365.2 | 13376.7 | 13402.1 | 13356.3 | 13411.6 | 12377.6 | 13439.8 | 12418.5 | 35.2342 | 34.9056 | 35.428 | 35.1738 | 35.3197 | 35.1237 | 0 | 48.947 | 0 | 0 | 48.9 | 49.1883 | 3.4218 | 2.3906 | 3.4648 | 1.5309 | 3.4199 | 3.2133 | 7.715 | 7.12 | 7.3767 | 7.7867 | 7.9367 | 7.9533 | 6.9507 | 6.9961 | 7.0091 | 6.9006 | 7.0127 | 7.0426 | 1.8282 | 1.9044 | 1.7002 | 2.2756 | 2.1037 | 1.8424 | 7.383 | 7.4161 | 7.31 | 7.3503 | 7.3752 | 7.3656 | 0.45532 | 0.50272 | 0.42833 | 0.45667 | 0.43313 | 0.48339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 903127 | 1681 | 890029 | 1702 | 98276.341 | 221.267 | 6.9507 | 6.9961 | 7.0091 | 6.9006 | 7.0127 | 7.0426 | 7.383 | 7.4161 | 7.31 | 7.3503 | 7.3752 | 7.3656 | 994000 | 1000 | 986000 | 1000 | 1974400 | 3467 | 1978000 | 1970933 | 12.35 | 6.9853 | 1.9424 | 7.3667 | 0.45993 | 27.81% | 6.243% | 35.1975 | 49.0118 | 2.9069 | 7.6481 | 1987718.7 | 1955667 | 2389204.14 | 81.85% | 26 | 0
2025-04-06 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 335090.89 | 6:43 | 19:04 | 12146 | 12508.3 | 12448.2 | 12464.2 | 12511.9 | 12542.7 | 12467.2 | 12703 | 12496.4 | 12474 | 12408.4 | 12493.4 | 12529.3 | 12448.6 | 12496.3 | 12567.7 | 12408.2 | 12489.2 | 12526.1 | 12600.5 | 12522 | 12545.7 | 12400.1 | 12474 | 12347.8 | 11218.2 | 12372.6 | 12340 | 12529.7 | 12388.9 | 12411.1 | 12530.6 | 12883.3 | 12968.1 | 13070.1 | 12985.8 | 12589.6 | 12468 | 12443.8 | 12416 | 13079.6 | 12361.7 | 12980.9 | 12235.6 | 12581.6 | 13323.5 | 12124.7 | 13060.9 | 12445.6 | 12639.7 | 12599.6 | 12170.6 | 12824.8 | 12515.8 | 12793.1 | 12574.5 | 11846.8 | 12911.2 | 11892.7 | 12915.1 | 12833.2 | 11869.6 | 12562.7 | 12192.3 | 12362.4 | 11907.2 | 12358.2 | 12649.2 | 12831.6 | 12067 | 12736.5 | 11715.9 | 12502.9 | 12416.1 | 11944.7 | 12716.2 | 11796.4 | 12878 | 11924 | 12726.7 | 12149.1 | 12698 | 12172.7 | 12937 | 12094.3 | 12546 | 12008.3 | 10868 | 12603.3 | 12411.1 | 11886.7 | 12934.2 | 12683.5 | 12097 | 11966.9 | 12721.9 | 11865.2 | 12252.6 | 12840.9 | 11935.6 | 12866.3 | 11915.7 | 12740.2 | 12113.5 | 12734.2 | 11575.8 | 12810.7 | 12069.6 | 12724.7 | 12007.8 | 12739.5 | 12231.7 | 11940.3 | 12649.8 | 12083.1 | 11873.2 | 12708.6 | 12826.8 | 12670 | 12058.7 | 12753.4 | 11951.6 | 12569.3 | 12090.8 | 12449.3 | 11295.1 | 12622.5 | 11975.4 | 12024.2 | 11982 | 11908.1 | 10441.6 | 11828.3 | 10602.8 | 11846.5 | 11891 | 13072.4 | 12093.5 | 13132.3 | 12315.9 | 13016.5 | 12128.6 | 12265.3 | 12099 | 12948.4 | 13193.1 | 13114.4 | 13039.9 | 13045.5 | 13057 | 12404.5 | 13089.8 | 13142.5 | 13138.7 | 13150.7 | 13122 | 13174.1 | 12419 | 13213.4 | 12448.4 | 38.4 | 38.04 | 38.61 | 38.39 | 38.84 | 38.36 | 0 | 50.5 | 0 | 0 | 50.8 | 51.08 | 4.34 | 2.85 | 4.14 | 2.51 | 3.92 | 3.71 | 8.83 | 8.38 | 8.42 | 8.46 | 8.53 | 8.71 | 7.3 | 7.34 | 7.34 | 7.21 | 7.35 | 7.37 | 1.91 | 2 | 1.77 | 2.38 | 2.21 | 1.93 | 7.74 | 7.78 | 7.64 | 7.67 | 7.71 | 7.71 | 0.47 | 0.52 | 0.44 | 0.47 | 0.45 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 904118 | 1683 | 891016 | 1704 | 100252.941 | 225.733 | 7.3 | 7.34 | 7.34 | 7.21 | 7.35 | 7.37 | 7.74 | 7.78 | 7.64 | 7.67 | 7.71 | 7.71 | 991000 | 2000 | 987000 | 2000 | 1976600 | 4466 | 1974000 | 1972134 | 12.35 | 7.3183 | 2.0333 | 7.7083 | 0.475 | 27.78% | 6.162% | 38.44 | 50.7933 | 3.5783 | 8.555 | 1989573.1 | 2001755 | 2460955.4065 | 81.34% | 28 | 0
2025-04-07 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 335090.89 | 6:45 | 19:04 | 11257 | 11626.3 | 11587.4 | 11604.4 | 11644.9 | 11674.4 | 11605.2 | 11864.2 | 11627.4 | 11603.6 | 11528.1 | 11616 | 11654.4 | 11577.4 | 11613.3 | 11707.5 | 11537.1 | 11625.3 | 11660.5 | 11720.1 | 11654.1 | 11671.2 | 11515 | 11601.7 | 11468.1 | 10320.1 | 11485.1 | 11453.6 | 11670.3 | 11508.8 | 11531.7 | 11673 | 12615.9 | 12709.5 | 12783.9 | 12685.9 | 11723.4 | 11596.6 | 11579.5 | 11552.9 | 12233.6 | 11447 | 12133.9 | 11296 | 11712.1 | 12501.2 | 11202.5 | 12222.9 | 11574.3 | 11764 | 11722.2 | 11207.9 | 11961.3 | 11634.6 | 11909.9 | 11683.7 | 10857.2 | 12025 | 10925.6 | 12034.5 | 11958.2 | 10909.2 | 11667.6 | 11253 | 11430.9 | 10901.4 | 11422.7 | 11738.2 | 11946.2 | 11079.1 | 11831.2 | 10737.8 | 11593 | 11473.7 | 10946.4 | 11823.4 | 10809.8 | 11985.5 | 10927.7 | 11833.5 | 11170.3 | 11786.3 | 11217.1 | 12040.8 | 11127 | 11649.4 | 11040.5 | 10004.7 | 11739.8 | 11500.8 | 10899.2 | 12064.2 | 11796.6 | 11115.1 | 10979.9 | 11829 | 10877.1 | 11319.7 | 11982.2 | 10962.5 | 11998.9 | 10936.6 | 11850 | 11136.2 | 11868.9 | 10635.3 | 11938.4 | 11090.7 | 11835.8 | 11014.6 | 11842 | 11237.2 | 10971.9 | 11773.6 | 11118.6 | 10890.3 | 11830.9 | 11951.2 | 11787.3 | 11086 | 11895.3 | 10966.8 | 11671.6 | 11102.2 | 11546.6 | 10387.3 | 11734 | 10991.8 | 11039.8 | 11007.5 | 10919.5 | 9637.3 | 10837.3 | 9780.6 | 10869.5 | 10924.8 | 12239.1 | 11174 | 12300.9 | 11420.4 | 12181.6 | 11217.5 | 11368.9 | 11162.6 | 12061.9 | 12317.4 | 12249.6 | 12182.8 | 12195.4 | 12212.4 | 11507.7 | 12239.1 | 12287.2 | 12292.2 | 12299.3 | 12272.6 | 12319.1 | 11508.9 | 12355 | 11546 | 37.7941 | 37.4942 | 38.2532 | 37.6891 | 37.5118 | 37.7428 | 0 | 53.106 | 0 | 0 | 53.2422 | 53.5 | 2.7096 | 0.32744 | 2.6464 | 0.63009 | 2.6007 | 2.7148 | 6.57 | 6.4267 | 7.6133 | 6.3867 | 6.2667 | 6.075 | 7.1429 | 7.1944 | 7.1954 | 7.0421 | 7.202 | 7.23 | 1.8599 | 1.946 | 1.7338 | 2.316 | 2.1439 | 1.8802 | 7.5603 | 7.6042 | 7.4791 | 7.4663 | 7.5401 | 7.5312 | 0.45061 | 0.49652 | 0.42282 | 0.44584 | 0.42642 | 0.47823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 905041 | 1685 | 891931 | 1705 | 102090.275 | 230.267 | 7.1429 | 7.1944 | 7.1954 | 7.0421 | 7.202 | 7.23 | 7.5603 | 7.6042 | 7.4791 | 7.4663 | 7.5401 | 7.5312 | 923000 | 2000 | 915000 | 1000 | 1837334 | 4534 | 1835000 | 1832800 | 12.3167 | 7.1678 | 1.98 | 7.5302 | 0.45341 | 27.62% | 6.021% | 37.7475 | 53.2827 | 1.9382 | 6.5564 | 1847572.8 | 1956509.95 | 2388027.7493 | 81.93% | 23 | 9899
2025-04-08 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 335090.89 | 6:47 | 19:04 | 12173 | 12650.6 | 12587.4 | 12590 | 12665.7 | 12697.8 | 12606.3 | 12914.4 | 12632 | 12599.3 | 12508.3 | 12620.4 | 12658.1 | 12569.6 | 12597.9 | 12710.8 | 12531.5 | 12632.5 | 12682.7 | 12731.4 | 12678.5 | 12685.4 | 12502.3 | 12606.4 | 12438.8 | 10992.4 | 12459.1 | 12426 | 12687.6 | 12517.2 | 12522 | 12705.3 | 12635.9 | 12736.9 | 12824.9 | 12753.3 | 12790.1 | 12613.5 | 12605.5 | 12567.8 | 13354.4 | 12388.5 | 13244.8 | 12211.6 | 12633.7 | 13532.7 | 12097.9 | 13332.2 | 12561 | 12795.6 | 12736.6 | 12133.7 | 13019.9 | 12627.2 | 12999.7 | 12730.1 | 11689.3 | 13136.2 | 11734 | 13136.2 | 13028 | 11730.6 | 12695.3 | 12204.4 | 12456.2 | 11799.3 | 12436.8 | 12819.6 | 13078.2 | 12024.8 | 12953.4 | 11550.6 | 12650 | 12508.1 | 11836.3 | 12930.5 | 11645.5 | 13118.5 | 11806.9 | 12922.9 | 12115.7 | 12877 | 12168.6 | 13178.4 | 12064 | 12704.6 | 11989 | 10604.6 | 12828.8 | 12529.9 | 11750.5 | 13215.5 | 12915 | 12091.2 | 11943.2 | 12942.3 | 11725 | 12271.8 | 13083.7 | 11823.5 | 13109 | 11785.5 | 12922.7 | 12029.5 | 12948.3 | 11393.2 | 13027.1 | 12005.3 | 12902.9 | 11890.4 | 12942.1 | 12176.2 | 11829.4 | 12833.8 | 12025.5 | 11727.1 | 12921.5 | 13057.6 | 12874.3 | 11977.4 | 12982.6 | 11840.7 | 12730 | 12021.5 | 12585.3 | 11089.2 | 12792.3 | 11854.9 | 11917.8 | 11890.6 | 11780.2 | 10165.6 | 11673.3 | 10297 | 11685.2 | 11750.6 | 13379.1 | 12094.2 | 13446.8 | 12379.9 | 13310.3 | 12124.3 | 12322 | 12061.8 | 13229.7 | 13481.7 | 13376.2 | 13295.4 | 13301.8 | 13330.7 | 12487.7 | 13364 | 13423.9 | 13432.5 | 13452.7 | 13403.7 | 13467.3 | 12487.1 | 13508.2 | 12528 | 39.45 | 39.02 | 39.28 | 39.21 | 39.1 | 39.46 | 0 | 51.27 | 0 | 0 | 51.4 | 51.5 | 5.42 | 5.21 | 5.24 | 4.05 | 5.34 | 5.25 | 10.41 | 10.02 | 9.16 | 9.33 | 9.75 | 8.95 | 7.12 | 7.18 | 7.19 | 7.07 | 7.18 | 7.23 | 1.88 | 1.96 | 1.75 | 2.33 | 2.16 | 1.89 | 7.52 | 7.57 | 7.44 | 7.47 | 7.52 | 7.5 | 0.47 | 0.52 | 0.44 | 0.47 | 0.45 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 906039 | 1686 | 892924 | 1707 | 104079.541 | 234.733 | 7.12 | 7.18 | 7.19 | 7.07 | 7.18 | 7.23 | 7.52 | 7.57 | 7.44 | 7.47 | 7.52 | 7.5 | 998000 | 1000 | 993000 | 2000 | 1989266 | 4466 | 1988000 | 1984800 | 12.2833 | 7.1617 | 1.995 | 7.5033 | 0.475 | 27.86% | 6.331% | 39.2533 | 51.39 | 5.085 | 9.6033 | 2002346.7 | 1970266 | 2414843.1 | 81.59% | 23 | 0
2025-04-09 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 335090.89 | 6:44 | 19:05 | 12141.5 | 12617.2 | 12564.6 | 12566.7 | 12637.2 | 12668.9 | 12605.4 | 12902.5 | 12593 | 12560.4 | 12471.9 | 12580.5 | 12620.2 | 12541.9 | 12577 | 12690.9 | 12509.5 | 12615.2 | 12651.6 | 12707.1 | 12647.8 | 12659.2 | 12474.7 | 12579.4 | 12423.9 | 10999.6 | 12438.2 | 12407.7 | 12659.8 | 12491.8 | 12500.6 | 12672.5 | 12642.8 | 12735.9 | 12819.4 | 12749 | 12764.7 | 12593 | 12589.8 | 12550.7 | 13324.5 | 12401.4 | 13218.2 | 12228.6 | 12633.8 | 13529.3 | 12099.1 | 13308.1 | 12551.1 | 12770.1 | 12714.1 | 12124.9 | 12991.8 | 12599.1 | 12961.5 | 12700.3 | 11693 | 13099.2 | 11738.9 | 13096 | 12996.1 | 11735.3 | 12666.6 | 12178.8 | 12419.1 | 11790.8 | 12413.4 | 12784.4 | 13037 | 12015.6 | 12915.8 | 11551.7 | 12621.7 | 12475.3 | 11841.7 | 12891.3 | 11645.1 | 13085.3 | 11806.6 | 12880.6 | 12103.1 | 12834.9 | 12151.8 | 13139.2 | 12052.5 | 12667.3 | 11955 | 10597.2 | 12788.1 | 12498.7 | 11739.7 | 13158.3 | 12874.9 | 12104.5 | 11971.5 | 12911 | 11704.6 | 12255.7 | 13029.9 | 11823.4 | 13074.6 | 11793.9 | 12884.2 | 12032.7 | 12916.6 | 11394.5 | 12991.2 | 12004.8 | 12873.4 | 11905.1 | 12895.2 | 12173.4 | 11838.9 | 12792.7 | 12025.4 | 11731.4 | 12876 | 13017 | 12826.4 | 11974.2 | 12942.5 | 11841.6 | 12684.5 | 12013.8 | 12532.2 | 11077.6 | 12743.2 | 11848.4 | 11907.4 | 11887.9 | 11769.3 | 10152.4 | 11663.6 | 10294.9 | 11655.3 | 11715.6 | 13324.1 | 12074.3 | 13403 | 12355 | 13259.7 | 12095.7 | 12277.8 | 12031 | 13151.7 | 13501.9 | 13342.2 | 13259.9 | 13264.4 | 13289.6 | 12468.4 | 13335.6 | 13384.5 | 13395.3 | 13415.6 | 13378.7 | 13435.7 | 12473.8 | 13462.4 | 12504.2 | 37.99 | 37.64 | 38.13 | 37.75 | 38.01 | 38.09 | 0 | 50.47 | 0 | 0 | 50.7 | 50.8 | 4.11 | 3.65 | 4.02 | 2.33 | 3.75 | 4.12 | 9.01 | 9.22 | 8.87 | 8.94 | 9.03 | 9.42 | 7.13 | 7.18 | 7.2 | 7.07 | 7.2 | 7.22 | 1.89 | 1.96 | 1.76 | 2.35 | 2.17 | 1.89 | 7.51 | 7.56 | 7.45 | 7.45 | 7.51 | 7.5 | 0.46 | 0.51 | 0.44 | 0.46 | 0.44 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 907035 | 1688 | 893915 | 1709 | 106065.208 | 238.467 | 7.13 | 7.18 | 7.2 | 7.07 | 7.2 | 7.22 | 7.51 | 7.56 | 7.45 | 7.45 | 7.51 | 7.5 | 996000 | 2000 | 991000 | 2000 | 1985667 | 3734 | 1983000 | 1981933 | 12.35 | 7.1667 | 2.0033 | 7.4967 | 0.46833 | 27.95% | 6.247% | 37.935 | 50.6567 | 3.6633 | 9.0817 | 1998756.5 | 1953600 | 2394420.6 | 81.59% | 22 | 486
2025-04-10 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 335090.89 | 6:36 | 19:04 | 12197 | 12689.1 | 12631.8 | 12632.3 | 12711.6 | 12741.6 | 12658.4 | 12996.2 | 12658.1 | 12648 | 12524.2 | 12647 | 12670.3 | 12605.7 | 12628 | 12746.3 | 12554.1 | 12670.6 | 12696.6 | 12757.1 | 12694.6 | 12699.2 | 12515 | 12616 | 12457.4 | 10993.7 | 12469.6 | 12435 | 12714.7 | 12538.9 | 12529.2 | 12725.8 | 12769 | 12870.7 | 12930 | 12853.8 | 12819.1 | 12639 | 12638.8 | 12606 | 13437.7 | 12423.7 | 13311 | 12235.4 | 12714.5 | 13774.8 | 12115.4 | 13438.6 | 12608.2 | 12842.3 | 12765 | 12143.4 | 13086.1 | 12780.1 | 13049.9 | 12764.7 | 11721 | 13207.4 | 11769.5 | 13196.8 | 13094.3 | 11762 | 12753 | 12217.6 | 12481.1 | 11828.9 | 12469.7 | 12878.5 | 13155.7 | 12053.7 | 13008.4 | 11577.8 | 12694.1 | 12525.6 | 11862 | 12980.2 | 11666 | 13192 | 11826 | 12979.4 | 12127.2 | 12903.8 | 12187.5 | 13245.6 | 12084 | 12735.8 | 12039.9 | 10641.1 | 12879.3 | 12572 | 11752 | 13250.8 | 12946.2 | 12111 | 11981.4 | 13006.3 | 11727.8 | 12301.8 | 13148.7 | 11852.6 | 13174.2 | 11806.4 | 12947 | 12056.9 | 13001.3 | 11415.2 | 13074.8 | 12026.7 | 12935.3 | 11914.5 | 12954 | 12191.9 | 11860.2 | 12880.7 | 12049.3 | 11756.2 | 12975.7 | 13119.2 | 12911.7 | 12002.7 | 13047.6 | 11856.4 | 12749 | 12029.7 | 12591.4 | 11098.8 | 12807.2 | 11868.2 | 11926.6 | 11923.2 | 11789.6 | 10172.5 | 11693 | 10310.6 | 11709.6 | 11765.8 | 13460.2 | 12092.4 | 13533.6 | 12377.2 | 13387.9 | 12127 | 12310.5 | 12073.1 | 13209.2 | 13571.7 | 13457.7 | 13381 | 13389.9 | 13418.1 | 12492.1 | 13458.8 | 13519.5 | 13529.7 | 13550.8 | 13511.7 | 13560.8 | 12493.7 | 13590.2 | 12536.2 | 34.8418 | 34.5327 | 34.9996 | 34.7352 | 34.729 | 34.9543 | 0 | 47.5347 | 0 | 0 | 47.9 | 48.2657 | 5.144 | 5.0089 | 4.8742 | 4.1021 | 5.1972 | 5.1108 | 11.2333 | 11.185 | 11.8 | 10.96 | 11.11 | 11.3117 | 7.0677 | 7.1286 | 7.1194 | 7.0049 | 7.1412 | 7.1625 | 1.8648 | 1.9201 | 1.7367 | 2.3149 | 2.1245 | 1.8463 | 7.4238 | 7.4682 | 7.3379 | 7.376 | 7.4253 | 7.3926 | 0.4771 | 0.52983 | 0.44786 | 0.47867 | 0.45597 | 0.50881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 908034 | 1689 | 894911 | 1710 | 108060.342 | 243 | 7.0677 | 7.1286 | 7.1194 | 7.0049 | 7.1412 | 7.1625 | 7.4238 | 7.4682 | 7.3379 | 7.376 | 7.4253 | 7.3926 | 999000 | 1000 | 996000 | 1000 | 1995134 | 4533 | 1993000 | 1990601 | 12.4667 | 7.1041 | 1.9679 | 7.404 | 0.48304 | 27.7% | 6.524% | 34.7988 | 47.9001 | 4.9062 | 11.2667 | 2008891.9 | 1975267 | 2421411.128 | 81.58% | 25 | 0
2025-04-11 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 335090.89 | 6:45 | 19:05 | 10584.5 | 11038.5 | 10992.7 | 10971.5 | 11069.8 | 11095 | 11023.5 | 11348.8 | 10990.1 | 11020 | 10872.7 | 10972.1 | 11013 | 10952 | 10982.3 | 11089.9 | 10915.6 | 11011.4 | 11028.9 | 11062 | 11031.9 | 11025.2 | 10869.4 | 10951.5 | 10765.7 | 9534 | 10787.1 | 10749 | 11031.5 | 10879.9 | 10857 | 11041.1 | 10962.7 | 11069.7 | 11154.2 | 11079.2 | 11100.1 | 10935.8 | 10946.4 | 10889.9 | 11784.7 | 10782.3 | 11666.9 | 10611 | 11027.2 | 12084.1 | 10498.5 | 11793 | 10984.8 | 11164.5 | 11065.7 | 10502.8 | 11384.8 | 11119.2 | 11331.2 | 11082 | 10103.7 | 11422.3 | 10217.5 | 11449.1 | 11350.8 | 10202.4 | 10998.7 | 10504 | 10671.4 | 10097.6 | 10663.6 | 11038.4 | 11342 | 10289.7 | 11179.2 | 9925.7 | 10909.6 | 10705.5 | 10170.3 | 11141.9 | 9988.4 | 11376.9 | 10140.7 | 11156.6 | 10366.7 | 11082.6 | 10449.6 | 11428.9 | 10345.1 | 10952.9 | 10282.3 | 9169.5 | 11049.5 | 10783.7 | 10067.8 | 11412.6 | 11119.3 | 10327.6 | 10213.8 | 11173.6 | 10025.9 | 10501.4 | 11289.7 | 10130.5 | 11321.3 | 10088.6 | 11080.5 | 10292.9 | 11153.9 | 9785.3 | 11225.8 | 10271.4 | 11099 | 10207.1 | 11139.9 | 10418.3 | 10154.9 | 11056.6 | 10281.4 | 10073.2 | 11144.2 | 11306.9 | 11091.7 | 10300.5 | 11245.8 | 10191.5 | 10918.3 | 10294 | 10803.3 | 9603.6 | 11015.6 | 10204.4 | 10194.6 | 10156.1 | 10107.5 | 8744.3 | 9959.9 | 8841.3 | 9983.9 | 10028.3 | 11589.6 | 10309.6 | 11643.3 | 10535.1 | 11496.1 | 10295.1 | 10472.1 | 10252.9 | 11279.9 | 11628.1 | 11551.9 | 11480.5 | 11501.7 | 11544.6 | 10624.9 | 11549.9 | 11611.9 | 11596.2 | 11546.9 | 11523.5 | 11579 | 10573.5 | 11681 | 10646.2 | 34.0774 | 33.8059 | 34.0838 | 33.8225 | 33.6192 | 34.045 | 0 | 45.2 | 0 | 0 | 45 | 45.4008 | 6.0414 | 6.2044 | 5.8471 | 5.759 | 6.1084 | 6.2869 | 11.0567 | 11.205 | 10.6783 | 11.0533 | 10.4817 | 13.58 | 6.1213 | 6.1519 | 6.1732 | 6.0148 | 6.1002 | 6.0615 | 1.5809 | 1.6994 | 1.4742 | 1.9463 | 1.8367 | 1.639 | 6.3709 | 6.3997 | 6.2908 | 6.2431 | 6.2678 | 6.2569 | 0.43233 | 0.4828 | 0.40685 | 0.43625 | 0.41527 | 0.45731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 908902 | 1691 | 895765 | 1712 | 109779.809 | 247.6 | 6.1213 | 6.1519 | 6.1732 | 6.0148 | 6.1002 | 6.0615 | 6.3709 | 6.3997 | 6.2908 | 6.2431 | 6.2678 | 6.2569 | 868000 | 2000 | 854000 | 2000 | 1719467 | 4600 | 1718000 | 1714867 | 12.3333 | 6.1038 | 1.6961 | 6.3049 | 0.43847 | 27.79% | 6.954% | 33.909 | 45.2003 | 6.0412 | 11.3425 | 1730096.6 | 1704267 | 2095267.9995 | 81.34% | 38 | 0
2025-04-12 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 335090.89 | 6:43 | 19:05 | 12241.6 | 12830.5 | 12707.6 | 12695.4 | 12800.2 | 12869.3 | 12790.3 | 13135.8 | 12794.8 | 12768.9 | 12675.6 | 12778.6 | 12847.2 | 12769.7 | 12749.4 | 12912.7 | 12715.4 | 12823.9 | 12896.8 | 12933.7 | 12904.2 | 12883.6 | 12707.9 | 12811.3 | 12633.3 | 11047.8 | 12622.9 | 12595.4 | 12910.3 | 12738.2 | 12737.2 | 12956.7 | 12746.2 | 12860.3 | 12951.2 | 12865.5 | 11891.8 | 11762.9 | 11761.3 | 11721.3 | 12444.7 | 11583.6 | 12343.4 | 11450 | 11842.3 | 12724.8 | 11310.2 | 12435.4 | 12800.9 | 13018.7 | 12932 | 12188.8 | 13263.6 | 12953.6 | 13257.3 | 12968.2 | 11728.5 | 13363.8 | 11807.6 | 13381.4 | 13254.3 | 11796.4 | 12865.2 | 12269 | 12547 | 11803.5 | 12526.4 | 12958.8 | 13304 | 12039.3 | 13141.9 | 11556.4 | 12816.6 | 12580.1 | 11859.8 | 13090.7 | 11641.9 | 13344.4 | 11818.6 | 13074 | 11284.8 | 11881.5 | 11303.2 | 12176.3 | 11245.7 | 11735.7 | 11186.1 | 10191.6 | 11786.4 | 11600.8 | 11036.8 | 12151.8 | 11913.6 | 11256.4 | 11146.6 | 11926.4 | 10988.2 | 11407.3 | 12076.8 | 11111.6 | 12094.4 | 11082.5 | 11915.1 | 11260.4 | 11955.5 | 10813.9 | 12033.8 | 11233.6 | 11925.3 | 11166.6 | 11938.5 | 11368.8 | 11131 | 11875.6 | 11250.7 | 11075.7 | 11948.6 | 12085.8 | 11904.5 | 11235.5 | 12023.5 | 11139.7 | 11764.3 | 11252.5 | 11634.1 | 10629.3 | 11830.1 | 11170 | 11139.2 | 11067.6 | 11051.7 | 9770.6 | 10896.4 | 9822.1 | 10860 | 10901.9 | 12319.2 | 11206.2 | 12352.5 | 11406.7 | 12194.9 | 11146 | 11299.6 | 11089.8 | 12093.1 | 12387.9 | 12319.1 | 12246.8 | 12263.2 | 12289.2 | 11495.4 | 12295.5 | 12362.3 | 12360.7 | 12348.3 | 12325.7 | 12371.6 | 11497.6 | 12422.9 | 11546.7 | 34.2408 | 33.8181 | 34.2696 | 34.0741 | 33.9775 | 34.1756 | 0 | 47.7 | 0 | 0 | 48 | 48.2 | 4.7449 | 5.0318 | 4.7594 | 4.3603 | 5.2779 | 5.2706 | 9.265 | 8.7367 | 9.28 | 8.6183 | 8.9917 | 9.3233 | 7.1205 | 7.1963 | 7.1567 | 7.0547 | 7.1627 | 7.1524 | 1.8553 | 1.9518 | 1.7277 | 2.3024 | 2.1343 | 1.8552 | 7.4429 | 7.4996 | 7.3439 | 7.3778 | 7.4113 | 7.3569 | 0.48369 | 0.54049 | 0.45409 | 0.48651 | 0.4641 | 0.51178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 909901 | 1692 | 896697 | 1714 | 111698.342 | 252.133 | 7.1205 | 7.1963 | 7.1567 | 7.0547 | 7.1627 | 7.1524 | 7.4429 | 7.4996 | 7.3439 | 7.3778 | 7.4113 | 7.3569 | 999000 | 1000 | 932000 | 2000 | 1918533 | 4533 | 1928000 | 1914000 | 12.3667 | 7.1405 | 1.9711 | 7.4054 | 0.49011 | 27.6% | 6.618% | 34.0926 | 47.9667 | 4.9075 | 9.0358 | 1931231.1 | 1932193.25 | 2416992.9869 | 79.94% | 31 | 0
2025-04-13 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 335090.89 | 6:40 | 19:06 | 12283.4 | 12765.9 | 12689.7 | 12691 | 12767 | 12789.1 | 12691.4 | 12979.5 | 12697.1 | 12626.7 | 12582.8 | 12668.4 | 12745.5 | 12669.6 | 12689.6 | 12837.3 | 12637.8 | 12754.5 | 12778.2 | 12834.6 | 12768.7 | 12785.3 | 12614.6 | 12710.1 | 12561.3 | 11125 | 12569 | 12535 | 12787 | 12603.5 | 12627.2 | 12810.5 | 12818.5 | 12921.2 | 13017 | 12923.2 | 12883.2 | 12727.2 | 12713.9 | 12692.6 | 13492.2 | 12559.5 | 13373.8 | 12378.2 | 12790.6 | 13702.3 | 12218.6 | 13481.1 | 12735.6 | 12924.8 | 12852.3 | 12249 | 13131.3 | 12835.7 | 13109.6 | 12841.2 | 11828 | 13230.9 | 11892.5 | 13253.5 | 13152.9 | 11883.7 | 12782.2 | 12277 | 12535.8 | 11935.9 | 12556.8 | 12948.8 | 13184.1 | 12172.3 | 13056.4 | 11704.8 | 12759.4 | 12617.8 | 11988.9 | 13033.5 | 11792.7 | 13228.8 | 11937.7 | 13012.6 | 12269.2 | 12999.3 | 12346.8 | 13313.7 | 12247 | 12856.9 | 12135.1 | 10767.4 | 12892.6 | 12659.2 | 11879.3 | 13281.7 | 12984.6 | 12160.4 | 11989.3 | 13041.8 | 11842.5 | 12420 | 13200.9 | 12015.9 | 13238.8 | 11973.9 | 13034.8 | 12195.5 | 13072 | 11554.5 | 13152.6 | 12174 | 13020 | 12067.4 | 13038.2 | 12332 | 12016.3 | 12961.2 | 12188.1 | 11892 | 13027.3 | 13198.4 | 12982.8 | 12159.1 | 13121.9 | 12017.2 | 12832 | 12177.1 | 12669.8 | 11240.9 | 12904.6 | 12019 | 12018.3 | 11950.6 | 11885.1 | 10250.6 | 11694.5 | 10322.2 | 11647.1 | 11733.7 | 13526.1 | 12231.4 | 13582.7 | 12505 | 13423.8 | 12203.3 | 12407.5 | 12097.6 | 13301.3 | 13639.1 | 13537.4 | 13451.7 | 13469.2 | 13490.6 | 12618 | 13521.8 | 13571 | 13574.9 | 13591.4 | 13559.4 | 13615.6 | 12619.9 | 13633.9 | 12646.9 | 36.55 | 36.11 | 36.5 | 36.59 | 36.44 | 36.39 | 0 | 51.13 | 0 | 0 | 51.1 | 51.3 | 3.76 | 3.45 | 3.58 | 1.95 | 3.79 | 3.59 | 8.19 | 8.16 | 8 | 8.2 | 7.97 | 7.17 | 7.31 | 7.36 | 7.34 | 7.26 | 7.39 | 7.41 | 1.9 | 1.99 | 1.77 | 2.35 | 2.2 | 1.92 | 7.62 | 7.68 | 7.52 | 7.59 | 7.63 | 7.61 | 0.48 | 0.53 | 0.45 | 0.48 | 0.46 | 0.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 910907 | 1693 | 897690 | 1715 | 113706.142 | 256.6 | 7.31 | 7.36 | 7.34 | 7.26 | 7.39 | 7.41 | 7.62 | 7.68 | 7.52 | 7.59 | 7.63 | 7.61 | 1006000 | 1000 | 993000 | 1000 | 2007800 | 4467 | 1997000 | 2003333 | 12.4333 | 7.345 | 2.0217 | 7.6083 | 0.485 | 27.52% | 6.375% | 36.43 | 51.1767 | 3.3533 | 7.9483 | 2021702.5 | 1974467 | 2429273.7099 | 81.28% | 27 | 0
2025-04-14 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 335090.89 | 6:38 | 19:06 | 4209.3 | 4402.2 | 4385.8 | 4405.2 | 4407.8 | 4411.1 | 4335.6 | 4491.9 | 4390.5 | 4363.6 | 4317.7 | 4350.2 | 4407 | 4357.6 | 4373.6 | 4466.7 | 4328 | 4380.5 | 4395.9 | 4402.5 | 4397.2 | 4393.8 | 4319.3 | 4361.7 | 4298 | 3747.4 | 4295 | 4271.9 | 4405.7 | 4310.3 | 4339.7 | 4436.1 | 4374.4 | 4450.9 | 4484.1 | 4427.6 | 4477.9 | 4393.5 | 4397.9 | 4388.9 | 4830.5 | 4303.4 | 4757.9 | 4230.3 | 4421.4 | 4952.4 | 4145.5 | 4842.8 | 4092.6 | 4186.3 | 4155.5 | 3896.3 | 4300.7 | 4137.8 | 4298.7 | 4146 | 3991.2 | 4619.4 | 4017 | 4635.8 | 4586.3 | 4018 | 4345.7 | 4102.3 | 4308.7 | 4075 | 4316.4 | 4529.3 | 4641.5 | 4144 | 4572.7 | 3990.5 | 4436.8 | 4340.6 | 4086.1 | 4580.6 | 4021.5 | 4674.4 | 4058.5 | 4559.1 | 4172.2 | 4521.8 | 4217.5 | 4701.7 | 4171.4 | 4457.2 | 4128.3 | 3655.5 | 4464.4 | 4369.2 | 4019.2 | 4660.9 | 4500.9 | 4102.6 | 4041.2 | 4540.7 | 4008.9 | 4257.4 | 4657.5 | 4103.6 | 4672.5 | 4079.9 | 4557.3 | 4159.1 | 4604.3 | 3936.6 | 4636.9 | 4168.2 | 4528.8 | 4091.1 | 4549.9 | 4223 | 4104.5 | 4530.6 | 4154.4 | 4047.1 | 4562.6 | 4654 | 4541.9 | 4164.2 | 4620.7 | 4099 | 4454.3 | 4152.5 | 4369.1 | 3832.7 | 4487.8 | 4110.7 | 4023.9 | 3976 | 3991.5 | 3437.8 | 3899.2 | 3443.5 | 3858.6 | 3896.7 | 4784.6 | 4105.4 | 4819.5 | 4232.8 | 4724 | 4113.2 | 4206.8 | 4051.7 | 4615.2 | 4812.7 | 4731 | 4699.3 | 4729.7 | 4750.6 | 4282.8 | 4767.5 | 4786.8 | 4786.2 | 4816.8 | 4792 | 4805.8 | 4269.2 | 4811.3 | 4275.6 | 37.91 | 37.4 | 38.03 | 38.04 | 37.79 | 37.61 | 0 | 54.69 | 0 | 0 | 54.5 | 54.68 | 2.74 | 2.29 | 2.74 | 0.79 | 2.14 | 2.48 | 6.69 | 7.1 | 6.06 | 6.91 | 6.84 | 7.3 | 7.04 | 7.08 | 7.1 | 7 | 7.13 | 7.15 | 1.84 | 1.93 | 1.72 | 2.28 | 2.13 | 1.86 | 7.32 | 7.38 | 7.26 | 7.3 | 7.33 | 7.32 | 0.48 | 0.53 | 0.45 | 0.48 | 0.46 | 0.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 911254 | 1695 | 898036 | 1717 | 114398.142 | 260.733 | 7.04 | 7.08 | 7.1 | 7 | 7.13 | 7.15 | 7.32 | 7.38 | 7.26 | 7.3 | 7.33 | 7.32 | 347000 | 2000 | 346000 | 2000 | 692000 | 4133 | 689000 | 687867 | 12.4667 | 7.0833 | 1.96 | 7.3183 | 0.485 | 27.67% | 6.627% | 37.7967 | 54.6233 | 2.1967 | 6.8167 | 695047 | 578599 | 705188.2828 | 82.05% | 20 | 0
2025-04-15 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 335090.89 | 6:35 | 19:05 | 10376 | 10827.4 | 10789.4 | 10797.6 | 10842.7 | 10862.7 | 10733.7 | 11003 | 10785.8 | 10745.5 | 10641.6 | 10727.5 | 10827 | 10717 | 10734.6 | 10917.7 | 10756.7 | 10820 | 10838.6 | 10881.9 | 10782.3 | 10885.5 | 10648 | 10763.2 | 10029.9 | 8248.9 | 10639.4 | 10586.7 | 10854.3 | 10658.7 | 10687 | 10877.5 | 10742.5 | 10857.5 | 10942.3 | 10838.6 | 10940.8 | 10765.4 | 10766.1 | 10719.7 | 11421 | 10542.5 | 11355.6 | 10353.1 | 10709.9 | 11564.4 | 10208.2 | 11466.4 | 10820.2 | 10993.1 | 10929.3 | 10277.9 | 11194.7 | 10887.7 | 11188.3 | 10891.9 | 9958.1 | 11308 | 9970.2 | 11323.9 | 11234 | 9977.2 | 10862.3 | 10350.3 | 10544.6 | 9964.3 | 10565.2 | 10962.9 | 11203.9 | 10175.7 | 11101 | 9788.5 | 10829.8 | 10643.6 | 10068.8 | 10990.6 | 9883 | 11271.9 | 9979.7 | 11054.7 | 11849.4 | 12735.7 | 11948.4 | 13008.3 | 11731.5 | 11900.3 | 11689.6 | 10359.7 | 12575.4 | 12315.2 | 11413.8 | 12961.6 | 12652.3 | 11652.5 | 11446.5 | 12690.4 | 11311.8 | 11977.4 | 12886.4 | 11524.1 | 12952.1 | 11491.7 | 12718.2 | 11690.8 | 12794 | 11089.9 | 12875 | 11701.9 | 12725.6 | 11616 | 12788.3 | 11846.7 | 11546.3 | 12642 | 11695.4 | 11391.8 | 12715.7 | 12865 | 12659 | 11690.9 | 12806.4 | 11536.8 | 12502.4 | 11707.1 | 12293.5 | 10777.5 | 12561.6 | 11540.6 | 11504.3 | 11423.3 | 11380.7 | 9809.1 | 11253.5 | 10072.6 | 11093.4 | 11214.4 | 13228.5 | 11783 | 13288.6 | 12115.1 | 13137.3 | 11847.9 | 12075.4 | 11613.9 | 13139.5 | 13563.2 | 13250.1 | 13145.5 | 13158.2 | 13170.9 | 12132.1 | 11921.7 | 13271.5 | 13298.8 | 13293.8 | 13243.4 | 13294.8 | 12229 | 13332.2 | 12256.1 | 39.2964 | 38.6913 | 39.0658 | 39.12 | 38.8815 | 38.8246 | 0 | 52.466 | 0 | 0 | 51.9743 | 51.7495 | 2.913 | 2.7182 | 2.8894 | 0.72096 | 2.6897 | 2.6268 | 6.685 | 9.5417 | 6.3617 | 6.0433 | 5.675 | 6.45 | 7.0321 | 7.0273 | 7.0647 | 6.9834 | 7.0727 | 7.103 | 1.8351 | 1.9404 | 1.7031 | 2.2706 | 2.1186 | 1.8721 | 7.3027 | 7.3234 | 7.2221 | 7.282 | 7.2676 | 7.2514 | 0.48493 | 0.5354 | 0.45749 | 0.49378 | 0.45748 | 0.51055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 912129 | 1714 | 899007 | 1718 | 116218.009 | 262.667 | 7.0321 | 7.0273 | 7.0647 | 6.9834 | 7.0727 | 7.103 | 7.3027 | 7.3234 | 7.2221 | 7.282 | 7.2676 | 7.2514 | 875000 | 19000 | 971000 | 1000 | 1819867 | 1934 | 1826000 | 1817933 | 12.5 | 7.0472 | 1.9566 | 7.2749 | 0.48994 | 27.76% | 6.735% | 38.9799 | 52.0633 | 2.4263 | 6.7928 | 1831071.4 | 1771266 | 2281268.653 | 77.64% | 32 | 46791
2025-04-16 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 335090.89 | 6:33 | 19:06 | 11551.5 | 12085.9 | 12073.3 | 12083 | 12136.6 | 12136.9 | 11997.8 | 12320.2 | 12053 | 12029.5 | 11885.7 | 12023 | 12077.5 | 11971.6 | 12037.9 | 12167.6 | 12040.3 | 12083.7 | 12122.5 | 12154.7 | 12135.4 | 12139 | 11860.8 | 12011.2 | 11847.3 | 10356.1 | 11848.4 | 11803.8 | 12115.5 | 11881.1 | 11917.3 | 12166.8 | 12034.9 | 12179.7 | 12246.5 | 12140 | 12248.6 | 12063.4 | 12062 | 12024.9 | 12891.7 | 11740.4 | 12793.5 | 11528.5 | 11977.7 | 13046.6 | 11358 | 12890.5 | 12081 | 12278.8 | 12168.5 | 11424.2 | 12504.1 | 12155.6 | 12497 | 12184.6 | 11083 | 12693.2 | 11097.8 | 12677.3 | 12564.8 | 11101.8 | 12195.4 | 11569.6 | 11812.4 | 11143 | 11823.3 | 12341.6 | 12615.8 | 11393.1 | 12484.9 | 10934.9 | 12122.6 | 11906.1 | 11206.4 | 12461 | 11030.4 | 12670.4 | 11153 | 12427.2 | 11492.4 | 12402.6 | 11576 | 12750 | 11452.5 | 12203.6 | 11350 | 10042.8 | 12256.7 | 11960.9 | 11063.2 | 12676.8 | 12330.2 | 11291.1 | 11099.7 | 12412.4 | 10982.9 | 11629.7 | 12635.6 | 11197.9 | 12678.3 | 11169.1 | 12416.8 | 11360.1 | 12502 | 10784.9 | 12591.8 | 11373.6 | 12427.4 | 11295.7 | 12481.1 | 11524.6 | 11208.5 | 12356.1 | 11369 | 11081.1 | 12448 | 12615.6 | 12387 | 11364 | 12546.9 | 11212.9 | 12207.7 | 11386.3 | 11968.3 | 10482 | 12258 | 11212.6 | 11170 | 11078 | 11055.4 | 9526 | 10916.4 | 9757.6 | 10801.3 | 10894.3 | 12970 | 11433 | 13058 | 11773 | 12914 | 11501 | 11747 | 11272 | 12732 | 13183 | 12982 | 12903 | 12919.1 | 12939.7 | 11904.8 | 12976.5 | 13029 | 13039 | 13033.8 | 12977.6 | 13037.2 | 11858.8 | 13106.2 | 11927.1 | 38.1784 | 37.7943 | 38.368 | 38.0338 | 37.9074 | 38.0946 | 0 | 53 | 0 | 0 | 52.9294 | 53.3 | 2.7819 | 2.088 | 2.5502 | 1.3258 | 2.3987 | 2.6476 | 8.1167 | 7.235 | 6.395 | 7.545 | 7.6483 | 6.5633 | 6.8566 | 6.8625 | 6.8865 | 6.8094 | 6.9361 | 6.9684 | 1.8124 | 1.8652 | 1.6853 | 2.2424 | 1.9198 | 1.8142 | 7.09 | 7.1089 | 7.0053 | 7.0729 | 7.1013 | 7.1068 | 0.46886 | 0.51603 | 0.44253 | 0.47559 | 0.44155 | 0.49528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 913108 | 1715 | 899972 | 1739 | 118117.876 | 265.267 | 6.8566 | 6.8625 | 6.8865 | 6.8094 | 6.9361 | 6.9684 | 7.09 | 7.1089 | 7.0053 | 7.0729 | 7.1013 | 7.1068 | 979000 | 1000 | 965000 | 21000 | 1899867 | 2600 | 1922000 | 1897267 | 12.55 | 6.8866 | 1.8899 | 7.0809 | 0.47331 | 27.44% | 6.684% | 38.0627 | 53.0765 | 2.2987 | 7.2506 | 1912076.8 | 1854401 | 2235134.4223 | 82.97% | 30 | 1891
2025-04-17 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 335090.89 | 6:37 | 19:07 | 12200.7 | 12652.4 | 12591.6 | 12618.2 | 12648.5 | 12682.5 | 12550.4 | 12806.4 | 12593.5 | 12541.5 | 12478.5 | 12565.7 | 12689 | 12542.1 | 12697.5 | 12779.8 | 12659.4 | 12699.5 | 12717.8 | 12785.8 | 12725.2 | 12747 | 12553.2 | 12651.1 | 12499.8 | 11053.4 | 12512.8 | 12470.5 | 12713.9 | 12501.8 | 12580.5 | 12761.2 | 12772.1 | 12927.9 | 12996.9 | 12888.6 | 12803.7 | 12654.6 | 12640.9 | 12634.3 | 13409.9 | 12444.4 | 13286.4 | 12269 | 12675 | 13632.5 | 12088.6 | 13411.2 | 12674.2 | 12851.7 | 12772 | 12183.3 | 13069.4 | 12774.2 | 13040.4 | 12776.6 | 11788.9 | 13201.4 | 11816 | 13193.2 | 13094.1 | 11806.1 | 12707.8 | 12201.4 | 12459.6 | 11866.3 | 12491.2 | 12890 | 13130.8 | 12113.1 | 13008.9 | 11640.9 | 12709.9 | 12553.7 | 11919 | 12969.7 | 11709 | 13157.3 | 11844 | 12934.5 | 12174.5 | 12897.4 | 12233.2 | 13226.6 | 12126.1 | 12746.1 | 12029.4 | 10668 | 12745.2 | 12545.8 | 11747.2 | 13126.9 | 12836.1 | 11969.3 | 11764.4 | 12887.5 | 11624.1 | 12287.6 | 13074.5 | 11866 | 13129.2 | 11839.7 | 12927.6 | 12049.4 | 12967.8 | 11443.3 | 13066.9 | 12059.9 | 12943.4 | 11983.9 | 12971.4 | 12231.7 | 11889.1 | 12825.5 | 12044.4 | 11747.2 | 12904.4 | 13072.9 | 12858 | 12055.2 | 13013.9 | 11899.5 | 12717.1 | 12071.6 | 12546.1 | 11138 | 12806 | 11917.1 | 11835.4 | 11728.6 | 11711.9 | 10093.3 | 11552.5 | 10321.7 | 11476.3 | 11556.5 | 13428 | 12125 | 13486 | 12403 | 13373 | 12179 | 12377 | 11948 | 13180.9 | 13518.8 | 13441.2 | 13354.5 | 13356.4 | 13390.5 | 12509.6 | 13418.7 | 13488.7 | 13486.6 | 13503.5 | 13471.1 | 13511.8 | 12515.4 | 13550.4 | 12563.8 | 36.4 | 36.06 | 36.66 | 36.17 | 36.07 | 36.37 | 0 | 50.17 | 0 | 0 | 50.67 | 51.24 | 4.43 | 4.78 | 4.08 | 4.08 | 4.63 | 4.46 | 8.07 | 8.35 | 8.09 | 8.14 | 8.39 | 8.17 | 7.19 | 7.28 | 7.25 | 7.14 | 7.27 | 7.3 | 1.89 | 1.98 | 1.76 | 2.34 | 2.05 | 1.91 | 7.47 | 7.47 | 7.36 | 7.4 | 7.42 | 7.44 | 0.5 | 0.55 | 0.47 | 0.51 | 0.47 | 0.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 914086 | 1716 | 900968 | 1739 | 120111.676 | 269.667 | 7.19 | 7.28 | 7.25 | 7.14 | 7.27 | 7.3 | 7.47 | 7.47 | 7.36 | 7.4 | 7.42 | 7.44 | 978000 | 1000 | 996000 | 0 | 1993800 | 4400 | 1973000 | 1989400 | 12.5 | 7.2383 | 1.9883 | 7.4267 | 0.505 | 27.47% | 6.8% | 36.2883 | 50.6933 | 4.41 | 8.2017 | 2006709 | 1953533 | 2395841.7796 | 81.54% | 32 | 0
2025-04-18 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 335090.89 | 6:36 | 19:05 | 11115.1 | 11566.5 | 11508.7 | 11534.5 | 11576.9 | 11600.6 | 11494 | 11800.1 | 11536.6 | 11483 | 11396.9 | 11500 | 11576.1 | 11465 | 11595.7 | 11655.2 | 11562.1 | 11600.3 | 11604.1 | 11660.4 | 11617.2 | 11620.2 | 11458.8 | 11540.9 | 11391.5 | 10118.4 | 11400.1 | 11364.7 | 11611.4 | 11453.7 | 11468.8 | 11642.4 | 11682.6 | 11798.8 | 11880.4 | 11782.2 | 11690.8 | 11538 | 11543.4 | 11542.8 | 12281.2 | 11345 | 12158.6 | 11189 | 11637.4 | 12569.4 | 11038 | 12285.6 | 11567.6 | 11742 | 11654.1 | 11095.5 | 11968.8 | 11696.9 | 11931.6 | 11678.3 | 10756.8 | 12086.7 | 10792.2 | 12069.5 | 11960.1 | 10776 | 11625.9 | 11121.4 | 11379.9 | 10808 | 11367.2 | 11758.7 | 12004.7 | 10992.6 | 11855.6 | 10577.5 | 11590.1 | 11414.9 | 10835.7 | 11856.2 | 10663.2 | 12041.5 | 10790.1 | 11829.8 | 11040.5 | 11754.5 | 11112.9 | 12092 | 11009.7 | 11627.4 | 10950.3 | 9719.9 | 11668 | 11456.5 | 10704.5 | 12052.1 | 11760.4 | 10949.8 | 10825.1 | 11826.2 | 10670.6 | 11199.4 | 11997 | 10803.6 | 12025 | 10774.5 | 11816.6 | 10980.6 | 11864.8 | 10442 | 11946.3 | 10957.5 | 11827.2 | 10908.3 | 11855.8 | 11116.3 | 10817.4 | 11719.5 | 10961.7 | 10706.8 | 11813.1 | 11952 | 11758.4 | 10958.4 | 11891.1 | 10822 | 11603.9 | 10969.5 | 11370.9 | 10175.5 | 11681.8 | 10848.8 | 10837.8 | 10779.3 | 10725.1 | 9278.2 | 10622.3 | 9467.4 | 10575 | 10615.2 | 12348.7 | 11041.3 | 12401.4 | 11295.1 | 12277.7 | 11076 | 11247.6 | 10907.5 | 12086.7 | 12428.5 | 12317.6 | 12256.3 | 12267 | 12296.1 | 11385.5 | 12314.5 | 12403.1 | 12408.3 | 12443.2 | 12390.2 | 12436.8 | 11407.9 | 12453.4 | 11449.2 | 37.79 | 37.35 | 37.64 | 37.48 | 37.4 | 37.65 | 0 | 46.76 | 0 | 0 | 46.41 | 47.35 | 8.59 | 8.72 | 8.46 | 8.02 | 8.72 | 8.75 | 15.18 | 15.7 | 14.62 | 15.46 | 15.53 | 14.9 | 6.57 | 6.64 | 6.6 | 6.48 | 6.6 | 6.65 | 1.85 | 1.78 | 1.72 | 2.19 | 1.92 | 1.69 | 6.73 | 6.78 | 6.66 | 6.69 | 6.73 | 6.66 | 0.52 | 0.58 | 0.49 | 0.53 | 0.51 | 0.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 915005 | 1717 | 901877 | 1741 | 121935.143 | 273.933 | 6.57 | 6.64 | 6.6 | 6.48 | 6.6 | 6.65 | 6.73 | 6.78 | 6.66 | 6.69 | 6.73 | 6.66 | 919000 | 1000 | 909000 | 2000 | 1823467 | 4266 | 1825000 | 1819201 | 12.4833 | 6.59 | 1.8583 | 6.7083 | 0.53167 | 28.2% | 7.925% | 37.5517 | 46.84 | 8.5433 | 15.2317 | 1833798.2 | 1791617.4225 | 2180775.2854 | 82.16% | 28 | 5205
2025-04-19 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 335090.89 | 6:33 | 19:07 | 11176.2 | 11624.8 | 11579.5 | 11584.9 | 11654.2 | 11710.4 | 11673.5 | 11967.5 | 11604 | 11562.1 | 11480.7 | 11579.1 | 11648.7 | 11557.4 | 11638.8 | 11736 | 11624.1 | 11662.1 | 11665.6 | 11720.7 | 11679.3 | 11662.5 | 11506.4 | 11591 | 11444.6 | 10319.7 | 11461.5 | 11424.9 | 11690.7 | 11546.7 | 11525.7 | 11712.4 | 12475.3 | 12574.5 | 12641.5 | 12543.8 | 11768.1 | 11612.2 | 11620.1 | 11612 | 12336.9 | 11333.9 | 12218.8 | 11182.8 | 11718.9 | 12732.7 | 11081.8 | 12342.2 | 11643.1 | 11826.5 | 11733.9 | 11177.3 | 12054.1 | 11778 | 12017.7 | 11748.2 | 10864 | 12167.7 | 10927.7 | 12155 | 12047.9 | 10901.4 | 11692.3 | 11185.8 | 11425.8 | 10904.1 | 11418.3 | 11770.5 | 12091.7 | 11043.2 | 11942.5 | 10706.7 | 11660.4 | 11472.4 | 10948.5 | 11936.5 | 10801.1 | 12147.4 | 10912 | 11916.3 | 11038.9 | 11746.4 | 11130.1 | 12094 | 11028.3 | 11621.2 | 10983.1 | 9990.6 | 11747.8 | 11456.6 | 10781.3 | 12126.6 | 11841.2 | 11094.2 | 11004.4 | 11886.8 | 10801.3 | 11192.4 | 12026.9 | 10829.9 | 12056.7 | 10809 | 11808.1 | 11024.8 | 11887.9 | 10555.3 | 11960 | 10963.5 | 11833.9 | 10940.1 | 11887.8 | 11125.8 | 10850.4 | 11746 | 10979.2 | 10789.1 | 11847.4 | 11965.3 | 11774.3 | 10986.3 | 11903.6 | 10868.9 | 11611.8 | 10983.9 | 11506.3 | 10369.7 | 11674.4 | 10913.5 | 10956.3 | 10938.2 | 10862.6 | 9688.6 | 10845.5 | 9899.5 | 10769.7 | 10797.7 | 12360.1 | 11057.9 | 12414.4 | 11268.8 | 12306.3 | 11123.5 | 11291.2 | 11023.3 | 12074.4 | 12463.2 | 12313.7 | 12266.2 | 12274.8 | 12303.6 | 11378.6 | 12332.7 | 12383.3 | 12397.5 | 12423.5 | 12379.8 | 12411.4 | 11366 | 12459 | 11417.4 | 34.38 | 33.81 | 34.02 | 34.08 | 34.02 | 34.16 | 0 | 46.2 | 0 | 0 | 45.6 | 46.3 | 6.42 | 6.49 | 6.35 | 6.1 | 6.33 | 6.36 | 10.11 | 10.71 | 10.84 | 10.13 | 10.61 | 11.29 | 6.94 | 6.98 | 7 | 6.89 | 7 | 7.03 | 1.86 | 1.91 | 1.74 | 2.23 | 2.04 | 1.83 | 7.11 | 7.11 | 7.04 | 7.06 | 7.11 | 7.07 | 0.54 | 0.61 | 0.52 | 0.56 | 0.54 | 0.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 915933 | 1718 | 902790 | 1742 | 123771.21 | 278.267 | 6.94 | 6.98 | 7 | 6.89 | 7 | 7.03 | 7.11 | 7.11 | 7.04 | 7.06 | 7.11 | 7.07 | 928000 | 1000 | 913000 | 1000 | 1836067 | 4334 | 1839000 | 1831733 | 12.5667 | 6.9733 | 1.935 | 7.0833 | 0.56 | 27.75% | 7.906% | 34.0783 | 46.0333 | 6.3417 | 10.615 | 1847122.9 | 1871178.9212 | 2317495.1369 | 80.74% | 31 | 2760
2025-04-20 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 335090.89 | 6:36 | 19:06 | 12484.3 | 12898.8 | 12872.1 | 12866.1 | 12953.4 | 12992.7 | 12959.2 | 13184.4 | 12868.4 | 12890 | 12768.6 | 12853.6 | 12937.1 | 12832.6 | 12956.4 | 13023.6 | 12902.8 | 12939.6 | 12959.6 | 13036 | 12960 | 12976.6 | 12812.4 | 12893.7 | 12756.1 | 11520.7 | 12768.9 | 12730.7 | 12965 | 12813.8 | 12824.3 | 12986.4 | 13145 | 13223.7 | 13309.5 | 13232.4 | 13049.2 | 12910.8 | 12901.9 | 12889.6 | 13567.4 | 12703.5 | 13454.9 | 12547.4 | 13006.9 | 13890.2 | 12418.9 | 13560.6 | 12944.7 | 13121 | 13036.1 | 12515 | 13304.6 | 13040.5 | 13263.8 | 13033.7 | 12179.3 | 13414.6 | 12260.6 | 13410.1 | 13324.8 | 12229.9 | 13002.3 | 12549.5 | 12737.9 | 12245.2 | 12765 | 13091.5 | 13342.3 | 12412.5 | 13233.9 | 12055.7 | 12960.2 | 12830.8 | 12298.5 | 13207 | 12139.4 | 13397.8 | 12260.4 | 13190.1 | 12441 | 13103 | 12512 | 13406 | 12416 | 12918 | 12334 | 11051 | 13085.5 | 12796.6 | 12175.9 | 13444.4 | 13151.8 | 12452.5 | 12333.9 | 13162.2 | 12134.1 | 12579 | 13303.7 | 12214.8 | 13338.5 | 12200.5 | 13150.1 | 12422.8 | 13179.2 | 11881.3 | 13266.5 | 12358.6 | 13160.2 | 12325.5 | 13194.1 | 12525.2 | 12224 | 13064.6 | 12366.9 | 12156.4 | 13151.4 | 13261.5 | 13086.5 | 12363.5 | 13195 | 12243.4 | 12961.1 | 12377.4 | 12857.9 | 11540 | 13012.6 | 12281.5 | 12327.8 | 12311.9 | 12202 | 10604.7 | 12219.6 | 10894.9 | 12053.3 | 12089.1 | 13585.6 | 12421.8 | 13630.3 | 12625.8 | 13539.5 | 12461.1 | 12626.8 | 12342.2 | 13347.4 | 13658.6 | 13597.2 | 13525.6 | 13531.4 | 13552.1 | 12732.6 | 13577 | 13631.5 | 13636 | 13648.3 | 13626.3 | 13660.1 | 12735.6 | 13697.5 | 12780.2 | 35.25 | 34.76 | 35 | 35 | 35.19 | 35.14 | 0 | 47.8 | 0 | 0 | 47.5 | 48.22 | 5.26 | 4.88 | 5.11 | 4.18 | 5.25 | 4.93 | 10.51 | 10.2 | 9.91 | 10.2 | 10.37 | 9.89 | 7.55 | 7.59 | 7.62 | 7.48 | 7.62 | 7.63 | 1.99 | 2.13 | 1.86 | 2.4 | 2.27 | 2.04 | 7.77 | 7.82 | 7.7 | 7.71 | 7.77 | 7.76 | 0.56 | 0.62 | 0.53 | 0.57 | 0.54 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 916961 | 1720 | 903807 | 1744 | 125809.743 | 282.667 | 7.55 | 7.59 | 7.62 | 7.48 | 7.62 | 7.63 | 7.77 | 7.82 | 7.7 | 7.71 | 7.77 | 7.76 | 1028000 | 2000 | 1017000 | 2000 | 2038533 | 4400 | 2041000 | 2034133 | 12.5 | 7.5817 | 2.115 | 7.755 | 0.57 | 27.9% | 7.35% | 35.0567 | 47.84 | 4.935 | 10.18 | 2052833.9 | 2000800 | 2503528.7197 | 79.92% | 26 | 0
2025-04-21 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 335090.89 | 6:30 | 19:10 | 12685.7 | 13134.5 | 13119.1 | 13095.7 | 13212.1 | 13207.3 | 13174.7 | 13545.1 | 13133.3 | 13126.9 | 13004.2 | 13112.5 | 13158.1 | 13054.7 | 13190.2 | 13249.2 | 13131.2 | 13167.2 | 13184.6 | 13263 | 13189 | 13205.8 | 13022.1 | 13111.4 | 12979.1 | 11635 | 12997.4 | 12953.6 | 13192.7 | 13031.3 | 13047.2 | 13213.6 | 13377.4 | 13435.2 | 13529.3 | 13442.9 | 13290.8 | 13142.3 | 13128.5 | 13101.7 | 13891.5 | 12985.7 | 13769 | 12814.3 | 13283.9 | 14213.6 | 12666 | 13888.6 | 13180.9 | 13372.8 | 13290.9 | 12739.2 | 13563.9 | 13275.6 | 13509.6 | 13269.7 | 12365.9 | 13666.9 | 12448 | 13663.5 | 13575.2 | 12424 | 13254.6 | 12782.4 | 12983.7 | 12386.2 | 12974.2 | 13340.5 | 13582.3 | 12610.7 | 13465.9 | 12178.1 | 13182.1 | 13033.9 | 12488 | 13437.4 | 12299.4 | 13646 | 12459.9 | 13442.7 | 12704.8 | 13387.7 | 12772.7 | 13688.3 | 12668 | 13245.2 | 12610.5 | 11219.8 | 13352.5 | 13052.9 | 12401.7 | 13711.1 | 13412.3 | 12661.9 | 12521.4 | 13438.6 | 12332.9 | 12842.7 | 13596.2 | 12470.8 | 13630.2 | 12454.1 | 13452.2 | 12673.8 | 13473.9 | 12067.5 | 13568.1 | 12625.7 | 13437.5 | 12542.4 | 13470.4 | 12782.7 | 12460 | 13339.4 | 12620.5 | 12366 | 13428 | 13550.3 | 13369 | 12612.6 | 13484.8 | 12474.7 | 13244.6 | 12631.8 | 13115.9 | 11693.7 | 13295 | 12501.2 | 12590.9 | 12577 | 12429.3 | 10767.3 | 12356.6 | 10944.9 | 12207.4 | 12274 | 13880.3 | 12672.3 | 13922.8 | 12891.6 | 13833.1 | 12706.7 | 12878.2 | 12603.8 | 13652.7 | 13982.3 | 13891.6 | 13818.1 | 13825.7 | 13843.6 | 13008 | 13873.5 | 13932.6 | 13929.3 | 13936.4 | 13903.2 | 13953.7 | 12997.9 | 14000.2 | 13049.2 | 35.382 | 34.9461 | 35.3994 | 35.2696 | 35.4766 | 35.1683 | 0 | 49.1552 | 0 | 0 | 49.4 | 49.8523 | 3.5867 | 2.873 | 3.2732 | 1.848 | 3.4111 | 3.317 | 8.7783 | 9.455 | 8.4467 | 9.2817 | 9.0333 | 8.3417 | 7.7368 | 7.7579 | 7.7875 | 7.6666 | 7.8154 | 7.8451 | 2.0449 | 2.1564 | 1.9073 | 2.454 | 2.3068 | 2.0655 | 7.911 | 7.9574 | 7.844 | 7.9103 | 7.9443 | 7.9 | 0.56635 | 0.62862 | 0.53546 | 0.57427 | 0.54426 | 0.59749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 918007 | 1721 | 904844 | 1745 | 127887.01 | 287.067 | 7.7368 | 7.7579 | 7.7875 | 7.6666 | 7.8154 | 7.8451 | 7.911 | 7.9574 | 7.844 | 7.9103 | 7.9443 | 7.9 | 1046000 | 1000 | 1037000 | 1000 | 2077267 | 4400 | 2081000 | 2072867 | 12.6667 | 7.7682 | 2.1558 | 7.9112 | 0.57441 | 27.75% | 7.261% | 35.2737 | 49.4692 | 3.0515 | 8.8894 | 2091974.5 | 2035601 | 2522395.478 | 80.7% | 27 | 0
2025-04-22 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 335090.89 | 6:26 | 19:14 | 13163.5 | 13581.5 | 13541.4 | 13553 | 13658.1 | 13665.1 | 13640.5 | 13911.3 | 13616.5 | 13557 | 13495.4 | 13576.9 | 13638 | 13527.4 | 13640.1 | 13685.8 | 13572.1 | 13602.2 | 13615.1 | 13705.3 | 13624.8 | 13640.4 | 13489.6 | 13562.9 | 13443.8 | 12273.5 | 13452.6 | 13414.2 | 13639.9 | 13488 | 13505.6 | 13650.4 | 13881.3 | 13949.9 | 14064.1 | 13976.4 | 13728.6 | 13596.2 | 13580 | 13538.3 | 14275.3 | 13477.1 | 14154.6 | 13336.7 | 13758.9 | 14578.4 | 13167.9 | 14253.9 | 13609.6 | 13801.4 | 13731.9 | 13263.9 | 13983.7 | 13750 | 13933.3 | 13703.7 | 12910.7 | 14071.8 | 12994.4 | 14065.3 | 13976.4 | 12959 | 13681.5 | 13252 | 13458.7 | 12952.1 | 13448.8 | 13795.1 | 13988.2 | 13136.9 | 13877.5 | 12798.3 | 13618.4 | 13502.3 | 13023.7 | 13852.8 | 12866.5 | 14051.2 | 12998.5 | 13861.5 | 13245.1 | 13863.1 | 13297.3 | 14118.3 | 13215 | 13725.3 | 13148.1 | 11905.3 | 13800.4 | 13561.7 | 12971 | 14116.5 | 13841.6 | 13176.6 | 13047.6 | 13920.2 | 12987.6 | 13381.4 | 14038.1 | 13032.4 | 14054 | 13020.7 | 13912.5 | 13232.3 | 13918.2 | 12716.9 | 14009 | 13162.2 | 13877.4 | 13071.4 | 13946.4 | 13336.9 | 13036.7 | 13824.8 | 13171.6 | 12977.7 | 13877.2 | 14008.1 | 13831.8 | 13176.4 | 13932.3 | 13050.3 | 13725.1 | 13186.3 | 13621.4 | 12382.4 | 13773.6 | 13109.3 | 13149.3 | 13114.8 | 13057.3 | 11426.6 | 12954 | 11676.4 | 12921.7 | 12958.4 | 14238.5 | 13194.3 | 14306.4 | 13418.8 | 14215.4 | 13235.2 | 13392.2 | 13182.5 | 14101.5 | 14379.4 | 14310.6 | 14238.4 | 14241 | 14248.3 | 13528.8 | 14281.6 | 14317.5 | 14320.1 | 14320.2 | 14288.6 | 14339.7 | 13519.4 | 14396.6 | 13556.5 | 35.8578 | 35.5281 | 35.8394 | 35.8927 | 36.1299 | 35.6888 | 0 | 47.7887 | 0 | 0 | 47.5 | 47.5505 | 4.4905 | 3.95 | 4.2086 | 2.8445 | 4.2561 | 3.796 | 8.585 | 8.415 | 7.9133 | 8.2233 | 8.58 | 7.845 | 8.128 | 8.1827 | 8.2162 | 8.1031 | 8.2556 | 8.2943 | 2.1698 | 2.2593 | 2.0268 | 2.6019 | 2.4435 | 2.1862 | 8.2836 | 8.3638 | 8.2316 | 8.346 | 8.3568 | 8.3265 | 0.58771 | 0.65402 | 0.55341 | 0.60117 | 0.56158 | 0.62392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 919090 | 1723 | 905922 | 1747 | 130040.477 | 291.2 | 8.128 | 8.1827 | 8.2162 | 8.1031 | 8.2556 | 8.2943 | 8.2836 | 8.3638 | 8.2316 | 8.346 | 8.3568 | 8.3265 | 1083000 | 2000 | 1078000 | 2000 | 2153467 | 4133 | 2157000 | 2149334 | 12.8 | 8.1966 | 2.2812 | 8.318 | 0.59697 | 27.83% | 7.177% | 35.8228 | 47.6131 | 3.9243 | 8.2603 | 2169534.1 | 2108067 | 2649342.7305 | 79.57% | 29 | 0
2025-04-23 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 335090.89 | 6:23 | 19:15 | 12854.5 | 13324.6 | 13258.3 | 13281 | 13399.8 | 13412.9 | 13429.7 | 13700.5 | 13327.3 | 13266.7 | 13201 | 13285.3 | 13362.6 | 13247.4 | 13342 | 13406.4 | 13293 | 13326.8 | 13357.4 | 13435.2 | 13367.8 | 13387.2 | 13190.8 | 13282.1 | 13148.5 | 11797.8 | 13166.1 | 13117.8 | 13368.5 | 13227 | 13221.6 | 13381.3 | 13419 | 13482.9 | 13622 | 13518.1 | 13467 | 13313.1 | 13305.9 | 13257.2 | 14025.1 | 13147.1 | 13905.3 | 12998.2 | 13418.2 | 14292.6 | 12837.8 | 14013.3 | 13323.9 | 13520.7 | 13448.2 | 12936.3 | 13714.5 | 13508.9 | 13671.1 | 13421.8 | 12510.5 | 13814.2 | 12597.3 | 13798.5 | 13693.5 | 12585.1 | 13432.5 | 12980.6 | 13152.5 | 12546.8 | 13130.4 | 13476.8 | 13709.6 | 12777 | 13601.5 | 12336.9 | 13360.4 | 13193.5 | 12665.3 | 13577.8 | 12455.6 | 13794.4 | 12615.1 | 13587.4 | 12881.1 | 13552.2 | 12960.1 | 13842.4 | 12859.9 | 13426.7 | 12804.4 | 11407.5 | 13495.2 | 13241.2 | 12559.1 | 13860.3 | 13584.2 | 12868 | 12724.6 | 13638.3 | 12661.9 | 13049.8 | 13791.7 | 12649.9 | 13760.5 | 12644.2 | 13607.9 | 12869.6 | 13639.9 | 12259.2 | 13720.8 | 12784.4 | 13590 | 12745.4 | 13664.3 | 12966.6 | 12645 | 13542.6 | 12808.1 | 12575.9 | 13601.9 | 13705.1 | 13555.2 | 12801.2 | 13640.8 | 12649.8 | 13436.9 | 12813.5 | 13322.2 | 11852.1 | 13459.4 | 12682.6 | 12759.3 | 12744.6 | 12638.2 | 10922 | 12577 | 11207.6 | 12540.3 | 12590.9 | 13981.5 | 12878.3 | 14093.6 | 13104.2 | 13984 | 12921.9 | 13078.1 | 12852.6 | 13841.8 | 14168.8 | 14053.3 | 13980.5 | 13988.3 | 14001.3 | 13215 | 14048.4 | 14074.2 | 14090.7 | 14101.6 | 14055.1 | 14116.1 | 13213.4 | 14147.6 | 13250.1 | 37.1699 | 36.713 | 37.1733 | 37.2111 | 37.4601 | 37.068 | 0 | 50.3247 | 0 | 0 | 50.5 | 50.965 | 3.6256 | 2.899 | 3.4472 | 1.6726 | 3.5661 | 3.3419 | 8.48 | 7.7317 | 7.5283 | 7.26 | 7.1483 | 7.8817 | 7.9011 | 7.9265 | 7.9349 | 7.8447 | 7.9781 | 8.0296 | 2.1093 | 2.1841 | 1.9686 | 2.5292 | 2.3596 | 2.1081 | 8.045 | 8.0888 | 7.9478 | 8.057 | 8.0643 | 8.0642 | 0.56481 | 0.63283 | 0.53662 | 0.57918 | 0.5438 | 0.60536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 920148 | 1723 | 906974 | 1748 | 132145.01 | 294.467 | 7.9011 | 7.9265 | 7.9349 | 7.8447 | 7.9781 | 8.0296 | 8.045 | 8.0888 | 7.9478 | 8.057 | 8.0643 | 8.0642 | 1058000 | 0 | 1052000 | 1000 | 2104533 | 3267 | 2109000 | 2101266 | 12.8667 | 7.9358 | 2.2098 | 8.0445 | 0.5771 | 27.85% | 7.174% | 37.1326 | 50.5966 | 3.0921 | 7.6717 | 2119554.2 | 2063067 | 2552057.5986 | 80.84% | 29 | 0
2025-04-24 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 335090.89 | 6:26 | 19:12 | 12717.8 | 13224.5 | 13176.8 | 13147.7 | 13287.3 | 13283.2 | 13301.2 | 13519.8 | 13195.4 | 13133.1 | 13056.6 | 13140.3 | 13239.2 | 13106 | 13229.3 | 13289 | 13173 | 13199.1 | 13238.2 | 13320.3 | 13245.3 | 13263.4 | 13064 | 13152.5 | 13005 | 11582.1 | 13018.5 | 12979.8 | 13255.7 | 13129.4 | 13087.6 | 13256.2 | 13233.9 | 13299.2 | 13428.8 | 13331.9 | 13339.7 | 13175.7 | 13161 | 13136.3 | 13901.4 | 13015 | 13786.3 | 12844.8 | 13198.5 | 14071.8 | 12698.8 | 13886.7 | 13182.7 | 13378.7 | 13319.5 | 12778 | 13592.8 | 13367.3 | 13547.9 | 13296.6 | 12322.1 | 13709 | 12389.1 | 13682.2 | 13573.5 | 12380.8 | 13310.8 | 12836.2 | 13009.8 | 12371.5 | 12982.1 | 13353.4 | 13598.6 | 12613 | 13476.9 | 12127.2 | 13217.1 | 13057.3 | 12478.6 | 13454 | 12264.9 | 13670.7 | 12435.9 | 13460.3 | 12730.9 | 13441.4 | 12815.6 | 13747.7 | 12712.4 | 13304 | 12665.1 | 11214.7 | 13389.4 | 13120.5 | 12373.6 | 13770.6 | 13497.5 | 12749.3 | 12616.1 | 13532.4 | 12490.5 | 12911.7 | 13703.4 | 12494.9 | 13679.3 | 12470.9 | 13507.2 | 12715.1 | 13547 | 12074 | 13631.7 | 12637.7 | 13508.1 | 12591.4 | 13561.8 | 12809.9 | 12476.6 | 13425.4 | 12651.8 | 12390 | 13496.5 | 13611.4 | 13441.8 | 12629.5 | 13540.4 | 12482.8 | 13309.3 | 12640.3 | 13183.3 | 11674.6 | 13340.8 | 12492.4 | 12566.7 | 12548 | 12448.9 | 10735.9 | 12381.1 | 11010.7 | 12347.2 | 12410.7 | 13880.4 | 12722 | 13998.2 | 12953.2 | 13896.9 | 12771.2 | 12945.1 | 12696.7 | 13736.1 | 14079.2 | 13949.4 | 13879.3 | 13882 | 13901.2 | 13067.1 | 13943 | 13977.8 | 13986.7 | 14002.4 | 13961 | 14018.3 | 13059.3 | 14058.9 | 13105.9 | 38.0747 | 37.6124 | 37.9132 | 38.0461 | 38.1228 | 37.9607 | 0 | 50.7 | 0 | 0 | 50.8 | 51.3793 | 4.4579 | 4.2877 | 4.3097 | 2.4896 | 4.2938 | 4.1789 | 9.3317 | 8.7583 | 8.4433 | 9.9917 | 9.1317 | 8.6467 | 7.7399 | 7.8042 | 7.7782 | 7.6934 | 7.8101 | 7.9067 | 2.0599 | 2.1474 | 1.9243 | 2.479 | 2.3136 | 2.0613 | 7.8736 | 7.9552 | 7.7899 | 7.8928 | 7.914 | 7.8905 | 0.55385 | 0.62 | 0.52681 | 0.56835 | 0.53544 | 0.59263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 921192 | 1725 | 908012 | 1750 | 134228.277 | 298.733 | 7.7399 | 7.8042 | 7.7782 | 7.6934 | 7.8101 | 7.9067 | 7.8736 | 7.9552 | 7.7899 | 7.8928 | 7.914 | 7.8905 | 1044000 | 2000 | 1038000 | 2000 | 2083267 | 4266 | 2078000 | 2079001 | 12.7667 | 7.7888 | 2.1643 | 7.886 | 0.56618 | 27.79% | 7.18% | 37.955 | 50.9598 | 4.003 | 9.0506 | 2097488.8 | 2039600 | 2501438.2635 | 81.54% | 29 | 0
2025-04-25 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 335090.89 | 6:28 | 19:11 | 12294 | 12797.3 | 12718.6 | 12728.8 | 12795.4 | 12791.8 | 12813.5 | 13065.7 | 12744 | 12673.4 | 12597.7 | 12669.1 | 12775.3 | 12619.7 | 12706.8 | 12779.2 | 12662.1 | 12662.4 | 12740.7 | 12815.3 | 12725.2 | 12727.8 | 12524.2 | 12616.3 | 12460 | 11108.4 | 12479.9 | 12455.7 | 12687.7 | 12552.4 | 12504.5 | 12684.1 | 12641.7 | 12717.2 | 12849.6 | 12764.1 | 12756.4 | 12591.3 | 12579.7 | 12543.4 | 13147.5 | 12307.8 | 13037.4 | 12049.2 | 12599 | 13429.9 | 12087.9 | 13164.7 | 12656.7 | 12846.5 | 12760 | 12264.9 | 12916.9 | 12861.7 | 13004.8 | 12736.8 | 11868.3 | 13166.9 | 11914.8 | 13128 | 12920.8 | 11915.8 | 12794.7 | 12370.6 | 12546.5 | 11955.1 | 12509.6 | 12883 | 13074.2 | 12196.1 | 12961.7 | 11702 | 12736.6 | 12581.2 | 12039.5 | 12968.9 | 11830.4 | 13162.5 | 12017.1 | 12976.6 | 12277.6 | 12928 | 12400.2 | 12813 | 12265.8 | 12625.9 | 12218.8 | 10788.5 | 12821.5 | 12615.5 | 11866.5 | 13132.4 | 12849.2 | 12194.2 | 12027.7 | 12896.9 | 11952.7 | 12358 | 13056.8 | 11956.8 | 12972.5 | 11900 | 12816.9 | 12115.2 | 12845.5 | 11483.2 | 12927.6 | 12037.6 | 12803.1 | 11947.5 | 12835.8 | 12150.6 | 11971.9 | 12863.6 | 12111.6 | 11885.8 | 12899.4 | 12993.6 | 12857.8 | 12086.4 | 12926.1 | 11935.4 | 12706.9 | 12012.5 | 12614.6 | 11126.2 | 12747.2 | 11948.8 | 12052.6 | 12073.6 | 11876.2 | 10267.8 | 11926.7 | 10590.8 | 12004.4 | 12049.4 | 13381.7 | 12336.3 | 13542.8 | 12520.5 | 13406.6 | 12407.1 | 12549.5 | 12344.8 | 13336 | 13676.9 | 13357.8 | 13401.9 | 13373.5 | 13273.2 | 12661.1 | 13472.3 | 13480.3 | 13541.3 | 13577 | 13337.1 | 13544.3 | 12691.7 | 13606.6 | 12714.1 | 38.1522 | 37.7753 | 38.0319 | 37.8129 | 37.6664 | 38.0787 | 0 | 49.9 | 0 | 0 | 50 | 50.9995 | 5.5839 | 5.73 | 5.7322 | 5.2445 | 5.7477 | 5.6111 | 9.7283 | 10.83 | 10.045 | 10.9333 | 10.8283 | 10.705 | 7.4582 | 7.4814 | 7.3431 | 7.3657 | 7.4783 | 7.6501 | 2.0232 | 2.0423 | 1.859 | 2.4278 | 2.2171 | 1.9821 | 7.5719 | 7.5904 | 7.3391 | 7.5723 | 7.5797 | 7.6174 | 0.54805 | 0.61473 | 0.51393 | 0.56239 | 0.53438 | 0.59351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 922200 | 1726 | 909014 | 1751 | 136226.611 | 301.667 | 7.4582 | 7.4814 | 7.3431 | 7.3657 | 7.4783 | 7.6501 | 7.5719 | 7.5904 | 7.3391 | 7.5723 | 7.5797 | 7.6174 | 1008000 | 1000 | 1002000 | 1000 | 1998334 | 2934 | 2008000 | 1995400 | 12.7167 | 7.4628 | 2.0919 | 7.5451 | 0.56116 | 28.03% | 7.437% | 37.9196 | 50.2998 | 5.6082 | 10.5117 | 2012458.2 | 1957867 | 2419487.3874 | 80.92% | 25 | 0
2025-04-26 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 335090.89 | 6:27 | 19:18 | 12203.6 | 12788.4 | 12736 | 12709.9 | 12850.2 | 12888.5 | 12896.9 | 13186.9 | 12755.9 | 12682.6 | 12618.4 | 12695.7 | 12824.6 | 12663.4 | 12798.1 | 12878.5 | 12741.5 | 12756.6 | 12829.5 | 12895.3 | 12833 | 12823.7 | 12611.6 | 12722.6 | 12573 | 11037.5 | 12575.1 | 12538.8 | 12826.3 | 12706.6 | 12657.1 | 12855.2 | 12758.8 | 12826.8 | 12938.5 | 12840.9 | 12932.8 | 12757.5 | 12749.3 | 12684.5 | 13519.5 | 12501.8 | 13398.9 | 12283.8 | 12831.1 | 13741.7 | 12227.4 | 13493.9 | 12754.2 | 12970.3 | 12869.8 | 12195.1 | 13168.7 | 12970.6 | 13161.8 | 12895.7 | 11742.4 | 13312.6 | 11795.5 | 13282.8 | 13161.9 | 11807.8 | 12869.4 | 12329.1 | 12567.8 | 11796.5 | 12506.6 | 12930.2 | 13180.1 | 12064.7 | 13042.2 | 11566.1 | 12794.4 | 12586.2 | 11891.4 | 13042.2 | 11659.3 | 13269.6 | 11884 | 13069.3 | 12174 | 13016 | 12317 | 13311 | 12182 | 12863 | 12130 | 10671 | 12940.5 | 12677.3 | 11772.4 | 13315.6 | 13019.9 | 12156 | 11999.5 | 13102.9 | 11900.4 | 12367.3 | 13249 | 11867 | 13233 | 11844 | 13053.1 | 12099.5 | 13107.5 | 11447.1 | 13165 | 12001.3 | 13038.6 | 11960.1 | 13120.8 | 12180.9 | 11855.2 | 12956.7 | 12031.8 | 11737.6 | 13015.8 | 13125.2 | 12956.3 | 12000.8 | 13047.9 | 11833.9 | 12821.8 | 12007.2 | 12683.2 | 11052.2 | 12853.8 | 11847.4 | 11941.7 | 11947.5 | 11797.1 | 10179.6 | 11810.9 | 10472.4 | 11737.7 | 11800.9 | 13450.1 | 12134.8 | 13547.9 | 12425.8 | 13422.1 | 12245 | 12456.3 | 12148.6 | 6657.4 | 6853.2 | 6743.5 | 6723.9 | 6723.6 | 6733.5 | 6284.1 | 6756.6 | 13532.7 | 13563.9 | 13581.6 | 13512.9 | 13579.6 | 12561.3 | 13628.3 | 12614 | 38.0485 | 37.4991 | 37.9464 | 38.0382 | 37.9865 | 37.7698 | 0 | 51.1 | 0 | 0 | 51.2286 | 51.856 | 3.6306 | 3.3534 | 3.4762 | 2.9331 | 3.4912 | 3.4239 | 8.1683 | 7.12 | 6.2333 | 6.8583 | 6.9383 | 6.8417 | 7.2965 | 7.3299 | 7.3342 | 7.2354 | 7.3326 | 7.4409 | 1.9676 | 2.071 | 1.8317 | 2.3757 | 2.212 | 1.9936 | 7.3867 | 7.4619 | 7.341 | 7.4219 | 7.4042 | 7.4475 | 0.56066 | 0.62913 | 0.53395 | 0.58185 | 0.54191 | 0.59574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 923208 | 1727 | 909961 | 1752 | 138179.811 | 304.933 | 7.2965 | 7.3299 | 7.3342 | 7.2354 | 7.3326 | 7.4409 | 7.3867 | 7.4619 | 7.341 | 7.4219 | 7.4042 | 7.4475 | 1008000 | 1000 | 947000 | 1000 | 1953200 | 3266 | 1953000 | 1949934 | 12.85 | 7.3283 | 2.0753 | 7.4105 | 0.57387 | 28.32% | 7.744% | 37.8814 | 51.3949 | 3.3847 | 7.0267 | 1966464.5 | 1933667 | 2384346.2582 | 81.1% | 32 | 0
2025-04-27 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 335090.89 | 6:28 | 19:16 | 12236.3 | 12808.1 | 12780.8 | 12751 | 12878.6 | 12914.8 | 12937.6 | 13297.3 | 12818.9 | 12721.8 | 12674.6 | 12765.3 | 12849.5 | 12706 | 12796.3 | 12898.9 | 12757.9 | 12786.5 | 12847.9 | 12916.4 | 12840.2 | 12852.8 | 12610.8 | 12736.4 | 12584.2 | 11053.3 | 12588.7 | 12547.7 | 12841.9 | 12691.9 | 12650.9 | 12863.3 | 12823.7 | 12853.4 | 12963.9 | 12867.5 | 12950.4 | 12770.7 | 12768.5 | 12714.4 | 13574.3 | 12517.9 | 13442.4 | 12302 | 12692.5 | 13667 | 12226.9 | 13555.6 | 12792.5 | 13000.9 | 12890.8 | 12252.4 | 13207.1 | 12996.6 | 13175.4 | 12900.4 | 11768.1 | 13345.3 | 11818.3 | 13329.7 | 13219.7 | 11842.5 | 12904.6 | 12386.2 | 12563.7 | 11823.7 | 12524.8 | 12973 | 13247.6 | 12093.7 | 13117.5 | 11608 | 12810.4 | 12612.4 | 11928.5 | 13105.9 | 11712.2 | 13342.9 | 11940.5 | 13136.1 | 12187 | 13010 | 12316 | 13319 | 12188 | 12859 | 12115 | 10688 | 12983.6 | 12663.5 | 11819.1 | 13349.7 | 13012 | 12157.8 | 11988.3 | 13142 | 11923.9 | 12396.6 | 13287.5 | 11917.2 | 13268 | 11895.1 | 13089.4 | 12153.1 | 13132.9 | 11505.3 | 13204.2 | 12071.5 | 13081.4 | 12018.9 | 13144.1 | 12243.2 | 11884.8 | 12983.2 | 12080.9 | 11790.9 | 13056.5 | 13191.6 | 12999.7 | 12057.9 | 13114 | 11900.8 | 12861.7 | 12066.2 | 12714.5 | 11117.4 | 12893.9 | 11897.5 | 12055 | 12085.8 | 11858.2 | 10260 | 11890.2 | 10530 | 11792.6 | 11841 | 13532.7 | 12207.2 | 13609.5 | 12476.9 | 13487.7 | 12291.3 | 12491.4 | 12203.1 | 13427.4 | 13860.5 | 13566.8 | 13474.6 | 13484.6 | 13509.7 | 12631.6 | 13565.5 | 13592.4 | 13620.3 | 13634 | 13566.8 | 13632 | 12602.4 | 13686 | 12654 | 39.8816 | 39.3282 | 39.9138 | 39.8422 | 39.8266 | 39.4996 | 0 | 53.0533 | 0 | 0 | 52.9 | 53.3142 | 2.7855 | 1.9115 | 2.5634 | 1.042 | 2.6052 | 2.1242 | 8.0817 | 6.895 | 7.815 | 6.5417 | 6.54 | 6.42 | 7.4359 | 7.4581 | 7.4699 | 7.3696 | 7.5563 | 7.5915 | 1.9925 | 2.0991 | 1.8677 | 2.4158 | 2.2505 | 2.0194 | 7.5112 | 7.5839 | 7.4502 | 7.5477 | 7.577 | 7.5767 | 0.55144 | 0.61742 | 0.52496 | 0.57037 | 0.53495 | 0.59107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 924218 | 1729 | 910965 | 1753 | 140192.411 | 309.267 | 7.4359 | 7.4581 | 7.4699 | 7.3696 | 7.5563 | 7.5915 | 7.5112 | 7.5839 | 7.4502 | 7.5477 | 7.577 | 7.5767 | 1010000 | 2000 | 1004000 | 1000 | 2012600 | 4334 | 2011000 | 2008266 | 12.8 | 7.4802 | 2.1075 | 7.5411 | 0.56504 | 28.17% | 7.493% | 39.7153 | 53.0892 | 2.172 | 7.0489 | 2025932.1 | 1967668 | 2361247.7041 | 83.33% | 28 | 0
2025-04-28 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 335090.89 | 6:24 | 19:15 | 12107.7 | 12728.4 | 12683 | 12655.5 | 12788.8 | 12830 | 12838 | 13225.8 | 12750.1 | 12643.1 | 12576.8 | 12686.8 | 12759.2 | 12622.6 | 12692.4 | 12810.7 | 12662.1 | 12695 | 12761.3 | 12816.3 | 12759.3 | 12754.3 | 12503.4 | 12631.8 | 12467.3 | 10898.2 | 12457.7 | 12422.9 | 12758.2 | 12603.5 | 12552.5 | 12792.8 | 12712.1 | 12752.2 | 12861.7 | 12760.2 | 12884.8 | 12692.1 | 12702.8 | 12627.3 | 13557 | 12413.8 | 13434.6 | 12187.7 | 12692.5 | 13711.9 | 12099.6 | 13533.3 | 12697 | 12912.1 | 12799.6 | 12080 | 13136 | 12928.2 | 13103.2 | 12806.9 | 11601.4 | 13287.2 | 11661.4 | 13259.1 | 13133.4 | 11673.1 | 12828.8 | 12237.2 | 12438.1 | 11648.7 | 12372.9 | 12887 | 13180.5 | 11916.2 | 13039.5 | 11425.3 | 12688.2 | 12460.8 | 11734.1 | 13025.8 | 11539.8 | 13255.7 | 11738.3 | 13052.2 | 12027.3 | 12932.5 | 12147.9 | 13263.3 | 12028.3 | 12768.7 | 11979.6 | 10546 | 12944.7 | 12549.2 | 11660.8 | 13307 | 12968.3 | 12033.6 | 11875.6 | 13062.8 | 11732.4 | 12246.9 | 13208.6 | 11761.5 | 13208 | 11730.3 | 12996.4 | 11928.9 | 13065.8 | 11338.1 | 13124.7 | 11910.5 | 12988.2 | 11850.5 | 12901.4 | 12068.9 | 11743.5 | 12898.4 | 11933 | 11641 | 12980.1 | 13103.6 | 12922.5 | 11910.2 | 13035.6 | 11744.4 | 12764 | 11901.6 | 12612.8 | 10952.3 | 12794.4 | 11741.4 | 11903 | 11941.5 | 11722.7 | 10134 | 11691.1 | 10351.9 | 11613.3 | 11667.1 | 13511.1 | 12077.3 | 13583.7 | 12367 | 13454.9 | 12147.3 | 12376.1 | 12045.3 | 13405.3 | 13865.3 | 13489.4 | 13412.5 | 13418.4 | 13451.4 | 12506.8 | 13513.5 | 13531.8 | 13573.4 | 13591.5 | 13513.9 | 13595.2 | 12480.8 | 13642 | 12539.4 | 39.5615 | 39.0471 | 39.5931 | 39.394 | 39.4673 | 39.2956 | 0 | 53.5 | 0 | 0 | 53.5 | 54.2458 | 3.1908 | 2.6464 | 2.9372 | 1.2685 | 2.7654 | 2.8809 | 9.81 | 8.2817 | 8.1217 | 8.2917 | 8.0667 | 7.63 | 7.4336 | 7.4429 | 7.4744 | 7.4125 | 7.5023 | 7.5458 | 1.943 | 2.0512 | 1.823 | 2.3544 | 2.2009 | 1.9838 | 7.5 | 7.5441 | 7.4256 | 7.4878 | 7.5359 | 7.5421 | 0.53621 | 0.60073 | 0.51166 | 0.55003 | 0.51945 | 0.57317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 925221 | 1730 | 911960 | 1755 | 142188.278 | 313 | 7.4336 | 7.4429 | 7.4744 | 7.4125 | 7.5023 | 7.5458 | 7.5 | 7.5441 | 7.4256 | 7.4878 | 7.5359 | 7.5421 | 1003000 | 1000 | 995000 | 2000 | 1995867 | 3733 | 1995000 | 1992134 | 12.85 | 7.4686 | 2.0594 | 7.5059 | 0.54854 | 27.57% | 7.308% | 39.3931 | 53.7486 | 2.6149 | 8.3669 | 2009060.2 | 1975400 | 2389697.0667 | 82.66% | 24 | 0
2025-04-29 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 335090.89 | 6:25 | 19:17 | 11396.6 | 11935.6 | 11908.9 | 11888.8 | 11987 | 12043.5 | 12074.1 | 12444.7 | 11963.4 | 11872.7 | 11782.1 | 11891.9 | 11952.8 | 11823 | 11893.3 | 12016.3 | 11873.9 | 11906.1 | 11957.8 | 12010.1 | 11961.7 | 11954.2 | 11722 | 11838 | 11669.6 | 10245.3 | 11666.8 | 11620.2 | 11953.4 | 11795.1 | 11753.9 | 11986.9 | 11920 | 11956.4 | 12052.9 | 11944 | 12048.6 | 11861.5 | 11875.3 | 11835.4 | 12785.5 | 11659 | 12659.3 | 11460.8 | 11973.8 | 13039.3 | 11404.1 | 12800.4 | 11910.4 | 12110 | 11995.7 | 11353 | 12318.6 | 12115.6 | 12283.4 | 11983.6 | 10918.9 | 12466.4 | 10994.6 | 12449.9 | 12332.6 | 10997.1 | 12014.8 | 11473.3 | 11642.7 | 10933.3 | 11581.4 | 12047.8 | 12347.6 | 11157.3 | 12180.9 | 10698.3 | 11872 | 11642.5 | 11034 | 12179.7 | 10846.7 | 12430.3 | 11014.7 | 12217.6 | 11259.4 | 12103.8 | 11279.9 | 12470 | 11249.2 | 11932 | 11215.1 | 9878.1 | 12120.3 | 11755.1 | 10927.7 | 12528.9 | 12191.8 | 11283 | 11143.4 | 12288.5 | 11010.2 | 11487.8 | 12496.1 | 11052.1 | 12493.1 | 11021.6 | 12224.1 | 11170.3 | 12329.1 | 10669.5 | 12405.1 | 11209.7 | 12242.8 | 11160.4 | 12223.7 | 11360.7 | 11029.1 | 12154.9 | 11233 | 10954.1 | 12276.4 | 12434.2 | 12203.9 | 11234.6 | 12359.3 | 11076.7 | 12034.1 | 11208.5 | 11881.5 | 10338 | 12065.8 | 11078.6 | 11187.7 | 11205 | 11040.5 | 9538.4 | 10960.2 | 9709.9 | 10950.3 | 10987.6 | 12775.9 | 11311 | 12870.2 | 11594.8 | 12778.2 | 11396.9 | 11604.5 | 11300.4 | 12516.7 | 12955.3 | 12764.9 | 12676.2 | 12671.1 | 12706.2 | 11693 | 12756.8 | 12791.1 | 12825.2 | 12869 | 12813.1 | 12859.7 | 11670.3 | 12882.1 | 11736.8 | 40.0819 | 39.4454 | 40.0387 | 39.8946 | 39.8044 | 39.775 | 0 | 53.3 | 0 | 0 | 53.3 | 53.5 | 2.6929 | 2.0538 | 2.6026 | 0.80976 | 2.4159 | 2.5624 | 8.0483 | 7.735 | 6.8033 | 6.8917 | 8.3467 | 6.93 | 6.9853 | 7.0164 | 7.0404 | 6.9369 | 7.0498 | 7.0538 | 1.8572 | 1.9079 | 1.7397 | 2.2463 | 2.0596 | 1.8309 | 7.0113 | 7.0616 | 6.9505 | 6.9885 | 7.052 | 6.9887 | 0.52114 | 0.58314 | 0.50048 | 0.54055 | 0.50724 | 0.55139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 926162 | 1732 | 912897 | 1757 | 144064.278 | 317.4 | 6.9853 | 7.0164 | 7.0404 | 6.9369 | 7.0498 | 7.0538 | 7.0113 | 7.0616 | 6.9505 | 6.9885 | 7.052 | 6.9887 | 941000 | 2000 | 937000 | 2000 | 1876000 | 4400 | 1874000 | 1871600 | 12.8667 | 7.0138 | 1.9403 | 7.0088 | 0.53399 | 27.66% | 7.619% | 39.84 | 53.3667 | 2.1896 | 7.4592 | 1887754.9 | 1853601 | 2231330.6555 | 83.07% | 33 | 5405
2025-04-30 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 335090.89 | 6:29 | 19:12 | 11960.4 | 12569.4 | 12564.4 | 12512.7 | 12676.2 | 12691.5 | 12735.8 | 13096.8 | 12610 | 12575 | 12414.4 | 12522 | 12591.4 | 12449.4 | 12587.4 | 12662 | 12531.1 | 12558.7 | 12615.4 | 12673.9 | 12613.9 | 12615.8 | 12327.7 | 12467.3 | 12314 | 10754.4 | 12292.6 | 12250.5 | 12624.2 | 12441.8 | 12384.4 | 12654.2 | 12588.3 | 12646.5 | 12731.1 | 12616.9 | 12735.9 | 12542.7 | 12558.7 | 12491.9 | 13436.1 | 12233 | 13301.7 | 11995.3 | 12613.6 | 13726.4 | 11945.4 | 13445.2 | 12558.7 | 12774.8 | 12634.5 | 11939.5 | 13016.8 | 12789.9 | 12969 | 12665.5 | 11467.5 | 13157.5 | 11516.1 | 13134 | 13015.4 | 11517.2 | 12690.3 | 12037.7 | 12287.7 | 11523.3 | 12234.7 | 12767.7 | 13075.5 | 11781.7 | 12926.2 | 11304.3 | 12546.9 | 12326.1 | 11594.9 | 12905.5 | 11353.9 | 13127.9 | 11605.5 | 12934.7 | 11894.1 | 12829 | 11987.5 | 13179.1 | 11877.2 | 12645.1 | 11844.2 | 10422.3 | 12779.7 | 12425 | 11508.4 | 13161.3 | 12837.9 | 11845 | 11684.7 | 12916.4 | 11569.6 | 12102 | 13104.4 | 11597.1 | 13099.2 | 11571.4 | 12862.3 | 11823.9 | 12939.9 | 11189.8 | 13004.5 | 11749.2 | 12858.1 | 11684.8 | 12884.9 | 11905.6 | 11590.7 | 12765.6 | 11769.4 | 11481 | 12850.8 | 12982.5 | 12781.8 | 11748.4 | 12924.3 | 11580 | 12619.6 | 11742.9 | 12443.1 | 10818.4 | 12653.6 | 11583.4 | 11689.3 | 11691.1 | 11504 | 9955.8 | 11444.8 | 10148.7 | 11459.5 | 11502.6 | 13412.6 | 11904.2 | 13484.8 | 12190.5 | 13340.6 | 11927.9 | 12165.7 | 11835.8 | 13203.5 | 13662 | 13408.1 | 13313.3 | 13317.6 | 13346 | 12329.3 | 13393.7 | 13473.8 | 13497.5 | 13513.7 | 13455.7 | 13508.6 | 12314.6 | 13546.7 | 12385.3 | 37.9865 | 37.6561 | 37.6561 | 37.9185 | 37.777 | 37.9146 | 0 | 52.2401 | 0 | 0 | 52.4811 | 53.4877 | 3.2158 | 2.8912 | 3.9102 | 2.6765 | 3.1865 | 3.2449 | 6.4133 | 6.975 | 9.405 | 6.175 | 6.2083 | 7.9417 | 7.3277 | 7.3116 | 7.7004 | 7.3134 | 7.397 | 7.409 | 1.915 | 2.0195 | 1.6493 | 2.3366 | 2.1629 | 1.9605 | 7.3689 | 7.3804 | 7.6357 | 7.369 | 7.4046 | 7.3743 | 0.53474 | 0.59844 | 0.52457 | 0.55326 | 0.52029 | 0.57181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 927155 | 1733 | 913890 | 1758 | 146037.411 | 321.867 | 7.3277 | 7.3116 | 7.7004 | 7.3134 | 7.397 | 7.409 | 7.3689 | 7.3804 | 7.6357 | 7.369 | 7.4046 | 7.3743 | 993000 | 1000 | 993000 | 1000 | 1973133 | 4467 | 1984000 | 1968666 | 12.7167 | 7.4099 | 2.0073 | 7.4222 | 0.55052 | 27.09% | 7.417% | 37.8181 | 52.7363 | 3.1875 | 7.1864 | 1986574.7 | 1914133 | 2334647.9762 | 81.99% | 27 | 0
2025-05-01 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 335090.89 | 6:29 | 17:16 | 10523.5 | 11053.3 | 11067 | 11026.7 | 11177.1 | 11188.3 | 11170 | 11518.2 | 11103.6 | 11064.6 | 10906 | 10995.9 | 11082.1 | 10943.1 | 11056 | 11147.7 | 11042.7 | 11086.4 | 11139.6 | 11182.9 | 11131.3 | 11118.9 | 10870.2 | 10993 | 10846.6 | 9479.1 | 10842.5 | 10771.8 | 11146.9 | 10975.5 | 10910.4 | 11167.7 | 11096.7 | 11145.7 | 11210.6 | 11109.3 | 11250.2 | 11070 | 11092.2 | 11041.7 | 11882.1 | 10762 | 11781.4 | 10550.6 | 11097.6 | 12119 | 10501.2 | 11891.3 | 11078.5 | 11266.2 | 11137.5 | 10516.1 | 11517.3 | 11282.1 | 11484.7 | 11193 | 10110.7 | 11608.5 | 10136.7 | 11608.8 | 11466.5 | 10120.7 | 11189 | 10568.4 | 10854 | 10173.1 | 10793.1 | 11247.8 | 11586.8 | 10391.9 | 11433.9 | 9966.2 | 11061.3 | 10864.4 | 10216.4 | 11421 | 9987.6 | 11599.6 | 10216.3 | 11417.9 | 10502.3 | 11355.5 | 10586.1 | 11703 | 10476.8 | 11168.8 | 10453.4 | 9195.7 | 11306.2 | 10973.5 | 10105 | 11674.7 | 11366.8 | 10427.5 | 10265.7 | 11474.8 | 10267.3 | 10679.1 | 11655 | 10224.3 | 11624.3 | 10202.2 | 11364.1 | 10404.7 | 11478.1 | 9878.8 | 11537.8 | 10324 | 11385 | 10318.3 | 11446.9 | 10488.3 | 10213.2 | 11318.5 | 10340.9 | 10148.3 | 11365.5 | 11518.2 | 11332.6 | 10358.3 | 11457 | 10170.8 | 11149.6 | 10358.4 | 11004.5 | 9556.4 | 11167.2 | 10224.6 | 10360.3 | 10356.5 | 10199.9 | 8840.7 | 10220.1 | 9061.7 | 10125 | 10157 | 11947 | 10516.3 | 12029.1 | 10791.7 | 11880.1 | 10545.4 | 10758.6 | 10458.7 | 11758.7 | 12257.6 | 11930.4 | 11846.8 | 11842.6 | 11877.4 | 10905.8 | 11927.9 | 12026.7 | 12063.5 | 12089.2 | 12012.8 | 12054.4 | 10894.9 | 12102.5 | 10972.1 | 37.4836 | 37.1965 | 37.7534 | 37.3125 | 37.0839 | 37.3895 | 0 | 52.6 | 0 | 0 | 52.4129 | 52.9 | 3.9352 | 4.3205 | 3.6809 | 3.4538 | 4.1684 | 4.2587 | 8.515 | 8.6583 | 9.4383 | 7.7467 | 7.705 | 8.9617 | 6.3911 | 6.4242 | 6.4457 | 6.3801 | 6.4441 | 6.4757 | 1.7393 | 1.7363 | 1.6299 | 2.1131 | 1.8921 | 1.6729 | 6.4459 | 6.4987 | 6.4105 | 6.4631 | 6.5007 | 6.447 | 0.47495 | 0.53318 | 0.45448 | 0.495 | 0.46484 | 0.50915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 928030 | 1735 | 914751 | 1760 | 147780.678 | 327 | 6.3911 | 6.4242 | 6.4457 | 6.3801 | 6.4441 | 6.4757 | 6.4459 | 6.4987 | 6.4105 | 6.4631 | 6.5007 | 6.447 | 875000 | 2000 | 861000 | 2000 | 1743267 | 5133 | 1732000 | 1738134 | 10.7833 | 6.4268 | 1.7973 | 6.461 | 0.4886 | 27.97% | 7.562% | 37.3699 | 52.6376 | 3.9696 | 8.5042 | 1755655.6 | 1728267 | 2113702.1268 | 81.76% | 30 | 33591
2025-05-02 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 335090.89 | 6:25 | 19:09 | 10102.2 | 10623.5 | 10592.4 | 10546 | 10693.4 | 10727 | 10670.6 | 11057.9 | 10643.8 | 10613.3 | 10514.3 | 10666.4 | 10623.4 | 10583.7 | 10635.5 | 10711 | 10614.5 | 10624.5 | 10628.8 | 10689.2 | 10654.7 | 10638.3 | 10429.7 | 10530 | 10417.9 | 9084.1 | 10339.7 | 10343.6 | 10699.2 | 10619.5 | 10491.3 | 10729.9 | 10622.3 | 10674.7 | 10750.8 | 10647 | 10792 | 10634.2 | 10656.2 | 10581.8 | 11329.3 | 10149.9 | 11269.9 | 10006.5 | 10833.2 | 12045.8 | 10087.8 | 11301.1 | 10735.3 | 10867.2 | 10668.1 | 10038 | 11086.6 | 10844.2 | 10977 | 10857 | 9710.2 | 11213 | 9737.3 | 11185.4 | 11061 | 9739.6 | 10788.9 | 10194.3 | 10473.3 | 9822.6 | 10400.7 | 10768 | 11174.5 | 9931.6 | 11004.8 | 9527.6 | 10598.5 | 10314.7 | 9766.7 | 10956.2 | 9586.8 | 11142.5 | 9716.9 | 10927.9 | 9955.9 | 10775.5 | 10156.1 | 11210.8 | 10020 | 10755.1 | 9897.2 | 8633.8 | 10808.9 | 10440.7 | 9520.7 | 11199.8 | 10831 | 10014.3 | 9970.5 | 10743.5 | 9643.4 | 10040.3 | 11056.3 | 9647.1 | 11011.7 | 9581 | 10744.2 | 9834.7 | 10916 | 9347 | 10985 | 9829 | 10789 | 9765 | 10741 | 9949 | 9709.4 | 10834.8 | 9838.7 | 9631 | 10955.4 | 11015 | 10806.1 | 9844.5 | 10886.9 | 9649.3 | 10611.6 | 9823 | 10445.7 | 9060.3 | 10516.4 | 9620.1 | 9973.6 | 10058.6 | 9697.6 | 8468.9 | 9854.3 | 8657.4 | 9903.1 | 9907.6 | 11417.9 | 9876.9 | 11562.9 | 10100.2 | 11381.7 | 10010.6 | 10260.2 | 9966.1 | 11041.3 | 11619.9 | 11396.9 | 11331.4 | 11323.5 | 11368.4 | 10298.8 | 11509.6 | 11378.2 | 11469.9 | 11388.1 | 11431.6 | 11454.5 | 10124.7 | 11575 | 10299.5 | 36.748 | 36.5521 | 36.9094 | 36.6864 | 36.7121 | 36.9345 | 0 | 49.4 | 0 | 0 | 49.6 | 49.9 | 3.0763 | 3.1891 | 2.798 | 1.6587 | 3.1183 | 2.7871 | 7.18 | 7.4283 | 6.6717 | 7.1533 | 7.3833 | 7.3267 | 6.4164 | 6.4724 | 6.5079 | 6.4281 | 6.4874 | 6.5052 | 1.4841 | 1.6319 | 1.3972 | 1.8614 | 1.7228 | 1.5862 | 6.447 | 6.5172 | 6.4254 | 6.4644 | 6.4848 | 6.4602 | 0.47217 | 0.52442 | 0.46946 | 0.49842 | 0.47819 | 0.51661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 928871 | 1736 | 915591 | 1762 | 149449.612 | 331.267 | 6.4164 | 6.4724 | 6.5079 | 6.4281 | 6.4874 | 6.5052 | 6.447 | 6.5172 | 6.4254 | 6.4644 | 6.4848 | 6.4602 | 841000 | 1000 | 840000 | 2000 | 1668934 | 4267 | 1678000 | 1664667 | 12.7333 | 6.4696 | 1.6139 | 6.4665 | 0.49321 | 24.95% | 7.627% | 36.7571 | 49.6333 | 2.7713 | 7.1906 | 1677908.8 | 1642200 | 2113024.5466 | 77.72% | 25 | 0
2025-05-03 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 335090.89 | 6:35 | 19:20 | 10982.3 | 11490 | 11382.2 | 11383.1 | 11410.4 | 11584.1 | 11435.3 | 11917.2 | 11537.3 | 11539.9 | 11297.3 | 11403.5 | 11538.3 | 11337.7 | 11467.2 | 11608.2 | 11460.4 | 11488.8 | 11451.2 | 11518.9 | 11438.8 | 11412.7 | 11209 | 11284.8 | 11161.7 | 9766.2 | 11210.2 | 11102 | 11464 | 11287.7 | 11236.4 | 11502.7 | 11419.5 | 11525.4 | 11536.8 | 11419.5 | 11552.4 | 11328.5 | 11357.4 | 11405.8 | 12105.9 | 10797 | 11929.8 | 10594.8 | 11285.4 | 12702.1 | 10574.1 | 12206.6 | 11532.4 | 11663.8 | 11518.8 | 10778.9 | 11948.4 | 11693.6 | 11883.5 | 11645.3 | 10456.6 | 12045.1 | 10523.1 | 12042 | 11887.9 | 10519.1 | 11474.7 | 10838 | 11225.6 | 10571.2 | 11224.3 | 11563 | 12108.4 | 10721.3 | 11900.4 | 10285.3 | 11485 | 11168.4 | 10604.4 | 11877.2 | 10426.6 | 12094.6 | 10520.2 | 11846.7 | 10707 | 11647.8 | 10860.4 | 12074 | 10727.9 | 11433.5 | 10506.6 | 9296.5 | 11278 | 11090.2 | 10122.7 | 11810.7 | 11469.5 | 10501.1 | 10408.3 | 11334.2 | 10119.8 | 10758.2 | 11818.3 | 10390.5 | 11780.7 | 10296.1 | 11529 | 10534 | 11720.9 | 10015.7 | 11795.1 | 10565.6 | 11553 | 10449.8 | 11482.2 | 10660.1 | 10483.3 | 11640.1 | 10579.5 | 10369.1 | 11728.1 | 11936.1 | 11644.1 | 10711.2 | 11825.6 | 10488.7 | 11404.9 | 10578.9 | 11136.5 | 9796.4 | 11436.2 | 10507.6 | 10678.2 | 10677 | 10405.3 | 9067.2 | 10466.6 | 9194.1 | 10556.8 | 10572.7 | 12519.7 | 10802.4 | 12612.6 | 11045 | 12359.3 | 10801.2 | 11083.3 | 10748.6 | 9787.4 | 9832.3 | 12499.2 | 12442 | 12429.9 | 12479.3 | 11213.3 | 12530 | 12556.7 | 12631.3 | 12537.3 | 12581.1 | 12598.2 | 11205.2 | 12641 | 11312.2 | 37.8308 | 37.4262 | 37.7671 | 37.6821 | 37.5777 | 37.7116 | 0 | 51.1258 | 0 | 0 | 50.9504 | 51.3802 | 4.2452 | 4.4656 | 3.914 | 3.2983 | 4.2793 | 4.221 | 9.5317 | 10.1817 | 9.0767 | 9.4067 | 11.06 | 9.55 | 6.9264 | 6.8889 | 6.9038 | 6.905 | 6.9722 | 7.1034 | 1.6075 | 1.7368 | 1.4794 | 1.9952 | 1.8768 | 1.7414 | 6.9542 | 6.9301 | 6.8012 | 0 | 6.9382 | 7.072 | 0.5209 | 0.57677 | 0.50954 | 0.54643 | 0.53341 | 0.58436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 929776 | 1738 | 916470 | 1763 | 151241.212 | 335.6 | 6.9264 | 6.8889 | 6.9038 | 6.905 | 6.9722 | 7.1034 | 6.9542 | 6.9301 | 6.8012 | 0 | 6.9382 | 7.072 | 905000 | 2000 | 879000 | 1000 | 1791600 | 4333 | 1781000 | 1787267 | 12.75 | 6.9499 | 1.7395 | 6.9392 | 0.54524 | 25.03% | 7.857% | 37.6659 | 51.1521 | 4.0705 | 9.8011 | 1800994.4 | 1770200 | 2275579.5514 | 77.79% | 18 | 660
2025-05-04 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 335090.89 | 6:28 | 19:14 | 11687.2 | 12235.8 | 12183.7 | 12122.8 | 12267.6 | 12296.1 | 12342.8 | 12592.5 | 12240.9 | 12302.7 | 12108.5 | 12249.1 | 12212 | 12192.1 | 12253.3 | 12288.2 | 12187.4 | 12199.3 | 12247.2 | 12318.3 | 12261.2 | 12268.5 | 12016.6 | 12131.9 | 11984 | 10529.2 | 11997.5 | 11956.4 | 12284.3 | 12181.1 | 12027 | 12257.4 | 12299.7 | 12246.2 | 12431.1 | 12327.2 | 12337.6 | 12176.9 | 12188.3 | 12111.7 | 12899.4 | 11795.9 | 12742.2 | 11580.1 | 12282.9 | 13364.7 | 11647.3 | 12926.9 | 12359.8 | 12477.7 | 12309.4 | 11703.5 | 12632.2 | 12483.6 | 12592.7 | 12520.3 | 11278.8 | 12797.9 | 11262.1 | 12730.4 | 12626.9 | 11237 | 12397 | 11871.8 | 11957.3 | 11228.2 | 11950.2 | 12334.3 | 12612 | 11466 | 12527.7 | 11030.3 | 12222.9 | 11937.5 | 11340.5 | 12503.6 | 11132.5 | 12719.5 | 11355.8 | 12551.8 | 11493.5 | 12339.8 | 11613.8 | 12682.1 | 11475.8 | 12116.6 | 11468.2 | 10059.1 | 12443.7 | 11974.5 | 11155.6 | 12758.9 | 12442 | 11586.6 | 11450.3 | 12496.3 | 11316.7 | 11685.9 | 12620.2 | 11147.7 | 12666.5 | 11135.2 | 12359.7 | 11414.3 | 12407 | 10795 | 12466 | 11292 | 12324 | 11263 | 12280 | 11433 | 11163.9 | 12300.1 | 11318.1 | 11081.3 | 12409.2 | 12467.2 | 12292.6 | 11311.5 | 12392.5 | 11163.4 | 12138.9 | 11295.4 | 12010.1 | 10462.1 | 12156 | 11163.7 | 11444 | 11558.9 | 11247.1 | 9729.6 | 11333.9 | 10032.4 | 11270.6 | 11312.8 | 12823.7 | 11413 | 12889.3 | 11649.8 | 12838.4 | 11567.6 | 11746.8 | 11526.3 | 12505.7 | 12875.9 | 12826 | 12736.7 | 12740.4 | 12775 | 11778.4 | 12798.2 | 12895.7 | 12893 | 12781 | 12859 | 12891 | 11722 | 12869.3 | 11829.3 | 30.8697 | 30.5351 | 30.6499 | 30.6215 | 30.3116 | 30.5415 | 0 | 43.5 | 0 | 0 | 43.3921 | 43.7 | 4.5496 | 4.3387 | 4.0511 | 3.0604 | 4.4053 | 4.1705 | 8.0283 | 7.74 | 8.19 | 7.41 | 7.6733 | 7.9683 | 6.841 | 6.9159 | 6.9383 | 6.8835 | 6.8862 | 6.907 | 1.4989 | 1.4141 | 1.3706 | 1.8051 | 1.5489 | 1.4814 | 6.9193 | 6.9366 | 6.8088 | 0 | 6.7804 | 6.8861 | 0.42173 | 0.47634 | 0.39372 | 0.44683 | 0.37143 | 0.42416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 930744 | 1739 | 917418 | 1765 | 153151.679 | 340 | 6.841 | 6.9159 | 6.9383 | 6.8835 | 6.8862 | 6.907 | 6.9193 | 6.9366 | 6.8088 | 0 | 6.7804 | 6.8861 | 968000 | 1000 | 948000 | 2000 | 1910467 | 4400 | 1913000 | 1906067 | 12.7667 | 6.8953 | 1.5199 | 6.8662 | 0.42237 | 22.04% | 6.151% | 30.5882 | 43.5307 | 4.0959 | 7.835 | 1923381.7 | 1875333 | 2288521.431 | 81.95% | 23 | 9683
2025-05-05 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 335090.89 | 7:28 | 19:13 | 4614.4 | 4868.5 | 4825.9 | 4779.8 | 4866.6 | 4885.9 | 4930.5 | 5137.3 | 4887.4 | 4926.6 | 4820.2 | 4877.7 | 4879.7 | 4875.7 | 4734.5 | 4902.4 | 4774.7 | 4697.3 | 4739.3 | 4785.2 | 4845 | 4722 | 4694.4 | 4711.4 | 4776.3 | 4185 | 4783.8 | 4760.9 | 4937.3 | 4920.4 | 4855.4 | 4945.5 | 4957.8 | 4952.7 | 4964.2 | 4932 | 4877.6 | 4747.7 | 4944.2 | 4738.3 | 5192.2 | 4607.7 | 5191.5 | 4522.9 | 4859.3 | 5431.7 | 4560.3 | 5346.5 | 4952 | 5000.9 | 4909.7 | 4649.9 | 5077.3 | 5031.2 | 5088.2 | 5042.1 | 4479.3 | 5191.9 | 4462.4 | 5131.1 | 5057.4 | 4452.7 | 4920.8 | 4657.5 | 4740.9 | 4490.8 | 4601.2 | 4801.1 | 5135.1 | 4586.1 | 5054.9 | 4393.4 | 4913.1 | 4755.6 | 4505 | 5049.9 | 4415.2 | 5137 | 4479.2 | 5027.7 | 6567.7 | 7071.9 | 6693.6 | 7258.8 | 6593.8 | 7000.5 | 6774 | 5825.9 | 7194.5 | 6912 | 6449.7 | 7397.3 | 7200 | 6685.5 | 6619.4 | 7293 | 6569.6 | 6777.1 | 7400.6 | 6544 | 7410 | 6531.5 | 7224.4 | 6695.9 | 7487.8 | 6419.9 | 7362.8 | 6660.6 | 7242.3 | 6589.5 | 7361.2 | 6764.8 | 6456.2 | 7142.5 | 6550.4 | 6434.1 | 6987.7 | 7226.7 | 7155.4 | 6637.5 | 7249 | 6544.3 | 7051.2 | 6554.5 | 6999.6 | 6125.5 | 7089.9 | 6586.6 | 6047.9 | 6663.9 | 6505.7 | 5597.7 | 6555.8 | 5805.2 | 6497.2 | 6424.5 | 7328.6 | 6451.3 | 7499.3 | 6242.6 | 7053.3 | 6677.5 | 6342.7 | 6721.6 | 6955.7 | 7207.9 | 6775 | 6802.9 | 6702 | 6801.3 | 6243.8 | 6885.4 | 6854.8 | 7182.2 | 7377.7 | 6836.7 | 6775.2 | 6144.6 | 6886.4 | 6211.6 | 28.112 | 27.9157 | 28.2473 | 28.0685 | 27.7675 | 27.9773 | 0 | 41.548 | 0 | 0 | 41.6368 | 42.335 | 3.682 | 3.5467 | 3.4518 | 2.1764 | 3.8504 | 3.75 | 7.5717 | 8.1117 | 7.7567 | 6.5917 | 8.94 | 7.7617 | 5.2297 | 5.3203 | 5.3949 | 5.2677 | 5.449 | 5.5054 | 0.98872 | 0.94834 | 0.98998 | 1.2418 | 1.1088 | 1.1168 | 5.1928 | 5.3065 | 5.2465 | 0 | 5.3817 | 5.4465 | 0.33354 | 0.40921 | 0.33008 | 0.37318 | 0.32993 | 0.36596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 931131 | 1741 | 917959 | 1766 | 154076.145 | 344.533 | 5.2297 | 5.3203 | 5.3949 | 5.2677 | 5.449 | 5.5054 | 5.1928 | 5.3065 | 5.2465 | 0 | 5.3817 | 5.4465 | 387000 | 2000 | 541000 | 1000 | 924466 | 4533 | 925000 | 919933 | 11.75 | 5.3612 | 1.0657 | 5.3148 | 0.35699 | 19.88% | 6.717% | 28.0147 | 41.8399 | 3.4096 | 7.7889 | 929392.9 | 824866 | 1074671.7329 | 76.76% | 26 | 38830
2025-05-06 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 335090.89 | 6:25 | 19:17 | 8512.6 | 8949 | 8938.4 | 8896.3 | 9000.3 | 9006.8 | 9014.7 | 9393.3 | 8969.3 | 8993.3 | 8806.3 | 8949.2 | 8959.1 | 8943.7 | 9002.8 | 9023.5 | 8962.6 | 8559.4 | 8962.4 | 9033.9 | 9058.9 | 8589.4 | 8833 | 8905.4 | 8811 | 7735.7 | 8772.4 | 8779.5 | 9000.1 | 9026.8 | 8908.1 | 9059.6 | 9060.9 | 9000 | 9147.4 | 9077.3 | 9142.2 | 9007.1 | 9061.2 | 8831.6 | 9828.9 | 8881.3 | 9741.5 | 8370.4 | 9331.2 | 10199.9 | 8748.2 | 9816.1 | 9075.7 | 9157.6 | 8996.3 | 8505.8 | 9157.5 | 9227.9 | 9263.5 | 8843.4 | 8020.7 | 9344.4 | 8240.4 | 9376.6 | 8937.5 | 8212.7 | 9033.3 | 8571.9 | 8662.1 | 8228.7 | 8664.1 | 9088.1 | 9308.5 | 8409.8 | 9193.4 | 7546.1 | 8978.3 | 8655.2 | 8244 | 9193.6 | 7936.8 | 9354.3 | 7956.1 | 9156.9 | 8432.6 | 9113.7 | 8584.5 | 9268.2 | 8475.1 | 9020.3 | 8461.7 | 7408.6 | 9265.2 | 8900 | 8263.1 | 9539.4 | 9289.6 | 8613.1 | 8533.6 | 9374.5 | 8244.4 | 8744.4 | 9545 | 8401.8 | 9566.7 | 8388.4 | 9345.5 | 8591.6 | 9462.2 | 8066.2 | 9335.7 | 8536.3 | 9369 | 8572.4 | 9300.6 | 8292.7 | 8430 | 9237.2 | 8566.5 | 8287.3 | 9313 | 9442.2 | 9354.1 | 8593.3 | 9426.8 | 8488.1 | 9236.3 | 8460 | 9141.6 | 7938.1 | 9249.5 | 8524.3 | 8584.9 | 8751.1 | 8605.6 | 7414.7 | 8572.7 | 7564.7 | 8548.4 | 8555.6 | 9755.4 | 8592.4 | 9816.1 | 8787.9 | 9722.4 | 8733.2 | 8832 | 8710.2 | 9457.1 | 9755.7 | 9627.5 | 9629.7 | 9639.6 | 9671.3 | 8857.6 | 9695.1 | 9626.4 | 9680.2 | 9711.1 | 9602.3 | 9466.1 | 8769.3 | 9656 | 8784.4 | 28.7308 | 28.5022 | 28.6853 | 28.5661 | 28.7967 | 28.5443 | 0 | 37.2921 | 0 | 0 | 37.1 | 37 | 4.286 | 4.2081 | 4.0548 | 2.7387 | 4.2914 | 4.0296 | 8.8633 | 9.9133 | 9.7733 | 8.5817 | 10.2283 | 9.1817 | 4.9079 | 5.0207 | 5.1317 | 4.8708 | 5.0737 | 5.0895 | 1.146 | 1.0121 | 1.1128 | 1.3232 | 1.1852 | 1.018 | 4.84 | 4.9466 | 4.9726 | 0 | 5.0161 | 4.9389 | 0.3116 | 0.36163 | 0.32209 | 0.32833 | 0.31898 | 0.34359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 931841 | 1742 | 918672 | 1768 | 155494.079 | 349.133 | 4.9079 | 5.0207 | 5.1317 | 4.8708 | 5.0737 | 5.0895 | 4.84 | 4.9466 | 4.9726 | 0 | 5.0161 | 4.9389 | 710000 | 1000 | 713000 | 2000 | 1417934 | 4600 | 1420000 | 1413334 | 12.8667 | 5.0157 | 1.1329 | 4.9428 | 0.33104 | 22.59% | 6.697% | 28.6376 | 37.1307 | 3.9348 | 9.4236 | 1427314.3 | 1391200 | 1679849.6539 | 82.82% | 29 | 123474
2025-05-07 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 335090.89 | 6:20 | 19:16 | 12020.2 | 12665.5 | 12657.9 | 12579.5 | 12770.2 | 12832.9 | 12860.3 | 13296.5 | 12686 | 12578.7 | 12604.3 | 12736.4 | 12715.3 | 12697.7 | 12804.2 | 12841.8 | 12686.9 | 12717.3 | 12644.7 | 12829.3 | 12789.6 | 12778.2 | 12476.1 | 12611 | 12474.7 | 10917.7 | 12449.2 | 12426 | 12814.3 | 12694.2 | 12502.1 | 12793.2 | 12747.5 | 12797.9 | 12939.3 | 12803.6 | 12876.5 | 12682.6 | 12677.4 | 12594.9 | 13562.1 | 12309 | 13440.7 | 12076.4 | 12841.8 | 14060.3 | 12147.8 | 13590.4 | 12839.4 | 13017.2 | 12839.2 | 12105 | 13109.7 | 13068.6 | 13119.4 | 12925.4 | 11650.9 | 13297.8 | 11674.4 | 13282.7 | 13144.8 | 11640 | 12860.3 | 12225.2 | 12353.2 | 11635.4 | 12370.8 | 12883.2 | 13055.9 | 11899.7 | 13042 | 11412.5 | 12688.2 | 12346.6 | 11708.2 | 13023.8 | 11408.5 | 13230.7 | 11675 | 12995.2 | 11917.7 | 12904.2 | 12082.5 | 13278.3 | 11931.1 | 12725 | 11894.6 | 10467.1 | 12987.3 | 12492.9 | 11480.1 | 13326.3 | 12970.2 | 11989.2 | 11800.4 | 13014.6 | 11254.4 | 11910.9 | 13166.7 | 11589.5 | 13204.1 | 11495.9 | 12901.2 | 11864.6 | 12982.1 | 11211.3 | 13059.6 | 11770.2 | 12893.4 | 11747.8 | 12953.7 | 11948.5 | 11609.8 | 12869.6 | 11797.1 | 11535.7 | 12975.8 | 13047.6 | 12845.4 | 11793.9 | 12978.2 | 11628.8 | 12690.4 | 11770.8 | 12516.3 | 10883.4 | 12696.5 | 11639.8 | 11865.5 | 11967 | 11691.3 | 10096.3 | 11670.6 | 10343.1 | 11712.5 | 11759.1 | 13575.9 | 11953.8 | 13624.9 | 12225.4 | 13517 | 12088.1 | 12245.2 | 11999.4 | 13237.9 | 13652.6 | 13556.8 | 13492.7 | 13497.1 | 13522.1 | 12380.5 | 13510.1 | 13628 | 13643.2 | 13559.7 | 13534.6 | 13645.2 | 12350.4 | 13668.9 | 12440.1 | 30.7353 | 30.3007 | 30.8054 | 30.4405 | 30.1848 | 30.3848 | 0 | 46.1084 | 0 | 0 | 46 | 46.2 | 2.1814 | 2.1286 | 1.9693 | 0.23605 | 2.2239 | 1.9595 | 6.2633 | 5.03 | 5.1667 | 4.5317 | 5.415 | 5.4667 | 7.2283 | 7.2733 | 7.308 | 7.204 | 7.2353 | 7.07 | 1.6681 | 1.609 | 1.5418 | 1.8978 | 1.8245 | 1.5328 | 7.1914 | 7.2344 | 7.108 | 7.1572 | 7.1658 | 7.2052 | 0.47263 | 0.52613 | 0.48817 | 0.47344 | 0.47615 | 0.49897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 932847 | 1744 | 919663 | 1769 | 157484.612 | 353.667 | 7.2283 | 7.2733 | 7.308 | 7.204 | 7.2353 | 7.07 | 7.1914 | 7.2344 | 7.108 | 7.1572 | 7.1658 | 7.2052 | 1006000 | 2000 | 991000 | 1000 | 1990533 | 4534 | 1994000 | 1985999 | 12.9333 | 7.2198 | 1.679 | 7.177 | 0.48925 | 23.26% | 6.817% | 30.4753 | 46.1028 | 1.7831 | 5.3122 | 2004778.5 | 1963867 | 2383493.6742 | 82.39% | 23 | 0
2025-05-08 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 335090.89 | 6:23 | 19:12 | 10833 | 11395.6 | 11318.9 | 11259 | 11434 | 11435.8 | 11524.9 | 11950.8 | 11472.5 | 11374.3 | 11307.7 | 11449.9 | 11484.3 | 11429.8 | 11678.5 | 11654.4 | 11732.3 | 11804 | 11711.5 | 11847.7 | 11967.2 | 11930.6 | 11823.9 | 11862.1 | 11780.3 | 10250.7 | 11575.6 | 11673.9 | 12131.2 | 12161.1 | 12081 | 12232.8 | 12314.6 | 12324.9 | 12264.5 | 12244.8 | 12416 | 12249.2 | 12065.5 | 12228.5 | 13016.5 | 11750.3 | 12902.7 | 11552.1 | 12174.6 | 13503.8 | 11669.6 | 13058.3 | 11792.1 | 11884.8 | 11757.5 | 11149.6 | 12153.1 | 11959.2 | 12152.6 | 12131 | 10674.4 | 12285.1 | 10575.1 | 12136.1 | 11950.6 | 10501.2 | 11722.2 | 11100.2 | 11567.5 | 10935.2 | 11446.2 | 12075.6 | 12017.6 | 11055.3 | 12028.8 | 10583.1 | 11607.3 | 11365.2 | 10700 | 11974.5 | 10538.7 | 12116.5 | 10667.1 | 11864 | 11118.4 | 12036.1 | 11395 | 12507.1 | 11282.7 | 12054.8 | 11275.9 | 9954.3 | 12422.6 | 11897.4 | 11000.2 | 12847.7 | 12528.8 | 11602.9 | 11466.4 | 12655 | 11206.6 | 11601.3 | 12612.1 | 11050.3 | 12699 | 10965.7 | 12372.8 | 11331.3 | 12484 | 10747 | 12529 | 11242 | 12362 | 11220 | 12399 | 11387 | 11045.4 | 12268.6 | 11228.9 | 10983.9 | 12413.3 | 12481.2 | 12302.8 | 11217.4 | 12392.8 | 11049.7 | 12127.7 | 11200.6 | 11903.4 | 10353.7 | 12087 | 11068.5 | 11234.8 | 11310.6 | 11076.5 | 9563.5 | 11032.5 | 9767.3 | 10986.1 | 11038.5 | 12835.4 | 11259.5 | 12852.5 | 11504.6 | 12741.6 | 11343.5 | 11525.5 | 11268.9 | 12617.2 | 13024.4 | 12842.6 | 12794.8 | 12789 | 12794.3 | 11654.5 | 12744.9 | 12854.3 | 12893.1 | 12735.5 | 12758.7 | 12940.5 | 11700.2 | 12933.5 | 11771.4 | 33.5139 | 33.2465 | 33.7882 | 33.4706 | 33.1615 | 33.4856 | 0 | 48.6 | 0 | 0 | 48.8 | 49.5418 | 3.1728 | 3.0788 | 2.9188 | 0.53347 | 3.0949 | 2.7122 | 6.1733 | 6.3117 | 5.8617 | 6.13 | 5.8567 | 6.4133 | 6.5032 | 6.9382 | 7.0571 | 6.7382 | 6.962 | 7.0165 | 1.5719 | 1.6011 | 1.5532 | 1.8474 | 1.8837 | 1.4863 | 6.4452 | 6.8889 | 6.858 | 6.725 | 6.9024 | 6.8742 | 0.44734 | 0.53474 | 0.48916 | 0.46494 | 0.49555 | 0.50491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 933780 | 1746 | 920605 | 1772 | 159355.479 | 358.067 | 6.5032 | 6.9382 | 7.0571 | 6.7382 | 6.962 | 7.0165 | 6.4452 | 6.8889 | 6.858 | 6.725 | 6.9024 | 6.8742 | 933000 | 2000 | 942000 | 3000 | 1870867 | 4400 | 1870000 | 1866467 | 12.8167 | 6.8692 | 1.6573 | 6.7823 | 0.48944 | 24.13% | 7.216% | 33.4444 | 48.9806 | 2.5852 | 6.1244 | 1883342.1 | 1853400 | 2246484.3892 | 82.5% | 22 | 5888
2025-05-09 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 335090.89 | 6:44 | 19:17 | 11188.1 | 11805.4 | 11777.5 | 11675.9 | 11869 | 11836.7 | 11975.4 | 12458 | 11827.6 | 11853.7 | 11674.7 | 11834.7 | 11692.9 | 11762.6 | 11868.9 | 11884.6 | 11786.1 | 11747.5 | 11660.3 | 11863.8 | 11825.3 | 11804.5 | 11532.9 | 11652.7 | 11371.9 | 10071.3 | 11491.3 | 11464.2 | 11875.9 | 11778.9 | 11594.2 | 11780.2 | 11803.9 | 11790.4 | 11928.6 | 11823.6 | 11960 | 11781.4 | 11535 | 11727.3 | 12754 | 11407 | 12598.9 | 11206.1 | 11831.9 | 13319.1 | 11258.1 | 12790.2 | 11994.5 | 12108.8 | 11899.2 | 11196.5 | 12304.4 | 12158.5 | 12224.2 | 12149.3 | 10794.9 | 12478.3 | 10805.9 | 12396.8 | 12271.4 | 10789.7 | 11860.1 | 11395.8 | 11470.9 | 10768.4 | 11457.2 | 11962.6 | 12180.7 | 11016.6 | 12181.5 | 10595.1 | 11798.5 | 11483.3 | 10877.4 | 12179.8 | 10683.6 | 12446 | 10898.9 | 12204.5 | 10956.1 | 11981.3 | 11203.2 | 12393.6 | 11042.1 | 11808.6 | 11021.7 | 9654.6 | 12174.5 | 11602.5 | 10673 | 12539.8 | 12135.2 | 11174.2 | 11037.6 | 12258.1 | 10949.6 | 11324.1 | 12427.8 | 10813.4 | 12446.7 | 10702.2 | 12067.9 | 11075.5 | 12188.1 | 10477 | 12240.3 | 10958.4 | 12030.3 | 10877.7 | 12138.5 | 11107.9 | 10841.3 | 12070.4 | 11002.3 | 10758.5 | 12186.5 | 12247.3 | 12046.7 | 10971.5 | 12161.1 | 10822.2 | 11849.6 | 10941.5 | 11625.4 | 10114.2 | 11828 | 10836.5 | 11086.9 | 11191.5 | 10937.8 | 9436.7 | 10953.3 | 9705 | 10938.4 | 10983.7 | 12743.1 | 11067.4 | 12802.3 | 11310.6 | 12727.1 | 11222 | 11405.1 | 11180.9 | 12310.2 | 12796.1 | 12673.1 | 12601.5 | 12618.9 | 12671.8 | 11444.8 | 12614.9 | 12765.6 | 12771.6 | 12570 | 12599.6 | 12783.5 | 11378.2 | 12789.7 | 11447.2 | 30.3088 | 30.0704 | 30.2318 | 30.3687 | 30.1179 | 30.2086 | 0 | 41.2921 | 0 | 0 | 41.6 | 41 | 3.8335 | 3.8178 | 3.7078 | 3.2276 | 3.7887 | 3.1609 | 6.95 | 6.4433 | 6.495 | 6.8617 | 7.1367 | 7.3283 | 6.5048 | 6.5148 | 6.6022 | 6.4838 | 6.5589 | 6.5802 | 1.363 | 1.4023 | 1.2895 | 1.5395 | 1.5715 | 1.3328 | 6.4905 | 6.5061 | 6.4977 | 6.448 | 6.4957 | 6.5077 | 0.4198 | 0.48505 | 0.4216 | 0.42359 | 0.42351 | 0.45129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 934715 | 1747 | 921530 | 1773 | 161210.746 | 362.467 | 6.5048 | 6.5148 | 6.6022 | 6.4838 | 6.5589 | 6.5802 | 6.4905 | 6.5061 | 6.4977 | 6.448 | 6.4957 | 6.5077 | 935000 | 1000 | 925000 | 1000 | 1855267 | 4400 | 1858000 | 1850867 | 12.55 | 6.5408 | 1.4165 | 6.491 | 0.43747 | 21.66% | 6.74% | 30.2177 | 41.2974 | 3.5894 | 6.8692 | 1867148.5 | 1824067 | 2175313.6838 | 83.85% | 23 | 413
2025-05-10 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 335090.89 | 6:21 | 19:17 | 12151.2 | 12779.7 | 12721 | 12648.3 | 12811.1 | 12840.6 | 12893.5 | 13318.1 | 12798.6 | 12855.6 | 12652.7 | 12790.7 | 12697 | 12718.6 | 12797.4 | 12836.3 | 12724.7 | 12711.2 | 12721.2 | 12815.9 | 12766.2 | 12762.3 | 12490.6 | 12618.1 | 12333.9 | 10920.4 | 12455.8 | 12440.4 | 12825.7 | 12716.2 | 12563.4 | 12736.7 | 12819.4 | 12838.5 | 12936.2 | 12815.9 | 12897.2 | 12725.2 | 12640.4 | 12695.3 | 13594.6 | 12391.1 | 13473.6 | 12168.7 | 12781.1 | 14063.9 | 12220.3 | 13605.8 | 12889.3 | 13054.7 | 12869.7 | 12146.6 | 13225.6 | 13063.7 | 13148.9 | 13059.6 | 11700.6 | 13382.6 | 11714.9 | 13324.6 | 13197.2 | 11692.3 | 12830.2 | 12304.1 | 12415.3 | 11683.9 | 12406 | 12931.5 | 13126.1 | 11931 | 13089.5 | 11455.4 | 12734.4 | 12412.6 | 11763.2 | 13083.4 | 11560.2 | 13322.3 | 11779.3 | 13095.3 | 11974.6 | 12931.3 | 12131.7 | 13318.4 | 11988.3 | 12794.1 | 11953.4 | 10499 | 13040.8 | 12563.1 | 11618.5 | 13412.6 | 13071.5 | 12134.8 | 11984.8 | 13147.9 | 11806.8 | 12267.6 | 13320.7 | 11730.8 | 13354.1 | 11540.8 | 13049.6 | 12002.9 | 13115.4 | 11361.8 | 13179 | 11905.6 | 13015.6 | 11855.8 | 13060 | 12068.2 | 11726 | 12987.3 | 11918.5 | 11664.9 | 13088.5 | 13179 | 12962.2 | 11882.9 | 13113.8 | 11761.6 | 12828.7 | 11897.3 | 12643.7 | 10987.6 | 12834.5 | 11762 | 11950.1 | 12027.3 | 11781.4 | 10181.7 | 11777.1 | 10421.9 | 11764.1 | 11829.5 | 13607.1 | 12028.6 | 13655.6 | 12317 | 13571.3 | 12188.7 | 12396.7 | 12070.3 | 13280.6 | 13700.2 | 13583.7 | 13520.4 | 13534.9 | 13550.4 | 12459.5 | 13531 | 13599.6 | 13641.6 | 13465.6 | 13496.5 | 13651.1 | 12402.5 | 13631.1 | 12463.7 | 33.9855 | 33.6414 | 34.0853 | 34.1045 | 33.8116 | 33.8063 | 0 | 48.3173 | 0 | 0 | 48.5 | 48.3 | 2.2702 | 1.7915 | 2.0729 | 0.87494 | 2.1827 | 0.70305 | 4.5367 | 4.8267 | 4.66 | 4.4833 | 5.1183 | 4.005 | 7.3409 | 7.3399 | 7.4326 | 7.3057 | 7.3888 | 7.4376 | 1.6936 | 1.6527 | 1.5602 | 1.8445 | 1.944 | 1.5467 | 7.2782 | 7.2729 | 7.2501 | 7.2124 | 7.2713 | 7.2686 | 0.49525 | 0.55515 | 0.4933 | 0.47345 | 0.50577 | 0.52054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 935723 | 1748 | 922528 | 1774 | 163212.813 | 366.733 | 7.3409 | 7.3399 | 7.4326 | 7.3057 | 7.3888 | 7.4376 | 7.2782 | 7.2729 | 7.2501 | 7.2124 | 7.2713 | 7.2686 | 1008000 | 1000 | 998000 | 1000 | 2002067 | 4266 | 2004000 | 1997801 | 12.9333 | 7.3742 | 1.707 | 7.2589 | 0.50724 | 23.15% | 6.988% | 33.9058 | 48.3724 | 1.6492 | 4.605 | 2015493.1 | 1981066 | 2389965.9293 | 82.89% | 17 | 0
2025-05-11 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 335090.89 | 6:19 | 19:18 | 11905.2 | 12551.4 | 12468.9 | 12405 | 12571.7 | 12661.8 | 12719.8 | 13228.3 | 12580.7 | 12674 | 12420.1 | 12559 | 12513.8 | 12493.5 | 12569.5 | 12622 | 12526.4 | 12539.7 | 12533.7 | 12578.6 | 12563 | 12535 | 12278.8 | 12392 | 12188.9 | 10704.5 | 12185 | 12194.1 | 12653 | 12538.6 | 12376.2 | 12607.1 | 12576.2 | 12594.8 | 12723.2 | 12586 | 12746.5 | 12535.2 | 12504.4 | 12514.1 | 13551.4 | 12159.9 | 13417.7 | 11936.8 | 12574.4 | 14061.2 | 11990.5 | 13578.1 | 12728 | 12859.9 | 12622.6 | 11894.6 | 13043.5 | 12885.6 | 12982.8 | 12872.6 | 11485.1 | 13282.4 | 11490.9 | 13207.7 | 13060.1 | 11470.5 | 12766.2 | 12063.1 | 12202.7 | 11492.9 | 12195.3 | 12765.8 | 13153.7 | 11730.1 | 12969.3 | 11258.6 | 12533.3 | 12202.3 | 11561.8 | 12962.1 | 11367.4 | 13231.7 | 11558.4 | 12947.2 | 11770 | 12759.2 | 11900.5 | 13218.5 | 11764.2 | 12568.2 | 11733.8 | 10327.7 | 12857.7 | 12339.7 | 11425.5 | 13317.3 | 12935.1 | 11906 | 11763.7 | 13034.4 | 11567.9 | 12057 | 13236.1 | 11523.4 | 13275 | 11395.1 | 12887.9 | 11779.3 | 13016.1 | 11160.9 | 13068.5 | 11713.9 | 12844.9 | 11628.2 | 12916.2 | 11870 | 11522.8 | 12825.5 | 11698.1 | 11453.2 | 12963.3 | 13063.2 | 12823.4 | 11700.2 | 13003.7 | 11558.6 | 12643.9 | 11697.4 | 12436.9 | 10820.2 | 12625 | 11551.1 | 11703.6 | 11771.2 | 11528.7 | 9957 | 11523.2 | 10195.3 | 11537.8 | 11606.7 | 13550 | 11817.3 | 13610.8 | 12108.3 | 13528.1 | 11982.3 | 12192 | 11863.5 | 13156.6 | 13690 | 13494.6 | 13419.6 | 13432.2 | 13448.6 | 12211.1 | 13478 | 13483.2 | 13593.3 | 13549.3 | 13513.9 | 13605.7 | 12163.5 | 13630 | 12234.7 | 36.3807 | 36.0977 | 36.5953 | 36.3215 | 36.2594 | 36.5241 | 0 | 50.6 | 0 | 0 | 50.8 | 51.3 | 2.8914 | 2.9903 | 2.7281 | 1.2802 | 3.0158 | 2.1463 | 7.1733 | 6.2583 | 6.7867 | 6.395 | 5.94 | 7.1167 | 7.2736 | 7.3067 | 7.3622 | 7.2675 | 7.3489 | 7.3772 | 1.7208 | 1.6697 | 1.5786 | 1.8626 | 1.9715 | 1.5476 | 7.1951 | 7.2266 | 7.161 | 7.1728 | 7.2032 | 7.2034 | 0.50653 | 0.56614 | 0.50189 | 0.48188 | 0.52341 | 0.5283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 936716 | 1750 | 923513 | 1776 | 165187.813 | 371.133 | 7.2736 | 7.3067 | 7.3622 | 7.2675 | 7.3489 | 7.3772 | 7.1951 | 7.2266 | 7.161 | 7.1728 | 7.2032 | 7.2034 | 993000 | 2000 | 985000 | 2000 | 1975000 | 4400 | 1974000 | 1970600 | 12.9833 | 7.3227 | 1.7251 | 7.1937 | 0.51803 | 23.56% | 7.201% | 36.3631 | 50.9 | 2.5087 | 6.6117 | 1987766.4 | 1953333 | 2350858.1761 | 83.09% | 24 | 0
2025-05-12 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 335090.89 | 6:21 | 19:17 | 11818.4 | 12248.3 | 12179.9 | 12174.6 | 12260.6 | 12316.7 | 12327.2 | 12587.2 | 12253.3 | 12283.3 | 12131.4 | 12219.7 | 12252.5 | 12155.2 | 12296.9 | 12311.5 | 12206.9 | 12215.8 | 12219.1 | 12299.9 | 12231.5 | 12245.6 | 12083.2 | 12146.6 | 12035.9 | 10904.6 | 12017.8 | 12009.3 | 12271.8 | 12174.1 | 12120.7 | 12259.2 | 13060.7 | 13062 | 13179.8 | 13077.3 | 12322.2 | 12194.2 | 12211.6 | 12187.2 | 12851.6 | 12023 | 12738.6 | 11874.7 | 12393.3 | 13286.1 | 11857.2 | 12860.7 | 12346.2 | 12454.3 | 12324.7 | 11848.4 | 12578.4 | 12463.1 | 12522.6 | 12459 | 11515.1 | 12692.8 | 11560.4 | 12656.4 | 12552.3 | 11509.9 | 12325 | 11893.2 | 12030.8 | 11521 | 12028.5 | 12369.6 | 12580.2 | 11691.1 | 12464.8 | 11350.9 | 12230.9 | 12032.1 | 11571.8 | 12449.8 | 11413.9 | 12636.9 | 11583 | 12478.1 | 11732.9 | 12369.1 | 11818.1 | 12654.4 | 11723.7 | 12259.1 | 11692.7 | 10610.1 | 12425.5 | 12114 | 11471.4 | 12704.8 | 12435.7 | 11807.6 | 11696.1 | 12504.5 | 11610.9 | 11949 | 12653.4 | 11544.2 | 12683.6 | 11548.5 | 12483.4 | 11770.2 | 12498.5 | 11266.3 | 12566.9 | 11685.3 | 12425.3 | 11608.7 | 12498.2 | 11857.3 | 11538 | 12391.2 | 11680.1 | 11511.9 | 12484.3 | 12540.1 | 12406.2 | 11703.5 | 12499.5 | 11583.3 | 12300.9 | 11690.8 | 12165.7 | 11034.7 | 12332 | 11622.3 | 11752.1 | 11785.8 | 11577.2 | 10326 | 11603.1 | 10545.4 | 11576 | 11607.7 | 12891.7 | 11778.1 | 12920.6 | 11976.1 | 12853.2 | 11865.1 | 12011.8 | 11782 | 12636.4 | 12925.9 | 12881.7 | 12820.2 | 12814 | 12837.1 | 12065.3 | 12858.3 | 12870.7 | 12914.7 | 12911.4 | 12894.6 | 12926.3 | 12044.3 | 12955.6 | 12104.6 | 36.0535 | 35.8478 | 36.1873 | 35.8356 | 35.5937 | 36.1416 | 0 | 48.7 | 0 | 0 | 49 | 49.4 | 5.2577 | 5.5364 | 5.2549 | 4.1459 | 5.3628 | 5.5266 | 9.5267 | 9.565 | 10.73 | 9.03 | 9.3333 | 9.99 | 7.5217 | 7.5542 | 7.6086 | 7.5037 | 7.5976 | 7.6408 | 1.8052 | 1.7508 | 1.6549 | 1.947 | 2.0546 | 1.6267 | 7.4251 | 7.464 | 7.3823 | 7.3944 | 7.4186 | 7.4574 | 0.5507 | 0.61361 | 0.53695 | 0.5223 | 0.56501 | 0.57241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 937689 | 1751 | 924478 | 1777 | 167123.68 | 375.333 | 7.5217 | 7.5542 | 7.6086 | 7.5037 | 7.5976 | 7.6408 | 7.4251 | 7.464 | 7.3823 | 7.3944 | 7.4186 | 7.4574 | 973000 | 1000 | 965000 | 1000 | 1935867 | 4200 | 1936000 | 1931667 | 12.9333 | 7.5711 | 1.8065 | 7.4236 | 0.56016 | 23.86% | 7.546% | 35.9432 | 49.0333 | 5.1807 | 9.6958 | 1947041 | 2001687.875 | 2461644.7407 | 81.32% | 28 | 0
2025-05-13 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 335090.89 | 6:16 | 19:18 | 12079.4 | 12603.9 | 12541.1 | 12521.5 | 12637.3 | 12705.2 | 12714.9 | 13097.8 | 12614.4 | 12662.9 | 12464.9 | 12571 | 12603.5 | 12505.4 | 12655.1 | 12681.2 | 12571.3 | 12584.3 | 12596.7 | 12661.5 | 12610.1 | 12616.1 | 12408.8 | 12490.8 | 12362.5 | 11100.3 | 12328.5 | 12321.9 | 12649 | 12528.5 | 12451.1 | 12647.2 | 13053.1 | 13061.8 | 13156.4 | 13041.3 | 12723.7 | 12559.2 | 12588.7 | 12557.3 | 13362.8 | 12299.6 | 13237.4 | 12129.4 | 12784.5 | 13868.7 | 12134 | 13382.8 | 12731.1 | 12855.8 | 12684.8 | 12094.5 | 13015.9 | 12863.8 | 12948.4 | 12880.1 | 11766 | 13162.9 | 11798.2 | 13109.7 | 12984 | 11743.1 | 12750.7 | 12205.4 | 12379 | 11766.2 | 12324.3 | 12765.6 | 13042.4 | 11940.2 | 12897.1 | 11578.2 | 12586.8 | 12323.9 | 11809.1 | 12864.6 | 11641.7 | 13098.9 | 11830 | 12905.1 | 11974.6 | 12746.1 | 12071.7 | 13099.4 | 11969.8 | 12610.7 | 11935.5 | 10704.7 | 12857.6 | 12440.3 | 11721 | 13186 | 12870.2 | 12098 | 11981.4 | 12977.1 | 11865.3 | 12233.1 | 13129.8 | 11776.8 | 13158.3 | 11792.4 | 12881.6 | 12030.4 | 12940.7 | 11503.5 | 13009.5 | 11934.4 | 12851 | 11885.8 | 12927.8 | 12108.3 | 11782.6 | 12808 | 11930.7 | 11747.8 | 12918 | 12977.7 | 12807.2 | 11945.1 | 12927.1 | 11825.3 | 12677.7 | 11935.6 | 12556.6 | 11225.5 | 12686.6 | 11857.8 | 12004.7 | 12052.8 | 11842.4 | 10386.8 | 11878.7 | 10691.7 | 11848.9 | 11879.4 | 13393.3 | 12039.6 | 13441.6 | 12251.6 | 13360.8 | 12139.6 | 12317 | 12067.9 | 13081.5 | 13476.4 | 13355.8 | 13292.4 | 13290.2 | 13322.4 | 12357.6 | 13350.2 | 13393.4 | 13415.6 | 13423.1 | 13384.9 | 13422.7 | 12317.6 | 13468 | 12394.2 | 36.64 | 36.5 | 36.79 | 36.43 | 36.28 | 36.72 | 0 | 48.7 | 0 | 0 | 49 | 49.3 | 5.46 | 5.77 | 5.43 | 4.53 | 5.54 | 5.77 | 9.92 | 9.46 | 11.17 | 9.5 | 9.29 | 10.35 | 7.5 | 7.53 | 7.58 | 7.52 | 7.57 | 7.6 | 1.83 | 1.76 | 1.69 | 1.97 | 2.07 | 1.63 | 7.38 | 7.42 | 7.33 | 7.35 | 7.37 | 7.41 | 0.57 | 0.63 | 0.55 | 0.54 | 0.58 | 0.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 938689 | 1753 | 925471 | 1779 | 169112.68 | 379.6 | 7.5 | 7.53 | 7.58 | 7.52 | 7.57 | 7.6 | 7.38 | 7.42 | 7.33 | 7.35 | 7.37 | 7.41 | 1000000 | 2000 | 993000 | 2000 | 1989000 | 4267 | 1989000 | 1984733 | 13.0333 | 7.55 | 1.825 | 7.3767 | 0.575 | 24.17% | 7.795% | 36.56 | 49 | 5.4167 | 9.9483 | 2002101.2 | 2002211.45 | 2438790.7992 | 82.1% | 30 | 0
2025-05-14 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 335090.89 | 6:19 | 19:20 | 12579.7 | 13156.2 | 13096.1 | 13059.9 | 13205.9 | 13268.4 | 13277.4 | 13644.2 | 13169.1 | 13217.5 | 13011 | 13118.3 | 13160.8 | 13043.6 | 13215.7 | 13233 | 13129.6 | 13129.6 | 13152.4 | 13218.9 | 13162.9 | 13170.3 | 12940.6 | 13033.8 | 12900.1 | 11340.1 | 12861.6 | 12856.4 | 13177.1 | 13050.9 | 12984.5 | 13188.8 | 13246.5 | 13252.6 | 13364.8 | 13263.5 | 13261.2 | 13095.2 | 13121.3 | 13089.9 | 13889.1 | 12817.8 | 13763.6 | 12607.7 | 13296.5 | 14344.6 | 12632.3 | 13903.3 | 12355.7 | 12472.2 | 12323.9 | 11717.7 | 12662.2 | 12523.3 | 12597.3 | 12523.7 | 12128.7 | 13691.6 | 12149.4 | 13643.6 | 13513.4 | 12113.6 | 13280.4 | 12737.3 | 12890.1 | 12150 | 12836.4 | 13290.1 | 13574.4 | 12378.1 | 13439 | 11889.1 | 13122.5 | 12848.5 | 12220.3 | 13400.2 | 11996.9 | 13638.4 | 12235 | 13436.8 | 12428 | 13274.3 | 12554.8 | 13604.5 | 12423.7 | 13145.5 | 12389.1 | 10914.1 | 13345 | 12954 | 12072 | 13687 | 13379 | 12557 | 12421 | 13472 | 12249.4 | 12723.6 | 13624.9 | 12170.8 | 13659.9 | 12172.2 | 13412.8 | 12466.1 | 13444.7 | 11800.1 | 13516.8 | 12366.3 | 13372 | 12280.7 | 13441.3 | 12540.8 | 12160.7 | 13313.1 | 12293.2 | 12090.6 | 13418.7 | 13494.1 | 13324 | 12371.6 | 13437.8 | 12217.7 | 13180.6 | 12314.8 | 13055 | 11445 | 13219.3 | 12228.2 | 12414.3 | 12468.5 | 12210.2 | 10569.8 | 12250.6 | 10849.8 | 12249.4 | 12277.1 | 13890.1 | 12528.5 | 13937.5 | 12769.5 | 13859.7 | 12631.1 | 12841.2 | 12553.3 | 13662.5 | 14059.9 | 13865.8 | 13790.5 | 13780.3 | 13815.6 | 12887.2 | 13854.4 | 13921.9 | 13924.2 | 13926.3 | 13887.6 | 13933.4 | 12856.2 | 13972.8 | 12930.1 | 36.513 | 36.3695 | 36.7054 | 36.3494 | 36.1135 | 36.6738 | 0 | 49.1949 | 0 | 0 | 49.7566 | 50.2 | 4.9003 | 5.0174 | 4.6508 | 4.2728 | 4.8436 | 5.0997 | 8.59 | 8.64 | 8.6917 | 8.325 | 8.015 | 9.1883 | 7.7051 | 7.7283 | 7.7739 | 7.7143 | 7.76 | 7.7972 | 1.8731 | 1.8194 | 1.7333 | 2.0188 | 2.1244 | 1.6939 | 7.5599 | 7.5988 | 7.5093 | 7.5181 | 7.5333 | 7.601 | 0.57216 | 0.63461 | 0.55736 | 0.54126 | 0.5806 | 0.58943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 939722 | 1754 | 926499 | 1780 | 171169.813 | 383.867 | 7.7051 | 7.7283 | 7.7739 | 7.7143 | 7.76 | 7.7972 | 7.5599 | 7.5988 | 7.5093 | 7.5181 | 7.5333 | 7.601 | 1033000 | 1000 | 1028000 | 1000 | 2057133 | 4267 | 2059000 | 2052866 | 13.0167 | 7.7465 | 1.8772 | 7.5534 | 0.57924 | 24.23% | 7.669% | 36.4541 | 49.7172 | 4.7974 | 8.575 | 2071281.2 | 2039934 | 2493017.2137 | 81.83% | 36 | 0
2025-05-15 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 335090.89 | 6:18 | 19:19 | 12455 | 13030.2 | 13000.9 | 12942.1 | 13133.6 | 13153.4 | 13170 | 13529.5 | 13051.6 | 13103 | 12882.7 | 12986 | 13039.1 | 12915.5 | 13088.6 | 13113.4 | 13016.3 | 13020.1 | 13038.8 | 13100.8 | 13058.2 | 13056.6 | 12822.8 | 12918 | 12787.3 | 11226.3 | 12739.6 | 12729.6 | 13065.3 | 12929.1 | 12870.2 | 13086.1 | 13088.5 | 13093.2 | 13201.8 | 13097.9 | 13156.9 | 12979.8 | 13009.2 | 12979.8 | 13799.7 | 12708.2 | 13671.9 | 12488.1 | 13134.2 | 14179 | 12515.6 | 13817.5 | 13155.2 | 13275.5 | 13116.7 | 12467.4 | 13447.7 | 13301.6 | 13380.5 | 13293.7 | 11997.7 | 13582.7 | 12021.8 | 13540.9 | 13412.8 | 11998.3 | 13148.7 | 12589.5 | 12789 | 11988.9 | 12719.4 | 13186.6 | 13465.7 | 12255.4 | 13330.1 | 11766.4 | 13010.7 | 12731.5 | 12094.1 | 13304.5 | 11875 | 13542.3 | 12120.1 | 13343.8 | 12310.4 | 13194.2 | 12436.4 | 13536.3 | 12301.4 | 13046.1 | 12292 | 10813.1 | 13278 | 12854 | 11968 | 13623 | 13275 | 12404 | 12263 | 13415 | 12153 | 12631.4 | 13564.4 | 12065.1 | 13590.5 | 12066.7 | 13317 | 12353.1 | 13370.1 | 11690.1 | 13438.3 | 12241.9 | 13282.8 | 12183.9 | 13357.7 | 12419.6 | 12053 | 13245.3 | 12236.7 | 11998.6 | 13333.4 | 13414.7 | 13234.1 | 12244.7 | 13356.4 | 12091.7 | 13100.5 | 12225 | 12943.4 | 11322.7 | 13104.2 | 12098.1 | 12293 | 12357.7 | 12131.3 | 10463.8 | 12095.8 | 10714.1 | 12146.8 | 12171.6 | 13852.3 | 12435 | 13904.2 | 12682 | 13815.1 | 12524.8 | 12727.4 | 12450.9 | 13568.9 | 13987.8 | 13827.1 | 13759.5 | 13751.7 | 13779.3 | 12799.2 | 13824.4 | 13873.3 | 13886.6 | 13893.7 | 13852.3 | 13899.6 | 12770.6 | 13917.9 | 12836.7 | 38.0247 | 37.7591 | 38.1792 | 37.9146 | 37.5841 | 38.1906 | 0 | 51.6 | 0 | 0 | 51.7 | 52.2 | 3.8342 | 3.9898 | 3.5207 | 1.8471 | 3.9518 | 3.6323 | 8.2383 | 7.1833 | 8.2617 | 7.4283 | 7.26 | 8.0933 | 7.6899 | 7.7332 | 7.7641 | 7.7041 | 7.7461 | 7.8047 | 1.881 | 1.8175 | 1.7405 | 2.0277 | 2.1267 | 1.695 | 7.5286 | 7.5922 | 7.483 | 7.4948 | 7.498 | 7.5928 | 0.57358 | 0.63632 | 0.56087 | 0.53925 | 0.58286 | 0.59186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 940749 | 1756 | 927519 | 1782 | 173217.814 | 388.333 | 7.6899 | 7.7332 | 7.7641 | 7.7041 | 7.7461 | 7.8047 | 7.5286 | 7.5922 | 7.483 | 7.4948 | 7.498 | 7.5928 | 1027000 | 2000 | 1020000 | 2000 | 2048001 | 4466 | 2043000 | 2043535 | 13.0167 | 7.7404 | 1.8814 | 7.5316 | 0.58079 | 24.31% | 7.711% | 37.942 | 51.8333 | 3.4626 | 7.7442 | 2061967.6 | 2029867 | 2461206.2481 | 82.47% | 36 | 0
2025-05-16 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 335090.89 | 6:20 | 19:19 | 12396.3 | 13001.6 | 12952.8 | 12907.7 | 13095.1 | 13124 | 13122.9 | 13475 | 13024.1 | 13053.2 | 12850.9 | 12943 | 13025.6 | 12875.9 | 13066.1 | 13089.8 | 12998.2 | 12993.8 | 13022.5 | 13084.2 | 13041.8 | 13032.7 | 12816.9 | 12911.9 | 12754 | 11173.5 | 12717.3 | 12718.4 | 13028.6 | 12908.9 | 12857.7 | 13060.6 | 13053.6 | 13059.2 | 13166.8 | 13055.9 | 13112.2 | 12938.8 | 12974.5 | 12950.6 | 13767.3 | 12693.5 | 13646.4 | 12466.1 | 13141.3 | 14115.4 | 12504.9 | 13772.2 | 13085.5 | 13226.9 | 13100.7 | 12409.8 | 13405.4 | 13271.4 | 13355.5 | 13266.8 | 11934.9 | 13540.8 | 11957.9 | 13486.1 | 13340.2 | 11925.9 | 13095 | 12558.7 | 12771.6 | 11976.9 | 12676.4 | 13135.6 | 13424.3 | 12183.3 | 13279.8 | 11693.4 | 12972.8 | 12658.9 | 12021.9 | 13244 | 11809.9 | 13487.6 | 12060.1 | 13284 | 12239.1 | 13135.5 | 12365.1 | 13460.1 | 12237.1 | 12999.6 | 12220.2 | 10748 | 13208 | 12818 | 11895 | 13581.5 | 13264 | 12410 | 12281 | 13383 | 12108 | 12572.8 | 13501.4 | 12005.4 | 13529.5 | 11995 | 13283.9 | 12282.9 | 13316.5 | 11620.4 | 13389 | 12166.3 | 13253.8 | 12101.2 | 13348.6 | 12343.8 | 11971.7 | 13184.4 | 12165.8 | 11932.9 | 13288.6 | 13355.1 | 13205.8 | 12148 | 13289 | 12009.7 | 13065.3 | 12152 | 12920.7 | 11252.6 | 13069.9 | 12014.9 | 12235 | 12321.2 | 12061.3 | 10415.7 | 12069 | 10666.9 | 12074.7 | 12093.4 | 13755.6 | 12353.7 | 13815.6 | 12624.7 | 13721.9 | 12465.9 | 12693.6 | 12376.2 | 13594.4 | 14035.7 | 13737 | 13663.8 | 13646.9 | 13679.9 | 12749.9 | 13736.4 | 13797.5 | 13809.9 | 13819.7 | 13758 | 13825.6 | 12717.4 | 13849.3 | 12796.6 | 38.6972 | 38.4034 | 38.6206 | 38.5365 | 38.1945 | 38.7009 | 0 | 50.8 | 0 | 0 | 50.7 | 51.1 | 5.8301 | 5.934 | 5.7741 | 4.5305 | 5.8466 | 5.9403 | 9.445 | 10.1833 | 9.9117 | 9.8767 | 9.7217 | 9.19 | 7.6309 | 7.6778 | 7.7212 | 7.6483 | 7.6752 | 7.7275 | 1.8844 | 1.8002 | 1.7472 | 2.0536 | 2.1093 | 1.6706 | 0 | 7.5498 | 7.4293 | 0 | 7.4193 | 7.5002 | 0.57825 | 0.64395 | 0.56762 | 0.54505 | 0.59208 | 0.59856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 941777 | 1757 | 928536 | 1784 | 175257.28 | 392.8 | 7.6309 | 7.6778 | 7.7212 | 7.6483 | 7.6752 | 7.7275 | 0 | 7.5498 | 7.4293 | 0 | 7.4193 | 7.5002 | 1028000 | 1000 | 1017000 | 2000 | 2039466 | 4467 | 2042000 | 2034999 | 12.9833 | 7.6801 | 1.8775 | 7.4746 | 0.58758 | 24.45% | 7.861% | 38.5255 | 50.8667 | 5.6426 | 9.7214 | 2054238.2 | 2005600 | 2440748.9097 | 82.17% | 38 | 0
2025-05-17 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 335090.89 | 6:17 | 19:21 | 12589.5 | 13151.7 | 13108 | 13048.2 | 13242.5 | 13277 | 13298.6 | 13659.3 | 13162 | 13222.2 | 12997.4 | 13088.8 | 13155.1 | 13023.1 | 13211 | 13224.4 | 13121.5 | 13132 | 13149.6 | 13226.2 | 13165.7 | 13171.6 | 12953.2 | 13036.9 | 12904.5 | 11361.8 | 12871 | 12868.8 | 13169.9 | 13040.3 | 12991.2 | 13190.9 | 13257.4 | 13266.6 | 13382.2 | 13273.6 | 13258.6 | 13084.7 | 13118.8 | 13090.3 | 13893.6 | 12843.1 | 13755.4 | 12643.4 | 13327.7 | 14369 | 12661.4 | 13913 | 13262.2 | 13396.2 | 13247.6 | 12625.9 | 13578.8 | 13426.4 | 13497.3 | 13410.5 | 12159.2 | 13700.5 | 12181.7 | 13651 | 13520.1 | 12143.3 | 13295.9 | 12753.8 | 12927.8 | 12204.3 | 12861.9 | 13303.2 | 13582.1 | 12423.9 | 13447.8 | 11931.9 | 13133.5 | 12874.7 | 12250.3 | 13414.4 | 12036.1 | 13654.4 | 12288 | 13460.9 | 12471.2 | 13303.2 | 12595.5 | 13657.9 | 12470.2 | 13176.5 | 12437.7 | 10960.2 | 13381 | 12986 | 12114 | 13754 | 13444 | 12622 | 12495 | 13531 | 12313.8 | 12773 | 13675.7 | 12224.8 | 13701.5 | 12211.1 | 13434.1 | 12510.1 | 13477.5 | 11835.2 | 13548 | 12397.6 | 13387.4 | 12307.5 | 13466.9 | 12584.2 | 12209.9 | 13363.4 | 12387 | 12162 | 13461.3 | 13530.5 | 13353.8 | 12381.3 | 13470.1 | 12242.5 | 13212.8 | 12384.6 | 13068 | 11475.9 | 13230.9 | 12254.1 | 12477.6 | 12552.3 | 12282.9 | 10623.1 | 12313 | 10897.8 | 12321.1 | 12343.7 | 13949.3 | 12563.6 | 14004.8 | 12796.5 | 13910.9 | 12653.9 | 12863.1 | 12589.3 | 13662.2 | 14058.1 | 13928.3 | 13861.6 | 13856.5 | 13890.5 | 12924.7 | 13926.2 | 13976.3 | 13977.5 | 13986.4 | 13951.1 | 13997.2 | 12894.7 | 14042.1 | 12965.6 | 36.6979 | 36.46 | 36.7737 | 36.4221 | 36.1441 | 36.7827 | 0 | 49.2 | 0 | 0 | 49 | 49.8617 | 5.6086 | 5.7369 | 5.5497 | 4.9265 | 5.4949 | 5.7471 | 10.3333 | 9.6233 | 11.5667 | 10.0833 | 10.0067 | 9.825 | 7.7266 | 7.7686 | 7.8408 | 7.7419 | 7.7673 | 7.8278 | 1.9069 | 1.835 | 1.7698 | 2.0853 | 2.1438 | 1.7108 | 0 | 7.6233 | 7.4915 | 0 | 7.4747 | 7.579 | 0.59519 | 0.66325 | 0.5828 | 0.56379 | 0.60826 | 0.61579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 942819 | 1759 | 929570 | 1785 | 177326.281 | 397 | 7.7266 | 7.7686 | 7.8408 | 7.7419 | 7.7673 | 7.8278 | 0 | 7.6233 | 7.4915 | 0 | 7.4747 | 7.579 | 1042000 | 2000 | 1034000 | 1000 | 2069001 | 4200 | 2073000 | 2064801 | 13.0667 | 7.7788 | 1.9086 | 7.5421 | 0.60485 | 24.54% | 8.02% | 36.5468 | 49.3539 | 5.5106 | 10.2397 | 2083076.1 | 2019600 | 2465353.7002 | 81.92% | 30 | 0
2025-05-18 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 335090.89 | 6:19 | 19:22 | 12135.6 | 12641.3 | 12596.2 | 12523.7 | 12726.9 | 12750.3 | 12779.1 | 13113.5 | 12653.2 | 12694.7 | 12501.5 | 12581.5 | 12650.4 | 12519.8 | 12706.5 | 12713 | 12612.9 | 12617.5 | 12641 | 12716.3 | 12653.6 | 12660.1 | 12465.3 | 12539 | 12411.2 | 11169.7 | 12381.1 | 12377.1 | 12650.2 | 12536.5 | 12496.7 | 12672.5 | 13091 | 13095 | 13213 | 13100.7 | 12725.9 | 12568.3 | 12513.1 | 12569.3 | 13330.6 | 12357 | 13194.1 | 12190.4 | 12745 | 13777.9 | 12188.1 | 13352.9 | 12737.3 | 12863.2 | 12736.7 | 12189.2 | 13031 | 12895.3 | 12963.8 | 12882.2 | 11830.6 | 13144.6 | 11878.8 | 13101.7 | 12973 | 11821.6 | 12687.5 | 12260.5 | 12450.5 | 11853 | 12381.3 | 12767.7 | 12938.4 | 12009.7 | 12902.7 | 11662.7 | 12581.3 | 12389.5 | 11889.1 | 12872.8 | 11733.5 | 13101.4 | 11934.4 | 12922.7 | 12053.1 | 12771.8 | 12145.5 | 13102.7 | 12052.8 | 12660.4 | 12028.2 | 10797.2 | 12858 | 12493 | 11797 | 13206 | 12902 | 12181 | 12071 | 12982 | 11960.5 | 12306.6 | 13130.3 | 11869.6 | 13157.9 | 11822.4 | 12914.9 | 12094.8 | 12941.7 | 11582.6 | 13006.1 | 12005.8 | 12867.1 | 11963.5 | 12938.2 | 12181.1 | 11865.3 | 12836.7 | 12016.4 | 11845 | 12930.7 | 12988.6 | 12841.6 | 12018.5 | 12927.3 | 11894.4 | 12704.7 | 12004 | 12585.9 | 11295.6 | 12719.4 | 11927.5 | 12078.8 | 12120.2 | 11931.6 | 10462.6 | 11949.2 | 10765.6 | 11971.2 | 11983.4 | 13395.1 | 12122.1 | 13447.5 | 12326.4 | 13355.4 | 12191.5 | 12375.7 | 12150.4 | 13124.6 | 13502.9 | 13373.3 | 13306.5 | 13298.9 | 13334.8 | 12441.2 | 13372.8 | 13417.3 | 13414.5 | 13430.3 | 13400 | 13437.7 | 12404.8 | 13482.6 | 12472 | 37.1599 | 36.8498 | 37.0527 | 36.9102 | 36.6107 | 37.1929 | 0 | 49 | 0 | 0 | 48.8 | 49.1 | 6.9645 | 7.0435 | 6.8993 | 6.7604 | 6.7722 | 7.0574 | 11.5983 | 10.8133 | 11.6567 | 11.1883 | 11.275 | 11.5933 | 7.5927 | 7.6132 | 7.6878 | 7.6052 | 7.6264 | 7.7597 | 1.8795 | 1.7995 | 1.7406 | 2.057 | 2.1114 | 1.6978 | 0 | 7.4737 | 7.3752 | 0 | 7.3357 | 7.5125 | 0.59203 | 0.65968 | 0.57999 | 0.56177 | 0.60478 | 0.61502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 943823 | 1760 | 930566 | 1787 | 179321.881 | 401.2 | 7.5927 | 7.6132 | 7.6878 | 7.6052 | 7.6264 | 7.7597 | 0 | 7.4737 | 7.3752 | 0 | 7.3357 | 7.5125 | 1004000 | 1000 | 996000 | 2000 | 1995600 | 4200 | 1997000 | 1991400 | 13.05 | 7.6475 | 1.881 | 7.4243 | 0.60221 | 24.6% | 8.111% | 36.9627 | 48.9667 | 6.9162 | 11.3542 | 2008375.2 | 1993489.5775 | 2438965.6707 | 81.74% | 29 | 0
2025-05-19 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 335090.89 | 6:17 | 19:23 | 12007 | 12408 | 12358.2 | 12327.1 | 12456.2 | 12476.4 | 12508.8 | 12769.2 | 12411.6 | 12435.2 | 12289.8 | 12358.4 | 12416.8 | 12297.4 | 12475.5 | 12478.5 | 12380.4 | 12378.7 | 12396.6 | 12490 | 12409.9 | 12433.4 | 12284.7 | 12340 | 12184.2 | 11206.6 | 12206.3 | 12196.2 | 12413.9 | 12313.8 | 12298.8 | 12401.3 | 13170.6 | 13170.7 | 13293.2 | 13177.1 | 12480.3 | 12354 | 12242.9 | 12346.5 | 12957.7 | 12215.7 | 12836 | 12089 | 12463.5 | 13332.5 | 12073.9 | 12974.1 | 12503.6 | 12605.3 | 12503.1 | 12083.2 | 12738.7 | 12613.5 | 12677 | 12607.2 | 11798.7 | 12823.3 | 11855.7 | 12794.5 | 12692 | 11790 | 12427.4 | 12124.1 | 12265.3 | 11801.5 | 12225.4 | 12515.4 | 12615.9 | 11929.7 | 12613.3 | 11647.4 | 12356.1 | 12283.5 | 11839.1 | 12585.3 | 11702.7 | 12762.2 | 11870.3 | 12625.7 | 11973 | 12521.9 | 12045.3 | 12776.1 | 11970.1 | 12435 | 11924.8 | 10834.6 | 12586 | 12292.1 | 11760.4 | 12860.2 | 12628.9 | 12089.8 | 11983.1 | 12667.2 | 11896.8 | 12174.2 | 12803.4 | 11815 | 12824.8 | 11761.2 | 12648.4 | 12032 | 12638.7 | 11575.6 | 12706.6 | 11929.2 | 12607.8 | 11896.3 | 12649.1 | 12096.4 | 11812 | 12565.3 | 11943.6 | 11805.9 | 12640.5 | 12690.2 | 12567.3 | 11954.1 | 12636.8 | 11842.1 | 12463.3 | 11934.5 | 12367.1 | 11330.5 | 12486.4 | 11888.1 | 12014.3 | 12038.5 | 11897.8 | 10525 | 11886.3 | 10807.2 | 11910 | 11923.3 | 12988.1 | 12001 | 13046.3 | 12177.7 | 12964.1 | 12068 | 12200.8 | 12042.4 | 12788.8 | 13046.6 | 13016.3 | 12956.3 | 12948.1 | 12967.5 | 12276.2 | 12960.7 | 13038.6 | 13026.4 | 12996.5 | 12991.1 | 13053.7 | 12256.9 | 13100.5 | 12307.7 | 38.5946 | 38.2904 | 38.434 | 38.343 | 38.0701 | 38.5676 | 0 | 49.9 | 0 | 0 | 49.8 | 50.1 | 7.1798 | 7.3281 | 7.0905 | 6.936 | 6.9458 | 7.1275 | 11.0517 | 11.3383 | 11.2983 | 11.165 | 10.6917 | 11.475 | 7.6652 | 7.6836 | 7.7703 | 7.6536 | 7.6979 | 7.8232 | 1.9288 | 1.8276 | 1.7861 | 2.1077 | 2.1473 | 1.7213 | 0 | 7.5346 | 7.4483 | 0 | 7.4003 | 7.561 | 0.60162 | 0.6724 | 0.59321 | 0.57245 | 0.61998 | 0.62583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 944810 | 1762 | 931547 | 1788 | 181286.147 | 405.333 | 7.6652 | 7.6836 | 7.7703 | 7.6536 | 7.6979 | 7.8232 | 0 | 7.5346 | 7.4483 | 0 | 7.4003 | 7.561 | 987000 | 2000 | 981000 | 1000 | 1964266 | 4133 | 1965000 | 1960133 | 13.1 | 7.7156 | 1.9198 | 7.486 | 0.61425 | 24.88% | 8.205% | 38.3833 | 49.9333 | 7.1013 | 11.17 | 1976817.1 | 2007922.35 | 2446054.3414 | 82.09% | 24 | 0
2025-05-20 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 335090.89 | 6:18 | 19:24 | 12296 | 12947 | 12905.5 | 12824.2 | 13026 | 13053.3 | 13111.8 | 13474.2 | 12959.7 | 12995.9 | 12774.5 | 12884.7 | 12912.4 | 12806.4 | 12999 | 13013.5 | 12920.6 | 12883 | 12932.2 | 13010.1 | 12966.6 | 12954.3 | 12704.1 | 12814.2 | 12535.2 | 11085.3 | 12624.7 | 12621.6 | 12956.8 | 12831.5 | 12757.3 | 12925 | 12990.6 | 12992 | 13103.2 | 12987.6 | 13069 | 12891.6 | 12724.9 | 12891.4 | 13726.4 | 12578.1 | 13603.2 | 12350.8 | 12895.3 | 14087.2 | 12378.9 | 13744 | 13056.3 | 13193.5 | 13036.3 | 12325.9 | 13379.9 | 13233.1 | 13313 | 13212.1 | 11861.6 | 13524.1 | 11880.8 | 13471.5 | 13328.4 | 11847.3 | 12978.2 | 12489 | 12674.1 | 11886.6 | 12593.7 | 13105.4 | 13265.5 | 12119.1 | 13255.9 | 11632.8 | 12836.8 | 12695.2 | 11938 | 13233 | 11723.4 | 13478.2 | 11965.3 | 13265.2 | 12168.1 | 13114 | 12299.7 | 13475.6 | 12171.3 | 12961.5 | 12159.3 | 10692.9 | 13200 | 12767.1 | 11816.7 | 13576.2 | 13257.5 | 12331.7 | 12197.6 | 13335.9 | 12017.4 | 12489.4 | 13498.2 | 11930.8 | 13523.1 | 11813.9 | 13238.8 | 12187 | 13305.2 | 11543.1 | 13366 | 12091 | 13194.4 | 12012 | 13285.4 | 12275.3 | 11929.6 | 13189.5 | 12120.1 | 11870.4 | 13290.1 | 13358.8 | 13185.7 | 12103.6 | 13293.4 | 11952.9 | 13020.7 | 12081.4 | 12852.8 | 11193.1 | 13024.3 | 11960.6 | 12176.3 | 12267.1 | 12007.9 | 10371.7 | 12012 | 10626.1 | 12010.8 | 12046.7 | 13790.1 | 12296 | 13851.1 | 12559.4 | 13751.7 | 12394 | 12617.2 | 12311.2 | 13520.2 | 13982.8 | 13768.4 | 13709.5 | 13684.5 | 13722.7 | 12694.8 | 13718.2 | 13816.7 | 13833.5 | 13788.1 | 13743.7 | 13860.5 | 12660.7 | 13891.5 | 12738.5 | 38.6588 | 38.2126 | 38.4025 | 38.5025 | 38.24 | 38.555 | 0 | 50.4 | 0 | 0 | 50 | 50.4 | 5.5595 | 5.5842 | 5.3511 | 4.6328 | 5.5318 | 5.4495 | 8.8467 | 9.2 | 9.0017 | 9.2233 | 9.215 | 9.2283 | 7.5491 | 7.693 | 7.6461 | 7.5534 | 7.5719 | 7.7103 | 1.9 | 1.8337 | 1.7531 | 2.081 | 2.1433 | 1.7457 | 0 | 7.5395 | 7.3518 | 0 | 7.2768 | 7.4896 | 0.60714 | 0.67301 | 0.59624 | 0.57851 | 0.63284 | 0.63078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 945831 | 1763 | 932561 | 1790 | 183317.881 | 409.4 | 7.5491 | 7.693 | 7.6461 | 7.5534 | 7.5719 | 7.7103 | 0 | 7.5395 | 7.3518 | 0 | 7.2768 | 7.4896 | 1021000 | 1000 | 1014000 | 2000 | 2031734 | 4067 | 2032000 | 2027667 | 13.1 | 7.6206 | 1.9095 | 7.4144 | 0.61975 | 25.06% | 8.359% | 38.4285 | 50.2667 | 5.3515 | 9.1192 | 2045266.7 | 1997734 | 2417035.2472 | 82.65% | 34 | 0
2025-05-21 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 335090.89 | 6:18 | 19:24 | 12566 | 13154.7 | 13097.1 | 13035.3 | 13220.5 | 13244.8 | 13292.6 | 13616.2 | 13155.4 | 13171.1 | 12981.8 | 13066.6 | 13131.6 | 12994.7 | 13209.2 | 13225.8 | 13134 | 13086.7 | 13148.6 | 13230.5 | 13188.4 | 13177.6 | 12963.8 | 13055.2 | 12781.8 | 11350.8 | 12867.2 | 12866.4 | 13161.8 | 13042.9 | 12997.2 | 13136.3 | 13174.5 | 13183.1 | 13313.1 | 13206.7 | 13262.8 | 13093.9 | 12948.5 | 13096.9 | 13884.7 | 12840.7 | 13760.1 | 12635.9 | 13052 | 14123.2 | 12648.5 | 13894.3 | 13233.2 | 13377.7 | 13251.2 | 12606.2 | 13558.3 | 13418.9 | 13502.3 | 13397.6 | 12126.4 | 13675.2 | 12151.7 | 13634.2 | 13503.6 | 12113.6 | 13130 | 12711.5 | 12921.8 | 12182.3 | 12849.8 | 13293 | 13444.1 | 12393 | 13433.5 | 11884.6 | 13060.7 | 12929.3 | 12212 | 13398 | 11993.6 | 13593.3 | 12248.6 | 13426.6 | 12432.6 | 13283.4 | 12554 | 13626.3 | 12431.3 | 13147.9 | 12455.3 | 10935.5 | 13362.8 | 12974.4 | 12085.7 | 13718.6 | 13403.8 | 12576 | 12433.2 | 13511.5 | 12306.2 | 12765.3 | 13652.5 | 12205.3 | 13667.2 | 12095.2 | 13432.5 | 12486.1 | 13468.6 | 11813.4 | 13533 | 12364.4 | 13402.7 | 12321.4 | 13469.8 | 12558.3 | 12192.5 | 13350 | 12394.2 | 12137.1 | 13447.2 | 13511.4 | 13358 | 12376.5 | 13440.9 | 12215.3 | 13196.8 | 12340.2 | 13064.1 | 11440.9 | 13213.9 | 12225.3 | 12451.8 | 12530.8 | 12281.2 | 10600.7 | 12267.9 | 10847 | 12293.4 | 12319.6 | 13920.4 | 12549.6 | 13978.4 | 12789.2 | 13866.7 | 12631.6 | 12834.5 | 12569.4 | 13683.9 | 14111.6 | 13906.2 | 13836 | 13817.5 | 13852.9 | 12916 | 13847.8 | 13960.2 | 13971.5 | 13919.6 | 13874.2 | 13982.4 | 12890.8 | 14031.8 | 12969.6 | 38.5985 | 38.2704 | 38.4977 | 38.357 | 38.0381 | 38.5464 | 0 | 50.7 | 0 | 0 | 50.2098 | 51.4881 | 5.9219 | 5.9852 | 5.8345 | 5.5004 | 5.9691 | 6.0077 | 9.4667 | 9.3567 | 10.9517 | 9.3267 | 9.2517 | 10.3767 | 7.8019 | 7.9378 | 8.0472 | 7.7761 | 7.8235 | 7.9294 | 1.9583 | 1.8738 | 1.8118 | 2.1488 | 2.1918 | 1.7851 | 0 | 7.7404 | 7.6456 | 0 | 7.6856 | 7.6694 | 0.61228 | 0.68118 | 0.60152 | 0.58022 | 0.63753 | 0.63764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 946869 | 1764 | 933591 | 1791 | 185382.214 | 413.333 | 7.8019 | 7.9378 | 8.0472 | 7.7761 | 7.8235 | 7.9294 | 0 | 7.7404 | 7.6456 | 0 | 7.6856 | 7.6694 | 1038000 | 1000 | 1030000 | 1000 | 2064333 | 3933 | 2066000 | 2060400 | 13.1 | 7.886 | 1.9616 | 7.6853 | 0.62506 | 24.87% | 8.133% | 38.3847 | 50.7993 | 5.8698 | 9.7883 | 2078810 | 2009334 | 2484674.6828 | 80.87% | 34 | 0
2025-05-22 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 335090.89 | 6:19 | 19:25 | 12426.4 | 13026.3 | 12966.2 | 12914 | 13091.2 | 13118 | 13159.6 | 13498.1 | 13038.3 | 13051.9 | 12848.5 | 12931.4 | 13018.7 | 12862.3 | 13077 | 13110.2 | 13011.8 | 12953.4 | 13035.1 | 13116.8 | 13069.4 | 13050.8 | 12832.5 | 12930.9 | 12637.7 | 11161.5 | 12739.1 | 12716.4 | 13036.8 | 12914.7 | 12874.5 | 13017.2 | 13015 | 13029.6 | 13160 | 13051.8 | 13152.7 | 12975.8 | 12829.1 | 12971.7 | 13775.6 | 12682.7 | 13654.6 | 12459.4 | 12955.7 | 14067.3 | 12511.9 | 13791.9 | 10946.6 | 11093.3 | 10960.1 | 10380.8 | 11233.8 | 11122 | 11194.4 | 11078.9 | 11964.2 | 13564.6 | 11990.4 | 13515.6 | 13379.4 | 11959.3 | 12940.5 | 12557.7 | 12801 | 12013.5 | 12713.3 | 13169.4 | 13336.6 | 12235.7 | 13322.5 | 11732.6 | 12936.1 | 12796.9 | 12061.6 | 13288.3 | 11839.7 | 13542.4 | 12087.8 | 13325.3 | 12280 | 13202.7 | 12398.8 | 13559.8 | 12273.9 | 13040 | 12303.2 | 10798.9 | 13274.7 | 12874.4 | 11948.6 | 13672.5 | 13357.2 | 12476.5 | 12341.9 | 13448.3 | 12159.1 | 12621.3 | 13587 | 12059.4 | 13606.4 | 11950 | 13335.3 | 12322.7 | 13389.5 | 11664.4 | 13455.1 | 12210.1 | 13298.1 | 12156.6 | 13389.1 | 12397.9 | 12041.6 | 13272.6 | 12252.9 | 11990.1 | 13368.3 | 13441.7 | 13271.6 | 12226.9 | 13366.5 | 12066 | 13112.1 | 12195.5 | 12960.7 | 11296.8 | 13116.5 | 12072.8 | 12287.3 | 12387.6 | 12131.4 | 10469 | 12150 | 10725.4 | 12135.1 | 12171.6 | 13869.4 | 12405.4 | 13923.9 | 12661.9 | 13807.5 | 12491.1 | 12716 | 12439.9 | 13538.4 | 14113.9 | 13841.1 | 13775.9 | 13752.4 | 13790.3 | 12803.3 | 13783.9 | 13891.9 | 13908.1 | 13856.1 | 13799.2 | 13914.7 | 12758.3 | 13972 | 12846.5 | 39.2578 | 38.9172 | 39.1071 | 39.0787 | 38.832 | 39.2408 | 0 | 51.2 | 0 | 0 | 51.3 | 51.9282 | 5.5657 | 5.6476 | 5.4445 | 4.7549 | 5.4244 | 5.5062 | 8.8517 | 9.3217 | 9.8967 | 9.0067 | 9.32 | 9.285 | 7.7029 | 7.8291 | 7.9234 | 7.6807 | 7.7227 | 7.8249 | 1.9473 | 1.8622 | 1.7998 | 2.1409 | 2.1783 | 1.7724 | 0 | 7.6428 | 7.5291 | 0 | 7.5792 | 7.5698 | 0.61522 | 0.68283 | 0.601 | 0.58427 | 0.63972 | 0.63975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 947879 | 1766 | 934613 | 1793 | 187410.415 | 417.4 | 7.7029 | 7.8291 | 7.9234 | 7.6807 | 7.7227 | 7.8249 | 0 | 7.6428 | 7.5291 | 0 | 7.5792 | 7.5698 | 1010000 | 2000 | 1022000 | 2000 | 2028201 | 4067 | 2028000 | 2024134 | 13.1 | 7.7806 | 1.9502 | 7.5802 | 0.62713 | 25.06% | 8.273% | 39.0723 | 51.4761 | 5.3906 | 9.2803 | 2042430.3 | 1960601 | 2426110.1401 | 80.81% | 28 | 0
2025-05-23 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 335090.89 | 6:19 | 19:27 | 12109.5 | 12632.3 | 12605.5 | 12540.4 | 12724.6 | 12738.6 | 12760.1 | 13062.6 | 12644.8 | 12680.9 | 12463.4 | 12540 | 12612.9 | 12475.6 | 12699.4 | 12711.8 | 12619.9 | 12580.7 | 12631.9 | 12716.7 | 12670.7 | 12656.3 | 12454 | 12541 | 12285.5 | 11133.6 | 12361.9 | 12313.9 | 12652.3 | 12532.3 | 12484.8 | 12619.7 | 13031.3 | 13064.5 | 13193.3 | 13087.7 | 12760.9 | 12589.6 | 12446.5 | 12586.5 | 13373 | 12364.6 | 13253.6 | 12202.6 | 12582.2 | 13643.6 | 12202 | 13376.2 | 12727.3 | 12857.9 | 12725.5 | 12164.7 | 13032 | 12896.1 | 12974.6 | 12859.7 | 11821.5 | 13153.8 | 11857.3 | 13107.5 | 12982.5 | 11807.3 | 12595.1 | 12238.7 | 12417.7 | 11832.7 | 12349.3 | 12771.8 | 12911.6 | 11990 | 12895.2 | 11638.6 | 12545.5 | 12412 | 11875.3 | 12866.9 | 11701.9 | 13110 | 11888.8 | 12910 | 12016.7 | 12755 | 12103.9 | 13072.3 | 12008.9 | 12604.9 | 12011.1 | 10821.4 | 12805.2 | 12455.9 | 11784.3 | 13181.7 | 12902 | 12172.1 | 12053 | 12964.4 | 11921 | 12270.7 | 13092.9 | 11852.4 | 13122.8 | 11777.2 | 12886 | 12069.7 | 12928.9 | 11564.7 | 12985.6 | 11974 | 12858.6 | 11953.7 | 12928.4 | 12157.4 | 11847.6 | 12811.3 | 11933 | 11804.9 | 12894.7 | 12966.2 | 12816.3 | 12001.6 | 12907.8 | 11867.7 | 12679.1 | 11984.2 | 12548.7 | 11307.1 | 12685.7 | 11896.3 | 12044.4 | 12087.6 | 11925.9 | 10484.6 | 11916 | 10751.5 | 11924.3 | 11952.7 | 13347 | 12088.7 | 13406.4 | 12305.1 | 13297.1 | 12163.7 | 12328.8 | 12135.5 | 13129.4 | 13551.4 | 13336.7 | 13280.3 | 13257.8 | 13291.8 | 12411.1 | 13280.3 | 13375.1 | 13397.2 | 13349.4 | 13299 | 13408.2 | 12382.6 | 13455.6 | 12449.7 | 40.8645 | 0 | 40.6473 | 40.6737 | 40.4627 | 40.7576 | 0 | 0 | 0 | 0 | 51.3 | 51,8 | 6.1193 | 0 | 5.8893 | 5.0761 | 6.2316 | 6.1474 | 11.055 | 0 | 10.635 | 11.1483 | 10.8833 | 10.5017 | 7.7432 | 0 | 7.9712 | 7.7176 | 7.7423 | 7.8434 | 1.9894 | 0 | 1.8354 | 2.1856 | 2.2125 | 1.7949 | 0 | 0 | 7.5807 | 0 | 7.5988 | 7.584 | 0.63408 | 0 | 0.61985 | 0.60632 | 0.66054 | 0.66046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 948878 | 1767 | 935607 | 1795 | 189402.681 | 421.6 | 7.7432 | 0 | 7.9712 | 7.7176 | 7.7423 | 7.8434 | 0 | 0 | 7.5807 | 0 | 7.5988 | 7.584 | 999000 | 1000 | 994000 | 2000 | 1992266 | 4200 | 1990000 | 1988066 | 13.1333 | 7.8035 | 2.0035 | 7.5878 | 0.63625 | 25.67% | 8.385% | 40.6811 | 51.3 | 5.8927 | 10.8447 | 2004758.4 | 1988557.7125 | 2444731.4034 | 81.34% | 30 | 0
2025-05-24 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 335090.89 | 6:18 | 19:24 | 11981 | 12597.7 | 12552.8 | 12500.3 | 12666.7 | 12688.3 | 12731.4 | 13088 | 12602.4 | 12657.4 | 12355.5 | 12441.1 | 12517.7 | 12383.1 | 12581 | 12634.2 | 12486.6 | 12432 | 12540 | 12611.2 | 12561 | 12546.7 | 12273.6 | 12408.7 | 12097.4 | 10623.2 | 12218.5 | 12102.1 | 12541.5 | 12403.2 | 12333.5 | 12514.4 | 12536.2 | 12569.2 | 12682.3 | 12567.7 | 12677.2 | 12494.3 | 12320.1 | 12467.2 | 13414.3 | 12270.2 | 13312 | 12062.3 | 12487.6 | 13605.3 | 12024.6 | 13349.1 | 12665.6 | 12804.9 | 12672.4 | 11916.3 | 12978.2 | 12827.3 | 12922.3 | 12795.1 | 11458.2 | 13114 | 11504.7 | 13080.1 | 12924.4 | 11481.5 | 12570.4 | 12046.8 | 12245.8 | 11492.9 | 12171 | 12684.8 | 12889.7 | 11715.7 | 12800.7 | 11238.9 | 12432.8 | 12262 | 11555.5 | 12815.1 | 11368.4 | 13085.3 | 11606.8 | 12880.7 | 11751.2 | 12671.4 | 11865.8 | 12962.5 | 11762.2 | 12488.6 | 11756.5 | 10351.9 | 12750.2 | 12366.4 | 11461.2 | 13128.9 | 12794.3 | 11900.8 | 11744.8 | 12886 | 11626.2 | 12088.7 | 13038 | 11582.4 | 13097.7 | 11491.1 | 12857.8 | 11845.8 | 12927.9 | 11226 | 12984.3 | 11805.2 | 12869.3 | 11717.7 | 13006.8 | 12027.6 | 11550.6 | 12791.7 | 11652.7 | 11507.9 | 12849 | 13004.9 | 12755.2 | 11804.4 | 12995.3 | 11738.1 | 12711.7 | 11859.9 | 12672.2 | 11049.3 | 12831.5 | 11799.8 | 11911 | 11974.3 | 11853.5 | 10186.5 | 11809.4 | 10450.6 | 11715.9 | 11753.9 | 13312.4 | 11950.4 | 13431.1 | 12242.4 | 13306.2 | 12087.7 | 12291.3 | 12060.1 | 13165.5 | 13803 | 13320 | 13302 | 13290.2 | 13314.3 | 12371.6 | 13348 | 13250.2 | 13306.9 | 13278.4 | 13200.3 | 13373 | 12282.8 | 13413.6 | 12347.2 | 39.1363 | 0 | 38.9234 | 39.1119 | 39.1961 | 38.9283 | 0 | 0 | 0 | 0 | 51.5 | 51.5 | 4.2879 | 0 | 4.0248 | 2.6154 | 4.2821 | 4.2103 | 15.945 | 0 | 14.155 | 13.6883 | 12.5267 | 12 | 7.4712 | 0 | 7.5902 | 7.3329 | 7.4388 | 7.514 | 1.9066 | 0 | 1.7622 | 2.0949 | 2.1078 | 1.6961 | 0 | 0 | 7.2433 | 0 | 7.3143 | 7.2848 | 0.58465 | 0 | 0.57753 | 0.55993 | 0.60428 | 0.60704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 949867 | 1768 | 936592 | 1796 | 191374.148 | 425.933 | 7.4712 | 0 | 7.5902 | 7.3329 | 7.4388 | 7.514 | 0 | 0 | 7.2433 | 0 | 7.3143 | 7.2848 | 989000 | 1000 | 985000 | 1000 | 1971467 | 4333 | 1972000 | 1967134 | 13.1 | 7.4694 | 1.9135 | 7.2808 | 0.58669 | 25.62% | 8.058% | 39.0592 | 51.5 | 3.8841 | 13.663 | 1984633.2 | 1938067 | 2337419.9458 | 82.91% | 34 | 0
2025-05-25 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 335090.89 | 6:55 | 19:21 | 7878.7 | 7253.3 | 7273.9 | 7270.8 | 7111 | 7361 | 6286.7 | 6302.2 | 6744.6 | 6800.4 | 6941.7 | 6451.8 | 6826.4 | 6996.8 | 7108.6 | 7519.2 | 7805.7 | 7722.4 | 7489.5 | 6464.7 | 8120.2 | 7794.6 | 8432.5 | 8412.9 | 6643.5 | 5712.8 | 6467.3 | 7093.1 | 8127.1 | 7514 | 8053.8 | 8022.6 | 7901.5 | 7765.2 | 7264.9 | 7461.4 | 7826.5 | 7562.4 | 7554.1 | 8390.6 | 8976.4 | 8013 | 8906.3 | 7871.9 | 8186.5 | 9142.8 | 7595.2 | 9143.1 | 8089.3 | 8212.2 | 8409.8 | 7216.7 | 8512.7 | 7266.4 | 8668.8 | 8277.5 | 7413 | 8630 | 7371.5 | 7805.6 | 6603.2 | 6016.7 | 7350.8 | 7051.2 | 7714.7 | 7760.4 | 7950.5 | 8546.3 | 8696.6 | 7883.2 | 8657.1 | 7554.4 | 8116.7 | 8036.2 | 7469.4 | 7511.1 | 6172.1 | 8235.8 | 6001.2 | 6680.8 | 7700.3 | 8464.7 | 7197 | 8751.2 | 7414.8 | 7687.2 | 6997.9 | 6611.9 | 6511.7 | 7849.1 | 7199.9 | 7816.8 | 8020.5 | 7099.7 | 6927.3 | 7178 | 6060 | 7371.9 | 8097.6 | 6991.1 | 8258.7 | 7353.2 | 8284.2 | 7154 | 8272.4 | 7055.4 | 8373.9 | 7515.7 | 8108 | 7255.9 | 7857.8 | 7689 | 7298.8 | 7741.4 | 7220.6 | 7061.9 | 7783.9 | 8593.9 | 8111.5 | 7674.3 | 8515 | 7571 | 7904.3 | 7665.8 | 7621.2 | 7118.1 | 8312.8 | 7931.2 | 6506.2 | 5896.4 | 6761.1 | 5668 | 6773.6 | 5600.3 | 6496 | 6615.3 | 8735.4 | 7486.2 | 8457.1 | 7545.6 | 7944.1 | 6608 | 6953.9 | 6666.5 | 8272 | 8730.1 | 8741.8 | 8821.8 | 8684.7 | 8648.4 | 7644.4 | 8437 | 9072.8 | 9096.3 | 8665.8 | 8789.5 | 8645.7 | 7780.9 | 9146.2 | 8046.3 | 38.8687 | 38.4601 | 38.6977 | 38.758 | 38.5321 | 38.5094 | 0 | 48.5845 | 0 | 0 | 48.6531 | 48.5263 | 3.0315 | 2.9532 | 2.7762 | 0.98697 | 3.0159 | 2.4852 | 6.01 | 5.65 | 5.9967 | 5.7017 | 5.8783 | 5.4933 | 4.6724 | 5.0788 | 5.1447 | 4.994 | 5.1039 | 5.0901 | 1.3191 | 1.3013 | 1.1857 | 1.4123 | 1.4826 | 1.2344 | 0 | 5.029 | 5.0224 | 0 | 4.9799 | 4.9767 | 0.47993 | 0.50637 | 0.47593 | 0.45841 | 0.4915 | 0.48601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 950473 | 1769 | 937205 | 1798 | 192591.082 | 430.267 | 4.6724 | 5.0788 | 5.1447 | 4.994 | 5.1039 | 5.0901 | 0 | 5.029 | 5.0224 | 0 | 4.9799 | 4.9767 | 606000 | 1000 | 613000 | 2000 | 1216934 | 4334 | 1216000 | 1212600 | 12.4333 | 5.014 | 1.3226 | 5.002 | 0.48303 | 26.38% | 9.657% | 38.6377 | 48.588 | 2.5415 | 5.7883 | 1220637.4 | 1197133 | 1639412.0355 | 73.02% | 30 | 2358
2025-05-26 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 335090.89 | 6:29 | 19:23 | 10274.5 | 10155.2 | 9917.3 | 10233.1 | 9676.7 | 10046.8 | 9009.4 | 9710.6 | 9398.1 | 10205.3 | 9467.3 | 8474.3 | 10547.7 | 9279.8 | 10520 | 10754.5 | 10726.9 | 10796.2 | 10639.7 | 10317.1 | 10662.9 | 10614.8 | 10716 | 10795.5 | 10500.5 | 9011.1 | 10465.2 | 10464.8 | 10389.1 | 9426 | 10710.4 | 10947.5 | 10430 | 10602.6 | 10632.6 | 10288 | 10550.1 | 10302.2 | 10469.1 | 10734.1 | 11727.3 | 10490.3 | 11522 | 10271.1 | 10690.1 | 11767.5 | 9828.1 | 11807.7 | 10521.7 | 10603.7 | 10926.5 | 10083.1 | 11146.9 | 10254.4 | 11304.4 | 10702.8 | 9646.2 | 11297.9 | 9778.7 | 11331.2 | 11012.6 | 9647.3 | 10167.9 | 9650 | 9855.4 | 10003.5 | 10557.4 | 11084.2 | 11424.2 | 10199.7 | 11255.4 | 9711.6 | 10830.7 | 10633.1 | 10013.2 | 11168.6 | 9728.4 | 11392.6 | 9347 | 10430.4 | 10120.1 | 10955.9 | 9478.4 | 11348.8 | 9654.1 | 10048.3 | 9022.3 | 8696.6 | 8236.2 | 10342.8 | 9250.4 | 9944.6 | 10356.4 | 9169.4 | 8991.5 | 9184.8 | 7660.4 | 9662.6 | 10500.5 | 9206.1 | 10860.4 | 9664 | 10855.3 | 9331.1 | 10908.1 | 9178.6 | 11018 | 10049.3 | 10661.1 | 9599.9 | 10357.6 | 10290.2 | 9758.4 | 10305.5 | 9657.2 | 9357.3 | 10302 | 11384.5 | 10678.6 | 10174.8 | 11312.3 | 10040.9 | 10480.9 | 10186 | 9880.6 | 9347 | 10977.9 | 10198 | 8349.7 | 7492.3 | 8644.4 | 7215.8 | 9016.8 | 7523.8 | 8548.2 | 8656.9 | 11602.1 | 9835.4 | 11570.2 | 10221.4 | 10667.2 | 8709.6 | 9200.2 | 8662 | 11167.8 | 11686.8 | 11438.4 | 11476.9 | 11433.2 | 11479.8 | 10371.1 | 11330.7 | 11996.4 | 11833.7 | 11845.9 | 11766 | 11641.7 | 10413.8 | 12020.6 | 10438.6 | 38.1713 | 37.7555 | 38.1667 | 38.0761 | 37.8412 | 37.8909 | 0 | 48.246 | 0 | 0 | 47.9374 | 47.8672 | 3.891 | 3.7371 | 3.5305 | 1.8577 | 3.655 | 3.5278 | 7.4 | 8.0567 | 7.14 | 6.56 | 6.7567 | 6.6817 | 6.0455 | 6.2974 | 6.3518 | 6.233 | 6.421 | 6.3688 | 1.6483 | 1.5437 | 1.4915 | 1.7662 | 1.7948 | 1.473 | 0 | 6.1548 | 6.1488 | 0 | 6.1483 | 6.207 | 0.57114 | 0.60766 | 0.56464 | 0.54855 | 0.58853 | 0.5842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 951303 | 1771 | 938010 | 1800 | 194222.082 | 434.333 | 6.0455 | 6.2974 | 6.3518 | 6.233 | 6.421 | 6.3688 | 0 | 6.1548 | 6.1488 | 0 | 6.1483 | 6.207 | 830000 | 2000 | 805000 | 2000 | 1631000 | 4066 | 1631000 | 1626934 | 12.9 | 6.2862 | 1.6196 | 6.1647 | 0.57746 | 25.76% | 9.367% | 37.9836 | 48.0169 | 3.3665 | 7.0992 | 1639580.9 | 1610000 | 2028552.3346 | 79.37% | 37 | 0
2025-05-27 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 335090.89 | 6:20 | 19:24 | 10786.5 | 11094.3 | 10844.1 | 10966.7 | 10965.9 | 10980.2 | 10176.1 | 10854.8 | 9984.7 | 11055.2 | 10087.3 | 9031.2 | 11157.9 | 9819.4 | 11166.9 | 11290.6 | 11320.3 | 11339.1 | 11319.2 | 11263.8 | 11301.9 | 11277.8 | 11154.1 | 11276.5 | 11104.8 | 9624.8 | 11013.9 | 10955.6 | 11167.2 | 10664.1 | 11197.9 | 11450.5 | 11234.7 | 11176.2 | 11434.3 | 11179.5 | 11345.8 | 11115.5 | 11277.1 | 11266.3 | 12383 | 11046.5 | 12163.8 | 10820.9 | 11119 | 12267.7 | 10380.4 | 12457.1 | 10958.8 | 11136.4 | 11424.5 | 10679 | 11748.3 | 11058.5 | 11795.4 | 11167.9 | 10117.9 | 11857.6 | 10323.7 | 11940.5 | 11781.9 | 10290.9 | 10766.4 | 10167.5 | 10742.9 | 10442.8 | 11046.8 | 11634.6 | 11938.8 | 10694.2 | 11764.7 | 10186.2 | 11357.2 | 11170.5 | 10494.3 | 11758.8 | 10295.8 | 12011.7 | 10322.1 | 11486.1 | 10716.6 | 11673.1 | 9986.2 | 12052.2 | 10175 | 10614.5 | 10167.3 | 9282.8 | 9122.9 | 11169.9 | 9702.5 | 10534.3 | 10889.3 | 9709.8 | 9533.7 | 10567.3 | 9570.8 | 10776 | 11687.4 | 10144 | 11719.1 | 10423.1 | 11597.4 | 10522.2 | 11719.4 | 10064.6 | 11789.1 | 10601.4 | 11507.4 | 10410.8 | 11478 | 10775.4 | 10460 | 11388.4 | 10569.5 | 10192.6 | 11350.3 | 11934.3 | 11383.4 | 10691.7 | 11867.7 | 10537.3 | 11201.3 | 10639 | 10753.4 | 9833.6 | 11470.3 | 10552.2 | 8869.5 | 8000.3 | 9727.2 | 7743.7 | 9758.4 | 8740.6 | 9776.2 | 9970.1 | 12314.1 | 10487.8 | 12410.8 | 10964.2 | 11548.7 | 9722.3 | 10175.7 | 10043.4 | 11957 | 12419.7 | 12172.6 | 12217 | 12126.5 | 12265 | 11091.3 | 12325.3 | 12530.7 | 12493.7 | 12536.5 | 12458.5 | 12466.3 | 11072.6 | 12611.9 | 11119.6 | 40.097 | 39.5568 | 40.0461 | 39.9252 | 39.764 | 39.5989 | 0 | 51.7324 | 0 | 0 | 51.4 | 51.3944 | 2.71 | 2.6101 | 2.2906 | 0.2708 | 2.4042 | 1.938 | 5.9183 | 5.5367 | 7.9483 | 5.3 | 5.9283 | 5.01 | 6.5431 | 6.5908 | 6.6438 | 6.5245 | 6.7023 | 6.7379 | 1.72 | 1.6248 | 1.5537 | 1.8466 | 1.8769 | 1.5508 | 0 | 6.4316 | 6.4501 | 0 | 6.3947 | 6.5243 | 0.5692 | 0.6112 | 0.56467 | 0.54201 | 0.58519 | 0.58225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 952183 | 1772 | 938876 | 1801 | 195966.482 | 438.6 | 6.5431 | 6.5908 | 6.6438 | 6.5245 | 6.7023 | 6.7379 | 0 | 6.4316 | 6.4501 | 0 | 6.3947 | 6.5243 | 880000 | 1000 | 866000 | 1000 | 1744400 | 4267 | 1744000 | 1740133 | 13.0667 | 6.6237 | 1.6955 | 6.4502 | 0.57575 | 25.6% | 8.926% | 39.8314 | 51.5089 | 2.0373 | 5.9403 | 1754549.5 | 1722067 | 2093595.3529 | 82.25% | 35 | 0
2025-05-28 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 335090.89 | 6:20 | 19:30 | 9650 | 10096.4 | 10121.5 | 10085.3 | 10165.9 | 10287.9 | 10187.3 | 10631.2 | 10199.2 | 10128.2 | 10082.2 | 10172.9 | 10190.1 | 10166.8 | 10158.6 | 10276.6 | 10165.4 | 10198.6 | 10227.9 | 10272.9 | 10238.7 | 10163 | 10027.5 | 10128.9 | 9970 | 8728 | 9957.5 | 9873.8 | 10263.3 | 10133.5 | 10092 | 10296 | 10298.8 | 10340.6 | 10394.1 | 10289.8 | 10406.6 | 10202.8 | 10264.6 | 10256.4 | 11217.3 | 10012 | 11132.3 | 9878.6 | 10402.8 | 11814.7 | 9795.1 | 11210.7 | 10325.7 | 10485.7 | 10319.2 | 9720.6 | 10659.1 | 10385.2 | 10658.4 | 10542.7 | 9380 | 10870 | 9379.3 | 10806.8 | 10643.8 | 9370.3 | 10253.9 | 9721 | 10014.6 | 9442.2 | 9991.5 | 10518.3 | 10796 | 9644.8 | 10618.3 | 9245.8 | 10275.1 | 10058.7 | 9468.2 | 10608.6 | 9274.9 | 10845.5 | 9430.5 | 10575.9 | 9721 | 10555.1 | 9795.3 | 10961.8 | 9710.2 | 10372.7 | 9667.6 | 8555.6 | 10523 | 10248.2 | 9424.5 | 10975.3 | 10589.3 | 9675.4 | 9526.7 | 10631.3 | 9434.3 | 9950.6 | 10943.8 | 9514.8 | 10996.1 | 9528.2 | 10657.4 | 9713.6 | 10789.3 | 9229.4 | 10850.5 | 9695.4 | 10662.5 | 9680 | 10648.6 | 9824.5 | 9580.7 | 10639 | 9701.7 | 9503.2 | 10655.4 | 10879.8 | 10657.3 | 9744 | 10821.8 | 9621.2 | 10399.6 | 9727.4 | 10326.6 | 9005.8 | 10513.4 | 9624.3 | 9678.5 | 9597.6 | 9488.9 | 8191.2 | 9470.1 | 8367.9 | 9402.1 | 9528 | 11325.1 | 9777.7 | 11369.9 | 9989.4 | 11236.2 | 9832.6 | 10020.3 | 9798.8 | 10904.8 | 11388.3 | 11218.9 | 11201.8 | 11191.8 | 11247.9 | 10111 | 11285.1 | 11346.3 | 11358.7 | 11407.4 | 11370.9 | 11339.8 | 10095.8 | 11404.6 | 10065.7 | 37.2238 | 36.843 | 37.1099 | 37.3807 | 37.6444 | 37.5828 | 0 | 49.3 | 0 | 0 | 50 | 50.2 | 2.6876 | 3.2073 | 2.8484 | 0.59116 | 3.2463 | 3.4654 | 5.62 | 6.8867 | 6.065 | 6.2633 | 6.885 | 7.175 | 5.9792 | 6.1723 | 6.2338 | 6.0273 | 6.2375 | 6.1264 | 1.4196 | 1.3497 | 1.2408 | 1.5711 | 1.647 | 1.3452 | 0 | 6.0561 | 5.8625 | 0 | 5.922 | 5.9248 | 0.46958 | 0.53745 | 0.42073 | 0.46857 | 0.50269 | 0.51336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 952996 | 1773 | 939692 | 1803 | 197592.015 | 442.867 | 5.9792 | 6.1723 | 6.2338 | 6.0273 | 6.2375 | 6.1264 | 0 | 6.0561 | 5.8625 | 0 | 5.922 | 5.9248 | 813000 | 1000 | 816000 | 2000 | 1625533 | 4267 | 1626000 | 1621266 | 13.1667 | 6.1294 | 1.4289 | 5.9413 | 0.4854 | 23.31% | 8.17% | 37.2974 | 49.8333 | 2.6743 | 6.4825 | 1634051.2 | 1603133 | 1956019.8606 | 81.96% | 29 | 786
2025-05-29 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 335090.89 | 6:26 | 19:28 | 9936.6 | 10397.5 | 10413.6 | 10372.6 | 10450.9 | 10643.4 | 10596.3 | 11045.1 | 10531.1 | 10339.4 | 10352.8 | 10437.7 | 10484.8 | 10396.3 | 10417.3 | 10530.8 | 10402.7 | 10445.6 | 10478.7 | 10539.7 | 10482.4 | 10397.4 | 10264.8 | 10353.9 | 10164.8 | 8899.7 | 10069.1 | 10049.3 | 10490.2 | 10333.6 | 10275.4 | 10483.8 | 10540.2 | 10516.5 | 10607.6 | 10506.1 | 10509.3 | 10282.6 | 10457 | 10479.1 | 11262.8 | 10049 | 11184.8 | 9886.5 | 10539.3 | 11852.6 | 9649.9 | 11164.8 | 10549.4 | 10716.9 | 10571.6 | 9969.6 | 10939 | 10724 | 10890.3 | 10755.4 | 9586.9 | 11101.7 | 9623.8 | 11058.9 | 10908.5 | 9608.1 | 10500.3 | 9936.2 | 10259.5 | 9689.3 | 10249.1 | 10885.9 | 11089.2 | 9974.7 | 10908.7 | 9561.1 | 10563.3 | 10371.4 | 9748.9 | 10941.4 | 9579.7 | 11159.3 | 9720.3 | 10905.6 | 10139.4 | 10987.7 | 10182.2 | 11404.8 | 10076.6 | 10754 | 9970.5 | 8886.3 | 10739.8 | 10620.7 | 9688 | 11220.4 | 10808.7 | 9838.8 | 9680.9 | 10940 | 9534.8 | 10257.5 | 11291.6 | 9798.7 | 11352.6 | 9837.9 | 11001.7 | 10013.6 | 11132.2 | 9533.9 | 11204.6 | 10021 | 11002.3 | 9972.1 | 11076.2 | 10139.3 | 9883.1 | 10914.8 | 10005.6 | 9801.7 | 11056.1 | 11176.5 | 10969.5 | 10022.1 | 11120.1 | 9891.4 | 10815.5 | 10052.6 | 10626 | 9286.1 | 10824.9 | 9923.9 | 9805.9 | 9710.8 | 9732.8 | 8371.7 | 9569.6 | 8475.4 | 9803.5 | 9836 | 11734.2 | 10116.7 | 11779.4 | 10379.8 | 11627.8 | 10160.1 | 10373.7 | 10096 | 11311.6 | 11787.1 | 11629.8 | 11610.9 | 11604.4 | 11631 | 10465.3 | 11674.1 | 11861.8 | 11817.9 | 11849.9 | 11809.7 | 11763.2 | 10473.2 | 11892.7 | 10514.2 | 34.1951 | 33.7954 | 33.9191 | 34.1005 | 33.794 | 34.3367 | 0 | 44.7 | 0 | 0 | 45.3351 | 45.8 | 1.8234 | 5.2301 | 5.0834 | 4.67 | 5.3288 | 5.0333 | 9.9283 | 11 | 10.29 | 10.925 | 12.9117 | 11.94 | 6.1605 | 6.1968 | 6.1372 | 6.2102 | 6.3924 | 6.4248 | 1.5185 | 1.3999 | 1.3556 | 1.6762 | 1.6847 | 1.3496 | 0 | 6.0605 | 5.9281 | 0 | 6.2273 | 6.2184 | 0.47392 | 0.5349 | 0.43881 | 0.46852 | 0.50651 | 0.50616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 953827 | 1774 | 940534 | 1805 | 199259.949 | 447.2 | 6.1605 | 6.1968 | 6.1372 | 6.2102 | 6.3924 | 6.4248 | 0 | 6.0605 | 5.9281 | 0 | 6.2273 | 6.2184 | 831000 | 1000 | 842000 | 2000 | 1667934 | 4333 | 1670000 | 1663601 | 13.0333 | 6.2537 | 1.4974 | 6.1086 | 0.48814 | 23.94% | 7.991% | 34.0235 | 45.2784 | 4.5282 | 11.1658 | 1678762.3 | 1619067 | 2001372.1359 | 80.9% | 32 | 12103
2025-05-30 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 335090.89 | 6:19 | 19:26 | 11827.7 | 12453.1 | 12403.2 | 12337.4 | 12514 | 12579.8 | 12627.3 | 13092.7 | 12496.6 | 12451.9 | 12291.7 | 12410.2 | 12430.1 | 12379.5 | 12455.9 | 12518.5 | 12400.7 | 12417.1 | 12449 | 12547.7 | 12471.8 | 12373.4 | 12193.3 | 12309.2 | 12168 | 10625.9 | 12110.4 | 12033.2 | 12529.8 | 12443.7 | 12267.8 | 12543.1 | 12510.2 | 12504.9 | 12599.3 | 12503.3 | 12647.1 | 12421.5 | 12489.5 | 12425.8 | 13339.3 | 11974.4 | 13238.5 | 11761.6 | 12608.7 | 13939.3 | 11587.8 | 13236.1 | 12538.4 | 12751.1 | 12535 | 11807.9 | 12956 | 12774.8 | 12854.8 | 12772.4 | 11344.2 | 13090.7 | 11389.1 | 13042.8 | 12888.3 | 11357.9 | 12525.9 | 11890 | 12063.2 | 11373.7 | 12035.6 | 12627.3 | 12992.2 | 11609.7 | 12805.9 | 11142.7 | 12425.1 | 12156.9 | 11466.8 | 12803.7 | 11243.9 | 13102.3 | 11490.3 | 12845.7 | 11654.1 | 12624.9 | 11750.6 | 13018.2 | 11626.1 | 12421.9 | 11616.8 | 10224.3 | 12737.6 | 12238.8 | 11320.8 | 13120.6 | 12757.8 | 11759.8 | 11605.7 | 12907.3 | 11524.3 | 11964.4 | 13069.1 | 11408.3 | 13105.5 | 11422.9 | 12764.9 | 11693 | 12873.4 | 11082.1 | 12933.3 | 11589.1 | 12743.3 | 11545.2 | 12858.8 | 11767.5 | 11423.2 | 12695.7 | 11588.5 | 11359.3 | 12811.3 | 12873.6 | 12699.6 | 11555.4 | 12810.7 | 11417.6 | 12529.7 | 11589.3 | 12355.1 | 10703.5 | 12483.1 | 11423 | 11628.6 | 11699.8 | 11472.2 | 9902.4 | 11448.3 | 10123.4 | 11278.3 | 11325.8 | 13266.1 | 11623.4 | 13321.6 | 11881.6 | 13201.7 | 11678.3 | 11906.5 | 11583.2 | 12920.5 | 13435.2 | 13205.5 | 13139 | 13134.9 | 13179.1 | 11993.1 | 13190.2 | 13289.7 | 13302.9 | 13292 | 13247 | 13260 | 11940 | 13388.2 | 12038.9 | 35.9096 | 35.8068 | 36.0947 | 35.8111 | 35.7183 | 35.9541 | 0 | 48.5 | 0 | 0 | 48.8459 | 49.2 | 0.56715 | 5.4292 | 4.681 | 5.0871 | 5.239 | 5.1482 | 7.7567 | 8.4767 | 8.5433 | 8.8483 | 8.3267 | 9.1667 | 7.314 | 7.4144 | 7.4393 | 7.3825 | 7.4137 | 7.3813 | 1.8035 | 1.6981 | 1.6228 | 1.991 | 1.972 | 1.6181 | 0 | 7.1955 | 7.0736 | 0 | 7.1263 | 7.0974 | 0.58001 | 0.64321 | 0.52543 | 0.56484 | 0.5708 | 0.59213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 954812 | 1776 | 941506 | 1806 | 201211.882 | 451.467 | 7.314 | 7.4144 | 7.4393 | 7.3825 | 7.4137 | 7.3813 | 0 | 7.1955 | 7.0736 | 0 | 7.1263 | 7.0974 | 985000 | 2000 | 972000 | 1000 | 1951933 | 4267 | 1954000 | 1947666 | 13.1167 | 7.3909 | 1.7842 | 7.1232 | 0.5794 | 24.14% | 8.134% | 35.8824 | 48.8486 | 4.3586 | 8.5197 | 1964991.7 | 1925933 | 2346160.8979 | 82.09% | 41 | 0
2025-05-31 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 335090.89 | 6:19 | 19:27 | 11320.1 | 11770.7 | 11715.2 | 11670.8 | 11803.7 | 11864.6 | 11858.2 | 12212.4 | 11781.1 | 11734.2 | 11620.7 | 11701.2 | 11774.9 | 11679.7 | 11793 | 11859.7 | 11744.6 | 11771.5 | 11769.3 | 11869.2 | 11791.6 | 11729.9 | 11633 | 11700.1 | 11558.1 | 10354 | 11526.3 | 11470.1 | 11824.1 | 11744.2 | 11652.5 | 11833.2 | 12179.3 | 12183.8 | 12280 | 12190.1 | 11904.1 | 11737.1 | 11778 | 11749.2 | 12503.6 | 11496.8 | 12412.4 | 11358.7 | 11930.5 | 13065.3 | 11237.2 | 12473.5 | 11834 | 12006.4 | 11870.3 | 11335.7 | 12179 | 11990.7 | 12099.1 | 12027.5 | 10992.3 | 12273 | 11065.8 | 12242.2 | 12120.8 | 11025 | 11776.4 | 11318.9 | 11518.7 | 10939.3 | 11511.1 | 11926.7 | 12204.7 | 11191.6 | 12048.2 | 10856.4 | 11787.6 | 11594.9 | 11091.2 | 12041.5 | 10922.9 | 12277.3 | 11093.7 | 12060.7 | 11241.1 | 11939.6 | 11294.5 | 12285.6 | 11216.2 | 11793 | 11171.9 | 10011.6 | 11972.5 | 11673.7 | 10989.3 | 12338.6 | 12014.9 | 11270.7 | 11141.9 | 12122.3 | 11101.7 | 11449.2 | 12294.7 | 11041.1 | 12320.3 | 11054.9 | 12034.9 | 11276.2 | 12106.5 | 10785 | 12176.7 | 11187.7 | 12007.9 | 11113.6 | 12106.6 | 11349.6 | 11058 | 11997.8 | 11101.3 | 11026.9 | 12103.2 | 12165.3 | 12001.6 | 11208.9 | 12102.5 | 11093.3 | 11861.4 | 11211.6 | 11766 | 10501.9 | 11871.8 | 11126.8 | 11234 | 11240.3 | 11267.2 | 9681.7 | 11060.5 | 9862.5 | 11012.6 | 11057.9 | 12548.5 | 11256.5 | 12584.9 | 11427.5 | 12457.4 | 11240.7 | 11412.4 | 11244.3 | 12196.7 | 12572.4 | 12494.2 | 12449 | 12445.7 | 12493 | 11520.2 | 12491.8 | 12586.9 | 12582.3 | 12575.5 | 12556.8 | 12544.7 | 11508.4 | 12650.6 | 11570.4 | 35.6542 | 35.5112 | 35.6246 | 35.604 | 35.3322 | 35.8887 | 0 | 46.5 | 0 | 0 | 46.5 | 46.7 | 1.1927 | 7.8748 | 7.588 | 8.0351 | 7.6136 | 8.2587 | 8.975 | 11.65 | 12.0717 | 11.7733 | 11.1817 | 11.6533 | 7.0035 | 7.0732 | 7.1195 | 7.0501 | 7.0861 | 7.0876 | 1.761 | 1.6782 | 1.5887 | 1.941 | 1.9468 | 1.595 | 0 | 6.9006 | 6.7988 | 0 | 6.8382 | 6.8713 | 0.58796 | 0.65076 | 0.54129 | 0.57218 | 0.58515 | 0.60177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 955748 | 1777 | 942435 | 1808 | 203072.949 | 455.733 | 7.0035 | 7.0732 | 7.1195 | 7.0501 | 7.0861 | 7.0876 | 0 | 6.9006 | 6.7988 | 0 | 6.8382 | 6.8713 | 936000 | 1000 | 929000 | 2000 | 1861067 | 4266 | 1862000 | 1856801 | 13.1333 | 7.07 | 1.7518 | 6.8522 | 0.58985 | 24.78% | 8.608% | 35.6025 | 46.5667 | 6.7605 | 11.2175 | 1871744.9 | 1794879.16 | 2189670.9235 | 81.97% | 30 | 0
2025-06-01 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 335090.89 | 6:31 | 19:25 | 9566.7 | 9898.4 | 9851.5 | 9817.3 | 9923.8 | 9975.6 | 9948.1 | 10173.7 | 9877.2 | 9835.7 | 9772.1 | 9803.3 | 9921.9 | 9808.5 | 9929.5 | 9997 | 9900.5 | 9923.3 | 9913 | 10007.8 | 9937.8 | 9878.4 | 9833.1 | 9881 | 9756.6 | 8968.3 | 9743.6 | 9699.1 | 9958.5 | 9882.5 | 9852.8 | 9969 | 11776.6 | 11809.9 | 11934.3 | 11815.3 | 10010 | 9888.3 | 9912.2 | 9891.8 | 10394.7 | 9691.2 | 10332.8 | 9586.8 | 9957.1 | 10758.5 | 9532.8 | 10411.5 | 10000.2 | 10066.9 | 9994.2 | 9586 | 10207.2 | 10048.3 | 10146.2 | 10102.2 | 9354.2 | 10282.4 | 9413.8 | 10243.3 | 10141.4 | 9373.2 | 9929.4 | 9596.5 | 9684 | 9389.6 | 9714.3 | 10041.3 | 10217.4 | 9518.1 | 10122.9 | 9294.6 | 9918.4 | 9817.4 | 9422.7 | 10131.8 | 9324.7 | 10281.4 | 9433.3 | 10134.4 | 9549 | 10076.1 | 9592.1 | 10286.7 | 9517.2 | 9927.1 | 9481 | 8808.4 | 10046.6 | 9834.6 | 9334.5 | 10289.6 | 10025.3 | 9484.9 | 9373.6 | 10098.4 | 9428.9 | 9676.4 | 10276.9 | 9402.7 | 10313.2 | 9402.7 | 10115.9 | 9559.1 | 10157.6 | 9227.4 | 10209.1 | 9502.1 | 10101.5 | 9478.8 | 10170.6 | 9632.6 | 9398.8 | 10063.7 | 9457.9 | 9378.6 | 10089.6 | 10188.7 | 10059.5 | 9467.3 | 10155.8 | 9448.3 | 9988.5 | 9515.6 | 9908.8 | 9101.8 | 10001.8 | 9487.7 | 9494.2 | 9493.1 | 9074.6 | 8494.8 | 9330.7 | 8663.7 | 9453.2 | 9470.6 | 10509.2 | 9572.4 | 10561.6 | 9718.1 | 10444.1 | 9547.8 | 9672.3 | 9590.3 | 10278 | 10550.6 | 10491.4 | 10450.7 | 10448.3 | 10485.9 | 9784.2 | 10488 | 10538.1 | 10536.2 | 10523.9 | 10505.5 | 10516 | 9767.5 | 10601.2 | 9810.3 | 34.3113 | 34.083 | 34.3038 | 34.1815 | 33.8937 | 34.4216 | 0 | 46.9 | 0 | 0 | 46.8968 | 47.3 | 1.0048 | 6.0243 | 5.5626 | 6.0522 | 5.8246 | 6.0278 | 9.2083 | 10.0583 | 10.8417 | 10.3217 | 9.335 | 10.2667 | 6.8355 | 6.8875 | 6.887 | 6.7856 | 6.7869 | 6.8001 | 1.6774 | 1.6365 | 1.5039 | 1.8463 | 1.8785 | 1.5596 | 0 | 6.753 | 6.607 | 0 | 6.5511 | 6.6391 | 0.56589 | 0.625 | 0.51831 | 0.54717 | 0.56453 | 0.57798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 956540 | 1779 | 943224 | 1809 | 204649.683 | 459.133 | 6.8355 | 6.8875 | 6.887 | 6.7856 | 6.7869 | 6.8001 | 0 | 6.753 | 6.607 | 0 | 6.5511 | 6.6391 | 792000 | 2000 | 789000 | 1000 | 1576734 | 3400 | 1578000 | 1573334 | 12.9 | 6.8304 | 1.6837 | 6.6376 | 0.56648 | 24.65% | 8.534% | 34.1991 | 47.0323 | 5.0827 | 10.0053 | 1584800.6 | 1748670 | 2208510.9978 | 79.18% | 31 | 800
2025-06-02 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 335090.89 | 6:18 | 19:27 | 11678.3 | 12148.9 | 12094.3 | 12055.3 | 12190.4 | 12267.2 | 12246.7 | 12564.5 | 12114.8 | 12134.2 | 11969.2 | 12000.5 | 12170 | 12020.3 | 12209.1 | 12250.2 | 12141.2 | 12152.6 | 12157.7 | 12251 | 12186.4 | 12121.8 | 12016.7 | 12088 | 11947.7 | 10739.2 | 11911.3 | 11860.9 | 12198.8 | 12077.2 | 12046.4 | 12223.8 | 12564.3 | 12627.9 | 12743.2 | 12625.1 | 12281.3 | 12103.1 | 12130.4 | 12118.8 | 12939.1 | 11914.9 | 12828.2 | 11760.5 | 12323.5 | 13443.8 | 11731.5 | 12964.6 | 12267 | 12375.9 | 12256.6 | 11713.2 | 12565.3 | 12377.5 | 12492.4 | 12417 | 11378 | 12678.7 | 11424.1 | 12631.8 | 12490 | 11377.8 | 12204.1 | 11700.1 | 11913 | 11397.6 | 11862.1 | 12307.9 | 12559.9 | 11558.3 | 12409.4 | 11216.3 | 12135.6 | 11961.9 | 11428.2 | 12398.7 | 11266.5 | 12625 | 11442.6 | 12415.9 | 11599.7 | 12305.1 | 11638.9 | 12659.4 | 11557.1 | 12139.9 | 11547.7 | 10356 | 12334.4 | 12015.7 | 11327.4 | 12696.1 | 12320.3 | 11546.6 | 11393.3 | 12407.1 | 11462.6 | 11797.3 | 12668.7 | 11414 | 12704.3 | 11424.8 | 12421.4 | 11638.7 | 12484 | 11146 | 12547.3 | 11561.4 | 12407.9 | 11543.7 | 12466.9 | 11743.7 | 11410.1 | 12342 | 11553.7 | 11379.1 | 12457 | 12525.3 | 12356.8 | 11575.7 | 12476.1 | 11455.3 | 12231 | 11579.5 | 12106.5 | 10863.2 | 12247.8 | 11493.1 | 11538.3 | 11517.5 | 11477.4 | 9980.4 | 11279.6 | 10070.4 | 11423.1 | 11446.3 | 12944.7 | 11629.4 | 12992.3 | 11808.8 | 12861.6 | 11598 | 11791.4 | 11604.6 | 12579.8 | 12961.3 | 12893.3 | 12831.3 | 12840.6 | 12883.2 | 11915.8 | 12891.1 | 12954.8 | 12950 | 12955.3 | 12924.4 | 12939.8 | 11876.8 | 13020.5 | 11939 | 34.7744 | 34.5777 | 34.9692 | 34.63 | 34.4988 | 34.8334 | 0 | 47.2 | 0 | 0 | 47.3228 | 47.7 | 0.76106 | 6.6695 | 5.8759 | 6.7375 | 6.3558 | 6.6168 | 8.77 | 10.5017 | 11.0167 | 10.355 | 9.705 | 10.3117 | 7.3814 | 7.4244 | 7.4888 | 7.3286 | 7.3068 | 7.2967 | 1.8142 | 1.7461 | 1.6447 | 1.9942 | 2.0046 | 1.6514 | 0 | 7.2239 | 7.1227 | 0 | 6.9883 | 7.0745 | 0.60734 | 0.66744 | 0.56347 | 0.58466 | 0.60049 | 0.614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 957508 | 1780 | 944178 | 1810 | 206569.483 | 462.2 | 7.3814 | 7.4244 | 7.4888 | 7.3286 | 7.3068 | 7.2967 | 0 | 7.2239 | 7.1227 | 0 | 6.9883 | 7.0745 | 968000 | 1000 | 954000 | 1000 | 1919800 | 3067 | 1920000 | 1916733 | 13.15 | 7.3711 | 1.8092 | 7.1023 | 0.60623 | 24.54% | 8.536% | 34.7139 | 47.4076 | 5.5028 | 10.11 | 1931233.6 | 1881512.4 | 2299203.3734 | 81.83% | 23 | 0
2025-06-03 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 335090.89 | 6:16 | 19:26 | 11514.9 | 12031.3 | 11980.8 | 11915.6 | 12102 | 12138.3 | 12147.1 | 12526.4 | 11997.8 | 12044.4 | 11831.5 | 11879.2 | 12016 | 11878.7 | 12048.4 | 12099.9 | 11987.1 | 11994.5 | 12001.9 | 12090.2 | 12034.6 | 11958.2 | 11826.6 | 11910.9 | 11778.6 | 10414.3 | 11736.3 | 11678.6 | 12009.4 | 11907.5 | 11866.7 | 12069.4 | 12205.1 | 12238.2 | 12340.9 | 12233 | 12152.2 | 11967.7 | 12013.3 | 11978.9 | 12850 | 11720.2 | 12742.8 | 11570.8 | 12197.9 | 13392.5 | 11541 | 12883.9 | 12120.8 | 12237 | 12096 | 11503.5 | 12459.9 | 12242.4 | 12373.3 | 12300.3 | 11119 | 12581.4 | 11157.2 | 12525.7 | 12377.1 | 11123.4 | 12088.9 | 11541.4 | 11802.1 | 11175.3 | 11707 | 12201.3 | 12487.2 | 11363.3 | 12321 | 10958.3 | 12017.7 | 11806.5 | 11159.3 | 12292.6 | 11023.5 | 12559.6 | 11253.4 | 12361.5 | 11398.5 | 12187.2 | 11489.6 | 12578.7 | 11392 | 12059.5 | 11349.1 | 10075.4 | 12233.3 | 11901.2 | 11071.5 | 12623.6 | 12266.5 | 11452 | 11331.4 | 12384.5 | 11230.2 | 11651.6 | 12594.6 | 11190.7 | 12603.7 | 11186.3 | 12294.3 | 11435.1 | 12376.1 | 10872.2 | 12443.6 | 11339.5 | 12283.5 | 11321.9 | 12379.6 | 11521.6 | 11195.3 | 12270.5 | 11335 | 11159.1 | 12375.1 | 12439.7 | 12249.9 | 11338.3 | 12379.2 | 11226.7 | 12108 | 11350.6 | 11979.5 | 10557.6 | 12115.8 | 11248.5 | 11356.3 | 11362.6 | 11246.9 | 9735.7 | 11051.8 | 9791.6 | 11218 | 11242.2 | 12909.1 | 11475.1 | 12972.7 | 11676.4 | 12852 | 11512 | 11718.3 | 11471.6 | 12530.6 | 12954.9 | 12844.1 | 12788 | 12793.4 | 12841.8 | 11790.4 | 12862.8 | 12913.2 | 12921.3 | 12933.7 | 12899.7 | 12925.5 | 11756 | 12989.9 | 11818.3 | 34.8475 | 34.6862 | 34.8512 | 34.7329 | 34.4759 | 35.049 | 0 | 46.1 | 0 | 0 | 45.9837 | 46.4 | 0.91096 | 7.0943 | 6.7845 | 7.0518 | 6.7553 | 7.1136 | 8.98 | 11.5483 | 11.505 | 10.6067 | 10.7133 | 11.535 | 7.1052 | 7.1535 | 7.1702 | 7.0322 | 7.0183 | 7.0232 | 1.7986 | 1.7254 | 1.6296 | 1.9777 | 1.9837 | 1.6372 | 0 | 6.9726 | 6.8438 | 0 | 6.7591 | 6.8606 | 0.61743 | 0.68158 | 0.57682 | 0.59919 | 0.61591 | 0.63132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 958460 | 1782 | 945125 | 1811 | 208466.683 | 466.333 | 7.1052 | 7.1535 | 7.1702 | 7.0322 | 7.0183 | 7.0232 | 0 | 6.9726 | 6.8438 | 0 | 6.7591 | 6.8606 | 952000 | 2000 | 947000 | 1000 | 1897200 | 4133 | 1896000 | 1893067 | 13.1667 | 7.0838 | 1.792 | 6.859 | 0.62038 | 25.3% | 9.045% | 34.7738 | 46.1612 | 5.9517 | 10.8147 | 1907785.6 | 1904689.85 | 2289422.5094 | 83.2% | 15 | 0
2025-06-04 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 335090.89 | 6:17 | 19:25 | 11206.5 | 11575.7 | 11517.9 | 11500.8 | 11601 | 11629.2 | 11637.6 | 11875.5 | 11557.5 | 11552.7 | 11478.8 | 11541.9 | 11587.3 | 11521 | 11619.1 | 11658.6 | 11543.8 | 11563.9 | 11563.8 | 11642.6 | 11587.5 | 11599.1 | 11466.2 | 11523 | 11409.6 | 10462.9 | 11396.7 | 11368.3 | 11586.3 | 11475.9 | 11485.3 | 11609 | 12587 | 12628.1 | 12734.7 | 12611 | 11658 | 11537.1 | 11554.8 | 11526.9 | 12127.5 | 11381.7 | 12043.2 | 11273.9 | 11703.4 | 12537 | 11234.6 | 12140.6 | 11660.4 | 11744.8 | 11661.1 | 11242.7 | 11894.4 | 11731.1 | 11835.1 | 11778.1 | 10965.9 | 11973.2 | 11027.5 | 11944.7 | 11847.2 | 10976.4 | 11619.7 | 11243.6 | 11420.9 | 10983.1 | 11366.5 | 11715.5 | 11875.2 | 11127.9 | 11773.3 | 10862.8 | 11577.2 | 11445.9 | 11022.9 | 11751.8 | 10890.8 | 11937.3 | 11068.6 | 11807.7 | 11175.3 | 11720.5 | 11230.5 | 11975.2 | 11163.8 | 11631.5 | 11122.5 | 10228.7 | 11747 | 11501 | 10972.8 | 12027.2 | 11783.9 | 11244.1 | 11135.9 | 11817.8 | 11069.5 | 11364.9 | 11975.7 | 11025.1 | 12002.2 | 11043.3 | 11825.1 | 11232.4 | 11828.4 | 10812.6 | 11895.8 | 11148.1 | 11796.1 | 11126.8 | 11835.4 | 11302 | 11041 | 11751 | 11131.4 | 11008.7 | 11801.4 | 11871.7 | 11746.3 | 11150.9 | 11834.7 | 11058.9 | 11651.6 | 11148.6 | 11562.9 | 10603.5 | 11686.9 | 11099.4 | 11179.3 | 11162.5 | 11045.9 | 9951.8 | 10902.6 | 10057.6 | 11052.7 | 11096.7 | 12185 | 11206.5 | 12229 | 11371.9 | 12153.1 | 11249.7 | 11383.1 | 11232.5 | 11959.8 | 12212.4 | 12188 | 12123 | 12120.8 | 12145.9 | 11453.9 | 12163.2 | 12224 | 12206.8 | 12208.4 | 12196.8 | 12215.3 | 11439.7 | 12286.4 | 11488.7 | 34.9716 | 34.7103 | 35.2148 | 34.8738 | 34.6858 | 34.9439 | 0 | 47.8 | 0 | 0 | 48.0188 | 48.4 | 0.58071 | 5.9986 | 4.8555 | 5.4965 | 5.6943 | 5.7784 | 7.1933 | 9.405 | 9.1267 | 9.6967 | 8.7883 | 9.7583 | 7.408 | 7.4853 | 7.4561 | 7.3241 | 7.2927 | 7.2869 | 1.8808 | 1.8052 | 1.7042 | 2.0683 | 2.0624 | 1.6979 | 0 | 7.2576 | 7.0841 | 0 | 6.9843 | 7.1327 | 0.63974 | 0.70252 | 0.59671 | 0.61737 | 0.63178 | 0.64618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959382 | 1783 | 946044 | 1812 | 210305.15 | 470.6 | 7.408 | 7.4853 | 7.4561 | 7.3241 | 7.2927 | 7.2869 | 0 | 7.2576 | 7.0841 | 0 | 6.9843 | 7.1327 | 922000 | 1000 | 919000 | 1000 | 1838467 | 4267 | 1839000 | 1834200 | 13.1333 | 7.3755 | 1.8698 | 7.1147 | 0.63905 | 25.35% | 8.982% | 34.9 | 48.0729 | 4.734 | 8.9947 | 1847400.8 | 1899898.5 | 2323739.1417 | 81.76% | 20 | 0
2025-06-05 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 335090.89 | 6:16 | 19:27 | 12109.4 | 12752.3 | 12706.4 | 12633.6 | 12818.3 | 12881.3 | 12925 | 13280.7 | 12772 | 12791.4 | 12641.1 | 12788 | 12736.4 | 12709.2 | 12766 | 12833.5 | 12707.1 | 12736 | 12746.7 | 12817.9 | 12783 | 12769.8 | 12504.5 | 12622.9 | 12462.3 | 10877.8 | 12413.3 | 12414.7 | 12759.1 | 12580.1 | 12561.3 | 12808.1 | 12770.3 | 12794.1 | 12894.7 | 12793.2 | 12903.4 | 12689.2 | 12739.4 | 12687.7 | 13612.7 | 12346.8 | 13493.5 | 12159.2 | 12903.4 | 14161.2 | 12184.9 | 13652.4 | 12838.7 | 12959.5 | 12819.9 | 12086.5 | 13216.7 | 13003.8 | 13103.5 | 13021.6 | 11606.4 | 13331.9 | 11663.4 | 13283 | 13138.1 | 11636.8 | 12836.8 | 12159.1 | 12438.3 | 11654.6 | 12311.4 | 12912.7 | 13212.1 | 11898.1 | 13047.9 | 11421.7 | 12698.1 | 12442.9 | 11717 | 13021.4 | 11492.8 | 13290.1 | 11767.7 | 13076.4 | 11955.8 | 12908.4 | 12053.3 | 13318.1 | 11938.9 | 12742 | 11953.7 | 10508.2 | 12976 | 12557.3 | 11581.6 | 13388.5 | 13005.3 | 12007.1 | 11870.3 | 13093.1 | 11764.4 | 12252.2 | 13346.4 | 11722.6 | 13361.7 | 11714.1 | 13025 | 11983.8 | 13116.3 | 11345.8 | 13183.6 | 11903.3 | 12976 | 11810.7 | 13082.1 | 12098.1 | 11727.5 | 12978 | 11915.4 | 11654.6 | 13106.9 | 13200.3 | 12984.2 | 11900.8 | 13124 | 11743.7 | 12360.1 | 11475.4 | 12204.9 | 10623.1 | 12819.4 | 11752.8 | 11918.2 | 11960.2 | 11685.4 | 10138.8 | 11680.7 | 10351.4 | 11752 | 11811.4 | 13654 | 12058 | 13724.1 | 12314.3 | 13622.9 | 12128 | 12378.9 | 12075.4 | 13285.8 | 13734.8 | 13621.2 | 13559.8 | 13548.2 | 13596.4 | 12449.8 | 13627.2 | 13691 | 13691.6 | 13704.8 | 13677 | 13694 | 12405.5 | 13757.5 | 12488.9 | 35.4862 | 35.2529 | 35.6243 | 35.3856 | 35.0866 | 35.5252 | 0 | 48.3 | 0 | 0 | 48.1357 | 48.6 | 1.3456 | 5.464 | 5.024 | 5.128 | 5.2141 | 5.3741 | 7.6117 | 9.6367 | 10.14 | 10.07 | 8.685 | 9.7333 | 7.5282 | 7.6098 | 7.6565 | 7.4221 | 7.3724 | 7.6153 | 1.8855 | 1.8339 | 1.7145 | 2.0806 | 2.0804 | 1.7348 | 0 | 7.377 | 7.2667 | 0 | 7.0664 | 7.3202 | 0.62538 | 0.69294 | 0.58349 | 0.60295 | 0.62382 | 0.64352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 960385 | 1785 | 947041 | 1814 | 212305.683 | 474.8 | 7.5282 | 7.6098 | 7.6565 | 7.4221 | 7.3724 | 7.6153 | 0 | 7.377 | 7.2667 | 0 | 7.0664 | 7.3202 | 1003000 | 2000 | 997000 | 2000 | 2000533 | 4200 | 1996000 | 1996333 | 13.1833 | 7.534 | 1.8883 | 7.2576 | 0.62868 | 25.06% | 8.662% | 35.3935 | 48.3452 | 4.5916 | 9.3128 | 2012506.2 | 1908133 | 2329248.1077 | 81.92% | 22 | 0
2025-06-06 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 335090.89 | 6:17 | 19:29 | 12361.4 | 13008.5 | 13005.7 | 12909.1 | 13158.4 | 13172.8 | 13191.9 | 13591.3 | 13046.8 | 13086.9 | 12895.9 | 13039.2 | 13015.2 | 12968.3 | 13059 | 13107.9 | 12997.2 | 13013.9 | 13023.2 | 13129.4 | 13056.4 | 13043.3 | 12790.3 | 12901.9 | 12744.4 | 11132.2 | 12703.1 | 12701.8 | 13030.1 | 12861.2 | 12833.9 | 13074.6 | 13083.8 | 13087.1 | 13203.1 | 13087.8 | 13168.7 | 12955.4 | 12999.4 | 12957.5 | 13861.2 | 12630 | 13724.6 | 12437.7 | 13189.2 | 14379.7 | 12459.8 | 13894.4 | 13109.8 | 13270.1 | 13108 | 12381.3 | 13485.6 | 13274 | 13388.2 | 13286.8 | 11875.1 | 13606.1 | 11921.4 | 13557.6 | 13415 | 11895.8 | 13112.7 | 12426.8 | 12740.8 | 11948.7 | 12602 | 13197.4 | 13498.2 | 12171.1 | 12023.1 | 0 | 12933.5 | 12674.4 | 12002.3 | 13302.4 | 11764.7 | 13584.4 | 12039.9 | 13349.1 | 12222.4 | 13191.8 | 12323.5 | 13571.4 | 12206.3 | 13013.9 | 12254.3 | 10747.3 | 13221.9 | 12855.3 | 11843.8 | 13627 | 13260.7 | 12254.7 | 12115.8 | 13414.6 | 12050.2 | 12566.3 | 13597.8 | 11994.4 | 13595.3 | 11988.4 | 13300.4 | 12267.5 | 13379.7 | 11613.6 | 13448 | 12170 | 13260.3 | 12103.8 | 13363.7 | 12367.6 | 11987.4 | 13261 | 12167.3 | 11920.9 | 13372.9 | 13446.1 | 13254 | 12164.5 | 13369.3 | 12002.6 | 12582.4 | 12132.9 | 11640.3 | 10742.6 | 13091.1 | 12016.1 | 12165.5 | 12231.2 | 12046 | 10384.4 | 11955.8 | 10561.6 | 11997.1 | 12050.1 | 13895.6 | 12356.3 | 13959.8 | 12619.3 | 13849.5 | 12447.8 | 12680.1 | 12351.6 | 13575 | 14026.9 | 13854.1 | 13803.6 | 13778.7 | 13822 | 12753.4 | 13870.1 | 13923.9 | 13936.1 | 13948 | 13897 | 13941.3 | 12713.8 | 13994.7 | 12789.2 | 37.3941 | 36.9094 | 37.056 | 37.1257 | 36.8351 | 37.2421 | 0 | 48.6 | 0 | 0 | 48.2 | 48.6 | 4.6004 | 6.5272 | 6.3956 | 6.5491 | 6.3973 | 6.5317 | 8.9283 | 10.69 | 11.28 | 10.355 | 10.0433 | 9.9183 | 7.7637 | 7.8118 | 7.8792 | 7.6465 | 7.5704 | 7.837 | 1.9667 | 1.8926 | 1.7929 | 2.1748 | 2.1526 | 1.7927 | 0 | 7.5462 | 7.4465 | 0 | 7.3187 | 7.5 | 0.64956 | 0.72367 | 0.60834 | 0.62995 | 0.65552 | 0.67502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 961394 | 1786 | 948057 | 1815 | 214334.883 | 478.8 | 7.7637 | 7.8118 | 7.8792 | 7.6465 | 7.5704 | 7.837 | 0 | 7.5462 | 7.4465 | 0 | 7.3187 | 7.5 | 1009000 | 1000 | 1016000 | 1000 | 2029200 | 4000 | 2023000 | 2025200 | 13.2 | 7.7514 | 1.9621 | 7.4528 | 0.65701 | 25.31% | 8.816% | 37.0938 | 48.4667 | 6.1669 | 10.2025 | 2042243.5 | 1956800 | 2400315.0825 | 81.52% | 20 | 0
2025-06-07 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 335090.89 | 6:13 | 19:30 | 12319.1 | 12953 | 12982.1 | 12878.1 | 13127.3 | 13141.7 | 13122.4 | 13564.7 | 13006.5 | 13019.5 | 12842.2 | 12976.3 | 13001.4 | 12924.7 | 13020.9 | 13107.6 | 12970.7 | 13000.7 | 13009.8 | 13105 | 13038.3 | 13024.7 | 12766.6 | 12885.4 | 12726.4 | 11102.8 | 12383.7 | 12565.1 | 13026.2 | 12828.5 | 12823.5 | 13081.8 | 13035.6 | 13058.9 | 13175.7 | 13054.2 | 13164.4 | 12946.8 | 12992.4 | 12950.4 | 13862.6 | 12608.9 | 13750.3 | 12401.4 | 13091 | 14284.8 | 12398.9 | 13880.7 | 13093.6 | 13296 | 13097.6 | 12340.9 | 13478.8 | 13276.6 | 13387.2 | 13285.6 | 11834.1 | 13586.9 | 11883.6 | 13553.2 | 13410.7 | 11858.4 | 13110.9 | 12419.5 | 12723.7 | 11915.6 | 12580.1 | 13207 | 13492.1 | 12151.2 | 13331.8 | 11666 | 12959.9 | 12707.4 | 11972 | 13298.4 | 11732.9 | 13580.4 | 12015.2 | 13350.1 | 12199.1 | 13191.3 | 12268.2 | 13592.7 | 12173.7 | 12992.9 | 12231.1 | 10737.3 | 13254.5 | 12827.4 | 11834.6 | 13699.3 | 13337.2 | 12325.3 | 12185.1 | 13447.9 | 12032.5 | 12537.6 | 13632.6 | 11979.9 | 13644.4 | 11974 | 13319 | 12248.3 | 13409.5 | 11600.4 | 13479.2 | 12164.7 | 13264 | 12039.1 | 13374.8 | 12345.6 | 11973.1 | 13273.2 | 12180.5 | 11909.4 | 13401.8 | 13467.1 | 13276.2 | 12151.2 | 13398.1 | 11990.6 | 12430.3 | 11505.9 | 12165.6 | 10572.8 | 13093.7 | 12002.3 | 12164.2 | 12228 | 12007.9 | 10370 | 11857.9 | 10481.2 | 11967.4 | 12009.3 | 13942.4 | 12330 | 14007.3 | 12603.6 | 13896.4 | 12422.2 | 12664.5 | 12345.8 | 13590.7 | 14068.7 | 13884.8 | 13824.9 | 13817 | 13864.2 | 12732.6 | 13904.7 | 13966.3 | 13969 | 13985.1 | 13937.9 | 13973 | 12674.2 | 14036.2 | 12747.5 | 37.5562 | 37.1829 | 37.5028 | 37.4181 | 37.1235 | 37.4472 | 0 | 50.6 | 0 | 0 | 50.3381 | 50.8 | 3.4836 | 4.9709 | 4.7453 | 5.0141 | 5.1388 | 5.0294 | 6.6483 | 7.2883 | 8.0617 | 7.815 | 9.7583 | 7.9817 | 7.8826 | 7.9231 | 7.9978 | 7.7271 | 7.6369 | 7.906 | 1.9758 | 1.922 | 1.8012 | 2.1898 | 2.1726 | 1.8267 | 0 | 7.634 | 7.5032 | 0 | 7.3519 | 7.5439 | 0.65519 | 0.72831 | 0.60865 | 0.63155 | 0.65983 | 0.67779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 962414 | 1788 | 949074 | 1816 | 216374.884 | 482.867 | 7.8826 | 7.9231 | 7.9978 | 7.7271 | 7.6369 | 7.906 | 0 | 7.634 | 7.5032 | 0 | 7.3519 | 7.5439 | 1020000 | 2000 | 1017000 | 1000 | 2040001 | 4067 | 2034000 | 2035934 | 13.2833 | 7.8456 | 1.9813 | 7.5082 | 0.66022 | 25.25% | 8.793% | 37.3718 | 50.5794 | 4.7304 | 7.9256 | 2052991 | 1928466 | 2352061.3952 | 81.99% | 35 | 0
2025-06-08 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 335090.89 | 6:15 | 19:30 | 12468 | 13070.4 | 13066.2 | 13007.3 | 13186.4 | 13186.5 | 13257.3 | 13640.3 | 13134.5 | 13146.9 | 12985.4 | 13096.2 | 13121.6 | 13037.5 | 13157.4 | 13202.6 | 13081.1 | 13088.7 | 13120.3 | 13223.8 | 13144.4 | 13137 | 12903.3 | 13009 | 12864.9 | 11290.1 | 12821.3 | 12826.8 | 13123.4 | 12957.6 | 12953.5 | 13167.9 | 13225.4 | 13239.4 | 13384.9 | 13278.8 | 13257.3 | 13079 | 13099.5 | 13057.7 | 13849.6 | 12756.2 | 13750.3 | 12545.9 | 13195.6 | 14190.2 | 12588.2 | 13852.3 | 13183 | 13380.6 | 13216.2 | 12531.2 | 13538.8 | 13400.5 | 13470.3 | 13146.3 | 12035.4 | 13638.9 | 12066.6 | 13615.1 | 13477.8 | 12043 | 13195.9 | 12592 | 12868 | 12077.8 | 12742.6 | 13264.3 | 13532.9 | 12295.8 | 13381.5 | 11819.4 | 13083.1 | 12845.2 | 12145.3 | 13363.9 | 11914.9 | 13625.7 | 12180.9 | 13413.3 | 12329.9 | 13239.9 | 12418.9 | 13562.4 | 12320.9 | 13076.5 | 12363.2 | 10887.1 | 13292.4 | 12912.5 | 11994.7 | 13664.8 | 13377.4 | 12510.9 | 12380.8 | 13446 | 12208.2 | 12680.4 | 13592.4 | 12141.6 | 13612.6 | 12130.1 | 13373.3 | 12402.4 | 13419 | 11752.7 | 13484.9 | 12301.4 | 13337.5 | 12240.9 | 13427.4 | 12483.9 | 12141.2 | 13312.5 | 12320.5 | 12063.8 | 13415.4 | 13472.8 | 13320.8 | 12306.9 | 13397.9 | 12142 | 12915.3 | 12005.9 | 12811.3 | 11212.9 | 13175.8 | 12146 | 12353.9 | 12422.8 | 12171.1 | 10552.2 | 12060.2 | 10671.1 | 12151.5 | 12184.9 | 13853.8 | 12483.3 | 13913.1 | 12747 | 13808.6 | 12560.6 | 12789.6 | 12489.2 | 13650 | 14079.5 | 13827.6 | 13772.8 | 13748 | 13788.6 | 12882.4 | 13842.1 | 13872 | 13875.2 | 13891.1 | 13834.5 | 13901 | 12814.9 | 13963.4 | 12881.9 | 38.8413 | 38.4217 | 38.4893 | 38.7268 | 38.576 | 38.7649 | 0 | 50.3 | 0 | 0 | 49.8 | 50.2 | 4.418 | 6.1236 | 5.9339 | 5.6514 | 6.0677 | 5.9773 | 9.385 | 11.3017 | 11.9317 | 10.6783 | 11.645 | 11.3433 | 8.0051 | 8.0387 | 8.1276 | 7.8455 | 7.7658 | 8.0477 | 2.0466 | 1.977 | 1.8638 | 2.2683 | 2.2388 | 1.888 | 0 | 7.7471 | 7.6174 | 0 | 7.4913 | 7.6726 | 0.678 | 0.75489 | 0.63468 | 0.65679 | 0.68309 | 0.70664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 963440 | 1789 | 950099 | 1817 | 218431.884 | 487 | 8.0051 | 8.0387 | 8.1276 | 7.8455 | 7.7658 | 8.0477 | 0 | 7.7471 | 7.6174 | 0 | 7.4913 | 7.6726 | 1026000 | 1000 | 1025000 | 1000 | 2057000 | 4133 | 2049000 | 2052867 | 13.25 | 7.9717 | 2.0471 | 7.6321 | 0.68568 | 25.68% | 8.984% | 38.6367 | 50.1 | 5.6953 | 11.0475 | 2070280 | 1979589.6755 | 2391201.0752 | 82.79% | 34 | 0
2025-06-09 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 335090.89 | 6:15 | 19:31 | 12498.2 | 13076.5 | 13119.7 | 13033.6 | 13248.3 | 13219.5 | 13284.6 | 13701.1 | 13164.1 | 13193.4 | 13009.4 | 13114.1 | 13159.1 | 13057.2 | 13191.9 | 13253.7 | 13119.5 | 13141.2 | 13158.1 | 13263.6 | 13180.1 | 13176.5 | 12936.3 | 13041.7 | 12896.6 | 11284.1 | 12856.9 | 12857.8 | 13152.3 | 12959.7 | 12986.2 | 13209.3 | 13224.7 | 13251.8 | 13402.1 | 13273.8 | 13293.3 | 13103.3 | 13125.7 | 13088.7 | 13989.4 | 12796.4 | 13849.8 | 12575.4 | 13250.1 | 14438.8 | 12598.1 | 14019.3 | 13243.5 | 13440.5 | 13264 | 12564.3 | 13622.4 | 13463.1 | 13530.2 | 13414.3 | 12040.6 | 13720 | 12081 | 13698.1 | 13564.1 | 12053.3 | 13233.2 | 12601.3 | 12901.3 | 12106.8 | 12791.5 | 13335.3 | 13632 | 12335.5 | 13467 | 11844.5 | 13139 | 12906 | 12174.6 | 13446.1 | 11933.7 | 13729.9 | 12203.3 | 13488.4 | 12368.6 | 13310.9 | 12482 | 13668.6 | 12372.2 | 13148.2 | 12386.9 | 10880.1 | 13375.4 | 12958.9 | 12015 | 13776.3 | 13423.8 | 12487.7 | 12351.2 | 13501.1 | 12187.2 | 12707.7 | 13680.8 | 12157.9 | 13696.1 | 12140.9 | 13422.7 | 12420.8 | 13485.7 | 11755.3 | 13565.1 | 12326.3 | 13383.6 | 12258.6 | 13489.2 | 12504.7 | 12164.4 | 13390.8 | 12344.5 | 12074.9 | 13475.8 | 13561.5 | 13391.2 | 12331.9 | 13490.1 | 12158 | 13227.9 | 12287.3 | 13047.1 | 11384.7 | 13218.7 | 12166.7 | 12324.5 | 12397.9 | 12168.5 | 10508 | 12108.2 | 10639.6 | 12176.8 | 12211.8 | 13993.5 | 12500.6 | 14050.1 | 12765.3 | 13935 | 12563.8 | 12800.8 | 12475 | 13687.6 | 14123.9 | 13938.3 | 13889.5 | 13875 | 13914.9 | 12899.1 | 13960.7 | 14005 | 14005 | 14022.3 | 13976.3 | 14018.7 | 12834.6 | 14078.8 | 12903.5 | 38.3246 | 37.8281 | 37.9367 | 38.0919 | 37.8969 | 38.2202 | 0 | 49.6 | 0 | 0 | 49.7 | 50.4458 | 4.1623 | 6.3041 | 6.0604 | 6.3732 | 6.4428 | 6.1971 | 8.5267 | 9.7233 | 9.5617 | 9.7117 | 9.1167 | 8.9883 | 7.9496 | 7.9723 | 8.0616 | 7.8007 | 7.6985 | 7.9741 | 2.0281 | 1.966 | 1.8464 | 2.2503 | 2.2228 | 1.8592 | 0 | 7.6825 | 7.5548 | 0 | 7.4068 | 7.6066 | 0.67566 | 0.75145 | 0.62996 | 0.65545 | 0.68118 | 0.70522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 964470 | 1791 | 951128 | 1819 | 220497.751 | 491.333 | 7.9496 | 7.9723 | 8.0616 | 7.8007 | 7.6985 | 7.9741 | 0 | 7.6825 | 7.5548 | 0 | 7.4068 | 7.6066 | 1030000 | 2000 | 1029000 | 2000 | 2065867 | 4333 | 2055000 | 2061534 | 13.2667 | 7.9095 | 2.0288 | 7.5627 | 0.68315 | 25.65% | 9.033% | 38.0497 | 49.9153 | 5.9233 | 9.2714 | 2078951.4 | 1954400 | 2376420.1236 | 82.24% | 29 | 0
2025-06-10 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 335090.89 | 6:15 | 19:31 | 12404.3 | 12985 | 13037.1 | 12946.2 | 13178.7 | 13137.9 | 13187.4 | 13657.1 | 13082.7 | 13113.2 | 12919.5 | 13030.1 | 13081.5 | 12968.5 | 13099.4 | 13175.4 | 13037.8 | 13067.6 | 13075.1 | 13178.2 | 13104 | 13092.2 | 12856.7 | 12959.9 | 12817.2 | 11192.5 | 12765.2 | 12770 | 13076 | 12878 | 12903 | 13141.4 | 13123.7 | 13155.3 | 13311.2 | 13172.2 | 13225.3 | 13034 | 13062.3 | 13021.1 | 13942 | 12700.3 | 13798.9 | 12481.3 | 13184.4 | 14404.3 | 12497.5 | 13978 | 13165.2 | 13359.8 | 13176.6 | 12458.7 | 13548.3 | 13375.7 | 13456.4 | 13346.9 | 11946.9 | 13645.3 | 11989.5 | 13622.9 | 13481.7 | 11959.3 | 13185.8 | 12551.7 | 12836.4 | 12013 | 12695.8 | 13261.9 | 13562 | 12241.8 | 13391.7 | 11752.9 | 13053.3 | 12812.6 | 12067.5 | 13361.7 | 11838.3 | 13649 | 12124.8 | 13421.5 | 12280.6 | 13233.1 | 12406 | 13620.8 | 12290.7 | 13092.8 | 12317.9 | 10809 | 13327.7 | 12891.2 | 11926.6 | 13734.1 | 13398.8 | 12467.8 | 12347.6 | 13496.3 | 12153.1 | 12623.4 | 13660.9 | 12066.1 | 13677.7 | 12055.2 | 13379.6 | 12349.1 | 13447.6 | 11684.9 | 13513.4 | 12241.3 | 13332.3 | 12176.5 | 13432.5 | 12427.5 | 12070.1 | 13328.2 | 12261.3 | 12001.6 | 13458.1 | 13514.8 | 13333.7 | 12219.2 | 13436.5 | 12064.6 | 13164.3 | 12209.4 | 13016.3 | 11311.1 | 13150.7 | 12075.7 | 12222.1 | 12277.9 | 12099.5 | 10417.7 | 12069.9 | 10657.6 | 12119.9 | 12161.8 | 13969 | 12417.4 | 14029.7 | 12685.5 | 13926.6 | 12521.6 | 12762.7 | 12419.8 | 13637.5 | 14078.6 | 13921.2 | 13859.8 | 13845.9 | 13893 | 12827.8 | 13939.8 | 13996.5 | 13993 | 14002.8 | 13968.3 | 14005.7 | 12772.3 | 14058.1 | 12849.5 | 37.523 | 37.145 | 37.3159 | 37.3375 | 36.8904 | 37.4924 | 0 | 49.8 | 0 | 0 | 49.1 | 49.6 | 2.4506 | 6.4399 | 6.2503 | 6.3182 | 6.2817 | 6.3926 | 8.0933 | 9.56 | 10.1433 | 9.84 | 9.11 | 9.6483 | 7.8733 | 7.9047 | 7.9834 | 7.8832 | 0.27103 | 7.9076 | 2.0042 | 1.9457 | 1.8293 | 2.2317 | 2.2038 | 1.8539 | 0 | 7.6043 | 7.4751 | 0 | 7.482 | 7.5312 | 0.66389 | 0.74419 | 0.62036 | 0.64588 | 0.67311 | 0.69807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 965495 | 1793 | 952154 | 1820 | 222553.217 | 495.533 | 7.8733 | 7.9047 | 7.9834 | 7.8832 | 0.27103 | 7.9076 | 0 | 7.6043 | 7.4751 | 0 | 7.482 | 7.5312 | 1025000 | 2000 | 1026000 | 1000 | 2055466 | 4200 | 2048000 | 2051266 | 13.2667 | 6.6372 | 2.0114 | 7.5232 | 0.67425 | 30.31% | 8.962% | 37.284 | 49.5 | 5.6889 | 9.3992 | 2068251.7 | 1934334 | 2351151.3168 | 82.27% | 28 | 0
2025-06-11 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 335090.89 | 6:14 | 19:33 | 12695.5 | 13276.3 | 13328.9 | 13264.7 | 13463 | 13443 | 13525.7 | 13926.4 | 13410.5 | 13437 | 13228.4 | 13333.1 | 13388.2 | 13262.1 | 13407.6 | 13470.5 | 13341.7 | 13365.1 | 13392.4 | 13497.5 | 13423.4 | 13411.9 | 13158 | 13266.4 | 13120.3 | 11464.2 | 13066.3 | 13073.7 | 13402 | 13225.6 | 13216.2 | 13449.9 | 12184.6 | 12207.3 | 12346.1 | 12231.7 | 12316.9 | 12148.4 | 12165.8 | 12106.8 | 14206.6 | 13012 | 14084.9 | 12789.9 | 13531.9 | 14648.9 | 12828.1 | 14229.4 | 13453.7 | 13653.9 | 13491.1 | 12769.5 | 13836.2 | 13689 | 13766 | 13663.9 | 12250.1 | 13957.7 | 12281.1 | 13914.6 | 13771.6 | 12246.9 | 13479.6 | 12854.6 | 13124.1 | 12305.8 | 12995.7 | 13568.9 | 13852.3 | 12536.2 | 13696.7 | 12025.2 | 13363.7 | 13109.4 | 12363.4 | 13657.4 | 12113.7 | 13931.4 | 12396.4 | 13699.8 | 12584.7 | 13541 | 12691.8 | 13928.1 | 12579.9 | 13396.3 | 12609.5 | 11074.5 | 13591.7 | 13194.7 | 12210.7 | 14013.2 | 13691.6 | 12736 | 12590.4 | 13783.1 | 12435.9 | 12933.4 | 13958.4 | 12347.7 | 13982.5 | 12348.8 | 13698.4 | 12633.6 | 13758.2 | 11952 | 13818.4 | 12531.8 | 13659 | 12461.7 | 13746.1 | 12726.5 | 12355.6 | 13620.2 | 12557.5 | 12279.7 | 13729.7 | 13799.5 | 13636.1 | 12528.7 | 13737.6 | 12350.2 | 13475.3 | 12512.8 | 13314.3 | 11566.3 | 13466.2 | 12358.1 | 12496.9 | 12541.8 | 12394 | 10647.9 | 12315 | 10880.9 | 12333.9 | 12389 | 14245.6 | 12699.5 | 14316.1 | 12981.8 | 14213.6 | 12819.9 | 13063.4 | 12701.1 | 13968.4 | 14398.5 | 14201.9 | 14139.6 | 14125.8 | 14169.2 | 13114.5 | 14217.5 | 14276.3 | 14271.3 | 14287.5 | 14241.5 | 14289.5 | 13054.5 | 14350.6 | 13131.4 | 0 | 0 | 36.8998 | 36.8703 | 36.4487 | 37.0494 | 0 | 0 | 0 | 0 | 49.8354 | 50.3 | 0 | 0 | 5.2529 | 5.354 | 5.3822 | 5.4137 | 0 | 0 | 9.32 | 8.5467 | 8.84 | 8.7467 | 0 | 0 | 8.2005 | 8.1101 | 8.0944 | 8.0944 | 0 | 0 | 1.89 | 2.3129 | 2.2727 | 1.9024 | 0 | 0 | 7.6653 | 0 | 7.6632 | 7.7591 | 0 | 0 | 0.63487 | 0.66424 | 0.68933 | 0.71261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 966533 | 1794 | 953202 | 1821 | 224644.484 | 499.667 | 0 | 0 | 8.2005 | 8.1101 | 8.0944 | 8.0944 | 0 | 0 | 7.6653 | 0 | 7.6632 | 7.7591 | 1038000 | 1000 | 1048000 | 1000 | 2091267 | 4134 | 2084000 | 2087133 | 13.3167 | 8.1249 | 2.0945 | 7.6959 | 0.67526 | 25.78% | 8.774% | 36.8171 | 50.0677 | 5.3507 | 8.8633 | 2105370.2 | 1977667 | 2422301.1537 | 81.64% | 22 | 0
2025-06-12 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 335090.89 | 6:15 | 19:32 | 12130 | 12547.7 | 12607.3 | 12577.8 | 12720.9 | 12721.5 | 12708.7 | 12997 | 12659 | 12663.2 | 12501.8 | 12577.4 | 12658.8 | 12522.6 | 12684.8 | 12723.3 | 12589.9 | 12618.2 | 12638.2 | 12751.1 | 12655.6 | 12678.6 | 12488.1 | 12562 | 12452.5 | 11163.5 | 12418.9 | 12411.2 | 12668.2 | 12544.1 | 12524.2 | 12679.1 | 13232.3 | 13252.5 | 13393.6 | 13269.2 | 12753.3 | 12615.8 | 12623.1 | 12575.3 | 13239.8 | 12386 | 13138.6 | 12215.3 | 12768.5 | 13623.3 | 12224.6 | 13248.1 | 12706.7 | 12871.8 | 12748.2 | 12216 | 13005.1 | 12886.4 | 12936.2 | 12857 | 11792.1 | 13083.9 | 11834.4 | 13062.2 | 12954.2 | 11791 | 12694.2 | 12229.7 | 12448.5 | 11822.4 | 12378.2 | 12778.4 | 12971.5 | 12005.9 | 12860.8 | 11615.4 | 12622 | 12457.8 | 11876.8 | 12842.4 | 11696.9 | 13050.7 | 11909.7 | 12885.1 | 12062.7 | 12766.6 | 12146.9 | 13042.7 | 12063.1 | 12674.6 | 12029.1 | 10832.2 | 12808.8 | 12490 | 11774.9 | 13106.6 | 12863.7 | 12181.6 | 12026.3 | 12882.5 | 11918.5 | 12338.8 | 13059.2 | 11861.3 | 13081 | 11883 | 12902.8 | 12116.9 | 12906.3 | 11560.5 | 12971.4 | 12015.6 | 12863.1 | 11961.9 | 12904.5 | 12189.6 | 11886 | 12836 | 12023.1 | 11831.3 | 12908.9 | 12954 | 12820.9 | 12030.3 | 12897.9 | 11880.2 | 12710.2 | 12013.2 | 12584.6 | 11259.4 | 12730.2 | 11910 | 12022.6 | 12059 | 11892.8 | 10477.8 | 11753 | 10640.7 | 11880 | 11923.5 | 13293.9 | 12159.2 | 13334.4 | 12385.2 | 13241.7 | 12236 | 12402 | 12171.5 | 13081.5 | 13368 | 13291.4 | 13225.9 | 13212.7 | 13238.4 | 12497.6 | 13269.8 | 13328.5 | 13316.9 | 13319.4 | 13294.9 | 13333.7 | 12454 | 13391.4 | 12516 | 0 | 0 | 37.3726 | 36.9669 | 36.7262 | 37.1708 | 0 | 0 | 52.0848 | 52.015 | 52.0848 | 53.4634 | 0 | 0 | 3.3518 | 3.4276 | 3.8595 | 3.8877 | 0 | 0 | 6.6633 | 7.1467 | 6.8733 | 6.7817 | 0 | 0 | 8.099 | 8.0095 | 7.9245 | 8.0597 | 0 | 0 | 1.8658 | 2.29 | 2.2518 | 1.9113 | 0 | 0 | 7.5659 | 0 | 7.5478 | 7.6806 | 0 | 0 | 0.62487 | 0.6538 | 0.66628 | 0.69625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 967527 | 1797 | 954196 | 1823 | 226638.951 | 503.8 | 0 | 0 | 8.099 | 8.0095 | 7.9245 | 8.0597 | 0 | 0 | 7.5659 | 0 | 7.5478 | 7.6806 | 994000 | 3000 | 994000 | 2000 | 1994467 | 4133 | 1983000 | 1990334 | 13.2833 | 8.0232 | 2.0797 | 7.5981 | 0.6603 | 25.92% | 8.69% | 37.0591 | 52.412 | 3.6317 | 6.8662 | 2005872.4 | 1943852.68 | 2327868.827 | 83.5% | 21 | 0
12768.348
Formulas:
Days = DAY(EOMONTH([Date],0))
Date = [Date, row above]+1
Note on GZ46: Author: Data Taken Fron RB1
Note on HF46: Author: Data Taken Fron RB1
Note on GZ47: Author: Data Taken Fron RB1
Note on HF47: Author: Data Taken Fron RB1
Note on GZ48: Author: Data Taken Fron RB1
Note on HF48: Author: Data Taken Fron RB1
Note on GZ50: Author: Data Taken Fron RB1
Note on HF50: Author: Data Taken Fron RB1
Note on GZ77: Author: Data Taken Fron RB1
Note on HF77: Author: Data Taken Fron RB1
Note on GZ78: Author: Data Taken Fron RB1
Note on HF78: Author: Data Taken Fron RB1
Note on GZ80: Author: Data Taken Fron RB1
Note on HF80: Author: Data Taken Fron RB1
Note on GZ81: Author: Data Taken Fron RB1
Note on HF81: Author: Data Taken Fron RB1
Note on GZ82: Author: Data Taken Fron RB1
Note on HF82: Author: Data Taken Fron RB1
Note on GZ84: Author: Data Taken Fron RB1
Note on HF84: Author: Data Taken Fron RB1
Note on GZ91: Author: Data Taken Fron RB1
Note on HF91: Author: Data Taken Fron RB1
Note on GZ93: Author: Data Taken Fron RB1
Note on HF93: Author: Data Taken Fron RB1
Note on GZ95: Author: Data Taken Fron RB1
Note on HF95: Author: Data Taken Fron RB1
Note on GZ96: Author: Data Taken Fron RB1
Note on HF96: Author: Data Taken Fron RB1
Note on GZ97: Author: Data Taken Fron RB1
Note on HF97: Author: Data Taken Fron RB1
Note on GZ98: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on HF98: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on GZ99: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on HF99: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on GZ100: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on HF100: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on GZ102: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on HF102: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on GZ103: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on HF103: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on GZ104: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on HF104: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on GZ105: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on HF105: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on GZ106: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on HF106: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on GZ108: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on HF108: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on GZ109: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on HF109: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on GZ110: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on HF110: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on GZ111: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on HF111: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on GZ112: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on HF112: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on GZ113: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on HF113: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on GZ114: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on HF114: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on GZ115: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on HF115: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on GZ118: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on HF118: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on GZ119: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on HF119: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on GZ120: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on HF120: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on GZ121: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on HF121: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on GZ122: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on HF122: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on GZ123: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on HF123: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on GZ124: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on HF124: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on GZ125: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on HF125: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on GZ126: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on HF126: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on GZ127: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on HF127: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on GZ128: all POA value taken from RB-1 data Logger
Note on HF128: all POA value taken from RB-1 data Logger
Note on GZ129: POA value taken from RB-1 data Logger
Note on HF129: POA value taken from RB-1 data Logger
Note on GZ130: POA value taken from RB-1 data Logger
Note on HF130: POA value taken from RB-1 data Logger
Note on GZ131: POA value taken from RB-1 data Logger
Note on HF131: POA value taken from RB-1 data Logger
Note on GZ132: POA value taken from RB-1 data Logger
Note on HF132: POA value taken from RB-1 data Logger
Note on GZ133: POA value taken from RB-1 data Logger
Note on HF133: POA value taken from RB-1 data Logger
Note on GZ134: POA value taken from RB-1 data Logger
Note on HF134: POA value taken from RB-1 data Logger
Note on GZ135: POA value taken from RB-1 data Logger
Note on HF135: POA value taken from RB-1 data Logger
Note on GZ136: POA value taken from RB-1 data Logger
Note on HF136: POA value taken from RB-1 data Logger
Note on GZ137: POA value taken from RB-1 data Logger
Note on HF137: POA value taken from RB-1 data Logger
Note on GZ138: POA value taken from RB-1 data Logger
Note on HF138: POA value taken from RB-1 data Logger
Note on GZ139: POA value taken from RB-1 data Logger
Note on HF139: POA value taken from RB-1 data Logger
Note on GZ140: POA value taken from RB-1 data Logger
Note on HF140: POA value taken from RB-1 data Logger
Note on GZ141: POA value taken from RB-1 data Logger
Note on HF141: POA value taken from RB-1 data Logger
Note on GZ142: POA value taken from RB-1 data Logger
Note on HF142: POA value taken from RB-1 data Logger
Note on GZ143: POA value taken from RB-1 data Logger
Note on HF143: POA value taken from RB-1 data Logger
Note on GZ144: POA value taken from RB-1 data Logger
Note on HF144: POA value taken from RB-1 data Logger
Note on GZ145: POA value taken from RB-1 data Logger
Note on HF145: POA value taken from RB-1 data Logger
Note on GZ146: POA value taken from RB-1 data Logger
Note on HF146: POA value taken from RB-1 data Logger
Note on GZ147: POA value taken from RB-1 data Logger
Note on HF147: POA value taken from RB-1 data Logger
Note on GZ148: POA value taken from RB-1 data Logger
Note on HF148: POA value taken from RB-1 data Logger
Note on GZ149: POA value taken from RB-1 data Logger
Note on HF149: POA value taken from RB-1 data Logger
Note on GZ150: POA value taken from RB-1 data Logger
Note on HF150: POA value taken from RB-1 data Logger
Note on GZ151: POA value taken from RB-1 data Logger
Note on HF151: POA value taken from RB-1 data Logger
Note on GZ152: POA value taken from RB-1 data Logger
Note on HF152: POA value taken from RB-1 data Logger
Note on GZ153: POA value taken from RB-1 data Logger
Note on HF153: POA value taken from RB-1 data Logger
Note on GZ154: POA value taken from RB-1 data Logger
Note on HF154: POA value taken from RB-1 data Logger
Note on GZ155: POA value taken from RB-1 data Logger
Note on HF155: POA value taken from RB-1 data Logger
Note on GZ156: POA value taken from RB-1 data Logger
Note on HF156: POA value taken from RB-1 data Logger
Note on GZ157: POA value taken from RB-1 data Logger
Note on HF157: POA value taken from RB-1 data Logger
Note on GZ158: Data logger Hanged reading taken from scada
Note on HC158: Data logger Hanged reading taken from scada
Note on HF158: Data logger Hanged reading taken from scada
Note on HI158: Data logger Hanged reading taken from scada
Note on GZ159: POA data taken from Plot-2 Scada
Note on HC159: Data logger Hanged reading taken from scada
Note on HF159: POA data taken from Plot-2 Scada
Note on HI159: Data logger Hanged reading taken from scada
Note on GZ160: POA data taken from Plot-2 Scada
Note on HF160: POA data taken from Plot-2 Scada
Note on GZ161: POA data taken from Plot-2 Scada
Note on HF161: POA data taken from Plot-2 Scada
Note on GZ162: POA data taken from Plot-2 Scada
Note on HF162: POA data taken from Plot-2 Scada
Note on GZ163: POA data taken from Plot-2 Scada
Note on HF163: POA data taken from Plot-2 Scada
Note on GZ164: POA data taken from Plot-2 Scada
Note on HF164: POA data taken from Plot-2 Scada
Note on GZ165: POA data taken from Plot-1
Note on HF165: POA data taken from Plot-1
Note on GZ166: POA data taken from Plot-2 Scada
Note on HF166: POA data taken from Plot-2 Scada
Note on GZ167: POA data taken from Plot-2 Scada
Note on HF167: POA data taken from Plot-2 Scada
Note on GZ168: Author: datat ccollect from Rb-2 Scada
Note on HF168: Author: datat ccollect from Rb-2 Scada
Note on GZ169: datat ccollect from Rb-2 Scada
Note on HF169: datat ccollect from Rb-2 Scada
Note on GZ170: datat ccollect from Rb-2 Scada
Note on HF170: datat ccollect from Rb-2 Scada
Note on GZ171: datat ccollect from Rb-2 Scada
Note on HF171: datat ccollect from Rb-2 Scada
Note on GZ172: datat ccollect from Rb-2 Scada
Note on HF172: datat ccollect from Rb-2 Scada
Note on GZ173: datat ccollect from Rb-2 Scada
Note on HF173: datat ccollect from Rb-2 Scada
Note on GZ174: datat ccollect from Rb-2 Scada
Note on HF174: datat ccollect from Rb-2 Scada
Note on GZ175: datat ccollect from Rb-2 Scada
Note on HF175: datat ccollect from Rb-2 Scada
Note on GZ176: Author: data collect from sacda plot-2
Note on HF176: Author: data collect from sacda plot-2
Note on GZ177: data collect from sacda plot-2
Note on HF177: data collect from sacda plot-2
Note on GZ178: Author: Data From scada Plot-2
Note on HF178: Author: Data From scada Plot-2
Note on GZ179: Data From scada Plot-2 data collect from Plot-2
Note on HF179: Data From scada Plot-2 data collect from Plot-2
Note on GZ180: data collect from Plot-2
Note on HF180: data collect from Plot-2
Note on GZ181: data collect from Plot-2
Note on HF181: data collect from Plot-2
Note on GZ182: data collect from Plot-2
Note on HF182: data collect from Plot-2
Note on GZ183: data collect from Plot-2
Note on HF183: data collect from Plot-2
Note on GZ184: data collect from Plot-2
Note on HF184: data collect from Plot-2
Note on GZ185: Author: data collect from Plot-2
Note on HF185: Author: data collect from Plot-2
Note on GZ186: data collect from Plot-2
Note on HF186: data collect from Plot-2
Note on GZ187: data collect from Plot-2
Note on HF187: data collect from Plot-2
Note on GZ188: data collect from Plot-2
Note on HF188: data collect from Plot-2
Note on GZ189: data collect from Plot-2
Note on HF189: data collect from Plot-2
Note on GZ190: data collect from Plot-2
Note on HF190: data collect from Plot-2
Note on GZ191: GTI value not show proper in SCADA. so we consider in DGR Plot-01 GTI value.
Note on HF191: GTI value not show proper in SCADA. so we consider in DGR Plot-01 GTI value.
Note on GZ192: Author: Data Collect From Scada pLOT-2
Note on HF192: Author: Data Collect From Scada pLOT-2
Note on GZ193: Data Collect From Scada pLOT-2
Note on HF193: Data Collect From Scada pLOT-2
Note on GZ194: Data Collect From Scada pLOT-2
Note on HF194: Data Collect From Scada pLOT-2
Note on GZ195: Data Collect From Scada pLOT-2
Note on HF195: Data Collect From Scada pLOT-2
Note on GZ196: Data Collect From Scada pLOT-2
Note on HF196: Data Collect From Scada pLOT-2
Note on GZ197: Data Collect From Scada pLOT-2
Note on HF197: Data Collect From Scada pLOT-2
Note on GZ198: Data Collect From Scada pLOT-2
Note on HF198: Data Collect From Scada pLOT-2
Note on GZ199: Data Collect From Scada pLOT-2
Note on HF199: Data Collect From Scada pLOT-2
Note on GZ200: Data Collect From Scada pLOT-2
Note on HF200: Data Collect From Scada pLOT-2
Note on GZ201: Data Collect From Scada pLOT-2
Note on HF201: Data Collect From Scada pLOT-2
Note on GZ202: Data Collect From Scada pLOT-2
Note on HF202: Data Collect From Scada pLOT-2
Note on GZ203: Data Collect From Scada pLOT-2
Note on HF203: Data Collect From Scada pLOT-2
Note on GZ204: Data Collect From Scada pLOT-2
Note on HF204: Data Collect From Scada pLOT-2
Note on GZ205: Data Collect From Scada pLOT-2
Note on HF205: Data Collect From Scada pLOT-2
Note on GZ206: Data Collect From Scada pLOT-2
Note on HF206: Data Collect From Scada pLOT-2
Note on GZ207: Data Collect From Scada pLOT-2
Note on HF207: Data Collect From Scada pLOT-2
Note on GZ208: Data Collect From Scada pLOT-2
Note on HF208: Data Collect From Scada pLOT-2
Note on GZ209: Data Collect From Scada pLOT-2
Note on HF209: Data Collect From Scada pLOT-2
Note on GZ210: Data Collect From Scada pLOT-2
Note on HF210: Data Collect From Scada pLOT-2
Note on GZ212: Author: Plot-2 Scada GTI value
Note on HF212: Author: Plot-2 Scada GTI value
Note on GZ213: Author: collect datta from scada Plot-2
Note on HF213: Author: collect datta from scada Plot-2
Note on GZ214: Author: data collect from scada Plot-2
Note on HF214: Author: data collect from scada Plot-2
Note on GZ215: Author: data collect from scada plot-2
Note on HF215: Author: data collect from scada plot-2
Note on GZ216: Author: scada Datat Colllect From Plot-2
Note on HF216: Author: scada Datat Colllect From Plot-2
Note on GZ217: Author: data Collect From scada Plot-2
Note on HF217: Author: data Collect From scada Plot-2
Note on GZ218: Author: data collect from Scada Plot-2
Note on HF218: Author: data collect from Scada Plot-2
Note on GZ219: Author: Scada Data -Plot-2
Note on HF219: Author: Scada Data -Plot-2
Note on GZ225: Author: gti value from plot1
Note on HF225: Author: gti value from plot1
Note on GZ233: Author: gti value from plot1
Note on HF233: Author: gti value from plot1
Note on GZ234: Author: GTI Value Consider From Plot-1
Note on HF234: Author: GTI Value Consider From Plot-1
Note on HC251: Author: GTI-Plot-1
Note on HI251: Author: GTI-Plot-1
Note on HC252: Author: GTI-Plot-1
Note on HI252: Author: GTI-Plot-1
Note on HC253: Author: GTI-Plot-1
Note on HI253: Author: GTI-Plot-1
Note on HC254: Author: GTI-Plot-1
Note on HI254: Author: GTI-Plot-1
Note on HC255: Author: GTI-Plot-1
Note on HI255: Author: GTI-Plot-1
Note on HC256: Author: GTI-Plot-1
Note on HI256: Author: GTI-Plot-1
Note on HC257: Author: GTI-Plot-1
Note on HI257: Author: GTI-Plot-1
Note on HC258: Author: GTI-Plot-1
Note on HI258: Author: GTI-Plot-1
Note on HC259: Author: GTI-Plot-1
Note on HI259: Author: GTI-Plot-1
Note on HC260: Author: GTI-Plot-1
Note on HI260: Author: GTI-Plot-1
Note on HC261: Author: GTI-Plot-1
Note on HI261: Author: GTI-Plot-1
Note on HC262: Author: GTI-Plot-1
Note on HI262: Author: GTI-Plot-1
Note on HC263: Author: GTI-Plot-1
Note on HI263: Author: GTI-Plot-1
Note on HC264: Author: GTI-Plot-1
Note on HI264: Author: GTI-Plot-1
Note on HC265: Author: GTI-Plot-1
Note on HI265: Author: GTI-Plot-1
Note on HC266: Author: GTI-Plot-1
Note on HI266: Author: GTI-Plot-1
Note on HC267: Author: GTI-Plot-1
Note on HI267: Author: GTI-Plot-1
Note on HC268: Author: GTI-Plot-1
Note on HI268: Author: GTI-Plot-1
Note on HC269: Author: GTI-Plot-1
Note on HI269: Author: GTI-Plot-1
Note on HC270: Author: GTI-Plot-1
Note on HI270: Author: GTI-Plot-1
Note on HC271: Author: GTI-Plot-1
Note on HI271: Author: GTI-Plot-1
Note on HC272: Author: GTI-Plot-1
Note on HI272: Author: GTI-Plot-1
Note on HC273: Author: GTI-Plot-1
Note on HI273: Author: GTI-Plot-1
Note on HC274: Author: GTI-Plot-1
Note on HI274: Author: GTI-Plot-1
Note on HC275: Author: GTI-Plot-1
Note on HI275: Author: GTI-Plot-1
Note on HC276: Author: GTI-Plot-1
Note on HI276: Author: GTI-Plot-1
Note on HC277: Author: GTI-Plot-1
Note on HI277: Author: GTI-Plot-1
Note on HC278: Author: GTI-Plot-1
Note on HI278: Author: GTI-Plot-1
Note on GZ279: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HC279: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF279: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HI279: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ280: Author:
Note on HC280: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF280: Author:
Note on HI280: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ281: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HC281: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF281: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HI281: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ282: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HC282: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF282: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HI282: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ283: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HC283: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF283: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HI283: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ284: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HC284: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF284: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HI284: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ285: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HC285: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF285: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HI285: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ286: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HC286: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF286: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HI286: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ287: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HC287: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF287: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HI287: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ288: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HC288: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF288: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HI288: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ289: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HC289: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF289: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HI289: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ290: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HC290: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF290: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HI290: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ291: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HC291: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF291: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HI291: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ292: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HC292: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF292: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HI292: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ293: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HC293: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF293: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HI293: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ294: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HF294: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on GZ295: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HC295: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF295: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HI295: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ296: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HC296: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF296: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HI296: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ297: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HC297: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF297: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HI297: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ298: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HC298: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF298: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HI298: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ299: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HC299: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF299: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HI299: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ300: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HC300: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF300: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HI300: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ301: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HC301: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF301: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HI301: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ302: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HC302: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF302: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HI302: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ303: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HC303: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF303: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on HI303: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HC304: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HI304: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HC305: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HI305: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HC306: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HI306: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HC307: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HI307: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HC308: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HI308: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ310: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HC310: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF310: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HI310: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ311: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HC311: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF311: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HI311: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ312: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HC312: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF312: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HI312: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ313: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HC313: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF313: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HI313: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ314: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HC314: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF314: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HI314: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ315: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HC315: Plot-1 Data Logger Hanged.GTI Reading Taken From Plot-1 Scada Pc
Note on HF315: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HI315: Plot-1 Data Logger Hanged.GTI Reading Taken From Plot-1 Scada Pc
Note on GZ316: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HC316: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF316: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HI316: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ317: Author: Pyranometer Table Tilt In 5 degree
Note on HC317: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF317: Author: Pyranometer Table Tilt In 5 degree
Note on HI317: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ318: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HC318: Plot-1 Data Logger Hanged.GTI Reading Taken From Plot 2 (Avg-Pyranometer-1&2)
Note on HF318: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HI318: Plot-1 Data Logger Hanged.GTI Reading Taken From Plot 2 (Avg-Pyranometer-1&2)
Note on GZ319: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HC319: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF319: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HI319: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ320: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HC320: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF320: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HI320: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ321: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HC321: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF321: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HI321: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ322: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HC322: Plot-1 Data Logger Hanged.GTI Reading Taken From Plot-1 Scada Pc
Note on HF322: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HI322: Plot-1 Data Logger Hanged.GTI Reading Taken From Plot-1 Scada Pc
Note on GZ323: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HC323: Plot-1 Data Logger Hanged.GTI Reading Taken From Plot-1 Scada Pc
Note on HF323: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HI323: Plot-1 Data Logger Hanged.GTI Reading Taken From Plot-1 Scada Pc
Note on GZ324: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HC324: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF324: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HI324: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ325: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HC325: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF325: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HI325: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ326: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HC326: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF326: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HI326: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ327: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HC327: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF327: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HI327: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ328: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HC328: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF328: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HI328: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ329: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HC329: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF329: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HI329: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ330: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HC330: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF330: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HI330: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ331: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HC331: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF331: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HI331: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ332: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HC332: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF332: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HI332: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ333: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HC333: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF333: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HI333: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ334: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HC334: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF334: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HI334: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ335: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HC335: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF335: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on HI335: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ336: Author: GTI:- PLOT2 Avr.(Pyranometer 1&2 )
Note on HC336: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on HF336: Author: GTI:- PLOT2 Avr.(Pyranometer 1&2 )
Note on HI336: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on GZ337: Author: GTI:- PLOT2 Avg (Pranometer 1&2 )
Note on HC337: Author: GTI:- Plot 1 Avg Pyranometer 1 &2
Note on HF337: Author: GTI:- PLOT2 Avg (Pranometer 1&2 )
Note on HI337: Author: GTI:- Plot 1 Avg Pyranometer 1 &2
Note on GZ338: Author: GTI :-PLOT2 (Avg Pyranomeetr 1 &2 )
Note on HC338: Author: GTI :PLOT 1 Avr Pyranometer 1&2
Note on HF338: Author: GTI :-PLOT2 (Avg Pyranomeetr 1 &2 )
Note on HI338: Author: GTI :PLOT 1 Avr Pyranometer 1&2
Note on GZ339: Author: GTI:-PLOT2 avg. Pyranometer 1&2
Note on HC339: Author: GTI :-Plot1 Avg. Pyranometer 1&2
Note on HF339: Author: GTI:-PLOT2 avg. Pyranometer 1&2
Note on HI339: Author: GTI :-Plot1 Avg. Pyranometer 1&2

## PA
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37
Sr. No. | Date | Financial Year | Calendar Year | Contractual Year | Operating Year | Month Year | Days | Sunrise Time (POA>20 W/m2) | Sunset Time (POA<20 W/m2) | Total Generation Time | Inverter Station Number (if Bd in filed) | Inverter number (If Inv, SCb or Str BD) | Inverter Module Number | SCB Number (If SCB or Str BD) | String Type(If String BD) | Equipment (If any BD other than PV array and inv) | C1 | C2 | Affected Equipment | DC Capacity Affected (kW) | Plant Equivalent Weightage | Fault Category | Fault Code (As per HMI) | Breakdown Description | Fault Time | Acknowledgement Time | Work Start time on Fault | Work Completion time on fault | Acknow. time | Response Time | Resolution Time | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Lost PoA(Wh/m2) | Approximate Energy Loss (KWh) | Job Card/PTW Nos.
1 | 2023-04-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:36 | 18:59 | 12.3833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:36 | NA | NA | 18:59 |  |  |  | 12.3833 |  | Open | 0.00095381 |  | 0
2 | 2023-04-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:36 | 18:59 | 12.3833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:36 | NA | NA | 18:59 |  |  |  | 12.3833 |  | Open | 0.00095381 |  | 0
3 | 2023-04-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:36 | 18:59 | 12.3833 | IS20 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:36 | NA | NA | 18:59 |  |  |  | 12.3833 |  | Open | 0.0011574 |  | 0
4 | 2023-04-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:36 | 18:59 | 12.3833 | IS20 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:36 | NA | NA | 18:59 |  |  |  | 12.3833 |  | Open | 0.0011574 |  | 0
5 | 2023-04-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:36 | 18:59 | 12.3833 | IS18 | INV4 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:36 | NA | NA | 18:59 |  |  |  | 12.3833 |  | Open | 0.0011574 |  | 0
6 | 2023-04-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:36 | 18:59 | 12.3833 | IS18 | INV4 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:36 | NA | NA | 18:59 |  |  |  | 12.3833 |  | Open | 0.0011574 |  | 0
7 | 2023-04-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:36 | 18:59 | 12.3833 | IS19 | INV2 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:36 | NA | NA | 18:59 |  |  |  | 12.3833 |  | Open | 0.0011574 |  | 0
8 | 2023-04-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:36 | 18:59 | 12.3833 | IS20 | INV2 | M2 | SCB8 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:36 | NA | NA | 18:59 |  |  |  | 12.3833 |  | Open | 0.00095381 |  | 0
9 | 2023-04-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:36 | 18:59 | 12.3833 | IS20 | INV2 | M2 | SCB2 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:36 | NA | NA | 18:59 |  |  |  | 12.3833 |  | Open | 0.00095381 |  | 0
10 | 2023-04-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:36 | 18:59 | 12.3833 | IS20 | INV2 | M1 | SCB6 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:36 | NA | NA | 18:59 |  |  |  | 12.3833 |  | Open | 0.00095381 |  | 0
11 | 2023-04-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:36 | 18:59 | 12.3833 | IS20 | INV2 | M1 | SCB3 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:36 | NA | NA | 18:59 |  |  |  | 12.3833 |  | Open | 0.00095381 |  | 0
12 | 2023-04-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:36 | 18:59 | 12.3833 | IS20 | INV2 | M2 | SCB1 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:36 | NA | NA | 18:59 |  |  |  | 12.3833 |  | Open | 0.00095381 |  | 0
13 | 2023-04-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:36 | 18:59 | 12.3833 | IS20 | INV2 | M2 | SCB8 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:36 | NA | NA | 18:59 |  |  |  | 12.3833 |  | Open | 0.00095381 |  | 0
14 | 2023-04-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:36 | 18:59 | 12.3833 | IS20 | INV3 | M2 | SCB2 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:36 | NA | NA | 18:59 |  |  |  | 12.3833 |  | Open | 0.00095381 |  | 0
15 | 2023-04-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:36 | 18:59 | 12.3833 | IS20 | INV4 | M2 | SCB6 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:36 | NA | NA | 18:59 |  |  |  | 12.3833 |  | Open | 0.00095381 |  | 0
16 | 2023-04-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:36 | 18:59 | 12.3833 | IS20 | INV2 | M1 | SCB2 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:36 | NA | NA | 18:59 |  |  |  | 12.3833 |  | Open | 0.00095381 |  | 0
17 | 2023-04-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:36 | 18:59 | 12.3833 | IS20 | INV2 | M1 | SCB2 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:36 | NA | NA | 18:59 |  |  |  | 12.3833 |  | Open | 0.00095381 |  | 0
18 | 2023-04-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:36 | 18:59 | 12.3833 | IS19 | INV4 | M1 | SCB9 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:36 | NA | NA | 18:59 |  |  |  | 12.3833 |  | Open | 0.00095381 |  | 0
19 | 2023-04-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:36 | 18:59 | 12.3833 | IS2 | INV3 | M2 | SCB8 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:36 | NA | NA | 18:59 |  |  |  | 12.3833 |  | Open | 0.00095381 |  | 0
20 | 2023-04-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:36 | 18:59 | 12.3833 | IS2 | INV3 | M2 | SCB8 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:36 | NA | NA | 18:59 |  |  |  | 12.3833 |  | Open | 0.00095381 |  | 0
21 | 2023-04-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:36 | 18:59 | 12.3833 | IS2 | INV4 | M1 | SCB9 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:36 | NA | NA | 18:59 |  |  |  | 12.3833 |  | Open | 0.00095381 |  | 0
22 | 2023-04-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:36 | 18:59 | 12.3833 | IS2 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:36 | NA | NA | 18:59 |  |  |  | 12.3833 |  | Open | 0.00095381 |  | 0
23 | 2023-04-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:36 | 18:59 | 12.3833 | IS9 | INV3 | M1 | SCB6 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:36 | NA | NA | 18:59 |  |  |  | 12.3833 |  | Open | 0.00095381 |  | 0
24 | 2023-04-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:33 | 19:00 | 12.45 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:33 | NA | NA | 19:00 |  |  |  | 12.45 |  | Open | 0.00095895 |  | 0
25 | 2023-04-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:33 | 19:00 | 12.45 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:33 | NA | NA | 19:00 |  |  |  | 12.45 |  | Open | 0.00095895 |  | 0
26 | 2023-04-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:33 | 19:00 | 12.45 | IS20 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:33 | NA | NA | 19:00 |  |  |  | 12.45 |  | Open | 0.0011637 |  | 0
27 | 2023-04-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:33 | 19:00 | 12.45 | IS20 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:33 | NA | NA | 19:00 |  |  |  | 12.45 |  | Open | 0.0011637 |  | 0
28 | 2023-04-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:33 | 19:00 | 12.45 | IS18 | INV4 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:33 | NA | NA | 19:00 |  |  |  | 12.45 |  | Open | 0.0011637 |  | 0
29 | 2023-04-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:33 | 19:00 | 12.45 | IS18 | INV4 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:33 | NA | NA | 19:00 |  |  |  | 12.45 |  | Open | 0.0011637 |  | 0
30 | 2023-04-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:33 | 19:00 | 12.45 | IS19 | INV2 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:33 | NA | NA | 19:00 |  |  |  | 12.45 |  | Open | 0.0011637 |  | 0
31 | 2023-04-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:33 | 19:00 | 12.45 | IS20 | INV2 | M2 | SCB8 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:33 | NA | NA | 19:00 |  |  |  | 12.45 |  | Open | 0.00095895 |  | 0
32 | 2023-04-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:33 | 19:00 | 12.45 | IS20 | INV2 | M2 | SCB3 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:33 | NA | NA | 19:00 |  |  |  | 12.45 |  | Open | 0.00095895 |  | 0
33 | 2023-04-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:33 | 19:00 | 12.45 | IS20 | INV2 | M1 | SCB6 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:33 | NA | NA | 19:00 |  |  |  | 12.45 |  | Open | 0.00095895 |  | 0
34 | 2023-04-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:33 | 19:00 | 12.45 | IS20 | INV2 | M1 | SCB3 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:33 | NA | NA | 19:00 |  |  |  | 12.45 |  | Open | 0.00095895 |  | 0
35 | 2023-04-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:33 | 19:00 | 12.45 | IS20 | INV2 | M2 | SCB2 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:33 | NA | NA | 19:00 |  |  |  | 12.45 |  | Open | 0.00095895 |  | 0
36 | 2023-04-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:33 | 19:00 | 12.45 | IS20 | INV2 | M2 | SCB9 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:33 | NA | NA | 19:00 |  |  |  | 12.45 |  | Open | 0.00095895 |  | 0
37 | 2023-04-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:33 | 19:00 | 12.45 | IS20 | INV3 | M2 | SCB2 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:33 | NA | NA | 19:00 |  |  |  | 12.45 |  | Open | 0.00095895 |  | 0
38 | 2023-04-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:33 | 19:00 | 12.45 | IS20 | INV4 | M2 | SCB2 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:33 | NA | NA | 19:00 |  |  |  | 12.45 |  | Open | 0.00095895 |  | 0
39 | 2023-04-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:33 | 19:00 | 12.45 | IS20 | INV2 | M1 | SCB2 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:33 | NA | NA | 19:00 |  |  |  | 12.45 |  | Open | 0.00095895 |  | 0
40 | 2023-04-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:33 | 19:00 | 12.45 | IS20 | INV2 | M1 | SCB2 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:33 | NA | NA | 19:00 |  |  |  | 12.45 |  | Open | 0.00095895 |  | 0
41 | 2023-04-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:33 | 19:00 | 12.45 | IS19 | INV4 | M1 | SCB9 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:33 | NA | NA | 19:00 |  |  |  | 12.45 |  | Open | 0.00095895 |  | 0
42 | 2023-04-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:33 | 19:00 | 12.45 | IS2 | INV3 | M2 | SCB7 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:33 | NA | NA | 19:00 |  |  |  | 12.45 |  | Open | 0.00095895 |  | 0
43 | 2023-04-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:33 | 19:00 | 12.45 | IS2 | INV3 | M2 | SCB7 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:33 | NA | NA | 19:00 |  |  |  | 12.45 |  | Open | 0.00095895 |  | 0
44 | 2023-04-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:33 | 19:00 | 12.45 | IS2 | INV4 | M1 | SCB9 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:33 | NA | NA | 19:00 |  |  |  | 12.45 |  | Open | 0.00095895 |  | 0
45 | 2023-04-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:33 | 19:00 | 12.45 | IS2 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:33 | NA | NA | 19:00 |  |  |  | 12.45 |  | Open | 0.00095895 |  | 0
46 | 2023-04-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:33 | 19:00 | 12.45 | IS9 | INV3 | M1 | SCB6 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:33 | NA | NA | 19:00 |  |  |  | 12.45 |  | Open | 0.00095895 |  | 0
47 | 2023-04-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:34 | 19:01 | 12.45 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:34 | NA | NA | 19:01 |  |  |  | 12.45 |  | Open | 0.00095895 |  | 0
48 | 2023-04-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:34 | 19:01 | 12.45 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:34 | NA | NA | 19:01 |  |  |  | 12.45 |  | Open | 0.00095895 |  | 0
49 | 2023-04-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:34 | 19:01 | 12.45 | IS20 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:34 | NA | NA | 19:01 |  |  |  | 12.45 |  | Open | 0.0011637 |  | 0
50 | 2023-04-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:34 | 19:01 | 12.45 | IS20 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:34 | NA | NA | 19:01 |  |  |  | 12.45 |  | Open | 0.0011637 |  | 0
51 | 2023-04-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:34 | 19:01 | 12.45 | IS18 | INV4 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:34 | NA | NA | 19:01 |  |  |  | 12.45 |  | Open | 0.0011637 |  | 0
52 | 2023-04-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:34 | 19:01 | 12.45 | IS18 | INV4 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:34 | NA | NA | 19:01 |  |  |  | 12.45 |  | Open | 0.0011637 |  | 0
53 | 2023-04-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:34 | 19:01 | 12.45 | IS19 | INV2 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:34 | NA | NA | 19:01 |  |  |  | 12.45 |  | Open | 0.0011637 |  | 0
54 | 2023-04-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:34 | 19:01 | 12.45 | IS20 | INV2 | M2 | SCB2 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:34 | NA | NA | 19:01 |  |  |  | 12.45 |  | Open | 0.00095895 |  | 0
55 | 2023-04-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:34 | 19:01 | 12.45 | IS20 | INV2 | M1 | SCB6 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:34 | NA | NA | 19:01 |  |  |  | 12.45 |  | Open | 0.00095895 |  | 0
56 | 2023-04-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:34 | 19:01 | 12.45 | IS20 | INV2 | M1 | SCB3 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:34 | NA | NA | 19:01 |  |  |  | 12.45 |  | Open | 0.00095895 |  | 0
57 | 2023-04-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:34 | 19:01 | 12.45 | IS20 | INV2 | M2 | SCB1 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:34 | NA | NA | 19:01 |  |  |  | 12.45 |  | Open | 0.00095895 |  | 0
58 | 2023-04-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:34 | 19:01 | 12.45 | IS20 | INV2 | M2 | SCB8 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:34 | NA | NA | 19:01 |  |  |  | 12.45 |  | Open | 0.00095895 |  | 0
59 | 2023-04-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:34 | 19:01 | 12.45 | IS20 | INV3 | M2 | SCB1 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:34 | NA | NA | 19:01 |  |  |  | 12.45 |  | Open | 0.00095895 |  | 0
60 | 2023-04-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:34 | 19:01 | 12.45 | IS20 | INV4 | M2 | SCB6 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:34 | NA | NA | 19:01 |  |  |  | 12.45 |  | Open | 0.00095895 |  | 0
61 | 2023-04-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:34 | 19:01 | 12.45 | IS20 | INV2 | M1 | SCB2 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:34 | NA | NA | 19:01 |  |  |  | 12.45 |  | Open | 0.00095895 |  | 0
62 | 2023-04-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:34 | 19:01 | 12.45 | IS20 | INV2 | M1 | SCB2 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:34 | NA | NA | 19:01 |  |  |  | 12.45 |  | Open | 0.00095895 |  | 0
63 | 2023-04-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:34 | 19:01 | 12.45 | IS2 | INV3 | M2 | SCB10 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:34 | NA | NA | 19:01 |  |  |  | 12.45 |  | Open | 0.00095895 |  | 0
64 | 2023-04-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:34 | 19:01 | 12.45 | IS2 | INV3 | M2 | SCB10 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:34 | NA | NA | 19:01 |  |  |  | 12.45 |  | Open | 0.00095895 |  | 0
65 | 2023-04-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:34 | 19:01 | 12.45 | IS2 | INV4 | M1 | SCB9 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:34 | NA | NA | 19:01 |  |  |  | 12.45 |  | Open | 0.00095895 |  | 0
66 | 2023-04-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:34 | 19:01 | 12.45 | IS2 | INV4 | M2 | SCB7 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:34 | NA | NA | 19:01 |  |  |  | 12.45 |  | Open | 0.00095895 |  | 0
67 | 2023-04-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:34 | 19:01 | 12.45 | IS6 |  |  |  |  | Tx | 0 | 1 | IS6Tx | 17170.9 | 5.124% | IDT | Tx_Manual Tripped for Bushing Replacement | IDT-6 Manual stop for LV side damaged bushing replacement | 17:34 | 17:34 | 17:35 | 19:01 | 0 | 0.016667 | 1.45 | 1.45 | IDT Charged after bushing change | Close | 0.074302 |  | 0 | JC74597
68 | 2023-04-04 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:32 | 18:55 | 12.3833 | IS13 |  |  |  |  | Tx | 0 | 1 | IS13Tx | 16599.6 | 4.954% | IDT | Tx_Manual Tripped for Bushing Replacement | IDT-13 Manual stop for LV side damaged bushing replacement | 18:19 | 18:19 | 18:20 | 18:54 | 0 | 0.016667 | 0.58333 | 0.58333 | IDT Charged after bushing change | Close | 0.028897 |  | 0 | JC74616
69 | 2023-04-04 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:32 | 18:55 | 12.3833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:34 | NA | NA | 18:54 |  |  |  | 12.3333 |  | Open | 0.00094996 |  | 0
70 | 2023-04-04 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:32 | 18:55 | 12.3833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:34 | NA | NA | 18:54 |  |  |  | 12.3333 |  | Open | 0.00094996 |  | 0
71 | 2023-04-04 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:32 | 18:55 | 12.3833 | IS20 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:34 | NA | NA | 18:54 |  |  |  | 12.3333 |  | Open | 0.0011528 |  | 0
72 | 2023-04-04 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:32 | 18:55 | 12.3833 | IS20 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:34 | NA | NA | 18:54 |  |  |  | 12.3333 |  | Open | 0.0011528 |  | 0
73 | 2023-04-04 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:32 | 18:55 | 12.3833 | IS18 | INV4 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:34 | NA | NA | 18:54 |  |  |  | 12.3333 |  | Open | 0.0011528 |  | 0
74 | 2023-04-04 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:32 | 18:55 | 12.3833 | IS18 | INV4 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:34 | NA | NA | 18:54 |  |  |  | 12.3333 |  | Open | 0.0011528 |  | 0
75 | 2023-04-04 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:32 | 18:55 | 12.3833 | IS19 | INV2 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:34 | NA | NA | 18:54 |  |  |  | 12.3333 |  | Open | 0.0011528 |  | 0
76 | 2023-04-04 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:32 | 18:55 | 12.3833 | IS20 | INV2 | M2 | SCB2 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:34 | NA | NA | 18:54 |  |  |  | 12.3333 |  | Open | 0.0011528 |  | 0
77 | 2023-04-04 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:32 | 18:55 | 12.3833 | IS20 | INV2 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:34 | NA | NA | 18:54 |  |  |  | 12.3333 |  | Open | 0.0011528 |  | 0
78 | 2023-04-04 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:32 | 18:55 | 12.3833 | IS20 | INV2 | M1 | SCB3 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:34 | NA | NA | 18:54 |  |  |  | 12.3333 |  | Open | 0.0011528 |  | 0
79 | 2023-04-04 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:32 | 18:55 | 12.3833 | IS20 | INV2 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:34 | NA | NA | 18:54 |  |  |  | 12.3333 |  | Open | 0.00094996 |  | 0
80 | 2023-04-04 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:32 | 18:55 | 12.3833 | IS20 | INV2 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:34 | NA | NA | 18:54 |  |  |  | 12.3333 |  | Open | 0.00094996 |  | 0
81 | 2023-04-04 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:32 | 18:55 | 12.3833 | IS20 | INV3 | M2 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:34 | NA | NA | 18:54 |  |  |  | 12.3333 |  | Open | 0.0011528 |  | 0
82 | 2023-04-04 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:32 | 18:55 | 12.3833 | IS20 | INV4 | M2 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:34 | NA | NA | 18:54 |  |  |  | 12.3333 |  | Open | 0.0011528 |  | 0
83 | 2023-04-04 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:32 | 18:55 | 12.3833 | IS20 | INV2 | M1 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:34 | NA | NA | 18:54 |  |  |  | 12.3333 |  | Open | 0.0011528 |  | 0
84 | 2023-04-04 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:32 | 18:55 | 12.3833 | IS20 | INV2 | M1 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:34 | NA | NA | 18:54 |  |  |  | 12.3333 |  | Open | 0.0011528 |  | 0
85 | 2023-04-04 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:32 | 18:55 | 12.3833 | IS2 | INV3 | M2 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:34 | NA | NA | 18:54 |  |  |  | 12.3333 |  | Open | 0.0011528 |  | 0
86 | 2023-04-04 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:32 | 18:55 | 12.3833 | IS2 | INV3 | M2 | SCB8 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:34 | NA | NA | 18:54 |  |  |  | 12.3333 |  | Open | 0.0011528 |  | 0
87 | 2023-04-04 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:32 | 18:55 | 12.3833 | IS2 | INV4 | M1 | SCB9 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:34 | NA | NA | 18:54 |  |  |  | 12.3333 |  | Open | 0.0011528 |  | 0
88 | 2023-04-04 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:32 | 18:55 | 12.3833 | IS2 | INV4 | M2 | SCB4 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:34 | NA | NA | 18:54 |  |  |  | 12.3333 |  | Open | 0.0011528 |  | 0
89 | 2023-04-05 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:33 | 18:57 | 12.4 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:33 | NA | NA | 18:57 |  |  |  | 12.4 |  | Open | 0.0009551 |  | 0
90 | 2023-04-05 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:33 | 18:57 | 12.4 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:33 | NA | NA | 18:57 |  |  |  | 12.4 |  | Open | 0.0009551 |  | 0
91 | 2023-04-05 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:33 | 18:57 | 12.4 | IS20 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:33 | NA | NA | 18:57 |  |  |  | 12.4 |  | Open | 0.001159 |  | 0
92 | 2023-04-05 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:33 | 18:57 | 12.4 | IS20 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:33 | NA | NA | 18:57 |  |  |  | 12.4 |  | Open | 0.001159 |  | 0
93 | 2023-04-05 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:33 | 18:57 | 12.4 | IS18 | INV4 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:33 | NA | NA | 18:57 |  |  |  | 12.4 |  | Open | 0.001159 |  | 0
94 | 2023-04-05 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:33 | 18:57 | 12.4 | IS18 | INV4 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:33 | NA | NA | 18:57 |  |  |  | 12.4 |  | Open | 0.001159 |  | 0
95 | 2023-04-05 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:33 | 18:57 | 12.4 | IS19 | INV2 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:33 | NA | NA | 18:57 |  |  |  | 12.4 |  | Open | 0.001159 |  | 0
96 | 2023-04-05 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:33 | 18:57 | 12.4 | IS2 | INV3 | M2 | SCB7 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:33 | NA | NA | 18:57 |  |  |  | 12.4 |  | Open | 0.00047755 |  | 0
97 | 2023-04-05 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:33 | 18:57 | 12.4 | IS2 | INV3 | M2 | SCB7 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:33 | NA | NA | 18:57 |  |  |  | 12.4 |  | Open | 0.00047755 |  | 0
98 | 2023-04-05 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:33 | 18:57 | 12.4 | IS2 | INV4 | M1 | SCB9 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:33 | NA | NA | 18:57 |  |  |  | 12.4 |  | Open | 0.00047755 |  | 0
99 | 2023-04-05 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:33 | 18:57 | 12.4 | IS2 | INV4 | M2 | SCB4 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:33 | NA | NA | 18:57 |  |  |  | 12.4 |  | Open | 0.00047755 |  | 0
100 | 2023-04-06 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:31 | 18:58 | 12.45 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:31 | NA | NA | 18:58 |  |  |  | 12.45 |  | Open | 0.00095895 |  | 0
101 | 2023-04-06 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:31 | 18:58 | 12.45 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:31 | NA | NA | 18:58 |  |  |  | 12.45 |  | Open | 0.00095895 |  | 0
102 | 2023-04-06 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:31 | 18:58 | 12.45 | IS20 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:31 | NA | NA | 18:58 |  |  |  | 12.45 |  | Open | 0.0011637 |  | 0
103 | 2023-04-06 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:31 | 18:58 | 12.45 | IS20 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:31 | NA | NA | 18:58 |  |  |  | 12.45 |  | Open | 0.0011637 |  | 0
104 | 2023-04-06 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:31 | 18:58 | 12.45 | IS18 | INV4 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:31 | NA | NA | 18:58 |  |  |  | 12.45 |  | Open | 0.0011637 |  | 0
105 | 2023-04-06 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:31 | 18:58 | 12.45 | IS18 | INV4 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:31 | NA | NA | 18:58 |  |  |  | 12.45 |  | Open | 0.0011637 |  | 0
106 | 2023-04-06 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:31 | 18:58 | 12.45 | IS19 | INV2 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:31 | NA | NA | 18:58 |  |  |  | 12.45 |  | Open | 0.0011637 |  | 0
107 | 2023-04-06 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:31 | 18:58 | 12.45 | IS2 | INV3 | M2 | SCB7 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:31 | NA | NA | 18:58 |  |  |  | 12.45 |  | Open | 0.00047947 |  | 0
108 | 2023-04-06 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:31 | 18:58 | 12.45 | IS2 | INV3 | M2 | SCB7 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:31 | NA | NA | 18:58 |  |  |  | 12.45 |  | Open | 0.00047947 |  | 0
109 | 2023-04-06 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:31 | 18:58 | 12.45 | IS2 | INV4 | M1 | SCB9 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:31 | NA | NA | 18:58 |  |  |  | 12.45 |  | Open | 0.00047947 |  | 0
110 | 2023-04-06 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:31 | 18:58 | 12.45 | IS2 | INV4 | M2 | SCB4 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:31 | NA | NA | 18:58 |  |  |  | 12.45 |  | Open | 0.00047947 |  | 0
111 | 2023-04-07 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:30 | 18:59 | 12.4833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:30 | NA | NA | 18:59 |  |  |  | 12.4833 | Waiting for Materials | Open | 0.00096151 |  | 0
112 | 2023-04-07 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:30 | 18:59 | 12.4833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:30 | NA | NA | 18:59 |  |  |  | 12.4833 | Waiting for Materials | Open | 0.00096151 |  | 0
113 | 2023-04-07 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:30 | 18:59 | 12.4833 | IS20 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:30 | NA | NA | 18:59 |  |  |  | 12.4833 | Waiting for Materials | Open | 0.0011668 |  | 0
114 | 2023-04-07 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:30 | 18:59 | 12.4833 | IS20 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:30 | NA | NA | 18:59 |  |  |  | 12.4833 | Waiting for Materials | Open | 0.0011668 |  | 0
115 | 2023-04-07 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:30 | 18:59 | 12.4833 | IS18 | INV4 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:30 | NA | NA | 18:59 |  |  |  | 12.4833 | Waiting for Materials | Open | 0.0011668 |  | 0
116 | 2023-04-07 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:30 | 18:59 | 12.4833 | IS18 | INV4 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:30 | NA | NA | 18:59 |  |  |  | 12.4833 | Waiting for Materials | Open | 0.0011668 |  | 0
117 | 2023-04-07 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:30 | 18:59 | 12.4833 | IS19 | INV2 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:30 | NA | NA | 18:59 |  |  |  | 12.4833 | Waiting for Materials | Open | 0.0011668 |  | 0
118 | 2023-04-07 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:30 | 18:59 | 12.4833 | IS2 | INV3 | M2 | SCB7 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:30 | NA | NA | 18:59 |  |  | 12.4833 | 12.4833 | Module reinstalled and string restored | Close | 0.00048076 |  | 0
119 | 2023-04-07 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:30 | 18:59 | 12.4833 | IS2 | INV3 | M2 | SCB7 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:30 | NA | NA | 18:59 |  |  | 12.4833 | 12.4833 | Module reinstalled and string restored | Close | 0.00048076 |  | 0
120 | 2023-04-07 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:30 | 18:59 | 12.4833 | IS2 | INV4 | M1 | SCB9 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:30 | NA | NA | 18:59 |  |  | 12.4833 | 12.4833 | Module reinstalled and string restored | Close | 0.00048076 |  | 0
121 | 2023-04-07 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:30 | 18:59 | 12.4833 | IS2 | INV4 | M2 | SCB4 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:30 | NA | NA | 18:59 |  |  | 12.4833 | 12.4833 | Module reinstalled and string restored | Close | 0.00048076 |  | 0
122 | 2023-04-07 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:30 | 18:59 | 12.4833 | IS11 |  |  |  |  | Tx | 0 | 1 | IS11Tx | 16595.25 | 4.952% | IDT | Tx_Manual Tripped for Bushing Replacement | IDT-11 Manual stop for LV side damaged bushing replacement | 17:54 | 17:54 | 18:00 | 18:59 | 0 | 0.1 | 1.0833 | 1.0833 | IDT manual trip for LV bushing replacement | Close | 0.053652 |  | 0 | JC74692
123 | 2023-04-08 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:30 | 18:58 | 12.4667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:30 | NA | NA | 18:58 |  |  |  | 12.4667 | Waiting for Materials | Open | 0.00096023 | 6.85 | 143.2792
124 | 2023-04-08 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:30 | 18:58 | 12.4667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:30 | NA | NA | 18:58 |  |  |  | 12.4667 | Waiting for Materials | Open | 0.00096023 | 6.85 | 143.2792
125 | 2023-04-08 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:30 | 18:58 | 12.4667 | IS20 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:30 | NA | NA | 18:58 |  |  |  | 12.4667 | Waiting for Materials | Open | 0.0011652 | 6.85 | 173.8669
126 | 2023-04-08 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:30 | 18:58 | 12.4667 | IS20 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:30 | NA | NA | 18:58 |  |  |  | 12.4667 | Waiting for Materials | Open | 0.0011652 | 6.85 | 173.8669
127 | 2023-04-08 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:30 | 18:58 | 12.4667 | IS18 | INV4 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:30 | NA | NA | 18:58 |  |  |  | 12.4667 | Waiting for Materials | Open | 0.0011652 | 6.85 | 173.8669
128 | 2023-04-08 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:30 | 18:58 | 12.4667 | IS18 | INV4 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:30 | NA | NA | 18:58 |  |  |  | 12.4667 | Waiting for Materials | Open | 0.0011652 | 6.85 | 173.8669
129 | 2023-04-08 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:30 | 18:58 | 12.4667 | IS19 | INV2 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:30 | NA | NA | 18:58 |  |  |  | 12.4667 | Waiting for Materials | Open | 0.0011652 | 6.85 | 173.8669
130 | 2023-04-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:30 | 18:50 | 12.3333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:30 | NA | NA | 18:50 |  |  |  | 12.3333 | Waiting for Materials | Open | 0.00094996 |  | 0
131 | 2023-04-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:30 | 18:50 | 12.3333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:30 | NA | NA | 18:50 |  |  |  | 12.3333 | Waiting for Materials | Open | 0.00094996 |  | 0
132 | 2023-04-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:30 | 18:50 | 12.3333 | IS20 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:30 | NA | NA | 18:50 |  |  |  | 12.3333 | Waiting for Materials | Open | 0.0011528 |  | 0
133 | 2023-04-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:30 | 18:50 | 12.3333 | IS20 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:30 | NA | NA | 18:50 |  |  |  | 12.3333 | Waiting for Materials | Open | 0.0011528 |  | 0
134 | 2023-04-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:30 | 18:50 | 12.3333 | IS18 | INV4 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:30 | NA | NA | 18:50 |  |  |  | 12.3333 | Waiting for Materials | Open | 0.0011528 |  | 0
135 | 2023-04-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:30 | 18:50 | 12.3333 | IS18 | INV4 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:30 | NA | NA | 18:50 |  |  |  | 12.3333 | Waiting for Materials | Open | 0.0011528 |  | 0
136 | 2023-04-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:30 | 18:50 | 12.3333 | IS19 | INV2 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:30 | NA | NA | 18:50 |  |  |  | 12.3333 | Waiting for Materials | Open | 0.0011528 |  | 0
137 | 2023-04-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:30 | 18:50 | 12.3333 | IS15 |  |  |  |  | Tx | 0 | 1 | IS15Tx | 16756.2 | 5% | IDT | Tx_tripped in Diff. Protection | IDT LV-4 all CTs craked and differential prtn operated | 14:12 | 14:15 | 14:30 | 16:59 | 0.05 | 0.3 | 2.7833 | 2.7833 | IDT LV-4 all CTs craked and replaced. IDT Charged | Close | 0.13918 |  | 0
138 | 2023-04-10 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 18:50 | 12.5 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 18:50 |  |  |  | 12.5 | Waiting for Materials | Open | 0.0009628 |  | 0
139 | 2023-04-10 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 18:50 | 12.5 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 18:50 |  |  |  | 12.5 | Waiting for Materials | Open | 0.0009628 |  | 0
140 | 2023-04-10 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 18:50 | 12.5 | IS20 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 18:50 |  |  |  | 12.5 | Waiting for Materials | Open | 0.0011683 |  | 0
141 | 2023-04-10 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 18:50 | 12.5 | IS20 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 18:50 |  |  |  | 12.5 | Waiting for Materials | Open | 0.0011683 |  | 0
142 | 2023-04-10 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 18:50 | 12.5 | IS18 | INV4 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 18:50 |  |  |  | 12.5 | Waiting for Materials | Open | 0.0011683 |  | 0
143 | 2023-04-10 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 18:50 | 12.5 | IS18 | INV4 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 18:50 |  |  |  | 12.5 | Waiting for Materials | Open | 0.0011683 |  | 0
144 | 2023-04-10 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 18:50 | 12.5 | IS19 | INV2 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 18:50 |  |  |  | 12.5 | Waiting for Materials | Open | 0.0011683 |  | 0
145 | 2023-04-10 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 18:50 | 12.5 | IS15 |  |  |  |  | Tx | 0 | 1 | IS15Tx | 16756.2 | 5% | IDT | Tx_ tripped in Diff. Protection | IDT LV-3 R-Phase CTs craked and differential prtn operated | 11:31 | 11:33 | 11:45 | 13:04 | 0.033333 | 0.23333 | 1.55 | 1.55 | IDT LV-3 R-Phase CT craked and replaced. IDT Charged | Close | 0.077508 |  | 0
146 | 2023-04-11 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:00 | 12.6667 | IS15 | INV4 | M1 |  |  |  | 1 | 1 | IS15INV4M1 | 2192.4 | 0.6543% | Inverter | Inv_ Ins fault | Unit manual stop for rectification or unit-2 fault | 7:28 | 7:28 | 7:30 | 8:38 | 0 | 0.033333 | 1.1667 | 1.1667 | Unit started after checking all SCB | Close | 0.0076332 |  | 0
147 | 2023-04-11 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:00 | 12.6667 | IS15 | INV4 | M2 |  |  |  | 1 | 1 | IS15INV4M2 | 2004.48 | 0.5982% | Inverter | Inv_tripped of GFDI | Inv unit tripped under GFDI Pro fault | 6:20 | 6:20 | 6:30 | 19:00 | 0 | 0.16667 | 12.6667 | 12.6667 | Need support from OEM | Close | 0.075771 |  | 0
148 | 2023-04-11 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:00 | 12.6667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 19:00 |  |  |  | 12.6667 | Waiting for Materials | Open | 0.00097564 |  | 0
149 | 2023-04-11 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:00 | 12.6667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 19:00 |  |  |  | 12.6667 | Waiting for Materials | Open | 0.00097564 |  | 0
150 | 2023-04-11 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:00 | 12.6667 | IS20 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 19:00 |  |  |  | 12.6667 | Waiting for Materials | Open | 0.0011839 |  | 0
151 | 2023-04-11 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:00 | 12.6667 | IS20 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 19:00 |  |  |  | 12.6667 | Waiting for Materials | Open | 0.0011839 |  | 0
152 | 2023-04-11 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:00 | 12.6667 | IS18 | INV4 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 19:00 |  |  |  | 12.6667 | Waiting for Materials | Open | 0.0011839 |  | 0
153 | 2023-04-11 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:00 | 12.6667 | IS18 | INV4 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 19:00 |  |  |  | 12.6667 | Waiting for Materials | Open | 0.0011839 |  | 0
154 | 2023-04-11 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:00 | 12.6667 | IS19 | INV2 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 19:00 |  |  |  | 12.6667 | Waiting for Materials | Open | 0.0011839 |  | 0
155 | 2023-04-12 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:00 | 12.6667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 19:00 |  |  |  | 12.6667 | Waiting for Materials | Open | 0.00097564 |  | 0
156 | 2023-04-12 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:00 | 12.6667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 19:00 |  |  |  | 12.6667 | Waiting for Materials | Open | 0.00097564 |  | 0
157 | 2023-04-12 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:00 | 12.6667 | IS20 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 19:00 |  |  |  | 12.6667 | Waiting for Materials | Open | 0.0011839 |  | 0
158 | 2023-04-12 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:00 | 12.6667 | IS20 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 19:00 |  |  |  | 12.6667 | Waiting for Materials | Open | 0.0011839 |  | 0
159 | 2023-04-12 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:00 | 12.6667 | IS18 | INV4 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 19:00 |  |  |  | 12.6667 | Waiting for Materials | Open | 0.0011839 |  | 0
160 | 2023-04-12 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:00 | 12.6667 | IS18 | INV4 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 19:00 |  |  |  | 12.6667 | Waiting for Materials | Open | 0.0011839 |  | 0
161 | 2023-04-12 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:00 | 12.6667 | IS15 | INV4 | M1 |  |  |  | 1 | 1 | IS15INV4M1 | 2192.4 | 0.6543% | Inverter | Inv_ Ins fault | Unit manual stop for rectification or unit-2 fault | 6:20 | 6:20 | 6:30 | 8:09 | 0 | 0.16667 | 1.8167 | 1.8167 | All SCB made ON and after checking Inverter ON | Close | 0.011886 |  | 0
162 | 2023-04-12 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:00 | 12.6667 | IS15 | INV4 | M2 |  |  |  | 1 | 1 | IS15INV4M2 | 2004.48 | 0.5982% | Inverter | Inv_tripped of GFDI | Inv unit tripped under GFDI Pro fault | 6:20 | 6:20 | 6:30 | 8:09 | 0 | 0.16667 | 1.8167 | 1.8167 | All SCB made ON and after checking Inverter ON | Close | 0.010867 |  | 0
163 | 2023-04-12 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:00 | 12.6667 | IS15 |  |  |  |  | Tx | 0 | 1 | IS15Tx | 16756.2 | 5% | IDT | Tx_Tripped in High OTI temp | IDT tripped in OIL TEMP fault | 12:08 | 12:15 | 12:30 | 14:38 | 0.11667 | 0.36667 | 2.5 | 2.5 | OTI Meter resetted and IDT charged | Close | 0.12501 |  | 0
164 | 2023-04-13 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:00 | 12.6667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 19:00 |  |  |  | 12.6667 | Waiting for Materials | Open | 0.00097564 |  | 0
165 | 2023-04-13 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:00 | 12.6667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 19:00 |  |  |  | 12.6667 | Waiting for Materials | Open | 0.00097564 |  | 0
166 | 2023-04-13 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:00 | 12.6667 | IS20 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 19:00 |  |  |  | 12.6667 | Waiting for Materials | Open | 0.0011839 |  | 0
167 | 2023-04-13 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:00 | 12.6667 | IS20 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 19:00 |  |  |  | 12.6667 | Waiting for Materials | Open | 0.0011839 |  | 0
168 | 2023-04-13 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:00 | 12.6667 | IS18 | INV4 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 19:00 |  |  |  | 12.6667 | Waiting for Materials | Open | 0.0011839 |  | 0
169 | 2023-04-13 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:00 | 12.6667 | IS18 | INV4 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 19:00 |  |  |  | 12.6667 | Waiting for Materials | Open | 0.0011839 |  | 0
170 | 2023-04-13 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:00 | 12.6667 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | PV module Half String JB Burn | Module Half string JB Burn | 6:20 | NA | NA | 19:00 |  |  |  | 12.6667 | Waiting for Materials | Open | 0.00059196 |  | 0
171 | 2023-04-14 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:00 | 12.6667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 19:00 |  |  |  | 12.6667 | Waiting for Materials | Open | 0.00097564 |  | 0
172 | 2023-04-14 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:00 | 12.6667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 19:00 |  |  |  | 12.6667 | Waiting for Materials | Open | 0.00097564 |  | 0
173 | 2023-04-14 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:00 | 12.6667 | IS20 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 19:00 |  |  |  | 12.6667 | Waiting for Materials | Open | 0.0011839 |  | 0
174 | 2023-04-14 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:00 | 12.6667 | IS20 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 19:00 |  |  |  | 12.6667 | Waiting for Materials | Open | 0.0011839 |  | 0
175 | 2023-04-14 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:00 | 12.6667 | IS18 | INV4 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 19:00 |  |  |  | 12.6667 | Waiting for Materials | Open | 0.0011839 |  | 0
176 | 2023-04-14 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:00 | 12.6667 | IS18 | INV4 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 19:00 |  |  |  | 12.6667 | Waiting for Materials | Open | 0.0011839 |  | 0
177 | 2023-04-14 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:00 | 12.6667 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | PV module Half String JB Burn | Module Half string JB Burn | 6:20 | NA | NA | 19:00 |  |  |  | 12.6667 | Waiting for Materials | Open | 0.00059196 |  | 0
178 | 2023-04-14 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:00 | 12.6667 | IS20 |  |  |  |  | Tx | 0 | 1 | IS20Tx | 17539.2 | 5.234% | IDT | Tx_Tripped in High WTI temp | IDT tripped in LV winding-3 | 15:08 | 15:08 | 15:10 | 15:24 | 0 | 0.033333 | 0.26667 | 0.26667 | Checked and reset setting and IDT charged | Close | 0.013958 |  | 0
179 | 2023-04-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:00 | 12.6667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 19:00 |  |  |  | 12.6667 | Waiting for Materials | Open | 0.00097564 |  | 0
180 | 2023-04-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:00 | 12.6667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 19:00 |  |  |  | 12.6667 | Waiting for Materials | Open | 0.00097564 |  | 0
181 | 2023-04-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:00 | 12.6667 | IS20 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 19:00 |  |  |  | 12.6667 | Waiting for Materials | Open | 0.0011839 |  | 0
182 | 2023-04-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:00 | 12.6667 | IS20 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 19:00 |  |  |  | 12.6667 | Waiting for Materials | Open | 0.0011839 |  | 0
183 | 2023-04-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:00 | 12.6667 | IS18 | INV4 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 19:00 |  |  |  | 12.6667 | Waiting for Materials | Open | 0.0011839 |  | 0
184 | 2023-04-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:00 | 12.6667 | IS18 | INV4 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 19:00 |  |  |  | 12.6667 | Waiting for Materials | Open | 0.0011839 |  | 0
185 | 2023-04-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:00 | 12.6667 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:20 | NA | NA | 19:00 |  |  |  | 12.6667 | Waiting for Materials | Open | 0.00059196 |  | 0
186 | 2023-04-16 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 18:50 | 12.5 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 18:50 |  |  |  | 12.5 | Waiting for Materials | Open | 0.0009628 |  | 0
187 | 2023-04-16 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 18:50 | 12.5 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 18:50 |  |  |  | 12.5 | Waiting for Materials | Open | 0.0009628 |  | 0
188 | 2023-04-16 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 18:50 | 12.5 | IS20 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 18:50 |  |  |  | 12.5 | Waiting for Materials | Open | 0.0011683 |  | 0
189 | 2023-04-16 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 18:50 | 12.5 | IS20 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 18:50 |  |  |  | 12.5 | Waiting for Materials | Open | 0.0011683 |  | 0
190 | 2023-04-16 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 18:50 | 12.5 | IS18 | INV4 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 18:50 |  |  |  | 12.5 | Waiting for Materials | Open | 0.0011683 |  | 0
191 | 2023-04-16 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 18:50 | 12.5 | IS18 | INV4 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 18:50 |  |  |  | 12.5 | Waiting for Materials | Open | 0.0011683 |  | 0
192 | 2023-04-16 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 18:50 | 12.5 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:20 | NA | NA | 18:50 |  |  |  | 12.5 | Waiting for Materials | Open | 0.00058417 |  | 0
193 | 2023-04-17 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:19 | 19:08 | 12.8167 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:19 | NA | NA | 19:08 |  |  |  | 12.8167 | Waiting for Materials | Open | 0.00098719 |  | 0
194 | 2023-04-17 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:19 | 19:08 | 12.8167 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:19 | NA | NA | 19:08 |  |  |  | 12.8167 | Waiting for Materials | Open | 0.00098719 |  | 0
195 | 2023-04-17 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:19 | 19:08 | 12.8167 | IS20 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:19 | NA | NA | 19:08 |  |  |  | 12.8167 | Waiting for Materials | Open | 0.0011979 |  | 0
196 | 2023-04-17 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:19 | 19:08 | 12.8167 | IS20 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:19 | NA | NA | 19:08 |  |  |  | 12.8167 | Waiting for Materials | Open | 0.0011979 |  | 0
197 | 2023-04-17 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:19 | 19:08 | 12.8167 | IS18 | INV4 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:19 | NA | NA | 19:08 |  |  |  | 12.8167 | Waiting for Materials | Open | 0.0011979 |  | 0
198 | 2023-04-17 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:19 | 19:08 | 12.8167 | IS18 | INV4 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:19 | NA | NA | 19:08 |  |  |  | 12.8167 | Waiting for Materials | Open | 0.0011979 |  | 0
199 | 2023-04-17 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:19 | 19:08 | 12.8167 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:19 | NA | NA | 19:08 |  |  |  | 12.8167 | Waiting for Materials | Open | 0.00059897 |  | 0
200 | 2023-04-18 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:21 | 19:05 | 12.7333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:21 | NA | NA | 19:05 |  |  |  | 12.7333 | Waiting for Materials | Open | 0.00098077 |  | 0
201 | 2023-04-18 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:21 | 19:05 | 12.7333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:21 | NA | NA | 19:05 |  |  |  | 12.7333 | Waiting for Materials | Open | 0.00098077 |  | 0
202 | 2023-04-18 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:21 | 19:05 | 12.7333 | IS20 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:21 | NA | NA | 19:05 |  |  |  | 12.7333 | Waiting for Materials | Open | 0.0011901 |  | 0
203 | 2023-04-18 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:21 | 19:05 | 12.7333 | IS20 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:21 | NA | NA | 19:05 |  |  |  | 12.7333 | Waiting for Materials | Open | 0.0011901 |  | 0
204 | 2023-04-18 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:21 | 19:05 | 12.7333 | IS18 | INV4 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:21 | NA | NA | 19:05 |  |  |  | 12.7333 | Waiting for Materials | Open | 0.0011901 |  | 0
205 | 2023-04-18 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:21 | 19:05 | 12.7333 | IS18 | INV4 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:21 | NA | NA | 19:05 |  |  |  | 12.7333 | Waiting for Materials | Open | 0.0011901 |  | 0
206 | 2023-04-18 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:21 | 19:05 | 12.7333 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:21 | NA | NA | 19:05 |  |  |  | 12.7333 | Waiting for Materials | Open | 0.00059507 |  | 0
207 | 2023-04-19 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:02 | 12.7 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 19:02 |  |  |  | 12.7 | Waiting for Materials | Open | 0.0009782 |  | 0
208 | 2023-04-19 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:02 | 12.7 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 19:02 |  |  |  | 12.7 | Waiting for Materials | Open | 0.0009782 |  | 0
209 | 2023-04-19 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:02 | 12.7 | IS20 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 19:02 |  |  |  | 12.7 | Waiting for Materials | Open | 0.001187 |  | 0
210 | 2023-04-19 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:02 | 12.7 | IS20 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 19:02 |  |  |  | 12.7 | Waiting for Materials | Open | 0.001187 |  | 0
211 | 2023-04-19 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:02 | 12.7 | IS18 | INV4 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 19:02 |  |  |  | 12.7 | Waiting for Materials | Open | 0.001187 |  | 0
212 | 2023-04-19 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:02 | 12.7 | IS18 | INV4 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | NA | NA | 19:02 |  |  |  | 12.7 | Waiting for Materials | Open | 0.001187 |  | 0
213 | 2023-04-19 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:20 | 19:02 | 12.7 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:20 | NA | NA | 19:02 |  |  |  | 12.7 | Waiting for Materials | Open | 0.00059352 |  | 0
214 | 2023-04-20 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:22 | 19:17 | 12.9167 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:22 | NA | NA | 19:17 |  |  |  | 12.9167 | Waiting for Materials | Open | 0.00099489 |  | 0
215 | 2023-04-20 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:22 | 19:17 | 12.9167 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:22 | NA | NA | 19:17 |  |  |  | 12.9167 | Waiting for Materials | Open | 0.00099489 |  | 0
216 | 2023-04-20 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:22 | 19:17 | 12.9167 | IS20 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:22 | NA | NA | 19:17 |  |  |  | 12.9167 | Waiting for Materials | Open | 0.0012073 |  | 0
217 | 2023-04-20 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:22 | 19:17 | 12.9167 | IS20 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:22 | NA | NA | 19:17 |  |  |  | 12.9167 | Waiting for Materials | Open | 0.0012073 |  | 0
218 | 2023-04-20 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:22 | 19:17 | 12.9167 | IS18 | INV4 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:22 | NA | NA | 19:17 |  |  |  | 12.9167 | Waiting for Materials | Open | 0.0012073 |  | 0
219 | 2023-04-20 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:22 | 19:17 | 12.9167 | IS18 | INV4 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module theft | PV modules removed by unknown Person | 6:22 | NA | NA | 19:17 |  |  |  | 12.9167 | Waiting for Materials | Open | 0.0012073 |  | 0
220 | 2023-04-20 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:22 | 19:17 | 12.9167 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:22 | NA | NA | 19:17 |  |  |  | 12.9167 | Waiting for Materials | Open | 0.00060364 |  | 0
221 | 2023-04-21 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:21 | 19:12 | 12.85 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:21 | NA | NA | 19:12 |  |  |  | 12.85 | Waiting for Materials | Open | 0.00098976 |  | 0
222 | 2023-04-21 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:21 | 19:12 | 12.85 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:21 | NA | NA | 19:12 |  |  |  | 12.85 | Waiting for Materials | Open | 0.00098976 |  | 0
223 | 2023-04-21 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:21 | 19:12 | 12.85 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:21 | NA | NA | 19:12 |  |  |  | 12.85 | Waiting for Materials | Open | 0.00060053 |  | 0
224 | 2023-04-22 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:23 | 19:12 | 12.8167 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:23 | NA | NA | 19:12 |  |  |  | 12.8167 | Waiting for Materials | Open | 0.00098719 |  | 0
225 | 2023-04-22 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:23 | 19:12 | 12.8167 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:23 | NA | NA | 19:12 |  |  |  | 12.8167 | Waiting for Materials | Open | 0.00098719 |  | 0
226 | 2023-04-22 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:23 | 19:12 | 12.8167 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:23 | NA | NA | 19:12 |  |  |  | 12.8167 | Waiting for Materials | Open | 0.00059897 |  | 0
227 | 2023-04-23 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:18 | 19:10 | 12.8667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:18 | NA | NA | 19:10 |  |  |  | 12.8667 | Waiting for Materials | Open | 0.00099104 |  | 0
228 | 2023-04-23 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:18 | 19:10 | 12.8667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:18 | NA | NA | 19:10 |  |  |  | 12.8667 | Waiting for Materials | Open | 0.00099104 |  | 0
229 | 2023-04-23 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:18 | 19:10 | 12.8667 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:18 | NA | NA | 19:10 |  |  |  | 12.8667 | Waiting for Materials | Open | 0.00060131 |  | 0
230 | 2023-04-24 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:10 | 19:12 | 13.0333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:10 | NA | NA | 19:12 |  |  |  | 13.0333 | Waiting for Materials | Open | 0.0010039 |  | 0
231 | 2023-04-24 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:10 | 19:12 | 13.0333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:10 | NA | NA | 19:12 |  |  |  | 13.0333 | Waiting for Materials | Open | 0.0010039 |  | 0
232 | 2023-04-24 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:10 | 19:12 | 13.0333 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:10 | NA | NA | 19:12 |  |  |  | 13.0333 | Waiting for Materials | Open | 0.00060909 |  | 0
233 | 2023-04-25 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:12 | 19:06 | 12.9 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:10 | NA | NA | 19:12 |  |  |  | 13.0333 | Waiting for Materials | Open | 0.0010039 |  | 0
234 | 2023-04-25 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:12 | 19:06 | 12.9 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:10 | NA | NA | 19:12 |  |  |  | 13.0333 | Waiting for Materials | Open | 0.0010039 |  | 0
235 | 2023-04-25 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:12 | 19:06 | 12.9 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:10 | NA | NA | 19:12 |  |  |  | 13.0333 | Waiting for Materials | Open | 0.00060909 |  | 0
236 | 2023-04-25 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:12 | 19:06 | 12.9 | IS3 | INV2 | M1 |  |  |  | 1 | 1 | IS3INV2M1 | 2090.61 | 0.6239% | Inverter | Inv_tripped of GFDI | Unit manual stop for rectification or unit-2 fault | 13:58 | 13:58 | 13:58 | 14:12 | 0 | 0 | 0.23333 | 0.23333 | Unit manual stop for rectification or unit-2 fault | Close | 0.0014558 |  | 0
237 | 2023-04-25 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:12 | 19:06 | 12.9 | IS3 | INV2 | M2 |  |  |  | 1 | 1 | IS3INV2M2 | 2090.61 | 0.6239% | Inverter | Inv_tripped of GFDI | Inv unit tripped under GFDI Pro fault | 10:00 | 10:00 | 10:15 | 14:33 | 0 | 0.25 | 4.55 | 4.55 | Unit started after checking all SCB | Close | 0.028387 |  | 0
238 | 2023-04-26 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:11 | 19:07 | 12.9333 | IS3 | INV2 | M2 |  |  |  | 1 | 1 | IS3INV2M2 | 2090.61 | 0.6239% | Inverter | Inv_tripped of GFDI | Inv unit tripped under GFDI Pro fault | 11:23 | 11:23 | 11:30 | 19:07 | 0 | 0.11667 | 7.7333 | 7.7333 | Unit under breakdown in Internal fault (WIP) | Close | 0.048248 |  | 0
239 | 2023-04-26 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:11 | 19:07 | 12.9333 | IS3 | INV2 | M1 |  |  |  | 1 | 1 | IS3INV2M1 | 2090.61 | 0.6239% | Inverter | Inv_tripped of GFDI | Unit manual stop for rectification or unit-2 fault | 11:23 | 11:23 | 11:23 | 11:35 | 0 | 0 | 0.2 | 0.2 | Unit manual stop for rectification or unit-2 fault | Close | 0.0012478 |  | 0
240 | 2023-04-26 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:11 | 19:07 | 12.9333 | IS3 | INV2 | M1 |  |  |  | 1 | 1 | IS3INV2M1 | 2090.61 | 0.6239% | Inverter | Inv_tripped of GFDI | Unit manual stop for rectification or unit-2 fault | 12:57 | 12:57 | 12:57 | 13:12 | 0 | 0 | 0.25 | 0.25 | Unit manual stop for rectification or unit-2 fault | Close | 0.0015597 |  | 0
241 | 2023-04-26 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:11 | 19:07 | 12.9333 | IS3 | INV2 | M1 |  |  |  | 1 | 1 | IS3INV2M1 | 2090.61 | 0.6239% | Inverter | Inv_tripped of GFDI | Unit manual stop for rectification or unit-2 fault | 13:24 | 13:24 | 13:24 | 13:36 | 0 | 0 | 0.2 | 0.2 | Unit manual stop for rectification or unit-2 fault | Close | 0.0012478 |  | 0
242 | 2023-04-26 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:11 | 19:07 | 12.9333 | IS3 | INV2 | M1 |  |  |  | 1 | 1 | IS3INV2M1 | 2090.61 | 0.6239% | Inverter | Inv_tripped of GFDI | Unit manual stop for rectification or unit-2 fault | 13:53 | 13:53 | 13:53 | 14:21 | 0 | 0 | 0.46667 | 0.46667 | Unit manual stop for rectification or unit-2 fault | Close | 0.0029115 |  | 0
243 | 2023-04-26 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:11 | 19:07 | 12.9333 | IS3 | INV2 | M1 |  |  |  | 1 | 1 | IS3INV2M1 | 2090.61 | 0.6239% | Inverter | Inv_tripped of GFDI | Unit manual stop for rectification or unit-2 fault | 15:24 | 15:24 | 15:24 | 15:46 | 0 | 0 | 0.36667 | 0.36667 | Unit manual stop for rectification or unit-2 fault | Close | 0.0022876 |  | 0
244 | 2023-04-26 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:11 | 19:07 | 12.9333 | IS3 | INV2 | M1 |  |  |  | 1 | 1 | IS3INV2M1 | 2090.61 | 0.6239% | Inverter | Inv_tripped of GFDI | Unit manual stop for rectification or unit-2 fault | 15:58 | 15:58 | 15:58 | 19:07 | 0 | 0 | 3.15 | 3.15 | Unit manual stop for rectification or unit-2 fault | Close | 0.019653 |  | 0
245 | 2023-04-26 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:11 | 19:07 | 12.9333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:11 | 6:11 | 6:11 | 19:07 | 0 | 0 |  | 12.9333 | Waiting for Materials | Open | 0.00099618 |  | 0
246 | 2023-04-26 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:11 | 19:07 | 12.9333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:11 | 6:11 | 6:11 | 19:07 | 0 | 0 |  | 12.9333 | Waiting for Materials | Open | 0.00099618 |  | 0
247 | 2023-04-26 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:11 | 19:07 | 12.9333 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:11 | 6:11 | 6:11 | 19:07 | 0 | 0 |  | 12.9333 | Waiting for Materials | Open | 0.00060442 |  | 0
248 | 2023-04-27 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:09 | 19:14 | 13.0833 | IS3 | INV2 | M2 |  |  |  | 1 | 1 | IS3INV2M2 | 2090.61 | 0.6239% | Inverter | Inv_tripped of GFDI | Inv unit tripped under GFDI Pro fault | 6:09 | 6:09 | 6:09 | 9:00 | 0 | 0 | 2.85 | 2.85 | Unit started after checking related connection discussion with sungrow team and checked floating value of all SCB | Close | 0.017781 |  | 0
249 | 2023-04-27 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:09 | 19:14 | 13.0833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:09 | 6:09 | 6:09 | 19:14 | 0 | 0 |  | 13.0833 | Waiting for Materials | Open | 0.0010077 |  | 0
250 | 2023-04-27 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:09 | 19:14 | 13.0833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:09 | 6:09 | 6:09 | 19:14 | 0 | 0 |  | 13.0833 | Waiting for Materials | Open | 0.0010077 |  | 0
251 | 2023-04-27 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:09 | 19:14 | 13.0833 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:09 | 6:09 | 6:09 | 19:14 | 0 | 0 |  | 13.0833 | Waiting for Materials | Open | 0.00061143 |  | 0
252 | 2023-04-28 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:07 | 19:01 | 12.9 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:07 | 6:07 | 6:07 | 19:01 | 0 | 0 |  | 12.9 | Waiting for Materials | Open | 0.00099361 |  | 0
253 | 2023-04-28 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:07 | 19:01 | 12.9 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:07 | 6:07 | 6:07 | 19:01 | 0 | 0 |  | 12.9 | Waiting for Materials | Open | 0.00099361 |  | 0
254 | 2023-04-28 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:07 | 19:01 | 12.9 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:07 | 6:07 | 6:07 | 19:01 | 0 | 0 |  | 12.9 | Waiting for Materials | Open | 0.00060286 |  | 0
255 | 2023-04-28 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:07 | 19:01 | 12.9 | [5 empty] | Power_Tx1 | 0 | 1 | Power_Tx1 | 167322.75 | 49.93% | IDT | Power transformer 01 triped in Differential protection operated | Power transformer 01 triped in Differential protection operated | 14:54 | 14:54 | 18:09 | 18:09 | 0 | 3.25 | 3.25 | 3.25 | Checked fault records and parameters on SAS as well as on relay we observed R phase voltage down and Y & B phase current high. After we check and tighten it related connection on switchyard CT Junction box as well as CRP panel found ok then trafo charged. | Close | 1.6228 |  | 0
256 | 2023-04-29 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:08 | 19:15 | 13.1167 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:08 | 6:08 | 6:08 | 19:15 | 0 | 0 |  | 13.1167 | Waiting for Materials | Open | 0.0010103 |  | 0
257 | 2023-04-29 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:08 | 19:15 | 13.1167 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:08 | 6:08 | 6:08 | 19:15 | 0 | 0 |  | 13.1167 | Waiting for Materials | Open | 0.0010103 |  | 0
258 | 2023-04-29 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:08 | 19:15 | 13.1167 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:08 | 6:08 | 6:08 | 19:15 | 0 | 0 |  | 13.1167 | Waiting for Materials | Open | 0.00061299 |  | 0
259 | 2023-04-30 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:07 | 19:15 | 13.1333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:08 | 6:08 | 6:08 | 19:15 | 0 | 0 |  | 13.1167 | Waiting for Materials | Open | 0.0010103 |  | 0
260 | 2023-04-30 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:07 | 19:15 | 13.1333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:08 | 6:08 | 6:08 | 19:15 | 0 | 0 |  | 13.1167 | Waiting for Materials | Open | 0.0010103 |  | 0
261 | 2023-04-30 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:07 | 19:15 | 13.1333 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:08 | 6:08 | 6:08 | 19:15 | 0 | 0 |  | 13.1167 | Waiting for Materials | Open | 0.00061299 |  | 0
262 | 2023-04-30 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:07 | 19:15 | 13.1333 | IS3 | INV2 | M1 |  |  |  | 1 | 1 | IS3INV2M1 | 2090.61 | 0.6239% | Inverter | Inv_tripped of GFDI | Inverter tripped in GFDI Fault | 11:47 | 11:47 | 12:00 | 12:50 | 0 | 0.21667 | 1.05 | 1.05 | IR done and found no fault | Close | 0.0065509 |  | 0
263 | 2023-04-30 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:07 | 19:15 | 13.1333 | IS3 | INV2 | M2 |  |  |  | 1 | 1 | IS3INV2M2 | 2090.61 | 0.6239% | Inverter | Inv_tripped of GFDI | Inverter tripped in GFDI Fault | 8:42 | 8:42 | 8:50 | 19:15 | 0 | 0.13333 | 10.55 | 10.55 | IR done and found no fault | Close | 0.065821 |  | 0
264 | 2023-04-30 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:07 | 19:15 | 13.1333 | IS3 | INV2 | M2 | SCB3 |  |  | 1 | 1 | IS3INV2M2SCB3 | 232.29 | 0.06932% | SCB | SCB_Removed for GFDI fault | SCB dismantled due to GFDI Fault | 8:42 | 8:42 | 8:50 | 19:15 | 0 | 0.13333 | 10.55 | 10.55 | IR done and found no fault | Close | 0.0073134 |  | 0
265 | 2023-04-30 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:07 | 19:15 | 13.1333 | IS3 | INV2 | M2 | SCB8 |  |  | 1 | 1 | IS3INV2M2SCB8 | 232.29 | 0.06932% | SCB | SCB_Removed for GFDI fault | SCB dismantled due to GFDI Fault | 8:42 | 8:42 | 8:50 | 19:15 | 0 | 0.13333 | 10.55 | 10.55 | IR done and found no fault | Close | 0.0073134 |  | 0
266 | 2023-04-30 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:07 | 19:15 | 13.1333 | IS3 | INV2 | M2 | SCB9 |  |  | 1 | 1 | IS3INV2M2SCB9 | 232.29 | 0.06932% | SCB | SCB_Removed for GFDI fault | SCB dismantled due to GFDI Fault | 8:42 | 8:42 | 8:50 | 19:15 | 0 | 0.13333 | 10.55 | 10.55 | IR done and found no fault | Close | 0.0073134 |  | 0
267 | 2023-04-30 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:07 | 19:15 | 13.1333 | IS3 | INV2 | M2 | SCB10 |  |  | 1 | 1 | IS3INV2M2SCB10 | 0 | 0% | SCB | SCB_Removed for GFDI fault | SCB dismantled due to GFDI Fault | 8:42 | 8:42 | 8:50 | 19:15 | 0 | 0.13333 | 10.55 | 10.55 | IR done and found no fault | Close | 0 |  | 0
268 | 2023-05-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:16 | 13.1833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:05 | 6:05 | 6:05 | 19:16 | 0 | 0 |  | 13.1833 | Waiting for Materials | Open | 0.0010154 | 6.41 | 139.9826
269 | 2023-05-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:16 | 13.1833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:05 | 6:05 | 6:05 | 19:16 | 0 | 0 |  | 13.1833 | Waiting for Materials | Open | 0.0010154 | 6.41 | 139.9826
270 | 2023-05-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:16 | 13.1833 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:05 | 6:05 | 6:05 | 19:16 | 0 | 0 |  | 13.1833 | Waiting for Materials | Open | 0.0006161 | 6.41 | 84.9332
271 | 2023-05-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:16 | 13.1833 | IS3 | INV2 | M2 |  |  |  | 1 | 1 | IS3INV2M2 | 2090.61 | 0.6239% | Inverter | Inv_tripped of GFDI | Inv unit tripped under GFDI Pro fault | 6:05 | 6:05 | 6:05 | 19:16 | 0 | 0 | 13.1833 | 13.1833 | Unit started after checking related connection discussion with sungrow team and checked floating value of all SCB | Close | 0.08225 | 6.41 | 11338.5877
272 | 2023-05-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:02 | 19:07 | 13.0833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | SCB | SCB_Removed for GFDI fault | SCB dismantled due to GFDI Fault | 6:02 | 6:02 | 6:02 | 19:16 | 0 | 0 |  | 13.2333 | Waiting for Materials | Open | 0.0010193 | 7.19 | 157.0163
273 | 2023-05-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:02 | 19:07 | 13.0833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:02 | 6:02 | 6:02 | 19:16 | 0 | 0 |  | 13.2333 | Waiting for Materials | Open | 0.0010193 | 7.19 | 157.0163
274 | 2023-05-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:02 | 19:07 | 13.0833 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | PV Module theft | PV modules removed by unknown Person | 6:02 | 6:02 | 6:02 | 19:16 | 0 | 0 |  | 13.2333 | Waiting for Materials | Open | 0.00061844 | 7.19 | 95.2683
275 | 2023-05-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:02 | 19:07 | 13.0833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:02 | 6:02 | 6:02 | 19:16 | 0 | 0 |  | 13.2333 | Waiting for Materials | Open | 0.0010193 | 7.47 | 163.131
276 | 2023-05-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:02 | 19:07 | 13.0833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:02 | 6:02 | 6:02 | 19:16 | 0 | 0 |  | 13.2333 | Waiting for Materials | Open | 0.0010193 | 7.47 | 163.131
277 | 2023-05-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:02 | 19:07 | 13.0833 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:02 | 6:02 | 6:02 | 19:16 | 0 | 0 |  | 13.2333 | Waiting for Materials | Open | 0.00061844 | 7.47 | 98.9784
278 | 2023-05-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:02 | 19:07 | 13.0833 | IS10 | INV2 | M2 |  |  |  | 1 | 1 | IS10INV2M2 | 2223.72 | 0.6636% | Inverter | Inv Unit_AC Coil failure | Inverter Unit tripped under AC Switch breaking | 6:02 | 6:02 | 6:02 | 19:16 | 0 | 0 |  | 13.2333 | Waiting for Materials | Open | 0.087819 | 7.47 | 14054.9276
279 | 2023-05-04 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:03 | 19:14 | 13.1833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:02 | 6:02 | 6:02 | 19:14 | 0 | 0 |  | 13.2 | Waiting for Materials | Open | 0.0010167 | 6.98 | 152.4303
280 | 2023-05-04 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:03 | 19:14 | 13.1833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:02 | 6:02 | 6:02 | 19:14 | 0 | 0 |  | 13.2 | Waiting for Materials | Open | 0.0010167 | 6.98 | 152.4303
281 | 2023-05-04 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:03 | 19:14 | 13.1833 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:02 | 6:02 | 6:02 | 19:14 | 0 | 0 |  | 13.2 | Waiting for Materials | Open | 0.00061688 | 6.98 | 92.4858
282 | 2023-05-05 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:17 | 19:12 | 12.9167 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | SCB_Removed for GFDI fault | SCB dismantled due to GFDI Fault | 6:17 | 6:17 | 6:17 | 19:12 | 0 | 0 |  | 12.9167 | Waiting for Materials | Open | 0.00099489 | 6.91 | 150.9016
283 | 2023-05-05 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:17 | 19:12 | 12.9167 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:17 | 6:17 | 6:17 | 19:12 | 0 | 0 |  | 12.9167 | Waiting for Materials | Open | 0.00099489 | 6.91 | 150.9016
284 | 2023-05-05 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:17 | 19:12 | 12.9167 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:17 | 6:17 | 6:17 | 19:12 | 0 | 0 |  | 12.9167 | Waiting for Materials | Open | 0.00060364 | 6.91 | 91.5583
285 | 2023-05-06 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:12 | 13.1167 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:05 | 6:05 | 6:05 | 19:12 | 0 | 0 |  | 13.1167 | Waiting for Materials | Open | 0.0010103 | 7.17 | 156.5796
286 | 2023-05-06 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:12 | 13.1167 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:05 | 6:05 | 6:05 | 19:12 | 0 | 0 |  | 13.1167 | Waiting for Materials | Open | 0.0010103 | 7.17 | 156.5796
287 | 2023-05-06 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:12 | 13.1167 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:05 | 6:05 | 6:05 | 19:12 | 0 | 0 |  | 13.1167 | Waiting for Materials | Open | 0.00061299 | 7.17 | 95.0033
288 | 2023-05-07 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:16 | 13.1833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:05 | 6:05 | 6:05 | 19:16 | 0 | 0 |  | 13.1833 | Waiting for Materials | Open | 0.0010154 | 7.49 | 163.5678
289 | 2023-05-07 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:16 | 13.1833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:05 | 6:05 | 6:05 | 19:16 | 0 | 0 |  | 13.1833 | Waiting for Materials | Open | 0.0010154 | 7.49 | 163.5678
290 | 2023-05-07 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:16 | 13.1833 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:05 | 6:05 | 6:05 | 19:16 | 0 | 0 |  | 13.1833 | Waiting for Materials | Open | 0.0006161 | 7.49 | 99.2434
291 | 2023-05-08 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:02 | 19:13 | 13.1833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:05 | 6:05 | 6:05 | 19:16 | 0 | 0 |  | 13.1833 | Waiting for Materials | Open | 0.0010154 | 8.13 | 177.5442
292 | 2023-05-08 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:02 | 19:13 | 13.1833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:05 | 6:05 | 6:05 | 19:16 | 0 | 0 |  | 13.1833 | Waiting for Materials | Open | 0.0010154 | 8.13 | 177.5442
293 | 2023-05-08 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:02 | 19:13 | 13.1833 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:05 | 6:05 | 6:05 | 19:16 | 0 | 0 |  | 13.1833 | Waiting for Materials | Open | 0.0006161 | 8.13 | 107.7234
294 | 2023-05-08 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:02 | 19:13 | 13.1833 | IS10 | INV2 | M1 |  |  |  | 1 | 1 | IS10INV2M1 | 1973.16 | 0.5888% | Inverter | Inv_tripped in IDC protn. | Inv Tripped in Branch rev IDC High Fault | 12:23 | 12:23 | 12:23 | 13:50 | 0 | 0 | 1.45 | 1.45 | Check related parameters on HMI then discussed with sungrow team and inverter start | Close | 0.0085382 | 1.53 | 2554.3573
295 | 2023-05-08 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:02 | 19:13 | 13.1833 | IS10 | INV2 | M2 |  |  |  | 1 | 1 | IS10INV2M2 | 2223.72 | 0.6636% | Inverter | Inv_tripped in IDC protn. | Inv Tripped in Branch rev IDC High Fault | 12:23 | 12:23 | 12:23 | 13:50 | 0 | 0 | 1.45 | 1.45 | Check related parameters on HMI then discussed with sungrow team and inverter start | Close | 0.0096224 | 1.53 | 2878.7201
296 | 2023-05-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:07 | 19:17 | 13.1667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:07 | 6:07 | 6:07 | 19:17 | 0 | 0 |  | 13.1667 | Waiting for Materials | Open | 0.0010141 | 8 | 174.7052
297 | 2023-05-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:07 | 19:17 | 13.1667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:07 | 6:07 | 6:07 | 19:17 | 0 | 0 |  | 13.1667 | Waiting for Materials | Open | 0.0010141 | 8 | 174.7052
298 | 2023-05-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:07 | 19:17 | 13.1667 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:07 | 6:07 | 6:07 | 19:17 | 0 | 0 |  | 13.1667 | Waiting for Materials | Open | 0.00061533 | 8 | 106.0009
299 | 2023-05-10 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:06 | 19:18 | 13.2 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:06 | 6:06 | 6:06 | 19:18 | 0 | 0 |  | 13.2 | Waiting for Materials | Open | 0.0010167 | 7.52 | 164.2229
300 | 2023-05-10 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:06 | 19:18 | 13.2 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:06 | 6:06 | 6:06 | 19:18 | 0 | 0 |  | 13.2 | Waiting for Materials | Open | 0.0010167 | 7.52 | 164.2229
301 | 2023-05-10 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:06 | 19:18 | 13.2 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:06 | 6:06 | 6:06 | 19:18 | 0 | 0 |  | 13.2 | Waiting for Materials | Open | 0.00061688 | 7.52 | 99.6409
302 | 2023-05-10 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:06 | 19:18 | 13.2 | IS3 | INV2 | M2 |  |  |  | 1 | 1 | IS3INV2M2 | 2090.61 | 0.6239% | Inverter | Inv_tripped in PDP protection | Inv unit tripped under PDP protection | 12:08 | 12:08 | 12:08 | 19:18 | 0 | 0 | 7.1667 | 7.1667 | Checked related connection and parameters on HMI as per discussion with sungrow team then changed PA Card and cheked related connection. | Close | 0.044712 | 4.2 | 7429.3398
303 | 2023-05-10 | FY24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 6:06 | 19:18 | 13.2 | IS3 | INV2 | M1 |  |  |  | 1 | 1 | IS3INV2M1 | 2090.61 | 0.6239% | Inverter | Inv_Manual Stop | Unit manual stop for rectification or unit-2 fault | 12:37 | 12:37 | 12:37 | 12:57 | 0 | 0 | 0.33333 | 0.33333 | Unit manual stop for rectification or unit-2 fault | Close | 0.0020796 | 0.32 | 566.0449
304 | 2023-05-11 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:16 | 13.1833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:06 | 6:06 | 6:06 | 19:18 | 0 | 0 |  | 13.2 | Waiting for Materials | Open | 0.0010167 | 6.77 | 147.8443
305 | 2023-05-11 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:16 | 13.1833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:06 | 6:06 | 6:06 | 19:18 | 0 | 0 |  | 13.2 | Waiting for Materials | Open | 0.0010167 | 6.77 | 147.8443
306 | 2023-05-11 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:16 | 13.1833 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:06 | 6:06 | 6:06 | 19:18 | 0 | 0 |  | 13.2 | Waiting for Materials | Open | 0.00061688 | 6.77 | 89.7033
307 | 2023-05-11 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:16 | 13.1833 | IS3 | INV2 | M2 |  |  |  | 1 | 1 | IS3INV2M2 | 2090.61 | 0.6239% | Inverter | Inv_tripped in PDP protection | Inv unit tripped under PDP protection | 8:22 | 8:22 | 8:22 | 19:16 | 0 | 0 |  | 10.9 | Checked related connection and parameters on HMI as per discussion with sungrow team then found reactor faulty waiting for material.. | Open | 0.068004 | 6 | 10613.3426
308 | 2023-05-11 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:16 | 13.1833 | IS3 | INV2 | M1 |  |  |  | 1 | 1 | IS3INV2M1 | 2090.61 | 0.6239% | Inverter | Inv_Manual Stop | Unit manual stop for rectification or unit-2 fault | 9:26 | 9:26 | 9:26 | 9:34 | 0 | 0 | 0.13333 | 0.13333 | Unit manual stop for rectification or unit-2 fault | Close | 0.00083186 | 0.13 | 229.9558
309 | 2023-05-11 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:16 | 13.1833 | IS3 |  |  |  |  | Tx | 0 | 1 | IS3Tx | 16766.64 | 5.004% | IDT | Tx_Manually tripped for IR test at Inverter AC section | IDT Manually tripped for IR test at Inverter AC section | 12:54 | 12:54 | 12:54 | 13:51 | 0 | 0 | 0.95 | 0.95 | IDT Manually tripped for IR test done and IDT charge | Close | 0.047534 | 0.95 | 13477.1343
310 | 2023-05-12 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:03 | 19:14 | 13.1833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:03 | 6:03 | 6:03 | 19:14 | 0 | 0 |  | 13.1833 | Waiting for Materials | Open | 0.0010154 | 7.25 | 158.3266
311 | 2023-05-12 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:03 | 19:14 | 13.1833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:03 | 6:03 | 6:03 | 19:14 | 0 | 0 |  | 13.1833 | Waiting for Materials | Open | 0.0010154 | 7.25 | 158.3266
312 | 2023-05-12 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:03 | 19:14 | 13.1833 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:03 | 6:03 | 6:03 | 19:14 | 0 | 0 |  | 13.1833 | Waiting for Materials | Open | 0.0006161 | 7.25 | 96.0633
313 | 2023-05-12 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:03 | 19:14 | 13.1833 | IS3 | INV2 | M2 |  |  |  | 1 | 1 | IS3INV2M2 | 2090.61 | 0.6239% | Inverter | Inv_tripped in PDP protection | Inv unit tripped under PDP protection | 6:03 | 6:03 | 6:03 | 19:14 | 0 | 0 | 13.1833 | 13.1833 | Checked related connection and parameters on HMI as per discussion with sungrow team then found reactor faulty waiting for material.. | Close | 0.08225 | 7.25 | 12824.4557
314 | 2023-05-13 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:04 | 19:12 | 13.1333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:04 | 6:04 | 6:04 | 19:14 | 0 | 0 |  | 13.1667 | Waiting for Materials | Open | 0.0010141 | 7.92 | 172.9582
315 | 2023-05-13 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:04 | 19:12 | 13.1333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:04 | 6:04 | 6:04 | 19:14 | 0 | 0 |  | 13.1667 | Waiting for Materials | Open | 0.0010141 | 7.92 | 172.9582
316 | 2023-05-13 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:04 | 19:12 | 13.1333 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:04 | 6:04 | 6:04 | 19:14 | 0 | 0 |  | 13.1667 | Waiting for Materials | Open | 0.00061533 | 7.92 | 104.9409
317 | 2023-05-13 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:04 | 19:12 | 13.1333 | IS3 | INV2 | M2 |  |  |  | 1 | 1 | IS3INV2M2 | 2090.61 | 0.6239% | Inverter | Inv Unit_AC Coil failure | Inverter tripped in AC switch breaking | 6:04 | 6:04 | 6:04 | 7:27 | 0 | 0 | 1.3833 | 1.3833 | Checked related connection and parameters on HMI as per discussion with sungrow team then found AC breaker open the reset it and inverter start.. | Close | 0.0086305 | 0.13 | 229.9558
318 | 2023-05-14 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:04 | 19:19 | 13.25 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:04 | 6:04 | 6:04 | 19:19 | 0 | 0 |  | 13.25 | Waiting for Materials | Open | 0.0010206 | 7.11 | 155.2693
319 | 2023-05-14 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:04 | 19:19 | 13.25 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:04 | 6:04 | 6:04 | 19:19 | 0 | 0 |  | 13.25 | Waiting for Materials | Open | 0.0010206 | 7.11 | 155.2693
320 | 2023-05-14 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:04 | 19:19 | 13.25 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:04 | 6:04 | 6:04 | 19:19 | 0 | 0 |  | 13.25 | Waiting for Materials | Open | 0.00061922 | 7.11 | 94.2083
321 | 2023-05-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:11 | 13.1 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:04 | 6:04 | 6:04 | 19:19 | 0 | 0 |  | 13.25 | Waiting for Materials | Open | 0.0010206 | 7.05 | 153.959
322 | 2023-05-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:11 | 13.1 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:04 | 6:04 | 6:04 | 19:19 | 0 | 0 |  | 13.25 | Waiting for Materials | Open | 0.0010206 | 7.05 | 153.959
323 | 2023-05-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:11 | 13.1 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:04 | 6:04 | 6:04 | 19:19 | 0 | 0 |  | 13.25 | Waiting for Materials | Open | 0.00061922 | 7.05 | 93.4133
324 | 2023-05-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:11 | 13.1 | [5 empty] | Power_Tx1 | 0 | 1 | Power_Tx1 | 167322.75 | 49.93% | PTR | Triped in Overvoltage | Triped in Overvoltage | 12:39 | 12:39 | 12:39 | 13:24 | 0 | 0 | 0.75 | 0.75 | Check related parameters on HMI & Bay relay, voltage normlised then restored | Close | 0.3745 | 0.7 | 99101.6634
325 | 2023-05-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:11 | 13.1 | [5 empty] | Power_Tx2 | 0 | 1 | Power_Tx2 | 167768.915 | 50.07% | PTR | Triped in Overvoltage | Triped in Overvoltage | 12:39 | 12:39 | 12:39 | 13:24 | 0 | 0 | 0.75 | 0.75 | Check related parameters on HMI & Bay relay, voltage normlised then restored | Close | 0.3755 | 0.7 | 99365.9173
326 | 2023-05-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:11 | 13.1 | IS1 | INV1 | M1 |  |  |  | 1 | 1 | IS1INV1M1 | 2064.8 | 0.6162% | Inverter | Inv_Tripped in Mod. Fault | Inverter tripped in Module fault | 13:25 | 13:25 | 13:25 | 14:33 | 0 | 0 | 1.1333 | 1.1333 | Check related parameters on HMI then discussed with sungrow team and inverter start | Close | 0.0069835 | 1.11 | 1939.228
327 | 2023-05-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:11 | 13.1 | IS1 | INV1 | M2 |  |  |  | 1 | 1 | IS1INV1M2 | 2090.61 | 0.6239% | Inverter | Inv_Tripped in Mod. Fault | Inverter tripped in Module fault | 13:25 | 13:25 | 13:25 | 14:33 | 0 | 0 | 1.1333 | 1.1333 | Check related parameters on HMI then discussed with sungrow team and inverter start | Close | 0.0070708 | 1.11 | 1963.4684
328 | 2023-05-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:11 | 13.1 | IS5 | INV1 | M2 |  |  |  | 1 | 1 | IS5INV1M2 | 2090.61 | 0.6239% | Inverter | Inv_Tripped in Mod. Fault | Inverter tripped in Module fault | 13:25 | 13:25 | 13:25 | 14:09 | 0 | 0 | 0.73333 | 0.73333 | Check related parameters on HMI then discussed with sungrow team and inverter start | Close | 0.0045752 | 0.71 | 1255.9122
329 | 2023-05-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:11 | 13.1 | IS10 | INV3 | M1 |  |  |  | 1 | 1 | IS10INV3M1 | 1941.84 | 0.5795% | Inverter | Inv_Tripped in Mod. Fault | Inverter tripped in Module fault | 13:25 | 13:25 | 13:25 | 14:05 | 0 | 0 | 0.66667 | 0.66667 | Check related parameters on HMI then discussed with sungrow team and inverter start | Close | 0.0038633 | 0.65 | 1067.9593
330 | 2023-05-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:11 | 13.1 | IS10 | INV3 | M2 |  |  |  | 1 | 1 | IS10INV3M2 | 2255.04 | 0.673% | Inverter | Inv_Tripped in Mod. Fault | Inverter tripped in Module fault | 13:25 | 13:25 | 13:25 | 14:08 | 0 | 0 | 0.71667 | 0.71667 | Check related parameters on HMI then discussed with sungrow team and inverter start | Close | 0.0048229 | 0.69 | 1316.5315
331 | 2023-05-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:11 | 13.1 | IS11 | INV1 | M1 |  |  |  | 1 | 1 | IS11INV1M1 | 2023.04 | 0.6037% | Inverter | Inv_Tripped in Mod. Fault | Inverter tripped in Module fault | 13:25 | 13:25 | 13:25 | 14:12 | 0 | 0 | 0.78333 | 0.78333 | Check related parameters on HMI then discussed with sungrow team and inverter start | Close | 0.0047292 | 0.75 | 1283.789
332 | 2023-05-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:11 | 13.1 | IS11 | INV1 | M2 |  |  |  | 1 | 1 | IS11INV1M2 | 2212.7 | 0.6603% | Inverter | Inv_Tripped in Mod. Fault | Inverter tripped in Module fault | 13:25 | 13:25 | 13:25 | 14:10 | 0 | 0 | 0.75 | 0.75 | Check related parameters on HMI then discussed with sungrow team and inverter start | Close | 0.0049525 | 0.72 | 1347.9784
333 | 2023-05-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:11 | 13.1 | IS11 | INV2 | M1 |  |  |  | 1 | 1 | IS11INV2M1 | 2275.92 | 0.6792% | Inverter | Inv_Tripped in Mod. Fault | Inverter tripped in Module fault | 13:25 | 13:25 | 13:25 | 14:09 | 0 | 0 | 0.73333 | 0.73333 | Check related parameters on HMI then discussed with sungrow team and inverter start | Close | 0.0049808 | 0.7 | 1347.9784
334 | 2023-05-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:11 | 13.1 | IS11 | INV2 | M2 |  |  |  | 1 | 1 | IS11INV2M2 | 2038.845 | 0.6084% | Inverter | Inv_Tripped in Mod. Fault | Inverter tripped in Module fault | 13:25 | 13:25 | 13:25 | 14:10 | 0 | 0 | 0.75 | 0.75 | Check related parameters on HMI then discussed with sungrow team and inverter start | Close | 0.0045633 | 0.72 | 1242.0658
335 | 2023-05-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:11 | 13.1 | IS13 | INV1 | M1 |  |  |  | 1 | 1 | IS13INV1M1 | 2004.48 | 0.5982% | Inverter | Inv_Tripped in Mod. Fault | Inverter tripped in Module fault | 13:25 | 13:25 | 13:25 | 14:20 | 0 | 0 | 0.91667 | 0.91667 | Check related parameters on HMI then discussed with sungrow team and inverter start | Close | 0.0054834 | 0.89 | 1509.4532
336 | 2023-05-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:11 | 13.1 | IS13 | INV1 | M2 |  |  |  | 1 | 1 | IS13INV1M2 | 2004.48 | 0.5982% | Inverter | Inv_Tripped in Mod. Fault | Inverter tripped in Module fault | 13:25 | 13:25 | 13:25 | 14:20 | 0 | 0 | 0.91667 | 0.91667 | Check related parameters on HMI then discussed with sungrow team and inverter start | Close | 0.0054834 | 0.89 | 1509.4532
337 | 2023-05-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:11 | 13.1 | IS13 | INV4 | M1 |  |  |  | 1 | 1 | IS13INV4M1 | 2192.4 | 0.6543% | Inverter | Inv_Tripped in Mod. Fault | Inverter tripped in Module fault | 13:25 | 13:25 | 13:25 | 14:21 | 0 | 0 | 0.93333 | 0.93333 | Check related parameters on HMI then discussed with sungrow team and inverter start | Close | 0.0061065 | 0.89 | 1650.9644
338 | 2023-05-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:11 | 13.1 | IS13 | INV4 | M2 |  |  |  | 1 | 1 | IS13INV4M2 | 2004.48 | 0.5982% | Inverter | Inv_Tripped in Mod. Fault | Inverter tripped in Module fault | 13:25 | 13:25 | 13:25 | 14:21 | 0 | 0 | 0.93333 | 0.93333 | Check related parameters on HMI then discussed with sungrow team and inverter start | Close | 0.0055831 | 0.89 | 1509.4532
339 | 2023-05-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:11 | 13.1 | IS14 | INV1 | M1 |  |  |  | 1 | 1 | IS14INV1M1 | 2223.72 | 0.6636% | Inverter | Inv_Tripped in Mod. Fault | Inverter tripped in Module fault | 13:25 | 13:25 | 13:25 | 14:32 | 0 | 0 | 1.1167 | 1.1167 | Check related parameters on HMI then discussed with sungrow team and inverter start | Close | 0.0074104 | 1.09 | 2050.8529
340 | 2023-05-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:11 | 13.1 | IS14 | INV1 | M2 |  |  |  | 1 | 1 | IS14INV1M2 | 1910.52 | 0.5701% | Inverter | Inv_Tripped in Mod. Fault | Inverter tripped in Module fault | 13:25 | 13:25 | 13:25 | 14:32 | 0 | 0 | 1.1167 | 1.1167 | Check related parameters on HMI then discussed with sungrow team and inverter start | Close | 0.0063667 | 1.09 | 1762.0004
341 | 2023-05-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:11 | 13.1 | IS15 | INV2 | M1 |  |  |  | 1 | 1 | IS15INV2M1 | 2004.48 | 0.5982% | Inverter | Inv_Tripped in Mod. Fault | Inverter tripped in Module fault | 13:25 | 13:25 | 13:25 | 15:09 | 0 | 0 | 1.7333 | 1.7333 | Check related parameters on HMI then discussed with sungrow team and inverter start | Close | 0.010369 | 1.69 | 2866.265
342 | 2023-05-16 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:08 | 19:11 | 13.05 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:08 | 6:08 | 6:08 | 19:11 | 0 | 0 |  | 13.05 | Waiting for Materials | Open | 0.0010052 | 7.54 | 164.6597
343 | 2023-05-16 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:08 | 19:11 | 13.05 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:08 | 6:08 | 6:08 | 19:11 | 0 | 0 |  | 13.05 | Waiting for Materials | Open | 0.0010052 | 7.54 | 164.6597
344 | 2023-05-16 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:08 | 19:11 | 13.05 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:08 | 6:08 | 6:08 | 19:11 | 0 | 0 |  | 13.05 | Waiting for Materials | Open | 0.00060987 | 7.54 | 99.9059
345 | 2023-05-17 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:11 | 19:16 | 13.0833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:11 | 6:11 | 6:11 | 19:16 | 0 | 0 |  | 13.0833 | Waiting for Materials | Open | 0.0010077 | 7.43 | 162.2575
346 | 2023-05-17 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:11 | 19:16 | 13.0833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:11 | 6:11 | 6:11 | 19:16 | 0 | 0 |  | 13.0833 | Waiting for Materials | Open | 0.0010077 | 7.43 | 162.2575
347 | 2023-05-17 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:11 | 19:16 | 13.0833 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:11 | 6:11 | 6:11 | 19:16 | 0 | 0 |  | 13.0833 | Waiting for Materials | Open | 0.00061143 | 7.43 | 98.4484
348 | 2023-05-18 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:07 | 19:15 | 13.1333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:07 | 6:07 | 6:07 | 19:15 | 0 | 0 |  | 13.1333 | Waiting for Materials | Open | 0.0010116 | 7.24 | 158.1082
349 | 2023-05-18 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:07 | 19:15 | 13.1333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:07 | 6:07 | 6:07 | 19:15 | 0 | 0 |  | 13.1333 | Waiting for Materials | Open | 0.0010116 | 7.24 | 158.1082
350 | 2023-05-18 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:07 | 19:15 | 13.1333 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:07 | 6:07 | 6:07 | 19:15 | 0 | 0 |  | 13.1333 | Waiting for Materials | Open | 0.00061377 | 7.24 | 95.9308
351 | 2023-05-19 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:03 | 19:17 | 13.2333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:03 | 6:03 | 6:03 | 19:17 | 0 | 0 |  | 13.2333 | Waiting for Materials | Open | 0.0010193 | 7.46 | 162.9126
352 | 2023-05-19 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:03 | 19:17 | 13.2333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:03 | 6:03 | 6:03 | 19:17 | 0 | 0 |  | 13.2333 | Waiting for Materials | Open | 0.0010193 | 7.46 | 162.9126
353 | 2023-05-19 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:03 | 19:17 | 13.2333 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:03 | 6:03 | 6:03 | 19:17 | 0 | 0 |  | 13.2333 | Waiting for Materials | Open | 0.00061844 | 7.46 | 98.8459
354 | 2023-05-20 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:18 | 13.2167 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:05 | 6:05 | 6:05 | 19:18 | 0 | 0 |  | 13.2167 | Waiting for Materials | Open | 0.001018 | 7.76 | 169.4641
355 | 2023-05-20 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:18 | 13.2167 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:05 | 6:05 | 6:05 | 19:18 | 0 | 0 |  | 13.2167 | Waiting for Materials | Open | 0.001018 | 7.76 | 169.4641
356 | 2023-05-20 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:18 | 13.2167 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:05 | 6:05 | 6:05 | 19:18 | 0 | 0 |  | 13.2167 | Waiting for Materials | Open | 0.00061766 | 7.76 | 102.8209
357 | 2023-05-21 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:04 | 19:16 | 13.2 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:04 | 6:04 | 6:04 | 19:16 | 0 | 0 |  | 13.2 | Waiting for Materials | Open | 0.0010167 | 7.82 | 170.7744
358 | 2023-05-21 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:04 | 19:16 | 13.2 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:04 | 6:04 | 6:04 | 19:16 | 0 | 0 |  | 13.2 | Waiting for Materials | Open | 0.0010167 | 7.82 | 170.7744
359 | 2023-05-21 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:04 | 19:16 | 13.2 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:04 | 6:04 | 6:04 | 19:16 | 0 | 0 |  | 13.2 | Waiting for Materials | Open | 0.00061688 | 7.82 | 103.6159
360 | 2023-05-22 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:08 | 19:15 | 13.1167 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:08 | 6:08 | 6:08 | 19:15 | 0 | 0 |  | 13.1167 | Waiting for Materials | Open | 0.0010103 | 7.89 | 172.303
361 | 2023-05-22 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:08 | 19:15 | 13.1167 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:08 | 6:08 | 6:08 | 19:15 | 0 | 0 |  | 13.1167 | Waiting for Materials | Open | 0.0010103 | 7.89 | 172.303
362 | 2023-05-22 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:08 | 19:15 | 13.1167 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:08 | 6:08 | 6:08 | 19:15 | 0 | 0 |  | 13.1167 | Waiting for Materials | Open | 0.00061299 | 7.89 | 104.5434
363 | 2023-05-23 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:10 | 19:15 | 13.0833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:10 | 6:10 | 6:10 | 19:15 | 0 | 0 |  | 13.0833 | Waiting for Materials | Open | 0.0010077 | 7.31 | 159.6369
364 | 2023-05-23 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:10 | 19:15 | 13.0833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:10 | 6:10 | 6:10 | 19:15 | 0 | 0 |  | 13.0833 | Waiting for Materials | Open | 0.0010077 | 7.31 | 159.6369
365 | 2023-05-23 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:10 | 19:15 | 13.0833 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:10 | 6:10 | 6:10 | 19:15 | 0 | 0 |  | 13.0833 | Waiting for Materials | Open | 0.00061143 | 7.31 | 96.8583
366 | 2023-05-24 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:03 | 19:16 | 13.2167 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:03 | 6:03 | 6:03 | 19:16 | 0 | 0 |  | 13.2167 | Waiting for Materials | Open | 0.001018 | 7.48 | 163.3494
367 | 2023-05-24 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:03 | 19:16 | 13.2167 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:03 | 6:03 | 6:03 | 19:16 | 0 | 0 |  | 13.2167 | Waiting for Materials | Open | 0.001018 | 7.48 | 163.3494
368 | 2023-05-24 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:03 | 19:16 | 13.2167 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:03 | 6:03 | 6:03 | 19:16 | 0 | 0 |  | 13.2167 | Waiting for Materials | Open | 0.00061766 | 7.48 | 99.1109
369 | 2023-05-25 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:07 | 18:45 | 12.6333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:10 | 6:10 | 6:10 | 19:15 | 0 | 0 |  | 13.0833 | Waiting for Materials | Open | 0.0010077 | 6.76 | 147.6259
370 | 2023-05-25 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:07 | 18:45 | 12.6333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:10 | 6:10 | 6:10 | 19:15 | 0 | 0 |  | 13.0833 | Waiting for Materials | Open | 0.0010077 | 6.76 | 147.6259
371 | 2023-05-25 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:07 | 18:45 | 12.6333 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:10 | 6:10 | 6:10 | 19:15 | 0 | 0 |  | 13.0833 | Waiting for Materials | Open | 0.00061143 | 6.76 | 89.5708
372 | 2023-05-25 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:07 | 18:45 | 12.6333 | IS10 |  |  |  |  | Tx | 0 | 1 | IS10Tx | 16756.2 | 5% | IDT | LV 4 Winding trip | LV 4 Winding trip | 13:20 | 13:20 | 13:20 | 14:09 | 0 | 0 | 0.81667 | 0.81667 | Related parameter checked on alarm and trip setting on WTI meter and checked related connection then IDT charged | Close | 0.040837 | 0.79 | 11200.3227
373 | 2023-05-26 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:17 | 13.2 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:05 | 6:05 | 6:05 | 19:17 | 0 | 0 |  | 13.2 | Waiting for Materials | Open | 0.0010167 | 6.92 | 151.12
374 | 2023-05-26 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:17 | 13.2 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:05 | 6:05 | 6:05 | 19:17 | 0 | 0 |  | 13.2 | Waiting for Materials | Open | 0.0010167 | 6.92 | 151.12
375 | 2023-05-26 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:17 | 13.2 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:05 | 6:05 | 6:05 | 19:17 | 0 | 0 |  | 13.2 | Waiting for Materials | Open | 0.00061688 | 6.92 | 91.6908
376 | 2023-05-26 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:17 | 13.2 | IS5 |  |  |  |  | Tx | 0 | 1 | IS5Tx | 16724.88 | 4.991% | IDT | Tx_Manually tripped for AC Coil replacement at Inverter AC section | IDT Manually tripped for AC Coil replacement at Inverter AC section | 8:14 | 8:14 | 8:14 | 8:41 | 0 | 0 | 0.45 | 0.45 | IDT Manually tripped for AC Coil replacement at Inverter AC section | Close | 0.02246 | 0.41 | 5801.9606
377 | 2023-05-26 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:17 | 13.2 | IS5 | INV3 | M2 |  |  |  | 1 | 1 | IS5INV3M2 | 2090.61 | 0.6239% | Inverter | Inv Unit_AC Coil failure | AC Switch breaking | 6:05 | 6:05 | 6:05 | 8:14 | 0 | 0 | 2.15 | 2.15 | AC Switch breaking | Close | 0.013414 | 0.12 | 212.2669
378 | 2023-05-26 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:17 | 13.2 | IS5 | INV3 | M1 |  |  |  | 1 | 1 | IS5INV3M1 | 2090.61 | 0.6239% | Inverter | Inverter Unit Manual stop for AC Coil replacement | Inverter Unit Manual stop for AC Coil replacement | 9:19 | 9:19 | 9:19 | 9:48 | 0 | 0 | 0.48333 | 0.48333 | Inverter Unit Manual stop for AC Coil replacement | Close | 0.0030155 | 0.38 | 672.1784
379 | 2023-05-26 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:17 | 13.2 | IS5 | INV3 | M1 |  |  |  | 1 | 1 | IS5INV3M1 | 2090.61 | 0.6239% | Inverter | Inverter Unit Manual stop for AC Coil replacement | Inverter Unit Manual stop for AC Coil replacement | 7:54 | 7:54 | 7:54 | 8:47 | 0 | 0 | 0.88333 | 0.88333 | Inverter Unit Manual stop for AC Coil replacement | Close | 0.0055111 | 0.83 | 1468.1791
380 | 2023-05-26 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:05 | 19:17 | 13.2 | IS5 | INV3 | M2 |  |  |  | 1 | 1 | IS5INV3M2 | 2090.61 | 0.6239% | Inverter | Inv Unit_AC Coil failure | AC Switch breaking | 8:14 | 8:14 | 8:14 | 9:48 | 0 | 0 | 1.5667 | 1.5667 | AC Switch breaking | Close | 0.0097743 | 0.46 | 813.6896
381 | 2023-05-27 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:03 | 19:17 | 13.2333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:03 | 6:03 | 6:03 | 19:17 | 0 | 0 |  | 13.2333 | Waiting for Materials | Open | 0.0010193 | 6.18 | 134.9598
382 | 2023-05-27 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:03 | 19:17 | 13.2333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:03 | 6:03 | 6:03 | 19:17 | 0 | 0 |  | 13.2333 | Waiting for Materials | Open | 0.0010193 | 6.18 | 134.9598
383 | 2023-05-27 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:03 | 19:17 | 13.2333 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:03 | 6:03 | 6:03 | 19:17 | 0 | 0 |  | 13.2333 | Waiting for Materials | Open | 0.00061844 | 6.18 | 81.8857
384 | 2023-05-27 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:03 | 19:17 | 13.2333 | IS2 | INV1 | M2 |  |  |  | 1 | 1 | IS2INV1M2 | 2090.61 | 0.6239% | Inverter | Inv_tripped of GFDI | Inv unit tripped under GFDI Pro fault | 12:07 | 12:07 | 12:07 | 18:03 | 0 | 0 | 5.9333 | 5.9333 | checking related connection and parameters discussion with sungrow team and checked floating value of all SCB found ok then we Measured IR value of all inverter DC cable of unit 2, were one of the positive cable SCB 03 IR value low as compare to other so we dissconnect the cable from inverter unit, now SCB OFF. | Close | 0.037018 | 3.85 | 6810.2282
385 | 2023-05-27 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:03 | 19:17 | 13.2333 | IS2 | INV1 | M1 |  |  |  | 1 | 1 | IS2INV1M1 | 2090.61 | 0.6239% | Inverter | Inverter Unit Manual stop for fault rectification | Inverter Unit Manual stop for fault rectification | 12:44 | 12:44 | 12:44 | 13:00 | 0 | 0 | 0.26667 | 0.26667 | Inverter Unit Manual stop for fault rectification | Close | 0.0016637 | 0.24 | 424.5337
386 | 2023-05-27 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:03 | 19:17 | 13.2333 | IS2 | INV1 | M1 |  |  |  | 1 | 1 | IS2INV1M1 | 2090.61 | 0.6239% | Inverter | Inverter Unit Manual stop for fault rectification | Inverter Unit Manual stop for fault rectification | 13:50 | 13:50 | 13:50 | 13:55 | 0 | 0 | 0.083333 | 0.083333 | Inverter Unit Manual stop for fault rectification | Close | 0.00051991 | 0.05 | 88.4445
387 | 2023-05-27 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:03 | 19:17 | 13.2333 | IS2 | INV1 | M1 |  |  |  | 1 | 1 | IS2INV1M1 | 2090.61 | 0.6239% | Inverter | Inverter Unit Manual stop for fault rectification | Inverter Unit Manual stop for fault rectification | 14:36 | 14:36 | 14:36 | 14:46 | 0 | 0 | 0.16667 | 0.16667 | Inverter Unit Manual stop for fault rectification | Close | 0.0010398 | 0.12 | 212.2669
388 | 2023-05-28 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:04 | 19:05 | 13.0167 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:04 | 6:04 | 6:04 | 19:05 | 0 | 0 |  | 13.0167 | Waiting for Materials | Open | 0.0010026 | 4.84 | 105.6967
389 | 2023-05-28 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:04 | 19:05 | 13.0167 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:04 | 6:04 | 6:04 | 19:05 | 0 | 0 |  | 13.0167 | Waiting for Materials | Open | 0.0010026 | 4.84 | 105.6967
390 | 2023-05-28 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:04 | 19:05 | 13.0167 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:04 | 6:04 | 6:04 | 19:05 | 0 | 0 |  | 13.0167 | Waiting for Materials | Open | 0.00060832 | 4.84 | 64.1306
391 | 2023-05-28 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:04 | 19:05 | 13.0167 | IS2 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS2INV1M2SCB4 | 232.29 | 0.06932% | SCB | Inv_tripped of GFDI | Positive DC Cable IR value lower then other cables due to this GFDI Fault happened, so we dissconect the cable from inv unit | 6:04 | 6:04 | 6:04 | 19:05 | 0 | 0 |  | 13.0167 | Positive cable dissconect from inv unit | Open | 0.0090233 | 4.84 | 951.27
392 | 2023-05-29 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:00 | 19:19 | 13.3167 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:00 | 6:00 | 6:00 | 19:19 | 0 | 0 |  | 13.3167 | Waiting for Materials | Open | 0.0010257 | 6.73 | 146.9708
393 | 2023-05-29 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:00 | 19:19 | 13.3167 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:00 | 6:00 | 6:00 | 19:19 | 0 | 0 |  | 13.3167 | Waiting for Materials | Open | 0.0010257 | 6.73 | 146.9708
394 | 2023-05-29 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:00 | 19:19 | 13.3167 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:00 | 6:00 | 6:00 | 19:19 | 0 | 0 |  | 13.3167 | Waiting for Materials | Open | 0.00062234 | 6.73 | 89.1733
395 | 2023-05-29 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:00 | 19:19 | 13.3167 | IS2 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS2INV1M2SCB4 | 232.29 | 0.06932% | SCB | Inv_tripped of GFDI | Positive DC Cable IR value lower then other cables due to this GFDI Fault happened, so we dissconect the cable from inv unit | 6:00 | 6:00 | 6:00 | 19:19 | 0 | 0 |  | 13.3167 | Positive cable dissconect from inv unit | Open | 0.0092313 | 6.73 | 1322.737
396 | 2023-05-30 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:21 | 19:26 | 13.0833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:21 | 6:21 | 6:21 | 19:26 | 0 | 0 |  | 13.0833 | Waiting for Materials | Open | 0.0010077 | 3.26 | 71.1924
397 | 2023-05-30 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:21 | 19:26 | 13.0833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:21 | 6:21 | 6:21 | 19:26 | 0 | 0 |  | 13.0833 | Waiting for Materials | Open | 0.0010077 | 3.26 | 71.1924
398 | 2023-05-30 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:21 | 19:26 | 13.0833 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:21 | 6:21 | 6:21 | 19:26 | 0 | 0 |  | 13.0833 | Waiting for Materials | Open | 0.00061143 | 3.26 | 43.1954
399 | 2023-05-30 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:21 | 19:26 | 13.0833 | IS2 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS2INV1M2SCB4 | 232.29 | 0.06932% | SCB | Inv_tripped of GFDI | Positive DC Cable IR value lower then other cables due to this GFDI Fault happened, so we dissconect the cable from inv unit | 6:21 | 6:21 | 6:21 | 19:26 | 0 | 0 |  | 13.0833 | Positive cable dissconect from inv unit | Open | 0.0090696 | 3.26 | 640.7314
400 | 2023-05-30 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:21 | 19:26 | 13.0833 | IS1 | INV1 | M1 |  |  |  | 1 | 1 | IS1INV1M1 | 2064.8 | 0.6162% | Module | Inv_tripped of GFDI | Inv unit tripped under GFDI Pro fault | 6:21 | 6:21 | 6:21 | 14:53 | 0 | 0 | 8.5333 | 8.5333 | checking related connection and parameters discussion with sungrow team and checked floating value of all SCB found ok then we Measured IR value of all inverter DC cable of unit 2, were one of the positive cable SCB 08 IR value low as compare to other so we dissconnect the cable from inverter unit, now SCB OFF. | Close | 0.052582 | 1.96 | 3424.2225
401 | 2023-05-30 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:21 | 19:26 | 13.0833 | IS3 |  |  |  |  | Tx | 0 | 1 | IS3Tx | 16766.64 | 5.004% | IDT | IDT tripped in Diff. Protection | We checked related parameter on differntial protection relay, were we observed LV 3 B phase current recorded high as compare to other phase so we open LV box 3, were we notice B phase CT wire short with busbar and wire damage also R phase CT cracked | 8:54 | 8:54 | 8:54 | 11:49 | 0 | 0 | 2.9167 | 2.9167 | Rectification done | Close | 0.14594 | 0.69 | 9788.6554
402 | 2023-05-30 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 6:21 | 19:26 | 13.0833 | IS1 | INV1 | M1 | SCB8 |  |  | 1 | 1 | IS1INV1M1SCB8 | 232.29 | 0.06932% | SCB | Inv_tripped of GFDI | Positive DC Cable IR value lower then other cables due to this GFDI Fault happened, so we dissconect the cable from inv unit | 14:53 | 14:53 | 14:53 | 19:26 | 0 | 0 |  | 4.55 | Positive cable dissconect from inv unit | Open | 0.0031541 | 3.26 | 640.7314
403 | 2023-05-31 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 5:53 | 19:29 | 13.6 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 5:53 | 5:53 | 5:53 | 19:29 | 0 | 0 |  | 13.6 | Waiting for Materials | Open | 0.0010475 | 7.39 | 161.384
404 | 2023-05-31 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 5:53 | 19:29 | 13.6 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 5:53 | 5:53 | 5:53 | 19:29 | 0 | 0 |  | 13.6 | Waiting for Materials | Open | 0.0010475 | 7.39 | 161.384
405 | 2023-05-31 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 5:53 | 19:29 | 13.6 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 5:53 | 5:53 | 5:53 | 19:29 | 0 | 0 |  | 13.6 | Waiting for Materials | Open | 0.00063558 | 7.39 | 97.9184
406 | 2023-05-31 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 5:53 | 19:29 | 13.6 | IS2 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS2INV1M2SCB4 | 232.29 | 0.06932% | SCB | Inv_tripped of GFDI | Positive DC Cable IR value lower then other cables due to this GFDI Fault happened, so we dissconect the cable from inv unit | 5:53 | 5:53 | 5:53 | 19:29 | 0 | 0 | 13.6 | 13.6 | Positive DC cable jointing Done | Close | 0.0094277 | 7.39 | 1452.4556
407 | 2023-05-31 | FY24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 5:53 | 19:29 | 13.6 | IS1 | INV1 | M1 | SCB8 |  |  | 1 | 1 | IS1INV1M1SCB8 | 232.29 | 0.06932% | SCB | Inv_tripped of GFDI | Positive DC Cable IR value lower then other cables due to this GFDI Fault happened, so we dissconect the cable from inv unit | 5:53 | 5:53 | 5:53 | 19:29 | 0 | 0 | 13.6 | 13.6 | Positive DC cable jointing Done | Close | 0.0094277 | 7.39 | 1452.4556
408 | 2023-06-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:05 | 19:23 | 13.3 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:05 | 6:05 | 6:05 | 19:23 | 0 | 0 |  | 13.3 | Waiting for Materials | Open | 0.0010244 | 4.42 | 94.8232
409 | 2023-06-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:05 | 19:23 | 13.3 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:05 | 6:05 | 6:05 | 19:23 | 0 | 0 |  | 13.3 | Waiting for Materials | Open | 0.0010244 | 4.42 | 94.8232
410 | 2023-06-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:05 | 19:23 | 13.3 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:05 | 6:05 | 6:05 | 19:23 | 0 | 0 |  | 13.3 | Waiting for Materials | Open | 0.00062156 | 4.42 | 57.5332
411 | 2023-06-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:05 | 19:23 | 13.3 | IS3 | INV2 | M2 |  |  |  | 1 | 1 | IS3INV2M2 | 2090.61 | 0.6239% | Inverter | Inv Unit_AC Coil failure | AC Switch breaking | 6:05 | 6:05 | 6:05 | 8:29 | 0 | 0 | 2.4 | 2.4 | Inverter Unit Manual stop for AC Coil replacement done | Close | 0.014973 | 0.11 | 191.1482
412 | 2023-06-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:05 | 19:23 | 13.3 | IS3 | INV2 | M1 |  |  |  | 1 | 1 | IS3INV2M1 | 2090.61 | 0.6239% | Inverter | Inverter Unit Manual stop for AC Coil replacement | Inverter Unit Manual stop for AC Coil replacement | 7:55 | 7:55 | 7:55 | 8:29 | 0 | 0 | 0.56667 | 0.56667 | Inverter Unit Manual stop for AC Coil replacement done | Close | 0.0035354 | 0.11 | 191.1482
413 | 2023-06-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:05 | 19:23 | 13.3 | IS19 | INV2 | M1 |  |  |  | 1 | 1 | IS19INV2M1 | 2223.72 | 0.6636% | Inverter | Inv_Manual Key Stop | Inverter Key Stop | 6:05 | 6:05 | 6:05 | 7:39 | 0 | 0 | 1.5667 | 1.5667 | Inverter Key Stop | Close | 0.010397 | 0.14 | 258.7692
414 | 2023-06-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:05 | 19:23 | 13.3 | IS19 | INV2 | M2 |  |  |  | 1 | 1 | IS19INV2M2 | 2223.72 | 0.6636% | Inverter | Inv_Manual Key Stop | Inverter Key Stop | 6:05 | 6:05 | 6:05 | 7:39 | 0 | 0 | 1.5667 | 1.5667 | Inverter Key Stop | Close | 0.010397 | 0.14 | 258.7692
415 | 2023-06-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:08 | 19:29 | 13.35 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:08 | 6:08 | 6:08 | 19:29 | 0 | 0 |  | 13.35 | Waiting for Materials | Open | 0.0010283 | 6.76 | 145.0238
416 | 2023-06-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:08 | 19:29 | 13.35 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:08 | 6:08 | 6:08 | 19:29 | 0 | 0 |  | 13.35 | Waiting for Materials | Open | 0.0010283 | 6.76 | 145.0238
417 | 2023-06-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:08 | 19:29 | 13.35 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:08 | 6:08 | 6:08 | 19:29 | 0 | 0 |  | 13.35 | Waiting for Materials | Open | 0.00062389 | 6.76 | 87.992
418 | 2023-06-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:01 | 19:22 | 13.35 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:01 | 6:01 | 6:01 | 19:22 | 0 | 0 |  | 13.35 | Waiting for Materials | Open | 0.0010283 | 6.85 | 146.9546
419 | 2023-06-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:01 | 19:22 | 13.35 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:01 | 6:01 | 6:01 | 19:22 | 0 | 0 |  | 13.35 | Waiting for Materials | Open | 0.0010283 | 6.85 | 146.9546
420 | 2023-06-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:01 | 19:22 | 13.35 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:01 | 6:01 | 6:01 | 19:22 | 0 | 0 |  | 13.35 | Waiting for Materials | Open | 0.00062389 | 6.85 | 89.1634
421 | 2023-06-04 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:09 | 19:23 | 13.2333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:09 | 6:09 | 6:09 | 19:23 | 0 | 0 |  | 13.2333 | Waiting for Materials | Open | 0.0010193 | 7.13 | 152.9615
422 | 2023-06-04 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:09 | 19:23 | 13.2333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:09 | 6:09 | 6:09 | 19:23 | 0 | 0 |  | 13.2333 | Waiting for Materials | Open | 0.0010193 | 7.13 | 152.9615
423 | 2023-06-04 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:09 | 19:23 | 13.2333 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:09 | 6:09 | 6:09 | 19:23 | 0 | 0 |  | 13.2333 | Waiting for Materials | Open | 0.00061844 | 7.13 | 92.8081
424 | 2023-06-05 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:08 | 19:03 | 12.9167 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:08 | 6:08 | 6:08 | 19:03 | 0 | 0 |  | 12.9167 | Waiting for Materials | Open | 0.00099489 | 6.59 | 141.3767
425 | 2023-06-05 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:08 | 19:03 | 12.9167 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:08 | 6:08 | 6:08 | 19:03 | 0 | 0 |  | 12.9167 | Waiting for Materials | Open | 0.00099489 | 6.59 | 141.3767
426 | 2023-06-05 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:08 | 19:03 | 12.9167 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:08 | 6:08 | 6:08 | 19:03 | 0 | 0 |  | 12.9167 | Waiting for Materials | Open | 0.00060364 | 6.59 | 85.7791
427 | 2023-06-06 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:02 | 19:30 | 13.4667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:02 | 6:02 | 6:02 | 19:30 | 0 | 0 |  | 13.4667 | Waiting for Materials | Open | 0.0010373 | 7.15 | 153.3905
428 | 2023-06-06 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:02 | 19:30 | 13.4667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:02 | 6:02 | 6:02 | 19:30 | 0 | 0 |  | 13.4667 | Waiting for Materials | Open | 0.0010373 | 7.15 | 153.3905
429 | 2023-06-06 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:02 | 19:30 | 13.4667 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:02 | 6:02 | 6:02 | 19:30 | 0 | 0 |  | 13.4667 | Waiting for Materials | Open | 0.00062935 | 7.15 | 93.0684
430 | 2023-06-06 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:02 | 19:30 | 13.4667 | [5 empty] | Power_Tx1 | 0 | 1 | Power_Tx1 | 167322.75 | 49.93% | PTR | Tx_Tripped in Bucholz Optd | Bucholz relay trip Optd | 17:50 | 17:50 | 17:50 | 19:30 | 0 | 0 | 1.6667 | 1.6667 | Related parameter checked & related connection then PTR charged | Close | 0.83223 | 0.09 | 12517.0503
431 | 2023-06-07 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 5:57 | 19:24 | 13.45 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 5:57 | 5:57 | 5:57 | 19:24 | 0 | 0 |  | 13.45 | Waiting for Materials | Open | 0.001036 | 7.29 | 156.394
432 | 2023-06-07 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 5:57 | 19:24 | 13.45 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 5:57 | 5:57 | 5:57 | 19:24 | 0 | 0 |  | 13.45 | Waiting for Materials | Open | 0.001036 | 7.29 | 156.394
433 | 2023-06-07 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 5:57 | 19:24 | 13.45 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 5:57 | 5:57 | 5:57 | 19:24 | 0 | 0 |  | 13.45 | Waiting for Materials | Open | 0.00062857 | 7.29 | 94.8907
434 | 2023-06-07 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 5:57 | 19:24 | 13.45 | IS17 | INV1 | M2 |  |  |  | 1 | 1 | IS17INV1M2 | 2004.48 | 0.5982% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 5:57 | 5:57 | 5:57 | 8:24 | 0 | 0 | 2.45 | 2.45 | Related Parameter checked at SCB side then foun SCB 13 floating value not ok then we checked string 4 and 7 module damage due to this GFDI fault happened so we isolate the particular module and string connected to SCB | Close | 0.014656 | 0.31 | 516.4971
435 | 2023-06-07 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 5:57 | 19:24 | 13.45 | IS18 | INV4 | M2 |  |  |  | 1 | 1 | IS18INV4M2 | 2004.48 | 0.5982% | Inverter | Inverter Unit tripped in INS fault | Inverter Unit tripped in INS fault | 5:57 | 5:57 | 5:57 | 7:14 | 0 | 0 | 1.2833 | 1.2833 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.0076768 | 0.11 | 183.2732
436 | 2023-06-07 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 5:57 | 19:24 | 13.45 | IS2 | INV3 | M1 | SCB9 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Module | String_Brk for Module damage | String Breakdown due to Module damage | 5:57 | 5:57 | 5:57 | 19:24 | 0 | 0 |  | 13.45 | String Breakdown due to Module damage | Open | 0.00051799 | 7.49 | 80.3423
437 | 2023-06-07 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 5:57 | 19:24 | 13.45 | IS4 | INV4 | M1 | SCB5 | Str_Typ2 (450*29) |  | 0 | 0 | Str_Typ2 (450*29) | 13.05 | 0.003894% | Module | String_Brk for Module damage | String Breakdown due to Module damage | 5:57 | 5:57 | 5:57 | 19:24 | 0 | 0 |  | 13.45 | String Breakdown due to Module damage | Open | 0.00052381 | 7.49 | 81.245
438 | 2023-06-07 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 5:57 | 19:24 | 13.45 | IS6 | INV3 | M2 | SCB5 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | String_Brk for Module damage | String Breakdown due to Module damage | 5:57 | 5:57 | 5:57 | 19:24 | 0 | 0 |  | 13.45 | String Breakdown due to Module damage | Open | 0.00062857 | 7.49 | 97.494
439 | 2023-06-07 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 5:57 | 19:24 | 13.45 | IS6 | INV3 | M1 | SCB10 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | String_Brk for Module damage | String Breakdown due to Module damage | 5:57 | 5:57 | 5:57 | 19:24 | 0 | 0 |  | 13.45 | String Breakdown due to Module damage | Open | 0.00062857 | 7.49 | 97.494
440 | 2023-06-08 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:02 | 19:26 | 13.4 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:02 | 6:02 | 6:02 | 19:26 | 0 | 0 |  | 13.4 | Waiting for Materials | Open | 0.0010321 | 7.49 | 160.6846
441 | 2023-06-08 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:02 | 19:26 | 13.4 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:02 | 6:02 | 6:02 | 19:26 | 0 | 0 |  | 13.4 | Waiting for Materials | Open | 0.0010321 | 7.49 | 160.6846
442 | 2023-06-08 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:02 | 19:26 | 13.4 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:02 | 6:02 | 6:02 | 19:26 | 0 | 0 |  | 13.4 | Waiting for Materials | Open | 0.00062623 | 7.49 | 97.494
443 | 2023-06-08 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:02 | 19:26 | 13.4 | IS2 | INV3 | M2 | SCB7 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | String_Brk for Module damage | String Breakdown due to Module damage | 6:02 | 6:02 | 6:02 | 19:26 | 0 | 0 |  | 13.4 | Waiting for Materials | Open | 0.0010321 | 7.49 | 160.6846
444 | 2023-06-08 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:02 | 19:26 | 13.4 | IS2 | INV3 | M2 | SCB7 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | String_Brk for Module damage | String Breakdown due to Module damage | 6:02 | 6:02 | 6:02 | 19:26 | 0 | 0 |  | 13.4 | Waiting for Materials | Open | 0.0010321 | 7.49 | 160.6846
445 | 2023-06-08 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:02 | 19:26 | 13.4 | IS2 | INV4 | M1 | SCB5 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | String_Brk for Module damage | String Breakdown due to Module damage | 6:02 | 6:02 | 6:02 | 19:26 | 0 | 0 |  | 13.4 | Waiting for Materials | Open | 0.0010321 | 7.49 | 160.6846
446 | 2023-06-08 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:02 | 19:26 | 13.4 | IS8 | INV4 | M2 | SCB7 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Module | String_Brk for Module damage | String Breakdown due to Module damage | 6:02 | 6:02 | 6:02 | 19:26 | 0 | 0 |  | 13.4 | Waiting for Materials | Open | 0.0010437 | 7.49 | 162.4901
447 | 2023-06-08 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:02 | 19:26 | 13.4 | IS8 | INV4 | M2 | SCB7 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Module | String_Brk for Module damage | String Breakdown due to Module damage | 6:02 | 6:02 | 6:02 | 19:26 | 0 | 0 |  | 13.4 | Waiting for Materials | Open | 0.0010437 | 7.49 | 162.4901
448 | 2023-06-08 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:02 | 19:26 | 13.4 | IS16 | INV1 | M2 | SCB4 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | String_Brk for Module damage | String Breakdown due to Module damage | 6:02 | 6:02 | 6:02 | 19:26 | 0 | 0 |  | 13.4 | Waiting for Materials | Open | 0.0012525 | 7.49 | 194.9881
449 | 2023-06-08 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:02 | 19:26 | 13.4 | IS8 | INV1 | M1 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | String_Brk for Module damage | String Breakdown due to Module damage | 6:02 | 6:02 | 6:02 | 19:26 | 0 | 0 | 13.4 | 13.4 | Waiting for Materials | Close | 0.0012525 | 7.49 | 194.9881
450 | 2023-06-08 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:02 | 19:26 | 13.4 | IS18 | INV4 | M2 | SCB10 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | String_Brk for Module damage | String Breakdown due to Module damage | 6:02 | 6:02 | 6:02 | 19:26 | 0 | 0 | 13.4 | 13.4 | Waiting for Materials | Close | 0.0012525 | 7.49 | 194.9881
451 | 2023-06-08 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:02 | 19:26 | 13.4 | IS12 | INV1 | M1 | SCB4 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Module | String_Brk for Module damage | String Breakdown due to Module damage | 6:02 | 6:02 | 6:02 | 19:26 | 0 | 0 | 13.4 | 13.4 | Waiting for Materials | Close | 0.0012641 | 7.49 | 196.7935
452 | 2023-06-08 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:02 | 19:26 | 13.4 | IS11 | INV4 | M1 | SCB5 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Module | String_Brk for Module damage | String Breakdown due to Module damage | 6:02 | 6:02 | 6:02 | 19:26 | 0 | 0 | 13.4 | 13.4 | Waiting for Materials | Close | 0.0012641 | 7.49 | 196.7935
453 | 2023-06-08 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:02 | 19:26 | 13.4 | IS13 | INV3 | M1 | SCB7 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Module | String_Brk for Module damage | String Breakdown due to Module damage | 6:02 | 6:02 | 6:02 | 19:26 | 0 | 0 | 13.4 | 13.4 | Waiting for Materials | Close | 0.0012641 | 7.49 | 196.7935
454 | 2023-06-08 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:02 | 19:26 | 13.4 | IS14 | INV4 | M1 | SCB3 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Module | String_Brk for Module damage | String Breakdown due to Module damage | 6:02 | 6:02 | 6:02 | 19:26 | 0 | 0 | 13.4 | 13.4 | Waiting for Materials | Close | 0.0012641 | 7.49 | 196.7935
455 | 2023-06-08 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:02 | 19:26 | 13.4 | IS16 | INV3 | M1 | SCB4 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Module | String_Brk for Module damage | String Breakdown due to Module damage | 6:02 | 6:02 | 6:02 | 19:26 | 0 | 0 | 13.4 | 13.4 | Waiting for Materials | Close | 0.0012641 | 6.87 | 180.5035
456 | 2023-06-08 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:02 | 19:26 | 13.4 | IS17 | INV1 | M2 | SCB3 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Module | String_Brk for Module damage | String Breakdown due to Module damage | 6:02 | 6:02 | 6:02 | 19:26 | 0 | 0 | 13.4 | 13.4 | Waiting for Materials | Close | 0.0012641 | 6.87 | 180.5035
457 | 2023-06-08 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:02 | 19:26 | 13.4 | IS17 | INV1 | M2 | SCB3 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Module | String_Brk for Module damage | String Breakdown due to Module damage | 6:02 | 6:02 | 6:02 | 19:26 | 0 | 0 | 13.4 | 13.4 | Waiting for Materials | Close | 0.0012641 | 6.87 | 180.5035
458 | 2023-06-08 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:02 | 19:26 | 13.4 | IS18 | INV4 | M2 | SCB10 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Module | String_Brk for Module damage | String Breakdown due to Module damage | 6:02 | 6:02 | 6:02 | 19:26 | 0 | 0 |  | 13.4 | Waiting for Materials | Open | 0.0012641 | 6.87 | 180.5035
459 | 2023-06-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:00 | 19:22 | 13.3667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:00 | 6:00 | 6:00 | 19:22 | 0 | 0 |  | 13.3667 | Waiting for Materials | Open | 0.0010296 | 6.87 | 147.3836
460 | 2023-06-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:00 | 19:22 | 13.3667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:00 | 6:00 | 6:00 | 19:22 | 0 | 0 |  | 13.3667 | Waiting for Materials | Open | 0.0010296 | 6.87 | 147.3836
461 | 2023-06-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:00 | 19:22 | 13.3667 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:00 | 6:00 | 6:00 | 19:22 | 0 | 0 |  | 13.3667 | Waiting for Materials | Open | 0.00062467 | 6.87 | 89.4238
462 | 2023-06-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:00 | 19:22 | 13.3667 | IS12 | INV1 | M2 | SCB3 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Module | String_Brk for Module damage | String Breakdown due to Module damage | 6:00 | 6:00 | 6:00 | 19:22 | 0 | 0 | 13.3667 | 13.3667 | Waiting for Materials | Close | 0.0012609 | 6.87 | 180.5035
463 | 2023-06-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:00 | 19:22 | 13.3667 | IS12 | INV2 | M1 | SCB6 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Module | String_Brk for Module damage | String Breakdown due to Module damage | 6:00 | 6:00 | 6:00 | 19:22 | 0 | 0 | 13.3667 | 13.3667 | Waiting for Materials | Close | 0.0012609 | 6.87 | 180.5035
464 | 2023-06-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:00 | 19:22 | 13.3667 | IS12 | INV2 | M2 | SCB5 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Module | String_Brk for Module damage | String Breakdown due to Module damage | 6:00 | 6:00 | 6:00 | 19:22 | 0 | 0 | 13.3667 | 13.3667 | Waiting for Materials | Close | 0.0012609 | 6.87 | 180.5035
465 | 2023-06-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:00 | 19:22 | 13.3667 | IS14 | INV4 | M1 | SCB2 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Module | String_Brk for Module damage | String Breakdown due to Module damage | 6:00 | 6:00 | 6:00 | 19:22 | 0 | 0 | 13.3667 | 13.3667 | Waiting for Materials | Close | 0.0012609 | 6.87 | 180.5035
466 | 2023-06-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:00 | 19:22 | 13.3667 | IS16 | INV3 | M1 | SCB8 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Module | String_Brk for Module damage | String Breakdown due to Module damage | 6:00 | 6:00 | 6:00 | 19:22 | 0 | 0 | 13.3667 | 13.3667 | Waiting for Materials | Close | 0.0012609 | 6.87 | 180.5035
467 | 2023-06-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:00 | 19:22 | 13.3667 | IS16 | INV2 | M2 | SCB8 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Module | String_Brk for Module damage | String Breakdown due to Module damage | 6:00 | 6:00 | 6:00 | 19:22 | 0 | 0 | 13.3667 | 13.3667 | Waiting for Materials | Close | 0.0012609 | 6.87 | 180.5035
468 | 2023-06-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:00 | 19:22 | 13.3667 | IS16 | INV2 | M2 | SCB8 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Module | String_Brk for Module damage | String Breakdown due to Module damage | 6:00 | 6:00 | 6:00 | 19:22 | 0 | 0 | 13.3667 | 13.3667 | Waiting for Materials | Close | 0.0012609 | 6.87 | 180.5035
469 | 2023-06-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:00 | 19:22 | 13.3667 | IS16 | INV3 | M1 | SCB4 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Module | String_Brk for Module damage | String Breakdown due to Module damage | 6:00 | 6:00 | 6:00 | 19:22 | 0 | 0 | 13.3667 | 13.3667 | Waiting for Materials | Close | 0.0012609 | 6.87 | 180.5035
470 | 2023-06-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:00 | 19:22 | 13.3667 | IS17 | INV1 | M2 | SCB6 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Module | String_Brk for Module damage | String Breakdown due to Module damage | 6:00 | 6:00 | 6:00 | 19:22 | 0 | 0 | 13.3667 | 13.3667 | Waiting for Materials | Close | 0.0012609 | 6.87 | 180.5035
471 | 2023-06-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:00 | 19:22 | 13.3667 | IS18 | INV4 | M2 | SCB10 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Module | String_Brk for Module damage | String Breakdown due to Module damage | 6:00 | 6:00 | 6:00 | 19:22 | 0 | 0 | 13.3667 | 13.3667 | Waiting for Materials | Close | 0.0012609 | 6.87 | 180.5035
472 | 2023-06-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:00 | 19:22 | 13.3667 | IS11 | INV4 | M1 | SCB5 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Module | String_Brk for Module damage | String Breakdown due to Module damage | 6:00 | 6:00 | 6:00 | 19:22 | 0 | 0 | 13.3667 | 13.3667 | Waiting for Materials | Close | 0.0012609 | 6.87 | 180.5035
473 | 2023-06-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:00 | 19:22 | 13.3667 | IS8 | INV1 | M2 | SCB3 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | String_Brk for Module damage | String Breakdown due to Module damage | 6:00 | 6:00 | 6:00 | 19:22 | 0 | 0 | 13.3667 | 13.3667 | Waiting for Materials | Close | 0.0012493 | 6.87 | 178.8475
474 | 2023-06-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:00 | 19:22 | 13.3667 | IS9 | INV3 | M2 | SCB5 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Module | String_Brk for Module damage | String Breakdown due to Module damage | 6:00 | 6:00 | 6:00 | 19:22 | 0 | 0 | 13.3667 | 13.3667 | Waiting for Materials | Close | 0.0012609 | 6.87 | 180.5035
475 | 2023-06-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:00 | 19:22 | 13.3667 | IS2 | INV3 | M2 | SCB7 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | String_Brk for Module damage | String Breakdown due to Module damage | 6:02 | 6:02 | 6:02 | 19:26 | 0 | 0 | 13.4 | 13.4 | Waiting for Materials | Close | 0.0010321 | 6.87 | 147.3836
476 | 2023-06-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:00 | 19:22 | 13.3667 | IS2 | INV3 | M2 | SCB7 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | String_Brk for Module damage | String Breakdown due to Module damage | 6:02 | 6:02 | 6:02 | 19:26 | 0 | 0 | 13.4 | 13.4 | Waiting for Materials | Close | 0.0010321 | 7.35 | 157.6812
477 | 2023-06-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:00 | 19:22 | 13.3667 | IS2 | INV4 | M1 | SCB5 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | String_Brk for Module damage | String Breakdown due to Module damage | 6:02 | 6:02 | 6:02 | 19:26 | 0 | 0 | 13.4 | 13.4 | Waiting for Materials | Close | 0.0010321 | 7.35 | 157.6812
478 | 2023-06-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:00 | 19:22 | 13.3667 | IS8 | INV4 | M2 | SCB7 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Module | String_Brk for Module damage | String Breakdown due to Module damage | 6:02 | 6:02 | 6:02 | 19:26 | 0 | 0 | 13.4 | 13.4 | Waiting for Materials | Close | 0.0010437 | 7.35 | 159.4529
479 | 2023-06-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:00 | 19:22 | 13.3667 | IS8 | INV4 | M2 | SCB7 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Module | String_Brk for Module damage | String Breakdown due to Module damage | 6:02 | 6:02 | 6:02 | 19:26 | 0 | 0 | 13.4 | 13.4 | Waiting for Materials | Close | 0.0010437 | 7.84 | 170.0831
480 | 2023-06-10 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:07 | 19:27 | 13.3333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:07 | 6:07 | 6:07 | 19:27 | 0 | 0 |  | 13.3333 | Waiting for Materials | Open | 0.001027 | 7.84 | 168.1932
481 | 2023-06-10 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:07 | 19:27 | 13.3333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:07 | 6:07 | 6:07 | 19:27 | 0 | 0 |  | 13.3333 | Waiting for Materials | Open | 0.001027 | 7.84 | 168.1932
482 | 2023-06-10 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:07 | 19:27 | 13.3333 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:07 | 6:07 | 6:07 | 19:27 | 0 | 0 |  | 13.3333 | Waiting for Materials | Open | 0.00062311 | 7.25 | 94.3701
483 | 2023-06-11 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:06 | 19:26 | 13.3333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:00 | 6:00 | 6:00 | 19:22 | 0 | 0 |  | 13.3667 | Waiting for Materials | Open | 0.0010296 | 7.25 | 155.5358
484 | 2023-06-11 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:06 | 19:26 | 13.3333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:00 | 6:00 | 6:00 | 19:22 | 0 | 0 |  | 13.3667 | Waiting for Materials | Open | 0.0010296 | 7.25 | 155.5358
485 | 2023-06-11 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:06 | 19:26 | 13.3333 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:00 | 6:00 | 6:00 | 19:22 | 0 | 0 |  | 13.3667 | Waiting for Materials | Open | 0.00062467 | 7.2 | 93.7192
486 | 2023-06-12 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:04 | 19:28 | 13.4 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  |  |  | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:04 | 6:04 | 6:04 | 19:28 | 0 | 0 |  | 13.4 | Waiting for Materials | Open | 0.0010321 | 7.2 | 154.4632
487 | 2023-06-12 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:04 | 19:28 | 13.4 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  |  |  | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:04 | 6:04 | 6:04 | 19:28 | 0 | 0 |  | 13.4 | Waiting for Materials | Open | 0.0010321 | 7.2 | 154.4632
488 | 2023-06-12 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:04 | 19:28 | 13.4 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:04 | 6:04 | 6:04 | 19:28 | 0 | 0 |  | 13.4 | Waiting for Materials | Open | 0.00062623 | 6.65 | 86.5601
489 | 2023-06-13 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:08 | 19:12 | 13.0667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:08 | 6:08 | 6:08 | 19:12 | 0 | 0 |  | 13.0667 | Waiting for Materials | Open | 0.0010064 | 6.65 | 142.6639
490 | 2023-06-13 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:08 | 19:12 | 13.0667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:08 | 6:08 | 6:08 | 19:12 | 0 | 0 |  | 13.0667 | Waiting for Materials | Open | 0.0010064 | 6.65 | 142.6639
491 | 2023-06-13 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:08 | 19:12 | 13.0667 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:08 | 6:08 | 6:08 | 19:12 | 0 | 0 |  | 13.0667 | Waiting for Materials | Open | 0.00061065 | 4.72 | 61.4382
492 | 2023-06-14 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:08 | 19:07 | 12.9833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:08 | 6:08 | 6:08 | 19:09 | 0 | 0 |  | 13.0167 | Waiting for Materials | Open | 0.0010026 | 4.72 | 101.2592
493 | 2023-06-14 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:08 | 19:07 | 12.9833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:08 | 6:08 | 6:08 | 19:09 | 0 | 0 |  | 13.0167 | Waiting for Materials | Open | 0.0010026 | 4.72 | 101.2592
494 | 2023-06-14 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:08 | 19:07 | 12.9833 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:08 | 6:08 | 6:08 | 19:09 | 0 | 0 |  | 13.0167 | Waiting for Materials | Open | 0.00060832 | 0.05 | 0.65083
495 | 2023-06-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:09 | 19:20 | 13.1833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:09 | 6:09 | 6:09 | 19:20 | 0 | 0 |  | 13.1833 | Waiting for Materials | Open | 0.0010154 | 0.05 | 1.0727
496 | 2023-06-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:09 | 19:20 | 13.1833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:09 | 6:09 | 6:09 | 19:20 | 0 | 0 |  | 13.1833 | Waiting for Materials | Open | 0.0010154 | 3.73 | 80.0205
497 | 2023-06-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:09 | 19:20 | 13.1833 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:09 | 6:09 | 6:09 | 19:20 | 0 | 0 |  | 13.1833 | Waiting for Materials | Open | 0.0006161 | 3.73 | 48.5518
498 | 2023-06-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:09 | 19:20 | 13.1833 | IS10 | INV3 | M1 |  |  |  | 1 | 1 | IS10INV3M1 | 1941.84 | 0.5795% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 17:58 | 17:58 | 17:58 | 18:56 | 0 | 0 | 0.96667 | 0.96667 | Auto reset | Close | 0.0056018 | 3.73 | 6020.4197
499 | 2023-06-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:09 | 19:20 | 13.1833 | IS10 | INV3 | M2 |  |  |  | 1 | 1 | IS10INV3M2 | 2255.04 | 0.673% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 17:58 | 17:58 | 17:58 | 18:56 | 0 | 0 | 0.96667 | 0.96667 | Auto reset | Close | 0.0065053 | 0.65 | 1218.3501
500 | 2023-06-16 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:09 | 19:05 | 12.9333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:09 | 6:09 | 6:09 | 19:05 | 0 | 0 |  | 12.9333 | Waiting for Materials | Open | 0.00099618 | 3.7345 | 80.1161
501 | 2023-06-16 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:09 | 19:05 | 12.9333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:09 | 6:09 | 6:09 | 19:05 | 0 | 0 |  | 12.9333 | Waiting for Materials | Open | 0.00099618 | 3.7345 | 80.1161
502 | 2023-06-16 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:09 | 19:05 | 12.9333 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:09 | 6:09 | 6:09 | 19:05 | 0 | 0 |  | 12.9333 | Waiting for Materials | Open | 0.00060442 | 3.7345 | 48.6098
503 | 2023-06-16 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:09 | 19:05 | 12.9333 | IS4 | INV3 | M1 |  |  |  | 1 | 1 | IS4INV3M1 | 2114.1 | 0.6309% | Inverter | Inverter Unit tripped in Revers branch over current fault | Inverter Unit tripped in Revers branch over current fault | 16:17 | 16:17 | 16:17 | 18:44 | 0 | 0 | 2.45 | 2.45 | Floting found ok then inverter restart | Close | 0.015457 | 0.64844 | 1139.467
504 | 2023-06-17 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:18 | 19:08 | 12.8333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:09 | 6:09 | 6:09 | 19:05 | 0 | 0 |  | 12.9333 | Waiting for Materials | Open | 0.00099618 | 1.7013 | 36.4992
505 | 2023-06-17 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:18 | 19:08 | 12.8333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:09 | 6:09 | 6:09 | 19:05 | 0 | 0 |  | 12.9333 | Waiting for Materials | Open | 0.00099618 | 1.7013 | 36.4992
506 | 2023-06-17 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:18 | 19:08 | 12.8333 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:09 | 6:09 | 6:09 | 19:05 | 0 | 0 |  | 12.9333 | Waiting for Materials | Open | 0.00060442 | 1.7013 | 22.1456
507 | 2023-06-18 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:10 | 19:26 | 13.2667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:10 | 6:10 | 6:10 | 19:26 | 0 | 0 |  | 13.2667 | Waiting for Materials | Open | 0.0010218 | 4.7512 | 101.9276
508 | 2023-06-18 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:10 | 19:26 | 13.2667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:10 | 6:10 | 6:10 | 19:26 | 0 | 0 |  | 13.2667 | Waiting for Materials | Open | 0.0010218 | 4.7512 | 101.9276
509 | 2023-06-18 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:10 | 19:26 | 13.2667 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:10 | 6:10 | 6:10 | 19:26 | 0 | 0 |  | 13.2667 | Waiting for Materials | Open | 0.00062 | 4.7512 | 61.8437
510 | 2023-06-19 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:09 | 19:25 | 13.2667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:09 | 6:09 | 6:09 | 19:25 | 0 | 0 |  | 13.2667 | Waiting for Materials | Open | 0.0010218 | 6.4866 | 139.1578
511 | 2023-06-19 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:09 | 19:25 | 13.2667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:09 | 6:09 | 6:09 | 19:25 | 0 | 0 |  | 13.2667 | Waiting for Materials | Open | 0.0010218 | 6.4866 | 139.1578
512 | 2023-06-19 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:09 | 19:25 | 13.2667 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:09 | 6:09 | 6:09 | 19:25 | 0 | 0 |  | 13.2667 | Waiting for Materials | Open | 0.00062 | 6.4866 | 84.4328
513 | 2023-06-20 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:04 | 19:22 | 13.3 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:04 | 6:04 | 6:04 | 19:22 | 0 | 0 |  | 13.3 | Waiting for Materials | Open | 0.0010244 | 7.32 | 157.0376
514 | 2023-06-20 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:04 | 19:22 | 13.3 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:04 | 6:04 | 6:04 | 19:22 | 0 | 0 |  | 13.3 | Waiting for Materials | Open | 0.0010244 | 7.32 | 157.0376
515 | 2023-06-20 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:04 | 19:22 | 13.3 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:04 | 6:04 | 6:04 | 19:22 | 0 | 0 |  | 13.3 | Waiting for Materials | Open | 0.00062156 | 7.32 | 95.2812
516 | 2023-06-21 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:14 | 19:21 | 13.1167 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:14 | 6:14 | 6:14 | 19:21 | 0 | 0 |  | 13.1167 | Waiting for Materials | Open | 0.0010103 | 7.3604 | 157.9047
517 | 2023-06-21 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:14 | 19:21 | 13.1167 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:14 | 6:14 | 6:14 | 19:21 | 0 | 0 |  | 13.1167 | Waiting for Materials | Open | 0.0010103 | 7.3604 | 157.9047
518 | 2023-06-21 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:14 | 19:21 | 13.1167 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:14 | 6:14 | 6:14 | 19:21 | 0 | 0 |  | 13.1167 | Waiting for Materials | Open | 0.00061299 | 7.3604 | 95.8073
519 | 2023-06-22 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:09 | 19:23 | 13.2333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:09 | 6:09 | 6:09 | 19:23 | 0 | 0 |  | 13.2333 | Waiting for Materials | Open | 0.0010193 | 7.0472 | 151.1861
520 | 2023-06-22 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:09 | 19:23 | 13.2333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:09 | 6:09 | 6:09 | 19:23 | 0 | 0 |  | 13.2333 | Waiting for Materials | Open | 0.0010193 | 7.0472 | 151.1861
521 | 2023-06-22 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:09 | 19:23 | 13.2333 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:09 | 6:09 | 6:09 | 19:23 | 0 | 0 |  | 13.2333 | Waiting for Materials | Open | 0.00061844 | 7.0472 | 91.7309
522 | 2023-06-23 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 5:50 | 19:30 | 13.6667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 5:50 | 5:50 | 5:50 | 19:30 | 0 | 0 |  | 13.6667 | Waiting for Materials | Open | 0.0010527 | 7.34 | 157.4666
523 | 2023-06-23 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 5:50 | 19:30 | 13.6667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 5:50 | 5:50 | 5:50 | 19:30 | 0 | 0 |  | 13.6667 | Waiting for Materials | Open | 0.0010527 | 7.34 | 157.4666
524 | 2023-06-23 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 5:50 | 19:30 | 13.6667 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 5:50 | 5:50 | 5:50 | 19:30 | 0 | 0 |  | 13.6667 | Waiting for Materials | Open | 0.00063869 | 7.34 | 95.5416
525 | 2023-06-24 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 5:50 | 19:30 | 13.6667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 5:50 | 5:50 | 5:50 | 19:30 | 0 | 0 |  | 13.6667 | Waiting for Materials | Open | 0.0010527 | 7.1 | 152.3179
526 | 2023-06-24 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 5:50 | 19:30 | 13.6667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 5:50 | 5:50 | 5:50 | 19:30 | 0 | 0 |  | 13.6667 | Waiting for Materials | Open | 0.0010527 | 7.1 | 152.3179
527 | 2023-06-24 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 5:50 | 19:30 | 13.6667 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 5:50 | 5:50 | 5:50 | 19:30 | 0 | 0 |  | 13.6667 | Waiting for Materials | Open | 0.00063869 | 7.1 | 92.4176
528 | 2023-06-25 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:00 | 19:40 | 13.6667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:00 | 6:00 | 6:00 | 19:40 | 0 | 0 |  | 13.6667 | Waiting for Materials | Open | 0.0010527 | 7.1 | 152.3179
529 | 2023-06-25 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:00 | 19:40 | 13.6667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:00 | 6:00 | 6:00 | 19:40 | 0 | 0 |  | 13.6667 | Waiting for Materials | Open | 0.0010527 | 7.1 | 152.3179
530 | 2023-06-25 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:00 | 19:40 | 13.6667 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:00 | 6:00 | 6:00 | 19:40 | 0 | 0 |  | 13.6667 | Waiting for Materials | Open | 0.00063869 | 7.1 | 92.4176
531 | 2023-06-26 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 5:50 | 19:30 | 13.6667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 5:50 | 5:50 | 5:50 | 19:30 | 0 | 0 |  | 13.6667 | Waiting for Materials | Open | 0.0010527 | 6.48 | 139.0169
532 | 2023-06-26 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 5:50 | 19:30 | 13.6667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 5:50 | 5:50 | 5:50 | 19:30 | 0 | 0 |  | 13.6667 | Waiting for Materials | Open | 0.0010527 | 6.48 | 139.0169
533 | 2023-06-26 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 5:50 | 19:30 | 13.6667 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 5:50 | 5:50 | 5:50 | 19:30 | 0 | 0 |  | 13.6667 | Waiting for Materials | Open | 0.00063869 | 6.48 | 84.3473
534 | 2023-06-27 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:00 | 19:20 | 13.3333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:00 | 6:00 | 6:00 | 19:20 | 0 | 0 |  | 13.3333 | Waiting for Materials | Open | 0.001027 | 5.9 | 126.574
535 | 2023-06-27 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:00 | 19:20 | 13.3333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:00 | 6:00 | 6:00 | 19:20 | 0 | 0 |  | 13.3333 | Waiting for Materials | Open | 0.001027 | 5.9 | 126.574
536 | 2023-06-27 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:00 | 19:20 | 13.3333 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:00 | 6:00 | 6:00 | 19:20 | 0 | 0 |  | 13.3333 | Waiting for Materials | Open | 0.00062311 | 5.9 | 76.7977
537 | 2023-06-28 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:00 | 19:40 | 13.6667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:00 | 6:00 | 6:00 | 19:40 | 0 | 0 |  | 13.6667 | Waiting for Materials | Open | 0.0010527 | 7.31 | 156.823
538 | 2023-06-28 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:00 | 19:40 | 13.6667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:00 | 6:00 | 6:00 | 19:40 | 0 | 0 |  | 13.6667 | Waiting for Materials | Open | 0.0010527 | 7.31 | 156.823
539 | 2023-06-28 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:00 | 19:40 | 13.6667 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 6:00 | 6:00 | 6:00 | 19:40 | 0 | 0 |  | 13.6667 | Waiting for Materials | Open | 0.00063869 | 7.31 | 95.1511
540 | 2023-06-28 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 6:00 | 19:40 | 13.6667 | IS10 |  |  |  |  | Tx | 0 | 1 | IS10Tx | 16756.2 | 5% | IDT | Tx_Tripped in High WTI temp | IDT tripped under LV winding 4 tripped | 13:42 | 13:42 | 13:50 | 14:52 | 0 | 0.13333 | 1.1667 | 1.1667 | Checked all parameters and charged IDT | Close | 0.058339 | 1.05 | 14624.106
541 | 2023-06-29 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 5:50 | 18:10 | 12.3333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 5:50 | 5:50 | 5:50 | 18:10 | 0 | 0 |  | 12.3333 | Waiting for Materials | Open | 0.00094996 | 6.4 | 137.3006
542 | 2023-06-29 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 5:50 | 18:10 | 12.3333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 5:50 | 5:50 | 5:50 | 18:10 | 0 | 0 |  | 12.3333 | Waiting for Materials | Open | 0.00094996 | 6.4 | 137.3006
543 | 2023-06-29 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 5:50 | 18:10 | 12.3333 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 5:50 | 5:50 | 5:50 | 18:10 | 0 | 0 |  | 12.3333 | Waiting for Materials | Open | 0.00057638 | 6.4 | 83.306
544 | 2023-06-29 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 5:50 | 18:10 | 12.3333 | IS3 | INV2 | M2 |  |  |  | 1 | 1 | IS3INV2M2 | 2090.61 | 0.6239% | Inverter | Inv Unit_AC Coil failure | Inverter Unit tripped under AC Switch breaking | 5:50 | 5:50 | 6:00 | 8:34 | 0 | 0.16667 | 2.7333 | 2.7333 | AC Coil replaced | Close | 0.017053 | 0.23 | 399.6735
545 | 2023-06-29 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 5:50 | 18:10 | 12.3333 | IS3 | INV2 | M1 |  |  |  | 1 | 1 | IS3INV2M1 | 2090.61 | 0.6239% | Inverter | Inv_Manual stop for AC Coil replacement | Inv. Unit manual stop for replacing of AC coil | 7:35 | 7:35 | 7:35 | 8:34 | 0 | 0 | 0.98333 | 0.98333 | AC Coil replaced | Close | 0.0061349 | 0.12 | 208.5253
546 | 2023-06-30 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 5:50 | 19:30 | 13.6667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 5:50 | 5:50 | 5:50 | 19:30 | 0 | 0 |  | 13.6667 | Waiting for Materials | Open | 0.0010527 | 7.13 | 152.9615
547 | 2023-06-30 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 5:50 | 19:30 | 13.6667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 5:50 | 5:50 | 5:50 | 19:30 | 0 | 0 |  | 13.6667 | Waiting for Materials | Open | 0.0010527 | 7.13 | 152.9615
548 | 2023-06-30 | FY24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 5:50 | 19:30 | 13.6667 | IS14 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Module | Module Half string JB Burn | Module Half string JB Burn | 5:50 | 5:50 | 5:50 | 19:30 | 0 | 0 |  | 13.6667 | Waiting for Materials | Open | 0.00063869 | 7.13 | 92.8081
549 | 2023-07-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:05 | 19:21 | 13.2667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:05 | 6:05 | 6:05 | 19:21 | 0 | 0 |  | 13.2667 | Waiting for Materials | Open | 0.0010218 | 7.2197 | 162.0203
550 | 2023-07-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:05 | 19:21 | 13.2667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:05 | 6:05 | 6:05 | 19:21 | 0 | 0 |  | 13.2667 | Waiting for Materials | Open | 0.0010218 | 7.2197 | 162.0203
551 | 2023-07-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:02 | 19:29 | 13.45 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:02 | 6:02 | 6:02 | 19:29 | 0 | 0 |  | 13.45 | Waiting for Materials | Open | 0.001036 | 7.2842 | 163.4679
552 | 2023-07-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:02 | 19:29 | 13.45 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:02 | 6:02 | 6:02 | 19:29 | 0 | 0 |  | 13.45 | Waiting for Materials | Open | 0.001036 | 7.2842 | 163.4679
553 | 2023-07-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:02 | 19:29 | 13.45 | IS6 |  |  |  |  | Tx | 0 | 1 | IS6Tx | 17170.9 | 5.124% | IDT | Tx_tripped of MOG | IDT tripped in MOG | 6:02 | 6:02 | 6:02 | 15:05 | 0 | 0 | 9.05 | 9.05 | Check related connection and parameter then check BDV and oil top up | Close | 0.46374 | 5.6523 | 84388.0756
554 | 2023-07-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:02 | 19:29 | 13.45 | IS15 | INV3 | M2 |  |  |  | 1 | 1 | IS15INV3M2 | 2192.4 | 0.6543% | Inverter | Inv Unit_AC Coil failure | Inverter Unit tripped under AC Switch breaking | 6:02 | 6:02 | 6:02 | 19:29 | 0 | 0 | 13.45 | 13.45 | Checked Related connection and parameter and AC Coil replaced but not resolved. Discussed with OEM team and replaced AC breaker and PD card | Close | 0.087999 | 7.2842 | 13885.5915
555 | 2023-07-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:02 | 19:29 | 13.45 | IS15 | INV3 | M1 |  |  |  | 1 | 1 | IS15INV3M1 | 2223.72 | 0.6636% | Inverter | Inv_Manual stop for AC Coil replacement | Inv. Unit manual stop for replacing of AC coil | 6:02 | 6:02 | 9:07 | 10:31 | 0 | 3.0833 | 4.4833 | 4.4833 | Inv. Unit manual stop for replacing of AC coil | Close | 0.029752 | 0.88887 | 1718.6173
556 | 2023-07-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:04 | 19:28 | 13.4 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:04 | 6:04 | 6:04 | 19:28 | 0 | 0 |  | 13.4 | Waiting for Materials | Open | 0.0010321 | 7.3727 | 165.4527
557 | 2023-07-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:04 | 19:28 | 13.4 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:04 | 6:04 | 6:04 | 19:28 | 0 | 0 |  | 13.4 | Waiting for Materials | Open | 0.0010321 | 7.3727 | 165.4527
558 | 2023-07-04 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:06 | 19:27 | 13.35 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:06 | 6:06 | 6:06 | 19:27 | 0 | 0 |  | 13.35 | Waiting for Materials | Open | 0.0010283 | 7.2858 | 163.5025
559 | 2023-07-04 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:06 | 19:27 | 13.35 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:06 | 6:06 | 6:06 | 19:27 | 0 | 0 |  | 13.35 | Waiting for Materials | Open | 0.0010283 | 7.2858 | 163.5025
560 | 2023-07-05 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:06 | 19:29 | 13.3833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:06 | 6:06 | 6:06 | 19:29 | 0 | 0 |  | 13.3833 | Waiting for Materials | Open | 0.0010308 | 6.7019 | 150.3992
561 | 2023-07-05 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:06 | 19:29 | 13.3833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:06 | 6:06 | 6:06 | 19:29 | 0 | 0 |  | 13.3833 | Waiting for Materials | Open | 0.0010308 | 6.7019 | 150.3992
562 | 2023-07-06 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:07 | 19:17 | 13.1667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:07 | 6:07 | 6:07 | 19:17 | 0 | 0 |  | 13.1667 | Waiting for Materials | Open | 0.0010141 | 6.1339 | 137.6535
563 | 2023-07-06 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:07 | 19:17 | 13.1667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:07 | 6:07 | 6:07 | 19:17 | 0 | 0 |  | 13.1667 | Waiting for Materials | Open | 0.0010141 | 6.1339 | 137.6535
564 | 2023-07-07 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:04 | 19:19 | 13.25 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:04 | 6:04 | 6:04 | 19:19 | 0 | 0 |  | 13.25 | Waiting for Materials | Open | 0.0010206 | 4.6633 | 104.6517
565 | 2023-07-07 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:04 | 19:19 | 13.25 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:04 | 6:04 | 6:04 | 19:19 | 0 | 0 |  | 13.25 | Waiting for Materials | Open | 0.0010206 | 4.6633 | 104.6517
566 | 2023-07-07 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:04 | 19:19 | 13.25 | IS10 | INV2 | M1 |  |  |  | 1 | 1 | IS10INV2M1 | 1973.16 | 0.5888% | Inverter | Inv Unit_AC Coil failure | AC switch Breaking/ IDC leakage | 14:13 | 14:13 | 14:13 | 17:09 | 0 | 0 | 2.9333 | 2.9333 | Related parameter and connection checked then restart the inverter but error as is it so we discussed with OEM so we checked all SCB at field side an off all SCB then inverter start then SCB on then unit 02 not start in AC coil break down so we replaced AC coil an inverter unit start | Close | 0.017273 | 0.79611 | 1365.8274
567 | 2023-07-07 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:04 | 19:19 | 13.25 | IS10 | INV2 | M2 |  |  |  | 1 | 1 | IS10INV2M2 | 2223.72 | 0.6636% | Inverter | Inv Unit_AC Coil failure | AC switch Breaking/ IDC leakage | 14:13 | 14:13 | 14:13 | 19:19 | 0 | 0 | 5.1 | 5.1 | Related parameter and connection checked then restart the inverter but error as is it so we discussed with OEM so we checked all SCB at field side an off all SCB then inverter start then SCB on then unit 02 not start in AC coil break down so we replaced AC coil an inverter unit start | Close | 0.033844 | 0.87592 | 1693.5741
568 | 2023-07-08 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:03 | 19:20 | 13.2833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:03 | 6:03 | 6:03 | 19:20 | 0 | 0 |  | 13.2833 | Waiting for Materials | Open | 0.0010231 | 3.9871 | 89.4769
569 | 2023-07-08 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:03 | 19:20 | 13.2833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:03 | 6:03 | 6:03 | 19:20 | 0 | 0 |  | 13.2833 | Waiting for Materials | Open | 0.0010231 | 3.9871 | 89.4769
570 | 2023-07-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:00 | 19:08 | 13.1333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:00 | 6:00 | 6:00 | 19:08 | 0 | 0 |  | 13.1333 | Waiting for Materials | Open | 0.0010116 | 6.4291 | 144.2773
571 | 2023-07-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:00 | 19:08 | 13.1333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:00 | 6:00 | 6:00 | 19:08 | 0 | 0 |  | 13.1333 | Waiting for Materials | Open | 0.0010116 | 6.4291 | 144.2773
572 | 2023-07-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:00 | 19:08 | 13.1333 | IS10 |  |  |  |  | Tx | 0 | 1 | IS10Tx | 16756.2 | 5% | IDT | Tx_Tripped in High WTI temp | LV 4 Winding trip | 14:41 | 14:41 | 14:41 | 15:11 | 0 | 0 | 0.5 | 0.5 | Related parameter checked and connection checked found ok then IDT charged | Close | 0.025002 | 0.44887 | 6539.724
573 | 2023-07-10 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:02 | 19:28 | 13.4333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:02 | 6:02 | 6:02 | 19:28 | 0 | 0 |  | 13.4333 | Waiting for Materials | Open | 0.0010347 | 4.8944 | 109.8369
574 | 2023-07-10 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:02 | 19:28 | 13.4333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:02 | 6:02 | 6:02 | 19:28 | 0 | 0 |  | 13.4333 | Waiting for Materials | Open | 0.0010347 | 4.8944 | 109.8369
575 | 2023-07-11 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:03 | 19:26 | 13.3833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:03 | 6:03 | 6:03 | 19:26 | 0 | 0 |  | 13.3833 | Waiting for Materials | Open | 0.0010308 | 6.6701 | 149.6857
576 | 2023-07-11 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:03 | 19:26 | 13.3833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:03 | 6:03 | 6:03 | 19:26 | 0 | 0 |  | 13.3833 | Waiting for Materials | Open | 0.0010308 | 6.6701 | 149.6857
577 | 2023-07-12 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:07 | 19:23 | 13.2667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:07 | 6:07 | 6:07 | 19:23 | 0 | 0 |  | 13.2667 | Waiting for Materials | Open | 0.0010218 | 7.2377 | 162.4246
578 | 2023-07-12 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:07 | 19:23 | 13.2667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:07 | 6:07 | 6:07 | 19:23 | 0 | 0 |  | 13.2667 | Waiting for Materials | Open | 0.0010218 | 7.2377 | 162.4246
579 | 2023-07-13 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:00 | 19:30 | 13.5 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:00 | 6:00 | 6:00 | 19:30 | 0 | 0 |  | 13.5 | Waiting for Materials | Open | 0.0010398 | 7.29 | 163.5974
580 | 2023-07-13 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:00 | 19:30 | 13.5 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:00 | 6:00 | 6:00 | 19:30 | 0 | 0 |  | 13.5 | Waiting for Materials | Open | 0.0010398 | 7.29 | 163.5974
581 | 2023-07-14 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:00 | 19:30 | 13.5 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:00 | 6:00 | 6:00 | 19:30 | 0 | 0 |  | 13.5 | Waiting for Materials | Open | 0.0010398 | 7.09 | 159.1092
582 | 2023-07-14 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:00 | 19:30 | 13.5 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:00 | 6:00 | 6:00 | 19:30 | 0 | 0 |  | 13.5 | Waiting for Materials | Open | 0.0010398 | 7.09 | 159.1092
583 | 2023-07-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:06 | 19:25 | 13.3167 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:06 | 6:06 | 6:06 | 19:25 | 0 | 0 |  | 13.3167 | Waiting for Materials | Open | 0.0010257 | 7.2371 | 162.4098
584 | 2023-07-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:06 | 19:25 | 13.3167 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:06 | 6:06 | 6:06 | 19:25 | 0 | 0 |  | 13.3167 | Waiting for Materials | Open | 0.0010257 | 7.2371 | 162.4098
585 | 2023-07-16 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:12 | 19:24 | 13.2 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:12 | 6:12 | 6:12 | 19:24 | 0 | 0 |  | 13.2 | Waiting for Materials | Open | 0.0010167 | 6.7403 | 151.2623
586 | 2023-07-16 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:12 | 19:24 | 13.2 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:12 | 6:12 | 6:12 | 19:24 | 0 | 0 |  | 13.2 | Waiting for Materials | Open | 0.0010167 | 6.7403 | 151.2623
587 | 2023-07-17 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:00 | 19:40 | 13.6667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:00 | 6:00 | 6:00 | 19:40 | 0 | 0 |  | 13.6667 | Waiting for Materials | Open | 0.0010527 | 6.7403 | 151.2623
588 | 2023-07-17 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:00 | 19:40 | 13.6667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:00 | 6:00 | 6:00 | 19:40 | 0 | 0 |  | 13.6667 | Waiting for Materials | Open | 0.0010527 | 6.7403 | 151.2623
589 | 2023-07-17 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:00 | 19:40 | 13.6667 | IS10 | INV2 | M1 |  |  |  | 1 | 1 | IS10INV2M1 | 1973.16 | 0.5888% | Inverter | Inv Unit_AC Coil failure | AC switch Breaking/ IDC leakage | 12:53 | 12:55 | 13:10 | 19:40 | 0.033333 | 0.28333 |  | 6.7833 | AC Coil replaced | Open | 0.039943 | 3.3 | 5661.5741
590 | 2023-07-17 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:00 | 19:40 | 13.6667 | IS10 | INV2 | M2 |  |  |  | 1 | 1 | IS10INV2M2 | 2223.72 | 0.6636% | Inverter | Inv Unit_AC Coil failure | AC switch Breaking/ IDC leakage | 12:53 | 12:55 | 13:10 | 19:40 | 0.033333 | 0.28333 |  | 6.7833 | AC Coil replaced | Open | 0.045015 | 3.3 | 6380.5041
591 | 2023-07-18 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:05 | 19:35 | 13.5 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:05 | 6:05 | 6:05 | 19:35 | 0 | 0 |  | 13.5 | Waiting for Materials | Open | 0.0010398 | 6.6 | 148.1129
592 | 2023-07-18 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:05 | 19:35 | 13.5 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:05 | 6:05 | 6:05 | 19:35 | 0 | 0 |  | 13.5 | Waiting for Materials | Open | 0.0010398 | 6.6 | 148.1129
593 | 2023-07-19 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:07 | 19:07 | 13 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:07 | 6:07 | 6:07 | 19:07 | 0 | 0 |  | 13 | Waiting for Materials | Open | 0.0010013 | 5.55 | 124.5495
594 | 2023-07-19 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:07 | 19:07 | 13 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:07 | 6:07 | 6:07 | 19:07 | 0 | 0 |  | 13 | Waiting for Materials | Open | 0.0010013 | 5.55 | 124.5495
595 | 2023-07-20 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:00 | 19:30 | 13.5 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:00 | 6:00 | 6:00 | 19:30 | 0 | 0 |  | 13.5 | Waiting for Materials | Open | 0.0010398 | 4.94 | 110.8603
596 | 2023-07-20 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:00 | 19:30 | 13.5 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:00 | 6:00 | 6:00 | 19:30 | 0 | 0 |  | 13.5 | Waiting for Materials | Open | 0.0010398 | 4.94 | 110.8603
597 | 2023-07-21 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:00 | 19:28 | 13.4667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:00 | 6:00 | 6:00 | 19:28 | 0 | 0 |  | 13.4667 | Waiting for Materials | Open | 0.0010373 | 6.22 | 139.5852
598 | 2023-07-21 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:00 | 19:28 | 13.4667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:00 | 6:00 | 6:00 | 19:28 | 0 | 0 |  | 13.4667 | Waiting for Materials | Open | 0.0010373 | 6.22 | 139.5852
599 | 2023-07-22 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:07 | 19:30 | 13.3833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:07 | 6:07 | 6:07 | 19:30 | 0 | 0 |  | 13.3833 | Waiting for Materials | Open | 0.0010308 | 5.09 | 114.2265
600 | 2023-07-22 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:07 | 19:30 | 13.3833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:07 | 6:07 | 6:07 | 19:30 | 0 | 0 |  | 13.3833 | Waiting for Materials | Open | 0.0010308 | 5.09 | 114.2265
601 | 2023-07-23 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:06 | 19:29 | 13.3833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:06 | 6:06 | 6:06 | 19:29 | 0 | 0 |  | 13.3833 | Waiting for Materials | Open | 0.0010308 | 5.4 | 121.1833
602 | 2023-07-23 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:06 | 19:29 | 13.3833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:06 | 6:06 | 6:06 | 19:29 | 0 | 0 |  | 13.3833 | Waiting for Materials | Open | 0.0010308 | 5.4 | 121.1833
603 | 2023-07-24 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 5:55 | 19:26 | 13.5167 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 5:55 | 5:55 | 5:55 | 19:26 | 0 | 0 |  | 13.5167 | Waiting for Materials | Open | 0.0010411 | 5.32 | 119.388
604 | 2023-07-24 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 5:55 | 19:26 | 13.5167 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 5:55 | 5:55 | 5:55 | 19:26 | 0 | 0 |  | 13.5167 | Waiting for Materials | Open | 0.0010411 | 5.32 | 119.388
605 | 2023-07-25 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:09 | 19:20 | 13.1833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:09 | 6:09 | 6:09 | 19:20 | 0 | 0 |  | 13.1833 | Waiting for Materials | Open | 0.0010154 | 5.32 | 119.388
606 | 2023-07-25 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:09 | 19:20 | 13.1833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:09 | 6:09 | 6:09 | 19:20 | 0 | 0 |  | 13.1833 | Waiting for Materials | Open | 0.0010154 | 5.32 | 119.388
607 | 2023-07-26 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:14 | 19:29 | 13.25 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:14 | 6:14 | 6:14 | 19:29 | 0 | 0 |  | 13.25 | Waiting for Materials | Open | 0.0010206 | 4.58 | 102.7814
608 | 2023-07-26 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:14 | 19:29 | 13.25 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:14 | 6:14 | 6:14 | 19:29 | 0 | 0 |  | 13.25 | Waiting for Materials | Open | 0.0010206 | 4.58 | 102.7814
609 | 2023-07-27 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:15 | 19:28 | 13.2167 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:15 | 6:15 | 6:15 | 19:28 | 0 | 0 |  | 13.2167 | Waiting for Materials | Open | 0.001018 | 3.34 | 74.9541
610 | 2023-07-27 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:15 | 19:28 | 13.2167 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:15 | 6:15 | 6:15 | 19:28 | 0 | 0 |  | 13.2167 | Waiting for Materials | Open | 0.001018 | 3.34 | 74.9541
611 | 2023-07-27 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:15 | 19:28 | 13.2167 | IS10 | INV3 | M1 |  |  |  | 1 | 1 | IS10INV3M1 | 1941.84 | 0.5795% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 15:57 | 16:00 | 16:00 | 16:39 | 0.05 | 0.05 | 0.7 | 0.7 | Checked all parameters and found no abnormalities. Inverter reset and charged | Close | 0.0040565 | 0.15 | 253.2594
612 | 2023-07-27 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:15 | 19:28 | 13.2167 | IS10 | INV3 | M2 |  |  |  | 1 | 1 | IS10INV3M2 | 2255.04 | 0.673% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 15:57 | 16:00 | 16:00 | 17:18 | 0.05 | 0.05 | 1.35 | 1.35 | Checked all parameters and found no abnormalities. Inverter reset and charged | Close | 0.009085 | 0.28 | 549.0011
613 | 2023-07-28 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:12 | 19:27 | 13.25 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:12 | 6:12 | 6:12 | 19:27 | 0 | 0 |  | 13.25 | Waiting for Materials | Open | 0.0010206 | 3.65 | 81.9109
614 | 2023-07-28 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:12 | 19:27 | 13.25 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:12 | 6:12 | 6:12 | 19:27 | 0 | 0 |  | 13.25 | Waiting for Materials | Open | 0.0010206 | 3.65 | 81.9109
615 | 2023-07-29 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:08 | 19:40 | 13.5333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:08 | 6:08 | 6:08 | 19:40 | 0 | 0 |  | 13.5333 | Waiting for Materials | Open | 0.0010424 | 4.62 | 103.679
616 | 2023-07-29 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:08 | 19:40 | 13.5333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:08 | 6:08 | 6:08 | 19:40 | 0 | 0 |  | 13.5333 | Waiting for Materials | Open | 0.0010424 | 4.62 | 103.679
617 | 2023-07-29 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:08 | 19:40 | 13.5333 | IS10 | INV3 | M1 |  |  |  | 1 | 1 | IS10INV3M1 | 1941.84 | 0.5795% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 17:39 | 17:39 | 17:39 | 18:11 | 0 | 0 | 0.53333 | 0.53333 | Inverter auto restarted | Close | 0.0030906 | 0.1 | 168.8396
618 | 2023-07-29 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:08 | 19:40 | 13.5333 | IS10 | INV3 | M2 |  |  |  | 1 | 1 | IS10INV3M2 | 2255.04 | 0.673% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 17:39 | 17:39 | 17:39 | 18:26 | 0 | 0 | 0.78333 | 0.78333 | Inverter auto restarted | Close | 0.0052715 | 0.12 | 235.2862
619 | 2023-07-30 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:08 | 19:32 | 13.4 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:08 | 6:08 | 6:08 | 19:32 | 0 | 0 |  | 13.4 | Waiting for Materials | Open | 0.0010321 | 5.68 | 127.4669
620 | 2023-07-30 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:08 | 19:32 | 13.4 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:08 | 6:08 | 6:08 | 19:32 | 0 | 0 |  | 13.4 | Waiting for Materials | Open | 0.0010321 | 5.68 | 127.4669
621 | 2023-07-31 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:08 | 19:32 | 13.4 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:08 | 6:08 | 6:08 | 19:32 | 0 | 0 |  | 13.4 | Waiting for Materials | Open | 0.0010321 | 6.63 | 148.7861
622 | 2023-07-31 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:08 | 19:32 | 13.4 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:08 | 6:08 | 6:08 | 19:32 | 0 | 0 |  | 13.4 | Waiting for Materials | Open | 0.0010321 | 6.63 | 148.7861
623 | 2023-07-31 | FY24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 6:08 | 19:32 | 13.4 | IS18 | INV4 | M2 |  |  |  | 1 | 1 | IS18INV4M2 | 2004.48 | 0.5982% | Inverter | Inv Unit_AC Coil failure | AC switch Disconnection | 6:08 | 6:08 | 6:08 | 8:38 | 0 | 0 | 2.5 | 2.5 | AC Coil replaced | Close | 0.014955 | 0.008 | 13.9429
624 | 2023-08-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:08 | 19:32 | 13.4 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:08 | 6:08 | 6:08 | 19:32 | 0 | 0 |  | 13.4 | Waiting for Materials | Open | 0.0010321 | 6.23 | 138.0076
625 | 2023-08-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:10 | 19:34 | 13.4 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:10 | 6:10 | 6:10 | 19:34 | 0 | 0 |  | 13.4 | Waiting for Materials | Open | 0.0010321 | 5.8 | 128.4822
626 | 2023-08-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:10 | 19:34 | 13.4 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:10 | 6:10 | 6:10 | 19:30 | 0 | 0 |  | 13.3333 | Waiting for Materials | Open | 0.001027 | 4.93 | 109.2098
627 | 2023-08-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:10 | 19:34 | 13.4 | IS11 | INV1 | M1 |  |  |  | 1 | 1 | IS11INV1M1 | 2023.04 | 0.6037% | Inverter | Inv_tripped of GFDI | Inverter tripped in GFDI Fault | 6:30 | 6:30 | 6:30 | 8:46 | 0 | 0 | 2.2667 | 2.2667 | Floting found ok then inverter restart | Close | 0.013685 | 0.42 | 729.2569
628 | 2023-08-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:10 | 19:34 | 13.4 | IS11 | INV1 | M2 |  |  |  | 1 | 1 | IS11INV1M2 | 2212.7 | 0.6603% | Inverter | Inv_tripped of GFDI | Inverter manual trip for rectification of GFDI Fault | 7:50 | 7:50 | 7:50 | 7:57 | 0 | 0 | 0.11667 | 0.11667 | Floting found ok then inverter restart | Close | 0.00077038 | 0.027 | 51.2759
629 | 2023-08-04 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:12 | 19:26 | 13.2333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:12 | 6:12 | 6:12 | 19:26 | 0 | 0 |  | 13.2333 | Waiting for Materials | Open | 0.0010193 | 5.41 | 119.8428
630 | 2023-08-05 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:11 | 19:26 | 13.25 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:11 | 6:11 | 6:11 | 19:26 | 0 | 0 |  | 13.25 | Waiting for Materials | Open | 0.0010206 | 6.17 | 136.6784
631 | 2023-08-05 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:11 | 19:26 | 13.25 | IS18 | INV4 | M1 |  |  |  | 1 | 1 | IS18INV4M1 | 2004.48 | 0.5982% | Inverter | Inv Unit_AC Coil failure | Inverter Unit Manual stop for AC Coil replacement | 7:45 | 7:45 | 7:45 | 8:21 | 0 | 0 | 0.6 | 0.6 | Work completed | Close | 0.0035891 | 0.13 | 223.6515
632 | 2023-08-05 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:11 | 19:26 | 13.25 | IS18 | INV4 | M2 |  |  |  | 1 | 1 | IS18INV4M2 | 2004.48 | 0.5982% | Inverter | Inv Unit_AC Coil failure | Inverter Unit tripped under AC Switch breaking | 6:11 | 6:11 | 6:11 | 8:54 | 0 | 0 | 2.7167 | 2.7167 | AC Coil replaced | Close | 0.016251 | 0.43 | 739.7705
633 | 2023-08-06 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:10 | 19:22 | 13.2 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:10 | 6:10 | 6:10 | 19:25 | 0 | 0 |  | 13.25 | Waiting for Materials | Open | 0.0010206 | 6.42 | 142.2165
634 | 2023-08-07 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:15 | 19:28 | 13.2167 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:15 | 6:15 | 6:15 | 19:28 | 0 | 0 |  | 13.2167 | Waiting for Materials | Open | 0.001018 | 5.92 | 131.1404
635 | 2023-08-08 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:15 | 19:36 | 13.35 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:15 | 6:15 | 6:15 | 19:36 | 0 | 0 |  | 13.35 | Waiting for Materials | Open | 0.0010283 | 6.12 | 135.5708
636 | 2023-08-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:15 | 19:35 | 13.3333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:15 | 6:15 | 6:15 | 19:35 | 0 | 0 |  | 13.3333 | Waiting for Materials | Open | 0.001027 | 5.59 | 123.8302
637 | 2023-08-10 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:15 | 19:30 | 13.25 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:15 | 6:15 | 6:15 | 19:30 | 0 | 0 |  | 13.25 | Waiting for Materials | Open | 0.0010206 | 5.89 | 130.4758
638 | 2023-08-10 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:15 | 19:30 | 13.25 | IS18 | INV4 | M1 |  |  |  | 1 | 1 | IS18INV4M1 | 2004.48 | 0.5982% | Inverter | Inv Unit_AC Coil failure | Inverter manual trip for rectification of AC switch Fault | 7:00 | 7:00 | 7:00 | 7:40 | 0 | 0 | 0.66667 | 0.66667 | Checked all connection and reset | Close | 0.0039879 | 0.07 | 120.4278
639 | 2023-08-10 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:15 | 19:30 | 13.25 | IS18 | INV4 | M2 |  |  |  | 1 | 1 | IS18INV4M2 | 2004.48 | 0.5982% | Inverter | Inv Unit_AC Coil failure | Inverter tripped under AC Switch dis connection fault | 6:15 | 6:15 | 6:15 | 9:23 | 0 | 0 | 3.1333 | 3.1333 | Checked all connection and reset | Close | 0.018743 | 0.43 | 739.7705
640 | 2023-08-10 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:15 | 19:30 | 13.25 | IS2 | INV3 | M1 |  |  |  | 1 | 1 | IS2INV3M1 | 2064.8 | 0.6162% | Inverter | Inv Unit_AC Coil failure | Inverter tripped under AC Switch dis connection fault | 6:15 | 6:15 | 6:15 | 8:42 | 0 | 0 | 2.45 | 2.45 | Checked all connection and reset | Close | 0.015097 | 0.26 | 460.7636
641 | 2023-08-11 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:12 | 19:23 | 13.1833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:12 | 6:12 | 6:12 | 19:23 | 0 | 0 |  | 13.1833 | Waiting for Materials | Open | 0.0010154 | 5.52 | 122.2796
642 | 2023-08-12 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:13 | 19:25 | 13.2 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:13 | 6:13 | 6:13 | 19:25 | 0 | 0 |  | 13.2 | Waiting for Materials | Open | 0.0010167 | 5.8 | 128.4822
643 | 2023-08-13 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:15 | 19:25 | 13.1667 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:15 | 6:15 | 6:15 | 19:25 | 0 | 0 |  | 13.1667 | Waiting for Materials | Open | 0.0010141 | 5.12 | 113.4187
644 | 2023-08-14 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:18 | 19:20 | 13.0333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:18 | 6:18 | 6:18 | 19:25 | 0 | 0 |  | 13.1167 | Waiting for Materials | Open | 0.0010103 | 5.55 | 122.9441
645 | 2023-08-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:19 | 19:18 | 12.9833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:19 | 6:19 | 6:19 | 19:18 | 0 | 0 |  | 12.9833 | Waiting for Materials | Open | 0.001 | 4.13 | 91.4882
646 | 2023-08-16 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:14 | 19:20 | 13.1 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:14 | 6:14 | 6:14 | 19:20 | 0 | 0 |  | 13.1 | Waiting for Materials | Open | 0.001009 | 5.64 | 124.9378
647 | 2023-08-17 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:16 | 19:11 | 12.9167 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:15 | 6:15 | 6:15 | 19:10 | 0 | 0 |  | 12.9167 | Waiting for Materials | Open | 0.00099489 | 5.32 | 117.8491
648 | 2023-08-17 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:16 | 19:11 | 12.9167 | IS1 | INV1 | M1 | SCB1 |  |  | 1 | 1 | IS1INV1M1SCB1 | 232.29 | 0.06932% | Cables | String Cable Theft | String cable theft | 6:15 | 6:15 | 6:15 | 17:30 | 0 | 0 | 11.25 | 11.25 | Restoration completed | Close | 0.0077987 | 5.32 | 1060.6423
649 | 2023-08-17 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:16 | 19:11 | 12.9167 | IS1 | INV1 | M1 | SCB2 |  |  | 1 | 1 | IS1INV1M1SCB2 | 232.29 | 0.06932% | Cables | String Cable Theft | String cable theft | 6:15 | 6:15 | 6:15 | 19:10 | 0 | 0 |  | 12.9167 | Restoration WIP | Open | 0.008954 | 5.32 | 1060.6423
650 | 2023-08-17 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:16 | 19:11 | 12.9167 | IS2 | INV1 | M1 | SCB2 |  |  | 1 | 1 | IS2INV1M1SCB2 | 232.29 | 0.06932% | Cables | String Cable Theft | String cable theft | 6:15 | 6:15 | 6:15 | 19:10 | 0 | 0 |  | 12.9167 | Restoration WIP | Open | 0.008954 | 5.32 | 1060.6423
651 | 2023-08-17 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:16 | 19:11 | 12.9167 | IS2 | INV1 | M2 | SCB2 |  |  | 1 | 1 | IS2INV1M2SCB2 | 232.29 | 0.06932% | Cables | String Cable Theft | String cable theft | 6:15 | 6:15 | 6:15 | 16:40 | 0 | 0 | 10.4167 | 10.4167 | Restoration completed | Close | 0.007221 | 5.32 | 1060.6423
652 | 2023-08-17 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:16 | 19:11 | 12.9167 | IS2 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS2INV1M2SCB3 | 232.29 | 0.06932% | Cables | String Cable Theft | String cable theft | 6:15 | 6:15 | 6:15 | 19:00 | 0 | 0 | 12.75 | 12.75 | Restoration completed | Close | 0.0088385 | 5.32 | 1060.6423
653 | 2023-08-17 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:16 | 19:11 | 12.9167 | IS2 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS2INV1M2SCB6 | 232.29 | 0.06932% | Cables | String Cable Theft | String cable theft | 6:15 | 6:15 | 6:15 | 19:10 | 0 | 0 |  | 12.9167 | Restoration WIP | Open | 0.008954 | 5.32 | 1060.6423
654 | 2023-08-17 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:16 | 19:11 | 12.9167 | IS2 | INV1 | M2 | SCB7 |  |  | 1 | 1 | IS2INV1M2SCB7 | 232.29 | 0.06932% | Cables | String Cable Theft | String cable theft | 6:15 | 6:15 | 6:15 | 19:10 | 0 | 0 |  | 12.9167 | Restoration WIP | Open | 0.008954 | 5.32 | 1060.6423
655 | 2023-08-18 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:16 | 19:28 | 13.2 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:15 | 6:15 | 6:15 | 19:10 | 0 | 0 |  | 12.9167 | Waiting for Materials | Open | 0.00099489 | 5.32 | 117.8491
656 | 2023-08-18 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:16 | 19:28 | 13.2 | IS1 | INV1 | M1 | SCB2 |  |  | 1 | 1 | IS1INV1M1SCB2 | 232.29 | 0.06932% | Cables | String Cable Theft | String cable theft | 6:16 | 6:16 | 6:16 | 17:15 | 0 | 0 | 10.9833 | 10.9833 | Restoration completed | Close | 0.0076138 | 6.49 | 1293.9039
657 | 2023-08-18 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:16 | 19:28 | 13.2 | IS2 | INV1 | M1 | SCB2 |  |  | 1 | 1 | IS2INV1M1SCB2 | 232.29 | 0.06932% | Cables | String Cable Theft | String cable theft | 6:16 | 6:16 | 6:16 | 13:26 | 0 | 0 | 7.1667 | 7.1667 | Restoration completed | Close | 0.004968 | 3.85 | 767.5701
658 | 2023-08-18 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:16 | 19:28 | 13.2 | IS2 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS2INV1M2SCB6 | 232.29 | 0.06932% | Cables | String Cable Theft | String cable theft | 6:16 | 6:16 | 6:16 | 10:07 | 0 | 0 | 3.85 | 3.85 | Restoration completed | Close | 0.0026689 | 1.11 | 221.2994
659 | 2023-08-18 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:16 | 19:28 | 13.2 | IS2 | INV1 | M2 | SCB7 |  |  | 1 | 1 | IS2INV1M2SCB7 | 232.29 | 0.06932% | Cables | String Cable Theft | String cable theft | 6:16 | 6:16 | 6:16 | 11:24 | 0 | 0 | 5.1333 | 5.1333 | Restoration completed | Close | 0.0035585 | 1.98 | 394.7503
660 | 2023-08-19 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:20 | 19:23 | 13.05 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | 6:20 | 6:20 | 19:23 | 0 | 0 |  | 13.05 | Waiting for Materials | Open | 0.0010052 | 6.77 | 149.9697
661 | 2023-08-20 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:21 | 19:16 | 12.9167 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:21 | 6:21 | 6:21 | 19:16 | 0 | 0 |  | 12.9167 | Waiting for Materials | Open | 0.00099489 | 4.22 | 93.4818
662 | 2023-08-21 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:19 | 19:25 | 13.1 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:19 | 6:19 | 6:19 | 19:25 | 0 | 0 |  | 13.1 | Waiting for Materials | Open | 0.001009 | 6.41 | 141.9949
663 | 2023-08-21 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:19 | 19:25 | 13.1 | IS2 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS2INV1M2SCB4 | 232.29 | 0.06932% | SCB | Inv_tripped of GFDI | Cable Fault on GFDI | 14:46 | 14:46 | 14:46 | 19:25 | 0 | 0 |  | 4.65 | Work in progress | Open | 0.0032234 | 1.4 | 279.1164
664 | 2023-08-21 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:19 | 19:25 | 13.1 | IS2 | INV1 | M1 |  |  |  | 1 | 1 | IS2INV1M1 | 2090.61 | 0.6239% | Inverter | Inv_Manual stop | Inverter Unit Manual stop for fault rectification | 14:46 | 14:46 | 14:46 | 15:06 | 0 | 0 | 0.33333 | 0.33333 | Restoration completed | Close | 0.0020796 | 0.2 | 358.8639
665 | 2023-08-21 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:19 | 19:25 | 13.1 | IS2 | INV1 | M2 |  |  |  | 1 | 1 | IS2INV1M2 | 2090.61 | 0.6239% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 14:46 | 14:46 | 14:46 | 17:57 | 0 | 0 | 3.1833 | 3.1833 | Restoration completed | Close | 0.019861 | 1.4 | 2512.0476
666 | 2023-08-21 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:19 | 19:25 | 13.1 | IS3 | INV4 | M1 | SCB5 |  |  | 1 | 1 | IS3INV4M1SCB5 | 234.9 | 0.0701% | SCB | Inv_tripped of GFDI | Cable Fault on GFDI | 14:46 | 14:46 | 14:46 | 19:25 | 0 | 0 |  | 4.65 | Work in progress | Open | 0.0032597 | 1.4 | 282.2525
667 | 2023-08-21 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:19 | 19:25 | 13.1 | IS3 | INV4 | M1 |  |  |  | 1 | 1 | IS3INV4M1 | 2114.1 | 0.6309% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 14:46 | 14:46 | 14:46 | 18:30 | 0 | 0 | 3.7333 | 3.7333 | Restoration completed | Close | 0.023554 | 1.3 | 2358.8248
668 | 2023-08-21 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:19 | 19:25 | 13.1 | IS3 | INV4 | M2 |  |  |  | 1 | 1 | IS3INV4M2 | 2088 | 0.6231% | Inverter | Inv_Manual Stop | Inverter Unit Manual stop for fault rectification | 16:36 | 16:36 | 16:36 | 16:47 | 0 | 0 | 0.18333 | 0.18333 | Restoration completed | Close | 0.0011424 | 0.1 | 179.208
669 | 2023-08-22 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:17 | 19:26 | 13.15 | IS2 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS2INV1M2SCB4 | 232.29 | 0.06932% | SCB | Inv_tripped of GFDI | Cable Fault on GFDI | 6:17 | 6:17 | 6:17 | 19:25 | 0 | 0 |  | 13.1333 | Work in progress | Open | 0.0091042 | 7.1 | 1415.5189
670 | 2023-08-22 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:17 | 19:26 | 13.15 | IS3 | INV4 | M1 | SCB5 |  |  | 1 | 1 | IS3INV4M1SCB5 | 234.9 | 0.0701% | SCB | Inv_tripped of GFDI | Cable Fault on GFDI | 6:17 | 6:17 | 6:17 | 19:25 | 0 | 0 |  | 13.1333 | Work in progress | Open | 0.0092065 | 7.1 | 1431.4236
671 | 2023-08-22 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:17 | 19:26 | 13.15 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:17 | 6:17 | 6:17 | 19:25 | 0 | 0 |  | 13.1333 | Waiting for Materials | Open | 0.0010116 | 7.1 | 157.2799
672 | 2023-08-23 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:23 | 19:19 | 12.9333 | IS2 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS2INV1M2SCB4 | 232.29 | 0.06932% | SCB | Inv_tripped of GFDI | Cable Fault on GFDI | 6:19 | 6:19 | 6:19 | 19:19 | 0 | 0 |  | 13 | Work in progress | Open | 0.0090118 | 5.3 | 1056.655
673 | 2023-08-23 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:23 | 19:19 | 12.9333 | IS3 | INV4 | M1 | SCB5 |  |  | 1 | 1 | IS3INV4M1SCB5 | 234.9 | 0.0701% | SCB | Inv_tripped of GFDI | Cable Fault on GFDI | 6:19 | 6:19 | 6:19 | 19:19 | 0 | 0 |  | 13 | Work in progress | Open | 0.009113 | 5.3 | 1068.5275
674 | 2023-08-23 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:23 | 19:19 | 12.9333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:19 | 6:19 | 6:19 | 19:19 | 0 | 0 |  | 13 | Waiting for Materials | Open | 0.0010013 | 5.3 | 117.4061
675 | 2023-08-24 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:25 | 19:15 | 12.8333 | IS2 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS2INV1M2SCB4 | 232.29 | 0.06932% | SCB | Inv_tripped of GFDI | Cable Fault on GFDI | 6:25 | 6:25 | 6:25 | 19:15 | 0 | 0 |  | 12.8333 | Work in progress | Open | 0.0088963 | 5.79 | 1154.3457
676 | 2023-08-24 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:25 | 19:15 | 12.8333 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:25 | 6:25 | 6:25 | 19:15 | 0 | 0 |  | 12.8333 | Waiting for Materials | Open | 0.00098847 | 5.79 | 128.2606
677 | 2023-08-25 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:25 | 19:16 | 12.85 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:25 | 6:25 | 6:25 | 19:16 | 0 | 0 |  | 12.85 | Waiting for Materials | Open | 0.00098976 | 5.7 | 126.2669
678 | 2023-08-26 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:19 | 19:10 | 12.85 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:19 | 6:19 | 6:19 | 19:10 | 0 | 0 |  | 12.85 | Waiting for Materials | Open | 0.00098976 | 4.55 | 100.792
679 | 2023-08-27 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:21 | 19:10 | 12.8167 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:21 | 6:21 | 6:21 | 19:10 | 0 | 0 |  | 12.8167 | Waiting for Materials | Open | 0.00098719 | 5.05 | 111.8681
680 | 2023-08-28 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:22 | 19:09 | 12.7833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:22 | 6:22 | 6:22 | 19:09 | 0 | 0 |  | 12.7833 | Waiting for Materials | Open | 0.00098462 | 5.76 | 127.5961
681 | 2023-08-29 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:22 | 19:09 | 12.7833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:22 | 6:22 | 6:22 | 19:09 | 0 | 0 |  | 12.7833 | Waiting for Materials | Open | 0.00098462 | 5.4735 | 121.2499
682 | 2023-08-29 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:22 | 19:09 | 12.7833 | IS12 | INV1 | M2 |  |  |  | 1 | 1 | IS12INV1M2 | 2114.1 | 0.6309% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 9:10 | 9:10 | 9:10 | 10:00 | 0 | 0 | 0.83333 | 0.83333 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.0052575 | 0.16936 | 307.2931
683 | 2023-08-29 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:22 | 19:09 | 12.7833 | IS12 | INV4 | M1 |  |  |  | 1 | 1 | IS12INV4M1 | 2004.48 | 0.5982% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 8:55 | 8:55 | 8:55 | 9:45 | 0 | 0 | 0.83333 | 0.83333 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.0049849 | 0.10706 | 184.1889
684 | 2023-08-29 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:22 | 19:09 | 12.7833 | IS12 | INV4 | M2 |  |  |  | 1 | 1 | IS12INV4M2 | 2208.06 | 0.6589% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 8:55 | 8:55 | 8:55 | 9:12 | 0 | 0 | 0.28333 | 0.28333 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.001867 | 0.015483 | 29.3427
685 | 2023-08-29 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:22 | 19:09 | 12.7833 | IS9 | INV1 | M1 |  |  |  | 1 | 1 | IS9INV1M1 | 2102.065 | 0.6273% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 8:58 | 8:58 | 8:58 | 9:45 | 0 | 0 | 0.78333 | 0.78333 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.0049139 | 0.10706 | 193.1559
686 | 2023-08-29 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:22 | 19:09 | 12.7833 | IS11 | INV1 | M1 |  |  |  | 1 | 1 | IS11INV1M1 | 2023.04 | 0.6037% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 9:08 | 9:08 | 9:08 | 10:08 | 0 | 0 | 1 | 1 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.0060373 | 0.22058 | 382.9918
687 | 2023-08-29 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:22 | 19:09 | 12.7833 | IS17 | INV4 | M1 |  |  |  | 1 | 1 | IS17INV4M1 | 2004.48 | 0.5982% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 9:05 | 9:05 | 9:05 | 9:38 | 0 | 0 | 0.55 | 0.55 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.00329 | 0.072387 | 124.5342
688 | 2023-08-29 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:22 | 19:09 | 12.7833 | IS10 | INV3 | M1 |  |  |  | 1 | 1 | IS10INV3M1 | 1941.84 | 0.5795% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 9:01 | 9:01 | 9:01 | 10:13 | 0 | 0 | 1.2 | 1.2 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.006954 | 0.25674 | 427.8849
689 | 2023-08-30 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:20 | 19:07 | 12.7833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | 6:20 | 6:20 | 19:07 | 0 | 0 |  | 12.7833 | Waiting for Materials | Open | 0.00098462 | 6.96 | 154.1786
690 | 2023-08-31 | FY24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 6:20 | 19:07 | 12.7833 | IS2 | INV1 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | 6:20 | 6:20 | 19:07 | 0 | 0 |  | 12.7833 | Waiting for Materials | Open | 0.00098462 | 7.05 | 156.1723
691 | 2023-09-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:20 | 19:06 | 12.7667 | IS2 | INV1 | M2 | SCB4 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | 6:20 | 6:20 | 19:06 | 0 | 0 |  | 12.7667 | Waiting for Materials | Open | 0.00049167 | 7.12 | 75.31
692 | 2023-09-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:20 | 19:06 | 12.7667 | IS2 | INV1 | M2 | SCB8 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Cables | String Cable Theft | String cable theft | 6:20 | 6:20 | 6:20 | 11:55 | 0 | 0 | 5.5833 | 5.5833 | Restoration completed | Close | 0.00021502 | 2.6 | 27.5008
693 | 2023-09-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:20 | 19:06 | 12.7667 | IS2 | INV1 | M2 | SCB8 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Cables | String Cable Theft | String cable theft | 6:20 | 6:20 | 6:20 | 11:55 | 0 | 0 | 5.5833 | 5.5833 | Restoration completed | Close | 0.00021502 | 2.6 | 27.5008
694 | 2023-09-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:20 | 19:06 | 12.7667 | IS2 | INV1 | M2 | SCB8 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Cables | String Cable Theft | String cable theft | 6:20 | 6:20 | 6:20 | 11:55 | 0 | 0 | 5.5833 | 5.5833 | Restoration completed | Close | 0.00021502 | 2.6 | 27.5008
695 | 2023-09-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:20 | 19:06 | 12.7667 | IS2 | INV1 | M2 | SCB8 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Cables | String Cable Theft | String cable theft | 6:20 | 6:20 | 6:20 | 11:55 | 0 | 0 | 5.5833 | 5.5833 | Restoration completed | Close | 0.00021502 | 2.6 | 27.5008
696 | 2023-09-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:20 | 19:06 | 12.7667 | IS2 | INV1 | M2 | SCB8 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Cables | String Cable Theft | String cable theft | 6:20 | 6:20 | 6:20 | 11:55 | 0 | 0 | 5.5833 | 5.5833 | Restoration completed | Close | 0.00021502 | 2.6 | 27.5008
697 | 2023-09-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:20 | 19:06 | 12.7667 | IS2 | INV1 | M2 | SCB2 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Cables | String Cable Theft | String cable theft | 6:20 | 6:20 | 6:20 | 12:17 | 0 | 0 | 5.95 | 5.95 | Restoration completed | Close | 0.00022915 | 2.94 | 31.0971
698 | 2023-09-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:20 | 19:06 | 12.7667 | IS2 | INV1 | M2 | SCB9 |  |  | 1 | 1 | IS2INV1M2SCB9 | 232.29 | 0.06932% | SCB | String Cable Theft | String cable theft | 6:20 | 6:20 | 6:20 | 15:45 | 0 | 0 | 9.4167 | 9.4167 | Restoration completed | Close | 0.0065278 | 6.02 | 1146.1505
699 | 2023-09-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:20 | 19:06 | 12.7667 | IS15 | INV3 | M2 |  |  |  | 1 | 1 | IS15INV3M2 | 2192.4 | 0.6543% | Inverter | Inv Unit_AC Coil failure | AC switch Disconnection | 6:20 | 6:20 | 6:20 | 7:52 | 0 | 0 | 1.5333 | 1.5333 | AC Coil replaced | Close | 0.010032 | 0.12 | 215.6332
700 | 2023-09-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:20 | 19:06 | 12.7667 | IS15 | INV3 | M1 |  |  |  | 1 | 1 | IS15INV3M1 | 2223.72 | 0.6636% | Inverter | Inv_Manual Stop | Inverter Unit Manual stop for AC Coil replacement | 7:20 | 7:20 | 7:20 | 7:52 | 0 | 0 | 0.53333 | 0.53333 | AC Coil replaced | Close | 0.0035393 | 0.1 | 182.2614
701 | 2023-09-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:20 | 19:04 | 12.7333 | IS2 | INV1 | M2 | SCB4 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | 6:20 | 6:20 | 19:04 | 0 | 0 |  | 12.7333 | Waiting for Materials | Open | 0.00049039 | 7.39 | 78.1659
702 | 2023-09-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:20 | 19:04 | 12.7333 | IS2 | INV1 | M2 | SCB4 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Module | PV Module theft | PV modules removed by unknown Person | 6:20 | 6:20 | 6:20 | 19:04 | 0 | 0 |  | 12.7333 | Waiting for Materials | Open | 0.00049039 | 7.24 | 76.5793
703 | 2023-09-04 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:28 | 18:51 | 12.3833 | IS2 | INV1 | M2 | SCB4 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Module | PV Module theft | PV modules removed by unknown Person | 6:28 | 6:28 | 6:28 | 18:51 | 0 | 0 |  | 12.3833 | Waiting for Materials | Open | 0.00047691 | 7.18 | 75.9446
704 | 2023-09-05 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:29 | 18:48 | 12.3167 | IS2 | INV1 | M2 | SCB4 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Module | PV Module theft | PV modules removed by unknown Person | 6:29 | 6:29 | 6:29 | 18:48 | 0 | 0 |  | 12.3167 | Waiting for Materials | Open | 0.00047434 | 7.0507 | 74.577
705 | 2023-09-06 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:22 | 18:59 | 12.6167 | IS2 | INV1 | M2 | SCB4 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Module | PV Module theft | PV modules removed by unknown Person | 6:18 | 6:18 | 6:18 | 18:48 | 0 | 0 |  | 12.5 | Waiting for Materials | Open | 0.0004814 | 6.79 | 71.8195
706 | 2023-09-06 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:22 | 18:59 | 12.6167 | IS10 |  |  |  |  | Tx | 0 | 1 | IS10Tx | 16756.2 | 5% | IDT | Tx_Tripped in High WTI temp | IDT tripped in LV winding-4 fault | 13:40 | 13:40 | 13:40 | 14:18 | 0 | 0 | 0.63333 | 0.63333 | Checked related parameter and IDT charged | Close | 0.03167 | 0.61 | 8377.6079
707 | 2023-09-07 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:23 | 18:57 | 12.5667 | IS2 | INV1 | M2 | SCB4 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Module | PV Module theft | PV modules removed by unknown Person | 6:23 | 6:23 | 6:23 | 18:57 | 0 | 0 |  | 12.5667 | Waiting for Materials | Open | 0.00048397 | 6.5 | 68.7521
708 | 2023-09-08 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:26 | 18:57 | 12.5167 | IS2 | INV1 | M2 | SCB4 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Module | PV Module theft | PV modules removed by unknown Person | 6:26 | 6:26 | 6:26 | 18:57 | 0 | 0 |  | 12.5167 | Waiting for Materials | Open | 0.00048204 | 6.51 | 68.8579
709 | 2023-09-08 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:26 | 18:57 | 12.5167 | IS10 |  |  |  |  | Tx | 0 | 1 | IS10Tx | 16756.2 | 5% | IDT | Tx_Tripped in High WTI temp | IDT tripped in LV winding-4 fault | 13:49 | 13:49 | 13:49 | 14:22 | 0 | 0 | 0.55 | 0.55 | Checked related parameter and IDT charged | Close | 0.027503 | 0.52 | 7141.5674
710 | 2023-09-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:26 | 18:56 | 12.5 | IS2 | INV1 | M2 | SCB4 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Module | PV Module theft | PV modules removed by unknown Person | 6:26 | 6:26 | 6:26 | 18:56 | 0 | 0 |  | 12.5 | Waiting for Materials | Open | 0.0004814 | 6.85 | 72.4541
711 | 2023-09-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:26 | 18:56 | 12.5 | IS11 |  |  |  |  | Tx | 0 | 1 | IS11Tx | 16595.25 | 4.952% | IDT | Tx_Manual trip for LV thermography | IDT manual tripped for LV side thermography | 12:36 | 12:36 | 12:36 | 12:48 | 0 | 0 | 0.2 | 0.2 | IDT charged after thermography | Close | 0.0099049 | 0.21 | 2856.3916
712 | 2023-09-10 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:28 | 18:55 | 12.45 | IS2 | INV1 | M2 | SCB4 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Module | PV Module theft | PV modules removed by unknown Person | 6:28 | 6:28 | 6:28 | 18:55 | 0 | 0 |  | 12.45 | Waiting for Materials | Open | 0.00047947 | 6.6 | 69.8098
713 | 2023-09-11 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:29 | 19:00 | 12.5167 | IS2 | INV1 | M2 | SCB4 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Module | PV Module theft | PV modules removed by unknown Person | 6:29 | 6:29 | 6:29 | 19:00 | 0 | 0 |  | 12.5167 | Waiting for Materials | Open | 0.00048204 | 6.66 | 70.4445
714 | 2023-09-11 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:29 | 19:00 | 12.5167 | IS12 |  |  |  |  | Tx | 0 | 1 | IS12Tx | 16912.8 | 5.047% | IDT | Tx_Manual trip for LV thermography | IDT manual tripped for LV side thermography | 13:30 | 13:30 | 13:30 | 13:41 | 0 | 0 | 0.18333 | 0.18333 | IDT charged after thermography | Close | 0.0092532 | 0.18 | 2495.1846
715 | 2023-09-12 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:25 | 18:43 | 12.3 | IS2 | INV1 | M2 | SCB4 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Module | PV Module theft | PV modules removed by unknown Person | 6:25 | 6:25 | 6:25 | 18:43 | 0 | 0 |  | 12.3 | Waiting for Materials | Open | 0.0004737 | 6.86 | 72.5599
716 | 2023-09-12 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:25 | 18:43 | 12.3 | IS20 |  |  |  |  | Tx | 0 | 1 | IS20Tx | 17539.2 | 5.234% | IDT | Tx_Manual trip for LV thermography | IDT manual tripped for LV side thermography | 12:33 | 12:33 | 12:33 | 12:45 | 0 | 0 | 0.2 | 0.2 | IDT charged after thermography | Close | 0.010468 | 0.19 | 2731.3543
717 | 2023-09-13 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:26 | 18:51 | 12.4167 | IS2 | INV1 | M2 | SCB4 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Module | PV Module theft | PV modules removed by unknown Person | 6:26 | 6:26 | 6:26 | 18:51 | 0 | 0 |  | 12.4167 | Waiting for Materials | Open | 0.00047819 | 6.43 | 68.0117
718 | 2023-09-14 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:48 | 18:52 | 12.0667 | IS2 | INV1 | M2 | SCB4 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Module | PV Module theft | PV modules removed by unknown Person | 6:48 | 6:48 | 6:48 | 18:52 | 0 | 0 |  | 12.0667 | Waiting for Materials | Open | 0.00046471 | 4.2 | 44.4244
719 | 2023-09-14 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:48 | 18:52 | 12.0667 | IS9 | INV1 | M1 |  |  |  | 1 | 1 | IS9INV1M1 | 2102.065 | 0.6273% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 13:59 | 13:59 | 14:09 | 14:22 | 0 | 0.16667 | 0.38333 | 0.38333 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.0024047 | 0.14 | 241.2064
720 | 2023-09-14 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:48 | 18:52 | 12.0667 | IS9 | INV1 | M1 |  |  |  | 1 | 1 | IS9INV1M1 | 2102.065 | 0.6273% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 15:06 | 15:06 | 15:10 | 15:57 | 0 | 0.066667 | 0.85 | 0.85 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.0053321 | 0.21 | 361.8096
721 | 2023-09-14 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:48 | 18:52 | 12.0667 | IS9 | INV1 | M2 |  |  |  | 1 | 1 | IS9INV1M2 | 2023.04 | 0.6037% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 13:59 | 13:59 | 14:06 | 14:22 | 0 | 0.11667 | 0.38333 | 0.38333 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.0023143 | 0.14 | 232.1385
722 | 2023-09-14 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:48 | 18:52 | 12.0667 | IS9 | INV3 | M1 |  |  |  | 1 | 1 | IS9INV3M1 | 2275.33 | 0.679% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 15:08 | 15:08 | 15:20 | 15:58 | 0 | 0.2 | 0.83333 | 0.83333 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.0056585 | 0.14 | 261.0881
723 | 2023-09-14 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:48 | 18:52 | 12.0667 | IS10 | INV2 | M2 |  |  |  | 1 | 1 | IS10INV2M2 | 2223.72 | 0.6636% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 15:06 | 15:06 | 15:10 | 16:09 | 0 | 0.066667 | 1.05 | 1.05 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.006968 | 0.31 | 565.0104
724 | 2023-09-14 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:48 | 18:52 | 12.0667 | IS10 | INV3 | M1 |  |  |  | 1 | 1 | IS10INV3M1 | 1941.84 | 0.5795% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 14:33 | 14:33 | 14:40 | 14:53 | 0 | 0.11667 | 0.33333 | 0.33333 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.0019317 | 0.07 | 111.4105
725 | 2023-09-14 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:48 | 18:52 | 12.0667 | IS10 | INV3 | M2 |  |  |  | 1 | 1 | IS10INV3M2 | 2255.04 | 0.673% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 14:33 | 14:33 | 14:40 | 15:32 | 0 | 0.11667 | 0.98333 | 0.98333 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.0066175 | 0.15 | 277.2427
726 | 2023-09-14 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:48 | 18:52 | 12.0667 | IS11 | INV1 | M1 |  |  |  | 1 | 1 | IS11INV1M1 | 2023.04 | 0.6037% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 13:56 | 13:56 | 14:10 | 14:30 | 0 | 0.23333 | 0.56667 | 0.56667 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.0034211 | 0.14 | 232.1385
727 | 2023-09-14 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:48 | 18:52 | 12.0667 | IS11 | INV1 | M2 |  |  |  | 1 | 1 | IS11INV1M2 | 2212.7 | 0.6603% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 13:56 | 13:56 | 14:10 | 14:05 | 0 | 0.23333 | 0.15 | 0.15 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.00099049 | 0.05 | 90.6791
728 | 2023-09-14 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:48 | 18:52 | 12.0667 | IS12 | INV1 | M2 |  |  |  | 1 | 1 | IS12INV1M2 | 2114.1 | 0.6309% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 13:58 | 13:58 | 14:10 | 14:27 | 0 | 0.2 | 0.48333 | 0.48333 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.0030494 | 0.14 | 242.5874
729 | 2023-09-14 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:48 | 18:52 | 12.0667 | IS12 | INV1 | M2 |  |  |  | 1 | 1 | IS12INV1M2 | 2114.1 | 0.6309% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 15:07 | 15:07 | 15:15 | 15:28 | 0 | 0.13333 | 0.35 | 0.35 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.0022082 | 0.04 | 69.3107
730 | 2023-09-14 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:48 | 18:52 | 12.0667 | IS12 | INV4 | M1 |  |  |  | 1 | 1 | IS12INV4M1 | 2004.48 | 0.5982% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 15:10 | 15:10 | 15:15 | 15:50 | 0 | 0.083333 | 0.66667 | 0.66667 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.0039879 | 0.13 | 213.5796
731 | 2023-09-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:40 | 18:51 | 12.1833 | IS2 | INV1 | M2 | SCB4 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Module | PV Module theft | PV modules removed by unknown Person | 6:40 | 6:40 | 6:40 | 18:51 | 0 | 0 |  | 12.1833 | Waiting for Materials | Open | 0.0004692 | 5.11 | 54.0497
732 | 2023-09-16 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:42 | 18:55 | 12.2167 | IS2 | INV1 | M2 | SCB4 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Module | PV Module theft | PV modules removed by unknown Person | 6:42 | 6:42 | 6:42 | 18:55 | 0 | 0 |  | 12.2167 | Waiting for Materials | Open | 0.00047049 | 5.2067 | 55.0725
733 | 2023-09-17 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:28 | 18:48 | 12.3333 | IS2 | INV1 | M2 | SCB4 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Module | PV Module theft | PV modules removed by unknown Person | 6:28 | 6:28 | 6:28 | 18:48 | 0 | 0 |  | 12.3333 | Waiting for Materials | Open | 0.00047498 | 5.2067 | 55.0725
734 | 2023-09-17 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:28 | 18:48 | 12.3333 | IS8 | INV1 | M1 |  |  |  | 1 | 1 | IS8INV1M1 | 2004.48 | 0.5982% | Inverter | inv_tripped of IDM.com fit | Inverter tripped after PL card change | 6:28 | 6:28 | 6:28 | 7:26 | 0 | 0 | 0.96667 | 0.96667 | Setting changed as per OEM and inverter charged | Close | 0.0057825 | 0.04 | 65.7168
735 | 2023-09-17 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:28 | 18:48 | 12.3333 | IS8 | INV4 | M1 |  |  |  | 1 | 1 | IS8INV4M1 | 2088 | 0.6231% | Inverter | inv_tripped of IDM.com fit | Inverter tripped after PL card change | 6:28 | 6:28 | 6:28 | 8:02 | 0 | 0 | 1.5667 | 1.5667 | Setting changed as per OEM and inverter charged | Close | 0.0097621 | 0.2 | 342.275
736 | 2023-09-18 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:32 | 18:45 | 12.2167 | IS2 | INV1 | M2 | SCB4 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Module | PV Module theft | PV modules removed by unknown Person | 6:32 | 6:32 | 6:32 | 18:45 | 0 | 0 |  | 12.2167 | Waiting for Materials | Open | 0.00047049 | 2.72 | 28.7701
737 | 2023-09-18 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:32 | 18:45 | 12.2167 | IS9 | INV1 | M1 |  |  |  | 1 | 1 | IS9INV1M1 | 2102.065 | 0.6273% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 14:54 | 14:54 | 14:54 | 15:15 | 0 | 0 | 0.35 | 0.35 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.0021956 | 0.15 | 258.4354
738 | 2023-09-18 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:32 | 18:45 | 12.2167 | IS9 | INV1 | M2 |  |  |  | 1 | 1 | IS9INV1M2 | 2023.04 | 0.6037% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 14:54 | 14:54 | 14:54 | 15:15 | 0 | 0 | 0.35 | 0.35 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.002113 | 0.15 | 248.7198
739 | 2023-09-18 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:32 | 18:45 | 12.2167 | IS11 | INV1 | M1 |  |  |  | 1 | 1 | IS11INV1M1 | 2023.04 | 0.6037% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 14:27 | 14:27 | 14:27 | 15:39 | 0 | 0 | 1.2 | 1.2 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.0072447 | 0.32 | 530.6023
740 | 2023-09-19 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:30 | 18:26 | 11.9333 | IS2 | INV1 | M2 | SCB4 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Module | PV Module theft | PV modules removed by unknown Person | 6:30 | 6:30 | 6:30 | 18:26 | 0 | 0 |  | 11.9333 | Waiting for Materials | Open | 0.00045958 | 3.14 | 33.2126
741 | 2023-09-19 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:30 | 18:26 | 11.9333 | IS9 | INV1 | M1 |  |  |  | 1 | 1 | IS9INV1M1 | 2102.065 | 0.6273% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 9:37 | 9:37 | 9:37 | 10:00 | 0 | 0 | 0.38333 | 0.38333 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.0024047 | 0.11 | 189.5193
742 | 2023-09-20 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:46 | 18:41 | 11.9167 | IS2 | INV1 | M2 | SCB4 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Module | PV Module theft | PV modules removed by unknown Person | 6:46 | 6:46 | 6:46 | 18:41 | 0 | 0 |  | 11.9167 | Waiting for Materials | Open | 0.00045893 | 4.7 | 49.7131
743 | 2023-09-21 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:29 | 18:45 | 12.2667 | IS2 | INV1 | M2 | SCB4 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Module | PV Module theft | PV modules removed by unknown Person | 6:29 | 6:29 | 6:29 | 18:45 | 0 | 0 |  | 12.2667 | Waiting for Materials | Open | 0.00047241 | 6.2 | 65.5789
744 | 2023-09-22 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:33 | 18:43 | 12.1667 | IS9 | INV1 | M1 |  |  |  | 1 | 1 | IS9INV1M1 | 2102.065 | 0.6273% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 6:33 | 6:33 | 6:33 | 8:30 | 0 | 0 | 1.95 | 1.95 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.012233 | 0.27 | 465.1838
745 | 2023-09-22 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:33 | 18:43 | 12.1667 | IS13 | INV4 | M2 |  |  |  | 1 | 1 | IS13INV4M2 | 2004.48 | 0.5982% | Inverter | Inv Unit_AC Coil failure | AC switch Disconnection | 6:33 | 6:33 | 6:33 | 8:05 | 0 | 0 | 1.5333 | 1.5333 | AC Coil replaced | Close | 0.0091722 | 0.15 | 246.438
746 | 2023-09-23 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:30 | 18:42 | 12.2 | IS10 | INV4 | M1 |  |  |  | 1 | 1 | IS10INV4M1 | 1973.16 | 0.5888% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 9:26 | 9:26 | 9:26 | 9:52 | 0 | 0 | 0.43333 | 0.43333 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.0025517 | 0.28 | 452.8298
747 | 2023-09-26 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:32 | 18:35 | 12.05 | IS20 | INV3 | M2 | SCB8 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String_MC4 Connector burn | MC4 connector burn | 6:32 | 6:32 | 6:32 | 16:00 | 0 | 0 | 9.4667 | 9.4667 | MC4 connector replaced and string charged | Close | 0.00088482 | 5 | 128.3531
748 | 2023-09-28 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:29 | 18:35 | 12.1 | IS2 | INV3 | M1 |  |  |  | 1 | 1 | IS2INV3M1 | 2064.8 | 0.6162% | Inverter | Inv Unit_AC Coil failure | AC switch Disconnection | 6:30 | 6:30 | 6:30 | 10:48 | 0 | 0 | 4.3 | 4.3 | Communicate with Sungrown and Removed the glue from AC coil switch and inverter restarted | Close | 0.026496 | 1.65 | 2792.3933
749 | 2023-09-28 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:29 | 18:35 | 12.1 | IS2 | INV4 | M2 |  |  |  | 1 | 1 | IS2INV4M2 | 2090.61 | 0.6239% | Inverter | Inv Unit_AC Coil failure | AC switch Disconnection | 6:30 | 6:30 | 6:30 | 9:23 | 0 | 0 | 2.8833 | 2.8833 | Communicate with Sungrown and Removed the glue from AC coil switch and inverter restarted | Close | 0.017989 | 0.67 | 1148.0544
750 | 2023-09-28 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:29 | 18:35 | 12.1 | IS2 | INV4 | M1 |  |  |  | 1 | 1 | IS2INV4M1 | 2090.61 | 0.6239% | Inverter | Inv Unit_AC Coil failure | AC switch Disconnection | 8:22 | 8:22 | 8:22 | 9:23 | 0 | 0 | 1.0167 | 1.0167 | Communicate with Sungrown and Removed the glue from AC coil switch and inverter restarted | Close | 0.0063429 | 0.67 | 1148.0544
751 | 2023-09-28 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:29 | 18:35 | 12.1 | IS3 | INV1 | M2 |  |  |  | 1 | 1 | IS3INV1M2 | 2090.61 | 0.6239% | Inverter | Inv Unit_AC Coil failure | AC switch Disconnection | 6:30 | 6:30 | 6:30 | 8:04 | 0 | 0 | 1.5667 | 1.5667 | Communicate with Sungrown and Removed the glue from AC coil switch and inverter restarted | Close | 0.0097743 | 0.14 | 239.892
752 | 2023-09-28 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:29 | 18:35 | 12.1 | IS3 | INV3 | M1 |  |  |  | 1 | 1 | IS3INV3M1 | 2114.1 | 0.6309% | Inverter | Inv Unit_AC Coil failure | AC switch Disconnection | 6:30 | 6:30 | 6:30 | 10:10 | 0 | 0 | 3.6667 | 3.6667 | Communicate with Sungrown and Removed the glue from AC coil switch and inverter restarted | Close | 0.023133 | 1.16 | 2010.0098
753 | 2023-09-28 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:29 | 18:35 | 12.1 | IS3 | INV3 | M2 |  |  |  | 1 | 1 | IS3INV3M2 | 2088 | 0.6231% | Inverter | Inv Unit_AC Coil failure | AC switch Disconnection | 6:30 | 6:30 | 6:30 | 10:10 | 0 | 0 | 3.6667 | 3.6667 | Communicate with Sungrown and Removed the glue from AC coil switch and inverter restarted | Close | 0.022848 | 1.16 | 1985.1949
754 | 2023-09-28 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:29 | 18:35 | 12.1 | IS4 | INV4 | M2 |  |  |  | 1 | 1 | IS4INV4M2 | 2061.9 | 0.6153% | Inverter | Inv_tripped of INS fault | Inverter Unit tripped in INS fault | 6:30 | 6:30 | 6:30 | 7:15 | 0 | 0 | 0.75 | 0.75 | Ins fault observer due to a string cable punctcured and rectification completed | Close | 0.0046149 | 0.02 | 33.7997
755 | 2023-09-29 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:32 | 18:34 | 12.0333 | IS5 | INV2 | M1 |  |  |  | 1 | 1 | IS5INV2M1 | 2090.61 | 0.6239% | Inverter | Inv Unit_AC Coil failure | Inverter tripped in AC switch disconnection fault | 6:32 | 6:32 | 6:32 | 18:34 | 0 | 0 | 12.0333 | 12.0333 | OEM changed the AC breaker and charged the inverter | Close | 0.075075 | 6.72 | 11514.8147
756 | 2023-09-29 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:32 | 18:34 | 12.0333 | IS5 | INV2 | M2 |  |  |  | 1 | 1 | IS5INV2M2 | 2090.61 | 0.6239% | Inverter | Inv_Manual stop for AC Coil replacement | Inverter Unit Manual stop for AC Coil replacement | 7:56 | 7:56 | 7:56 | 8:23 | 0 | 0 | 0.45 | 0.45 | Inverter Unit manual stop for Unit-1 fault rectification | Close | 0.0028075 | 0.13 | 222.7568
757 | 2023-09-29 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:32 | 18:34 | 12.0333 | IS5 | INV2 | M2 |  |  |  | 1 | 1 | IS5INV2M2 | 2090.61 | 0.6239% | Inverter | Inv_Manual stop for AC Coil replacement | Inverter Unit Manual stop for AC Coil replacement | 8:37 | 8:37 | 8:37 | 11:15 | 0 | 0 | 2.6333 | 2.6333 | Inverter Unit manual stop for Unit-1 fault rectification | Close | 0.016429 | 1.8 | 3084.3254
758 | 2023-09-29 | FY24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 6:32 | 18:34 | 12.0333 | IS5 | INV2 | M2 |  |  |  | 1 | 1 | IS5INV2M2 | 2090.61 | 0.6239% | Inverter | Inv_Manual stop for AC Coil replacement | Inverter Unit Manual stop for AC Coil replacement | 13:08 | 13:08 | 13:08 | 13:50 | 0 | 0 | 0.7 | 0.7 | Inverter Unit manual stop for Unit-1 fault rectification | Close | 0.0043673 | 0.68 | 1165.1896
759 | 2023-10-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:35 | 18:33 | 11.9667 | IS8 | INV4 | M2 | SCB4 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Connectors | SCB_MC4 connector Burn | MC4 connector burn | 6:35 | 6:35 | 6:35 | 18:30 | 0 | 0 | 11.9167 | 11.9167 | MC4 connector replaced and string charged | Close | 0.00092818 | 6.87 | 151.2721
760 | 2023-10-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:33 | 18:31 | 11.9667 | IS8 | INV3 | M2 | SCB7 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | SCB_MC4 connector Burn | MC4 connector burn | 6:33 | 6:33 | 6:33 | 18:31 | 0 | 0 | 11.9667 | 11.9667 | MC4 connector replaced and string charged | Close | 0.0011185 | 6.99 | 184.6972
761 | 2023-10-04 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:33 | 18:30 | 11.95 | IS12 | INV1 | M2 |  |  |  | 1 | 1 | IS12INV1M2 | 2114.1 | 0.6309% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 6:33 | 6:33 | 6:33 | 8:02 | 0 | 0 | 1.4833 | 1.4833 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.0093584 | 0.14 | 249.698
762 | 2023-10-04 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:33 | 18:30 | 11.95 | IS8 | INV3 | M2 | SCB7 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | String Fuses | String fuse damaged | Fuse replaced and string charged | 6:33 | 6:33 | 6:33 | 18:31 | 0 | 0 | 11.9667 | 11.9667 | Stringfuse replaced and string charged | Close | 0.0011185 | 6.92 | 182.8476
763 | 2023-10-05 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:33 | 18:29 | 11.9333 | IS6 | INV3 | M1 |  |  |  | 1 | 1 | IS6INV3M1 | 2192.4 | 0.6543% | Inverter | Inv_tripped in INS Fault | Inverter Unit tripped in INS fault | 6:33 | 6:33 | 6:33 | 7:29 | 0 | 0 | 0.93333 | 0.93333 | Floating checked and found healthy. Inverter charged | Close | 0.0061065 | 0.04 | 73.9846
764 | 2023-10-05 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:33 | 18:29 | 11.9333 | IS7 | INV3 | M2 |  |  |  | 1 | 1 | IS7INV3M2 | 1973.16 | 0.5888% | Inverter | Inv_tripped in INS Fault | Inverter Unit tripped in INS fault | 6:33 | 6:33 | 6:33 | 7:15 | 0 | 0 | 0.7 | 0.7 | Floating checked and found healthy. Inverter charged | Close | 0.0041219 | 0.02 | 33.2931
765 | 2023-10-05 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:33 | 18:29 | 11.9333 | IS10 | INV3 | M1 |  |  |  | 1 | 1 | IS10INV3M1 | 1941.84 | 0.5795% | Inverter | Inv_tripped in INS Fault | Inverter Unit tripped in INS fault | 6:33 | 6:33 | 6:33 | 7:40 | 0 | 0 | 1.1167 | 1.1167 | Floating checked and found healthy. Inverter charged | Close | 0.006471 | 0.07 | 114.6761
766 | 2023-10-05 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:33 | 18:29 | 11.9333 | IS10 | INV3 | M2 |  |  |  | 1 | 1 | IS10INV3M2 | 2255.04 | 0.673% | Inverter | Inv_tripped in INS Fault | Inverter Unit tripped in INS fault | 6:33 | 6:33 | 6:33 | 7:40 | 0 | 0 | 1.1167 | 1.1167 | Floating checked and found healthy. Inverter charged | Close | 0.0075148 | 0.07 | 133.1723
767 | 2023-10-05 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:33 | 18:29 | 11.9333 | IS10 | INV4 | M2 |  |  |  | 1 | 1 | IS10INV4M2 | 2223.72 | 0.6636% | Inverter | Inv_tripped in INS Fault | Inverter Unit tripped in INS fault | 6:33 | 6:33 | 6:33 | 7:40 | 0 | 0 | 1.1167 | 1.1167 | Floating checked and found healthy. Inverter charged | Close | 0.0074104 | 0.07 | 131.3226
768 | 2023-10-05 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:33 | 18:29 | 11.9333 | IS12 | INV1 | M2 |  |  |  | 1 | 1 | IS12INV1M2 | 2114.1 | 0.6309% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 6:33 | 6:33 | 6:33 | 7:53 | 0 | 0 | 1.3333 | 1.3333 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.008412 | 0.11 | 196.1913
769 | 2023-10-05 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:33 | 18:29 | 11.9333 | IS13 | INV4 | M1 |  |  |  | 1 | 1 | IS13INV4M1 | 2192.4 | 0.6543% | Inverter | Inv_tripped in INS Fault | Inverter Unit tripped in INS fault | 6:33 | 6:33 | 6:33 | 7:21 | 0 | 0 | 0.8 | 0.8 | Floating checked and found healthy. Inverter charged | Close | 0.0052342 | 0.03 | 55.4884
770 | 2023-10-05 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:33 | 18:29 | 11.9333 | IS17 | INV4 | M1 |  |  |  | 1 | 1 | IS17INV4M1 | 2004.48 | 0.5982% | Inverter | Inv_tripped in INS Fault | Inverter Unit tripped in INS fault | 6:33 | 6:33 | 6:33 | 7:35 | 0 | 0 | 1.0333 | 1.0333 | Floating checked and found healthy. Inverter charged | Close | 0.0061813 | 0.06 | 101.4646
771 | 2023-10-06 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:34 | 18:28 | 11.9 | IS2 | INV1 | M2 |  |  |  | 1 | 1 | IS2INV1M2 | 2090.61 | 0.6239% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 6:59 | 6:59 | 6:59 | 8:33 | 0 | 0 | 1.5667 | 1.5667 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.0097743 | 0.26 | 458.5723
772 | 2023-10-06 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:34 | 18:28 | 11.9 | IS2 | INV1 | M1 |  |  |  | 1 | 1 | IS2INV1M1 | 2090.61 | 0.6239% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 7:17 | 7:17 | 7:17 | 8:33 | 0 | 0 | 1.2667 | 1.2667 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.0079026 | 0.26 | 458.5723
773 | 2023-10-06 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:34 | 18:28 | 11.9 | IS2 | INV1 | M2 | SCB9 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Cables | String_ Fault of GFDI | Inverter tripped of GFDI | 6:59 | 6:59 | 6:59 | 11:00 | 0 | 0 | 4.0167 | 4.0167 | String cable replaced and new cable lying done | Close | 0.00030938 | 1.88 | 40.9362
774 | 2023-10-06 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:34 | 18:28 | 11.9 | IS2 | INV1 | M2 | SCB9 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Cables | String_ Fault of GFDI | Inverter tripped of GFDI | 6:59 | 6:59 | 6:59 | 15:00 | 0 | 0 | 8.0167 | 8.0167 | String cable replaced and new cable lying done | Close | 0.00061747 | 5.6 | 121.9376
775 | 2023-10-06 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:34 | 18:28 | 11.9 | IS2 | INV1 | M2 | SCB9 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Cables | String_ Fault of GFDI | Inverter tripped of GFDI | 6:59 | 6:59 | 6:59 | 15:00 | 0 | 0 | 8.0167 | 8.0167 | String cable replaced and new cable lying done | Close | 0.00061747 | 5.6 | 121.9376
776 | 2023-10-08 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:36 | 18:25 | 11.8167 | IS7 | INV1 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | SCB_MC4 connector Burn | MC4 connector burn | 6:36 | 6:36 | 6:36 | 18:25 | 0 | 0 | 11.8167 | 11.8167 | MC4 connector replaced and string charged | Close | 0.00055224 | 6.71 | 88.6494
777 | 2023-10-08 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:36 | 18:25 | 11.8167 | IS20 | INV4 | M1 | SCB5 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | SCB_MC4 connector Burn | MC4 connector burn | 6:36 | 6:36 | 6:36 | 18:25 | 0 | 0 | 11.8167 | 11.8167 | MC4 connector replaced and string charged | Close | 0.00055224 | 6.71 | 88.6494
778 | 2023-10-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:36 | 18:24 | 11.8 | IS11 | INV3 | M2 |  |  |  | 1 | 1 | IS11INV3M2 | 2212.7 | 0.6603% | Inverter | Inv Unit_AC Coil failure | Inverter tripped in AC switch disconnection fault | 6:36 | 6:36 | 6:36 | 7:41 | 0 | 0 | 1.0833 | 1.0833 | AC Coil replaced | Close | 0.0071536 | 0.06 | 112.0044
779 | 2023-10-10 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:37 | 18:23 | 11.7667 | IS15 | INV2 | M2 |  |  |  | 1 | 1 | IS15INV2M2 | 1941.84 | 0.5795% | Inverter | Inv_tripped in INS Fault | Inverter Unit tripped in INS fault | 6:37 | 6:37 | 6:37 | 7:25 | 0 | 0 | 0.8 | 0.8 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.004636 | 0.02 | 32.7646
780 | 2023-10-10 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:37 | 18:23 | 11.7667 | IS13 | INV4 | M1 |  |  |  | 1 | 1 | IS13INV4M1 | 2192.4 | 0.6543% | Inverter | Inv_tripped in INS Fault | Inverter Unit tripped in INS fault | 6:37 | 6:37 | 6:37 | 7:14 | 0 | 0 | 0.61667 | 0.61667 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.0040347 | 0.01 | 18.4961
781 | 2023-10-12 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:37 | 18:22 | 11.75 | IS1 | INV1 | M2 | SCB5 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | String Fuses | String_fuse burn | String fuse burn | 6:37 | 6:37 | 6:37 | 18:22 | 0 | 0 | 11.75 | 11.75 | String fuse replaced and string charged | Close | 0.00045252 | 6.33 | 68.9165
782 | 2023-10-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:38 | 18:15 | 11.6167 | IS6 | INV3 | M2 |  |  |  | 1 | 1 | IS6INV3M2 | 2380.32 | 0.7104% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 7:30 | 7:30 | 7:30 | 8:54 | 0 | 0 | 1.4 | 1.4 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.0099449 | 0.39 | 783.1797
783 | 2023-10-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:38 | 18:15 | 11.6167 | IS10 | INV2 | M1 |  |  |  | 1 | 1 | IS10INV2M1 | 1973.16 | 0.5888% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 7:37 | 7:37 | 7:37 | 8:07 | 0 | 0 | 0.5 | 0.5 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.0029442 | 0.1 | 166.4653
784 | 2023-10-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:38 | 18:15 | 11.6167 | IS10 | INV2 | M2 |  |  |  | 1 | 1 | IS10INV2M2 | 2223.72 | 0.6636% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 6:38 | 6:38 | 6:38 | 8:03 | 0 | 0 | 1.4167 | 1.4167 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.0094012 | 0.13 | 243.8849
785 | 2023-10-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:38 | 18:15 | 11.6167 | IS10 | INV3 | M1 |  |  |  | 1 | 1 | IS10INV3M1 | 1941.84 | 0.5795% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 8:13 | 8:13 | 8:13 | 8:31 | 0 | 0 | 0.3 | 0.3 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.0017385 | 0.1 | 163.823
786 | 2023-10-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:38 | 18:15 | 11.6167 | IS10 | INV3 | M2 |  |  |  | 1 | 1 | IS10INV3M2 | 2255.04 | 0.673% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 8:13 | 8:13 | 8:13 | 8:31 | 0 | 0 | 0.3 | 0.3 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.0020189 | 0.1 | 190.2461
787 | 2023-10-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:38 | 18:15 | 11.6167 | IS12 | INV1 | M2 |  |  |  | 1 | 1 | IS12INV1M2 | 2114.1 | 0.6309% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 6:47 | 6:47 | 6:47 | 8:09 | 0 | 0 | 1.3667 | 1.3667 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.0086223 | 0.16 | 285.3691
788 | 2023-10-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:38 | 18:15 | 11.6167 | IS14 | INV4 | M1 |  |  |  | 1 | 1 | IS14INV4M1 | 2192.4 | 0.6543% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 6:37 | 6:37 | 6:37 | 7:16 | 0 | 0 | 0.65 | 0.65 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.0042528 | 0.01 | 18.4961
789 | 2023-10-16 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:50 | 17:51 | 11.0167 | IS7 | INV4 | M2 |  |  |  | 1 | 1 | IS7INV4M2 | 1973.16 | 0.5888% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 15:36 | 15:36 | 15:36 | 16:53 | 0 | 0 | 1.2833 | 1.2833 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.0075568 | 0.14 | 233.0514
790 | 2023-10-16 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:50 | 17:51 | 11.0167 | IS3 | INV2 | M1 |  |  |  | 1 | 1 | IS3INV2M1 | 2090.61 | 0.6239% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 16:06 | 16:06 | 16:06 | 16:35 | 0 | 0 | 0.48333 | 0.48333 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.0030155 | 0.09 | 158.7366
791 | 2023-10-16 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:50 | 17:51 | 11.0167 | IS16 | INV4 | M1 | SCB2 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | SCB_MC4 connector Burn | MC4 connector burn | 6:50 | 6:50 | 6:50 | 17:51 | 0 | 0 | 11.0167 | 11.0167 | MC4 connector replaced and string charged | Close | 0.00051485 | 3.84 | 50.7323
792 | 2023-10-20 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:53 | 18:02 | 11.15 | IS14 | INV3 | M2 |  |  |  | 1 | 1 | IS14INV3M2 | 2004.48 | 0.5982% | Inverter | Inv_tripped in INS Fault | Inverter Unit tripped in INS fault | 6:44 | 6:44 | 6:44 | 7:30 | 0 | 0 | 0.76667 | 0.76667 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.0045861 | 0.031977 | 54.0763
793 | 2023-10-22 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:52 | 18:16 | 11.4 | IS11 | INV3 | M2 |  |  |  | 1 | 1 | IS11INV3M2 | 2212.7 | 0.6603% | Inverter | Inv Unit_AC Coil failure | Inverter tripped in AC switch disconnection fault | 6:52 | 6:52 | 6:52 | 18:27 | 0 | 0 | 11.5833 | 11.5833 | checked related connection and parameter then AC Coil replaced by sungrow Team | Close | 0.076488 | 5.7 | 10640.4217
794 | 2023-10-23 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:58 | 18:00 | 11.0333 | IS5 | INV4 | M1 | SCB7 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Connectors | SCB_MC4 connector Burn | MC4 connector burn | 6:58 | 6:58 | 6:58 | 18:00 | 0 | 0 | 11.0333 | 11.0333 | checked condition of module and its interconnection then found T 386 MC4 connector found burn out so we replaced it and checked VOC found ok | Close | 0.00042491 | 6.005 | 65.3781
795 | 2023-10-23 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:58 | 18:00 | 11.0333 | IS16 | INV4 | M2 | SCB5 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | SCB_MC4 connector Burn | MC4 connector burn | 6:58 | 6:58 | 6:58 | 18:00 | 0 | 0 | 11.0333 | 11.0333 | checked condition of module and its interconnection then found T 428 MC4 connector found open so we replaced it and checked VOC found ok | Close | 0.00051563 | 6.005 | 79.3353
796 | 2023-10-24 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:46 | 18:08 | 11.3667 | IS16 | INV4 | M2 | SCB6 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | SCB_MC4 connector Burn | MC4 connector burn | 6:46 | 6:46 | 6:46 | 18:08 | 0 | 0 | 11.3667 | 11.3667 | Checked module condition as well as its module interconnection then found St 07 and T 510 MC4 connector burn out, so we replaced it with new one and checked VOC found ok |  | 0.0005312 | 5.9794 | 78.9971
797 | 2023-10-24 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:46 | 18:08 | 11.3667 | IS14 | INV2 | M2 |  |  |  | 1 | 1 | IS14INV2M2 | 2004.48 | 0.5982% | Inverter | Inv Unit_AC Coil failure | Inverter tripped in AC switch disconnection fault | 6:58 | 6:58 | 6:58 | 8:19 | 0 | 0 | 1.35 | 1.35 | checked related connection and parameter then AC Coil replaced by sungrow Team | Close | 0.0080756 | 0.16775 | 283.6787
798 | 2023-10-24 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:46 | 18:08 | 11.3667 | IS14 | INV2 | M1 |  |  |  | 1 | 1 | IS14INV2M1 | 2223.72 | 0.6636% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 7:10 | 7:10 | 7:10 | 8:10 | 0 | 0 | 1 | 1 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0066362 | 0.12614 | 236.6418
799 | 2023-10-24 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:46 | 18:08 | 11.3667 | IS10 | INV2 | M2 |  |  |  | 1 | 1 | IS10INV2M2 | 2223.72 | 0.6636% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 6:58 | 6:58 | 6:58 | 7:52 | 0 | 0 | 0.9 | 0.9 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.0059726 | 0.070457 | 132.1803
800 | 2023-10-24 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:46 | 18:08 | 11.3667 | IS10 | INV3 | M1 |  |  |  | 1 | 1 | IS10INV3M1 | 1941.84 | 0.5795% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 6:58 | 6:58 | 6:58 | 7:54 | 0 | 0 | 0.93333 | 0.93333 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.0054086 | 0.070457 | 115.4251
801 | 2023-10-25 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:50 | 18:03 | 11.2167 | IS1 | INV2 | M2 | SCB6 | Str_Typ2 (450*29) |  | 0 | 0 | Str_Typ2 (450*29) | 13.05 | 0.003894% | Connectors | SCB_MC4 connector open | MC4 connector open | 6:50 | 6:50 | 6:50 | 18:03 | 0 | 0 | 11.2167 | 11.2167 | Checked module and its interconnection then found T-295, St-04 MC4 connector found open so resolve it . | Close | 0.00043683 | 6.2 | 68.2596
802 | 2023-10-26 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:52 | 18:06 | 11.2333 | IS15 | INV3 | M2 |  |  |  | 1 | 1 | IS15INV3M2 | 2192.4 | 0.6543% | Inverter | Inv Unit_AC Coil failure | Inverter tripped in AC switch disconnection fault | 6:52 | 6:52 | 6:52 | 7:44 | 0 | 0 | 0.86667 | 0.86667 | checked related connection and parameter then rboot the inverter and start | Close | 0.0056703 | 0.060457 | 111.8225
803 | 2023-10-27 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:48 | 18:07 | 11.3167 | IS15 | INV3 | M2 |  |  |  | 1 | 1 | IS15INV3M2 | 2192.4 | 0.6543% | Inverter | Inv Unit_AC Coil failure | Inverter tripped in AC switch disconnection fault | 6:48 | 6:48 | 6:48 | 8:09 | 0 | 0 | 1.35 | 1.35 | checked related connection and parameter then AC Coil found faulty after discussion with sungrow Team replaced it | Close | 0.0088326 | 0.1 | 184.9615
804 | 2023-10-28 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:50 | 18:10 | 11.3333 | IS15 | INV3 | M2 |  |  |  | 1 | 1 | IS15INV3M2 | 2192.4 | 0.6543% | Inverter | Inv Unit_AC Coil failure | Inverter tripped in AC switch disconnection fault | 6:50 | 6:50 | 6:50 | 7:25 | 0 | 0 | 0.58333 | 0.58333 | checked related connection and parameter then AC Coil replaced by sungrow Team | Close | 0.0038166 | 0.05 | 92.4807
805 | 2023-10-28 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:50 | 18:10 | 11.3333 | IS15 | INV3 | M1 |  |  |  | 1 | 1 | IS15INV3M1 | 2223.72 | 0.6636% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 7:54 | 7:54 | 7:54 | 8:06 | 0 | 0 | 0.2 | 0.2 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0013272 | 0.030281 | 56.8077
806 | 2023-10-29 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:51 | 18:04 | 11.2167 | IS15 | INV3 | M2 |  |  |  | 1 | 1 | IS15INV3M2 | 2192.4 | 0.6543% | Inverter | Inv Unit_AC Coil failure | Inverter tripped in AC switch disconnection fault | 6:51 | 6:51 | 6:51 | 8:19 | 0 | 0 | 1.4667 | 1.4667 | checked related connection and parameter then rboot the inverter and start | Close | 0.009596 | 0.09 | 166.4653
807 | 2023-10-30 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:52 | 18:05 | 11.2167 | IS15 | INV3 | M2 |  |  |  | 1 | 1 | IS15INV3M2 | 2192.4 | 0.6543% | Inverter | Inv Unit_AC Coil failure | Inverter tripped in AC switch disconnection fault | 6:52 | 6:52 | 6:52 | 7:27 | 0 | 0 | 0.58333 | 0.58333 | checked related connection and parameter then rboot the inverter and start | Close | 0.0038166 | 0.05 | 92.4807
808 | 2023-10-31 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:57 | 18:00 | 11.05 | IS7 | INV4 | M1 |  |  |  | 1 | 1 | IS7INV4M1 | 2223.72 | 0.6636% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 14:38 | 14:38 | 14:38 | 14:49 | 0 | 0 | 0.18333 | 0.18333 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.0012166 | 0.015769 | 29.5824
809 | 2023-10-31 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:57 | 18:00 | 11.05 | IS7 | INV4 | M2 |  |  |  | 1 | 1 | IS7INV4M2 | 1973.16 | 0.5888% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 14:38 | 14:38 | 14:38 | 15:17 | 0 | 0 | 0.65 | 0.65 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.0038275 | 0.066139 | 110.0981
810 | 2023-10-31 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:57 | 18:00 | 11.05 | IS12 | INV1 | M1 |  |  |  | 1 | 1 | IS12INV1M1 | 2192.4 | 0.6543% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 14:55 | 14:55 | 14:55 | 15:12 | 0 | 0 | 0.28333 | 0.28333 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.0018538 | 0.031471 | 58.2094
811 | 2023-10-31 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:57 | 18:00 | 11.05 | IS9 | INV1 | M1 |  |  |  | 1 | 1 | IS9INV1M1 | 2102.065 | 0.6273% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 14:57 | 14:57 | 14:57 | 15:33 | 0 | 0 | 0.6 | 0.6 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.0037639 | 0.085798 | 152.1547
812 | 2023-10-31 | FY24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 6:57 | 18:00 | 11.05 | IS9 | INV1 | M2 |  |  |  | 1 | 1 | IS9INV1M2 | 2023.04 | 0.6037% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 14:57 | 14:57 | 14:57 | 15:08 | 0 | 0 | 0.18333 | 0.18333 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.0011068 | 0.020553 | 35.078
813 | 2023-11-08 | FY24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 6:52 | 18:01 | 11.15 | IS14 | INV1 | M2 |  |  |  | 1 | 1 | IS14INV1M2 | 1910.52 | 0.5701% | Inverter | Inv Unit_AC Coil failure | Inverter tripped in AC switch disconnection fault | 6:51 | 6:51 | 6:51 | 7:41 | 0 | 0 | 0.83333 | 0.83333 | checked related connection and parameter then rboot the inverter and start | Close | 0.0047512 | 0.05 | 82.0749
814 | 2023-11-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 6:50 | 18:01 | 11.1833 | IS9 | INV2 | M1 |  |  |  | 1 | 1 | IS9INV2M1 | 2102.065 | 0.6273% | Inverter | Inv Unit_AC Coil failure | Inverter tripped in AC switch disconnection fault | 6:50 | 6:50 | 6:50 | 7:42 | 0 | 0 | 0.86667 | 0.86667 | checked related connection and parameter then rboot the inverter and start | Close | 0.0054367 | 0.08 | 144.4858
815 | 2023-11-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 6:50 | 18:01 | 11.1833 | IS11 | INV2 | M2 |  |  |  | 1 | 1 | IS11INV2M2 | 2038.845 | 0.6084% | Inverter | Inv Unit_AC Coil failure | Inverter tripped in AC switch disconnection fault | 6:50 | 6:50 | 6:50 | 7:54 | 0 | 0 | 1.0667 | 1.0667 | checked related connection and parameter then rboot the inverter and start | Close | 0.0064901 | 0.07 | 122.6228
816 | 2023-11-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 6:50 | 18:01 | 11.1833 | IS18 | INV4 | M2 |  |  |  | 1 | 1 | IS18INV4M2 | 2004.48 | 0.5982% | Inverter | Inv Unit_AC Coil failure | Inverter tripped in AC switch disconnection fault | 6:50 | 6:50 | 6:50 | 8:16 | 0 | 0 | 1.4333 | 1.4333 | checked related connection and parameter then rboot the inverter and start | Close | 0.0085741 | 0.1 | 172.2228
817 | 2023-11-09 | FY24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 6:50 | 18:01 | 11.1833 | IS6 | INV1 | M1 |  |  |  | 1 | 1 | IS6INV1M1 | 2234.16 | 0.6667% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 7:54 | 7:54 | 7:54 | 8:19 | 0 | 0 | 0.41667 | 0.41667 | checked related connection and parameter then rboot the inverter and start | Close | 0.0027781 | 0.05 | 95.9783
818 | 2023-11-10 | FY24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 6:54 | 17:59 | 11.0833 | IS12 | INV1 | M2 |  |  |  | 1 | 1 | IS12INV1M2 | 2114.1 | 0.6309% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 7:18 | 7:18 | 7:18 | 7:57 | 0 | 0 | 0.65 | 0.65 | checked related connection and parameter then rboot the inverter and start | Close | 0.0041009 | 0.05 | 90.8206
819 | 2023-11-10 | FY24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 6:54 | 17:59 | 11.0833 | IS12 | INV1 | M1 |  |  |  | 1 | 1 | IS12INV1M1 | 2192.4 | 0.6543% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 6:59 | 6:59 | 6:59 | 8:55 | 0 | 0 | 1.9333 | 1.9333 | checked related connection and parameter then rboot the inverter and start | Close | 0.012649 | 0.09 | 169.5318
820 | 2023-11-12 | FY24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 6:50 | 18:01 | 11.1833 | IS5 | INV1 | M2 |  |  |  | 1 | 1 | IS5INV1M2 | 2090.61 | 0.6239% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 6:50 | 6:50 | 6:50 | 7:31 | 0 | 0 | 0.68333 | 0.68333 | checked related connection and parameter then rboot the inverter and start | Close | 0.0042633 | 0.02 | 35.9246
821 | 2023-11-12 | FY24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 6:50 | 18:01 | 11.1833 | IS6 | INV3 | M2 |  |  |  | 1 | 1 | IS6INV3M2 | 2380.32 | 0.7104% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 6:50 | 6:50 | 6:50 | 7:31 | 0 | 0 | 0.68333 | 0.68333 | checked related connection and parameter then rboot the inverter and start | Close | 0.0048541 | 0.02 | 40.9029
822 | 2023-11-12 | FY24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 6:50 | 18:01 | 11.1833 | IS7 | INV4 | M2 |  |  |  | 1 | 1 | IS7INV4M2 | 1973.16 | 0.5888% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 6:50 | 6:50 | 6:50 | 7:48 | 0 | 0 | 0.96667 | 0.96667 | checked related connection and parameter then rboot the inverter and start | Close | 0.0056921 | 0.02 | 33.9064
823 | 2023-11-12 | FY24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 6:50 | 18:01 | 11.1833 | IS10 | INV2 | M2 |  |  |  | 1 | 1 | IS10INV2M2 | 2223.72 | 0.6636% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 6:50 | 6:50 | 6:50 | 7:34 | 0 | 0 | 0.73333 | 0.73333 | checked related connection and parameter then rboot the inverter and start | Close | 0.0048665 | 0.02 | 38.2119
824 | 2023-11-12 | FY24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 6:50 | 18:01 | 11.1833 | IS14 | INV3 | M2 |  |  |  | 1 | 1 | IS14INV3M2 | 2004.48 | 0.5982% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 6:50 | 6:50 | 6:50 | 7:42 | 0 | 0 | 0.86667 | 0.86667 | checked related connection and parameter then rboot the inverter and start | Close | 0.0051843 | 0.02 | 34.4446
825 | 2023-11-12 | FY24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 6:50 | 18:01 | 11.1833 | IS14 | INV4 | M1 |  |  |  | 1 | 1 | IS14INV4M1 | 2192.4 | 0.6543% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 6:50 | 6:50 | 6:50 | 7:42 | 0 | 0 | 0.86667 | 0.86667 | checked related connection and parameter then rboot the inverter and start | Close | 0.0056703 | 0.02 | 37.6737
826 | 2023-11-12 | FY24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 6:50 | 18:01 | 11.1833 | IS17 | INV4 | M2 |  |  |  | 1 | 1 | IS17INV4M2 | 2004.48 | 0.5982% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 6:50 | 6:50 | 6:50 | 7:26 | 0 | 0 | 0.6 | 0.6 | checked related connection and parameter then rboot the inverter and start | Close | 0.0035891 | 0.02 | 34.4446
827 | 2023-11-13 | FY24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 6:51 | 17:50 | 10.9833 | IS13 | INV3 | M1 |  |  |  | 1 | 1 | IS13INV3M1 | 2192.4 | 0.6543% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 7:21 | 7:21 | 7:21 | 8:17 | 0 | 0 | 0.93333 | 0.93333 | checked related connection and parameter then rboot the inverter and start | Close | 0.0061065 | 0.07 | 131.8581
828 | 2023-11-13 | FY24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 6:51 | 17:50 | 10.9833 | IS13 | INV3 | M2 |  |  |  | 1 | 1 | IS13INV3M2 | 2004.48 | 0.5982% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 7:21 | 7:21 | 7:21 | 8:17 | 0 | 0 | 0.93333 | 0.93333 | checked related connection and parameter then rboot the inverter and start | Close | 0.0055831 | 0.07 | 120.556
829 | 2023-11-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 6:57 | 17:57 | 11 | IS18 | INV4 | M2 |  |  |  | 1 | 1 | IS18INV4M2 | 2004.48 | 0.5982% | Inverter | Inv Unit_AC Coil failure | Inverter tripped in AC switch disconnection fault | 6:57 | 6:57 | 6:57 | 17:57 | 0 | 0 | 11 | 11 | AC breaker changed by OEM | Close | 0.065801 | 5.23 | 9007.254
830 | 2023-11-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 6:57 | 17:57 | 11 | IS18 | INV4 | M1 |  |  |  | 1 | 1 | IS18INV4M1 | 2004.48 | 0.5982% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 7:16 | 7:16 | 7:16 | 8:00 | 0 | 0 | 0.73333 | 0.73333 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0043867 | 0.04 | 68.8891
831 | 2023-11-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 6:57 | 17:57 | 11 | IS18 | INV4 | M1 |  |  |  | 1 | 1 | IS18INV4M1 | 2004.48 | 0.5982% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 8:15 | 8:15 | 8:15 | 8:54 | 0 | 0 | 0.65 | 0.65 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0038882 | 0.17 | 292.7788
832 | 2023-11-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 6:57 | 17:57 | 11 | IS18 | INV4 | M1 |  |  |  | 1 | 1 | IS18INV4M1 | 2004.48 | 0.5982% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 9:47 | 9:47 | 9:47 | 10:00 | 0 | 0 | 0.21667 | 0.21667 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0012961 | 0.12 | 206.6674
833 | 2023-11-15 | FY24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 6:57 | 17:57 | 11 | IS18 | INV4 | M1 |  |  |  | 1 | 1 | IS18INV4M1 | 2004.48 | 0.5982% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 11:18 | 11:18 | 11:18 | 12:00 | 0 | 0 | 0.7 | 0.7 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0041873 | 0.55 | 947.2256
834 | 2023-11-19 | FY24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 7:02 | 17:56 | 10.9 | IS13 |  |  |  |  | Tx | 0 | 1 | IS13Tx | 16599.6 | 4.954% | IDT | IDT_Manual stop for Thermography | IDT manual stop for thermography work | 13:30 | 13:30 | 13:30 | 13:50 | 0 | 0 | 0.33333 | 0.33333 | Thermography done and IDT charged | Close | 0.016513 | 0.24 | 3422.9288
835 | 2023-11-19 | FY24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 7:02 | 17:56 | 10.9 | IS4 |  |  |  |  | Tx | 0 | 1 | IS4Tx | 16547.4 | 4.938% | IDT | IDT_Manual stop for Thermography | IDT manual stop for thermography work | 14:12 | 14:12 | 14:12 | 14:34 | 0 | 0 | 0.36667 | 0.36667 | Thermography done and IDT charged | Close | 0.018107 | 0.24 | 3412.1648
836 | 2023-11-21 | FY24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 7:01 | 17:57 | 10.9333 | IS15 | INV3 | M1 |  |  |  | 1 | 1 | IS15INV3M1 | 2223.72 | 0.6636% | Inverter | Inv Unit_AC Coil failure | Inverter tripped in AC switch disconnection fault | 7:01 | 7:01 | 7:01 | 7:50 | 0 | 0 | 0.81667 | 0.81667 | Reset AC coil and restarted | Close | 0.0054195 | 0.02 | 38.2119
837 | 2023-11-21 | FY24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 7:01 | 17:57 | 10.9333 | IS15 | INV3 | M2 |  |  |  | 1 | 1 | IS15INV3M2 | 2192.4 | 0.6543% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 7:01 | 7:01 | 7:01 | 7:50 | 0 | 0 | 0.81667 | 0.81667 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0053432 | 0.02 | 37.6737
838 | 2023-11-22 | FY24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 7:01 | 17:56 | 10.9167 | IS5 | INV2 | M1 |  |  |  | 1 | 1 | IS5INV2M1 | 2090.61 | 0.6239% | Inverter | Inv_alarm running for Fan-2 error | Alarm for fan-2 error | 12:52 | 12:52 | 12:52 | 12:58 | 0 | 0 | 0.1 | 0.1 | Restarted the inverter and charged | Close | 0.00062389 | 0.1 | 179.623
839 | 2023-11-22 | FY24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 7:01 | 17:56 | 10.9167 | IS5 | INV2 | M2 |  |  |  | 1 | 1 | IS5INV2M2 | 2090.61 | 0.6239% | Inverter | Inv_alarm running for Fan-2 error | Alarm for fan-2 error | 12:52 | 12:52 | 12:52 | 12:58 | 0 | 0 | 0.1 | 0.1 | Restarted the inverter and charged | Close | 0.00062389 | 0.1 | 179.623
840 | 2023-11-26 | FY24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 7:42 | 17:44 | 10.0333 | IS10 | INV3 | M1 |  |  |  | 1 | 1 | IS10INV3M1 | 1941.84 | 0.5795% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 9:55 | 9:55 | 10:05 | 10:20 | 0 | 0.16667 | 0.41667 | 0.41667 | checked related connection and parameter then rboot the inverter and start | Close | 0.0024146 | 0.02 | 33.3682
841 | 2023-11-26 | FY24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 7:42 | 17:44 | 10.0333 | IS10 | INV3 | M2 |  |  |  | 1 | 1 | IS10INV3M2 | 2255.04 | 0.673% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 9:55 | 9:55 | 10:05 | 10:43 | 0 | 0.16667 | 0.8 | 0.8 | checked related connection and parameter then rboot the inverter and start | Close | 0.0053837 | 0.05 | 96.8753
842 | 2023-11-28 | FY24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 7:09 | 17:53 | 10.7333 | IS6 |  |  |  |  | Tx | 0 | 1 | IS6Tx | 17170.9 | 5.124% | IDT | IDT_tripped of Nitrogen Inject | Nitrogen inject occurred at time of bushing replacement | 7:09 | 7:09 | 7:09 | 13:00 | 0 | 0 | 5.85 | 5.85 | Oil filtration done, LHD rectified and meggaring done, then IDT charged | Close | 0.29977 | 2.25 | 33194.3808
843 | 2023-12-01 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:10 | 17:54 | 10.7333 | IS4 | INV1 | M2 |  |  |  | 1 | 1 | IS4INV1M2 | 1879.2 | 0.5608% | Inverter | Inv Unit_AC Coil failure | Inverter tripped in AC switch disconnection fault | 7:10 | 7:10 | 7:10 | 7:53 | 0 | 0 | 0.71667 | 0.71667 | Reset AC coil and restarted after discussion with OEM | Close | 0.0040191 | 0.01 | 17.0716
844 | 2023-12-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:10 | 17:55 | 10.75 | IS5 | INV1 | M2 |  |  |  | 1 | 1 | IS5INV1M2 | 2090.61 | 0.6239% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 7:10 | 7:10 | 7:10 | 7:51 | 0 | 0 | 0.68333 | 0.68333 | Rectification done | Close | 0.0042633 | 0.01 | 18.9922
845 | 2023-12-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:10 | 17:55 | 10.75 | IS6 | INV3 | M2 |  |  |  | 1 | 1 | IS6INV3M2 | 2380.32 | 0.7104% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 7:10 | 7:10 | 7:10 | 8:21 | 0 | 0 | 1.1833 | 1.1833 | Rectification done | Close | 0.0084058 | 0.06 | 129.7442
846 | 2023-12-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:10 | 17:55 | 10.75 | IS7 | INV3 | M1 |  |  |  | 1 | 1 | IS7INV3M1 | 2223.72 | 0.6636% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 7:10 | 7:10 | 7:10 | 7:51 | 0 | 0 | 0.68333 | 0.68333 | Rectification done | Close | 0.0045347 | 0.01 | 20.2014
847 | 2023-12-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:10 | 17:55 | 10.75 | IS7 | INV4 | M2 |  |  |  | 1 | 1 | IS7INV4M2 | 1973.16 | 0.5888% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 7:10 | 7:10 | 7:10 | 8:39 | 0 | 0 | 1.4833 | 1.4833 | Rectification done | Close | 0.0087345 | 0.12 | 215.1022
848 | 2023-12-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:10 | 17:55 | 10.75 | IS10 | INV2 | M2 |  |  |  | 1 | 1 | IS10INV2M2 | 2223.72 | 0.6636% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 7:10 | 7:10 | 7:10 | 8:23 | 0 | 0 | 1.2167 | 1.2167 | Rectification done | Close | 0.008074 | 0.07 | 141.4098
849 | 2023-12-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:10 | 17:55 | 10.75 | IS11 | INV4 | M1 |  |  |  | 1 | 1 | IS11INV4M1 | 2023.04 | 0.6037% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 7:10 | 7:10 | 7:10 | 8:00 | 0 | 0 | 0.83333 | 0.83333 | Rectification done | Close | 0.0050311 | 0.02 | 36.7566
850 | 2023-12-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:10 | 17:55 | 10.75 | IS14 | INV1 | M2 |  |  |  | 1 | 1 | IS14INV1M2 | 1910.52 | 0.5701% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 7:10 | 7:10 | 7:10 | 7:46 | 0 | 0 | 0.6 | 0.6 | Rectification done | Close | 0.0034209 | 0.01 | 17.3561
851 | 2023-12-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:10 | 17:55 | 10.75 | IS14 | INV3 | M2 |  |  |  | 1 | 1 | IS14INV3M2 | 2004.48 | 0.5982% | Inverter | Inv_tripped of GFDI | Inverter Unit tripped in GFDI fault | 7:10 | 7:10 | 7:10 | 8:13 | 0 | 0 | 1.05 | 1.05 | Rectification done | Close | 0.006281 | 0.04 | 72.8388 |  | 7566
852 | 2023-12-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:10 | 17:55 | 10.75 | IS17 | INV3 | M1 | SCB6 |  |  | 1 | 1 | IS17INV3M1SCB6 | 250.56 | 0.07477% | Cables | SCB_String Cable Theft | SCB_String Cable Theft | 7:10 | 7:10 | 7:10 | 17:55 | 0 | 0 |  | 10.75 | Work in progress | Open | 0.0080382 | 4.86 | 1106.2399
853 | 2023-12-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:10 | 17:55 | 10.75 | IS17 | INV3 | M1 | SCB7 |  |  | 1 | 1 | IS17INV3M1SCB7 | 234.9 | 0.0701% | Cables | SCB_String Cable Theft | SCB_String Cable Theft | 7:10 | 7:10 | 7:10 | 17:55 | 0 | 0 |  | 10.75 | Work in progress | Open | 0.0075358 | 4.86 | 1037.0999
854 | 2023-12-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:10 | 17:55 | 10.75 | IS17 | INV3 | M1 | SCB8 |  |  | 1 | 1 | IS17INV3M1SCB8 | 250.56 | 0.07477% | Cables | SCB_String Cable Theft | SCB_String Cable Theft | 7:10 | 7:10 | 7:10 | 17:55 | 0 | 0 |  | 10.75 | Work in progress | Open | 0.0080382 | 4.86 | 1106.2399
855 | 2023-12-02 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:10 | 17:55 | 10.75 | IS17 | INV1 | M1 | SCB7 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Cables | SCB_String Cable Theft | SCB_String Cable Theft | 7:10 | 7:10 | 7:10 | 17:55 | 0 | 0 |  | 10.75 | Work in progress | Open | 0.0010048 | 4.86 | 138.28
856 | 2023-12-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:08 | 17:57 | 10.8167 | IS17 | INV3 | M1 | SCB6 |  |  | 1 | 1 | IS17INV3M1SCB6 | 250.56 | 0.07477% | Cables | SCB_String Cable Theft | SCB_String Cable Theft | 7:08 | 7:08 | 7:08 | 14:00 | 0 | 0 | 6.8667 | 6.8667 | Rectification done | Close | 0.0051345 | 3.6503 | 830.891
857 | 2023-12-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:08 | 17:57 | 10.8167 | IS17 | INV3 | M1 | SCB7 |  |  | 1 | 1 | IS17INV3M1SCB7 | 234.9 | 0.0701% | Cables | SCB_String Cable Theft | SCB_String Cable Theft | 7:08 | 7:08 | 7:08 | 11:00 | 0 | 0 | 3.8667 | 3.8667 | Rectification done | Close | 0.0027105 | 1.2849 | 274.1837
858 | 2023-12-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:08 | 17:57 | 10.8167 | IS17 | INV3 | M1 | SCB8 |  |  | 1 | 1 | IS17INV3M1SCB8 | 250.56 | 0.07477% | Cables | SCB_String Cable Theft | SCB_String Cable Theft | 7:08 | 7:08 | 7:08 | 16:00 | 0 | 0 | 8.8667 | 8.8667 | Rectification done | Close | 0.0066299 | 4.8498 | 1103.9185
859 | 2023-12-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:08 | 17:57 | 10.8167 | IS1 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS1INV1M1SCB4 | 232.29 | 0.06932% | Cables | SCB_String Cable Theft | SCB_String Cable Theft | 7:08 | 7:08 | 7:08 | 17:57 | 0 | 0 |  | 10.8167 | Work in progress | Open | 0.0074983 | 5.1933 | 1095.9179
860 | 2023-12-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:08 | 17:57 | 10.8167 | IS1 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS1INV1M1SCB5 | 206.48 | 0.06162% | Cables | SCB_String Cable Theft | SCB_String Cable Theft | 7:08 | 7:08 | 7:08 | 17:57 | 0 | 0 |  | 10.8167 | Work in progress | Open | 0.0066651 | 5.1933 | 974.1493
861 | 2023-12-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:08 | 17:57 | 10.8167 | IS2 | INV1 | M1 | SCB2 |  |  | 1 | 1 | IS2INV1M1SCB2 | 232.29 | 0.06932% | Cables | SCB_String Cable Theft | SCB_String Cable Theft | 7:08 | 7:08 | 7:08 | 17:57 | 0 | 0 |  | 10.8167 | Work in progress | Open | 0.0074983 | 5.1933 | 1095.9179
862 | 2023-12-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:08 | 17:57 | 10.8167 | IS2 | INV1 | M2 | SCB8 |  |  | 1 | 1 | IS2INV1M2SCB8 | 232.29 | 0.06932% | Cables | SCB_String Cable Theft | SCB_String Cable Theft | 7:08 | 7:08 | 7:08 | 17:57 | 0 | 0 |  | 10.8167 | Work in progress | Open | 0.0074983 | 5.1933 | 1095.9179
863 | 2023-12-03 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:08 | 17:57 | 10.8167 | IS2 | INV1 | M2 | SCB9 |  |  | 1 | 1 | IS2INV1M2SCB9 | 232.29 | 0.06932% | Cables | SCB_String Cable Theft | SCB_String Cable Theft | 7:08 | 7:08 | 7:08 | 17:57 | 0 | 0 |  | 10.8167 | Work in progress | Open | 0.0074983 | 5.1933 | 1095.9179
864 | 2023-12-04 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:10 | 17:56 | 10.7667 | IS1 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS1INV1M1SCB4 | 232.29 | 0.06932% | Cables | SCB_String Cable Theft | SCB_String Cable Theft | 7:10 | 7:10 | 7:10 | 13:57 | 0 | 0 | 6.7833 | 6.7833 | Rectification done | Close | 0.0047023 | 3.76 | 793.4502
865 | 2023-12-04 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:10 | 17:56 | 10.7667 | IS1 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS1INV1M1SCB5 | 206.48 | 0.06162% | Cables | SCB_String Cable Theft | SCB_String Cable Theft | 7:10 | 7:10 | 7:10 | 14:57 | 0 | 0 | 7.7833 | 7.7833 | Rectification done | Close | 0.004796 | 4.48 | 840.3444
866 | 2023-12-04 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:10 | 17:56 | 10.7667 | IS2 | INV1 | M1 | SCB2 |  |  | 1 | 1 | IS2INV1M1SCB2 | 232.29 | 0.06932% | Cables | SCB_String Cable Theft | SCB_String Cable Theft | 7:10 | 7:10 | 7:10 | 11:03 | 0 | 0 | 3.8833 | 3.8833 | Rectification done | Close | 0.002692 | 1.41 | 297.5438
867 | 2023-12-04 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:10 | 17:56 | 10.7667 | IS2 | INV1 | M2 | SCB8 |  |  | 1 | 1 | IS2INV1M2SCB8 | 232.29 | 0.06932% | Cables | SCB_String Cable Theft | SCB_String Cable Theft | 7:10 | 7:10 | 7:10 | 12:13 | 0 | 0 | 5.05 | 5.05 | Rectification done | Close | 0.0035007 | 2.33 | 491.6859
868 | 2023-12-04 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:10 | 17:56 | 10.7667 | IS2 | INV1 | M2 | SCB9 |  |  | 1 | 1 | IS2INV1M2SCB9 | 232.29 | 0.06932% | Cables | SCB_String Cable Theft | SCB_String Cable Theft | 7:10 | 7:10 | 7:10 | 12:31 | 0 | 0 | 5.35 | 5.35 | Rectification done | Close | 0.0037087 | 2.58 | 544.4419
869 | 2023-12-04 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:10 | 17:56 | 10.7667 | IS2 | INV1 | M2 | SCB9 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Cables | SCB_String Cable Theft | SCB_String Cable Theft | 7:10 | 7:10 | 7:10 | 17:56 | 0 | 0 |  | 10.7667 | Work in progress | Open | 0.00082929 | 5.44 | 127.5523
870 | 2023-12-04 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:10 | 17:56 | 10.7667 | IS2 | INV1 | M2 | SCB5 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Cables | SCB_String Cable Theft | SCB_String Cable Theft | 7:10 | 7:10 | 7:10 | 17:56 | 0 | 0 |  | 10.7667 | Work in progress | Open | 0.00082929 | 5.44 | 127.5523
871 | 2023-12-05 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:13 | 17:56 | 10.7167 | IS2 | INV1 | M2 | SCB9 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Cables | SCB_String Cable Theft | SCB_String Cable Theft | 7:13 | 7:13 | 7:13 | 16:03 | 0 | 0 | 8.8333 | 8.8333 | Rectification done | Close | 0.00068038 | 5.07 | 118.8768
872 | 2023-12-05 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:13 | 17:56 | 10.7167 | IS2 | INV1 | M2 | SCB5 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Cables | SCB_String Cable Theft | SCB_String Cable Theft | 7:13 | 7:13 | 7:13 | 12:59 | 0 | 0 | 5.7667 | 5.7667 | Rectification done | Close | 0.00044417 | 2.97 | 69.6379
873 | 2023-12-05 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:13 | 17:56 | 10.7167 | IS2 | INV1 | M1 |  |  |  | 1 | 1 | IS2INV1M1 | 2090.61 | 0.6239% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 11:50 | 11:50 | 11:50 | 12:00 | 0 | 0 | 0.16667 | 0.16667 | Rectification done | Close | 0.0010398 | 0.15 | 284.8824
874 | 2023-12-05 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:13 | 17:56 | 10.7167 | IS2 | INV1 | M2 |  |  |  | 1 | 1 | IS2INV1M2 | 2090.61 | 0.6239% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 11:50 | 11:50 | 11:50 | 12:00 | 0 | 0 | 0.16667 | 0.16667 | Rectification done | Close | 0.0010398 | 0.15 | 284.8824
875 | 2023-12-05 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:13 | 17:56 | 10.7167 | IS1 | INV1 | M1 |  |  |  | 1 | 1 | IS1INV1M1 | 2064.8 | 0.6162% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 16:57 | 16:57 | 16:57 | 17:40 | 0 | 0 | 0.71667 | 0.71667 | Rectification done | Close | 0.004416 | 0.06 | 112.5461
876 | 2023-12-05 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:13 | 17:56 | 10.7167 | IS1 | INV1 | M2 |  |  |  | 1 | 1 | IS1INV1M2 | 2090.61 | 0.6239% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 16:57 | 16:57 | 16:57 | 17:40 | 0 | 0 | 0.71667 | 0.71667 | Rectification done | Close | 0.0044712 | 0.06 | 113.953
877 | 2023-12-05 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:13 | 17:56 | 10.7167 | IS11 | INV1 | M1 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | String Fuses | String_brk for MC4 connector damaged | MC4 connector burn | 7:13 | 7:13 | 7:13 | 17:57 | 0 | 0 | 10.7333 | 10.7333 | MC4 connector replaced and string charged | Close | 0.0010032 | 5.44 | 154.7825
878 | 2023-12-06 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:12 | 17:56 | 10.7333 | IS1 |  |  |  |  | Tx | 0 | 1 | IS1Tx | 16789.405 | 5.01% | IDT | IDT_Manual Stop for Checking of LV section | IDT manual stop for checking of inverter LV section | 13:16 | 13:16 | 13:16 | 13:29 | 0 | 0 | 0.21667 | 0.21667 | IDT charged after checking of LV | Close | 0.010856 | 0.18 | 2745.4221
879 | 2023-12-06 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:12 | 17:56 | 10.7333 | IS1 |  |  |  |  | Tx | 0 | 1 | IS1Tx | 16789.405 | 5.01% | IDT | IDT_Manual Stop for Checking of LV section | IDT manual stop for checking of inverter LV section | 15:16 | 15:16 | 15:16 | 15:26 | 0 | 0 | 0.16667 | 0.16667 | IDT charged after checking of LV | Close | 0.0083507 | 0.1 | 1525.2345
880 | 2023-12-06 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:12 | 17:56 | 10.7333 | IS1 | INV2 | M1 |  |  |  | 1 | 1 | IS1INV2M1 | 2090.61 | 0.6239% | Inverter | Inv_manual stop for checking LV voltage | Inverter manual stop for checking of LV side voltage | 10:34 | 10:34 | 10:34 | 10:40 | 0 | 0 | 0.1 | 0.1 | Inverter charged after checking | Close | 0.00062389 | 0.07 | 132.9451
881 | 2023-12-06 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:12 | 17:56 | 10.7333 | IS1 | INV2 | M1 |  |  |  | 1 | 1 | IS1INV2M1 | 2090.61 | 0.6239% | Inverter | Inv_manual stop for checking LV voltage | Inverter manual stop for checking of LV side voltage | 10:34 | 10:34 | 10:34 | 10:40 | 0 | 0 | 0.1 | 0.1 | Inverter charged after checking | Close | 0.00062389 | 0.07 | 132.9451
882 | 2023-12-06 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:12 | 17:56 | 10.7333 | IS1 | INV1 | M1 |  |  |  | 1 | 1 | IS1INV1M1 | 2064.8 | 0.6162% | Inverter | Inv_tripped of GFDI | Due to AC section issue inv tripped of GFDI fault | 7:13 | 7:13 | 7:13 | 13:16 | 0 | 0 | 6.05 | 6.05 | Work in progress | Close | 0.03728 | 3.18 | 5964.9448
883 | 2023-12-06 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:12 | 17:56 | 10.7333 | IS1 | INV1 | M2 |  |  |  | 1 | 1 | IS1INV1M2 | 2090.61 | 0.6239% | Inverter | Inv_tripped of GFDI | Due to AC section issue inv tripped of GFDI fault | 7:13 | 7:13 | 7:13 | 13:16 | 0 | 0 | 6.05 | 6.05 | Work in progress | Close | 0.037746 | 3.18 | 6039.5066
884 | 2023-12-06 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:12 | 17:56 | 10.7333 | IS1 | INV1 | M1 |  |  |  | 1 | 1 | IS1INV1M1 | 2064.8 | 0.6162% | Inverter | Inv_tripped of GFDI | Due to AC section issue inv tripped of GFDI fault | 13:29 | 13:29 | 13:29 | 15:16 | 0 | 0 | 1.7833 | 1.7833 | Work in progress | Close | 0.010989 | 1.28 | 2400.9841
885 | 2023-12-06 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:12 | 17:56 | 10.7333 | IS1 | INV1 | M2 |  |  |  | 1 | 1 | IS1INV1M2 | 2090.61 | 0.6239% | Inverter | Inv_tripped of GFDI | Due to AC section issue inv tripped of GFDI fault | 13:29 | 13:29 | 13:29 | 15:16 | 0 | 0 | 1.7833 | 1.7833 | Work in progress | Close | 0.011126 | 1.28 | 2430.9964
886 | 2023-12-06 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:12 | 17:56 | 10.7333 | IS1 | INV1 | M1 |  |  |  | 1 | 1 | IS1INV1M1 | 2064.8 | 0.6162% | Inverter | Inv_tripped of GFDI | Due to AC section issue inv tripped of GFDI fault | 15:26 | 15:26 | 15:26 | 17:56 | 0 | 0 | 2.5 | 2.5 | Checked IDT LV section and rectification done | Close | 0.015405 | 0.59 | 1106.7036
887 | 2023-12-06 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:12 | 17:56 | 10.7333 | IS1 | INV1 | M2 |  |  |  | 1 | 1 | IS1INV1M2 | 2090.61 | 0.6239% | Inverter | Inv_tripped of GFDI | Due to AC section issue inv tripped of GFDI fault | 15:26 | 15:26 | 15:26 | 17:56 | 0 | 0 | 2.5 | 2.5 | Checked IDT LV section and rectification done | Close | 0.015597 | 0.59 | 1120.5374
888 | 2023-12-06 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:12 | 17:56 | 10.7333 | IS3 | INV1 | M1 |  |  |  | 1 | 1 | IS3INV1M1 | 2090.61 | 0.6239% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 7:13 | 7:13 | 7:13 | 8:09 | 0 | 0 | 0.93333 | 0.93333 | Rectification done | Close | 0.005823 | 0.04 | 75.9686
889 | 2023-12-06 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:12 | 17:56 | 10.7333 | IS3 | INV1 | M2 |  |  |  | 1 | 1 | IS3INV1M2 | 2090.61 | 0.6239% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 7:13 | 7:13 | 7:13 | 8:09 | 0 | 0 | 0.93333 | 0.93333 | Rectification done | Close | 0.005823 | 0.04 | 75.9686
890 | 2023-12-07 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:12 | 17:57 | 10.75 | IS14 | INV2 | M1 |  |  |  | 1 | 1 | IS14INV2M1 | 2223.72 | 0.6636% | Inverter | Inv Unit_AC Coil failure | Inverter tripped in AC switch disconnection fault | 7:12 | 7:12 | 7:12 | 8:00 | 0 | 0 | 0.8 | 0.8 | Reset AC coil and restarted after discussion with OEM | Close | 0.0053089 | 0.02 | 40.4028
891 | 2023-12-07 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:12 | 17:57 | 10.75 | IS14 | INV2 | M2 |  |  |  | 1 | 1 | IS14INV2M2 | 2004.48 | 0.5982% | Inverter | Inv Unit_AC Coil failure | Inverter tripped in AC switch disconnection fault | 7:12 | 7:12 | 7:12 | 8:00 | 0 | 0 | 0.8 | 0.8 | Reset AC coil and restarted after discussion with OEM | Close | 0.0047855 | 0.02 | 36.4194
892 | 2023-12-11 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:13 | 17:58 | 10.75 | IS8 | INV2 | M1 |  |  |  | 1 | 1 | IS8INV2M1 | 2255.04 | 0.673% | Inverter | Inv Unit_AC Switch Disconnection | Inverter tripped in AC switch disconnection fault | 13:54 | 13:54 | 13:54 | 13:57 | 0 | 0 | 0.05 | 0.05 | Inverter unit reset automatically | Close | 0.00033648 | 0.05 | 102.4296
893 | 2023-12-16 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:17 | 17:59 | 10.7 | IS11 | INV1 | M1 | SCB3 | Str_Typ5(545*29) |  | 0 | 0 | Str_Typ5(545*29) | 15.805 | 0.004717% | String Fuses | String_Breakdown for MC4 burn | String breakdown due to MC4 burn | 7:17 | 7:17 | 7:17 | 17:59 | 0 | 0 | 10.7 | 10.7 | MC4 connector replaced and string charged | Close | 0.00050468 | 5.19 | 74.5183
894 | 2023-12-16 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:17 | 17:59 | 10.7 | IS11 | INV2 | M2 | SCB6 | Str_Typ5(545*29) |  | 0 | 0 | Str_Typ5(545*29) | 15.805 | 0.004717% | String Fuses | String_Breakdown for MC4 burn | String breakdown due to MC4 burn | 7:17 | 7:17 | 7:17 | 17:59 | 0 | 0 | 10.7 | 10.7 | MC4 connector replaced and string charged | Close | 0.00050468 | 5.19 | 74.5183
895 | 2023-12-16 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:17 | 17:59 | 10.7 | IS11 | INV3 | M2 | SCB4 | Str_Typ5(545*29) |  | 0 | 0 | Str_Typ5(545*29) | 15.805 | 0.004717% | String Fuses | String_Breakdown for MC4 burn | String breakdown due to MC4 burn | 7:17 | 7:17 | 7:17 | 17:59 | 0 | 0 | 10.7 | 10.7 | MC4 connector replaced and string charged | Close | 0.00050468 | 5.19 | 74.5183
896 | 2023-12-17 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:18 | 18:00 | 10.7 | IS5 | INV4 | M1 | SCB5 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | String Fuses | String_Breakdown for MC4 burn | String breakdown due to MC4 burn | 7:18 | 7:18 | 7:18 | 18:00 | 0 | 0 | 10.7 | 10.7 | MC4 connector replaced and string charged | Close | 0.00041208 | 5.34 | 62.6038
897 | 2023-12-19 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:22 | 18:01 | 10.65 | IS3 | INV1 | M1 |  |  |  | 1 | 1 | IS3INV1M1 | 2090.61 | 0.6239% | Inverter | Inv Unit_AC Coil failure | Inverter tripped in AC switch disconnection fault | 7:22 | 7:22 | 7:22 | 8:04 | 0 | 0 | 0.7 | 0.7 | Reset AC coil and restarted after discussion with OEM | Close | 0.0043673 | 0.02 | 37.9843
898 | 2023-12-21 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:25 | 18:04 | 10.65 | IS14 | INV1 | M1 |  |  |  | 1 | 1 | IS14INV1M1 | 2223.72 | 0.6636% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 8:43 | 8:43 | 8:43 | 9:08 | 0 | 0 | 0.41667 | 0.41667 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0027651 | 0.14 | 282.8196
899 | 2023-12-21 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:25 | 18:04 | 10.65 | IS14 | INV1 | M2 |  |  |  | 1 | 1 | IS14INV1M2 | 1910.52 | 0.5701% | Inverter | Inv Unit_AC Switch Disconnection | Inverter tripped in AC switch disconnection fault | 7:25 | 7:25 | 7:25 | 9:08 | 0 | 0 | 1.7167 | 1.7167 | Reset AC coil and restarted after discussion with OEM | Close | 0.0097876 | 0.31 | 538.04
900 | 2023-12-22 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:31 | 18:04 | 10.55 | IS14 | INV1 | M1 |  |  |  | 1 | 1 | IS14INV1M1 | 2223.72 | 0.6636% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 8:00 | 8:00 | 8:00 | 8:26 | 0 | 0 | 0.43333 | 0.43333 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0028757 | 0.02 | 40.4028
901 | 2023-12-22 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:31 | 18:04 | 10.55 | IS14 | INV1 | M2 |  |  |  | 1 | 1 | IS14INV1M2 | 1910.52 | 0.5701% | Inverter | Inv Unit_AC Switch Disconnection | Inverter tripped in AC switch disconnection fault | 7:31 | 7:31 | 7:31 | 8:26 | 0 | 0 | 0.91667 | 0.91667 | Reset AC coil and restarted after discussion with OEM | Close | 0.0052264 | 0.02 | 34.7123
902 | 2023-12-24 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:20 | 18:02 | 10.7 | IS14 | INV1 | M1 |  |  |  | 1 | 1 | IS14INV1M1 | 2223.72 | 0.6636% | Inverter | Inv Unit_AC Switch Disconnection | Inverter tripped in AC switch disconnection fault | 7:20 | 7:20 | 7:20 | 8:56 | 0 | 0 | 1.6 | 1.6 | Fault was coming on Unit_2 and AC breaker replaced by OEM. After this fault came to Unit_1 and NO-NC connection interchanged by OEM instruction. Inverter charged | Close | 0.010618 | 0.15 | 303.021
903 | 2023-12-24 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:20 | 18:02 | 10.7 | IS14 | INV1 | M1 |  |  |  | 1 | 1 | IS14INV1M1 | 2223.72 | 0.6636% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 7:40 | 7:40 | 7:40 | 8:56 | 0 | 0 | 1.2667 | 1.2667 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0084058 | 0.15 | 303.021
904 | 2023-12-24 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:20 | 18:02 | 10.7 | IS4 | INV2 | M1 | SCB1 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Connectors | String_Breakdown for MC4 burn | String breakdown due to MC4 burn | 7:40 | 7:40 | 7:40 | 18:02 | 0 | 0 | 10.3667 | 10.3667 | MC4 connector replaced and string charged | Close | 0.00039924 | 4.8 | 56.2731
905 | 2023-12-25 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:23 | 18:02 | 10.65 | IS14 | INV1 | M1 |  |  |  | 1 | 1 | IS14INV1M1 | 2223.72 | 0.6636% | Inverter | Inv Unit_AC Switch Disconnection | Inverter tripped in AC switch disconnection fault | 15:20 | 15:45 | 15:45 | 18:02 | 0.41667 | 0.41667 | 2.7 | 2.7 | Fault was coming on Unit_2 and AC breaker replaced by OEM. After this fault came to Unit_1 and by OEM instruction we reset the inverter. Inverter charged | Close | 0.017918 | 0.6 | 1212.0839
906 | 2023-12-31 | FY24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 7:25 | 18:08 | 10.7167 | IS9 | INV3 | M1 | SCB1 | Str_Typ5(545*29) |  | 0 | 0 | Str_Typ5(545*29) | 15.805 | 0.004717% | Connectors | String_Breakdown for MC4 burn | String breakdown due to MC4 burn | 7:25 | 7:25 | 7:25 | 18:08 | 0 | 0 | 10.7167 | 10.7167 | MC4 connector replaced and string charged | Close | 0.00050547 | 5.33 | 76.5285
907 | 2024-01-01 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:26 | 18:08 | 10.7 | IS2 | INV3 | M2 |  |  |  | 1 | 1 | IS2INV3M2 | 2090.61 | 0.6239% | Inverter | Inv_tripped in INS Fault | Inverter Unit tripped in INS fault | 7:26 | 7:26 | 7:26 | 8:19 | 0 | 0 | 0.88333 | 0.88333 | Checked related parameter and floating value on inverte side found ok then reboot the inverter and start the inverter | Close | 0.0055111 | 0.05 | 94.6017
908 | 2024-01-01 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:26 | 18:08 | 10.7 | IS4 | INV2 | M1 |  |  |  | 1 | 1 | IS4INV2M1 | 2114.1 | 0.6309% | Inverter | Inv_tripped in INS Fault | Inverter Unit tripped in INS fault | 7:26 | 7:26 | 7:26 | 8:08 | 0 | 0 | 0.7 | 0.7 | checked related connection and parameter then rboot the inverter and start | Close | 0.0044163 | 0.03 | 57.3988
909 | 2024-01-01 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:26 | 18:08 | 10.7 | IS6 | INV3 | M2 |  |  |  | 1 | 1 | IS6INV3M2 | 2380.32 | 0.7104% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 7:26 | 7:26 | 7:26 | 8:20 | 0 | 0 | 0.9 | 0.9 | checked related connection and parameter then rboot the inverter and start | Close | 0.0063932 | 0.05 | 107.7113
910 | 2024-01-01 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:26 | 18:08 | 10.7 | IS12 | INV1 | M1 |  |  |  | 1 | 1 | IS12INV1M1 | 2192.4 | 0.6543% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 7:26 | 7:26 | 7:26 | 8:30 | 0 | 0 | 1.0667 | 1.0667 | checked related connection and parameter then rboot the inverter and start | Close | 0.0069789 | 0.08 | 158.7324
911 | 2024-01-01 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:26 | 18:08 | 10.7 | IS12 | INV1 | M2 |  |  |  | 1 | 1 | IS12INV1M2 | 2114.1 | 0.6309% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 7:58 | 7:58 | 7:58 | 9:04 | 0 | 0 | 1.1 | 1.1 | checked related connection and parameter then rboot the inverter and start | Close | 0.0069399 | 0.24 | 459.1901
912 | 2024-01-01 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:26 | 18:08 | 10.7 | IS15 | INV1 | M2 |  |  |  | 1 | 1 | IS15INV1M2 | 2192.4 | 0.6543% | Inverter | Inv_tripped in INS Fault | Inverter Unit tripped in INS fault | 7:26 | 7:26 | 7:26 | 8:30 | 0 | 0 | 1.0667 | 1.0667 | checked related connection and parameter then rboot the inverter and start | Close | 0.0069789 | 0.08 | 158.7324
913 | 2024-01-01 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:26 | 18:08 | 10.7 | IS16 | INV4 | M1 |  |  |  | 1 | 1 | IS16INV4M1 | 2129.76 | 0.6356% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 7:26 | 7:26 | 7:26 | 9:20 | 0 | 0 | 1.9 | 1.9 | checked related connection and parameter then rboot the inverter and start | Close | 0.012076 | 0.33 | 636.0634
914 | 2024-01-01 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:26 | 18:08 | 10.7 | IS17 | INV4 | M2 |  |  |  | 1 | 1 | IS17INV4M2 | 2004.48 | 0.5982% | Inverter | Inv_tripped in INS Fault | Inverter Unit tripped in INS fault | 7:26 | 7:26 | 7:26 | 8:45 | 0 | 0 | 1.3167 | 1.3167 | checked related connection and parameter then rboot the inverter and start | Close | 0.0078762 | 0.14 | 253.9718
915 | 2024-01-01 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:26 | 18:08 | 10.7 | IS20 | INV4 | M1 |  |  |  | 1 | 1 | IS20INV4M1 | 2255.04 | 0.673% | Inverter | Inv_tripped in INS Fault | Inverter Unit tripped in INS fault | 7:26 | 7:26 | 7:26 | 8:30 | 0 | 0 | 1.0667 | 1.0667 | checked related connection and parameter then rboot the inverter and start | Close | 0.0071783 | 0.08 | 163.2676
916 | 2024-01-01 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:26 | 18:08 | 10.7 | IS6 | INV3 | M1 |  |  |  | 1 | 1 | IS6INV3M1 | 2192.4 | 0.6543% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 7:26 | 7:26 | 7:26 | 9:36 | 0 | 0 | 2.1667 | 2.1667 | checked related connection and parameter then rboot the inverter and start | Close | 0.014176 | 0.46 | 912.7112
917 | 2024-01-01 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:26 | 18:08 | 10.7 | IS12 | INV3 | M1 |  |  |  | 1 | 1 | IS12INV3M1 | 2192.4 | 0.6543% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 9:19 | 9:19 | 9:19 | 9:50 | 0 | 0 | 0.51667 | 0.51667 | checked related connection and parameter then rboot the inverter and start | Close | 0.0033804 | 0.24 | 476.1972
918 | 2024-01-01 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:26 | 18:08 | 10.7 | IS12 | INV3 | M2 |  |  |  | 1 | 1 | IS12INV3M2 | 2004.48 | 0.5982% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 9:19 | 9:19 | 9:19 | 9:50 | 0 | 0 | 0.51667 | 0.51667 | checked related connection and parameter then rboot the inverter and start | Close | 0.0030906 | 0.24 | 435.3803
919 | 2024-01-02 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:25 | 18:08 | 10.7167 | IS6 | INV3 | M1 |  |  |  | 1 | 1 | IS6INV3M1 | 2192.4 | 0.6543% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 7:26 | 7:26 | 7:26 | 9:15 | 0 | 0 | 1.8167 | 1.8167 | 1 no module found damaged and replaced | Close | 0.011886 | 0.29 | 575.4049
920 | 2024-01-02 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:25 | 18:08 | 10.7167 | IS6 | INV3 | M2 |  |  |  | 1 | 1 | IS6INV3M2 | 2380.32 | 0.7104% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 7:26 | 7:26 | 7:26 | 9:15 | 0 | 0 | 1.8167 | 1.8167 | 1 no module found damaged and replaced | Close | 0.012905 | 0.29 | 624.7253
921 | 2024-01-02 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:25 | 18:08 | 10.7167 | IS7 | INV4 | M2 |  |  |  | 1 | 1 | IS7INV4M2 | 1973.16 | 0.5888% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 7:26 | 7:26 | 7:26 | 8:06 | 0 | 0 | 0.66667 | 0.66667 | checked related connection and parameter then rboot the inverter and start | Close | 0.0039256 | 0.05 | 89.287
922 | 2024-01-02 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:25 | 18:08 | 10.7167 | IS10 | INV2 | M2 |  |  |  | 1 | 1 | IS10INV2M2 | 2223.72 | 0.6636% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 7:26 | 7:26 | 7:26 | 8:23 | 0 | 0 | 0.95 | 0.95 | checked related connection and parameter then rboot the inverter and start | Close | 0.0063044 | 0.05 | 100.625
923 | 2024-01-02 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:25 | 18:08 | 10.7167 | IS10 | INV2 | M2 |  |  |  | 1 | 1 | IS10INV2M2 | 2223.72 | 0.6636% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 7:26 | 7:26 | 7:26 | 8:23 | 0 | 0 | 0.95 | 0.95 | checked related connection and parameter then rboot the inverter and start | Close | 0.0063044 | 0.05 | 100.625
924 | 2024-01-02 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:25 | 18:08 | 10.7167 | IS10 | INV3 | M1 |  |  |  | 1 | 1 | IS10INV3M1 | 1941.84 | 0.5795% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 7:26 | 7:26 | 7:26 | 8:23 | 0 | 0 | 0.95 | 0.95 | 1 no module found damaged and replaced | Close | 0.0055052 | 0.05 | 87.8697
925 | 2024-01-02 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:25 | 18:08 | 10.7167 | IS11 | INV2 | M2 |  |  |  | 1 | 1 | IS11INV2M2 | 2038.845 | 0.6084% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 7:26 | 7:26 | 7:26 | 8:50 | 0 | 0 | 1.4 | 1.4 | checked related connection and parameter then rboot the inverter and start | Close | 0.0085182 | 0.2 | 369.0371
926 | 2024-01-02 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:25 | 18:08 | 10.7167 | IS12 | INV1 | M2 |  |  |  | 1 | 1 | IS12INV1M2 | 2114.1 | 0.6309% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 7:26 | 7:26 | 7:26 | 9:02 | 0 | 0 | 1.6 | 1.6 | checked related connection and parameter then rboot the inverter and start | Close | 0.010094 | 0.21 | 401.7914
927 | 2024-01-03 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:26 | 18:09 | 10.7167 | IS1 | INV1 | M1 | SCB2 |  |  | 1 | 1 | IS1INV1M1SCB2 | 232.29 | 0.06932% | SCB | SCB_String Cable Theft | String cable theft | 7:26 | 7:26 | 7:26 | 18:09 | 0 | 0 |  | 10.7167 | Cable Restoration WIP | Open | 0.007429 | 5.39 | 1133.1178
928 | 2024-01-03 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:26 | 18:09 | 10.7167 | IS1 | INV1 | M1 | SCB8 |  |  | 1 | 1 | IS1INV1M1SCB8 | 232.29 | 0.06932% | SCB | SCB_String Cable Theft | String cable theft | 7:26 | 7:26 | 7:26 | 18:09 | 0 | 0 |  | 10.7167 | Cable Restoration WIP | Open | 0.007429 | 5.39 | 1133.1178
929 | 2024-01-03 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:26 | 18:09 | 10.7167 | IS1 | INV1 | M1 | SCB7 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | SCB | SCB_String Cable Theft | String cable theft | 7:26 | 7:26 | 7:26 | 18:09 | 0 | 0 |  | 10.7167 | Cable Restoration WIP | Open | 0.00082544 | 5.39 | 125.902
930 | 2024-01-03 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:26 | 18:09 | 10.7167 | IS1 | INV1 | M1 | SCB5 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | SCB | SCB_String Cable Theft | String cable theft | 7:26 | 7:26 | 7:26 | 18:09 | 0 | 0 |  | 10.7167 | Cable Restoration WIP | Open | 0.00082544 | 5.39 | 125.902
931 | 2024-01-03 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:26 | 18:09 | 10.7167 | IS1 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS1INV1M1SCB4 | 232.29 | 0.06932% | SCB | SCB_String Cable Theft | String cable theft | 7:26 | 7:26 | 7:26 | 18:09 | 0 | 0 |  | 10.7167 | Cable Restoration WIP | Open | 0.007429 | 5.39 | 1133.1178
932 | 2024-01-03 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:26 | 18:09 | 10.7167 | IS1 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS1INV1M1SCB6 | 232.29 | 0.06932% | SCB | SCB_String Cable Theft | String cable theft | 7:26 | 7:26 | 7:26 | 18:09 | 0 | 0 |  | 10.7167 | Cable Restoration WIP | Open | 0.007429 | 5.39 | 1133.1178
933 | 2024-01-03 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:26 | 18:09 | 10.7167 | IS1 | INV1 | M1 | SCB7 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | SCB | SCB_String Cable Theft | String cable theft | 7:26 | 7:26 | 7:26 | 18:09 | 0 | 0 |  | 10.7167 | Cable Restoration WIP | Open | 0.00082544 | 5.39 | 125.902
934 | 2024-01-03 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:26 | 18:09 | 10.7167 | IS1 | INV1 | M1 | SCB7 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | SCB | SCB_String Cable Theft | String cable theft | 7:26 | 7:26 | 7:26 | 18:09 | 0 | 0 |  | 10.7167 | Cable Restoration WIP | Open | 0.00082544 | 5.39 | 125.902
935 | 2024-01-03 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:26 | 18:09 | 10.7167 | IS1 | INV1 | M1 | SCB7 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | SCB | SCB_String Cable Theft | String cable theft | 7:26 | 7:26 | 7:26 | 18:09 | 0 | 0 |  | 10.7167 | Cable Restoration WIP | Open | 0.00082544 | 5.39 | 125.902
936 | 2024-01-03 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:26 | 18:09 | 10.7167 | IS1 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS1INV1M1SCB3 | 232.29 | 0.06932% | SCB | SCB_String Cable Theft | String cable theft | 7:26 | 7:26 | 7:26 | 18:09 | 0 | 0 |  | 10.7167 | Cable Restoration WIP | Open | 0.007429 | 5.39 | 1133.1178
937 | 2024-01-03 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:26 | 18:09 | 10.7167 | IS2 | INV1 | M1 | SCB2 |  |  | 1 | 1 | IS2INV1M1SCB2 | 232.29 | 0.06932% | SCB | SCB_String Cable Theft | String cable theft | 7:26 | 7:26 | 7:26 | 18:09 | 0 | 0 |  | 10.7167 | Cable Restoration WIP | Open | 0.007429 | 5.39 | 1133.1178
938 | 2024-01-03 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:26 | 18:09 | 10.7167 | IS2 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS2INV1M1SCB3 | 232.29 | 0.06932% | SCB | SCB_String Cable Theft | String cable theft | 7:26 | 7:26 | 7:26 | 18:09 | 0 | 0 |  | 10.7167 | Cable Restoration WIP | Open | 0.007429 | 5.39 | 1133.1178
939 | 2024-01-03 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:26 | 18:09 | 10.7167 | IS2 | INV1 | M2 | SCB9 |  |  | 1 | 1 | IS2INV1M2SCB9 | 232.29 | 0.06932% | SCB | SCB_String Cable Theft | String cable theft | 7:26 | 7:26 | 7:26 | 18:09 | 0 | 0 |  | 10.7167 | Cable Restoration WIP | Open | 0.007429 | 5.39 | 1133.1178
940 | 2024-01-03 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:26 | 18:09 | 10.7167 | IS2 | INV1 | M2 | SCB9 |  |  | 1 | 1 | IS2INV1M2SCB9 | 232.29 | 0.06932% | SCB | SCB_String Cable Theft | String cable theft | 7:26 | 7:26 | 7:26 | 18:09 | 0 | 0 |  | 10.7167 | Cable Restoration WIP | Open | 0.007429 | 5.39 | 1133.1178
941 | 2024-01-03 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:26 | 18:09 | 10.7167 | IS2 | INV1 | M2 | SCB9 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | SCB | SCB_String Cable Theft | String cable theft | 7:26 | 7:26 | 7:26 | 13:40 | 0 | 0 | 6.2333 | 6.2333 | Cable Restoration completed and scb charged | Close | 0.00048012 | 3.28 | 76.6157
942 | 2024-01-03 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:26 | 18:09 | 10.7167 | IS2 | INV1 | M2 | SCB9 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | SCB | SCB_String Cable Theft | String cable theft | 7:26 | 7:26 | 7:26 | 13:40 | 0 | 0 | 6.2333 | 6.2333 | Cable Restoration completed and scb charged | Close | 0.00048012 | 3.28 | 76.6157
943 | 2024-01-03 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:26 | 18:09 | 10.7167 | IS2 | INV1 | M2 | SCB8 |  |  | 1 | 1 | IS2INV1M2SCB8 | 232.29 | 0.06932% | SCB | SCB_String Cable Theft | String cable theft | 7:26 | 7:26 | 7:26 | 16:20 | 0 | 0 | 8.9 | 8.9 | Cable Restoration completed and scb charged | Close | 0.0061696 | 5.39 | 1133.1178
944 | 2024-01-03 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:26 | 18:09 | 10.7167 | IS2 | INV1 | M2 | SCB7 |  |  | 1 | 1 | IS2INV1M2SCB7 | 232.29 | 0.06932% | SCB | SCB_String Cable Theft | String cable theft | 7:26 | 7:26 | 7:26 | 18:09 | 0 | 0 |  | 10.7167 | Cable Restoration WIP | Open | 0.007429 | 5.39 | 1133.1178
945 | 2024-01-03 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:26 | 18:09 | 10.7167 | IS2 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS2INV1M2SCB6 | 232.29 | 0.06932% | SCB | SCB_String Cable Theft | String cable theft | 7:26 | 7:26 | 7:26 | 18:09 | 0 | 0 |  | 10.7167 | Cable Restoration WIP | Open | 0.007429 | 5.39 | 1133.1178
946 | 2024-01-03 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:26 | 18:09 | 10.7167 | IS17 | INV1 | M1 | SCB7 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | SCB | SCB_String Cable Theft | String cable theft | 7:26 | 7:26 | 7:26 | 16:12 | 0 | 0 | 8.7667 | 8.7667 | Cable Restoration completed and scb charged | Close | 0.0008194 | 4.96 | 140.5915
947 | 2024-01-03 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:26 | 18:09 | 10.7167 | IS17 | INV3 | M1 | SCB7 |  |  | 1 | 1 | IS17INV3M1SCB7 | 234.9 | 0.0701% | SCB | SCB_String Cable Theft | String cable theft | 7:26 | 7:26 | 7:26 | 14:30 | 0 | 0 | 7.0667 | 7.0667 | Cable Restoration completed and scb charged | Close | 0.0049538 | 4.96 | 1054.4366
948 | 2024-01-03 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:26 | 18:09 | 10.7167 | IS17 | INV3 | M1 | SCB8 |  |  | 1 | 1 | IS17INV3M1SCB8 | 250.56 | 0.07477% | SCB | SCB_String Cable Theft | String cable theft | 7:26 | 7:26 | 7:26 | 18:09 | 0 | 0 |  | 10.7167 | Cable Restoration WIP | Open | 0.0080133 | 5.39 | 1222.2394
949 | 2024-01-03 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:26 | 18:09 | 10.7167 | IS17 | INV3 | M1 | SCB6 |  |  | 1 | 1 | IS17INV3M1SCB6 | 250.56 | 0.07477% | SCB | SCB_String Cable Theft | String cable theft | 7:26 | 7:26 | 7:26 | 18:09 | 0 | 0 | 10.7167 | 10.7167 | Cable Restoration completed and scb charged | Close | 0.0080133 | 5.2 | 1179.1549
950 | 2024-01-04 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:30 | 18:09 | 10.65 | IS1 | INV1 | M1 | SCB2 |  |  | 1 | 1 | IS1INV1M1SCB2 | 232.29 | 0.06932% | SCB | SCB_String Cable Theft | String cable theft | 7:30 | 7:30 | 7:30 | 18:09 | 0 | 0 |  | 10.65 | Cable Restoration WIP | Open | 0.0073827 | 5.2 | 1093.1749
951 | 2024-01-04 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:30 | 18:09 | 10.65 | IS1 | INV1 | M1 | SCB8 |  |  | 1 | 1 | IS1INV1M1SCB8 | 232.29 | 0.06932% | SCB | SCB_String Cable Theft | String cable theft | 7:30 | 7:30 | 7:30 | 16:20 | 0 | 0 | 8.8333 | 8.8333 | Cable Restoration completed and scb charged | Close | 0.0061234 | 4.97 | 1044.8229
952 | 2024-01-04 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:30 | 18:09 | 10.65 | IS1 | INV1 | M1 | SCB5 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | SCB | SCB_String Cable Theft | String cable theft | 7:30 | 7:30 | 7:30 | 17:46 | 0 | 0 | 10.2667 | 10.2667 | Cable Restoration completed and scb charged | Close | 0.00079078 | 5.2 | 121.4639
953 | 2024-01-04 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:30 | 18:09 | 10.65 | IS1 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS1INV1M1SCB4 | 232.29 | 0.06932% | SCB | SCB_String Cable Theft | String cable theft | 7:30 | 7:30 | 7:30 | 17:46 | 0 | 0 | 10.2667 | 10.2667 | Cable Restoration completed and scb charged | Close | 0.007117 | 5.2 | 1093.1749
954 | 2024-01-04 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:30 | 18:09 | 10.65 | IS1 | INV1 | M1 | SCB7 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | SCB | SCB_String Cable Theft | String cable theft | 7:30 | 7:30 | 7:30 | 17:00 | 0 | 0 | 9.5 | 9.5 | Cable Restoration completed and scb charged | Close | 0.00073173 | 5.16 | 120.5295
955 | 2024-01-04 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:30 | 18:09 | 10.65 | IS1 | INV1 | M1 | SCB7 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | SCB | SCB_String Cable Theft | String cable theft | 7:30 | 7:30 | 7:30 | 17:00 | 0 | 0 | 9.5 | 9.5 | Cable Restoration completed and scb charged | Close | 0.00073173 | 5.16 | 120.5295
956 | 2024-01-04 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:30 | 18:09 | 10.65 | IS1 | INV1 | M1 | SCB7 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | SCB | SCB_String Cable Theft | String cable theft | 7:30 | 7:30 | 7:30 | 17:00 | 0 | 0 | 9.5 | 9.5 | Cable Restoration completed and scb charged | Close | 0.00073173 | 5.16 | 120.5295
957 | 2024-01-04 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:30 | 18:09 | 10.65 | IS1 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS1INV1M1SCB3 | 232.29 | 0.06932% | SCB | SCB_String Cable Theft | String cable theft | 7:30 | 7:30 | 7:30 | 18:09 | 0 | 0 |  | 10.65 | Cable Restoration WIP | Open | 0.0073827 | 5.2 | 1093.1749
958 | 2024-01-04 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:30 | 18:09 | 10.65 | IS2 | INV1 | M1 | SCB2 |  |  | 1 | 1 | IS2INV1M1SCB2 | 232.29 | 0.06932% | SCB | SCB_String Cable Theft | String cable theft | 7:30 | 7:30 | 7:30 | 17:00 | 0 | 0 | 9.5 | 9.5 | Cable Restoration completed and scb charged | Close | 0.0065855 | 5.16 | 1084.7658
959 | 2024-01-04 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:30 | 18:09 | 10.65 | IS2 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS2INV1M1SCB3 | 232.29 | 0.06932% | SCB | SCB_String Cable Theft | String cable theft | 7:30 | 7:30 | 7:30 | 16:35 | 0 | 0 | 9.0833 | 9.0833 | Cable Restoration completed and scb charged | Close | 0.0062967 | 5.05 | 1061.641
960 | 2024-01-04 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:30 | 18:09 | 10.65 | IS2 | INV1 | M2 | SCB9 |  |  | 1 | 1 | IS2INV1M2SCB9 | 232.29 | 0.06932% | SCB | SCB_String Cable Theft | String cable theft | 7:30 | 7:30 | 7:30 | 13:00 | 0 | 0 | 5.5 | 5.5 | Cable Restoration completed and scb charged | Close | 0.0038127 | 3.1 | 651.7004
961 | 2024-01-04 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:30 | 18:09 | 10.65 | IS2 | INV1 | M2 | SCB9 |  |  | 1 | 1 | IS2INV1M2SCB9 | 232.29 | 0.06932% | SCB | SCB_String Cable Theft | String cable theft | 7:30 | 7:30 | 7:30 | 13:30 | 0 | 0 | 6 | 6 | Cable Restoration completed and scb charged | Close | 0.0041593 | 3.1 | 651.7004
962 | 2024-01-04 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:30 | 18:09 | 10.65 | IS2 | INV1 | M2 | SCB7 |  |  | 1 | 1 | IS2INV1M2SCB7 | 232.29 | 0.06932% | SCB | SCB_String Cable Theft | String cable theft | 7:30 | 7:30 | 7:30 | 12:20 | 0 | 0 | 4.8333 | 4.8333 | Cable Restoration completed and scb charged | Close | 0.0033505 | 2.8 | 588.6326
963 | 2024-01-04 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:30 | 18:09 | 10.65 | IS2 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS2INV1M2SCB6 | 232.29 | 0.06932% | SCB | SCB_String Cable Theft | String cable theft | 7:30 | 7:30 | 7:30 | 12:00 | 0 | 0 | 4.5 | 4.5 | Cable Restoration completed and scb charged | Close | 0.0031195 | 2.8 | 588.6326
964 | 2024-01-04 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:30 | 18:09 | 10.65 | IS17 | INV3 | M1 | SCB8 |  |  | 1 | 1 | IS17INV3M1SCB8 | 250.56 | 0.07477% | SCB | SCB_String Cable Theft | String cable theft | 7:30 | 7:30 | 7:30 | 11:00 | 0 | 0 | 3.5 | 3.5 | Cable Restoration completed and scb charged | Close | 0.0026171 | 1.01 | 229.0282
965 | 2024-01-04 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:30 | 18:09 | 10.65 | IS3 | INV2 | M2 |  |  |  | 1 | 1 | IS3INV2M2 | 2090.61 | 0.6239% | Inverter | Inv_tripped in INS Fault | Inverter Unit tripped in INS fault | 7:30 | 7:30 | 7:30 | 8:30 | 0 | 0 | 1 | 1 | checked related connection and parameter then rboot the inverter and start | Close | 0.0062389 | 0.02 | 37.8407
966 | 2024-01-04 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:30 | 18:09 | 10.65 | IS12 | INV1 | M2 |  |  |  | 1 | 1 | IS12INV1M2 | 2114.1 | 0.6309% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 7:30 | 7:30 | 7:30 | 9:11 | 0 | 0 | 1.6833 | 1.6833 | checked related connection and parameter then rboot the inverter and start | Close | 0.01062 | 0.07 | 133.9305
967 | 2024-01-04 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:30 | 18:09 | 10.65 | IS12 | INV4 | M2 |  |  |  | 1 | 1 | IS12INV4M2 | 2208.06 | 0.6589% | Inverter | Inv Unit_AC Switch Disconnection | Inverter tripped in AC switch disconnection fault | 7:30 | 7:30 | 7:30 | 9:05 | 0 | 0 | 1.5833 | 1.5833 | Reset AC coil and restarted after discussion with OEM | Close | 0.010433 | 0.07 | 139.8829
968 | 2024-01-05 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:26 | 18:09 | 10.7167 | IS1 | INV1 | M1 | SCB2 |  |  | 1 | 1 | IS1INV1M1SCB2 | 232.29 | 0.06932% | SCB | SCB_String Cable Theft | String cable theft | 7:30 | 7:30 | 7:30 | 10:00 | 0 | 0 | 2.5 | 2.5 | Cable Restoration completed and scb charged | Close | 0.001733 | 0.56 | 117.7265
969 | 2024-01-05 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:26 | 18:09 | 10.7167 | IS1 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS1INV1M1SCB3 | 232.29 | 0.06932% | SCB | SCB_String Cable Theft | String cable theft | 7:30 | 7:30 | 7:30 | 10:30 | 0 | 0 | 3 | 3 | Cable Restoration completed and scb charged | Close | 0.0020796 | 0.86 | 180.7943
970 | 2024-01-05 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:26 | 18:09 | 10.7167 | IS10 | INV2 | M2 |  |  |  | 1 | 1 | IS10INV2M2 | 2223.72 | 0.6636% | Inverter | Inv_tripped in INS Fault | Inverter Unit tripped in INS fault | 7:26 | 7:26 | 7:26 | 8:00 | 0 | 0 | 0.56667 | 0.56667 | checked related connection and parameter then rboot the inverter and start | Close | 0.0037605 | 0.02 | 40.25
971 | 2024-01-05 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:26 | 18:09 | 10.7167 | IS4 | INV4 | M2 |  |  |  | 1 | 1 | IS4INV4M2 | 2061.9 | 0.6153% | Inverter | Inv_tripped in INS Fault | Inverter Unit tripped in INS fault | 7:26 | 7:26 | 7:26 | 7:52 | 0 | 0 | 0.43333 | 0.43333 | checked related connection and parameter then rboot the inverter and start | Close | 0.0026664 | 0.01 | 18.6605
972 | 2024-01-05 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:26 | 18:09 | 10.7167 | IS11 | INV4 | M1 |  |  |  | 1 | 1 | IS11INV4M1 | 2023.04 | 0.6037% | Inverter | Inv Unit_AC Switch Disconnection | Inverter tripped in AC switch disconnection fault | 7:26 | 7:26 | 7:26 | 8:13 | 0 | 0 | 0.78333 | 0.78333 | checked related connection and parameter then rboot the inverter and start | Close | 0.0047292 | 0.04 | 73.2353
973 | 2024-01-07 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:27 | 18:12 | 10.75 | IS6 | INV3 | M2 |  |  |  | 1 | 1 | IS6INV3M2 | 2380.32 | 0.7104% | Inverter | Inv_tripped in INS Fault | Inverter Unit tripped in INS fault | 7:26 | 7:26 | 7:26 | 8:07 | 0 | 0 | 0.68333 | 0.68333 | checked related connection and parameter then rboot the inverter and start | Close | 0.0048541 | 0.01 | 21.5423
974 | 2024-01-07 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:27 | 18:12 | 10.75 | IS10 | INV2 | M2 |  |  |  | 1 | 1 | IS10INV2M2 | 2223.72 | 0.6636% | Inverter | Inv_tripped in INS Fault | Inverter Unit tripped in INS fault | 7:26 | 7:26 | 7:26 | 8:17 | 0 | 0 | 0.85 | 0.85 | checked related connection and parameter then rboot the inverter and start | Close | 0.0056407 | 0.02 | 40.25
975 | 2024-01-09 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:41 | 18:14 | 10.55 | IS10 | INV1 | M2 |  |  |  | 1 | 1 | IS10INV1M2 | 2098.44 | 0.6262% | Inverter | Inv_tripped in INS Fault | Inverter Unit tripped in INS fault | 7:41 | 7:41 | 7:41 | 8:31 | 0 | 0 | 0.83333 | 0.83333 | checked related connection and parameter then rboot the inverter and start | Close | 0.0052186 | 0.02 | 37.9824
976 | 2024-01-09 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:41 | 18:14 | 10.55 | IS17 | INV4 | M1 |  |  |  | 1 | 1 | IS17INV4M1 | 2004.48 | 0.5982% | Inverter | Inv_tripped in INS Fault | Inverter Unit tripped in INS fault | 7:41 | 7:41 | 7:41 | 8:33 | 0 | 0 | 0.86667 | 0.86667 | checked related connection and parameter then rboot the inverter and start | Close | 0.0051843 | 0.02 | 36.2817
977 | 2024-01-11 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:26 | 18:16 | 10.8333 | IS17 | INV4 | M1 |  |  |  | 1 | 1 | IS17INV4M1 | 2004.48 | 0.5982% | Inverter | Inv Unit_AC Switch Disconnection | Inverter tripped in AC switch disconnection fault | 7:26 | 7:26 | 7:26 | 7:55 | 0 | 0 | 0.48333 | 0.48333 | checked related connection and parameter then rboot the inverter and start | Close | 0.0028913 | 0 | 0
978 | 2024-01-13 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:21 | 18:17 | 10.9333 | IS18 | INV1 | M2 |  |  |  | 1 | 1 | IS18INV1M2 | 1973.16 | 0.5888% | Inverter | Inv Unit_AC Switch Disconnection | Inverter tripped in AC switch disconnection fault | 7:21 | 7:21 | 7:21 | 9:19 | 0 | 0 | 1.9667 | 1.9667 | checked related connection and parameter then rboot the inverter and start | Close | 0.011581 | 0.37 | 660.7236
979 | 2024-01-13 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:21 | 18:17 | 10.9333 | IS17 | INV4 | M2 |  |  |  | 1 | 1 | IS17INV4M2 | 2004.48 | 0.5982% | Inverter | Inv Unit_AC Switch Disconnection | Inverter tripped in AC switch disconnection fault | 7:21 | 7:21 | 7:21 | 7:51 | 0 | 0 | 0.5 | 0.5 | checked related connection and parameter then rboot the inverter and start | Close | 0.0029909 | 0 | 0
980 | 2024-01-13 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:21 | 18:17 | 10.9333 | IS18 | INV1 | M1 |  |  |  | 1 | 1 | IS18INV1M1 | 2255.04 | 0.673% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 8:06 | 8:06 | 8:06 | 8:25 | 0 | 0 | 0.31667 | 0.31667 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0021311 | 0.05 | 102.0423
981 | 2024-01-13 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:21 | 18:17 | 10.9333 | IS18 | INV1 | M1 |  |  |  | 1 | 1 | IS18INV1M1 | 2255.04 | 0.673% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 8:44 | 8:44 | 8:44 | 9:03 | 0 | 0 | 0.31667 | 0.31667 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0021311 | 0.11 | 224.493
982 | 2024-01-13 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:21 | 18:17 | 10.9333 | IS18 | INV1 | M1 |  |  |  | 1 | 1 | IS18INV1M1 | 2255.04 | 0.673% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 9:12 | 9:12 | 9:12 | 9:19 | 0 | 0 | 0.11667 | 0.11667 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.00078512 | 0.05 | 102.0423
983 | 2024-01-16 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:20 | 18:20 | 11 | IS16 | INV4 | M2 | SCB4 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | SCB_String Y coonector burn | String Y connector burn | 7:20 | 7:20 | 7:20 | 18:20 | 0 | 0 | 11 | 11 | Y connector replaced | Close | 0.0010281 | 5.65 | 160.1496
984 | 2024-01-18 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:20 | 18:10 | 10.8333 | IS14 | INV4 | M1 |  |  |  | 1 | 1 | IS14INV4M1 | 2192.4 | 0.6543% | Inverter | Inv_tripped in INS Fault | Inverter Unit tripped in INS fault | 7:30 | 7:30 | 7:30 | 8:05 | 0 | 0 | 0.58333 | 0.58333 | checked related connection and parameter then rboot the inverter and start | Close | 0.0038166 | 0.017 | 33.7306
985 | 2024-01-18 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:20 | 18:10 | 10.8333 | IS8 | INV1 | M1 |  |  |  | 1 | 1 | IS8INV1M1 | 2004.48 | 0.5982% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 7:46 | 7:46 | 7:46 | 8:42 | 0 | 0 | 0.93333 | 0.93333 | checked related connection and parameter then the inverter and start | Close | 0.0055831 | 0.11 | 199.5493
986 | 2024-01-18 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:20 | 18:10 | 10.8333 | IS8 | INV1 | M1 |  |  |  | 1 | 1 | IS8INV1M1 | 2004.48 | 0.5982% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 8:56 | 8:56 | 8:56 | 9:46 | 0 | 0 | 0.83333 | 0.83333 | checked related connection and parameter scb floting check one by one then the inverter and start | Close | 0.0049849 | 0.33 | 598.6479
987 | 2024-01-18 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:20 | 18:10 | 10.8333 | IS8 | INV1 | M2 |  |  |  | 1 | 1 | IS8INV1M2 | 2255.04 | 0.673% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 7:46 | 7:46 | 7:46 | 8:26 | 0 | 0 | 0.66667 | 0.66667 | checked related connection and parameter scb floting check one by one then the inverter and start | Close | 0.0044864 | 0.057 | 116.3282
988 | 2024-01-18 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:20 | 18:10 | 10.8333 | IS8 | INV1 | M2 |  |  |  | 1 | 1 | IS8INV1M2 | 2255.04 | 0.673% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 8:56 | 8:56 | 8:56 | 9:20 | 0 | 0 | 0.4 | 0.4 | checked related connection and parameter then the inverter and start | Close | 0.0026919 | 0.14 | 285.7183
989 | 2024-01-18 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:20 | 18:10 | 10.8333 | IS12 | INV1 | M1 |  |  |  | 1 | 1 | IS12INV1M1 | 2192.4 | 0.6543% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 7:30 | 7:30 | 7:30 | 7:53 | 0 | 0 | 0.38333 | 0.38333 | checked related connection and parameter then the inverter and start | Close | 0.002508 | 0 | 0
990 | 2024-01-18 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:20 | 18:10 | 10.8333 | IS12 | INV1 | M1 |  |  |  | 1 | 1 | IS12INV1M1 | 2192.4 | 0.6543% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 8:11 | 8:11 | 8:11 | 8:25 | 0 | 0 | 0.23333 | 0.23333 | checked related connection and parameter scb floting check one by one then the inverter and start | Close | 0.0015266 | 0.03 | 59.5246
991 | 2024-01-18 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:20 | 18:10 | 10.8333 | IS12 | INV1 | M2 |  |  |  | 1 | 1 | IS12INV1M2 | 2114.1 | 0.6309% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 7:59 | 7:59 | 7:59 | 8:15 | 0 | 0 | 0.26667 | 0.26667 | checked related connection and parameter then the inverter and start | Close | 0.0016824 | 0.02 | 38.2658
992 | 2024-01-18 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:20 | 18:10 | 10.8333 | IS12 | INV1 | M2 |  |  |  | 1 | 1 | IS12INV1M2 | 2114.1 | 0.6309% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 8:26 | 8:26 | 8:26 | 8:38 | 0 | 0 | 0.2 | 0.2 | checked related connection and parameter scb floting check one by one then the inverter and start | Close | 0.0012618 | 0.04 | 76.5317
993 | 2024-01-20 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:30 | 18:10 | 10.6667 | IS15 | INV4 | M1 |  |  |  | 1 | 1 | IS15INV4M1 | 2192.4 | 0.6543% | Inverter | Inv Unit_AC Switch Disconnection | Manualy stop for Inv Unit_AC Coil failure rectification | 7:30 | 7:30 | 7:30 | 8:08 | 0 | 0 | 0.63333 | 0.63333 | checked related connection and parameter then the inverter breaker reset and charge | Close | 0.0041437 | 0.031 | 61.5088
994 | 2024-01-20 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:30 | 18:10 | 10.6667 | IS15 | INV4 | M2 |  |  |  | 1 | 1 | IS15INV4M2 | 2004.48 | 0.5982% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 7:30 | 7:30 | 7:30 | 8:08 | 0 | 0 | 0.63333 | 0.63333 | checked related connection and parameter then the inverter breaker reset and charge | Close | 0.0037885 | 0.031 | 56.2366
995 | 2024-01-21 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:30 | 18:20 | 10.8333 | IS12 | INV1 | M2 |  |  |  | 1 | 1 | IS12INV1M2 | 2114.1 | 0.6309% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 7:43 | 7:43 | 7:43 | 8:05 | 0 | 0 | 0.36667 | 0.36667 | checked related connection and parameter scb floting check one by one then the inverter and start | Close | 0.0023133 | 0.01 | 19.1329
996 | 2024-01-21 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:30 | 18:20 | 10.8333 | IS12 | INV1 | M1 |  |  |  | 1 | 1 | IS12INV1M1 | 2192.4 | 0.6543% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 7:54 | 7:54 | 7:54 | 8:05 | 0 | 0 | 0.18333 | 0.18333 | checked related connection and parameter scb floting check one by one then the inverter and start | Close | 0.0011995 | 0.007 | 13.8891
997 | 2024-01-22 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:30 | 18:10 | 10.6667 | IS11 | INV4 | M1 |  |  |  | 1 | 1 | IS11INV4M1 | 2023.04 | 0.6037% | Inverter | Inv_tripped in INS Fault | Inverter Unit tripped in INS fault | 7:29 | 7:29 | 7:29 | 8:10 | 0 | 0 | 0.68333 | 0.68333 | checked related connection and parameter then rboot the inverter and start | Close | 0.0041255 | 0.03 | 54.9264
998 | 2024-01-22 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:30 | 18:10 | 10.6667 | IS12 | INV1 | M1 |  |  |  | 1 | 1 | IS12INV1M1 | 2192.4 | 0.6543% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 7:47 | 7:47 | 7:47 | 8:02 | 0 | 0 | 0.25 | 0.25 | checked related connection and parameter scb floting check one by one then the inverter and start | Close | 0.0016357 | 0.01 | 19.8415
999 | 2024-01-22 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:30 | 18:10 | 10.6667 | IS12 | INV1 | M2 |  |  |  | 1 | 1 | IS12INV1M2 | 2114.1 | 0.6309% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 7:36 | 7:36 | 7:36 | 9:01 | 0 | 0 | 1.4167 | 1.4167 | checked related connection and parameter scb floting check one by one then the inverter and start | Close | 0.0089378 | 0.211 | 403.7047
1000 | 2024-01-22 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:30 | 18:10 | 10.6667 | IS14 | INV3 | M2 |  |  |  | 1 | 1 | IS14INV3M2 | 2004.48 | 0.5982% | Inverter | Inv_tripped in INS Fault | Inverter Unit tripped in INS fault | 7:38 | 7:38 | 7:38 | 8:14 | 0 | 0 | 0.6 | 0.6 | checked related connection and parameter then rboot the inverter and start | Close | 0.0035891 | 0.03 | 54.4225
1001 | 2024-01-26 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:20 | 18:00 | 10.6667 | IS3 | INV4 | M1 |  |  |  | 1 | 1 | IS3INV4M1 | 2114.1 | 0.6309% | Inverter | Inv Unit_AC Switch Disconnection | Manualy stop for Inv Unit_AC Coil failure rectification | 7:20 | 7:20 | 7:20 | 7:43 | 0 | 0 | 0.38333 | 0.38333 | checked related connection and parameter then the inverter breaker reset and charge | Close | 0.0024185 | 0.003 | 5.7399
1002 | 2024-01-27 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:20 | 18:10 | 10.8333 | IS17 | INV4 | M1 |  |  |  | 1 | 1 | IS17INV4M1 | 2004.48 | 0.5982% | Inverter | Inv Unit_AC Switch Disconnection | Manualy stop for Inv Unit_AC Coil failure rectification | 8:01 | 8:01 | 8:01 | 8:21 | 0 | 0 | 0.33333 | 0.33333 | checked related connection and parameter then the inverter breaker reset and charge | Close | 0.001994 | 0.018 | 32.6535
1003 | 2024-01-27 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:20 | 18:10 | 10.8333 | IS17 | INV4 | M1 |  |  |  | 1 | 1 | IS17INV4M1 | 2004.48 | 0.5982% | Inverter | Inv Unit_AC Switch Disconnection | Manualy stop for Inv Unit_AC Coil failure rectification | 8:59 | 8:59 | 8:59 | 9:55 | 0 | 0 | 0.93333 | 0.93333 | checked related connection and parameter then the inverter breaker reset and charge | Close | 0.0055831 | 0.191 | 346.4901
1004 | 2024-01-27 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:20 | 18:10 | 10.8333 | IS17 | INV4 | M1 |  |  |  | 1 | 1 | IS17INV4M1 | 2004.48 | 0.5982% | Inverter | Inv Unit_AC Switch Disconnection | Manualy stop for Inv Unit_AC Coil failure rectification | 14:17 | 14:17 | 14:17 | 15:02 | 0 | 0 | 0.75 | 0.75 | Sungrow engineer check inverter for rectification work | Close | 0.0044864 | 0.4 | 725.6338
1005 | 2024-01-27 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:20 | 18:10 | 10.8333 | IS17 | INV4 | M2 |  |  |  | 1 | 1 | IS17INV4M2 | 2004.48 | 0.5982% | Inverter | Inv Unit_AC Switch Disconnection | Inverter tripped in AC switch disconnection fault | 7:20 | 7:20 | 7:20 | 18:10 | 0 | 0 | 10.8333 | 10.8333 | checked related connection and parameter then the inverter AC coil replace but inverter not start. | Close | 0.064804 | 3.69 | 6693.9716
1006 | 2024-01-29 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:30 | 18:10 | 10.6667 | IS16 | INV3 | M1 |  |  |  | 1 | 1 | IS16INV3M1 | 2129.76 | 0.6356% | Inverter | Inv Unit_AC Switch Disconnection | Inverter tripped in AC switch disconnection fault | 7:39 | 7:39 | 7:39 | 8:02 | 0 | 0 | 0.38333 | 0.38333 | checked related connection and parameter then the inverter breaker reset and charge | Close | 0.0024364 | 0.009 | 17.3472
1007 | 2024-01-29 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:30 | 18:10 | 10.6667 | IS16 | INV3 | M2 |  |  |  | 1 | 1 | IS16INV3M2 | 1879.2 | 0.5608% | Inverter | Inv Unit_AC Switch Disconnection | Manualy stop for Inv Unit_AC Coil failure rectification | 7:50 | 7:50 | 7:50 | 8:02 | 0 | 0 | 0.2 | 0.2 | checked related connection and parameter then the inverter breaker reset and charge | Close | 0.0011216 | 0.006 | 10.2042
1008 | 2024-01-30 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:30 | 18:00 | 10.5 | IS11 | INV4 | M1 |  |  |  | 1 | 1 | IS11INV4M1 | 2023.04 | 0.6037% | Inverter | Inv Unit_AC Switch Disconnection | Inverter tripped in AC switch disconnection fault | 7:30 | 7:30 | 7:30 | 8:03 | 0 | 0 | 0.55 | 0.55 | checked related connection and parameter then the inverter breaker reset and charge | Close | 0.0033205 | 0.012 | 21.9706
1009 | 2024-01-30 | FY24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 7:30 | 18:00 | 10.5 | IS11 | INV4 | M2 |  |  |  | 1 | 1 | IS11INV4M2 | 1785.965 | 0.533% | Inverter | Inv Unit_AC Switch Disconnection | Manualy stop for Inv Unit_AC Coil failure rectification | 7:58 | 7:58 | 7:58 | 8:03 | 0 | 0 | 0.083333 | 0.083333 | checked related connection and parameter then the inverter breaker reset and charge | Close | 0.00044415 | 0.003 | 4.849
1010 | 2024-02-05 | FY24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 7:30 | 18:29 | 10.9833 | IS16 | INV2 | M1 | SCB3 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | SCB_String Y coonector burn | Y-Connector burn | 7:30 | 7:30 | 7:30 | 18:29 | 0 | 0 | 10.9833 | 10.9833 | Y-Connector replaced and String Charged | Close | 0.0010266 | 5.82 | 149.0779
1011 | 2024-02-06 | FY24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 7:29 | 18:30 | 11.0167 | IS16 | INV2 | M1 | SCB3 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | String Fuses | SCB_String fuse fault | SCB Fuse burn and string breakdown | 7:29 | 7:29 | 7:29 | 18:30 | 0 | 0 | 11.0167 | 11.0167 | SCB fuse fault and replaced | Close | 0.0010297 | 5.49 | 140.6251
1012 | 2024-02-06 | FY24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 7:29 | 18:30 | 11.0167 | IS9 | INV3 | M2 | SCB5 | Str_Typ5(545*29) |  | 0 | 0 | Str_Typ5(545*29) | 15.805 | 0.004717% | Connectors | SCB_MC4 coonector burn | MC4 connector burn | 7:29 | 7:29 | 7:29 | 18:30 | 0 | 0 | 11.0167 | 11.0167 | MC4 connector replaced and string charged | Close | 0.00051962 | 5.49 | 70.9636
1013 | 2024-02-11 | FY24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 7:23 | 18:38 | 11.25 | IS4 | INV3 | M1 | SCB3 | Str_Typ2 (450*29) |  | 0 | 0 | Str_Typ2 (450*29) | 13.05 | 0.003894% | Connectors | SCB_MC4 coonector burn | MC4 connector burn | 7:23 | 7:23 | 7:23 | 18:38 | 0 | 0 | 11.25 | 11.25 | MC4 connector replaced and string charged | Close | 0.00043813 | 6.79 | 72.4684
1014 | 2024-02-15 | FY24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 7:20 | 18:40 | 11.3333 | IS5 | INV4 | M1 | SCB2 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | String Fuses | Sting_Manual shutdown for IV test | String Manual stop for IV test by O2 HO | 12:00 | 12:00 | 12:00 | 14:30 | 0 | 0 | 2.5 | 2.5 | After IV test sting charged | Close | 0.00019256 | 2.67 | 56.3596
1015 | 2024-02-16 | FY24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 7:22 | 18:38 | 11.2667 | IS5 | INV4 | M1 | SCB2 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | String Fuses | Sting_Manual shutdown for IV test | String Manual stop for IV test by O2 HO | 12:00 | 12:00 | 12:00 | 12:30 | 0 | 0 | 0.5 | 0.5 | After IV test sting charged | Close | 3.8512e-05 | 0.47 | 9.921
1016 | 2024-02-16 | FY24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 7:22 | 18:38 | 11.2667 | IS5 | INV4 | M1 | SCB2 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | String Fuses | Sting_Manual shutdown for IV test | String Manual stop for IV test by O2 HO | 12:30 | 12:30 | 12:30 | 13:00 | 0 | 0 | 0.5 | 0.5 | After IV test sting charged | Close | 3.8512e-05 | 0.47 | 9.921
1017 | 2024-02-18 | FY24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 7:10 | 18:44 | 11.5667 | [5 empty] | MCR_MVP_Inc1 | 0 | 1 | MCR_MVP_Inc1 | 35109.72 | 10.48% | MV Panel | I/C-01_Tripped under O/C Fault | Incomer-01 tripped under O/C Fault | 11:15 | 11:15 | 11:20 | 12:17 | 0 | 0.083333 | 1.0333 | 1.0333 | I/C Tripped time line voltage was 208KV and 33kv feeder side voltage was 32KV. Current setting was 0.92% and tripped when current goes to 0.93%. We raised the tap position and maintained a voltage level upto 33.5kv. Then I/C charged. | Close | 0.10827 | 0.97 | 27852.7274
1018 | 2024-02-18 | FY24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 7:10 | 18:44 | 11.5667 | [5 empty] | MCR_MVP_Inc12 | 0 | 1 | MCR_MVP_Inc12 | 33488.475 | 9.994% | MV Panel | I/C-12_Tripped under O/C Fault | Incomer-12 tripped under O/C Fault | 11:50 | 11:50 | 11:55 | 13:26 | 0 | 0.083333 | 1.6 | 1.6 | I/C Tripped time line voltage was 208KV and 33kv feeder side voltage was 32KV. Current setting was 0.92% and tripped when current goes to 0.93%. We raised the tap position and maintained a voltage level upto 33.5kv. Then I/C charged. | Close | 0.1599 | 1.51 | 41356.2305
1019 | 2024-02-18 | FY24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 7:10 | 18:44 | 11.5667 | IS5 | INV4 | M1 | SCB4 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Connectors | SCB_String MC4 coonector burn | MC4 Connector burn | 7:10 | 7:10 | 7:10 | 18:44 | 0 | 0 | 11.5667 | 11.5667 | MC4 connector replaced and string charged | Close | 0.00044545 | 6.31 | 66.5972
1020 | 2024-02-19 | FY24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 7:26 | 18:42 | 11.2667 | [5 empty] | MCR_MVP_Inc1 | 0 | 1 | MCR_MVP_Inc1 | 35109.72 | 10.48% | MV Panel | I/C-01_Tripped under O/C Fault | Incomer-01 tripped under O/C Fault | 11:30 | 11:30 | 11:30 | 12:09 | 0 | 0 | 0.65 | 0.65 | I/C Tripped time line voltage was 208KV and 33kv feeder side voltage was 32KV. Current setting was 0.92% and tripped when current goes to 0.93%. We changed the current setting to 1.0% and maintained a voltage level upto 33.5kv. Then I/C charged. | Close | 0.068105 | 0.59 | 16941.3497
1021 | 2024-02-19 | FY24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 7:26 | 18:42 | 11.2667 | IS10 | INV1 | M2 | SCB4 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | SCB_String MC4 coonector burn | Under SCB MC4 connector broken and disconnected | 7:26 | 7:26 | 7:26 | 16:30 | 0 | 0 | 9.0667 | 9.0667 | We replace a new MC4 connector with lead cable and charged the string | Close | 0.00084744 | 5.72 | 146.5165
1022 | 2024-02-22 | FY24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 7:24 | 18:45 | 11.35 | IS1 | INV3 | M1 |  |  |  | 1 | 1 | IS1INV3M1 | 2090.61 | 0.6239% | Inverter | Inv Unit_AC Switch Disconnection | Inverter tripped in AC switch disconnection fault | 7:24 | 7:24 | 7:24 | 7:51 | 0 | 0 | 0.45 | 0.45 | As discussed with OEM breaker manually discharged and PU reset. Then Inv charged | Close | 0.0028075 | 0.01 | 17.0979
1023 | 2024-02-22 | FY24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 7:24 | 18:45 | 11.35 | IS17 | INV3 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | SCB_MC4 coonector burn | MC4 connector burn | 7:24 | 7:24 | 7:24 | 18:45 | 0 | 0 | 11.35 | 11.35 | MC4 connector replaced and string charged | Close | 0.0010609 | 6.34 | 162.3976
1024 | 2024-02-22 | FY24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 7:24 | 18:45 | 11.35 | IS16 | INV3 | M1 |  |  |  | 1 | 1 | IS16INV3M1 | 2129.76 | 0.6356% | Inverter | Inv Unit_AC Switch Disconnection | Inverter tripped in AC switch disconnection fault | 7:15 | 7:15 | 7:15 | 7:52 | 0 | 0 | 0.61667 | 0.61667 | As discussed with OEM breaker manually discharged and PU reset. Then Inv charged | Close | 0.0039194 | 0.03 | 52.2541
1025 | 2024-02-24 | FY24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 7:13 | 18:46 | 11.55 | IS16 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | SCB_String MC4 coonector burn | SCB MC4 connector broken and disconnected | 7:13 | 18:46 | 18:46 | 18:46 | 11.55 | 11.55 |  | 11.55 | String breakdown | Open | 0.0010795 | 7.09 | 181.6087
1026 | 2024-02-25 | FY24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 7:14 | 18:40 | 11.4333 | IS16 | INV4 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | SCB_String MC4 coonector burn | MC4 connector broken and disconnected | 7:14 | 7:14 | 7:14 | 11:30 | 0 | 0 | 4.2667 | 4.2667 | We replace a new MC4 connector with lead cable and charged the string | Close | 0.00039879 | 2.02 | 51.7418
1027 | 2024-02-25 | FY24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 7:14 | 18:40 | 11.4333 | IS5 | INV4 | M1 | SCB4 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Connectors | SCB_String MC4 coonector burn | MC4 connector burn | 7:14 |  |  | 18:40 | -7.2333 | -7.2333 |  | 11.4333 | String breakdown | Open | 0.00044032 | 4.71 | 49.7104
1028 | 2024-02-26 | FY24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 7:22 | 18:44 | 11.3667 | IS5 | INV4 | M1 | SCB4 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Connectors | SCB_String MC4 coonector burn | MC4 connector burn | 7:22 | 7:22 | 7:22 | 10:00 | 0 | 0 | 2.6333 | 2.6333 | MC4 connector replaced and string charged | Close | 0.00010141 | 0.02 | 0.21108
1029 | 2024-02-28 | FY24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 7:13 | 18:48 | 11.5833 | IS15 | INV1 | M1 | SCB2 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | SCB_String MC4 coonector burn | MC4 connector burn | 7:13 | 7:13 | 7:13 | 18:48 | 0 | 0 | 11.5833 | 11.5833 | MC4 connector replaced and string charged | Close | 0.0010827 | 6.72 | 172.1312
1030 | 2024-03-03 | FY24 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 7:05 | 18:51 | 11.7667 | IS16 | INV2 | M2 | SCB1 |  |  | 1 | 1 | IS16INV2M2SCB1 | 250.56 | 0.07477% | Cables | SCB_String Cable Theft | String cable theft | 7:05 | 7:05 | 7:05 | 11:00 | 0 | 0 | 3.9167 | 3.9167 | String Cable restoration completed and SCB Charged | Close | 0.0029286 | 1.82 | 381.6851
1031 | 2024-03-03 | FY24 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 7:05 | 18:51 | 11.7667 | IS16 | INV2 | M2 | SCB2 |  |  | 1 | 1 | IS16INV2M2SCB2 | 250.56 | 0.07477% | Cables | SCB_String Cable Theft | String cable theft | 7:05 | 7:05 | 7:05 | 13:00 | 0 | 0 | 5.9167 | 5.9167 | String Cable restoration completed and SCB Charged | Close | 0.0044241 | 3.84 | 805.3137
1032 | 2024-03-03 | FY24 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 7:05 | 18:51 | 11.7667 | IS16 | INV1 | M2 | SCB9 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Cables | SCB_String Cable Theft | String cable theft | 7:05 | 7:05 | 7:05 | 11:00 | 0 | 0 | 3.9167 | 3.9167 | String Cable restoration completed and SCB Charged | Close | 0.00036608 | 1.82 | 47.7106
1033 | 2024-03-03 | FY24 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 7:05 | 18:51 | 11.7667 | IS16 | INV1 | M2 | SCB9 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Cables | SCB_String Cable Theft | String cable theft | 7:05 | 7:05 | 7:05 | 11:00 | 0 | 0 | 3.9167 | 3.9167 | String Cable restoration completed and SCB Charged | Close | 0.00036608 | 1.82 | 47.7106
1034 | 2024-03-07 | FY24 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 7:04 | 18:52 | 11.8 | IS14 | INV2 | M1 | SCB2 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | SCB_String MC4 coonector burn | MC4 connector burn | 7:04 | 7:04 | 7:04 | 15:00 | 0 | 0 | 7.9333 | 7.9333 | MC4 connector replaced and string charged | Close | 0.00074151 | 5.45 | 142.8698
1035 | 2024-03-12 | FY24 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 7:00 | 18:53 | 11.8833 | IS18 | INV2 | M2 | SCB8 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | Y connector burn | MC4 connector burn | 7:00 | 7:00 | 7:00 | 13:00 | 0 | 0 | 6 | 6 | Y connector replaced and string charge | Close | 0.0005608 | 3.65 | 95.6834
1036 | 2024-03-12 | FY24 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 7:00 | 18:53 | 11.8833 | IS6 | INV1 | M2 | SCB3 | Str_Typ8(535*58) |  | 0 | 0 | Str_Typ8(535*58) | 31.03 | 0.00926% | Connectors | SCB_String MC4 coonector burn | MC4 connector burn | 7:00 | 7:00 | 7:00 | 13:20 | 0 | 0 | 6.3333 | 6.3333 | MC4 connector replaced and string charged | Close | 0.00058648 | 3.98 | 103.3682
1037 | 2024-03-13 | FY24 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 7:00 | 18:54 | 11.9 | IS4 | INV1 | M1 | SCB8 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Mc4 connector | MC4 connector burn | 7:00 | 7:00 | 7:00 | 10:25 | 0 | 0 | 3.4167 | 3.4167 | Mc4 connector connect properly | Close | 0.00026316 | 1.23 | 26.5714
1038 | 2024-03-14 | FY24 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 6:59 | 18:56 | 11.95 | IS6 |  |  |  |  | Tx | 0 | 1 | IS6Tx | 17170.9 | 5.124% | IDT | IDT_Tripped of Differential Protection | IDT Tripped in differential protection after CT replacement | 8:29 | 8:29 | 8:29 | 9:54 | 0 | 0 | 1.4167 | 1.4167 | CT connection interchanged and IDT charged after reset of differential protection | Close | 0.072594 | 0.7 | 10060.3527
1039 | 2024-03-15 | FY24 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 6:58 | 18:51 | 11.8833 | IS6 | INV4 | M2 | SCB3 | Str_Typ3(535*29) |  | 0 | 0 | Str_Typ3(535*29) | 15.515 | 0.00463% | Connectors | SCB_String MC4 coonector open | MC4 Connector found open | 6:58 | 6:58 | 6:58 | 13:00 | 0 | 0 | 6.0333 | 6.0333 | MC4 Connecoter closed and string charged | Close | 0.00027935 | 3.6 | 46.7494
1040 | 2024-03-15 | FY24 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 6:58 | 18:51 | 11.8833 | IS6 | INV4 | M2 | SCB4 | Str_Typ3(535*29) |  | 0 | 0 | Str_Typ3(535*29) | 15.515 | 0.00463% | Connectors | SCB_String MC4 coonector open | MC4 Connector found open | 6:58 | 6:58 | 6:58 | 13:00 | 0 | 0 | 6.0333 | 6.0333 | MC4 Connecoter closed and string charged | Close | 0.00027935 | 3.6 | 46.7494
1041 | 2024-03-18 | FY24 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 6:53 | 18:57 | 12.0667 | IS15 | INV1 | M2 | SCB2 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | SCB_String MC4 coonector burn | MC4 connector burn | 6:53 | 6:53 | 6:53 | 18:57 | 0 | 0 | 12.0667 | 12.0667 | MC4 connector replaced and string charged | Close | 0.0011278 | 7.4 | 193.9883
1042 | 2024-03-19 | FY24 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 6:56 | 18:56 | 12 | IS7 | INV1 | M1 |  |  |  | 1 | 1 | IS7INV1M1 | 1973.16 | 0.5888% | Inverter | Inv_unit tripped under Module Temp High | Inverter unit tripped under Module temp High fault | 13:00 | 13:00 | 13:00 | 13:59 | 0 | 0 | 0.98333 | 0.98333 | Discussed with OEM and checked all parameter. Reset the unit and inverter charged. At evening filter cleaning completed. | Close | 0.0057903 | 1 | 1651.5222
1043 | 2024-03-19 | FY24 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 6:56 | 18:56 | 12 | IS7 | INV1 | M2 |  |  |  | 1 | 1 | IS7INV1M2 | 1973.16 | 0.5888% | Inverter | Inv_manual trip for reset of Inverter | Unit Manual stop for rectification or unit-1 fault | 13:56 | 13:56 | 13:56 | 13:59 | 0 | 0 | 0.05 | 0.05 | Reset the Unit-1 and inverter charged | Close | 0.00029442 | 1 | 1651.5222
1044 | 2024-03-21 | FY24 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 6:59 | 18:58 | 11.9833 | IS7 | INV1 | M1 |  |  |  | 1 | 1 | IS7INV1M1 | 1973.16 | 0.5888% | Inverter | Inv_unit tripped under Module Temp High | Inverter unit tripped under Module temp High fault | 12:16 | 12:16 | 12:16 | 13:03 | 0 | 0 | 0.78333 | 0.78333 | Discussed with OEM and checked all parameter. Reset the unit and inverter charged. At evening OEM visited the site and changed 2 stacks of IGBT and cleaned the filter | Close | 0.0046126 | 0.8 | 1321.2177
1045 | 2024-03-21 | FY24 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 6:59 | 18:58 | 11.9833 | IS7 | INV1 | M1 |  |  |  | 1 | 1 | IS7INV1M1 | 1973.16 | 0.5888% | Inverter | Inv_unit tripped under Module Temp High | Inverter unit tripped under Module temp High fault | 13:49 | 13:49 | 13:49 | 14:25 | 0 | 0 | 0.6 | 0.6 | Discussed with OEM and checked all parameter. Reset the unit and inverter charged. At evening OEM visited the site and changed 2 stacks of IGBT and cleaned the filter | Close | 0.0035331 | 0.57 | 941.3676
1046 | 2024-04-10 | FY24 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 6:56 | 19:04 | 12.1333 | IS17 | INV4 | M1 | SCB10 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | SCB_String MC4 coonector burn | MC4 connector burn | 6:56 | 6:56 | 6:56 | 14:12 | 0 | 0 | 7.2667 | 7.2667 | MC4 connector replaced and string charged | Close | 0.00067919 | 4.33 | 110.7365
1047 | 2024-04-13 | FY24 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 6:30 | 19:01 | 12.5167 | [5 empty] | Power_Tx2 | 0 | 1 | Power_Tx2 | 167768.915 | 50.07% | PTR | Power transformer 02 triped in Earth fault | Power transformer 02 triped in Earth fault | 15:03 | 15:03 | 15:03 | 16:09 | 0 | 0 | 1.1 | 1.1 | Y phase End termination replaced | Close | 0.55073 | 0.76 | 104113.2637 | PTW227982
1048 | 2024-04-13 | FY24 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 6:30 | 19:01 | 12.5167 | IS13 |  |  |  |  | Tx | 0 | 1 | IS13Tx | 16599.6 | 4.954% | IDT | Power transformer 02 triped in Earth fault | Power transformer 02 triped in Earth fault | 16:09 | 16:09 | 16:09 | 18:03 | 0 | 0 | 1.9 | 1.9 | shift Bus copler and IDT charge one by One | Close | 0.094121 | 0.488 | 6614.5213 | PTW227982
1049 | 2024-04-13 | FY24 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 6:30 | 19:01 | 12.5167 | [5 empty] | MCR_MVP_Inc1 | 0 | 1 | MCR_MVP_Inc1 | 35109.72 | 10.48% | MV Panel | Power transformer 02 triped in Earth fault | Power transformer 02 triped in Earth fault | 16:09 | 16:09 | 16:09 | 17:38 | 0 | 0 | 1.4833 | 1.4833 | Shift to bus copler | Close | 0.15542 | 0.459 | 13158.9436 | PTW227982
1050 | 2024-04-13 | FY24 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 6:30 | 19:01 | 12.5167 | [5 empty] | MCR_MVP_Inc2 | 0 | 1 | MCR_MVP_Inc2 | 32118.66 | 9.585% | MV Panel | Power transformer 02 triped in Earth fault | Power transformer 02 triped in Earth fault | 16:09 | 16:09 | 16:09 | 17:55 | 0 | 0 | 1.7667 | 1.7667 | Shift to bus copler | Close | 0.16934 | 0.48 | 12588.6636 | PTW227982
1051 | 2024-04-13 | FY24 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 6:30 | 19:01 | 12.5167 | IS14 |  |  |  |  | Tx | 0 | 1 | IS14Tx | 16756.2 | 5% | IDT | Power transformer 02 triped in Earth fault | Power transformer 02 triped in Earth fault | 16:09 | 16:09 | 16:09 | 19:01 | 0 | 0 | 2.8667 | 2.8667 | shift Bus copler and IDT charge one by One | Close | 0.14335 | 0.499 | 6827.4268
1052 | 2024-04-13 | FY24 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 6:30 | 19:01 | 12.5167 | IS15 |  |  |  |  | Tx | 0 | 1 | IS15Tx | 16756.2 | 5% | IDT | Power transformer 02 triped in Earth fault | Power transformer 02 triped in Earth fault | 16:09 | 16:09 | 16:09 | 16:44 | 0 | 0 | 0.58333 | 0.58333 | shift Bus copler and IDT charge one by One | Close | 0.02917 | 0.22 | 3010.088
1053 | 2024-04-13 | FY24 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 6:30 | 19:01 | 12.5167 | IS16 |  |  |  |  | Tx | 0 | 1 | IS16Tx | 16474.32 | 4.916% | IDT | Power transformer 02 triped in Earth fault | Power transformer 02 triped in Earth fault | 16:09 | 16:09 | 16:09 | 19:01 | 0 | 0 | 2.8667 | 2.8667 | shift Bus copler and IDT charge one by One | Close | 0.14094 | 0.499 | 6712.5729
1054 | 2024-04-13 | FY24 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 6:30 | 19:01 | 12.5167 | IS13 | INV4 | M1 |  |  |  | 1 | 1 | IS13INV4M1 | 2192.4 | 0.6543% | Inverter | Inverter Stand by mode | Inverter Stand by mode | 18:03 | 18:03 | 18:03 | 19:01 | 0 | 0 | 0.96667 | 0.96667 | Low radition so inverter not start | Close | 0.0063246 | 0.012 | 21.4824
1055 | 2024-04-13 | FY24 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 6:30 | 19:01 | 12.5167 | IS13 | INV4 | M2 |  |  |  | 1 | 1 | IS13INV4M2 | 2004.48 | 0.5982% | Inverter | Inverter Stand by mode | Inverter Stand by mode | 18:03 | 18:03 | 18:03 | 19:01 | 0 | 0 | 0.96667 | 0.96667 | Low radition so inverter not start | Close | 0.0057825 | 0.012 | 19.641
1056 | 2024-04-14 | FY24 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 6:36 | 18:59 | 12.3833 | IS10 | INV4 | M1 | SCB8 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Cables | String cable faulty found | String cable faulty found | 6:36 | 6:36 | 6:36 | 16:00 | 0 | 0 | 9.4 | 9.4 | String cable replaced and new cable lying done | Close | 0.00087859 | 5.09 | 130.1729
1057 | 2024-04-14 | FY24 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 6:36 | 18:59 | 12.3833 | IS12 | INV1 | M1 |  |  |  | 1 | 1 | IS12INV1M1 | 2192.4 | 0.6543% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 6:36 | 6:36 | 6:36 | 7:45 | 0 | 0 | 1.15 | 1.15 | checked related connection and parameter scb floting check one by one then the inverter and start | Close | 0.0075241 | 0.097 | 173.6491
1058 | 2024-04-15 | FY24 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 6:32 | 19:01 | 12.4833 | IS11 | INV1 | M1 | SCB4 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Connectors | SCB_String MC4 coonector burn | MC4 connector burn | 6:32 | 6:32 | 6:32 | 11:30 | 0 | 0 | 4.9667 | 4.9667 | New mc4 connector replaced | Close | 0.00046852 | 1.6 | 41.2977
1059 | 2024-04-15 | FY24 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 6:32 | 19:01 | 12.4833 | IS13 | INV2 | M1 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | Mc4 connector open found | Mc4 connector open found | 6:32 | 6:32 | 6:32 | 10:45 | 0 | 0 | 4.2167 | 4.2167 | Mc4 connector connect properly | Close | 0.00039412 | 1.223 | 31.2773
1060 | 2024-04-18 | FY24 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 6:29 | 19:03 | 12.5667 | IS12 | INV1 | M2 |  |  |  | 1 | 1 | IS12INV1M2 | 2114.1 | 0.6309% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 15:50 | 15:50 | 15:50 | 16:38 | 0 | 0 | 0.8 | 0.8 | checked related connection and parameter scb floting check one by one then the inverter and start | Close | 0.0050472 | 0.19 | 327.9896
1061 | 2024-04-18 | FY24 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 6:29 | 19:03 | 12.5667 | IS15 | INV2 | M1 |  |  |  | 1 | 1 | IS15INV2M1 | 2004.48 | 0.5982% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 15:47 | 15:47 | 15:47 | 16:08 | 0 | 0 | 0.35 | 0.35 | checked related connection and parameter scb floting check one by one then the inverter and start | Close | 0.0020937 | 0.02 | 32.735
1062 | 2024-04-18 | FY24 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 6:29 | 19:03 | 12.5667 | IS15 | INV2 | M2 |  |  |  | 1 | 1 | IS15INV2M2 | 1941.84 | 0.5795% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 15:47 | 15:47 | 15:47 | 15:57 | 0 | 0 | 0.16667 | 0.16667 | checked related connection and parameter scb floting check one by one then the inverter and start | Close | 0.00096583 | 0.007 | 11.0992
1063 | 2024-04-18 | FY24 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 6:29 | 19:03 | 12.5667 | IS15 | INV3 | M1 |  |  |  | 1 | 1 | IS15INV3M1 | 2223.72 | 0.6636% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 15:47 | 15:47 | 15:47 | 16:02 | 0 | 0 | 0.25 | 0.25 | checked related connection and parameter scb floting check one by one then the inverter and start | Close | 0.001659 | 0.02 | 36.3154
1064 | 2024-04-18 | FY24 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 6:29 | 19:03 | 12.5667 | IS15 | INV3 | M2 |  |  |  | 1 | 1 | IS15INV3M2 | 2192.4 | 0.6543% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 15:47 | 15:47 | 15:47 | 16:11 | 0 | 0 | 0.4 | 0.4 | checked related connection and parameter scb floting check one by one then the inverter and start | Close | 0.0026171 | 0.03 | 53.7059
1065 | 2024-04-22 | FY24 | 2024 | Year_3 | Year_3 | 2024-04-01 | 30 | 6:23 | 19:13 | 12.8333 | IS12 | INV1 | M1 | SCB10 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | SCB_String MC4 coonector burn | MC4 connector burn | 6:23 | 6:23 | 6:23 | 15:45 | 0 | 0 | 9.3667 | 9.3667 | New mc4 connector replaced | Close | 0.00087548 | 0.08 | 2.0459
1066 | 2024-05-07 | FY24 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 6:23 | 19:18 | 12.9167 | IS19 | INV3 | M1 |  |  |  | 1 | 1 | IS19INV3M1 | 2223.72 | 0.6636% | Inverter | Inv_unit tripped under Module Temp High | Inverter tripped under module temp fault | 13:40 | 13:40 | 13:40 | 16:50 | 0 | 0 | 3.1667 | 3.1667 | Opened the Indoor section and cleaned IGBT section, cleaned all filter and after temp decreased charged the inverter | Close | 0.021015 | 2.38 | 4379.7002
1067 | 2024-05-08 | FY24 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 6:18 | 19:20 | 13.0333 | IS19 | INV3 | M1 |  |  |  | 1 | 1 | IS19INV3M1 | 2223.72 | 0.6636% | Inverter | Inv_unit tripped under Module Temp High | Inverter tripped under module temp fault | 10:37 | 10:37 | 10:37 | 10:40 | 0 | 0 | 0.05 | 0.05 | Inverter reseted automatically | Close | 0.00033181 | 0.05 | 92.0105 | PTW231445
1068 | 2024-05-08 | FY24 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 6:18 | 19:20 | 13.0333 | IS19 | INV3 | M1 |  |  |  | 1 | 1 | IS19INV3M1 | 2223.72 | 0.6636% | Inverter | Inv_unit tripped under Module Temp High | Inverter tripped under module temp fault | 10:53 | 10:53 | 10:53 | 10:56 | 0 | 0 | 0.05 | 0.05 | Inverter reseted automatically | Close | 0.00033181 | 0.05 | 92.0105 | PTW231445
1069 | 2024-05-08 | FY24 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 6:18 | 19:20 | 13.0333 | IS19 | INV3 | M1 |  |  |  | 1 | 1 | IS19INV3M1 | 2223.72 | 0.6636% | Inverter | Inv_unit tripped under Module Temp High | Inverter tripped under module temp fault | 11:09 | 11:09 | 11:09 | 11:12 | 0 | 0 | 0.05 | 0.05 | Inverter reseted automatically | Close | 0.00033181 | 0.05 | 92.0105 | PTW231445
1070 | 2024-05-08 | FY24 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 6:18 | 19:20 | 13.0333 | IS19 | INV3 | M1 |  |  |  | 1 | 1 | IS19INV3M1 | 2223.72 | 0.6636% | Inverter | Inv_unit tripped under Module Temp High | Inverter tripped under module temp fault | 11:24 | 11:24 | 11:24 | 11:27 | 0 | 0 | 0.05 | 0.05 | Inverter reseted automatically | Close | 0.00033181 | 0.06 | 110.4126 | PTW231445
1071 | 2024-05-08 | FY24 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 6:18 | 19:20 | 13.0333 | IS19 | INV3 | M1 |  |  |  | 1 | 1 | IS19INV3M1 | 2223.72 | 0.6636% | Inverter | Inv_unit tripped under Module Temp High | Inverter tripped under module temp fault | 11:42 | 11:42 | 11:42 | 11:47 | 0 | 0 | 0.083333 | 0.083333 | Inverter reseted automatically | Close | 0.00055301 | 0.09 | 165.6189 | PTW231445
1072 | 2024-05-08 | FY24 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 6:18 | 19:20 | 13.0333 | IS19 | INV3 | M1 |  |  |  | 1 | 1 | IS19INV3M1 | 2223.72 | 0.6636% | Inverter | Inv_unit tripped under Module Temp High | Inverter tripped under module temp fault | 11:58 | 11:58 | 11:58 | 12:05 | 0 | 0 | 0.11667 | 0.11667 | Inverter Reset and Run | Close | 0.00077422 | 0.13 | 239.2273 | PTW231445
1073 | 2024-05-08 | FY24 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 6:18 | 19:20 | 13.0333 | IS19 | INV3 | M1 |  |  |  | 1 | 1 | IS19INV3M1 | 2223.72 | 0.6636% | Inverter | Inv_unit tripped under Module Temp High | Inverter tripped under module temp fault | 12:19 | 12:19 | 12:19 | 12:22 | 0 | 0 | 0.05 | 0.05 | Inverter reseted automatically | Close | 0.00033181 | 0.06 | 110.4126 | PTW231445
1074 | 2024-05-08 | FY24 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 6:18 | 19:20 | 13.0333 | IS19 | INV3 | M1 |  |  |  | 1 | 1 | IS19INV3M1 | 2223.72 | 0.6636% | Inverter | Inv_unit tripped under Module Temp High | Inverter tripped under module temp fault | 12:34 | 12:34 | 12:34 | 12:37 | 0 | 0 | 0.05 | 0.05 | Inverter reseted automatically | Close | 0.00033181 | 0.06 | 110.4126 | PTW231445
1075 | 2024-05-08 | FY24 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 6:18 | 19:20 | 13.0333 | IS19 | INV3 | M1 |  |  |  | 1 | 1 | IS19INV3M1 | 2223.72 | 0.6636% | Inverter | Inv_unit tripped under Module Temp High | Inverter tripped under module temp fault | 12:50 | 12:50 | 12:50 | 12:53 | 0 | 0 | 0.05 | 0.05 | Inverter reseted automatically | Close | 0.00033181 | 0.06 | 110.4126 | PTW231445
1076 | 2024-05-08 | FY24 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 6:18 | 19:20 | 13.0333 | IS19 | INV3 | M1 |  |  |  | 1 | 1 | IS19INV3M1 | 2223.72 | 0.6636% | Inverter | Inv_unit tripped under Module Temp High | Inverter tripped under module temp fault | 13:04 | 13:04 | 13:04 | 13:07 | 0 | 0 | 0.05 | 0.05 | Inverter reseted automatically | Close | 0.00033181 | 0.06 | 110.4126 | PTW231445
1077 | 2024-05-08 | FY24 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 6:18 | 19:20 | 13.0333 | IS19 | INV3 | M1 |  |  |  | 1 | 1 | IS19INV3M1 | 2223.72 | 0.6636% | Inverter | Inv_unit tripped under Module Temp High | Inverter tripped under module temp fault | 13:17 | 13:17 | 13:17 | 13:24 | 0 | 0 | 0.11667 | 0.11667 | Inverter Reset and Run | Close | 0.00077422 | 0.13 | 239.2273 | PTW231445
1078 | 2024-05-08 | FY24 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 6:18 | 19:20 | 13.0333 | IS19 | INV3 | M1 |  |  |  | 1 | 1 | IS19INV3M1 | 2223.72 | 0.6636% | Inverter | Inv_unit tripped under Module Temp High | Inverter tripped under module temp fault | 13:39 | 13:39 | 13:39 | 13:42 | 0 | 0 | 0.05 | 0.05 | Inverter reseted automatically | Close | 0.00033181 | 0.06 | 110.4126 | PTW231445
1079 | 2024-05-08 | FY24 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 6:18 | 19:20 | 13.0333 | IS19 | INV3 | M1 |  |  |  | 1 | 1 | IS19INV3M1 | 2223.72 | 0.6636% | Inverter | Inv_unit tripped under Module Temp High | Inverter tripped under module temp fault | 13:57 | 13:57 | 13:57 | 14:01 | 0 | 0 | 0.066667 | 0.066667 | Inverter reseted automatically | Close | 0.00044241 | 0.07 | 128.8147 | PTW231445
1080 | 2024-05-08 | FY24 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 6:18 | 19:20 | 13.0333 | IS19 | INV3 | M1 |  |  |  | 1 | 1 | IS19INV3M1 | 2223.72 | 0.6636% | Inverter | Inv_unit tripped under Module Temp High | Inverter tripped under module temp fault | 14:25 | 14:25 | 14:25 | 14:28 | 0 | 0 | 0.05 | 0.05 | Inverter reseted automatically | Close | 0.00033181 | 0.05 | 92.0105 | PTW231445
1081 | 2024-05-08 | FY24 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 6:18 | 19:20 | 13.0333 | IS19 | INV3 | M1 |  |  |  | 1 | 1 | IS19INV3M1 | 2223.72 | 0.6636% | Inverter | Inv_unit tripped under Module Temp High | Inverter tripped under module temp fault | 14:41 | 14:41 | 14:41 | 14:45 | 0 | 0 | 0.066667 | 0.066667 | Inverter reseted automatically | Close | 0.00044241 | 0.07 | 128.8147 | PTW231445
1082 | 2024-05-08 | FY24 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 6:18 | 19:20 | 13.0333 | IS19 | INV3 | M2 |  |  |  | 1 | 1 | IS19INV3M2 | 2255.04 | 0.673% | Inverter | Inv_unit tripped under Module Temp High | Inverter tripped under module temp fault | 11:44 | 11:44 | 11:44 | 11:47 | 0 | 0 | 0.05 | 0.05 | Inverter Reset and Run | Close | 0.00033648 | 0.05 | 93.3064 | PTW231445
1083 | 2024-05-08 | FY24 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 6:18 | 19:20 | 13.0333 | IS19 | INV3 | M2 |  |  |  | 1 | 1 | IS19INV3M2 | 2255.04 | 0.673% | Inverter | Inv_unit tripped under Module Temp High | Inverter tripped under module temp fault | 11:59 | 11:59 | 11:59 | 12:05 | 0 | 0 | 0.1 | 0.1 | Inverter Reset and Run | Close | 0.00067296 | 0.11 | 205.2741 | PTW231445
1084 | 2024-05-08 | FY24 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 6:18 | 19:20 | 13.0333 | IS19 | INV3 | M2 |  |  |  | 1 | 1 | IS19INV3M2 | 2255.04 | 0.673% | Inverter | Inv_unit tripped under Module Temp High | Inverter tripped under module temp fault | 13:21 | 13:21 | 13:21 | 13:24 | 0 | 0 | 0.05 | 0.05 | Inverter Reset and Run | Close | 0.00033648 | 0.05 | 93.3064 | PTW231445
1085 | 2024-05-12 | FY24 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 6:12 | 19:23 | 13.1833 | IS17 | INV3 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | Y-Connector found burn. | Y-Connector found burn. | 6:12 | 6:12 | 19:23 | 19:23 | 0 | 13.1833 | 13.1833 | 13.1833 | Y-Connector Fuse Replaced. | Close | 0.0012322 | 7.39 | 191.5374
1086 | 2024-05-12 | FY24 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 6:12 | 19:23 | 13.1833 | IS11 | INV3 | M1 | SCB4 | Str_Typ5(545*29) |  | 0 | 0 | Str_Typ5(545*29) | 15.805 | 0.004717% | Connectors | MC4 connector found burn. | MC4 connector found burn. | 6:12 | 6:12 | 19:23 | 19:23 | 0 | 13.1833 | 13.1833 | 13.1833 | MC4 connector replaced and string charged | Close | 0.00062181 | 7.23 | 94.5628
1087 | 2024-05-12 | FY24 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 6:12 | 19:23 | 13.1833 | IS11 | INV3 | M1 | SCB5 | Str_Typ5(545*29) |  | 0 | 0 | Str_Typ5(545*29) | 15.805 | 0.004717% | Connectors | MC4 connector found burn. | MC4 connector found burn. | 6:12 | 6:12 | 19:23 | 19:23 | 0 | 13.1833 | 13.1833 | 13.1833 | MC4 connector replaced and string charged | Close | 0.00062181 | 7.23 | 94.5628
1088 | 2024-05-12 | FY24 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 6:12 | 19:23 | 13.1833 | IS11 | INV3 | M2 | SCB3 | Str_Typ5(545*29) |  | 0 | 0 | Str_Typ5(545*29) | 15.805 | 0.004717% | Connectors | MC4 connector found burn. | MC4 connector found burn. | 6:12 | 6:12 | 19:23 | 19:23 | 0 | 13.1833 | 13.1833 | 13.1833 | MC4 connector replaced and string charged | Close | 0.00062181 | 7.23 | 94.5628
1089 | 2024-05-14 | FY24 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 6:11 | 19:23 | 13.2 | IS12 | INV1 | M2 |  |  |  | 1 | 1 | IS12INV1M2 | 2114.1 | 0.6309% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 16:53 | 16:53 | 17:00 | 17:14 | 0 | 0.11667 | 0.35 | 0.35 | checked related connection and parameter scb floting check one by one then the inverter and start | Close | 0.0022082 | 0.016 | 27.9919
1090 | 2024-05-14 | FY24 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 6:11 | 19:23 | 13.2 | IS15 | INV2 | M1 |  |  |  | 1 | 1 | IS15INV2M1 | 2004.48 | 0.5982% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 16:47 | 16:47 | 16:53 | 17:22 | 0 | 0.1 | 0.58333 | 0.58333 | checked related connection and parameter scb floting check one by one then the inverter and start | Close | 0.0034894 | 0.023 | 38.152
1091 | 2024-05-14 | FY24 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 6:11 | 19:23 | 13.2 | IS15 | INV2 | M2 |  |  |  | 1 | 1 | IS15INV2M2 | 1941.84 | 0.5795% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 16:47 | 16:47 | 16:53 | 16:58 | 0 | 0.1 | 0.18333 | 0.18333 | checked related connection and parameter scb floting check one by one then the inverter and start | Close | 0.0010624 | 0.0063 | 10.1237
1092 | 2024-05-14 | FY24 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 6:11 | 19:23 | 13.2 | IS15 | INV3 | M1 |  |  |  | 1 | 1 | IS15INV3M1 | 2223.72 | 0.6636% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 16:47 | 16:47 | 16:53 | 17:23 | 0 | 0.1 | 0.6 | 0.6 | checked related connection and parameter scb floting check one by one then the inverter and start | Close | 0.0039817 | 0.024 | 44.165
1093 | 2024-05-14 | FY24 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 6:11 | 19:23 | 13.2 | IS15 | INV3 | M2 |  |  |  | 1 | 1 | IS15INV3M2 | 2192.4 | 0.6543% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 16:47 | 16:47 | 16:53 | 17:23 | 0 | 0.1 | 0.6 | 0.6 | checked related connection and parameter scb floting check one by one then the inverter and start | Close | 0.0039256 | 0.024 | 43.543
1094 | 2024-05-16 | FY24 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 6:15 | 19:23 | 13.1333 | IS19 | INV2 | M1 | SCB8 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | SCB_String MC4 coonector burn | MC4 connector found burn. | 6:15 | 6:15 | 19:23 | 19:23 | 0 | 13.1333 | 13.1333 | 13.1333 | MC4 connector replaced and string charged | Close | 0.0012275 | 7.3 | 189.2047
1095 | 2024-05-19 | FY24 | 2024 | Year_3 | Year_3 | 2024-05-01 | 31 | 6:11 | 19:24 | 13.2167 | IS11 | INV4 | M2 | SCB5 | Str_Typ5(545*29) |  | 0 | 0 | Str_Typ5(545*29) | 15.805 | 0.004717% | Connectors | MC4 connector found burn. | MC4 connector found burn. | 6:11 | 6:11 | 19:24 | 19:24 | 0 | 13.2167 | 13.2167 | 13.2167 | MC4 connector replaced and string charged | Close | 0.00062338 | 6.7 | 87.6308
1096 | 2024-06-02 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:10 | 19:34 | 13.4 | IS10 | INV1 | M1 |  |  |  | 1 | 1 | IS10INV1M1 | 2067.12 | 0.6169% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 7:25 | 7:25 | 7:28 | 7:35 | 0 | 0.05 | 0.16667 | 0.16667 | Inverter reseted automatically | Close | 0.0010281 | 0.037 | 64.2639 | PTW234756
1097 | 2024-06-02 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:10 | 19:34 | 13.4 | IS10 | INV2 | M2 |  |  |  | 1 | 1 | IS10INV2M2 | 2223.72 | 0.6636% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 7:25 | 7:25 | 7:28 | 7:35 | 0 | 0.05 | 0.16667 | 0.16667 | Inverter reseted automatically | Close | 0.001106 | 0.037 | 69.1324 | PTW234756
1098 | 2024-06-02 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:10 | 19:34 | 13.4 | IS10 | INV1 | M1 |  |  |  | 1 | 1 | IS10INV1M1 | 2067.12 | 0.6169% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 7:25 | 7:25 | 7:28 | 7:35 | 0 | 0.05 | 0.16667 | 0.16667 | Inverter reseted automatically | Close | 0.0010281 | 0.037 | 64.2639 | PTW234756
1099 | 2024-06-02 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:10 | 19:34 | 13.4 | IS10 | INV2 | M2 |  |  |  | 1 | 1 | IS10INV2M2 | 2223.72 | 0.6636% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 7:25 | 7:25 | 7:28 | 7:35 | 0 | 0.05 | 0.16667 | 0.16667 | Inverter reseted automatically | Close | 0.001106 | 0.037 | 69.1324 | PTW234756
1100 | 2024-06-03 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:11 | 19:33 | 13.3667 | IS10 | INV1 | M1 |  |  |  | 1 | 1 | IS10INV1M1 | 2067.12 | 0.6169% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 7:21 | 7:21 | 7:25 | 7:31 | 0 | 0.066667 | 0.16667 | 0.16667 | Inverter reseted automatically | Close | 0.0010281 | 0.037 | 64.2639 | PTW234859
1101 | 2024-06-03 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:11 | 19:33 | 13.3667 | IS10 | INV2 | M2 |  |  |  | 1 | 1 | IS10INV2M2 | 2223.72 | 0.6636% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 7:21 | 7:21 | 7:25 | 7:31 | 0 | 0.066667 | 0.16667 | 0.16667 | Inverter reseted automatically | Close | 0.001106 | 0.037 | 69.1324 | PTW234859
1102 | 2024-06-03 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:11 | 19:33 | 13.3667 | IS10 | INV1 | M1 |  |  |  | 1 | 1 | IS10INV1M1 | 2067.12 | 0.6169% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 7:21 | 7:21 | 7:25 | 7:31 | 0 | 0.066667 | 0.16667 | 0.16667 | Inverter reseted automatically | Close | 0.0010281 | 0.037 | 64.2639 | PTW234859
1103 | 2024-06-03 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:11 | 19:33 | 13.3667 | IS10 | INV2 | M2 |  |  |  | 1 | 1 | IS10INV2M2 | 2223.72 | 0.6636% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 7:21 | 7:21 | 7:25 | 7:31 | 0 | 0.066667 | 0.16667 | 0.16667 | Inverter reseted automatically | Close | 0.001106 | 0.037 | 69.1324 | PTW234859
1104 | 2024-06-04 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:08 | 19:34 | 13.4333 | IS10 | INV1 | M1 |  |  |  | 1 | 1 | IS10INV1M1 | 2067.12 | 0.6169% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 7:18 | 7:18 | 7:22 | 7:29 | 0 | 0.066667 | 0.18333 | 0.18333 | Inverter reseted automatically | Close | 0.001131 | 0.037 | 64.2639 | PTW234980
1105 | 2024-06-04 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:08 | 19:34 | 13.4333 | IS10 | INV2 | M2 |  |  |  | 1 | 1 | IS10INV2M2 | 2223.72 | 0.6636% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 7:18 | 7:18 | 7:22 | 7:29 | 0 | 0.066667 | 0.18333 | 0.18333 | Inverter reseted automatically | Close | 0.0012166 | 0.037 | 69.1324 | PTW234980
1106 | 2024-06-04 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:08 | 19:34 | 13.4333 | IS10 | INV1 | M1 |  |  |  | 1 | 1 | IS10INV1M1 | 2067.12 | 0.6169% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 7:18 | 7:18 | 7:22 | 7:29 | 0 | 0.066667 | 0.18333 | 0.18333 | Inverter reseted automatically | Close | 0.001131 | 0.037 | 64.2639 | PTW234980
1107 | 2024-06-04 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:08 | 19:34 | 13.4333 | IS10 | INV2 | M2 |  |  |  | 1 | 1 | IS10INV2M2 | 2223.72 | 0.6636% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 7:18 | 7:18 | 7:22 | 7:29 | 0 | 0.066667 | 0.18333 | 0.18333 | Inverter reseted automatically | Close | 0.0012166 | 0.037 | 69.1324 | PTW234980
1108 | 2024-06-05 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:06 | 19:28 | 13.3667 | IS10 | INV1 | M1 |  |  |  | 1 | 1 | IS10INV1M1 | 2067.12 | 0.6169% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 7:24 | 7:24 | 7:28 | 7:36 | 0 | 0.066667 | 0.2 | 0.2 | Inverter reseted automatically | Close | 0.0012338 | 0.047 | 81.6325 | PTW235100
1109 | 2024-06-05 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:06 | 19:28 | 13.3667 | IS10 | INV2 | M2 |  |  |  | 1 | 1 | IS10INV2M2 | 2223.72 | 0.6636% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 7:24 | 7:24 | 7:28 | 7:36 | 0 | 0.066667 | 0.2 | 0.2 | Inverter reseted automatically | Close | 0.0013272 | 0.047 | 87.8168 | PTW235100
1110 | 2024-06-05 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:06 | 19:28 | 13.3667 | IS10 | INV1 | M1 |  |  |  | 1 | 1 | IS10INV1M1 | 2067.12 | 0.6169% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 7:24 | 7:24 | 7:28 | 7:36 | 0 | 0.066667 | 0.2 | 0.2 | Inverter reseted automatically | Close | 0.0012338 | 0.047 | 81.6325 | PTW235100
1111 | 2024-06-05 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:06 | 19:28 | 13.3667 | IS10 | INV2 | M2 |  |  |  | 1 | 1 | IS10INV2M2 | 2223.72 | 0.6636% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 7:24 | 7:24 | 7:28 | 7:36 | 0 | 0.066667 | 0.2 | 0.2 | Inverter reseted automatically | Close | 0.0013272 | 0.047 | 87.8168 | PTW235100
1112 | 2024-06-05 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:06 | 19:28 | 13.3667 | IS10 | INV4 | M1 | SCB-11 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | SCB_String MC4 connector burn | MC4 connector burn | 6:06 | 6:06 | 19:28 | 19:28 | 0 | 13.3667 | 13.3667 | 13.3667 | MC4 connector replaced and string charged | Close | 0.00062467 | 7.1 | 93.4221
1113 | 2024-06-05 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:06 | 19:28 | 13.3667 | IS8 | INV2 | M1 | SCB-4 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | Module Busbar Found damage | Module busbar found damage | 6:06 | 6:06 | 19:28 | 19:28 | 0 | 13.3667 | 13.3667 | 13.3667 | Module reinstalled and string restored | Close | 0.00062467 | 7.1 | 93.4221
1114 | 2024-06-06 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:07 | 19:29 | 13.3667 | IS9 | INV4 | M1 | SCB-7 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Connectors | SCB Side MC4 Connector Burn | SCB Side MC4 Connector Burn | 6:07 | 6:07 | 19:29 | 19:29 | 0 | 13.3667 | 13.3667 | 13.3667 | MC4 connector replaced and string charged | Close | 0.0012609 | 6.77 | 179.8096
1115 | 2024-06-08 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:08 | 19:33 | 13.4167 | IS2 | INV3 | M2 |  |  |  | 1 | 1 | IS2INV3M2 | 2090.61 | 0.6239% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 6:13 | 6:13 | 6:17 | 6:17 | 0 | 0.066667 | 0.066667 | 0.066667 | As discussed with OEM breaker Coil Replaced. Then Inv charged |  | 0.00041593 | 0.434 | 762.364 | PTW235412
1116 | 2024-06-08 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:08 | 19:33 | 13.4167 | IS2 | INV3 | M1 |  |  |  | 1 | 1 | IS2INV3M1 | 2064.8 | 0.6162% | Inverter | Inverter tripped in AC switch disconnection fault | Manualy stop for Inv Unit_AC Coil failure rectification | 7:39 | 7:39 | 7:39 | 7:39 | 0 | 0 | 0 | 0 | Manualy stop for Inv Unit_AC Coil failure rectification |  | 0 | 0.093 | 161.3469 | PTW235412
1117 | 2024-06-08 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:08 | 19:33 | 13.4167 | IS2 | INV3 | M1 |  |  |  | 1 | 1 | IS2INV3M1 | 2064.8 | 0.6162% | Inverter | Inverter tripped in AC switch disconnection fault | Manualy stop for Inv Unit_AC Coil failure rectification | 8:04 | 8:04 | 8:04 | 8:04 | 0 | 0 | 0 | 0 | Manualy stop for Inv Unit_AC Coil failure rectification |  | 0 | 0.055 | 95.4202 | PTW235412
1118 | 2024-06-15 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:17 | 19:35 | 13.3 | IS10 | INV1 | M1 |  |  |  | 1 | 1 | IS10INV1M1 | 2067.12 | 0.6169% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 8:10 | 8:10 | 8:15 | 8:20 | 0 | 0.083333 | 0.16667 | 0.16667 | Inverter reseted automatically | Close | 0.0010281 | 0.0683 | 118.6277 | PTW236236
1119 | 2024-06-15 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:17 | 19:35 | 13.3 | IS10 | INV2 | M2 |  |  |  | 1 | 1 | IS10INV2M2 | 2223.72 | 0.6636% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 8:10 | 8:10 | 8:15 | 8:20 | 0 | 0.083333 | 0.16667 | 0.16667 | Inverter reseted automatically | Close | 0.001106 | 0.0683 | 127.6146 | PTW236236
1120 | 2024-06-15 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:17 | 19:35 | 13.3 | IS10 | INV1 | M1 |  |  |  | 1 | 1 | IS10INV1M1 | 2067.12 | 0.6169% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 8:10 | 8:10 | 8:15 | 8:25 | 0 | 0.083333 | 0.25 | 0.25 | Inverter reseted automatically | Close | 0.0015422 | 0.101 | 175.4231 | PTW236236
1121 | 2024-06-15 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:17 | 19:35 | 13.3 | IS10 | INV2 | M2 |  |  |  | 1 | 1 | IS10INV2M2 | 2223.72 | 0.6636% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 8:10 | 8:10 | 8:15 | 8:25 | 0 | 0.083333 | 0.25 | 0.25 | Inverter reseted automatically | Close | 0.001659 | 0.101 | 188.7127 | PTW236236
1122 | 2024-06-22 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:20 | 19:40 | 13.3333 | IS17 | INV4 | M1 |  |  |  | 1 | 1 | IS17INV4M1 | 2004.48 | 0.5982% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 14:07 | 14:07 | 14:11 | 14:35 | 0 | 0.066667 | 0.46667 | 0.46667 | Inverter reseted automatically | Close | 0.0027916 | 0.053 | 89.2642 | PTW237103
1123 | 2024-06-22 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:20 | 19:40 | 13.3333 | IS17 | INV4 | M2 |  |  |  | 1 | 1 | IS17INV4M2 | 2004.48 | 0.5982% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 14:07 | 14:07 | 14:11 | 14:17 | 0 | 0.066667 | 0.16667 | 0.16667 | Inverter reseted automatically | Close | 0.00099698 | 0.024 | 40.4215 | PTW237103
1124 | 2024-06-22 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:20 | 19:40 | 13.3333 | IS17 | INV4 | M2 |  |  |  | 1 | 1 | IS17INV4M2 | 2004.48 | 0.5982% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 14:32 | 14:32 | 14:38 | 14:35 | 0 | 0.1 | 0.05 | 0.05 | Inverter reseted automatically | Close | 0.00029909 | 0.006 | 10.1054 | PTW237103
1125 | 2024-06-22 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:20 | 19:40 | 13.3333 | IS17 | INV4 | M1 |  |  |  | 1 | 1 | IS17INV4M1 | 2004.48 | 0.5982% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 15:05 | 15:05 | 15:10 | 15:20 | 0 | 0.083333 | 0.25 | 0.25 | Inverter reseted automatically | Close | 0.0014955 | 0.0117 | 19.7055 | PTW237103
1126 | 2024-06-22 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:20 | 19:40 | 13.3333 | IS17 | INV4 | M2 |  |  |  | 1 | 1 | IS17INV4M2 | 2004.48 | 0.5982% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 15:05 | 15:05 | 15:10 | 15:15 | 0 | 0.083333 | 0.16667 | 0.16667 | Inverter reseted automatically | Close | 0.00099698 | 0.0072 | 12.1265 | PTW237103
1127 | 2024-06-22 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:20 | 19:40 | 13.3333 | IS10 | INV1 | M1 |  |  |  | 1 | 1 | IS10INV1M1 | 2067.12 | 0.6169% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 15:15 | 15:15 | 15:21 | 15:42 | 0 | 0.1 | 0.45 | 0.45 | Inverter reseted automatically | Close | 0.002776 | 0.0455 | 79.0272 | PTW237103
1128 | 2024-06-22 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:20 | 19:40 | 13.3333 | IS10 | INV2 | M1 |  |  |  | 1 | 1 | IS10INV2M1 | 1973.16 | 0.5888% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 15:15 | 15:15 | 15:21 | 15:41 | 0 | 0.1 | 0.43333 | 0.43333 | Inverter reseted automatically | Close | 0.0025517 | 0.037 | 61.3428 | PTW237103
1129 | 2024-06-22 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:20 | 19:40 | 13.3333 | IS10 | INV2 | M2 |  |  |  | 1 | 1 | IS10INV2M2 | 2223.72 | 0.6636% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 15:15 | 15:15 | 15:21 | 15:41 | 0 | 0.1 | 0.43333 | 0.43333 | Inverter reseted automatically | Close | 0.0028757 | 0.037 | 69.1324 | PTW237103
1130 | 2024-06-22 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:20 | 19:40 | 13.3333 | IS12 | INV2 | M1 |  |  |  | 1 | 1 | IS12INV2M1 | 1941.84 | 0.5795% | Inverter | Inv_tripped in PDP protection fault | Inv_tripped in PDP protection fault | 15:04 | 15:04 | 15:09 | 16:23 | 0 | 0.083333 | 1.3167 | 1.3167 | Inverter Reset and Run | Close | 0.00763 | 0.174 | 283.898 | PTW237103
1131 | 2024-06-22 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:20 | 19:40 | 13.3333 | IS12 | INV2 | M2 |  |  |  | 1 | 1 | IS12INV2M2 | 2255.04 | 0.673% | Inverter | Inv_tripped in PDP protection fault | Inv_tripped in PDP protection fault | 15:48 | 15:48 | 15:53 | 16:07 | 0 | 0.083333 | 0.31667 | 0.31667 | Inverter Reset and Run | Close | 0.0021311 | 0.06 | 113.6855 | PTW237103
1132 | 2024-06-22 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:20 | 19:40 | 13.3333 | IS19 | INV3 | M2 | SCB-8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | MC4 connector found burn. | MC4 connector found burn. | 6:20 | 6:20 | 19:40 | 19:40 | 0 | 13.3333 | 13.3333 | 13.3333 | MC4 connector replaced and string charged | Close | 0.00062311 | 4.02 | 52.8953
1133 | 2024-06-23 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:21 | 19:38 | 13.2833 | IS15 | INV4 | M1 |  |  |  | 1 | 1 | IS15INV4M1 | 2192.4 | 0.6543% | Inverter | Inv_unit tripped under Module Temp High | Inverter tripped under module temp fault | 12:42 | 12:42 | 12:42 | 12:46 | 0 | 0 | 0.066667 | 0.066667 | Inverter reseted automatically | Close | 0.00043618 | 0.08 | 147.3701
1134 | 2024-06-23 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:21 | 19:38 | 13.2833 | IS15 | INV4 | M1 |  |  |  | 1 | 1 | IS15INV4M1 | 2192.4 | 0.6543% | Inverter | Inv_unit tripped under Module Temp High | Inverter tripped under module temp fault | 13:11 | 13:11 | 13:11 | 13:15 | 0 | 0 | 0.066667 | 0.066667 | Inverter reseted automatically | Close | 0.00043618 | 0.08 | 147.3701
1135 | 2024-06-23 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:21 | 19:38 | 13.2833 | IS15 | INV4 | M1 |  |  |  | 1 | 1 | IS15INV4M1 | 2192.4 | 0.6543% | Inverter | Inv_unit tripped under Module Temp High | Inverter tripped under module temp fault | 13:38 | 13:38 | 13:38 | 13:42 | 0 | 0 | 0.066667 | 0.066667 | Inverter reseted automatically | Close | 0.00043618 | 0.08 | 147.3701
1136 | 2024-06-24 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:19 | 19:37 | 13.3 | IS3 | INV2 | M1 | SCB-3 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Y-Connector MC4 found burn. | MC4 connector found burn. | 6:19 | 6:19 | 19:37 | 19:37 | 0 | 13.3 | 13.3 | 13.3 | MC4 connector replaced and string charged | Close | 0.0010244 | 5.79 | 125.5643
1137 | 2024-06-25 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:15 | 19:47 | 13.5333 | IS17 | INV4 | M1 |  |  |  | 1 | 1 | IS17INV4M1 | 2004.48 | 0.5982% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 17:21 | 17:21 | 17:31 | 17:54 | 0 | 0.16667 | 0.55 | 0.55 | checked related connection and parameter then the inverter and start | Close | 0.00329 | 0.035 | 58.948
1138 | 2024-06-25 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:15 | 19:47 | 13.5333 | IS17 | INV4 | M2 |  |  |  | 1 | 1 | IS17INV4M2 | 2004.48 | 0.5982% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 17:37 | 17:37 | 17:39 | 17:47 | 0 | 0.033333 | 0.16667 | 0.16667 | checked related connection and parameter then the inverter and start | Close | 0.00099698 | 0.009 | 15.1581
1139 | 2024-06-29 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:29 | 19:30 | 13.0167 | IS10 | INV1 | M2 |  |  |  | 1 | 1 | IS10INV1M2 | 2098.44 | 0.6262% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 6:32 | 6:32 | 6:40 | 7:39 | 0 | 0.13333 | 1.1167 | 1.1167 | checked related connection and parameter scb floting check one by one then the inverter and start | Close | 0.0069929 | 0.114 | 201.0023 | PTW237927
1140 | 2024-06-29 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-01 | 30 | 6:29 | 19:30 | 13.0167 | IS10 | INV1 | M2 | SCB-10 |  |  | 1 | 1 | IS10INV1M2SCB-10 | 2129.76 |  | SCB | Inv_tripped of GFDI | SCB stop due to rectification work of inverter GFDI Fault | 7:39 | 7:39 | 7:42 | 8:24 | 0 | 0.05 | 0.75 | 0.75 | checked related connection and parameter scb floting check and start | Close |  | 0.1 | 178.9494 | PTW237927
1141 | 2024-07-01 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:21 | 19:43 | 13.3667 | [5 empty] | Power_Tx1 | 0 | 1 | Power_Tx1 | 167322.75 | 49.93% | PTR | Power transformer 01 manually triped due to RRVPNL CB Relay panal 201l sparking issue | Check related parameters, rectification work & voltage normlised then restored | 7:27 | 7:27 | 7:40 | 11:00 | 0 | 0.21667 | 3.55 | 3.55 | Check related parameters, rectification work & voltage normlised then restored | Close | 1.7726 | 1.598 | 227373.0434 | PTW238141
1142 | 2024-07-01 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:21 | 19:43 | 13.3667 | [5 empty] | Power_Tx2 | 0 | 1 | Power_Tx2 | 167768.915 | 50.07% | PTR | Power transformer 02 manually triped due to RRVPNL CB Relay panal 201 sparking issue | Check related parameters, rectification work & voltage normlised then restored | 7:57 | 7:57 | 7:40 | 10:58 | 0 | -0.28333 | 3.0167 | 3.0167 | Check related parameters, rectification work & voltage normlised then restored | Close | 1.5103 | 1.426 | 203440.8809 | PTW238141
1143 | 2024-07-03 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:27 | 19:37 | 13.1667 | [5 empty] | Tx | 0 | 1 | Tx | 16737.785 |  | MV Panel | ICR_1 trip due to LT panal Flashover | IDT LV side LT panel suply disconnect and suply to UPS by DG & Check related parameter then restored | 6:27 | 6:27 | 6:40 | 19:37 | 0 | 0.21667 | 13.1667 | 13.1667 | IDT LV side LT panel suply disconnect and suply to UPS by DG & Check related parameter then restored | Close |  | 7 | 99633.0055 | PTW238392
1144 | 2024-07-03 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:27 | 19:37 | 13.1667 | [5 empty] | Tx | 0 | 1 | Tx | 16719.08 |  | MV Panel | ICR_2 Manually trip due to ICR-1 LT panal Flashover | ICR-1 Isolate properly for rectification work then ICR_2 Charge | 6:27 | 6:27 | 6:40 | 6:54 | 0 | 0.21667 | 0.45 | 0.45 | ICR-1 Isolate properly for rectification work then ICR_2 Charge | Close |  | 0.024 | 341.2171 | PTW238392
1145 | 2024-07-03 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:27 | 19:37 | 13.1667 | [5 empty] | Tx | 0 | 1 | Tx | 16719.08 |  | MV Panel | ICR_2 Manually trip due to ICR-1 normlization work | ICR-1 normlization work | 18:38 | 18:38 | 18:38 | 18:44 | 0 | 0 | 0.1 | 0.1 | ICR-1 normlization work | Close |  | 0.0098 | 139.3303 | PTW238392
1146 | 2024-07-05 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:19 | 19:39 | 13.3333 | IS2 | INV1 | M1 |  |  |  | 1 | 1 | IS2INV1M1 | 2090.61 | 0.6239% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 14:25 | 14:25 | 14:25 | 14:40 | 0 | 0 | 0.25 | 0.25 | Inverter Auto-Reset and Run | Close | 0.0015597 | 0.18868 | 335.4364 | PTW238633
1147 | 2024-07-05 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:19 | 19:39 | 13.3333 | IS2 | INV1 | M1 |  |  |  | 1 | 1 | IS2INV1M1 | 2090.61 | 0.6239% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 14:50 | 14:50 | 14:56 | 14:55 | 0 | 0.1 | 0.083333 | 0.083333 | Inverter Manually trip for unit-2 rectification work | Close | 0.00051991 | 0.069266 | 123.1401 | PTW238633
1148 | 2024-07-05 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:19 | 19:39 | 13.3333 | IS2 | INV1 | M1 |  |  |  | 1 | 1 | IS2INV1M1 | 2090.61 | 0.6239% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 15:39 | 15:39 | 15:39 | 15:44 | 0 | 0 | 0.083333 | 0.083333 | Inverter Manually trip for unit-2 rectification work | Close | 0.00051991 | 0.062843 | 111.7208 | PTW238633
1149 | 2024-07-05 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:19 | 19:39 | 13.3333 | IS2 | INV1 | M1 |  |  |  | 1 | 1 | IS2INV1M1 | 2090.61 | 0.6239% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 15:54 | 15:54 | 15:54 | 16:05 | 0 | 0 | 0.18333 | 0.18333 | Inverter Manually trip for unit-2 rectification work | Close | 0.0011438 | 0.10935 | 194.4046 | PTW238633
1150 | 2024-07-05 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:19 | 19:39 | 13.3333 | IS2 | INV1 | M1 |  |  |  | 1 | 1 | IS2INV1M1 | 2090.61 | 0.6239% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 16:49 | 16:49 | 16:49 | 17:01 | 0 | 0 | 0.2 | 0.2 | Inverter Manually trip for unit-2 rectification work | Close | 0.0012478 | 0.079948 | 142.1301 | PTW238633
1151 | 2024-07-05 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:19 | 19:39 | 13.3333 | IS2 | INV1 | M1 |  |  |  | 1 | 1 | IS2INV1M1 | 2090.61 | 0.6239% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 17:58 | 17:58 | 17:58 | 19:00 | 0 | 0 | 1.0333 | 1.0333 | Inverter Manually trip for unit-2 rectification work | Close | 0.0064469 | 0.12825 | 228.0027 | PTW238633
1152 | 2024-07-05 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:19 | 19:39 | 13.3333 | IS2 | INV1 | M2 |  |  |  | 1 | 1 | IS2INV1M2 | 2090.61 | 0.6239% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 14:25 | 14:25 | 14:35 | 18:50 | 0 | 0.16667 |  | 4.4167 | Found SCB_3 nagetive and SCB_7 positive DC cable faulty | Open | 0.027555 | 1.8119 | 3221.1514 | PTW238633
1153 | 2024-07-05 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:19 | 19:39 | 13.3333 | IS8 | INV2 | M1 | SCB4 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | Y-Connector MC4 found burn. | Y-connector side MC4 burn | 6:19 | 6:19 | 6:19 | 19:39 | 0 | 0 | 13.3333 | 13.3333 | MC4 connector replaced | Close | 0.0012462 | 6.2314 | 165.9649
1154 | 2024-07-05 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:19 | 19:39 | 13.3333 | IS16 | INV4 | M2 | SCB3 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | MC4 found open | MC4 Connector found open | 6:19 | 6:19 | 6:19 | 19:39 | 0 | 0 | 13.3333 | 13.3333 | MC4 connect properly | Close | 0.00062311 | 6.4091 | 85.3489
1155 | 2024-07-06 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:17 | 19:38 | 13.35 | IS2 | INV2 | M1 |  |  |  | 1 | 1 | IS2INV2M1 | 2090.61 | 0.6239% | Inverter | Inverter Manually trip for unit-2 Cable rectification work | Inverter Manually trip for unit-2 Cable rectification work | 6:17 | 6:17 | 6:17 | 9:05 | 0 | 0 | 2.8 | 2.8 | Inverter Manually trip for unit-2 Cable rectification work | Close | 0.017469 | 0.651 | 1157.3407 | PTW238747
1156 | 2024-07-06 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:17 | 19:38 | 13.35 | IS2 | INV2 | M2 |  |  |  | 1 | 1 | IS2INV2M2 | 2090.61 | 0.6239% | Inverter | Inverter Manually trip for unit-2 Cable rectification work | Inverter Manually trip for unit-2 Cable rectification work | 6:17 | 6:17 | 6:17 | 9:05 | 0 | 0 | 2.8 | 2.8 | Inverter Manually trip for unit-2 Cable rectification work | Close | 0.017469 | 0.651 | 1157.3407 | PTW238747
1157 | 2024-07-06 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:17 | 19:38 | 13.35 | IS2 | INV2 | M2 | SCB3 |  |  | 1 | 1 | IS2INV2M2SCB3 | 232.29 | 0.06932% | SCB | Manully stop due to cable rectification work | cable jointing work and check IR value & cable connect | 6:17 | 6:17 | 6:17 | 19:38 | 0 | 0 | 13.35 | 13.35 | cable jointing work and check IR value & cable connect | Close | 0.0092544 | 6.6 | 1303.712 | PTW238747
1158 | 2024-07-06 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:17 | 19:38 | 13.35 | IS2 | INV2 | M2 | SCB7 |  |  | 1 | 1 | IS2INV2M2SCB7 | 232.29 | 0.06932% | SCB | Manully stop due to cable rectification work | cable jointing work and check IR value & cable connect | 6:17 | 6:17 | 6:17 | 19:38 | 0 | 0 | 13.35 | 13.35 | cable jointing work and check IR value & cable connect | Close | 0.0092544 | 6.6 | 1303.712 | PTW238747
1159 | 2024-07-07 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:29 | 19:40 | 13.1833 | IS4 |  |  |  |  | Tx | 0 | 1 | IS4Tx | 16547.4 | 4.938% | IDT | IDT trip in under diffencial oprate | differential Oprate due to protection relay malfuctioning. | 10:05 | 10:05 | 10:20 | 16:50 | 0 | 0.25 | 6.75 | 6.75 | check IR value HV & LV both side, not found any abnormal and check Relay but not found any record today fault but relay indicates tripping this happened due to malfunctioning. | Close | 0.33333 | 2.6743 | 37630.6557 | PTW238953
1160 | 2024-07-07 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:29 | 19:40 | 13.1833 | IS9 | INV3 | M1 |  |  |  | 1 | 1 | IS9INV3M1 | 2275.33 | 0.679% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 11:46 | 11:46 | 11:55 | 12:29 | 0 | 0.15 | 0.71667 | 0.71667 | Inverter Auto-Reset and Run | Close | 0.0048663 | 0.16175 | 312.9605
1161 | 2024-07-07 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:29 | 19:40 | 13.1833 | IS17 | INV4 | M1 |  |  |  | 1 | 1 | IS17INV4M1 | 2004.48 | 0.5982% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 11:31 | 11:31 | 11:40 | 11:52 | 0 | 0.15 | 0.35 | 0.35 | Inverter Auto-Reset and Run | Close | 0.0020937 | 0.051202 | 87.2754
1162 | 2024-07-07 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:29 | 19:40 | 13.1833 | IS10 | INV1 | M1 |  |  |  | 1 | 1 | IS10INV1M1 | 2067.12 | 0.6169% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 11:57 | 11:57 | 12:05 | 12:12 | 0 | 0.13333 | 0.25 | 0.25 | Inverter Auto-Reset and Run | Close | 0.0015422 | 0.050239 | 88.31
1163 | 2024-07-07 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:29 | 19:40 | 13.1833 | IS10 | INV1 | M2 |  |  |  | 1 | 1 | IS10INV1M2 | 2098.44 | 0.6262% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 11:57 | 11:57 | 12:05 | 12:43 | 0 | 0.13333 | 0.76667 | 0.76667 | Inverter Auto-Reset and Run | Close | 0.0048011 | 0.1986 | 354.3944
1164 | 2024-07-07 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:29 | 19:40 | 13.1833 | IS10 | INV2 | M1 |  |  |  | 1 | 1 | IS10INV2M1 | 1973.16 | 0.5888% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 11:57 | 11:57 | 12:05 | 12:12 | 0 | 0.13333 | 0.25 | 0.25 | Inverter Auto-Reset and Run | Close | 0.0014721 | 0.050239 | 84.2959
1165 | 2024-07-07 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:29 | 19:40 | 13.1833 | IS10 | INV2 | M2 |  |  |  | 1 | 1 | IS10INV2M2 | 2223.72 | 0.6636% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 11:57 | 11:57 | 12:05 | 12:43 | 0 | 0.13333 | 0.76667 | 0.76667 | Inverter Auto-Reset and Run | Close | 0.0050877 | 0.1986 | 375.5523
1166 | 2024-07-08 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:23 | 19:07 | 12.7333 | IS10 | INV1 | M1 |  |  |  | 1 | 1 | IS10INV1M1 | 2067.12 | 0.6169% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 11:47 | 11:47 | 11:52 | 16:17 | 0 | 0.083333 | 4.5 | 4.5 | Inverter Auto-Reset and Run | Close | 0.02776 | 0.050809 | 89.312
1167 | 2024-07-08 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:23 | 19:07 | 12.7333 | IS10 | INV1 | M2 |  |  |  | 1 | 1 | IS10INV1M2 | 2098.44 | 0.6262% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 11:47 | 11:47 | 11:52 | 17:05 | 0 | 0.083333 | 5.3 | 5.3 | Inverter Auto-Reset and Run | Close | 0.03319 | 0.069292 | 123.6476
1168 | 2024-07-08 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:23 | 19:07 | 12.7333 | IS10 | INV2 | M1 |  |  |  | 1 | 1 | IS10INV2M1 | 1973.16 | 0.5888% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 11:47 | 11:47 | 11:52 | 16:17 | 0 | 0.083333 | 4.5 | 4.5 | Inverter Auto-Reset and Run | Close | 0.026498 | 0.050809 | 85.2523
1169 | 2024-07-08 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:23 | 19:07 | 12.7333 | IS10 | INV2 | M2 |  |  |  | 1 | 1 | IS10INV2M2 | 2223.72 | 0.6636% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 11:47 | 11:47 | 11:52 | 19:07 | 0 | 0.083333 | 7.3333 | 7.3333 | Inverter Auto-Reset and Run | Close | 0.048665 | 0.11577 | 218.9248
1170 | 2024-07-09 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:22 | 19:36 | 13.2333 | IS4 | INV4 | M2 |  |  |  | 1 | 1 | IS4INV4M2 | 2061.9 | 0.6153% | Inverter | Inv_tripped in INS Fault | Inv_tripped in INS Fault | 6:22 | 6:22 | 6:22 | 19:36 | 0 | 0 | 13.2333 | 13.2333 | Inv_tripped in INS Fault | Close | 0.081428 | 5.6478 | 9902.6793 | PTW239295
1171 | 2024-07-09 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:22 | 19:36 | 13.2333 | IS11 | INV4 | M2 |  |  |  | 1 | 1 | IS11INV4M2 | 1785.965 | 0.533% | Inverter | Inv_tripped in INS Fault | Inv_tripped in INS Fault | 6:22 | 6:22 | 6:22 | 19:36 | 0 | 0 | 13.2333 | 13.2333 | Inv_tripped in INS Fault | Close | 0.070531 | 5.551 | 8430.3962 | PTW239295
1172 | 2024-07-09 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:22 | 19:36 | 13.2333 | IS14 | INV4 | M1 |  |  |  | 1 | 1 | IS14INV4M1 | 2192.4 | 0.6543% | Inverter | Inv_tripped in INS Fault | Inv_tripped in INS Fault | 6:22 | 6:22 | 6:22 | 19:36 | 0 | 0 | 13.2333 | 13.2333 | Inv_tripped in INS Fault | Close | 0.086582 | 5.432 | 10127.0695 | PTW239295
1173 | 2024-07-09 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:22 | 19:36 | 13.2333 | IS16 | INV2 | M2 |  |  |  | 1 | 1 | IS16INV2M2 | 2004.48 | 0.5982% | Inverter | Inv_tripped in INS Fault | Inv_tripped in INS Fault | 6:22 | 6:22 | 6:22 | 19:36 | 0 | 0 | 13.2333 | 13.2333 | Inv_tripped in INS Fault | Close | 0.07916 | 5.432 | 9259.035 | PTW239295
1174 | 2024-07-15 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:27 | 19:37 | 13.1667 | IS2 | INV1 | M1 | SCB3 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | SCB | Y-connector fuse damage | Y-connector fuse damage | 6:27 | 6:27 | 6:27 | 19:37 | 0 | 0 | 13.1667 | 13.1667 | Y-Connector fuse Replaced. | Close | 0.0010141 | 5.99 | 131.4686
1175 | 2024-07-16 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:26 | 19:46 | 13.3333 | IS2 | INV1 | M1 | SCB3 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | SCB | Y-connector fuse damage | Y-connector fuse damage | 6:26 | 6:26 | 6:26 | 19:46 | 0 | 0 | 13.3333 | 13.3333 | Y-Connector fuse Replaced. | Close | 0.001027 | 6.28 | 137.8335
1176 | 2024-07-16 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:26 | 19:46 | 13.3333 | IS15 | INV4 | M1 | SCB2 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | SCB | MC4 connector burn | MC4 connector burn | 6:26 | 6:26 | 6:26 | 19:46 | 0 | 0 | 13.3333 | 13.3333 | MC4 connector Replaced. | Close | 0.00062311 | 6.354 | 84.6148
1177 | 2024-07-18 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:26 | 19:17 | 12.85 | IS8 | INV4 | M1 | SCB2 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | SCB | MC4 Connector found open | MC4 Connector found open | 6:26 | 6:26 | 6:26 | 19:17 | 0 | 0 | 12.85 | 12.85 | Mc4 connector connect properly | Close | 0.00060053 | 6.706 | 89.3023
1178 | 2024-07-18 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:26 | 19:17 | 12.85 | IS1 | INV2 | M1 | SCB1 | Str_Typ2 (450*29) |  | 0 | 0 | Str_Typ2 (450*29) | 13.05 | 0.003894% | SCB | MC4 Connector found open | MC4 Connector found open | 6:26 | 6:26 | 6:26 | 19:17 | 0 | 0 | 12.85 | 12.85 | Mc4 connector connect properly | Close | 0.00050044 | 6.825 | 75.7391
1179 | 2024-07-19 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:37 | 19:44 | 13.1167 | IS3 | INV3 | M1 | SCB9 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | SCB | Y-connector fuse damage | Y-connector fuse damage | 6:37 | 6:37 | 6:37 | 19:44 | 0 | 0 | 13.1167 | 13.1167 | Y-Connector fuse Replaced. | Close | 0.0010103 | 6.905 | 151.551
1180 | 2024-07-19 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:28 | 19:03 | 12.5833 | IS3 | INV3 | M1 | SCB9 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | SCB | 10 Nos. Module VOC Value found Zero. | 10 Nos. Module VOC Value found Zero. | 6:37 | 6:37 | 6:37 | 19:03 | 0 | 0 |  | 12.4333 | We planned today for module JB replacement work. | Open | 0.00047883 | 6.6283 | 72.7391
1181 | 2024-07-24 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:45 | 19:40 | 12.9167 | IS12 | INV1 | M2 | SCB10 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | SCB | MC4 Connector found open | MC4 Connector found open | 6:45 | 6:45 | 6:45 | 19:40 | 0 | 0 | 12.9167 | 12.9167 | Mc4 connector connect properly | Close | 0.00060364 | 6.88 | 91.6194
1182 | 2024-07-25 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:36 | 19:36 | 13 | IS8 | INV2 | M1 | SCB4 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | SCB | MC4 Connector found open | MC4 Connector found open | 6:36 | 6:36 | 6:36 | 19:36 | 0 | 0 | 13 | 13 | Mc4 connector connect properly | Close | 0.00060754 | 6.5031 | 86.6004
1183 | 2024-08-02 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 6:56 | 19:21 | 12.4167 | IS11 | INV1 | M1 |  |  |  | 1 | 1 | IS11INV1M1 | 2023.04 | 0.6037% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 11:59 | 11:59 | 11:59 | 12:44 | 0 | 0 | 0.75 | 0.75 | Inverter Auto-Reset and Run | Close | 0.004528 | 0.1372 | 232.983
1184 | 2024-08-02 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 6:56 | 19:21 | 12.4167 | IS11 | INV1 | M2 |  |  |  | 1 | 1 | IS11INV1M2 | 2212.7 | 0.6603% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 11:59 | 11:59 | 11:59 | 12:37 | 0 | 0 | 0.63333 | 0.63333 | Inverter Auto-Reset and Run | Close | 0.0041821 | 0.10794 | 200.4798
1185 | 2024-08-02 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 6:56 | 19:21 | 12.4167 | IS15 | INV2 | M1 |  |  |  | 1 | 1 | IS15INV2M1 | 2004.48 | 0.5982% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 11:57 | 11:57 | 11:57 | 12:57 | 0 | 0 | 1 | 1 | Inverter Auto-Reset and Run | Close | 0.0059819 | 0.21958 | 369.4538
1186 | 2024-08-02 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 6:56 | 19:21 | 12.4167 | IS15 | INV2 | M2 |  |  |  | 1 | 1 | IS15INV2M2 | 1941.84 | 0.5795% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 11:57 | 11:57 | 11:57 | 12:20 | 0 | 0 | 0.38333 | 0.38333 | Inverter Auto-Reset and Run | Close | 0.0022214 | 0.055705 | 90.7974
1187 | 2024-08-02 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 6:56 | 19:21 | 12.4167 | IS15 | INV3 | M1 |  |  |  | 1 | 1 | IS15INV3M1 | 2223.72 | 0.6636% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 11:57 | 11:57 | 11:57 | 12:57 | 0 | 0 | 1 | 1 | Inverter Auto-Reset and Run | Close | 0.0066362 | 0.21958 | 409.8628
1188 | 2024-08-02 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 6:56 | 19:21 | 12.4167 | IS15 | INV3 | M2 |  |  |  | 1 | 1 | IS15INV3M2 | 2192.4 | 0.6543% | Inverter | Inv_tripped of GFDI | Inverter tripped under GFDI Fault | 11:57 | 11:57 | 11:57 | 12:12 | 0 | 0 | 0.25 | 0.25 | Inverter Auto-Reset and Run | Close | 0.0016357 | 0.03574 | 65.7718
1189 | 2024-08-03 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 6:59 | 19:13 | 12.2333 | IS11 | INV1 | M1 |  |  |  | 1 | 1 | IS11INV1M1 | 2023.04 | 0.6037% | Inverter | Inverter Unit tripped in INS fault | Inverter Unit tripped in INS fault | 6:59 | 6:59 | 7:05 | 7:45 | 0 | 0.1 | 0.76667 | 0.76667 | checked related connection and parameter then rboot the inverter and start | Close | 0.0046286 | 0.03 | 50.9438 | PTW242591
1190 | 2024-08-03 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 6:59 | 19:13 | 12.2333 | IS11 | INV4 | M1 |  |  |  | 1 | 1 | IS11INV4M1 | 2023.04 | 0.6037% | Inverter | Inverter Unit tripped in INS fault | Inverter Unit tripped in INS fault | 6:59 | 6:59 | 7:05 | 7:45 | 0 | 0.1 | 0.76667 | 0.76667 | checked related connection and parameter then rboot the inverter and start | Close | 0.0046286 | 0.03 | 50.9438 | PTW242591
1191 | 2024-08-03 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 6:59 | 19:13 | 12.2333 | IS15 | INV4 | M2 |  |  |  | 1 | 1 | IS15INV4M2 | 2004.48 | 0.5982% | Inverter | Inverter Unit tripped in INS fault | Inverter Unit tripped in INS fault | 6:59 | 6:59 | 7:15 | 7:40 | 0 | 0.26667 | 0.68333 | 0.68333 | checked related connection and parameter then rboot the inverter and start | Close | 0.0040876 | 0.02 | 33.651 | PTW242591
1192 | 2024-08-03 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 6:59 | 19:13 | 12.2333 | IS16 | INV3 | M1 |  |  |  | 1 | 1 | IS16INV3M1 | 2129.76 | 0.6356% | Inverter | Inverter Unit tripped in INS fault | Inverter Unit tripped in INS fault | 6:59 | 6:59 | 7:10 | 7:50 | 0 | 0.18333 | 0.85 | 0.85 | checked related connection and parameter then rboot the inverter and start | Close | 0.0054024 | 0.03 | 53.6312 | PTW242591
1193 | 2024-08-05 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 8:56 | 18:00 | 9.0667 | IS2 | INV1 | M2 |  |  |  | 1 | 1 | IS2INV1M2 | 2090.61 | 0.6239% | Inverter | Inverter Unit tripped in INS fault | Inverter Unit tripped in INS fault | 8:55 | 8:55 | 8:55 | 9:33 | 0 | 0 | 0.63333 | 0.63333 | Due to Heavy Rain Inverter B/D not attend | Close | 0.0039513 | 0.084518 | 148.316
1194 | 2024-08-05 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 8:56 | 18:00 | 9.0667 | IS7 | INV4 | M2 |  |  |  | 1 | 1 | IS7INV4M2 | 1973.16 | 0.5888% | Inverter | Inverter Unit tripped in INS fault | Inverter Unit tripped in INS fault | 9:00 | 9:00 | 9:00 | 18:00 | 0 | 0 | 9 | 9 | Due to Heavy Rain Inverter B/D not attend | Close | 0.052996 | 1.1465 | 1898.8991
1195 | 2024-08-05 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 8:56 | 18:00 | 9.0667 | IS15 | INV4 | M1 |  |  |  | 1 | 1 | IS15INV4M1 | 2192.4 | 0.6543% | Inverter | Inverter Unit tripped in INS fault | Inverter Unit tripped in INS fault | 9:00 | 9:00 | 9:00 | 18:00 | 0 | 0 | 9 | 9 | Due to Heavy Rain Inverter B/D not attend | Close | 0.058884 | 1.0995 | 2023.3912
1196 | 2024-08-05 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 8:56 | 18:00 | 9.0667 | IS16 | INV3 | M1 |  |  |  | 1 | 1 | IS16INV3M1 | 2129.76 | 0.6356% | Inverter | Inverter Unit tripped in INS fault | Inverter Unit tripped in INS fault | 9:05 | 9:05 | 9:05 | 18:00 | 0 | 0 | 8.9167 | 8.9167 | Due to Heavy Rain Inverter B/D not attend | Close | 0.056672 | 1.0976 | 1962.2218
1197 | 2024-08-05 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 8:56 | 18:00 | 9.0667 | IS19 | INV3 | M1 |  |  |  | 1 | 1 | IS19INV3M1 | 2223.72 | 0.6636% | Inverter | Inverter Unit tripped in INS fault | Inverter Unit tripped in INS fault | 9:00 | 9:00 | 9:00 | 18:00 | 0 | 0 | 9 | 9 | Due to Heavy Rain Inverter B/D not attend | Close | 0.059726 | 1.0832 | 2021.8212
1198 | 2024-08-06 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 6:56 | 19:16 | 12.3333 | IS4 | INV4 | M2 |  |  |  | 1 | 1 | IS4INV4M2 | 2061.9 | 0.6153% | Inverter | Inverter Unit tripped in INS fault | Inverter Unit tripped in INS fault | 6:56 | 6:56 | 6:56 | 11:41 | 0 | 0 | 4.75 | 4.75 | checked related connection and parameter then rboot the inverter and start | Close | 0.029228 | 0.22701 | 392.8957 | PTW242808
1199 | 2024-08-06 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 6:56 | 19:16 | 12.3333 | IS5 | INV4 | M1 |  |  |  | 1 | 1 | IS5INV4M1 | 2090.61 | 0.6239% | Inverter | Inverter tripped under GFDI Fault | Inverter tripped under GFDI Fault | 6:56 | 6:56 | 6:56 | 19:16 | 0 | 0 | 12.3333 | 12.3333 | Due to Water logging inverter B/D could not attend | Close | 0.076947 | 0.89088 | 1563.3499 | PTW242808
1200 | 2024-08-06 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 6:56 | 19:16 | 12.3333 | IS7 | INV1 | M1 |  |  |  | 1 | 1 | IS7INV1M1 | 1973.16 | 0.5888% | Inverter | Inverter Unit tripped in INS fault | Inverter Unit tripped in INS fault | 6:56 | 6:56 | 6:56 | 9:10 | 0 | 0 | 2.2333 | 2.2333 | checked related connection and parameter then rboot the inverter and start | Close | 0.013151 | 0.077192 | 127.8496 | PTW242808
1201 | 2024-08-06 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 6:56 | 19:16 | 12.3333 | IS11 | INV4 | M2 |  |  |  | 1 | 1 | IS11INV4M2 | 1785.965 | 0.533% | Inverter | Inverter Unit tripped in INS fault | Inverter Unit tripped in INS fault | 6:56 | 6:56 | 6:56 | 11:27 | 0 | 0 | 4.5167 | 4.5167 | checked related connection and parameter then rboot the inverter and start | Close | 0.024073 | 0.24632 | 369.2649 | PTW242808
1202 | 2024-08-06 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 6:56 | 19:16 | 12.3333 | IS12 | INV1 | M1 |  |  |  | 1 | 1 | IS12INV1M1 | 2192.4 | 0.6543% | Inverter | Inverter Unit tripped in INS fault | Inverter Unit tripped in INS fault | 6:56 | 6:56 | 6:56 | 10:11 | 0 | 0 | 3.25 | 3.25 | checked related connection and parameter then rboot the inverter and start | Close | 0.021264 | 0.14544 | 267.6455 | PTW242808
1203 | 2024-08-06 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 6:56 | 19:16 | 12.3333 | IS15 | INV4 | M1 |  |  |  | 1 | 1 | IS15INV4M1 | 2192.4 | 0.6543% | Inverter | Inverter Unit tripped in INS fault | Inverter Unit tripped in INS fault | 6:56 | 6:56 | 6:56 | 10:43 | 0 | 0 | 3.7833 | 3.7833 | checked related connection and parameter then rboot the inverter and start | Close | 0.024753 | 0.18648 | 343.173 | PTW242808
1204 | 2024-08-06 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 6:56 | 19:16 | 12.3333 | IS16 | INV3 | M1 |  |  |  | 1 | 1 | IS16INV3M1 | 2129.76 | 0.6356% | Inverter | Inverter tripped under GFDI Fault | Inverter tripped under GFDI Fault | 6:56 | 6:56 | 6:56 | 19:16 | 0 | 0 | 12.3333 | 12.3333 | Due to Water logging inverter B/D could not attend | Close | 0.078388 | 0.87614 | 1566.286 | PTW242808
1205 | 2024-08-06 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 6:56 | 19:16 | 12.3333 | IS19 | INV2 | M1 |  |  |  | 1 | 1 | IS19INV2M1 | 2223.72 | 0.6636% | Inverter | Inverter tripped under GFDI Fault | Inverter tripped under GFDI Fault | 6:56 | 6:56 | 6:56 | 19:16 | 0 | 0 | 12.3333 | 12.3333 | Due to Water logging inverter B/D could not attend | Close | 0.081846 | 0.82898 | 1547.3577 | PTW242808
1206 | 2024-08-07 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 6:55 | 19:26 | 12.5167 | IS19 | INV2 | M1 |  |  |  | 1 | 1 | IS19INV2M1 | 2223.72 | 0.6636% | Inverter | Inverter tripped under GFDI Fault | Inverter tripped under GFDI Fault | 6:55 | 6:55 | 6:55 | 19:26 | 0 | 0 | 12.5167 | 12.5167 | After Genration checked cable IR testing work. | Close | 0.083063 | 2.7537 | 5140.0162 | PTW243117
1207 | 2024-08-08 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 6:41 | 19:29 | 12.8 | IS19 | INV2 | M1 |  |  |  | 1 | 1 | IS19INV2M1 | 2223.72 | 0.6636% | Inverter | Inverter tripped under GFDI Fault | Found SCB_2 positive DC cable faulty | 6:41 | 6:41 | 7:30 | 10:12 | 0 | 0.81667 | 3.5167 | 3.5167 | Found SCB_2 positive DC cable faulty | Close | 0.023337 | 0.85311 | 1592.404 | PTW243197
1208 | 2024-08-08 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 6:41 | 19:29 | 12.8 | IS19 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS19INV2M1SCB2 | 219.24 | 0.06543% | SCB | SCB-2 Stop due to DC cable faulty issue | SCB-2 Stop due to DC cable faulty issue | 10:12 | 10:12 | 10:12 | 19:29 | 0 | 0 |  | 9.2833 | SCB Cable Jointing work in progress | Open | 0.0060738 | 4.8914 | 900.1503 | PTW243197
1209 | 2024-08-09 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 6:39 | 19:16 | 12.6167 | IS19 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS19INV2M1SCB2 | 219.24 | 0.06543% | SCB | Manully stop due to cable rectification work | cable jointing work and check IR value & cable connect | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 | 12.6167 | 12.6167 | cable jointing work and check IR value & cable connect | Close | 0.0082547 | 6.1887 | 1138.9056 | PTW243378
1210 | 2024-08-11 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 6:49 | 19:26 | 12.6167 | IS2 | INV1 | M2 |  |  |  | 1 | 1 | IS2INV1M2 | 2090.61 | 0.6239% | Inverter | Inverter tripped under GFDI Fault | After Genration checked cable IR testing work. | 10:45 | 10:45 | 11:18 | 19:26 | 0 | 0.55 |  | 8.6833 | Inverter tripped under GFDI Fault | Open | 0.054175 | 4.4416 | 7794.2397 | PTW243598
1211 | 2024-08-11 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 6:49 | 19:26 | 12.6167 | IS5 | INV1 | M2 | SCB5 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | SCB | MC4 connector damage | MC4 connector Replaced. | 6:49 | 6:49 | 6:49 | 19:26 | 0 | 0 | 12.6167 | 12.6167 | MC4 connector Replaced. | Close | 0.00097178 | 5.58 | 120.8898
1212 | 2024-08-11 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 6:49 | 19:26 | 12.6167 | IS5 | INV4 | M2 | SCB8 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | SCB | MC4 connector damage | MC4 connector Replaced. | 6:49 | 6:49 | 6:49 | 19:26 | 0 | 0 | 12.6167 | 12.6167 | MC4 connector Replaced. | Close | 0.00097178 | 5.58 | 120.8898
1213 | 2024-08-12 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 6:41 | 19:25 | 12.7333 | IS2 | INV1 | M2 |  |  |  | 1 | 1 | IS2INV1M2 | 2090.61 | 0.6239% | Inverter | Inverter tripped under GFDI Fault | Due to water logging issue in all SCB area so fault not attend | 6:41 | 6:41 | 6:41 | 19:25 | 0 | 0 |  | 12.7333 | Inverter tripped under GFDI Fault | Open | 0.079442 | 5.8879 | 10332.4058 | PTW243673
1214 | 2024-08-12 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 6:40 | 18:40 | 12 | IS2 | INV1 | M2 |  |  |  | 1 | 1 | IS2INV1M2 | 2090.61 | 0.6239% | Inverter | Inverter tripped under GFDI Fault | Inverter tripped under GFDI Fault | 6:40 | 6:40 | 6:55 | 7:50 | 0 | 0.25 | 1.1667 | 1.1667 | checked related connection and parameter then rboot the inverter and start | Close | 0.0072788 | 0.12539 | 220.04 | PTW243673
1215 | 2024-08-15 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 7:06 | 19:18 | 12.2 | IS5 | INV4 | M1 |  |  |  | 1 | 1 | IS5INV4M1 | 2090.61 | 0.6239% | Inverter | Inverter tripped under GFDI Fault | Inverter tripped under GFDI Fault | 10:56 | 10:56 | 10:56 | 11:30 | 0 | 0 | 0.56667 | 0.56667 | Inverter Auto-Reset and Run | Close | 0.0035354 | 0.2858 | 501.5346 | PTW244149
1216 | 2024-08-16 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 7:15 | 18:50 | 11.5833 | IS7 | INV1 | M1 |  |  |  | 1 | 1 | IS7INV1M1 | 1973.16 | 0.5888% | Inverter | Inverter tripped under GFDI Fault | Inverter tripped under GFDI Fault | 7:04 | 7:04 | 7:04 | 9:35 | 0 | 0 | 2.5167 | 2.5167 | Inverter Auto-Reset and Run | Close | 0.014819 | 2.5167 | 4168.2491 | PTW244197
1217 | 2024-08-16 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 7:15 | 18:50 | 11.5833 | IS4 | INV4 | M2 |  |  |  | 1 | 1 | IS4INV4M2 | 2061.9 | 0.6153% | Inverter | Inverter tripped under GFDI Fault | Inverter tripped under GFDI Fault | 7:04 | 7:04 | 7:04 | 9:18 | 0 | 0 | 2.2333 | 2.2333 | Inverter Auto-Reset and Run | Close | 0.013742 | 2.2333 | 3865.3321 | PTW244197
1218 | 2024-08-16 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 7:15 | 18:50 | 11.5833 | IS5 | INV4 | M1 |  |  |  | 1 | 1 | IS5INV4M1 | 2090.61 | 0.6239% | Inverter | Inverter tripped under GFDI Fault | Inverter tripped under GFDI Fault | 7:04 | 7:04 | 7:04 | 12:45 | 0 | 0 | 5.6833 | 5.6833 | checked related connection and parameter then rboot the inverter and start | Close | 0.035458 | 5.6833 | 9973.3674 | PTW244197
1219 | 2024-08-16 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 7:15 | 18:50 | 11.5833 | IS7 | INV1 | M1 |  |  |  | 1 | 1 | IS7INV1M1 | 1973.16 | 0.5888% | Inverter | Inverter tripped under GFDI Fault | Inverter tripped under GFDI Fault | 13:58 | 13:58 | 13:58 | 17:00 | 0 | 0 | 3.0333 | 3.0333 | checked related connection and parameter then rboot the inverter and start | Close | 0.017862 | 3.0333 | 5023.9824 | PTW244197
1220 | 2024-08-16 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 7:15 | 18:50 | 11.5833 | IS7 | INV4 | M2 |  |  |  | 1 | 1 | IS7INV4M2 | 1973.16 | 0.5888% | Inverter | Inverter tripped under GFDI Fault | Inverter tripped under GFDI Fault | 7:04 | 7:04 | 7:04 | 9:22 | 0 | 0 | 2.3 | 2.3 | Inverter Auto-Reset and Run | Close | 0.013543 | 2.3 | 3809.3932 | PTW244197
1221 | 2024-08-16 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 7:15 | 18:50 | 11.5833 | IS5 | INV4 | M1 | SCB5 |  |  | 1 | 1 | IS5INV4M1SCB5 | 232.29 | 0.06932% | SCB | Isolated due to the inverter Ground Fault. | Isolated due to the inverter Ground Fault. | 12:45 | 12:45 | 12:45 | 18:50 | 0 | 0 |  | 6.0833 | Isolated due to the inverter Ground Fault. | Open | 0.0042171 | 6.0833 | 1186.145 | PTW244234
1222 | 2024-08-17 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 6:52 | 19:07 | 12.25 | IS6 | INV2 | M1 |  |  |  | 1 | 1 | IS6INV2M1 | 2203.13 | 0.6575% | Inverter | Inverter tripped under GFDI Fault | Inverter tripped under GFDI Fault | 7:24 | 7:24 | 7:24 | 10:01 | 0 | 0 | 2.6167 | 2.6167 | Inverter Auto-Reset and Run | Close | 0.017204 | 0.22959 | 424.586 | PTW244308
1223 | 2024-08-17 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 6:52 | 19:07 | 12.25 | IS15 | INV2 | M1 |  |  |  | 1 | 1 | IS15INV2M1 | 2004.48 | 0.5982% | Inverter | Inverter tripped under GFDI Fault | Inverter tripped under GFDI Fault | 7:24 | 7:24 | 7:24 | 14:30 | 0 | 0 | 7.1 | 7.1 | checked related connection and parameter then rboot the inverter and start | Close | 0.042471 | 1.8437 | 3102.0544 | PTW244308
1224 | 2024-08-17 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 6:52 | 19:07 | 12.25 | IS16 | INV2 | M1 |  |  |  | 1 | 1 | IS16INV2M1 | 2161.08 | 0.6449% | Inverter | Inverter tripped under GFDI Fault | Inverter tripped under GFDI Fault | 7:24 | 7:24 | 7:24 | 14:45 | 0 | 0 | 7.35 | 7.35 | checked related connection and parameter then rboot the inverter and start | Close | 0.047402 | 1.9336 | 3507.5986 | PTW244308
1225 | 2024-08-17 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 6:52 | 19:07 | 12.25 | IS19 | INV2 | M1 |  |  |  | 1 | 1 | IS19INV2M1 | 2223.72 | 0.6636% | Inverter | Inverter tripped under GFDI Fault | Inverter tripped under GFDI Fault | 7:24 | 7:24 | 7:24 | 14:50 | 0 | 0 | 7.4333 | 7.4333 | checked related connection and parameter then rboot the inverter and start | Close | 0.049329 | 2.0253 | 3780.3377 | PTW244308
1226 | 2024-08-23 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 6:44 | 19:05 | 12.35 | [5 empty] | Power_Tx1 | 0 | 1 | Power_Tx1 | 167322.75 | 49.93% | PTR | PTR tripped in WTI LV-2 temperature high | PTR tripped in WTI LV-2 temperature high | 13:51 | 13:51 | 14:20 | 15:36 | 0 | 0.48333 | 1.75 | 1.75 | Checked all parameters then charge | Close | 0.87384 | 1.3635 | 191504.0968 | PTW245242
1227 | 2024-09-04 | FY24 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 7:52 | 19:02 | 11.1667 | IS7 | INV1 | M2 |  |  |  | 1 | 1 | IS7INV1M2 | 1973.16 | 0.5888% | Inverter | Inverter tripped under GFDI Fault | Inverter tripped under GFDI Fault | 7:52 | 7:52 | 8:05 | 9:05 | 0 | 0.21667 | 1.2167 | 1.2167 | checked related connection and parameter then rboot the inverter and start | Close | 0.0071643 | 0.16901 | 276.2699 | PTW246796
1228 | 2024-09-07 | FY24 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 6:56 | 19:03 | 12.1167 | IS20 | INV1 | M2 | SCB5 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | SCB | Stiring cable found damage | MC4 connector apply and 50A fuse replace & restored the string. | 6:56 | 6:56 | 6:56 | 19:03 | 0 | 0 | 12.1167 | 12.1167 | MC4 connector apply and 50A fuse replace & restored the string. | Close | 0.0011325 | 6.7534 | 175.2264 | PTW247269
1229 | 2024-09-07 | FY24 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 6:56 | 19:03 | 12.1167 | IS14 | INV3 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | SCB | MC4 connector found damage | SCB nagetive side MC4 found dameged so replace the MC4 connector and restored the string. | 6:56 | 6:56 | 6:56 | 19:03 | 0 | 0 | 12.1167 | 12.1167 | SCB nagetive side MC4 found dameged so replace the MC4 connector and restored the string. | Close | 0.0011325 | 7.1897 | 186.5466 | PTW247269
1230 | 2024-09-07 | FY24 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 6:56 | 19:03 | 12.1167 | IS20 | INV2 | M1 | SCB2 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | SCB | MC4 connector found damage | Near by structure String cable found damage, MC4 connector apply and restored the string. | 6:56 | 6:56 | 6:56 | 19:03 | 0 | 0 | 12.1167 | 12.1167 | Near by structure String cable found damage, MC4 connector apply and restored the string. | Close | 0.0011325 | 6.7534 | 175.2264 | PTW247269
1231 | 2024-09-08 | FY24 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 6:58 | 19:01 | 12.05 | IS2 |  |  |  |  | Tx | 0 | 1 | IS2Tx | 16699.07 | 4.983% | IDT | IDT trip due to malfuntion | In relay no fault show and no alarm show in display. | 15:58 | 17:58 | 18:30 | 21:03 | 2 | 2.5333 | 5.0833 | 5.0833 | check related all parameter and IDT charge successfully. | Close | 0.25333 | 0.62189 | 8603.2175
1232 | 2024-09-11 | FY24 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 6:58 | 18:52 | 11.9 | IS7 | INV2 | M1 |  |  |  | 1 | 1 | IS7INV2M1 | 2098.44 | 0.6262% | Inverter | Inverter tripped under GFDI Fault | Inverter tripped under GFDI Fault | 15:33 | 15:33 | 15:33 | 15:48 | 0 | 0 | 0.25 | 0.25 | Inverter Auto-Reset and Run | Close | 0.0015656 | 0.014404 | 25.0394
1233 | 2024-09-11 | FY24 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 6:58 | 18:52 | 11.9 | IS2 | INV2 | M2 |  |  |  | 1 | 1 | IS2INV2M2 | 2090.61 | 0.6239% | Inverter | Inverter tripped under GFDI Fault | Inverter tripped under GFDI Fault | 15:33 | 15:33 | 15:33 | 16:19 | 0 | 0 | 0.76667 | 0.76667 | Inverter Auto-Reset and Run | Close | 0.0047832 | 0.059516 | 103.0772
1234 | 2024-09-16 | FY24 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 6:51 | 18:44 | 11.8833 | IS19 | INV1 |  |  |  |  | 1 | 1 | IS19INV1 | 4416.12 |  | Inverter | Fan abnormal alarm | Fan Not avilable in Sungrow Store | 6:51 | 6:51 | 6:51 | 18:44 | 0 | 0 |  | 11.8833 | Fan Not avilable in Sungrow Store | Open |  | 3.49 | 12767.9412 | PTW248705
1235 | 2024-09-17 | FY24 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 6:51 | 18:46 | 11.9167 | IS19 | INV1 |  |  |  |  | 1 | 1 | IS19INV1 | 4416.12 |  | Inverter | Fan abnormal alarm | Running on half load due to fan failuer. | 9:05 | 9:05 | 9:05 | 18:46 | 0 | 0 | 9.6833 | 9.6833 | Fan Replaced by OEM team | Close |  | 3.29 | 12036.254 | PTW248705
1236 | 2024-09-23 | FY24 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 6:56 | 18:39 | 11.7167 | IS2 | INV1 | M2 | SCB10 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | SCB | MC4 connector found damage | Near by structure String cable found damage, MC4 connector apply and restored the string. | 6:56 | 6:56 | 6:56 | 18:39 | 0 | 0 | 11.7167 | 11.7167 | Near by structure String cable found damage, MC4 connector apply and restored the string. | Close | 0.00090246 | 6.36 | 135.9877
1237 | 2024-09-29 | FY24 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 6:52 | 18:31 | 11.65 | IS1 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS1INV1M1SCB6 | 232.29 | 0.06932% | SCB | SCB Manully Stop due to IV Testing Work by testing team | SCB Manully Stop due to IV Testing Work by testing team | 15:09 | 15:09 | 15:09 | 15:25 | 0 | 0 | 0.26667 | 0.26667 | SCB Manully Stop due to IV Testing Work by testing team | Close | 0.00018486 | 0.19252 | 37.0477 | PTW250770
1238 | 2024-09-29 | FY24 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 6:52 | 18:31 | 11.65 | IS1 | INV2 | M1 | SCB1 |  |  | 1 | 1 | IS1INV2M1SCB1 | 232.29 | 0.06932% | SCB | SCB Manully Stop due to IV Testing Work by testing team | SCB Manully Stop due to IV Testing Work by testing team | 12:50 | 12:50 | 12:50 | 13:58 | 0 | 0 | 1.1333 | 1.1333 | SCB Manully Stop due to IV Testing Work by testing team | Close | 0.00078564 | 1.0657 | 205.0881 | PTW250770
1239 | 2024-10-01 | FY24 | 2024 | Year_3 | Year_3 | 2024-10-01 | 31 | 6:57 | 18:30 | 11.55 | IS6 | INV1 | M1 | SCB7 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | SCB | MC4 connector found burn. | MC4 connector Replaced. | 6:57 | 6:57 | 6:57 | 18:30 | 0 | 0 | 11.55 | 11.55 | MC4 connector Replaced. | Close | 0.0010795 | 6.5305 | 168.7879
1240 | 2024-10-16 | FY24 | 2024 | Year_3 | Year_3 | 2024-10-01 | 31 | 6:50 | 18:16 | 11.4333 | IS2 | INV2 | M2 | SCB1 |  |  | 1 | 1 | IS2INV2M2SCB1 | 232.29 | 0.06932% | SCB | SCB Breaker Break | SCB Breaker damage during grass cutting by tractor | 6:50 | 6:50 | 6:50 | 18:16 | 0 | 0 |  | 11.4333 | SCB Breaker damage during grass cutting by tractor | Open | 0.0079258 | 5.73 | 1098.3943
1241 | 2024-10-17 | FY24 | 2024 | Year_3 | Year_3 | 2024-10-01 | 31 | 6:49 | 18:13 | 11.4 | IS2 | INV2 | M2 | SCB1 |  |  | 1 | 1 | IS2INV2M2SCB1 | 232.29 | 0.06932% | SCB | SCB Breaker Break | SCB Breaker damage during grass cutting by tractor | 6:49 | 6:49 | 6:49 | 18:13 | 0 | 0 |  | 11.4 | SCB Breaker damage during grass cutting by tractor | Open | 0.0079026 | 6.3154 | 1210.6053
1242 | 2024-10-18 | FY24 | 2024 | Year_3 | Year_3 | 2024-10-01 | 31 | 7:00 | 18:12 | 11.2 | IS2 | INV2 | M2 | SCB1 |  |  | 1 | 1 | IS2INV2M2SCB1 | 232.29 | 0.06932% | SCB | SCB Breaker Break | SCB Breaker damage during grass cutting by tractor | 7:00 | 7:00 | 7:00 | 18:12 | 0 | 0 | 11.2 | 11.2 | SCB Replaced and charged | Close | 0.007764 | 5.44 | 1042.8037 | PTW255038
1243 | 2024-10-20 | FY24 | 2024 | Year_3 | Year_3 | 2024-10-01 | 31 | 6:58 | 18:11 | 11.2167 | IS17 | INV4 | M1 |  |  |  | 1 | 1 | IS17INV4M1 | 2004.48 | 0.5982% | Inverter | Inverter tripped under GFDI Fault | Inverter tripped under GFDI Fault | 16:55 | 16:55 | 17:20 | 18:00 | 0 | 0.41667 | 1.0833 | 1.0833 | Inverter Auto-Reset and Run | Close | 0.0064804 | 0.070205 | 116.1296
1244 | 2024-10-20 | FY24 | 2024 | Year_3 | Year_3 | 2024-10-01 | 31 | 6:58 | 18:11 | 11.2167 | IS17 | INV4 | M2 |  |  |  | 1 | 1 | IS17INV4M2 | 2004.48 | 0.5982% | Inverter | Inverter tripped under GFDI Fault | Inverter tripped under GFDI Fault | 16:55 | 16:55 | 17:20 | 18:00 | 0 | 0.41667 | 1.0833 | 1.0833 | Inverter Auto-Reset and Run | Close | 0.0064804 | 0.070205 | 116.1296
1245 | 2024-10-24 | FY24 | 2024 | Year_3 | Year_3 | 2024-10-01 | 31 | 6:58 | 18:08 | 11.1667 | IS9 | INV4 | M1 |  |  |  | 1 | 1 | IS9INV4M1 | 2244.31 | 0.6698% | Inverter | Inverter tripped in AC switch disconnection fault Unit-2 | Manualy stop for Inv Unit-2_AC Coil failure rectification | 8:58 | 8:58 | 8:58 | 9:32 | 0 | 0 | 0.56667 | 0.56667 | Manualy stop for Inv Unit-2_AC Coil failure rectification | Close | 0.0037953 | 0.74544 | 1380.5961 | PTW256198
1246 | 2024-10-24 | FY24 | 2024 | Year_3 | Year_3 | 2024-10-01 | 31 | 6:58 | 18:08 | 11.1667 | IS9 | INV4 | M2 |  |  |  | 1 | 1 | IS9INV4M2 | 1959.82 | 0.5849% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 7:04 | 7:04 | 7:30 | 9:32 | 0 | 0.43333 | 2.4667 | 2.4667 | Inverter tripped in AC switch disconnection fault | Close | 0.014427 | 0.30954 | 500.6122 | PTW256198
1247 | 2024-11-09 | FY24 | 2024 | Year_3 | Year_3 | 2024-11-01 | 30 | 7:09 | 18:00 | 10.85 | IS5 | INV2 | M1 |  |  |  | 1 | 1 | IS5INV2M1 | 2090.61 | 0.6239% | Inverter | Fan abnormal alarm | Running on half load due to fan failuer. | 14:00 | 14:00 | 14:00 | 18:00 | 0 | 0 | 4 | 4 | Fan Replaced by OEM team | Close | 0.024956 | 1.7744 | 3222.0189 | PTW259186
1248 | 2024-11-09 | FY24 | 2024 | Year_3 | Year_3 | 2024-11-01 | 30 | 7:09 | 18:00 | 10.85 | IS5 | INV2 | M2 |  |  |  | 1 | 1 | IS5INV2M2 | 2090.61 | 0.6239% | Inverter | Fan abnormal alarm | Running on half load due to fan failuer. | 14:00 | 14:00 | 14:00 | 18:00 | 0 | 0 | 4 | 4 | Fan Replaced by OEM team | Close | 0.024956 | 1.7744 | 3222.0189 | PTW259186
1249 | 2024-11-16 | FY24 | 2024 | Year_3 | Year_3 | 2024-11-01 | 30 | 7:15 | 17:55 | 10.6667 | [6 empty] | 1 | 1 | All Inverter | 328840.9 | 97.5% | Inverter | Due to SCADA Error All Inverter are off condition(PPC Set Point Zero so It's take off command continously. | Due to SCADA Error All Inverter are off condition(PPC Set Point Zero so It's take off command continously. | 7:15 | 7:15 | 7:15 | 9:00 | 0 | 0 | 1.75 | 1.75 | As discussed with PPC Team Resolved the issue | Close | 1.7063 | 0.28 | 79973.7335 | SCADA ERROR
1250 | 2024-11-26 | FY24 | 2024 | Year_3 | Year_3 | 2024-11-01 | 30 | 7:20 | 17:51 | 10.5167 | [5 empty] | MCR_MVP_OG2 | 0 | 1 | MCR_MVP_OG2 | 167768.915 | 50.07% | PTR | Outgoing-2 Trip due to emergency activated. | Outgoing-2 Trip due to emergency activated. | 12:30 | 12:30 | 12:30 | 12:32 | 0 | 0 | 0.033333 | 0.033333 | Release the emergency and charged outgoing-2 feeder & after one by one all incomer feeder charged. | Close | 0.016689 | 0.040822 | 5948.5573
1251 | 2024-11-26 | FY24 | 2024 | Year_3 | Year_3 | 2024-11-01 | 30 | 7:20 | 17:51 | 10.5167 | IS11 |  |  |  |  | Tx | 0 | 1 | IS11Tx | 16595.25 | 4.952% | IDT | Due to outgoing-2 emergency activate block ICOG Trip | Due to outgoing-2 emergency activate block ICOG Trip | 12:33 | 12:33 | 12:33 | 12:47 | 0 | 0 | 0.23333 | 0.23333 | Checked parameters then charge | Close | 0.011556 | 0.20422 | 2943.598
1252 | 2024-11-26 | FY24 | 2024 | Year_3 | Year_3 | 2024-11-01 | 30 | 7:20 | 17:51 | 10.5167 | IS12 |  |  |  |  | Tx | 0 | 1 | IS12Tx | 16912.8 | 5.047% | IDT | Due to outgoing-2 emergency activate block ICOG Trip | Due to outgoing-2 emergency activate block ICOG Trip | 12:33 | 12:33 | 12:33 | 12:59 | 0 | 0 | 0.43333 | 0.43333 | Checked parameters then charge | Close | 0.021871 | 0.36526 | 5365.5862
1253 | 2024-11-26 | FY24 | 2024 | Year_3 | Year_3 | 2024-11-01 | 30 | 7:20 | 17:51 | 10.5167 | IS14 |  |  |  |  | Tx | 0 | 1 | IS14Tx | 16756.2 | 5% | IDT | Due to outgoing-2 emergency activate block ICOG Trip | Due to outgoing-2 emergency activate block ICOG Trip | 12:33 | 12:33 | 12:33 | 13:10 | 0 | 0 | 0.61667 | 0.61667 | Checked parameters then charge | Close | 0.030836 | 0.50719 | 7381.6353
1254 | 2024-11-26 | FY24 | 2024 | Year_3 | Year_3 | 2024-11-01 | 30 | 7:20 | 17:51 | 10.5167 | IS20 |  |  |  |  | Tx | 0 | 1 | IS20Tx | 17539.2 | 5.234% | IDT | Due to outgoing-2 emergency activate block ICOG Trip | Due to outgoing-2 emergency activate block ICOG Trip | 12:33 | 12:33 | 12:33 | 13:04 | 0 | 0 | 0.51667 | 0.51667 | Checked parameters then charge | Close | 0.027043 | 0.4296 | 6544.5672
1255 | 2024-12-16 | FY24 | 2024 | Year_3 | Year_3 | 2024-12-01 | 31 | 7:30 | 17:58 | 10.4667 | IS20 | INV2 | M1 | SCB2 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | String Fuses | Y-connector fuse damage | Y-connector fuse damage | 6:00 | 6:00 | 6:00 | 6:40 | 0 | 0 | 0.66667 | 0.66667 | Y-Connector fuse Replaced. | Close | 6.2311e-05 | 5.76 | 160.2936 | PTW265928
1256 | 2024-12-24 | FY24 | 2024 | Year_3 | Year_3 | 2024-12-01 | 31 | 7:43 | 17:59 | 10.2667 | IS7 | INV2 | M2 |  |  |  | 1 | 1 | IS7INV2M2 | 2004.48 | 0.5982% | Inverter | Inverter tripped under GFDI Fault | Inverter tripped under GFDI Fault | 7:43 | 7:43 | 8:00 | 8:10 | 0 | 0.28333 | 0.45 | 0.45 | checked related connection and parameter then rboot the inverter and start | Close | 0.0026919 | 0.013561 | 24.153 | PTW267272
1257 | 2024-12-24 | FY24 | 2024 | Year_3 | Year_3 | 2024-12-01 | 31 | 7:43 | 17:59 | 10.2667 | IS10 | INV2 | M2 |  |  |  | 1 | 1 | IS10INV2M2 | 2223.72 | 0.6636% | Inverter | Inverter tripped under GFDI Fault | Inverter tripped under GFDI Fault | 7:43 | 7:43 | 8:00 | 9:08 | 0 | 0.28333 | 1.4167 | 1.4167 | checked related connection and parameter then rboot the inverter and start | Close | 0.0094012 | 0.12554 | 248.0419 | PTW267272
1258 | 2024-12-24 | FY24 | 2024 | Year_3 | Year_3 | 2024-12-01 | 31 | 7:43 | 17:59 | 10.2667 | IS13 | INV1 | M1 |  |  |  | 1 | 1 | IS13INV1M1 | 2004.48 | 0.5982% | Inverter | Inverter tripped under GFDI Fault | Inverter tripped under GFDI Fault | 7:43 | 7:43 | 8:00 | 9:19 | 0 | 0.28333 | 1.6 | 1.6 | checked related connection and parameter then rboot the inverter and start | Close | 0.009571 | 0.16281 | 289.9685 | PTW267272
1259 | 2024-12-24 | FY24 | 2024 | Year_3 | Year_3 | 2024-12-01 | 31 | 7:43 | 17:59 | 10.2667 | IS17 | INV4 | M1 |  |  |  | 1 | 1 | IS17INV4M1 | 2004.48 | 0.5982% | Inverter | Inverter tripped under GFDI Fault | Inverter tripped under GFDI Fault | 7:43 | 7:43 | 8:00 | 9:11 | 0 | 0.28333 | 1.4667 | 1.4667 | checked related connection and parameter then rboot the inverter and start | Close | 0.0087734 | 0.13502 | 240.4734 | PTW267272
1260 | 2024-12-29 | FY24 | 2024 | Year_3 | Year_3 | 2024-12-01 | 31 | 7:35 | 18:09 | 10.5667 | IS5 |  |  |  |  | Tx | 0 | 1 | IS5Tx | 16724.88 | 4.991% | Cables | Incomer-10(ICR-5 & 6) trip in O/C & E/F. | Due to ICR-6 cable end termination failure. | 13:16 | 13:16 | 13:34 | 14:58 | 0 | 0.3 | 1.7 | 1.7 | Checked parameters then charge | Close | 0.084849 | 1.3407 | 19924.0898 | PTW268371
1261 | 2024-12-29 | FY24 | 2024 | Year_3 | Year_3 | 2024-12-01 | 31 | 7:35 | 18:09 | 10.5667 | IS6 |  |  |  |  | Tx | 0 | 1 | IS6Tx | 17170.9 | 5.124% | Cables | Incomer-10(ICR-5 & 6) trip in O/C & E/F. | Due to ICR-6 cable end termination failure. | 13:16 | 13:16 | 13:34 | 18:09 | 0 | 0.3 | 4.8833 | 4.8833 | Cable end termination replace and cheaked all parameters then IDT charged. | Close | 0.25023 | 2.3467 | 35803.8799 | PTW268371
1262 | 2025-01-01 | FY25 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 7:33 | 18:05 | 10.5333 | IS7 |  |  |  |  | Tx | 0 | 1 | IS7Tx | 16443 | 4.907% | IDT | IDT_Manual stop for Thermography | IDT manual stop for thermography work | 14:08 | 14:08 | 14:08 | 14:33 | 0 | 0 | 0.41667 | 0.41667 | Thermography done and IDT charged | Close | 0.020446 | 0.33519 | 4878.4085 | PTW268885
1263 | 2025-01-02 | FY25 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 7:34 | 18:10 | 10.6 | IS7 | INV2 | M2 |  |  |  | 1 | 1 | IS7INV2M2 | 2004.48 | 0.5982% | Inverter | Inverter tripped under GFDI Fault | Inverter tripped under GFDI Fault | 16:40 | 16:40 | 17:02 | 18:10 | 0 | 0.36667 | 1.5 | 1.5 | checked related connection and parameter then rboot the inverter and start | Close | 0.0089728 | 0.14368 | 254.9187
1264 | 2025-01-11 | FY25 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 7:55 | 18:13 | 10.3 | IS15 | INV1 | M1 |  |  |  | 1 | 1 | IS15INV1M1 | 2004.48 | 0.5982% | Inverter | Inverter tripped under GFDI Fault | Inverter tripped under GFDI Fault | 8:25 | 8:25 | 8:32 | 9:05 | 0 | 0.11667 | 0.66667 | 0.66667 | checked related connection and parameter then rboot the inverter and start | Close | 0.0039879 | 0.093182 | 165.3238 | PTW270596
1265 | 2025-01-20 | FY25 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 7:42 | 18:18 | 10.6 | IS15 | INV2 | M1 |  |  |  | 1 | 1 | IS15INV2M1 | 2004.48 | 0.5982% | Inverter | Inverter tripped under GFDI Fault | Inverter tripped under GFDI Fault | 7:45 | 7:45 | 8:12 | 8:31 | 0 | 0.45 | 0.76667 | 0.76667 | checked related connection and parameter then rboot the inverter and start | Close | 0.0045861 | 0.057127 | 101.3552 | PTW272319
1266 | 2025-01-20 | FY25 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 7:42 | 18:18 | 10.6 | IS15 | INV3 | M1 |  |  |  | 1 | 1 | IS15INV3M1 | 2223.72 | 0.6636% | Inverter | Inverter tripped under GFDI Fault | Inverter tripped under GFDI Fault | 7:45 | 7:45 | 8:12 | 8:31 | 0 | 0.45 | 0.76667 | 0.76667 | checked related connection and parameter then rboot the inverter and start | Close | 0.0050877 | 0.057127 | 112.441 | PTW272319
1267 | 2025-02-04 | FY25 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 7:36 | 18:29 | 10.8833 | IS18 | INV3 | M1 |  |  |  | 1 | 1 | IS18INV3M1 | 2223.72 | 0.6636% | Inverter | Inverter Manully trip due to Isolation for IV Testing work | Inverter Manully trip due to Isolation for IV Testing work | 13:27 | 13:27 | 13:27 | 13:31 | 0 | 0 | 0.066667 | 0.066667 | After Complete work inverter restart | Close | 0.00044241 | 0.066667 | 125.9927 | PTW275690
1268 | 2025-02-04 | FY25 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 7:36 | 18:29 | 10.8833 | IS18 | INV3 | M2 |  |  |  | 1 | 1 | IS18INV3M2 | 1973.16 | 0.5888% | Inverter | Inverter Manully trip due to Isolation for IV Testing work | Inverter Manully trip due to Isolation for IV Testing work | 13:27 | 13:27 | 13:27 | 13:31 | 0 | 0 | 0.066667 | 0.066667 | After Complete work inverter restart | Close | 0.00039256 | 0.066667 | 111.7963 | PTW275690
1269 | 2025-02-10 | FY25 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 7:35 | 18:34 | 10.9833 | IS18 | INV3 | M1 |  |  |  | 1 | 1 | IS18INV3M1 | 2223.72 | 0.6636% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 7:35 | 7:35 | 7:35 | 11:04 | 0 | 0 | 3.4833 | 3.4833 | As per instruction Sungrow team AC Breaker manually discharge & PU reset then inverter start. | Close | 0.023116 | 1.2338 | 2331.8217 | PTW276747
1270 | 2025-02-10 | FY25 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 7:35 | 18:34 | 10.9833 | IS18 | INV3 | M2 |  |  |  | 1 | 1 | IS18INV3M2 | 1973.16 | 0.5888% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 8:21 | 8:21 | 8:21 | 9:51 | 0 | 0 | 1.5 | 1.5 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0088326 | 0.4778 | 801.25 | PTW276747
1271 | 2025-02-10 | FY25 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 7:35 | 18:34 | 10.9833 | IS18 | INV3 | M2 |  |  |  | 1 | 1 | IS18INV3M2 | 1973.16 | 0.5888% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 10:52 | 10:52 | 10:52 | 11:04 | 0 | 0 | 0.2 | 0.2 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0011777 | 0.14335 | 240.3873 | PTW276747
1272 | 2025-03-04 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:14 | 18:48 | 11.5667 | IS11 | INV3 | M1 |  |  |  | 1 | 1 | IS11INV3M1 | 2023.04 | 0.6037% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 7:14 | 7:14 | 7:14 | 8:51 | 0 | 0 | 1.6167 | 1.6167 | As per instruction Sungrow team AC coil replace and Breaker manually discharge & PU reset then inverter start. | Close | 0.0097603 | 0.37026 | 613.2695 | PTW280924
1273 | 2025-03-04 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:14 | 18:48 | 11.5667 | IS11 | INV3 | M2 |  |  |  | 1 | 1 | IS11INV3M2 | 2212.7 | 0.6603% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 7:54 | 7:54 | 7:54 | 8:51 | 0 | 0 | 0.95 | 0.95 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0062731 | 0.31253 | 566.1863 | PTW280924
1274 | 2025-03-04 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:14 | 18:48 | 11.5667 | [5 empty] | Power_Tx1 | 0 | 1 | Power_Tx1 | 167322.75 | 49.93% | PTR | PTR-1 Trip 64 LV REF protection stage-1 operated | Reptile found in outgoing LV panel then we cleaned burn spot and cheack the unwanted hole in panel & close. After we check IR value then PTR-1 charge. | 10:51 | 10:51 | 10:51 | 14:10 | 0 | 0 | 3.3167 | 3.3167 | Reptile found in outgoing LV panel then we cleaned burn spot and cheack the unwanted hole in panel & close. After we check IR value then PTR-1 charge. | Close | 1.6561 | 3.5252 | 482921.9126 | PTW281047
1275 | 2025-03-08 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:08 | 18:49 | 11.6833 | [5 empty] | Power_Tx1 | 0 | 1 | Power_Tx1 | 167322.75 | 49.93% | PTR | PTR-1 Trip 64 LV REF protection stage-1 operated | Y phase End termination replaced and Check related parameters, rectification work & voltage normlised then restored | 18:33 | 18:33 | 18:40 | 18:49 | 0 | 0.11667 | 0.26667 | 0.26667 | Y phase End termination replaced and Check related parameters, rectification work & voltage normlised then restored | Close | 0.13316 | 0.0024338 | 333.4141 | PTW281984
1276 | 2025-03-08 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:08 | 18:49 | 11.6833 | IS3 | INV1 | M2 |  |  |  | 1 | 1 | IS3INV1M2 | 2090.61 | 0.6239% | Inverter | Inv_tripped in GFDI Fault | checked related connection and parameter then rboot the inverter and start | 7:39 | 7:39 | 7:39 | 8:59 | 0 | 0 | 1.3333 | 1.3333 | checked related connection and parameter then rboot the inverter and start | Close | 0.0083186 | 0.34591 | 592.0745 | PTW281818
1277 | 2025-03-08 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:08 | 18:49 | 11.6833 | IS3 | INV1 | M1 |  |  |  | 1 | 1 | IS3INV1M1 | 2090.61 | 0.6239% | Inverter | Manualy stop for Inv Unit_ GFDI Fault rectification | Manualy stop for Inv Unit_ GFDI Fault rectification | 7:51 | 7:51 | 7:51 | 7:58 | 0 | 0 | 0.11667 | 0.11667 | Manualy stop for Inv Unit_ GFDI Fault rectification | Close | 0.00072788 | 0.019905 | 34.0701 | PTW281818
1278 | 2025-03-08 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:08 | 18:49 | 11.6833 | IS3 | INV1 | M1 |  |  |  | 1 | 1 | IS3INV1M1 | 2090.61 | 0.6239% | Inverter | Manualy stop for Inv Unit_ GFDI Fault rectification | Manualy stop for Inv Unit_ GFDI Fault rectification | 8:55 | 8:55 | 8:55 | 8:59 | 0 | 0 | 0.066667 | 0.066667 | Manualy stop for Inv Unit_ GFDI Fault rectification | Close | 0.00041593 | 0.03528 | 60.3865 | PTW281818
1279 | 2025-03-08 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:08 | 18:49 | 11.6833 | IS3 | INV1 | M2 | SCB10 |  |  | 1 | 1 | IS3INV1M2SCB10 | 0 | 0% | SCB | Manualy stop for Inv Unit_ GFDI Fault rectification | Manualy stop for Inv Unit_ GFDI Fault rectification | 8:59 | 8:59 | 8:59 | 10:15 | 0 | 0 | 1.2667 | 1.2667 | Manualy stop for Inv Unit_ GFDI Fault rectification | Close | 0 | 0.75396 | 0 | PTW281818
1280 | 2025-03-08 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:08 | 18:49 | 11.6833 | IS3 | INV1 | M2 | SCB10 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | SCB | MC4 connector found Burn | MC4 connector replaced and restored the string. | 10:15 | 10:15 | 10:15 | 18:49 | 0 | 0 | 8.5667 | 8.5667 | MC4 connector replaced and restored the string. | Close | 0.00065984 | 6.1717 | 130.4157 | PTW281984(During PTR-1 shutdown string fault attend)
1281 | 2025-03-09 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:07 | 18:48 | 11.6833 | IS15 | INV4 | M1 |  |  |  | 1 | 1 | IS15INV4M1 | 2192.4 | 0.6543% | Inverter | Inv_tripped in PM High Fault | Inv_tripped in PM High Fault | 13:42 | 13:42 | 14:15 | 15:42 | 0 | 0.55 | 2 | 2 | As per discussion and instruction by sungrow team checked related all parameter then reboot the inverter and start | Close | 0.013085 | 1.768 | 3173.5424 | PTW282144
1282 | 2025-03-09 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:07 | 18:48 | 11.6833 | IS15 | INV4 | M2 |  |  |  | 1 | 1 | IS15INV4M2 | 2004.48 | 0.5982% | Inverter | Manualy stop for Inv Unit_ PM High Fault rectification | Manualy stop for Inv Unit_ PM High Fault rectification | 15:39 | 15:39 | 15:39 | 15:42 | 0 | 0 | 0.05 | 0.05 | Manualy stop for Inv Unit_ PM High Fault rectification | Close | 0.00029909 | 0.047348 | 77.7042 | PTW282144
1283 | 2025-03-10 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:15 | 18:48 | 11.55 | IS15 | INV4 | M1 |  |  |  | 1 | 1 | IS15INV4M1 | 2192.4 | 0.6543% | Inverter | Inv_tripped in PM High Fault | Inv_tripped in PM High Fault | 11:17 | 11:17 | 11:17 | 11:19 | 0 | 0 | 0.033333 | 0.033333 | Inverter Auto-Reset and Run | Close | 0.00021809 | 0.04705 | 84.4535 | PTW282327
1284 | 2025-03-10 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:15 | 18:48 | 11.55 | IS15 | INV4 | M1 |  |  |  | 1 | 1 | IS15INV4M1 | 2192.4 | 0.6543% | Inverter | Inv_tripped in PM High Fault | Inv_tripped in PM High Fault | 11:47 | 11:47 | 11:47 | 15:52 | 0 | 0 | 4.0833 | 4.0833 | Inverter Auto-Reset and Run | Close | 0.026716 | 0.09995 | 179.4076 | PTW282327
1285 | 2025-03-10 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:15 | 18:48 | 11.55 | IS15 | INV4 | M1 |  |  |  | 1 | 1 | IS15INV4M1 | 2192.4 | 0.6543% | Inverter | Inv_tripped in PM High Fault | Inv_tripped in PM High Fault | 12:05 | 12:05 | 12:05 | 12:10 | 0 | 0 | 0.083333 | 0.083333 | Inverter Auto-Reset and Run | Close | 0.00054523 | 0.10123 | 181.7111 | PTW282327
1286 | 2025-03-10 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:15 | 18:48 | 11.55 | IS15 | INV4 | M1 |  |  |  | 1 | 1 | IS15INV4M1 | 2192.4 | 0.6543% | Inverter | Inv_tripped in PM High Fault | Inv_tripped in PM High Fault | 12:23 | 12:23 | 12:23 | 12:29 | 0 | 0 | 0.1 | 0.1 | checked related connection and parameter then rboot the inverter and start | Close | 0.00065427 | 0.11707 | 210.1315 | PTW282327
1287 | 2025-03-10 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:15 | 18:48 | 11.55 | IS15 | INV4 | M1 |  |  |  | 1 | 1 | IS15INV4M1 | 2192.4 | 0.6543% | Inverter | Inv_tripped in PM High Fault | Inv_tripped in PM High Fault | 12:40 | 12:40 | 12:40 | 12:43 | 0 | 0 | 0.05 | 0.05 | Inverter Auto-Reset and Run | Close | 0.00032714 | 0.067383 | 120.9513 | PTW282327
1288 | 2025-03-10 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:15 | 18:48 | 11.55 | IS15 | INV4 | M1 |  |  |  | 1 | 1 | IS15INV4M1 | 2192.4 | 0.6543% | Inverter | Inv_tripped in PM High Fault | Inv_tripped in PM High Fault | 12:54 | 12:54 | 12:54 | 13:02 | 0 | 0 | 0.13333 | 0.13333 | Inverter Auto-Reset and Run | Close | 0.00087236 | 0.1643 | 294.9141 | PTW282327
1289 | 2025-03-10 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:15 | 18:48 | 11.55 | IS15 | INV4 | M1 |  |  |  | 1 | 1 | IS15INV4M1 | 2192.4 | 0.6543% | Inverter | Inv_tripped in PM High Fault | Inv_tripped in PM High Fault | 13:30 | 13:30 | 13:30 | 13:42 | 0 | 0 | 0.2 | 0.2 | checked related connection and parameter then rboot the inverter and start | Close | 0.0013085 | 0.19526 | 350.4894 | PTW282327
1290 | 2025-03-10 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:15 | 18:48 | 11.55 | IS15 | INV4 | M2 |  |  |  | 1 | 1 | IS15INV4M2 | 2004.48 | 0.5982% | Inverter | Manualy stop for Inv Unit_1 PM High Fault rectification | Manualy stop for Inv Unit_1 PM High Fault rectification | 12:26 | 12:26 | 12:26 | 14:29 | 0 | 0 | 2.05 | 2.05 | Manualy stop for Inv Unit_1 PM High Fault rectification | Close | 0.012263 | 0.06735 | 110.5293 | PTW282327
1291 | 2025-03-10 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:15 | 18:48 | 11.55 | IS15 | INV4 | M2 |  |  |  | 1 | 1 | IS15INV4M2 | 2004.48 | 0.5982% | Inverter | Manualy stop for Inv Unit_1 PM High Fault rectification | Manualy stop for Inv Unit_1 PM High Fault rectification | 13:30 | 13:30 | 13:30 | 13:42 | 0 | 0 | 0.2 | 0.2 | Manualy stop for Inv Unit_1 PM High Fault rectification | Close | 0.0011964 | 0.19526 | 320.4475 | PTW282327
1292 | 2025-03-11 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:13 | 18:50 | 11.6167 | IS15 | INV4 | M1 |  |  |  | 1 | 1 | IS15INV4M1 | 2192.4 | 0.6543% | Inverter | Inv_tripped in PM High Fault | Inv_tripped in PM High Fault | 14:31 | 14:31 | 14:31 | 14:54 | 0 | 0 | 0.38333 | 0.38333 | Inverter Auto-Reset and Run | Close | 0.002508 | 0.27518 | 493.9347
1293 | 2025-03-11 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:13 | 18:50 | 11.6167 | IS10 | INV1 | M1 |  |  |  | 1 | 1 | IS10INV1M1 | 2067.12 | 0.6169% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 7:13 | 7:27 | 7:13 | 8:47 | 0.23333 | 0 | 1.5667 | 1.5667 | As per instruction Sungrow team AC Breaker manually discharge & PU reset then inverter start. | Close | 0.0096645 | 0.23773 | 402.3308 | PTW282398
1294 | 2025-03-11 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:13 | 18:50 | 11.6167 | IS10 | INV1 | M2 |  |  |  | 1 | 1 | IS10INV1M2 | 2098.44 | 0.6262% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 8:05 | 8:05 | 8:05 | 8:47 | 0 | 0 | 0.7 | 0.7 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0043836 | 0.18051 | 310.1216 | PTW282398
1295 | 2025-03-12 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:11 | 18:47 | 11.6 | IS15 |  |  |  |  | Tx | 0 | 1 | IS15Tx | 16756.2 | 5% | IDT | IDT trip due to loose connection back side of relay | IDT trip due to loose connection back side of relay | 8:50 | 8:50 | 9:02 | 9:17 | 0 | 0.2 | 0.45 | 0.45 | Relay reset and found loose connection back side of relay tightness done then IDT charge | Close | 0.022502 | 0.19997 | 2743.3331 | PTW282678
1296 | 2025-03-15 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:06 | 18:54 | 11.8 | IS11 | INV3 | M1 |  |  |  | 1 | 1 | IS11INV3M1 | 2023.04 | 0.6037% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 7:06 | 7:06 | 7:30 | 8:19 | 0 | 0.4 | 1.2167 | 1.2167 | As per instruction Sungrow team AC Breaker manually discharge & PU reset then inverter start. | Close | 0.0073454 | 0.1575 | 260.8736 | PTW283073
1297 | 2025-03-15 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:06 | 18:54 | 11.8 | IS11 | INV3 | M2 |  |  |  | 1 | 1 | IS11INV3M2 | 2212.7 | 0.6603% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 7:30 | 7:30 | 7:30 | 8:19 | 0 | 0 | 0.81667 | 0.81667 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0053927 | 0.14039 | 254.3356 | PTW283073
1298 | 2025-03-16 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:06 | 18:53 | 11.7833 | IS11 | INV3 | M1 |  |  |  | 1 | 1 | IS11INV3M1 | 2023.04 | 0.6037% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 7:06 | 7:06 | 7:18 | 7:41 | 0 | 0.2 | 0.58333 | 0.58333 | As per instruction Sungrow team AC Breaker manually discharge & PU reset then inverter start. | Close | 0.0035217 | 0.038659 | 64.0323 | PTW283187
1299 | 2025-03-16 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:06 | 18:53 | 11.7833 | IS11 | INV3 | M2 |  |  |  | 1 | 1 | IS11INV3M2 | 2212.7 | 0.6603% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 7:32 | 7:32 | 7:32 | 7:41 | 0 | 0 | 0.15 | 0.15 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.00099049 | 0.017345 | 31.4227 | PTW283187
1300 | 2025-03-20 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:02 | 18:55 | 11.8833 | IS11 | INV3 | M1 |  |  |  | 1 | 1 | IS11INV3M1 | 2023.04 | 0.6037% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 7:02 | 7:02 | 7:20 | 7:42 | 0 | 0.3 | 0.66667 | 0.66667 | As per instruction Sungrow team AC Breaker manually discharge & PU reset then inverter start. | Close | 0.0040249 | 0.029175 | 48.3232 | PTW283956
1301 | 2025-03-20 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:02 | 18:55 | 11.8833 | IS11 | INV3 | M2 |  |  |  | 1 | 1 | IS11INV3M2 | 2212.7 | 0.6603% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 7:29 | 7:29 | 7:29 | 7:42 | 0 | 0 | 0.21667 | 0.21667 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0014307 | 0.016465 | 29.8285 | PTW283956
1302 | 2025-03-21 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:01 | 18:56 | 11.9167 | IS11 | INV3 | M1 |  |  |  | 1 | 1 | IS11INV3M1 | 2023.04 | 0.6037% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 7:01 | 7:01 | 7:11 | 7:30 | 0 | 0.16667 | 0.48333 | 0.48333 | AC Breaker manually discharge & PU reset then inverter start. | Close | 0.002918 | 0.023135 | 38.3185 | PTW284158
1303 | 2025-03-21 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:01 | 18:56 | 11.9167 | IS11 | INV3 | M2 |  |  |  | 1 | 1 | IS11INV3M2 | 2212.7 | 0.6603% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 7:11 | 7:11 | 7:11 | 7:30 | 0 | 0 | 0.31667 | 0.31667 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.002091 | 0.019363 | 35.0782 | PTW284158
1304 | 2025-03-21 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:01 | 18:56 | 11.9167 | IS5 |  |  |  |  | Tx | 0 | 1 | IS5Tx | 16724.88 | 4.991% | IDT | Incomer-10(ICR-5 & 6) trip in O/C & E/F. | Due to ICR-6 cable end termination failure. | 11:16 | 11:16 | 11:35 | 12:43 | 0 | 0.31667 | 1.45 | 1.45 | Checked parameters then charge | Close | 0.072372 | 1.4211 | 19459.9216 | PTW284281
1305 | 2025-03-21 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:01 | 18:56 | 11.9167 | IS6 |  |  |  |  | Tx | 0 | 1 | IS6Tx | 17170.9 | 5.124% | IDT | Incomer-10(ICR-5 & 6) trip in O/C & E/F. | Due to ICR-6 cable end termination failure. | 11:16 | 11:16 | 11:35 | 18:56 | 0 | 0.31667 | 7.6667 | 7.6667 | Cable end termination replace and cheaked all parameters then IDT charged. | Close | 0.39286 | 5.0046 | 70356.5871 | PTW284289
1306 | 2025-03-23 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 6:58 | 18:56 | 11.9667 | IS10 | INV1 | M1 |  |  |  | 1 | 1 | IS10INV1M1 | 2067.12 | 0.6169% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 6:58 | 6:58 | 7:13 | 18:56 | 0 | 0.25 |  | 11.9667 | As per guidance sungrow team after generation we attend Block-10 Inverter-1 M_1 AC switch breaking fault and clean according to sungrow team after that we charge IDT and Check breaker SVG test but breaker showing fault. after that we reboot inverter and Now inverter kept in observation. | Open | 0.07382 | 7.52 | 12726.8723 | PTW284689
1307 | 2025-03-23 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 6:58 | 18:56 | 11.9667 | IS10 | INV1 | M2 |  |  |  | 1 | 1 | IS10INV1M2 | 2098.44 | 0.6262% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 7:13 | 7:13 | 7:13 | 8:38 | 0 | 0 | 1.4167 | 1.4167 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0088716 | 0.31 | 532.5942 | PTW284540
1308 | 2025-03-24 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 6:59 | 18:58 | 11.9833 | IS10 | INV1 | M1 |  |  |  | 1 | 1 | IS10INV1M1 | 2067.12 | 0.6169% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 6:59 | 6:59 | 6:59 | 18:58 | 0 | 0 | 11.9833 | 11.9833 | After Genration AC Breaker Replace with Sungrow Team. | Close | 0.073923 | 7.57 | 12811.4925 | PTW284913
1309 | 2025-03-24 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 6:59 | 18:58 | 11.9833 | IS5 | INV2 | M1 |  |  |  | 1 | 1 | IS5INV2M1 | 2090.61 | 0.6239% | Inverter | Inverter Manully Stop due to IV Testing Work | Inverter Manully Stop due to IV Testing Work | 13:00 | 13:00 | 13:00 | 13:06 | 0 | 0 | 0.1 | 0.1 | Inverter Manully Stop due to IV Testing Work | Close | 0.00062389 | 0.12 | 205.3962 | PTW284855
1310 | 2025-03-24 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 6:59 | 18:58 | 11.9833 | IS5 | INV2 | M2 |  |  |  | 1 | 1 | IS5INV2M2 | 2090.61 | 0.6239% | Inverter | Inverter Manully Stop due to IV Testing Work | Inverter Manully Stop due to IV Testing Work | 13:00 | 13:00 | 13:00 | 13:06 | 0 | 0 | 0.1 | 0.1 | Inverter Manully Stop due to IV Testing Work | Close | 0.00062389 | 0.12 | 205.3962 | PTW284855
1311 | 2025-04-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:43 | 19:04 | 12.35 | IS1 | INV4 | M2 |  |  |  | 1 | 1 | IS1INV4M2 | 2193.85 | 0.6547% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 6:43 | 6:43 | 6:54 | 7:17 | 0 | 0.18333 | 0.56667 | 0.56667 | AC Breaker manually discharge & PU reset then inverter start. | Close | 0.00371 | 0.026 | 45.9987 | PTW287226
1312 | 2025-04-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:43 | 19:04 | 12.35 | IS1 | INV4 | M1 |  |  |  | 1 | 1 | IS1INV4M1 | 2090.61 | 0.6239% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 7:06 | 7:06 | 7:06 | 7:17 | 0 | 0 | 0.18333 | 0.18333 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0011438 | 0.014 | 23.6029 | PTW287226
1312 | 2025-04-14 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:38 | 19:06 | 12.4667 | [5 empty] | Power_Tx1 | 0 | 1 | Power_Tx1 | 167322.75 | 49.93% | PTR | PTR-1 Trip in 86 activated. | PTR-1 Trip in 86 activated. | 22:58 | 22:58 | 23:36 | 4:25 | 0 | 0.63333 |  |  | PTR-01 tripped, and 86 was activated. Upon inspection, it was observed that one phase (Y Phase) was out, which led to a disturbance in the OLTC supply. Further investigation revealed a malfunction in the contactor. Necessary checks were carried out. The issue was resolved in coordination with the HT Team, and the transformer was restored to normal operation. | Close | 0 | 0 | 0 | PTW289015
1313 | 2025-04-15 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:35 | 19:05 | 12.5 | [5 empty] | Power_Tx1 | 0 | 1 | Power_Tx1 | 167322.75 | 49.93% | PTR | PTR-1 Trip and 86 activated. | PTR-1 Trip and 86 activated. | 11:34 | 11:34 | 11:47 | 12:32 | 0 | 0.21667 | 0.96667 | 0.96667 | After discussing with our HT team PTR1 Oltc put in manual mode and charge the PTR 1. | Close | 0.48269 | 0.94 | 126837.5797 | PTW289155
1314 | 2025-04-15 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:35 | 19:05 | 12.5 | [5 empty] | Power_Tx1 | 0 | 1 | Power_Tx1 | 167322.75 | 49.93% | PTR | PTR-1 Trip and 86 activated. | PTR-1 Trip and 86 activated. | 18:08 | 18:08 | 18:32 | 19:05 | 0 | 0.4 | 0.95 | 0.95 | After PTR-01 tripped Site Team and O2 Team checked the visually but no issue found. So, further checked its control circuit and found NIFPS PLC device malfunctioned and send continue signal to Master Relay 86.1, so bypassed the NIFPS tripping signal. Also parallely done transformer necessary testing and get satisfactory result. Finally, discussion with our HT Team charged the PTR-01 and its all incomers normally. Now PTR-01 keep under observation. | Close | 0.47437 | 0.047 | 6341.879 | PTW289207
1315 | 2025-04-16 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:33 | 19:06 | 12.55 | [5 empty] | Power_Tx1 | 0 | 1 | Power_Tx1 | 167322.75 | 49.93% | PTR | PTR-1 Trip and 86 activated. | PTR-1 Trip and 86 activated. | 6:33 | 6:33 | 6:33 | 6:46 | 0 | 0 | 0.21667 | 0.21667 | After PTR-01 tripped Site Team and O2 Team checked the visually but no issue found. So, further checked its control circuit and found NIFPS PLC device malfunctioned and send continue signal to Master Relay 86.1, so bypassed the NIFPS tripping signal. Also parallely done transformer necessary testing and get satisfactory result. Finally, discussion with our HT Team charged the PTR-01 and its all incomers normally. Now PTR-01 keep under observation. | Close | 0.10819 | 0.0046 | 620.6945 | PTW289207
1316 | 2025-04-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:26 | 19:12 | 12.7667 | IS4 | INV1 | M1 | SCB4 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 10:02 | 10:02 | 10:02 | 10:13 | 0 | 0 | 0.18333 | 0.18333 | String Manully shutdown for IV Testing work | Close | 1.428e-05 | 0.16113 | 3.3914 | PTW290892
1317 | 2025-04-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:26 | 19:12 | 12.7667 | IS4 | INV2 | M1 | SCB3 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 10:16 | 10:16 | 10:16 | 10:28 | 0 | 0 | 0.2 | 0.2 | String Manully shutdown for IV Testing work | Close | 1.5578e-05 | 0.1839 | 3.8707 | PTW290892
1318 | 2025-04-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:26 | 19:12 | 12.7667 | IS4 | INV3 | M1 | SCB6 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 10:40 | 10:40 | 10:40 | 10:53 | 0 | 0 | 0.21667 | 0.21667 | String Manully shutdown for IV Testing work | Close | 1.6876e-05 | 0.21328 | 4.4891 | PTW290892
1319 | 2025-04-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:26 | 19:12 | 12.7667 | IS4 | INV4 | M1 | SCB4 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:10 | 11:10 | 11:10 | 11:28 | 0 | 0 | 0.3 | 0.3 | String Manully shutdown for IV Testing work | Close | 2.3367e-05 | 0.31248 | 6.5771 | PTW290892
1320 | 2025-04-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:26 | 19:12 | 12.7667 | IS5 | INV1 | M1 | SCB6 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:45 | 11:45 | 11:45 | 11:53 | 0 | 0 | 0.13333 | 0.13333 | String Manully shutdown for IV Testing work | Close | 1.2578e-05 | 0.15543 | 3.9622 | PTW290892
1321 | 2025-04-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:26 | 19:12 | 12.7667 | IS5 | INV2 | M2 | SCB2 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:05 | 12:05 | 12:05 | 12:16 | 0 | 0 | 0.18333 | 0.18333 | String Manully shutdown for IV Testing work | Close | 1.7294e-05 | 0.21042 | 5.3638 | PTW290892
1322 | 2025-04-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:26 | 19:12 | 12.7667 | IS5 | INV3 | M1 | SCB4 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:25 | 12:25 | 12:25 | 12:35 | 0 | 0 | 0.16667 | 0.16667 | String Manully shutdown for IV Testing work | Close | 1.5722e-05 | 0.19703 | 5.0226 | PTW290892
1323 | 2025-04-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:26 | 19:12 | 12.7667 | IS5 | INV4 | M1 | SCB3 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:42 | 12:42 | 12:42 | 12:53 | 0 | 0 | 0.18333 | 0.18333 | String Manully shutdown for IV Testing work | Close | 1.7294e-05 | 0.21285 | 5.4258 | PTW290892
1324 | 2025-04-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:26 | 19:12 | 12.7667 | IS7 | INV1 | M1 | SCB4 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 14:03 | 14:03 | 14:03 | 14:22 | 0 | 0 | 0.31667 | 0.31667 | String Manully shutdown for IV Testing work | Close | 2.9598e-05 | 0.33362 | 8.4263 | PTW290892
1325 | 2025-04-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:26 | 19:12 | 12.7667 | IS7 | INV2 | M1 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 14:34 | 14:34 | 14:34 | 14:43 | 0 | 0 | 0.15 | 0.15 | String Manully shutdown for IV Testing work | Close | 1.402e-05 | 0.15852 | 4.0037 | PTW290892
1326 | 2025-04-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:26 | 19:12 | 12.7667 | IS7 | INV3 | M2 | SCB4 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 14:48 | 14:48 | 14:48 | 15:01 | 0 | 0 | 0.21667 | 0.21667 | String Manully shutdown for IV Testing work | Close | 2.0251e-05 | 0.20882 | 5.2741 | PTW290892
1327 | 2025-04-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:26 | 19:12 | 12.7667 | IS7 | INV4 | M2 | SCB7 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 15:06 | 15:06 | 15:06 | 15:24 | 0 | 0 | 0.3 | 0.3 | String Manully shutdown for IV Testing work | Close | 2.804e-05 | 0.26922 | 6.7997 | PTW290892
1328 | 2025-04-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:28 | 19:11 | 12.7167 | IS8 | INV1 | M2 | SCB8 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 10:30 | 10:30 | 10:30 | 10:41 | 0 | 0 | 0.18333 | 0.18333 | String Manully shutdown for IV Testing work | Close | 1.7136e-05 | 0.17552 | 4.4331 | PTW291131
1329 | 2025-04-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:28 | 19:11 | 12.7167 | IS8 | INV2 | M1 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 10:45 | 10:45 | 10:45 | 10:57 | 0 | 0 | 0.2 | 0.2 | String Manully shutdown for IV Testing work | Close | 1.8693e-05 | 0.19862 | 5.0165 | PTW291131
1330 | 2025-04-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:28 | 19:11 | 12.7167 | IS8 | INV3 | M1 | SCB8 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:00 | 11:00 | 11:00 | 11:10 | 0 | 0 | 0.16667 | 0.16667 | String Manully shutdown for IV Testing work | Close | 1.5578e-05 | 0.17423 | 4.4007 | PTW291131
1331 | 2025-04-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:28 | 19:11 | 12.7167 | IS8 | INV4 | M1 | SCB1 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:15 | 11:15 | 11:15 | 11:24 | 0 | 0 | 0.15 | 0.15 | String Manully shutdown for IV Testing work | Close | 1.1683e-05 | 0.1633 | 3.4371 | PTW291131
1332 | 2025-04-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:28 | 19:11 | 12.7167 | IS9 | INV1 | M1 | SCB6 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:28 | 11:28 | 11:28 | 11:40 | 0 | 0 | 0.2 | 0.2 | String Manully shutdown for IV Testing work | Close | 1.8867e-05 | 0.21728 | 5.5388 | PTW291131
1333 | 2025-04-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:28 | 19:11 | 12.7167 | IS9 | INV2 | M1 | SCB4 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:42 | 11:42 | 11:42 | 11:53 | 0 | 0 | 0.18333 | 0.18333 | String Manully shutdown for IV Testing work | Close | 1.7294e-05 | 0.20497 | 5.2248 | PTW291131
1334 | 2025-04-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:28 | 19:11 | 12.7167 | IS9 | INV3 | M1 | SCB7 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:57 | 11:57 | 11:57 | 12:07 | 0 | 0 | 0.16667 | 0.16667 | String Manully shutdown for IV Testing work | Close | 1.5722e-05 | 0.19012 | 4.8463 | PTW291131
1335 | 2025-04-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:28 | 19:11 | 12.7167 | IS9 | INV4 | M1 | SCB1 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:14 | 12:14 | 12:14 | 12:25 | 0 | 0 | 0.18333 | 0.18333 | String Manully shutdown for IV Testing work | Close | 1.7294e-05 | 0.20878 | 5.3221 | PTW291131
1336 | 2025-04-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:28 | 19:11 | 12.7167 | IS10 | INV1 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:35 | 12:35 | 12:35 | 12:44 | 0 | 0 | 0.15 | 0.15 | String Manully shutdown for IV Testing work | Close | 1.402e-05 | 0.17405 | 4.396 | PTW291131
1337 | 2025-04-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:28 | 19:11 | 12.7167 | IS10 | INV2 | M1 | SCB7 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:47 | 12:47 | 12:47 | 12:59 | 0 | 0 | 0.2 | 0.2 | String Manully shutdown for IV Testing work | Close | 1.8693e-05 | 0.22575 | 5.7018 | PTW291131
1338 | 2025-04-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:28 | 19:11 | 12.7167 | IS10 | INV3 | M2 | SCB2 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:06 | 13:06 | 13:06 | 13:15 | 0 | 0 | 0.15 | 0.15 | String Manully shutdown for IV Testing work | Close | 1.402e-05 | 0.17207 | 4.3459 | PTW291131
1339 | 2025-04-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:28 | 19:11 | 12.7167 | IS10 | INV4 | M1 | SCB8 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:18 | 13:18 | 13:18 | 13:29 | 0 | 0 | 0.18333 | 0.18333 | String Manully shutdown for IV Testing work | Close | 1.7136e-05 | 0.20537 | 5.187 | PTW291131
1340 | 2025-04-26 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:27 | 19:18 | 12.85 | IS19 |  |  |  |  | Tx | 0 | 1 | IS19Tx | 17570.52 | 5.244% | IDT | ICR-19 VCB trip in O/C & E/F. | Due to IDT-19 HV cable end termination failure. | 12:39 | 12:39 | 13:12 | 19:18 | 0 | 0.55 | 6.65 | 6.65 | Cable end termination replace and cheaked all parameters then IDT charged. | Close | 0.34869 | 3.9097 | 55397.8456 | PTW291363
1341 | 2025-04-26 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:27 | 19:18 | 12.85 | IS11 | INV1 | M2 | SCB5 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:58 | 11:58 | 11:58 | 12:13 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 2.3583e-05 | 0.2656 | 6.7705 | PTW291340
1342 | 2025-04-26 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:27 | 19:18 | 12.85 | IS11 | INV2 | M1 | SCB4 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:20 | 12:20 | 12:20 | 12:31 | 0 | 0 | 0.18333 | 0.18333 | String Manully shutdown for IV Testing work | Close | 1.7294e-05 | 0.2006 | 5.1135 | PTW291340
1343 | 2025-04-26 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:27 | 19:18 | 12.85 | IS11 | INV3 | M1 | SCB1 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:35 | 12:35 | 12:35 | 12:44 | 0 | 0 | 0.15 | 0.15 | String Manully shutdown for IV Testing work | Close | 1.415e-05 | 0.16588 | 4.2286 | PTW291340
1344 | 2025-04-26 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:27 | 19:18 | 12.85 | IS11 | INV4 | M1 | SCB7 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:50 | 12:50 | 12:50 | 12:59 | 0 | 0 | 0.15 | 0.15 | String Manully shutdown for IV Testing work | Close | 1.415e-05 | 0.16417 | 4.1848 | PTW291340
1345 | 2025-04-26 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:27 | 19:18 | 12.85 | IS12 | INV1 | M1 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:03 | 13:03 | 13:03 | 13:12 | 0 | 0 | 0.15 | 0.15 | String Manully shutdown for IV Testing work | Close | 1.402e-05 | 0.16362 | 4.1325 | PTW291340
1346 | 2025-04-26 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:27 | 19:18 | 12.85 | IS12 | INV2 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:20 | 13:20 | 13:20 | 13:31 | 0 | 0 | 0.18333 | 0.18333 | String Manully shutdown for IV Testing work | Close | 1.7136e-05 | 0.1917 | 4.8418 | PTW291340
1347 | 2025-04-26 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:27 | 19:18 | 12.85 | IS12 | INV3 | M2 | SCB7 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:34 | 13:34 | 13:34 | 13:45 | 0 | 0 | 0.18333 | 0.18333 | String Manully shutdown for IV Testing work | Close | 1.7136e-05 | 0.19295 | 4.8734 | PTW291340
1348 | 2025-04-26 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:27 | 19:18 | 12.85 | IS12 | INV4 | M2 | SCB4 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:51 | 13:51 | 13:51 | 14:02 | 0 | 0 | 0.18333 | 0.18333 | String Manully shutdown for IV Testing work | Close | 1.7136e-05 | 0.18493 | 4.6709 | PTW291340
1349 | 2025-04-28 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:24 | 19:15 | 12.85 | IS13 | INV1 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:55 | 11:55 | 11:55 | 12:07 | 0 | 0 | 0.2 | 0.2 | String Manully shutdown for IV Testing work | Close | 1.8693e-05 | 0.21632 | 5.4636 | PTW291748
1350 | 2025-04-28 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:24 | 19:15 | 12.85 | IS13 | INV2 | M1 | SCB3 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:10 | 12:10 | 12:10 | 12:21 | 0 | 0 | 0.18333 | 0.18333 | String Manully shutdown for IV Testing work | Close | 1.7136e-05 | 0.20387 | 5.1491 | PTW291748
1351 | 2025-04-28 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:24 | 19:15 | 12.85 | IS13 | INV3 | M2 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:26 | 12:26 | 12:26 | 12:36 | 0 | 0 | 0.16667 | 0.16667 | String Manully shutdown for IV Testing work | Close | 1.5578e-05 | 0.18787 | 4.745 | PTW291748
1352 | 2025-04-28 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:24 | 19:15 | 12.85 | IS13 | INV4 | M2 | SCB5 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:38 | 12:38 | 12:38 | 12:47 | 0 | 0 | 0.15 | 0.15 | String Manully shutdown for IV Testing work | Close | 1.402e-05 | 0.17047 | 4.3055 | PTW291748
1353 | 2025-04-28 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:24 | 19:15 | 12.85 | IS14 | INV1 | M2 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:02 | 13:02 | 13:02 | 13:13 | 0 | 0 | 0.18333 | 0.18333 | String Manully shutdown for IV Testing work | Close | 1.7136e-05 | 0.20227 | 5.1087 | PTW291748
1354 | 2025-04-28 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:24 | 19:15 | 12.85 | IS14 | INV2 | M2 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:20 | 13:20 | 13:20 | 13:31 | 0 | 0 | 0.18333 | 0.18333 | String Manully shutdown for IV Testing work | Close | 1.7136e-05 | 0.20093 | 5.075 | PTW291748
1355 | 2025-04-28 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:24 | 19:15 | 12.85 | IS14 | INV3 | M2 | SCB8 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:33 | 13:33 | 13:33 | 13:42 | 0 | 0 | 0.15 | 0.15 | String Manully shutdown for IV Testing work | Close | 1.402e-05 | 0.16383 | 4.138 | PTW291748
1356 | 2025-04-28 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:24 | 19:15 | 12.85 | IS14 | INV4 | M2 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:46 | 13:46 | 13:46 | 13:56 | 0 | 0 | 0.16667 | 0.16667 | String Manully shutdown for IV Testing work | Close | 1.5578e-05 | 0.17563 | 4.436 | PTW291748
1357 | 2025-04-29 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:25 | 19:17 | 12.8667 | IS15 | INV1 | M2 | SCB7 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 10:35 | 10:35 | 10:35 | 10:46 | 0 | 0 | 0.18333 | 0.18333 | String Manully shutdown for IV Testing work | Close | 1.7136e-05 | 0.15533 | 3.9231 | PTW291888
1358 | 2025-04-29 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:25 | 19:17 | 12.8667 | IS15 | INV2 | M2 | SCB8 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 10:51 | 10:51 | 10:51 | 11:01 | 0 | 0 | 0.16667 | 0.16667 | String Manully shutdown for IV Testing work | Close | 1.5578e-05 | 0.16387 | 4.1388 | PTW291888
1359 | 2025-04-29 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:25 | 19:17 | 12.8667 | IS15 | INV3 | M1 | SCB9 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:05 | 11:05 | 11:05 | 11:16 | 0 | 0 | 0.18333 | 0.18333 | String Manully shutdown for IV Testing work | Close | 1.7136e-05 | 0.16528 | 4.1745 | PTW291888
1360 | 2025-04-29 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:25 | 19:17 | 12.8667 | IS15 | INV4 | M1 | SCB7 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:21 | 11:21 | 11:21 | 11:33 | 0 | 0 | 0.2 | 0.2 | String Manully shutdown for IV Testing work | Close | 1.8693e-05 | 0.2065 | 5.2156 | PTW291888
1361 | 2025-04-29 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:25 | 19:17 | 12.8667 | IS16 | INV1 | M1 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:55 | 11:55 | 11:55 | 12:05 | 0 | 0 | 0.16667 | 0.16667 | String Manully shutdown for IV Testing work | Close | 1.5578e-05 | 0.18367 | 4.6389 | PTW291888
1362 | 2025-04-29 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:25 | 19:17 | 12.8667 | IS16 | INV2 | M2 | SCB5 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:13 | 12:13 | 12:13 | 12:24 | 0 | 0 | 0.18333 | 0.18333 | String Manully shutdown for IV Testing work | Close | 1.7136e-05 | 0.20125 | 5.083 | PTW291888
1363 | 2025-04-29 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:25 | 19:17 | 12.8667 | IS16 | INV3 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:35 | 12:35 | 12:35 | 12:46 | 0 | 0 | 0.18333 | 0.18333 | String Manully shutdown for IV Testing work | Close | 1.7136e-05 | 0.20648 | 5.2152 | PTW291888
1364 | 2025-04-29 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:25 | 19:17 | 12.8667 | IS16 | INV4 | M1 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:57 | 12:57 | 12:57 | 13:08 | 0 | 0 | 0.18333 | 0.18333 | String Manully shutdown for IV Testing work | Close | 1.7136e-05 | 0.17515 | 4.4238 | PTW291888
1365 | 2025-04-29 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:25 | 19:17 | 12.8667 | IS13 | INV4 | M2 | SCB4 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | String Fuses | Y-connector fuse damage | Y-connector fuse damage | 6:25 | 6:25 | 6:25 | 19:17 | 0 | 0 | 12.8667 | 12.8667 | Y-connector fuse Replaced. | Close | 0.00060131 | 7.05 | 89.032 | PTW292024
1366 | 2025-04-29 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:25 | 19:17 | 12.8667 | IS11 | INV2 | M1 | SCB2 | Str_Typ5(545*29) |  | 0 | 0 | Str_Typ5(545*29) | 15.805 | 0.004717% | Connectors | MC4 Connector found open | MC4 Connector found open | 6:25 | 6:25 | 6:25 | 19:17 | 0 | 0 | 12.8667 | 12.8667 | Mc4 connector connect properly | Close | 0.00060687 | 7.05 | 89.8563 | PTW292024
1367 | 2025-04-29 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:25 | 19:17 | 12.8667 | IS14 | INV4 | M1 | SCB9 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | String Fuses | Y-connector fuse damage | Y-connector fuse damage | 6:25 | 6:25 | 6:25 | 19:17 | 0 | 0 | 12.8667 | 12.8667 | Y-connector fuse Replaced. | Close | 0.00060131 | 7.05 | 89.032 | PTW292024
1368 | 2025-05-01 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:29 | 17:16 | 10.7833 | IS17 | INV1 | M1 | SCB8 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 10:02 | 10:02 | 10:02 | 10:13 | 0 | 0 | 0.18333 | 0.18333 | String Manully shutdown for IV Testing work | Close | 1.7136e-05 | 0.14257 | 3.6502 | PTW292263
1369 | 2025-05-01 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:29 | 17:16 | 10.7833 | IS17 | INV2 | M2 | SCB2 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 10:16 | 10:16 | 10:16 | 10:28 | 0 | 0 | 0.2 | 0.2 | String Manully shutdown for IV Testing work | Close | 1.8693e-05 | 0.16362 | 4.1893 | PTW292263
1370 | 2025-05-01 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:29 | 17:16 | 10.7833 | IS17 | INV3 | M2 | SCB3 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 10:40 | 10:40 | 10:40 | 10:53 | 0 | 0 | 0.21667 | 0.21667 | String Manully shutdown for IV Testing work | Close | 2.0251e-05 | 0.19213 | 4.9192 | PTW292263
1371 | 2025-05-01 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:29 | 17:16 | 10.7833 | IS17 | INV4 | M2 | SCB5 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:19 | 11:19 | 11:19 | 11:28 | 0 | 0 | 0.15 | 0.15 | String Manully shutdown for IV Testing work | Close | 1.402e-05 | 0.14928 | 3.8221 | PTW292263
1372 | 2025-05-01 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:29 | 17:16 | 10.7833 | IS18 | INV1 | M1 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:45 | 11:45 | 11:45 | 11:53 | 0 | 0 | 0.13333 | 0.13333 | String Manully shutdown for IV Testing work | Close | 1.2462e-05 | 0.14052 | 3.5976 | PTW292263
1373 | 2025-05-01 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:29 | 17:16 | 10.7833 | IS18 | INV2 | M1 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:05 | 12:05 | 12:05 | 12:16 | 0 | 0 | 0.18333 | 0.18333 | String Manully shutdown for IV Testing work | Close | 1.7136e-05 | 0.19172 | 4.9085 | PTW292263
1374 | 2025-05-01 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:29 | 17:16 | 10.7833 | IS18 | INV3 | M1 | SCB2 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:25 | 12:25 | 12:25 | 12:35 | 0 | 0 | 0.16667 | 0.16667 | String Manully shutdown for IV Testing work | Close | 1.5578e-05 | 0.17758 | 4.5467 | PTW292263
1375 | 2025-05-01 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:29 | 17:16 | 10.7833 | IS18 | INV4 | M1 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:42 | 12:42 | 12:42 | 12:53 | 0 | 0 | 0.18333 | 0.18333 | String Manully shutdown for IV Testing work | Close | 1.7136e-05 | 0.19448 | 4.9793 | PTW292263
1376 | 2025-05-02 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:25 | 19:09 | 12.7333 | IS12 | INV4 | M2 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Affected Due to Wind Strom. | String Affected Due to Wind Strom. | 6:25 | 6:25 | 6:25 | 19:09 | 0 | 0 | 12.7333 | 12.7333 | String Affected Due to Wind Strom. | Close | 0.00059507 | 6.52 | 83.4655 | PTW292403
1377 | 2025-05-02 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:25 | 19:09 | 12.7333 | IS11 | INV3 | M1 | SCB3 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Affected Due to Wind Strom. | String Affected Due to Wind Strom. | 6:25 | 6:25 | 6:25 | 19:09 | 0 | 0 | 12.7333 | 12.7333 | String Affected Due to Wind Strom. | Close | 0.00059507 | 6.52 | 83.4655 | PTW292403
1378 | 2025-05-02 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:25 | 19:09 | 12.7333 | IS6 | INV3 | M2 | SCB10 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Affected Due to Wind Strom. | String Affected Due to Wind Strom. | 6:25 | 6:25 | 6:25 | 19:09 | 0 | 0 | 12.7333 | 12.7333 | String Affected Due to Wind Strom. | Close | 0.00059507 | 6.52 | 83.4655 | PTW292403
1379 | 2025-05-02 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:25 | 19:09 | 12.7333 | IS6 | INV3 | M1 | SCB6 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Affected Due to Wind Strom. | String Affected Due to Wind Strom. | 6:25 | 6:25 | 6:25 | 19:09 | 0 | 0 | 12.7333 | 12.7333 | String Affected Due to Wind Strom. | Close | 0.00059507 | 6.52 | 83.4655 | PTW292403
1380 | 2025-05-02 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:25 | 19:09 | 12.7333 | IS6 | INV3 | M1 | SCB1 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Affected Due to Wind Strom. | String Affected Due to Wind Strom. | 6:25 | 6:25 | 6:25 | 19:09 | 0 | 0 | 12.7333 | 12.7333 | String Affected Due to Wind Strom. | Close | 0.00059507 | 6.52 | 83.4655 | PTW292403
1381 | 2025-05-02 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:25 | 19:09 | 12.7333 | IS6 | INV4 | M1 | SCB6 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Affected Due to Wind Strom. | String Affected Due to Wind Strom. | 6:25 | 6:25 | 6:25 | 19:09 | 0 | 0 | 12.7333 | 12.7333 | String Affected Due to Wind Strom. | Close | 0.00059507 | 6.52 | 83.4655 | PTW292403
1382 | 2025-05-02 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:25 | 19:09 | 12.7333 | IS13 | INV4 | M2 | SCB9 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Affected Due to Wind Strom. | String Affected Due to Wind Strom. | 6:25 | 6:25 | 6:25 | 19:09 | 0 | 0 | 12.7333 | 12.7333 | String Affected Due to Wind Strom. | Close | 0.00059507 | 6.52 | 83.4655 | PTW292403
1383 | 2025-05-02 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:25 | 19:09 | 12.7333 | IS7 | INV4 | M1 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Affected Due to Wind Strom. | String Affected Due to Wind Strom. | 6:25 | 6:25 | 6:25 | 19:09 | 0 | 0 | 12.7333 | 12.7333 | String Affected Due to Wind Strom. | Close | 0.00059507 | 6.52 | 83.4655 | PTW292403
1384 | 2025-05-02 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:25 | 19:09 | 12.7333 | IS4 | INV2 | M2 | SCB1 | Str_Typ2 (450*29) |  | 0 | 0 | Str_Typ2 (450*29) | 13.05 | 0.003894% | Connectors | String Affected Due to Wind Strom. | String Affected Due to Wind Strom. | 6:25 | 6:25 | 6:25 | 19:09 | 0 | 0 | 12.7333 | 12.7333 | String Affected Due to Wind Strom. | Close | 0.0004959 | 6.52 | 69.5546 | PTW292403
1385 | 2025-05-02 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:25 | 19:09 | 12.7333 | IS16 | INV4 | M2 | SCB7 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Affected Due to Wind Strom. | String Affected Due to Wind Strom. | 6:25 | 6:25 | 6:25 | 19:09 | 0 | 0 | 12.7333 | 12.7333 | String Affected Due to Wind Strom. | Close | 0.00059507 | 6.52 | 83.4655 | PTW292403
1386 | 2025-05-02 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:25 | 19:09 | 12.7333 | IS3 | INV3 | M2 | SCB2 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Connectors | String Affected Due to Wind Strom. | String Affected Due to Wind Strom. | 6:25 | 6:25 | 6:25 | 19:09 | 0 | 0 | 12.7333 | 12.7333 | String Affected Due to Wind Strom. | Close | 0.00049039 | 6.52 | 68.7818 | PTW292403
1387 | 2025-05-02 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:25 | 19:09 | 12.7333 | IS18 | INV4 | M2 | SCB6 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Affected Due to Wind Strom. | String Affected Due to Wind Strom. | 6:25 | 6:25 | 6:25 | 19:09 | 0 | 0 | 12.7333 | 12.7333 | String Affected Due to Wind Strom. | Close | 0.00059507 | 6.52 | 83.4655 | PTW292403
1388 | 2025-05-02 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:25 | 19:09 | 12.7333 | IS18 | INV4 | M2 | SCB6 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Affected Due to Wind Strom. | String Affected Due to Wind Strom. | 6:25 | 6:25 | 6:25 | 19:09 | 0 | 0 | 12.7333 | 12.7333 | String Affected Due to Wind Strom. | Close | 0.00059507 | 6.52 | 83.4655 | PTW292403
1389 | 2025-05-02 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:25 | 19:09 | 12.7333 | IS17 | INV1 | M1 | SCB1 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Affected Due to Wind Strom. | String Affected Due to Wind Strom. | 6:25 | 6:25 | 6:25 | 19:09 | 0 | 0 | 12.7333 | 12.7333 | String Affected Due to Wind Strom. | Close | 0.00059507 | 6.52 | 83.4655 | PTW292403
1390 | 2025-05-02 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:25 | 19:09 | 12.7333 | IS19 | INV1 | M1 | SCB8 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Affected Due to Wind Strom. | String Affected Due to Wind Strom. | 6:25 | 6:25 | 6:25 | 19:09 | 0 | 0 | 12.7333 | 12.7333 | String Affected Due to Wind Strom. | Close | 0.00059507 | 6.52 | 83.4655 | PTW292403
1391 | 2025-05-02 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:25 | 19:09 | 12.7333 | IS20 | INV4 | M1 | SCB7 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Affected Due to Wind Strom. | String Affected Due to Wind Strom. | 6:25 | 6:25 | 6:25 | 19:09 | 0 | 0 | 12.7333 | 12.7333 | String Affected Due to Wind Strom. | Close | 0.00059507 | 6.52 | 83.4655 | PTW292403
1392 | 2025-05-02 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:25 | 19:09 | 12.7333 | IS20 | INV2 | M2 | SCB6 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Affected Due to Wind Strom. | String Affected Due to Wind Strom. | 6:25 | 6:25 | 6:25 | 19:09 | 0 | 0 | 12.7333 | 12.7333 | String Affected Due to Wind Strom. | Close | 0.00059507 | 6.52 | 83.4655 | PTW292403
1393 | 2025-05-02 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:25 | 19:09 | 12.7333 | IS20 | INV2 | M1 | SCB7 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Affected Due to Wind Strom. | String Affected Due to Wind Strom. | 6:25 | 6:25 | 6:25 | 19:09 | 0 | 0 | 12.7333 | 12.7333 | String Affected Due to Wind Strom. | Close | 0.00059507 | 6.52 | 83.4655 | PTW292403
1394 | 2025-05-02 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:25 | 19:09 | 12.7333 | IS20 | INV3 | M2 | SCB5 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Affected Due to Wind Strom. | String Affected Due to Wind Strom. | 6:25 | 6:25 | 6:25 | 19:09 | 0 | 0 | 12.7333 | 12.7333 | String Affected Due to Wind Strom. | Close | 0.00059507 | 6.52 | 83.4655 | PTW292403
1395 | 2025-05-03 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:35 | 19:20 | 12.75 | IS19 | INV1 | M1 |  |  |  | 1 | 1 | IS19INV1M1 | 2161.08 | 0.6449% | Inverter | Fan abnormal alarm | Running on half load due to fan failuer. | 14:00 | 14:00 | 14:00 | 19:20 | 0 | 0 | 5.3333 | 5.3333 | After Genration Fan Replace by OEM Team. | Close | 0.034396 | 2.61 | 4610.8295 | PTW292723
1396 | 2025-05-03 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:35 | 19:20 | 12.75 | IS19 | INV1 | M2 |  |  |  | 1 | 1 | IS19INV1M2 | 2255.04 | 0.673% | Inverter | Fan abnormal alarm | Running on half load due to fan failuer. | 14:00 | 14:00 | 14:00 | 19:20 | 0 | 0 | 5.3333 | 5.3333 | After Genration Fan Replace by OEM Team. | Close | 0.035891 | 2.61 | 4811.3004 | PTW292723
1397 | 2025-05-04 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:28 | 19:14 | 12.7667 | IS11 | INV3 | M2 | SCB9 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Connectors | Y-connector fuse damage | Y-connector fuse damage | 6:28 | 6:28 | 6:28 | 19:14 | 0 | 0 | 12.7667 | 12.7667 | Y-connector fuse Replaced. | Close | 0.0012043 | 6.89 | 178.0375 | PTW292890
1398 | 2025-05-04 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:28 | 19:14 | 12.7667 | IS20 | INV2 | M1 | SCB4 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | MC4 Connector found open | MC4 Connector found open | 6:28 | 6:28 | 6:28 | 19:14 | 0 | 0 | 12.7667 | 12.7667 | Mc4 connector connect properly | Close | 0.00059663 | 6.89 | 88.2021 | PTW292890
1399 | 2025-05-04 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:28 | 19:14 | 12.7667 | IS6 | INV3 | M2 | SCB2 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | MC4 Connector found open | MC4 Connector found open | 6:28 | 6:28 | 6:28 | 19:14 | 0 | 0 | 12.7667 | 12.7667 | Mc4 connector connect properly | Close | 0.00059663 | 6.89 | 88.2021 | PTW292890
1400 | 2025-05-05 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 7:28 | 19:13 | 11.75 | IS20 | INV3 | M1 |  |  |  | 1 | 1 | IS20INV3M1 | 2255.04 | 0.673% | Inverter | Inverter Unit tripped in INS fault | Inverter Unit tripped in INS fault | 7:28 | 7:28 | 7:28 | 8:10 | 0 | 0 | 0.7 | 0.7 | checked related connection and parameter then rboot the inverter and start | Close | 0.0047107 | 0.033891 | 62.4753 | PTW292903
1401 | 2025-05-05 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 7:28 | 19:13 | 11.75 | IS19 | INV3 | M1 |  |  |  | 1 | 1 | IS19INV3M1 | 2223.72 | 0.6636% | Inverter | Inverter Unit tripped in INS fault | Inverter Unit tripped in INS fault | 7:28 | 7:28 | 7:28 | 8:17 | 0 | 0 | 0.81667 | 0.81667 | checked related connection and parameter then rboot the inverter and start | Close | 0.0054195 | 0.049313 | 89.6412 | PTW292903
1402 | 2025-05-05 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 7:28 | 19:13 | 11.75 | IS15 | INV3 | M1 |  |  |  | 1 | 1 | IS15INV3M1 | 2223.72 | 0.6636% | Inverter | Inverter Unit tripped in INS fault | Inverter Unit tripped in INS fault | 7:28 | 7:28 | 7:28 | 8:31 | 0 | 0 | 1.05 | 1.05 | checked related connection and parameter then rboot the inverter and start | Close | 0.006968 | 0.098206 | 178.5187 | PTW292903
1403 | 2025-05-05 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 7:28 | 19:13 | 11.75 | IS13 | INV1 | M1 |  |  |  | 1 | 1 | IS13INV1M1 | 2004.48 | 0.5982% | Inverter | Inverter Unit tripped in INS fault | Inverter Unit tripped in INS fault | 7:28 | 7:28 | 7:28 | 8:16 | 0 | 0 | 0.8 | 0.8 | checked related connection and parameter then rboot the inverter and start | Close | 0.0047855 | 0.052687 | 86.3325 | PTW292903
1404 | 2025-05-05 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 7:28 | 19:13 | 11.75 | [5 empty] | Power_Tx1 | 0 | 1 | Power_Tx1 | 167322.75 | 49.93% | PTR | PTR-1 Trip in Differencial Protection | PTR-1 Trip in Differencial Protection | 14:13 | 14:13 | 14:29 | 15:05 | 0 | 0.26667 | 0.86667 | 0.86667 | After IR Testing & CT connection check, after discussed with our HT Team charged the PTR-1 Normally. | Close | 0.43276 | 0.73943 | 101139.5346 | PTW293037
1405 | 2025-05-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:20 | 19:16 | 12.9333 | IS13 | INV1 | M1 |  |  |  | 1 | 1 | IS13INV1M1 | 2004.48 | 0.5982% | Inverter | Inverter tripped under GFDI Fault | Inverter tripped under GFDI Fault | 7:28 | 7:28 | 7:36 | 7:59 | 0 | 0.13333 | 0.51667 | 0.51667 | One Nos. Module found is ground, so bypass the module and restart the inverter. | Close | 0.0030906 | 0.13064 | 214.065 | PTW293345
1406 | 2025-05-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:20 | 19:16 | 12.9333 | IS13 | INV1 | M2 |  |  |  | 1 | 1 | IS13INV1M2 | 2004.48 | 0.5982% | Inverter | Manualy stop for Inv Unit_ GFDI Fault rectification | Manualy stop for Inv Unit_ GFDI Fault rectification | 7:38 | 7:38 | 7:38 | 7:59 | 0 | 0 | 0.35 | 0.35 | Manualy stop for Inv Unit_ GFDI Fault rectification | Close | 0.0020937 | 0.09626 | 157.7304 | PTW293345
1407 | 2025-05-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:20 | 19:16 | 12.9333 | IS5 | INV4 | M1 | SCB5 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:20 | NA | NA | 19:16 |  |  |  | 12.9333 |  | Open | 0.00099618 | 7.21 | 152.1216 | PTW293405
1408 | 2025-05-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:20 | 19:16 | 12.9333 | IS5 | INV4 | M1 | SCB8 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:20 | NA | NA | 19:16 |  |  |  | 12.9333 |  | Open | 0.00099618 | 7.21 | 152.1216 | PTW293405
1409 | 2025-05-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:20 | 19:16 | 12.9333 | IS6 | INV3 | M2 | SCB7 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:20 | NA | NA | 19:16 |  |  |  | 12.9333 |  | Open | 0.0012088 | 7.21 | 184.597 | PTW293405
1410 | 2025-05-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:20 | 19:16 | 12.9333 | IS6 | INV3 | M1 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:20 | NA | NA | 19:16 |  |  |  | 12.9333 |  | Open | 0.0012088 | 7.21 | 184.597 | PTW293405
1411 | 2025-05-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:20 | 19:16 | 12.9333 | IS9 | INV3 | M1 | SCB6 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:20 | NA | NA | 19:16 |  |  |  | 12.9333 |  | Open | 0.00122 | 7.21 | 186.3063 | PTW293405
1412 | 2025-05-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:20 | 19:16 | 12.9333 | IS20 | INV2 | M1 | SCB2 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:20 | NA | NA | 19:16 |  |  |  | 12.9333 |  | Open | 0.0012088 | 7.21 | 184.597 | PTW293405
1413 | 2025-05-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:20 | 19:16 | 12.9333 | IS20 | INV2 | M1 | SCB2 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:20 | NA | NA | 19:16 |  |  |  | 12.9333 |  | Open | 0.0012088 | 7.21 | 184.597 | PTW293405
1414 | 2025-05-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:20 | 19:16 | 12.9333 | IS20 | INV2 | M1 | SCB3 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:20 | NA | NA | 19:16 |  |  |  | 12.9333 |  | Open | 0.0012088 | 7.21 | 184.597 | PTW293405
1415 | 2025-05-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:20 | 19:16 | 12.9333 | IS20 | INV2 | M2 | SCB8 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:20 | NA | NA | 19:16 |  |  |  | 12.9333 |  | Open | 0.0012088 | 7.21 | 184.597 | PTW293405
1416 | 2025-05-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:20 | 19:16 | 12.9333 | IS19 | INV4 | M1 | SCB9 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:20 | NA | NA | 19:16 |  |  |  | 12.9333 |  | Open | 0.0012088 | 7.21 | 184.597 | PTW293405
1417 | 2025-05-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:20 | 19:16 | 12.9333 | IS3 | INV2 | M2 | SCB6 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:20 | NA | NA | 19:16 |  |  |  | 12.9333 |  | Open | 0.00099618 | 7.21 | 152.1216 | PTW293405
1418 | 2025-05-08 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:23 | 19:12 | 12.8167 | IS4 | INV1 | M2 | SCB2 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:23 | NA | NA | 19:12 |  |  |  | 12.8167 |  | Open | 0.00099828 | 6.9 | 147.2168 | PTW293628
1419 | 2025-05-08 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:23 | 19:12 | 12.8167 | IS8 | INV4 | M1 | SCB1 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:23 | NA | NA | 19:12 |  |  |  | 12.8167 |  | Open | 0.00099828 | 6.9 | 147.2168 | PTW293628
1420 | 2025-05-08 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:23 | 19:12 | 12.8167 | IS2 | INV3 | M2 | SCB7 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:23 | NA | NA | 19:12 |  |  |  | 12.8167 |  | Open | 0.00098719 | 6.9 | 145.581 | PTW293628
1421 | 2025-05-08 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:23 | 19:12 | 12.8167 | IS13 | INV3 | M2 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:23 | NA | NA | 19:12 |  |  |  | 12.8167 |  | Open | 0.0011979 | 6.9 | 176.6601 | PTW293628
1422 | 2025-05-08 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:23 | 19:12 | 12.8167 | IS4 | INV4 | M1 | SCB1 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:23 | NA | NA | 19:12 |  |  |  | 12.8167 |  | Open | 0.00099828 | 6.9 | 147.2168 | PTW293628
1423 | 2025-05-09 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:44 | 19:17 | 12.55 | IS2 | INV1 | M2 | SCB9 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | SCB | Stiring cable found damage | Stiring cable found damage | 6:44 | 6:44 | 6:44 | 19:17 | 0 | 0 | 12.55 | 12.55 | MC4 connector apply and fuse replace & restored the string. | Close | 0.00096665 | 6.5 | 137.1416 | PTW293802
1424 | 2025-05-09 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:44 | 19:17 | 12.55 | IS12 | INV2 | M1 | SCB7 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | MC4 Connector Found Open | MC4 Connector Found Open | 6:44 | 6:44 | 6:44 | 19:17 | 0 | 0 | 12.55 | 12.55 | MC4 Connector Connect properly. | Close | 0.00058651 | 6.5 | 83.2095 | PTW293802
1425 | 2025-05-09 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:44 | 19:17 | 12.55 | IS11 | INV1 | M1 | SCB2 | Str_Typ5(545*29) |  | 0 | 0 | Str_Typ5(545*29) | 15.805 | 0.004717% | Connectors | MC4 Connector Found Burn | MC4 Connector Found Burn | 6:44 | 6:44 | 6:44 | 19:17 | 0 | 0 | 12.55 | 12.55 | MC4 Connector Replace. | Close | 0.00059194 | 6.5 | 83.9799 | PTW293802
1426 | 2025-05-14 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:20 | 13.0167 | IS7 |  |  |  |  | Tx | 0 | 1 | IS7Tx | 16443 | 4.907% | IDT | IDT_Manual stop for LV Side Thermography | IDT manual stop for thermography work | 12:56 | 12:56 | 12:56 | 13:13 | 0 | 0 | 0.28333 | 0.28333 | After LV Box Cover Open IDT Charged. | Close | 0.013903 | 0.3 | 4032.4596 | PTW295047
1427 | 2025-05-14 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:20 | 13.0167 | IS7 |  |  |  |  | Tx | 0 | 1 | IS7Tx | 16443 | 4.907% | IDT | IDT_Manual stop for LV Side Thermography | IDT manual stop for thermography work | 13:37 | 13:37 | 13:37 | 13:49 | 0 | 0 | 0.2 | 0.2 | After thermography work done IDT Charged. | Close | 0.0098141 | 0.21 | 2822.7217 | PTW295047
1428 | 2025-05-15 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:19 | 13.0167 | IS9 | INV1 | M2 | SCB9 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:13 | 12:13 | 12:13 | 12:52 | 0 | 0 | 0.65 | 0.65 | String Manully shutdown for IV Testing work | Close | 6.0754e-05 | 0.6501 | 16.6445 | PTW295240
1429 | 2025-05-15 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:19 | 13.0167 | IS9 | INV1 | M2 | SCB9 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:55 | 12:55 | 12:55 | 13:46 | 0 | 0 | 0.85 | 0.85 | String Manully shutdown for IV Testing work | Close | 7.9447e-05 | 0.82918 | 21.2295 | PTW295240
1430 | 2025-05-18 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:22 | 13.05 | IS13 | INV3 | M2 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | NA | NA | 19:22 |  |  |  | 13.05 |  | Open | 0.0012197 | 7.48 | 191.5098 | PTW295805
1431 | 2025-05-18 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:22 | 13.05 | IS6 | INV3 | M2 | SCB7 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | NA | NA | 19:22 |  |  |  | 13.05 |  | Open | 0.0012197 | 7.48 | 191.5098 | PTW295805
1432 | 2025-05-18 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:22 | 13.05 | IS6 | INV3 | M1 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | NA | NA | 19:22 |  |  |  | 13.05 |  | Open | 0.0012197 | 7.48 | 191.5098 | PTW295805
1433 | 2025-05-18 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:22 | 13.05 | IS9 | INV3 | M1 | SCB6 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | NA | NA | 19:22 |  |  |  | 13.05 |  | Open | 0.001231 | 7.48 | 193.2831 | PTW295805
1434 | 2025-05-18 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:22 | 13.05 | IS5 | INV4 | M1 | SCB5 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | NA | NA | 19:22 |  |  |  | 13.05 |  | Open | 0.0010052 | 7.48 | 157.8183 | PTW295805
1435 | 2025-05-18 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:22 | 13.05 | IS5 | INV4 | M1 | SCB8 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | NA | NA | 19:22 |  |  |  | 13.05 |  | Open | 0.0010052 | 7.48 | 157.8183 | PTW295805
1436 | 2025-05-18 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:22 | 13.05 | IS8 | INV4 | M1 | SCB1 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | NA | NA | 19:22 |  |  |  | 13.05 |  | Open | 0.0010165 | 7.48 | 159.5915 | PTW295805
1437 | 2025-05-19 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:17 | 19:23 | 13.1 | IS2 | INV3 | M2 | SCB7 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:17 | NA | NA | 19:23 |  |  |  | 13.1 |  | Open | 0.001009 | 7.56 | 159.5062 | PTW295967
1438 | 2025-05-19 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:17 | 19:23 | 13.1 | IS3 | INV2 | M2 | SCB6 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:17 | NA | NA | 19:23 |  |  |  | 13.1 |  | Open | 0.001009 | 7.56 | 159.5062 | PTW295967
1439 | 2025-05-19 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:17 | 19:23 | 13.1 | IS4 | INV1 | M2 | SCB2 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:17 | NA | NA | 19:23 |  |  |  | 13.1 |  | Open | 0.0010203 | 7.56 | 161.2984 | PTW295967
1440 | 2025-05-19 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:17 | 19:23 | 13.1 | IS20 | INV2 | M1 | SCB2 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:17 | NA | NA | 19:23 |  |  |  | 13.1 |  | Open | 0.0012244 | 7.56 | 193.5581 | PTW295967
1441 | 2025-05-19 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:17 | 19:23 | 13.1 | IS20 | INV2 | M1 | SCB2 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:17 | NA | NA | 19:23 |  |  |  | 13.1 |  | Open | 0.0012244 | 7.56 | 193.5581 | PTW295967
1442 | 2025-05-19 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:17 | 19:23 | 13.1 | IS20 | INV2 | M1 | SCB3 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:17 | NA | NA | 19:23 |  |  |  | 13.1 |  | Open | 0.0012244 | 7.56 | 193.5581 | PTW295967
1443 | 2025-05-19 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:17 | 19:23 | 13.1 | IS20 | INV2 | M2 | SCB8 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:17 | NA | NA | 19:23 |  |  |  | 13.1 |  | Open | 0.0012244 | 7.56 | 193.5581 | PTW295967
1444 | 2025-05-19 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:17 | 19:23 | 13.1 | IS19 | INV4 | M1 | SCB9 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:17 | NA | NA | 19:23 |  |  |  | 13.1 |  | Open | 0.0012244 | 7.56 | 193.5581 | PTW295967
1445 | 2025-05-20 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS13 | INV3 | M2 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | NA | NA | 19:24 |  |  |  | 13.1 |  | Open | 0.0012244 | 7.5 | 192.0219 | PTW295805
1446 | 2025-05-20 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS6 | INV3 | M2 | SCB7 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | NA | NA | 19:24 |  |  |  | 13.1 |  | Open | 0.0012244 | 7.5 | 192.0219 | PTW295805
1447 | 2025-05-20 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS6 | INV3 | M1 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | NA | NA | 19:24 |  |  |  | 13.1 |  | Open | 0.0012244 | 7.5 | 192.0219 | PTW295805
1448 | 2025-05-20 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS9 | INV3 | M1 | SCB6 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | NA | NA | 19:24 |  |  |  | 13.1 |  | Open | 0.0012358 | 7.5 | 193.7999 | PTW295805
1449 | 2025-05-20 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS5 | INV4 | M1 | SCB5 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | NA | NA | 19:24 |  |  |  | 13.1 |  | Open | 0.001009 | 7.5 | 158.2403 | PTW295805
1450 | 2025-05-20 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS5 | INV4 | M1 | SCB8 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | NA | NA | 19:24 |  |  |  | 13.1 |  | Open | 0.001009 | 7.5 | 158.2403 | PTW295805
1451 | 2025-05-20 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS8 | INV4 | M1 | SCB1 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | NA | NA | 19:24 |  |  |  | 13.1 |  | Open | 0.0010203 | 7.5 | 160.0182 | PTW295805
1452 | 2025-05-20 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS2 | INV3 | M2 | SCB7 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | NA | NA | 19:24 |  |  |  | 13.1 |  | Open | 0.001009 | 7.5 | 158.2403 | PTW295967
1453 | 2025-05-20 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS3 | INV2 | M2 | SCB6 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | NA | NA | 19:24 |  |  |  | 13.1 |  | Open | 0.001009 | 7.5 | 158.2403 | PTW295967
1454 | 2025-05-20 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS4 | INV1 | M2 | SCB2 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | NA | NA | 19:24 |  |  |  | 13.1 |  | Open | 0.0010203 | 7.5 | 160.0182 | PTW295967
1455 | 2025-05-20 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS20 | INV2 | M1 | SCB2 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | NA | NA | 19:24 |  |  |  | 13.1 |  | Open | 0.0012244 | 7.5 | 192.0219 | PTW295967
1456 | 2025-05-20 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS20 | INV2 | M1 | SCB2 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | NA | NA | 19:24 |  |  |  | 13.1 |  | Open | 0.0012244 | 7.5 | 192.0219 | PTW295967
1457 | 2025-05-20 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS20 | INV2 | M1 | SCB3 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | NA | NA | 19:24 |  |  |  | 13.1 |  | Open | 0.0012244 | 7.5 | 192.0219 | PTW295967
1458 | 2025-05-20 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS20 | INV2 | M2 | SCB8 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | NA | NA | 19:24 |  |  |  | 13.1 |  | Open | 0.0012244 | 7.5 | 192.0219 | PTW295967
1459 | 2025-05-20 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS19 | INV4 | M1 | SCB9 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | NA | NA | 19:24 |  |  |  | 13.1 |  | Open | 0.0012244 | 7.5 | 192.0219 | PTW295967
1460 | 2025-05-21 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS13 | INV3 | M2 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | NA | NA | 19:24 |  |  |  | 13.1 |  | Open | 0.0012244 | 7.75 | 198.4226 | PTW295805
1461 | 2025-05-21 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS6 | INV3 | M2 | SCB7 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | NA | NA | 19:24 |  |  |  | 13.1 |  | Open | 0.0012244 | 7.75 | 198.4226 | PTW295805
1462 | 2025-05-21 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS6 | INV3 | M1 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | NA | NA | 19:24 |  |  |  | 13.1 |  | Open | 0.0012244 | 7.75 | 198.4226 | PTW295805
1463 | 2025-05-21 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS9 | INV3 | M1 | SCB6 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | NA | NA | 19:24 |  |  |  | 13.1 |  | Open | 0.0012358 | 7.75 | 200.2599 | PTW295805
1464 | 2025-05-21 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS5 | INV4 | M1 | SCB5 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | NA | NA | 19:24 |  |  |  | 13.1 |  | Open | 0.001009 | 7.75 | 163.5149 | PTW295805
1465 | 2025-05-21 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS5 | INV4 | M1 | SCB8 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | NA | NA | 19:24 |  |  |  | 13.1 |  | Open | 0.001009 | 7.75 | 163.5149 | PTW295805
1466 | 2025-05-21 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS8 | INV4 | M1 | SCB1 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | NA | NA | 19:24 |  |  |  | 13.1 |  | Open | 0.0010203 | 7.75 | 165.3522 | PTW295805
1467 | 2025-05-21 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS2 | INV3 | M2 | SCB7 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | NA | NA | 19:24 |  |  |  | 13.1 |  | Open | 0.001009 | 7.75 | 163.5149 | PTW295967
1468 | 2025-05-21 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS3 | INV2 | M2 | SCB6 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | NA | NA | 19:24 |  |  |  | 13.1 |  | Open | 0.001009 | 7.75 | 163.5149 | PTW295967
1469 | 2025-05-21 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS4 | INV1 | M2 | SCB2 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | NA | NA | 19:24 |  |  |  | 13.1 |  | Open | 0.0010203 | 7.75 | 165.3522 | PTW295967
1470 | 2025-05-21 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS20 | INV2 | M1 | SCB2 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | NA | NA | 19:24 |  |  |  | 13.1 |  | Open | 0.0012244 | 7.75 | 198.4226 | PTW295967
1471 | 2025-05-21 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS20 | INV2 | M1 | SCB2 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | NA | NA | 19:24 |  |  |  | 13.1 |  | Open | 0.0012244 | 7.75 | 198.4226 | PTW295967
1472 | 2025-05-21 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS20 | INV2 | M1 | SCB3 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | NA | NA | 19:24 |  |  |  | 13.1 |  | Open | 0.0012244 | 7.75 | 198.4226 | PTW295967
1473 | 2025-05-21 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS20 | INV2 | M2 | SCB8 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | NA | NA | 19:24 |  |  |  | 13.1 |  | Open | 0.0012244 | 7.75 | 198.4226 | PTW295967
1474 | 2025-05-21 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS19 | INV4 | M1 | SCB9 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | NA | NA | 19:24 |  |  |  | 13.1 |  | Open | 0.0012244 | 7.75 | 198.4226 | PTW295967
1475 | 2025-05-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:25 | 13.1 | IS13 | INV3 | M2 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | NA | NA | 19:25 |  |  |  | 13.1 |  | Open | 0.0012244 | 7.64 | 195.6063 | PTW295805
1476 | 2025-05-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:25 | 13.1 | IS6 | INV3 | M2 | SCB7 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | NA | NA | 19:25 |  |  |  | 13.1 |  | Open | 0.0012244 | 7.64 | 195.6063 | PTW295805
1477 | 2025-05-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:25 | 13.1 | IS6 | INV3 | M1 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | NA | NA | 19:25 |  |  |  | 13.1 |  | Open | 0.0012244 | 7.64 | 195.6063 | PTW295805
1478 | 2025-05-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:25 | 13.1 | IS9 | INV3 | M1 | SCB6 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | NA | NA | 19:25 |  |  |  | 13.1 |  | Open | 0.0012358 | 7.64 | 197.4175 | PTW295805
1479 | 2025-05-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:25 | 13.1 | IS5 | INV4 | M1 | SCB5 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | NA | NA | 19:25 |  |  |  | 13.1 |  | Open | 0.001009 | 7.64 | 161.1941 | PTW295805
1480 | 2025-05-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:25 | 13.1 | IS5 | INV4 | M1 | SCB8 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | NA | NA | 19:25 |  |  |  | 13.1 |  | Open | 0.001009 | 7.64 | 161.1941 | PTW295805
1481 | 2025-05-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:25 | 13.1 | IS8 | INV4 | M1 | SCB1 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | NA | NA | 19:25 |  |  |  | 13.1 |  | Open | 0.0010203 | 7.64 | 163.0052 | PTW295805
1482 | 2025-05-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:25 | 13.1 | IS2 | INV3 | M2 | SCB7 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | NA | NA | 19:25 |  |  |  | 13.1 |  | Open | 0.001009 | 7.64 | 161.1941 | PTW295967
1483 | 2025-05-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:25 | 13.1 | IS3 | INV2 | M2 | SCB6 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | NA | NA | 19:25 |  |  |  | 13.1 |  | Open | 0.001009 | 7.64 | 161.1941 | PTW295967
1484 | 2025-05-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:25 | 13.1 | IS4 | INV1 | M2 | SCB2 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | NA | NA | 19:25 |  |  |  | 13.1 |  | Open | 0.0010203 | 7.64 | 163.0052 | PTW295967
1485 | 2025-05-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:25 | 13.1 | IS20 | INV2 | M1 | SCB2 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | NA | NA | 19:25 |  |  |  | 13.1 |  | Open | 0.0012244 | 7.64 | 195.6063 | PTW295967
1486 | 2025-05-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:25 | 13.1 | IS20 | INV2 | M1 | SCB2 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | NA | NA | 19:25 |  |  |  | 13.1 |  | Open | 0.0012244 | 7.64 | 195.6063 | PTW295967
1487 | 2025-05-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:25 | 13.1 | IS20 | INV2 | M1 | SCB3 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | NA | NA | 19:25 |  |  |  | 13.1 |  | Open | 0.0012244 | 7.64 | 195.6063 | PTW295967
1488 | 2025-05-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:25 | 13.1 | IS20 | INV2 | M2 | SCB8 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | NA | NA | 19:25 |  |  |  | 13.1 |  | Open | 0.0012244 | 7.64 | 195.6063 | PTW295967
1489 | 2025-05-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:25 | 13.1 | IS19 | INV4 | M1 | SCB9 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | NA | NA | 19:25 |  |  |  | 13.1 |  | Open | 0.0012244 | 7.64 | 195.6063 | PTW295967
1490 | 2025-05-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:25 | 13.1 | IS7 |  |  |  |  | Tx | 0 | 1 | IS7Tx | 16443 | 4.907% | IDT | IDT_Manual stop for LV Side Thermography | IDT manual stop for thermography work | 12:47 | 12:47 | 12:47 | 13:33 | 0 | 0 | 0.76667 | 0.76667 | After thermography work done IDT Charged. | Close | 0.037621 | 0.78542 | 10557.2033 | PTW296741
1491 | 2025-05-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:25 | 13.1 | IS7 |  |  |  |  | Tx | 0 | 1 | IS7Tx | 16443 | 4.907% | IDT | IDT_Manual stop for LV Side Thermography | IDT manual stop for thermography work | 14:10 | 14:10 | 14:10 | 14:41 | 0 | 0 | 0.51667 | 0.51667 | After thermography work done IDT Charged. | Close | 0.025353 | 0.48248 | 6485.3152 | PTW296741
1492 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS13 | INV3 | M2 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | NA | NA | 19:27 |  |  |  | 13.1333 |  | Open | 0.0012275 | 7.6 | 194.5822 | PTW295805
1493 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS6 | INV3 | M2 | SCB7 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | NA | NA | 19:27 |  |  |  | 13.1333 |  | Open | 0.0012275 | 7.6 | 194.5822 | PTW295805
1494 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS6 | INV3 | M1 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | NA | NA | 19:27 |  |  |  | 13.1333 |  | Open | 0.0012275 | 7.6 | 194.5822 | PTW295805
1495 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS9 | INV3 | M1 | SCB6 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | NA | NA | 19:27 |  |  |  | 13.1333 |  | Open | 0.0012389 | 7.6 | 196.3839 | PTW295805
1496 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS5 | INV4 | M1 | SCB5 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | NA | NA | 19:27 |  |  |  | 13.1333 |  | Open | 0.0010116 | 7.6 | 160.3501 | PTW295805
1497 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS5 | INV4 | M1 | SCB8 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | NA | NA | 19:27 |  |  |  | 13.1333 |  | Open | 0.0010116 | 7.6 | 160.3501 | PTW295805
1498 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS8 | INV4 | M1 | SCB1 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | NA | NA | 19:27 |  |  |  | 13.1333 |  | Open | 0.0010229 | 7.6 | 162.1518 | PTW295805
1499 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS2 | INV3 | M2 | SCB7 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | NA | NA | 19:27 |  |  |  | 13.1333 |  | Open | 0.0010116 | 7.6 | 160.3501 | PTW295967
1500 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS3 | INV2 | M2 | SCB6 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | NA | NA | 19:27 |  |  |  | 13.1333 |  | Open | 0.0010116 | 7.6 | 160.3501 | PTW295967
1501 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS4 | INV1 | M2 | SCB2 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | NA | NA | 19:27 |  |  |  | 13.1333 |  | Open | 0.0010229 | 7.6 | 162.1518 | PTW295967
1502 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS20 | INV2 | M1 | SCB2 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | NA | NA | 19:27 |  |  |  | 13.1333 |  | Open | 0.0012275 | 7.6 | 194.5822 | PTW295967
1503 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS20 | INV2 | M1 | SCB2 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | NA | NA | 19:27 |  |  |  | 13.1333 |  | Open | 0.0012275 | 7.6 | 194.5822 | PTW295967
1504 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS20 | INV2 | M1 | SCB3 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | NA | NA | 19:27 |  |  |  | 13.1333 |  | Open | 0.0012275 | 7.6 | 194.5822 | PTW295967
1505 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS20 | INV2 | M2 | SCB8 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | NA | NA | 19:27 |  |  |  | 13.1333 |  | Open | 0.0012275 | 7.6 | 194.5822 | PTW295967
1506 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS19 | INV4 | M1 | SCB9 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | NA | NA | 19:27 |  |  |  | 13.1333 |  | Open | 0.0012275 | 7.6 | 194.5822 | PTW295967
1507 | 2025-05-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS5 | INV4 | M1 | SCB5 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | NA | NA | 19:24 |  |  |  | 13.1 |  | Open | 0.001009 | 7.31 | 154.2315 | PTW295805
1508 | 2025-05-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS5 | INV4 | M1 | SCB8 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | NA | NA | 19:24 |  |  |  | 13.1 |  | Open | 0.001009 | 7.31 | 154.2315 | PTW295805
1509 | 2025-05-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS2 | INV3 | M2 | SCB7 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | NA | NA | 19:24 |  |  |  | 13.1 |  | Open | 0.001009 | 7.31 | 154.2315 | PTW295967
1510 | 2025-05-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS3 | INV2 | M2 | SCB6 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | NA | NA | 19:24 |  |  |  | 13.1 |  | Open | 0.001009 | 7.31 | 154.2315 | PTW295967
1511 | 2025-05-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS4 | INV1 | M2 | SCB2 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | NA | NA | 19:24 |  |  |  | 13.1 |  | Open | 0.0010203 | 7.31 | 155.9644 | PTW295967
1512 | 2025-05-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS20 | INV2 | M1 | SCB2 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | NA | NA | 19:24 |  |  |  | 13.1 |  | Open | 0.0012244 | 7.31 | 187.1573 | PTW295967
1513 | 2025-05-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS20 | INV2 | M1 | SCB2 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | NA | NA | 19:24 |  |  |  | 13.1 |  | Open | 0.0012244 | 7.31 | 187.1573 | PTW295967
1514 | 2025-05-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS20 | INV2 | M1 | SCB3 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | NA | NA | 19:24 |  |  |  | 13.1 |  | Open | 0.0012244 | 7.31 | 187.1573 | PTW295967
1515 | 2025-05-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS20 | INV2 | M2 | SCB8 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | NA | NA | 19:24 |  |  |  | 13.1 |  | Open | 0.0012244 | 7.31 | 187.1573 | PTW295967
1516 | 2025-05-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS19 | INV4 | M1 | SCB9 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | NA | NA | 19:24 |  |  |  | 13.1 |  | Open | 0.0012244 | 7.31 | 187.1573 | PTW295967
1517 | 2025-05-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS15 | INV2 | M1 |  |  |  | 1 | 1 | IS15INV2M1 | 2004.48 | 0.5982% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 6:18 | 6:18 | 6:42 | 7:20 | 0 | 0.4 | 1.0333 | 1.0333 | AC Breaker manually discharge & PU reset then inverter start. | Close | 0.0061813 | 0.097872 | 160.3723 | PTW297021
1518 | 2025-05-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS15 | INV2 | M2 |  |  |  | 1 | 1 | IS15INV2M2 | 1941.84 | 0.5795% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 7:02 | 7:02 | 7:02 | 7:20 | 0 | 0 | 0.3 | 0.3 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0017385 | 0.047683 | 75.6916 | PTW297021
1519 | 2025-05-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:55 | 19:21 | 12.4333 | IS5 | INV4 | M1 | SCB5 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:55 | NA | NA | 19:21 |  |  |  | 12.4333 |  | Open | 0.00095766 | 5.03 | 106.1265 | PTW295805
1520 | 2025-05-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:55 | 19:21 | 12.4333 | IS5 | INV4 | M1 | SCB8 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:55 | NA | NA | 19:21 |  |  |  | 12.4333 |  | Open | 0.00095766 | 5.03 | 106.1265 | PTW295805
1521 | 2025-05-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:55 | 19:21 | 12.4333 | IS2 | INV3 | M2 | SCB7 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:55 | NA | NA | 19:21 |  |  |  | 12.4333 |  | Open | 0.00095766 | 5.03 | 106.1265 | PTW295967
1522 | 2025-05-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:55 | 19:21 | 12.4333 | IS3 | INV2 | M2 | SCB6 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:55 | NA | NA | 19:21 |  |  |  | 12.4333 |  | Open | 0.00095766 | 5.03 | 106.1265 | PTW295967
1523 | 2025-05-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:55 | 19:21 | 12.4333 | IS4 | INV1 | M2 | SCB2 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:55 | NA | NA | 19:21 |  |  |  | 12.4333 |  | Open | 0.00096842 | 5.03 | 107.3189 | PTW295967
1524 | 2025-05-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:55 | 19:21 | 12.4333 | IS20 | INV2 | M1 | SCB2 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:55 | NA | NA | 19:21 |  |  |  | 12.4333 |  | Open | 0.0011621 | 5.03 | 128.7827 | PTW295967
1525 | 2025-05-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:55 | 19:21 | 12.4333 | IS20 | INV2 | M1 | SCB2 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:55 | NA | NA | 19:21 |  |  |  | 12.4333 |  | Open | 0.0011621 | 5.03 | 128.7827 | PTW295967
1526 | 2025-05-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:55 | 19:21 | 12.4333 | IS20 | INV2 | M1 | SCB3 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:55 | NA | NA | 19:21 |  |  |  | 12.4333 |  | Open | 0.0011621 | 5.03 | 128.7827 | PTW295967
1527 | 2025-05-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:55 | 19:21 | 12.4333 | IS20 | INV2 | M2 | SCB8 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:55 | NA | NA | 19:21 |  |  |  | 12.4333 |  | Open | 0.0011621 | 5.03 | 128.7827 | PTW295967
1528 | 2025-05-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:55 | 19:21 | 12.4333 | IS19 | INV4 | M1 | SCB9 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:55 | NA | NA | 19:21 |  |  |  | 12.4333 |  | Open | 0.0011621 | 5.03 | 128.7827 | PTW295967
1529 | 2025-05-28 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:20 | 19:30 | 13.1667 | IS6 | INV3 | M2 | SCB10 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Affected Due to Wind Strom. | String Affected Due to Wind Strom. | 6:20 | 6:20 | 6:20 | 19:30 | 0 | 0 | 13.1667 | 13.1667 | String Affected Due to Wind Strom. | Close | 0.00061533 | 6.6 | 84.4896 | PTW297811
1530 | 2025-05-28 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:20 | 19:30 | 13.1667 | IS14 | INV4 | M1 | SCB5 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Affected Due to Wind Strom. | String Affected Due to Wind Strom. | 6:20 | 6:20 | 6:20 | 19:30 | 0 | 0 | 13.1667 | 13.1667 | String Affected Due to Wind Strom. | Close | 0.00061533 | 6.6 | 84.4896 | PTW297811
1531 | 2025-05-28 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:20 | 19:30 | 13.1667 | IS13 | INV1 | M1 | SCB4 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Affected Due to Wind Strom. | String Affected Due to Wind Strom. | 6:20 | 6:20 | 6:20 | 19:30 | 0 | 0 | 13.1667 | 13.1667 | String Affected Due to Wind Strom. | Close | 0.00061533 | 6.6 | 84.4896 | PTW297811
1532 | 2025-05-28 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:20 | 19:30 | 13.1667 | IS12 | INV4 | M2 | SCB7 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Affected Due to Wind Strom. | String Affected Due to Wind Strom. | 6:20 | 6:20 | 6:20 | 19:30 | 0 | 0 | 13.1667 | 13.1667 | String Affected Due to Wind Strom. | Close | 0.00061533 | 6.6 | 84.4896 | PTW297811
1533 | 2025-05-28 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:20 | 19:30 | 13.1667 | IS20 | INV4 | M2 | SCB7 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Affected Due to Wind Strom. | String Affected Due to Wind Strom. | 6:20 | 6:20 | 6:20 | 19:30 | 0 | 0 | 13.1667 | 13.1667 | String Affected Due to Wind Strom. | Close | 0.00061533 | 6.6 | 84.4896 | PTW297811
1534 | 2025-05-28 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:20 | 19:30 | 13.1667 | IS6 | INV4 | M2 | SCB4 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:20 | NA | NA | 19:30 |  |  |  | 13.1667 |  | Open | 0.0012307 | 6.6 | 168.9793 | PTW297883
1535 | 2025-05-28 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:20 | 19:30 | 13.1667 | IS6 | INV4 | M1 | SCB3 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:20 | NA | NA | 19:30 |  |  |  | 13.1667 |  | Open | 0.0012307 | 6.6 | 168.9793 | PTW297883
1536 | 2025-05-28 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:20 | 19:30 | 13.1667 | IS6 | INV4 | M2 | SCB4 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:20 | NA | NA | 19:30 |  |  |  | 13.1667 |  | Open | 0.0012307 | 6.6 | 168.9793 | PTW297883
1537 | 2025-05-29 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:26 | 19:28 | 13.0333 | IS6 | INV4 | M2 | SCB4 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:26 | NA | NA | 19:28 |  |  |  | 13.0333 |  | Open | 0.0012182 | 6.23 | 159.5062 | PTW297883
1538 | 2025-05-29 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:26 | 19:28 | 13.0333 | IS6 | INV4 | M1 | SCB3 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:26 | NA | NA | 19:28 |  |  |  | 13.0333 |  | Open | 0.0012182 | 6.23 | 159.5062 | PTW297883
1539 | 2025-05-29 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:26 | 19:28 | 13.0333 | IS6 | INV4 | M2 | SCB4 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:26 | NA | NA | 19:28 |  |  |  | 13.0333 |  | Open | 0.0012182 | 6.23 | 159.5062 | PTW297883
1540 | 2025-05-30 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:26 | 13.1167 | IS6 | INV4 | M2 | SCB4 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | NA | NA | 19:26 |  |  |  | 13.1167 |  | Open | 0.001226 | 7.08 | 181.2687 | PTW297883
1541 | 2025-05-30 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:26 | 13.1167 | IS6 | INV4 | M1 | SCB3 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | NA | NA | 19:26 |  |  |  | 13.1167 |  | Open | 0.001226 | 7.08 | 181.2687 | PTW297883
1542 | 2025-05-30 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:26 | 13.1167 | IS6 | INV4 | M2 | SCB4 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | NA | NA | 19:26 |  |  |  | 13.1167 |  | Open | 0.001226 | 7.08 | 181.2687 | PTW297883
1543 | 2025-05-31 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS9 | INV1 | M2 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | Manully stop due to IV Testing work | Manully stop due to IV Testing work | 10:35 | 10:35 | 10:35 | 13:26 | 0 | 0 | 2.85 | 2.85 |  | Close | 0.00026638 | 2.53 | 64.7754 | PTW298338
1544 | 2025-05-31 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS9 | INV1 | M2 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | Manully stop due to IV Testing work | Manully stop due to IV Testing work | 10:35 | 10:35 | 10:35 | 13:26 | 0 | 0 | 2.85 | 2.85 |  | Close | 0.00026638 | 2.53 | 64.7754 | PTW298338
1545 | 2025-05-31 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS7 | INV1 | M1 | SCB3 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | MC4 connector damage | MC4 connector Replaced. | 6:19 | 6:19 | 6:19 | 19:27 | 0 | 0 | 13.1333 | 13.1333 | MC4 connector Replaced. | Close | 0.00061377 | 6.91 | 88.4581 | PTW298409
1546 | 2025-06-01 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:31 | 19:25 | 12.9 | [5 empty] | Power_Tx2 | 0 | 1 | Power_Tx2 | 167768.915 | 50.07% | PTR | Tripped due to the 87T Differential Protection operation. | R-Phase Cable End Termination Failure | 19:25 | 19:25 | 19:25 | 5:15 | 0 | 0 |  |  | R phase End termination replaced and Check IR Value then PTR Charged. | Close | 0 | 0 | 0 | PTW298610
1547 | 2025-06-03 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:16 | 19:26 | 13.1667 | IS4 | INV3 | M1 | SCB6 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 10:56 | 10:56 | 10:56 | 12:35 | 0 | 0 | 1.65 | 1.65 | String Manully shutdown for IV Testing work | Close | 0.00012852 | 1.49 | 32.2737 | PTW298884
1548 | 2025-06-05 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:16 | 19:27 | 13.1833 | IS1 | INV3 | M2 | SCB1 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 10:46 | 10:46 | 10:46 | 11:06 | 0 | 0 | 0.33333 | 0.33333 | String Manully shutdown for IV Testing work | Close | 1.2837e-05 | 0.30154 | 3.2294 | PTW299319
1549 | 2025-06-05 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:16 | 19:27 | 13.1833 | IS5 | INV3 | M1 | SCB1 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:15 | 11:15 | 11:15 | 11:30 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 9.628e-06 | 0.24352 | 2.608 | PTW299319
1550 | 2025-06-05 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:16 | 19:27 | 13.1833 | IS9 | INV1 | M2 | SCB3 | Str_Typ5(545*29) |  | 0 | 0 | Str_Typ5(545*29) | 15.805 | 0.004717% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:45 | 11:45 | 11:45 | 12:00 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1792e-05 | 0.25457 | 3.3391 | PTW299319
1551 | 2025-06-05 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:16 | 19:27 | 13.1833 | IS12 | INV1 | M2 | SCB3 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:20 | 12:20 | 12:20 | 12:35 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1683e-05 | 0.26092 | 3.3909 | PTW299319
1552 | 2025-06-05 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:16 | 19:27 | 13.1833 | IS16 | INV3 | M1 | SCB4 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:45 | 12:45 | 12:45 | 13:00 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1683e-05 | 0.26183 | 3.4028 | PTW299319
1553 | 2025-06-05 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:16 | 19:27 | 13.1833 | IS18 | INV4 | M1 | SCB1 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:10 | 13:10 | 13:10 | 13:30 | 0 | 0 | 0.33333 | 0.33333 | String Manully shutdown for IV Testing work | Close | 1.5578e-05 | 0.33905 | 4.4063 | PTW299319
1554 | 2025-06-05 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:16 | 19:27 | 13.1833 | IS6 | INV2 | M1 | SCB2 | Str_Typ3(535*29) |  | 0 | 0 | Str_Typ3(535*29) | 15.515 | 0.00463% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 14:45 | 14:45 | 14:45 | 15:03 | 0 | 0 | 0.3 | 0.3 | String Manully shutdown for IV Testing work | Close | 1.389e-05 | 0.25993 | 3.3467 | PTW299319
1555 | 2025-06-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:17 | 19:29 | 13.2 | IS1 | INV3 | M2 | SCB1 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 10:30 | 10:30 | 10:30 | 10:45 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 9.628e-06 | 0.22043 | 2.3608 | PTW299485
1556 | 2025-06-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:17 | 19:29 | 13.2 | IS5 | INV3 | M1 | SCB1 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:00 | 11:00 | 11:00 | 11:15 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 9.628e-06 | 0.2379 | 2.5479 | PTW299485
1557 | 2025-06-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:17 | 19:29 | 13.2 | IS9 | INV1 | M2 | SCB3 | Str_Typ5(545*29) |  | 0 | 0 | Str_Typ5(545*29) | 15.805 | 0.004717% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:30 | 11:30 | 11:30 | 11:45 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1792e-05 | 0.25215 | 3.3073 | PTW299485
1558 | 2025-06-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:17 | 19:29 | 13.2 | IS12 | INV1 | M2 | SCB3 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:00 | 12:00 | 12:00 | 12:15 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1683e-05 | 0.26067 | 3.3877 | PTW299485
1559 | 2025-06-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:17 | 19:29 | 13.2 | IS16 | INV3 | M1 | SCB4 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:30 | 12:30 | 12:30 | 12:45 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1683e-05 | 0.26505 | 3.4446 | PTW299485
1560 | 2025-06-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:17 | 19:29 | 13.2 | IS18 | INV4 | M1 | SCB1 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:00 | 13:00 | 13:00 | 13:15 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1683e-05 | 0.26388 | 3.4295 | PTW299485
1561 | 2025-06-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:17 | 19:29 | 13.2 | IS6 | INV2 | M1 | SCB2 | Str_Typ3(535*29) |  | 0 | 0 | Str_Typ3(535*29) | 15.515 | 0.00463% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:30 | 13:30 | 13:30 | 13:45 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1575e-05 | 0.25915 | 3.3368 | PTW299485
1562 | 2025-06-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:17 | 19:29 | 13.2 | IS9 | INV4 | M2 |  |  |  | 1 | 1 | IS9INV4M2 | 1959.82 | 0.5849% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 6:17 | 6:17 | 6:45 | 19:29 | 0 | 0.46667 | 13.2 | 13.2 | After Genration AC Breaker Replace with Sungrow Team. | Close | 0.077202 | 7.3191 | 11904.0443 | PTW299590
1563 | 2025-06-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:17 | 19:29 | 13.2 | IS9 | INV4 | M1 |  |  |  | 1 | 1 | IS9INV4M1 | 2244.31 | 0.6698% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 7:55 | 7:55 | 7:55 | 9:11 | 0 | 0 | 1.2667 | 1.2667 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0084836 | 0.56024 | 1043.4672 | PTW299590
1564 | 2025-06-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:17 | 19:29 | 13.2 | IS9 | INV4 | M1 |  |  |  | 1 | 1 | IS9INV4M1 | 2244.31 | 0.6698% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 9:35 | 9:35 | 9:35 | 9:47 | 0 | 0 | 0.2 | 0.2 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0013395 | 0.14326 | 266.8238 | PTW299590
1565 | 2025-06-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:17 | 19:29 | 13.2 | IS16 | INV3 | M1 |  |  |  | 1 | 1 | IS16INV3M1 | 2129.76 | 0.6356% | Inverter | Inverter trip in GFDI falut | Inverter trip in GFDI falut | 14:28 | 14:45 | 14:45 | 15:22 | 0.28333 | 0.28333 | 0.9 | 0.9 | Inverter Auto Reset and Run | Close | 0.0057202 | 0.72991 | 1290.0983
1566 | 2025-06-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:13 | 19:30 | 13.2833 | IS4 | INV2 | M1 |  |  |  | 1 | 1 | IS4INV2M1 | 2114.1 | 0.6309% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 6:20 | 6:20 | 7:05 | 7:40 | 0 | 0.75 | 1.3333 | 1.3333 | AC Breaker manually discharge & PU reset then inverter start. | Close | 0.008412 | 0.15156 | 265.9083 | PTW299810
1567 | 2025-06-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:13 | 19:30 | 13.2833 | IS4 | INV2 | M2 |  |  |  | 1 | 1 | IS4INV2M2 | 2088 | 0.6231% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 7:25 | 7:25 | 7:25 | 7:40 | 0 | 0 | 0.25 | 0.25 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0015578 | 0.054265 | 94.0312 | PTW299810
1568 | 2025-06-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:13 | 19:30 | 13.2833 | IS1 | INV3 | M2 | SCB1 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 10:30 | 10:30 | 10:30 | 10:45 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 9.628e-06 | 0.2207 | 2.3636 | PTW299638
1569 | 2025-06-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:13 | 19:30 | 13.2833 | IS5 | INV3 | M1 | SCB1 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:00 | 11:00 | 11:00 | 11:15 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 9.628e-06 | 0.23875 | 2.557 | PTW299638
1570 | 2025-06-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:13 | 19:30 | 13.2833 | IS9 | INV1 | M2 | SCB3 | Str_Typ5(545*29) |  | 0 | 0 | Str_Typ5(545*29) | 15.805 | 0.004717% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:30 | 11:30 | 11:30 | 11:45 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1792e-05 | 0.2523 | 3.3093 | PTW299638
1571 | 2025-06-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:13 | 19:30 | 13.2833 | IS12 | INV1 | M2 | SCB3 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:00 | 12:00 | 12:00 | 12:15 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1683e-05 | 0.26177 | 3.402 | PTW299638
1572 | 2025-06-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:13 | 19:30 | 13.2833 | IS16 | INV3 | M1 | SCB4 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:30 | 12:30 | 12:30 | 12:45 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1683e-05 | 0.26597 | 3.4565 | PTW299638
1573 | 2025-06-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:13 | 19:30 | 13.2833 | IS18 | INV4 | M1 | SCB1 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:00 | 13:00 | 13:00 | 13:15 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1683e-05 | 0.26517 | 3.4461 | PTW299638
1574 | 2025-06-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:13 | 19:30 | 13.2833 | IS6 | INV2 | M1 | SCB2 | Str_Typ3(535*29) |  | 0 | 0 | Str_Typ3(535*29) | 15.515 | 0.00463% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:30 | 13:30 | 13:30 | 13:45 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1575e-05 | 0.26072 | 3.3569 | PTW299638
1575 | 2025-06-08 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:30 | 13.25 | IS1 | INV3 | M2 | SCB1 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 10:31 | 10:31 | 10:31 | 10:45 | 0 | 0 | 0.23333 | 0.23333 | String Manully shutdown for IV Testing work | Close | 8.9861e-06 | 0.21297 | 2.2808 | PTW299846
1576 | 2025-06-08 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:30 | 13.25 | IS5 | INV3 | M1 | SCB1 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:02 | 11:02 | 11:02 | 11:15 | 0 | 0 | 0.21667 | 0.21667 | String Manully shutdown for IV Testing work | Close | 8.3443e-06 | 0.21248 | 2.2756 | PTW299846
1577 | 2025-06-08 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:30 | 13.25 | IS9 | INV1 | M2 | SCB3 | Str_Typ5(545*29) |  | 0 | 0 | Str_Typ5(545*29) | 15.805 | 0.004717% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:31 | 11:31 | 11:31 | 11:45 | 0 | 0 | 0.23333 | 0.23333 | String Manully shutdown for IV Testing work | Close | 1.1005e-05 | 0.2381 | 3.123 | PTW299846
1578 | 2025-06-08 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:30 | 13.25 | IS12 | INV1 | M2 | SCB3 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:00 | 12:00 | 12:00 | 12:15 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1683e-05 | 0.24873 | 3.2326 | PTW299846
1579 | 2025-06-08 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:30 | 13.25 | IS16 | INV3 | M1 | SCB4 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:30 | 12:30 | 12:30 | 12:45 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1683e-05 | 0.25043 | 3.2547 | PTW299846
1580 | 2025-06-08 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:30 | 13.25 | IS18 | INV4 | M1 | SCB1 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:01 | 13:01 | 13:01 | 13:15 | 0 | 0 | 0.23333 | 0.23333 | String Manully shutdown for IV Testing work | Close | 1.0905e-05 | 0.24678 | 3.2072 | PTW299846
1581 | 2025-06-08 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:30 | 13.25 | IS6 | INV2 | M1 | SCB2 | Str_Typ3(535*29) |  | 0 | 0 | Str_Typ3(535*29) | 15.515 | 0.00463% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:30 | 13:30 | 13:30 | 13:45 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1575e-05 | 0.25177 | 3.2417 | PTW299846
1582 | 2025-06-09 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:31 | 13.2667 | IS1 | INV3 | M2 | SCB1 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 10:30 | 10:30 | 10:30 | 10:45 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 9.628e-06 | 0.20813 | 2.2291 | PTW300061
1583 | 2025-06-09 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:31 | 13.2667 | IS5 | INV3 | M1 | SCB1 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:02 | 11:02 | 11:02 | 11:15 | 0 | 0 | 0.21667 | 0.21667 | String Manully shutdown for IV Testing work | Close | 8.3443e-06 | 0.21002 | 2.2492 | PTW300061
1584 | 2025-06-09 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:31 | 13.2667 | IS9 | INV1 | M2 | SCB3 | Str_Typ5(545*29) |  | 0 | 0 | Str_Typ5(545*29) | 15.805 | 0.004717% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:31 | 11:31 | 11:31 | 11:45 | 0 | 0 | 0.23333 | 0.23333 | String Manully shutdown for IV Testing work | Close | 1.1005e-05 | 0.23737 | 3.1134 | PTW300061
1585 | 2025-06-09 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:31 | 13.2667 | IS12 | INV1 | M2 | SCB3 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:00 | 12:00 | 12:00 | 12:15 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1683e-05 | 0.26255 | 3.4121 | PTW300061
1586 | 2025-06-09 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:31 | 13.2667 | IS16 | INV3 | M1 | SCB4 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:30 | 12:30 | 12:30 | 12:45 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1683e-05 | 0.25037 | 3.2538 | PTW300061
1587 | 2025-06-09 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:31 | 13.2667 | IS18 | INV4 | M1 | SCB1 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:01 | 13:01 | 13:01 | 13:15 | 0 | 0 | 0.23333 | 0.23333 | String Manully shutdown for IV Testing work | Close | 1.0905e-05 | 0.25013 | 3.2508 | PTW300061
1588 | 2025-06-09 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:31 | 13.2667 | IS6 | INV2 | M1 | SCB2 | Str_Typ3(535*29) |  | 0 | 0 | Str_Typ3(535*29) | 15.515 | 0.00463% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:31 | 13:31 | 13:31 | 13:45 | 0 | 0 | 0.23333 | 0.23333 | String Manully shutdown for IV Testing work | Close | 1.0804e-05 | 0.24548 | 3.1608 | PTW300061
1589 | 2025-06-10 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:31 | 13.2667 | IS9 | INV1 | M2 | SCB3 | Str_Typ5(545*29) |  | 0 | 0 | Str_Typ5(545*29) | 15.805 | 0.004717% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:00 | 12:00 | 12:00 | 12:15 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1792e-05 | 0.25882 | 3.3948 | PTW300295
1590 | 2025-06-10 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:31 | 13.2667 | IS12 | INV1 | M2 | SCB3 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:30 | 12:30 | 12:30 | 12:45 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1683e-05 | 0.26412 | 3.4325 | PTW300295
1591 | 2025-06-11 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:14 | 19:33 | 13.3167 | IS9 | INV1 | M2 | SCB3 | Str_Typ5(545*29) |  | 0 | 0 | Str_Typ5(545*29) | 15.805 | 0.004717% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:15 | 12:15 | 12:15 | 12:37 | 0 | 0 | 0.36667 | 0.36667 | String Manully shutdown for IV Testing work | Close | 1.7294e-05 | 0.37892 | 4.97 | PTW300457
1592 | 2025-06-11 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:14 | 19:33 | 13.3167 | IS12 | INV1 | M2 | SCB3 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:54 | 12:54 | 12:54 | 13:08 | 0 | 0 | 0.23333 | 0.23333 | String Manully shutdown for IV Testing work | Close | 1.0905e-05 | 0.24947 | 3.2421 | PTW300457
1593 | 2025-06-11 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:14 | 19:33 | 13.3167 | IS7 |  |  |  |  | Tx | 0 | 1 | IS7Tx | 16443 | 4.907% | IDT | IDT_Manual stop for LV Side Thermography | IDT manual stop for thermography work | 12:17 | 12:17 | 12:17 | 12:59 | 0 | 0 | 0.7 | 0.7 | After thermography work IDT Charged Sucessfully. | Close | 0.034349 | 0.71287 | 9727.723 | PTW300540
1594 | 2025-06-12 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:32 | 13.2833 | IS9 | INV1 | M2 | SCB3 | Str_Typ5(545*29) |  | 0 | 0 | Str_Typ5(545*29) | 15.805 | 0.004717% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:37 | 12:37 | 12:37 | 13:02 | 0 | 0 | 0.41667 | 0.41667 | String Manully shutdown for IV Testing work | Close | 1.9653e-05 | 0.43092 | 5.6521 | PTW300678
1595 | 2025-06-12 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:32 | 13.2833 | IS12 | INV1 | M2 | SCB3 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:15 | 13:15 | 13:15 | 13:32 | 0 | 0 | 0.28333 | 0.28333 | String Manully shutdown for IV Testing work | Close | 1.3241e-05 | 0.29373 | 3.8174 | PTW300678
[25 empty] | 994.4231 | 25855 | 0.43092
[25 empty] | 979.1111 | 17624 | 0.29373
Formulas:
Days = DAY(EOMONTH(PA[[#This Row],[Month Year]],0))

## GA
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22
Sr. No. | Date | Financial Year | Calendar Year | Contractual Year | Operating Year | Month Year | Days | Sunrise Time (POA>20 W/m2) | Sunset Time (POA<20 W/m2) | Total Generation Time | Affected Equipment | DC Capacity Affected (kW) | Plant Equivalent Weightage | Breakdown Description | Fault Time | Work Completion time on fault | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Lost PoA(Wh/m2) | Approximate Energy Loss (KWh)
1 | 2022-07-06 | FY22 | 2022 | Year_2 | Year_2 | 2022-07-01 | 31 | 6:30 | 18:55 | 12.3833 | Grid | 335091.665 | 100% | Outgoing line tripped in Over volatage | 18:13 | 19:30 | 1.2833 | Restored plant post Grid resumed | Close | 1.2833
2 | 2022-07-07 | FY22 | 2022 | Year_2 | Year_2 | 2022-07-01 | 31 | 6:30 | 18:55 | 12.3833 | Grid | 335091.665 | 100% | Outgoing line tripped in Over volatage | 17:50 | 18:37 | 0.78333 | Restored plant post Grid resumed | Close | 0.78333
3 | 2022-07-07 | FY22 | 2022 | Year_2 | Year_2 | 2022-07-01 | 31 | 6:30 | 18:55 | 12.3833 | Grid | 335091.665 | 100% | Outgoing line tripped in Over volatage | 18:51 | 19:30 | 0.65 | Restored plant post Grid resumed | Close | 0.65
4 | 2022-07-08 | FY22 | 2022 | Year_2 | Year_2 | 2022-07-01 | 31 | 6:30 | 18:55 | 12.3833 | Grid | 335091.665 | 100% | Outgoing line tripped in Over volatage | 16:59 | 17:34 | 0.58333 | Restored plant post Grid resumed | Close | 0.58333
5 | 2022-07-10 | FY22 | 2022 | Year_2 | Year_2 | 2022-07-01 | 31 | 6:30 | 18:55 | 12.3833 | Grid | 335091.665 | 100% | Outgoing line tripped in Over volatage | 14:13 | 14:26 | 0.21667 | Restored plant post Grid resumed | Close | 0.21667
6 | 2022-07-17 | FY22 | 2022 | Year_2 | Year_2 | 2022-07-01 | 31 | 6:30 | 18:55 | 12.3833 | Grid | 335091.665 | 100% | Outgoing line tripped in Over volatage | 16:00 | 16:15 | 0.25 | Restored plant post Grid resumed | Close | 0.25
7 | 2022-09-07 | FY22 | 2022 | Year_2 | Year_2 | 2022-09-01 | 30 | 6:30 | 18:55 | 12.3833 | Grid | 335091.665 | 100% | Line Shurt Down | 20:04 | 23:59 | 3.9167 | Restored plant post Grid resumed | Close | 3.9167
8 | 2022-09-12 | FY22 | 2022 | Year_2 | Year_2 | 2022-09-01 | 30 | 6:30 | 18:55 | 12.3833 | Grid | 335091.665 | 100% | Line tripped | 17:58 | 19:00 | 1.0333 | Restored plant post Grid resumed | Close | 1.0333
9 | 2023-01-22 | FY23 | 2023 | Year_2 | Year_2 | 2023-01-01 | 31 | 6:30 | 18:55 | 12.3833 | Grid | 335091.665 | 100% | Line tripped | 7:26 | 8:46 | 1.3333 | Restored plant post Grid resumed | Close | 1.3333
10 | 2023-05-18 | FY23 | 2023 | Year_2 | Year_2 | 2023-05-18 | 31 | 6:15 | 19:24 | 12.3833 | Grid | 335091.665 | 100% | Line Shurt Down | 19:46 | 23:25 | 3.65 | Restored plant post Grid resumed | Close | 3.65
11 | 2024-06-30 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-30 | 30 | 6:21 | 19:41 | 12.3833 | Grid | 335091.665 | 100% | Line Shurt Down | 19:47 | 5:29 | 9.42 | Restored plant post Grid resumed | Close | 9.42
12 | 2024-07-01 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:21 | 19:43 | 12.3833 | Grid | 335091.665 | 100% | Emergency Line Shutdown | 9:04 | 10:29 | 1.25 | Restored plant post Grid resumed | Close | 1.25
13 | 2024-07-01 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:21 | 19:43 | 12.3833 | Grid | 335091.665 | 100% | Line Shut Down | 20:42 | 2:26 | 5.44 | Restored plant post Grid resumed | Close
14 | 2024-07-02 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:13 | 19:40 | 12.3833 | Grid | 335091.665 | 100% | Line Shut Down | 21:06 | 3:05 | 5.59 | Restored plant post Grid resumed | Close
15 | 2024-07-05 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:19 | 19:39 | 12.3833 | Grid | 335091.665 | 100% | Line Shurt Down From GSS End due to Maintenance Work Purpose | 20:39 | 2:53 | 6.14 | Restored plant post Grid resumed | Close
16 | 2024-08-19 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 6:47 | 19:10 | 12.3833 | Grid | 335091.665 | 100% | Line Shurt Down From GSS End due to Maintenance Work Purpose | 21:00 | 6:00 |  | Restored plant post Grid resumed | Close | 0
17 | 2024-08-28 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 6:42 | 19:05 | 12.3833 | Grid | 335091.665 | 100% | Line Trip From GSS End due to Bus-1 fail | 10:20 | 13:35 | 3.25 | Restored plant post Grid resumed | Close | 3.25 | 2.18
18 | 2024-09-19 | FY24 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 7:00 | 18:42 | 12.3833 | Grid | 335091.665 | 100% | 220KV Line trip due to GSS End ICT trip during load shifting. | 8:09 | 9:26 | 1.2833 | Restored plant post Grid resumed | Close | 1.2833
19 | 2024-09-20 | FY24 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 6:53 | 18:37 | 12.3833 | Grid | 335091.665 | 100% | 220KV Line trip GSS End due to other line Y-phase Jumper Open. | 12:01 | 14:04 | 2.05 | Restored plant post Grid resumed | Close | 2.05
20 | 2024-09-21 | FY24 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 7:34 | 18:38 | 12.3833 | Grid | 335091.665 | 100% | 220KV Line Shutdown to GSS End due to Bus Jumper Replace Work. | 6:50 | 7:30 | 0.66667 | Restored plant post Grid resumed | Close | 0.66667
21 | 2024-12-11 | FY24 | 2024 | Year_3 | Year_3 | 2024-12-11 | 31 | 7:28 | 17:56 | 12.3833 | Grid | 335091.665 | 100% | 220KV Jaisalmer blackout occurred when the main line (Aakl-1 & 2) tripped. | 12:13 | 16:10 | 3.95 | Restored plant post Grid resumed | Close | 3.95 | 3.097 | 922015
22 | 2024-12-30 | FY24 | 2024 | Year_3 | Year_3 | 2024-12-11 | 31 | 7:36 | 18:07 | 12.3833 | Grid | 335091.665 | 100% | Line tripped from GSS End. | 18:11 | 21:00 |  | Restored plant post Grid resumed | Close | 0
23 | 2025-02-05 | FY25 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 7:32 | 18:31 | 12.45 | Grid | 335091.665 | 100% | 220KV Line Shutdown to GSS End due to New T/F Jumper Work. | 18:52 | 22:13 |  | Restored plant post Grid resumed | Close | 0
24 | 2025-02-06 | FY25 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 7:31 | 18:31 | 12.45 | Grid | 335091.665 | 100% | 220KV Line trip due to GSS End ICT trip during load shifting. | 11:30 | 12:28 | 0.96667 | Restored plant post Grid resumed | Close | 0.96667 | 0.92 | 262004
25 | 2025-02-25 | FY25 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 7:18 | 18:23 | 12.45 | Grid | 335091.665 | 100% | 220KV Line Shutdown to GSS End due to Aux. Bus Charge. | 18:25 | 18:46 |  | Restored plant post Grid resumed | Close | 0
26 | 2025-02-25 | FY25 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 7:18 | 18:23 | 12.45 | Grid | 335091.665 | 100% | 220KV Line Shutdown to GSS End due to Relay Inspection work. | 19:31 | 3:27 |  | Restored plant post Grid resumed | Close | 0
27 | 2025-03-03 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:18 | 18:50 | 12.45 | Grid | 335091.665 | 100% | 220KV Line Shutdown to GSS End For erection and stringing work in new 220 KV LV side bay-206 for ICT-2 of New 400/220 KV 500 MVA ICT2 | 19:15 | 4:34 |  | Restored plant post Grid resumed | Close | 0
28 | 2025-03-04 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:14 | 18:48 | 12.45 | Grid | 335091.665 | 100% | 220kV line manually tripped(S/D) from 400kV GSS Bhainsara for erection and stringing work in new 220 KV LV side bay-206 for ICT-2 of New 400/220 KV 500 MVA ICT3 at 400 kV GSS Bhainsara. | 19:15 | 5:37 |  | Restored plant post Grid resumed | Close | 0
29 | 2025-03-05 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:08 | 18:50 | 12.45 | Grid | 335091.665 | 100% | 220KV Line Shutdown to GSS End For erection and stringing work in new 220 KV LV side bay-206 for ICT-2 of New 400/220 KV 500 MVA ICT2 | 19:00 | 1:00 |  | Restored plant post Grid resumed | Close | 0
30 | 2025-03-07 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:11 | 18:50 | 12.45 | Grid | 335091.665 | 100% | 220kV Line manually tripped(S/D) by 400kV GSS, Bhainsara for erection and stringing work in new 220 KV LV side (for New 400/220 KV 500 MVA ICT2) | 19:15 | 0:15 |  | Restored plant post Grid resumed | Close | 0
31 | 2025-03-21 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:01 | 18:56 | 12.45 | Grid | 335091.665 | 100% | 220KV Line Shutdown to GSS End due to Bay maintinance. | 20:01 | 5:20 |  | Restored plant post Grid resumed | Close | 0
32 | 2025-03-29 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 6:49 | 19:01 | 12.45 | Grid | 335091.665 | 100% | 220KV Line Shutdown to GSS End due to Bay maintinance. | 21:50 | 4:29 |  | Restored plant post Grid resumed | Close | 0
33 | 2025-03-30 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 6:46 | 19:03 | 12.45 | Grid | 335091.665 | 100% | 220KV Line Shutdown to GSS End due to Bay maintinance. | 19:30 | 6:52 |  | Restored plant post Grid resumed | Close | 0
34 | 2025-03-31 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 6:45 | 19:02 | 12.45 | Grid | 335091.665 | 100% | 220KV Line Shutdown to GSS End due to Bay maintinance. | 6:45 | 7:18 | 0.55 | Restored plant post Grid resumed | Close | 0.55 | 0.025244 | 6940.6095
35 | 2025-04-14 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:38 | 19:06 | 12.45 | Grid | 335091.665 | 100% | Due to 220KV GSS End Line protection panel sparking issue, Load Down Zero. | 10:45 | 16:10 | 5.4167 | Restored plant post Grid resumed | Close | 5.4167 | 4.876 | 1317626.8056
36 | 2025-04-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:28 | 19:11 | 12.45 | Grid | 335091.665 | 100% | Line Shut-Down for Switchyard Maintinance work | 18:25 | 3:09 | 8.44 | Restored plant post Grid resumed | Close | 8.44
37 | 2025-05-05 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 7:28 | 19:13 | 12.45 | Grid | 335091.665 | 100% | SF6 Line CB tripped Due to Fault at GSS End. (NTPC Feeder R-Phase Jumper broken) | 11:52 | 14:12 | 2.3333 | Restored plant post Grid resumed | Close | 2.3333 | 1.9244 | 525936
38 | 2025-05-12 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:21 | 19:17 | 12.45 | Grid |  | 0% | Load Curtailment 20% of Active Power. | 12:48 | 15:07 |  |  | Close | 0 | 2.125 | 82821.875
39 | 2025-05-13 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:16 | 19:18 | 12.45 | Grid |  | 0% | Load Curtailment 10% of Active Power. | 12:03 | 13:53 |  |  | Close | 0 | 1.79 | 36077.45
40 | 2025-05-18 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:22 | 12.45 | Grid |  | 0% | Load Curtailment 10% of Active Power. | 12:05 | 14:15 |  |  | Close | 0 | 2.08 | 41615.6
41 | 2025-05-19 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:17 | 19:23 | 12.45 | Grid |  | 0% | Load Curtailment 10% of Active Power. | 10:15 | 15:04 |  |  | Close | 0 | 4.445 | 87255.35
42 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 12.45 | Grid |  | 0% | Load Curtailment 10% of Active Power. | 11:21 | 13:34 |  |  | Close | 0 | 2.207 | 43891.7125
43 | 2025-05-31 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 12.45 | Grid |  | 0% | Load Curtailment 10% of Active Power. | 11:45 | 13:50 |  |  | Close | 0 | 1.912 | 38345.16
44 | 2025-06-01 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:31 | 19:25 | 12.45 | Grid |  | 0% | Load Curtailment 20% of Current Load. | 10:06 | 13:45 |  |  | Close | 0 | 3.1 | 196137
45 | 2025-06-02 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:18 | 19:27 | 12.45 | Grid |  | 0% | Load Curtailment 10% of Active Power. | 11:50 | 14:10 |  |  | Close | 0 | 2.16 | 43178.4
46 | 2025-06-03 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:16 | 19:26 | 12.45 | Grid |  | 0% | Load Curtailment 10% of Active Power. | 12:25 | 14:01 |  |  | Close | 0 | 1.46 | 29889.85
47 | 2025-06-04 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:17 | 19:25 | 12.45 | Grid |  | 0% | Load Curtailment 20% of Active Power. | 10:31 | 12:59 |  |  | Close | 0 | 2.2 | 84524
48 | 2025-06-04 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:17 | 19:25 | 12.45 | Grid |  | 0% | Load Curtailment 10% of Active Power. | 12:59 | 14:44 |  |  | Close | 0 | 1.55 | 29775.5
49 | 2025-06-08 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:30 | 12.45 | Grid |  | 0% | Load Curtailment 20% of Current Load. | 15:27 | 16:55 |  |  | Close | 0 | 0.881 | 29456.6755
50 | 2025-06-12 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:32 | 12.45 | Grid |  | 0% | Load Curtailment 20% of Active Power due to 400KV Akal Line trip. | 13:49 | 14:43 |  |  | Close | 0 | 0.842 | 33309.52
51 | 2025-06-12 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:32 | 12.45 | Grid |  | 0% | Load Curtailment 30% of Active Power due to 400KV Akal Line trip. | 14:44 | 16:27 |  |  | Close | 0 | 1.24 | 68676.16
Formulas:
Days = DAY(EOMONTH(GA[[#This Row],[Month Year]],0))

## Inv_SY
| 2013.18 | 2090.61 | 2090.61 | 2077.705 | 2090.61 | 2090.61 | 2090.61 | 2193.85 | 2090.61 | 2116.42 | 2064.8 | 2090.61 | 2064.8 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2111.49 | 2114.1 | 2061.9 | 2088 | 2088 | 1853.1 | 2111.49 | 2114.1 | 2114.1 | 2088 | 2061.9 | 2114.1 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2234.16 | 1985.92 | 2203.13 | 1954.89 | 2161.08 | 2442.96 | 1954.89 | 2234.16 | 1973.16 | 2020.14 | 2145.42 | 2004.48 | 2223.72 | 1973.16 | 2223.72 | 1973.16 | 1973.16 | 2270.7 | 1973.16 | 2239.38 | 2223.72 | 1973.16 | 2192.4 | 2088 | 2102.065 | 1991.43 | 2102.065 | 2212.7 | 2275.92 | 2023.04 | 2244.31 | 1959.82 | 2161.08 | 2129.76 | 1973.16 | 2239.38 | 1941.84 | 2255.04 | 1973.16 | 2223.72 | 2023.04 | 2196.895 | 2054.65 | 2275.92 | 2023.04 | 2181.09 | 2023.04 | 1785.965 | 2192.4 | 2129.76 | 1941.84 | 2255.04 | 2192.4 | 2004.48 | 2004.48 | 2208.06 | 1957.5 | 2035.8 | 2239.38 | 1941.84 | 2255.04 | 1941.84 | 2192.4 | 2004.48 | 2223.72 | 1910.52 | 2223.72 | 2004.48 | 2192.4 | 2004.48 | 2192.4 | 2004.48 | 1973.16 | 2192.4 | 2004.48 | 1941.84 | 2208.06 | 2223.72 | 2192.4 | 2004.48 | 2223.72 | 1973.16 | 2129.76 | 1973.16 | 2098.44 | 1847.88 | 2161.08 | 1973.16 | 2004.48 | 2004.48 | 1988.82 | 1722.6 | 1973.16 | 1753.92 | 2004.48 | 2004.48 | 2255.04 | 1941.84 | 2255.04 | 1973.16 | 2223.72 | 1973.16 | 2004.48 | 2004.48 | 2161.08 | 2255.04 | 2223.72 | 2223.72 | 2223.72 | 2255.04 | 2004.48 | 2223.72 | 2239.38 | 2255.04 | 2255.04 | 2255.04 | 2255.04 | 2004.48 | 2255.04 | 2004.48
Date | IS1_INV1_M1 | IS1_INV1_M2 | IS1_INV2_M1 | IS1_INV2_M2 | IS1_INV3_M1 | IS1_INV3_M2 | IS1_INV4_M1 | IS1_INV4_M2 | IS2_INV1_M1 | IS2_INV1_M2 | IS2_INV2_M1 | IS2_INV2_M2 | IS2_INV3_M1 | IS2_INV3_M2 | IS2_INV4_M1 | IS2_INV4_M2 | IS3_INV1_M1 | IS3_INV1_M2 | IS3_INV2_M1 | IS3_INV2_M2 | IS3_INV3_M1 | IS3_INV3_M2 | IS3_INV4_M1 | IS3_INV4_M2 | IS4_INV1_M1 | IS4_INV1_M2 | IS4_INV2_M1 | IS4_INV2_M2 | IS4_INV3_M1 | IS4_INV3_M2 | IS4_INV4_M1 | IS4_INV4_M2 | IS5_INV1_M1 | IS5_INV1_M2 | IS5_INV2_M1 | IS5_INV2_M2 | IS5_INV3_M1 | IS5_INV3_M2 | IS5_INV4_M1 | IS5_INV4_M2 | IS6_INV1_M1 | IS6_INV1_M2 | IS6_INV2_M1 | IS6_INV2_M2 | IS6_INV3_M1 | IS6_INV3_M2 | IS6_INV4_M1 | IS6_INV4_M2 | IS7_INV1_M1 | IS7_INV1_M2 | IS7_INV2_M1 | IS7_INV2_M2 | IS7_INV3_M1 | IS7_INV3_M2 | IS7_INV4_M1 | IS7_INV4_M2 | IS8_INV1_M1 | IS8_INV1_M2 | IS8_INV2_M1 | IS8_INV2_M2 | IS8_INV3_M1 | IS8_INV3_M2 | IS8_INV4_M1 | IS8_INV4_M2 | IS9_INV1_M1 | IS9_INV1_M2 | IS9_INV2_M1 | IS9_INV2_M2 | IS9_INV3_M1 | IS9_INV3_M2 | IS9_INV4_M1 | IS9_INV4_M2 | IS10_INV1_M1 | IS10_INV1_M2 | IS10_INV2_M1 | IS10_INV2_M2 | IS10_INV3_M1 | IS10_INV3_M2 | IS10_INV4_M1 | IS10_INV4_M2 | IS11_INV1_M1 | IS11_INV1_M2 | IS11_INV2_M1 | IS11_INV2_M2 | IS11_INV3_M1 | IS11_INV3_M2 | IS11_INV4_M1 | IS11_INV4_M2 | IS12_INV1_M1 | IS12_INV1_M2 | IS12_INV2_M1 | IS12_INV2_M2 | IS12_INV3_M1 | IS12_INV3_M2 | IS12_INV4_M1 | IS12_INV4_M2 | IS13_INV1_M1 | IS13_INV1_M2 | IS13_INV2_M1 | IS13_INV2_M2 | IS13_INV3_M1 | IS13_INV3_M2 | IS13_INV4_M1 | IS13_INV4_M2 | IS14_INV1_M1 | IS14_INV1_M2 | IS14_INV2_M1 | IS14_INV2_M2 | IS14_INV3_M1 | IS14_INV3_M2 | IS14_INV4_M1 | IS14_INV4_M2 | IS15_INV1_M1 | IS15_INV1_M2 | IS15_INV2_M1 | IS15_INV2_M2 | IS15_INV3_M1 | IS15_INV3_M2 | IS15_INV4_M1 | IS15_INV4_M2 | IS16_INV1_M1 | IS16_INV1_M2 | IS16_INV2_M1 | IS16_INV2_M2 | IS16_INV3_M1 | IS16_INV3_M2 | IS16_INV4_M1 | IS16_INV4_M2 | IS17_INV1_M1 | IS17_INV1_M2 | IS17_INV2_M1 | IS17_INV2_M2 | IS17_INV3_M1 | IS17_INV3_M2 | IS17_INV4_M1 | IS17_INV4_M2 | IS18_INV1_M1 | IS18_INV1_M2 | IS18_INV2_M1 | IS18_INV2_M2 | IS18_INV3_M1 | IS18_INV3_M2 | IS18_INV4_M1 | IS18_INV4_M2 | IS19_INV1_M1 | IS19_INV1_M2 | IS19_INV2_M1 | IS19_INV2_M2 | IS19_INV3_M1 | IS19_INV3_M2 | IS19_INV4_M1 | IS19_INV4_M2 | IS20_INV1_M1 | IS20_INV1_M2 | IS20_INV2_M1 | IS20_INV2_M2 | IS20_INV3_M1 | IS20_INV3_M2 | IS20_INV4_M1 | IS20_INV4_M2
2025-05-12 | 1.016% | 0.8127% | 0.2497% | 0.8285% | 0.914% | 1.376% | 1.462% | -1.273% | 0.8539% | -1.068% | 1.099% | 0.5773% | 2.108% | 0.04644% | 1.213% | 1.333% | 0.472% | 0.5452% | 0.5724% | 1.237% | -0.3211% | -0.3294% | 0.8386% | 0.1006% | -0.8117% | 1.257% | -2.063% | -2.253% | -0.1161% | 0.3273% | 1.152% | -0.2187% | 7.499% | 7.51% | 8.48% | 7.636% | 1.421% | 0.3674% | 0.5107% | 0.3098% | -1.018% | 4.175% | -0.5066% | 4.523% | -1.32% | -6.418% | 4.369% | -0.9481% | 7.667% | 6.084% | -1.15% | 1.712% | -2.668% | 8.687% | -3.099% | 8.651% | 0.4195% | -3.82% | 0.8145% | -2.755% | -2.869% | 0.3741% | -3.266% | -1.988% | -1.517% | -0.4508% | -1.536% | -3.807% | -4.862% | -0.5595% | -4.431% | -0.3387% | -2.613% | -2.787% | 0.9139% | -4.336% | 1.142% | -3.573% | 1.012% | -3.444% | -0.2039% | -3.105% | -1.026% | -4.325% | -0.2822% | -3.284% | -0.5459% | 2.225% | -2.477% | -2.126% | 1.652% | -3.055% | -2.397% | 1.361% | 0.4042% | -2.553% | 2.065% | 0.9971% | -2.772% | 2.297% | -3.217% | 2.335% | -2.023% | 1.04% | -3.286% | 1.471% | -2.756% | 0.3115% | -2.479% | -0.3461% | -1.907% | 1.788% | 0.6197% | -2.746% | 0.2669% | 2.011% | -2.711% | -2.964% | -2.629% | 0.4677% | -3.278% | 1.014% | -0.6155% | 1.952% | -0.2408% | 2.754% | -1.808% | 1.354% | 0.8849% | 1.174% | 0.1661% | 3.148% | 1.187% | 3.458% | -0.6268% | -0.3547% | -1.629% | 4.37% | -1.408% | 4.44% | -0.5411% | 3.472% | 3.114% | 1.142% | 0.6155% | -1.368% | -0.3206% | -0.7964% | -0.8444% | -2.045% | 3.574% | -0.5016% | -1.102% | -1.453% | -1.478% | -1.607% | -1.365% | 3.393% | -1.141% | 3.911%
2025-05-13 | 0.4071% | 0.8866% | 0.3839% | 0.8496% | 1.154% | 1.697% | 1.775% | -0.09366% | 0.9707% | -0.815% | 1.021% | 0.6233% | 2.144% | 0.09818% | 1.296% | 1.505% | 0.6257% | 0.7297% | 0.829% | 1.348% | -0.06189% | -0.1378% | 0.708% | 0.1063% | -0.922% | 0.2392% | -2.294% | -2.467% | 0.1226% | 0.4084% | 1.051% | 0.1084% | 4.482% | 4.552% | 5.309% | 4.388% | 1.846% | 0.5288% | 0.7649% | 0.5136% | 0.08865% | 3.641% | 0.5459% | 3.829% | -1.005% | -5.001% | 3.868% | 0.2384% | 7.971% | 6.493% | -1.06% | 0.9689% | -2.052% | 9.096% | -2.56% | 9.234% | -0.2143% | -3.001% | 0.05875% | -2.042% | -2.292% | -0.4085% | -2.677% | -2.181% | -1.454% | -1.128% | -1.889% | -3.457% | -4.079% | -1.234% | -3.836% | -1.139% | -2.536% | -3.168% | 0.1512% | -3.868% | 0.3239% | -2.796% | 0.3284% | -2.886% | -0.9492% | -2.898% | -1.682% | -3.685% | -0.9889% | -3.246% | -1.273% | 0.3005% | -1.861% | -2.253% | 1.007% | -2.15% | -1.765% | 0.9982% | 0.02475% | -1.651% | 1.433% | 0.5549% | -1.886% | 1.488% | -2.356% | 1.623% | -1.678% | 0.4338% | -2.618% | 0.7581% | -2.1% | -0.3676% | -1.911% | -0.7734% | -1.325% | 1.084% | -0.07305% | -2.24% | -0.3985% | 1.238% | -2.099% | -2.339% | -2.246% | -0.2783% | -2.72% | 0.2886% | -0.3881% | 1.224% | 0.133% | 1.656% | -1.763% | 0.5642% | 0.2193% | 0.6208% | -0.3572% | 0.9018% | 0.7415% | 2.009% | -1.081% | -0.8268% | -0.6118% | 3.753% | -0.2533% | 3.904% | 0.5435% | 2.954% | 2.826% | 0.7469% | 1.295% | 0.004896% | 0.5059% | 0.02877% | 0.01221% | -1.138% | 3.165% | 0.4637% | 0.084% | -0.4463% | -0.3906% | -0.6741% | -0.3936% | 2.831% | -0.05744% | 3.471%
2025-05-14 | 1.073% | 1.79% | 1.325% | 1.673% | 2.175% | 2.658% | 2.728% | 0.5981% | 1.89% | 0.07123% | 1.925% | 1.497% | 3.099% | 0.919% | 2.251% | 2.384% | 1.584% | 1.584% | 1.761% | 2.275% | 0.835% | 0.7671% | 1.516% | 0.9693% | -0.06648% | -1.016% | -1.473% | -1.635% | 0.8191% | 1.102% | 1.861% | 0.9086% | 2.489% | 2.536% | 3.404% | 2.62% | 2.603% | 1.318% | 1.52% | 1.277% | 0.5561% | 4.4% | 1.051% | 4.319% | -0.4789% | -5.023% | 4.522% | 0.6589% | 1.287% | -0.1357% | -7.085% | -5.444% | -7.896% | 2.661% | -8.368% | 2.664% | -0.5739% | -2.475% | -0.4042% | -1.458% | -1.705% | -0.6977% | -2.019% | -1.328% | -0.8121% | -1.313% | -1.225% | -2.847% | -3.501% | -1.031% | -3.143% | -1.875% | -1.781% | -2.418% | 0.177% | -3.21% | -0.06809% | -2.173% | 0.2975% | -2.262% | -0.6323% | -2.251% | -1.163% | -3.312% | -0.6667% | -2.512% | -0.9433% | -1.153% | -1.543% | -1.617% | 0.5575% | -1.825% | -1.292% | 1.329% | 0.2313% | -1.311% | 1.219% | 1.094% | -1.587% | 1.38% | -2.019% | 1.392% | -1.043% | 0.5952% | -2.204% | -0.09605% | -1.68% | -0.2101% | -1.344% | -0.9008% | -0.8323% | 1.198% | -0.311% | -1.778% | -0.8% | 0.7124% | -1.701% | -1.845% | -1.698% | -0.1673% | -2.255% | 0.1557% | 0.1044% | 0.9517% | 0.6303% | 0.1822% | -1.057% | 0.2418% | 0.1772% | 0.6146% | -0.6939% | -0.7499% | 0.4254% | 0.06001% | -1.153% | -0.9299% | -0.3678% | 4.36% | -0.02781% | 4.679% | 0.8143% | 3.545% | 3.622% | 1.299% | 2.261% | 0.8502% | 0.8587% | 0.311% | 0.2368% | -0.9022% | 3.993% | 0.7758% | 0.5586% | -0.1232% | -0.1081% | -0.3857% | -0.05722% | 3.743% | 0.2254% | 4.339%
2025-05-15 | 0.5233% | 1.271% | 1.043% | 1.211% | 2.074% | 2.228% | 2.357% | 0.203% | 1.437% | -0.3476% | 1.376% | 0.9272% | 2.607% | 0.3793% | 1.725% | 1.917% | 1.163% | 1.192% | 1.338% | 1.819% | 0.4847% | 0.3484% | 1.046% | 0.5242% | -0.4929% | -1.566% | -1.967% | -2.165% | 0.4152% | 0.6106% | 1.42% | 0.5751% | 1.724% | 1.76% | 2.604% | 1.797% | 2.255% | 0.879% | 1.108% | 0.879% | 0.3601% | 3.975% | 0.8311% | 3.796% | -1.25% | -5.695% | 4.024% | 0.4896% | 8.328% | 6.776% | -0.6614% | 1.06% | -1.741% | 9.534% | -2.232% | 9.469% | -1.204% | -2.814% | -1.005% | -1.758% | -1.996% | -1.199% | -2.553% | -2.032% | -1.146% | -2.182% | -1.684% | -3.169% | -3.841% | -1.57% | -3.494% | -2.449% | -2.178% | -2.87% | -0.4097% | -3.467% | -0.6367% | -2.424% | -0.1956% | -2.5% | -1.128% | -2.402% | -1.653% | -3.362% | -1.2% | -2.812% | -1.276% | -1.625% | -1.595% | -1.935% | 0.1415% | -1.842% | -1.617% | 0.5462% | -0.5967% | -1.284% | 0.8759% | 0.8143% | -1.581% | 0.9539% | -2.076% | 0.9673% | -1.306% | 0.1336% | -2.308% | -0.5803% | -1.809% | -0.7677% | -1.559% | -1.238% | -1.004% | 0.6727% | -0.7476% | -1.837% | -0.8099% | 0.3975% | -1.885% | -1.982% | -1.92% | -0.745% | -2.408% | -0.4295% | -0.05455% | 0.6682% | 0.2207% | -0.4407% | -1.475% | -0.3768% | -0.3535% | 0.1709% | -0.89% | -1.301% | -0.3957% | -0.7452% | -1.539% | -1.338% | -0.1901% | 4.049% | 0.1838% | 4.431% | 0.9438% | 3.137% | 3.168% | 0.9264% | 2.019% | 0.7862% | 1.032% | 0.5376% | 0.4806% | -0.7161% | 3.75% | 1.012% | 0.6602% | 0.057% | 0.1082% | -0.1901% | 0.1507% | 3.518% | 0.2825% | 4.054%
2025-05-16 | 0.426% | 1.429% | 1.048% | 1.322% | 2.158% | 2.384% | 2.375% | 0.1748% | 1.604% | -0.3528% | 1.506% | 0.9715% | 2.886% | 0.448% | 1.932% | 2.117% | 1.402% | 1.368% | 1.592% | 2.073% | 0.7362% | 0.5416% | 1.38% | 0.8548% | -0.3786% | -1.661% | -1.77% | -1.883% | 0.51% | 0.8314% | 1.703% | 0.7568% | 1.834% | 1.878% | 2.717% | 1.852% | 2.291% | 0.9387% | 1.217% | 1.031% | 0.5012% | 4.245% | 1.022% | 4.003% | -0.8245% | -5.765% | 4.327% | 0.537% | 8.16% | 6.786% | -0.4092% | 0.9718% | -1.681% | 9.696% | -2.047% | 9.658% | -1.351% | -2.749% | -1.161% | -1.787% | -2.159% | -1.425% | -2.586% | -1.904% | -0.9086% | -1.912% | -1.647% | -3.18% | -3.776% | -1.781% | -3.496% | -2.689% | -2.096% | -3.06% | -0.6317% | -3.544% | -0.8096% | -2.452% | -0.316% | -2.572% | -1.331% | -2.471% | -1.849% | -3.544% | -1.347% | -2.794% | -1.483% | -1.85% | -1.745% | -1.842% | -0.09486% | -1.773% | -1.329% | 0.9734% | -0.07622% | -1.149% | 0.8806% | 0.7242% | -1.67% | 0.8324% | -2.149% | 0.745% | -1.181% | -0.06076% | -2.333% | -0.8012% | -1.801% | -1.009% | -1.404% | -1.539% | -0.6992% | 0.4347% | -1.046% | -1.921% | -1.014% | 0.2235% | -1.847% | -2.05% | -1.761% | -1.158% | -2.535% | -0.7326% | 0.05195% | 0.4436% | 0.4214% | -0.6847% | -1.363% | -0.6896% | -0.4505% | 0.2509% | -1.091% | -1.385% | -0.2424% | -0.8106% | -1.755% | -1.603% | -0.514% | 3.758% | -0.08002% | 4.351% | 0.6401% | 3.038% | 3.281% | 0.6984% | 2.595% | 1.512% | 0.7508% | 0.214% | 0.09001% | -1.061% | 3.739% | 0.7464% | 0.4869% | -0.1212% | -0.05037% | -0.4966% | -0.007695% | 3.475% | 0.1637% | 4.119%
2025-05-17 | 0.5792% | 1.179% | 0.843% | 1.006% | 1.878% | 2.143% | 2.309% | 0.1392% | 1.258% | -0.46% | 1.242% | 0.6953% | 2.47% | 0.1899% | 1.635% | 1.739% | 0.9469% | 1.028% | 1.163% | 1.752% | 0.2853% | 0.2064% | 1.04% | 0.4214% | -0.5984% | -1.388% | -1.959% | -2.097% | 0.1935% | 0.4476% | 1.336% | 0.3532% | 1.992% | 2.063% | 2.953% | 2.117% | 2.002% | 0.6638% | 0.9261% | 0.7069% | 0.01912% | 4.014% | 0.4189% | 4.022% | -0.8102% | -5.4% | 4.17% | 0.1588% | 8.103% | 6.655% | -0.6867% | 1.308% | -1.788% | 9.441% | -2.378% | 9.311% | -0.8882% | -2.964% | -0.7048% | -1.963% | -2.213% | -1.018% | -2.461% | -1.759% | -1.085% | -1.433% | -1.589% | -3.302% | -3.993% | -1.228% | -3.628% | -2.079% | -2.256% | -2.773% | -0.1457% | -3.656% | -0.3093% | -2.613% | 0.1616% | -2.641% | -0.8515% | -2.593% | -1.404% | -3.482% | -0.8594% | -2.835% | -1.118% | -1.298% | -1.836% | -1.932% | 0.336% | -1.903% | -1.374% | 1.277% | 0.2575% | -1.44% | 1.175% | 0.9114% | -1.779% | 1.254% | -2.277% | 1.14% | -1.447% | 0.3787% | -2.521% | -0.3662% | -2.011% | -0.524% | -1.789% | -1.247% | -1.206% | 0.9733% | -0.4745% | -1.965% | -0.609% | 0.7335% | -1.948% | -2.138% | -2.036% | -0.6548% | -2.574% | -0.2092% | -0.2193% | 0.949% | 0.1602% | -0.1161% | -1.531% | -0.1147% | 0.1179% | 0.7173% | -0.6683% | -0.8142% | 0.3654% | -0.06639% | -1.138% | -0.9565% | -0.5097% | 4.06% | -0.1139% | 4.307% | 0.6138% | 3.144% | 3.211% | 1.014% | 1.679% | 0.2663% | 0.7397% | 0.2572% | 0.2204% | -0.9291% | 3.705% | 0.7245% | 0.3799% | -0.3086% | -0.2451% | -0.4969% | -0.1681% | 3.465% | 0.1522% | 4.034%
2025-05-18 | 0.5591% | 0.8699% | 0.51% | 0.5522% | 1.553% | 1.74% | 1.969% | -0.2864% | 0.9648% | -0.8765% | 1.001% | 0.3927% | 2.204% | -0.09961% | 1.39% | 1.442% | 0.6433% | 0.68% | 0.8675% | 1.468% | -0.03042% | -0.1025% | 0.8505% | 0.1787% | -0.8424% | 0.5508% | -2.183% | -2.336% | -0.1807% | 0.1587% | 1.105% | -0.004704% | 4.458% | 4.49% | 5.432% | 4.536% | 1.545% | 0.2874% | -0.1531% | 0.2954% | -0.4645% | 3.799% | -0.0961% | 4.025% | -1.619% | -5.917% | 4.006% | -0.2979% | 7.686% | 6.221% | -0.9653% | 1.442% | -2.245% | 9.021% | -2.749% | 8.911% | 0.02009% | -3.439% | 0.4276% | -2.408% | -2.68% | -0.05599% | -3.462% | -2.046% | -1.194% | -0.7099% | -1.743% | -3.743% | -5.141% | -0.9692% | -4.095% | -0.7282% | -2.883% | -2.957% | 0.5147% | -4.107% | 0.7992% | -3.082% | 0.8977% | -3.057% | -0.6113% | -3.006% | -1.39% | -3.961% | -0.6138% | -3.169% | -0.8166% | 0.8512% | -2.165% | -2.146% | 1.345% | -2.308% | -1.83% | 1.373% | 0.458% | -1.922% | 1.927% | 0.843% | -2.189% | 1.968% | -2.664% | 1.563% | -1.732% | 0.656% | -2.915% | 1.134% | -2.431% | -0.08466% | -2.095% | -0.4367% | -1.554% | 1.374% | 0.314% | -2.327% | 0.003556% | 1.757% | -2.309% | -2.563% | -2.289% | 0.02103% | -3.023% | 0.5595% | -0.4878% | 1.486% | 0.05309% | 1.971% | -1.816% | 0.8393% | 0.5229% | 0.8674% | 0.0797% | 1.321% | 1.023% | 2.393% | -0.3726% | -0.2711% | -0.9089% | 4.138% | -0.5213% | 4.212% | 0.1889% | 3.071% | 2.994% | 1.119% | 1.311% | -0.1115% | 0.3232% | -0.1779% | -0.235% | -1.355% | 3.539% | 0.3194% | -0.05061% | -0.7654% | -0.6485% | -0.8727% | -0.5938% | 3.236% | -0.2616% | 3.795%
2025-05-19 | 1.082% | 0.5889% | 0.1851% | 0.5537% | 0.9796% | 1.143% | 1.406% | -1.354% | 0.6181% | -1.353% | 0.876% | 0.1868% | 1.918% | -0.3077% | 1.136% | 1.16% | 0.3651% | 0.3513% | 0.4964% | 1.254% | -0.3906% | -0.3252% | 0.976% | 0.1627% | -1.102% | 2.493% | -2.025% | -2.227% | -0.4815% | -0.05001% | 1.092% | -0.5825% | 6.771% | 6.772% | 7.765% | 6.824% | 1.175% | 0.1511% | -0.7496% | 0.0903% | -1.704% | 4.25% | -1.256% | 4.807% | -2.256% | -7.505% | 4.676% | -1.58% | 7.397% | 5.753% | -1.23% | 2.165% | -2.912% | 8.341% | -3.382% | 8.287% | 1.343% | -4.295% | 1.832% | -3.175% | -3.268% | 1.268% | -3.931% | -1.59% | -1.11% | 0.4369% | -1.432% | -4.139% | -6.029% | -0.05842% | -4.75% | 0.7242% | -3.098% | -2.251% | 1.69% | -4.752% | 2.14% | -4.084% | 1.958% | -3.773% | 0.3043% | -3.386% | -0.6424% | -4.86% | 0.28% | -3.374% | -0.09947% | 2.816% | -2.705% | -2.182% | 2.643% | -3.347% | -2.374% | 2.221% | 1.318% | -2.772% | 3.003% | 1.351% | -3.101% | 3.12% | -3.613% | 2.65% | -2.223% | 1.732% | -3.674% | 2.686% | -3.157% | 0.8627% | -2.537% | 0.5846% | -2.218% | 2.276% | 1.458% | -2.865% | 0.9845% | 3.04% | -2.977% | -3.282% | -2.85% | 1.073% | -3.688% | 1.716% | -0.8201% | 2.509% | -0.1168% | 3.919% | -2.076% | 2.111% | 1.582% | 1.787% | 1.389% | 3.552% | 2.095% | 4.43% | 0.7004% | 0.8129% | -2.386% | 4.743% | -1.948% | 4.598% | -1.194% | 3.656% | 3.159% | 1.82% | 0.2952% | -1.946% | -0.7961% | -1.253% | -1.316% | -2.541% | 3.797% | -1.22% | -1.321% | -2.098% | -2.323% | -2.363% | -1.893% | 3.633% | -1.541% | 4.063%
2025-05-20 | 0.05043% | 1.446% | 1.121% | 1.108% | 2.065% | 2.279% | 2.737% | 0.6083% | 1.545% | -0.355% | 1.345% | 0.9576% | 2.439% | 0.3441% | 1.853% | 1.967% | 1.239% | 0.9443% | 1.33% | 1.94% | 0.5946% | 0.3751% | 0.9285% | 0.5307% | -1.658% | -2.009% | -2.058% | -2.203% | 0.3945% | 0.6664% | 1.351% | 0.1481% | 1.787% | 1.798% | 2.67% | 1.764% | 2.402% | 1.012% | -0.2945% | 1.01% | 0.6422% | 3.751% | 1.144% | 3.493% | -2.254% | -5.54% | 3.728% | 0.7712% | 8.392% | 6.983% | -0.4641% | 0.729% | -1.438% | 9.859% | -1.931% | 9.685% | -1.527% | -2.443% | -1.367% | -1.463% | -1.817% | -1.645% | -3.031% | -2.021% | -1.234% | -2.224% | -1.86% | -2.979% | -4.497% | -1.87% | -3.247% | -2.769% | -2.698% | -2.356% | -0.8924% | -3.202% | -1.104% | -2.093% | -0.6658% | -2.283% | -1.473% | -2.204% | -1.939% | -3.01% | -1.447% | -2.654% | -1.544% | -1.925% | -1.374% | -1.803% | -0.3171% | -1.381% | -0.9443% | 0.7764% | -0.3195% | -1.065% | 0.5649% | 0.4949% | -1.262% | 0.6454% | -1.766% | -0.3408% | -1.084% | -0.4061% | -1.988% | -1.029% | -1.54% | -1.191% | -1.416% | -1.836% | -0.7358% | 0.3155% | -0.9616% | -1.452% | -0.9528% | 0.1359% | -1.405% | -1.593% | -1.481% | -1.088% | -2.075% | -0.7687% | 0.1478% | 0.2981% | 0.3319% | -0.7766% | -1.276% | -0.7048% | -0.4935% | 0.2485% | -1.097% | -1.371% | -0.2781% | -0.7566% | -1.846% | -1.553% | 0.173% | 3.726% | 0.6162% | 4.266% | 1.301% | 2.893% | 3.11% | 0.6089% | 2.483% | 1.573% | 1.424% | 0.9902% | 0.806% | -0.3166% | 3.744% | 1.054% | 1.068% | 0.4883% | 0.1585% | -0.164% | 0.6844% | 3.465% | 0.9096% | 4.101%
2025-05-21 | 0.5975% | 1.41% | 0.966% | 1.114% | 1.917% | 2.105% | 2.473% | 0.02806% | 1.415% | -0.6412% | 1.328% | 0.7308% | 2.497% | 0.1766% | 1.83% | 1.958% | 1.25% | 0.8858% | 1.363% | 1.994% | 0.6644% | 0.4578% | 1.33% | 0.7688% | -1.342% | -1.281% | -1.787% | -1.915% | 0.3373% | 0.6738% | 1.591% | 0.1429% | 1.563% | 1.629% | 2.631% | 1.811% | 2.243% | 0.9413% | -0.1796% | 0.9644% | 0.1602% | 4.208% | 0.6594% | 4.173% | -2.663% | -6.827% | 4.277% | 0.2294% | 8.087% | 6.727% | -0.4559% | 1.357% | -1.735% | 9.604% | -2.141% | 9.43% | -0.9527% | -2.945% | -0.7461% | -1.882% | -2.132% | -1.057% | -3.48% | -1.884% | -0.9283% | -1.409% | -1.48% | -3.178% | -4.773% | -1.271% | -3.533% | -2.267% | -2.598% | -2.16% | -0.2536% | -3.576% | -0.4574% | -2.85% | 0.04537% | -2.69% | -0.9555% | -2.539% | -1.527% | -3.507% | -0.9659% | -2.847% | -0.7747% | -1.318% | -1.769% | -1.819% | 0.307% | -1.954% | -1.467% | 1.115% | -0.0336% | -1.38% | 1.32% | 1.058% | -1.744% | 1.3% | -2.322% | 0.3858% | -1.256% | 0.3917% | -2.385% | -0.3457% | -1.919% | -0.5868% | -1.475% | -0.9325% | -0.982% | 0.9722% | -0.4123% | -1.863% | -0.3472% | 0.7336% | -1.849% | -2.075% | -1.804% | -0.4895% | -2.586% | -0.2266% | -0.1356% | 0.7936% | 0.3358% | -0.2164% | -1.455% | -0.1449% | 0.1159% | 0.7511% | -0.4782% | -0.8203% | 0.203% | -0.3281% | -1.158% | -0.947% | -0.5121% | 4.157% | -0.09757% | 4.461% | 0.5% | 3.174% | 3.193% | 1.061% | 2.05% | 0.8544% | 0.7862% | 0.2775% | 0.1434% | -0.9945% | 3.848% | 0.363% | 0.4701% | -0.1469% | -0.5178% | -0.8423% | -0.06898% | 3.646% | 0.2841% | 4.279%
2025-05-22 | 1.252% | 2.209% | 1.737% | 1.957% | 2.718% | 2.928% | 3.255% | 0.9267% | 2.303% | 0.2133% | 2.074% | 1.464% | 3.426% | 0.922% | 2.607% | 2.867% | 2.095% | 1.637% | 2.278% | 2.919% | 1.533% | 1.263% | 2.09% | 1.587% | -0.7163% | -1.198% | -1.033% | -1.331% | 1.155% | 1.46% | 2.424% | 1.003% | 2.12% | 2.235% | 3.258% | 2.409% | 3.201% | 1.813% | 0.6615% | 1.78% | 1.143% | 4.759% | 1.667% | 4.548% | -1.66% | -5.543% | 4.988% | 1.263% | -8.997% | -9.922% | -16.2% | -15.05% | -17.13% | -7.538% | -17.42% | -7.897% | -0.537% | -2.015% | -0.3191% | -1.003% | -1.305% | -0.5777% | -3.179% | -1.345% | -0.1063% | -1.043% | -0.7907% | -2.37% | -3.852% | -0.7879% | -2.626% | -1.798% | -1.809% | -1.437% | 0.2728% | -2.662% | 0.01558% | -1.49% | 0.4906% | -1.704% | -0.4287% | -1.405% | -1.012% | -2.268% | -0.4781% | -1.928% | -0.2406% | -0.8148% | -0.678% | -0.84% | 0.9355% | -0.5433% | -0.06076% | 2.101% | 0.9998% | -0.09277% | 1.892% | 1.697% | -0.4741% | 1.871% | -1.024% | 0.9473% | -0.2246% | 0.8427% | -1.23% | 0.1501% | -0.7462% | -0.07874% | -0.503% | -0.5166% | 0.1779% | 1.458% | 0.107% | -0.6937% | 0.2715% | 1.286% | -0.6871% | -0.845% | -0.7012% | 0.05874% | -1.4% | 0.3094% | 0.9908% | 1.386% | 1.315% | 0.2818% | -0.4394% | 0.3659% | 0.553% | 1.374% | 0.05893% | -0.3078% | 1.008% | 0.31% | -0.6925% | -0.3938% | 0.889% | 4.794% | 1.285% | 5.263% | 1.853% | 3.843% | 4.061% | 1.802% | 2.763% | 2.668% | 2.101% | 1.62% | 1.447% | 0.3136% | 4.776% | 1.679% | 1.759% | 1.171% | 0.7923% | 0.3784% | 1.219% | 4.407% | 1.635% | 5.129%
2025-05-23 | 0.5239% | 0.9799% | 0.7657% | 0.8679% | 1.718% | 1.83% | 2.002% | -0.4942% | 1.08% | -0.8056% | 0.8751% | 0.2421% | 2.085% | -0.2727% | 1.516% | 1.615% | 0.8808% | 0.5674% | 0.9767% | 1.655% | 0.2853% | 0.04764% | 0.9408% | 0.3754% | -1.67% | 0.4066% | -2.159% | -2.659% | 0.01602% | 0.3058% | 1.19% | -0.2417% | 4.169% | 4.435% | 5.464% | 4.62% | 2.008% | 0.6386% | -0.5053% | 0.6138% | 0.03228% | 4.05% | 0.5355% | 4.317% | -2.7% | -6.666% | 4.312% | 0.05622% | 7.795% | 6.369% | -0.8739% | 1.42% | -2.061% | 9.225% | -2.492% | 8.917% | 0.1235% | -3.197% | 0.4267% | -2.188% | -2.433% | 0.0032% | -3.992% | -2.044% | -1.276% | -0.7011% | -1.82% | -3.538% | -5.167% | -0.9532% | -3.978% | -0.7547% | -2.984% | -2.605% | 0.5791% | -3.978% | 0.7091% | -2.843% | 0.6935% | -2.978% | -0.7327% | -2.959% | -1.551% | -4.011% | -0.7971% | -3.419% | -0.7789% | 1.26% | -2.39% | -2.261% | 1.418% | -2.312% | -1.653% | 1.482% | 0.4891% | -1.878% | 1.774% | 0.7302% | -2.291% | 2.004% | -2.748% | 1.357% | -1.775% | 0.6283% | -2.836% | 1.16% | -2.41% | -0.1695% | -1.983% | -0.3388% | -1.451% | 1.36% | 0.345% | -2.344% | -0.5114% | 1.596% | -2.405% | -2.555% | -2.306% | 0.06058% | -2.994% | 0.5148% | -0.5091% | 1.501% | -0.06266% | 2.259% | -1.9% | 0.757% | 0.4174% | 0.7776% | 0.2124% | 1.717% | 0.9238% | 2.444% | -0.5839% | -0.3471% | -1.087% | 4.038% | -0.6464% | 4.219% | -0.06849% | 3.022% | 2.789% | 1.177% | 1.531% | 0.4282% | 0.2291% | -0.1948% | -0.3638% | -1.496% | 3.475% | -0.1948% | -0.1852% | -0.7146% | -1.069% | -1.442% | -0.6331% | 3.237% | -0.2818% | 3.797%
2025-05-24 | 0.4657% | 1.725% | 1.362% | 1.565% | 2.282% | 2.456% | 2.804% | 0.7103% | 1.762% | 0.01456% | 1.016% | 0.46% | 2.342% | -0.008347% | 1.59% | 2.019% | 0.8274% | 0.3865% | 1.259% | 1.834% | 0.4252% | 0.187% | 0.4874% | 0.3236% | -2.193% | -3.225% | -2.313% | -3.363% | 0.1455% | 0.2792% | 0.9779% | -0.07092% | 1.228% | 1.494% | 2.408% | 1.482% | 2.366% | 0.8896% | -0.5171% | 0.6707% | 1.359% | 4.303% | 2.002% | 4.163% | -2.453% | -5.985% | 3.838% | 0.8661% | 8.36% | 7.005% | -0.2865% | 0.3569% | -1.476% | 9.744% | -1.9% | 9.468% | -1.969% | -2.511% | -1.572% | -1.403% | -1.884% | -1.77% | -3.209% | -2.602% | -1.656% | -2.575% | -2.257% | -3.224% | -4.367% | -2.238% | -3.715% | -3.191% | -2.881% | -2.806% | -1.137% | -3.395% | -1.169% | -2.043% | -0.6981% | -2.216% | -1.942% | -2.617% | -2.509% | -3.852% | -1.85% | -3.34% | -1.897% | -2.151% | -1.824% | -1.979% | -0.3622% | -1.716% | -1.485% | 0.2263% | -1.087% | -1.482% | 0.2636% | 0.2425% | -1.714% | 0.6914% | -1.95% | -0.1023% | -0.9957% | -0.2369% | -1.858% | -0.807% | -1.43% | -0.5788% | -0.9071% | -1.316% | 0.1516% | 1.294% | -1.178% | -1.505% | -1.863% | 0.04377% | -1.765% | -1.273% | -1.786% | -0.5855% | -1.346% | 0.4252% | 0.7582% | 1.467% | 1.944% | 0.9412% | 0.2337% | 0.9531% | 0.3122% | 0.8453% | 0.614% | -0.173% | 1.035% | 0.5863% | -1.331% | -1.011% | -0.3426% | 3.891% | 0.546% | 4.74% | 1.014% | 3.416% | 3.515% | 1.568% | 2.843% | 3.33% | 1.119% | 0.9821% | 0.8925% | -0.3284% | 4.191% | 1.331% | -0.1146% | -0.3838% | -0.5971% | -1.182% | 0.111% | 3.443% | 0.415% | 3.986%
2025-05-25 | 7.417% | -4.772% | -4.502% | -3.95% | -6.64% | -3.358% | -17.46% | -21.15% | -11.45% | -12.63% | -7.724% | -15.3% | -9.257% | -8.14% | -6.672% | -1.281% | 2.48% | 1.387% | -1.671% | -15.13% | 5.555% | 1.197% | 12.25% | 10.59% | -12.67% | -15.38% | -15.93% | -7.91% | 5.514% | -1.226% | 7.21% | 4.158% | 3.738% | 1.948% | -4.62% | -2.04% | 2.753% | -0.7141% | -0.8231% | 10.16% | 10.28% | 10.75% | 10.96% | 10.52% | 3.975% | 2.722% | 6.639% | 12.33% | 12.53% | 11.58% | 7.591% | -1.182% | 5.072% | 1.078% | 6.999% | 15.14% | 3.118% | 4.31% | 2.54% | -4.335% | -18.5% | -16.31% | -7.973% | -7.31% | 0.7335% | 6.96% | 3.812% | 6.012% | 4.907% | 6.954% | 5.874% | 5.8% | 3.088% | 3.567% | 3.902% | -7.939% | -12.76% | 0.2426% | -16.52% | -17.54% | 4.473% | 5.77% | -3.858% | 5.539% | 0.5995% | -3.262% | -5.057% | 1.614% | -18.48% | 1.156% | 1.769% | -4.857% | 0.4113% | -2.784% | -5.144% | -10.77% | -15.03% | -0.6094% | -0.7502% | -1.183% | 0.5214% | 3.935% | 3.713% | -2.04% | 2.106% | 1.361% | 3.359% | 2.913% | 1.507% | -0.6448% | -1.626% | 5.286% | 1.53% | -3.083% | -1.128% | -0.1819% | -3.242% | 6.075% | 1.551% | 5.084% | 5.101% | 5.315% | 1.867% | 6.634% | -0.3155% | 5.728% | 5.579% | 10.33% | -10.91% | -19.26% | -6.691% | -9.688% | -5.777% | -12.36% | -11.05% | -9.417% | 6.324% | 5.815% | 2.936% | 4.962% | -1.946% | -8.08% | -4.78% | -8.715% | 5.061% | 6.259% | 7.9% | 8.888% | 7.195% | 5.265% | 4.675% | 4.138% | 11.2% | 10.72% | 5.476% | 6.982% | 5.232% | 6.544% | 11.32% | 10.18%
2025-05-26 | 4.288% | -0.7409% | -3.066% | 0.6417% | -5.418% | -1.8% | -11.94% | -9.553% | -8.141% | -2.391% | -6.308% | -17.17% | 4.384% | -9.297% | 2.825% | 5.117% | 4.847% | 5.524% | 3.995% | 0.8415% | 3.191% | 2.599% | 6.199% | 5.649% | 2.762% | -0.6349% | 1.278% | 1.149% | 0.417% | -7.753% | 6.143% | 5.814% | 1.945% | 3.632% | 3.925% | 0.5571% | 3.119% | 0.6959% | 2.327% | 4.917% | 7.26% | 7.94% | 6.867% | 7.362% | 1.08% | -1.571% | 2.731% | 7.996% | 8.963% | 7.258% | 4.07% | 2.789% | 2.43% | 6.195% | 3.878% | 10.84% | -0.1038% | 1.664% | 1.268% | 3.389% | 1.196% | -0.09246% | -5.231% | -5.561% | -4.196% | 2.646% | 2.628% | 2.361% | 2.597% | 3.024% | 2.479% | 1.258% | 2.41% | 2.02% | 3.697% | 1.912% | 2.372% | 3.234% | -3.202% | -4.154% | 2.22% | 1.918% | -5.735% | 1.894% | -2.487% | -5.86% | -8.869% | -0.4981% | -23.24% | -0.7656% | -2.658% | -9.887% | -3.474% | -6.525% | -8.339% | -15% | -20.03% | -3.013% | -4.184% | -3.124% | -1.588% | 1.695% | 1.176% | -4.877% | 0.236% | -1.83% | 1.246% | 2.445% | -0.6342% | -2.137% | -3.463% | 4.9% | 1.059% | -3.949% | -1.553% | -1.533% | -4.662% | 4.614% | -0.4711% | 3.724% | 3.95% | 3.984% | 0.5594% | 5.486% | -3.785% | 3.36% | 3.801% | 5.611% | -14.88% | -23.62% | -11.18% | -14.4% | -6.622% | -12.34% | -12.86% | -11.75% | 5.133% | 3.498% | 4.843% | 5.853% | -1.978% | -9.803% | -6.211% | -11.7% | 5.597% | 5.9% | 5.109% | 5.463% | 5.061% | 4.024% | 5.725% | 4.119% | 9.466% | 7.231% | 7.342% | 6.618% | 5.491% | 6.16% | 8.925% | 6.413%
2025-05-27 | 2.31% | 1.333% | -0.9527% | 0.7892% | 0.1598% | 0.2904% | -7.054% | -5.521% | -8.802% | -1.19% | -6.713% | -17.51% | 3.187% | -10.31% | 1.996% | 3.125% | 3.397% | 3.568% | 3.387% | 2.881% | 2.208% | 1.864% | 3.297% | 3.125% | 1.555% | -0.8221% | -0.3966% | -1.046% | 0.8651% | -2.475% | 3.703% | 3.424% | 2.615% | 2.081% | 4.438% | 2.111% | 3.63% | 1.526% | 3.002% | 2.904% | 5.836% | 6.215% | 5.427% | 5.697% | -1.754% | -4.111% | 1.394% | 6.469% | 6.053% | 5.265% | 1.683% | 1.73% | 0.8828% | 7.018% | 1.287% | 8.076% | -2.085% | -0.2915% | -0.09319% | 1.81% | 1.171% | -0.4106% | -6.228% | -7.017% | -2.412% | 0.1322% | 0.3488% | 0.404% | 0.1932% | 0.9406% | 0.09676% | -0.7529% | 0.3512% | 0.153% | 1.558% | 0.2668% | 1.244% | 1.712% | -0.1087% | -1.369% | 1.152% | 1.475% | -7.192% | 1.119% | -3.96% | -7.072% | -4.033% | -0.7506% | -20.54% | 0.1476% | -4.59% | -10.8% | -5.158% | -7.502% | -9.18% | -8.615% | -6.638% | 1.075% | -0.342% | -0.2489% | -0.7656% | 2.496% | 1.01% | 0.2367% | 0.6346% | 0.5928% | 1.233% | 0.9912% | 0.2258% | -0.8245% | -0.03029% | 2.649% | 1.226% | -0.8107% | 0.6873% | 0.229% | -1.844% | 2.48% | -0.8542% | 1.851% | 1.908% | 1.974% | 0.4291% | 2.958% | -2.148% | 1.616% | 1.351% | 2.118% | -15.51% | -23.79% | -6.607% | -14.16% | -5.564% | -4.84% | -6.87% | -5.023% | 4.273% | 3.132% | 5.091% | 6.105% | -0.8312% | -5.913% | -3.064% | -4.324% | 5.651% | 5.167% | 4.526% | 4.907% | 4.13% | 3.857% | 5.658% | 5.837% | 6.849% | 5.793% | 6.156% | 5.495% | 5.561% | 5.48% | 6.794% | 5.928%
2025-05-28 | -1.72% | -0.9817% | -0.7355% | -0.4762% | -0.3001% | 0.8964% | -0.09021% | -0.6433% | 0.0265% | -2.8% | 0.115% | -0.2314% | 1.186% | -0.2913% | -0.3717% | 0.7856% | -0.305% | 0.02061% | 0.308% | 0.7493% | -0.5791% | -1.436% | -0.2881% | -0.5388% | -2.099% | -3.431% | -3.31% | -4.241% | -0.4632% | -0.4936% | 0.3533% | -0.1461% | 1.003% | 1.413% | 1.938% | 0.915% | 2.061% | 0.06181% | 0.6679% | 0.5875% | 2.943% | 3.367% | 3.602% | 3.608% | -1.304% | -0.8419% | 2.733% | 2.882% | 7.295% | 6.424% | -1.382% | -0.5709% | -1.721% | 7.913% | -1.727% | 9.55% | -2.532% | -1.856% | -2.539% | -1.062% | -1.862% | -2.633% | -4.106% | -4.544% | -2.319% | -2.786% | -2.544% | -2.536% | -2.716% | -2.251% | -2.995% | -3.272% | -2.515% | -3.165% | -1.615% | -2.87% | -2.07% | -1.391% | -2.007% | -2.488% | -1.479% | -1.478% | -2.253% | -1.248% | -1.589% | -2.492% | -2.02% | -1.78% | -1.589% | -1.34% | -0.49% | -0.2107% | -0.9694% | -1.033% | -2.554% | -1.282% | -1.183% | 0.2158% | 0.1988% | 0.4635% | -0.02155% | 0.605% | -0.3325% | -0.6425% | -0.5201% | -0.9524% | 0.04413% | -0.8287% | -0.2848% | -0.9862% | -0.4148% | 0.4918% | -0.4459% | -0.5046% | -0.7643% | 0.341% | -1.058% | 0.3143% | -0.3335% | -0.3316% | -0.2205% | -0.02557% | 0.117% | 1.078% | 0.8981% | -0.07584% | -0.2543% | 0.006639% | -1.002% | -1.829% | -2.177% | -2.504% | -1.596% | -2.18% | -3.829% | -2.541% | 2.97% | 3.239% | 3.377% | 3.8% | 3.6% | 2.171% | 2.495% | 0.2289% | 3.459% | 3.544% | 3.441% | 3.283% | 3.191% | 2.268% | 3.422% | 4.051% | 3.884% | 3.275% | 3.718% | 3.386% | 3.103% | 3.267% | 3.693% | 2.959%
2025-05-29 | -1.496% | -0.7446% | -0.5909% | -0.3672% | -0.2348% | 1.603% | 1.153% | 0.4757% | 0.5308% | -3.416% | 0.06409% | -0.3608% | 1.34% | -0.756% | -0.5555% | 0.5279% | -0.6949% | -0.2854% | 0.03059% | 0.6129% | -0.9236% | -1.848% | -0.6469% | -1.037% | -2.845% | -4.154% | -4.83% | -5.134% | -0.9723% | -1.231% | -0.5443% | -1.033% | 0.6177% | 0.3914% | 1.261% | 0.2922% | 0.3227% | -1.841% | -0.1766% | 0.03441% | 0.6075% | 0.9856% | 1.318% | 0.9296% | -2.672% | -3.173% | -1.486% | -0.2679% | 6.7% | 5.873% | -1.661% | -0.74% | -1.826% | 8.466% | -2.263% | 8.783% | -3.035% | -2.433% | -2.662% | -1.45% | -2.1% | -2.821% | -4.417% | -5.03% | -2.596% | -2.899% | -2.694% | -1.816% | -2.736% | -1.6% | -2.996% | -2.638% | -2.45% | -2.814% | -1.397% | -2.491% | -1.545% | -1.24% | -1.686% | -2.126% | 0.02446% | -0.1713% | -1.099% | 0.006705% | -0.5951% | -1.6% | -1.642% | -0.7006% | -2.237% | -0.4776% | -0.4322% | -0.6993% | -1.61% | -2.042% | -3.614% | -1.121% | -2.791% | 0.5553% | 0.6297% | 0.7056% | 0.4707% | 1.108% | 0.1471% | -0.3019% | -0.09221% | -0.4096% | 0.5576% | -0.2282% | 0.1526% | -0.7151% | 0.8253% | 0.9496% | -0.03879% | -0.6439% | -0.3815% | 0.7364% | -0.07146% | 0.3054% | -0.146% | -0.2173% | -0.2008% | 0.04466% | 1.348% | 1.675% | 1.058% | 0.2901% | -0.03419% | 0.3734% | -2.37% | -3.317% | -2.335% | -3.01% | -3.21% | -3.562% | -2.394% | -2.07% | 3.848% | 3.974% | 4.248% | 4.984% | 4.356% | 2.762% | 3.283% | 0.5185% | 4.46% | 4.316% | 4.374% | 4.204% | 4.146% | 2.935% | 4.195% | 4.771% | 5.711% | 4.589% | 4.872% | 4.516% | 4.105% | 4.274% | 5.251% | 4.682%
2025-05-30 | 0.1716% | 1.562% | 1.155% | 1.243% | 2.059% | 2.595% | 2.983% | 1.753% | 1.917% | -0.6257% | 1.499% | 1.212% | 2.642% | 0.9618% | 1.585% | 2.095% | 1.135% | 1.268% | 1.529% | 2.334% | 0.7087% | -0.2092% | 0.8279% | 0.5139% | -0.6391% | -2.233% | -2.21% | -2.953% | 1.052% | 1.612% | 1.444% | 1.159% | 2.028% | 1.984% | 2.754% | 1.971% | 3.144% | 1.304% | 1.859% | 1.339% | 1.8% | 2.806% | 2.453% | 2.582% | -0.5221% | -2.714% | 1.066% | 1.012% | 8.344% | 7.62% | -0.3817% | 0.438% | -0.6615% | 10.39% | -1.437% | 10.37% | -1.975% | -1.711% | -1.587% | -0.7015% | -1.181% | -1.856% | -2.587% | -2.909% | -2.154% | -2.621% | -2.378% | -2.7% | -2.643% | -2.154% | -2.713% | -3.06% | -1.971% | -2.676% | -0.9152% | -2.516% | -1.274% | -0.935% | -0.7122% | -1.507% | -1.78% | -2.005% | -2.49% | -2.474% | -2.016% | -2.895% | -2.094% | -2.392% | -0.9408% | -2.021% | -0.599% | -0.7966% | -0.7837% | 0.02882% | -1.282% | -0.333% | 0.3783% | 0.2035% | -0.495% | 0.1692% | -0.9108% | 0.2974% | -0.7285% | -0.5394% | -1.295% | -1.1% | -0.8355% | -1.423% | -0.8965% | -1.797% | 0.001744% | 0.09431% | -1.291% | -1.267% | -1.428% | -0.261% | -1.074% | -1.293% | -1.236% | -1.71% | -1.776% | -1.34% | 0.3083% | 0.1433% | 0.3868% | -1.24% | -1.513% | -1.294% | -1.087% | -0.4815% | -1.649% | -1.987% | -1.075% | -1.589% | -4.067% | -3.663% | 0.3035% | 2.058% | 0.7231% | 2.669% | 1.222% | 0.9123% | 1.277% | -1.473% | 1.938% | 1.582% | 1.252% | 0.7417% | 0.7102% | -0.3543% | 2.013% | 1.134% | 1.185% | 0.5817% | 0.4993% | 0.1591% | 0.2573% | 1.562% | 1.227% | 2.403%