## O2Summary
Performance Summary TGPXIIPL
Month | 2025-06-01
Date | 2025-06-12
Financial Year | Year-1
Year Start Date | 2025-04-01
Year End Date | 2026-03-31
Sr. No. | Particular | Target | Measured | Deviation | Remarks
1 | E_Grid Daily (MWh) | 801.6133 | 904.05 | 12.78%
| E_Grid MTD(MWh) | 9619.3593 | 10525.05 | 9.415%
| E_Grid YTD (MWh) | 58722.2291 | 48099.15 | -18.09%
2 | Wind Speed Daily | 7.15 | 7.6641 | 7.19%
| Wind Speed MTD | 7.15 | 7.5851 | 6.085%
| Wind Speed YTD | 6.9967 | 6.6559 | -4.871%
3 | PA Daily | 96.03% | 99.75% | 3.872%
| PA MTD | 96.03% | 98.68% | 2.762%
| PA YTD | 96.03% | 94.1% | -2.013%
4 | EGA Daily | 99.5% | 100% | 0.5025%
| EGA MTD | 99.5% | 100% | 0.5025%
| EGA YTD | 99.5% | 100% | 0.5025%
5 | IGA Daily | 99% | 100% | 1.01%
| IGA MTD | 99% | 100% | 1.006%
| IGA YTD | 99% | 96.74% | -2.28%
6 | MA Daily | 97% | 99.75% | 2.833%
| MA MTD | 97% | 98.69% | 1.739%
| MA YTD | 97% | 97.27% | 0.2737%
7 | CUF Daily | 47.58% | 53.66% | 12.78%
| CUF MTD | 47.58% | 52.06% | 9.415%
| CUF YTD | 47.75% | 39.11% | -18.09%
8 | Line Loss Daily | 5% | 3.282% | 34.37%
| Line Loss MTD | 5% | 3.121% | 37.58%
| Line Loss YTD | 5% | 3.431% | 31.37%
9 | Reactive Power Daily | 5% | 0.2888% | 94.22%
| Reactive Power MTD | 5% | 1.081% | 78.38%
| Reactive Power YTD | 5% | 0.7953% | 84.09%
10 | Expected Energy Daily | 956.64 | 934.724 | -2.291%
| Expected Energy MTD | 10530.99 | 10862.9467 | 3.152%
| Expected Energy YTD | 52161.6945 | 49770.8967 | -4.583%

## MonthlyKPI
Till Date | 2025-06-12 | 0 | 0 | 0 | 0
TGPXIIPL Performance Summary (MTD)
Year | Days | Estimated WS(m/s) | Measured WS (m/s) | Budgeted Energy (MWh) | Measured Energy (MWh) | Target CUF (%) | Measured CUF (%) | Target GA (%) | Measured GA (%) | Target MA (%) | Measured MA (%) | Target IGA (%) | Measured IGA (%) | Target PA(%) | Measured PA (%) | WTG Total (MWh) | Line Losses(%) | E_WS_Corrected | Expected Energy | Loss (%) | Reactive Power (%)
2025-06-01 | 12 | 7.15 | 7.5851 | 9619.3593 | 10525.05 | 47.58% | 52.06% | 99.5% | 100% | 97% | 98.69% | 99% | 100% | 96.03% | 98.68% | 10862.9467 | 3.21% | 10530.99 | 10530.99 | 3.121% | 1.081%
Start Date | 2025-06-06
End Date | 2025-06-12
TGPXIIPL Performance Summary (WTD)
Year | Days | Estimated WS(m/s) | Measured WS (m/s) | Budgeted Energy (MWh) | Measured Energy (MWh) | Target CUF (%) | Measured CUF (%) | Target GA (%) | Measured GA (%) | Target MA (%) | Measured MA (%) | Target IGA (%) | Measured IGA (%) | Target PA(%) | Measured PA (%) | E_WS_Corrected
2025-06-01 | 7 | 7.15 | 7.4341 | 5611.2929 | 5998.05 | 47.58% | 50.86% | 99.5% | 100% | 97% | 98.18% | 99% | 100% | 96.03% | 98.18% | 6348.31
Start Date | 2025-05-14
End Date | 2025-06-12
TGPXIIPL Performance Summary (LTD)
Year | Days | Estimated WS(m/s) | Measured WS (m/s) | Budgeted Energy (MWh) | Measured Energy (MWh) | Target CUF (%) | Measured CUF (%) | Target GA (%) | Measured GA (%) | Target MA (%) | Measured MA (%) | Target IGA (%) | Measured IGA (%) | Target PA(%) | Measured PA (%)
2025-06-01 | 30 | 7.15 | 6.9088 | 25976.1646 | 22325.7457 | 51.39% | 44.17% | 99.7% | 100% | 98.6% | 98.02% | 99.5% | 96.76% | 98.11% | 94.85%
Formulas:
Days = [Days, row below]-6

## Analytices
Start Date | 2025-06-01
End Date | 2025-06-12 | 288 | 7.55
WTG No. | O2_01 | O2_02 | O2_03 | O2_04 | O2_05 | O2_06 | O2_07 | O2_08 | O2_09 | O2_10 | O2_11 | O2_12 | O2_13 | O2_14 | O2_15 | O2_16 | O2_17 | O2_18 | O2_19 | O2_20 | O2_21 | O2_22 | O2_23 | O2_24 | O2_25 | O2_26
MA | 93.84% | 99.8% | 97.96% | 95.63% | 98.72% | 99.61% | 93.47% | 99.32% | 99.82% | 96.97% | 99.76% | 99.92% | 98.83% | 99.64% | 99.83% | 97.15% | 98.97% | 99.97% | 98.09% | 99.86% | 99.76% | 99.93% | 99.18% | 99.76% | 99.67% | 99.7%
WTG BD Hours | 17.7333 | 0.56667 | 5.8833 | 12.5833 | 3.7 | 1.1333 | 18.8167 | 1.9667 | 0.51667 | 8.7167 | 0.68333 | 0.23333 | 3.3833 | 1.0333 | 0.48333 | 8.2 | 2.9667 | 0.1 | 5.5 | 0.4 | 0.68333 | 0.2 | 2.3667 | 0.7 | 0.95 | 0.86667
IGA | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
METERING YARD
FEEDER | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OG
TRANSFER | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
USS
EGA | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
External Grid | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Generation | 383306.5 | 453065 | 395077 | 440521 | 426462 | 446896 | 413458 | 416330 | 401773 | 361545.1667 | 398254.3333 | 396532.3 | 393497 | 400526.8333 | 410757.8333 | 399824 | 460006 | 447756 | 432617 | 422524.5 | 411421.5 | 467752 | 405989.8 | 422250.8 | 441187.5 | 413615.6667
PA | 93.84% | 99.8% | 97.96% | 95.63% | 98.72% | 99.61% | 93.47% | 99.32% | 99.82% | 96.97% | 99.76% | 99.92% | 98.83% | 99.64% | 99.83% | 97.15% | 98.97% | 99.97% | 98.09% | 99.86% | 99.76% | 99.93% | 99.18% | 99.76% | 99.67% | 99.7%
Sum of BD | 17.7333 | 0.56667 | 5.8833 | 12.5833 | 3.7 | 1.1333 | 18.8167 | 1.9667 | 0.51667 | 8.7167 | 0.68333 | 0.23333 | 3.3833 | 1.0333 | 0.48333 | 8.2 | 2.9667 | 0.1 | 5.5 | 0.4 | 0.68333 | 0.2 | 2.3667 | 0.7 | 0.95 | 0.86667
Count of BD | 10 | 3 | 2 | 24 | 13 | 7 | 5 | 14 | 2 | 10 | 6 | 1 | 7 | 7 | 4 | 5 | 7 | 1 | 11 | 4 | 5 | 2 | 11 | 5 | 5 | 6
MTTR WTG | 1.7733 | 0.18889 | 2.9417 | 0.52431 | 0.28462 | 0.1619 | 3.7633 | 0.14048 | 0.25833 | 0.87167 | 0.11389 | 0.23333 | 0.48333 | 0.14762 | 0.12083 | 1.64 | 0.42381 | 0.1 | 0.5 | 0.1 | 0.13667 | 0.1 | 0.21515 | 0.14 | 0.19 | 0.14444
MTBF WTG | 27.0267 | 95.8111 | 141.0583 | 11.4757 | 21.8692 | 40.981 | 53.8367 | 20.431 | 143.7417 | 27.9283 | 47.8861 | 287.7667 | 40.6595 | 40.9952 | 71.8792 | 55.96 | 40.719 | 287.9 | 25.6818 | 71.9 | 57.4633 | 143.9 | 25.9667 | 57.46 | 57.41 | 47.8556
WS (M/S) | 7.5 | 7.8 | 7.4 | 7.9 | 7.7 | 7.8 | 7.8 | 7.5 | 7.4 | 7.3 | 7.4 | 7.4 | 7.3 | 7.4 | 7.5 | 7.6 | 8 | 7.7 | 7.6 | 7.6 | 7.5 | 8 | 7.5 | 7.5 | 7.6 | 7.6
Fault Analysis
2023-04-01
|  |  | Put hour Here |  | Default hour for full Data
|  |  | 19272 |  | 19272
Finacial Year | (Multiple Items)
Row Labels | Sum of Breakdown Time | Count of Error Text | MTTR | MTBF
Grand Total |  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.

## Daily KPI
Date | Financial Year | Calendar Year | Month Year | Days | Operating Hours | GHI-UP (KWh/m2) | GHI-Down(KWh/m2) | POA-UP(KWh/m2) | POA-Down(KWh/m2) | Amb_Temp(°C) | Mod_Temp(°C) | WS_Avg(m/s) | WS_Max(m/s) | PA(%) | MA (%) | IGA (%) | EGA(%) | EMA (%) | TA (%) | PR(%) | WPR(%) | CUF(%) | Gen_Exp (kWh) | Mtr_Export (kWh) | Mtr_Import (kWh) | Mtr_Net_Exp (KWh) | Operational Capacity (MW) | Bugt_Resource | Bugt_Energy | Bugt PR | Bugt CUF | Bugt_PA | Bugt_EGA | Expected Energy | Actual Energy WPR | RA (%) | Mod Clean Dry (Num) | Mod Clean Wet (Num) | Line Loss(%) | Reactive Power (%) | Bugt Line loss (%) (Wind) | Bugt Reactive Power (%) (Wind) | Bugt Capacity | CC*Bugt
2024-04-01 | 2025 | 2024 | 2024-04-01 | 30 | [7 empty] | 5.2935 | 0 | [9 empty] | 8754 | 0 | 0 | 0 | 24.3 | 6.65 | 0 |  |  | 96.03% | 99.5% | 0 |  |  |  |  | 100% | 0% | 5% | 5% | 0
2024-04-02 | 2025 | 2024 | 2024-04-01 | 30 | [7 empty] | 5.5173 | 0 | [9 empty] | 5402 | 0 | 0 | 0 | 24.3 | 6.65 | 0 |  |  | 96.03% | 99.5% | 0 |  |  |  |  | 100% | 0% | 5% | 5% | 0
2024-04-03 | 2025 | 2024 | 2024-04-01 | 30 | [7 empty] | 6.2453 | 0 | [9 empty] | 2654 | 0 | 0 | 0 | 24.3 | 6.65 | 0 |  |  | 96.03% | 99.5% | 0 |  |  |  |  | 100% | 0% | 5% | 5% | 0
2024-04-04 | 2025 | 2024 | 2024-04-01 | 30 | [7 empty] | 5.2402 | 0 | [9 empty] | 3564 | 0 | 0 | 0 | 24.3 | 6.65 | 0 |  |  | 96.03% | 99.5% | 0 |  |  |  |  | 100% | 0% | 5% | 5% | 0
2024-04-05 | 2025 | 2024 | 2024-04-01 | 30 | [7 empty] | 4.165 | 0 | [9 empty] | 0 | 0 | 0 | 0 | 24.3 | 6.65 | 0 |  |  | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 0
2024-04-06 | 2025 | 2024 | 2024-04-01 | 30 | [7 empty] | 4.5033 | 0 | [9 empty] | 0 | 0 | 0 | 0 | 24.3 | 6.65 | 0 |  |  | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 0
2024-04-07 | 2025 | 2024 | 2024-04-01 | 30 | [7 empty] | 4.44 | 0 | [9 empty] | 0 | 0 | 0 | 0 | 24.3 | 6.65 | 0 |  |  | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 0
2024-04-08 | 2025 | 2024 | 2024-04-01 | 30 | [7 empty] | 2.7071 | 0 | [9 empty] | 0 | 0 | 0 | 0 | 24.3 | 6.65 | 0 |  |  | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 0
2024-04-09 | 2025 | 2024 | 2024-04-01 | 30 | [7 empty] | 3.32 | 0 | [9 empty] | 0 | 0 | 0 | 0 | 24.3 | 6.65 | 0 |  |  | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 0
2024-04-10 | 2025 | 2024 | 2024-04-01 | 30 | [7 empty] | 3.3183 | 0 | [9 empty] | 0 | 0 | 0 | 0 | 24.3 | 6.65 | 0 |  |  | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 0
2024-04-11 | 2025 | 2024 | 2024-04-01 | 30 | [7 empty] | 4.3017 | 0 | [9 empty] | 0 | 0 | 0 | 0 | 24.3 | 6.65 | 0 |  |  | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 0
2024-04-12 | 2025 | 2024 | 2024-04-01 | 30 | [7 empty] | 4.1667 | 0 | [9 empty] | 0 | 0 | 0 | 0 | 24.3 | 6.65 | 0 |  |  | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 0
2024-04-13 | 2025 | 2024 | 2024-04-01 | 30 | [7 empty] | 3.1817 | 0 | [9 empty] | 0 | 0 | 0 | 0 | 24.3 | 6.65 | 0 |  |  | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 0
2024-04-14 | 2025 | 2024 | 2024-04-01 | 30 | [7 empty] | 4.8621 | 0 | [9 empty] | 0 | 0 | 0 | 0 | 24.3 | 6.65 | 0 |  |  | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 0
2024-04-15 | 2025 | 2024 | 2024-04-01 | 30 | [7 empty] | 5.7291 | 0 | 100% | 100% | 100% | 100% | [5 empty] | 5578 | 5400 | 900 | 4500 | 24.3 | 6.65 | 0 |  |  | 96.03% | 99.5% | 0 |  |  |  |  | 3.191% | 0% | 5% | 5% | 0
2024-04-16 | 2025 | 2024 | 2024-04-01 | 30 | [7 empty] | 5.7648 | 0 | 100% | 100% | 100% | 100% | [5 empty] | 1573 | 1350 | 900 | 450 | 24.3 | 6.65 | 0 |  |  | 96.03% | 99.5% | 0 |  |  |  |  | 14.18% | 0% | 5% | 5% | 0
2024-04-17 | 2025 | 2024 | 2024-04-01 | 30 | [7 empty] | 5.7101 | 0 | 100% | 100% | 100% | 100% | [5 empty] | 71 | 0 | 900 | -900 | 24.3 | 6.65 | 0 |  |  | 96.03% | 99.5% | 0 |  |  |  |  | 100% | 0% | 5% | 5% | 0
2024-04-18 | 2025 | 2024 | 2024-04-01 | 30 | [7 empty] | 5.2813 | 0 | 100% | 100% | 100% | 100% | [5 empty] | 94 | 0 | 1800 | -1800 | 24.3 | 6.65 | 0 |  |  | 96.03% | 99.5% | 0 |  |  |  |  | 100% | 0% | 5% | 5% | 0
2024-04-19 | 2025 | 2024 | 2024-04-01 | 30 | [7 empty] | 6.7932 | 0 | 100% | 100% | 100% | 100% | [5 empty] | 3907 | 3600 | 1350 | 2250 | 24.3 | 6.65 | 0 |  |  | 96.03% | 99.5% | 0 |  |  |  |  | 7.858% | 0% | 5% | 5% | 0
2024-04-20 | 2025 | 2024 | 2024-04-01 | 30 | [7 empty] | 6.7423 | 0 | 100% | 100% | 100% | 100% | [5 empty] | 0 | 0 | 450 | -450 | 24.3 | 6.65 | 0 |  |  | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 0
2024-04-21 | 2025 | 2024 | 2024-04-01 | 30 | [7 empty] | 5.9923 | 0 | 100% | 100% | 100% | 100% | [5 empty] | 0 | 0 | 1350 | -1350 | 24.3 | 6.65 | 0 |  |  | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 0
2024-04-22 | 2025 | 2024 | 2024-04-01 | 30 | [7 empty] | 6.6763 | 0 | 100% | 100% | 100% | 100% | [5 empty] | 0 | 0 | 1800 | -1800 | 24.3 | 6.65 | 0 |  |  | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 0
2024-04-23 | 2025 | 2024 | 2024-04-01 | 30 | [7 empty] | 5.7655 | 0 | 100% | 100% | 100% | 100% | [5 empty] | 0 | 0 | 1800 | -1800 | 24.3 | 6.65 | 0 |  |  | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 0
2024-04-24 | 2025 | 2024 | 2024-04-01 | 30 | [7 empty] | 5.6918 | 0 | 100% | 100% | 100% | 100% | [5 empty] | 0 | 0 | 1800 | -1800 | 24.3 | 6.65 | 0 |  |  | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 0
2024-04-25 | 2025 | 2024 | 2024-04-01 | 30 | [7 empty] | 5.6562 | 0 | 100% | 100% | 100% | 100% | [5 empty] | 0 | 0 | 1350 | -1350 | 24.3 | 6.65 | 0 |  |  | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 0
2024-04-26 | 2025 | 2024 | 2024-04-01 | 30 | [7 empty] | 5.5579 | 0 | 100% | 100% | 100% | 100% | [5 empty] | 0 | 0 | 1350 | -1350 | 24.3 | 6.65 | 0 |  |  | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 0
2024-04-27 | 2025 | 2024 | 2024-04-01 | 30 | [7 empty] | 4.6719 | 0 | 100% | 100% | 100% | 100% | [5 empty] | 0 | 0 | 900 | -900 | 24.3 | 6.65 | 0 |  |  | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 0
2024-04-28 | 2025 | 2024 | 2024-04-01 | 30 | [7 empty] | 6.3726 | 0 | 100% | 100% | 100% | 100% | [5 empty] | 0 | 0 | 900 | -900 | 24.3 | 6.65 | 0 |  |  | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 0
2024-04-29 | 2025 | 2024 | 2024-04-01 | 30 | [7 empty] | 7.2876 | 0 | 100% | 100% | 100% | 100% | [5 empty] | 0 | 0 | 1350 | -1350 | 24.3 | 6.65 | 0 |  |  | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 0
2024-04-30 | 2025 | 2024 | 2024-04-01 | 30 | [7 empty] | 6.2722 | 0 | 100% | 100% | 100% | 100% | [5 empty] | 0 | 0 | 1350 | -1350 | 24.3 | 6.65 | 0 |  |  | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 0
2024-05-01 | 2025 | 2024 | 2024-05-01 | 31 | [7 empty] | 8.0744 | 0 | 100% | 100% | 100% | 100% |  |  |  |  | -0.1389% | 0 | 0 | 900 | -900 | 24.3 | 7.19 | 281008.5484 |  | 43.37% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 27
2024-05-02 | 2025 | 2024 | 2024-05-01 | 31 | [7 empty] | 5.1912 | 0 | 17.17% | 17.17% | 100% | 100% |  |  |  |  | 0.625% | 6218 | 4950 | 900 | 4050 | 24.3 | 7.19 | 281008.5484 |  | 43.37% | 96.03% | 99.5% | 0 |  |  |  |  | 20.39% | 0% | 5% | 5% | 27
2024-05-03 | 2025 | 2024 | 2024-05-01 | 31 | [7 empty] | 4.762 | 0 | 35.62% | 35.62% | 100% | 100% |  |  |  |  | 2.847% | 20451 | 18900 | 450 | 18450 | 24.3 | 7.19 | 281008.5484 |  | 43.37% | 96.03% | 99.5% | 0 |  |  |  |  | 7.584% | 0% | 5% | 5% | 27
2024-05-04 | 2025 | 2024 | 2024-05-01 | 31 | [7 empty] | 6.4334 | 0 | 20.35% | 20.35% | 100% | 100% |  |  |  |  | 4.861% | 33310 | 31500 | 0 | 31500 | 24.3 | 7.19 | 281008.5484 |  | 43.37% | 96.03% | 99.5% | 0 |  |  |  |  | 5.434% | 0% | 5% | 5% | 27
2024-05-05 | 2025 | 2024 | 2024-05-01 | 31 | [7 empty] | 6.9082 | 0 | 45.83% | 45.83% | 100% | 100% |  |  |  |  | 7.986% | 53642 | 51750 | 0 | 51750 | 24.3 | 7.19 | 281008.5484 |  | 43.37% | 96.03% | 99.5% | 0 |  |  |  |  | 3.527% | 0% | 5% | 5% | 27
2024-05-06 | 2025 | 2024 | 2024-05-01 | 31 | [7 empty] | 6.5096 | 0 | 57.01% | 57.01% | 100% | 100% |  |  |  |  | 14.93% | 97232 | 96750 | 0 | 96750 | 24.3 | 7.19 | 281008.5484 |  | 43.37% | 96.03% | 99.5% | 0 |  |  |  |  | 0.4957% | 0% | 5% | 5% | 27
2024-05-07 | 2025 | 2024 | 2024-05-01 | 31 | [7 empty] | 4.9985 | 0 | 72.74% | 72.74% | 100% | 100% |  |  |  |  | 12.92% | 86731 | 84150 | 450 | 83700 | 24.3 | 7.19 | 281008.5484 |  | 43.37% | 96.03% | 99.5% | 0 |  |  |  |  | 2.976% | 0% | 5% | 5% | 27
2024-05-08 | 2025 | 2024 | 2024-05-01 | 31 | [7 empty] | 5.8453 | 0 | 64.62% | 64.62% | 100% | 100% |  |  |  |  | 17.85% | 117903 | 116100 | 450 | 115650 | 24.3 | 7.19 | 281008.5484 |  | 43.37% | 96.03% | 99.5% | 0 |  |  |  |  | 1.529% | 0% | 5% | 5% | 27
2024-05-09 | 2025 | 2024 | 2024-05-01 | 31 | [7 empty] | 6.2267 | 0 | 73.84% | 73.84% | 100% | 100% |  |  |  |  | 21.81% | 144016 | 141300 | 0 | 141300 | 24.3 | 7.19 | 281008.5484 |  | 43.37% | 96.03% | 99.5% | 0 |  |  |  |  | 1.886% | 0% | 5% | 5% | 27
2024-05-10 | 2025 | 2024 | 2024-05-01 | 31 | [7 empty] | 6.389 | 0 | 66.91% | 66.91% | 100% | 100% |  |  |  |  | 18.61% | 123690 | 120600 | 0 | 120600 | 24.3 | 7.19 | 281008.5484 |  | 43.37% | 96.03% | 99.5% | 0 |  |  |  |  | 2.498% | 0% | 5% | 5% | 27
2024-05-11 | 2025 | 2024 | 2024-05-01 | 31 | [7 empty] | 5.033 | 0 | 52.94% | 52.94% | 100% | 95.55% |  |  |  |  | 10.76% | 72639 | 70200 | 450 | 69750 | 24.3 | 7.19 | 281008.5484 |  | 43.37% | 96.03% | 99.5% | 0 |  |  |  |  | 3.358% | 0% | 5% | 5% | 27
2024-05-12 | 2025 | 2024 | 2024-05-01 | 31 | [7 empty] | 5.6566 | 0 | 55.09% | 55.09% | 100% | 100% |  |  |  |  | 11.6% | 76859 | 75150 | 0 | 75150 | 24.3 | 7.19 | 281008.5484 |  | 43.37% | 96.03% | 99.5% | 0 |  |  |  |  | 2.224% | 0% | 5% | 5% | 27
2024-05-13 | 2025 | 2024 | 2024-05-01 | 31 | [7 empty] | 6.6418 | 0 | 48.34% | 48.34% | 100% | 100% |  |  |  |  | 10.9% | 76110 | 70650 | 0 | 70650 | 24.3 | 7.19 | 281008.5484 |  | 43.37% | 96.03% | 99.5% | 0 |  |  |  |  | 7.174% | 0% | 5% | 5% | 27
2024-05-14 | 2025 | 2024 | 2024-05-01 | 31 | [7 empty] | 6.188 | 0 | 40.7% | 40.7% | 100% | 100% |  |  |  |  | 8.958% | 56125 | 58500 | 450 | 58050 | 24.3 | 7.19 | 281008.5484 |  | 43.37% | 96.03% | 99.5% | 0 |  |  |  |  | -4.232% | 0% | 5% | 5% | 27
2024-05-15 | 2025 | 2024 | 2024-05-01 | 31 | [7 empty] | 5.6628 | 0 | 16.21% | 19.02% | 85.23% | 100% |  |  |  |  | 1.389% | 10325 | 9450 | 450 | 9000 | 24.3 | 7.19 | 281008.5484 |  | 43.37% | 96.03% | 99.5% | 0 |  |  |  |  | 8.475% | 0% | 5% | 5% | 27
2024-05-16 | 2025 | 2024 | 2024-05-01 | 31 | [7 empty] | 6.2083 | 0 | 11.1% | 39.54% | 28.06% | 100% |  |  |  |  | 3.889% | 26830 | 25650 | 450 | 25200 | 24.3 | 7.19 | 281008.5484 |  | 43.37% | 96.03% | 99.5% | 0 |  |  |  |  | 4.398% | 0% | 5% | 5% | 27
2024-05-17 | 2025 | 2024 | 2024-05-01 | 31 | [7 empty] | 6.0393 | 0 | 60.52% | 72.54% | 83.42% | 100% |  |  |  |  | 18.19% | 120571 | 117900 | 0 | 117900 | 24.3 | 7.19 | 281008.5484 |  | 43.37% | 96.03% | 99.5% | 0 |  |  |  |  | 2.215% | 0% | 5% | 5% | 27
2024-05-18 | 2025 | 2024 | 2024-05-01 | 31 | [7 empty] | 5.2849 | 0 | 73.9% | 75.08% | 98.43% | 100% |  |  |  |  | 14.31% | 96337 | 93150 | 450 | 92700 | 24.3 | 7.19 | 281008.5484 |  | 43.37% | 96.03% | 99.5% | 0 |  |  |  |  | 3.308% | 0% | 5% | 5% | 27
2024-05-19 | 2025 | 2024 | 2024-05-01 | 31 | [7 empty] | 7.5672 | 0 | 87.8% | 87.8% | 100% | 100% |  |  |  |  | 43.47% | 284809 | 281700 | 0 | 281700 | 24.3 | 7.19 | 281008.5484 |  | 43.37% | 96.03% | 99.5% | 0 |  |  |  |  | 1.092% | 0% | 5% | 5% | 27
2024-05-20 | 2025 | 2024 | 2024-05-01 | 31 | [7 empty] | 7.1542 | 0 | 85.58% | 85.58% | 100% | 100% |  |  |  |  | 36.94% | 244313 | 239400 | 0 | 239400 | 24.3 | 7.19 | 281008.5484 |  | 43.37% | 96.03% | 99.5% | 0 |  |  |  |  | 2.011% | 0% | 5% | 5% | 27
2024-05-21 | 2025 | 2024 | 2024-05-01 | 31 | [7 empty] | 6.5918 | 0 | 88.57% | 90.2% | 98.2% | 100% |  |  |  |  | 34.58% | 229184 | 224100 | 0 | 224100 | 24.3 | 7.19 | 281008.5484 |  | 43.37% | 96.03% | 99.5% | 0 |  |  |  |  | 2.218% | 0% | 5% | 5% | 27
2024-05-22 | 2025 | 2024 | 2024-05-01 | 31 | [7 empty] | 7.3044 | 0 | 93.78% | 93.78% | 100% | 100% |  |  |  |  | 48.4% | 316870 | 313650 | 0 | 313650 | 29.7 | 7.19 | 281008.5484 |  | 43.37% | 96.03% | 99.5% | 0 |  |  |  |  | 1.016% | 0% | 5% | 5% | 27
2024-05-23 | 2025 | 2024 | 2024-05-01 | 31 | [7 empty] | 8.3619 | 0 | 86.47% | 86.47% | 100% | 100% |  |  |  |  | 60.56% | 403321 | 392400 | 0 | 392400 | 29.7 | 7.19 | 281008.5484 |  | 43.37% | 96.03% | 99.5% | 0 |  |  |  |  | 2.708% | 0% | 5% | 5% | 27
2024-05-24 | 2025 | 2024 | 2024-05-01 | 31 | [7 empty] | 8.4647 | 0 | 78.15% | 91.29% | 85.6% | 100% |  |  |  |  | 64.51% | 422711 | 418500 | 450 | 418050 | 32.4 | 7.19 | 281008.5484 |  | 43.37% | 96.03% | 99.5% | 0 |  |  |  |  | 0.9962% | 0% | 5% | 5% | 27
2024-05-25 | 2025 | 2024 | 2024-05-01 | 31 | [7 empty] | 7.3178 | 0 | 90.55% | 90.55% | 100% | 100% |  |  |  |  | 55.21% | 355525 | 357750 | 0 | 357750 | 32.4 | 7.19 | 281008.5484 |  | 43.37% | 96.03% | 99.5% | 0 |  |  |  |  | -0.6258% | 0% | 5% | 5% | 27
2024-05-26 | 2025 | 2024 | 2024-05-01 | 31 | [7 empty] | 8.3852 | 0 | 91.52% | 91.52% | 100% | 100% |  |  |  |  | 68.89% | 454184 | 446400 | 0 | 446400 | 32.4 | 7.19 | 281008.5484 |  | 43.37% | 96.03% | 99.5% | 0 |  |  |  |  | 1.714% | 0% | 5% | 5% | 27
2024-05-27 | 2025 | 2024 | 2024-05-01 | 31 | [7 empty] | 9.897 | 0 | 56.25% | 95.38% | 58.97% | 100% |  |  |  |  | 64.17% | 423434 | 415800 | 0 | 415800 | 32.4 | 7.19 | 281008.5484 |  | 43.37% | 96.03% | 99.5% | 0 |  |  |  |  | 1.803% | 0% | 5% | 5% | 27
2024-05-28 | 2025 | 2024 | 2024-05-01 | 31 | [7 empty] | 10.5297 | 0 | 44.23% | 95.86% | 46.14% | 100% |  |  |  |  | 60.89% | 404057 | 394537 | 0 | 394537 | 32.4 | 7.19 | 281008.5484 |  | 43.37% | 96.03% | 99.5% | 0 |  |  |  |  | 2.356% | 0% | 5% | 5% | 27
2024-05-29 | 2025 | 2024 | 2024-05-01 | 31 | [7 empty] | 10.2291 | 0 | 91.69% | 91.69% | 100% | 100% |  |  |  |  | 89.51% | 577249 | 580050 | 0 | 580050 | 32.4 | 7.19 | 281008.5484 |  | 43.37% | 96.03% | 99.5% | 0 |  |  |  |  | -0.4852% | 0% | 5% | 5% | 27
2024-05-30 | 2025 | 2024 | 2024-05-01 | 31 | [7 empty] | 7.8958 | 0 | 93.59% | 93.59% | 100% | 100% |  |  |  |  | 64.58% | 423450 | 418500 | 0 | 418500 | 32.4 | 7.19 | 281008.5484 |  | 43.37% | 96.03% | 99.5% | 0 |  |  |  |  | 1.169% | 0% | 5% | 5% | 27
2024-05-31 | 2025 | 2024 | 2024-05-01 | 31 | [7 empty] | 7.478 | 0 | 95.26% | 95.26% | 100% | 100% |  |  |  |  | 56.94% | 377423 | 369000 | 0 | 369000 | 32.4 | 7.19 | 281008.5484 |  | 43.37% | 96.03% | 99.5% | 0 |  |  |  |  | 2.232% | 0% | 5% | 5% | 27
2024-06-01 | 2025 | 2024 | 2024-06-01 | 30 | [7 empty] | 7.5045 | 0 | 55.23% | 97.53% | 56.63% | 100% |  |  |  |  | 47.15% | 311995 | 305550 | 0 | 305550 | 32.4 | 7.15 | 247889.7 |  | 38.25% | 96.03% | 99.5% | 0 |  |  |  |  | 2.066% | 0% | 5% | 5% | 27
2024-06-02 | 2025 | 2024 | 2024-06-01 | 30 | [7 empty] | 5.4039 | 0 | 87.7% | 91.46% | 95.89% | 100% |  |  |  |  | 27.22% | 181177 | 176400 | 0 | 176400 | 32.4 | 7.15 | 247889.7 |  | 38.25% | 96.03% | 99.5% | 0 |  |  |  |  | 2.637% | 0% | 5% | 5% | 27
2024-06-03 | 2025 | 2024 | 2024-06-01 | 30 | [7 empty] | 6.1897 | 0 | 70.86% | 97.39% | 72.76% | 100% |  |  |  |  | 37.43% | 248652 | 242550 | 0 | 242550 | 32.4 | 7.15 | 247889.7 |  | 38.25% | 96.03% | 99.5% | 0 |  |  |  |  | 2.454% | 0% | 5% | 5% | 27
2024-06-04 | 2025 | 2024 | 2024-06-01 | 30 | [7 empty] | 7.2136 | 0 | 79.06% | 83.08% | 95.16% | 100% |  |  |  |  | 37.85% | 249384 | 245250 | 0 | 245250 | 32.4 | 7.15 | 247889.7 |  | 38.25% | 96.03% | 99.5% | 0 |  |  |  |  | 1.658% | 0% | 5% | 5% | 27
2024-06-05 | 2025 | 2024 | 2024-06-01 | 30 | [7 empty] | 7.1921 | 0 | 79.94% | 92.83% | 86.12% | 100% |  |  |  |  | 45.42% | 298169 | 294300 | 0 | 294300 | 32.4 | 7.15 | 247889.7 |  | 38.25% | 96.03% | 99.5% | 0 |  |  |  |  | 1.298% | 0% | 5% | 5% | 27
2024-06-06 | 2025 | 2024 | 2024-06-01 | 30 | [7 empty] | 6.1493 | 0 | 98.47% | 98.47% | 100% | 100% |  |  |  |  | 39.65% | 263822 | 256950 | 0 | 256950 | 32.4 | 7.15 | 247889.7 |  | 38.25% | 96.03% | 99.5% | 0 |  |  |  |  | 2.605% | 0% | 5% | 5% | 27
2024-06-07 | 2025 | 2024 | 2024-06-01 | 30 | [7 empty] | 6.1119 | 0 | 97.66% | 97.66% | 100% | 100% |  |  |  |  | 41.11% | 273508 | 266850 | 450 | 266400 | 32.4 | 7.15 | 247889.7 |  | 38.25% | 96.03% | 99.5% | 0 |  |  |  |  | 2.434% | 0% | 5% | 5% | 27
2024-06-08 | 2025 | 2024 | 2024-06-01 | 30 | [7 empty] | 5.4394 | 0 | 84.91% | 90.3% | 94.03% | 100% |  |  |  |  | 30% | 200026 | 195300 | 900 | 194400 | 32.4 | 7.15 | 247889.7 |  | 38.25% | 96.03% | 99.5% | 0 |  |  |  |  | 2.363% | 0% | 5% | 5% | 27
2024-06-09 | 2025 | 2024 | 2024-06-01 | 30 | [7 empty] | 6.4048 | 0 | 79.3% | 88.44% | 89.66% | 100% |  |  |  |  | 29.58% | 195710 | 191700 | 0 | 191700 | 32.4 | 7.15 | 247889.7 |  | 38.25% | 96.03% | 99.5% | 0 |  |  |  |  | 2.049% | 0% | 5% | 5% | 27
2024-06-10 | 2025 | 2024 | 2024-06-01 | 30 | [7 empty] | 6.2531 | 0 | 84.37% | 87.99% | 95.89% | 100% |  |  |  |  | 34.24% | 226666 | 221850 | 0 | 221850 | 32.4 | 7.15 | 247889.7 |  | 38.25% | 96.03% | 99.5% | 0 |  |  |  |  | 2.125% | 0% | 5% | 5% | 27
2024-06-11 | 2025 | 2024 | 2024-06-01 | 30 | [7 empty] | 8.1742 | 0 | 84.5% | 88.73% | 95.24% | 100% |  |  |  |  | 61.88% | 409019 | 400950 | 0 | 400950 | 32.4 | 7.15 | 247889.7 |  | 38.25% | 96.03% | 99.5% | 0 |  |  |  |  | 1.973% | 0% | 5% | 5% | 27
2024-06-12 | 2025 | 2024 | 2024-06-01 | 30 | [7 empty] | 7.8755 | 0 | 84.06% | 92.39% | 90.98% | 100% |  |  |  |  | 51.04% | 336832 | 330750 | 0 | 330750 | 32.4 | 7.15 | 247889.7 |  | 38.25% | 96.03% | 99.5% | 0 |  |  |  |  | 1.806% | 0% | 5% | 5% | 27
2024-06-13 | 2025 | 2024 | 2024-06-01 | 30 | [7 empty] | 7.4848 | 0 | 65.68% | 97.28% | 67.51% | 100% |  |  |  |  | 41.74% | 276420 | 270450 | 0 | 270450 | 32.4 | 7.15 | 247889.7 |  | 38.25% | 96.03% | 99.5% | 0 |  |  |  |  | 2.16% | 0% | 5% | 5% | 27
2024-06-14 | 2025 | 2024 | 2024-06-01 | 30 | [7 empty] | 6.873 | 0 | 89.2% | 91.36% | 97.64% | 100% |  |  |  |  | 50.21% | 333052 | 325350 | 0 | 325350 | 32.4 | 7.15 | 247889.7 |  | 38.25% | 96.03% | 99.5% | 0 |  |  |  |  | 2.313% | 0% | 5% | 5% | 27
2024-06-15 | 2025 | 2024 | 2024-06-01 | 30 | [7 empty] | 5.388 | 0 | 95.98% | 95.98% | 100% | 100% |  |  |  |  | 26.6% | 176303 | 172350 | 0 | 172350 | 35.1 | 7.15 | 247889.7 |  | 38.25% | 96.03% | 99.5% | 0 |  |  |  |  | 2.242% | 0% | 5% | 5% | 27
2024-06-16 | 2025 | 2024 | 2024-06-01 | 30 | [7 empty] | 5.0811 | 0 | 97.39% | 97.39% | 100% | 100% |  |  |  |  | 26.74% | 178012 | 173250 | 0 | 173250 | 35.1 | 7.15 | 247889.7 |  | 38.25% | 96.03% | 99.5% | 0 |  |  |  |  | 2.675% | 0% | 5% | 5% | 27
2024-06-17 | 2025 | 2024 | 2024-06-01 | 30 | [7 empty] | 5.2404 | 0 | 97.99% | 97.99% | 100% | 100% |  |  |  |  | 26.53% | 175456 | 171900 | 0 | 171900 | 35.1 | 7.15 | 247889.7 |  | 38.25% | 96.03% | 99.5% | 0 |  |  |  |  | 2.027% | 0% | 5% | 5% | 27
2024-06-18 | 2025 | 2024 | 2024-06-01 | 30 | [7 empty] | 6.7468 | 0 | 86.7% | 94.52% | 91.73% | 100% |  |  |  |  | 48.82% | 314790 | 316350 | 0 | 316350 | 35.1 | 7.15 | 247889.7 |  | 38.25% | 96.03% | 99.5% | 0 |  |  |  |  | -0.4956% | 0% | 5% | 5% | 27
2024-06-19 | 2025 | 2024 | 2024-06-01 | 30 | [7 empty] | 7.2821 | 0 | 96.58% | 96.83% | 99.74% | 100% |  |  |  |  | 59.44% | 394947 | 385200 | 0 | 385200 | 35.1 | 7.15 | 247889.7 |  | 38.25% | 96.03% | 99.5% | 0 |  |  |  |  | 2.468% | 0% | 5% | 5% | 27
2024-06-20 | 2025 | 2024 | 2024-06-01 | 30 | [7 empty] | 7.5862 | 0 | 92.06% | 98.68% | 93.29% | 100% |  |  |  |  | 66.46% | 441650 | 430650 | 0 | 430650 | 35.1 | 7.15 | 247889.7 |  | 38.25% | 96.03% | 99.5% | 0 |  |  |  |  | 2.491% | 0% | 5% | 5% | 27
2024-06-21 | 2025 | 2024 | 2024-06-01 | 30 | [7 empty] | 7.6622 | 0 | 91.7% | 98.49% | 93.11% | 100% |  |  |  |  | 70.9% | 470177 | 459450 | 0 | 459450 | 35.1 | 7.15 | 247889.7 |  | 38.25% | 96.03% | 99.5% | 0 |  |  |  |  | 2.281% | 0% | 5% | 5% | 27
2024-06-22 | 2025 | 2024 | 2024-06-01 | 30 | [7 empty] | 6.0788 | 0 | 90.6% | 93.86% | 96.53% | 100% |  |  |  |  | 41.53% | 276265 | 269100 | 0 | 269100 | 35.1 | 7.15 | 247889.7 |  | 38.25% | 96.03% | 99.5% | 0 |  |  |  |  | 2.594% | 0% | 5% | 5% | 27
2024-06-23 | 2025 | 2024 | 2024-06-01 | 30 | [7 empty] | 5.4488 | 0 | 60.59% | 93.12% | 65.06% | 100% |  |  |  |  | 28.61% | 189600 | 185400 | 0 | 185400 | 35.1 | 7.15 | 247889.7 |  | 38.25% | 96.03% | 99.5% | 0 |  |  |  |  | 2.215% | 0% | 5% | 5% | 27
2024-06-24 | 2025 | 2024 | 2024-06-01 | 30 | [7 empty] | 3.5098 | 0 | 93.81% | 98.32% | 95.41% | 100% |  |  |  |  | 10.9% | 72300 | 70650 | 0 | 70650 | 35.1 | 7.15 | 247889.7 |  | 38.25% | 96.03% | 99.5% | 0 |  |  |  |  | 2.282% | 0% | 5% | 5% | 27
2024-06-25 | 2025 | 2024 | 2024-06-01 | 30 | [7 empty] | 3.9616 | 0 | 88.85% | 93.13% | 95.4% | 100% |  |  |  |  | 15.69% | 105125 | 101700 | 0 | 101700 | 37.8 | 7.15 | 247889.7 |  | 38.25% | 96.03% | 99.5% | 0 |  |  |  |  | 3.258% | 0% | 5% | 5% | 27
2024-06-26 | 2025 | 2024 | 2024-06-01 | 30 | [7 empty] | 4.0453 | 0 | 95.72% | 96.55% | 99.14% | 100% |  |  |  |  | 17.57% | 118908 | 114750 | 900 | 113850 | 37.8 | 7.15 | 247889.7 |  | 38.25% | 96.03% | 99.5% | 0 |  |  |  |  | 3.497% | 0% | 5% | 5% | 27
2024-06-27 | 2025 | 2024 | 2024-06-01 | 30 | [7 empty] | 5.0845 | 0 | 97.27% | 97.27% | 100% | 100% |  |  |  |  | 28.19% | 187844 | 183150 | 450 | 182700 | 40.5 | 7.15 | 247889.7 |  | 38.25% | 96.03% | 99.5% | 0 |  |  |  |  | 2.499% | 0% | 5% | 5% | 27
2024-06-28 | 2025 | 2024 | 2024-06-01 | 30 | [7 empty] | 5.922 | 0 | 93.66% | 99.85% | 93.8% | 100% |  |  |  |  | 41.67% | 278940 | 270000 | 0 | 270000 | 43.2 | 7.15 | 247889.7 |  | 38.25% | 96.03% | 99.5% | 0 |  |  |  |  | 3.205% | 0% | 5% | 5% | 27
2024-06-29 | 2025 | 2024 | 2024-06-01 | 30 | [7 empty] | 6.9392 | 0 | 93.33% | 97.65% | 95.57% | 100% |  |  |  |  | 64.44% | 424145 | 417600 | 0 | 417600 | 43 | 7.15 | 247889.7 |  | 38.25% | 96.03% | 99.5% | 0 |  |  |  |  | 1.543% | 0% | 5% | 5% | 27
2024-06-30 | 2025 | 2024 | 2024-06-01 | 30 | [7 empty] | 6.6714 | 0 | 99.69% | 99.69% | 100% | 100% |  |  |  |  | 57.92% | 381432 | 375300 | 0 | 375300 | 43 | 7.15 | 247889.7 |  | 38.25% | 96.03% | 99.5% | 0 |  |  |  |  | 1.608% | 0% | 5% | 5% | 27
2024-07-01 | 2025 | 2024 | 2024-07-01 | 31 | [7 empty] | 8.0193 | 0 | 96.88% | 96.88% | 100% | 100% |  |  |  |  | 33.15% | 574747 | 558450 | 0 | 558450 | 43 | 8.18 | 774981.4516 |  | 46% | 96.03% | 99.5% | 0 |  |  |  |  | 2.836% | 0% | 5% | 5% | 70.2
2024-07-02 | 2025 | 2024 | 2024-07-01 | 31 | [7 empty] | 9.6035 | 0 | 91.87% | 94.99% | 96.72% | 100% |  |  |  |  | 47.41% | 821647 | 798750 | 0 | 798750 | 43 | 8.18 | 774981.4516 |  | 46% | 96.03% | 99.5% | 0 |  |  |  |  | 2.787% | 0% | 5% | 5% | 70.2
2024-07-03 | 2025 | 2024 | 2024-07-01 | 31 | [7 empty] | 8.1994 | 0 | 88.35% | 88.35% | 100% | 100% |  |  |  |  | 37.1% | 641251 | 625050 | 0 | 625050 | 43 | 8.18 | 774981.4516 |  | 46% | 96.03% | 99.5% | 0 |  |  |  |  | 2.526% | 0% | 5% | 5% | 70.2
2024-07-04 | 2025 | 2024 | 2024-07-01 | 31 | [7 empty] | 6.6621 | 0 | 89.64% | 89.64% | 100% | 100% |  |  |  |  | 22.3% | 383466 | 375750 | 0 | 375750 | 43 | 8.18 | 774981.4516 |  | 46% | 96.03% | 99.5% | 0 |  |  |  |  | 2.012% | 0% | 5% | 5% | 70.2
2024-07-05 | 2025 | 2024 | 2024-07-01 | 31 | [7 empty] | 6.1196 | 0 | 95.19% | 95.19% | 100% | 100% |  |  |  |  | 16.69% | 288587 | 281700 | 450 | 281250 | 43 | 8.18 | 774981.4516 |  | 46% | 96.03% | 99.5% | 0 |  |  |  |  | 2.386% | 0% | 5% | 5% | 70.2
2024-07-06 | 2025 | 2024 | 2024-07-01 | 31 | [7 empty] | 7.4568 | 0 | 96.57% | 96.57% | 100% | 100% |  |  |  |  | 30.98% | 598114 | 522000 | 0 | 522000 | 43 | 8.18 | 774981.4516 |  | 46% | 96.03% | 99.5% | 0 |  |  |  |  | 12.73% | 0% | 5% | 5% | 70.2
2024-07-07 | 2025 | 2024 | 2024-07-01 | 31 | [7 empty] | 7.4306 | 0 | 98.44% | 98.77% | 99.67% | 100% |  |  |  |  | 32.85% | 566726 | 553500 | 0 | 553500 | 43 | 8.18 | 774981.4516 |  | 46% | 96.03% | 99.5% | 0 |  |  |  |  | 2.334% | 0% | 5% | 5% | 70.2
2024-07-08 | 2025 | 2024 | 2024-07-01 | 31 | [7 empty] | 5.2695 | 0 | 95.04% | 95.04% | 100% | 100% |  |  |  |  | 13.03% | 225025 | 219600 | 0 | 219600 | 43 | 8.18 | 774981.4516 |  | 46% | 96.03% | 99.5% | 0 |  |  |  |  | 2.411% | 0% | 5% | 5% | 70.2
2024-07-09 | 2025 | 2024 | 2024-07-01 | 31 | [7 empty] | 4.7641 | 0 | 98.07% | 98.07% | 100% | 100% |  |  |  |  | 10.23% | 177534 | 172350 | 0 | 172350 | 43 | 8.18 | 774981.4516 |  | 46% | 96.03% | 99.5% | 0 |  |  |  |  | 2.92% | 0% | 5% | 5% | 70.2
2024-07-10 | 2025 | 2024 | 2024-07-01 | 31 | [7 empty] | 4.5678 | 0 | 93.94% | 96.92% | 96.92% | 100% |  |  |  |  | 8.387% | 145923 | 142650 | 1350 | 141300 | 43 | 8.18 | 774981.4516 |  | 46% | 96.03% | 99.5% | 0 |  |  |  |  | 2.243% | 0% | 5% | 5% | 70.2
2024-07-11 | 2025 | 2024 | 2024-07-01 | 31 | [7 empty] | 6.5663 | 0 | 81.62% | 95.57% | 85.4% | 100% |  |  |  |  | 16.72% | 287713 | 281700 | 0 | 281700 | 43 | 8.18 | 774981.4516 |  | 46% | 96.03% | 99.5% | 0 |  |  |  |  | 2.09% | 0% | 5% | 5% | 70.2
2024-07-12 | 2025 | 2024 | 2024-07-01 | 31 | [7 empty] | 8.4372 | 0 | 77.18% | 92.78% | 83.18% | 100% |  |  |  |  | 29.73% | 514002 | 500850 | 0 | 500850 | 43 | 8.18 | 774981.4516 |  | 46% | 96.03% | 99.5% | 0 |  |  |  |  | 2.559% | 0% | 5% | 5% | 70.2
2024-07-13 | 2025 | 2024 | 2024-07-01 | 31 | [7 empty] | 7.9693 | 0 | 91.14% | 96.7% | 94.25% | 93.97% |  |  |  |  | 32.85% | 567859 | 553500 | 0 | 553500 | 43 | 8.18 | 774981.4516 |  | 46% | 96.03% | 99.5% | 0 |  |  |  |  | 2.529% | 0% | 5% | 5% | 70.2
2024-07-14 | 2025 | 2024 | 2024-07-01 | 31 | [7 empty] | 6.8033 | 0 | 94.88% | 99.76% | 95.1% | 100% |  |  |  |  | 26.15% | 449958 | 440550 | 0 | 440550 | 43 | 8.18 | 774981.4516 |  | 46% | 96.03% | 99.5% | 0 |  |  |  |  | 2.091% | 0% | 5% | 5% | 70.2
2024-07-15 | 2025 | 2024 | 2024-07-01 | 31 | [7 empty] | 4.9319 | 0 | 97.01% | 97.01% | 100% | 100% |  |  |  |  | 11.38% | 197725 | 191700 | 0 | 191700 | 43 | 8.18 | 774981.4516 |  | 46% | 96.03% | 99.5% | 0 |  |  |  |  | 3.047% | 0% | 5% | 5% | 70.2
2024-07-16 | 2025 | 2024 | 2024-07-01 | 31 | [7 empty] | 4.9478 | 0 | 93.3% | 95.4% | 97.8% | 100% |  |  |  |  | 10.52% | 182058 | 177750 | 450 | 177300 | 43 | 8.18 | 774981.4516 |  | 46% | 96.03% | 99.5% | 0 |  |  |  |  | 2.366% | 0% | 5% | 5% | 70.2
2024-07-17 | 2025 | 2024 | 2024-07-01 | 31 | [7 empty] | 4.9635 | 0 | 92.4% | 92.4% | 100% | 100% |  |  |  |  | 9.562% | 165494 | 161100 | 0 | 161100 | 43 | 8.18 | 774981.4516 |  | 46% | 96.03% | 99.5% | 0 |  |  |  |  | 2.655% | 0% | 5% | 5% | 70.2
2024-07-18 | 2025 | 2024 | 2024-07-01 | 31 | [7 empty] | 4.7274 | 0 | 97.83% | 97.83% | 100% | 100% |  |  |  |  | 10.28% | 178348 | 173250 | 0 | 173250 | 43 | 8.18 | 774981.4516 |  | 46% | 96.03% | 99.5% | 0 |  |  |  |  | 2.858% | 0% | 5% | 5% | 70.2
2024-07-19 | 2025 | 2024 | 2024-07-01 | 31 | [7 empty] | 5.6897 | 0 | 76.7% | 97.61% | 78.58% | 100% |  |  |  |  | 12.95% | 220777 | 218700 | 450 | 218250 | 43 | 8.18 | 774981.4516 |  | 46% | 96.03% | 99.5% | 0 |  |  |  |  | 0.9408% | 0% | 5% | 5% | 70.2
2024-07-20 | 2025 | 2024 | 2024-07-01 | 31 | [7 empty] | 5.2261 | 0 | 78.77% | 96.79% | 81.39% | 100% |  |  |  |  | 9.749% | 165682 | 164250 | 0 | 164250 | 43 | 8.18 | 774981.4516 |  | 46% | 96.03% | 99.5% | 0 |  |  |  |  | 0.8643% | 0% | 5% | 5% | 70.2
2024-07-21 | 2025 | 2024 | 2024-07-01 | 31 | [7 empty] | 5.4829 | 0 | 92.42% | 92.42% | 100% | 100% |  |  |  |  | 18% | 312243 | 304200 | 900 | 303300 | 45.9 | 8.18 | 774981.4516 |  | 46% | 96.03% | 99.5% | 0 |  |  |  |  | 2.576% | 0% | 5% | 5% | 70.2
2024-07-22 | 2025 | 2024 | 2024-07-01 | 31 | [7 empty] | 7.6032 | 0 | 92.58% | 92.58% | 100% | 100% |  |  |  |  | 29.35% | 505357 | 494550 | 0 | 494550 | 45.9 | 8.18 | 774981.4516 |  | 46% | 96.03% | 99.5% | 0 |  |  |  |  | 2.138% | 0% | 5% | 5% | 70.2
2024-07-23 | 2025 | 2024 | 2024-07-01 | 31 | [7 empty] | 9.3262 | 0 | 92.47% | 92.47% | 100% | 100% |  |  |  |  | 46.42% | 781798 | 782100 | 0 | 782100 | 45.9 | 8.18 | 774981.4516 |  | 46% | 96.03% | 99.5% | 0 |  |  |  |  | -0.03863% | 0% | 5% | 5% | 70.2
2024-07-24 | 2025 | 2024 | 2024-07-01 | 31 | [7 empty] | 10.2301 | 0 | 92.72% | 92.72% | 100% | 100% |  |  |  |  | 54.51% | 945365 | 918450 | 0 | 918450 | 45.9 | 8.18 | 774981.4516 |  | 46% | 96.03% | 99.5% | 0 |  |  |  |  | 2.847% | 0% | 5% | 5% | 70.2
2024-07-25 | 2025 | 2024 | 2024-07-01 | 31 | [7 empty] | 10.0261 | 0 | 89.19% | 89.19% | 100% | 100% |  |  |  |  | 54.46% | 945910 | 917550 | 0 | 917550 | 45.9 | 8.18 | 774981.4516 |  | 46% | 96.03% | 99.5% | 0 |  |  |  |  | 2.998% | 0% | 5% | 5% | 70.2
2024-07-26 | 2025 | 2024 | 2024-07-01 | 31 | [7 empty] | 9.2061 | 0 | 97.4% | 97.4% | 100% | 100% |  |  |  |  | 53.98% | 938695 | 909450 | 0 | 909450 | 48.6 | 8.18 | 774981.4516 |  | 46% | 96.03% | 99.5% | 0 |  |  |  |  | 3.115% | 0% | 5% | 5% | 70.2
2024-07-27 | 2025 | 2024 | 2024-07-01 | 31 | [7 empty] | 8.0815 | 0 | 97.55% | 97.55% | 100% | 100% |  |  |  |  | 42.84% | 709798 | 721800 | 0 | 721800 | 48.6 | 8.18 | 774981.4516 |  | 46% | 96.03% | 99.5% | 0 |  |  |  |  | -1.691% | 0% | 5% | 5% | 70.2
2024-07-28 | 2025 | 2024 | 2024-07-01 | 31 | [7 empty] | 6.4821 | 0 | 97.34% | 97.34% | 100% | 92.89% |  |  |  |  | 22.09% | 362384 | 372150 | 0 | 372150 | 48.6 | 8.18 | 774981.4516 |  | 46% | 96.03% | 99.5% | 0 |  |  |  |  | -2.695% | 0% | 5% | 5% | 70.2
2024-07-29 | 2025 | 2024 | 2024-07-01 | 31 | [7 empty] | 6.882 | 0 | 96.35% | 96.35% | 100% | 100% |  |  |  |  | 27.72% | 476951 | 467100 | 0 | 467100 | 48.6 | 8.18 | 774981.4516 |  | 46% | 96.03% | 99.5% | 0 |  |  |  |  | 2.065% | 0% | 5% | 5% | 70.2
2024-07-30 | 2025 | 2024 | 2024-07-01 | 31 | [7 empty] | 6.7183 | 0 | 98.05% | 98.05% | 100% | 100% |  |  |  |  | 25.75% | 441160 | 433800 | 0 | 433800 | 48.6 | 8.18 | 774981.4516 |  | 46% | 96.03% | 99.5% | 0 |  |  |  |  | 1.668% | 0% | 5% | 5% | 70.2
2024-07-31 | 2025 | 2024 | 2024-07-01 | 31 | [7 empty] | 7.3082 | 0 | 97.89% | 97.89% | 100% | 100% |  |  |  |  | 30.15% | 520353 | 508050 | 0 | 508050 | 48.6 | 8.18 | 774981.4516 |  | 46% | 96.03% | 99.5% | 0 |  |  |  |  | 2.364% | 0% | 5% | 5% | 70.2
2024-08-01 | 2025 | 2024 | 2024-08-01 | 31 | [7 empty] | 8.6486 | 0 | 92.51% | 92.51% | 100% | 100% |  |  |  |  | 42.52% | 738348 | 716400 | 0 | 716400 | 48.6 | 9.01 | 720184.7742 |  | 42.75% | 96.03% | 99.5% | 0 |  |  |  |  | 2.973% | 0% | 5% | 5% | 70.2
2024-08-02 | 2025 | 2024 | 2024-08-01 | 31 | [7 empty] | 9.1562 | 0 | 94.81% | 94.81% | 100% | 100% |  |  |  |  | 51.76% | 899383 | 872100 | 0 | 872100 | 48.6 | 9.01 | 720184.7742 |  | 42.75% | 96.03% | 99.5% | 0 |  |  |  |  | 3.034% | 0% | 5% | 5% | 70.2
2024-08-03 | 2025 | 2024 | 2024-08-01 | 31 | [7 empty] | 9.6241 | 0 | 95.26% | 95.26% | 100% | 100% |  |  |  |  | 56.38% | 978096 | 949950 | 0 | 949950 | 48.6 | 9.01 | 720184.7742 |  | 42.75% | 96.03% | 99.5% | 0 |  |  |  |  | 2.878% | 0% | 5% | 5% | 70.2
2024-08-04 | 2025 | 2024 | 2024-08-01 | 31 | [7 empty] | 8.4203 | 0 | 90.55% | 95.3% | 95.01% | 100% |  |  |  |  | 42.04% | 727177 | 708300 | 0 | 708300 | 48.6 | 9.01 | 720184.7742 |  | 42.75% | 96.03% | 99.5% | 0 |  |  |  |  | 2.596% | 0% | 5% | 5% | 70.2
2024-08-05 | 2025 | 2024 | 2024-08-01 | 31 | [7 empty] | 7.3002 | 0 | 98.44% | 98.44% | 100% | 100% |  |  |  |  | 31.68% | 546795 | 533700 | 0 | 533700 | 48.6 | 9.01 | 720184.7742 |  | 42.75% | 96.03% | 99.5% | 0 |  |  |  |  | 2.395% | 0% | 5% | 5% | 70.2
2024-08-06 | 2025 | 2024 | 2024-08-01 | 31 | [7 empty] | 7.9576 | 0 | 98.65% | 98.65% | 100% | 100% |  |  |  |  | 39.69% | 670905 | 668700 | 0 | 668700 | 48.6 | 9.01 | 720184.7742 |  | 42.75% | 96.03% | 99.5% | 0 |  |  |  |  | 0.3287% | 0% | 5% | 5% | 70.2
2024-08-07 | 2025 | 2024 | 2024-08-01 | 31 | [7 empty] | 8.0336 | 0 | 95.29% | 95.29% | 100% | 100% |  |  |  |  | 40.49% | 699904 | 682200 | 0 | 682200 | 48.6 | 9.01 | 720184.7742 |  | 42.75% | 96.03% | 99.5% | 0 |  |  |  |  | 2.529% | 0% | 5% | 5% | 70.2
2024-08-08 | 2025 | 2024 | 2024-08-01 | 31 | [7 empty] | 7.3002 | 0 | 91.79% | 91.79% | 100% | 100% |  |  |  |  | 30.48% | 523594 | 513450 | 0 | 513450 | 48.6 | 9.01 | 720184.7742 |  | 42.75% | 96.03% | 99.5% | 0 |  |  |  |  | 1.937% | 0% | 5% | 5% | 70.2
2024-08-09 | 2025 | 2024 | 2024-08-01 | 31 | [7 empty] | 7.5365 | 0 | 91.45% | 91.45% | 100% | 100% |  |  |  |  | 31.89% | 550498 | 537300 | 0 | 537300 | 48.6 | 9.01 | 720184.7742 |  | 42.75% | 96.03% | 99.5% | 0 |  |  |  |  | 2.397% | 0% | 5% | 5% | 70.2
2024-08-10 | 2025 | 2024 | 2024-08-01 | 31 | [7 empty] | 8.2017 | 0 | 91.97% | 92.86% | 99.04% | 100% |  |  |  |  | 38.92% | 671574 | 655650 | 0 | 655650 | 48.6 | 9.01 | 720184.7742 |  | 42.75% | 96.03% | 99.5% | 0 |  |  |  |  | 2.371% | 0% | 5% | 5% | 70.2
2024-08-11 | 2025 | 2024 | 2024-08-01 | 31 | [7 empty] | 8.7801 | 0 | 93.66% | 93.66% | 100% | 100% |  |  |  |  | 47.28% | 818105 | 796500 | 0 | 796500 | 48.6 | 9.01 | 720184.7742 |  | 42.75% | 96.03% | 99.5% | 0 |  |  |  |  | 2.641% | 0% | 5% | 5% | 70.2
2024-08-12 | 2025 | 2024 | 2024-08-01 | 31 | [7 empty] | 7.3422 | 0 | 86.14% | 94.51% | 91.14% | 100% |  |  |  |  | 29.99% | 514829 | 505350 | 0 | 505350 | 48.6 | 9.01 | 720184.7742 |  | 42.75% | 96.03% | 99.5% | 0 |  |  |  |  | 1.841% | 0% | 5% | 5% | 70.2
2024-08-13 | 2025 | 2024 | 2024-08-01 | 31 | [7 empty] | 5.6961 | 0 | 85.85% | 91.83% | 93.49% | 100% |  |  |  |  | 15.95% | 274662 | 268650 | 0 | 268650 | 48.6 | 9.01 | 720184.7742 |  | 42.75% | 96.03% | 99.5% | 0 |  |  |  |  | 2.189% | 0% | 5% | 5% | 70.2
2024-08-14 | 2025 | 2024 | 2024-08-01 | 31 | [7 empty] | 5.5092 | 0 | 91.83% | 91.83% | 100% | 100% |  |  |  |  | 14.29% | 245859 | 240750 | 0 | 240750 | 48.6 | 9.01 | 720184.7742 |  | 42.75% | 96.03% | 99.5% | 0 |  |  |  |  | 2.078% | 0% | 5% | 5% | 70.2
2024-08-15 | 2025 | 2024 | 2024-08-01 | 31 | [7 empty] | 6.1079 | 0 | 93.42% | 93.42% | 100% | 100% |  |  |  |  | 19.63% | 337172 | 330750 | 0 | 330750 | 48.6 | 9.01 | 720184.7742 |  | 42.75% | 96.03% | 99.5% | 0 |  |  |  |  | 1.905% | 0% | 5% | 5% | 70.2
2024-08-16 | 2025 | 2024 | 2024-08-01 | 31 | [7 empty] | 5.7929 | 0 | 91.72% | 91.72% | 100% | 100% |  |  |  |  | 16.64% | 285974 | 280350 | 0 | 280350 | 48.6 | 9.01 | 720184.7742 |  | 42.75% | 96.03% | 99.5% | 0 |  |  |  |  | 1.967% | 0% | 5% | 5% | 70.2
2024-08-17 | 2025 | 2024 | 2024-08-01 | 31 | [7 empty] | 5.4616 | 0 | 96.73% | 96.73% | 100% | 100% |  |  |  |  | 15.73% | 271674 | 265050 | 0 | 265050 | 48.6 | 9.01 | 720184.7742 |  | 42.75% | 96.03% | 99.5% | 0 |  |  |  |  | 2.438% | 0% | 5% | 5% | 70.2
2024-08-18 | 2025 | 2024 | 2024-08-01 | 31 | [7 empty] | 4.3419 | 0 | 98.27% | 98.27% | 100% | 100% |  |  |  |  | 9.776% | 171065 | 165150 | 450 | 164700 | 48.6 | 9.01 | 720184.7742 |  | 42.75% | 96.03% | 99.5% | 0 |  |  |  |  | 3.458% | 0% | 5% | 5% | 70.2
2024-08-19 | 2025 | 2024 | 2024-08-01 | 31 | [7 empty] | 4.2639 | 0 | 94.27% | 94.27% | 100% | 100% |  |  |  |  | 6.784% | 118212 | 114750 | 450 | 114300 | 48.6 | 9.01 | 720184.7742 |  | 42.75% | 96.03% | 99.5% | 0 |  |  |  |  | 2.929% | 0% | 5% | 5% | 70.2
2024-08-20 | 2025 | 2024 | 2024-08-01 | 31 | [7 empty] | 4.662 | 0 | 92.4% | 92.4% | 100% | 100% |  |  |  |  | 9.696% | 167977 | 163350 | 0 | 163350 | 48.6 | 9.01 | 720184.7742 |  | 42.75% | 96.03% | 99.5% | 0 |  |  |  |  | 2.755% | 0% | 5% | 5% | 70.2
2024-08-21 | 2025 | 2024 | 2024-08-01 | 31 | [7 empty] | 3.4717 | 0 | 92.71% | 93.9% | 98.74% | 100% |  |  |  |  | 4.861% | 81318 | 83250 | 1350 | 81900 | 48.6 | 9.01 | 720184.7742 |  | 42.75% | 96.03% | 99.5% | 0 |  |  |  |  | -2.376% | 0% | 5% | 5% | 70.2
2024-08-22 | 2025 | 2024 | 2024-08-01 | 31 | [7 empty] | 3.371 | 0 | 96.8% | 96.8% | 100% | 100% |  |  |  |  | 3.579% | 64857 | 61650 | 1350 | 60300 | 51.3 | 9.01 | 720184.7742 |  | 42.75% | 96.03% | 99.5% | 0 |  |  |  |  | 4.945% | 0% | 5% | 5% | 70.2
2024-08-23 | 2025 | 2024 | 2024-08-01 | 31 | [7 empty] | 4.3956 | 0 | 90.84% | 90.84% | 100% | 100% |  |  |  |  | 6.41% | 112595 | 108000 | 0 | 108000 | 51.3 | 9.01 | 720184.7742 |  | 42.75% | 96.03% | 99.5% | 0 |  |  |  |  | 4.081% | 0% | 5% | 5% | 70.2
2024-08-24 | 2025 | 2024 | 2024-08-01 | 31 | [7 empty] | 7.1959 | 0 | 86.86% | 91.8% | 94.63% | 100% |  |  |  |  | 25.93% | 449157 | 436950 | 0 | 436950 | 51.3 | 9.01 | 720184.7742 |  | 42.75% | 96.03% | 99.5% | 0 |  |  |  |  | 2.718% | 0% | 5% | 5% | 70.2
2024-08-25 | 2025 | 2024 | 2024-08-01 | 31 | [7 empty] | 10.6882 | 0 | 97.81% | 97.81% | 100% | 100% |  |  |  |  | 64.05% | 1118460 | 1079100 | 0 | 1079100 | 51.3 | 9.01 | 720184.7742 |  | 42.75% | 96.03% | 99.5% | 0 |  |  |  |  | 3.519% | 0% | 5% | 5% | 70.2
2024-08-26 | 2025 | 2024 | 2024-08-01 | 31 | [7 empty] | 12.8023 | 0 | 88.04% | 88.04% | 100% | 62.3% |  |  |  |  | 39.45% | 687584 | 664650 | 0 | 664650 | 51.3 | 9.01 | 720184.7742 |  | 42.75% | 96.03% | 99.5% | 0 |  |  |  |  | 3.335% | 0% | 5% | 5% | 70.2
2024-08-27 | 2025 | 2024 | 2024-08-01 | 31 | [7 empty] | 12.2414 | 0 | 87.54% | 87.54% | 100% | 100% |  |  |  |  | 57.88% | 1002130 | 975150 | 0 | 975150 | 51.3 | 9.01 | 720184.7742 |  | 42.75% | 96.03% | 99.5% | 0 |  |  |  |  | 2.692% | 0% | 5% | 5% | 70.2
2024-08-28 | 2025 | 2024 | 2024-08-01 | 31 | [7 empty] | 13.2479 | 0 | 83.02% | 83.33% | 99.62% | 100% |  |  |  |  | 57.13% | 993705 | 962550 | 0 | 962550 | 51.3 | 9.01 | 720184.7742 |  | 42.75% | 96.03% | 99.5% | 0 |  |  |  |  | 3.135% | 0% | 5% | 5% | 70.2
2024-08-29 | 2025 | 2024 | 2024-08-01 | 31 | [7 empty] | 11.253 | 0 | 86.6% | 86.6% | 100% | 100% |  |  |  |  | 63.27% | 1102491 | 1066050 | 0 | 1066050 | 51.3 | 9.01 | 720184.7742 |  | 42.75% | 96.03% | 99.5% | 0 |  |  |  |  | 3.305% | 0% | 5% | 5% | 70.2
2024-08-30 | 2025 | 2024 | 2024-08-01 | 31 | [7 empty] | 7.1542 | 0 | 93.5% | 95.15% | 98.27% | 100% |  |  |  |  | 36.35% | 628872 | 612425 | 0 | 612425 | 51.3 | 9.01 | 720184.7742 |  | 42.75% | 96.03% | 99.5% | 0 |  |  |  |  | 2.615% | 0% | 5% | 5% | 70.2
2024-08-31 | 2025 | 2024 | 2024-08-01 | 31 | [7 empty] | 4.5452 | 0 | 89.27% | 91.23% | 97.85% | 100% |  |  |  |  | 9.375% | 162320 | 157950 | 0 | 157950 | 51.3 | 9.01 | 720184.7742 |  | 42.75% | 96.03% | 99.5% | 0 |  |  |  |  | 2.692% | 0% | 5% | 5% | 70.2
2024-09-01 | 2025 | 2024 | 2024-09-01 | 30 | [7 empty] | 4.8063 | 0 | 94.13% | 94.13% | 100% | 100% |  |  |  |  | 11.7% | 203342 | 197100 | 0 | 197100 | 51.3 | 8.16 | 531658.1333 |  | 31.56% | 96.03% | 99.5% | 0 |  |  |  |  | 3.07% | 0% | 5% | 5% | 70.2
2024-09-02 | 2025 | 2024 | 2024-09-01 | 30 | [7 empty] | 4.9588 | 0 | 93.48% | 93.48% | 100% | 73.8% |  |  |  |  | 8.841% | 152443 | 148950 | 0 | 148950 | 51.3 | 8.16 | 531658.1333 |  | 31.56% | 96.03% | 99.5% | 0 |  |  |  |  | 2.291% | 0% | 5% | 5% | 70.2
2024-09-03 | 2025 | 2024 | 2024-09-01 | 30 | [7 empty] | 5.1129 | 0 | 83.78% | 84.29% | 99.41% | 100% |  |  |  |  | 12.23% | 211063 | 206100 | 0 | 206100 | 51.3 | 8.16 | 531658.1333 |  | 31.56% | 96.03% | 99.5% | 0 |  |  |  |  | 2.351% | 0% | 5% | 5% | 70.2
2024-09-04 | 2025 | 2024 | 2024-09-01 | 30 | [7 empty] | 5.9674 | 0 | 91.08% | 91.73% | 99.29% | 100% |  |  |  |  | 18.99% | 327229 | 319950 | 0 | 319950 | 51.3 | 8.16 | 531658.1333 |  | 31.56% | 96.03% | 99.5% | 0 |  |  |  |  | 2.224% | 0% | 5% | 5% | 70.2
2024-09-05 | 2025 | 2024 | 2024-09-01 | 30 | [7 empty] | 7.1692 | 0 | 94.71% | 94.71% | 100% | 100% |  |  |  |  | 33.79% | 584390 | 569250 | 0 | 569250 | 51.3 | 8.16 | 531658.1333 |  | 31.56% | 96.03% | 99.5% | 0 |  |  |  |  | 2.591% | 0% | 5% | 5% | 70.2
2024-09-06 | 2025 | 2024 | 2024-09-01 | 30 | [7 empty] | 6.7489 | 0 | 86.71% | 87.96% | 98.58% | 91.83% |  |  |  |  | 27.24% | 455104 | 459450 | 450 | 459000 | 56.7 | 8.16 | 531658.1333 |  | 31.56% | 96.03% | 99.5% | 0 |  |  |  |  | -0.9549% | 0% | 5% | 5% | 70.2
2024-09-07 | 2025 | 2024 | 2024-09-01 | 30 | [7 empty] | 5.6953 | 0 | 85.79% | 97.65% | 87.86% | 100% |  |  |  |  | 17.55% | 302475 | 295650 | 0 | 295650 | 56.7 | 8.16 | 531658.1333 |  | 31.56% | 96.03% | 99.5% | 0 |  |  |  |  | 2.256% | 0% | 5% | 5% | 70.2
2024-09-08 | 2025 | 2024 | 2024-09-01 | 30 | [7 empty] | 4.6209 | 0 | 94.74% | 96.37% | 98.31% | 100% |  |  |  |  | 9.776% | 169976 | 164700 | 0 | 164700 | 56.7 | 8.16 | 531658.1333 |  | 31.56% | 96.03% | 99.5% | 0 |  |  |  |  | 3.104% | 0% | 5% | 5% | 70.2
2024-09-09 | 2025 | 2024 | 2024-09-01 | 30 | [7 empty] | 5.39 | 0 | 88.75% | 92.05% | 96.41% | 100% |  |  |  |  | 14.72% | 253827 | 247950 | 0 | 247950 | 56.7 | 8.16 | 531658.1333 |  | 31.56% | 96.03% | 99.5% | 0 |  |  |  |  | 2.315% | 0% | 5% | 5% | 70.2
2024-09-10 | 2025 | 2024 | 2024-09-01 | 30 | [7 empty] | 5.7606 | 0 | 96.76% | 96.76% | 100% | 100% |  |  |  |  | 20.03% | 344751 | 337500 | 0 | 337500 | 56.7 | 8.16 | 531658.1333 |  | 31.56% | 96.03% | 99.5% | 0 |  |  |  |  | 2.103% | 0% | 5% | 5% | 70.2
2024-09-11 | 2025 | 2024 | 2024-09-01 | 30 | [7 empty] | 6.0521 | 0 | 98.56% | 98.56% | 100% | 100% |  |  |  |  | 22.25% | 383710 | 374850 | 0 | 374850 | 56.7 | 8.16 | 531658.1333 |  | 31.56% | 96.03% | 99.5% | 0 |  |  |  |  | 2.309% | 0% | 5% | 5% | 70.2
2024-09-12 | 2025 | 2024 | 2024-09-01 | 30 | [7 empty] | 7.0529 | 0 | 96.54% | 96.54% | 100% | 100% |  |  |  |  | 33.49% | 577181 | 564300 | 0 | 564300 | 56.7 | 8.16 | 531658.1333 |  | 31.56% | 96.03% | 99.5% | 0 |  |  |  |  | 2.232% | 0% | 5% | 5% | 70.2
2024-09-13 | 2025 | 2024 | 2024-09-01 | 30 | [7 empty] | 6.7652 | 0 | 93.96% | 94.68% | 99.23% | 100% |  |  |  |  | 30.9% | 534212 | 520650 | 0 | 520650 | 56.7 | 8.16 | 531658.1333 |  | 31.56% | 96.03% | 99.5% | 0 |  |  |  |  | 2.539% | 0% | 5% | 5% | 70.2
2024-09-14 | 2025 | 2024 | 2024-09-01 | 30 | [7 empty] | 6.2764 | 0 | 96.53% | 96.53% | 100% | 100% |  |  |  |  | 25.48% | 439907 | 429300 | 0 | 429300 | 56.7 | 8.16 | 531658.1333 |  | 31.56% | 96.03% | 99.5% | 0 |  |  |  |  | 2.411% | 0% | 5% | 5% | 70.2
2024-09-15 | 2025 | 2024 | 2024-09-01 | 30 | [7 empty] | 6.1036 | 0 | 95.84% | 95.84% | 100% | 100% |  |  |  |  | 23.1% | 398567 | 389250 | 0 | 389250 | 56.7 | 8.16 | 531658.1333 |  | 31.56% | 96.03% | 99.5% | 0 |  |  |  |  | 2.338% | 0% | 5% | 5% | 70.2
2024-09-16 | 2025 | 2024 | 2024-09-01 | 30 | [7 empty] | 5.7369 | 0 | 92.84% | 92.84% | 100% | 100% |  |  |  |  | 20.27% | 349465 | 341550 | 0 | 341550 | 56.7 | 8.16 | 531658.1333 |  | 31.56% | 96.03% | 99.5% | 0 |  |  |  |  | 2.265% | 0% | 5% | 5% | 70.2
2024-09-17 | 2025 | 2024 | 2024-09-01 | 30 | [7 empty] | 4.5733 | 0 | 95.52% | 95.52% | 100% | 85.73% |  |  |  |  | 8.627% | 150272 | 145350 | 0 | 145350 | 56.7 | 8.16 | 531658.1333 |  | 31.56% | 96.03% | 99.5% | 0 |  |  |  |  | 3.275% | 0% | 5% | 5% | 70.2
2024-09-18 | 2025 | 2024 | 2024-09-01 | 30 | [7 empty] | 4.8166 | 0 | 91.23% | 91.23% | 100% | 100% |  |  |  |  | 11.51% | 199055 | 193950 | 0 | 193950 | 56.7 | 8.16 | 531658.1333 |  | 31.56% | 96.03% | 99.5% | 0 |  |  |  |  | 2.565% | 0% | 5% | 5% | 70.2
2024-09-19 | 2025 | 2024 | 2024-09-01 | 30 | [7 empty] | 5.2283 | 0 | 92.73% | 92.73% | 100% | 100% |  |  |  |  | 14.85% | 256698 | 250200 | 0 | 250200 | 56.7 | 8.16 | 531658.1333 |  | 31.56% | 96.03% | 99.5% | 0 |  |  |  |  | 2.531% | 0% | 5% | 5% | 70.2
2024-09-20 | 2025 | 2024 | 2024-09-01 | 30 | [7 empty] | 5.7023 | 0 | 81.69% | 92.43% | 88.38% | 100% |  |  |  |  | 17.31% | 298431 | 291600 | 0 | 291600 | 56.7 | 8.16 | 531658.1333 |  | 31.56% | 96.03% | 99.5% | 0 |  |  |  |  | 2.289% | 0% | 5% | 5% | 70.2
2024-09-21 | 2025 | 2024 | 2024-09-01 | 30 | [7 empty] | 5.4287 | 0 | 90.86% | 92.94% | 97.76% | 100% |  |  |  |  | 18.59% | 320424 | 313200 | 0 | 313200 | 56.7 | 8.16 | 531658.1333 |  | 31.56% | 96.03% | 99.5% | 0 |  |  |  |  | 2.255% | 0% | 5% | 5% | 70.2
2024-09-22 | 2025 | 2024 | 2024-09-01 | 30 | [7 empty] | 5.1294 | 0 | 96.37% | 96.48% | 99.89% | 100% |  |  |  |  | 14.8% | 255643 | 249300 | 0 | 249300 | 56.7 | 8.16 | 531658.1333 |  | 31.56% | 96.03% | 99.5% | 0 |  |  |  |  | 2.481% | 0% | 5% | 5% | 70.2
2024-09-23 | 2025 | 2024 | 2024-09-01 | 30 | [7 empty] | 5.674 | 0 | 96.77% | 96.77% | 100% | 100% |  |  |  |  | 19.71% | 340350 | 332100 | 0 | 332100 | 56.7 | 8.16 | 531658.1333 |  | 31.56% | 96.03% | 99.5% | 0 |  |  |  |  | 2.424% | 0% | 5% | 5% | 70.2
2024-09-24 | 2025 | 2024 | 2024-09-01 | 30 | [7 empty] | 5.903 | 0 | 96.4% | 96.4% | 100% | 100% |  |  |  |  | 22.46% | 388290 | 378450 | 0 | 378450 | 59.4 | 8.16 | 531658.1333 |  | 31.56% | 96.03% | 99.5% | 0 |  |  |  |  | 2.534% | 0% | 5% | 5% | 70.2
2024-09-25 | 2025 | 2024 | 2024-09-01 | 30 | [7 empty] | 6.2803 | 0 | 91.67% | 91.67% | 100% | 100% |  |  |  |  | 26.01% | 448868 | 438300 | 0 | 438300 | 59.4 | 8.16 | 531658.1333 |  | 31.56% | 96.03% | 99.5% | 0 |  |  |  |  | 2.354% | 0% | 5% | 5% | 70.2
2024-09-26 | 2025 | 2024 | 2024-09-01 | 30 | [7 empty] | 5.5994 | 0 | 83.08% | 87.7% | 94.73% | 100% |  |  |  |  | 15.92% | 276025 | 268200 | 0 | 268200 | 59.4 | 8.16 | 531658.1333 |  | 31.56% | 96.03% | 99.5% | 0 |  |  |  |  | 2.835% | 0% | 5% | 5% | 70.2
2024-09-27 | 2025 | 2024 | 2024-09-01 | 30 | [7 empty] | 6.9493 | 0 | 91.57% | 91.57% | 100% | 100% |  |  |  |  | 37.71% | 656256 | 635850 | 450 | 635400 | 59.4 | 8.16 | 531658.1333 |  | 31.56% | 96.03% | 99.5% | 0 |  |  |  |  | 3.109% | 0% | 5% | 5% | 70.2
2024-09-28 | 2025 | 2024 | 2024-09-01 | 30 | [7 empty] | 5.7278 | 0 | 99.58% | 99.58% | 100% | 100% |  |  |  |  | 24.36% | 420691 | 410400 | 0 | 410400 | 59.4 | 8.16 | 531658.1333 |  | 31.56% | 96.03% | 99.5% | 0 |  |  |  |  | 2.446% | 0% | 5% | 5% | 70.2
2024-09-29 | 2025 | 2024 | 2024-09-01 | 30 | [7 empty] | 3.7807 | 0 | 98.95% | 98.95% | 100% | 97.32% |  |  |  |  | 7.131% | 126254 | 121050 | 900 | 120150 | 59.4 | 8.16 | 531658.1333 |  | 31.56% | 96.03% | 99.5% | 0 |  |  |  |  | 4.122% | 0% | 5% | 5% | 70.2
2024-09-30 | 2025 | 2024 | 2024-09-01 | 30 | [7 empty] | 4.3531 | 0 | 98.4% | 98.4% | 100% | 100% |  |  |  |  | 11.94% | 207264 | 202050 | 900 | 201150 | 59.4 | 8.16 | 531658.1333 |  | 31.56% | 96.03% | 99.5% | 0 |  |  |  |  | 2.516% | 0% | 5% | 5% | 70.2
2024-10-01 | 2025 | 2024 | 2024-10-01 | 31 | [7 empty] | 3.6858 | 0 | 96.23% | 97.47% | 98.73% | 100% |  |  |  |  | 6.757% | 119861 | 114750 | 900 | 113850 | 59.4 | 9.21 | 365311.129 |  | 21.68% | 96.03% | 99.5% | 0 |  |  |  |  | 4.264% | 0% | 5% | 5% | 70.2
2024-10-02 | 2025 | 2024 | 2024-10-01 | 31 | [7 empty] | 3.9374 | 0 | 97.5% | 98.66% | 98.82% | 100% |  |  |  |  | 5.849% | 102549 | 99000 | 450 | 98550 | 59.4 | 9.21 | 365311.129 |  | 21.68% | 96.03% | 99.5% | 0 |  |  |  |  | 3.461% | 0% | 5% | 5% | 70.2
2024-10-03 | 2025 | 2024 | 2024-10-01 | 31 | [7 empty] | 5.4259 | 0 | 95.88% | 97.18% | 98.66% | 100% |  |  |  |  | 17.9% | 309801 | 301500 | 0 | 301500 | 59.4 | 9.21 | 365311.129 |  | 21.68% | 96.03% | 99.5% | 0 |  |  |  |  | 2.679% | 0% | 5% | 5% | 70.2
2024-10-04 | 2025 | 2024 | 2024-10-01 | 31 | [7 empty] | 5.5516 | 0 | 97.82% | 97.82% | 100% | 100% |  |  |  |  | 21.05% | 362721 | 354600 | 0 | 354600 | 59.4 | 9.21 | 365311.129 |  | 21.68% | 96.03% | 99.5% | 0 |  |  |  |  | 2.239% | 0% | 5% | 5% | 70.2
2024-10-05 | 2025 | 2024 | 2024-10-01 | 31 | [7 empty] | 4.4072 | 0 | 96.3% | 98.14% | 98.13% | 100% |  |  |  |  | 11.83% | 205753 | 199800 | 450 | 199350 | 59.4 | 9.21 | 365311.129 |  | 21.68% | 96.03% | 99.5% | 0 |  |  |  |  | 2.893% | 0% | 5% | 5% | 70.2
2024-10-06 | 2025 | 2024 | 2024-10-01 | 31 | [7 empty] | 3.8574 | 0 | 96.88% | 99.62% | 97.24% | 100% |  |  |  |  | 4.808% | 86684 | 81900 | 900 | 81000 | 59.4 | 9.21 | 365311.129 |  | 21.68% | 96.03% | 99.5% | 0 |  |  |  |  | 5.519% | 0% | 5% | 5% | 70.2
2024-10-07 | 2025 | 2024 | 2024-10-01 | 31 | [7 empty] | 5.1132 | 0 | 94.71% | 98.26% | 96.38% | 100% |  |  |  |  | 16.93% | 293022 | 285300 | 0 | 285300 | 59.4 | 9.21 | 365311.129 |  | 21.68% | 96.03% | 99.5% | 0 |  |  |  |  | 2.635% | 0% | 5% | 5% | 70.2
2024-10-08 | 2025 | 2024 | 2024-10-01 | 31 | [7 empty] | 4.3635 | 0 | 96.64% | 97.33% | 99.3% | 100% |  |  |  |  | 10.26% | 178678 | 172800 | 0 | 172800 | 59.4 | 9.21 | 365311.129 |  | 21.68% | 96.03% | 99.5% | 0 |  |  |  |  | 3.29% | 0% | 5% | 5% | 70.2
2024-10-09 | 2025 | 2024 | 2024-10-01 | 31 | [7 empty] | 4.1867 | 0 | 91.47% | 97.78% | 93.55% | 100% |  |  |  |  | 7.051% | 120892 | 118800 | 0 | 118800 | 59.4 | 9.21 | 365311.129 |  | 21.68% | 96.03% | 99.5% | 0 |  |  |  |  | 1.73% | 0% | 5% | 5% | 70.2
2024-10-10 | 2025 | 2024 | 2024-10-01 | 31 | [7 empty] | 5.3502 | 0 | 97.36% | 97.36% | 100% | 100% |  |  |  |  | 19.2% | 333856 | 324000 | 450 | 323550 | 59.4 | 9.21 | 365311.129 |  | 21.68% | 96.03% | 99.5% | 0 |  |  |  |  | 2.952% | 0% | 5% | 5% | 70.2
2024-10-11 | 2025 | 2024 | 2024-10-01 | 31 | [7 empty] | 6.446 | 0 | 96.55% | 97.52% | 99.01% | 100% |  |  |  |  | 32.16% | 556797 | 541800 | 0 | 541800 | 59.4 | 9.21 | 365311.129 |  | 21.68% | 96.03% | 99.5% | 0 |  |  |  |  | 2.693% | 0% | 5% | 5% | 70.2
2024-10-12 | 2025 | 2024 | 2024-10-01 | 31 | [7 empty] | 5.0784 | 0 | 97.14% | 97.9% | 99.22% | 100% |  |  |  |  | 17.47% | 300875 | 294300 | 0 | 294300 | 59.4 | 9.21 | 365311.129 |  | 21.68% | 96.03% | 99.5% | 0 |  |  |  |  | 2.185% | 0% | 5% | 5% | 70.2
2024-10-13 | 2025 | 2024 | 2024-10-01 | 31 | [7 empty] | 3.9075 | 0 | 96.15% | 96.82% | 99.3% | 100% |  |  |  |  | 7.505% | 132111 | 126900 | 450 | 126450 | 59.4 | 9.21 | 365311.129 |  | 21.68% | 96.03% | 99.5% | 0 |  |  |  |  | 3.944% | 0% | 5% | 5% | 70.2
2024-10-14 | 2025 | 2024 | 2024-10-01 | 31 | [7 empty] | 3.7662 | 0 | 97.36% | 97.36% | 100% | 100% |  |  |  |  | 8.093% | 142579 | 136800 | 450 | 136350 | 59.4 | 9.21 | 365311.129 |  | 21.68% | 96.03% | 99.5% | 0 |  |  |  |  | 4.053% | 0% | 5% | 5% | 70.2
2024-10-15 | 2025 | 2024 | 2024-10-01 | 31 | [7 empty] | 3.2575 | 0 | 98.36% | 99.1% | 99.25% | 70.07% |  |  |  |  | 2.217% | 40256 | 38700 | 1350 | 37350 | 59.4 | 9.21 | 365311.129 |  | 21.68% | 96.03% | 99.5% | 0 |  |  |  |  | 3.865% | 0% | 5% | 5% | 70.2
2024-10-16 | 2025 | 2024 | 2024-10-01 | 31 | [7 empty] | 4.1483 | 0 | 80.43% | 93.49% | 86.02% | 100% |  |  |  |  | 7.639% | 134361 | 129150 | 450 | 128700 | 62.1 | 9.21 | 365311.129 |  | 21.68% | 96.03% | 99.5% | 0 |  |  |  |  | 3.878% | 0% | 5% | 5% | 70.2
2024-10-17 | 2025 | 2024 | 2024-10-01 | 31 | [7 empty] | 3.8526 | 0 | 92.91% | 97.94% | 94.86% | 100% |  |  |  |  | 7.532% | 131337 | 126900 | 0 | 126900 | 62.1 | 9.21 | 365311.129 |  | 21.68% | 96.03% | 99.5% | 0 |  |  |  |  | 3.378% | 0% | 5% | 5% | 70.2
2024-10-18 | 2025 | 2024 | 2024-10-01 | 31 | [7 empty] | 4.0239 | 0 | 81.62% | 97.41% | 83.79% | 100% |  |  |  |  | 6.757% | 115916 | 114300 | 450 | 113850 | 62.1 | 9.21 | 365311.129 |  | 21.68% | 96.03% | 99.5% | 0 |  |  |  |  | 1.394% | 0% | 5% | 5% | 70.2
2024-10-19 | 2025 | 2024 | 2024-10-01 | 31 | [7 empty] | 3.9551 | 0 | 85.6% | 97.88% | 87.46% | 100% |  |  |  |  | 8.814% | 155516 | 149400 | 900 | 148500 | 62.1 | 9.21 | 365311.129 |  | 21.68% | 96.03% | 99.5% | 0 |  |  |  |  | 3.933% | 0% | 5% | 5% | 70.2
2024-10-20 | 2025 | 2024 | 2024-10-01 | 31 | [7 empty] | 2.9019 | 0 | 99.45% | 99.45% | 100% | 100% |  |  |  |  | 4.229% | 80880 | 74400 | 3150 | 71250 | 62.1 | 9.21 | 365311.129 |  | 21.68% | 96.03% | 99.5% | 0 |  |  |  |  | 8.012% | 0% | 5% | 5% | 70.2
2024-10-21 | 2025 | 2024 | 2024-10-01 | 31 | [7 empty] | 3.3425 | 0 | 93.06% | 98.32% | 94.66% | 100% |  |  |  |  | 4.033% | 73108 | 69300 | 1350 | 67950 | 64.8 | 9.21 | 365311.129 |  | 21.68% | 96.03% | 99.5% | 0 |  |  |  |  | 5.209% | 0% | 5% | 5% | 70.2
2024-10-22 | 2025 | 2024 | 2024-10-01 | 31 | [7 empty] | 3.3579 | 0 | 95.55% | 95.55% | 100% | 100% |  |  |  |  | 3.713% | 67977 | 63000 | 450 | 62550 | 64.8 | 9.21 | 365311.129 |  | 21.68% | 96.03% | 99.5% | 0 |  |  |  |  | 7.322% | 0% | 5% | 5% | 70.2
2024-10-23 | 2025 | 2024 | 2024-10-01 | 31 | [7 empty] | 4.2379 | 0 | 98.03% | 98.03% | 100% | 100% |  |  |  |  | 9.802% | 170926 | 165150 | 0 | 165150 | 64.8 | 9.21 | 365311.129 |  | 21.68% | 96.03% | 99.5% | 0 |  |  |  |  | 3.379% | 0% | 5% | 5% | 70.2
2024-10-24 | 2025 | 2024 | 2024-10-01 | 31 | [7 empty] | 4.3338 | 0 | 93.48% | 96.77% | 96.59% | 100% |  |  |  |  | 12.71% | 219140 | 214200 | 0 | 214200 | 64.8 | 9.21 | 365311.129 |  | 21.68% | 96.03% | 99.5% | 0 |  |  |  |  | 2.254% | 0% | 5% | 5% | 70.2
2024-10-25 | 2025 | 2024 | 2024-10-01 | 31 | [7 empty] | 4.2488 | 0 | 94.71% | 96.49% | 98.15% | 100% |  |  |  |  | 12.23% | 212770 | 206100 | 0 | 206100 | 64.8 | 9.21 | 365311.129 |  | 21.68% | 96.03% | 99.5% | 0 |  |  |  |  | 3.135% | 0% | 5% | 5% | 70.2
2024-10-26 | 2025 | 2024 | 2024-10-01 | 31 | [7 empty] | 2.6054 | 0 | 91.29% | 91.29% | 100% | 100% |  |  |  |  | 1.015% | 19740 | 17550 | 450 | 17100 | 64.8 | 9.21 | 365311.129 |  | 21.68% | 96.03% | 99.5% | 0 |  |  |  |  | 11.09% | 0% | 5% | 5% | 70.2
2024-10-27 | 2025 | 2024 | 2024-10-01 | 31 | [7 empty] | 3.9896 | 0 | 91.47% | 92.13% | 99.29% | 100% |  |  |  |  | 8.387% | 150280 | 144000 | 2700 | 141300 | 64.8 | 9.21 | 365311.129 |  | 21.68% | 96.03% | 99.5% | 0 |  |  |  |  | 4.179% | 0% | 5% | 5% | 70.2
2024-10-28 | 2025 | 2024 | 2024-10-01 | 31 | [7 empty] | 4.4627 | 0 | 96.64% | 98.36% | 98.26% | 100% |  |  |  |  | 14.82% | 245837 | 250650 | 900 | 249750 | 64.8 | 9.21 | 365311.129 |  | 21.68% | 96.03% | 99.5% | 0 |  |  |  |  | -1.958% | 0% | 5% | 5% | 70.2
2024-10-29 | 2025 | 2024 | 2024-10-01 | 31 | [7 empty] | 3.9516 | 0 | 98.8% | 98.8% | 100% | 100% |  |  |  |  | 10.76% | 189131 | 181350 | 0 | 181350 | 67.5 | 9.21 | 365311.129 |  | 21.68% | 96.03% | 99.5% | 0 |  |  |  |  | 4.114% | 0% | 5% | 5% | 70.2
2024-10-30 | 2025 | 2024 | 2024-10-01 | 31 | [7 empty] | 3.8559 | 0 | 99.97% | 99.97% | 100% | 100% |  |  |  |  | 7.505% | 131465 | 126900 | 450 | 126450 | 67.5 | 9.21 | 365311.129 |  | 21.68% | 96.03% | 99.5% | 0 |  |  |  |  | 3.472% | 0% | 5% | 5% | 70.2
2024-10-31 | 2025 | 2024 | 2024-10-01 | 31 | [7 empty] | 4.7055 | 0 | 99.78% | 99.78% | 100% | 100% |  |  |  |  | 16.53% | 286079 | 278550 | 0 | 278550 | 67.5 | 9.21 | 365311.129 |  | 21.68% | 96.03% | 99.5% | 0 |  |  |  |  | 2.632% | 0% | 5% | 5% | 70.2
2024-11-01 | 2025 | 2024 | 2024-11-01 | 30 | [7 empty] | 3.6521 | 0 | 99.4% | 99.4% | 100% | 100% |  |  |  |  | 8.574% | 151105 | 145800 | 1350 | 144450 | 67.5 | 8.33 | 407713.3 |  | 24.2% | 96.03% | 99.5% | 0 |  |  |  |  | 3.511% | 0% | 5% | 5% | 70.2
2024-11-02 | 2025 | 2024 | 2024-11-01 | 30 | [7 empty] | 2.6407 | 0 | 99.86% | 99.86% | 100% | 100% |  |  |  |  | 1.976% | 38455 | 35100 | 1800 | 33300 | 67.5 | 8.33 | 407713.3 |  | 24.2% | 96.03% | 99.5% | 0 |  |  |  |  | 8.724% | 0% | 5% | 5% | 70.2
2024-11-03 | 2025 | 2024 | 2024-11-01 | 30 | [7 empty] | 2.7584 | 0 | 99.5% | 99.5% | 100% | 100% |  |  |  |  | 2.457% | 46880 | 43650 | 2250 | 41400 | 67.5 | 8.33 | 407713.3 |  | 24.2% | 96.03% | 99.5% | 0 |  |  |  |  | 6.89% | 0% | 5% | 5% | 70.2
2024-11-04 | 2025 | 2024 | 2024-11-01 | 30 | [7 empty] | 2.9951 | 0 | 99.77% | 99.77% | 100% | 100% |  |  |  |  | 1.95% | 38526 | 34200 | 1350 | 32850 | 67.5 | 8.33 | 407713.3 |  | 24.2% | 96.03% | 99.5% | 0 |  |  |  |  | 11.23% | 0% | 5% | 5% | 70.2
2024-11-05 | 2025 | 2024 | 2024-11-01 | 30 | [7 empty] | 4.5305 | 0 | 98.6% | 98.6% | 100% | 100% |  |  |  |  | 11.81% | 205166 | 198900 | 0 | 198900 | 67.5 | 8.33 | 407713.3 |  | 24.2% | 96.03% | 99.5% | 0 |  |  |  |  | 3.054% | 0% | 5% | 5% | 70.2
2024-11-06 | 2025 | 2024 | 2024-11-01 | 30 | [7 empty] | 4.8262 | 0 | 97.63% | 97.63% | 100% | 100% |  |  |  |  | 15.38% | 261066 | 259200 | 0 | 259200 | 67.5 | 8.33 | 407713.3 |  | 24.2% | 96.03% | 99.5% | 0 |  |  |  |  | 0.7148% | 0% | 5% | 5% | 70.2
2024-11-07 | 2025 | 2024 | 2024-11-01 | 30 | [7 empty] | 4.4204 | 0 | 96.5% | 97.13% | 99.35% | 100% |  |  |  |  | 14.58% | 253956 | 245700 | 0 | 245700 | 67.5 | 8.33 | 407713.3 |  | 24.2% | 96.03% | 99.5% | 0 |  |  |  |  | 3.251% | 0% | 5% | 5% | 70.2
2024-11-08 | 2025 | 2024 | 2024-11-01 | 30 | [7 empty] | 3.3928 | 0 | 97.69% | 98.12% | 99.56% | 100% |  |  |  |  | 3.659% | 67549 | 62550 | 900 | 61650 | 67.5 | 8.33 | 407713.3 |  | 24.2% | 96.03% | 99.5% | 0 |  |  |  |  | 7.401% | 0% | 5% | 5% | 70.2
2024-11-09 | 2025 | 2024 | 2024-11-01 | 30 | [7 empty] | 4.6271 | 0 | 94.2% | 95.17% | 98.98% | 100% |  |  |  |  | 14.05% | 243525 | 236700 | 0 | 236700 | 67.5 | 8.33 | 407713.3 |  | 24.2% | 96.03% | 99.5% | 0 |  |  |  |  | 2.803% | 0% | 5% | 5% | 70.2
2024-11-10 | 2025 | 2024 | 2024-11-01 | 30 | [7 empty] | 3.4859 | 0 | 99.68% | 99.68% | 100% | 100% |  |  |  |  | 5.475% | 98475 | 93600 | 1359 | 92241 | 67.5 | 8.33 | 407713.3 |  | 24.2% | 96.03% | 99.5% | 0 |  |  |  |  | 4.95% | 0% | 5% | 5% | 70.2
2024-11-11 | 2025 | 2024 | 2024-11-01 | 30 | [7 empty] | 3.9251 | 0 | 98.96% | 98.96% | 100% | 100% |  |  |  |  | 7.265% | 128058 | 122400 | 0 | 122400 | 67.5 | 8.33 | 407713.3 |  | 24.2% | 96.03% | 99.5% | 0 |  |  |  |  | 4.418% | 0% | 5% | 5% | 70.2
2024-11-12 | 2025 | 2024 | 2024-11-01 | 30 | [7 empty] | 4.0521 | 0 | 99.44% | 99.44% | 100% | 100% |  |  |  |  | 8.12% | 142562 | 136800 | 0 | 136800 | 67.5 | 8.33 | 407713.3 |  | 24.2% | 96.03% | 99.5% | 0 |  |  |  |  | 4.042% | 0% | 5% | 5% | 70.2
2024-11-13 | 2025 | 2024 | 2024-11-01 | 30 | [7 empty] | 4.3179 | 0 | 99.03% | 99.03% | 100% | 100% |  |  |  |  | 10.18% | 177493 | 171450 | 0 | 171450 | 67.5 | 8.33 | 407713.3 |  | 24.2% | 96.03% | 99.5% | 0 |  |  |  |  | 3.405% | 0% | 5% | 5% | 70.2
2024-11-14 | 2025 | 2024 | 2024-11-01 | 30 | [7 empty] | 4.7019 | 0 | 98.76% | 98.76% | 100% | 100% |  |  |  |  | 15.3% | 264535 | 257850 | 0 | 257850 | 67.5 | 8.33 | 407713.3 |  | 24.2% | 96.03% | 99.5% | 0 |  |  |  |  | 2.527% | 0% | 5% | 5% | 70.2
2024-11-15 | 2025 | 2024 | 2024-11-01 | 30 | [7 empty] | 3.2648 | 0 | 97.13% | 97.13% | 100% | 100% |  |  |  |  | 5.315% | 95549 | 91350 | 1800 | 89550 | 67.5 | 8.33 | 407713.3 |  | 24.2% | 96.03% | 99.5% | 0 |  |  |  |  | 4.395% | 0% | 5% | 5% | 70.2
2024-11-16 | 2025 | 2024 | 2024-11-01 | 30 | [7 empty] | 3.2737 | 0 | 98.73% | 98.73% | 100% | 100% |  |  |  |  | 4.14% | 75489 | 71550 | 1800 | 69750 | 67.5 | 8.33 | 407713.3 |  | 24.2% | 96.03% | 99.5% | 0 |  |  |  |  | 5.218% | 0% | 5% | 5% | 70.2
2024-11-17 | 2025 | 2024 | 2024-11-01 | 30 | [7 empty] | 4.9701 | 0 | 96.91% | 96.91% | 100% | 100% |  |  |  |  | 16% | 276591 | 269550 | 0 | 269550 | 67.5 | 8.33 | 407713.3 |  | 24.2% | 96.03% | 99.5% | 0 |  |  |  |  | 2.546% | 0% | 5% | 5% | 70.2
2024-11-18 | 2025 | 2024 | 2024-11-01 | 30 | [7 empty] | 5.3242 | 0 | 97.31% | 97.31% | 100% | 100% |  |  |  |  | 18.72% | 322237 | 315450 | 0 | 315450 | 67.5 | 8.33 | 407713.3 |  | 24.2% | 96.03% | 99.5% | 0 |  |  |  |  | 2.106% | 0% | 5% | 5% | 70.2
2024-11-19 | 2025 | 2024 | 2024-11-01 | 30 | [7 empty] | 5.0121 | 0 | 98.01% | 98.27% | 99.74% | 100% |  |  |  |  | 16.27% | 281343 | 274050 | 0 | 274050 | 67.5 | 8.33 | 407713.3 |  | 24.2% | 96.03% | 99.5% | 0 |  |  |  |  | 2.592% | 0% | 5% | 5% | 70.2
2024-11-20 | 2025 | 2024 | 2024-11-01 | 30 | [7 empty] | 4.707 | 0 | 99.25% | 99.25% | 100% | 100% |  |  |  |  | 13.78% | 238886 | 232200 | 0 | 232200 | 67.5 | 8.33 | 407713.3 |  | 24.2% | 96.03% | 99.5% | 0 |  |  |  |  | 2.799% | 0% | 5% | 5% | 70.2
2024-11-21 | 2025 | 2024 | 2024-11-01 | 30 | [7 empty] | 4.6063 | 0 | 97.67% | 97.67% | 100% | 100% |  |  |  |  | 12.77% | 220846 | 215100 | 0 | 215100 | 67.5 | 8.33 | 407713.3 |  | 24.2% | 96.03% | 99.5% | 0 |  |  |  |  | 2.602% | 0% | 5% | 5% | 70.2
2024-11-22 | 2025 | 2024 | 2024-11-01 | 30 | [7 empty] | 4.3547 | 0 | 97.76% | 97.76% | 100% | 100% |  |  |  |  | 10.92% | 189705 | 184050 | 0 | 184050 | 67.5 | 8.33 | 407713.3 |  | 24.2% | 96.03% | 99.5% | 0 |  |  |  |  | 2.981% | 0% | 5% | 5% | 70.2
2024-11-23 | 2025 | 2024 | 2024-11-01 | 30 | [7 empty] | 3.3959 | 0 | 99.23% | 99.23% | 100% | 100% |  |  |  |  | 5.342% | 94369 | 90000 | 0 | 90000 | 67.5 | 8.33 | 407713.3 |  | 24.2% | 96.03% | 99.5% | 0 |  |  |  |  | 4.63% | 0% | 5% | 5% | 70.2
2024-11-24 | 2025 | 2024 | 2024-11-01 | 30 | [7 empty] | 3.7985 | 0 | 88.25% | 97.93% | 90.12% | 100% |  |  |  |  | 5.689% | 99822 | 95850 | 0 | 95850 | 67.5 | 8.33 | 407713.3 |  | 24.2% | 96.03% | 99.5% | 0 |  |  |  |  | 3.979% | 0% | 5% | 5% | 70.2
2024-11-25 | 2025 | 2024 | 2024-11-01 | 30 | [7 empty] | 5.926 | 0 | 86.11% | 97.17% | 88.62% | 100% |  |  |  |  | 21.87% | 378775 | 368550 | 0 | 368550 | 67.5 | 8.33 | 407713.3 |  | 24.2% | 96.03% | 99.5% | 0 |  |  |  |  | 2.699% | 0% | 5% | 5% | 70.2
2024-11-26 | 2025 | 2024 | 2024-11-01 | 30 | [7 empty] | 5.9866 | 0 | 99.64% | 99.64% | 100% | 100% |  |  |  |  | 27.24% | 467347 | 459000 | 0 | 459000 | 67.5 | 8.33 | 407713.3 |  | 24.2% | 96.03% | 99.5% | 0 |  |  |  |  | 1.786% | 0% | 5% | 5% | 70.2
2024-11-27 | 2025 | 2024 | 2024-11-01 | 30 | [7 empty] | 5.4726 | 0 | 98.9% | 98.9% | 100% | 100% |  |  |  |  | 20.43% | 352915 | 344250 | 0 | 344250 | 67.5 | 8.33 | 407713.3 |  | 24.2% | 96.03% | 99.5% | 0 |  |  |  |  | 2.455% | 0% | 5% | 5% | 70.2
2024-11-28 | 2025 | 2024 | 2024-11-01 | 30 | [7 empty] | 5.3437 | 0 | 97.48% | 97.74% | 99.73% | 100% |  |  |  |  | 17.28% | 297983 | 291150 | 0 | 291150 | 67.5 | 8.33 | 407713.3 |  | 24.2% | 96.03% | 99.5% | 0 |  |  |  |  | 2.293% | 0% | 5% | 5% | 70.2
2024-11-29 | 2025 | 2024 | 2024-11-01 | 30 | [7 empty] | 6.4734 | 0 | 97.83% | 98.4% | 99.43% | 100% |  |  |  |  | 30.48% | 526391 | 513450 | 0 | 513450 | 67.5 | 8.33 | 407713.3 |  | 24.2% | 96.03% | 99.5% | 0 |  |  |  |  | 2.458% | 0% | 5% | 5% | 70.2
2024-11-30 | 2025 | 2024 | 2024-11-01 | 30 | [7 empty] | 7.3972 | 0 | 96.97% | 97.56% | 99.39% | 100% |  |  |  |  | 44.15% | 764589 | 743850 | 0 | 743850 | 67.5 | 8.33 | 407713.3 |  | 24.2% | 96.03% | 99.5% | 0 |  |  |  |  | 2.712% | 0% | 5% | 5% | 70.2
2024-12-01 | 2025 | 2024 | 2024-12-01 | 31 | [7 empty] | 7.15 | 0 | 97.55% | 98.75% | 98.78% | 100% |  |  |  |  | 39.26% | 680102 | 661500 | 0 | 661500 | 67.5 | 6.95 | 577322.0323 |  | 34.27% | 96.03% | 99.5% | 28.36 |  |  |  |  | 2.735% | 0% | 5% | 5% | 70.2
2024-12-02 | 2025 | 2024 | 2024-12-01 | 31 | [7 empty] | 7.1004 | 0 | 94.09% | 98.14% | 95.87% | 100% |  |  |  |  | 40.2% | 697846 | 677250 | 0 | 677250 | 67.5 | 6.95 | 577322.0323 |  | 34.27% | 96.03% | 99.5% | 29.083 |  |  |  |  | 2.951% | 0% | 5% | 5% | 70.2
2024-12-03 | 2025 | 2024 | 2024-12-01 | 31 | [7 empty] | 6.8623 | 0 | 96.3% | 97.25% | 99.03% | 100% |  |  |  |  | 37.18% | 648461 | 626400 | 0 | 626400 | 67.5 | 6.95 | 577322.0323 |  | 34.27% | 96.03% | 99.5% | 26.869 |  |  |  |  | 3.402% | 0% | 5% | 5% | 70.2
2024-12-04 | 2025 | 2024 | 2024-12-01 | 31 | [7 empty] | 8.4966 | 0 | 84.44% | 96.53% | 87.47% | 100% |  |  |  |  | 51.82% | 900414 | 873000 | 0 | 873000 | 67.5 | 6.95 | 577322.0323 |  | 34.27% | 96.03% | 99.5% | 37.613 |  |  |  |  | 3.045% | 0% | 5% | 5% | 70.2
2024-12-05 | 2025 | 2024 | 2024-12-01 | 31 | [7 empty] | 6.698 | 0 | 97.95% | 98.69% | 99.25% | 100% |  |  |  |  | 36.94% | 636052 | 622350 | 0 | 622350 | 67.5 | 6.95 | 577322.0323 |  | 34.27% | 96.03% | 99.5% | 26.685 |  |  |  |  | 2.154% | 0% | 5% | 5% | 70.2
2024-12-06 | 2025 | 2024 | 2024-12-01 | 31 | [7 empty] | 5.8269 | 0 | 98.68% | 98.68% | 100% | 100% |  |  |  |  | 29.59% | 509896 | 498600 | 0 | 498600 | 67.5 | 6.95 | 577322.0323 |  | 34.27% | 96.03% | 99.5% | 20.309 |  |  |  |  | 2.215% | 0% | 5% | 5% | 70.2
2024-12-07 | 2025 | 2024 | 2024-12-01 | 31 | [7 empty] | 3.9838 | 0 | 88.7% | 98.67% | 89.9% | 100% |  |  |  |  | 6.517% | 115306 | 110250 | 450 | 109800 | 67.5 | 6.95 | 577322.0323 |  | 34.27% | 96.03% | 99.5% | 4.436 |  |  |  |  | 4.385% | 0% | 5% | 5% | 70.2
2024-12-08 | 2025 | 2024 | 2024-12-01 | 31 | [7 empty] | 5.3829 | 0 | 92.32% | 95.17% | 97.01% | 100% |  |  |  |  | 16.99% | 311771 | 286200 | 0 | 286200 | 67.5 | 6.95 | 577322.0323 |  | 34.27% | 96.03% | 99.5% | 12.214 |  |  |  |  | 8.202% | 0% | 5% | 5% | 70.2
2024-12-09 | 2025 | 2024 | 2024-12-01 | 31 | [7 empty] | 8.4911 | 0 | 90.29% | 93.83% | 96.23% | 100% |  |  |  |  | 53.12% | 926126 | 895050 | 0 | 895050 | 67.5 | 6.95 | 577322.0323 |  | 34.27% | 96.03% | 99.5% | 30.03 |  |  |  |  | 3.355% | 0% | 5% | 5% | 70.2
2024-12-10 | 2025 | 2024 | 2024-12-01 | 31 | [7 empty] | 8.6859 | 0 | 94.11% | 94.11% | 100% | 100% |  |  |  |  | 59.96% | 1040749 | 1010250 | 0 | 1010250 | 67.5 | 6.95 | 577322.0323 |  | 34.27% | 96.03% | 99.5% | 22.761 |  |  |  |  | 2.93% | 0% | 5% | 5% | 70.2
2024-12-11 | 2025 | 2024 | 2024-12-01 | 31 | [7 empty] | 7.3315 | 0 | 88.04% | 91.43% | 96.29% | 100% |  |  |  |  | 37.74% | 648139 | 635850 | 0 | 635850 | 67.5 | 6.95 | 577322.0323 |  | 34.27% | 96.03% | 99.5% | 27.222 |  |  |  |  | 1.896% | 0% | 5% | 5% | 70.2
2024-12-12 | 2025 | 2024 | 2024-12-01 | 31 | [7 empty] | 7.6369 | 0 | 80.9% | 93.36% | 86.65% | 100% |  |  |  |  | 36.67% | 638237 | 617850 | 0.04 | 617849.96 | 67.5 | 6.95 | 577322.0323 |  | 34.27% | 96.03% | 99.5% | 26.361 |  |  |  |  | 3.194% | 0% | 5% | 5% | 70.2
2024-12-13 | 2025 | 2024 | 2024-12-01 | 31 | [7 empty] | 9.5191 | 0 | 91.92% | 92.95% | 98.89% | 100% |  |  |  |  | 63.73% | 1117772 | 1073700 | 0 | 1073700 | 67.5 | 6.95 | 577322.0323 |  | 34.27% | 96.03% | 99.5% | 46.439 |  |  |  |  | 3.943% | 0% | 5% | 5% | 70.2
2024-12-14 | 2025 | 2024 | 2024-12-01 | 31 | [7 empty] | 8.1793 | 0 | 80.88% | 93.85% | 86.18% | 100% |  |  |  |  | 48.16% | 824741 | 811350 | 0 | 811350 | 67.5 | 6.95 | 577322.0323 |  | 34.27% | 96.03% | 99.5% | 35.063 |  |  |  |  | 1.624% | 0% | 5% | 5% | 70.2
2024-12-15 | 2025 | 2024 | 2024-12-01 | 31 | [7 empty] | 5.5883 | 0 | 90.89% | 91.55% | 99.27% | 100% |  |  |  |  | 26.79% | 451562 | 451350 | 0 | 451350 | 67.5 | 6.95 | 577322.0323 |  | 34.27% | 96.03% | 99.5% | 19.66 |  |  |  |  | 0.04695% | 0% | 5% | 5% | 70.2
2024-12-16 | 2025 | 2024 | 2024-12-01 | 31 | [7 empty] | 4.5303 | 0 | 92.21% | 93.53% | 98.59% | 100% |  |  |  |  | 15.38% | 258372 | 260100 | 900 | 259200 | 67.5 | 6.95 | 577322.0323 |  | 34.27% | 96.03% | 99.5% | 11.128 |  |  |  |  | -0.6688% | 0% | 5% | 5% | 70.2
2024-12-17 | 2025 | 2024 | 2024-12-01 | 31 | [7 empty] | 5.4163 | 0 | 90.68% | 93.52% | 96.97% | 100% |  |  |  |  | 20.94% | 362128 | 352800 | 0 | 352800 | 67.5 | 6.95 | 577322.0323 |  | 34.27% | 96.03% | 99.5% | 15.026 |  |  |  |  | 2.576% | 0% | 5% | 5% | 70.2
2024-12-18 | 2025 | 2024 | 2024-12-01 | 31 | [7 empty] | 4.1807 | 0 | 93.01% | 93.3% | 99.69% | 100% |  |  |  |  | 15.28% | 263761 | 258750 | 1350 | 257400 | 70.2 | 6.95 | 577322.0323 |  | 34.27% | 96.03% | 99.5% | 10.666 |  |  |  |  | 1.9% | 0% | 5% | 5% | 70.2
2024-12-19 | 2025 | 2024 | 2024-12-01 | 31 | [7 empty] | 4.2757 | 0 | 84.83% | 85.23% | 99.53% | 100% |  |  |  |  | 10.04% | 176735 | 170550 | 1350 | 169200 | 70.2 | 6.95 | 577322.0323 |  | 34.27% | 96.03% | 99.5% | 4.73 |  |  |  |  | 3.5% | 0% | 5% | 5% | 70.2
2024-12-20 | 2025 | 2024 | 2024-12-01 | 31 | [7 empty] | 7.0349 | 0 | 85.98% | 92.46% | 93% | 100% |  |  |  |  | 35.15% | 607755 | 592200 | 0 | 592200 | 70.2 | 6.95 | 577322.0323 |  | 34.27% | 96.03% | 99.5% | 21.102 |  |  |  |  | 2.559% | 0% | 5% | 5% | 70.2
2024-12-21 | 2025 | 2024 | 2024-12-01 | 31 | [7 empty] | 4.2016 | 0 | 80.58% | 94.2% | 85.54% | 100% |  |  |  |  | 9.001% | 156534 | 152100 | 450 | 151650 | 70.2 | 6.95 | 577322.0323 |  | 34.27% | 96.03% | 99.5% | 6.076 |  |  |  |  | 2.833% | 0% | 5% | 5% | 70.2
2024-12-22 | 2025 | 2024 | 2024-12-01 | 31 | [7 empty] | 4.4623 | 0 | 89.5% | 96.19% | 93.04% | 100% |  |  |  |  | 9.615% | 167298 | 162000 | 0 | 162000 | 70.2 | 6.95 | 577322.0323 |  | 34.27% | 96.03% | 99.5% | 4.885 |  |  |  |  | 3.167% | 0% | 5% | 5% | 70.2
2024-12-23 | 2025 | 2024 | 2024-12-01 | 31 | [7 empty] | 5.2067 | 0 | 79.95% | 94.27% | 84.82% | 100% |  |  |  |  | 12.85% | 222779 | 216450 | 0 | 216450 | 70.2 | 6.95 | 577322.0323 |  | 34.27% | 96.03% | 99.5% | 0 |  |  |  |  | 2.841% | 0% | 5% | 5% | 70.2
2024-12-24 | 2025 | 2024 | 2024-12-01 | 31 | [7 empty] | 6.5481 | 0 | 90.88% | 91.18% | 99.67% | 100% |  |  |  |  | 30.34% | 526577 | 511200 | 0 | 511200 | 70.2 | 6.95 | 577322.0323 |  | 34.27% | 96.03% | 99.5% | 0 |  |  |  |  | 2.92% | 0% | 5% | 5% | 70.2
2024-12-25 | 2025 | 2024 | 2024-12-01 | 31 | [7 empty] | 6.442 | 0 | 78.67% | 93.01% | 84.58% | 100% |  |  |  |  | 26.98% | 467783 | 454500 | 0 | 454500 | 70.2 | 6.95 | 577322.0323 |  | 34.27% | 96.03% | 99.5% | 0 |  |  |  |  | 2.84% | 0% | 5% | 5% | 70.2
2024-12-26 | 2025 | 2024 | 2024-12-01 | 31 | [7 empty] | 5.0484 | 0 | 84.91% | 90.81% | 93.5% | 100% |  |  |  |  | 19.58% | 336105 | 331200 | 1350 | 329850 | 70.2 | 6.95 | 577322.0323 |  | 34.27% | 96.03% | 99.5% | 0 |  |  |  |  | 1.459% | 0% | 5% | 5% | 70.2
2024-12-27 | 2025 | 2024 | 2024-12-01 | 31 | [7 empty] | 5.8397 | 0 | 80.23% | 92.16% | 87.05% | 100% |  |  |  |  | 19.07% | 330708 | 321750 | 450 | 321300 | 70.2 | 6.95 | 577322.0323 |  | 34.27% | 96.03% | 99.5% | 0 |  |  |  |  | 2.709% | 0% | 5% | 5% | 70.2
2024-12-28 | 2025 | 2024 | 2024-12-01 | 31 | [7 empty] | 6.9508 | 0 | 86.53% | 94.8% | 91.28% | 100% |  |  |  |  | 30.93% | 538183 | 521100 | 0 | 521100 | 70.2 | 6.95 | 577322.0323 |  | 34.27% | 96.03% | 99.5% | 0 |  |  |  |  | 3.174% | 0% | 5% | 5% | 70.2
2024-12-29 | 2025 | 2024 | 2024-12-01 | 31 | [7 empty] | 6.5333 | 0 | 90.28% | 94.64% | 95.39% | 100% |  |  |  |  | 29.57% | 510812 | 498150 | 0 | 498150 | 70.2 | 6.95 | 577322.0323 |  | 34.27% | 96.03% | 99.5% | 0 |  |  |  |  | 2.479% | 0% | 5% | 5% | 70.2
2024-12-30 | 2025 | 2024 | 2024-12-01 | 31 | [7 empty] | 5.8585 | 0 | 93.13% | 97.9% | 95.13% | 100% |  |  |  |  | 27.38% | 473068 | 461250 | 0 | 461250 | 70.2 | 6.95 | 577322.0323 |  | 34.27% | 96.03% | 99.5% | 0 |  |  |  |  | 2.498% | 0% | 5% | 5% | 70.2
2024-12-31 | 2025 | 2024 | 2024-12-01 | 31 | [7 empty] | 5.1981 | 0 | 70.92% | 98.08% | 72.31% | 100% |  |  |  |  | 14.45% | 246233 | 243450 | 0 | 243450 | 70.2 | 6.95 | 577322.0323 |  | 34.27% | 96.03% | 99.5% | 0 |  |  |  |  | 1.13% | 0% | 5% | 5% | 70.2
2025-01-01 | 2025 | 2025 | 2025-01-01 | 31 | [7 empty] | 5.159 | 0 | 75.87% | 98.9% | 76.71% | 100% |  |  |  |  | 15.22% | 264444 | 257850 | 1350 | 256500 | 70.2 | 5.57 | 616462.5161 |  | 36.59% | 96.03% | 99.5% | 427.96 |  |  |  |  | 2.494% | 0% | 5% | 5% | 70.2
2025-01-02 | 2025 | 2025 | 2025-01-01 | 31 | [7 empty] | 4.022 | 0 | 87.6% | 93.56% | 93.63% | 100% |  |  |  |  | 6.971% | 123492 | 118350 | 900 | 117450 | 70.2 | 5.57 | 616462.5161 |  | 36.59% | 96.03% | 99.5% | 182.71 |  |  |  |  | 4.164% | 0% | 5% | 5% | 70.2
2025-01-03 | 2025 | 2025 | 2025-01-01 | 31 | [7 empty] | 2.756 | 0 | 84.66% | 84.66% | 100% | 100% |  |  |  |  | 0.828% | 19121 | 16200 | 2250 | 13950 | 70.2 | 5.57 | 616462.5161 |  | 36.59% | 96.03% | 99.5% | 26.94 |  |  |  |  | 15.28% | 0% | 5% | 5% | 70.2
2025-01-04 | 2025 | 2025 | 2025-01-01 | 31 | [7 empty] | 3.3312 | 0 | 88.61% | 91.2% | 97.16% | 100% |  |  |  |  | 4.728% | 84895 | 81900 | 2250 | 79650 | 70.2 | 5.57 | 616462.5161 |  | 36.59% | 96.03% | 99.5% | 125.29 |  |  |  |  | 3.528% | 0% | 5% | 5% | 70.2
2025-01-05 | 2025 | 2025 | 2025-01-01 | 31 | [7 empty] | 6.5228 | 0 | 85.7% | 96.19% | 89.09% | 100% |  |  |  |  | 24.76% | 427828 | 417150 | 0 | 417150 | 70.2 | 5.57 | 616462.5161 |  | 36.59% | 96.03% | 99.5% | 695.58 |  |  |  |  | 2.496% | 0% | 5% | 5% | 70.2
2025-01-06 | 2025 | 2025 | 2025-01-01 | 31 | [7 empty] | 8.272 | 0 | 73.52% | 97.13% | 75.69% | 100% |  |  |  |  | 40.2% | 687281 | 677250 | 0 | 677250 | 70.2 | 5.57 | 616462.5161 |  | 36.59% | 96.03% | 99.5% | 1184.81 |  |  |  |  | 1.46% | 0% | 5% | 5% | 70.2
2025-01-07 | 2025 | 2025 | 2025-01-01 | 31 | [7 empty] | 8.8414 | 0 | 75.73% | 96.11% | 78.8% | 100% |  |  |  |  | 48.9% | 851560 | 823950 | 0 | 823950 | 70.2 | 5.57 | 616462.5161 |  | 36.59% | 96.03% | 99.5% | 1183.83 |  |  |  |  | 3.242% | 0% | 5% | 5% | 70.2
2025-01-08 | 2025 | 2025 | 2025-01-01 | 31 | [7 empty] | 7.458 | 0 | 85.5% | 96.86% | 88.28% | 100% |  |  |  |  | 38.3% | 664966 | 645300 | 0 | 645300 | 70.2 | 5.57 | 616462.5161 |  | 36.59% | 96.03% | 99.5% | 1036.22 |  |  |  |  | 2.957% | 0% | 5% | 5% | 70.2
2025-01-09 | 2025 | 2025 | 2025-01-01 | 31 | [7 empty] | 4.9509 | 0 | 93.3% | 97.44% | 95.75% | 100% |  |  |  |  | 20.99% | 363765 | 355050 | 1350 | 353700 | 70.2 | 5.57 | 616462.5161 |  | 36.59% | 96.03% | 99.5% | 532.63 |  |  |  |  | 2.396% | 0% | 5% | 5% | 70.2
2025-01-10 | 2025 | 2025 | 2025-01-01 | 31 | [7 empty] | 4.7938 | 0 | 92.53% | 96.23% | 96.16% | 100% |  |  |  |  | 17.47% | 302612 | 295200 | 900 | 294300 | 70.2 | 5.57 | 616462.5161 |  | 36.59% | 96.03% | 99.5% | 430.5 |  |  |  |  | 2.449% | 0% | 5% | 5% | 70.2
2025-01-11 | 2025 | 2025 | 2025-01-01 | 31 | [7 empty] | 5.5457 | 0 | 91.14% | 95.58% | 95.36% | 100% |  |  |  |  | 15.54% | 269778 | 261900 | 0 | 261900 | 70.2 | 5.57 | 616462.5161 |  | 36.59% | 96.03% | 99.5% | 461.5818 |  |  |  |  | 2.92% | 0% | 5% | 5% | 70.2
2025-01-12 | 2025 | 2025 | 2025-01-01 | 31 | [7 empty] | 7.8878 | 0 | 96.63% | 98.47% | 98.14% | 100% |  |  |  |  | 42.44% | 737647 | 715050 | 0 | 715050 | 70.2 | 5.57 | 616462.5161 |  | 36.59% | 96.03% | 99.5% | 1054.22 |  |  |  |  | 3.063% | 0% | 5% | 5% | 70.2
2025-01-13 | 2025 | 2025 | 2025-01-01 | 31 | [7 empty] | 9.0294 | 0 | 93.53% | 96.15% | 97.28% | 100% |  |  |  |  | 58.31% | 1014236 | 982350 | 0 | 982350 | 70.2 | 5.57 | 616462.5161 |  | 36.59% | 96.03% | 99.5% | 1383.3742 |  |  |  |  | 3.144% | 0% | 5% | 5% | 70.2
2025-01-14 | 2025 | 2025 | 2025-01-01 | 31 | [7 empty] | 7.4956 | 0 | 97.18% | 97.32% | 99.85% | 100% |  |  |  |  | 40.22% | 696960 | 677700 | 0 | 677700 | 70.2 | 5.57 | 616462.5161 |  | 36.59% | 96.03% | 99.5% | 987.6764 |  |  |  |  | 2.763% | 0% | 5% | 5% | 70.2
2025-01-15 | 2025 | 2025 | 2025-01-01 | 31 | [7 empty] | 7.2247 | 0 | 95.92% | 95.92% | 100% | 100% |  |  |  |  | 31.57% | 546795 | 531900 | 0 | 531900 | 70.2 | 5.57 | 616462.5161 |  | 36.59% | 96.03% | 99.5% | 836.501 |  |  |  |  | 2.724% | 0% | 5% | 5% | 70.2
2025-01-16 | 2025 | 2025 | 2025-01-01 | 31 | [7 empty] | 9.3142 | 0 | 95.85% | 98.48% | 97.33% | 100% |  |  |  |  | 59.19% | 1030220 | 997200 | 0 | 997200 | 70.2 | 5.57 | 616462.5161 |  | 36.59% | 96.03% | 99.5% | 1234.5788 |  |  |  |  | 3.205% | 0% | 5% | 5% | 70.2
2025-01-17 | 2025 | 2025 | 2025-01-01 | 31 | [7 empty] | 8.2137 | 0 | 88.87% | 97.34% | 91.31% | 100% |  |  |  |  | 45.03% | 778839 | 758700 | 0 | 758700 | 70.2 | 5.57 | 616462.5161 |  | 36.59% | 96.03% | 99.5% | 1070.4026 |  |  |  |  | 2.586% | 0% | 5% | 5% | 70.2
2025-01-18 | 2025 | 2025 | 2025-01-01 | 31 | [7 empty] | 4.3087 | 0 | 97.01% | 98.93% | 98.06% | 100% |  |  |  |  | 15.92% | 273097 | 270000 | 1800 | 268200 | 70.2 | 5.57 | 616462.5161 |  | 36.59% | 96.03% | 99.5% | 365.5016 |  |  |  |  | 1.134% | 0% | 5% | 5% | 70.2
2025-01-19 | 2025 | 2025 | 2025-01-01 | 31 | [7 empty] | 3.9008 | 0 | 97.2% | 98.41% | 98.78% | 100% |  |  |  |  | 9.179% | 131456 | 156000 | 1350 | 154650 | 70.2 | 5.57 | 616462.5161 |  | 36.59% | 96.03% | 99.5% | 199.814 |  |  |  |  | -18.67% | 0% | 5% | 5% | 70.2
2025-01-20 | 2025 | 2025 | 2025-01-01 | 31 | [7 empty] | 3.386 | 0 | 93.45% | 97.03% | 96.31% | 100% |  |  |  |  | 3.072% | 56218 | 53100 | 1350 | 51750 | 70.2 | 5.57 | 616462.5161 |  | 36.59% | 96.03% | 99.5% | 87.1251 |  |  |  |  | 5.546% | 0% | 5% | 5% | 70.2
2025-01-21 | 2025 | 2025 | 2025-01-01 | 31 | [7 empty] | 4.505 | 0 | 96.35% | 96.35% | 100% | 100% |  |  |  |  | 8.387% | 146028 | 141300 | 0 | 141300 | 70.2 | 5.57 | 616462.5161 |  | 36.59% | 96.03% | 99.5% | 208.4434 |  |  |  |  | 3.238% | 0% | 5% | 5% | 70.2
2025-01-22 | 2025 | 2025 | 2025-01-01 | 31 | [7 empty] | 6.0834 | 0 | 96.27% | 96.27% | 100% | 100% |  |  |  |  | 17.74% | 305924 | 298800 | 0 | 298800 | 70.2 | 5.57 | 616462.5161 |  | 36.59% | 96.03% | 99.5% | 476.6758 |  |  |  |  | 2.329% | 0% | 5% | 5% | 70.2
2025-01-23 | 2025 | 2025 | 2025-01-01 | 31 | [7 empty] | 8.6117 | 0 | 85.89% | 99.17% | 86.61% | 100% |  |  |  |  | 44.55% | 771350 | 750600 | 0 | 750600 | 70.2 | 5.57 | 616462.5161 |  | 36.59% | 96.03% | 99.5% | 1094.2707 |  |  |  |  | 2.69% | 0% | 5% | 5% | 70.2
2025-01-24 | 2025 | 2025 | 2025-01-01 | 31 | [7 empty] | 9.5648 | 0 | 93.79% | 99.19% | 94.55% | 100% |  |  |  |  | 62.98% | 1098145 | 1061100 | 0 | 1061100 | 70.2 | 5.57 | 616462.5161 |  | 36.59% | 96.03% | 99.5% | 1433.7308 |  |  |  |  | 3.373% | 0% | 5% | 5% | 70.2
2025-01-25 | 2025 | 2025 | 2025-01-01 | 31 | [7 empty] | 7.0987 | 0 | 87.16% | 96.32% | 90.49% | 100% |  |  |  |  | 31.52% | 548720 | 531000 | 0 | 531000 | 70.2 | 5.57 | 616462.5161 |  | 36.59% | 96.03% | 99.5% | 834.5294 |  |  |  |  | 3.229% | 0% | 5% | 5% | 70.2
2025-01-26 | 2025 | 2025 | 2025-01-01 | 31 | [7 empty] | 5.2232 | 0 | 98.59% | 98.59% | 100% | 100% |  |  |  |  | 16.53% | 285933 | 278550 | 0 | 278550 | 70.2 | 5.57 | 616462.5161 |  | 36.59% | 96.03% | 99.5% | 396.8252 |  |  |  |  | 2.582% | 0% | 5% | 5% | 70.2
2025-01-27 | 2025 | 2025 | 2025-01-01 | 31 | [7 empty] | 4.0813 | 0 | 88.12% | 97.64% | 90.25% | 100% |  |  |  |  | 6.303% | 111356 | 106200 | 0 | 106200 | 70.2 | 5.57 | 616462.5161 |  | 36.59% | 96.03% | 99.5% | 175.54 |  |  |  |  | 4.63% | 0% | 5% | 5% | 70.2
2025-01-28 | 2025 | 2025 | 2025-01-01 | 31 | [7 empty] | 3.234 | 0 | 93.17% | 95.48% | 97.58% | 100% |  |  |  |  | 3.205% | 58988 | 55800 | 1800 | 54000 | 70.2 | 5.57 | 616462.5161 |  | 36.59% | 96.03% | 99.5% | 77.7525 |  |  |  |  | 5.404% | 0% | 5% | 5% | 70.2
2025-01-29 | 2025 | 2025 | 2025-01-01 | 31 | [7 empty] | 4.303 | 0 | 88.96% | 96.32% | 92.36% | 100% |  |  |  |  | 8.2% | 144745 | 138600 | 450 | 138150 | 70.2 | 5.57 | 616462.5161 |  | 36.59% | 96.03% | 99.5% | 223.7468 |  |  |  |  | 4.245% | 0% | 5% | 5% | 70.2
2025-01-30 | 2025 | 2025 | 2025-01-01 | 31 | [7 empty] | 5.2027 | 0 | 90.12% | 97.01% | 92.9% | 100% |  |  |  |  | 14.02% | 243083 | 237150 | 900 | 236250 | 70.2 | 5.57 | 616462.5161 |  | 36.59% | 96.03% | 99.5% | 368.1552 |  |  |  |  | 2.441% | 0% | 5% | 5% | 70.2
2025-01-31 | 2025 | 2025 | 2025-01-01 | 31 | [7 empty] | 5.4658 | 0 | 91.36% | 97.08% | 94.11% | 100% |  |  |  |  | 15.97% | 278453 | 269100 | 0 | 269100 | 70.2 | 5.57 | 616462.5161 |  | 36.59% | 96.03% | 99.5% | 411.2329 |  |  |  |  | 3.359% | 0% | 5% | 5% | 70.2
2025-02-01 | 2025 | 2025 | 2025-02-01 | 28 | [7 empty] | 5.7709 | 0 | 93.55% | 95.67% | 97.78% | 100% |  |  |  |  | 24.63% | 423926 | 414900 | 0 | 414900 | 70.2 | 5.52 | 525134.7143 |  | 31.17% | 96.03% | 99.5% | 525.5102 |  |  |  |  | 2.129% | 0% | 5% | 5% | 70.2
2025-02-02 | 2025 | 2025 | 2025-02-01 | 28 | [7 empty] | 3.323 | 0 | 99.25% | 99.25% | 100% | 100% |  |  |  |  | 4.861% | 86774 | 83250 | 1350 | 81900 | 70.2 | 5.52 | 525134.7143 |  | 31.17% | 96.03% | 99.5% | 90.1346 |  |  |  |  | 4.061% | 0% | 5% | 5% | 70.2
2025-02-03 | 2025 | 2025 | 2025-02-01 | 28 | [7 empty] | 3.1363 | 0 | 98.59% | 98.59% | 100% | 100% |  |  |  |  | 4.487% | 80544 | 77850 | 2250 | 75600 | 70.2 | 5.52 | 525134.7143 |  | 31.17% | 96.03% | 99.5% | 87.9835 |  |  |  |  | 3.345% | 0% | 5% | 5% | 70.2
2025-02-04 | 2025 | 2025 | 2025-02-01 | 28 | [7 empty] | 6.1453 | 0 | 87.1% | 96.88% | 89.91% | 100% |  |  |  |  | 25.35% | 437458 | 427050 | 0 | 427050 | 70.2 | 5.52 | 525134.7143 |  | 31.17% | 96.03% | 99.5% | 540.9671 |  |  |  |  | 2.379% | 0% | 5% | 5% | 70.2
2025-02-05 | 2025 | 2025 | 2025-02-01 | 28 | [7 empty] | 6.9033 | 0 | 96.16% | 96.16% | 100% | 100% |  |  |  |  | 33.73% | 567220 | 568350 | 0 | 568350 | 70.2 | 5.52 | 525134.7143 |  | 31.17% | 96.03% | 99.5% | 663.7691 |  |  |  |  | -0.1992% | 0% | 5% | 5% | 70.2
2025-02-06 | 2025 | 2025 | 2025-02-01 | 28 | [7 empty] | 9.5637 | 0 | 96.81% | 96.81% | 100% | 100% |  |  |  |  | 73.53% | 1280703 | 1238850 | 0 | 1238850 | 70.2 | 5.52 | 525134.7143 |  | 31.17% | 96.03% | 99.5% | 1460.1438 |  |  |  |  | 3.268% | 0% | 5% | 5% | 70.2
2025-02-07 | 2025 | 2025 | 2025-02-01 | 28 | [7 empty] | 8.8301 | 0 | 95.19% | 95.19% | 100% | 100% |  |  |  |  | 61.7% | 1077820 | 1039500 | 0 | 1039500 | 70.2 | 5.52 | 525134.7143 |  | 31.17% | 96.03% | 99.5% | 1199.0706 |  |  |  |  | 3.555% | 0% | 5% | 5% | 70.2
2025-02-08 | 2025 | 2025 | 2025-02-01 | 28 | [7 empty] | 4.7175 | 0 | 93.79% | 95.68% | 98.03% | 100% |  |  |  |  | 19.58% | 340671 | 329850 | 0 | 329850 | 70.2 | 5.52 | 525134.7143 |  | 31.17% | 96.03% | 99.5% | 406.9434 |  |  |  |  | 3.176% | 0% | 5% | 5% | 70.2
2025-02-09 | 2025 | 2025 | 2025-02-01 | 28 | [7 empty] | 3.3663 | 0 | 97.13% | 97.46% | 99.66% | 100% |  |  |  |  | 4.834% | 87899 | 82800 | 1350 | 81450 | 70.2 | 5.52 | 525134.7143 |  | 31.17% | 96.03% | 99.5% | 49.5865 |  |  |  |  | 5.801% | 0% | 5% | 5% | 70.2
2025-02-10 | 2025 | 2025 | 2025-02-01 | 28 | [7 empty] | 3.4213 | 0 | 95.93% | 96.49% | 99.42% | 100% |  |  |  |  | 6.197% | 109679 | 106200 | 1800 | 104400 | 70.2 | 5.52 | 525134.7143 |  | 31.17% | 96.03% | 99.5% | 109.7 |  |  |  |  | 3.172% | 0% | 5% | 5% | 70.2
2025-02-11 | 2025 | 2025 | 2025-02-01 | 28 | [7 empty] | 5.543 | 0 | 94.04% | 95.49% | 98.48% | 100% |  |  |  |  | 23.9% | 413142 | 402750 | 0 | 402750 | 70.2 | 5.52 | 525134.7143 |  | 31.17% | 96.03% | 99.5% | 397.98 |  |  |  |  | 2.515% | 0% | 5% | 5% | 70.2
2025-02-12 | 2025 | 2025 | 2025-02-01 | 28 | [7 empty] | 5.455 | 0 | 94.69% | 97.91% | 96.71% | 100% |  |  |  |  | 21.85% | 378927 | 368100 | 0 | 368100 | 70.2 | 5.52 | 525134.7143 |  | 31.17% | 96.03% | 99.5% | 443.69 |  |  |  |  | 2.857% | 0% | 5% | 5% | 70.2
2025-02-13 | 2025 | 2025 | 2025-02-01 | 28 | [7 empty] | 5.1571 | 0 | 97.72% | 98.37% | 99.33% | 100% |  |  |  |  | 21.07% | 364188 | 355050 | 0 | 355050 | 70.2 | 5.52 | 525134.7143 |  | 31.17% | 96.03% | 99.5% | 352.32 |  |  |  |  | 2.509% | 0% | 5% | 5% | 70.2
2025-02-14 | 2025 | 2025 | 2025-02-01 | 28 | [7 empty] | 4.0011 | 0 | 96.9% | 97.34% | 99.54% | 100% |  |  |  |  | 10.07% | 176209 | 171000 | 1350 | 169650 | 70.2 | 5.52 | 525134.7143 |  | 31.17% | 96.03% | 99.5% | 172.13 |  |  |  |  | 2.956% | 0% | 5% | 5% | 70.2
2025-02-15 | 2025 | 2025 | 2025-02-01 | 28 | [7 empty] | 6.9345 | 0 | 97.11% | 98.75% | 98.35% | 100% |  |  |  |  | 41.27% | 713213 | 695250 | 0 | 695250 | 70.2 | 5.52 | 525134.7143 |  | 31.17% | 96.03% | 99.5% | 754.9158 |  |  |  |  | 2.519% | 0% | 5% | 5% | 70.2
2025-02-16 | 2025 | 2025 | 2025-02-01 | 28 | [7 empty] | 6.214 | 0 | 96.25% | 97.2% | 99.02% | 100% |  |  |  |  | 33.87% | 585019 | 570600 | 0 | 570600 | 70.2 | 5.52 | 525134.7143 |  | 31.17% | 96.03% | 99.5% | 592.3055 |  |  |  |  | 2.465% | 0% | 5% | 5% | 70.2
2025-02-17 | 2025 | 2025 | 2025-02-01 | 28 | [7 empty] | 5.9847 | 0 | 97.03% | 97.33% | 99.7% | 100% |  |  |  |  | 30.24% | 518139 | 509400 | 0 | 509400 | 70.2 | 5.52 | 525134.7143 |  | 31.17% | 96.03% | 99.5% | 499.5663 |  |  |  |  | 1.687% | 0% | 5% | 5% | 70.2
2025-02-18 | 2025 | 2025 | 2025-02-01 | 28 | [7 empty] | 5.9744 | 0 | 96.93% | 99.61% | 97.3% | 100% |  |  |  |  | 28.66% | 494729 | 482850 | 0 | 482850 | 70.2 | 5.52 | 525134.7143 |  | 31.17% | 96.03% | 99.5% | 525.654 |  |  |  |  | 2.401% | 0% | 5% | 5% | 70.2
2025-02-19 | 2025 | 2025 | 2025-02-01 | 28 | [7 empty] | 6.1056 | 0 | 94.04% | 94.86% | 99.13% | 100% |  |  |  |  | 31.2% | 542332 | 525600 | 0 | 525600 | 70.2 | 5.52 | 525134.7143 |  | 31.17% | 96.03% | 99.5% | 547.4195 |  |  |  |  | 3.085% | 0% | 5% | 5% | 70.2
2025-02-20 | 2025 | 2025 | 2025-02-01 | 28 | [7 empty] | 5.6328 | 0 | 97.11% | 97.23% | 99.88% | 100% |  |  |  |  | 27.83% | 484207 | 468900 | 0 | 468900 | 70.2 | 5.52 | 525134.7143 |  | 31.17% | 96.03% | 99.5% | 258.0211 |  |  |  |  | 3.161% | 0% | 5% | 5% | 70.2
2025-02-21 | 2025 | 2025 | 2025-02-01 | 28 | [7 empty] | 5.0048 | 0 | 94.67% | 95.23% | 99.42% | 100% |  |  |  |  | 17.41% | 301215 | 293400 | 0 | 293400 | 70.2 | 5.52 | 525134.7143 |  | 31.17% | 96.03% | 99.5% | 326.5451 |  |  |  |  | 2.594% | 0% | 5% | 5% | 70.2
2025-02-22 | 2025 | 2025 | 2025-02-01 | 28 | [7 empty] | 4.0694 | 0 | 96.25% | 96.25% | 100% | 100% |  |  |  |  | 8.173% | 143972 | 137700 | 0 | 137700 | 70.2 | 5.52 | 525134.7143 |  | 31.17% | 96.03% | 99.5% | 143.4413 |  |  |  |  | 4.356% | 0% | 5% | 5% | 70.2
2025-02-23 | 2025 | 2025 | 2025-02-01 | 28 | [7 empty] | 4.3147 | 0 | 97.37% | 97.37% | 100% | 100% |  |  |  |  | 12.71% | 221770 | 214200 | 0 | 214200 | 70.2 | 5.52 | 525134.7143 |  | 31.17% | 96.03% | 99.5% | 214.9208 |  |  |  |  | 3.413% | 0% | 5% | 5% | 70.2
2025-02-24 | 2025 | 2025 | 2025-02-01 | 28 | [7 empty] | 4.542 | 0 | 90.83% | 91.97% | 98.76% | 100% |  |  |  |  | 14% | 242750 | 236250 | 450 | 235800 | 70.2 | 5.52 | 525134.7143 |  | 31.17% | 96.03% | 99.5% | 284.835 |  |  |  |  | 2.678% | 0% | 5% | 5% | 70.2
2025-02-25 | 2025 | 2025 | 2025-02-01 | 28 | [7 empty] | 6.1865 | 0 | 89.34% | 93.08% | 95.99% | 100% |  |  |  |  | 30.96% | 534841 | 521550 | 0 | 521550 | 70.2 | 5.52 | 525134.7143 |  | 31.17% | 96.03% | 99.5% | 622.1805 |  |  |  |  | 2.485% | 0% | 5% | 5% | 70.2
2025-02-26 | 2025 | 2025 | 2025-02-01 | 28 | [7 empty] | 4.7032 | 0 | 80.06% | 91.16% | 87.82% | 100% |  |  |  |  | 13.54% | 237691 | 228600 | 450 | 228150 | 70.2 | 5.52 | 525134.7143 |  | 31.17% | 96.03% | 99.5% | 389.9289 |  |  |  |  | 3.825% | 0% | 5% | 5% | 70.2
2025-02-27 | 2025 | 2025 | 2025-02-01 | 28 | [7 empty] | 4.5313 | 0 | 93.27% | 96.17% | 96.98% | 100% |  |  |  |  | 15.41% | 269219 | 260550 | 900 | 259650 | 70.2 | 5.52 | 525134.7143 |  | 31.17% | 96.03% | 99.5% | 300.9913 |  |  |  |  | 3.22% | 0% | 5% | 5% | 70.2
2025-02-28 | 2025 | 2025 | 2025-02-01 | 28 | [7 empty] | 7.1052 | 0 | 88.89% | 96.91% | 91.73% | 55.6% |  |  |  |  | 24.17% | 417790 | 407250 | 0 | 407250 | 70.2 | 5.52 | 525134.7143 |  | 31.17% | 96.03% | 99.5% | 573.3497 |  |  |  |  | 2.523% | 0% | 5% | 5% | 70.2
2025-03-01 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 6.2932 | 0 | 92.35% | 96.3% | 95.9% | 100% |  |  |  |  | 32.29% | 559452 | 544050 | 0 | 544050 | 70.2 | 6.89 | 632771.0323 |  | 37.56% | 96.03% | 99.5% | 654.3031 |  |  |  |  | 2.753% | 0% | 5% | 5% | 70.2
2025-03-02 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 5.2602 | 0 | 88.23% | 96.49% | 91.44% | 100% |  |  |  |  | 20.11% | 348818 | 339300 | 450 | 338850 | 70.2 | 6.89 | 632771.0323 |  | 37.56% | 96.03% | 99.5% | 468.6562 |  |  |  |  | 2.729% | 0% | 5% | 5% | 70.2
2025-03-03 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 6.0129 | 0 | 97.84% | 99.06% | 98.77% | 100% |  |  |  |  | 30.96% | 534951 | 522000 | 450 | 521550 | 70.2 | 6.89 | 632771.0323 |  | 37.56% | 96.03% | 99.5% | 550.83 |  |  |  |  | 2.421% | 0% | 5% | 5% | 70.2
2025-03-04 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 8.7561 | 0 | 86% | 95.32% | 90.22% | 100% |  |  |  |  | 59.43% | 1035924 | 1001250 | 0 | 1001250 | 70.2 | 6.89 | 632771.0323 |  | 37.56% | 96.03% | 99.5% | 1208.3668 |  |  |  |  | 3.347% | 0% | 5% | 5% | 70.2
2025-03-05 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 7.9612 | 0 | 90.75% | 96.42% | 94.12% | 100% |  |  |  |  | 51.31% | 896332 | 864450 | 0 | 864450 | 70.2 | 6.89 | 632771.0323 |  | 37.56% | 96.03% | 99.5% | 1131.4809 |  |  |  |  | 3.557% | 0% | 5% | 5% | 70.2
2025-03-06 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 5.3793 | 0 | 93.13% | 96.4% | 96.61% | 100% |  |  |  |  | 23.64% | 409654 | 398250 | 0 | 398250 | 70.2 | 6.89 | 632771.0323 |  | 37.56% | 96.03% | 99.5% | 420.8881 |  |  |  |  | 2.784% | 0% | 5% | 5% | 70.2
2025-03-07 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 4.2773 | 0 | 88.14% | 98.65% | 89.35% | 100% |  |  |  |  | 10.82% | 189237 | 182700 | 450 | 182250 | 70.2 | 6.89 | 632771.0323 |  | 37.56% | 96.03% | 99.5% | 273.0758 |  |  |  |  | 3.454% | 0% | 5% | 5% | 70.2
2025-03-08 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 5.0491 | 0 | 90.63% | 98.35% | 92.15% | 100% |  |  |  |  | 17.74% | 306891 | 298800 | 0 | 298800 | 70.2 | 6.89 | 632771.0323 |  | 37.56% | 96.03% | 99.5% | 337.2495 |  |  |  |  | 2.636% | 0% | 5% | 5% | 70.2
2025-03-09 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 4.5706 | 0 | 99.95% | 99.95% | 100% | 100% |  |  |  |  | 16.37% | 285839 | 276300 | 450 | 275850 | 70.2 | 6.89 | 632771.0323 |  | 37.56% | 96.03% | 99.5% | 236.6893 |  |  |  |  | 3.337% | 0% | 5% | 5% | 70.2
2025-03-10 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 4.3004 | 0 | 99.17% | 99.92% | 99.25% | 100% |  |  |  |  | 12.15% | 211504 | 205200 | 450 | 204750 | 70.2 | 6.89 | 632771.0323 |  | 37.56% | 96.03% | 99.5% | 224.9897 |  |  |  |  | 2.981% | 0% | 5% | 5% | 70.2
2025-03-11 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 4.5092 | 0 | 85.94% | 97.9% | 87.78% | 100% |  |  |  |  | 11.83% | 207095 | 199800 | 450 | 199350 | 70.2 | 6.89 | 632771.0323 |  | 37.56% | 96.03% | 99.5% | 300.7239 |  |  |  |  | 3.523% | 0% | 5% | 5% | 70.2
2025-03-12 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 5.5527 | 0 | 97.28% | 98.48% | 98.77% | 100% |  |  |  |  | 25.24% | 439791 | 425700 | 450 | 425250 | 70.2 | 6.89 | 632771.0323 |  | 37.56% | 96.03% | 99.5% | 468.4905 |  |  |  |  | 3.204% | 0% | 5% | 5% | 70.2
2025-03-13 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 7.3103 | 0 | 97.01% | 98.95% | 98.05% | 100% |  |  |  |  | 46.69% | 809599 | 786600 | 0 | 786600 | 70.2 | 6.89 | 632771.0323 |  | 37.56% | 96.03% | 99.5% | 877.3552 |  |  |  |  | 2.841% | 0% | 5% | 5% | 70.2
2025-03-14 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 6.7568 | 0 | 98.58% | 98.58% | 100% | 100% |  |  |  |  | 40.28% | 697373 | 678600 | 0 | 678600 | 70.2 | 6.89 | 632771.0323 |  | 37.56% | 96.03% | 99.5% | 738.4746 |  |  |  |  | 2.692% | 0% | 5% | 5% | 70.2
2025-03-15 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 5.2435 | 0 | 97.49% | 98.45% | 99.02% | 100% |  |  |  |  | 20.99% | 365203 | 353700 | 0 | 353700 | 70.2 | 6.89 | 632771.0323 |  | 37.56% | 96.03% | 99.5% | 290.4291 |  |  |  |  | 3.15% | 0% | 5% | 5% | 70.2
2025-03-16 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 5.8563 | 0 | 97.85% | 99.45% | 98.39% | 100% |  |  |  |  | 30.69% | 532770 | 517050 | 0 | 517050 | 70.2 | 6.89 | 632771.0323 |  | 37.56% | 96.03% | 99.5% | 557.7477 |  |  |  |  | 2.951% | 0% | 5% | 5% | 70.2
2025-03-17 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 5.0222 | 0 | 98.47% | 98.47% | 100% | 100% |  |  |  |  | 20.91% | 364153 | 352350 | 0 | 352350 | 70.2 | 6.89 | 632771.0323 |  | 37.56% | 96.03% | 99.5% | 375.6979 |  |  |  |  | 3.241% | 0% | 5% | 5% | 70.2
2025-03-18 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 5.1129 | 0 | 62.7% | 97.51% | 64.3% | 100% |  |  |  |  | 11.38% | 197790 | 191700 | 0 | 191700 | 70.2 | 6.89 | 632771.0323 |  | 37.56% | 96.03% | 99.5% | 460.3979 |  |  |  |  | 3.079% | 0% | 5% | 5% | 70.2
2025-03-19 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 6.0828 | 0 | 98.66% | 98.66% | 100% | 100% |  |  |  |  | 31.28% | 540426 | 526950 | 0 | 526950 | 70.2 | 6.89 | 632771.0323 |  | 37.56% | 96.03% | 99.5% | 565.4515 |  |  |  |  | 2.494% | 0% | 5% | 5% | 70.2
2025-03-20 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 6.7616 | 0 | 96.36% | 96.36% | 100% | 100% |  |  |  |  | 41.61% | 723385 | 701100 | 0 | 701100 | 70.2 | 6.89 | 632771.0323 |  | 37.56% | 96.03% | 99.5% | 775.2812 |  |  |  |  | 3.081% | 0% | 5% | 5% | 70.2
2025-03-21 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 5.5348 | 0 | 95.32% | 95.32% | 100% | 100% |  |  |  |  | 26.79% | 466047 | 451350 | 0 | 451350 | 70.2 | 6.89 | 632771.0323 |  | 37.56% | 96.03% | 99.5% | 456.1127 |  |  |  |  | 3.154% | 0% | 5% | 5% | 70.2
2025-03-22 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 4.6842 | 0 | 83.73% | 97.88% | 85.54% | 100% |  |  |  |  | 10.92% | 190396 | 184050 | 0 | 184050 | 70.2 | 6.89 | 632771.0323 |  | 37.56% | 96.03% | 99.5% | 242.0137 |  |  |  |  | 3.333% | 0% | 5% | 5% | 70.2
2025-03-23 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 4.4751 | 0 | 98.29% | 99.86% | 98.43% | 100% |  |  |  |  | 16.16% | 283782 | 272250 | 0 | 272250 | 70.2 | 6.89 | 632771.0323 |  | 37.56% | 96.03% | 99.5% | 295.4532 |  |  |  |  | 4.064% | 0% | 5% | 5% | 70.2
2025-03-24 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 4.5292 | 0 | 99.45% | 99.45% | 100% | 100% |  |  |  |  | 14.82% | 257134 | 250200 | 450 | 249750 | 70.2 | 6.89 | 632771.0323 |  | 37.56% | 96.03% | 99.5% | 265.9858 |  |  |  |  | 2.697% | 0% | 5% | 5% | 70.2
2025-03-25 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 5.9435 | 0 | 98.05% | 98.05% | 100% | 100% |  |  |  |  | 32.96% | 576356 | 555750 | 450 | 555300 | 70.2 | 6.89 | 632771.0323 |  | 37.56% | 96.03% | 99.5% | 624.3964 |  |  |  |  | 3.575% | 0% | 5% | 5% | 70.2
2025-03-26 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 6.0369 | 0 | 97.22% | 97.22% | 100% | 100% |  |  |  |  | 32.43% | 563230 | 546300 | 0 | 546300 | 70.2 | 6.89 | 632771.0323 |  | 37.56% | 96.03% | 99.5% | 653.87 |  |  |  |  | 3.006% | 0% | 5% | 5% | 70.2
2025-03-27 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 5.9277 | 0 | 97.1% | 97.1% | 100% | 100% |  |  |  |  | 29.09% | 502420 | 490050 | 0 | 490050 | 70.2 | 6.89 | 632771.0323 |  | 37.56% | 96.03% | 99.5% | 510.8896 |  |  |  |  | 2.462% | 0% | 5% | 5% | 70.2
2025-03-28 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 6.8496 | 0 | 97.62% | 97.62% | 100% | 100% |  |  |  |  | 41.29% | 716882 | 695700 | 0 | 695700 | 70.2 | 6.89 | 632771.0323 |  | 37.56% | 96.03% | 99.5% | 717.7885 |  |  |  |  | 2.955% | 0% | 5% | 5% | 70.2
2025-03-29 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 7.14 | 0 | 96.57% | 96.57% | 100% | 100% |  |  |  |  | 45.81% | 801666 | 771750 | 0 | 771750 | 70.2 | 6.89 | 632771.0323 |  | 37.56% | 96.03% | 99.5% | 843.5335 |  |  |  |  | 3.732% | 0% | 5% | 5% | 70.2
2025-03-30 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 5.9437 | 0 | 99.32% | 99.32% | 100% | 100% |  |  |  |  | 31.78% | 552111 | 535500 | 0 | 535500 | 70.2 | 6.89 | 632771.0323 |  | 37.56% | 96.03% | 99.5% | 562.5916 |  |  |  |  | 3.009% | 0% | 5% | 5% | 70.2
2025-03-31 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 6.513 | 0 | 98.8% | 98.8% | 100% | 100% |  |  |  |  | 38.38% | 667722 | 646650 | 0 | 646650 | 70.2 | 6.89 | 632771.0323 |  | 37.56% | 96.03% | 99.5% | 675.4049 |  |  |  |  | 3.156% | 0% | 5% | 5% | 70.2
2025-04-01 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 6.0269 | 0 | 98.29% | 98.29% | 100% | 100% |  |  |  |  | 31.2% | 544118 | 525600 | 0 | 525600 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 664.4211 |  |  |  |  | 3.403% | 0% | 5% | 5% | 70.2
2025-04-02 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.4382 | 0 | 98.14% | 98.14% | 100% | 100% |  |  |  |  | 16.37% | 285682 | 275850 | 0 | 275850 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 294.6404 |  |  |  |  | 3.442% | 0% | 5% | 5% | 70.2
2025-04-03 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.8482 | 0 | 97.62% | 97.65% | 99.96% | 100% |  |  |  |  | 20.51% | 357239 | 346050 | 450 | 345600 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 371.21 |  |  |  |  | 3.132% | 0% | 5% | 5% | 70.2
2025-04-04 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.285 | 0 | 97.59% | 97.59% | 100% | 100% |  |  |  |  | 15.25% | 269263 | 257400 | 450 | 256950 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 281.07 |  |  |  |  | 4.406% | 0.4846% | 5% | 5% | 70.2
2025-04-05 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.3639 | 0 | 94.43% | 95.49% | 98.89% | 100% |  |  |  |  | 12.71% | 223271 | 214200 | 0 | 214200 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 230.95 |  |  |  |  | 4.063% | 0.403% | 5% | 5% | 70.2
2025-04-06 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 6.4386 | 0 | 98.4% | 98.4% | 100% | 100% |  |  |  |  | 35.79% | 620284 | 603000 | 0 | 603000 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 667.03 |  |  |  |  | 2.786% | 0.5078% | 5% | 5% | 70.2
2025-04-07 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 7.1744 | 0 | 96.58% | 97.46% | 99.09% | 100% |  |  |  |  | 47.65% | 834723 | 802800 | 0 | 802800 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 890.54 |  |  |  |  | 3.824% | 3.828% | 5% | 5% | 70.2
2025-04-08 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 7.0791 | 0 | 97.18% | 97.18% | 100% | 100% |  |  |  |  | 47.09% | 823138 | 793800 | 450 | 793350 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 885.16 |  |  |  |  | 3.564% | 0.328% | 5% | 5% | 70.2
2025-04-09 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 7.09 | 0 | 98.75% | 98.75% | 100% | 100% |  |  |  |  | 44.07% | 766278 | 742500 | 0 | 742500 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 808 |  |  |  |  | 3.103% | 0.3523% | 5% | 5% | 70.2
2025-04-10 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 8.2136 | 0 | 98.08% | 98.08% | 100% | 100% |  |  |  |  | 57.85% | 1006142 | 974700 | 0 | 974700 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 1103.33 |  |  |  |  | 3.125% | 1.655% | 5% | 5% | 70.2
2025-04-11 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 8.1076 | 0 | 96.15% | 96.15% | 100% | 100% |  |  |  |  | 59.62% | 1041716 | 1004400 | 0 | 1004400 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 1083.02 |  |  |  |  | 3.582% | 0.5184% | 5% | 5% | 70.2
2025-04-12 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.9831 | 0 | 56.44% | 98.7% | 57.18% | 100% |  |  |  |  | 9.776% | 173786 | 164700 | 0 | 164700 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 176.01 |  |  |  |  | 5.228% | 0.2588% | 5% | 5% | 70.2
2025-04-13 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 7.6408 | 0 | 65.17% | 95.42% | 68.3% | 100% |  |  |  |  | 35.02% | 607437 | 589950 | 0 | 589950 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 682.2 |  |  |  |  | 2.879% | 0.3704% | 5% | 5% | 70.2
2025-04-14 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 8.9527 | 0 | 95.99% | 95.99% | 100% | 100% |  |  |  |  | 67.17% | 1174575 | 1131750 | 0 | 1131750 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 1310.71 |  |  |  |  | 3.646% | 1.303% | 5% | 5% | 70.2
2025-04-15 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 8.6514 | 0 | 93.62% | 93.62% | 100% | 100% |  |  |  |  | 62.93% | 1098717 | 1060200 | 0 | 1060200 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 1204.55 |  |  |  |  | 3.506% | 1.679% | 5% | 5% | 70.2
2025-04-16 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 7.9019 | 0 | 92.54% | 92.59% | 99.95% | 100% |  |  |  |  | 54.25% | 947749 | 913950 | 0 | 913950 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 1042.18 |  |  |  |  | 3.566% | 2.944% | 5% | 5% | 70.2
2025-04-17 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 7.2235 | 0 | 97.17% | 97.17% | 100% | 100% |  |  |  |  | 50.13% | 875991 | 845100 | 450 | 844650 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 924.98 |  |  |  |  | 3.526% | 4.212% | 5% | 5% | 70.2
2025-04-18 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 7.6607 | 0 | 96.46% | 96.46% | 100% | 100% |  |  |  |  | 49.65% | 864039 | 836550 | 0 | 836550 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 946.76 |  |  |  |  | 3.181% | 0.2604% | 5% | 5% | 70.2
2025-04-19 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 8.905 | 0 | 96.94% | 96.94% | 100% | 100% |  |  |  |  | 66.4% | 1158786 | 1118700 | 0 | 1118700 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 1285.97 |  |  |  |  | 3.459% | 0.8543% | 5% | 5% | 70.2
2025-04-20 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 6.8564 | 0 | 98.18% | 98.18% | 100% | 100% |  |  |  |  | 40.79% | 708938 | 687150 | 0 | 687150 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 742.63 |  |  |  |  | 3.073% | 0.1904% | 5% | 5% | 70.2
2025-04-21 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.9753 | 0 | 88.34% | 97.81% | 90.32% | 100% |  |  |  |  | 15.87% | 276454 | 267300 | 0 | 267300 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 287.24 |  |  |  |  | 3.311% | 0.1627% | 5% | 5% | 70.2
2025-04-22 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.212 | 0 | 94.53% | 96.33% | 98.13% | 100% |  |  |  |  | 19.71% | 342173 | 332100 | 0 | 332100 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 353.11 |  |  |  |  | 2.944% | 0.1315% | 5% | 5% | 70.2
2025-04-23 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.6525 | 0 | 96.84% | 96.84% | 100% | 100% |  |  |  |  | 27.56% | 480100 | 464400 | 0 | 464400 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 502.87 |  |  |  |  | 3.27% | 0.1874% | 5% | 5% | 70.2
2025-04-24 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.8495 | 0 | 97.63% | 97.63% | 100% | 100% |  |  |  |  | 29.01% | 502706 | 488700 | 0 | 488700 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 510 |  |  |  |  | 2.786% | 0.179% | 5% | 5% | 70.2
2025-04-25 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 6.1728 | 0 | 95.96% | 95.96% | 100% | 100% |  |  |  |  | 34.03% | 592507 | 573300 | 0 | 573300 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 628.86 |  |  |  |  | 3.242% | 0.2278% | 5% | 5% | 70.2
2025-04-26 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 6.2133 | 0 | 95.37% | 95.37% | 100% | 100% |  |  |  |  | 35.12% | 613361 | 591750 | 0 | 591750 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 645.69 |  |  |  |  | 3.523% | 1.761% | 5% | 5% | 70.2
2025-04-27 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.668 | 0 | 95.75% | 95.75% | 100% | 100% |  |  |  |  | 30.07% | 525996 | 507150 | 450 | 506700 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 546.95 |  |  |  |  | 3.583% | 0.2566% | 5% | 5% | 70.2
2025-04-28 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 6.61 | 0 | 95.84% | 96.39% | 99.43% | 100% |  |  |  |  | 37.9% | 659514 | 638550 | 0 | 638550 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 695.35 |  |  |  |  | 3.179% | 0.2729% | 5% | 5% | 70.2
2025-04-29 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 8.3967 | 0 | 95.43% | 95.43% | 100% | 100% |  |  |  |  | 58.68% | 1021944 | 988650 | 0 | 988650 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 1133.84 |  |  |  |  | 3.258% | 0.2642% | 5% | 5% | 70.2
2025-04-30 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 8.18 | 0 | 96.88% | 96.88% | 100% | 100% |  |  |  |  | 57.91% | 1009423 | 975600 | 0 | 975600 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 1088.32 |  |  |  |  | 3.351% | 0.2675% | 5% | 5% | 70.2
2025-05-01 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 8.4492 | 0 | 98.61% | 98.61% | 100% | 100% |  |  |  |  | 64.26% | 1122695 | 1082700 | 0 | 1082700 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 1190.71 |  |  |  |  | 3.562% | 0.2405% | 5% | 5% | 70.2
2025-05-02 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 6.8017 | 0 | 98.16% | 98.16% | 100% | 100% |  |  |  |  | 40.46% | 732600 | 681750 | 0 | 681750 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 781.68 |  |  |  |  | 6.941% | 0.3071% | 5% | 5% | 70.2
2025-05-03 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 8.6568 | 0 | 95.58% | 95.58% | 100% | 100% |  |  |  |  | 63.76% | 1085131 | 1074150 | 0 | 1074150 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 1224.47 |  |  |  |  | 1.012% | 2.654% | 5% | 5% | 70.2
2025-05-04 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 6.7652 | 0 | 96.81% | 96.81% | 100% | 100% |  |  |  |  | 40.68% | 711947 | 685800 | 450 | 685350 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 773.86 |  |  |  |  | 3.673% | 2.908% | 5% | 5% | 70.2
2025-05-05 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 7.2849 | 0 | 98.3% | 98.3% | 100% | 100% |  |  |  |  | 44.02% | 767792 | 741600 | 0 | 741600 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 837.33 |  |  |  |  | 3.411% | 2.93% | 5% | 5% | 70.2
2025-05-06 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 6.8863 | 0 | 63.23% | 90% | 70.25% | 100% |  |  |  |  | 24.49% | 425147 | 412650 | 0 | 412650 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 541.99 |  |  |  |  | 2.939% | 0.5292% | 5% | 5% | 70.2
2025-05-07 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 5.8334 | 0 | 80.68% | 87.46% | 92.24% | 100% |  |  |  |  | 22.38% | 391213 | 377100 | 0 | 377100 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 371.67 |  |  |  |  | 3.607% | 5.406% | 5% | 5% | 70.2
2025-05-08 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.144 | 0 | 97.14% | 98.12% | 99.01% | 100% |  |  |  |  | 11.08% | 194603 | 187200 | 450 | 186750 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 194.403 |  |  |  |  | 3.804% | 0.2311% | 5% | 5% | 70.2
2025-05-09 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.2123 | 0 | 96.35% | 99.71% | 96.63% | 100% |  |  |  |  | 12.47% | 218799 | 210150 | 0 | 210150 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 215.78 |  |  |  |  | 3.953% | 0.2056% | 5% | 5% | 70.2
2025-05-10 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.929 | 0 | 93.35% | 98.54% | 94.74% | 100% |  |  |  |  | 20.22% | 352993 | 341550 | 900 | 340650 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 361.29 |  |  |  |  | 3.242% | 0.2549% | 5% | 5% | 70.2
2025-05-11 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.7262 | 0 | 95.51% | 97.89% | 97.57% | 100% |  |  |  |  | 17.57% | 305561 | 296550 | 450 | 296100 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 313.28 |  |  |  |  | 2.949% | 0.1472% | 5% | 5% | 70.2
2025-05-12 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.93 | 0 | 97.36% | 99.44% | 97.9% | 100% |  |  |  |  | 18.16% | 314946 | 306000 | 0 | 306000 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 314.91 |  |  |  |  | 2.84% | 0.2857% | 5% | 5% | 70.2
2025-05-13 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 5.2229 | 0 | 98.29% | 98.46% | 99.82% | 100% |  |  |  |  | 23.8% | 415674 | 400950 | 0 | 400950 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 410.17 |  |  |  |  | 3.542% | 0.3248% | 5% | 5% | 70.2
2025-05-14 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 5.1362 | 0 | 98.83% | 99.01% | 99.81% | 100% |  |  |  |  | 23.5% | 410395 | 396450 | 450 | 396000 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 415.16 |  |  |  |  | 3.398% | 0.3289% | 5% | 5% | 70.2
2025-05-15 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.5069 | 0 | 94.43% | 95.98% | 98.39% | 100% |  |  |  |  | 14.74% | 258268 | 248850 | 450 | 248400 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 270.48 |  |  |  |  | 3.647% | 1.22% | 5% | 5% | 70.2
2025-05-16 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 5.468 | 0 | 91.46% | 94.61% | 96.67% | 100% |  |  |  |  | 22.6% | 394190 | 380700 | 0 | 380700 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 429.76 |  |  |  |  | 3.422% | 7.877% | 5% | 5% | 70.2
2025-05-17 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 5.165 | 0 | 92.82% | 93.13% | 99.66% | 100% |  |  |  |  | 19.74% | 342930 | 332550 | 0 | 332550 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 357.08 |  |  |  |  | 3.027% | 6.036% | 5% | 5% | 70.2
2025-05-18 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 5.0872 | 0 | 96.11% | 98.5% | 97.57% | 100% |  |  |  |  | 19.28% | 334985 | 324900 | 0 | 324900 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 337.37 |  |  |  |  | 3.011% | 0.403% | 5% | 5% | 70.2
2025-05-19 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 5.1563 | 0 | 98.66% | 98.66% | 100% | 100% |  |  |  |  | 22.41% | 390622 | 377550 | 0 | 377550 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 390.56 |  |  |  |  | 3.346% | 0.2304% | 5% | 5% | 70.2
2025-05-20 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 5.2799 | 0 | 97.92% | 98.97% | 98.94% | 100% |  |  |  |  | 20.99% | 366523 | 354150 | 450 | 353700 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 390.19 |  |  |  |  | 3.376% | 0.2455% | 5% | 5% | 70.2
2025-05-21 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.5324 | 0 | 74.24% | 96.12% | 77.24% | 100% |  |  |  |  | 11.08% | 193560 | 186750 | 0 | 186750 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 202.65 |  |  |  |  | 3.518% | 0.2324% | 5% | 5% | 70.2
2025-05-22 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 3.7635 | 0 | 84.65% | 99.01% | 85.5% | 100% |  |  |  |  | 7.879% | 139747 | 134100 | 1350 | 132750 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 158.54 |  |  |  |  | 4.041% | 0.6439% | 5% | 5% | 70.2
2025-05-23 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.8979 | 0 | 99.29% | 99.7% | 99.59% | 100% |  |  |  |  | 20.06% | 350115 | 337950 | 0 | 337950 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 371.21 |  |  |  |  | 3.475% | 0.257% | 5% | 5% | 70.2
2025-05-24 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 7.568 | 0 | 84.7% | 98.24% | 86.22% | 100% |  |  |  |  | 46.61% | 814043 | 785250 | 0 | 785250 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 847.72 |  |  |  |  | 3.537% | 0.2211% | 5% | 5% | 70.2
2025-05-25 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 7.6819 | 0 | 88.18% | 96.08% | 91.78% | 100% |  |  |  |  | 48.21% | 841018 | 812250 | 0 | 812250 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 893.8 |  |  |  |  | 3.421% | 1.819% | 5% | 5% | 70.2
2025-05-26 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 7.12 | 0 | 95.72% | 97.75% | 97.93% | 100% |  |  |  |  | 43.43% | 755322 | 731700 | 0 | 731700 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 797.2 |  |  |  |  | 3.127% | 0.4766% | 5% | 5% | 70.2
2025-05-27 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 9.4785 | 0 | 87.08% | 95.17% | 91.49% | 100% |  |  |  |  | 68.8% | 1203107 | 1159200 | 0 | 1159200 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 1294.88 |  |  |  |  | 3.649% | 0.8977% | 5% | 5% | 70.2
2025-05-28 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 8.42 | 0 | 83.38% | 99.15% | 84.1% | 100% |  |  |  |  | 55.8% | 971819 | 940050 | 0 | 940050 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 1024.62 |  |  |  |  | 3.269% | 0.3704% | 5% | 5% | 70.2
2025-05-29 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 7.4665 | 0 | 98.63% | 98.63% | 100% | 100% |  |  |  |  | 53.5% | 932530 | 901800 | 450 | 901350 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 986.68 |  |  |  |  | 3.295% | 0.7721% | 5% | 5% | 70.2
2025-05-30 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 9.8923 | 0 | 98.48% | 98.48% | 100% | 100% |  |  |  |  | 81.36% | 1422464 | 1370700 | 0 | 1370700 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 1505.57 |  |  |  |  | 3.639% | 2.373% | 5% | 5% | 70.2
2025-05-31 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 9.6238 | 0 | 97.17% | 99.23% | 97.92% | 100% |  |  |  |  | 76.74% | 1341161 | 1292850 | 0 | 1292850 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 1438.1 |  |  |  |  | 3.602% | 2.516% | 5% | 5% | 70.2
2025-06-01 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 9.3908 | 0 | 99.29% | 99.29% | 100% | 100% |  |  |  |  | 78.1% | 1340220.2667 | 1315800 | 0 | 1315800 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 1430.08 |  |  |  |  | 1.822% | 2.015% | 5% | 5% | 70.2
2025-06-02 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 9.4662 | 0 | 99.39% | 99.39% | 100% | 100% |  |  |  |  | 66.21% | 1165824.4667 | 1115550 | 0 | 1115550 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 1231.2 |  |  |  |  | 4.312% | 2.316% | 5% | 5% | 70.2
2025-06-03 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 8.4555 | 0 | 99.22% | 99.27% | 99.95% | 100% |  |  |  |  | 63.33% | 1102681 | 1066950 | 0 | 1066950 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 1108.56 |  |  |  |  | 3.24% | 0.3673% | 5% | 5% | 70.2
2025-06-04 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 6.5477 | 0 | 99.82% | 99.82% | 100% | 100% |  |  |  |  | 39.29% | 681987 | 661950 | 0 | 661950 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 27.04 |  |  |  |  | 2.938% | 0.3299% | 5% | 5% | 70.2
2025-06-05 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 5.1219 | 0 | 99.2% | 99.2% | 100% | 100% |  |  |  |  | 21.77% | 379657 | 367200 | 450 | 366750 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 385.8 |  |  |  |  | 3.281% | 2.608% | 5% | 5% | 70.2
2025-06-06 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 6.1272 | 0 | 98.05% | 98.05% | 100% | 100% |  |  |  |  | 33.41% | 580148 | 562950 | 0 | 562950 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 593.58 |  |  |  |  | 2.964% | 0.4654% | 5% | 5% | 70.2
2025-06-07 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 7.5199 | 0 | 98.11% | 98.11% | 100% | 100% |  |  |  |  | 51.07% | 886785 | 860400 | 0 | 860400 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 899.42 |  |  |  |  | 2.975% | 0.3045% | 5% | 5% | 70.2
2025-06-08 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 7.3034 | 0 | 96.26% | 96.26% | 100% | 100% |  |  |  |  | 47.3% | 820968 | 796950 | 0 | 796950 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 846.28 |  |  |  |  | 2.926% | 1.699% | 5% | 5% | 70.2
2025-06-09 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 7.9526 | 0 | 99.9% | 99.9% | 100% | 100% |  |  |  |  | 58.55% | 1019022 | 986400 | 0 | 986400 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 1032.83 |  |  |  |  | 3.201% | 0.9715% | 5% | 5% | 70.2
2025-06-10 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 8.1789 | 0 | 97.48% | 97.48% | 100% | 100% |  |  |  |  | 61.73% | 1075551 | 1039950 | 0 | 1039950 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 1108.35 |  |  |  |  | 3.31% | 0.3765% | 5% | 5% | 70.2
2025-06-11 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 7.2928 | 0 | 97.73% | 97.73% | 100% | 100% |  |  |  |  | 50.29% | 875379 | 847350 | 0 | 847350 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 911.21 |  |  |  |  | 3.202% | 1.234% | 5% | 5% | 70.2
2025-06-12 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 7.6641 | 0 | 99.75% | 99.75% | 100% | 100% |  |  |  |  | 53.66% | 934724 | 904050 | 0 | 904050 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 956.64 |  |  |  |  | 3.282% | 0.2888% | 5% | 5% | 70.2
2025-06-13 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-06-14 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-06-15 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-06-16 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-06-17 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-06-18 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-06-19 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-06-20 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-06-21 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-06-22 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-06-23 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-06-24 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-06-25 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-06-26 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-06-27 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-06-28 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-06-29 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-06-30 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-01 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-02 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-03 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-04 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-05 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-06 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-07 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-08 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-09 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-10 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-11 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-12 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-13 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-14 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-15 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-16 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-17 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-18 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-19 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-20 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-21 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-22 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-23 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-24 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-25 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-26 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-27 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-28 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-29 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-30 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-31 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-01 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-02 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-03 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-04 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-05 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-06 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-07 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-08 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-09 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-10 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-11 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-12 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-13 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-14 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-15 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-16 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-17 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-18 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-19 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-20 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-21 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-22 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-23 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-24 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-25 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-26 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-27 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-28 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-29 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-30 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-31 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-01 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-02 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-03 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-04 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-05 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-06 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-07 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-08 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-09 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-10 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-11 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-12 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-13 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-14 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-15 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-16 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-17 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-18 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-19 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-20 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-21 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-22 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-23 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-24 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-25 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-26 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-27 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-28 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-29 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-30 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-01 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-02 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-03 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-04 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-05 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-06 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-07 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-08 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-09 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-10 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-11 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-12 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-13 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-14 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-15 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-16 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-17 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-18 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-19 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-20 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-21 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-22 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-23 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-24 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-25 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-26 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-27 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-28 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-29 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-30 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-31 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-01 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-02 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-03 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-04 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-05 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-06 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-07 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-08 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-09 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-10 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-11 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-12 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-13 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-14 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-15 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-16 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-17 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-18 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-19 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-20 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-21 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-22 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-23 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-24 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-25 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-26 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-27 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-28 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-29 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-30 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-01 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-02 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-03 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-04 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-05 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-06 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-07 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-08 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-09 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-10 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-11 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-12 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-13 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-14 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-15 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-16 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-17 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-18 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-19 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-20 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-21 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-22 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-23 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-24 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-25 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-26 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-27 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-28 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-29 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-30 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-31 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-01 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-02 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-03 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-04 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-05 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-06 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-07 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-08 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-09 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-10 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-11 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-12 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-13 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-14 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-15 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-16 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-17 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-18 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-19 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-20 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-21 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-22 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-23 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-24 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-25 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-26 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-27 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-28 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-29 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-30 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-31 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-01 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-02 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-03 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-04 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-05 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-06 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-07 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-08 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-09 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-10 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-11 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-12 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-13 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-14 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-15 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-16 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-17 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-18 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-19 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-20 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-21 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-22 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-23 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-24 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-25 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-26 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-27 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-28 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-01 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-02 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-03 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-04 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-05 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-06 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-07 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-08 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-09 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-10 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-11 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-12 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-13 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-14 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-15 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-16 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-17 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-18 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-19 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-20 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-21 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-22 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-23 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-24 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-25 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-26 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-27 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-28 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-29 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-30 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-31 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
Formulas:
Month Year = Table13[[#This Row],[Date]]-DAY(Table13[[#This Row],[Date]])+1
Days = DAY(EOMONTH([Date],0))
Date = [Date, row above]+1

## AnnualKPI
Till Date | 2025-06-12 | 2025-06-01
TGPXIIPL Performance Summary-YTD
Year | Days | Estimated WS(m/s) | Measured WS (m/s) | Budgeted Energy (MWh) | Measured Energy (MWh) | Target CUF (%) | Measured CUF (%) | Target GA (%) | Measured GA (%) | Target MA (%) | Measured MA (%) | Target IGA(%) | Measured IGA (%) | Target PA(%) | Measured PA (%) | Expected Energy | Loss (%) | Reactive Power (%)
2026 | 73 | 6.9967 | 6.6559 | 58722.2291 | 48099.15 | 47.75% | 39.11% | 99.5% | 100% | 97% | 97.27% | 99% | 96.74% | 96.03% | 94.1% | 52161.6945 | 3.431% | 0.7953%

## WTG Reactive Power
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
Date | Financial Year | Calendar Year | Month Year | O2_01 (kVArh) | O2_02 (kVArh) | O2_03 (kVArh) | O2_04 (kVArh) | O2_05 (kVArh) | O2_06 (kVArh) | O2_07 (kVArh) | O2_08 (kVArh) | O2_09 (kVArh) | O2_10 (kVArh) | O2_11 (kVArh) | O2_12 (kVArh) | O2_13 (kVArh) | O2_14 (kVArh) | O2_15 (kVArh) | O2_16 (kVArh) | O2_17 (kVArh) | O2_18 (kVArh) | O2_19 (kVArh) | O2_20 (kVArh) | O2_21 (kVArh) | O2_22 (kVArh) | O2_23 (kVArh) | O2_24 (kVArh) | O2_25 (kVArh) | O2_26 (kVArh) | Total Reactive Power (kVArh)
2024-04-01 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-02 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-03 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-04 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-05 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-06 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-07 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-08 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-09 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-10 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-11 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-12 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-13 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-14 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-15 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-16 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-17 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-18 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-19 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-20 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-21 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-22 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-23 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-24 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-25 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-26 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-27 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-28 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-29 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-30 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-05-01 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-02 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-03 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-04 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-05 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-06 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-07 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-08 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-09 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-10 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-11 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-12 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-13 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-14 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-15 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-16 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-17 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-18 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-19 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-20 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-21 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-22 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-23 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-24 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-25 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-26 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-27 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-28 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-29 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-30 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-31 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-06-01 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-02 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-03 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-04 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-05 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-06 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-07 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-08 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-09 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-10 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-11 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-12 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-13 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-14 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-15 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-16 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-17 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-18 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-19 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-20 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-21 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-22 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-23 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-24 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-25 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-26 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-27 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-28 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-29 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-30 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-07-01 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-02 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-03 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-04 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-05 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-06 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-07 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-08 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-09 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-10 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-11 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-12 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-13 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-14 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-15 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-16 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-17 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-18 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-19 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-20 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-21 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-22 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-23 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-24 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-25 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-26 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-27 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-28 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-29 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-30 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-31 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-08-01 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-02 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-03 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-04 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-05 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-06 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-07 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-08 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-09 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-10 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-11 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-12 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-13 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-14 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-15 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-16 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-17 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-18 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-19 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-20 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-21 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-22 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-23 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-24 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-25 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-26 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-27 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-28 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-29 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-30 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-31 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-09-01 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-02 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-03 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-04 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-05 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-06 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-07 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-08 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-09 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-10 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-11 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-12 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-13 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-14 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-15 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-16 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-17 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-18 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-19 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-20 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-21 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-22 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-23 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-24 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-25 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-26 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-27 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-28 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-29 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-30 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-10-01 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-02 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-03 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-04 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-05 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-06 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-07 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-08 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-09 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-10 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-11 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-12 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-13 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-14 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-15 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-16 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-17 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-18 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-19 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-20 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-21 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-22 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-23 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-24 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-25 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-26 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-27 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-28 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-29 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-30 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-31 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-11-01 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-02 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-03 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-04 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-05 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-06 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-07 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-08 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-09 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-10 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-11 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-12 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-13 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-14 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-15 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-16 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-17 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-18 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-19 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-20 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-21 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-22 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-23 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-24 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-25 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-26 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-27 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-28 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-29 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-30 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-12-01 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-02 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-03 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-04 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-05 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-06 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-07 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-08 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-09 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-10 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-11 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-12 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-13 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-14 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-15 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-16 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-17 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-18 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-19 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-20 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-21 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-22 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-23 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-24 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-25 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-26 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-27 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-28 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-29 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-30 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-31 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2025-01-01 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-02 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-03 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-04 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-05 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-06 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-07 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-08 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-09 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-10 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-11 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-12 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-13 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-14 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-15 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-16 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-17 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-18 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-19 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-20 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-21 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-22 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-23 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-24 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-25 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-26 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-27 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-28 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-29 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-30 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-31 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-02-01 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-02 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-03 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-04 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-05 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-06 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-07 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-08 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-09 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-10 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-11 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-12 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-13 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-14 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-15 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-16 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-17 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-18 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-19 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-20 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-21 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-22 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-23 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-24 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-25 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-26 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-27 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-28 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-03-01 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-02 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-03 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-04 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-05 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-06 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-07 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-08 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-09 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-10 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-11 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-12 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-13 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-14 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-15 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-16 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-17 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-18 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-19 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-20 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-21 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-22 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-23 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-24 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-25 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-26 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-27 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-28 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-29 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-30 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-31 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-04-01 | 2026 | 2025 | 2025-04-01 | [26 empty] | 0
2025-04-02 | 2026 | 2025 | 2025-04-01 | [26 empty] | 0
2025-04-03 | 2026 | 2025 | 2025-04-01 | [26 empty] | 0
2025-04-04 | 2026 | 2025 | 2025-04-01 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 1304.94
2025-04-05 | 2026 | 2025 | 2025-04-01 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 899.86
2025-04-06 | 2026 | 2025 | 2025-04-01 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 3149.9
2025-04-07 | 2026 | 2025 | 2025-04-01 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 31949.84
2025-04-08 | 2026 | 2025 | 2025-04-01 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 2699.84
2025-04-09 | 2026 | 2025 | 2025-04-01 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 2699.84
2025-04-10 | 2026 | 2025 | 2025-04-01 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 16649.88
2025-04-11 | 2026 | 2025 | 2025-04-01 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 5399.94
2025-04-12 | 2026 | 2025 | 2025-04-01 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 449.8
2025-04-13 | 2026 | 2025 | 2025-04-01 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 2249.78
2025-04-14 | 2026 | 2025 | 2025-04-01 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 15299.96
2025-04-15 | 2026 | 2025 | 2025-04-01 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 18449.86
2025-04-16 | 2026 | 2025 | 2025-04-01 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 27899.82
2025-04-17 | 2026 | 2025 | 2025-04-01 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 36899.98
2025-04-18 | 2026 | 2025 | 2025-04-01 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 2249.78
2025-04-19 | 2026 | 2025 | 2025-04-01 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 9899.76
2025-04-20 | 2026 | 2025 | 2025-04-01 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 1349.92
2025-04-21 | 2026 | 2025 | 2025-04-01 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 449.8
2025-04-22 | 2026 | 2025 | 2025-04-01 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 449.8
2025-04-23 | 2026 | 2025 | 2025-04-01 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 899.86
2025-04-24 | 2026 | 2025 | 2025-04-01 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 899.86
2025-04-25 | 2026 | 2025 | 2025-04-01 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 1349.92
2025-04-26 | 2026 | 2025 | 2025-04-01 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 10799.88
2025-04-27 | 2026 | 2025 | 2025-04-01 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 1349.92
2025-04-28 | 2026 | 2025 | 2025-04-01 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 1799.98
2025-04-29 | 2026 | 2025 | 2025-04-01 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 2699.84
2025-04-30 | 2026 | 2025 | 2025-04-01 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 2699.84
2025-05-01 | 2026 | 2025 | 2025-05-01 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 2699.84
2025-05-02 | 2026 | 2025 | 2025-05-01 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 2249.78
2025-05-03 | 2026 | 2025 | 2025-05-01 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 28799.94
2025-05-04 | 2026 | 2025 | 2025-05-01 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 20699.9
2025-05-05 | 2026 | 2025 | 2025-05-01 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 22499.88
2025-05-06 | 2026 | 2025 | 2025-05-01 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 2249.78
2025-05-07 | 2026 | 2025 | 2025-05-01 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 21149.96
2025-05-08 | 2026 | 2025 | 2025-05-01 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 449.8
2025-05-09 | 2026 | 2025 | 2025-05-01 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 449.8
2025-05-10 | 2026 | 2025 | 2025-05-01 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 899.86
2025-05-11 | 2026 | 2025 | 2025-05-01 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 449.8
2025-05-12 | 2026 | 2025 | 2025-05-01 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 899.86
2025-05-13 | 2026 | 2025 | 2025-05-01 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 1349.92
2025-05-14 | 2026 | 2025 | 2025-05-01 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 1349.92
2025-05-15 | 2026 | 2025 | 2025-05-01 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 3149.9
2025-05-16 | 2026 | 2025 | 2025-05-01 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 31049.98
2025-05-17 | 2026 | 2025 | 2025-05-01 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 20699.9
2025-05-18 | 2026 | 2025 | 2025-05-01 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 1349.92
2025-05-19 | 2026 | 2025 | 2025-05-01 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 899.86
2025-05-20 | 2026 | 2025 | 2025-05-01 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 899.86
2025-05-21 | 2026 | 2025 | 2025-05-01 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 449.8
2025-05-22 | 2026 | 2025 | 2025-05-01 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 899.86
2025-05-23 | 2026 | 2025 | 2025-05-01 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 899.86
2025-05-24 | 2026 | 2025 | 2025-05-01 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 1799.98
2025-05-25 | 2026 | 2025 | 2025-05-01 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 15299.96
2025-05-26 | 2026 | 2025 | 2025-05-01 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 3599.96
2025-05-27 | 2026 | 2025 | 2025-05-01 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 10799.88
2025-05-28 | 2026 | 2025 | 2025-05-01 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 3599.96
2025-05-29 | 2026 | 2025 | 2025-05-01 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 7199.92
2025-05-30 | 2026 | 2025 | 2025-05-01 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 33749.82
2025-05-31 | 2026 | 2025 | 2025-05-01 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 33749.82
2025-06-01 | 2026 | 2025 | 2025-06-01 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 26999.96
2025-06-02 | 2026 | 2025 | 2025-06-01 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 26999.96
2025-06-03 | 2026 | 2025 | 2025-06-01 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 4049.76
2025-06-04 | 2026 | 2025 | 2025-06-01 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 2249.78
2025-06-05 | 2026 | 2025 | 2025-06-01 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 9899.76
2025-06-06 | 2026 | 2025 | 2025-06-01 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 2699.84
2025-06-07 | 2026 | 2025 | 2025-06-01 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 2699.84
2025-06-08 | 2026 | 2025 | 2025-06-01 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 13949.78
2025-06-09 | 2026 | 2025 | 2025-06-01 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 9899.76
2025-06-10 | 2026 | 2025 | 2025-06-01 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 4049.76
2025-06-11 | 2026 | 2025 | 2025-06-01 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 10799.88
2025-06-12 | 2026 | 2025 | 2025-06-01 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 2699.84
2025-06-13 | 2026 | 2025 | 2025-06-01 | [26 empty] | 0
2025-06-14 | 2026 | 2025 | 2025-06-01 | [26 empty] | 0
2025-06-15 | 2026 | 2025 | 2025-06-01 | [26 empty] | 0
2025-06-16 | 2026 | 2025 | 2025-06-01 | [26 empty] | 0
2025-06-17 | 2026 | 2025 | 2025-06-01 | [26 empty] | 0
2025-06-18 | 2026 | 2025 | 2025-06-01 | [26 empty] | 0
2025-06-19 | 2026 | 2025 | 2025-06-01 | [26 empty] | 0
2025-06-20 | 2026 | 2025 | 2025-06-01 | [26 empty] | 0
2025-06-21 | 2026 | 2025 | 2025-06-01 | [26 empty] | 0
2025-06-22 | 2026 | 2025 | 2025-06-01 | [26 empty] | 0
2025-06-23 | 2026 | 2025 | 2025-06-01 | [26 empty] | 0
2025-06-24 | 2026 | 2025 | 2025-06-01 | [26 empty] | 0
2025-06-25 | 2026 | 2025 | 2025-06-01 | [26 empty] | 0
2025-06-26 | 2026 | 2025 | 2025-06-01 | [26 empty] | 0
2025-06-27 | 2026 | 2025 | 2025-06-01 | [26 empty] | 0
2025-06-28 | 2026 | 2025 | 2025-06-01 | [26 empty] | 0
2025-06-29 | 2026 | 2025 | 2025-06-01 | [26 empty] | 0
2025-06-30 | 2026 | 2025 | 2025-06-01 | [26 empty] | 0
2025-07-01 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-02 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-03 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-04 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-05 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-06 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-07 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-08 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-09 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-10 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-11 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-12 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-13 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-14 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-15 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-16 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-17 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-18 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-19 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-20 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-21 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-22 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-23 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-24 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-25 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-26 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-27 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-28 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-29 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-30 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-31 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-08-01 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-02 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-03 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-04 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-05 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-06 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-07 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-08 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-09 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-10 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-11 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-12 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-13 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-14 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-15 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-16 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-17 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-18 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-19 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-20 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-21 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-22 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-23 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-24 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-25 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-26 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-27 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-28 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-29 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-30 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-31 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-09-01 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-02 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-03 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-04 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-05 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-06 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-07 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-08 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-09 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-10 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-11 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-12 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-13 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-14 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-15 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-16 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-17 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-18 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-19 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-20 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-21 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-22 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-23 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-24 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-25 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-26 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-27 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-28 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-29 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-30 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-10-01 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-02 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-03 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-04 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-05 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-06 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-07 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-08 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-09 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-10 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-11 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-12 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-13 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-14 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-15 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-16 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-17 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-18 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-19 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-20 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-21 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-22 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-23 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-24 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-25 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-26 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-27 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-28 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-29 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-30 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-31 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-11-01 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-02 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-03 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-04 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-05 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-06 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-07 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-08 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-09 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-10 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-11 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-12 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-13 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-14 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-15 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-16 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-17 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-18 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-19 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-20 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-21 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-22 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-23 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-24 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-25 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-26 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-27 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-28 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-29 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-30 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-12-01 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-02 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-03 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-04 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-05 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-06 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-07 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-08 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-09 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-10 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-11 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-12 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-13 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-14 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-15 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-16 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-17 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-18 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-19 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-20 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-21 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-22 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-23 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-24 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-25 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-26 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-27 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-28 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-29 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-30 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-31 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2026-01-01 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-02 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-03 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-04 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-05 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-06 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-07 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-08 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-09 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-10 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-11 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-12 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-13 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-14 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-15 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-16 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-17 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-18 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-19 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-20 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-21 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-22 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-23 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-24 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-25 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-26 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-27 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-28 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-29 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-30 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-31 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-02-01 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-02 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-03 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-04 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-05 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-06 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-07 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-08 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-09 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-10 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-11 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-12 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-13 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-14 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-15 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-16 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-17 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-18 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-19 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-20 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-21 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-22 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-23 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-24 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-25 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-26 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-27 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-28 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-03-01 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-02 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-03 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-04 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-05 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-06 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-07 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-08 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-09 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-10 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-11 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-12 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-13 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-14 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-15 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-16 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-17 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-18 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-19 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-20 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-21 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-22 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-23 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-24 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-25 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-26 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-27 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-28 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-29 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-30 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-31 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-04-01 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-02 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-03 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-04 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-05 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-06 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-07 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-08 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-09 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-10 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-11 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-12 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-13 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-14 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-15 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-16 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-17 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-18 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-19 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-20 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-21 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-22 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-23 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-24 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-25 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-26 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-27 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-28 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-29 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-30 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-05-01 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-02 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-03 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-04 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-05 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-06 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-07 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-08 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-09 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-10 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-11 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-12 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-13 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-14 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-15 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-16 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-17 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-18 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-19 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-20 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-21 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-22 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-23 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-24 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-25 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-26 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-27 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-28 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-29 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-30 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-31 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-06-01 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-02 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-03 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-04 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-05 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-06 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-07 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-08 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-09 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-10 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-11 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-12 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-13 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-14 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-15 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-16 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-17 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-18 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-19 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-20 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-21 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-22 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-23 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-24 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-25 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-26 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-27 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-28 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-29 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-30 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-07-01 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-02 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-03 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-04 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-05 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-06 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-07 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-08 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-09 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-10 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-11 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-12 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-13 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-14 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-15 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-16 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-17 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-18 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-19 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-20 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-21 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-22 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-23 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-24 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-25 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-26 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-27 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-28 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-29 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-30 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-31 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-08-01 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-02 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-03 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-04 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-05 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-06 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-07 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-08 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-09 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-10 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-11 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-12 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-13 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-14 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-15 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-16 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-17 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-18 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-19 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-20 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-21 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-22 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-23 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-24 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-25 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-26 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-27 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-28 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-29 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-30 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-31 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-09-01 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-02 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-03 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-04 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-05 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-06 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-07 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-08 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-09 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-10 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-11 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-12 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-13 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-14 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-15 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-16 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-17 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-18 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-19 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-20 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-21 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-22 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-23 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-24 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-25 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-26 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-27 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-28 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-29 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-30 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-10-01 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-02 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-03 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-04 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-05 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-06 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-07 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-08 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-09 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-10 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-11 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-12 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-13 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-14 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-15 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-16 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-17 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-18 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-19 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-20 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-21 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-22 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-23 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-24 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-25 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-26 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-27 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-28 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-29 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-30 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-31 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-11-01 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-02 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-03 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-04 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-05 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-06 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-07 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-08 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-09 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-10 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-11 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-12 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-13 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-14 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-15 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-16 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-17 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-18 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-19 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-20 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-21 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-22 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-23 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-24 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-25 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-26 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-27 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-28 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-29 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-30 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-12-01 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-02 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-03 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-04 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-05 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-06 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-07 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-08 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-09 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-10 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-11 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-12 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-13 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-14 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-15 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-16 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-17 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-18 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-19 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-20 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-21 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-22 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-23 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-24 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-25 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-26 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-27 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-28 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-29 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-30 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-31 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2027-01-01 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-02 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-03 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-04 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-05 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-06 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-07 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-08 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-09 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-10 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-11 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-12 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-13 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-14 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-15 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-16 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-17 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-18 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-19 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-20 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-21 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-22 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-23 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-24 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-25 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-26 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-27 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-28 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-29 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-30 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-31 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-02-01 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-02 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-03 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-04 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-05 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-06 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-07 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-08 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-09 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-10 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-11 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-12 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-13 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-14 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-15 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-16 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-17 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-18 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-19 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-20 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-21 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-22 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-23 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-24 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-25 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-26 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-27 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-28 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-03-01 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-02 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-03 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-04 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-05 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-06 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-07 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-08 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-09 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-10 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-11 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-12 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-13 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-14 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-15 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-16 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-17 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-18 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-19 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-20 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-21 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-22 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-23 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-24 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-25 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-26 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-27 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-28 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-29 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-30 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-31 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-04-01 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-02 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-03 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-04 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-05 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-06 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-07 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-08 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-09 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-10 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-11 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-12 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-13 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-14 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-15 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-16 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-17 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-18 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-19 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-20 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-21 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-22 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-23 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-24 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-25 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-26 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-27 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-28 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-29 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-30 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-05-01 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-02 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-03 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-04 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-05 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-06 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-07 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-08 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-09 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-10 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-11 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-12 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-13 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-14 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-15 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-16 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-17 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-18 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-19 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-20 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-21 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-22 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-23 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-24 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-25 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-26 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-27 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-28 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-29 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-30 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-31 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-06-01 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-02 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-03 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-04 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-05 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-06 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-07 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-08 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-09 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-10 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-11 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-12 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-13 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-14 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-15 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-16 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-17 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-18 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-19 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-20 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-21 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-22 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-23 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-24 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-25 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-26 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-27 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-28 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-29 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-30 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-07-01 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-02 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-03 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-04 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-05 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-06 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-07 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-08 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-09 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-10 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-11 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-12 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-13 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-14 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-15 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-16 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-17 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-18 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-19 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-20 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-21 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-22 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-23 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-24 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-25 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-26 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-27 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-28 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-29 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-30 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-31 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-08-01 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-02 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-03 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-04 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-05 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-06 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-07 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-08 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-09 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-10 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-11 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-12 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-13 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-14 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-15 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-16 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-17 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-18 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-19 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-20 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-21 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-22 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-23 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-24 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-25 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-26 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-27 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-28 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-29 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-30 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-31 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-09-01 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-02 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-03 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-04 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-05 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-06 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-07 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-08 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-09 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-10 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-11 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-12 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-13 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-14 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-15 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-16 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-17 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-18 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-19 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-20 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-21 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-22 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-23 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-24 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-25 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-26 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-27 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-28 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-29 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-30 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-10-01 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-02 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-03 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-04 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-05 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-06 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-07 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-08 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-09 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-10 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-11 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-12 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-13 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-14 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-15 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-16 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-17 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-18 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-19 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-20 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-21 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-22 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-23 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-24 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-25 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-26 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-27 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-28 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-29 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-30 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-31 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-11-01 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-02 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-03 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-04 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-05 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-06 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-07 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-08 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-09 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-10 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-11 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-12 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-13 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-14 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-15 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-16 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-17 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-18 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-19 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-20 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-21 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-22 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-23 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-24 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-25 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-26 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-27 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-28 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-29 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-30 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-12-01 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-02 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-03 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-04 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-05 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-06 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-07 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-08 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-09 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-10 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-11 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-12 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-13 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-14 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-15 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-16 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-17 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-18 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-19 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-20 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-21 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-22 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-23 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-24 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-25 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-26 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-27 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-28 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-29 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-30 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-31 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2028-01-01 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-02 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-03 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-04 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-05 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-06 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-07 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-08 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-09 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-10 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-11 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-12 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-13 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-14 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-15 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-16 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-17 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-18 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-19 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-20 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-21 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-22 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-23 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-24 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-25 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-26 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-27 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-28 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-29 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-30 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-31 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-02-01 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-02 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-03 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-04 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-05 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-06 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-07 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-08 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-09 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-10 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-11 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-12 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-13 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-14 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-15 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-16 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-17 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-18 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-19 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-20 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-21 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-22 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-23 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-24 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-25 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-26 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-27 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-28 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-29 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-03-01 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-02 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-03 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-04 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-05 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-06 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-07 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-08 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-09 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-10 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-11 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-12 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-13 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-14 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-15 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-16 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-17 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-18 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-19 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-20 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-21 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-22 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-23 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-24 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-25 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-26 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-27 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-28 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-29 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-30 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-31 | 2028 | 2028 | 2028-03-01 | 2411.487 | 891.6197 | 1879.9699 | 874.2626 | 880.4713 | 636.2265 | 372.8833 | 641.519 | 906.0887 | 2260.394 | 383.091 | 377.6865 | 2175.7978 | 1993.9216 | 1758.4657 | 2234.1107 | 1964.6707 | 2190.6098 | 441.9792 | 670.5095 | 1570.8376 | 1180.1707 | 1761.4244 | 0 | 999.7058 | 1757.046 | 33214.9493
Formulas:
Month Year = [Date]-DAY([Date])+1
Date = [Date, row above]+1

## Input_Raw
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | #REF!
[5 empty] | Energy Generated by individual Turbine | [25 empty] | Wind Speed (M/s) | [30 empty] | Calculated Energy Numbers
Date | Finacial Year | Calendor Year | Month Year | Days | O2_01 | O2_02 | O2_03 | O2_04 | O2_05 | O2_06 | O2_07 | O2_08 | O2_09 | O2_10 | O2_11 | O2_12 | O2_13 | O2_14 | O2_15 | O2_16 | O2_17 | O2_18 | O2_19 | O2_20 | O2_21 | O2_22 | O2_23 | O2_24 | O2_25 | O2_26 | WS_O2_01 | WS_O2_02 | WS_O2_03 | WS_O2_04 | WS_O2_05 | WS_O2_06 | WS_O2_07 | WS_O2_08 | WS_O2_09 | WS_O2_10 | WS_O2_11 | WS_O2_12 | WS_O2_13 | WS_O2_14 | WS_O2_15 | WS_O2_16 | WS_O2_17 | WS_O2_18 | WS_O2_19 | WS_O2_20 | WS_O2_21 | WS_O2_22 | WS_O2_23 | WS_O2_24 | WS_O2_25 | WS_O2_26 | WTG Total Gneration (KWh) | Wind Speed Average cumulative (m/S)2 | Wind Speed Max (m/S) | Rain (mm) | 66 kV_Wind_F1_Export_reading | 66 kV_Wind_F1_Import_reading | 66 kV_Wind_Net_Export (KWh) | 66 kV Line Loss (%) | 66 kV Line Loss (%). | Commissioned Capacity (MW) | Forecasting Penalties (INR) | Expected Power as per power curve. (MWh) | Reactive Energy (MVArH)
2024-03-31 | 2024 | 2024 | 2024-03-01 | 31 | [52 empty] | 0 | [5 empty] | 0 | 0 | #DIV/0! | 24.3
2024-04-01 | 2025 | 2024 | 2024-04-01 | 30 | [10 empty] | 73 | 4314 | 3977 | 390 | [22 empty] | 5.5523 | 5.624 | 4.6688 | 5.3289 | [12 empty] | 8754 | 5.2935 |  |  |  |  | 0 | 8754 | 1 | 24.3
2024-04-02 | 2025 | 2024 | 2024-04-01 | 30 |  |  | 113 | [6 empty] | 5289 | 0 | 0 | 0 | 0 | [14 empty] | 6.6268 | [6 empty] | 5.2324 | 5.4566 | 5.4799 | 5.05 | 5.2578 | [12 empty] | 5402 | 5.5173 |  |  |  |  | 0 | 5402 | 1 | 24.3
2024-04-03 | 2025 | 2024 | 2024-04-01 | 30 |  |  | 0 | [6 empty] | 2654 | 0 | 0 | 0 | 0 | [14 empty] | 6.3787 | [6 empty] | 5.8105 | 6.9149 | 6.1269 | 6.1 | 6.1408 | [12 empty] | 2654 | 6.2453 |  |  |  |  | 0 | 2654 | 1 | 24.3
2024-04-04 | 2025 | 2024 | 2024-04-01 | 30 |  |  | 3564 | [6 empty] | 0 | 0 | 0 | 0 | 0 | [14 empty] | 4.9012 | [6 empty] | 4.95 | 5.998 | 5.2122 | 5.22 | 5.16 | [12 empty] | 3564 | 5.2402 |  |  |  |  | 0 | 3564 | 1 | 24.3
2024-04-05 | 2025 | 2024 | 2024-04-01 | 30 |  |  | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | [14 empty] | 4.1 | [6 empty] | 4.2 | 4 | 4.23 | 4.11 | 4.35 | [12 empty] | 0 | 4.165 |  |  |  |  | 0 | 0 | #DIV/0! | 24.3
2024-04-06 | 2025 | 2024 | 2024-04-01 | 30 |  |  | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | [14 empty] | 4.55 | [6 empty] | 4.67 | 4.5 | 4.3 | 4.44 | 4.56 | [12 empty] | 0 | 4.5033 |  |  |  |  | 0 | 0 | #DIV/0! | 24.3
2024-04-07 | 2025 | 2024 | 2024-04-01 | 30 |  |  | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | [14 empty] | 4.44 | [6 empty] | 4.12 | 4.52 | 4.66 | 4.56 | 4.34 | [12 empty] | 0 | 4.44 |  |  |  |  | 0 | 0 | #DIV/0! | 24.3
2024-04-08 | 2025 | 2024 | 2024-04-01 | 30 |  |  | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | [14 empty] | 2.5931 | [6 empty] | 3.042 | 1.794 | 3.46 | 2.7909 | 2.5625 | [12 empty] | 0 | 2.7071 |  |  |  |  | 0 | 0 | #DIV/0! | 24.3
2024-04-09 | 2025 | 2024 | 2024-04-01 | 30 |  |  | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | [14 empty] | 3.4 | [6 empty] | 3.2 | 3.22 | 3.1 | 3.45 | 3.55 | [12 empty] | 0 | 3.32 |  |  |  |  | 0 | 0 | #DIV/0! | 24.3
2024-04-10 | 2025 | 2024 | 2024-04-01 | 30 |  |  | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | [14 empty] | 3.1 | [6 empty] | 3.45 | 3.3 | 3.5 | 3.23 | 3.33 | [12 empty] | 0 | 3.3183 |  |  |  |  | 0 | 0 | #DIV/0! | 24.3
2024-04-11 | 2025 | 2024 | 2024-04-01 | 30 |  |  | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | [14 empty] | 4.56 | [6 empty] | 4.33 | 4.2 | 4.3 | 4.1 | 4.32 | [12 empty] | 0 | 4.3017 |  |  |  |  | 0 | 0 | #DIV/0! | 24.3
2024-04-12 | 2025 | 2024 | 2024-04-01 | 30 |  |  | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | [14 empty] | 6.67 | [6 empty] | 3.67 | 3.44 | 3.65 | 3.8 | 3.77 | [12 empty] | 0 | 4.1667 |  |  |  |  | 0 | 0 | #DIV/0! | 24.3
2024-04-13 | 2025 | 2024 | 2024-04-01 | 30 |  |  | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | [14 empty] | 3.45 | [6 empty] | 3.11 | 3.1 | 3.22 | 3 | 3.21 | [12 empty] | 0 | 3.1817 |  |  |  |  | 0 | 0 | #DIV/0! | 24.3
2024-04-14 | 2025 | 2024 | 2024-04-01 | 30 |  |  | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | [14 empty] | 5.18 | [6 empty] | 2.11 | 5.44 | 5.34 | 5.4526 | 5.65 | [12 empty] | 0 | 4.8621 |  |  |  |  | 0 | 0 | #DIV/0! | 24.3
2024-04-15 | 2025 | 2024 | 2024-04-01 | 30 | 0 | 0 | 3085 | 0 | 0 | 0 | 0 | 0 | 0 | 2493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 5.7712 | [6 empty] | 6.1135 | 5.46 | 5.55 | 5.78 | 5.7 | [12 empty] | 5578 | 5.7291 |  |  | 5400 | 900 | 4500 | 178 | 3.191% | 24.3
2024-04-16 | 2025 | 2024 | 2024-04-01 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1573 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 6.0147 | [6 empty] | 5.854 | 5.47 | 5.77 | 5.67 | 5.88 | [5 empty] | 5.6948 | [6 empty] | 1573 | 5.7648 |  |  | 1350 | 900 | 450 | 223 | 14.18% | 24.3
2024-04-17 | 2025 | 2024 | 2024-04-01 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 5.334 | [6 empty] | 5.6587 | 5.8 | 5.6 | 5.7 | 5.5 |  | 6.9708 |  |  |  | 5.1172 | [6 empty] | 71 | 5.7101 |  |  | 0 | 900 | -900 | 71 | 100% | 24.3
2024-04-18 | 2025 | 2024 | 2024-04-01 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 5 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 5.9472 | [6 empty] | 4.76 | 4.2212 | 4.65 | 4.55 | 4.89 | 6.1064 | 6.2941 |  |  |  | 6.1128 | [6 empty] | 94 | 5.2813 |  |  | 0 | 1800 | -1800 | 94 | 100% | 24.3
2024-04-19 | 2025 | 2024 | 2024-04-01 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 923 | 433 | 0 | 0 | 0 | 2551 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 6.8899 | [6 empty] | 6.43 | 6.9398 | 6.77 | 6.9 | 6.515 | 6.6946 | 7.1805 |  |  |  | 6.8191 | [6 empty] | 3907 | 6.7932 |  |  | 3600 | 1350 | 2250 | 307 | 7.858% | 24.3
2024-04-20 | 2025 | 2024 | 2024-04-01 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 6.8164 | [6 empty] | 6.32 | 6.9965 | 6.8 | 6.84 | 6.56 | 6.6573 | 6.7843 |  |  |  | 6.906 | [6 empty] | 0 | 6.7423 |  |  | 0 | 450 | -450 | 0 | #DIV/0! | 24.3
2024-04-21 | 2025 | 2024 | 2024-04-01 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 6.1175 | [6 empty] | 6.2827 | 6.103 | 5.78 | 5.88 | 5.9 | 5.67 | 6.0552 |  |  |  | 6.1419 | [6 empty] | 0 | 5.9923 |  |  | 0 | 1350 | -1350 | 0 | #DIV/0! | 24.3
2024-04-22 | 2025 | 2024 | 2024-04-01 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 6.6327 | [6 empty] | 7.3851 | 6.7616 | 6.5 | 6.47 | 6.77 | 6.23 | 6.6863 |  |  |  | 6.6508 | [6 empty] | 0 | 6.6763 |  |  | 0 | 1800 | -1800 | 0 | #DIV/0! | 24.3
2024-04-23 | 2025 | 2024 | 2024-04-01 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 5.6231 | [6 empty] | 6.1746 | 6.162 | 6.11 | 5.4823 | 5.67 | 5.43 | 5.5576 |  |  |  | 5.6795 | [6 empty] | 0 | 5.7655 |  |  | 0 | 1800 | -1800 | 0 | #DIV/0! | 24.3
2024-04-24 | 2025 | 2024 | 2024-04-01 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 6.0854 | [6 empty] | 6.3008 | 5.2 | 5.12 | 5.4641 | 5.34 | 5.8977 | 5.912 |  |  |  | 5.9058 | [6 empty] | 0 | 5.6918 |  |  | 0 | 1800 | -1800 | 0 | #DIV/0! | 24.3
2024-04-25 | 2025 | 2024 | 2024-04-01 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 5.56 | [6 empty] | 6.6567 | 5.43 | 5.44 | 5.4593 | 5.12 | 5.8312 | 5.6453 |  |  |  | 5.7637 | [6 empty] | 0 | 5.6562 |  |  | 0 | 1350 | -1350 | 0 | #DIV/0! | 24.3
2024-04-26 | 2025 | 2024 | 2024-04-01 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 5.09 | [6 empty] | 5.1124 | 5.5 | 5.63 | 5.6117 | 5.55 | 5.43 | 6.6732 |  |  |  | 5.4237 | [6 empty] | 0 | 5.5579 |  |  | 0 | 1350 | -1350 | 0 | #DIV/0! | 24.3
2024-04-27 | 2025 | 2024 | 2024-04-01 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 5.0472 | [6 empty] | 4.89 | 4.34 | 4.78 | 4.8898 | 4.55 | 4.9 | 3.54 |  |  |  | 5.1103 | [6 empty] | 0 | 4.6719 |  |  | 0 | 900 | -900 | 0 | #DIV/0! | 24.3
2024-04-28 | 2025 | 2024 | 2024-04-01 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 6.6808 | [6 empty] | 6.2 | 6.11 | 6.2 | 6.13 | 6.5 | 6.55 | 6.35 |  |  |  | 6.6324 | [6 empty] | 0 | 6.3726 |  |  | 0 | 900 | -900 | 0 | #DIV/0! | 24.3
2024-04-29 | 2025 | 2024 | 2024-04-01 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 7.213 | [6 empty] | 7.22 | 7.4 | 7.1 | 7.1251 | 7.9303 | 7.1 | 7.3 |  |  |  | 7.2 | [6 empty] | 0 | 7.2876 |  |  | 0 | 1350 | -1350 | 0 | #DIV/0! | 24.3
2024-04-30 | 2025 | 2024 | 2024-04-01 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 7.64 | [6 empty] | 5.99 | 5.89 | 5.6 | 6.23 | 7.71 | 5.67 | 5.89 |  |  |  | 5.83 | [6 empty] | 0 | 6.2722 |  |  | 0 | 1350 | -1350 | 0 | #DIV/0! | 24.3
2024-05-01 | 2025 | 2024 | 2024-05-01 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 8.89 | [6 empty] | 7.9 | 7.6 | 7.43 | 7.99 | 8.24 | 7.77 | 7.89 |  |  |  | 8.96 | [6 empty] | 0 | 8.0744 |  |  | 0 | 900 | -900 | 0 | #DIV/0! | 24.3
2024-05-02 | 2025 | 2024 | 2024-05-01 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1399 | 0 | 2604 | 0 | 0 | 0 | 0 | 2215 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 5.1181 | [6 empty] | 4.3583 | 5.2 | 5.12 | 5.47 | 5.3748 | 5.25 | 5.33 |  |  |  | 5.5 | [6 empty] | 6218 | 5.1912 |  |  | 4950 | 900 | 4050 | 1268 | 20.39% | 24.3
2024-05-03 | 2025 | 2024 | 2024-05-01 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6921 | 0 | 4131 | 0 | 0 | 0 | 0 | 9399 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 5.1783 | [6 empty] | 4.9603 | 4.3 | 4.6 | 4.75 | 4.8994 | 4.38 | 4.89 |  |  |  | 4.9 | [6 empty] | 20451 | 4.762 |  |  | 18900 | 450 | 18450 | 1551 | 7.584% | 24.3
2024-05-04 | 2025 | 2024 | 2024-05-01 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11579 | 0 | 0 | 0 | 0 | 0 | 0 | 21731 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 6.7 | [6 empty] | 6.43 | 6.33 | 6.1 | 6.25 | 6.54 | 6.541 | 6.5 |  |  |  | 6.51 | [6 empty] | 33310 | 6.4334 |  |  | 31500 | 0 | 31500 | 1810 | 5.434% | 24.3
2024-05-05 | 2025 | 2024 | 2024-05-01 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3102 | 0 | 0 | 16076 | 2433 | 5640 | 0 | 0 | 0 | 0 | 26391 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 6.9223 | [6 empty] | 6.9485 | 7.9086 | 7.36 | 6.6283 | 6.466 | 6.5501 | 6.45 |  |  |  | 6.94 | [6 empty] | 53642 | 6.9082 |  |  | 51750 | 0 | 51750 | 1892 | 3.527% | 24.3
2024-05-06 | 2025 | 2024 | 2024-05-01 | 31 | 0 | 0 | 3414 | 0 | 0 | 0 | 0 | 0 | 0 | 14375 | 0 | 3722 | 21210 | 9010 | 19936 | 0 | 0 | 0 | 0 | 25565 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 6.4662 | [6 empty] | 6.3276 | 6.7651 | 6.3045 | 6.5502 | 6.4113 | 6.0723 | 7.0785 |  |  |  | 6.6111 | [6 empty] | 97232 | 6.5096 |  |  | 96750 | 0 | 96750 | 482 | 0.4957% | 24.3
2024-05-07 | 2025 | 2024 | 2024-05-01 | 31 | 0 | 0 | 12480 | 0 | 0 | 0 | 0 | 0 | 0 | 11297 | 0 | 13640 | 9035 | 13866 | 10544 | 0 | 0 | 0 | 0 | 15869 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 4.8877 | [6 empty] | 5.0583 | 5.0216 | 4.8995 | 4.8167 | 4.9554 | 5.0077 | 5.3858 |  |  |  | 4.954 | [6 empty] | 86731 | 4.9985 |  |  | 84150 | 450 | 83700 | 2581 | 2.976% | 24.3
2024-05-08 | 2025 | 2024 | 2024-05-01 | 31 | 0 | 0 | 18119 | 0 | 0 | 0 | 0 | 0 | 0 | 16403 | 0 | 20716 | 3846 | 16541 | 19027 | 0 | 0 | 0 | 0 | 23251 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 5.6083 | [6 empty] | 5.6751 | 5.797 | 5.7756 | 5.8744 | 5.8222 | 5.6432 | 6.4698 |  |  |  | 5.9423 | [6 empty] | 117903 | 5.8453 |  |  | 116100 | 450 | 115650 | 1803 | 1.529% | 24.3
2024-05-09 | 2025 | 2024 | 2024-05-01 | 31 | 0 | 0 | 16551 | 0 | 0 | 0 | 0 | 0 | 0 | 19683 | 0 | 23625 | 21965 | 17638 | 18676 | 0 | 0 | 0 | 0 | 25878 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 5.8797 | [6 empty] | 6.4109 | 6.2108 | 6.2832 | 5.9637 | 6.188 | 6.064 | 6.7509 |  |  |  | 6.2892 | [6 empty] | 144016 | 6.2267 |  |  | 141300 | 0 | 141300 | 2716 | 1.886% | 24.3
2024-05-10 | 2025 | 2024 | 2024-05-01 | 31 | 0 | 0 | 18797 | 0 | 0 | 0 | 0 | 0 | 0 | 15301 | 0 | 19756 | 21099 | 18099 | 17672 | 0 | 0 | 0 | 0 | 12966 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 6.0704 | [6 empty] | 6.4626 | 6.4873 | 6.3772 | 6.133 | 6.3923 | 6.3326 | 6.7399 |  |  |  | 6.506 | [6 empty] | 123690 | 6.389 |  |  | 120600 | 0 | 120600 | 3090 | 2.498% | 24.3
2024-05-11 | 2025 | 2024 | 2024-05-01 | 31 | 0 | 0 | 12682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14812 | 13845 | 15990 | 15310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 4.9412 | [6 empty] | 4.9225 | 5.0284 | 5.065 | 4.9214 | 5.1393 | 4.9873 | 5.2224 |  |  |  | 5.0698 | [6 empty] | 72639 | 5.033 |  |  | 70200 | 450 | 69750 | 2439 | 3.358% | 24.3
2024-05-12 | 2025 | 2024 | 2024-05-01 | 31 | 0 | 0 | 14629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16389 | 12961 | 16197 | 16683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 5.307 | [6 empty] | 5.654 | 5.7366 | 5.5112 | 5.4049 | 5.4993 | 5.3936 | 5.8592 |  |  |  | 6.5439 | [6 empty] | 76859 | 5.6566 |  |  | 75150 | 0 | 75150 | 1709 | 2.224% | 24.3
2024-05-13 | 2025 | 2024 | 2024-05-01 | 31 | 0 | 0 | 16437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19059 | 5551 | 18133 | 16930 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 6.1202 | [6 empty] | 5.9674 | 7.0093 | 6.3349 | 6.6901 | 6.3267 | 6.3403 | 7.6846 |  |  |  | 7.3028 | [6 empty] | 76110 | 6.6418 |  |  | 70650 | 0 | 70650 | 5460 | 7.174% | 24.3
2024-05-14 | 2025 | 2024 | 2024-05-01 | 31 | 0 | 0 | 14751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16384 | 958 | 8856 | 15136 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 5.2056 | [6 empty] | 7.469 | 6.0655 | 5.997 | 6.3684 | 6.2993 | 5.9608 | 6.0146 |  |  |  | 6.3114 | [6 empty] | 56125 | 6.188 |  |  | 58500 | 450 | 58050 | -2375 | -4.232% | 24.3
2024-05-15 | 2025 | 2024 | 2024-05-01 | 31 | 0 | 0 | 6148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 616 | 0 | 1464 | 2097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 4.7246 | [6 empty] | 6.5562 | 6.0373 | 5.6 | 5.1 | 5.4 | 6.6184 | 5.2234 |  |  |  | 5.705 | [6 empty] | 10325 | 5.6628 |  |  | 9450 | 450 | 9000 | 875 | 8.475% | 24.3 | 179817.75
2024-05-16 | 2025 | 2024 | 2024-05-01 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1490 | 0 | 2032 | 4059 | 5271 | 5036 | 8942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 7.4657 | [6 empty] | 6.1936 | 7.0469 | 6.1807 | 6.2992 | 6.5712 | 5.7087 | 4.9559 |  |  |  | 5.4529 | [6 empty] | 26830 | 6.2083 |  |  | 25650 | 450 | 25200 | 1180 | 4.398% | 24.3 | 167603.625
2024-05-17 | 2025 | 2024 | 2024-05-01 | 31 | 0 | 0 | 6642 | 0 | 0 | 0 | 0 | 0 | 0 | 15797 | 0 | 11363 | 18259 | 19849 | 18204 | 19585 | 0 | 0 | 0 | 10872 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 6.4033 | [6 empty] | 5.6113 | 6.3395 | 5.4515 | 5.8173 | 5.9269 | 5.6084 | 6.5751 |  |  |  | 6.6207 | [6 empty] | 120571 | 6.0393 |  |  | 117900 | 0 | 117900 | 2671 | 2.215% | 24.3 | 93913.75
2024-05-18 | 2025 | 2024 | 2024-05-01 | 31 | 0 | 0 | 7111 | 0 | 0 | 0 | 0 | 0 | 0 | 15340 | 0 | 7384 | 15281 | 13644 | 12158 | 11490 | 0 | 0 | 0 | 13929 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 4.6798 | [6 empty] | 4.7201 | 5.1606 | 9.3385 | 4.863 | 4.7206 | 4.4924 | 4.5946 |  |  |  | 4.9942 | [6 empty] | 96337 | 5.2849 |  |  | 93150 | 450 | 92700 | 3187 | 3.308% | 24.3 | 10863.5
2024-05-19 | 2025 | 2024 | 2024-05-01 | 31 | 0 | 0 | 29933 | 0 | 0 | 0 | 0 | 0 | 0 | 33498 | 0 | 35297 | 34733 | 36717 | 37499 | 38730 | 0 | 0 | 0 | 38402 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 7.082 | [6 empty] | 7.391 | 7.9508 | 7.5102 | 7.4096 | 7.7371 | 7.5868 | 7.8158 |  |  |  | 7.6217 | [6 empty] | 284809 | 7.5672 |  |  | 281700 | 0 | 281700 | 3109 | 1.092% | 24.3 | 12335.5
2024-05-20 | 2025 | 2024 | 2024-05-01 | 31 | 0 | 0 | 24202 | 0 | 0 | 0 | 0 | 0 | 0 | 29753 | 788 | 29863 | 32617 | 32848 | 28700 | 30957 | 0 | 0 | 0 | 34585 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 6.9724 | [6 empty] | 7.0952 | 7.4003 | 7.1163 | 7.2287 | 7.3286 | 6.8926 | 7.0888 |  |  |  | 7.2652 | [6 empty] | 244313 | 7.1542 |  |  | 239400 | 0 | 239400 | 4913 | 2.011% | 24.3 | 5953.625
2024-05-21 | 2025 | 2024 | 2024-05-01 | 31 | 0 | 0 | 20395 | 0 | 1759 | 0 | 0 | 0 | 2286 | 23338 | 8876 | 23676 | 29166 | 30172 | 28331 | 30204 | 0 | 0 | 0 | 30981 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 6.5058 |  | 5.7 |  |  |  | 6.471 | 6.7326 | 6.5644 | 6.6063 | 6.6723 | 6.8985 | 6.5857 | 6.924 |  |  |  | 6.8497 | [6 empty] | 229184 | 6.5918 |  |  | 224100 | 0 | 224100 | 5084 | 2.218% | 24.3 | 9739.661
2024-05-22 | 2025 | 2024 | 2024-05-01 | 31 | 0 | 0 | 31822 | 0 | 6670 | 0 | 0 | 0 | 10452 | 33573 | 30171 | 29755 | 33573 | 32373 | 34226 | 38712 | 0 | 0 | 0 | 35543 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 7.0002 |  | 7.25 |  |  |  | 6.9176 | 7.3691 | 7.0674 | 7.0894 | 7.2981 | 7.3777 | 7.4026 | 7.8977 |  |  |  | 7.6788 | [6 empty] | 316870 | 7.3044 |  |  | 313650 | 0 | 313650 | 3220 | 1.016% | 29.7 | 10678
2024-05-23 | 2025 | 2024 | 2024-05-01 | 31 | 0 | 0 | 46937 | 0 | 9078 | 0 | 0 | 0 | 24256 | 44184 | 42746 | 40711 | 44324 | 38334 | 42884 | 27872 | 0 | 0 | 0 | 41995 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 8.4697 |  | 8.43 |  |  |  | 8.1649 | 8.3874 | 8.4722 | 8.1751 | 8.3592 | 8.5377 | 8.3119 | 8.3928 |  |  |  | 8.2796 | [6 empty] | 403321 | 8.3619 |  |  | 392400 | 0 | 392400 | 10921 | 2.708% | 29.7 | 10863.5
2024-05-24 | 2025 | 2024 | 2024-05-01 | 31 | 0 | 3466 | 40939 | 0 | 14313 | 0 | 0 | 0 | 24975 | 42697 | 38541 | 41129 | 41632 | 32876 | 42671 | 48261 | 0 | 0 | 0 | 51211 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7.5575 | 8.2895 |  | 8.39 |  |  |  | 8.497 | 8.4778 | 8.3159 | 8.4356 | 8.5158 | 8.7412 | 8.5266 | 8.9723 |  |  |  | 8.857 | [6 empty] | 422711 | 8.4647 |  |  | 418500 | 450 | 418050 | 4211 | 0.9962% | 32.4 | 12335.5
2024-05-25 | 2025 | 2024 | 2024-05-01 | 31 | 0 | 10491 | 32736 | 0 | 8135 | 0 | 0 | 0 | 24813 | 34986 | 32661 | 32397 | 33628 | 35165 | 34128 | 37991 | 0 | 0 | 0 | 38394 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7.1855 | 7.181 |  | 6.6026 |  |  |  | 7.4851 | 7.5015 | 7.1546 | 7.2715 | 7.2858 | 7.5275 | 7.2574 | 7.7285 |  |  |  | 7.6326 | [6 empty] | 355525 | 7.3178 |  |  | 357750 | 0 | 357750 | -2225 | -0.6258% | 32.4 | 5953.625
2024-05-26 | 2025 | 2024 | 2024-05-01 | 31 | 0 | 17650 | 42548 | 0 | 11615 | 0 | 0 | 0 | 34080 | 42227 | 41980 | 37496 | 42157 | 44309 | 44035 | 47333 | 0 | 0 | 0 | 48754 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8.7207 | 8.1254 |  | 8.7443 |  |  |  | 8.256 | 8.1903 | 8.0935 | 8.1353 | 8.2484 | 8.4261 | 8.2691 | 8.7323 |  |  |  | 8.6808 | [6 empty] | 454184 | 8.3852 |  |  | 446400 | 0 | 446400 | 7784 | 1.714% | 32.4 | 9739.661
2024-05-27 | 2025 | 2024 | 2024-05-01 | 31 | 0 | 9245 | 39856 | 0 | 23369 | 0 | 0 | 0 | 33650 | 38602 | 34949 | 39488 | 37592 | 41241 | 40973 | 42037 | 0 | 0 | 0 | 42432 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10.1917 | 9.7687 |  | 10.1229 |  |  |  | 9.5438 | 9.7374 | 9.4172 | 9.8851 | 9.8015 | 9.9654 | 9.7763 | 10.3499 |  |  |  | 10.2036 | [6 empty] | 423434 | 9.897 |  |  | 415800 | 0 | 415800 | 7634 | 1.803% | 32.4 | 17764
2024-05-28 | 2025 | 2024 | 2024-05-01 | 31 | 0 | 8952 | 35241 | 0 | 28088 | 0 | 0 | 0 | 35853 | 42326 | 40475 | 35844 | 12757 | 40536 | 41810 | 42226 | 0 | 0 | 0 | 39949 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11.1379 | 10.2427 |  | 10.7621 |  |  |  | 10.3336 | 10.5457 | 10.3746 | 10.5424 | 10.2835 | 10.5743 | 10.4427 | 10.8007 |  |  |  | 10.3158 | [6 empty] | 404057 | 10.5297 |  |  | 394537 | 0 | 394537 | 9520 | 2.356% | 32.4 | 22892.825
2024-05-29 | 2025 | 2024 | 2024-05-01 | 31 | 0 | 12205 | 59669 | 0 | 28896 | 0 | 0 | 0 | 48123 | 57660 | 55708 | 48961 | 48390 | 56520 | 57663 | 50789 | 0 | 0 | 0 | 52665 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10.4859 | 10.3542 |  | 10.3016 |  |  |  | 10.4427 | 10.3577 | 10.2066 | 10.1568 | 9.9987 | 10.4099 | 10.1474 | 10.017 |  |  |  | 9.8707 | [6 empty] | 577249 | 10.2291 |  |  | 580050 | 0 | 580050 | -2801 | -0.4852% | 32.4 | 5876.625
2024-05-30 | 2025 | 2024 | 2024-05-01 | 31 | 0 | 14229 | 37221 | 0 | 33718 | 0 | 0 | 0 | 33703 | 40056 | 38626 | 38378 | 35282 | 38364 | 39324 | 38252 | 0 | 0 | 0 | 36297 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7.8728 | 7.7585 |  | 7.6871 |  |  |  | 8.009 | 8.079 | 7.8658 | 8.0622 | 7.8295 | 8.0966 | 7.9113 | 7.8738 |  |  |  | 7.704 | [6 empty] | 423450 | 7.8958 |  |  | 418500 | 0 | 418500 | 4950 | 1.169% | 32.4 | 4559.125
2024-05-31 | 2025 | 2024 | 2024-05-01 | 31 | 0 | 23074 | 32431 | 0 | 36777 | 0 | 0 | 0 | 34718 | 33851 | 31532 | 32627 | 26368 | 32773 | 32865 | 30152 | 0 | 0 | 0 | 30255 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7.9383 | 7.4779 |  | 7.8274 |  |  |  | 7.6351 | 7.5079 | 7.2447 | 7.5737 | 7.3305 | 7.5547 | 7.2509 | 7.1868 |  |  |  | 7.2077 | [6 empty] | 377423 | 7.478 |  |  | 369000 | 0 | 369000 | 8423 | 2.232% | 32.4 | 5654.05
2024-06-01 | 2025 | 2024 | 2024-06-01 | 30 | 0 | 28713 | 26239 | 0 | 28916 | 0 | 0 | 0 | 30319 | 28382 | 23116 | 27281 | 28402 | 28892 | 26252 | 15181 | 0 | 0 | 0 | 20302 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7.9166 | 7.3422 |  | 7.8301 |  |  |  | 7.7725 | 7.5183 | 7.3441 | 7.6184 | 7.5099 | 7.7233 | 7.2375 | 6.8445 |  |  |  | 7.3961 | [6 empty] | 311995 | 7.5045 |  |  | 305550 | 0 | 305550 | 6445 | 2.066% | 32.4 | 6181.5
2024-06-02 | 2025 | 2024 | 2024-06-01 | 30 | 0 | 15271 | 15044 | 0 | 13516 | 0 | 0 | 0 | 14635 | 15272 | 15884 | 15857 | 12863 | 15710 | 15504 | 15593 | 0 | 0 | 0 | 16028 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5.0985 | 5.116 |  | 5.0081 |  |  |  | 5.1005 | 6.4632 | 5.2201 | 5.3447 | 5.186 | 5.4254 | 6.4025 | 5.2855 |  |  |  | 5.1967 | [6 empty] | 181177 | 5.4039 |  |  | 176400 | 0 | 176400 | 4777 | 2.637% | 32.4 | 10312.8
2024-06-03 | 2025 | 2024 | 2024-06-01 | 30 | 0 | 24696 | 19873 | 0 | 21863 | 0 | 0 | 0 | 20868 | 22556 | 20704 | 21371 | 17474 | 20942 | 21324 | 22155 | 0 | 0 | 0 | 14826 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6.1365 | 5.969 |  | 6.096 |  |  |  | 5.9508 | 6.0904 | 5.8876 | 6.1201 | 5.7163 | 6.0378 | 5.8442 | 7.4401 |  |  |  | 6.9879 | [6 empty] | 248652 | 6.1897 |  |  | 242550 | 0 | 242550 | 6102 | 2.454% | 32.4 | 4383.625
2024-06-04 | 2025 | 2024 | 2024-06-01 | 30 | 0 | 24485 | 18831 | 0 | 15509 | 0 | 0 | 0 | 21294 | 24044 | 12859 | 18099 | 12518 | 24738 | 24561 | 25898 | 0 | 0 | 0 | 26548 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8.3205 | 7.4861 |  | 7.7881 |  |  |  | 7.9763 | 6.5745 | 7.4129 | 7.8683 | 6.4996 | 6.7512 | 6.5129 | 6.6784 |  |  |  | 6.694 | [6 empty] | 249384 | 7.2136 |  |  | 245250 | 0 | 245250 | 4134 | 1.658% | 32.4 | 6866.625
2024-06-05 | 2025 | 2024 | 2024-06-01 | 30 | 0 | 25114 | 20788 | 0 | 23248 | 0 | 0 | 0 | 26096 | 26136 | 25257 | 20583 | 22099 | 26165 | 24643 | 28499 | 0 | 0 | 0 | 29541 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7.3494 | 7.4931 |  | 7.2266 |  |  |  | 7.0838 | 7.2628 | 7.0108 | 7.5992 | 6.9158 | 7.3032 | 6.938 | 7.0234 |  |  |  | 7.0994 | [6 empty] | 298169 | 7.1921 |  |  | 294300 | 0 | 294300 | 3869 | 1.298% | 32.4 | 1707.65
2024-06-06 | 2025 | 2024 | 2024-06-01 | 30 | 0 | 25446 | 21245 | 0 | 24047 | 0 | 0 | 0 | 21715 | 20742 | 19566 | 21134 | 20866 | 22062 | 22299 | 22367 | 0 | 0 | 0 | 22333 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6.2787 | 5.9753 |  | 6.2381 |  |  |  | 6.1349 | 6.2865 | 5.9849 | 6.1771 | 5.9985 | 6.2666 | 6.1187 | 6.2285 |  |  |  | 6.1033 | [6 empty] | 263822 | 6.1493 |  |  | 256950 | 0 | 256950 | 6872 | 2.605% | 32.4 | 3374.275
2024-06-07 | 2025 | 2024 | 2024-06-01 | 30 | 0 | 26436 | 25281 | 0 | 18980 | 0 | 0 | 0 | 24935 | 21936 | 24138 | 23806 | 15951 | 22191 | 21721 | 23148 | 0 | 0 | 0 | 24985 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6.169 | 6.1238 |  | 6.2356 |  |  |  | 6.1706 | 6.0163 | 6.0713 | 6.2152 | 6.0144 | 6.0802 | 5.8435 | 6.255 |  |  |  | 6.1485 | [6 empty] | 273508 | 6.1119 |  |  | 266850 | 450 | 266400 | 6658 | 2.434% | 32.4 | 8902
2024-06-08 | 2025 | 2024 | 2024-06-01 | 30 | 0 | 19466 | 17060 | 0 | 18794 | 0 | 0 | 0 | 15182 | 15337 | 17214 | 15264 | 16333 | 15948 | 15921 | 15543 | 0 | 0 | 0 | 17964 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7.3314 | 5.0963 |  | 6.969 |  |  |  | 5.1657 | 4.9662 | 5.1689 | 5.0327 | 5.1193 | 5.1097 | 4.9399 | 5.1715 |  |  |  | 5.2018 | [6 empty] | 200026 | 5.4394 |  |  | 195300 | 900 | 194400 | 4726 | 2.363% | 32.4 | 19767.625
2024-06-09 | 2025 | 2024 | 2024-06-01 | 30 | 0 | 10389 | 16304 | 0 | 7504 | 0 | 0 | 0 | 16451 | 16471 | 17228 | 16191 | 16667 | 16891 | 15799 | 21416 | 0 | 0 | 0 | 24399 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7.5333 | 6.0354 |  | 7.521 |  |  |  | 5.9662 | 6.1939 | 5.9832 | 6.0065 | 5.964 | 6.3098 | 6.1606 | 6.4268 |  |  |  | 6.757 | [6 empty] | 195710 | 6.4048 |  |  | 191700 | 0 | 191700 | 4010 | 2.049% | 32.4 | 10182.85
2024-06-10 | 2025 | 2024 | 2024-06-01 | 30 | 0 | 9742 | 21923 | 0 | 0 | 0 | 0 | 0 | 19827 | 20912 | 22583 | 21394 | 20606 | 20787 | 20828 | 23479 | 0 | 0 | 0 | 24585 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8.0751 | 5.9467 |  | 5.64 |  |  |  | 5.96 | 6.3614 | 6.1167 | 6.2677 | 6.1001 | 6.1747 | 5.8781 | 6.2255 |  |  |  | 6.2914 | [6 empty] | 226666 | 6.2531 |  |  | 221850 | 0 | 221850 | 4816 | 2.125% | 32.4 | 30207
2024-06-11 | 2025 | 2024 | 2024-06-01 | 30 | 0 | 28087 | 29860 | 0 | 0 | 0 | 0 | 0 | 38083 | 35243 | 35851 | 38891 | 37012 | 37472 | 39598 | 43579 | 0 | 0 | 0 | 45343 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8.7293 | 8.075 |  | 8 |  |  |  | 8.2034 | 7.9909 | 7.9324 | 8.1771 | 7.9337 | 8.2055 | 8.0882 | 8.3702 |  |  |  | 8.3849 | [6 empty] | 409019 | 8.1742 |  |  | 400950 | 0 | 400950 | 8069 | 1.973% | 32.4 | 24202
2024-06-12 | 2025 | 2024 | 2024-06-01 | 30 | 0 | 14727 | 31052 | 0 | 8056 | 0 | 0 | 0 | 27774 | 28483 | 28915 | 33316 | 24954 | 30056 | 29690 | 41006 | 0 | 0 | 0 | 38803 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8.0812 | 7.5432 |  | 9.4339 |  |  |  | 7.6619 | 7.8413 | 7.3174 | 7.7763 | 7.4257 | 7.7633 | 7.5775 | 8.1292 |  |  |  | 7.9551 | [6 empty] | 336832 | 7.8755 |  |  | 330750 | 0 | 330750 | 6082 | 1.806% | 32.4 | 9383.875
2024-06-13 | 2025 | 2024 | 2024-06-01 | 30 | 0 | 23446 | 18757 | 0 | 22955 | 0 | 0 | 0 | 12279 | 24027 | 22548 | 19531 | 21059 | 23181 | 22895 | 33841 | 0 | 0 | 0 | 31901 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7.7475 | 7.2515 |  | 7.7536 |  |  |  | 7.5018 | 7.6077 | 7.2664 | 7.6159 | 7.2003 | 7.6681 | 7.4023 | 7.5323 |  |  |  | 7.2701 | [6 empty] | 276420 | 7.4848 |  |  | 270450 | 0 | 270450 | 5970 | 2.16% | 32.4 | 3111.25
2024-06-14 | 2025 | 2024 | 2024-06-01 | 30 | 2559 | 28861 | 27983 | 0 | 26887 | 0 | 0 | 0 | 20681 | 29963 | 27566 | 28089 | 26079 | 28711 | 28922 | 28412 | 0 | 0 | 0 | 28339 | 0 | 0 | 0 | 0 | 0 | 0 | 6.23 | 6.9106 | 6.9003 |  | 6.9218 |  |  |  | 6.8033 | 7.1412 | 6.8301 | 7.0183 | 6.8719 | 7.1213 | 6.9218 | 6.8215 |  |  |  | 6.8561 | [6 empty] | 333052 | 6.873 |  |  | 325350 | 0 | 325350 | 7702 | 2.313% | 32.4 | 9832.35
2024-06-15 | 2025 | 2024 | 2024-06-01 | 30 | 7693 | 15914 | 13737 | 0 | 15082 | 0 | 0 | 0 | 10265 | 15112 | 14666 | 15231 | 10399 | 15266 | 14290 | 13620 | 0 | 0 | 0 | 15028 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1 | 5.4046 | 5.5069 |  | 5.3482 |  |  |  | 5.6406 | 5.4997 | 5.3157 | 5.4826 | 5.2758 | 5.4996 | 5.2644 | 5.2592 |  |  |  | 5.4471 | [6 empty] | 176303 | 5.388 |  |  | 172350 | 0 | 172350 | 3953 | 2.242% | 35.1 | 22705.3
2024-06-16 | 2025 | 2024 | 2024-06-01 | 30 | 10788 | 16062 | 13339 | 0 | 15915 | 0 | 0 | 0 | 13440 | 14122 | 14545 | 13623 | 12625 | 13948 | 13812 | 11694 | 0 | 0 | 0 | 14099 | 0 | 0 | 0 | 0 | 0 | 0 | 5.17 | 5.1512 | 4.9131 |  | 5.2404 |  |  |  | 5.0977 | 5.07 | 5.1265 | 5.0678 | 4.9985 | 5.2881 | 4.9594 | 4.7735 |  |  |  | 5.1985 | [6 empty] | 178012 | 5.0811 |  |  | 173250 | 0 | 173250 | 4762 | 2.675% | 35.1 | 20490.875
2024-06-17 | 2025 | 2024 | 2024-06-01 | 30 | 10667 | 13534 | 14728 | 0 | 13188 | 0 | 0 | 0 | 15618 | 14845 | 14315 | 14327 | 14275 | 13120 | 13751 | 9782 | 0 | 0 | 0 | 13306 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9 | 4.8967 | 5.3131 |  | 4.9858 |  |  |  | 5.5196 | 5.3859 | 5.332 | 5.4856 | 5.2874 | 5.3801 | 5.1356 | 5.1862 |  |  |  | 5.3172 | [6 empty] | 175456 | 5.2404 |  |  | 171900 | 0 | 171900 | 3556 | 2.027% | 35.1 | 6092.75
2024-06-18 | 2025 | 2024 | 2024-06-01 | 30 | 14420 | 16068 | 26711 | 0 | 27503 | 0 | 0 | 0 | 28407 | 27545 | 27961 | 24789 | 26850 | 28512 | 27624 | 18116 | 0 | 0 | 0 | 20284 | 0 | 0 | 0 | 0 | 0 | 0 | 8.704 | 6.7973 | 6.6403 |  | 6.5819 |  |  |  | 6.7873 | 6.6365 | 6.7019 | 6.6048 | 6.6152 | 6.8876 | 6.5767 | 5.8705 |  |  |  | 6.3039 | [6 empty] | 314790 | 6.7468 |  |  | 316350 | 0 | 316350 | -1560 | -0.4956% | 35.1 | 10538.225
2024-06-19 | 2025 | 2024 | 2024-06-01 | 30 | 29406 | 32898 | 31322 | 0 | 30406 | 0 | 0 | 0 | 31507 | 24360 | 28155 | 29996 | 29064 | 32635 | 32722 | 30229 | 0 | 0 | 0 | 32247 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2505 | 7.2818 | 7.1468 |  | 7.2597 |  |  |  | 7.3776 | 7.3222 | 7.2727 | 7.4113 | 7.2903 | 7.4812 | 7.4145 | 6.9169 |  |  |  | 7.2422 | [6 empty] | 394947 | 7.2821 |  |  | 385200 | 0 | 385200 | 9747 | 2.468% | 35.1 | 10824.5
2024-06-20 | 2025 | 2024 | 2024-06-01 | 30 | 35101 | 36714 | 29917 | 0 | 34347 | 0 | 0 | 0 | 34912 | 35810 | 35020 | 35397 | 37785 | 37308 | 30898 | 29454 | 0 | 0 | 0 | 28987 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7 | 7.8 | 7.52 |  | 7.6 |  |  |  | 7.7 | 7.6 | 7.5 | 7.7 | 7.7 | 7.8 | 7.5 | 7.2 |  |  |  | 7.3 | [6 empty] | 441650 | 7.5862 |  |  | 430650 | 0 | 430650 | 11000 | 2.491% | 35.1 | 4930.3765
2024-06-21 | 2025 | 2024 | 2024-06-01 | 30 | 30761 | 33889 | 38666 | 0 | 32669 | 0 | 0 | 0 | 38679 | 41203 | 39382 | 37889 | 37875 | 39770 | 40000 | 28284 | 0 | 0 | 0 | 31110 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2802 | 6.3826 | 7.9972 |  | 7.3024 |  |  |  | 8.1337 | 8.3467 | 8.0085 | 8.0437 | 7.9767 | 8.2756 | 8.141 | 7.1569 |  |  |  | 7.5629 | [6 empty] | 470177 | 7.6622 |  |  | 459450 | 0 | 459450 | 10727 | 2.281% | 35.1 | 19247.7528
2024-06-22 | 2025 | 2024 | 2024-06-01 | 30 | 23085 | 25778 | 20298 | 0 | 24084 | 0 | 0 | 0 | 22988 | 20033 | 18918 | 20874 | 18489 | 19727 | 21604 | 19188 | 0 | 0 | 0 | 19073 | 2126 | 0 | 0 | 0 | 0 | 0 | 5.8945 | 6.1688 | 5.9472 |  | 6.3267 |  |  |  | 6.2508 | 6.1863 | 5.8749 | 6.1225 | 5.9248 | 6.1092 | 6.1762 | 5.9877 |  |  |  | 6.1544 | 5.9788 | [5 empty] | 276265 | 6.0788 |  |  | 269100 | 0 | 269100 | 7165 | 2.594% | 35.1 | 26775.5
2024-06-23 | 2025 | 2024 | 2024-06-01 | 30 | 14127 | 17928 | 12625 | 0 | 17361 | 1584 | 0 | 0 | 13689 | 10918 | 13120 | 12000 | 12950 | 12766 | 12933 | 15139 | 0 | 0 | 0 | 14759 | 7701 | 0 | 0 | 0 | 0 | 0 | 3.5616 | 3.8324 | 5.6353 |  | 6.1331 | 5.8 |  |  | 5.7683 | 5.5391 | 5.5581 | 5.7003 | 5.571 | 5.6523 | 5.6699 | 5.9563 |  |  |  | 5.9568 | 5.397 | [5 empty] | 189600 | 5.4488 |  |  | 185400 | 0 | 185400 | 4200 | 2.215% | 35.1 | 16383.375
2024-06-24 | 2025 | 2024 | 2024-06-01 | 30 | 4949 | 7701 | 4340 | 0 | 7475 | 3842 | 0 | 0 | 4790 | 4184 | 4062 | 4773 | 3822 | 4413 | 4842 | 4822 | 0 | 0 | 0 | 3774 | 4511 | 0 | 0 | 0 | 0 | 0 | 3.9803 | 4.0515 | 3.3343 |  | 3.8518 | 3.3 |  |  | 3.4722 | 3.4422 | 3.3094 | 3.6029 | 3.3562 | 3.5013 | 3.4258 | 3.426 |  |  |  | 3.2998 | 3.2934 | [5 empty] | 72300 | 3.5098 |  |  | 70650 | 0 | 70650 | 1650 | 2.282% | 35.1 | 7625.25
2024-06-25 | 2025 | 2024 | 2024-06-01 | 30 | 7293 | 5407 | 6716 | 0 | 7685 | 6778 | 0 | 0 | 6764 | 7180 | 6790 | 6045 | 4762 | 6317 | 7220 | 8735 | 0 | 1410 | 0 | 8370 | 7653 | 0 | 0 | 0 | 0 | 0 | 4.0552 | 3.8645 | 3.756 |  | 4.1783 | 4 |  |  | 3.8757 | 4.0278 | 3.769 | 4.0263 | 3.7997 | 3.8705 | 3.8981 | 4.2656 |  | 3.5 |  | 4.2759 | 4.2233 | [5 empty] | 105125 | 3.9616 |  |  | 101700 | 0 | 101700 | 3425 | 3.258% | 37.8 | 21849.625
2024-06-26 | 2025 | 2024 | 2024-06-01 | 30 | 7246 | 7363 | 7780 | 0 | 6755 | 7630 | 0 | 0 | 7061 | 2044 | 8016 | 7094 | 8161 | 8220 | 8133 | 9010 | 0 | 5151 | 0 | 9352 | 9892 | 0 | 0 | 0 | 0 | 0 | 4.8858 | 4.4535 | 3.8442 |  | 3.9011 | 3.9 |  |  | 3.8068 | 3.8792 | 3.8997 | 4.0093 | 3.8762 | 4.021 | 3.9749 | 4.0592 |  | 4 |  | 4.1183 | 4.0954 | [5 empty] | 118908 | 4.0453 |  |  | 114750 | 900 | 113850 | 4158 | 3.497% | 37.8 | 6261.75
2024-06-27 | 2025 | 2024 | 2024-06-01 | 30 | 7000 | 9592 | 12102 | 0 | 10992 | 10869 | 0 | 0 | 12959 | 11605 | 11781 | 13621 | 13207 | 12467 | 11115 | 12788 | 0 | 10869 | 0 | 13399 | 13478 | 0 | 0 | 0 | 0 | 0 | 5.5173 | 5.1433 | 4.7485 |  | 4.68 | 5.8738 |  |  | 4.9553 | 4.899 | 4.7318 | 5.0858 | 4.8891 | 5 | 4.898 | 4.9601 |  | 5.8738 |  | 5.0697 | 5.027 | [5 empty] | 187844 | 5.0845 |  |  | 183150 | 450 | 182700 | 4694 | 2.499% | 40.5 | 21325.625
2024-06-28 | 2025 | 2024 | 2024-06-01 | 30 | 15895 | 14944 | 17168 | 0 | 13441 | 18876 | 0 | 0 | 16566 | 18436 | 18403 | 18645 | 19080 | 18427 | 18678 | 18055 | 0 | 18876 | 0 | 15259 | 18191 | 0 | 0 | 0 | 0 | 0 | 6.8247 | 6.8579 | 5.5044 |  | 5.056 | 6.1765 |  |  | 5.5752 | 5.9428 | 5.6391 | 5.8356 | 5.7458 | 5.8664 | 5.7621 | 5.9055 |  | 6.1765 |  | 5.7336 | 6.1502 | [5 empty] | 278940 | 5.922 |  |  | 270000 | 0 | 270000 | 8940 | 3.205% | 43.2 | 27084.75
2024-06-29 | 2025 | 2024 | 2024-06-01 | 30 | 24593 | 26619 | 27154 | 0 | 25153 | 31808 | 0 | 0 | 26399 | 24943 | 27495 | 26527 | 26981 | 26641 | 28079 | 29407 | 0 | 31808 | 0 | 13283 | 27255 | 0 | 0 | 0 | 0 | 0 | 6.4767 | 6.4076 | 6.9059 |  | 6.7987 | 7.346 |  |  | 6.9386 | 6.9496 | 6.9851 | 6.9802 | 7.0364 | 7.0615 | 7.1796 | 7.0465 |  | 7.346 |  | 6.6737 | 6.895 | [5 empty] | 424145 | 6.9392 |  |  | 417600 | 0 | 417600 | 6545 | 1.543% | 43 | 39547.0007
2024-06-30 | 2025 | 2024 | 2024-06-01 | 30 | 23045 | 23606 | 23574 | 0 | 22295 | 23987 | 0 | 0 | 24276 | 24468 | 26820 | 25606 | 26444 | 24049 | 25074 | 22482 | 0 | 23987 | 0 | 19613 | 22106 | 0 | 0 | 0 | 0 | 0 | 7.6226 | 7.7405 | 6.3884 |  | 6.356 | 6.6026 |  |  | 6.5958 | 6.6457 | 6.7196 | 6.7085 | 6.673 | 6.6264 | 6.6076 | 6.3774 |  | 6.6026 |  | 6.1411 | 6.3354 | [5 empty] | 381432 | 6.6714 |  |  | 375300 | 0 | 375300 | 6132 | 1.608% | 43 | 10211.875
2024-07-01 | 2025 | 2024 | 2024-07-01 | 31 | 35536 | 37742 | 34150 | 0 | 20054 | 42245 | 0 | 0 | 35105 | 35591 | 36788 | 36617 | 34853 | 35280 | 35827 | 35148 | 0 | 42245 | 0 | 37386 | 40180 | 0 | 0 | 0 | 0 | 0 | 9.8115 | 9.7263 | 7.3998 |  | 7.47 | 8.2865 |  |  | 7.5753 | 7.6795 | 7.6741 | 7.7531 | 7.666 | 7.731 | 7.6706 | 7.7292 |  | 8.2865 |  | 7.8434 | 8.0059 | [5 empty] | 574747 | 8.0193 |  |  | 558450 | 0 | 558450 | 16297 | 2.836% | 43 | 56303.2002
2024-07-02 | 2025 | 2024 | 2024-07-01 | 31 | 53201 | 51800 | 42311 | 0 | 49143 | 59894 | 0 | 0 | 52293 | 49710 | 54774 | 52024 | 52054 | 50056 | 49259 | 53926 | 0 | 55815 | 0 | 36566 | 58821 | 0 | 0 | 0 | 0 | 0 | 8.5454 | 8.3317 | 9.7965 |  | 9.7378 | 9.8694 |  |  | 9.7632 | 9.5228 | 9.8286 | 9.8461 | 9.7136 | 9.9361 | 9.5904 | 9.7377 |  | 9.7412 |  | 9.7552 | 9.9406 | [5 empty] | 821647 | 9.6035 |  |  | 798750 | 0 | 798750 | 22897 | 2.787% | 43 | 8334.25
2024-07-03 | 2025 | 2024 | 2024-07-01 | 31 | 47115 | 25104 | 23324 | 0 | 44872 | 49266 | 0 | 0 | 46454 | 39456 | 44563 | 39356 | 22321 | 41710 | 44658 | 43882 | 0 | 49280 | 0 | 29394 | 50496 | 0 | 0 | 0 | 0 | 0 | 6.9954 | 6.834 | 8.3931 |  | 8.3203 | 8.7334 |  |  | 8.5265 | 7.9765 | 8.5327 | 8.1609 | 8.2553 | 8.3645 | 8.281 | 8.2703 |  | 8.479 |  | 8.3229 | 8.7442 | [5 empty] | 641251 | 8.1994 |  |  | 625050 | 0 | 625050 | 16201 | 2.526% | 43 | 7388.5812
2024-07-04 | 2025 | 2024 | 2024-07-01 | 31 | 28506 | 4664 | 4005 | 0 | 27881 | 30111 | 0 | 0 | 29124 | 24730 | 28787 | 25735 | 24649 | 26935 | 24093 | 19711 | 0 | 29566 | 0 | 24099 | 30870 | 0 | 0 | 0 | 0 | 0 | 5.8634 | 5.8287 | 6.9285 |  | 6.8482 | 7.111 |  |  | 7.0515 | 6.7067 | 6.9311 | 6.7624 | 6.5141 | 6.9631 | 6.4824 | 6.0826 |  | 6.8338 |  | 6.6001 | 7.086 | [5 empty] | 383466 | 6.6621 |  |  | 375750 | 0 | 375750 | 7716 | 2.012% | 43 | 4954.25
2024-07-05 | 2025 | 2024 | 2024-07-01 | 31 | 19552 | 21006 | 9677 | 0 | 20022 | 19622 | 0 | 0 | 20363 | 19576 | 19964 | 19791 | 7732 | 19258 | 18404 | 18571 | 0 | 19935 | 0 | 16702 | 18412 | 0 | 0 | 0 | 0 | 0 | 7.9445 | 8.0812 | 5.7503 |  | 5.8183 | 6.0041 |  |  | 5.8919 | 5.9394 | 5.8777 | 5.9108 | 5.9594 | 5.9616 | 5.7003 | 5.741 |  | 5.7805 |  | 5.6788 | 5.8731 | [5 empty] | 288587 | 6.1196 |  |  | 281700 | 450 | 281250 | 6887 | 2.386% | 43 | 8514.5
2024-07-06 | 2025 | 2024 | 2024-07-01 | 31 | 39233 | 41534 | 96488 | 0 | 41294 | 31192 | 0 | 0 | 42503 | 32945 | 36550 | 35811 | 25297 | 35379 | 31840 | 24700 | 0 | 29548 | 0 | 27183 | 26617 | 0 | 0 | 0 | 0 | 0 | 7.742 | 7.5167 | 7.771 |  | 8.0776 | 7.3087 |  |  | 8.1908 | 7.4553 | 7.6009 | 7.6497 | 7.3989 | 7.6922 | 7.2002 | 6.6079 |  | 6.9441 |  | 6.9671 | 7.185 | [5 empty] | 598114 | 7.4568 |  |  | 522000 | 0 | 522000 | 76114 | 12.73% | 43 | 6368.125
2024-07-07 | 2025 | 2024 | 2024-07-01 | 31 | 35306 | 27535 | 34811 | 0 | 36020 | 41710 | 0 | 0 | 35312 | 34346 | 35713 | 34348 | 32763 | 34913 | 34800 | 35188 | 0 | 40003 | 0 | 30706 | 43252 | 0 | 0 | 0 | 0 | 0 | 5.1551 | 5.1882 | 7.5703 |  | 7.6894 | 8.1748 |  |  | 7.7597 | 7.6421 | 7.7221 | 7.5813 | 7.4287 | 7.8676 | 7.6066 | 7.5563 |  | 7.8938 |  | 7.8158 | 8.237 | [5 empty] | 566726 | 7.4306 |  |  | 553500 | 0 | 553500 | 13226 | 2.334% | 43 | 6279.75
2024-07-08 | 2025 | 2024 | 2024-07-01 | 31 | 12717 | 15517 | 15282 | 0 | 14508 | 14234 | 0 | 0 | 14991 | 14293 | 15026 | 15035 | 11453 | 14398 | 11781 | 13428 | 0 | 14382 | 0 | 13358 | 14622 | 0 | 0 | 0 | 0 | 0 | 4.9117 | 5.0644 | 5.325 |  | 5.116 | 5.4909 |  |  | 5.3471 | 5.3333 | 5.3242 | 5.4913 | 5.1851 | 5.362 | 5.3944 | 5.1816 |  | 5.1989 |  | 5.2124 | 5.3735 | [5 empty] | 225025 | 5.2695 |  |  | 219600 | 0 | 219600 | 5425 | 2.411% | 43 | 2218.75
2024-07-09 | 2025 | 2024 | 2024-07-01 | 31 | 11185 | 14087 | 10057 | 0 | 13402 | 11728 | 0 | 0 | 10664 | 10061 | 10651 | 11050 | 10070 | 10711 | 9496 | 10743 | 0 | 11209 | 0 | 11528 | 10892 | 0 | 0 | 0 | 0 | 0 | 4.3038 | 4.2057 | 4.6769 |  | 5.0373 | 4.9805 |  |  | 4.7755 | 4.702 | 4.7408 | 4.9801 | 4.6969 | 5.0049 | 4.9113 | 4.7872 |  | 4.7536 |  | 4.9257 | 4.7437 | [5 empty] | 177534 | 4.7641 |  |  | 172350 | 0 | 172350 | 5184 | 2.92% | 43 | 6154.625
2024-07-10 | 2025 | 2024 | 2024-07-01 | 31 | 9688 | 9368 | 8906 | 0 | 9266 | 11058 | 0 | 0 | 8429 | 6942 | 9268 | 6518 | 8290 | 8998 | 9160 | 8787 | 0 | 10629 | 0 | 9632 | 10984 | 0 | 0 | 0 | 0 | 0 | 5.9728 | 6.1967 | 4.2631 |  | 4.3144 | 4.621 |  |  | 4.305 | 4.3222 | 4.3003 | 4.4195 | 4.215 | 4.3955 | 4.2459 | 4.2717 |  | 4.3626 |  | 4.3488 | 4.5299 | [5 empty] | 145923 | 4.5678 |  |  | 142650 | 1350 | 141300 | 3273 | 2.243% | 43 | 5647.5
2024-07-11 | 2025 | 2024 | 2024-07-01 | 31 | 12249 | 8361 | 15116 | 0 | 16031 | 28848 | 0 | 0 | 15302 | 10355 | 14764 | 15605 | 13798 | 15554 | 15907 | 26929 | 0 | 27787 | 0 | 24003 | 27104 | 0 | 0 | 0 | 0 | 0 | 8.4552 | 8.7197 | 5.9328 |  | 6.2167 | 6.9487 |  |  | 6.0982 | 6.1093 | 5.8966 | 6.1137 | 5.7696 | 6.1904 | 6.0622 | 6.6918 |  | 6.6178 |  | 6.5475 | 6.6898 | [5 empty] | 287713 | 6.5663 |  |  | 281700 | 0 | 281700 | 6013 | 2.09% | 43 | 14744.125
2024-07-12 | 2025 | 2024 | 2024-07-01 | 31 | 26908 | 31666 | 15943 | 0 | 25534 | 45397 | 0 | 0 | 29486 | 31545 | 10343 | 32905 | 31365 | 23845 | 27533 | 46052 | 0 | 44442 | 0 | 44492 | 46546 | 0 | 0 | 0 | 0 | 0 | 8.2432 | 8.4378 | 8.3885 |  | 8.7582 | 8.444 |  |  | 8.4578 | 8.2496 | 8.423 | 8.6308 | 8.2741 | 8.6749 | 8.1634 | 8.6067 |  | 8.2133 |  | 8.5249 | 8.5046 | [5 empty] | 514002 | 8.4372 |  |  | 500850 | 0 | 500850 | 13152 | 2.559% | 43 | 18066.7497
2024-07-13 | 2025 | 2024 | 2024-07-01 | 31 | 38667 | 41501 | 37972 | 0 | 41471 | 35323 | 0 | 0 | 38897 | 22536 | 30487 | 38420 | 33084 | 36236 | 34136 | 34039 | 0 | 33833 | 0 | 34202 | 37055 | 0 | 0 | 0 | 0 | 0 | 6.9464 | 7.0989 | 8.0871 |  | 8.4773 | 8.2375 |  |  | 8.2777 | 8.2269 | 7.954 | 8.2478 | 7.6706 | 8.0853 | 7.8529 | 8.1079 |  | 7.9994 |  | 7.981 | 8.2577 | [5 empty] | 567859 | 7.9693 |  |  | 553500 | 0 | 553500 | 14359 | 2.529% | 43 | 33194.8757
2024-07-14 | 2025 | 2024 | 2024-07-01 | 31 | 26272 | 29200 | 25783 | 0 | 28126 | 33681 | 0 | 0 | 24937 | 25338 | 26337 | 27214 | 24618 | 26714 | 26374 | 31891 | 0 | 32198 | 0 | 31011 | 30264 | 0 | 0 | 0 | 0 | 0 | 4.8525 | 5.0935 | 6.7651 |  | 7.0419 | 7.4456 |  |  | 6.866 | 7.6386 | 6.8335 | 7.0443 | 6.75 | 7.0678 | 6.8763 | 7.2149 |  | 7.0994 |  | 7.2039 | 7.0588 | [5 empty] | 449958 | 6.8033 |  |  | 440550 | 0 | 440550 | 9408 | 2.091% | 43 | 2552.875
2024-07-15 | 2025 | 2024 | 2024-07-01 | 31 | 12003 | 15375 | 10458 | 0 | 13804 | 15223 | 0 | 0 | 11655 | 9369 | 11760 | 12182 | 11161 | 11894 | 12957 | 13801 | 0 | 12584 | 0 | 13426 | 10073 | 0 | 0 | 0 | 0 | 0 | 4.8779 | 4.7239 | 4.8133 |  | 4.9926 | 5.3751 |  |  | 4.9337 | 5.1841 | 4.7622 | 4.9532 | 4.721 | 5.0562 | 4.8951 | 4.9874 |  | 4.932 |  | 5.0387 | 4.6647 | [5 empty] | 197725 | 4.9319 |  |  | 191700 | 0 | 191700 | 6025 | 3.047% | 43 | 12697.25
2024-07-16 | 2025 | 2024 | 2024-07-01 | 31 | 11410 | 7727 | 9363 | 0 | 13249 | 13803 | 0 | 0 | 9025 | 9692 | 11052 | 10738 | 11536 | 10016 | 11180 | 13410 | 0 | 13909 | 0 | 12589 | 13359 | 0 | 0 | 0 | 0 | 0 | 4.8773 | 5.796 | 4.521 |  | 5.0182 | 5.2075 |  |  | 4.6312 | 5.2929 | 4.7187 | 4.8412 | 4.6982 | 4.8833 | 4.7661 | 4.9547 |  | 4.9983 |  | 4.9783 | 4.9818 | [5 empty] | 182058 | 4.9478 |  |  | 177750 | 450 | 177300 | 4308 | 2.366% | 43 | 19378
2024-07-17 | 2025 | 2024 | 2024-07-01 | 31 | 10588 | 7594 | 2098 | 0 | 10943 | 13778 | 0 | 0 | 6099 | 6754 | 11293 | 11979 | 12414 | 11940 | 11766 | 11725 | 0 | 13874 | 0 | 11469 | 11180 | 0 | 0 | 0 | 0 | 0 | 4.1178 | 4.2895 | 4.9556 |  | 4.8578 | 5.3997 |  |  | 5.0271 | 5.4 | 4.9245 | 5.1092 | 5.0103 | 5.1304 | 4.9753 | 5.0105 |  | 5.1424 |  | 5.0274 | 5.0384 | [5 empty] | 165494 | 4.9635 |  |  | 161100 | 0 | 161100 | 4394 | 2.655% | 43 | 5136.375
2024-07-18 | 2025 | 2024 | 2024-07-01 | 31 | 8465 | 10620 | 9005 | 0 | 9303 | 13938 | 0 | 0 | 9579 | 12293 | 11134 | 11128 | 9407 | 10708 | 11197 | 11952 | 0 | 14927 | 0 | 11635 | 13057 | 0 | 0 | 0 | 0 | 0 | 5.4737 | 5.6484 | 4.298 |  | 4.1647 | 5.1693 |  |  | 4.2906 | 5.0848 | 4.4267 | 4.5457 | 4.348 | 4.5947 | 4.5715 | 4.6265 |  | 4.9724 |  | 4.652 | 4.7715 | [5 empty] | 178348 | 4.7274 |  |  | 173250 | 0 | 173250 | 5098 | 2.858% | 43 | 5570.0005
2024-07-19 | 2025 | 2024 | 2024-07-01 | 31 | 11950 | 11003 | 13139 | 0 | 10076 | 18893 | 0 | 0 | 12661 | 13909 | 13198 | 14440 | 9556 | 13532 | 11207 | 15746 | 0 | 17826 | 0 | 11853 | 17764 | 0 | 0 | 0 | 4024 | 0 | 4.9447 | 5.036 | 5.5679 |  | 5.4291 | 6.2208 |  |  | 5.5344 | 6.3528 | 5.562 | 5.9064 | 5.4063 | 5.9344 | 5.6275 | 5.8186 |  | 5.92 |  | 5.5677 | 6.0165 |  |  |  | 5.88 |  | 220777 | 5.6897 |  |  | 218700 | 450 | 218250 | 2077 | 0.9408% | 43 | 30402.375
2024-07-20 | 2025 | 2024 | 2024-07-01 | 31 | 9894 | 3319 | 9909 | 0 | 9301 | 11201 | 0 | 0 | 10549 | 11209 | 10768 | 11139 | 12419 | 11427 | 11686 | 8749 | 0 | 9497 | 0 | 6996 | 9046 | 0 | 0 | 0 | 8573 | 0 | 5.1341 | 5.5601 | 5.0624 |  | 4.885 | 5.4486 |  |  | 5.079 | 5.4426 | 5.104 | 5.4273 | 5.2938 | 5.3944 | 5.2453 | 5.0658 |  | 5.246 |  | 5.0381 | 5.1267 |  |  |  | 5.29 |  | 165682 | 5.2261 |  |  | 164250 | 0 | 164250 | 1432 | 0.8643% | 43 | 5939.625
2024-07-21 | 2025 | 2024 | 2024-07-01 | 31 | 20618 | 0 | 19797 | 0 | 21922 | 19860 | 0 | 0 | 19377 | 19807 | 20255 | 20644 | 19579 | 18454 | 20073 | 19930 | 0 | 20007 | 0 | 14521 | 21099 | 0 | 0 | 0 | 16300 | 0 | 6.7894 | 7.5605 | 5.1145 |  | 5.2586 | 5.344 |  |  | 5.1993 | 5.5238 | 5.2018 | 5.3581 | 5.179 | 5.3084 | 5.2611 | 5.2706 |  | 5.294 |  | 5.1219 | 5.2139 |  |  |  | 5.21 |  | 312243 | 5.4829 |  |  | 304200 | 900 | 303300 | 8043 | 2.576% | 45.9 | 15044.25
2024-07-22 | 2025 | 2024 | 2024-07-01 | 31 | 26971 | 0 | 31288 | 0 | 29707 | 31970 | 0 | 0 | 29372 | 35789 | 31146 | 35562 | 35230 | 34556 | 33928 | 32584 | 0 | 29746 | 0 | 32624 | 33289 | 0 | 0 | 0 | 21595 | 0 | 9.0433 | 10.1557 | 7.0753 |  | 6.9823 | 7.3311 |  |  | 7.1723 | 7.876 | 7.1574 | 7.6789 | 7.4811 | 7.6499 | 7.4594 | 7.388 |  | 7.1739 |  | 7.3978 | 7.4517 |  |  |  | 6.78 |  | 505357 | 7.6032 |  |  | 494550 | 0 | 494550 | 10807 | 2.138% | 45.9 | 23107.75
2024-07-23 | 2025 | 2024 | 2024-07-01 | 31 | 48896 | 0 | 52101 | 0 | 53001 | 46136 | 0 | 0 | 52561 | 52026 | 53767 | 52932 | 45408 | 50504 | 48292 | 47210 | 0 | 44683 | 0 | 49232 | 50156 | 0 | 0 | 0 | 34893 | 0 | 9.869 | 11.0695 | 9.1192 |  | 9.4141 | 8.9601 |  |  | 9.389 | 9.4044 | 9.2895 | 9.3135 | 9.0708 | 9.3553 | 9.0279 | 8.8466 |  | 8.8646 |  | 8.9961 | 9.0842 |  |  |  | 9.4713 |  | 781798 | 9.3262 |  |  | 782100 | 0 | 782100 | -302 | -0.03863% | 45.9 | 11570.5693
2024-07-24 | 2025 | 2024 | 2024-07-01 | 31 | 58630 | 0 | 58810 | 0 | 60785 | 59711 | 0 | 0 | 59592 | 60689 | 60852 | 60073 | 57058 | 59010 | 57475 | 60579 | 0 | 60593 | 0 | 58482 | 59642 | 0 | 0 | 0 | 53384 | 0 | 9.809 | 10.9148 | 9.8673 |  | 10.3487 | 10.1817 |  |  | 10.076 | 10.4944 | 10.1848 | 10.3753 | 10.082 | 10.2826 | 10.1723 | 10.3446 |  | 10.1239 |  | 10.1151 | 10.3376 |  |  |  | 10.202 |  | 945365 | 10.2301 |  |  | 918450 | 0 | 918450 | 26915 | 2.847% | 45.9 | 3208.9995
2024-07-25 | 2025 | 2024 | 2024-07-01 | 31 | 58137 | 1557 | 56297 | 0 | 58029 | 59917 | 0 | 0 | 58765 | 60762 | 58752 | 61748 | 52260 | 58687 | 62902 | 61654 | 0 | 58048 | 0 | 53126 | 61099 | 0 | 0 | 2949 | 61221 | 0 | 9.1435 | 9.5928 | 9.6537 |  | 10.0475 | 10.0086 |  |  | 10.0187 | 10.4589 | 10.0551 | 10.3338 | 10.2047 | 10.2556 | 10.3462 | 10.4461 |  | 10.1506 |  | 10.1199 | 10.3091 |  |  | 9.2515 | 10.0735 |  | 945910 | 10.0261 |  |  | 917550 | 0 | 917550 | 28360 | 2.998% | 45.9 | 1001.1245
2024-07-26 | 2025 | 2024 | 2024-07-01 | 31 | 52426 | 55982 | 51005 | 0 | 53417 | 54168 | 0 | 0 | 53843 | 57162 | 54875 | 56127 | 54487 | 52737 | 55244 | 56368 | 0 | 53614 | 0 | 51788 | 54363 | 0 | 0 | 13185 | 57904 | 0 | 7.8562 | 8.2047 | 8.8565 |  | 9.3977 | 9.2633 |  |  | 9.3586 | 9.7462 | 9.3589 | 9.4987 | 9.4268 | 9.5166 | 9.639 | 9.4648 |  | 9.1137 |  | 9.1475 | 9.3542 |  |  | 9.0083 | 9.4985 |  | 938695 | 9.2061 |  |  | 909450 | 0 | 909450 | 29245 | 3.115% | 48.6 | 4512.7505
2024-07-27 | 2025 | 2024 | 2024-07-01 | 31 | 37797 | 42878 | 29800 | 0 | 40938 | 41240 | 0 | 0 | 40862 | 41703 | 38368 | 44428 | 11231 | 42581 | 43987 | 44252 | 0 | 41943 | 0 | 40314 | 45349 | 0 | 0 | 37645 | 44482 | 0 | 6.2421 | 6.5133 | 7.6418 |  | 8.0795 | 8.2056 |  |  | 8.1334 | 8.5104 | 7.9752 | 8.4487 | 9.6359 | 8.3835 | 8.3202 | 8.3747 |  | 8.0158 |  | 8.1167 | 8.369 |  |  | 8.2561 | 8.2451 |  | 709798 | 8.0815 |  |  | 721800 | 0 | 721800 | -12002 | -1.691% | 48.6 | 12651.25
2024-07-28 | 2025 | 2024 | 2024-07-01 | 31 | 19325 | 23066 | 19357 | 0 | 21721 | 20585 | 0 | 0 | 20482 | 22294 | 20638 | 22437 | 5214 | 16027 | 21512 | 21968 | 0 | 20267 | 0 | 19586 | 21311 | 0 | 0 | 22486 | 24108 | 0 | 6.7641 | 7.0182 | 6.1665 |  | 6.4171 | 6.4822 |  |  | 6.3654 | 6.8416 | 6.3364 | 6.6764 | 5.8067 | 6.5824 | 6.4377 | 6.5094 |  | 6.1778 |  | 6.4428 | 6.4924 |  |  | 6.5685 | 6.5923 |  | 362384 | 6.4821 |  |  | 372150 | 0 | 372150 | -9766 | -2.695% | 48.6 | 5951.125
2024-07-29 | 2025 | 2024 | 2024-07-01 | 31 | 25729 | 29932 | 25842 | 0 | 30504 | 28341 | 0 | 0 | 20868 | 29126 | 25793 | 26233 | 25166 | 8064 | 24084 | 29723 | 0 | 28202 | 0 | 28194 | 30266 | 0 | 0 | 27865 | 33019 | 0 | 6.8683 | 6.7685 | 6.6046 |  | 7.1506 | 7.0904 |  |  | 6.4631 | 7.2784 | 6.6576 | 6.9109 | 6.6127 | 6.874 | 6.5167 | 7.0608 |  | 6.8372 |  | 6.9715 | 7.1567 |  |  | 6.8118 | 7.2426 |  | 476951 | 6.882 |  |  | 467100 | 0 | 467100 | 9851 | 2.065% | 48.6 | 7187.875
2024-07-30 | 2025 | 2024 | 2024-07-01 | 31 | 26943 | 27433 | 27896 | 0 | 26076 | 25841 | 0 | 0 | 28008 | 22132 | 26463 | 15549 | 23314 | 22352 | 22127 | 18589 | 0 | 25241 | 0 | 22641 | 25222 | 0 | 0 | 25245 | 30088 | 0 | 7.1825 | 7.4243 | 6.9733 |  | 6.7332 | 6.7747 |  |  | 7.0237 | 6.6071 | 6.7409 | 6.7552 | 6.392 | 6.781 | 6.3047 | 5.906 |  | 6.4703 |  | 6.4504 | 6.7899 |  |  | 6.5937 | 7.0258 |  | 441160 | 6.7183 |  |  | 433800 | 0 | 433800 | 7360 | 1.668% | 48.6 | 7376.3125
2024-07-31 | 2025 | 2024 | 2024-07-01 | 31 | 30381 | 31306 | 31365 | 0 | 32732 | 27166 | 0 | 0 | 31967 | 27926 | 27095 | 18106 | 29367 | 29487 | 28376 | 25883 | 0 | 27982 | 0 | 26006 | 29750 | 0 | 0 | 30438 | 35020 | 0 | 8.8773 | 9.0359 | 7.1566 |  | 7.3439 | 7.0474 |  |  | 7.3945 | 7.2751 | 6.9652 | 7.2069 | 6.9753 | 7.3169 | 6.9421 | 6.6269 |  | 6.8564 |  | 6.8291 | 7.1235 |  |  | 7.1138 | 7.4605 |  | 520353 | 7.3082 |  |  | 508050 | 0 | 508050 | 12303 | 2.364% | 48.6 | 7562.125
2024-08-01 | 2025 | 2024 | 2024-08-01 | 31 | 44099 | 46177 | 47165 | 0 | 48543 | 40747 | 0 | 0 | 45477 | 42789 | 17040 | 45513 | 40102 | 45053 | 41270 | 37895 | 0 | 40665 | 0 | 43935 | 44233 | 0 | 0 | 31889 | 35756 | 0 | 9.3131 | 9.681 | 8.8558 |  | 9.0239 | 8.5415 |  |  | 8.9459 | 8.8523 | 6.1786 | 8.869 | 8.5572 | 8.9599 | 8.4133 | 8.0778 |  | 8.3969 |  | 8.6093 | 8.6273 |  |  | 8.7392 | 9.0329 |  | 738348 | 8.6486 |  |  | 716400 | 0 | 716400 | 21948 | 2.973% | 48.6 | 14083.3658
2024-08-02 | 2025 | 2024 | 2024-08-01 | 31 | 51900 | 57384 | 52428 | 0 | 56218 | 45428 | 0 | 0 | 54413 | 28656 | 36548 | 53860 | 55006 | 52974 | 54422 | 42589 | 0 | 48218 | 0 | 49590 | 48911 | 0 | 0 | 53416 | 57422 | 0 | 9.6658 | 9.934 | 9.0589 |  | 9.5456 | 8.6624 |  |  | 9.4655 | 8.8703 | 7.135 | 9.5679 | 9.4103 | 9.5517 | 9.4031 | 8.7949 |  | 8.6994 |  | 9.1093 | 8.8681 |  |  | 9.4555 | 9.6135 |  | 899383 | 9.1562 |  |  | 872100 | 0 | 872100 | 27283 | 3.034% | 48.6 | 8910.2355
2024-08-03 | 2025 | 2024 | 2024-08-01 | 31 | 57347 | 58294 | 56228 | 0 | 58703 | 58271 | 0 | 0 | 56375 | 28530 | 56270 | 58882 | 56643 | 56652 | 55719 | 46036 | 0 | 55751 | 0 | 49957 | 50171 | 0 | 0 | 57044 | 61223 | 0 | 8.4066 | 8.2965 | 9.571 |  | 9.8091 | 9.8849 |  |  | 9.8066 | 9.5835 | 9.7383 | 9.9163 | 9.6531 | 9.8535 | 9.7144 | 9.8447 |  | 9.6928 |  | 9.6186 | 10.0021 |  |  | 9.8494 | 9.9926 |  | 978096 | 9.6241 |  |  | 949950 | 0 | 949950 | 28146 | 2.878% | 48.6 | 4690.7558
2024-08-04 | 2025 | 2024 | 2024-08-01 | 31 | 39088 | 31778 | 38418 | 0 | 37558 | 44792 | 0 | 0 | 39744 | 38003 | 37361 | 35822 | 37312 | 38002 | 39175 | 39028 | 0 | 47191 | 0 | 46406 | 48839 | 0 | 0 | 48587 | 40073 | 0 | 7.2008 | 7.3728 | 8.1941 |  | 8.4136 | 8.6259 |  |  | 8.4823 | 9.1473 | 8.4084 | 8.231 | 8.307 | 8.5559 | 8.4509 | 8.7612 |  | 8.5317 |  | 8.7099 | 8.7588 |  |  | 8.8733 | 8.5408 |  | 727177 | 8.4203 |  |  | 708300 | 0 | 708300 | 18877 | 2.596% | 48.6 | 10741.4745
2024-08-05 | 2025 | 2024 | 2024-08-01 | 31 | 30673 | 33729 | 31686 | 0 | 34554 | 33067 | 0 | 0 | 26417 | 23181 | 31157 | 30133 | 28823 | 30558 | 27982 | 24074 | 0 | 31858 | 0 | 27566 | 33648 | 0 | 0 | 31779 | 35910 | 0 | 8.0055 | 8.1657 | 7.1452 |  | 7.5078 | 7.4421 |  |  | 7.3144 | 7.4468 | 7.2977 | 7.167 | 6.9178 | 7.3337 | 6.8808 | 6.5792 |  | 7.0889 |  | 6.9471 | 7.4229 |  |  | 7.1806 | 7.5604 |  | 546795 | 7.3002 |  |  | 533700 | 0 | 533700 | 13095 | 2.395% | 48.6 | 23597.811
2024-08-06 | 2025 | 2024 | 2024-08-01 | 31 | 39337 | 42099 | 41034 | 0 | 33359 | 38635 | 0 | 0 | 40472 | 37810 | 38819 | 38314 | 36884 | 38476 | 34327 | 33371 | 0 | 36009 | 0 | 19978 | 38091 | 0 | 0 | 39578 | 44312 | 0 | 8.0083 | 8.2285 | 7.9838 |  | 8.306 | 7.9967 |  |  | 8.1517 | 8.1056 | 8.0081 | 7.9585 | 7.715 | 8.1482 | 7.5703 | 7.4757 |  | 7.6432 |  | 7.7116 | 7.9579 |  |  | 7.9666 | 8.3006 |  | 670905 | 7.9576 |  |  | 668700 | 0 | 668700 | 2205 | 0.3287% | 48.6 | 9269.855
2024-08-07 | 2025 | 2024 | 2024-08-01 | 31 | 39877 | 17159 | 42997 | 0 | 42330 | 41092 | 0 | 0 | 42788 | 40911 | 38800 | 41575 | 39492 | 41086 | 38552 | 37127 | 0 | 39614 | 0 | 39173 | 29371 | 0 | 0 | 42495 | 45465 | 0 | 7.2508 | 7.3609 | 8.1015 |  | 8.1928 | 8.2266 |  |  | 8.3107 | 8.3931 | 8.0322 | 8.2358 | 7.9118 | 8.3402 | 7.9413 | 7.7349 |  | 7.9403 |  | 8 | 8.1013 |  |  | 8.1847 | 8.345 |  | 699904 | 8.0336 |  |  | 682200 | 0 | 682200 | 17704 | 2.529% | 48.6 | 3157.785
2024-08-08 | 2025 | 2024 | 2024-08-01 | 31 | 31108 | 0 | 30165 | 0 | 33528 | 31599 | 0 | 0 | 33783 | 24581 | 30931 | 24569 | 31001 | 32270 | 29431 | 26773 | 0 | 30826 | 0 | 30388 | 32202 | 0 | 0 | 33936 | 36503 | 0 | 7.4199 | 7.7194 | 7.1187 |  | 7.446 | 7.3562 |  |  | 7.5288 | 7.1758 | 7.3207 | 7.4052 | 7.1514 | 7.5972 | 7.0326 | 6.751 |  | 6.9688 |  | 7.18 | 7.2699 |  |  | 7.3876 | 7.5735 |  | 523594 | 7.3002 |  |  | 513450 | 0 | 513450 | 10144 | 1.937% | 48.6 | 14407.16
2024-08-09 | 2025 | 2024 | 2024-08-01 | 31 | 33317 | 0 | 28271 | 0 | 34788 | 30796 | 0 | 0 | 34995 | 34923 | 33457 | 35486 | 23183 | 22870 | 33776 | 33423 | 0 | 32589 | 0 | 32482 | 33631 | 0 | 0 | 35163 | 37348 | 0 | 7.9869 | 8.1376 | 7.3758 |  | 7.6128 | 7.37 |  |  | 7.6807 | 7.5051 | 7.4774 | 7.6994 | 7.2106 | 7.7569 | 7.4306 | 7.4646 |  | 7.1665 |  | 7.14 | 7.3842 |  |  | 7.5167 | 7.7406 |  | 550498 | 7.5365 |  |  | 537300 | 0 | 537300 | 13198 | 2.397% | 48.6 | 3030.055
2024-08-10 | 2025 | 2024 | 2024-08-01 | 31 | 29366 | 0 | 36977 | 0 | 37650 | 41027 | 0 | 0 | 39143 | 42425 | 38435 | 41525 | 38669 | 38501 | 39514 | 43307 | 0 | 39100 | 0 | 39088 | 41863 | 0 | 0 | 44517 | 40467 | 0 | 8.7616 | 8.9155 | 7.7545 |  | 8.2303 | 8.2728 |  |  | 8.0973 | 8.165 | 8.0721 | 8.2637 | 7.8693 | 8.1489 | 8.0112 | 8.3267 |  | 7.9334 |  | 8.07 | 8.2333 |  |  | 8.3402 | 8.1645 |  | 671574 | 8.2017 |  |  | 655650 | 0 | 655650 | 15924 | 2.371% | 48.6 | 7386.49
2024-08-11 | 2025 | 2024 | 2024-08-01 | 31 | 45828 | 0 | 47234 | 0 | 49194 | 46612 | 0 | 0 | 50214 | 50097 | 46108 | 51033 | 47539 | 47410 | 49060 | 46673 | 0 | 46526 | 0 | 44346 | 47544 | 0 | 0 | 50310 | 52377 | 0 | 7.4896 | 7.5665 | 8.7027 |  | 9.0428 | 8.8521 |  |  | 9.1477 | 8.9751 | 8.8971 | 9.1541 | 8.8446 | 9.0125 | 8.9799 | 8.749 |  | 8.5906 |  | 9 | 8.8216 |  |  | 9.0738 | 9.1414 |  | 818105 | 8.7801 |  |  | 796500 | 0 | 796500 | 21605 | 2.641% | 48.6 | 4582.674
2024-08-12 | 2025 | 2024 | 2024-08-01 | 31 | 28934 | 0 | 30207 | 0 | 22821 | 30646 | 0 | 0 | 24658 | 31641 | 29846 | 31729 | 30863 | 29162 | 28891 | 31279 | 0 | 31240 | 0 | 31464 | 33072 | 0 | 0 | 36103 | 32273 | 0 | 5.5276 | 6.0158 | 7.4636 |  | 7.8653 | 7.3989 |  |  | 7.7425 | 7.673 | 7.6433 | 7.812 | 7.6105 | 7.6004 | 7.4049 | 7.1693 |  | 7.1299 |  | 7.4 | 7.4111 |  |  | 7.6376 | 7.6538 |  | 514829 | 7.3422 |  |  | 505350 | 0 | 505350 | 9479 | 1.841% | 48.6 | 13798.475
2024-08-13 | 2025 | 2024 | 2024-08-01 | 31 | 11414 | 0 | 14584 | 0 | 17594 | 19908 | 0 | 0 | 12341 | 15288 | 14363 | 15919 | 13695 | 14060 | 13939 | 18573 | 0 | 19126 | 0 | 17447 | 20651 | 0 | 0 | 17184 | 18576 | 0 | 5.48 | 5.9082 | 5.3492 |  | 5.9436 | 6.1473 |  |  | 5.5586 | 5.5523 | 5.5565 | 5.7346 | 5.2745 | 5.7159 | 5.3565 | 5.6514 |  | 5.7445 |  | 6 | 6.0381 |  |  | 5.5806 | 5.9385 |  | 274662 | 5.6961 |  |  | 268650 | 0 | 268650 | 6012 | 2.189% | 48.6 | 18293.69
2024-08-14 | 2025 | 2024 | 2024-08-01 | 31 | 13485 | 0 | 13595 | 0 | 17869 | 14283 | 0 | 0 | 14649 | 13210 | 12492 | 14477 | 11257 | 14418 | 14109 | 15459 | 0 | 14239 | 0 | 13664 | 13724 | 0 | 0 | 15520 | 19409 | 0 | 5.9893 | 6.4232 | 5.1627 |  | 5.7253 | 5.6997 |  |  | 5.4805 | 5.2294 | 5.2547 | 5.5344 | 5.124 | 5.5206 | 5.3386 | 5.4697 |  | 5.283 |  | 5.3 | 5.4103 |  |  | 5.4409 | 5.779 |  | 245859 | 5.5092 |  |  | 240750 | 0 | 240750 | 5109 | 2.078% | 48.6 | 851.1
2024-08-15 | 2025 | 2024 | 2024-08-01 | 31 | 19149 | 0 | 18098 | 0 | 21561 | 21439 | 0 | 0 | 19150 | 20053 | 18464 | 19021 | 14628 | 18803 | 19552 | 21431 | 0 | 20365 | 0 | 19288 | 21620 | 0 | 0 | 21838 | 22712 | 0 | 5.8538 | 5.9593 | 5.7601 |  | 6.2125 | 6.7378 |  |  | 6.0637 | 6.0713 | 6.0104 | 6.1683 | 5.7944 | 6.1476 | 6.0577 | 6.2242 |  | 6.0758 |  | 6 | 6.2954 |  |  | 6.2593 | 6.251 |  | 337172 | 6.1079 |  |  | 330750 | 0 | 330750 | 6422 | 1.905% | 48.6 | 4152.265
2024-08-16 | 2025 | 2024 | 2024-08-01 | 31 | 17203 | 5385 | 17706 | 0 | 19759 | 17890 | 0 | 0 | 12495 | 16755 | 14976 | 16715 | 15456 | 16473 | 16301 | 17494 | 0 | 17424 | 0 | 14966 | 17479 | 0 | 0 | 10347 | 21150 | 0 | 5.492 | 5.5339 | 5.7736 |  | 6.1955 | 6.1938 |  |  | 6.136 | 5.7649 | 5.7158 | 5.9268 | 5.5679 | 5.8646 | 5.673 | 5.6583 |  | 5.6243 |  | 5.7 | 5.7531 |  |  | 5.534 | 6.1642 |  | 285974 | 5.7929 |  |  | 280350 | 0 | 280350 | 5624 | 1.967% | 48.6 | 5541.97
2024-08-17 | 2025 | 2024 | 2024-08-01 | 31 | 14906 | 16420 | 14934 | 0 | 16618 | 12089 | 0 | 0 | 11034 | 15997 | 14152 | 14695 | 14202 | 14078 | 15067 | 14656 | 0 | 17192 | 0 | 15027 | 17265 | 0 | 0 | 15844 | 17498 | 0 | 4.3829 | 4.4833 | 5.4146 |  | 5.639 | 6.1022 |  |  | 5.5761 | 5.579 | 5.5391 | 5.6299 | 5.3133 | 5.5004 | 5.4177 | 5.3808 |  | 5.6383 |  | 5.7 | 5.7319 |  |  | 5.5324 | 5.7476 |  | 271674 | 5.4616 |  |  | 265050 | 0 | 265050 | 6624 | 2.438% | 48.6 | 10454.52
2024-08-18 | 2025 | 2024 | 2024-08-01 | 31 | 10042 | 11999 | 9728 | 0 | 10731 | 9365 | 0 | 0 | 10506 | 9790 | 8395 | 9775 | 7950 | 10224 | 3172 | 10267 | 0 | 9740 | 0 | 8911 | 9318 | 0 | 0 | 9821 | 11331 | 0 | 4.3287 | 4.3301 | 4.3047 |  | 4.4559 | 4.4041 |  |  | 4.5396 | 4.3493 | 4.3238 | 4.5399 | 4.0673 | 4.5146 | 4.1514 | 4.2833 |  | 4.2285 |  | 4.2 | 4.3083 |  |  | 4.324 | 4.5008 |  | 171065 | 4.3419 |  |  | 165150 | 450 | 164700 | 5915 | 3.458% | 48.6 | 4212.095
2024-08-19 | 2025 | 2024 | 2024-08-01 | 31 | 7639 | 8590 | 7008 | 0 | 7839 | 7592 | 0 | 0 | 7294 | 5005 | 6253 | 6273 | 6453 | 6284 | 0 | 6567 | 0 | 6963 | 0 | 7038 | 5985 | 0 | 0 | 6781 | 8648 | 0 | 4.7805 | 4.903 | 4.1435 |  | 4.3209 | 4.5959 |  |  | 4.3263 | 3.8809 | 4.2638 | 4.2974 | 4.0774 | 4.2161 | 4.0876 | 4.3664 |  | 4.065 |  | 3.9 | 3.9826 |  |  | 4.1811 | 4.3612 |  | 118212 | 4.2639 |  |  | 114750 | 450 | 114300 | 3462 | 2.929% | 48.6 | 327.425
2024-08-20 | 2025 | 2024 | 2024-08-01 | 31 | 9664 | 12013 | 7846 | 0 | 11505 | 13949 | 0 | 0 | 8813 | 6246 | 8004 | 7943 | 8229 | 8444 | 0 | 8460 | 0 | 12573 | 0 | 10986 | 9033 | 0 | 0 | 8709 | 11849 | 3711 | 3.5698 | 3.5676 | 4.4289 |  | 4.9322 | 5.6708 |  |  | 4.6989 | 4.2548 | 4.6873 | 4.7577 | 4.5973 | 4.8121 | 5.4353 | 4.9008 |  | 5.124 |  | 4.3 | 4.6481 |  |  | 4.7158 | 4.9773 | 4.5 | 167977 | 4.662 |  |  | 163350 | 0 | 163350 | 4627 | 2.755% | 48.6 | 1077.525
2024-08-21 | 2025 | 2024 | 2024-08-01 | 31 | 4716 | 5890 | 4754 | 0 | 6313 | 4501 | 0 | 0 | 4552 | 4230 | 4472 | 4310 | 4227 | 4337 | 0 | 4994 | 0 | 3301 | 0 | 0 | 4671 | 0 | 0 | 5486 | 6258 | 4306 | 3.1622 | 3.3781 | 3.5144 |  | 3.7276 | 3.848 |  |  | 3.5374 | 3.4571 | 3.5887 | 3.6343 | 3.4322 | 3.6519 | 3.5715 | 3.5729 |  | 3.602 |  | 1.8048 | 3.5378 |  |  | 3.6812 | 3.76 | 3.5 | 81318 | 3.4717 |  |  | 83250 | 1350 | 81900 | -1932 | -2.376% | 48.6 | 257.3
2024-08-22 | 2025 | 2024 | 2024-08-01 | 31 | 3381 | 4952 | 2999 | 0 | 4583 | 3781 | 0 | 0 | 3055 | 3170 | 2728 | 3199 | 3068 | 2954 | 2577 | 3668 | 0 | 2977 | 0 | 3416 | 3222 | 0 | 0 | 3602 | 4604 | 2921 | 4.0456 | 4.2858 | 3.1466 |  | 3.3897 | 3.534 |  |  | 3.2188 | 3.2597 | 3.1787 | 3.2552 | 3.1281 | 3.3206 | 3.333 | 3.2635 |  | 3.3134 |  | 3.2436 | 3.1889 |  |  | 3.2194 | 3.4236 | 3.3 | 64857 | 3.371 |  |  | 61650 | 1350 | 60300 | 3207 | 4.945% | 51.3 | 449.955
2024-08-23 | 2025 | 2024 | 2024-08-01 | 31 | 5710 | 7903 | 6325 | 0 | 7426 | 7739 | 0 | 0 | 4650 | 5526 | 5486 | 5218 | 5164 | 5718 | 0 | 6434 | 0 | 7277 | 0 | 6271 | 5458 | 0 | 0 | 6571 | 7475 | 6244 | 6.7064 | 6.9871 | 4.0306 |  | 4.4041 | 4.5394 |  |  | 4.2243 | 3.8251 | 4.0053 | 3.9833 | 3.7779 | 4.0264 | 4.0525 | 4.0691 |  | 4.1466 |  | 4.1025 | 4.2444 |  |  | 4.0285 | 4.2622 | 4.1 | 112595 | 4.3956 |  |  | 108000 | 0 | 108000 | 4595 | 4.081% | 51.3 | 39.735
2024-08-24 | 2025 | 2024 | 2024-08-01 | 31 | 25556 | 30017 | 27039 | 0 | 28749 | 25694 | 0 | 0 | 25488 | 22666 | 26652 | 24083 | 25025 | 27459 | 5306 | 19142 | 0 | 24327 | 0 | 20941 | 21420 | 0 | 0 | 17776 | 29354 | 22463 | 10.2815 | 10.7642 | 6.7922 |  | 6.9713 | 7.161 |  |  | 6.9531 | 6.3613 | 6.8672 | 6.6695 | 6.6303 | 7.0887 | 7.091 | 6.6763 |  | 6.925 |  | 6.8101 | 6.4468 |  |  | 6.6308 | 6.9015 | 6.7 | 449157 | 7.1959 |  |  | 436950 | 0 | 436950 | 12207 | 2.718% | 51.3 | 16443.675
2024-08-25 | 2025 | 2024 | 2024-08-01 | 31 | 60728 | 62742 | 59617 | 0 | 38581 | 59645 | 0 | 0 | 61353 | 55363 | 59702 | 60654 | 59916 | 56702 | 58969 | 60043 | 0 | 59621 | 0 | 60570 | 60617 | 0 | 0 | 60248 | 62491 | 60898 | 12.7805 | 13.546 | 10.1305 |  | 10.4935 | 10.4176 |  |  | 10.3449 | 9.9245 | 10.3062 | 10.3947 | 10.3103 | 10.4635 | 10.3692 | 10.5788 |  | 10.2214 |  | 10.6039 | 10.3592 |  |  | 10.6315 | 10.6991 | 10.5 | 1118460 | 10.6882 |  |  | 1079100 | 0 | 1079100 | 39360 | 3.519% | 51.3 | 2858.0147
2024-08-26 | 2025 | 2024 | 2024-08-01 | 31 | 40614 | 36268 | 40831 | 0 | 744 | 32891 | 0 | 0 | 41680 | 39639 | 39953 | 31500 | 43192 | 41501 | 38187 | 40099 | 0 | 38246 | 0 | 39306 | 34221 | 0 | 0 | 34962 | 38452 | 35298 | 12.5805 | 12.3583 | 12.4419 |  | 12.5629 | 12.576 |  |  | 12.7707 | 12.7642 | 12.7436 | 12.7694 | 12.8908 | 13.1292 | 12.7327 | 13.1126 |  | 12.8667 |  | 13.051 | 12.8412 |  |  | 12.957 | 13.1942 | 12.9 | 687584 | 12.8023 |  |  | 664650 | 0 | 664650 | 22934 | 3.335% | 51.3 | 99588.5015
2024-08-27 | 2025 | 2024 | 2024-08-01 | 31 | 66878 | 17579 | 64924 | 0 | 0 | 65060 | 0 | 0 | 63643 | 64811 | 62281 | 0 | 67093 | 64427 | 66212 | 63073 | 0 | 63482 | 0 | 65418 | 59890 | 0 | 0 | 65340 | 20147 | 61872 | 13.7796 | 13.6397 | 12.6278 |  | 11.4 | 11.8682 |  |  | 12.6253 | 11.7984 | 12.4669 | 12.9687 | 12.2299 | 12.36 | 12.0169 | 11.7889 |  | 11.9649 |  | 12.0571 | 11.7308 |  |  | 12.3349 | 12.5281 | 10.4 | 1002130 | 12.2414 |  |  | 975150 | 0 | 975150 | 26980 | 2.692% | 51.3 | 774.875
2024-08-28 | 2025 | 2024 | 2024-08-01 | 31 | 61416 | 55320 | 61664 | 0 | 18344 | 61375 | 0 | 0 | 59934 | 64092 | 64587 | 0 | 64199 | 64175 | 53780 | 58497 | 0 | 62586 | 0 | 54343 | 65427 | 0 | 0 | 63439 | 0 | 60527 | 11.5845 | 11.694 | 13.629 |  | 12.6591 | 13.6549 |  |  | 13.6158 | 13.1431 | 13.7838 | 14.7773 | 13.3034 | 13.6334 | 11.8945 | 13.4396 |  | 13.3945 |  | 13.6138 | 13.5488 |  |  | 13.6057 | 13.934 | 12.8 | 993705 | 13.2479 |  |  | 962550 | 0 | 962550 | 31155 | 3.135% | 51.3 | 5812.7502
2024-08-29 | 2025 | 2024 | 2024-08-01 | 31 | 63209 | 62645 | 62623 | 20943 | 64102 | 66318 | 0 | 0 | 64117 | 66080 | 65120 | 19738 | 67692 | 60375 | 64403 | 59726 | 0 | 52427 | 0 | 57540 | 62108 | 0 | 0 | 63522 | 0 | 59803 | 7.4718 | 7.4014 | 11.3397 | 11.4032 | 11.5277 | 11.8168 |  |  | 11.4191 | 11.4605 | 11.721 | 12.4174 | 11.7151 | 11.5246 | 11.6813 | 11.7078 |  | 11.8241 |  | 11.7565 | 11.6069 |  |  | 11.857 | 11.719 | 11.69 | 1102491 | 11.253 |  |  | 1066050 | 0 | 1066050 | 36441 | 3.305% | 51.3 | 1245.9997
2024-08-30 | 2025 | 2024 | 2024-08-01 | 31 | 33876 | 33939 | 36195 | 18489 | 32328 | 30540 | 0 | 0 | 36554 | 32690 | 37830 | 34342 | 36811 | 34954 | 34705 | 31452 | 0 | 31557 | 0 | 26553 | 28752 | 0 | 0 | 29155 | 17003 | 31147 | 4.2988 | 4.2805 | 7.6049 | 7.6588 | 7.2732 | 7.312 |  |  | 7.8318 | 7.34 | 7.9073 | 7.5155 | 7.6211 | 7.7104 | 7.7675 | 7.3158 |  | 7.1891 |  | 6.912 | 7.0527 |  |  | 7.1127 | 7.5407 | 7.84 | 628872 | 7.1542 |  |  | 612425 | 0 | 612425 | 16447 | 2.615% | 51.3 | 12063.938
2024-08-31 | 2025 | 2024 | 2024-08-01 | 31 | 7455 | 9060 | 8234 | 0 | 7952 | 11140 | 0 | 0 | 8573 | 8345 | 7850 | 8575 | 8524 | 8349 | 7197 | 10294 | 0 | 11073 | 0 | 6891 | 11422 | 0 | 0 | 8068 | 8336 | 4982 | 4.6063 | 4.9401 | 4.3863 | 4.6 | 4.1983 | 4.8483 |  |  | 4.5717 | 4.5153 | 4.6455 | 4.637 | 4.4764 | 4.6809 | 4.4838 | 4.5963 |  | 4.6747 |  | 4.2126 | 4.7229 |  |  | 4.2978 | 4.3388 | 4.47 | 162320 | 4.5452 |  |  | 157950 | 0 | 157950 | 4370 | 2.692% | 51.3 | 1212.125
2024-09-01 | 2025 | 2024 | 2024-09-01 | 30 | 10084 | 11910 | 8309 | 0 | 11790 | 13599 | 0 | 0 | 9768 | 10313 | 9039 | 10403 | 8101 | 9994 | 8972 | 11080 | 0 | 13188 | 0 | 11078 | 12640 | 0 | 0 | 11618 | 11938 | 9518 | 5.0146 | 5.2717 | 4.2784 | 4.5 | 4.83 | 5.3127 |  |  | 4.5664 | 4.7511 | 4.6297 | 4.9135 | 4.3621 | 4.8944 | 4.5275 | 4.8574 |  | 4.9986 |  | 4.8688 | 5.1 |  |  | 4.8706 | 4.8288 | 4.75 | 203342 | 4.8063 |  |  | 197100 | 0 | 197100 | 6242 | 3.07% | 51.3 | 2169.625
2024-09-02 | 2025 | 2024 | 2024-09-01 | 30 | 8307 | 10948 | 7346 | 0 | 9964 | 9344 | 0 | 0 | 8657 | 5874 | 6925 | 6820 | 7016 | 7547 | 7486 | 8585 | 0 | 8203 | 0 | 7362 | 6899 | 0 | 0 | 8048 | 10200 | 6912 | 5.155 | 5.2659 | 4.8057 | 4.0834 | 5.2875 | 5.4152 |  |  | 5.1868 | 4.476 | 4.9137 | 4.8634 | 4.7393 | 5.1278 | 4.8877 | 5.0217 |  | 5.0054 |  | 4.9315 | 4.7029 |  |  | 4.8561 | 5.2203 | 5.23 | 152443 | 4.9588 |  |  | 148950 | 0 | 148950 | 3493 | 2.291% | 51.3 | 0
2024-09-03 | 2025 | 2024 | 2024-09-01 | 30 | 12588 | 14516 | 11740 | 5096 | 11562 | 11249 | 401 | 0 | 12223 | 9624 | 11055 | 10863 | 10947 | 10983 | 10899 | 12026 | 0 | 10442 | 0 | 12130 | 6272 | 0 | 0 | 11583 | 14864 | 0 | 5.9457 | 6.118 | 4.971 | 5.143 | 5.3702 | 5.2642 | 4.5093 |  | 5.2135 | 4.728 | 5.0111 | 5.0666 | 4.8311 | 5.1141 | 4.9476 | 5.0309 |  | 4.9382 |  | 5.1215 | 4.681 |  |  | 4.9441 | 5.2908 | 5.13 | 211063 | 5.1129 |  |  | 206100 | 0 | 206100 | 4963 | 2.351% | 51.3 | 643.5
2024-09-04 | 2025 | 2024 | 2024-09-01 | 30 | 17108 | 19659 | 12092 | 19755 | 19057 | 11140 | 10472 | 0 | 16589 | 16155 | 15298 | 15341 | 13524 | 15459 | 14083 | 18019 | 0 | 17906 | 0 | 15756 | 16177 | 0 | 0 | 16941 | 19870 | 6828 | 7.4524 | 7.7518 | 5.7905 | 6.022 | 6.1797 | 6.2307 | 5.8442 |  | 5.8434 | 5.5936 | 5.6346 | 5.6602 | 5.2267 | 5.7746 | 5.5777 | 5.8349 |  | 5.9164 |  | 5.6907 | 5.7672 |  |  | 5.7034 | 6.1609 | 5.66 | 327229 | 5.9674 |  |  | 319950 | 0 | 319950 | 7279 | 2.224% | 51.3 | 25339.0007
2024-09-05 | 2025 | 2024 | 2024-09-01 | 30 | 32728 | 37749 | 30709 | 22771 | 31686 | 24029 | 14972 | 0 | 31384 | 24135 | 28463 | 28645 | 29173 | 20059 | 28937 | 29881 | 0 | 16213 | 0 | 29771 | 26457 | 0 | 0 | 30279 | 35526 | 30823 | 6.8158 | 7.0784 | 7.1267 | 7.6279 | 7.4925 | 7.2365 | 7.3988 |  | 7.4086 | 6.5551 | 7.1369 | 7.2733 | 7.0856 | 7.4347 | 7.1172 | 7.1332 |  | 6.8035 |  | 7.1857 | 6.7706 |  |  | 7.1387 | 7.5328 | 7.2 | 584390 | 7.1692 |  |  | 569250 | 0 | 569250 | 15140 | 2.591% | 51.3 | 5128.375
2024-09-06 | 2025 | 2024 | 2024-09-01 | 30 | 25458 | 29228 | 23889 | 11828 | 26184 | 30338 | 9513 | 0 | 25751 | 24888 | 21241 | 25198 | 24537 | 20770 | 26838 | 25782 | 0 | 1106 | 0 | 25248 | 29845 | 0 | 0 | 15336 | 23643 | 8483 | 5.5895 | 5.7994 | 6.5751 | 7.0319 | 6.9737 | 7.4316 | 6.6252 |  | 6.9195 | 6.6054 | 6.5649 | 6.7461 | 6.6022 | 6.8661 | 6.8469 | 6.894 |  | 7.2048 |  | 6.8825 | 7.1926 |  |  | 7.0089 | 7.0146 | 6.351 | 455104 | 6.7489 |  |  | 459450 | 450 | 459000 | -4346 | -0.9549% | 56.7 | 3010.25
2024-09-07 | 2025 | 2024 | 2024-09-01 | 30 | 14701 | 17420 | 14729 | 10432 | 17066 | 13509 | 11600 | 0 | 14986 | 17906 | 15081 | 17223 | 13758 | 15783 | 16721 | 13284 | 0 | 10718 | 0 | 11518 | 13807 | 0 | 0 | 11480 | 15103 | 15650 | 4.5306 | 4.6813 | 5.4847 | 5.5379 | 5.843 | 6.3788 | 5.7217 |  | 5.6318 | 5.8181 | 5.684 | 5.9265 | 5.3009 | 5.9185 | 5.6897 | 6.0478 |  | 6.0852 |  | 5.7618 | 6.2588 |  |  | 5.8857 | 5.7951 | 5.6201 | 302475 | 5.6953 |  |  | 295650 | 0 | 295650 | 6825 | 2.256% | 56.7 | 931.75
2024-09-08 | 2025 | 2024 | 2024-09-01 | 30 | 8625 | 10916 | 7221 | 9679 | 9370 | 7050 | 8666 | 0 | 8948 | 7503 | 7217 | 8362 | 6666 | 7862 | 7554 | 7721 | 0 | 6872 | 0 | 7650 | 6244 | 0 | 0 | 8367 | 9905 | 7578 | 5.4851 | 5.6522 | 4.2196 | 4.6053 | 4.5967 | 4.9944 | 4.5383 |  | 4.5601 | 4.279 | 4.4603 | 4.6488 | 4.195 | 4.6061 | 4.3869 | 4.5051 |  | 4.6634 |  | 4.4856 | 4.5544 |  |  | 4.5101 | 4.6263 | 4.4666 | 169976 | 4.6209 |  |  | 164700 | 0 | 164700 | 5276 | 3.104% | 56.7 | 1154
2024-09-09 | 2025 | 2024 | 2024-09-01 | 30 | 13121 | 12323 | 11876 | 16561 | 12159 | 12813 | 14723 | 0 | 12285 | 9821 | 10724 | 9378 | 11752 | 11674 | 11407 | 13179 | 0 | 13457 | 0 | 11403 | 10638 | 0 | 0 | 9466 | 12599 | 12468 | 5.7867 | 5.96 | 5.1906 | 5.6303 | 5.7033 | 5.6408 | 5.6169 |  | 5.3855 | 4.8916 | 5.2438 | 5.0974 | 5.1433 | 5.4629 | 5.1704 | 5.352 |  | 5.2648 |  | 5.3918 | 5.0599 |  |  | 5.2656 | 5.6218 | 5.3109 | 253827 | 5.39 |  |  | 247950 | 0 | 247950 | 5877 | 2.315% | 56.7 | 317.75
2024-09-10 | 2025 | 2024 | 2024-09-01 | 30 | 16629 | 20077 | 15739 | 20125 | 20489 | 15832 | 17797 | 0 | 16312 | 13468 | 12709 | 15448 | 16301 | 15942 | 16329 | 17349 | 0 | 14995 | 0 | 16801 | 11962 | 0 | 0 | 15139 | 19086 | 16222 | 5.9778 | 6.2507 | 5.5671 | 5.9703 | 6.1151 | 5.9373 | 5.9495 |  | 5.7626 | 5.3192 | 5.6846 | 5.756 | 5.6143 | 5.9326 | 5.6722 | 5.759 |  | 5.4103 |  | 5.8042 | 5.1342 |  |  | 5.7499 | 5.9247 | 5.6815 | 344751 | 5.7606 |  |  | 337500 | 0 | 337500 | 7251 | 2.103% | 56.7 | 2649.125
2024-09-11 | 2025 | 2024 | 2024-09-01 | 30 | 18135 | 22169 | 17635 | 21133 | 20474 | 20007 | 16332 | 0 | 19187 | 14644 | 16356 | 16401 | 17176 | 17673 | 18175 | 18593 | 0 | 19530 | 0 | 17863 | 15809 | 0 | 0 | 17365 | 20509 | 18544 | 6.7034 | 7.2516 | 5.8406 | 6.1417 | 6.1901 | 6.4176 | 5.9484 |  | 6.1257 | 5.5501 | 5.8494 | 5.8767 | 5.7675 | 6.1199 | 5.9072 | 5.946 |  | 5.9213 |  | 6.0135 | 5.6312 |  |  | 5.8114 | 6.084 | 5.9966 | 383710 | 6.0521 |  |  | 374850 | 0 | 374850 | 8860 | 2.309% | 56.7 | 6621.8448
2024-09-12 | 2025 | 2024 | 2024-09-01 | 30 | 21704 | 31222 | 26345 | 29355 | 25859 | 30457 | 26996 | 0 | 27611 | 28651 | 26646 | 28772 | 24710 | 26598 | 26814 | 30153 | 0 | 29900 | 0 | 20879 | 31605 | 0 | 0 | 30349 | 32111 | 20444 | 6.9523 | 7.0702 | 6.7547 | 7.0279 | 7.384 | 7.4332 | 7.1885 |  | 6.9944 | 6.9544 | 6.9512 | 7.109 | 6.5612 | 7.1522 | 6.8288 | 7.1507 |  | 6.9708 |  | 6.8161 | 7.3114 |  |  | 7.118 | 7.3694 | 7.0134 | 577181 | 7.0529 |  |  | 564300 | 0 | 564300 | 12881 | 2.232% | 56.7 | 4086.125
2024-09-13 | 2025 | 2024 | 2024-09-01 | 30 | 27012 | 30013 | 29169 | 23622 | 30259 | 27487 | 21980 | 0 | 29435 | 27037 | 27853 | 26984 | 21019 | 26439 | 25073 | 21322 | 0 | 28132 | 0 | 24833 | 28908 | 0 | 0 | 8223 | 28564 | 20848 | 6.1157 | 6.1168 | 6.9562 | 6.4741 | 7.1755 | 7.0722 | 6.6415 |  | 7.1094 | 6.7903 | 7.01 | 6.8995 | 6.6179 | 7.1026 | 6.5473 | 6.1399 |  | 6.7149 |  | 6.7412 | 6.9825 |  |  | 6.6905 | 7.1956 | 6.9748 | 534212 | 6.7652 |  |  | 520650 | 0 | 520650 | 13562 | 2.539% | 56.7 | 2966.125
2024-09-14 | 2025 | 2024 | 2024-09-01 | 30 | 19028 | 21764 | 21875 | 19567 | 22662 | 23592 | 14403 | 0 | 21483 | 22679 | 23418 | 21691 | 19526 | 21720 | 21880 | 16541 | 0 | 25586 | 0 | 22092 | 25424 | 0 | 0 | 11149 | 21553 | 22274 | 6.0009 | 6.4533 | 6.143 | 5.9178 | 6.2823 | 6.7936 | 5.6915 |  | 6.2302 | 6.1609 | 6.5181 | 6.1856 | 5.907 | 6.5551 | 6.1494 | 6.1643 |  | 6.4435 |  | 6.3418 | 6.6273 |  |  | 6.5982 | 6.3244 | 6.316 | 439907 | 6.2764 |  |  | 429300 | 0 | 429300 | 10607 | 2.411% | 56.7 | 589
2024-09-15 | 2025 | 2024 | 2024-09-01 | 30 | 18267 | 23842 | 17594 | 22058 | 20965 | 23029 | 14678 | 0 | 18590 | 19662 | 17396 | 19254 | 17621 | 18291 | 18452 | 20563 | 0 | 22851 | 0 | 18635 | 20823 | 0 | 0 | 4359 | 22265 | 19372 | 5.9356 | 6.1515 | 5.8004 | 6.261 | 6.2726 | 6.6554 | 5.9619 |  | 6.0158 | 5.9606 | 5.9246 | 6.1251 | 5.7995 | 6.2238 | 5.9145 | 6.1524 |  | 6.1667 |  | 6.0363 | 6.084 |  |  | 6.3733 | 6.3238 | 6.0372 | 398567 | 6.1036 |  |  | 389250 | 0 | 389250 | 9317 | 2.338% | 56.7 | 2218.375
2024-09-16 | 2025 | 2024 | 2024-09-01 | 30 | 17892 | 17074 | 17086 | 21801 | 18827 | 22169 | 13535 | 0 | 17367 | 14538 | 10975 | 15711 | 15422 | 17257 | 15627 | 18802 | 0 | 20748 | 0 | 17547 | 14936 | 0 | 0 | 5918 | 19578 | 16655 | 4.535 | 4.5531 | 5.6792 | 6.1513 | 5.9274 | 6.5492 | 5.7021 |  | 5.8949 | 5.3742 | 5.5376 | 5.7164 | 5.509 | 6.0765 | 5.6662 | 5.9739 |  | 6.0044 |  | 5.8662 | 5.478 |  |  | 6.4971 | 5.9582 | 5.826 | 349465 | 5.7369 |  |  | 341550 | 0 | 341550 | 7915 | 2.265% | 56.7 | 1680.5
2024-09-17 | 2025 | 2024 | 2024-09-01 | 30 | 6864 | 0 | 7621 | 8787 | 7470 | 10777 | 6633 | 0 | 6923 | 6632 | 7291 | 6857 | 6940 | 7375 | 7275 | 7787 | 0 | 9993 | 0 | 7355 | 7132 | 0 | 0 | 7288 | 6989 | 6283 | 4.7765 | 5.1714 | 4.3902 | 4.4258 | 4.4906 | 5.3634 | 4.3102 |  | 4.4337 | 4.276 | 4.5733 | 4.4675 | 4.4157 | 4.7235 | 4.4391 | 4.6245 |  | 4.7961 |  | 4.6011 | 4.4 |  |  | 4.4737 | 4.4599 | 4.4269 | 150272 | 4.5733 |  |  | 145350 | 0 | 145350 | 4922 | 3.275% | 56.7 | 6201.875
2024-09-18 | 2025 | 2024 | 2024-09-01 | 30 | 9536 | 0 | 8619 | 13361 | 13595 | 9980 | 9849 | 0 | 8656 | 8566 | 8573 | 9140 | 6222 | 9356 | 8904 | 10398 | 0 | 9690 | 0 | 10129 | 10499 | 0 | 0 | 11579 | 13704 | 8699 | 5.0524 | 5.4165 | 4.5109 | 5.0492 | 5.1285 | 5.0313 | 4.7444 |  | 4.6212 | 4.5153 | 4.6703 | 4.7642 | 4.4458 | 4.9144 | 4.5686 | 4.8329 |  | 4.5641 |  | 4.7899 | 4.9354 |  |  | 4.9223 | 5.066 | 4.6045 | 199055 | 4.8166 |  |  | 193950 | 0 | 193950 | 5105 | 2.565% | 56.7 | 796.25
2024-09-19 | 2025 | 2024 | 2024-09-01 | 30 | 11875 | 0 | 11219 | 16612 | 16072 | 12039 | 13320 | 0 | 10708 | 12598 | 11306 | 11565 | 11401 | 12076 | 12143 | 14415 | 0 | 12332 | 0 | 13578 | 13422 | 0 | 0 | 14150 | 14599 | 11268 | 5.7918 | 6.0545 | 4.9227 | 5.4828 | 5.4938 | 5.3919 | 5.2106 |  | 4.8727 | 5.0339 | 5.0432 | 5.104 | 4.8911 | 5.2635 | 5.0497 | 5.3347 |  | 4.9053 |  | 5.2451 | 5.2294 |  |  | 5.2503 | 5.3047 | 4.918 | 256698 | 5.2283 |  |  | 250200 | 0 | 250200 | 6498 | 2.531% | 56.7 | 3613.25
2024-09-20 | 2025 | 2024 | 2024-09-01 | 30 | 14708 | 0 | 13853 | 17901 | 19109 | 15168 | 17159 | 0 | 15658 | 12316 | 13557 | 13714 | 14219 | 7677 | 16236 | 15508 | 0 | 16127 | 0 | 14837 | 13095 | 0 | 0 | 15129 | 17794 | 14666 | 5.4355 | 5.8198 | 5.5651 | 5.9173 | 6.0762 | 6.2433 | 5.8619 |  | 5.7656 | 5.2631 | 5.6422 | 5.652 | 5.5352 | 5.6257 | 5.7392 | 5.6727 |  | 5.6415 |  | 5.6968 | 5.3555 |  |  | 5.5161 | 6.0742 | 5.6496 | 298431 | 5.7023 |  |  | 291600 | 0 | 291600 | 6831 | 2.289% | 56.7 | 2946.25
2024-09-21 | 2025 | 2024 | 2024-09-01 | 30 | 14803 | 0 | 13522 | 21470 | 17563 | 11774 | 18980 | 3424 | 15483 | 14600 | 14460 | 15260 | 14004 | 9308 | 15446 | 17638 | 0 | 18296 | 0 | 16595 | 17922 | 0 | 0 | 16740 | 17743 | 15393 | 5.0793 | 5.1581 | 5.1504 | 5.8782 | 5.6148 | 5.9981 | 5.6353 | 5.12 | 5.5014 | 5.3246 | 5.4274 | 5.4931 | 5.2421 | 4.6424 | 5.4184 | 5.628 |  | 5.5499 |  | 5.5826 | 5.6128 |  |  | 5.5012 | 5.4973 | 5.3756 | 320424 | 5.4287 |  |  | 313200 | 0 | 313200 | 7224 | 2.255% | 56.7 | 2052.625
2024-09-22 | 2025 | 2024 | 2024-09-01 | 30 | 11597 | 4167 | 11483 | 15676 | 15083 | 14078 | 12321 | 9824 | 10251 | 9756 | 11061 | 9831 | 11013 | 11037 | 12815 | 12296 | 0 | 12715 | 0 | 12529 | 10803 | 0 | 0 | 11871 | 14581 | 10855 | 5.5183 | 5.8335 | 4.9251 | 5.2944 | 5.3897 | 5.6245 | 5.0487 | 5 | 4.9064 | 4.694 | 5.019 | 4.9269 | 4.8615 | 5.3576 | 5.1226 | 5.0993 |  | 5.0001 |  | 5.1969 | 4.8563 |  |  | 5.0401 | 5.2519 | 4.879 | 255643 | 5.1294 |  |  | 249300 | 0 | 249300 | 6343 | 2.481% | 56.7 | 41.375
2024-09-23 | 2025 | 2024 | 2024-09-01 | 30 | 14035 | 19709 | 15183 | 18765 | 19140 | 14154 | 15504 | 13907 | 13848 | 12581 | 14879 | 14868 | 15185 | 15246 | 15101 | 10786 | 0 | 13390 | 0 | 16811 | 17353 | 0 | 0 | 18663 | 18634 | 12608 | 5.9369 | 6.2857 | 5.4604 | 5.8148 | 5.8911 | 5.7622 | 5.5695 | 5.4 | 5.4576 | 5.6078 | 5.5855 | 5.665 | 5.4545 | 5.9651 | 5.5126 | 5.6416 |  | 5.2256 |  | 5.7403 | 5.8299 |  |  | 5.8804 | 5.7678 | 5.3725 | 340350 | 5.674 |  |  | 332100 | 0 | 332100 | 8250 | 2.424% | 56.7 | 45.75
2024-09-24 | 2025 | 2024 | 2024-09-01 | 30 | 18054 | 23580 | 15980 | 21745 | 22007 | 16204 | 16820 | 14579 | 16145 | 16002 | 15918 | 15900 | 12769 | 17595 | 15139 | 17688 | 0 | 14347 | 0 | 18604 | 19476 | 0 | 0 | 20669 | 20961 | 18108 | 6.2795 | 6.4745 | 5.5669 | 6.1256 | 6.2609 | 5.9692 | 5.7541 | 5.7 | 5.7716 | 5.5519 | 5.731 | 5.8126 | 5.5876 | 6.2563 | 5.7508 | 5.8468 |  | 5.4473 |  | 5.9801 | 5.9543 |  |  | 6.0922 | 6.089 | 5.8644 | 388290 | 5.903 |  |  | 378450 | 0 | 378450 | 9840 | 2.534% | 59.4 | 7726.75
2024-09-25 | 2025 | 2024 | 2024-09-01 | 30 | 21106 | 25571 | 22079 | 24809 | 26862 | 20891 | 17910 | 14085 | 18422 | 20193 | 21782 | 19573 | 0 | 20968 | 21831 | 23508 | 0 | 18808 | 0 | 22835 | 21886 | 0 | 0 | 22707 | 25006 | 18036 | 5.5453 | 5.599 | 6.271 | 6.5069 | 6.6675 | 6.476 | 6.2481 | 6.1 | 6.0537 | 6.0729 | 6.3825 | 6.2415 | 6.7203 | 6.7401 | 6.2061 | 6.4694 |  | 5.9634 |  | 6.4735 | 6.5688 |  |  | 6.4578 | 6.4289 | 5.9736 | 448868 | 6.2803 |  |  | 438300 | 0 | 438300 | 10568 | 2.354% | 59.4 | 5104.375
2024-09-26 | 2025 | 2024 | 2024-09-01 | 30 | 16244 | 18216 | 13752 | 13738 | 15945 | 10665 | 5169 | 15068 | 15481 | 12439 | 14554 | 14835 | 0 | 14051 | 14179 | 10717 | 0 | 19 | 0 | 13510 | 10123 | 0 | 0 | 13194 | 18423 | 15703 | 6.8654 | 7.2574 | 5.3201 | 5.4562 | 5.6183 | 5.7182 | 5.4894 | 5.3 | 5.4681 | 5.1374 | 5.4312 | 5.5435 | 5.7143 | 5.796 | 5.3128 | 5.4605 |  | 4.8071 |  | 5.6208 | 5.18 |  |  | 5.5366 | 5.6486 | 5.504 | 276025 | 5.5994 |  |  | 268200 | 0 | 268200 | 7825 | 2.835% | 59.4 | 8505.5312
2024-09-27 | 2025 | 2024 | 2024-09-01 | 30 | 30042 | 35475 | 30610 | 21294 | 35359 | 34830 | 26301 | 30524 | 28775 | 30635 | 30533 | 28739 | 12833 | 31798 | 33417 | 34866 | 0 | 13335 | 0 | 33781 | 33580 | 0 | 0 | 35154 | 34403 | 29972 | 5.9698 | 6.2215 | 6.7792 | 7.2556 | 7.3319 | 7.3424 | 6.9405 | 7 | 6.7432 | 6.8095 | 6.9282 | 6.8662 | 6.7068 | 7.2651 | 7.0983 | 7.2954 |  | 6.8573 |  | 7.1916 | 7.2031 |  |  | 7.2297 | 7.1149 | 6.7338 | 656256 | 6.9493 |  |  | 635850 | 450 | 635400 | 20406 | 3.109% | 59.4 | 47121.582
2024-09-28 | 2025 | 2024 | 2024-09-01 | 30 | 19337 | 23025 | 19168 | 20695 | 21504 | 18489 | 17956 | 18313 | 17999 | 16823 | 19284 | 18460 | 18056 | 19891 | 18849 | 19651 | 0 | 16384 | 0 | 18951 | 16952 | 0 | 0 | 20391 | 22376 | 18137 | 3.8737 | 3.8719 | 5.9177 | 6.0222 | 6.1629 | 6.0747 | 5.7148 | 6 | 5.8793 | 5.7083 | 6.0388 | 5.9094 | 5.7285 | 6.1644 | 5.8374 | 6.0033 |  | 5.5648 |  | 5.9656 | 5.7117 |  |  | 5.9898 | 6.1052 | 5.7677 | 420691 | 5.7278 |  |  | 410400 | 0 | 410400 | 10291 | 2.446% | 59.4 | 39069.1912
2024-09-29 | 2025 | 2024 | 2024-09-01 | 30 | 6056 | 6967 | 5601 | 7696 | 7309 | 5482 | 7393 | 5769 | 5434 | 4260 | 5175 | 5403 | 4577 | 5177 | 4979 | 5900 | 0 | 5097 | 0 | 5528 | 4783 | 0 | 0 | 4726 | 7705 | 5237 | 4.3022 | 4.5324 | 3.6112 | 4.011 | 3.8778 | 3.8655 | 3.9241 | 3.4 | 3.7501 | 3.4141 | 3.665 | 3.6886 | 3.5415 | 3.9681 | 3.5963 | 3.7706 |  | 3.6076 |  | 3.7941 | 3.566 |  |  | 3.7254 | 3.9651 | 3.5991 | 126254 | 3.7807 |  |  | 121050 | 900 | 120150 | 5204 | 4.122% | 59.4 | 12572.75
2024-09-30 | 2025 | 2024 | 2024-09-01 | 30 | 7824 | 11628 | 8244 | 11311 | 10961 | 11032 | 9870 | 8327 | 7750 | 8699 | 7601 | 9002 | 7253 | 8384 | 8998 | 10937 | 0 | 9999 | 0 | 9238 | 10855 | 0 | 0 | 10127 | 11424 | 7800 | 3.6764 | 3.6206 | 4.2106 | 4.3962 | 4.5813 | 4.6898 | 4.2104 | 4.4 | 4.2774 | 4.3401 | 4.3234 | 4.4782 | 4.3126 | 4.7396 | 4.3575 | 4.5725 |  | 4.3601 |  | 4.424 | 4.4688 |  |  | 4.5168 | 4.6183 | 4.1933 | 207264 | 4.3531 |  |  | 202050 | 900 | 201150 | 5214 | 2.516% | 59.4 | 3396.125
2024-10-01 | 2025 | 2024 | 2024-10-01 | 31 | 4390 | 6613 | 4413 | 7234 | 6808 | 6932 | 7150 | 4730 | 4655 | 4026 | 4274 | 4760 | 4353 | 4685 | 5218 | 6216 | 0 | 5585 | 0 | 4946 | 5716 | 0 | 0 | 5790 | 6517 | 4850 | 3.7365 | 3.8057 | 3.5001 | 3.625 | 3.7632 | 4.1299 | 3.6824 | 4.3 | 3.5883 | 3.3453 | 3.6126 | 3.5649 | 3.3476 | 3.5827 | 3.5361 | 3.7807 |  | 3.597 |  | 3.6209 | 3.771 |  |  | 3.663 | 4.0064 | 3.5285 | 119861 | 3.6858 |  |  | 114750 | 900 | 113850 | 5111 | 4.264% | 59.4 | 28
2024-10-02 | 2025 | 2024 | 2024-10-01 | 31 | 4482 | 5984 | 3983 | 5695 | 5194 | 6454 | 5347 | 4423 | 4295 | 3657 | 3594 | 3898 | 3562 | 3913 | 4218 | 5082 | 0 | 5172 | 0 | 3910 | 5055 | 0 | 0 | 4792 | 5274 | 4565 | 5.544 | 5.6645 | 3.5592 | 3.8898 | 3.7699 | 4.253 | 3.9698 | 4 | 3.7294 | 3.4833 | 3.6855 | 3.7506 | 3.4993 | 3.8422 | 3.6067 | 3.8647 |  | 3.7062 |  | 3.6907 | 3.867 |  |  | 3.7665 | 3.75 | 3.7315 | 102549 | 3.9374 |  |  | 99000 | 450 | 98550 | 3549 | 3.461% | 59.4 | 68.5
2024-10-03 | 2025 | 2024 | 2024-10-01 | 31 | 13073 | 17668 | 13123 | 17125 | 18994 | 16418 | 16870 | 13899 | 12586 | 10656 | 13319 | 12395 | 10717 | 12854 | 11328 | 14700 | 0 | 15736 | 0 | 13148 | 14137 | 0 | 0 | 13736 | 16684 | 10635 | 5.7842 | 6.0289 | 5.1581 | 5.6144 | 5.8745 | 5.8355 | 5.6697 | 5.3 | 5.2529 | 5.3274 | 5.3714 | 5.2747 | 4.9548 | 5.5008 | 5.0149 | 5.4857 |  | 5.338 |  | 5.35 | 5.2055 |  |  | 5.277 | 5.606 | 5.1452 | 309801 | 5.4259 |  |  | 301500 | 0 | 301500 | 8301 | 2.679% | 59.4 | 2748.625
2024-10-04 | 2025 | 2024 | 2024-10-01 | 31 | 17718 | 21028 | 16449 | 20359 | 19692 | 17305 | 18490 | 16408 | 16049 | 14191 | 14671 | 15733 | 11818 | 16428 | 14961 | 15978 | 0 | 17424 | 0 | 13617 | 14061 | 0 | 0 | 16524 | 18575 | 15242 | 4.6235 | 4.8727 | 5.5342 | 5.9115 | 6.0113 | 6.0497 | 5.8217 | 5.6 | 5.684 | 5.3255 | 5.5417 | 5.6934 | 5.1339 | 5.8775 | 5.4826 | 5.6284 |  | 5.5709 |  | 5.5348 | 5.2862 |  |  | 5.6081 | 5.8672 | 5.4774 | 362721 | 5.5516 |  |  | 354600 | 0 | 354600 | 8121 | 2.239% | 59.4 | 603.75
2024-10-05 | 2025 | 2024 | 2024-10-01 | 31 | 10244 | 13457 | 8394 | 12905 | 11093 | 11856 | 11524 | 9543 | 7473 | 5430 | 6996 | 7120 | 7176 | 7653 | 9462 | 9173 | 0 | 10668 | 0 | 8489 | 7570 | 0 | 0 | 7950 | 12650 | 8927 | 3.6997 | 3.7087 | 4.2824 | 4.7758 | 4.6474 | 4.9981 | 4.6699 | 5.65 | 4.4832 | 3.7763 | 4.3802 | 4.2372 | 4.0798 | 4.4641 | 4.4148 | 4.4472 |  | 4.4749 |  | 4.3544 | 4.0171 |  |  | 4.1854 | 4.8158 | 4.3949 | 205753 | 4.4072 |  |  | 199800 | 450 | 199350 | 5953 | 2.893% | 59.4 | 909.875
2024-10-06 | 2025 | 2024 | 2024-10-01 | 31 | 4032 | 4798 | 3763 | 3548 | 4466 | 4959 | 3340 | 3893 | 4182 | 3037 | 2966 | 4099 | 3774 | 3450 | 3697 | 4351 | 0 | 3493 | 0 | 3513 | 4504 | 0 | 0 | 3966 | 4687 | 4166 | 5.5968 | 5.4338 | 3.5567 | 3.5272 | 3.7964 | 4.2245 | 3.5053 | 3.55 | 3.739 | 3.426 | 3.5367 | 3.9845 | 3.7799 | 3.7117 | 3.6276 | 3.8196 |  | 3.4712 |  | 3.6139 | 3.7964 |  |  | 3.6366 | 3.8077 | 3.7217 | 86684 | 3.8574 |  |  | 81900 | 900 | 81000 | 4784 | 5.519% | 59.4 | 293.25
2024-10-07 | 2025 | 2024 | 2024-10-01 | 31 | 16588 | 16453 | 13975 | 12785 | 15901 | 9417 | 13187 | 14442 | 16537 | 11380 | 13393 | 13188 | 13034 | 13011 | 12072 | 11416 | 0 | 10390 | 0 | 11321 | 11104 | 0 | 0 | 10222 | 18054 | 15152 | 4.4517 | 4.3187 | 5.1311 | 5.13 | 5.4871 | 5.2433 | 5.2447 | 5.27 | 5.5003 | 5.0018 | 5.2223 | 5.2992 | 5.0919 | 5.2655 | 5.1216 | 5.154 |  | 4.6678 |  | 4.9945 | 5.1648 |  |  | 4.7738 | 5.6536 | 5.3017 | 293022 | 5.1132 |  |  | 285300 | 0 | 285300 | 7722 | 2.635% | 59.4 | 3170.25
2024-10-08 | 2025 | 2024 | 2024-10-01 | 31 | 8945 | 8949 | 7697 | 6515 | 8847 | 11169 | 7376 | 7727 | 8489 | 6698 | 6027 | 7994 | 8246 | 7009 | 7964 | 8380 | 0 | 5970 | 0 | 6594 | 10670 | 0 | 0 | 10035 | 10223 | 7154 | 4.3501 | 4.1248 | 4.2888 | 3.9823 | 4.3783 | 5.093 | 4.2065 | 4.5 | 4.4856 | 4.1986 | 4.251 | 4.5933 | 4.3053 | 4.3237 | 4.3308 | 4.564 |  | 3.8801 |  | 4.2525 | 4.6504 |  |  | 4.4833 | 4.5424 | 4.2121 | 178678 | 4.3635 |  |  | 172800 | 0 | 172800 | 5878 | 3.29% | 59.4 | 248.8655
2024-10-09 | 2025 | 2024 | 2024-10-01 | 31 | 7458 | 6673 | 7088 | 5271 | 6421 | 3444 | 5090 | 4306 | 5985 | 5868 | 6128 | 6117 | 5313 | 5421 | 5617 | 5071 | 0 | 2854 | 0 | 4127 | 3336 | 0 | 0 | 5226 | 7291 | 6787 | 5.2414 | 5.2209 | 4.2178 | 4.0209 | 4.1985 | 3.9927 | 4.1179 | 4.1592 | 4.3058 | 3.977 | 4.201 | 4.2045 | 4.0252 | 4.0756 | 3.959 | 4.1743 |  | 3.7456 |  | 3.9037 | 3.7716 |  |  | 4.1628 | 4.2977 | 4.1335 | 120892 | 4.1867 |  |  | 118800 | 0 | 118800 | 2092 | 1.73% | 59.4 | 0
2024-10-10 | 2025 | 2024 | 2024-10-01 | 31 | 16564 | 16826 | 13227 | 11983 | 16327 | 14571 | 10256 | 14888 | 13295 | 14006 | 12711 | 15897 | 14636 | 13669 | 15708 | 20397 | 0 | 12797 | 0 | 15774 | 19869 | 0 | 0 | 19321 | 18086 | 13048 | 6.8813 | 6.6147 | 4.8071 | 4.6626 | 5.2874 | 6.0136 | 5.0201 | 5.1013 | 4.8244 | 4.9747 | 4.9222 | 5.3132 | 5.1094 | 5.2361 | 5.2162 | 5.8625 |  | 4.8214 |  | 5.5009 | 5.7988 |  |  | 5.6035 | 5.4251 | 4.7075 | 333856 | 5.3502 |  |  | 324000 | 450 | 323550 | 9856 | 2.952% | 59.4 | 34581
2024-10-11 | 2025 | 2024 | 2024-10-01 | 31 | 28593 | 26552 | 21877 | 20584 | 28998 | 33571 | 22099 | 26103 | 24453 | 26298 | 21009 | 23587 | 26108 | 22076 | 26695 | 30534 | 0 | 21157 | 0 | 23075 | 31805 | 0 | 0 | 18037 | 31212 | 22374 | 5.3109 | 5.0249 | 6.4865 | 6.0274 | 6.8702 | 7.3344 | 6.1988 | 6.5358 | 6.5222 | 6.5729 | 6.1918 | 6.3906 | 6.5726 | 6.5684 | 6.6047 | 7.013 |  | 6.3539 |  | 6.3693 | 7.1131 |  |  | 6.6363 | 6.9404 | 6.1735 | 556797 | 6.446 |  |  | 541800 | 0 | 541800 | 14997 | 2.693% | 59.4 | 15159.563
2024-10-12 | 2025 | 2024 | 2024-10-01 | 31 | 15030 | 12140 | 13735 | 10980 | 12203 | 18305 | 11827 | 14331 | 13232 | 14278 | 11816 | 14740 | 12397 | 10795 | 15355 | 16855 | 0 | 10301 | 0 | 14939 | 17644 | 0 | 0 | 15663 | 14932 | 9377 | 4.1715 | 3.9537 | 5.1249 | 4.826 | 5.2153 | 5.7657 | 4.959 | 5.1355 | 5.126 | 5.2171 | 5.0337 | 5.3777 | 4.9725 | 5.0724 | 5.3103 | 5.4967 |  | 4.6106 |  | 5.3275 | 5.6004 |  |  | 5.314 | 5.2389 | 4.8763 | 300875 | 5.0784 |  |  | 294300 | 0 | 294300 | 6575 | 2.185% | 59.4 | 19222.002
2024-10-13 | 2025 | 2024 | 2024-10-01 | 31 | 7297 | 6913 | 6487 | 4789 | 6794 | 6848 | 3575 | 5900 | 6985 | 5394 | 5015 | 6091 | 5233 | 5089 | 5923 | 6255 | 0 | 4896 | 586 | 5402 | 6489 | 0 | 0 | 5602 | 8271 | 6277 | 4.0002 | 3.7548 | 3.994 | 3.6771 | 4.0894 | 4.2881 | 3.6506 | 3.8074 | 4.2919 | 3.8451 | 3.8301 | 4.0713 | 3.8013 | 3.9079 | 3.8558 | 4.0669 |  | 3.6671 | 3.1415 | 3.9176 | 4.0729 |  |  | 3.9409 | 4.2725 | 3.9276 | 132111 | 3.9075 |  |  | 126900 | 450 | 126450 | 5211 | 3.944% | 59.4 | 9177.875
2024-10-14 | 2025 | 2024 | 2024-10-01 | 31 | 7370 | 7143 | 5491 | 6530 | 6553 | 7749 | 4621 | 5596 | 6296 | 5659 | 5125 | 5955 | 5490 | 5562 | 5950 | 6061 | 0 | 6995 | 6865 | 5826 | 6352 | 0 | 0 | 6022 | 7249 | 6119 | 3.427 | 3.124 | 3.6034 | 3.6794 | 3.8675 | 4.153 | 3.7723 | 3.6838 | 3.8415 | 3.6633 | 3.7036 | 3.7928 | 3.6972 | 3.831 | 3.7343 | 3.8999 |  | 3.9562 | 3.9527 | 3.8284 | 3.8872 |  |  | 3.826 | 3.9228 | 3.7744 | 142579 | 3.7662 |  |  | 136800 | 450 | 136350 | 5779 | 4.053% | 59.4 | 13123.25
2024-10-15 | 2025 | 2024 | 2024-10-01 | 31 | 2216 | 1790 | 2403 | 1405 | 1784 | 782 | 1533 | 1515 | 2571 | 1474 | 2212 | 1959 | 1517 | 1989 | 1785 | 1230 | 0 | 1465 | 1775 | 1437 | 1077 | 0 | 0 | 1672 | 2451 | 2214 | 4.4183 | 4.0006 | 3.3945 | 3.0188 | 3.3393 | 2.8294 | 3.075 | 3.0076 | 3.4754 | 3.2008 | 3.3921 | 3.3353 | 3.0644 | 3.2988 | 3.212 | 2.9436 |  | 3.0569 | 3.1481 | 3.0636 | 3.063 |  |  | 3.0764 | 3.2464 | 3.2618 | 40256 | 3.2575 |  |  | 38700 | 1350 | 37350 | 1556 | 3.865% | 59.4 | 0
2024-10-16 | 2025 | 2024 | 2024-10-01 | 31 | 10137 | 7316 | 7857 | 5066 | 7381 | 2206 | 4687 | 7197 | 5386 | 5284 | 7724 | 6228 | 2713 | 7441 | 6835 | 4041 | 0 | 4072 | 4528 | 3937 | 1651 | 0 | 0 | 4775 | 9241 | 8658 | 3.9772 | 3.9327 | 4.121 | 4.3997 | 4.0711 | 3.9014 | 4.5499 | 3.7892 | 4.3369 | 4.1337 | 4.1831 | 4.2346 | 3.9297 | 4.2068 | 3.9838 | 4.2936 |  | 4.117 | 4.4313 | 4.1897 | 3.7963 |  |  | 4.39 | 4.3045 | 4.1376 | 134361 | 4.1483 |  |  | 129150 | 450 | 128700 | 5211 | 3.878% | 62.1 | 3783.875
2024-10-17 | 2025 | 2024 | 2024-10-01 | 31 | 6961 | 7406 | 5777 | 5449 | 7598 | 5639 | 4176 | 5145 | 5313 | 6025 | 5157 | 5350 | 2405 | 5018 | 6975 | 5518 | 0 | 5088 | 5307 | 5218 | 5621 | 140 | 0 | 6071 | 7972 | 6008 | 4.0738 | 3.8623 | 3.7924 | 3.8167 | 4.0915 | 4.223 | 3.6789 | 3.5853 | 3.7818 | 3.8236 | 3.7692 | 3.8728 | 3.6264 | 3.754 | 3.8538 | 4.0785 |  | 3.8565 | 3.8398 | 3.9136 | 4.1171 | 3.21 |  | 3.9689 | 4.0951 | 3.7785 | 131337 | 3.8526 |  |  | 126900 | 0 | 126900 | 4437 | 3.378% | 62.1 | 870.375
2024-10-18 | 2025 | 2024 | 2024-10-01 | 31 | 4437 | 3995 | 4322 | 3359 | 3749 | 6621 | 5605 | 4182 | 5022 | 3539 | 3713 | 3807 | 3463 | 3610 | 3211 | 6834 | 0 | 6713 | 7172 | 5525 | 7056 | 3396 | 0 | 7000 | 5253 | 4332 | 4.6036 | 4.5375 | 3.9889 | 3.7726 | 3.9418 | 4.0404 | 3.8431 | 3.9788 | 4.2502 | 3.8239 | 3.8713 | 4.0683 | 3.8349 | 3.8781 | 3.7215 | 4.0947 |  | 3.9099 | 4.1131 | 3.917 | 4.1083 | 4.3152 |  | 3.9797 | 4.0734 | 3.9083 | 115916 | 4.0239 |  |  | 114300 | 450 | 113850 | 1616 | 1.394% | 62.1 | 909.875
2024-10-19 | 2025 | 2024 | 2024-10-01 | 31 | 8855 | 6160 | 7647 | 5146 | 7664 | 4759 | 4537 | 6202 | 7492 | 7176 | 7440 | 6457 | 7808 | 7357 | 7303 | 5943 | 0 | 5220 | 5425 | 5377 | 5128 | 4054 | 0 | 6331 | 9365 | 6670 | 2.7258 | 2.641 | 4.3473 | 3.7863 | 4.4437 | 3.4998 | 3.6082 | 4.5295 | 4.4547 | 4.2869 | 4.3477 | 4.2747 | 4.3992 | 4.474 | 4.3306 | 3.781 |  | 3.4388 | 3.6552 | 3.7677 | 3.4962 | 3.7695 |  | 3.7836 | 4.7395 | 4.3424 | 155516 | 3.9551 |  |  | 149400 | 900 | 148500 | 6116 | 3.933% | 62.1 | 16224.25
2024-10-20 | 2025 | 2024 | 2024-10-01 | 31 | 4055 | 2228 | 3520 | 3979 | 2962 | 4878 | 3523 | 2634 | 3134 | 2569 | 2555 | 2678 | 1663 | 2382 | 1736 | 4787 | 0 | 5022 | 4531 | 4692 | 3734 | 3920 | 0 | 4256 | 2705 | 2737 | 3.3635 | 3.234 | 2.907 | 2.6302 | 2.7086 | 3.0941 | 2.5938 | 2.801 | 2.921 | 2.8106 | 2.8519 | 2.7511 | 2.7164 | 2.8108 | 2.7052 | 2.9766 |  | 3.0735 | 2.7444 | 2.9519 | 3.0845 | 3.3378 |  | 2.9406 | 2.7448 | 2.8915 | 80880 | 2.9019 |  |  | 74400 | 3150 | 71250 | 6480 | 8.012% | 62.1 | 9567.25
2024-10-21 | 2025 | 2024 | 2024-10-01 | 31 | 2971 | 3108 | 2894 | 2413 | 2908 | 3845 | 1737 | 2725 | 3299 | 3158 | 2658 | 3061 | 2567 | 2720 | 3230 | 3151 | 0 | 3828 | 3432 | 2990 | 3524 | 3561 | 0 | 3017 | 3394 | 2917 | 3.3556 | 3.1804 | 3.3742 | 3.0907 | 3.291 | 3.5446 | 3.1626 | 3.2554 | 3.4507 | 3.4404 | 3.4187 | 3.4049 | 3.2518 | 3.3907 | 3.3677 | 3.3769 |  | 3.4205 | 3.1544 | 3.3693 | 3.4166 | 3.4764 |  | 3.3157 | 3.2994 | 3.4126 | 73108 | 3.3425 |  |  | 69300 | 1350 | 67950 | 3808 | 5.209% | 64.8 | 1514
2024-10-22 | 2025 | 2024 | 2024-10-01 | 31 | 3161 | 3143 | 2583 | 2742 | 2871 | 2984 | 2953 | 2551 | 3220 | 2658 | 2192 | 2757 | 2247 | 1952 | 2658 | 2803 | 0 | 3452 | 3672 | 2655 | 3327 | 1870 | 0 | 2753 | 3555 | 3218 | 4.5655 | 4.2615 | 3.2145 | 3.0602 | 3.2683 | 3.4788 | 3.2987 | 3.1306 | 3.4318 | 3.1642 | 3.2022 | 3.316 | 3.1554 | 2.9949 | 3.1618 | 3.3128 |  | 3.214 | 3.3912 | 3.3094 | 3.3482 | 3.5049 |  | 3.1677 | 3.3137 | 3.3223 | 67977 | 3.3579 |  |  | 63000 | 450 | 62550 | 4977 | 7.322% | 64.8 | 543.375
2024-10-23 | 2025 | 2024 | 2024-10-01 | 31 | 9022 | 7576 | 7972 | 6196 | 7524 | 6342 | 5443 | 5378 | 8869 | 7954 | 7761 | 7760 | 6360 | 5388 | 7964 | 5208 | 0 | 7896 | 7125 | 5683 | 6183 | 7812 | 0 | 6734 | 8418 | 8358 | 4.6347 | 4.2157 | 4.3232 | 4.0015 | 4.3994 | 4.1695 | 3.9939 | 3.7644 | 4.5952 | 4.3393 | 4.4074 | 4.4242 | 4.0721 | 3.8798 | 4.2469 | 4.1033 |  | 4.2036 | 4.3348 | 4.0435 | 4.0881 | 4.4122 |  | 4.2157 | 4.4316 | 4.4087 | 170926 | 4.2379 |  |  | 165150 | 0 | 165150 | 5776 | 3.379% | 64.8 | 357.75
2024-10-24 | 2025 | 2024 | 2024-10-01 | 31 | 11827 | 9016 | 11711 | 6355 | 9623 | 7763 | 5029 | 7706 | 13317 | 11786 | 10943 | 10928 | 8163 | 10562 | 9991 | 7173 | 0 | 9074 | 6677 | 7205 | 7799 | 8015 | 0 | 8284 | 11302 | 8891 | 4.5244 | 4.278 | 4.5955 | 3.8321 | 4.3574 | 4.2136 | 3.696 | 4.3985 | 4.8326 | 4.6001 | 4.603 | 4.556 | 4.1352 | 4.7396 | 4.3962 | 4.0802 |  | 4.2915 | 4.0127 | 4.1471 | 4.3247 | 4.3751 |  | 4.1944 | 4.5292 | 4.2969 | 219140 | 4.3338 |  |  | 214200 | 0 | 214200 | 4940 | 2.254% | 64.8 | 1363.625
2024-10-25 | 2025 | 2024 | 2024-10-01 | 31 | 9740 | 9023 | 11466 | 7335 | 9742 | 7669 | 5833 | 6147 | 10671 | 10194 | 11179 | 9863 | 8590 | 9497 | 10059 | 6843 | 0 | 9206 | 6233 | 9226 | 7989 | 8063 | 0 | 7043 | 10806 | 10353 | 2.5785 | 2.414 | 4.5707 | 4.1828 | 4.4714 | 4.3348 | 4.023 | 4.4263 | 4.6426 | 4.5835 | 4.6676 | 4.46 | 4.2456 | 4.667 | 4.4388 | 4.1942 |  | 4.3589 | 4.0831 | 4.5312 | 4.323 | 4.502 |  | 4.2667 | 4.5507 | 4.4549 | 212770 | 4.2488 |  |  | 206100 | 0 | 206100 | 6670 | 3.135% | 64.8 | 779.125
2024-10-26 | 2025 | 2024 | 2024-10-01 | 31 | 801 | 684 | 683 | 935 | 685 | 1076 | 693 | 40 | 933 | 892 | 729 | 978 | 494 | 643 | 786 | 941 | 0 | 1379 | 834 | 923 | 890 | 1123 | 106 | 1057 | 757 | 678 | 4.1447 | 4.1449 | 2.5298 | 2.3535 | 2.4668 | 2.5457 | 2.3122 | 2.2621 | 2.6153 | 2.48 | 2.4228 | 2.4505 | 2.2415 | 2.4181 | 2.4334 | 2.5217 |  | 2.6382 | 2.3603 | 2.492 | 2.518 | 2.6008 | 2.56 | 2.5267 | 2.4969 | 2.5995 | 19740 | 2.6054 |  |  | 17550 | 450 | 17100 | 2190 | 11.09% | 64.8 | 0
2024-10-27 | 2025 | 2024 | 2024-10-01 | 31 | 7333 | 5878 | 6510 | 6888 | 8083 | 5574 | 4751 | 3467 | 7340 | 5118 | 5610 | 6551 | 5835 | 6110 | 5685 | 5846 | 0 | 5867 | 3664 | 6038 | 5856 | 6430 | 4485 | 6233 | 8109 | 7019 | 4.1518 | 4.2199 | 4.062 | 4.0273 | 4.2276 | 3.9453 | 3.6399 | 4.0045 | 4.2585 | 3.8494 | 4.037 | 4.0237 | 3.8297 | 4.062 | 3.8741 | 3.9942 |  | 3.8767 | 3.2706 | 3.9239 | 4.0033 | 4.2864 | 4 | 3.929 | 4.1842 | 4.0589 | 150280 | 3.9896 |  |  | 144000 | 2700 | 141300 | 6280 | 4.179% | 64.8 | 1150.5
2024-10-28 | 2025 | 2024 | 2024-10-01 | 31 | 9793 | 11390 | 12049 | 11538 | 10679 | 11218 | 7875 | 8311 | 10863 | 8721 | 11408 | 10625 | 10877 | 10416 | 10812 | 10128 | 0 | 4317 | 10446 | 10217 | 9958 | 11806 | 1761 | 10909 | 10891 | 8829 | 4.2149 | 4.3648 | 4.7117 | 4.3771 | 4.147 | 4.9617 | 3.9809 | 3.9147 | 4.573 | 4.4012 | 4.707 | 4.4325 | 4.5199 | 4.6465 | 4.5914 | 4.6946 |  | 4.9539 | 4.2679 | 4.702 | 4.794 | 5.1207 | 3.6037 | 4.639 | 4.1578 | 4.089 | 245837 | 4.4627 |  |  | 250650 | 900 | 249750 | -4813 | -1.958% | 64.8 | 521.375
2024-10-29 | 2025 | 2024 | 2024-10-01 | 31 | 8625 | 10756 | 6875 | 9102 | 10945 | 6245 | 7372 | 7109 | 7267 | 5169 | 6226 | 7921 | 6669 | 6662 | 6091 | 7873 | 0 | 5470 | 5019 | 6778 | 7344 | 8028 | 7838 | 8940 | 11255 | 7552 | 4.0291 | 3.8265 | 3.8829 | 4.0885 | 4.4644 | 3.7693 | 3.9231 | 3.8241 | 3.9951 | 3.667 | 3.8928 | 4.1285 | 3.8983 | 4.0522 | 3.7673 | 4.1445 |  | 3.4 | 3.4935 | 3.9355 | 3.9481 | 3.9807 | 4.0801 | 4.1824 | 4.4553 | 3.9617 | 189131 | 3.9516 |  |  | 181350 | 0 | 181350 | 7781 | 4.114% | 67.5 | 1537.25
2024-10-30 | 2025 | 2024 | 2024-10-01 | 31 | 6214 | 5707 | 6075 | 5315 | 5832 | 4825 | 4846 | 4649 | 6447 | 5161 | 5504 | 5362 | 4068 | 5016 | 4681 | 5045 | 0 | 4920 | 4887 | 4505 | 4504 | 5240 | 5750 | 5433 | 6245 | 5234 | 5.2463 | 4.9206 | 3.9019 | 3.7858 | 3.9556 | 3.7077 | 3.7775 | 3.5435 | 4.016 | 3.6392 | 3.7915 | 3.7347 | 3.4483 | 3.8276 | 3.5321 | 3.7794 |  | 3.67 | 3.6825 | 3.6485 | 3.6594 | 3.8349 | 3.7979 | 3.8383 | 3.9482 | 3.7096 | 131465 | 3.8559 |  |  | 126900 | 450 | 126450 | 4565 | 3.472% | 67.5 | 15.125
2024-10-31 | 2025 | 2024 | 2024-10-01 | 31 | 15206 | 12342 | 13396 | 9899 | 13119 | 8365 | 9496 | 10106 | 14092 | 12107 | 12399 | 12250 | 10223 | 10695 | 10508 | 10326 | 0 | 11093 | 9341 | 9731 | 8697 | 10870 | 12437 | 11663 | 13652 | 14066 | 4.0727 | 3.4116 | 4.9917 | 4.5368 | 4.9947 | 4.4285 | 4.6217 | 4.5276 | 5.2067 | 4.8298 | 4.8976 | 4.9329 | 4.6447 | 4.9991 | 4.7919 | 4.7153 |  | 4.5 | 4.6572 | 4.6943 | 4.5817 | 4.8672 | 4.9119 | 4.7212 | 5.0356 | 5.0642 | 286079 | 4.7055 |  |  | 278550 | 0 | 278550 | 7529 | 2.632% | 67.5 | 581.125
2024-11-01 | 2025 | 2024 | 2024-11-01 | 30 | 7636 | 4722 | 8123 | 5557 | 6954 | 3847 | 4201 | 7047 | 7948 | 7044 | 7132 | 7501 | 3389 | 6296 | 5828 | 5423 | 0 | 5788 | 4301 | 4803 | 3531 | 5348 | 7324 | 6537 | 7190 | 7635 | 2.8227 | 2.7134 | 4.0495 | 3.5701 | 3.9394 | 3.3958 | 3.5446 | 3.7274 | 4.1036 | 3.9734 | 3.9286 | 3.9372 | 3.1287 | 3.9451 | 3.7525 | 3.639 |  | 3.42 | 3.4909 | 3.4814 | 3.4186 | 3.6648 | 3.961 | 3.7592 | 3.9633 | 3.9719 | 151105 | 3.6521 |  |  | 145800 | 1350 | 144450 | 5305 | 3.511% | 67.5 | 289.125
2024-11-02 | 2025 | 2024 | 2024-11-01 | 30 | 1874 | 2077 | 1782 | 1519 | 1953 | 1061 | 1465 | 1642 | 1562 | 1433 | 1173 | 1753 | 1169 | 999 | 1536 | 1764 | 0 | 1493 | 1292 | 1425 | 1112 | 1489 | 1743 | 1451 | 2065 | 1623 | 2.7978 | 2.7425 | 2.7669 | 2.5997 | 2.7832 | 2.5717 | 2.6233 | 2.5492 | 2.6831 | 2.6608 | 2.5344 | 2.6197 | 2.5047 | 2.5894 | 2.6689 | 2.7101 |  | 2.54 | 2.5808 | 2.6273 | 2.6031 | 2.7045 | 2.5977 | 2.6411 | 2.7501 | 2.5665 | 38455 | 2.6407 |  |  | 35100 | 1800 | 33300 | 3355 | 8.724% | 67.5 | 159.375
2024-11-03 | 2025 | 2024 | 2024-11-01 | 30 | 2105 | 1724 | 1466 | 1431 | 1672 | 2815 | 1908 | 1723 | 1410 | 1566 | 1439 | 2124 | 1749 | 1459 | 1821 | 2341 | 0 | 1640 | 1758 | 1878 | 2577 | 2782 | 1841 | 2085 | 2091 | 1475 | 2.9866 | 2.7762 | 2.555 | 2.61 | 2.7773 | 3.0353 | 2.8382 | 2.6551 | 2.4522 | 2.6361 | 2.5872 | 2.7465 | 2.6906 | 2.6081 | 2.7527 | 3.0631 |  | 2.59 | 2.8384 | 2.8416 | 3.015 | 3.0687 | 2.6031 | 2.8437 | 2.9245 | 2.4656 | 46880 | 2.7584 |  |  | 43650 | 2250 | 41400 | 3230 | 6.89% | 67.5 | 0
2024-11-04 | 2025 | 2024 | 2024-11-01 | 30 | 1814 | 1617 | 1405 | 1540 | 1398 | 1803 | 1751 | 1298 | 1833 | 1394 | 1069 | 1637 | 1210 | 1138 | 1471 | 1616 | 0 | 1102 | 1977 | 1237 | 1615 | 1900 | 1682 | 1627 | 1828 | 1564 | 4.748 | 4.5743 | 2.8507 | 2.7758 | 2.8079 | 2.9189 | 2.9034 | 2.6435 | 2.9177 | 2.8949 | 2.7103 | 2.8555 | 2.7141 | 2.7408 | 2.8856 | 2.9595 |  | 2.8 | 2.9564 | 2.8252 | 2.8785 | 3.0816 | 2.8786 | 2.8665 | 2.8968 | 2.7935 | 38526 | 2.9951 |  |  | 34200 | 1350 | 32850 | 4326 | 11.23% | 67.5 | 0
2024-11-05 | 2025 | 2024 | 2024-11-01 | 30 | 9865 | 9145 | 9904 | 8320 | 8321 | 5571 | 8695 | 8138 | 11398 | 7784 | 7978 | 8215 | 7816 | 7903 | 6638 | 7299 | 0 | 5758 | 9529 | 5876 | 6796 | 7615 | 8589 | 8317 | 10128 | 9568 | 5.2193 | 5.1608 | 4.6429 | 4.4237 | 4.5297 | 4.0214 | 4.5034 | 4.3315 | 4.8933 | 4.3824 | 4.3778 | 4.5467 | 4.3822 | 4.451 | 4.1478 | 4.4183 |  | 4.6 | 4.7204 | 4.1489 | 4.381 | 4.5984 | 4.6381 | 4.4896 | 4.6632 | 4.5914 | 205166 | 4.5305 |  |  | 198900 | 0 | 198900 | 6266 | 3.054% | 67.5 | 471.75
2024-11-06 | 2025 | 2024 | 2024-11-01 | 30 | 13438 | 12392 | 13094 | 9000 | 12340 | 7395 | 8568 | 10810 | 12470 | 11203 | 11077 | 10899 | 9165 | 9716 | 10288 | 9076 | 0 | 5372 | 10478 | 8744 | 8148 | 11155 | 9933 | 9848 | 13970 | 12487 | 4.9187 | 4.1752 | 5.101 | 4.5894 | 5.1715 | 4.4279 | 4.6483 | 4.8134 | 5.2476 | 4.9367 | 4.9182 | 4.9497 | 4.6303 | 4.9027 | 4.7385 | 4.7392 |  | 4.5235 | 4.9058 | 4.6706 | 4.6427 | 4.9669 | 4.9717 | 4.7335 | 5.2803 | 5.0513 | 261066 | 4.8262 |  |  | 259200 | 0 | 259200 | 1866 | 0.7148% | 67.5 | 1785.625
2024-11-07 | 2025 | 2024 | 2024-11-01 | 30 | 13836 | 7626 | 11123 | 8819 | 11131 | 9477 | 7313 | 12460 | 12283 | 12549 | 10720 | 11339 | 6700 | 10541 | 11795 | 8519 | 0 | 9949 | 7735 | 10492 | 9108 | 9368 | 10243 | 9425 | 10942 | 10463 | 3.6031 | 3.3594 | 4.6267 | 4.172 | 4.6453 | 4.3481 | 4.0704 | 4.6089 | 4.8727 | 4.7115 | 4.6067 | 4.6819 | 3.9998 | 4.6947 | 4.5651 | 4.2952 |  | 4.3188 | 4.2126 | 4.439 | 4.3234 | 4.7288 | 4.8749 | 4.3411 | 4.7808 | 4.63 | 253956 | 4.4204 |  |  | 245700 | 0 | 245700 | 8256 | 3.251% | 67.5 | 7758.375
2024-11-08 | 2025 | 2024 | 2024-11-01 | 30 | 4250 | 3528 | 3519 | 2507 | 3200 | 1569 | 2595 | 2560 | 4024 | 2608 | 2440 | 2681 | 2408 | 2307 | 2092 | 1921 | 0 | 2638 | 1496 | 1686 | 1934 | 2242 | 2994 | 2472 | 3987 | 3891 | 5.2103 | 5.0431 | 3.5126 | 3.0482 | 3.3175 | 2.9906 | 3.1367 | 3.1061 | 3.6734 | 3.2854 | 3.3738 | 3.2872 | 3.2053 | 3.3871 | 3.1212 | 3.0867 |  | 3.1728 | 2.9808 | 2.9788 | 3.1021 | 3.2132 | 3.4888 | 3.1733 | 3.4773 | 3.4485 | 67549 | 3.3928 |  |  | 62550 | 900 | 61650 | 4999 | 7.401% | 67.5 | 33.625
2024-11-09 | 2025 | 2024 | 2024-11-01 | 30 | 14219 | 13268 | 11532 | 10325 | 7981 | 7812 | 9205 | 10580 | 12195 | 10183 | 10515 | 11018 | 7935 | 10092 | 9982 | 8782 | 0 | 8179 | 8312 | 8563 | 7693 | 9105 | 1095 | 9895 | 12269 | 12790 | 3.6329 | 3.5065 | 4.8955 | 4.5917 | 5.1401 | 4.4715 | 4.4686 | 4.6542 | 5.0225 | 4.7343 | 4.784 | 4.8894 | 4.3385 | 4.933 | 4.6653 | 4.6311 |  | 4.3639 | 4.4284 | 4.6017 | 4.4989 | 4.687 | 4.9482 | 4.7209 | 5.1287 | 4.9413 | 243525 | 4.6271 |  |  | 236700 | 0 | 236700 | 6825 | 2.803% | 67.5 | 1587.375
2024-11-10 | 2025 | 2024 | 2024-11-01 | 30 | 4899 | 4778 | 3662 | 3946 | 4340 | 3404 | 4023 | 3701 | 4548 | 3420 | 3136 | 4196 | 3478 | 3467 | 3391 | 3402 | 0 | 3757 | 4211 | 3117 | 3516 | 4065 | 4117 | 3887 | 5082 | 4932 | 4.1904 | 4.0213 | 3.4904 | 3.2219 | 3.5138 | 3.3588 | 3.3798 | 3.3145 | 3.657 | 3.3988 | 3.3488 | 3.544 | 3.3858 | 3.5264 | 3.361 | 3.3974 |  | 3.3254 | 3.4288 | 3.3553 | 3.4019 | 3.5263 | 3.4637 | 3.4215 | 3.5953 | 3.5193 | 98475 | 3.4859 |  |  | 93600 | 1359 | 92241 | 4875 | 4.95% | 67.5 | 219.375
2024-11-11 | 2025 | 2024 | 2024-11-01 | 30 | 5983 | 5717 | 6672 | 4243 | 4773 | 4596 | 4550 | 5481 | 7245 | 4539 | 4690 | 5373 | 4554 | 4256 | 4421 | 4526 | 0 | 4431 | 5608 | 3957 | 4851 | 5333 | 5686 | 4214 | 6130 | 6229 | 4.2072 | 4.0908 | 4.1931 | 3.5912 | 3.8902 | 3.8456 | 3.7014 | 3.9117 | 4.3535 | 3.8133 | 3.8351 | 4.0383 | 3.8522 | 3.9607 | 3.7793 | 3.8435 |  | 3.6019 | 3.9496 | 3.7848 | 3.9214 | 3.9878 | 4.0769 | 3.6876 | 4.1185 | 4.0919 | 128058 | 3.9251 |  |  | 122400 | 0 | 122400 | 5658 | 4.418% | 67.5 | 0
2024-11-12 | 2025 | 2024 | 2024-11-01 | 30 | 6448 | 6242 | 5773 | 5115 | 5529 | 6049 | 5025 | 5573 | 6428 | 5233 | 4633 | 5948 | 5717 | 4997 | 5443 | 5861 | 0 | 4565 | 5909 | 4975 | 6059 | 6509 | 5972 | 6079 | 6195 | 6285 | 4.3283 | 4.2994 | 4.0313 | 3.8038 | 4.0467 | 4.1817 | 3.9026 | 3.9063 | 4.1708 | 3.9797 | 3.8714 | 4.1529 | 4.0564 | 4.1035 | 4.0024 | 4.1251 |  | 3.6675 | 3.9992 | 3.9649 | 4.1489 | 4.2162 | 4.0495 | 4.1158 | 4.1131 | 4.0647 | 142562 | 4.0521 |  |  | 136800 | 0 | 136800 | 5762 | 4.042% | 67.5 | 45.875
2024-11-13 | 2025 | 2024 | 2024-11-01 | 30 | 7567 | 7714 | 6671 | 6173 | 7289 | 7594 | 6597 | 6665 | 7712 | 6305 | 5637 | 6964 | 6976 | 6497 | 6994 | 7551 | 0 | 6050 | 7632 | 6395 | 8315 | 8917 | 7239 | 6425 | 8473 | 7141 | 4.9209 | 4.7173 | 4.1341 | 3.9306 | 4.3423 | 4.6577 | 4.1979 | 4.0767 | 4.3291 | 4.1597 | 3.9997 | 4.2394 | 4.2287 | 4.3456 | 4.2424 | 4.4926 |  | 4.0428 | 4.3626 | 4.2838 | 4.6175 | 4.6658 | 4.2065 | 4.1588 | 4.4206 | 4.1749 | 177493 | 4.3179 |  |  | 171450 | 0 | 171450 | 6043 | 3.405% | 67.5 | 3299.375
2024-11-14 | 2025 | 2024 | 2024-11-01 | 30 | 11055 | 9996 | 10555 | 7751 | 9726 | 14351 | 8820 | 10612 | 9890 | 10478 | 9562 | 11306 | 10266 | 8867 | 9948 | 12974 | 0 | 8586 | 8931 | 10970 | 13787 | 13534 | 11025 | 11632 | 11466 | 8447 | 3.335 | 3.0151 | 4.7773 | 4.3154 | 4.7726 | 5.3901 | 4.6429 | 4.7499 | 4.7308 | 4.8432 | 4.709 | 4.929 | 4.6684 | 4.7724 | 4.7681 | 5.2569 |  | 4.4087 | 4.6234 | 5.0246 | 5.371 | 5.2262 | 4.8827 | 5.0103 | 4.9245 | 4.4003 | 264535 | 4.7019 |  |  | 257850 | 0 | 257850 | 6685 | 2.527% | 67.5 | 662
2024-11-15 | 2025 | 2024 | 2024-11-01 | 30 | 3905 | 3069 | 3904 | 2042 | 2745 | 5204 | 2233 | 4070 | 1690 | 4794 | 3712 | 4018 | 3250 | 3501 | 4947 | 4664 | 0 | 4232 | 3136 | 4613 | 5282 | 5022 | 4219 | 4195 | 3739 | 3363 | 3.3222 | 3.2408 | 3.349 | 2.7689 | 3.0294 | 3.4585 | 2.957 | 3.2777 | 3.1769 | 3.4819 | 3.3574 | 3.2878 | 3.0525 | 3.374 | 3.5037 | 3.3556 |  | 3.1959 | 3.1361 | 3.2971 | 3.4561 | 3.5139 | 3.3965 | 3.2833 | 3.1863 | 3.1626 | 95549 | 3.2648 |  |  | 91350 | 1800 | 89550 | 4199 | 4.395% | 67.5 | 503.25
2024-11-16 | 2025 | 2024 | 2024-11-01 | 30 | 3838 | 3474 | 4027 | 2861 | 3088 | 2069 | 2632 | 2916 | 4308 | 3154 | 2651 | 3084 | 2718 | 2887 | 2589 | 2431 | 0 | 3025 | 2664 | 2429 | 2306 | 3128 | 3251 | 2555 | 3937 | 3467 | 5.2081 | 5.0309 | 3.2888 | 3.0862 | 3.2765 | 2.8337 | 3.1492 | 3.0337 | 3.3543 | 3.1376 | 2.9783 | 3.1729 | 3.0475 | 3.0851 | 2.9825 | 3.0742 |  | 3.0525 | 3.121 | 3.0332 | 2.9781 | 3.1824 | 3.14 | 3.0444 | 3.3958 | 3.1559 | 75489 | 3.2737 |  |  | 71550 | 1800 | 69750 | 3939 | 5.218% | 67.5 | 0
2024-11-17 | 2025 | 2024 | 2024-11-01 | 30 | 13350 | 12384 | 13858 | 10402 | 11612 | 8716 | 10927 | 9005 | 14111 | 10002 | 10005 | 11306 | 8541 | 9126 | 9839 | 10289 | 0 | 10913 | 12326 | 9797 | 10755 | 13404 | 11086 | 8276 | 13816 | 12745 | 5.5837 | 5.7903 | 5.2331 | 4.6919 | 5.0111 | 4.5575 | 4.8679 | 4.7153 | 5.3481 | 4.7324 | 4.7427 | 4.9851 | 4.8082 | 4.944 | 4.7142 | 4.8539 |  | 4.7337 | 5.3308 | 4.785 | 4.9819 | 5.1463 | 4.9013 | 4.4485 | 5.2389 | 5.1055 | 276591 | 4.9701 |  |  | 269550 | 0 | 269550 | 7041 | 2.546% | 67.5 | 428.25
2024-11-18 | 2025 | 2024 | 2024-11-01 | 30 | 14725 | 4136 | 13099 | 11448 | 14358 | 12941 | 12747 | 13923 | 15452 | 12260 | 10547 | 13817 | 12259 | 12378 | 13302 | 12857 | 0 | 10924 | 16277 | 11467 | 13868 | 15436 | 13434 | 10176 | 15613 | 14793 | 5.241 | 5.1976 | 5.2886 | 5.0261 | 5.5666 | 5.2809 | 5.2531 | 5.3691 | 5.6228 | 5.1989 | 5.0289 | 5.5104 | 5.2686 | 5.3001 | 5.3385 | 5.326 |  | 5.0269 | 5.6554 | 5.2369 | 5.5027 | 5.5671 | 5.3662 | 4.7928 | 5.5942 | 5.5454 | 322237 | 5.3242 |  |  | 315450 | 0 | 315450 | 6787 | 2.106% | 67.5 | 2080
2024-11-19 | 2025 | 2024 | 2024-11-01 | 30 | 12789 | 12916 | 12686 | 9343 | 11828 | 11134 | 11203 | 9978 | 12839 | 9666 | 8989 | 11141 | 10231 | 8852 | 11340 | 10983 | 0 | 10278 | 13212 | 10520 | 11886 | 13633 | 11830 | 8581 | 13372 | 12113 | 5.0406 | 4.8112 | 5.1752 | 4.6818 | 5.1846 | 4.9665 | 5.0171 | 4.8501 | 5.35 | 4.8201 | 4.7253 | 5.0888 | 4.9563 | 4.9016 | 5.0036 | 5.0403 |  | 4.8106 | 5.3987 | 4.9744 | 5.149 | 5.2828 | 5.0937 | 4.5808 | 5.2669 | 5.1331 | 281343 | 5.0121 |  |  | 274050 | 0 | 274050 | 7293 | 2.592% | 67.5 | 628.875
2024-11-20 | 2025 | 2024 | 2024-11-01 | 30 | 11532 | 10817 | 11335 | 8384 | 10417 | 9861 | 8623 | 9627 | 12239 | 8171 | 8015 | 9388 | 9220 | 8374 | 8548 | 9716 | 0 | 7429 | 10186 | 6810 | 10031 | 11123 | 7950 | 8491 | 12281 | 10318 | 4.7033 | 4.7378 | 4.8946 | 4.4417 | 4.9201 | 4.8275 | 4.568 | 4.6969 | 5.059 | 4.5004 | 4.5513 | 4.744 | 4.7019 | 4.5924 | 4.5724 | 4.8045 |  | 4.2131 | 4.7078 | 4.3926 | 4.877 | 4.9218 | 4.8295 | 4.5732 | 5.0546 | 4.7894 | 238886 | 4.707 |  |  | 232200 | 0 | 232200 | 6686 | 2.799% | 67.5 | 848.5
2024-11-21 | 2025 | 2024 | 2024-11-01 | 30 | 9265 | 10564 | 9192 | 8018 | 9759 | 9715 | 8451 | 8697 | 9643 | 7358 | 6044 | 8912 | 8581 | 7526 | 8505 | 9649 | 0 | 5430 | 9527 | 6811 | 10307 | 11684 | 8687 | 8215 | 11694 | 8612 | 4.6122 | 4.6025 | 4.6338 | 4.3367 | 4.8305 | 5.0278 | 4.7112 | 4.4787 | 4.7643 | 4.3456 | 4.2488 | 4.6722 | 4.5722 | 4.4265 | 4.5374 | 4.7778 |  | 4.0912 | 4.6585 | 4.4035 | 4.8916 | 4.9813 | 4.5898 | 4.5021 | 4.9408 | 4.5201 | 220846 | 4.6063 |  |  | 215100 | 0 | 215100 | 5746 | 2.602% | 67.5 | 3066.25
2024-11-22 | 2025 | 2024 | 2024-11-01 | 30 | 8313 | 9311 | 6557 | 6857 | 9346 | 9096 | 7111 | 5695 | 8176 | 6734 | 3988 | 7545 | 7596 | 5996 | 7661 | 8811 | 0 | 6228 | 9281 | 5913 | 8075 | 9155 | 7543 | 7050 | 9771 | 7896 | 3.4478 | 3.3978 | 4.2316 | 4.2174 | 4.7761 | 4.8001 | 4.3403 | 4.4025 | 4.5686 | 4.2444 | 4.1019 | 4.4601 | 4.4559 | 4.2075 | 4.4221 | 4.7048 |  | 4.0368 | 4.5957 | 4.2199 | 4.6771 | 4.6414 | 4.4193 | 4.3066 | 4.741 | 4.4497 | 189705 | 4.3547 |  |  | 184050 | 0 | 184050 | 5655 | 2.981% | 67.5 | 915.75
2024-11-23 | 2025 | 2024 | 2024-11-01 | 30 | 3900 | 4203 | 3939 | 2597 | 3993 | 5065 | 3625 | 2854 | 4718 | 2818 | 2389 | 4148 | 3412 | 3027 | 3657 | 4591 | 0 | 3204 | 3862 | 2739 | 4277 | 4869 | 3937 | 3902 | 4702 | 3941 | 3.8058 | 3.5718 | 3.3445 | 2.9963 | 3.4628 | 3.7281 | 3.3676 | 3.2908 | 3.5565 | 3.1463 | 3.1531 | 3.4957 | 3.2833 | 3.2119 | 3.2944 | 3.5935 |  | 3.2039 | 3.4365 | 3.2004 | 3.5286 | 3.6344 | 3.3618 | 3.3312 | 3.5273 | 3.3702 | 94369 | 3.3959 |  |  | 90000 | 0 | 90000 | 4369 | 4.63% | 67.5 | 24.75
2024-11-24 | 2025 | 2024 | 2024-11-01 | 30 | 4933 | 5227 | 4098 | 2455 | 5271 | 3349 | 2801 | 4485 | 5258 | 3647 | 2765 | 4524 | 4742 | 4013 | 4227 | 3626 | 0 | 2978 | 3660 | 2856 | 3305 | 4054 | 4195 | 3109 | 6337 | 3907 | 6.0895 | 6.0477 | 3.5707 | 3.1799 | 3.8491 | 3.6811 | 3.482 | 3.6193 | 3.8133 | 3.4694 | 3.2438 | 3.6969 | 3.6883 | 3.5788 | 3.5697 | 3.7103 |  | 3.3988 | 3.6668 | 3.5404 | 3.642 | 3.795 | 3.6876 | 3.4528 | 3.9157 | 3.5744 | 99822 | 3.7985 |  |  | 95850 | 0 | 95850 | 3972 | 3.979% | 67.5 | 844.75
2024-11-25 | 2025 | 2024 | 2024-11-01 | 30 | 19048 | 18801 | 15570 | 2057 | 20344 | 14657 | 5411 | 15362 | 17723 | 15127 | 11689 | 16036 | 16017 | 13445 | 18256 | 18173 | 0 | 16190 | 13312 | 10012 | 17003 | 17384 | 14924 | 15089 | 20536 | 16609 | 6.2492 | 6.311 | 5.5986 | 6.4569 | 6.2899 | 6.3026 | 7.1746 | 5.5476 | 5.9542 | 5.6213 | 5.2191 | 5.7912 | 5.7522 | 5.5318 | 5.9045 | 6.1128 |  | 5.6893 | 5.6424 | 5.5735 | 6.2224 | 6.0226 | 5.5767 | 5.6991 | 6.156 | 5.7497 | 378775 | 5.926 |  |  | 368550 | 0 | 368550 | 10225 | 2.699% | 67.5 | 3597.25
2024-11-26 | 2025 | 2024 | 2024-11-01 | 30 | 20148 | 21541 | 17258 | 16067 | 22022 | 22761 | 19364 | 17717 | 17416 | 15829 | 12440 | 17132 | 17909 | 15380 | 19544 | 21519 | 0 | 17781 | 18789 | 15417 | 21980 | 23059 | 17850 | 17540 | 22702 | 18182 | 5.7928 | 5.6522 | 5.8028 | 5.6627 | 6.4578 | 6.5157 | 6.0308 | 5.8467 | 6.1442 | 5.7756 | 5.356 | 5.9037 | 5.9564 | 5.7015 | 6.0932 | 6.3784 |  | 5.8087 | 5.942 | 5.8178 | 6.4571 | 6.4374 | 5.9385 | 5.8548 | 6.4094 | 5.9299 | 467347 | 5.9866 |  |  | 459000 | 0 | 459000 | 8347 | 1.786% | 67.5 | 1698.875
2024-11-27 | 2025 | 2024 | 2024-11-01 | 30 | 11985 | 15570 | 14499 | 13298 | 15595 | 16384 | 15234 | 13198 | 14943 | 12938 | 9672 | 12995 | 13326 | 12009 | 14661 | 15349 | 0 | 12576 | 15550 | 13133 | 16163 | 16198 | 12470 | 13661 | 16675 | 14833 | 5.3074 | 5.3555 | 5.479 | 5.2947 | 5.7544 | 5.8509 | 5.5858 | 5.294 | 5.6233 | 5.3782 | 4.941 | 5.4059 | 5.4296 | 5.2853 | 5.5158 | 5.701 |  | 5.1648 | 5.4919 | 5.406 | 5.8093 | 5.7156 | 5.3426 | 5.3955 | 5.7482 | 5.5382 | 352915 | 5.4726 |  |  | 344250 | 0 | 344250 | 8665 | 2.455% | 67.5 | 637.25
2024-11-28 | 2025 | 2024 | 2024-11-01 | 30 | 12118 | 13379 | 8573 | 10749 | 12480 | 15318 | 12846 | 12533 | 11178 | 7774 | 9398 | 11796 | 10212 | 9955 | 12555 | 13999 | 0 | 9481 | 12784 | 11280 | 15560 | 14790 | 11858 | 12076 | 13713 | 11578 | 6.6172 | 6.6062 | 5.1734 | 4.9525 | 5.3399 | 5.7332 | 5.2898 | 5.2401 | 5.0999 | 4.9868 | 4.9848 | 5.2867 | 5.1145 | 4.9663 | 5.2762 | 5.5322 |  | 4.6857 | 5.2421 | 5.2226 | 5.7283 | 5.5596 | 5.233 | 5.2354 | 5.3938 | 5.0926 | 297983 | 5.3437 |  |  | 291150 | 0 | 291150 | 6833 | 2.293% | 67.5 | 711.375
2024-11-29 | 2025 | 2024 | 2024-11-01 | 30 | 23086 | 23932 | 20778 | 19362 | 24840 | 27459 | 18816 | 18948 | 20016 | 19559 | 16856 | 21732 | 19824 | 17798 | 22340 | 25131 | 0 | 17699 | 20854 | 20067 | 27089 | 25090 | 19126 | 23079 | 16089 | 16821 | 7.6263 | 7.5561 | 6.2452 | 6.0935 | 6.8619 | 7.0535 | 6.471 | 6.059 | 6.2375 | 6.1878 | 5.9554 | 6.4169 | 6.2182 | 5.98 | 6.3974 | 6.777 |  | 5.7583 | 6.253 | 6.3474 | 7.0512 | 6.8276 | 6.1803 | 6.6456 | 6.7169 | 5.9181 | 526391 | 6.4734 |  |  | 513450 | 0 | 513450 | 12941 | 2.458% | 67.5 | 2652
2024-11-30 | 2025 | 2024 | 2024-11-01 | 30 | 32705 | 32485 | 30385 | 30249 | 31037 | 36509 | 34580 | 29772 | 30194 | 19188 | 22440 | 29533 | 28860 | 28650 | 31626 | 30182 | 0 | 30433 | 32408 | 28525 | 36486 | 33743 | 28674 | 29661 | 33885 | 32379 | 7.4978 | 7.1381 | 7.159 | 7.3066 | 7.5437 | 7.8712 | 7.7889 | 7.2522 | 7.3623 | 6.9145 | 6.6323 | 7.2188 | 7.2873 | 7.1515 | 7.4247 | 7.8761 |  | 7.1399 | 7.5125 | 7.3194 | 8.0069 | 7.8563 | 7.2022 | 7.4101 | 7.6206 | 7.4376 | 764589 | 7.3972 |  |  | 743850 | 0 | 743850 | 20739 | 2.712% | 67.5 | 970.5
2024-12-01 | 2025 | 2024 | 2024-12-01 | 31 | 25462 | 26188 | 27694 | 24840 | 26322 | 33617 | 27733 | 25249 | 28367 | 23965 | 14085 | 26473 | 25581 | 26641 | 28905 | 33193 | 0 | 29960 | 26025 | 25974 | 33249 | 31258 | 24210 | 30415 | 28537 | 26159 | 7.4988 | 7.5036 | 7.0975 | 6.6622 | 7.3994 | 7.5044 | 6.9806 | 7.0745 | 7.3147 | 6.9375 | 6.2026 | 7.066 | 7.1344 | 7.1026 | 7.2708 | 7.4674 |  | 7.0474 | 6.709 | 6.9432 | 7.5731 | 7.5567 | 6.9676 | 7.2047 | 7.4184 | 7.1141 | 680102 | 7.15 |  |  | 661500 | 0 | 661500 | 18602 | 2.735% | 67.5 | 3463.8045 | 28.36
2024-12-02 | 2025 | 2024 | 2024-12-01 | 31 | 30885 | 30976 | 25949 | 27750 | 23713 | 33262 | 28899 | 27887 | 27821 | 24238 | 17489 | 26490 | 26698 | 25171 | 28352 | 33801 | 0 | 27033 | 26897 | 25149 | 32773 | 31893 | 26190 | 27767 | 32551 | 28212 | 6.9519 | 6.7709 | 6.9745 | 7.0269 | 7.4983 | 7.549 | 7.176 | 7.1072 | 7.2311 | 6.8722 | 6.2261 | 7.062 | 7.0651 | 6.769 | 7.0282 | 7.5694 |  | 6.7657 | 6.9032 | 6.9576 | 7.5701 | 7.4978 | 7.1371 | 7.0356 | 7.6554 | 7.1089 | 697846 | 7.1004 |  |  | 677250 | 0 | 677250 | 20596 | 2.951% | 67.5 | 1888.125 | 29.083
2024-12-03 | 2025 | 2024 | 2024-12-01 | 31 | 27705 | 25535 | 28032 | 21408 | 24509 | 27132 | 20853 | 26240 | 27329 | 21529 | 22190 | 27536 | 25646 | 25826 | 27616 | 28618 | 0 | 25923 | 26421 | 23884 | 30201 | 29538 | 25589 | 24856 | 27788 | 26557 | 8.8767 | 8.6603 | 6.6857 | 6.144 | 6.814 | 6.8796 | 6.184 | 6.6 | 6.9161 | 6.5264 | 6.3147 | 6.7706 | 6.6522 | 6.5798 | 6.6928 | 7.0191 |  | 6.5261 | 6.691 | 6.5933 | 7.1935 | 7.1283 | 6.6577 | 6.7901 | 6.8962 | 6.7653 | 648461 | 6.8623 |  |  | 626400 | 0 | 626400 | 22061 | 3.402% | 67.5 | 881.8758 | 26.869
2024-12-04 | 2025 | 2024 | 2024-12-01 | 31 | 39074 | 25037 | 39751 | 30404 | 38029 | 37408 | 32180 | 36567 | 36757 | 36448 | 27765 | 37712 | 40153 | 38800 | 37914 | 40254 | 0 | 37392 | 32718 | 35333 | 37658 | 38016 | 30704 | 34155 | 40364 | 39821 | 7.1595 | 6.8358 | 8.3976 | 8.2643 | 8.6845 | 8.9208 | 8.3484 | 8.3725 | 8.7035 | 8.3547 | 7.9291 | 8.4279 | 8.7173 | 8.5458 | 8.4216 | 9.217 |  | 8.9508 | 8.414 | 8.7142 | 9.2403 | 9.1964 | 8.4529 | 8.7563 | 8.8911 | 8.4999 | 900414 | 8.4966 |  |  | 873000 | 0 | 873000 | 27414 | 3.045% | 67.5 | 6152.3747 | 37.613
2024-12-05 | 2025 | 2024 | 2024-12-01 | 31 | 28110 | 26471 | 23600 | 21000 | 24823 | 27367 | 21371 | 24142 | 28445 | 23098 | 21191 | 28101 | 25034 | 24835 | 23835 | 27623 | 0 | 25251 | 27458 | 20509 | 27764 | 29277 | 25869 | 24739 | 28071 | 28068 | 6.6231 | 5.8082 | 6.6749 | 6.2578 | 6.7826 | 6.8987 | 6.409 | 6.5565 | 7.1195 | 6.519 | 6.2987 | 7.0085 | 6.7029 | 6.7083 | 6.6015 | 6.8949 |  | 6.5059 | 6.8788 | 6.4213 | 7.0095 | 7.1554 | 6.8501 | 6.7943 | 7.0159 | 6.9555 | 636052 | 6.698 |  |  | 622350 | 0 | 622350 | 13702 | 2.154% | 67.5 | 816.1505 | 26.685
2024-12-06 | 2025 | 2024 | 2024-12-01 | 31 | 25416 | 19905 | 22693 | 19178 | 20835 | 14292 | 19182 | 16931 | 23178 | 22527 | 22029 | 22342 | 19892 | 21222 | 20705 | 19160 | 0 | 21662 | 18175 | 18612 | 16482 | 18109 | 20599 | 20923 | 22537 | 23310 | 4.0491 | 3.859 | 6.1527 | 5.8456 | 6.1656 | 5.41 | 5.8796 | 5.528 | 6.4734 | 6.2674 | 6.1564 | 6.2362 | 5.8621 | 6.1287 | 5.9686 | 5.7685 |  | 6.0595 | 5.7484 | 5.7761 | 5.6702 | 5.8238 | 6.1854 | 6.1833 | 6.246 | 6.2297 | 509896 | 5.8269 |  |  | 498600 | 0 | 498600 | 11296 | 2.215% | 67.5 | 6915.75 | 20.309
2024-12-07 | 2025 | 2024 | 2024-12-01 | 31 | 4502 | 4879 | 5658 | 5388 | 5104 | 4622 | 3932 | 2928 | 4732 | 4314 | 5402 | 3886 | 4249 | 5178 | 5629 | 4082 | 0 | 5029 | 4053 | 5240 | 3044 | 4314 | 4142 | 5719 | 5188 | 4092 | 5.4511 | 5.1126 | 4.182 | 3.7167 | 4.1025 | 3.8278 | 3.5034 | 3.5609 | 3.9696 | 3.9827 | 4.1667 | 3.875 | 3.7695 | 4.1103 | 4.1843 | 3.7376 |  | 3.7483 | 3.4981 | 3.822 | 3.6028 | 3.7238 | 3.9599 | 4.0153 | 4.0833 | 3.8885 | 115306 | 3.9838 |  |  | 110250 | 450 | 109800 | 5056 | 4.385% | 67.5 | 467.25 | 4.436
2024-12-08 | 2025 | 2024 | 2024-12-01 | 31 | 13148 | 0 | 15898 | 12882 | 11387 | 9658 | 9553 | 12174 | 16268 | 13938 | 14611 | 15682 | 10651 | 12826 | 14041 | 14160 | 0 | 14703 | 10486 | 13630 | 8857 | 12614 | 13407 | 14127 | 13197 | 13873 | 8.8089 | 8.6825 | 5.3526 | 4.9791 | 5.1224 | 4.5429 | 4.6422 | 5.0138 | 5.3694 | 5.2894 | 5.2336 | 5.4448 | 4.6465 | 5.1924 | 5.2396 | 5.1965 |  | 5.1273 | 4.7306 | 4.9774 | 4.3826 | 5.1189 | 5.4781 | 5.254 | 5.2817 | 5.4639 | 311771 | 5.3829 |  |  | 286200 | 0 | 286200 | 25571 | 8.202% | 67.5 | 2648 | 12.214
2024-12-09 | 2025 | 2024 | 2024-12-01 | 31 | 30891 | 0 | 44064 | 35723 | 37279 | 32016 | 38506 | 39379 | 44556 | 36722 | 41092 | 41546 | 34321 | 39971 | 38912 | 33593 | 0 | 41613 | 38622 | 42916 | 40106 | 38837 | 38197 | 37655 | 40287 | 39322 | 9.065 | 9.0472 | 8.7155 | 8.2125 | 8.703 | 7.6476 | 8.3789 | 8.4596 | 8.6779 | 8.3686 | 8.3574 | 8.5619 | 8.605 | 8.4053 | 8.4246 | 8.1219 |  | 8.3376 | 8.3653 | 8.2483 | 8.5235 | 8.634 | 8.646 | 8.3048 | 8.8976 | 8.5672 | 926126 | 8.4911 |  |  | 895050 | 0 | 895050 | 31076 | 3.355% | 67.5 | 24693.7505 | 30.03
2024-12-10 | 2025 | 2024 | 2024-12-01 | 31 | 46292 | 0 | 46155 | 32059 | 44942 | 44192 | 40792 | 44669 | 48519 | 38286 | 35250 | 44860 | 44736 | 43940 | 37281 | 45495 | 0 | 44120 | 46782 | 40802 | 47058 | 42350 | 44651 | 43273 | 47477 | 46768 | 7.7794 | 7.7043 | 8.6132 | 8.2126 | 9.0024 | 8.9374 | 8.6088 | 8.779 | 8.7913 | 8.6036 | 8.1713 | 8.7233 | 8.5431 | 8.5932 | 8.842 | 8.9435 |  | 8.6544 | 9.1188 | 8.318 | 9.2504 | 9.2628 | 8.7643 | 8.8386 | 9.2165 | 8.8741 | 1040749 | 8.6859 |  |  | 1010250 | 0 | 1010250 | 30499 | 2.93% | 67.5 | 303.2495 | 22.761
2024-12-11 | 2025 | 2024 | 2024-12-01 | 31 | 19694 | 0 | 21478 | 25876 | 24340 | 30871 | 30895 | 20431 | 24957 | 25322 | 20199 | 28725 | 27998 | 23344 | 27407 | 34272 | 0 | 34159 | 27558 | 29863 | 33845 | 32872 | 21805 | 36498 | 22582 | 23148 | 8.0005 | 7.7498 | 7.1777 | 7.0701 | 7.5008 | 7.2004 | 7.472 | 7.1612 | 7.3365 | 7.0256 | 6.5061 | 7.1555 | 6.9755 | 7.1179 | 7.3316 | 7.5795 |  | 7.4218 | 7.2447 | 7.0466 | 7.6512 | 7.579 | 6.9319 | 7.9536 | 7.8301 | 7.2685 | 648139 | 7.3315 |  |  | 635850 | 0 | 635850 | 12289 | 1.896% | 67.5 | 19440.9998 | 27.222
2024-12-12 | 2025 | 2024 | 2024-12-01 | 31 | 21202 | 0 | 29277 | 28247 | 20370 | 22152 | 29387 | 22517 | 27214 | 28786 | 27069 | 27970 | 26576 | 22475 | 23107 | 26173 | 0 | 30858 | 33414 | 31149 | 25617 | 28565 | 23021 | 30753 | 27416 | 24922 | 8.9451 | 10.2047 | 7.6484 | 7.3616 | 7.6783 | 6.7423 | 7.5698 | 7.0194 | 7.7401 | 7.61 | 7.4464 | 7.4738 | 7.4349 | 7.2951 | 7.5264 | 7.0272 |  | 7.5008 | 7.6294 | 7.3796 | 7.1541 | 7.4732 | 7.6237 | 8.0111 | 7.9403 | 7.4863 | 638237 | 7.6369 |  |  | 617850 | 0.04 | 617849.96 | 20387 | 3.194% | 67.5 | 39641.626 | 26.361
2024-12-13 | 2025 | 2024 | 2024-12-01 | 31 | 36317 | 0 | 48352 | 49174 | 35099 | 51467 | 51046 | 47789 | 47730 | 42456 | 22115 | 46738 | 45636 | 48571 | 50414 | 50020 | 0 | 49235 | 49112 | 48604 | 53191 | 50126 | 46807 | 51385 | 49895 | 46493 | 8.1067 | 8.424 | 9.3704 | 9.3188 | 9.9166 | 9.7579 | 9.4865 | 9.6136 | 9.7391 | 9.2646 | 8.525 | 9.5214 | 9.5726 | 9.3593 | 9.68 | 9.9283 |  | 9.6856 | 9.5224 | 9.5441 | 10.0977 | 9.8708 | 9.6836 | 10.2206 | 10.0787 | 9.6899 | 1117772 | 9.5191 |  |  | 1073700 | 0 | 1073700 | 44072 | 3.943% | 67.5 | 28048.9992 | 46.439
2024-12-14 | 2025 | 2024 | 2024-12-01 | 31 | 38844 | 0 | 37200 | 29462 | 18483 | 35217 | 33903 | 37769 | 35618 | 39782 | 28681 | 38598 | 37544 | 35237 | 30516 | 35551 | 0 | 31155 | 30049 | 33176 | 35649 | 34635 | 35759 | 35492 | 41664 | 34757 | 5.753 | 5.8439 | 7.6755 | 8.5456 | 8.7021 | 9.0951 | 8.9892 | 7.9017 | 7.6701 | 8.1705 | 7.3825 | 7.9852 | 8.0978 | 7.7836 | 8.527 | 9.1775 |  | 8.6046 | 8.3813 | 8.7446 | 9.5346 | 9.1296 | 7.7333 | 9.0646 | 8.4741 | 7.5156 | 824741 | 8.1793 |  |  | 811350 | 0 | 811350 | 13391 | 1.624% | 67.5 | 1924.375 | 35.063
2024-12-15 | 2025 | 2024 | 2024-12-01 | 31 | 20154 | 0 | 17970 | 15451 | 18679 | 23971 | 18848 | 20870 | 17691 | 19451 | 14621 | 18566 | 18368 | 16605 | 5441 | 23408 | 0 | 15837 | 16033 | 19874 | 24818 | 23638 | 19668 | 22918 | 20946 | 17736 | 4.6521 | 4.8237 | 5.4002 | 5.2035 | 5.931 | 6.2683 | 5.6362 | 5.8193 | 5.4631 | 5.5895 | 5.2066 | 5.5942 | 5.6201 | 5.3385 | 4.4085 | 6.2036 |  | 5.2596 | 5.7212 | 5.7438 | 6.3224 | 6.2269 | 5.7699 | 6.1254 | 5.8606 | 5.5187 | 451562 | 5.5883 |  |  | 451350 | 0 | 451350 | 212 | 0.04695% | 67.5 | 4906.2503 | 19.66
2024-12-16 | 2025 | 2024 | 2024-12-01 | 31 | 13008 | 0 | 12258 | 9409 | 11486 | 10050 | 10981 | 11284 | 13639 | 10717 | 9225 | 10751 | 11382 | 8903 | 10783 | 10305 | 0 | 8427 | 10961 | 8382 | 10567 | 12341 | 10618 | 11839 | 9338 | 11718 | 6.1333 | 5.6894 | 4.3687 | 4.1846 | 4.7488 | 4.4058 | 4.4015 | 4.3573 | 4.6123 | 4.3183 | 4.0849 | 4.3588 | 4.4162 | 4.1507 | 4.3517 | 4.4525 |  | 3.9777 | 4.7578 | 4.1497 | 4.4801 | 4.7331 | 4.5186 | 4.6071 | 4.5915 | 4.4072 | 258372 | 4.5303 |  |  | 260100 | 900 | 259200 | -1728 | -0.6688% | 67.5 | 4792.625 | 11.128
2024-12-17 | 2025 | 2024 | 2024-12-01 | 31 | 21473 | 0 | 21071 | 11022 | 15527 | 2919 | 12741 | 16261 | 19387 | 19333 | 17528 | 17301 | 12221 | 16635 | 17770 | 13613 | 0 | 14755 | 9395 | 13804 | 10171 | 11762 | 13254 | 16731 | 19514 | 17940 | 4.7416 | 4.7436 | 5.9719 | 5.3307 | 5.8799 | 4.2263 | 5.1967 | 5.3867 | 5.8357 | 5.8124 | 5.676 | 5.6667 | 5.0266 | 5.6532 | 5.6696 | 5.3093 |  | 5.3234 | 5.3928 | 5.3332 | 4.865 | 5.2022 | 5.8427 | 5.705 | 5.916 | 5.7014 | 362128 | 5.4163 |  |  | 352800 | 0 | 352800 | 9328 | 2.576% | 67.5 | 3858.8752 | 15.026
2024-12-18 | 2025 | 2024 | 2024-12-01 | 31 | 14518 | 0 | 14641 | 9434 | 11112 | 6738 | 9874 | 8309 | 15128 | 11902 | 12227 | 11027 | 10589 | 11354 | 10725 | 8392 | 2449 | 10828 | 7582 | 9700 | 8207 | 10338 | 11712 | 11469 | 13190 | 12316 | 4.5373 | 4.2292 | 4.6199 | 3.939 | 4.6023 | 3.6345 | 4.051 | 3.7464 | 4.726 | 4.352 | 4.3887 | 4.2035 | 4.0879 | 4.345 | 4.2124 | 3.8357 | 3.2167 | 4.1013 | 4.1259 | 3.9531 | 3.9288 | 4.0869 | 4.5075 | 4.3074 | 4.5676 | 4.3931 | 263761 | 4.1807 |  |  | 258750 | 1350 | 257400 | 5011 | 1.9% | 70.2 | 531.875 | 10.666
2024-12-19 | 2025 | 2024 | 2024-12-01 | 31 | 8765 | 0 | 8630 | 1615 | 5256 | 6526 | 5484 | 6271 | 8802 | 8873 | 8807 | 7798 | 6116 | 7921 | 8458 | 7872 | 7429 | 8309 | 4330 | 7963 | 5378 | 6322 | 4994 | 9265 | 7492 | 8059 | 7.9737 | 7.2828 | 4.5578 | 3.9679 | 4.1982 | 3.7224 | 3.5569 | 3.8606 | 4.5778 | 4.3111 | 4.3573 | 4.188 | 3.78 | 4.1785 | 4.2234 | 3.8597 | 3.5304 | 3.9533 | 3.511 | 3.9188 | 3.4721 | 3.5242 | 4.1227 | 4.1732 | 4.1399 | 4.2268 | 176735 | 4.2757 |  |  | 170550 | 1350 | 169200 | 6185 | 3.5% | 70.2 | 4482.4267 | 4.73
2024-12-20 | 2025 | 2024 | 2024-12-01 | 31 | 25179 | 0 | 24304 | 17794 | 24937 | 24914 | 20820 | 24377 | 24581 | 29873 | 25254 | 26525 | 19538 | 23609 | 28517 | 25755 | 25320 | 27117 | 15897 | 28643 | 23936 | 27537 | 17730 | 28512 | 24706 | 22380 | 4.5733 | 5.5773 | 7.1112 | 7.2079 | 7.811 | 7.0021 | 6.5302 | 7.0834 | 7.1816 | 7.6333 | 7.015 | 7.4184 | 6.3744 | 6.8655 | 7.4054 | 7.3103 | 8.1209 | 7.1149 | 6.6 | 7.2609 | 6.8646 | 7.3666 | 7.0238 | 7.6292 | 7.7554 | 7.0713 | 607755 | 7.0349 |  |  | 592200 | 0 | 592200 | 15555 | 2.559% | 70.2 | 17451.7507 | 21.102
2024-12-21 | 2025 | 2024 | 2024-12-01 | 31 | 9145 | 0 | 9596 | 6114 | 7485 | 3253 | 6246 | 6381 | 9570 | 6491 | 7004 | 6935 | 6285 | 5503 | 6836 | 4840 | 5341 | 3860 | 3912 | 4511 | 3627 | 5479 | 4928 | 5359 | 9903 | 7930 | 4.2395 | 4.5883 | 4.4485 | 3.8816 | 5.277 | 3.707 | 4.1719 | 4.0835 | 4.4581 | 3.9224 | 4.1007 | 4.1239 | 4.0846 | 4.1015 | 4.0079 | 4.0454 | 4.1231 | 3.6615 | 4.1384 | 3.9286 | 3.8776 | 4.1105 | 4.2112 | 4.2141 | 5.3824 | 4.3519 | 156534 | 4.2016 |  |  | 152100 | 450 | 151650 | 4434 | 2.833% | 70.2 | 2254.625 | 6.076
2024-12-22 | 2025 | 2024 | 2024-12-01 | 31 | 5622 | 0 | 4978 | 8982 | 2668 | 10256 | 4338 | 5555 | 4956 | 5258 | 5352 | 5560 | 5947 | 5598 | 5459 | 7668 | 12387 | 9720 | 6868 | 8592 | 10234 | 9618 | 4203 | 9076 | 3356 | 5047 | 4.229 | 5.553 | 4.0305 | 4.4861 | 4.3638 | 4.8916 | 4.4362 | 4.1103 | 3.9772 | 4.0466 | 4.1671 | 4.1597 | 4.2989 | 4.1732 | 4.0733 | 4.5308 | 5.0559 | 4.6488 | 5.017 | 4.5656 | 4.8304 | 4.8049 | 4.169 | 4.717 | 4.5637 | 4.1204 | 167298 | 4.4623 |  |  | 162000 | 0 | 162000 | 5298 | 3.167% | 70.2 | 2970.875 | 4.885
2024-12-23 | 2025 | 2024 | 2024-12-01 | 31 | 1094 | 0 | 10502 | 11640 | 5328 | 10325 | 8922 | 6657 | 8225 | 11286 | 6397 | 7183 | 7629 | 6560 | 11619 | 12197 | 14824 | 12843 | 5843 | 10943 | 9441 | 12513 | 5301 | 12687 | 6259 | 6561 | 7.56 | 6.058 | 5.2298 | 5.1419 | 5.1821 | 4.9475 | 4.702 | 5.1547 | 5.1409 | 5.2203 | 5.0417 | 5.0888 | 4.55 | 5.1818 | 5.3168 | 5.2008 | 5.2953 | 5.067 | 4.9667 | 5.0154 | 4.8779 | 5.1225 | 5.322 | 5.251 | 4.4376 | 5.301 | 222779 | 5.2067 |  |  | 216450 | 0 | 216450 | 6329 | 2.841% | 70.2 | 7310.3758
2024-12-24 | 2025 | 2024 | 2024-12-01 | 31 | 4774 | 0 | 25406 | 21457 | 25176 | 18996 | 15892 | 22546 | 25753 | 25342 | 23738 | 24252 | 11474 | 22809 | 23785 | 22793 | 26555 | 23724 | 9892 | 21448 | 16434 | 21490 | 16478 | 23646 | 26161 | 26556 | 7.0253 | 7.1543 | 6.7236 | 6.456 | 6.7364 | 6.189 | 5.9367 | 6.6125 | 6.8299 | 6.9278 | 6.6132 | 6.7083 | 5.0681 | 6.6466 | 6.6186 | 6.6564 | 6.7578 | 6.6108 | 6.1024 | 6.3425 | 5.9031 | 6.4304 | 6.762 | 6.8277 | 6.7412 | 6.8701 | 526577 | 6.5481 |  |  | 511200 | 0 | 511200 | 15377 | 2.92% | 70.2 | 6007.5
2024-12-25 | 2025 | 2024 | 2024-12-01 | 31 | 24370 | 0 | 22857 | 13798 | 22574 | 14785 | 13182 | 18167 | 22768 | 23320 | 20167 | 21417 | 21021 | 21757 | 22600 | 16320 | 15612 | 17327 | 11473 | 17280 | 15446 | 16034 | 18281 | 17583 | 17740 | 21904 | 5.395 | 5.4583 | 6.5026 | 8.1979 | 6.5736 | 5.9624 | 8.0457 | 6.2428 | 6.7598 | 6.6202 | 6.3498 | 6.5276 | 6.2903 | 6.3416 | 6.4599 | 6.256 | 5.8521 | 6.1188 | 6.2531 | 6.2957 | 5.9398 | 6.233 | 6.5931 | 6.5833 | 7.0401 | 6.5989 | 467783 | 6.442 |  |  | 454500 | 0 | 454500 | 13283 | 2.84% | 70.2 | 10111.2507
2024-12-26 | 2025 | 2024 | 2024-12-01 | 31 | 16030 | 0 | 13622 | 12392 | 17650 | 12953 | 9757 | 12909 | 12390 | 13254 | 11371 | 13387 | 13439 | 12840 | 14384 | 14702 | 11790 | 12826 | 8574 | 13125 | 13348 | 15285 | 10277 | 15318 | 18725 | 15757 | 6.1697 | 5.7675 | 4.777 | 4.8202 | 5.2616 | 4.8075 | 4.6241 | 4.6205 | 4.9178 | 4.7106 | 4.5801 | 4.7589 | 4.7326 | 4.7162 | 4.7861 | 5.026 | 5.4918 | 4.7033 | 6.2001 | 4.7793 | 5.2452 | 5.2928 | 4.907 | 5.1707 | 5.4096 | 4.9811 | 336105 | 5.0484 |  |  | 331200 | 1350 | 329850 | 4905 | 1.459% | 70.2 | 2870.25
2024-12-27 | 2025 | 2024 | 2024-12-01 | 31 | 19455 | 6788 | 14257 | 13655 | 19862 | 9047 | 10871 | 14678 | 13759 | 15714 | 14187 | 13922 | 10898 | 14401 | 17355 | 15078 | 0 | 10577 | 6374 | 13536 | 8879 | 10878 | 9114 | 15189 | 18026 | 14208 | 7.2304 | 6.7924 | 5.5304 | 5.5804 | 6.1442 | 5.725 | 5.2283 | 5.5637 | 5.523 | 5.8206 | 5.6314 | 5.5381 | 5.2471 | 5.6215 | 5.8931 | 5.7229 | 6.7007 | 6.217 | 5.2422 | 5.5225 | 5.8827 | 6.026 | 5.5049 | 5.9558 | 6.4679 | 5.5188 | 330708 | 5.8397 |  |  | 321750 | 450 | 321300 | 8958 | 2.709% | 70.2 | 2410.625
2024-12-28 | 2025 | 2024 | 2024-12-01 | 31 | 25193 | 28399 | 23159 | 21687 | 24622 | 19134 | 17927 | 20906 | 24353 | 26429 | 16506 | 22877 | 18461 | 22298 | 25755 | 21974 | 0 | 20932 | 13708 | 21843 | 17826 | 17965 | 18292 | 20919 | 25215 | 21803 | 7.0414 | 6.8897 | 6.9038 | 6.7335 | 6.9666 | 6.3329 | 6.4923 | 6.5268 | 7.0051 | 7.2807 | 7.9935 | 6.729 | 6.2583 | 6.7708 | 7.0919 | 6.8438 | 8.7207 | 6.5992 | 6.4647 | 6.6772 | 6.349 | 7.8021 | 7.219 | 6.8882 | 7.0945 | 7.0469 | 538183 | 6.9508 |  |  | 521100 | 0 | 521100 | 17083 | 3.174% | 70.2 | 7253.875
2024-12-29 | 2025 | 2024 | 2024-12-01 | 31 | 24116 | 28878 | 23195 | 19119 | 25719 | 17344 | 18515 | 21180 | 24320 | 20251 | 7580 | 22034 | 21766 | 20916 | 20531 | 17936 | 2531 | 19017 | 14237 | 16638 | 18354 | 20382 | 16928 | 19289 | 26376 | 23660 | 6.2196 | 6.0649 | 6.5944 | 6.4147 | 6.9038 | 6.081 | 6.5282 | 6.3869 | 6.8631 | 6.3405 | 7.0809 | 6.4916 | 6.4637 | 6.3488 | 6.2616 | 6.1686 | 7.9566 | 6.1159 | 6.6065 | 6.1235 | 6.3117 | 6.4296 | 6.7744 | 6.5754 | 7.1018 | 6.6578 | 510812 | 6.5333 |  |  | 498150 | 0 | 498150 | 12662 | 2.479% | 70.2 | 6358.625
2024-12-30 | 2025 | 2024 | 2024-12-01 | 31 | 19310 | 22686 | 19220 | 16321 | 20656 | 19384 | 15733 | 15960 | 21263 | 15690 | 11381 | 17662 | 17955 | 16579 | 18691 | 19615 | 24235 | 18036 | 11935 | 17394 | 19872 | 19160 | 12352 | 20052 | 22110 | 19816 | 5.9324 | 5.5914 | 5.8143 | 5.6641 | 6.004 | 6.0213 | 5.7553 | 5.5113 | 6.0708 | 5.5533 | 4.9477 | 5.6085 | 5.7123 | 5.4027 | 5.7162 | 6.1422 | 6.8048 | 5.7514 | 5.8445 | 5.89 | 6.1555 | 5.9881 | 5.6369 | 6.6877 | 6.2387 | 5.8767 | 473068 | 5.8585 |  |  | 461250 | 0 | 461250 | 11818 | 2.498% | 70.2 | 2116
2024-12-31 | 2025 | 2024 | 2024-12-01 | 31 | 11367 | 10729 | 9888 | 7782 | 9847 | 9740 | 7668 | 9590 | 11843 | 7567 | 7590 | 10638 | 9254 | 7777 | 9345 | 8677 | 12833 | 7529 | 8152 | 7069 | 10279 | 11967 | 6422 | 11613 | 10803 | 10264 | 5.9037 | 5.9449 | 5.5679 | 4.1911 | 5.8465 | 4.5384 | 4.293 | 5.7924 | 6.0351 | 5.3855 | 5.2742 | 5.81 | 5.5487 | 5.2627 | 5.6046 | 4.5044 | 4.8324 | 4.1223 | 4.7306 | 4.3649 | 4.6465 | 4.7774 | 5.728 | 4.8454 | 5.8546 | 5.7448 | 246233 | 5.1981 |  |  | 243450 | 0 | 243450 | 2783 | 1.13% | 70.2 | 1718.875
2025-01-01 | 2025 | 2025 | 2025-01-01 | 31 | 11056 | 12318 | 9791 | 8732 | 11803 | 10597 | 9031 | 9849 | 11376 | 7151 | 6317 | 9704 | 9619 | 7995 | 9338 | 10479 | 15077 | 7576 | 12501 | 7581 | 11471 | 11737 | 9780 | 11079 | 12085 | 10401 | 4.1566 | 3.8791 | 5.5967 | 4.532 | 6.1585 | 4.8913 | 4.727 | 5.5299 | 5.9712 | 5.1076 | 4.8982 | 5.6656 | 5.617 | 5.2457 | 5.4786 | 4.9197 | 5.2685 | 4.298 | 5.107 | 4.5531 | 5.0542 | 4.9805 | 5.6278 | 5.0892 | 6.0333 | 5.7487 | 264444 | 5.159 |  |  | 257850 | 1350 | 256500 | 6594 | 2.494% | 70.2 | 1111.625 | 427.96
2025-01-02 | 2025 | 2025 | 2025-01-01 | 31 | 4976 | 5618 | 3989 | 3651 | 5229 | 5424 | 4594 | 4411 | 3653 | 3890 | 3253 | 4480 | 3987 | 3217 | 4232 | 5752 | 8590 | 4116 | 4317 | 4036 | 6217 | 6657 | 4314 | 4362 | 6350 | 4177 | 2.7582 | 2.5524 | 3.7499 | 4.2503 | 4.1035 | 4.6118 | 4.5584 | 3.8634 | 3.667 | 3.9636 | 3.7737 | 3.9852 | 3.922 | 3.6652 | 4.389 | 4.4973 | 4.4545 | 3.7917 | 4.6405 | 4.108 | 4.5426 | 4.6058 | 3.8705 | 4.3159 | 4.2419 | 3.6897 | 123492 | 4.022 |  |  | 118350 | 900 | 117450 | 5142 | 4.164% | 70.2 | 0 | 182.71
2025-01-03 | 2025 | 2025 | 2025-01-01 | 31 | 850 | 798 | 637 | 599 | 608 | 1035 | 313 | 975 | 676 | 754 | 549 | 955 | 596 | 558 | 0 | 939 | 879 | 518 | 763 | 853 | 755 | 915 | 913 | 946 | 893 | 844 | 3.118 | 2.6864 | 2.5729 | 2.6629 | 2.6643 | 3.1152 | 2.7215 | 2.6865 | 2.46 | 2.6235 | 2.5983 | 2.7398 | 2.6195 | 2.5865 | 2.783 | 2.905 | 2.7974 | 2.8102 | 2.7115 | 2.6887 | 3.1699 | 3.1266 | 2.6721 | 2.7562 | 2.7314 | 2.65 | 19121 | 2.756 |  |  | 16200 | 2250 | 13950 | 2921 | 15.28% | 70.2 | 601.625 | 26.94
2025-01-04 | 2025 | 2025 | 2025-01-01 | 31 | 4015 | 3547 | 4684 | 4193 | 4510 | 2120 | 532 | 1361 | 4120 | 4627 | 4156 | 4028 | 3695 | 4465 | 0 | 3170 | 3245 | 3094 | 2833 | 3790 | 1163 | 1640 | 3881 | 3626 | 5142 | 3258 | 6.4046 | 6.7565 | 3.2289 | 2.9856 | 3.047 | 3.3293 | 2.1121 | 3.0219 | 3.1003 | 3.1981 | 3.2475 | 3.1122 | 2.9894 | 3.1813 | 2.2717 | 3.0833 | 3.2321 | 3.4898 | 2.9118 | 3.0635 | 3.1955 | 3.289 | 3.1227 | 3.0694 | 3.1845 | 2.9824 | 84895 | 3.3312 |  |  | 81900 | 2250 | 79650 | 2995 | 3.528% | 70.2 | 14492.0008 | 125.29
2025-01-05 | 2025 | 2025 | 2025-01-01 | 31 | 13295 | 20962 | 15213 | 23235 | 20397 | 17441 | 15001 | 12232 | 11604 | 17347 | 14194 | 12367 | 11422 | 14347 | 2438 | 21372 | 27863 | 22024 | 21311 | 20253 | 16035 | 15652 | 10849 | 22151 | 16245 | 12578 | 8.21 | 8.3956 | 6.3472 | 6.6361 | 6.9495 | 6.1681 | 5.8844 | 6.0065 | 5.8204 | 6.5057 | 6.2432 | 6.0036 | 5.7341 | 5.8866 | 6.3255 | 6.5639 | 8.1675 | 6.5279 | 6.4631 | 6.4451 | 6.0704 | 7.0638 | 5.6775 | 6.7118 | 6.9638 | 5.8219 | 427828 | 6.5228 |  |  | 417150 | 0 | 417150 | 10678 | 2.496% | 70.2 | 24083.8757 | 695.58
2025-01-06 | 2025 | 2025 | 2025-01-01 | 31 | 0 | 30086 | 27147 | 31840 | 27977 | 26028 | 30132 | 24295 | 25084 | 29278 | 30098 | 29051 | 24638 | 23828 | 34427 | 30014 | 33210 | 27365 | 30648 | 28529 | 26616 | 29522 | 24689 | 28243 | 11761 | 22775 | 5.08 | 8.8896 | 8.1654 | 8.0422 | 8.7695 | 8.3329 | 7.9455 | 8.1163 | 8.2158 | 8.4346 | 8.1498 | 8.1613 | 7.9698 | 7.854 | 8.4959 | 9.072 | 8.7544 | 8.6439 | 8.034 | 8.8419 | 8.6817 | 9.0498 | 7.9245 | 8.9143 | 8.6097 | 7.9242 | 687281 | 8.272 |  |  | 677250 | 0 | 677250 | 10031 | 1.46% | 70.2 | 37993.9993 | 1184.81
2025-01-07 | 2025 | 2025 | 2025-01-01 | 31 | 4235 | 33522 | 32468 | 36150 | 31205 | 38921 | 37379 | 24936 | 29271 | 31394 | 26888 | 32114 | 27084 | 28974 | 27759 | 38114 | 44675 | 39531 | 37682 | 35628 | 41137 | 42073 | 30813 | 38437 | 32211 | 28959 | 7.9077 | 7.6814 | 8.9017 | 8.8256 | 9.1426 | 8.9525 | 8.8782 | 8.5879 | 8.9177 | 8.9264 | 8.2131 | 8.8003 | 8.9098 | 8.463 | 8.9975 | 9.096 | 9.2264 | 9.1807 | 9.0737 | 8.8259 | 9.2433 | 9.3557 | 8.7286 | 9.1954 | 9.1186 | 8.7276 | 851560 | 8.8414 |  |  | 823950 | 0 | 823950 | 27610 | 3.242% | 70.2 | 13241.2508 | 1183.83
2025-01-08 | 2025 | 2025 | 2025-01-01 | 31 | 20730 | 27955 | 24437 | 23483 | 22370 | 34902 | 23144 | 18975 | 24873 | 21019 | 20149 | 25257 | 24973 | 22959 | 22765 | 34966 | 41019 | 28128 | 12012 | 26005 | 35549 | 32784 | 23238 | 32622 | 24275 | 16377 | 5.0393 | 4.7664 | 7.3189 | 7.4293 | 7.8083 | 8.0678 | 7.3141 | 7.7812 | 7.6228 | 7.1912 | 6.8706 | 7.603 | 7.7285 | 7.4561 | 7.6437 | 8.1914 | 8.2429 | 7.262 | 7.2221 | 7.6661 | 8.2601 | 8.1732 | 7.6541 | 8.0531 | 7.933 | 7.6084 | 664966 | 7.458 |  |  | 645300 | 0 | 645300 | 19666 | 2.957% | 70.2 | 455.125 | 1036.22
2025-01-09 | 2025 | 2025 | 2025-01-01 | 31 | 13807 | 13355 | 14404 | 11867 | 9959 | 18928 | 7670 | 11864 | 13020 | 13410 | 14315 | 14152 | 13214 | 11731 | 16638 | 17533 | 18462 | 12592 | 9868 | 16114 | 19475 | 18235 | 13782 | 15203 | 13427 | 10740 | 4.9281 | 4.4086 | 4.762 | 4.6604 | 4.9031 | 5.6178 | 2.7498 | 5.2436 | 4.8725 | 5.0548 | 4.9315 | 5.0262 | 4.9992 | 4.7052 | 5.0992 | 5.5072 | 5.2125 | 4.7835 | 4.5445 | 5.3649 | 5.6451 | 5.5735 | 4.9269 | 5.2844 | 5.2385 | 4.6806 | 363765 | 4.9509 |  |  | 355050 | 1350 | 353700 | 8715 | 2.396% | 70.2 | 5999.25 | 532.63
2025-01-10 | 2025 | 2025 | 2025-01-01 | 31 | 12647 | 10433 | 11022 | 8379 | 8726 | 17000 | 1253 | 11469 | 11285 | 11905 | 10313 | 11562 | 9555 | 12483 | 15554 | 13751 | 11712 | 16809 | 8150 | 13873 | 15937 | 14491 | 12686 | 12258 | 10426 | 8933 | 5.5779 | 5.5215 | 4.8023 | 4.3386 | 4.4232 | 5.491 | 1.1248 | 4.7367 | 4.7618 | 4.9739 | 4.7195 | 4.8962 | 4.7132 | 4.9545 | 5.1393 | 5.1145 | 4.4376 | 5.303 | 4.3063 | 5.1514 | 5.3733 | 5.1181 | 5.0035 | 5.0206 | 4.6856 | 4.9509 | 302612 | 4.7938 |  |  | 295200 | 900 | 294300 | 7412 | 2.449% | 70.2 | 4061.25 | 430.5
2025-01-11 | 2025 | 2025 | 2025-01-01 | 31 | 10292 | 13207 | 9032 | 15240 | 12810 | 10323 | 12668 | 10147 | 7206 | 7441 | 8137 | 9079 | 6702 | 7970 | 8137 | 12102 | 19601 | 11708 | 8752 | 11838 | 11086 | 12397 | 9422 | 12347 | 12078 | 56 | 8.1901 | 7.953 | 4.9886 | 5.7192 | 5.8031 | 5.2431 | 5.519 | 5.4072 | 5.1932 | 4.9805 | 5.1445 | 5.3239 | 4.8305 | 5.0868 | 5.0488 | 5.5533 | 5.8766 | 5.03 | 4.9121 | 5.4788 | 5.2867 | 5.4715 | 5.3645 | 5.6065 | 5.7282 | 5.4484 | 269778 | 5.5457 |  |  | 261900 | 0 | 261900 | 7878 | 2.92% | 70.2 | 12134.2503 | 461.5818
2025-01-12 | 2025 | 2025 | 2025-01-01 | 31 | 30368 | 33526 | 31526 | 29823 | 27860 | 19387 | 29832 | 24804 | 35158 | 28313 | 30608 | 28189 | 18497 | 29825 | 33126 | 24061 | 33837 | 32143 | 27251 | 27282 | 23520 | 27799 | 19733 | 28115 | 31974 | 31090 | 9.3448 | 9.2125 | 7.8638 | 7.7592 | 7.9365 | 6.8969 | 7.8239 | 7.4672 | 8.2599 | 7.8961 | 8.0263 | 7.7301 | 7.7049 | 7.9182 | 7.8294 | 7.3715 | 7.6124 | 7.8603 | 7.6801 | 7.7851 | 7.4414 | 7.7853 | 7.8321 | 7.9476 | 8.1607 | 7.938 | 737647 | 7.8878 |  |  | 715050 | 0 | 715050 | 22597 | 3.063% | 70.2 | 15119.5018 | 1054.22
2025-01-13 | 2025 | 2025 | 2025-01-01 | 31 | 39515 | 44709 | 40709 | 34707 | 39326 | 38531 | 41402 | 13917 | 33089 | 37092 | 33754 | 40316 | 34219 | 38439 | 45181 | 40376 | 53098 | 43342 | 42649 | 35843 | 42825 | 43520 | 34130 | 37485 | 42752 | 43310 | 7.8563 | 7.8322 | 8.8527 | 8.4981 | 9.1514 | 9.0148 | 9.1587 | 9.2978 | 9.2093 | 9.0133 | 8.3839 | 8.9701 | 9.0321 | 8.8565 | 9.2345 | 9.1649 | 9.6197 | 9.3669 | 9.369 | 9.2534 | 9.4946 | 9.6196 | 8.7987 | 9.2679 | 9.3258 | 9.1212 | 1014236 | 9.0294 |  |  | 982350 | 0 | 982350 | 31886 | 3.144% | 70.2 | 5005.8752 | 1383.3742
2025-01-14 | 2025 | 2025 | 2025-01-01 | 31 | 29911 | 33973 | 15127 | 23197 | 29073 | 26644 | 23945 | 24579 | 26361 | 23717 | 23376 | 26999 | 25113 | 23665 | 30103 | 28619 | 38561 | 27706 | 31044 | 21548 | 26628 | 29893 | 21347 | 26763 | 32360 | 26708 | 7.671 | 6.8814 | 7.3942 | 7.1027 | 7.8872 | 7.5845 | 7.1667 | 7.1408 | 7.2656 | 7.2685 | 7.0945 | 7.4444 | 7.4846 | 7.157 | 7.4167 | 7.7235 | 7.9894 | 7.4151 | 7.9973 | 7.2835 | 7.6475 | 7.8838 | 7.4369 | 7.8443 | 8.0866 | 7.6189 | 696960 | 7.4956 |  |  | 677700 | 0 | 677700 | 19260 | 2.763% | 70.2 | 6068 | 987.6764
2025-01-15 | 2025 | 2025 | 2025-01-01 | 31 | 26804 | 24576 | 1592 | 21058 | 22992 | 15662 | 21713 | 20649 | 23499 | 22931 | 22245 | 22866 | 17516 | 22231 | 27764 | 18899 | 26865 | 22617 | 17365 | 19574 | 16729 | 19587 | 19921 | 20969 | 25890 | 24281 | 9.7726 | 9.6092 | 7.6289 | 6.8646 | 7.4519 | 6.4175 | 6.8609 | 6.8698 | 7.1762 | 7.2412 | 7.1553 | 7.1149 | 6.8252 | 7.1682 | 7.2741 | 6.7338 | 6.82 | 6.795 | 6.7028 | 7.0027 | 6.6465 | 6.896 | 7.0681 | 7.1884 | 7.5658 | 6.9911 | 546795 | 7.2247 |  |  | 531900 | 0 | 531900 | 14895 | 2.724% | 70.2 | 27407.999 | 836.501
2025-01-16 | 2025 | 2025 | 2025-01-01 | 31 | 45199 | 38473 | 44243 | 35970 | 29166 | 36294 | 29432 | 35814 | 34996 | 44031 | 42853 | 39600 | 40231 | 40093 | 43886 | 42811 | 41002 | 41917 | 32251 | 40063 | 37693 | 38531 | 42139 | 42722 | 43342 | 47468 | 8.8293 | 8.929 | 9.2958 | 9.0591 | 9.6721 | 9.0021 | 9.4343 | 8.7261 | 9.9145 | 9.7296 | 9.4585 | 9.115 | 9.388 | 9.2524 | 9.2647 | 9.6735 | 8.5576 | 9.439 | 8.769 | 9.5936 | 9.1565 | 9.2829 | 9.5837 | 9.6597 | 9.7328 | 9.6516 | 1030220 | 9.3142 |  |  | 997200 | 0 | 997200 | 33020 | 3.205% | 70.2 | 9643.876 | 1234.5788
2025-01-17 | 2025 | 2025 | 2025-01-01 | 31 | 27143 | 11597 | 29903 | 28121 | 32014 | 35003 | 26417 | 31145 | 19646 | 29180 | 25514 | 32386 | 28827 | 29310 | 33062 | 34973 | 40522 | 33327 | 29886 | 25525 | 36408 | 34609 | 29920 | 34468 | 26582 | 33351 | 4.389 | 4.3159 | 8.0043 | 8.0727 | 8.7166 | 8.8291 | 9.2482 | 8.2642 | 8.6985 | 8.2036 | 7.8272 | 8.4704 | 8.3462 | 8.1897 | 8.3534 | 8.915 | 8.774 | 8.5153 | 8.4344 | 8.48 | 9.181 | 8.8302 | 8.3538 | 8.8675 | 8.918 | 8.3587 | 778839 | 8.2137 |  |  | 758700 | 0 | 758700 | 20139 | 2.586% | 70.2 | 1525.0007 | 1070.4026
2025-01-18 | 2025 | 2025 | 2025-01-01 | 31 | 11825 | 12706 | 10015 | 9526 | 13799 | 11196 | 10241 | 11367 | 9457 | 8357 | 7351 | 10139 | 9282 | 8486 | 10486 | 11937 | 14726 | 8504 | 8024 | 8653 | 12278 | 11947 | 9892 | 9248 | 13965 | 9690 | 4.0638 | 3.7045 | 4.0648 | 4.2164 | 4.6218 | 4.512 | 5.4458 | 4.2443 | 4.0216 | 3.9729 | 3.9185 | 4.1173 | 4.0717 | 3.9078 | 4.0822 | 4.6345 | 4.8793 | 4.0669 | 4.2109 | 4.7 | 4.7071 | 4.7773 | 4.1105 | 4.3707 | 4.5346 | 4.0683 | 273097 | 4.3087 |  |  | 270000 | 1800 | 268200 | 3097 | 1.134% | 70.2 | 77.75 | 365.5016
2025-01-19 | 2025 | 2025 | 2025-01-01 | 31 | 4946 | 5917 | 5460 | 3966 | 4104 | 5397 | 3929 | 5146 | 5519 | 4416 | 4929 | 5248 | 3478 | 3838 | 6022 | 5494 | 8193 | 5511 | 4147 | 4120 | 4655 | 6277 | 5320 | 3853 | 5742 | 5829 | 3.3503 | 3.2399 | 3.968 | 3.6022 | 3.8049 | 4.1896 | 4.5494 | 3.8575 | 3.9681 | 4.0498 | 3.9399 | 3.964 | 3.8128 | 3.6494 | 3.9694 | 4.1201 | 4.1555 | 3.7359 | 3.6925 | 3.54 | 4.1289 | 4.227 | 4.0378 | 4.0306 | 4.044 | 3.7941 | 131456 | 3.9008 |  |  | 156000 | 1350 | 154650 | -24544 | -18.67% | 70.2 | 0 | 199.814
2025-01-20 | 2025 | 2025 | 2025-01-01 | 31 | 2063 | 2940 | 1819 | 1972 | 2295 | 1982 | 2223 | 2049 | 2000 | 1983 | 1318 | 1906 | 1525 | 1444 | 1784 | 2192 | 4090 | 1899 | 2806 | 1279 | 1908 | 2838 | 1806 | 3194 | 2882 | 2021 | 4.7907 | 4.6143 | 3.0428 | 3.4158 | 3.4508 | 3.2916 | 3.7044 | 3.1104 | 3.0278 | 3.1091 | 2.9419 | 3.1698 | 3.2166 | 3.0481 | 3.0711 | 3.3879 | 3.7222 | 3.0938 | 3.902 | 3.08 | 3.3624 | 3.5554 | 3.0496 | 3.2314 | 3.544 | 3.1034 | 56218 | 3.386 |  |  | 53100 | 1350 | 51750 | 3118 | 5.546% | 70.2 | 0 | 87.1251
2025-01-21 | 2025 | 2025 | 2025-01-01 | 31 | 6215 | 8972 | 6658 | 5734 | 5567 | 3386 | 6371 | 5449 | 6724 | 9203 | 4989 | 4870 | 3822 | 4428 | 5365 | 3644 | 7450 | 4409 | 6905 | 2619 | 3405 | 4947 | 5181 | 6830 | 6619 | 6266 | 6.154 | 5.9897 | 4.6741 | 4.3365 | 4.749 | 3.9359 | 4.5711 | 4.262 | 4.7849 | 4.4417 | 4.4999 | 4.3797 | 4.2956 | 4.2927 | 4.3909 | 4.0885 | 4.4947 | 3.9964 | 4.6506 | 4.1 | 4.1207 | 4.4067 | 4.4206 | 3.9247 | 4.6928 | 4.4757 | 146028 | 4.505 |  |  | 141300 | 0 | 141300 | 4728 | 3.238% | 70.2 | 1392.25 | 208.4434
2025-01-22 | 2025 | 2025 | 2025-01-01 | 31 | 11285 | 15835 | 10559 | 11317 | 10653 | 10114 | 9061 | 9673 | 5616 | 19015 | 10795 | 10442 | 8956 | 9785 | 14834 | 11660 | 10802 | 11520 | 9156 | 20496 | 9478 | 9642 | 10574 | 20272 | 12002 | 12382 | 8.6261 | 8.7273 | 5.8431 | 5.82 | 6.2162 | 5.83 | 5.5041 | 5.4576 | 6.2883 | 5.889 | 6.0292 | 5.8408 | 5.8367 | 5.7965 | 6.1017 | 5.9329 | 5.9827 | 5.5819 | 5.4977 | 5.83 | 5.8301 | 5.7627 | 6.0103 | 5.9572 | 6.1626 | 5.8125 | 305924 | 6.0834 |  |  | 298800 | 0 | 298800 | 7124 | 2.329% | 70.2 | 24193.6265 | 476.6758
2025-01-23 | 2025 | 2025 | 2025-01-01 | 31 | 28030 | 33496 | 26462 | 30999 | 29417 | 28574 | 27825 | 26122 | 7976 | 37327 | 27642 | 23186 | 22085 | 25987 | 31940 | 44142 | 33768 | 31057 | 27085 | 42214 | 28682 | 30091 | 25354 | 45851 | 28450 | 27588 | 9.8916 | 9.8204 | 8.2252 | 8.6171 | 8.8897 | 8.4076 | 8.2696 | 8.1363 | 9.5166 | 8.7653 | 8.4175 | 8.4015 | 8.1563 | 8.2333 | 8.6218 | 8.7892 | 8.5088 | 8.5223 | 8.1105 | 8.15 | 8.5845 | 8.6388 | 8.3186 | 8.8929 | 8.6682 | 8.3509 | 771350 | 8.6117 |  |  | 750600 | 0 | 750600 | 20750 | 2.69% | 70.2 | 22743.1253 | 1094.2707
2025-01-24 | 2025 | 2025 | 2025-01-01 | 31 | 41014 | 42863 | 39812 | 36421 | 37924 | 45489 | 38928 | 38398 | 43018 | 52500 | 34649 | 35763 | 30683 | 35613 | 41368 | 60292 | 52888 | 45609 | 43130 | 48659 | 46289 | 46609 | 38071 | 46368 | 36372 | 39415 | 7.3047 | 7.1699 | 9.65 | 9.059 | 9.7831 | 9.9953 | 9.2472 | 9.5698 | 9.9806 | 9.8741 | 9.2212 | 9.5423 | 9.8865 | 9.475 | 9.832 | 10.2547 | 10.1461 | 10.0422 | 9.627 | 10.2 | 10.2458 | 10.3743 | 9.7367 | 8.9375 | 9.8636 | 9.6651 | 1098145 | 9.5648 |  |  | 1061100 | 0 | 1061100 | 37045 | 3.373% | 70.2 | 18387.2537 | 1433.7308
2025-01-25 | 2025 | 2025 | 2025-01-01 | 31 | 19114 | 24275 | 16817 | 16334 | 19021 | 22887 | 17996 | 16081 | 21558 | 29554 | 15950 | 19157 | 14758 | 15691 | 17992 | 31163 | 25832 | 20112 | 22647 | 23740 | 23755 | 25203 | 18303 | 28874 | 20880 | 21026 | 5.6931 | 5.2108 | 6.9337 | 6.6534 | 7.2602 | 7.382 | 6.8988 | 6.9957 | 7.2729 | 7.1491 | 6.7961 | 7.1773 | 6.8828 | 6.8364 | 7.4736 | 7.4966 | 7.8213 | 6.9251 | 8.011 | 7.79 | 7.7092 | 7.8544 | 7.0091 | 6.9564 | 7.3023 | 7.0745 | 548720 | 7.0987 |  |  | 531000 | 0 | 531000 | 17720 | 3.229% | 70.2 | 2491.875 | 834.5294
2025-01-26 | 2025 | 2025 | 2025-01-01 | 31 | 10853 | 12692 | 12328 | 8567 | 7314 | 5560 | 10598 | 10348 | 13337 | 18371 | 10395 | 9712 | 6876 | 8732 | 15579 | 13538 | 13197 | 9570 | 12341 | 12456 | 6687 | 8007 | 9622 | 17500 | 10645 | 11108 | 4.3864 | 4.2042 | 5.6318 | 4.9994 | 5.2494 | 4.5846 | 5.4702 | 5.2583 | 5.7717 | 5.4475 | 5.5392 | 5.5207 | 5.1845 | 5.2415 | 5.1616 | 5.0168 | 5.2299 | 5.0094 | 5.7293 | 5.13 | 5.1727 | 5.2583 | 5.3313 | 5.3725 | 5.5557 | 5.3469 | 285933 | 5.2232 |  |  | 278550 | 0 | 278550 | 7383 | 2.582% | 70.2 | 1329.625 | 396.8252
2025-01-27 | 2025 | 2025 | 2025-01-01 | 31 | 3695 | 5036 | 4195 | 3981 | 3295 | 2582 | 4237 | 2740 | 4582 | 5980 | 3379 | 6979 | 1940 | 3123 | 6022 | 5205 | 5138 | 3985 | 5664 | 4769 | 2699 | 3735 | 3686 | 6728 | 3868 | 4113 | 3.4846 | 2.8444 | 4.3882 | 4.0658 | 4.3395 | 3.755 | 4.306 | 3.9674 | 4.4602 | 4.1111 | 4.1859 | 4.2989 | 3.8899 | 4.1229 | 4.1016 | 3.9599 | 4.132 | 3.9681 | 4.6088 | 4.12 | 3.9672 | 4.2939 | 4.1684 | 3.9928 | 4.3385 | 4.2418 | 111356 | 4.0813 |  |  | 106200 | 0 | 106200 | 5156 | 4.63% | 70.2 | 0 | 175.54
2025-01-28 | 2025 | 2025 | 2025-01-01 | 31 | 2188 | 2309 | 2621 | 1564 | 1414 | 922 | 1570 | 1606 | 2884 | 3717 | 2654 | 3960 | 1475 | 1999 | 3891 | 2336 | 1511 | 2282 | 3131 | 2239 | 1088 | 1906 | 2335 | 2876 | 2041 | 2469 | 4.1778 | 4.129 | 3.4559 | 2.6932 | 2.9682 | 2.8383 | 2.7916 | 2.9406 | 3.4871 | 3.5763 | 3.4396 | 3.3299 | 3.106 | 3.273 | 3.316 | 3.0796 | 2.8734 | 3.266 | 2.8323 | 3.2 | 3.0216 | 3.2826 | 3.3572 | 3.2043 | 3.1001 | 3.3452 | 58988 | 3.234 |  |  | 55800 | 1800 | 54000 | 3188 | 5.404% | 70.2 | 1225.375 | 77.7525
2025-01-29 | 2025 | 2025 | 2025-01-01 | 31 | 4028 | 5953 | 5122 | 5000 | 3753 | 3993 | 3121 | 1534 | 6119 | 5280 | 10325 | 10563 | 4181 | 4307 | 9195 | 8695 | 6103 | 4755 | 7375 | 6157 | 3602 | 4037 | 4833 | 8992 | 4082 | 3640 | 5.0485 | 5.1593 | 4.4758 | 4.1454 | 4.1526 | 4.2154 | 4.4182 | 3.7772 | 4.5535 | 4.0131 | 4.5812 | 4.532 | 4.4588 | 4.3716 | 4.4453 | 4.3207 | 4.0299 | 4.0517 | 3.8831 | 4.1 | 4.2339 | 4.2096 | 4.5218 | 4.4088 | 4.0234 | 3.7465 | 144745 | 4.303 |  |  | 138600 | 450 | 138150 | 6145 | 4.245% | 70.2 | 1437 | 223.7468
2025-01-30 | 2025 | 2025 | 2025-01-01 | 31 | 6128 | 10426 | 8391 | 6933 | 6409 | 6553 | 4307 | 12112 | 8867 | 13364 | 12306 | 15239 | 6238 | 7491 | 14817 | 12990 | 10665 | 7783 | 12901 | 11046 | 5842 | 6698 | 7646 | 12816 | 7702 | 7413 | 5.5615 | 5.5781 | 5.3709 | 4.9561 | 5.0936 | 5.0779 | 5.3472 | 4.8437 | 5.4146 | 5.2089 | 5.3812 | 5.3424 | 5.3125 | 5.3938 | 5.3508 | 5.2016 | 5.0899 | 4.9383 | 4.9603 | 4.85 | 5.0844 | 5.2314 | 5.3242 | 5.2266 | 5.1312 | 4.9985 | 243083 | 5.2027 |  |  | 237150 | 900 | 236250 | 5933 | 2.441% | 70.2 | 5594.625 | 368.1552
2025-01-31 | 2025 | 2025 | 2025-01-01 | 31 | 9885 | 9932 | 7933 | 8955 | 7546 | 6774 | 6804 | 15685 | 8405 | 12713 | 15124 | 15000 | 5743 | 5934 | 14840 | 14393 | 8735 | 8073 | 19810 | 14390 | 5562 | 6839 | 7161 | 16232 | 19447 | 6538 | 6.1914 | 6.1116 | 5.3065 | 5.6265 | 5.6914 | 5.1838 | 6.4907 | 5.3117 | 5.3413 | 5.1052 | 5.3909 | 5.3189 | 5.2552 | 5.1962 | 5.3174 | 5.3935 | 5.4194 | 5.1062 | 5.6618 | 5.32 | 5.1081 | 5.365 | 5.3498 | 5.6661 | 5.7302 | 5.1532 | 278453 | 5.4658 |  |  | 269100 | 0 | 269100 | 9353 | 3.359% | 70.2 | 6986.75 | 411.2329
2025-02-01 | 2025 | 2025 | 2025-02-01 | 28 | 23251 | 15614 | 13146 | 17450 | 14435 | 11826 | 12480 | 22168 | 14084 | 20076 | 20423 | 19508 | 11100 | 9725 | 20489 | 22832 | 726 | 13699 | 26952 | 20735 | 11487 | 12900 | 12149 | 22522 | 23709 | 10440 | 3.7061 | 3.1326 | 5.8169 | 6.2969 | 6.4185 | 5.7605 | 5.7851 | 6.0387 | 6.0174 | 5.9719 | 6.0752 | 6.0473 | 5.8396 | 5.6604 | 5.9887 | 6.2259 | 4.7416 | 5.7765 | 6.1824 | 6.3 | 5.8971 | 6.0728 | 6.1227 | 6.3265 | 6.2885 | 5.5541 | 423926 | 5.7709 |  |  | 414900 | 0 | 414900 | 9026 | 2.129% | 70.2 | 0 | 525.5102
2025-02-02 | 2025 | 2025 | 2025-02-01 | 28 | 5678 | 2993 | 3656 | 2127 | 3686 | 2070 | 1633 | 3959 | 2840 | 4574 | 3794 | 4327 | 2013 | 2386 | 4490 | 3506 | 3397 | 2810 | 2899 | 3060 | 1736 | 2114 | 4081 | 3630 | 6030 | 3285 | 3.2301 | 2.9517 | 3.5436 | 3.2534 | 3.5613 | 3.2765 | 3.0148 | 3.2831 | 3.4433 | 3.439 | 3.3878 | 3.4926 | 3.2345 | 3.2526 | 3.3953 | 3.3144 | 3.3206 | 3.2667 | 3.081 | 3.1 | 3.3091 | 3.2596 | 3.4584 | 3.3615 | 3.6968 | 3.4712 | 86774 | 3.323 |  |  | 83250 | 1350 | 81900 | 3524 | 4.061% | 70.2 | 293.875 | 90.1346
2025-02-03 | 2025 | 2025 | 2025-02-01 | 28 | 4461 | 3239 | 2969 | 2627 | 2927 | 3127 | 1962 | 3008 | 3025 | 3784 | 4108 | 3849 | 2034 | 2455 | 3915 | 3164 | 2526 | 3085 | 3240 | 3269 | 1373 | 1746 | 3994 | 3296 | 4446 | 2915 | 6.5493 | 5.8121 | 3.1345 | 2.8719 | 3.0029 | 2.7358 | 2.8265 | 2.7267 | 3.1958 | 2.9163 | 3.1057 | 3.084 | 2.8582 | 2.9317 | 2.9112 | 2.78 | 2.7069 | 2.9477 | 2.7639 | 2.4 | 2.5978 | 2.7644 | 3.0238 | 2.8156 | 3.0968 | 2.9852 | 80544 | 3.1363 |  |  | 77850 | 2250 | 75600 | 2694 | 3.345% | 70.2 | 9484.25 | 87.9835
2025-02-04 | 2025 | 2025 | 2025-02-01 | 28 | 22803 | 14177 | 15404 | 14065 | 15624 | 20273 | 11254 | 19513 | 13602 | 20739 | 20387 | 19994 | 10801 | 13237 | 21493 | 20408 | 20092 | 22266 | 19327 | 20837 | 10684 | 12368 | 20477 | 20558 | 2763 | 14312 | 6.851 | 6.7154 | 6.1387 | 5.9122 | 6.3206 | 6.0201 | 5.6231 | 6.0605 | 6.2372 | 6.4582 | 6.3391 | 6.2419 | 5.6687 | 5.9961 | 6.4513 | 6.2385 | 6.1405 | 6.151 | 5.844 | 5.45 | 5.8099 | 6.1064 | 6.2767 | 6.3309 | 6.4779 | 5.9177 | 437458 | 6.1453 |  |  | 427050 | 0 | 427050 | 10408 | 2.379% | 70.2 | 12316.7502 | 540.9671
2025-02-05 | 2025 | 2025 | 2025-02-01 | 28 | 28786 | 23318 | 19148 | 17748 | 21238 | 25778 | 18802 | 26222 | 15407 | 25612 | 24643 | 25131 | 17795 | 17353 | 28108 | 25950 | 28603 | 27551 | 29142 | 0 | 13824 | 15290 | 25800 | 21679 | 23602 | 20690 | 9.958 | 9.5831 | 6.511 | 6.4801 | 6.8275 | 6.6165 | 6.6974 | 6.5451 | 6.9922 | 6.7041 | 6.6029 | 6.6605 | 6.5454 | 6.4514 | 6.8631 | 6.7593 | 7.0308 | 6.644 | 6.7619 | 6.5391 | 6.5146 | 6.7834 | 6.6814 | 6.2724 | 6.9826 | 6.4778 | 567220 | 6.9033 |  |  | 568350 | 0 | 568350 | -1130 | -0.1992% | 70.2 | 3832.3738 | 663.7691
2025-02-06 | 2025 | 2025 | 2025-02-01 | 28 | 55226 | 43711 | 46917 | 39424 | 47277 | 50382 | 41611 | 56591 | 38699 | 53986 | 53413 | 57391 | 45189 | 42555 | 57478 | 57161 | 43281 | 57274 | 61082 | 52404 | 42539 | 44189 | 55321 | 45592 | 55112 | 36898 | 9.4708 | 9.2135 | 9.4769 | 9.1185 | 9.6646 | 9.6072 | 9.3037 | 9.4902 | 10.1722 | 9.6357 | 9.3497 | 9.5398 | 9.4708 | 9.1897 | 9.6393 | 9.8705 | 9.6685 | 9.6724 | 9.6922 | 9.6324 | 9.6526 | 9.7969 | 9.6317 | 8.9822 | 9.8738 | 9.8397 | 1280703 | 9.5637 |  |  | 1238850 | 0 | 1238850 | 41853 | 3.268% | 70.2 | 5481.625 | 1460.1438
2025-02-07 | 2025 | 2025 | 2025-02-01 | 28 | 47800 | 43654 | 38264 | 34925 | 36148 | 49644 | 35356 | 45711 | 30347 | 41372 | 44113 | 48730 | 33765 | 39863 | 47911 | 47853 | 46641 | 44842 | 47996 | 42315 | 41583 | 42326 | 48440 | 44017 | 11497 | 42707 | 4.6927 | 4.4174 | 8.5579 | 8.5421 | 9.2052 | 9.8428 | 8.5651 | 9.0515 | 9.3321 | 8.8947 | 8.7858 | 9.4114 | 9.1869 | 9.014 | 9.3736 | 9.7984 | 9.4526 | 9.1115 | 9.0709 | 8.9728 | 9.964 | 9.8417 | 9.171 | 9.3517 | 8.9005 | 9.0733 | 1077820 | 8.8301 |  |  | 1039500 | 0 | 1039500 | 38320 | 3.555% | 70.2 | 6503.751 | 1199.0706
2025-02-08 | 2025 | 2025 | 2025-02-01 | 28 | 11334 | 7934 | 12630 | 8929 | 13282 | 19776 | 10149 | 12579 | 15284 | 14830 | 11660 | 16477 | 13112 | 11567 | 15423 | 17277 | 14955 | 14255 | 13978 | 14765 | 13134 | 12767 | 15536 | 15102 | 3131 | 10805 | 3.3444 | 3.2125 | 4.7185 | 4.2971 | 4.7813 | 5.3561 | 5.3482 | 4.5967 | 4.6517 | 4.839 | 4.6677 | 4.8532 | 4.966 | 4.6644 | 4.8197 | 5.0909 | 4.8889 | 4.6241 | 4.4565 | 4.8627 | 5.4301 | 5.2832 | 4.7479 | 4.8739 | 4.9442 | 4.3354 | 340671 | 4.7175 |  |  | 329850 | 0 | 329850 | 10821 | 3.176% | 70.2 | 277 | 406.9434
2025-02-09 | 2025 | 2025 | 2025-02-01 | 28 | 4155 | 3143 | 2660 | 2344 | 4191 | 4579 | 2005 | 3656 | 3355 | 3547 | 3596 | 3958 | 2149 | 2289 | 3699 | 4498 | 2215 | 3769 | 3403 | 3765 | 2332 | 3228 | 4074 | 3950 | 4514 | 2825 | 3.1732 | 3.144 | 3.3217 | 3.2335 | 3.3237 | 3.688 | 3.1631 | 3.2742 | 3.084 | 3.4654 | 3.3358 | 3.3763 | 3.2101 | 3.2253 | 3.2922 | 3.6474 | 3.8434 | 3.294 | 3.2062 | 3.4829 | 3.524 | 3.7269 | 3.3668 | 3.5297 | 3.3828 | 3.2096 | 87899 | 3.3663 |  |  | 82800 | 1350 | 81450 | 5099 | 5.801% | 70.2 | 976.5 | 49.5865
2025-02-10 | 2025 | 2025 | 2025-02-01 | 28 | 4909 | 4280 | 3806 | 5201 | 4884 | 5331 | 1347 | 4349 | 4960 | 3735 | 4766 | 5460 | 2669 | 3847 | 4317 | 4362 | 3881 | 5298 | 3834 | 4362 | 2385 | 2545 | 5513 | 5180 | 5222 | 3236 | 5.5847 | 5.7517 | 3.2971 | 3.2556 | 3.1729 | 3.4574 | 3.1244 | 3.0005 | 3.2067 | 3.2464 | 3.2627 | 3.303 | 3.0999 | 3.2617 | 3.1805 | 3.2097 | 3.4753 | 3.3006 | 3.2627 | 3.1872 | 3.3208 | 3.3217 | 3.2621 | 3.2582 | 3.1953 | 2.9549 | 109679 | 3.4213 |  |  | 106200 | 1800 | 104400 | 3479 | 3.172% | 70.2 | 8922 | 109.7
2025-02-11 | 2025 | 2025 | 2025-02-01 | 28 | 18618 | 17659 | 12147 | 16596 | 21542 | 14975 | 17764 | 17575 | 17104 | 13283 | 14989 | 19059 | 12069 | 13890 | 15134 | 16190 | 16026 | 14583 | 15351 | 15892 | 13270 | 13463 | 18619 | 18010 | 16222 | 13112 | 5.668 | 5.8778 | 5.4189 | 6.0073 | 5.9265 | 5.4138 | 5.5503 | 5.4388 | 5.4999 | 5.1358 | 5.3591 | 5.7999 | 5.2586 | 5.3891 | 5.2956 | 5.9687 | 5.4941 | 5.1573 | 5.1306 | 5.4864 | 5.6344 | 5.6487 | 5.6881 | 5.7705 | 5.889 | 5.2103 | 413142 | 5.543 |  |  | 402750 | 0 | 402750 | 10392 | 2.515% | 70.2 | 20071.7505 | 397.98
2025-02-12 | 2025 | 2025 | 2025-02-01 | 28 | 15308 | 14517 | 14572 | 17024 | 19076 | 10998 | 14580 | 14173 | 12640 | 13675 | 15716 | 14169 | 10952 | 10746 | 12881 | 17909 | 17533 | 15527 | 18433 | 15451 | 10911 | 10597 | 13725 | 17263 | 19240 | 11311 | 5.5258 | 5.3102 | 5.5417 | 5.6131 | 6.1419 | 4.9721 | 5.3307 | 5.3111 | 5.3139 | 5.3745 | 5.6126 | 5.4938 | 5.0997 | 5.0658 | 5.3187 | 5.7806 | 5.7054 | 5.414 | 5.6602 | 5.543 | 4.9214 | 5.4916 | 5.3642 | 5.6625 | 6.1023 | 5.1598 | 378927 | 5.455 |  |  | 368100 | 0 | 368100 | 10827 | 2.857% | 70.2 | 1179.1253 | 443.69
2025-02-13 | 2025 | 2025 | 2025-02-01 | 28 | 16547 | 14415 | 17400 | 13341 | 15369 | 10577 | 13702 | 14379 | 17492 | 13548 | 14209 | 15462 | 12831 | 12447 | 12948 | 11877 | 13307 | 13443 | 16782 | 11577 | 7434 | 14669 | 15953 | 13151 | 17515 | 13813 | 4.077 | 3.8376 | 5.4905 | 5.0735 | 5.4667 | 4.9831 | 5.1315 | 5.1969 | 5.5983 | 5.1869 | 5.1647 | 5.3931 | 5.1868 | 5.0897 | 5.15 | 5.0561 | 5.2978 | 5.0613 | 5.5846 | 5.0375 | 5.1595 | 5.5955 | 5.3674 | 5.0389 | 5.5677 | 5.2909 | 364188 | 5.1571 |  |  | 355050 | 0 | 355050 | 9138 | 2.509% | 70.2 | 3264.375 | 352.32
2025-02-14 | 2025 | 2025 | 2025-02-01 | 28 | 8924 | 7721 | 8681 | 7574 | 8030 | 4682 | 5962 | 5761 | 8412 | 5713 | 7040 | 6687 | 5707 | 6494 | 6123 | 6276 | 6204 | 6484 | 8084 | 5817 | 4646 | 6060 | 7565 | 6741 | 9518 | 5303 | 7.3169 | 7.4486 | 3.9524 | 3.7739 | 3.8934 | 3.4944 | 3.6125 | 3.4699 | 3.9685 | 3.717 | 3.7135 | 3.7326 | 3.6646 | 3.7147 | 3.5966 | 3.7148 | 3.7008 | 3.6105 | 3.8507 | 3.6531 | 3.5033 | 3.6857 | 3.7576 | 3.7648 | 4.1199 | 3.5981 | 176209 | 4.0011 |  |  | 171000 | 1350 | 169650 | 5209 | 2.956% | 70.2 | 13680.3753 | 172.13
2025-02-15 | 2025 | 2025 | 2025-02-01 | 28 | 31803 | 25663 | 28800 | 35543 | 29784 | 22143 | 26201 | 30178 | 26487 | 22864 | 27741 | 25188 | 24172 | 23920 | 25655 | 27169 | 24904 | 23453 | 27447 | 27963 | 28401 | 28370 | 30496 | 32035 | 30175 | 26658 | 6.5124 | 6.9396 | 7.0167 | 7.4963 | 7.945 | 6.4394 | 6.7055 | 7.2317 | 7.0738 | 6.437 | 6.9323 | 6.9487 | 6.6959 | 6.6122 | 6.7315 | 6.9668 | 6.7611 | 6.2887 | 6.6451 | 6.9351 | 6.9576 | 6.8926 | 7.1904 | 7.2578 | 7.6876 | 6.9961 | 713213 | 6.9345 |  |  | 695250 | 0 | 695250 | 17963 | 2.519% | 70.2 | 6605.3752 | 754.9158
2025-02-16 | 2025 | 2025 | 2025-02-01 | 28 | 26330 | 12811 | 23317 | 28209 | 32121 | 18587 | 22436 | 21701 | 23784 | 17231 | 20885 | 23459 | 19909 | 21271 | 19724 | 22134 | 21214 | 18247 | 23847 | 22286 | 18745 | 21886 | 25649 | 24455 | 30388 | 24393 | 6.1578 | 6.2498 | 6.28 | 6.5537 | 7.1297 | 5.8312 | 6.1108 | 6.2649 | 6.4126 | 5.9693 | 6.164 | 6.365 | 6.0314 | 6.1328 | 5.9072 | 6.1786 | 6.0807 | 5.6007 | 6.06 | 6.2181 | 5.7915 | 6.039 | 6.4799 | 6.3804 | 6.8242 | 6.3495 | 585019 | 6.214 |  |  | 570600 | 0 | 570600 | 14419 | 2.465% | 70.2 | 3431.3252 | 592.3055
2025-02-17 | 2025 | 2025 | 2025-02-01 | 28 | 22749 | 21562 | 20316 | 24888 | 26173 | 15080 | 20280 | 7333 | 20564 | 16091 | 20148 | 20497 | 18177 | 17546 | 17855 | 19500 | 23519 | 15575 | 26457 | 18083 | 18050 | 19569 | 22584 | 21442 | 25911 | 18190 | 6.0581 | 6.1337 | 5.9949 | 6.3549 | 6.6298 | 5.5478 | 5.9992 | 6.0998 | 6.023 | 5.6033 | 6.0106 | 6.0841 | 5.8227 | 5.7403 | 5.7288 | 5.9376 | 6.279 | 5.3402 | 6.3418 | 5.7702 | 5.8149 | 5.8636 | 6.1415 | 6.1369 | 6.3912 | 5.7553 | 518139 | 5.9847 |  |  | 509400 | 0 | 509400 | 8739 | 1.687% | 70.2 | 13545.125 | 499.5663
2025-02-18 | 2025 | 2025 | 2025-02-01 | 28 | 19107 | 20100 | 14672 | 22964 | 22599 | 17857 | 19904 | 14130 | 18825 | 14725 | 19897 | 18147 | 16654 | 18774 | 20144 | 19232 | 21818 | 17543 | 23835 | 18735 | 18642 | 21717 | 18377 | 22601 | 21195 | 12535 | 6.495 | 6.3164 | 6.0464 | 6.1506 | 6.4296 | 5.8247 | 5.8927 | 5.3972 | 5.9759 | 5.7843 | 6.1068 | 5.8645 | 5.7525 | 6.0004 | 6.0751 | 5.938 | 6.1799 | 5.6113 | 6.1522 | 5.8846 | 5.8403 | 6.0869 | 5.8742 | 6.2528 | 6.2665 | 5.1363 | 494729 | 5.9744 |  |  | 482850 | 0 | 482850 | 11879 | 2.401% | 70.2 | 17764.7493 | 525.654
2025-02-19 | 2025 | 2025 | 2025-02-01 | 28 | 21832 | 19332 | 4969 | 22843 | 21720 | 18165 | 18883 | 20914 | 23331 | 17674 | 23056 | 21929 | 17907 | 20601 | 21661 | 22691 | 24745 | 22759 | 21125 | 23196 | 18827 | 24115 | 22751 | 23648 | 22454 | 21204 | 5.9963 | 6.244 | 6.174 | 6.0754 | 6.5246 | 5.7212 | 5.7015 | 5.8637 | 6.2193 | 6.117 | 6.2126 | 6.1147 | 5.9812 | 6.044 | 6.3027 | 6.1067 | 6.3978 | 5.8599 | 5.693 | 6.19 | 5.8301 | 6.2381 | 6.1775 | 6.351 | 6.5468 | 6.063 | 542332 | 6.1056 |  |  | 525600 | 0 | 525600 | 16732 | 3.085% | 70.2 | 6960.4993 | 547.4195
2025-02-20 | 2025 | 2025 | 2025-02-01 | 28 | 21458 | 20558 | 18863 | 22429 | 24082 | 16112 | 19991 | 15469 | 18457 | 11514 | 19889 | 19054 | 16997 | 17517 | 17795 | 17239 | 19837 | 16093 | 22873 | 17057 | 15770 | 16911 | 19018 | 20246 | 24383 | 14595 | 5.342 | 4.8424 | 5.7435 | 5.9603 | 6.485 | 5.3974 | 5.7009 | 5.2762 | 5.7242 | 5.6448 | 5.8343 | 5.7954 | 5.6422 | 5.6209 | 5.5457 | 5.591 | 5.7234 | 5.2874 | 5.8952 | 5.5563 | 5.3643 | 5.5369 | 5.7514 | 5.8369 | 6.1808 | 5.175 | 484207 | 5.6328 |  |  | 468900 | 0 | 468900 | 15307 | 3.161% | 70.2 | 7338.75 | 258.0211
2025-02-21 | 2025 | 2025 | 2025-02-01 | 28 | 14384 | 10766 | 14015 | 11322 | 13214 | 10648 | 9861 | 12193 | 13775 | 0 | 13166 | 12767 | 9010 | 10494 | 13878 | 11499 | 11133 | 13396 | 10565 | 11613 | 9933 | 11076 | 12947 | 12074 | 13562 | 13924 | 4.2301 | 3.8145 | 5.3214 | 4.9888 | 5.198 | 4.9077 | 4.6416 | 4.9091 | 5.2876 | 6.2103 | 5.3095 | 5.109 | 4.7292 | 4.9631 | 5.2631 | 5.0493 | 4.9362 | 5.0901 | 4.7223 | 5.0344 | 4.7878 | 5.0018 | 5.1418 | 5.106 | 5.1355 | 5.2362 | 301215 | 5.0048 |  |  | 293400 | 0 | 293400 | 7815 | 2.594% | 70.2 | 0 | 326.5451
2025-02-22 | 2025 | 2025 | 2025-02-01 | 28 | 6584 | 5036 | 6900 | 4345 | 5491 | 5267 | 4364 | 5493 | 7115 | 1350 | 5424 | 6336 | 4688 | 4624 | 6273 | 4674 | 5307 | 6675 | 6659 | 5048 | 5196 | 6638 | 6325 | 5329 | 6910 | 5921 | 4.6421 | 4.0472 | 4.2608 | 3.5383 | 4.0288 | 3.991 | 3.6374 | 3.873 | 4.3174 | 4.8451 | 4.1253 | 4.159 | 3.962 | 3.9256 | 4.2119 | 3.8697 | 3.9539 | 4.0858 | 3.9326 | 3.961 | 3.9838 | 4.153 | 4.119 | 3.9293 | 4.2082 | 4.0422 | 143972 | 4.0694 |  |  | 137700 | 0 | 137700 | 6272 | 4.356% | 70.2 | 5897.875 | 143.4413
2025-02-23 | 2025 | 2025 | 2025-02-01 | 28 | 12175 | 7422 | 10727 | 6250 | 9664 | 6424 | 7155 | 9303 | 10897 | 10014 | 9178 | 9723 | 5828 | 7818 | 9192 | 8089 | 5598 | 8079 | 6693 | 7570 | 6057 | 7671 | 9907 | 9565 | 10410 | 10361 | 4.5305 | 4.2724 | 4.4801 | 4.6196 | 4.4304 | 4.1317 | 4.1812 | 4.2578 | 4.5542 | 4.4327 | 4.3592 | 4.4644 | 3.9399 | 4.2802 | 4.3538 | 4.3478 | 3.9869 | 4.0776 | 4.0546 | 4.3236 | 4.1341 | 4.2017 | 4.4142 | 4.4365 | 4.5256 | 4.3905 | 221770 | 4.3147 |  |  | 214200 | 0 | 214200 | 7570 | 3.413% | 70.2 | 5657.2503 | 214.9208
2025-02-24 | 2025 | 2025 | 2025-02-01 | 28 | 10773 | 9917 | 10532 | 0 | 11001 | 13195 | 10138 | 9044 | 11031 | 8687 | 7675 | 9778 | 8607 | 7498 | 9454 | 11107 | 11613 | 7926 | 8720 | 0 | 12138 | 12334 | 9860 | 10219 | 11647 | 9856 | 6.3487 | 6.1411 | 4.6694 | 4.8123 | 4.4588 | 4.6649 | 4.271 | 4.1466 | 4.719 | 4.1956 | 4.2314 | 4.3756 | 4.2387 | 4.1574 | 4.2261 | 4.4614 | 4.6026 | 3.9602 | 4.1981 | 4.7076 | 4.523 | 4.4958 | 4.4184 | 4.3161 | 4.3832 | 4.3684 | 242750 | 4.542 |  |  | 236250 | 450 | 235800 | 6500 | 2.678% | 70.2 | 9114.75 | 284.835
2025-02-25 | 2025 | 2025 | 2025-02-01 | 28 | 22053 | 19374 | 21802 | 5966 | 21735 | 28928 | 22126 | 19995 | 20055 | 20881 | 18349 | 21390 | 19833 | 17318 | 21828 | 25528 | 22503 | 22201 | 19485 | 0 | 28104 | 27410 | 21733 | 24136 | 23899 | 18209 | 4.0981 | 4.0909 | 6.2335 | 6.5483 | 6.4389 | 6.9149 | 6.228 | 6.1089 | 6.1614 | 6.1754 | 6.1735 | 6.3076 | 6.2427 | 5.9032 | 6.2906 | 6.5903 | 6.3457 | 6.0661 | 5.9073 | 7.2912 | 6.8876 | 6.7103 | 6.324 | 6.4453 | 6.5143 | 5.8507 | 534841 | 6.1865 |  |  | 521550 | 0 | 521550 | 13291 | 2.485% | 70.2 | 10597.5 | 622.1805
2025-02-26 | 2025 | 2025 | 2025-02-01 | 28 | 5711 | 4956 | 5842 | 10537 | 6024 | 21402 | 12635 | 4727 | 4149 | 7811 | 5869 | 5896 | 5524 | 4000 | 5158 | 16028 | 17437 | 7215 | 13515 | 2420 | 21192 | 18801 | 5176 | 15933 | 4994 | 4739 | 4.278 | 4.2221 | 4.1477 | 4.5879 | 4.2932 | 5.8204 | 4.8062 | 4.0999 | 3.9109 | 4.5272 | 4.4418 | 4.3795 | 4.2743 | 4.2144 | 4.5284 | 5.3065 | 5.3852 | 5.7314 | 4.9369 | 5.189 | 5.8381 | 5.5397 | 4.2519 | 5.3735 | 4.1326 | 4.0676 | 237691 | 4.7032 |  |  | 228600 | 450 | 228150 | 9091 | 3.825% | 70.2 | 4464.0003 | 389.9289
2025-02-27 | 2025 | 2025 | 2025-02-01 | 28 | 11270 | 10066 | 10929 | 10592 | 9647 | 11351 | 8581 | 9145 | 10363 | 8988 | 10738 | 10994 | 10252 | 10194 | 8755 | 12192 | 13256 | 6431 | 12583 | 10002 | 10406 | 11734 | 10789 | 12341 | 10596 | 7024 | 6.9781 | 6.8319 | 4.402 | 4.1892 | 4.1858 | 4.5201 | 3.9944 | 3.9938 | 4.3865 | 4.122 | 4.5356 | 4.4011 | 4.3333 | 4.3268 | 4.1516 | 4.5137 | 4.5848 | 4.8292 | 4.3747 | 4.2847 | 4.3968 | 4.5389 | 4.3868 | 4.5464 | 4.2631 | 3.7434 | 269219 | 4.5313 |  |  | 260550 | 900 | 259650 | 8669 | 3.22% | 70.2 | 31396.1255 | 300.9913
2025-02-28 | 2025 | 2025 | 2025-02-01 | 28 | 14969 | 14455 | 12878 | 20267 | 15647 | 17855 | 19727 | 11751 | 13155 | 7659 | 13894 | 15583 | 13677 | 13079 | 14109 | 21125 | 23397 | 17582 | 21717 | 20174 | 18359 | 18855 | 14026 | 22028 | 12427 | 9395 | 6.2563 | 6.6172 | 6.7862 | 7.4725 | 7.2321 | 7.094 | 7.3515 | 6.4608 | 6.8322 | 6.9741 | 7.2423 | 7.2248 | 7.0501 | 6.9444 | 6.9218 | 7.6342 | 7.9771 | 6.9758 | 7.5492 | 7.5115 | 7.366 | 7.3561 | 7.0764 | 7.7411 | 7.0846 | 6.0032 | 417790 | 7.1052 |  |  | 407250 | 0 | 407250 | 10540 | 2.523% | 70.2 | 6467.3755 | 573.3497
2025-03-01 | 2025 | 2025 | 2025-03-01 | 31 | 18245 | 22774 | 20814 | 30100 | 24149 | 24175 | 26315 | 15878 | 19487 | 18613 | 21147 | 21103 | 19361 | 18253 | 20791 | 26124 | 11242 | 21496 | 27388 | 24864 | 16750 | 25117 | 20044 | 27404 | 23032 | 14786 | 5.2265 | 5.2873 | 6.3188 | 6.8322 | 6.7819 | 6.409 | 6.5322 | 5.5881 | 6.2285 | 6.0196 | 6.4368 | 6.4253 | 6.3033 | 6.1847 | 6.3058 | 6.5658 | 6.6426 | 6.0011 | 6.544 | 6.4916 | 6.5251 | 6.4399 | 6.3539 | 6.7374 | 7.0503 | 5.3914 | 559452 | 6.2932 |  |  | 544050 | 0 | 544050 | 15402 | 2.753% | 70.2 | 18189.625 | 654.3031
2025-03-02 | 2025 | 2025 | 2025-03-01 | 31 | 13762 | 14998 | 12315 | 17473 | 16035 | 13408 | 13711 | 10104 | 12254 | 11834 | 11032 | 12884 | 10336 | 9964 | 11586 | 17159 | 19724 | 15159 | 17182 | 16221 | 2599 | 16302 | 11877 | 19148 | 12814 | 8937 | 6.0264 | 5.9417 | 5.0485 | 5.6725 | 5.5014 | 5.095 | 5.2706 | 4.7712 | 5.1572 | 4.9878 | 5.0927 | 5.1908 | 4.9062 | 4.9451 | 5.1277 | 5.4257 | 5.6367 | 5.0622 | 5.1779 | 5.3632 | 5.2319 | 5.3835 | 5.2256 | 5.6933 | 5.2113 | 4.6198 | 348818 | 5.2602 |  |  | 339300 | 450 | 338850 | 9518 | 2.729% | 70.2 | 9339.7503 | 468.6562
2025-03-03 | 2025 | 2025 | 2025-03-01 | 31 | 21678 | 21350 | 24476 | 23635 | 21865 | 16487 | 20121 | 14841 | 23199 | 17996 | 23339 | 23511 | 20080 | 21377 | 21814 | 21640 | 22425 | 16925 | 22200 | 19844 | 17194 | 18123 | 23415 | 23186 | 22327 | 11903 | 8.7679 | 8.7515 | 6.2176 | 5.9006 | 6.0292 | 5.3258 | 5.5543 | 5.3914 | 6.2744 | 5.7028 | 6.3985 | 6.0872 | 5.8037 | 5.9062 | 5.8972 | 5.8069 | 5.796 | 5.2409 | 5.6173 | 5.7154 | 5.4231 | 5.3797 | 6.1486 | 6.0456 | 5.9492 | 5.2034 | 534951 | 6.0129 |  |  | 522000 | 450 | 521550 | 12951 | 2.421% | 70.2 | 33516.7502 | 550.83
2025-03-04 | 2025 | 2025 | 2025-03-01 | 31 | 35368 | 35784 | 31923 | 49017 | 42379 | 45247 | 49495 | 32623 | 31495 | 34563 | 30798 | 38869 | 30451 | 28189 | 34731 | 43211 | 44032 | 45328 | 51449 | 47852 | 42374 | 51693 | 38236 | 44414 | 42383 | 34020 | 8.0313 | 8.0059 | 8.2991 | 9.1492 | 9.073 | 8.7192 | 9.2367 | 8.1803 | 8.7573 | 8.7391 | 8.8259 | 8.5694 | 8.5726 | 8.4273 | 8.6645 | 8.9986 | 9.2604 | 9.0797 | 9.3067 | 8.9628 | 8.5757 | 9.3043 | 8.6723 | 9.0089 | 9.0089 | 8.2296 | 1035924 | 8.7561 |  |  | 1001250 | 0 | 1001250 | 34674 | 3.347% | 70.2 | 43417.2507 | 1208.3668
2025-03-05 | 2025 | 2025 | 2025-03-01 | 31 | 33852 | 30269 | 35820 | 35440 | 36170 | 42313 | 35406 | 34931 | 28877 | 16113 | 33668 | 37020 | 34931 | 27807 | 31173 | 37872 | 37439 | 36757 | 42873 | 36854 | 43625 | 46148 | 37745 | 38681 | 32490 | 12058 | 5.5921 | 5.3237 | 7.7896 | 7.9473 | 8.3175 | 8.4354 | 7.9142 | 7.9014 | 8.282 | 8.2921 | 7.687 | 8.0063 | 7.9746 | 7.7275 | 7.7829 | 8.4242 | 9.0008 | 8.2253 | 8.4498 | 8.0047 | 8.7206 | 8.8549 | 8.1565 | 7.8607 | 8.2372 | 8.0828 | 896332 | 7.9612 |  |  | 864450 | 0 | 864450 | 31882 | 3.557% | 70.2 | 5395.2505 | 1131.4809
2025-03-06 | 2025 | 2025 | 2025-03-01 | 31 | 17804 | 15742 | 19731 | 15146 | 17310 | 12594 | 15416 | 13340 | 20490 | 13604 | 18554 | 17835 | 15551 | 15619 | 15563 | 14717 | 13899 | 16326 | 16887 | 15502 | 13644 | 17455 | 6133 | 15452 | 18960 | 16380 | 4.383 | 4.2013 | 5.6616 | 5.1907 | 5.4917 | 5.1341 | 5.287 | 4.9366 | 5.8651 | 5.99 | 5.6554 | 5.6053 | 5.3875 | 5.4421 | 5.3886 | 5.3319 | 5.3156 | 5.3869 | 5.4949 | 5.3624 | 5.2524 | 5.6421 | 5.79 | 5.33 | 5.5785 | 5.7567 | 409654 | 5.3793 |  |  | 398250 | 0 | 398250 | 11404 | 2.784% | 70.2 | 11521.25 | 420.8881
2025-03-07 | 2025 | 2025 | 2025-03-01 | 31 | 7581 | 7834 | 9277 | 9832 | 7101 | 7263 | 6301 | 3969 | 7110 | 7062 | 8127 | 5223 | 6174 | 7324 | 7091 | 8637 | 7009 | 10559 | 6815 | 9807 | 5134 | 8356 | 5031 | 8788 | 7176 | 4656 | 5.3172 | 5.2737 | 4.4403 | 4.3816 | 4.4186 | 4.135 | 3.7283 | 3.6689 | 4.2994 | 4.499 | 4.6016 | 4.0202 | 4.059 | 4.3964 | 4.1225 | 4.3896 | 3.9615 | 4.361 | 3.7496 | 4.5523 | 3.8704 | 4.3002 | 4.0202 | 4.4615 | 4.2386 | 3.9442 | 189237 | 4.2773 |  |  | 182700 | 450 | 182250 | 6537 | 3.454% | 70.2 | 5832.125 | 273.0758
2025-03-08 | 2025 | 2025 | 2025-03-01 | 31 | 15110 | 14725 | 14868 | 10963 | 14860 | 9027 | 7819 | 12991 | 14946 | 8849 | 11665 | 15498 | 12177 | 13731 | 11308 | 10126 | 6161 | 8463 | 11392 | 10048 | 9628 | 5424 | 15627 | 12952 | 16708 | 11825 | 4.6656 | 4.6145 | 5.3338 | 5.0137 | 5.3149 | 4.911 | 4.5424 | 4.9853 | 5.3926 | 4.9182 | 5.1558 | 5.5413 | 5.0694 | 5.2872 | 5.2053 | 5.1336 | 4.6129 | 4.5966 | 4.9658 | 5.0373 | 5.0003 | 4.8474 | 5.4569 | 5.3898 | 5.434 | 4.8514 | 306891 | 5.0491 |  |  | 298800 | 0 | 298800 | 8091 | 2.636% | 70.2 | 383 | 337.2495
2025-03-09 | 2025 | 2025 | 2025-03-01 | 31 | 11545 | 11462 | 10048 | 12064 | 13510 | 9828 | 11570 | 11149 | 10440 | 9332 | 9268 | 11676 | 9320 | 9842 | 10882 | 11511 | 13758 | 8424 | 12665 | 10221 | 9764 | 11664 | 10804 | 11294 | 14447 | 9351 | 4.36 | 4.3438 | 4.4714 | 4.6717 | 4.9435 | 4.5469 | 4.6888 | 4.552 | 4.5612 | 4.4069 | 4.4347 | 4.7524 | 4.3975 | 4.4603 | 4.5162 | 4.6795 | 4.8285 | 4.2165 | 4.6431 | 4.5508 | 4.4844 | 4.7699 | 4.5431 | 4.6732 | 4.9779 | 4.3601 | 285839 | 4.5706 |  |  | 276300 | 450 | 275850 | 9539 | 3.337% | 70.2 | 4387.5 | 236.6893
2025-03-10 | 2025 | 2025 | 2025-03-01 | 31 | 8082 | 7917 | 7682 | 8043 | 7982 | 10219 | 8054 | 8336 | 7857 | 7312 | 5885 | 7552 | 7162 | 6630 | 7983 | 9562 | 9375 | 7631 | 7628 | 8054 | 10157 | 9185 | 8258 | 8997 | 8632 | 7329 | 3.8362 | 4.0037 | 4.1898 | 4.1587 | 4.3548 | 4.6833 | 4.2505 | 4.2657 | 4.2447 | 4.1785 | 3.9704 | 4.3059 | 4.3049 | 4.1824 | 4.3217 | 4.63 | 4.5531 | 4.1229 | 4.217 | 4.3903 | 4.666 | 4.5731 | 4.2196 | 4.5483 | 4.4724 | 4.1664 | 211504 | 4.3004 |  |  | 205200 | 450 | 204750 | 6304 | 2.981% | 70.2 | 1052.25 | 224.9897
2025-03-11 | 2025 | 2025 | 2025-03-01 | 31 | 4927 | 4783 | 4781 | 8045 | 5135 | 15926 | 9344 | 4233 | 3979 | 7058 | 3862 | 4579 | 3426 | 5562 | 4179 | 12794 | 14138 | 11672 | 12609 | 10379 | 16586 | 14549 | 3861 | 13875 | 3575 | 3238 | 5.7931 | 5.3037 | 3.8712 | 4.2131 | 4.0141 | 5.2969 | 4.2989 | 3.759 | 3.8257 | 4.4279 | 3.9857 | 4.335 | 3.8898 | 4.2485 | 4.2547 | 4.9344 | 5.0961 | 4.6049 | 4.8174 | 4.7689 | 5.3235 | 5.1448 | 3.9396 | 5.3674 | 3.7475 | 3.9778 | 207095 | 4.5092 |  |  | 199800 | 450 | 199350 | 7295 | 3.523% | 70.2 | 13898.5 | 300.7239
2025-03-12 | 2025 | 2025 | 2025-03-01 | 31 | 21687 | 16517 | 19492 | 14802 | 17826 | 12475 | 11466 | 16622 | 18937 | 17799 | 19428 | 18994 | 15767 | 17591 | 18750 | 17438 | 14532 | 14501 | 14701 | 16469 | 12119 | 14262 | 19949 | 18318 | 19817 | 19532 | 7.3713 | 7.6583 | 5.5796 | 5.1397 | 5.5131 | 5.1763 | 4.6963 | 5.1605 | 5.5461 | 5.5043 | 5.6546 | 5.6447 | 5.4018 | 5.514 | 5.6085 | 5.539 | 5.199 | 5.1514 | 5.0719 | 5.3922 | 5.1474 | 5.2663 | 5.5948 | 5.6337 | 5.7317 | 5.4747 | 439791 | 5.5527 |  |  | 425700 | 450 | 425250 | 14091 | 3.204% | 70.2 | 11654.1255 | 468.4905
2025-03-13 | 2025 | 2025 | 2025-03-01 | 31 | 31466 | 30686 | 34121 | 29646 | 33763 | 28909 | 28410 | 32775 | 32268 | 29565 | 28840 | 34124 | 30451 | 31265 | 29800 | 30560 | 33775 | 31994 | 29113 | 29867 | 31370 | 30908 | 35138 | 33517 | 36406 | 20862 | 7.0054 | 7.1479 | 7.4073 | 7.4919 | 8.012 | 7.0386 | 7.021 | 7.3039 | 7.3387 | 7.1002 | 7.451 | 7.4542 | 7.2425 | 7.2973 | 7.1156 | 7.3019 | 7.6188 | 7.1588 | 6.9386 | 7.2796 | 7.3724 | 7.2742 | 7.5002 | 7.5884 | 7.6007 | 7.0067 | 809599 | 7.3103 |  |  | 786600 | 0 | 786600 | 22999 | 2.841% | 70.2 | 6896.25 | 877.3552
2025-03-14 | 2025 | 2025 | 2025-03-01 | 31 | 27511 | 30049 | 24971 | 35052 | 36667 | 24653 | 30707 | 25576 | 23156 | 19923 | 25173 | 23406 | 24794 | 21888 | 25752 | 27161 | 31566 | 24244 | 32004 | 25810 | 24390 | 28235 | 26398 | 27020 | 29053 | 22214 | 5.3359 | 5.3948 | 6.6471 | 7.4944 | 7.6739 | 6.7333 | 7.1883 | 6.6456 | 6.6288 | 6.5862 | 6.7012 | 6.5519 | 6.7057 | 6.3694 | 6.7808 | 7.0046 | 7.2963 | 6.5362 | 7.2194 | 6.8915 | 6.719 | 7.0733 | 6.7649 | 7.0305 | 7.3837 | 6.3201 | 697373 | 6.7568 |  |  | 678600 | 0 | 678600 | 18773 | 2.692% | 70.2 | 2078.25 | 738.4746
2025-03-15 | 2025 | 2025 | 2025-03-01 | 31 | 15819 | 16835 | 13477 | 16920 | 19913 | 13270 | 12411 | 15025 | 13669 | 10515 | 12587 | 12568 | 12463 | 12234 | 12326 | 12945 | 15606 | 12443 | 12960 | 13426 | 11758 | 14350 | 14843 | 14402 | 19125 | 13313 | 6.112 | 6.2651 | 5.0477 | 5.4103 | 5.7249 | 5.1567 | 5.0038 | 5.182 | 5.1588 | 4.91 | 4.976 | 5.2469 | 4.978 | 4.9288 | 4.8634 | 5.28 | 5.3688 | 4.9424 | 5.0015 | 5.2096 | 4.9609 | 5.2888 | 5.4442 | 5.2545 | 5.5629 | 5.0539 | 365203 | 5.2435 |  |  | 353700 | 0 | 353700 | 11503 | 3.15% | 70.2 | 5603.3748 | 290.4291
2025-03-16 | 2025 | 2025 | 2025-03-01 | 31 | 22333 | 24483 | 23780 | 17825 | 26358 | 18938 | 19561 | 16333 | 20398 | 20594 | 22682 | 20346 | 18566 | 20380 | 19823 | 19958 | 20869 | 20056 | 18167 | 19397 | 18269 | 20682 | 21209 | 20537 | 24825 | 16401 | 4.8219 | 5.1045 | 6.098 | 6.1801 | 6.5 | 5.7465 | 5.7728 | 5.455 | 5.8319 | 6.0367 | 6.0603 | 5.8912 | 5.7558 | 5.9233 | 6.0713 | 5.8919 | 6.0499 | 5.7247 | 5.7495 | 5.8605 | 5.6558 | 6.2379 | 5.9862 | 6.014 | 6.385 | 5.4587 | 532770 | 5.8563 |  |  | 517050 | 0 | 517050 | 15720 | 2.951% | 70.2 | 1860.5 | 557.7477
2025-03-17 | 2025 | 2025 | 2025-03-01 | 31 | 12299 | 15118 | 13606 | 14072 | 13830 | 15273 | 12407 | 11829 | 11500 | 12807 | 13140 | 14228 | 12731 | 13039 | 13296 | 16059 | 17780 | 15560 | 15448 | 14302 | 13561 | 17864 | 13046 | 15434 | 15860 | 10064 | 5.7413 | 4.9769 | 5.0076 | 4.7881 | 5.2925 | 5.177 | 4.6459 | 4.6488 | 4.7982 | 4.9426 | 4.9874 | 4.9587 | 4.9747 | 4.9278 | 4.9376 | 5.2087 | 5.2615 | 5.0697 | 4.939 | 5.1026 | 5.0124 | 5.4919 | 4.9256 | 5.1889 | 5.1344 | 4.4363 | 364153 | 5.0222 |  |  | 352350 | 0 | 352350 | 11803 | 3.241% | 70.2 | 29505.2503 | 375.6979
2025-03-18 | 2025 | 2025 | 2025-03-01 | 31 | 11581 | 7404 | 9996 | 6436 | 10763 | 5137 | 5727 | 9881 | 11302 | 8572 | 9829 | 7579 | 5320 | 7647 | 9374 | 6046 | 5805 | 6110 | 5600 | 7320 | 3922 | 5137 | 8342 | 7354 | 7069 | 8537 | 5.9437 | 6.5172 | 5.7344 | 4.97 | 5.6137 | 4.4442 | 4.4314 | 5.3706 | 5.804 | 5.1607 | 5.3902 | 5.1439 | 4.6611 | 5.0418 | 5.2918 | 4.582 | 4.4518 | 4.6088 | 4.3727 | 4.8269 | 4.4694 | 4.6261 | 5.3488 | 4.9405 | 5.7612 | 5.4293 | 197790 | 5.1129 |  |  | 191700 | 0 | 191700 | 6090 | 3.079% | 70.2 | 6104 | 460.3979
2025-03-19 | 2025 | 2025 | 2025-03-01 | 31 | 20529 | 25798 | 20488 | 26798 | 25492 | 20322 | 24285 | 16093 | 18475 | 18116 | 20717 | 19392 | 16303 | 19322 | 20735 | 19987 | 24866 | 19830 | 25311 | 19248 | 18484 | 21265 | 19373 | 21619 | 22963 | 14615 | 6.9527 | 7.2797 | 6.0287 | 6.4742 | 6.5562 | 6.0467 | 6.2092 | 5.3761 | 5.8109 | 5.7596 | 6.0535 | 5.8383 | 5.8358 | 5.9019 | 5.9925 | 6.0175 | 6.3503 | 5.8317 | 6.2856 | 5.9181 | 5.8967 | 6.1254 | 5.8638 | 6.1394 | 6.3956 | 5.213 | 540426 | 6.0828 |  |  | 526950 | 0 | 526950 | 13476 | 2.494% | 70.2 | 2125.3747 | 565.4515
2025-03-20 | 2025 | 2025 | 2025-03-01 | 31 | 28842 | 31812 | 30211 | 33906 | 32347 | 26280 | 26011 | 22290 | 27395 | 27205 | 30199 | 28246 | 15578 | 24944 | 30274 | 26842 | 27812 | 26136 | 25048 | 28232 | 27635 | 28380 | 29533 | 32805 | 32926 | 22496 | 5.488 | 6.0082 | 7.0058 | 7.282 | 7.3245 | 6.7004 | 6.5308 | 6.1728 | 6.7826 | 6.7559 | 7.0373 | 6.813 | 7.0856 | 7.2347 | 7.0062 | 6.8314 | 6.7369 | 6.5059 | 6.283 | 6.9252 | 6.7981 | 6.817 | 6.9788 | 7.3102 | 7.1799 | 6.2067 | 723385 | 6.7616 |  |  | 701100 | 0 | 701100 | 22285 | 3.081% | 70.2 | 13473.0013 | 775.2812
2025-03-21 | 2025 | 2025 | 2025-03-01 | 31 | 16872 | 22941 | 14774 | 22708 | 24147 | 20692 | 18670 | 17472 | 15491 | 16590 | 13493 | 16202 | 5239 | 14709 | 16749 | 17638 | 24456 | 12323 | 18782 | 16295 | 22543 | 23352 | 16526 | 19147 | 20391 | 17845 | 4.266 | 4.5974 | 5.1727 | 5.9372 | 6.0818 | 5.9567 | 5.6311 | 5.4021 | 5.2808 | 5.3744 | 5.0622 | 5.3853 | 5.2585 | 5.3741 | 5.4011 | 5.9499 | 6.2327 | 5.6796 | 5.6206 | 5.6194 | 6.0641 | 6.1461 | 5.4233 | 5.7342 | 5.7554 | 5.4976 | 466047 | 5.5348 |  |  | 451350 | 0 | 451350 | 14697 | 3.154% | 70.2 | 3900.625 | 456.1127
2025-03-22 | 2025 | 2025 | 2025-03-01 | 31 | 7080 | 9308 | 6464 | 7798 | 7973 | 7105 | 6871 | 7366 | 6641 | 6614 | 6566 | 7708 | 6534 | 6297 | 7025 | 7657 | 10324 | 5778 | 8168 | 6123 | 6628 | 8798 | 7110 | 7271 | 8918 | 6271 | 4.7056 | 4.3358 | 4.1115 | 5.0966 | 4.8399 | 5.2291 | 4.9828 | 4.2061 | 4.1989 | 4.2273 | 4.1944 | 4.283 | 4.1503 | 4.1383 | 4.2035 | 5.3096 | 5.6887 | 4.8084 | 5.4475 | 4.8988 | 5.2135 | 5.5901 | 4.2591 | 5.068 | 4.4742 | 4.1285 | 190396 | 4.6842 |  |  | 184050 | 0 | 184050 | 6346 | 3.333% | 70.2 | 20267.125 | 242.0137
2025-03-23 | 2025 | 2025 | 2025-03-01 | 31 | 14048 | 9522 | 9537 | 10826 | 12823 | 11588 | 8625 | 13393 | 11432 | 10118 | 10540 | 10498 | 8910 | 8901 | 11714 | 9350 | 11569 | 9878 | 8885 | 11430 | 11015 | 10928 | 11006 | 9892 | 14880 | 12474 | 4.5236 | 4.3826 | 4.3411 | 4.3635 | 4.6465 | 4.654 | 4.1651 | 4.5636 | 4.4548 | 4.3436 | 4.3873 | 4.3424 | 4.2062 | 4.2433 | 4.5214 | 4.3992 | 4.845 | 4.416 | 4.346 | 4.5469 | 4.6206 | 4.8836 | 4.3737 | 4.4618 | 4.7864 | 4.5347 | 283782 | 4.4751 |  |  | 272250 | 0 | 272250 | 11532 | 4.064% | 70.2 | 3696 | 295.4532
2025-03-24 | 2025 | 2025 | 2025-03-01 | 31 | 10679 | 9621 | 11138 | 10143 | 10109 | 8984 | 7936 | 8658 | 12354 | 10452 | 10661 | 10028 | 8193 | 8857 | 10055 | 9670 | 11413 | 10788 | 7576 | 8893 | 8564 | 10522 | 10802 | 9792 | 10321 | 10925 | 6.4 | 6.17 | 4.5022 | 4.4366 | 4.5034 | 4.2563 | 4.1303 | 4.1251 | 4.695 | 4.3598 | 4.4492 | 4.2813 | 4.0408 | 4.2272 | 4.281 | 4.4383 | 4.6325 | 4.338 | 4.5987 | 4.2862 | 4.2531 | 4.5006 | 4.4278 | 4.359 | 4.6384 | 4.429 | 257134 | 4.5292 |  |  | 250200 | 450 | 249750 | 6934 | 2.697% | 70.2 | 10818.1247 | 265.9858
2025-03-25 | 2025 | 2025 | 2025-03-01 | 31 | 26373 | 23233 | 23048 | 23801 | 25482 | 21834 | 19718 | 21092 | 21078 | 23966 | 17114 | 21916 | 19628 | 19985 | 23559 | 23215 | 26429 | 20183 | 14057 | 22632 | 20748 | 25804 | 22890 | 22103 | 25992 | 20476 | 6 | 6.57 | 5.92 | 6.14 | 6.02 | 5.83 | 5.65 | 5.76 | 5.82 | 6.02 | 5.9 | 5.79 | 5.52 | 5.52 | 5.95 | 6.03 | 6.3 | 5.78 | 5.93 | 6.05 | 5.79 | 6.22 | 5.79 | 6.07 | 6.45 | 5.71 | 576356 | 5.9435 |  |  | 555750 | 450 | 555300 | 20606 | 3.575% | 70.2 | 16750 | 624.3964
2025-03-26 | 2025 | 2025 | 2025-03-01 | 31 | 20986 | 21623 | 19727 | 25835 | 26149 | 22552 | 20911 | 20973 | 19811 | 18345 | 18670 | 19885 | 15341 | 19432 | 18941 | 23146 | 26322 | 22348 | 18374 | 22137 | 24043 | 26242 | 21228 | 23119 | 27672 | 19418 | 6.09 | 6.41 | 5.76 | 6.33 | 6.42 | 6.2 | 5.92 | 5.84 | 5.82 | 5.65 | 5.7 | 5.86 | 5.54 | 5.74 | 5.72 | 6.27 | 6.48 | 5.95 | 5.95 | 6.15 | 6.32 | 6.56 | 5.9 | 6.19 | 6.49 | 5.7 | 563230 | 6.0369 |  |  | 546300 | 0 | 546300 | 16930 | 3.006% | 70.2 | 11124.25 | 653.87
2025-03-27 | 2025 | 2025 | 2025-03-01 | 31 | 21044 | 17937 | 18640 | 24121 | 23489 | 21071 | 22056 | 18060 | 19430 | 15621 | 18917 | 16618 | 13834 | 17081 | 18776 | 18058 | 20680 | 19249 | 21753 | 18755 | 15835 | 21725 | 19296 | 18945 | 22925 | 18504 | 6.09 | 6.41 | 5.8 | 6.28 | 6.3 | 6.17 | 6.13 | 5.66 | 5.96 | 5.49 | 5.88 | 5.61 | 5.61 | 5.69 | 5.84 | 5.86 | 6.02 | 5.78 | 6.05 | 5.92 | 5.6 | 6.19 | 5.88 | 5.9 | 6.2 | 5.8 | 502420 | 5.9277 |  |  | 490050 | 0 | 490050 | 12370 | 2.462% | 70.2 | 12731.6248 | 510.8896
2025-03-28 | 2025 | 2025 | 2025-03-01 | 31 | 29528 | 31481 | 28299 | 30172 | 33131 | 24464 | 27153 | 25117 | 27072 | 29423 | 28839 | 28162 | 15301 | 23692 | 30594 | 28481 | 24157 | 28316 | 25523 | 26988 | 23346 | 29137 | 27013 | 30707 | 34138 | 26648 | 7.03 | 7.06 | 6.74 | 7.12 | 7.4 | 6.61 | 6.83 | 6.42 | 6.8 | 7.02 | 6.9 | 6.85 | 6.26 | 6.82 | 7.12 | 6.95 | 6.5 | 6.75 | 6.55 | 6.81 | 6.54 | 7.06 | 6.77 | 7.14 | 7.41 | 6.63 | 716882 | 6.8496 |  |  | 695700 | 0 | 695700 | 21182 | 2.955% | 70.2 | 16784.5013 | 717.7885
2025-03-29 | 2025 | 2025 | 2025-03-01 | 31 | 35421 | 34841 | 35623 | 29136 | 31321 | 28804 | 27095 | 30989 | 35332 | 31185 | 33050 | 33133 | 20694 | 19735 | 33471 | 31121 | 21884 | 33133 | 29914 | 31123 | 29026 | 32797 | 33300 | 28578 | 35313 | 35647 | 7.41 | 7.32 | 7.37 | 6.86 | 7.25 | 6.86 | 6.69 | 6.86 | 7.44 | 7.33 | 7.15 | 7.16 | 6.95 | 7 | 7.29 | 7.15 | 7.16 | 7.14 | 6.93 | 7.09 | 6.97 | 7.35 | 7.25 | 6.95 | 7.37 | 7.34 | 801666 | 7.14 |  |  | 771750 | 0 | 771750 | 29916 | 3.732% | 70.2 | 10730.7503 | 843.5335
2025-03-30 | 2025 | 2025 | 2025-03-01 | 31 | 27637 | 20373 | 26510 | 19936 | 22120 | 15645 | 16384 | 20002 | 27251 | 25559 | 24523 | 24046 | 12208 | 21400 | 24316 | 18394 | 15794 | 22717 | 15830 | 20448 | 14824 | 17472 | 25808 | 23294 | 24269 | 25351 | 6.601 | 5.7503 | 6.2931 | 5.8126 | 6.0321 | 5.3652 | 5.4792 | 5.5716 | 6.4743 | 6.3618 | 6.1913 | 6.2074 | 5.5847 | 6.0429 | 6.276 | 5.7388 | 5.3019 | 5.9562 | 5.3215 | 5.9623 | 5.3554 | 5.6883 | 6.3964 | 6.2215 | 6.2854 | 6.2647 | 552111 | 5.9437 |  |  | 535500 | 0 | 535500 | 16611 | 3.009% | 70.2 | 10615.75 | 562.5916
2025-03-31 | 2025 | 2025 | 2025-03-01 | 31 | 30792 | 23793 | 27249 | 21898 | 29803 | 22412 | 21150 | 28036 | 28127 | 27563 | 26632 | 27244 | 16465 | 23397 | 27726 | 24373 | 27055 | 25496 | 21578 | 25148 | 21585 | 26561 | 26851 | 26200 | 31615 | 28973 | 6.9635 | 6.1958 | 6.6373 | 6.4454 | 6.9128 | 6.2582 | 6.1592 | 6.5843 | 6.7456 | 6.7134 | 6.5781 | 6.543 | 5.6847 | 6.3172 | 6.7261 | 6.4801 | 6.5285 | 6.3689 | 6.1203 | 6.5566 | 6.2088 | 6.6996 | 6.6097 | 6.571 | 7.0082 | 6.7217 | 667722 | 6.513 |  |  | 646650 | 0 | 646650 | 21072 | 3.156% | 70.2 | 6658.3755 | 675.4049
2025-04-01 | 2026 | 2025 | 2025-04-01 | 30 | 24859 | 17522 | 22210 | 18174 | 24626 | 19200 | 16286 | 23133 | 22108 | 18242 | 21579 | 21528 | 16565 | 18906 | 23343 | 20048 | 25148 | 21049 | 16398 | 20464 | 19206 | 22090 | 22657 | 20113 | 25900 | 22764 | 6.4825 | 5.6122 | 6.1156 | 5.7692 | 6.3621 | 5.8644 | 5.5517 | 6.1421 | 6.3004 | 6.3972 | 6.1521 | 6.0389 | 5.5855 | 5.8669 | 6.2559 | 5.8794 | 6.1135 | 5.7826 | 5.4744 | 6.0081 | 5.9768 | 6.161 | 6.234 | 5.9271 | 6.4681 | 6.1781 | 544118 | 6.0269 |  |  | 525600 | 0 | 525600 | 18518 | 3.403% | 70.2 | 6090.625 | 664.4211
2025-04-02 | 2026 | 2025 | 2025-04-01 | 30 | 15390 | 9289 | 11294 | 9155 | 12752 | 10737 | 7398 | 13309 | 13339 | 9359 | 12012 | 11497 | 9164 | 11079 | 13298 | 8978 | 9302 | 10617 | 6666 | 10349 | 9694 | 9405 | 14168 | 10062 | 14691 | 12678 | 4.9065 | 4.2376 | 4.4292 | 4.1886 | 4.667 | 4.4215 | 4.084 | 4.5752 | 4.6524 | 4.4831 | 4.5495 | 4.4724 | 4.2004 | 4.4585 | 4.6362 | 4.3228 | 4.1913 | 4.3113 | 3.8907 | 4.4137 | 4.3231 | 4.4098 | 4.6672 | 4.351 | 4.9297 | 4.6202 | 285682 | 4.4382 |  |  | 275850 | 0 | 275850 | 9832 | 3.442% | 70.2 | 19037.625 | 294.6404
2025-04-03 | 2026 | 2025 | 2025-04-01 | 30 | 13383 | 13133 | 15729 | 11906 | 13760 | 12347 | 9696 | 13829 | 15125 | 15768 | 15119 | 14465 | 12202 | 13740 | 16142 | 12680 | 14651 | 15873 | 10731 | 14473 | 11665 | 13581 | 15118 | 13382 | 15074 | 13667 | 5.0588 | 4.738 | 4.9967 | 4.5332 | 4.8687 | 4.7207 | 4.2519 | 4.7908 | 4.9429 | 5.1479 | 4.9331 | 4.9058 | 4.6674 | 4.8718 | 5.1028 | 5.1621 | 4.8495 | 4.9916 | 4.2991 | 4.9842 | 4.6978 | 4.9978 | 4.8995 | 4.8812 | 5.0099 | 4.7497 | 357239 | 4.8482 |  |  | 346050 | 450 | 345600 | 11189 | 3.132% | 70.2 | 9135.9995 | 371.21
2025-04-04 | 2026 | 2025 | 2025-04-01 | 30 | 9606 | 13454 | 10576 | 13874 | 12870 | 10850 | 10070 | 5950 | 9655 | 9291 | 10519 | 9596 | 9913 | 9746 | 11533 | 10880 | 10328 | 9755 | 9910 | 10901 | 10715 | 11247 | 9751 | 9056 | 12074 | 7143 | 4.1075 | 4.4046 | 4.1697 | 4.5422 | 4.4671 | 4.5188 | 4.2656 | 3.5978 | 4.0915 | 4.2002 | 4.2415 | 4.2454 | 4.2494 | 4.1896 | 4.4556 | 4.5644 | 4.4336 | 4.2047 | 4.2848 | 4.4192 | 4.5513 | 4.681 | 4.1092 | 4.5283 | 4.2424 | 3.6447 | 269263 | 4.285 |  |  | 257400 | 450 | 256950 | 11863 | 4.406% | 70.2 | 11281.3755 | 281.07
2025-04-05 | 2026 | 2025 | 2025-04-01 | 30 | 10770 | 12690 | 8782 | 9733 | 12146 | 6432 | 7205 | 8811 | 10832 | 8037 | 9830 | 9113 | 7542 | 7556 | 8812 | 7842 | 7381 | 8147 | 5738 | 7721 | 6752 | 7069 | 10055 | 3479 | 12113 | 8683 | 4.5263 | 4.7994 | 4.7471 | 4.4608 | 4.8083 | 4.1983 | 4.1056 | 4.2779 | 4.6022 | 4.2916 | 4.4274 | 4.355 | 4.1561 | 4.1406 | 4.387 | 4.3794 | 4.1644 | 4.1692 | 3.7783 | 4.2717 | 4.2272 | 4.3283 | 4.4027 | 4.5231 | 4.7242 | 4.2093 | 223271 | 4.3639 |  |  | 214200 | 0 | 214200 | 9071 | 4.063% | 70.2 | 8341.2508 | 230.95
2025-04-06 | 2026 | 2025 | 2025-04-01 | 30 | 21007 | 29659 | 17733 | 28588 | 27930 | 24449 | 27191 | 18202 | 19159 | 21773 | 21595 | 20692 | 20944 | 20710 | 24021 | 24525 | 36389 | 23303 | 30908 | 21945 | 23865 | 29600 | 21012 | 24582 | 25647 | 14855 | 6.2017 | 6.8914 | 6.069 | 6.902 | 6.8794 | 6.5856 | 6.8617 | 5.6899 | 5.9826 | 6.2822 | 6.2399 | 6.1249 | 6.2119 | 6.1106 | 6.4949 | 6.5378 | 7.2668 | 6.3951 | 6.8189 | 6.5508 | 6.631 | 7.1519 | 6.1025 | 6.6 | 6.4892 | 5.3312 | 620284 | 6.4386 |  |  | 603000 | 0 | 603000 | 17284 | 2.786% | 70.2 |  | 667.03
2025-04-07 | 2026 | 2025 | 2025-04-01 | 30 | 31048 | 39935 | 29201 | 37264 | 38160 | 33948 | 36306 | 29713 | 26172 | 29496 | 28893 | 29862 | 17926 | 24680 | 30580 | 35026 | 42573 | 32649 | 33248 | 28989 | 35533 | 38083 | 29493 | 35825 | 32714 | 27406 | 6.8494 | 7.6928 | 6.7251 | 7.6072 | 7.6881 | 7.1946 | 7.4768 | 6.8182 | 6.7778 | 6.8461 | 6.8254 | 6.8973 | 6.783 | 6.9575 | 6.9858 | 7.4788 | 8.0268 | 6.9819 | 7.2324 | 7.2163 | 7.415 | 7.7592 | 6.8959 | 7.4988 | 7.4038 | 6.501 | 834723 | 7.1744 |  |  | 802800 | 0 | 802800 | 31923 | 3.824% | 70.2 |  | 890.54
2025-04-08 | 2026 | 2025 | 2025-04-01 | 30 | 32931 | 38913 | 30523 | 36527 | 29686 | 31629 | 31884 | 24450 | 23145 | 29213 | 27130 | 32730 | 23942 | 30642 | 33320 | 35024 | 41845 | 29300 | 35384 | 32867 | 32199 | 35456 | 31686 | 34444 | 34312 | 23956 | 7.0247 | 7.503 | 6.8145 | 7.5483 | 7.3112 | 6.937 | 6.9896 | 6.4571 | 7.0619 | 6.8082 | 6.961 | 7.0233 | 6.8967 | 6.8707 | 7.1692 | 7.4628 | 7.7799 | 6.6718 | 7.265 | 7.1443 | 7.1197 | 7.4435 | 7.0236 | 7.2678 | 7.3632 | 6.1385 | 823138 | 7.0791 |  |  | 793800 | 450 | 793350 | 29338 | 3.564% | 70.2 |  | 885.16
2025-04-09 | 2026 | 2025 | 2025-04-01 | 30 | 28683 | 35985 | 29958 | 32935 | 31490 | 28574 | 28440 | 26245 | 28445 | 26608 | 27370 | 29182 | 27038 | 28542 | 28611 | 31225 | 36940 | 29330 | 28437 | 30708 | 28985 | 31056 | 23479 | 32143 | 32309 | 23560 | 7.0392 | 7.6205 | 7.0383 | 7.3772 | 7.6401 | 7.0162 | 6.9249 | 6.6476 | 7.0435 | 6.8212 | 6.9276 | 6.976 | 6.8413 | 6.9871 | 7.0288 | 7.2906 | 7.5616 | 6.9319 | 6.7922 | 7.2261 | 7.124 | 7.2808 | 7.122 | 7.2891 | 7.4078 | 6.3833 | 766278 | 7.09 |  |  | 742500 | 0 | 742500 | 23778 | 3.103% | 70.2 |  | 808
2025-04-10 | 2026 | 2025 | 2025-04-01 | 30 | 37826 | 45183 | 36893 | 42701 | 41567 | 37890 | 42698 | 28587 | 35022 | 35686 | 35407 | 38699 | 34054 | 36725 | 33831 | 40822 | 53780 | 33218 | 46375 | 40773 | 39808 | 44573 | 30874 | 41245 | 41410 | 30495 | 7.9917 | 8.5594 | 7.8494 | 8.5016 | 8.3636 | 8.1974 | 8.6051 | 7.6975 | 7.7553 | 7.8515 | 7.9753 | 8.1052 | 7.7774 | 7.8892 | 8.1558 | 8.6735 | 9.3265 | 7.866 | 9.091 | 8.3635 | 8.351 | 8.7169 | 8.1003 | 8.3699 | 8.2224 | 7.1974 | 1006142 | 8.2136 |  |  | 974700 | 0 | 974700 | 31442 | 3.125% | 70.2 |  | 1103.33
2025-04-11 | 2026 | 2025 | 2025-04-01 | 30 | 41447 | 49347 | 40931 | 44979 | 46056 | 39764 | 38038 | 39635 | 41407 | 40631 | 37304 | 42973 | 36918 | 3872 | 40666 | 40181 | 44076 | 39510 | 42576 | 40190 | 40132 | 39622 | 41157 | 40939 | 47491 | 41874 | 8.3565 | 8.9344 | 8.22 | 8.6743 | 8.8362 | 8.1364 | 8.0317 | 8.2211 | 8.3112 | 8.1988 | 8.1662 | 8.3397 | 7.9668 | 2.4363 | 8.2474 | 8.3751 | 8.3534 | 8.1015 | 8.3621 | 8.2547 | 8.284 | 8.1916 | 8.3781 | 8.2961 | 8.786 | 8.3384 | 1041716 | 8.1076 |  |  | 1004400 | 0 | 1004400 | 37316 | 3.582% | 70.2 |  | 1083.02
2025-04-12 | 2026 | 2025 | 2025-04-01 | 30 | 7035 | 8948 | 7003 | 6732 | 9236 | 6096 | 5753 | 7293 | 7028 | 7345 | 6323 | 7785 | 6299 | 2021 | 7154 | 5854 | 5199 | 5776 | 6293 | 5916 | 6933 | 5641 | 6923 | 7181 | 8783 | 7236 | 5.18 | 5.4 | 5.08 | 4.97 | 5.52 | 4.93 | 4.75 | 5.13 | 5.5 | 5.11 | 5.08 | 5.22 | 4.93 | 3.35 | 5.1 | 4.7 | 4.65 | 4.7 | 4.81 | 4.86 | 5.06 | 4.74 | 5.15 | 5.05 | 5.52 | 5.07 | 173786 | 4.9831 |  |  | 164700 | 0 | 164700 | 9086 | 5.228% | 70.2 |  | 176.01
2025-04-13 | 2026 | 2025 | 2025-04-01 | 30 | 26489 | 28616 | 25705 | 25328 | 26101 | 23521 | 22036 | 10825 | 24188 | 25909 | 23698 | 25190 | 10703 | 23384 | 20653 | 24367 | 23858 | 22828 | 21328 | 24441 | 23356 | 23878 | 25584 | 24224 | 26202 | 25025 | 7.856 | 8.2075 | 7.5842 | 7.5783 | 8.1324 | 7.4854 | 7.1724 | 7.7008 | 7.5091 | 7.9007 | 7.585 | 7.5129 | 7.3763 | 7.4539 | 8.1924 | 7.5736 | 7.3922 | 7.5674 | 6.9816 | 7.5216 | 7.6607 | 7.5939 | 7.603 | 7.8746 | 8.1602 | 7.4845 | 607437 | 7.6408 |  |  | 589950 | 0 | 589950 | 17487 | 2.879% | 70.2 |  | 682.2
2025-04-14 | 2026 | 2025 | 2025-04-01 | 30 | 49494 | 54587 | 26547 | 55152 | 54526 | 43979 | 52855 | 45219 | 45058 | 42261 | 46926 | 44309 | 32069 | 41611 | 35797 | 46276 | 48303 | 42517 | 48676 | 47867 | 43699 | 49144 | 47758 | 48527 | 34863 | 46555 | 9.1019 | 9.6511 | 8.1617 | 9.6955 | 9.7078 | 8.5597 | 9.5655 | 8.9413 | 8.6056 | 8.3949 | 8.8494 | 8.6869 | 8.6396 | 8.4447 | 8.5943 | 8.9833 | 9.5735 | 8.3386 | 9.2369 | 8.9903 | 8.6319 | 9.0699 | 8.865 | 9.1472 | 9.5473 | 8.7862 | 1174575 | 8.9527 |  |  | 1131750 | 0 | 1131750 | 42825 | 3.646% | 70.2 |  | 1310.71
2025-04-15 | 2026 | 2025 | 2025-04-01 | 30 | 46514 | 48545 | 39223 | 47687 | 30448 | 45430 | 44148 | 45573 | 29654 | 39470 | 43359 | 40662 | 40685 | 41368 | 44736 | 36838 | 21163 | 45796 | 44525 | 47068 | 46010 | 50084 | 45181 | 45308 | 43881 | 45361 | 8.6085 | 9.1474 | 7.9455 | 9.1071 | 9.1824 | 8.5749 | 8.7967 | 8.525 | 8.4452 | 8.139 | 8.3094 | 8.1183 | 8.1345 | 8.2362 | 8.4833 | 9.1687 | 9.5176 | 8.4606 | 8.8022 | 8.8149 | 8.7622 | 9.1504 | 8.467 | 8.7845 | 8.7822 | 8.4726 | 1098717 | 8.6514 |  |  | 1060200 | 0 | 1060200 | 38517 | 3.506% | 70.2 |  | 1204.55
2025-04-16 | 2026 | 2025 | 2025-04-01 | 30 | 39687 | 43551 | 33252 | 42754 | 39116 | 41952 | 38923 | 32217 | 37241 | 34029 | 37090 | 34156 | 33570 | 30710 | 38531 | 37845 | 5990 | 33986 | 39068 | 39760 | 41205 | 46060 | 38562 | 36943 | 33701 | 37850 | 7.8429 | 8.2335 | 7.3058 | 8.2092 | 8.2521 | 8.1929 | 7.9235 | 7.8645 | 7.6393 | 7.3693 | 7.6581 | 7.4222 | 7.397 | 7.5144 | 7.7897 | 8.0989 | 8.6369 | 8.0579 | 7.9156 | 8.0108 | 8.152 | 8.6213 | 7.7801 | 7.8828 | 8.0145 | 7.6638 | 947749 | 7.9019 |  |  | 913950 | 0 | 913950 | 33799 | 3.566% | 70.2 |  | 1042.18
2025-04-17 | 2026 | 2025 | 2025-04-01 | 30 | 36843 | 37275 | 31117 | 40506 | 38564 | 34183 | 36587 | 34160 | 34958 | 25644 | 32786 | 27764 | 29488 | 29808 | 32423 | 30737 | 34358 | 33701 | 35632 | 33211 | 29664 | 37507 | 35381 | 32115 | 35469 | 36110 | 7.4667 | 7.8992 | 6.8693 | 7.7908 | 7.9419 | 7.1637 | 7.5519 | 7.2331 | 7.2426 | 6.3555 | 7.1822 | 7.0022 | 6.773 | 6.823 | 6.9757 | 7.0449 | 7.1734 | 7.0146 | 7.2396 | 7.1526 | 6.9462 | 7.5787 | 7.268 | 7.1542 | 7.6756 | 7.2931 | 875991 | 7.2235 |  |  | 845100 | 450 | 844650 | 30891 | 3.526% | 70.2 |  | 924.98
2025-04-18 | 2026 | 2025 | 2025-04-01 | 30 | 34294 | 34912 | 27346 | 45131 | 34316 | 28245 | 45438 | 32009 | 31138 | 26881 | 28371 | 30866 | 28163 | 29384 | 31417 | 34039 | 42599 | 31599 | 40021 | 34801 | 31662 | 36369 | 32033 | 31520 | 28659 | 32826 | 7.6378 | 8.3981 | 6.8683 | 8.6183 | 8.4025 | 7.2827 | 8.6867 | 7.3904 | 7.2176 | 7.0017 | 7.224 | 7.2451 | 7.0875 | 7.1581 | 7.338 | 7.7958 | 8.4907 | 7.244 | 8.1028 | 7.7815 | 7.5028 | 7.9106 | 7.3529 | 7.8792 | 8.1399 | 7.4213 | 864039 | 7.6607 |  |  | 836550 | 0 | 836550 | 27489 | 3.181% | 70.2 |  | 946.76
2025-04-19 | 2026 | 2025 | 2025-04-01 | 30 | 39027 | 53626 | 42200 | 51178 | 48525 | 46454 | 45064 | 39407 | 45465 | 44515 | 45528 | 44692 | 38827 | 42355 | 46436 | 44394 | 46112 | 32014 | 49651 | 46167 | 45633 | 46701 | 45695 | 45796 | 37623 | 45701 | 8.9352 | 9.3668 | 8.5899 | 9.2626 | 9.2918 | 8.9084 | 8.7253 | 8.4041 | 8.7478 | 8.714 | 8.8479 | 8.7184 | 8.2669 | 8.6298 | 8.8724 | 9.0203 | 8.9456 | 9.3124 | 9.1511 | 9.0035 | 8.9362 | 9.0537 | 8.8845 | 8.909 | 9.2601 | 8.7714 | 1158786 | 8.905 |  |  | 1118700 | 0 | 1118700 | 40086 | 3.459% | 70.2 |  | 1285.97
2025-04-20 | 2026 | 2025 | 2025-04-01 | 30 | 24919 | 30555 | 22769 | 30756 | 30469 | 30187 | 26515 | 23102 | 24698 | 25632 | 27364 | 27081 | 22181 | 25432 | 28875 | 27432 | 31607 | 26006 | 30730 | 28383 | 29926 | 28894 | 26129 | 26522 | 30437 | 22337 | 6.8326 | 7.0727 | 6.3584 | 7.1445 | 7.1428 | 7.1265 | 6.7781 | 6.4126 | 6.6051 | 6.5861 | 6.8372 | 6.7898 | 6.4397 | 6.6312 | 6.938 | 7.0153 | 7.2006 | 7.0682 | 7.0188 | 7.0672 | 7.1596 | 7.1419 | 6.7 | 6.8062 | 7.0358 | 6.3572 | 708938 | 6.8564 |  |  | 687150 | 0 | 687150 | 21788 | 3.073% | 70.2 |  | 742.63
2025-04-21 | 2026 | 2025 | 2025-04-01 | 30 | 9337 | 9782 | 9730 | 15664 | 12194 | 11266 | 14994 | 7248 | 11238 | 8551 | 6599 | 9575 | 9644 | 9107 | 9913 | 9599 | 13528 | 11087 | 12704 | 11274 | 9310 | 12120 | 11189 | 11760 | 11595 | 7446 | 5.6226 | 5.7542 | 4.5597 | 5.223 | 6.1471 | 4.8551 | 5.1047 | 5.0916 | 4.8307 | 4.3585 | 4.728 | 4.6615 | 4.5959 | 4.5663 | 4.6028 | 5.0522 | 4.9259 | 4.664 | 4.8502 | 4.854 | 4.4858 | 4.9748 | 4.8434 | 4.9052 | 6.0382 | 5.0628 | 276454 | 4.9753 |  |  | 267300 | 0 | 267300 | 9154 | 3.311% | 70.2 |  | 287.24
2025-04-22 | 2026 | 2025 | 2025-04-01 | 30 | 13330 | 17425 | 13108 | 17013 | 17905 | 10599 | 11872 | 11512 | 13364 | 12763 | 1075 | 12585 | 11275 | 13494 | 14815 | 13908 | 17560 | 12546 | 13070 | 12585 | 9979 | 12902 | 13128 | 14134 | 17975 | 12251 | 5.3521 | 5.482 | 5.0576 | 5.8486 | 5.606 | 4.8199 | 5.1763 | 4.8684 | 5.1595 | 5.1081 | 5.3994 | 5.0492 | 4.9238 | 5.1632 | 5.3535 | 5.3234 | 5.5098 | 4.9449 | 5.2193 | 5.1948 | 4.7258 | 5.2073 | 5.1302 | 5.2645 | 5.6369 | 4.9868 | 342173 | 5.212 |  |  | 332100 | 0 | 332100 | 10073 | 2.944% | 70.2 |  | 353.11
2025-04-23 | 2026 | 2025 | 2025-04-01 | 30 | 16960 | 21906 | 18529 | 21315 | 22924 | 18174 | 18316 | 12455 | 18013 | 16676 | 10518 | 18749 | 17915 | 18765 | 20642 | 20193 | 25074 | 14474 | 20286 | 18572 | 16989 | 19787 | 19115 | 20098 | 20542 | 13113 | 5.4665 | 5.7306 | 5.6083 | 5.7503 | 5.9513 | 5.6327 | 5.451 | 4.8827 | 5.6152 | 5.4492 | 6.0308 | 5.7333 | 5.636 | 5.7173 | 5.8375 | 5.8208 | 6.1108 | 5.5224 | 5.4928 | 5.7317 | 5.6434 | 5.8226 | 5.7935 | 5.8375 | 5.6966 | 4.9992 | 480100 | 5.6525 |  |  | 464400 | 0 | 464400 | 15700 | 3.27% | 70.2 |  | 502.87
2025-04-24 | 2026 | 2025 | 2025-04-01 | 30 | 19242 | 25780 | 15669 | 26930 | 25923 | 18405 | 22688 | 18517 | 17720 | 14637 | 16559 | 17908 | 15286 | 15295 | 16927 | 20003 | 22418 | 15157 | 19991 | 18458 | 18477 | 20201 | 18383 | 19838 | 23888 | 18406 | 5.8056 | 6.2622 | 5.4297 | 6.5066 | 6.3699 | 5.7963 | 6.2158 | 5.7027 | 5.6888 | 5.3344 | 5.6219 | 5.7266 | 5.4587 | 5.4043 | 5.5901 | 5.9983 | 6.4049 | 5.7536 | 5.7161 | 5.8346 | 5.8631 | 5.9811 | 5.7443 | 5.9727 | 6.1442 | 5.7595 | 502706 | 5.8495 |  |  | 488700 | 0 | 488700 | 14006 | 2.786% | 70.2 |  | 510
2025-04-25 | 2026 | 2025 | 2025-04-01 | 30 | 25182 | 30384 | 18648 | 19463 | 24911 | 24475 | 25522 | 21799 | 23355 | 18318 | 20809 | 19079 | 18888 | 19630 | 22699 | 24574 | 27533 | 17366 | 29263 | 19709 | 19854 | 23524 | 20988 | 22510 | 29620 | 24404 | 6.2807 | 6.6538 | 5.8174 | 6.6103 | 6.582 | 6.2724 | 6.3305 | 5.958 | 6.1063 | 5.5885 | 5.9245 | 5.8795 | 5.7399 | 5.8198 | 6.0397 | 6.3219 | 6.4678 | 6.192 | 6.6163 | 6.3278 | 5.8689 | 6.2653 | 5.9163 | 6.128 | 6.591 | 6.1946 | 592507 | 6.1728 |  |  | 573300 | 0 | 573300 | 19207 | 3.242% | 70.2 |  | 628.86
2025-04-26 | 2026 | 2025 | 2025-04-01 | 30 | 23625 | 30087 | 18188 | 32299 | 21016 | 25979 | 32148 | 22049 | 21341 | 18454 | 20631 | 21342 | 18941 | 19393 | 21293 | 26007 | 30680 | 22536 | 26408 | 20947 | 22561 | 28932 | 21099 | 23190 | 21022 | 23193 | 6.1048 | 6.669 | 5.5809 | 7.0202 | 6.7057 | 6.3908 | 7.0044 | 5.8494 | 5.8084 | 5.7265 | 5.8411 | 5.8868 | 5.6961 | 5.6831 | 5.881 | 6.3784 | 6.8857 | 6.0894 | 6.6792 | 6.0615 | 6.1051 | 6.7019 | 5.8595 | 6.1435 | 6.7365 | 6.0563 | 613361 | 6.2133 |  |  | 591750 | 0 | 591750 | 21611 | 3.523% | 70.2 |  | 645.69
2025-04-27 | 2026 | 2025 | 2025-04-01 | 30 | 21657 | 27721 | 15919 | 25863 | 25391 | 21983 | 23298 | 18429 | 17843 | 16452 | 18496 | 19386 | 18292 | 17831 | 19004 | 20954 | 22543 | 21921 | 7065 | 20943 | 17092 | 24160 | 18865 | 20722 | 24769 | 19397 | 5.7472 | 6.1592 | 5.1197 | 6.0952 | 6.1183 | 5.8899 | 5.8613 | 5.3438 | 5.3546 | 5.3179 | 5.4117 | 5.4963 | 5.4688 | 5.3865 | 5.5786 | 5.65 | 5.8974 | 5.7474 | 5.9916 | 5.6647 | 5.384 | 6.1233 | 5.4083 | 5.6394 | 5.9617 | 5.5513 | 525996 | 5.668 |  |  | 507150 | 450 | 506700 | 18846 | 3.583% | 70.2 |  | 546.95
2025-04-28 | 2026 | 2025 | 2025-04-01 | 30 | 25969 | 33725 | 20195 | 35034 | 28941 | 18752 | 34349 | 25046 | 23663 | 17565 | 22680 | 16866 | 21105 | 20172 | 22472 | 26758 | 30758 | 24323 | 33584 | 24463 | 21721 | 28665 | 23637 | 25311 | 30829 | 22931 | 6.5059 | 7.224 | 5.9941 | 7.3876 | 7.4201 | 6.5767 | 7.4235 | 6.456 | 6.2309 | 5.8614 | 6.3037 | 6.2457 | 6.1618 | 6.1025 | 6.2819 | 6.7829 | 7.3135 | 6.2673 | 7.0572 | 6.4876 | 6.3334 | 6.8923 | 6.3927 | 6.669 | 7.1106 | 6.3776 | 659514 | 6.61 |  |  | 638550 | 0 | 638550 | 20964 | 3.179% | 70.2 |  | 695.35
2025-04-29 | 2026 | 2025 | 2025-04-01 | 30 | 39002 | 46987 | 27484 | 47661 | 37871 | 30203 | 47322 | 39218 | 40871 | 33673 | 38381 | 36596 | 34720 | 36243 | 40415 | 41729 | 48820 | 43095 | 45273 | 41925 | 35807 | 41434 | 38719 | 40826 | 27193 | 40476 | 8.2575 | 8.9462 | 7.7198 | 9.1399 | 9.0706 | 8.4182 | 9.3492 | 8.2625 | 8.19 | 7.5788 | 8.0101 | 8.0178 | 7.8329 | 7.8897 | 8.2664 | 8.5734 | 9.0421 | 8.2504 | 8.9583 | 8.3748 | 7.9308 | 8.5792 | 8.1809 | 8.3817 | 8.7624 | 8.3298 | 1021944 | 8.3967 |  |  | 988650 | 0 | 988650 | 33294 | 3.258% | 70.2 |  | 1133.84
2025-04-30 | 2026 | 2025 | 2025-04-01 | 30 | 30766 | 46976 | 35656 | 44874 | 37428 | 40195 | 43595 | 31504 | 39102 | 33815 | 39981 | 32408 | 36204 | 35100 | 39028 | 40390 | 47298 | 40243 | 41700 | 39680 | 34897 | 40527 | 40076 | 39729 | 39918 | 38333 | 8.194 | 8.65 | 7.6236 | 8.8325 | 8.841 | 8.0705 | 8.6465 | 8.0776 | 8.0356 | 7.6161 | 8.0497 | 7.8434 | 7.8399 | 7.7305 | 8.0103 | 8.2765 | 8.6799 | 7.9736 | 8.4427 | 8.1253 | 7.8634 | 8.3185 | 8.1649 | 8.2602 | 8.5589 | 7.9543 | 1009423 | 8.18 |  |  | 975600 | 0 | 975600 | 33823 | 3.351% | 70.2 |  | 1088.32
2025-05-01 | 2026 | 2025 | 2025-05-01 | 31 | 44015 | 49670 | 35787 | 49041 | 47609 | 46547 | 45834 | 40949 | 42067 | 34234 | 40516 | 37980 | 36887 | 38537 | 42682 | 45078 | 48276 | 46077 | 47537 | 43931 | 38412 | 47524 | 41723 | 41385 | 45723 | 44674 | 8.4306 | 8.8271 | 7.7422 | 9.0086 | 8.9183 | 8.6306 | 8.9895 | 8.3082 | 8.2972 | 7.6025 | 8.0794 | 8.0581 | 7.9119 | 7.9996 | 8.2834 | 8.7056 | 8.7574 | 8.5746 | 9.1475 | 8.5126 | 8.146 | 8.9812 | 8.2779 | 8.5276 | 8.4943 | 8.4674 | 1122695 | 8.4492 |  |  | 1082700 | 0 | 1082700 | 39995 | 3.562% | 70.2 |  | 1190.71
2025-05-02 | 2026 | 2025 | 2025-05-01 | 31 | 29702 | 32978 | 24447 | 31464 | 33306 | 29048 | 26581 | 23768 | 27074 | 27547 | 26607 | 25954 | 22606 | 25514 | 27055 | 29106 | 34884 | 32010 | 27520 | 27553 | 23738 | 28813 | 28402 | 27823 | 33472 | 25628 | 6.922 | 7.1906 | 6.3539 | 7.1813 | 7.2628 | 6.856 | 6.7724 | 6.3506 | 6.6205 | 6.6928 | 6.5622 | 6.5078 | 6.2274 | 6.4798 | 6.6526 | 6.9531 | 7.408 | 7.0756 | 6.6686 | 6.7272 | 7.2083 | 7.0424 | 6.7051 | 6.7346 | 7.2115 | 6.4764 | 732600 | 6.8017 |  |  | 681750 | 0 | 681750 | 50850 | 6.941% | 70.2 |  | 781.68
2025-05-03 | 2026 | 2025 | 2025-05-01 | 31 | 29084 | 50749 | 38653 | 45482 | 50589 | 39457 | 42306 | 24327 | 40568 | 43941 | 41617 | 43049 | 33999 | 39854 | 42149 | 47857 | 52503 | 42004 | 45398 | 44438 | 47180 | 46189 | 43594 | 20716 | 45983 | 43445 | 8.5129 | 9.066 | 8.0985 | 8.8032 | 9.1381 | 8.6614 | 8.4251 | 8.132 | 8.3519 | 8.6158 | 8.3835 | 8.4734 | 7.8183 | 8.2897 | 8.4081 | 9.0144 | 9.3542 | 8.9001 | 8.8603 | 8.6981 | 8.9399 | 8.967 | 8.6199 | 9.0589 | 8.9481 | 8.5372 | 1085131 | 8.6568 |  |  | 1074150 | 0 | 1074150 | 10981 | 1.012% | 70.2 |  | 1224.47
2025-05-04 | 2026 | 2025 | 2025-05-01 | 31 | 17974 | 29174 | 25699 | 27656 | 29142 | 28832 | 23702 | 17190 | 28449 | 29343 | 28037 | 29548 | 25159 | 26738 | 27808 | 28968 | 30672 | 30284 | 28628 | 26654 | 30867 | 28077 | 29011 | 28077 | 25433 | 30825 | 6.6283 | 6.7307 | 6.5555 | 6.7367 | 6.8492 | 6.7621 | 6.2467 | 6.54 | 6.7583 | 6.9048 | 6.8124 | 6.8777 | 6.5328 | 6.6881 | 6.7801 | 7.0407 | 7.0868 | 6.8567 | 6.82 | 6.5917 | 6.9838 | 6.7583 | 6.8653 | 6.6847 | 6.8663 | 6.9374 | 711947 | 6.7652 |  |  | 685800 | 450 | 685350 | 26147 | 3.673% | 70.2 |  | 773.86
2025-05-05 | 2026 | 2025 | 2025-05-01 | 31 | 18835 | 31559 | 29715 | 30722 | 30948 | 30904 | 28268 | 27202 | 31886 | 31922 | 20276 | 31332 | 28547 | 29701 | 31905 | 30318 | 28089 | 33937 | 30708 | 29830 | 31289 | 25892 | 32518 | 30515 | 29760 | 31214 | 7.3475 | 7.3099 | 7.1846 | 7.2253 | 7.3093 | 7.2811 | 6.9722 | 7.1834 | 7.403 | 7.442 | 7.3674 | 7.37 | 7.1776 | 7.2469 | 7.3885 | 7.3498 | 7.2903 | 7.5298 | 7.2362 | 7.2922 | 7.3964 | 6.8903 | 7.4494 | 7.2444 | 7.1503 | 7.371 | 767792 | 7.2849 |  |  | 741600 | 0 | 741600 | 26192 | 3.411% | 70.2 |  | 837.33
2025-05-06 | 2026 | 2025 | 2025-05-01 | 31 | 10165 | 15091 | 15302 | 15082 | 14339 | 23291 | 18793 | 11190 | 15245 | 18504 | 16459 | 15671 | 14458 | 16788 | 17961 | 177 | 24296 | 25931 | 26460 | 24540 | 23651 | 21281 | 15228 | 87 | 14231 | 10926 | 7.0833 | 6.6335 | 6.8706 | 6.3598 | 6.7275 | 6.9846 | 6.1776 | 6.7678 | 6.8908 | 7.1291 | 6.9965 | 6.9837 | 6.8513 | 6.9905 | 7.1088 | 7.1132 | 7.2666 | 7.1202 | 6.9017 | 6.8773 | 6.9616 | 6.8491 | 6.8998 | 7.1285 | 6.467 | 6.9039 | 425147 | 6.8863 |  |  | 412650 | 0 | 412650 | 12497 | 2.939% | 70.2 |  | 541.99
2025-05-07 | 2026 | 2025 | 2025-05-01 | 31 | 11319 | 16965 | 1852 | 19556 | 16886 | 19918 | 16111 | 11676 | 15126 | 14677 | 14545 | 11445 | 15086 | 14856 | 14641 | 1279 | 19367 | 21456 | 20272 | 19397 | 21725 | 19485 | 12584 | 10416 | 15407 | 15166 | 5.7432 | 5.8574 | 5.5645 | 5.6083 | 5.9282 | 6.034 | 5.3851 | 5.6519 | 5.6113 | 5.6851 | 5.7726 | 5.8937 | 5.8009 | 5.7049 | 5.6932 | 5.7809 | 6.1783 | 6.1342 | 5.7728 | 6.1547 | 6.0544 | 5.9905 | 5.79 | 6.1613 | 6.0004 | 5.7176 | 391213 | 5.8334 |  |  | 377100 | 0 | 377100 | 14113 | 3.607% | 70.2 |  | 371.67
2025-05-08 | 2026 | 2025 | 2025-05-01 | 31 | 7575 | 10183 | 6151 | 9882 | 9278 | 7917 | 7381 | 6257 | 6464 | 6233 | 7094 | 6716 | 6390 | 6051 | 7149 | 7733 | 7908 | 8265 | 8140 | 6207 | 7764 | 7733 | 5173 | 9370 | 8720 | 6869 | 4.2821 | 4.4326 | 3.9808 | 4.3882 | 4.4838 | 4.251 | 4.0774 | 3.8574 | 3.9506 | 4.0057 | 4.1706 | 4.0232 | 3.9824 | 3.9163 | 4.0494 | 4.1438 | 4.2416 | 4.1926 | 4.1282 | 4.3726 | 4.0258 | 4.1732 | 3.9137 | 4.3362 | 4.322 | 4.0434 | 194603 | 4.144 |  |  | 187200 | 450 | 186750 | 7403 | 3.804% | 70.2 |  | 194.403
2025-05-09 | 2026 | 2025 | 2025-05-01 | 31 | 9128 | 12509 | 9207 | 5316 | 11663 | 6891 | 4777 | 9913 | 8780 | 9374 | 9372 | 10322 | 10508 | 10289 | 10040 | 6386 | 6518 | 6914 | 4077 | 6597 | 5387 | 7622 | 9232 | 7052 | 11182 | 9743 | 4.35 | 4.66 | 4.13 | 4 | 4.67 | 4.13 | 3.94 | 4.25 | 4.14 | 4.17 | 4.31 | 4.34 | 4.31 | 4.36 | 4.29 | 4.06 | 4.33 | 3.93 | 3.79 | 4.1 | 3.76 | 4.26 | 4.26 | 4.14 | 4.55 | 4.29 | 218799 | 4.2123 |  |  | 210150 | 0 | 210150 | 8649 | 3.953% | 70.2 |  | 215.78
2025-05-10 | 2026 | 2025 | 2025-05-01 | 31 | 14837 | 21132 | 12290 | 17359 | 19838 | 12904 | 13014 | 12886 | 13132 | 11294 | 13194 | 13400 | 12510 | 12935 | 13423 | 13663 | 15113 | 11997 | 0 | 12177 | 11514 | 15068 | 11818 | 12570 | 20756 | 14169 | 5.074 | 5.6715 | 4.8213 | 5.5293 | 5.6067 | 5.1672 | 4.9639 | 5.0511 | 4.8701 | 4.719 | 4.9156 | 4.9999 | 4.8692 | 4.9765 | 4.9662 | 5.21 | 5.9097 | 4.9219 | 0 | 5.004 | 4.856 | 5.7399 | 4.9135 | 4.9545 | 5.5285 | 4.9138 | 352993 | 4.929 |  |  | 341550 | 900 | 340650 | 11443 | 3.242% | 70.2 |  | 361.29
2025-05-11 | 2026 | 2025 | 2025-05-01 | 31 | 11784 | 18152 | 10710 | 14944 | 16638 | 12050 | 12314 | 12976 | 11136 | 9042 | 10160 | 7229 | 10619 | 10415 | 11894 | 10970 | 13086 | 10907 | 9508 | 9816 | 9404 | 13232 | 10858 | 10039 | 17651 | 10027 | 4.94 | 5.32 | 4.51 | 5.05 | 5.31 | 4.9 | 4.65 | 4.77 | 4.58 | 4.33 | 4.5 | 4.53 | 4.5 | 4.54 | 4.7 | 4.6 | 5.08 | 4.6 | 4.58 | 4.5 | 4.35 | 5.04 | 4.55 | 4.46 | 5.37 | 4.62 | 305561 | 4.7262 |  |  | 296550 | 450 | 296100 | 9011 | 2.949% | 70.2 |  | 313.28
2025-05-12 | 2026 | 2025 | 2025-05-01 | 31 | 13179 | 18885 | 12004 | 15005 | 16569 | 11228 | 10674 | 12686 | 12783 | 10350 | 11071 | 9535 | 10103 | 11238 | 11575 | 10406 | 12451 | 11034 | 9396 | 9383 | 9631 | 11832 | 12422 | 10435 | 17749 | 13322 | 5.2 | 5.56 | 4.87 | 5.29 | 5.43 | 5.14 | 4.58 | 4.9 | 4.99 | 4.59 | 4.8 | 4.76 | 4.61 | 4.79 | 4.81 | 4.73 | 5.14 | 4.81 | 4.66 | 4.56 | 4.6 | 5.18 | 4.91 | 4.65 | 5.62 | 5 | 314946 | 4.93 |  |  | 306000 | 0 | 306000 | 8946 | 2.84% | 70.2 |  | 314.91
2025-05-13 | 2026 | 2025 | 2025-05-01 | 31 | 15857 | 18876 | 15776 | 17095 | 17236 | 17663 | 12778 | 15814 | 16473 | 13813 | 14778 | 15300 | 13332 | 15553 | 14487 | 14790 | 16970 | 17995 | 15025 | 15229 | 16195 | 18584 | 16842 | 15551 | 17764 | 15898 | 5.4114 | 5.4339 | 5.0701 | 5.3212 | 5.3029 | 5.6258 | 4.8813 | 5.1025 | 5.188 | 4.8715 | 5.069 | 5.0838 | 4.9722 | 5.1481 | 5.0597 | 5.1417 | 5.5261 | 5.3897 | 5.0406 | 5.1537 | 5.1899 | 5.8051 | 5.2141 | 5.1444 | 5.479 | 5.1699 | 415674 | 5.2229 |  |  | 400950 | 0 | 400950 | 14724 | 3.542% | 70.2 |  | 410.17
2025-05-14 | 2026 | 2025 | 2025-05-01 | 31 | 16319 | 18583 | 14080 | 17417 | 15099 | 17720 | 11697 | 15283 | 15322 | 15415 | 14181 | 15302 | 13452 | 14700 | 15173 | 15303 | 18475 | 17089 | 16326 | 15624 | 16085 | 19544 | 14410 | 16242 | 16100 | 15454 | 5.0697 | 5.2797 | 5.0058 | 5.2352 | 5.3367 | 5.4969 | 4.6087 | 4.9868 | 5.0221 | 5.1212 | 4.961 | 5.0131 | 4.8338 | 5.0288 | 5.0728 | 5.1335 | 5.5705 | 5.2769 | 5.0337 | 5.0945 | 5.1835 | 5.7272 | 5.0189 | 5.0988 | 5.3312 | 5.0005 | 410395 | 5.1362 |  |  | 396450 | 450 | 396000 | 13945 | 3.398% | 70.2 |  | 415.16
2025-05-15 | 2026 | 2025 | 2025-05-01 | 31 | 10977 | 13755 | 10870 | 10727 | 12109 | 10080 | 3143 | 9579 | 10970 | 9261 | 9679 | 10295 | 9066 | 10110 | 10258 | 9560 | 7809 | 9672 | 9583 | 8813 | 8783 | 9938 | 8838 | 9045 | 14292 | 11056 | 4.6133 | 4.6857 | 4.5751 | 4.4538 | 4.7587 | 4.6811 | 4.0416 | 4.3451 | 4.6019 | 4.4359 | 4.4327 | 4.5008 | 4.2769 | 4.5788 | 4.5176 | 4.471 | 4.5255 | 4.4989 | 4.3186 | 4.4651 | 4.3518 | 4.8256 | 4.4764 | 4.3887 | 4.8763 | 4.4816 | 258268 | 4.5069 |  |  | 248850 | 450 | 248400 | 9418 | 3.647% | 70.2 |  | 270.48
2025-05-16 | 2026 | 2025 | 2025-05-01 | 31 | 15323 | 18473 | 17202 | 13328 | 17636 | 15436 | 0 | 17474 | 4818 | 15439 | 17201 | 16669 | 15204 | 17755 | 16720 | 13381 | 17700 | 16087 | 17687 | 13373 | 16523 | 14989 | 15167 | 15031 | 17672 | 17902 | 5.5061 | 5.6145 | 5.4803 | 5.2666 | 5.6366 | 5.5567 | 5.2729 | 5.519 | 5.3178 | 5.2531 | 5.5726 | 5.5027 | 5.364 | 5.5334 | 5.3435 | 5.2426 | 5.9712 | 5.4459 | 5.6102 | 5.2698 | 5.4586 | 5.5388 | 5.2906 | 5.391 | 5.6255 | 5.584 | 394190 | 5.468 |  |  | 380700 | 0 | 380700 | 13490 | 3.422% | 70.2 |  | 429.76
2025-05-17 | 2026 | 2025 | 2025-05-01 | 31 | 12936 | 13841 | 13636 | 14208 | 13981 | 15568 | 6613 | 13646 | 0 | 12377 | 12651 | 12234 | 12639 | 13588 | 11589 | 13521 | 16123 | 16373 | 16562 | 14646 | 15887 | 15871 | 12728 | 14583 | 14600 | 12529 | 4.9874 | 5.0358 | 5.0377 | 5.0835 | 5.1158 | 5.5332 | 5.1147 | 5.0208 | 5.0653 | 4.9758 | 5.0733 | 4.9411 | 5.0442 | 5.1525 | 4.9208 | 5.1012 | 5.6313 | 5.4148 | 5.4194 | 5.3 | 5.4234 | 5.6298 | 4.9781 | 5.252 | 5.1213 | 4.916 | 342930 | 5.165 |  |  | 332550 | 0 | 332550 | 10380 | 3.027% | 70.2 |  | 357.08
2025-05-18 | 2026 | 2025 | 2025-05-01 | 31 | 11946 | 13720 | 12694 | 13552 | 13489 | 14126 | 12289 | 12152 | 10459 | 13272 | 12398 | 12617 | 11059 | 11662 | 11511 | 13018 | 14762 | 14428 | 14526 | 11805 | 13482 | 13318 | 12401 | 13791 | 14092 | 12416 | 5.0464 | 5.1148 | 5.0215 | 4.996 | 5.1639 | 5.3816 | 4.9451 | 4.9598 | 5.1681 | 5.1108 | 5.0665 | 5.0718 | 4.9145 | 4.9747 | 4.8935 | 5.0484 | 5.4293 | 5.2307 | 5.1165 | 4.977 | 5.0487 | 5.3208 | 4.956 | 5.1421 | 5.1714 | 4.9966 | 334985 | 5.0872 |  |  | 324900 | 0 | 324900 | 10085 | 3.011% | 70.2 |  | 337.37
2025-05-19 | 2026 | 2025 | 2025-05-01 | 31 | 15558 | 18002 | 13334 | 16163 | 16621 | 15698 | 15577 | 13643 | 15728 | 14496 | 12657 | 13600 | 13181 | 14141 | 13808 | 14766 | 16170 | 16444 | 15562 | 13464 | 14918 | 15617 | 14305 | 14413 | 18378 | 14378 | 5.2353 | 5.3892 | 4.931 | 5.1551 | 5.3842 | 5.4276 | 5.1708 | 4.8988 | 5.2003 | 5.0985 | 4.9034 | 4.9524 | 4.9085 | 5.0753 | 4.9822 | 5.2071 | 5.5333 | 5.2873 | 5.1228 | 4.9801 | 5.1851 | 5.3824 | 5.0476 | 5.0416 | 5.4908 | 5.0735 | 390622 | 5.1563 |  |  | 377550 | 0 | 377550 | 13072 | 3.346% | 70.2 |  | 390.56
2025-05-20 | 2026 | 2025 | 2025-05-01 | 31 | 13354 | 14878 | 13186 | 14713 | 13341 | 17635 | 12687 | 11853 | 13578 | 11868 | 12633 | 12059 | 13608 | 13779 | 14995 | 15196 | 16025 | 16145 | 14966 | 13323 | 13934 | 19816 | 13677 | 13270 | 11901 | 14103 | 5.1534 | 5.165 | 5.1111 | 5.335 | 5.0268 | 5.9038 | 5.0603 | 5.2739 | 5.193 | 4.9713 | 5.1108 | 5.0332 | 5.1621 | 5.2392 | 5.2847 | 5.468 | 5.6389 | 5.571 | 5.2465 | 5.266 | 5.3048 | 5.9965 | 5.2114 | 5.168 | 5.2221 | 5.1612 | 366523 | 5.2799 |  |  | 354150 | 450 | 353700 | 12373 | 3.376% | 70.2 |  | 390.19
2025-05-21 | 2026 | 2025 | 2025-05-01 | 31 | 5803 | 6870 | 4988 | 8746 | 6797 | 12064 | 8259 | 5500 | 5730 | 4705 | 4932 | 5048 | 5506 | 4919 | 6055 | 9269 | 12347 | 10658 | 9074 | 7738 | 9422 | 13881 | 5134 | 7917 | 6874 | 5324 | 4.4813 | 4.6071 | 4.2281 | 4.4625 | 4.6091 | 5.2309 | 4.3908 | 4.3136 | 4.3978 | 4.1453 | 4.1941 | 4.2658 | 4.2231 | 4.2792 | 4.4517 | 4.6978 | 5.031 | 4.9651 | 4.5521 | 4.3837 | 4.7536 | 5.3845 | 4.2631 | 4.4425 | 4.6387 | 4.4501 | 193560 | 4.5324 |  |  | 186750 | 0 | 186750 | 6810 | 3.518% | 70.2 |  | 202.65
2025-05-22 | 2026 | 2025 | 2025-05-01 | 31 | 5325 | 4261 | 2693 | 5901 | 5814 | 7702 | 5581 | 3597 | 4651 | 4928 | 4947 | 3211 | 4996 | 4869 | 5244 | 7051 | 7589 | 7942 | 5630 | 6725 | 6408 | 7766 | 2985 | 6850 | 3810 | 3271 | 4.1618 | 4.1426 | 3.9926 | 3.2892 | 4.2083 | 3.7441 | 3.2205 | 3.7531 | 3.9939 | 3.4765 | 4.0462 | 4.0371 | 3.4254 | 4.0648 | 3.5271 | 3.5917 | 3.8218 | 3.6434 | 3.3441 | 3.5103 | 3.3944 | 3.7944 | 4.0029 | 3.5227 | 4.2637 | 3.8773 | 139747 | 3.7635 |  |  | 134100 | 1350 | 132750 | 5647 | 4.041% | 70.2 |  | 158.54
2025-05-23 | 2026 | 2025 | 2025-05-01 | 31 | 13668 | 14033 | 15582 | 13541 | 13606 | 14664 | 12284 | 12198 | 13305 | 12638 | 15506 | 12864 | 12326 | 13110 | 13871 | 14234 | 13106 | 14776 | 12232 | 13537 | 12398 | 14801 | 15126 | 12086 | 12387 | 12236 | 4.8401 | 4.7564 | 5.1458 | 4.727 | 4.8064 | 5.301 | 4.534 | 4.7815 | 4.9097 | 4.901 | 5.1875 | 4.8191 | 4.7542 | 4.966 | 4.9407 | 5.018 | 4.8984 | 5.1885 | 4.5148 | 4.9509 | 4.8264 | 5.2289 | 5.1031 | 4.7422 | 4.8134 | 4.6903 | 350115 | 4.8979 |  |  | 337950 | 0 | 337950 | 12165 | 3.475% | 70.2 |  | 371.21
2025-05-24 | 2026 | 2025 | 2025-05-01 | 31 | 27867 | 31651 | 27965 | 37041 | 32935 | 34792 | 37142 | 16489 | 27378 | 28918 | 28336 | 14646 | 29021 | 28337 | 27961 | 36391 | 43558 | 34099 | 37403 | 35369 | 36290 | 39991 | 28932 | 36419 | 29481 | 25631 | 8.5741 | 9.3281 | 6.7629 | 7.3269 | 9.2793 | 7.164 | 7.2506 | 8.749 | 8.543 | 6.8704 | 6.8695 | 6.7288 | 6.8412 | 6.8389 | 6.8011 | 7.326 | 8.011 | 6.9788 | 7.2006 | 7.0827 | 7.1904 | 7.7211 | 6.8802 | 7.1317 | 8.7937 | 8.5232 | 814043 | 7.568 |  |  | 785250 | 0 | 785250 | 28793 | 3.537% | 70.2 |  | 847.72
2025-05-25 | 2026 | 2025 | 2025-05-01 | 31 | 31523 | 31804 | 32524 | 35537 | 30576 | 37549 | 32089 | 13402 | 32584 | 30599 | 32802 | 29518 | 33578 | 34055 | 34662 | 37245 | 36698 | 36409 | 34792 | 36870 | 19043 | 39460 | 33513 | 36629 | 24177 | 33380 | 7.39 | 8.54 | 7.42 | 7.44 | 8.41 | 7.81 | 7.1 | 7.66 | 7.5 | 7.36 | 7.55 | 7.49 | 7.53 | 7.64 | 7.72 | 7.75 | 7.77 | 7.61 | 7.37 | 7.68 | 7.9 | 8.09 | 7.57 | 7.6 | 8.27 | 7.56 | 841018 | 7.6819 |  |  | 812250 | 0 | 812250 | 28768 | 3.421% | 70.2 |  | 893.8
2025-05-26 | 2026 | 2025 | 2025-05-01 | 31 | 30294 | 31689 | 28918 | 30880 | 29206 | 30683 | 29635 | 26348 | 30386 | 26076 | 29120 | 27828 | 27161 | 28114 | 26878 | 28386 | 31939 | 31288 | 28966 | 26825 | 27558 | 31331 | 30243 | 28117 | 27468 | 29985 | 7.26 | 7.51 | 6.95 | 7.26 | 7.45 | 7.23 | 7.14 | 7.21 | 7.18 | 6.69 | 7.06 | 6.95 | 6.86 | 6.97 | 6.79 | 6.98 | 7.38 | 7.15 | 6.93 | 6.81 | 7.15 | 7.45 | 7.14 | 6.94 | 7.29 | 7.39 | 755322 | 7.12 |  |  | 731700 | 0 | 731700 | 23622 | 3.127% | 70.2 |  | 797.2
2025-05-27 | 2026 | 2025 | 2025-05-01 | 31 | 45298 | 48703 | 30098 | 55945 | 44273 | 54646 | 50912 | 10998 | 43632 | 44057 | 43495 | 44780 | 44658 | 45661 | 45816 | 53730 | 55315 | 55192 | 55584 | 52891 | 53312 | 54059 | 44797 | 54974 | 24864 | 45417 | 9.3 | 9.71 | 8.98 | 9.82 | 9.44 | 9.5 | 9.72 | 9.58 | 9.19 | 9.29 | 9.21 | 9.31 | 9.22 | 9.36 | 9.43 | 9.59 | 9.86 | 9.48 | 9.78 | 9.47 | 9.43 | 9.83 | 9.33 | 9.53 | 9.65 | 9.43 | 1203107 | 9.4785 |  |  | 1159200 | 0 | 1159200 | 43907 | 3.649% | 70.2 |  | 1294.88
2025-05-28 | 2026 | 2025 | 2025-05-01 | 31 | 36145 | 38104 | 36941 | 36974 | 37270 | 38856 | 38555 | 28269 | 35976 | 40745 | 37551 | 39371 | 36909 | 39144 | 38829 | 38163 | 42635 | 39115 | 41216 | 35547 | 38234 | 39494 | 40262 | 37785 | 29365 | 30364 | 8.29 | 8.39 | 7.92 | 8.51 | 8.3 | 8.62 | 8.62 | 8.51 | 8.26 | 8.29 | 8.08 | 8.19 | 8.04 | 8.18 | 8.18 | 8.63 | 9.12 | 8.56 | 8.88 | 8.35 | 8.51 | 8.86 | 8.3 | 8.46 | 8.39 | 8.48 | 971819 | 8.42 |  |  | 940050 | 0 | 940050 | 31769 | 3.269% | 70.2 |  | 1024.62
2025-05-29 | 2026 | 2025 | 2025-05-01 | 31 | 34991 | 35336 | 34454 | 27457 | 34066 | 38069 | 36624 | 36586 | 35770 | 35884 | 35836 | 35861 | 34932 | 36054 | 35776 | 34759 | 40825 | 38317 | 35573 | 33065 | 38437 | 38478 | 36437 | 36704 | 36147 | 36092 | 7.31 | 7.48 | 7.19 | 7.46 | 7.41 | 7.75 | 7.54 | 7.41 | 7.34 | 7.39 | 7.49 | 7.42 | 7.29 | 7.4 | 7.39 | 7.36 | 7.97 | 7.64 | 7.4 | 7.17 | 7.7 | 7.86 | 7.49 | 7.43 | 7.38 | 7.46 | 932530 | 7.4665 |  |  | 901800 | 450 | 901350 | 30730 | 3.295% | 70.2 |  | 986.68
2025-05-30 | 2026 | 2025 | 2025-05-01 | 31 | 54422 | 56778 | 55357 | 51855 | 54055 | 55099 | 52504 | 54379 | 53124 | 54576 | 55825 | 54494 | 54331 | 55074 | 55209 | 53676 | 48430 | 54614 | 54160 | 53978 | 57017 | 57090 | 56047 | 56687 | 57270 | 56413 | 9.9 | 10.18 | 9.76 | 9.77 | 10.13 | 9.69 | 9.71 | 10.04 | 9.74 | 9.86 | 9.98 | 9.98 | 9.82 | 9.76 | 9.86 | 9.88 | 9.77 | 9.82 | 9.85 | 9.64 | 9.92 | 10.04 | 10 | 9.95 | 10.09 | 10.06 | 1422464 | 9.8923 |  |  | 1370700 | 0 | 1370700 | 51764 | 3.639% | 70.2 |  | 1505.57
2025-05-31 | 2026 | 2025 | 2025-05-01 | 31 | 54328 | 59812 | 55547 | 48432 | 57780 | 47521 | 50547 | 51528 | 52803 | 45951 | 54037 | 53252 | 50292 | 52651 | 52780 | 45969 | 51878 | 48505 | 48391 | 47567 | 47315 | 50992 | 54330 | 47157 | 60528 | 51268 | 9.89 | 10.23 | 9.62 | 9.86 | 10.1 | 9.17 | 9.72 | 9.64 | 9.68 | 9.25 | 9.65 | 9.55 | 9.65 | 9.55 | 9.53 | 9.31 | 9.65 | 9.28 | 9.41 | 9.34 | 9.37 | 9.71 | 9.65 | 9.42 | 10.27 | 9.72 | 1341161 | 9.6238 |  |  | 1292850 | 0 | 1292850 | 48311 | 3.602% | 70.2 |  | 1438.1
2025-06-01 | 2026 | 2025 | 2025-06-01 | 30 | 50690 | 51160 | 48703 | 53768 | 50924 | 52292 | 51412 | 49730 | 45520 | 48023.5 | 51597 | 49060 | 52138 | 49854.5 | 54464.8333 | 51338 | 53451 | 55267 | 53500 | 53693 | 52837.5 | 56229 | 49551.8 | 53390.8 | 51016.5 | 50608.8333 | 9.3 | 9.65 | 9.98 | 9.82 | 9 | 9.5 | 9.72 | 9 | 9 | 9.29 | 9.23 | 9.31 | 8.22 | 9.36 | 9.42 | 9.59 | 9.86 | 9.46 | 9.78 | 9.5 | 9.43 | 9.06 | 9.25 | 9.25 | 9.75 | 9.43 | 1340220.2667 | 9.3908 |  |  | 1315800 | 0 | 1315800 | 24420.2667 | 1.822% | 70.2 |  | 1430.08
2025-06-02 | 2026 | 2025 | 2025-06-01 | 30 | 45658.5 | 43828 | 44295 | 44252 | 38461 | 47731 | 43345 | 41140 | 44086 | 43054.6667 | 44131.3333 | 42844.3 | 43483 | 42894.3333 | 44019 | 43570 | 48680 | 49542 | 46699 | 44818.5 | 48023 | 51023 | 43122 | 46021 | 46453 | 44649.8333 | 9.3 | 9.71 | 8.95 | 9.82 | 9.67 | 9.5 | 9.6 | 9.43 | 9.19 | 9.29 | 9.21 | 9.32 | 9.22 | 9.35 | 9.42 | 9.42 | 9.89 | 9.46 | 9.78 | 9.47 | 9.43 | 9.83 | 9.33 | 9.53 | 9.5 | 9.5 | 1165824.4667 | 9.4662 |  |  | 1115550 | 0 | 1115550 | 50274.4667 | 4.312% | 70.2 |  | 1231.2
2025-06-03 | 2026 | 2025 | 2025-06-01 | 30 | 40925 | 42209 | 38087 | 42047 | 36685 | 45651 | 40929 | 42705 | 38850 | 41700 | 40451 | 41874 | 43273 | 42846 | 42470 | 42266 | 44084 | 49499 | 42974 | 43980 | 45569 | 49028 | 39881 | 43980 | 40698 | 40020 | 8.3613 | 8.3293 | 7.9692 | 8.4647 | 8.2582 | 8.8278 | 8.2866 | 8.3554 | 8.095 | 8.3624 | 8.3172 | 8.3362 | 8.463 | 8.4297 | 8.4471 | 8.4174 | 8.7751 | 8.9645 | 8.5001 | 8.5967 | 8.7317 | 9.2119 | 8.2733 | 8.5872 | 8.1648 | 8.3165 | 1102681 | 8.4555 |  |  | 1066950 | 0 | 1066950 | 35731 | 3.24% | 70.2 |  | 1108.56
2025-06-04 | 2026 | 2025 | 2025-06-01 | 30 | 24898 | 25759 | 26108 | 25763 | 24508 | 27140 | 24286 | 27126 | 25943 | 25043 | 25689 | 27206 | 25486 | 26571 | 25789 | 25548 | 27895 | 27513 | 26102 | 25085 | 26598 | 27739 | 27511 | 27210 | 26511 | 26960 | 6.4133 | 6.38 | 6.3997 | 6.5212 | 6.316 | 6.8666 | 6.3282 | 6.5191 | 6.4479 | 6.4703 | 6.5357 | 6.5948 | 6.4676 | 6.5564 | 6.4814 | 6.5065 | 6.9206 | 6.6987 | 6.5718 | 6.4744 | 6.6208 | 6.9825 | 6.616 | 6.6071 | 6.3789 | 6.5644 | 681987 | 6.5477 |  |  | 661950 | 0 | 661950 | 20037 | 2.938% | 70.2 |  | 27.04
2025-06-05 | 2026 | 2025 | 2025-06-01 | 30 | 13550 | 16125 | 13730 | 13586 | 16515 | 16771 | 12137 | 14453 | 13444 | 15036 | 14184 | 14072 | 11586 | 13691 | 13908 | 15393 | 17046 | 16278 | 13284 | 13474 | 14863 | 17240 | 13874 | 14133 | 16460 | 14824 | 5.0131 | 5.2413 | 5.0058 | 5.089 | 5.35 | 5.5488 | 4.7424 | 4.9908 | 4.9435 | 5.2642 | 5.141 | 5.079 | 4.7873 | 5.0693 | 5.0746 | 5.1963 | 5.4158 | 5.3292 | 4.7405 | 5.0078 | 5.1641 | 5.5613 | 5.0563 | 5.0798 | 5.202 | 5.0755 | 379657 | 5.1219 |  |  | 367200 | 450 | 366750 | 12457 | 3.281% | 70.2 |  | 385.8
2025-06-06 | 2026 | 2025 | 2025-06-01 | 30 | 23542 | 28011 | 21461 | 25991 | 25186 | 21010 | 24124 | 23491 | 22922 | 19049 | 21231 | 21248 | 15424 | 21157 | 21726 | 21529 | 21983 | 20504 | 24299 | 21713 | 17959 | 22267 | 20887 | 22271 | 27512 | 23651 | 6.396 | 6.5941 | 6.1098 | 6.4729 | 6.5211 | 6.0505 | 6.2222 | 6.1627 | 6.3328 | 5.79 | 6.0825 | 6.013 | 5.6119 | 6.0167 | 6.0845 | 5.9181 | 6.0956 | 5.8436 | 6.1321 | 5.9603 | 5.674 | 6.1553 | 6.2453 | 6.0592 | 6.5124 | 6.2502 | 580148 | 6.1272 |  |  | 562950 | 0 | 562950 | 17198 | 2.964% | 70.2 |  | 593.58
2025-06-07 | 2026 | 2025 | 2025-06-01 | 30 | 36444 | 39249 | 34508 | 37281 | 35981 | 35598 | 29552 | 35543 | 35377 | 27739 | 32412 | 32626 | 30645 | 31718 | 32828 | 34805 | 36795 | 33687 | 34286 | 33556 | 30481 | 36261 | 33585 | 33319 | 36168 | 36341 | 7.7685 | 7.8717 | 7.4576 | 8.0349 | 7.7258 | 7.6244 | 7.9135 | 7.6635 | 7.6497 | 6.8254 | 7.3806 | 7.3603 | 7.1381 | 7.2479 | 7.2614 | 7.4703 | 7.7663 | 7.3792 | 7.4387 | 7.3408 | 7.1207 | 7.8234 | 7.6009 | 7.3147 | 7.5799 | 7.7582 | 886785 | 7.5199 |  |  | 860400 | 0 | 860400 | 26385 | 2.975% | 70.2 |  | 899.42
2025-06-08 | 2026 | 2025 | 2025-06-01 | 30 | 32831 | 38753 | 28801 | 31181 | 35576 | 34796 | 27380 | 32471 | 32169 | 21370 | 27931 | 28514 | 29599 | 29807 | 29849 | 27769 | 37806 | 34026 | 32013 | 31913 | 29442 | 37250 | 30447 | 31586 | 36044 | 31644 | 7.4015 | 7.7237 | 6.9159 | 7.5828 | 7.5312 | 7.4843 | 8.5573 | 7.2618 | 7.364 | 6.7678 | 6.9065 | 6.9401 | 7.0048 | 7.0737 | 7.0331 | 7.2335 | 7.7298 | 7.2961 | 7.1389 | 7.1742 | 6.9294 | 7.8553 | 7.1547 | 7.1456 | 7.4145 | 7.267 | 820968 | 7.3034 |  |  | 796950 | 0 | 796950 | 24018 | 2.926% | 70.2 |  | 846.28
2025-06-09 | 2026 | 2025 | 2025-06-01 | 30 | 38655 | 43809 | 35879 | 43999 | 40683 | 40911 | 42416 | 40286 | 37517 | 33817 | 35565 | 36462 | 36617 | 36339 | 38249 | 35416 | 43247 | 39577 | 43313 | 39588 | 36821 | 41992 | 38136 | 39136 | 41879 | 38713 | 7.9085 | 8.2609 | 7.5985 | 8.3585 | 8.0426 | 8.0916 | 8.1931 | 7.98 | 7.8343 | 7.4884 | 7.7117 | 7.7317 | 7.7314 | 7.7606 | 7.8296 | 7.9069 | 8.2959 | 7.9583 | 8.2128 | 7.9706 | 7.7406 | 8.3485 | 7.9217 | 7.9288 | 8.0008 | 7.9617 | 1019022 | 7.9526 |  |  | 986400 | 0 | 986400 | 32622 | 3.201% | 70.2 |  | 1032.83
2025-06-10 | 2026 | 2025 | 2025-06-01 | 30 | 31902 | 48133 | 38820 | 45191 | 45509 | 45918 | 44939 | 41406 | 40203 | 24662 | 39174 | 38012 | 38340 | 40587 | 39946 | 36929 | 47784 | 45025 | 45854 | 41819 | 39222 | 47621 | 41629 | 42452 | 44148 | 40326 | 7.9992 | 8.5849 | 7.7553 | 8.7191 | 8.443 | 8.4359 | 8.9128 | 8.1028 | 7.9328 | 7.2729 | 7.9554 | 7.786 | 7.8585 | 8.0126 | 7.9769 | 8.1076 | 8.687 | 8.3174 | 8.5791 | 8.0747 | 7.8759 | 8.8274 | 8.1328 | 8.126 | 8.1667 | 8.0076 | 1075551 | 8.1789 |  |  | 1039950 | 0 | 1039950 | 35601 | 3.31% | 70.2 |  | 1108.35
2025-06-11 | 2026 | 2025 | 2025-06-01 | 30 | 9734 | 36977 | 29844 | 39436 | 36794 | 40136 | 37443 | 32554 | 31584 | 29395 | 30425 | 29594 | 30667 | 31516 | 33467 | 31802 | 43028 | 38012 | 38995 | 36328 | 32780 | 42577 | 32660 | 32861 | 34949 | 31821 | 7.0827 | 7.3478 | 6.831 | 7.7086 | 7.4348 | 7.7985 | 7.5848 | 7.161 | 7.0099 | 6.8957 | 6.9265 | 6.8606 | 6.9643 | 7.0266 | 7.2197 | 7.3999 | 8.0123 | 7.5483 | 7.5444 | 7.3913 | 7.1442 | 8.2019 | 7.1577 | 7.1294 | 7.1596 | 7.0726 | 875379 | 7.2928 |  |  | 847350 | 0 | 847350 | 28029 | 3.202% | 70.2 |  | 911.21
2025-06-12 | 2026 | 2025 | 2025-06-01 | 30 | 34477 | 39052 | 34841 | 38026 | 39640 | 38942 | 35495 | 35425 | 34158 | 32656 | 35464 | 35020 | 36239 | 33546 | 34042 | 33459 | 38207 | 38826 | 31298 | 36557 | 36826 | 38525 | 34706 | 35891 | 39349 | 34057 | 7.534 | 7.9267 | 7.3833 | 7.9136 | 8.0057 | 7.9624 | 7.6539 | 7.5212 | 7.4208 | 7.3535 | 7.5994 | 7.5747 | 7.6447 | 7.4271 | 7.4801 | 7.7637 | 8.1265 | 7.858 | 7.1226 | 7.7411 | 7.7533 | 8.1178 | 7.5441 | 7.6124 | 7.741 | 7.4847 | 934724 | 7.6641 |  |  | 904050 | 0 | 904050 | 30674 | 3.282% | 70.2 |  | 956.64
Formulas:
Month Year = [Date]-DAY([Date])+1
Days = DAY(EOMONTH(Input_Raw[[#This Row],[Date]],0))
Date = [Date, row above]+1

## WTG_BD
Sr. No. | Date | Finacial Year | Calendor Year | Month | Operating Year | Affected WTG | SPV | Concumaer | Plant Equivalent Weightage | Error Code | Error Text | Breakdown Description | Fault Start TimeStamp | Work Start TimeStamp | Fault Clearance time | Response Time | Resolution Time | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Paired WTG for Enegy based MA | Energy Production during breakdwon of paired WTG | Special remarks | Fault Category | Paired WTG Generation for loss calculation. | loss | Column4 | Column5 | Column6 | Column7 | PTW No. | Job Card No.
1 | 2024-04-15 | 2025 | 2024 | 2024-04-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
2 | 2024-04-15 | 2025 | 2024 | 2024-04-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
3 | 2024-04-15 | 2025 | 2024 | 2024-04-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
4 | 2024-04-15 | 2025 | 2024 | 2024-04-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
5 | 2024-04-15 | 2025 | 2024 | 2024-04-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.68819 | 0 | 16.5167 | 16.5167 | Turbine attending for project pending work | Open | 0.63526 |  |  |  | WTG Breakdown Maintenance |  | 0
6 | 2024-04-15 | 2025 | 2024 | 2024-04-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.77708 | 0 | 18.65 | 18.65 | Turbine attending for project pending work | Open | 0.71731 |  |  |  | WTG Breakdown Maintenance |  | 0
7 | 2024-04-16 | 2025 | 2024 | 2024-04-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
8 | 2024-04-16 | 2025 | 2024 | 2024-04-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
9 | 2024-04-16 | 2025 | 2024 | 2024-04-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
10 | 2024-04-16 | 2025 | 2024 | 2024-04-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
11 | 2024-04-16 | 2025 | 2024 | 2024-04-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
12 | 2024-04-16 | 2025 | 2024 | 2024-04-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
13 | 2024-04-16 | 2025 | 2024 | 2024-04-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | MS for WTG pending point closing | 0 | 0 | 0.82917 | 0 | 19.9 | 19.9 | Turbine stopped after commissioning for pending work | Open | 0.76538 |  |  |  | WTG Breakdown Maintenance |  | 0
14 | 2024-04-17 | 2025 | 2024 | 2024-04-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
15 | 2024-04-17 | 2025 | 2024 | 2024-04-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
16 | 2024-04-17 | 2025 | 2024 | 2024-04-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
17 | 2024-04-17 | 2025 | 2024 | 2024-04-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
18 | 2024-04-17 | 2025 | 2024 | 2024-04-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
19 | 2024-04-17 | 2025 | 2024 | 2024-04-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
20 | 2024-04-17 | 2025 | 2024 | 2024-04-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | MS for WTG pending point closing | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine stopped after commissioning for pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
21 | 2024-04-17 | 2025 | 2024 | 2024-04-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | MS for WTG pending point closing | 0 | 0 | 0.99375 | 0 | 23.85 | 23.85 | Turbine stopped after commissioning for pending work | Open | 0.91731 |  |  |  | WTG Breakdown Maintenance |  | 0
22 | 2024-04-18 | 2025 | 2024 | 2024-04-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
23 | 2024-04-18 | 2025 | 2024 | 2024-04-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
24 | 2024-04-18 | 2025 | 2024 | 2024-04-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
25 | 2024-04-18 | 2025 | 2024 | 2024-04-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
26 | 2024-04-18 | 2025 | 2024 | 2024-04-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
27 | 2024-04-18 | 2025 | 2024 | 2024-04-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
28 | 2024-04-18 | 2025 | 2024 | 2024-04-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | MS for WTG pending point closing | 0 | 0 | 0.99375 | 0 | 23.85 | 23.85 | Turbine stopped after commissioning for pending work | Open | 0.91731 |  |  |  | WTG Breakdown Maintenance |  | 0
29 | 2024-04-18 | 2025 | 2024 | 2024-04-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | MS for WTG pending point closing | 0 | 0 | 0.99653 | 0 | 23.9167 | 23.9167 | Turbine stopped after commissioning for pending work | Open | 0.91987 |  |  |  | WTG Breakdown Maintenance |  | 0
30 | 2024-04-18 | 2025 | 2024 | 2024-04-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | MS for WTG pending point closing | 0 | 0 | 0.99653 | 0 | 23.9167 | 23.9167 | Turbine stopped after commissioning for pending work | Open | 0.91987 |  |  |  | WTG Breakdown Maintenance |  | 0
31 | 2024-04-19 | 2025 | 2024 | 2024-04-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
32 | 2024-04-19 | 2025 | 2024 | 2024-04-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
33 | 2024-04-19 | 2025 | 2024 | 2024-04-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
34 | 2024-04-19 | 2025 | 2024 | 2024-04-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
35 | 2024-04-19 | 2025 | 2024 | 2024-04-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
36 | 2024-04-19 | 2025 | 2024 | 2024-04-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
37 | 2024-04-19 | 2025 | 2024 | 2024-04-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.92153 | 0 | 22.1167 | 22.1167 | Turbine attending for project pending work | Open | 0.85064 |  |  |  | WTG Breakdown Maintenance |  | 0
38 | 2024-04-19 | 2025 | 2024 | 2024-04-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.96319 | 0 | 23.1167 | 23.1167 | Turbine attending for project pending work | Open | 0.8891 |  |  |  | WTG Breakdown Maintenance |  | 0
39 | 2024-04-19 | 2025 | 2024 | 2024-04-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.78681 | 0 | 18.8833 | 18.8833 | Turbine attending for project pending work | Open | 0.72628 |  |  |  | WTG Breakdown Maintenance |  | 0
40 | 2024-04-20 | 2025 | 2024 | 2024-04-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.35556 | 0 | 8.5333 | 8.5333 | Turbine attending for project pending work | Open | 0.32821 |  |  |  | WTG Breakdown Maintenance |  | 0
41 | 2024-04-20 | 2025 | 2024 | 2024-04-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.35556 | 0 | 8.5333 | 8.5333 | Turbine attending for project pending work | Open | 0.32821 |  |  |  | WTG Breakdown Maintenance |  | 0
42 | 2024-04-20 | 2025 | 2024 | 2024-04-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.35556 | 0 | 8.5333 | 8.5333 | Turbine attending for project pending work | Open | 0.32821 |  |  |  | WTG Breakdown Maintenance |  | 0
43 | 2024-04-20 | 2025 | 2024 | 2024-04-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.35556 | 0 | 8.5333 | 8.5333 | Turbine attending for project pending work | Open | 0.32821 |  |  |  | WTG Breakdown Maintenance |  | 0
44 | 2024-04-20 | 2025 | 2024 | 2024-04-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.35556 | 0 | 8.5333 | 8.5333 | Turbine attending for project pending work | Open | 0.32821 |  |  |  | WTG Breakdown Maintenance |  | 0
45 | 2024-04-20 | 2025 | 2024 | 2024-04-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.35556 | 0 | 8.5333 | 8.5333 | Turbine attending for project pending work | Open | 0.32821 |  |  |  | WTG Breakdown Maintenance |  | 0
46 | 2024-04-20 | 2025 | 2024 | 2024-04-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.35556 | 0 | 8.5333 | 8.5333 | Turbine attending for project pending work | Open | 0.32821 |  |  |  | WTG Breakdown Maintenance |  | 0
47 | 2024-04-20 | 2025 | 2024 | 2024-04-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.35556 | 0 | 8.5333 | 8.5333 | Turbine attending for project pending work | Open | 0.32821 |  |  |  | WTG Breakdown Maintenance |  | 0
48 | 2024-04-20 | 2025 | 2024 | 2024-04-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.35556 | 0 | 8.5333 | 8.5333 | Turbine attending for project pending work | Open | 0.32821 |  |  |  | WTG Breakdown Maintenance |  | 0
49 | 2024-04-20 | 2025 | 2024 | 2024-04-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.97431 | 0.97431 | 0.99931 | 0 | 0.6 | 0.6 | Turbine attending for project pending work | Open | 0.023077 |  |  |  | WTG Breakdown Maintenance |  | 0
50 | 2024-04-20 | 2025 | 2024 | 2024-04-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.97431 | 0.97431 | 0.99931 | 0 | 0.6 | 0.6 | Turbine attending for project pending work | Open | 0.023077 |  |  |  | WTG Breakdown Maintenance |  | 0
51 | 2024-04-20 | 2025 | 2024 | 2024-04-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.97431 | 0.97431 | 0.99931 | 0 | 0.6 | 0.6 | Turbine attending for project pending work | Open | 0.023077 |  |  |  | WTG Breakdown Maintenance |  | 0
52 | 2024-04-20 | 2025 | 2024 | 2024-04-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.97431 | 0.97431 | 0.99931 | 0 | 0.6 | 0.6 | Turbine attending for project pending work | Open | 0.023077 |  |  |  | WTG Breakdown Maintenance |  | 0
53 | 2024-04-20 | 2025 | 2024 | 2024-04-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.97431 | 0.97431 | 0.99931 | 0 | 0.6 | 0.6 | Turbine attending for project pending work | Open | 0.023077 |  |  |  | WTG Breakdown Maintenance |  | 0
54 | 2024-04-20 | 2025 | 2024 | 2024-04-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.97431 | 0.97431 | 0.99931 | 0 | 0.6 | 0.6 | Turbine attending for project pending work | Open | 0.023077 |  |  |  | WTG Breakdown Maintenance |  | 0
55 | 2024-04-20 | 2025 | 2024 | 2024-04-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.97431 | 0.97431 | 0.99931 | 0 | 0.6 | 0.6 | Turbine attending for project pending work | Open | 0.023077 |  |  |  | WTG Breakdown Maintenance |  | 0
56 | 2024-04-20 | 2025 | 2024 | 2024-04-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.97431 | 0.97431 | 0.99931 | 0 | 0.6 | 0.6 | Turbine attending for project pending work | Open | 0.023077 |  |  |  | WTG Breakdown Maintenance |  | 0
57 | 2024-04-20 | 2025 | 2024 | 2024-04-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.97431 | 0.97431 | 0.99931 | 0 | 0.6 | 0.6 | Turbine attending for project pending work | Open | 0.023077 |  |  |  | WTG Breakdown Maintenance |  | 0
58 | 2024-04-21 | 2025 | 2024 | 2024-04-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
59 | 2024-04-21 | 2025 | 2024 | 2024-04-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
60 | 2024-04-21 | 2025 | 2024 | 2024-04-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
61 | 2024-04-21 | 2025 | 2024 | 2024-04-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
62 | 2024-04-21 | 2025 | 2024 | 2024-04-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
63 | 2024-04-21 | 2025 | 2024 | 2024-04-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
64 | 2024-04-21 | 2025 | 2024 | 2024-04-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
65 | 2024-04-21 | 2025 | 2024 | 2024-04-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
66 | 2024-04-21 | 2025 | 2024 | 2024-04-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
67 | 2024-04-22 | 2025 | 2024 | 2024-04-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
68 | 2024-04-22 | 2025 | 2024 | 2024-04-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
69 | 2024-04-22 | 2025 | 2024 | 2024-04-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
70 | 2024-04-22 | 2025 | 2024 | 2024-04-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
71 | 2024-04-22 | 2025 | 2024 | 2024-04-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
72 | 2024-04-22 | 2025 | 2024 | 2024-04-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
73 | 2024-04-22 | 2025 | 2024 | 2024-04-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
74 | 2024-04-22 | 2025 | 2024 | 2024-04-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
75 | 2024-04-22 | 2025 | 2024 | 2024-04-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
76 | 2024-04-23 | 2025 | 2024 | 2024-04-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
77 | 2024-04-23 | 2025 | 2024 | 2024-04-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
78 | 2024-04-23 | 2025 | 2024 | 2024-04-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
79 | 2024-04-23 | 2025 | 2024 | 2024-04-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
80 | 2024-04-23 | 2025 | 2024 | 2024-04-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
81 | 2024-04-23 | 2025 | 2024 | 2024-04-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
82 | 2024-04-23 | 2025 | 2024 | 2024-04-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
83 | 2024-04-23 | 2025 | 2024 | 2024-04-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
84 | 2024-04-23 | 2025 | 2024 | 2024-04-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
85 | 2024-04-24 | 2025 | 2024 | 2024-04-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
86 | 2024-04-24 | 2025 | 2024 | 2024-04-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
87 | 2024-04-24 | 2025 | 2024 | 2024-04-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
88 | 2024-04-24 | 2025 | 2024 | 2024-04-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
89 | 2024-04-24 | 2025 | 2024 | 2024-04-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
90 | 2024-04-24 | 2025 | 2024 | 2024-04-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
91 | 2024-04-24 | 2025 | 2024 | 2024-04-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
92 | 2024-04-24 | 2025 | 2024 | 2024-04-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
93 | 2024-04-24 | 2025 | 2024 | 2024-04-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
94 | 2024-04-25 | 2025 | 2024 | 2024-04-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
95 | 2024-04-25 | 2025 | 2024 | 2024-04-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
96 | 2024-04-25 | 2025 | 2024 | 2024-04-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
97 | 2024-04-25 | 2025 | 2024 | 2024-04-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
98 | 2024-04-25 | 2025 | 2024 | 2024-04-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
99 | 2024-04-25 | 2025 | 2024 | 2024-04-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
100 | 2024-04-25 | 2025 | 2024 | 2024-04-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
101 | 2024-04-25 | 2025 | 2024 | 2024-04-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
102 | 2024-04-25 | 2025 | 2024 | 2024-04-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
103 | 2024-04-26 | 2025 | 2024 | 2024-04-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
104 | 2024-04-26 | 2025 | 2024 | 2024-04-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
105 | 2024-04-26 | 2025 | 2024 | 2024-04-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
106 | 2024-04-26 | 2025 | 2024 | 2024-04-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
107 | 2024-04-26 | 2025 | 2024 | 2024-04-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
108 | 2024-04-26 | 2025 | 2024 | 2024-04-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
109 | 2024-04-26 | 2025 | 2024 | 2024-04-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
110 | 2024-04-26 | 2025 | 2024 | 2024-04-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
111 | 2024-04-26 | 2025 | 2024 | 2024-04-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
112 | 2024-04-27 | 2025 | 2024 | 2024-04-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
113 | 2024-04-27 | 2025 | 2024 | 2024-04-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
114 | 2024-04-27 | 2025 | 2024 | 2024-04-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
115 | 2024-04-27 | 2025 | 2024 | 2024-04-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
116 | 2024-04-27 | 2025 | 2024 | 2024-04-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
117 | 2024-04-27 | 2025 | 2024 | 2024-04-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
118 | 2024-04-27 | 2025 | 2024 | 2024-04-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
119 | 2024-04-27 | 2025 | 2024 | 2024-04-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
120 | 2024-04-27 | 2025 | 2024 | 2024-04-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
121 | 2024-04-28 | 2025 | 2024 | 2024-04-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
122 | 2024-04-28 | 2025 | 2024 | 2024-04-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
123 | 2024-04-28 | 2025 | 2024 | 2024-04-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
124 | 2024-04-28 | 2025 | 2024 | 2024-04-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
125 | 2024-04-28 | 2025 | 2024 | 2024-04-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
126 | 2024-04-28 | 2025 | 2024 | 2024-04-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
127 | 2024-04-28 | 2025 | 2024 | 2024-04-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
128 | 2024-04-28 | 2025 | 2024 | 2024-04-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
129 | 2024-04-28 | 2025 | 2024 | 2024-04-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
130 | 2024-04-29 | 2025 | 2024 | 2024-04-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
131 | 2024-04-29 | 2025 | 2024 | 2024-04-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
132 | 2024-04-29 | 2025 | 2024 | 2024-04-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
133 | 2024-04-29 | 2025 | 2024 | 2024-04-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
134 | 2024-04-29 | 2025 | 2024 | 2024-04-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
135 | 2024-04-29 | 2025 | 2024 | 2024-04-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
136 | 2024-04-29 | 2025 | 2024 | 2024-04-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
137 | 2024-04-29 | 2025 | 2024 | 2024-04-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
138 | 2024-04-29 | 2025 | 2024 | 2024-04-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 |  |  |  | WTG Breakdown Maintenance |  | 0
139 | 2024-04-30 | 2025 | 2024 | 2024-04-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.50625 | 0 | 12.15 | 12.15 | Turbine and USS attending for project pending work | Open | 0.46731 |  |  |  | WTG Breakdown Maintenance |  | 0
140 | 2024-04-30 | 2025 | 2024 | 2024-04-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.50625 | 0 | 12.15 | 12.15 | Turbine and USS attending for project pending work | Open | 0.46731 |  |  |  | WTG Breakdown Maintenance |  | 0
141 | 2024-04-30 | 2025 | 2024 | 2024-04-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.50625 | 0 | 12.15 | 12.15 | Turbine and USS attending for project pending work | Open | 0.46731 |  |  |  | WTG Breakdown Maintenance |  | 0
142 | 2024-04-30 | 2025 | 2024 | 2024-04-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.50625 | 0 | 12.15 | 12.15 | Turbine and USS attending for project pending work | Open | 0.46731 |  |  |  | WTG Breakdown Maintenance |  | 0
143 | 2024-04-30 | 2025 | 2024 | 2024-04-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.50625 | 0 | 12.15 | 12.15 | Turbine and USS attending for project pending work | Open | 0.46731 |  |  |  | WTG Breakdown Maintenance |  | 0
144 | 2024-04-30 | 2025 | 2024 | 2024-04-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.50625 | 0 | 12.15 | 12.15 | Turbine and USS attending for project pending work | Open | 0.46731 |  |  |  | WTG Breakdown Maintenance |  | 0
145 | 2024-04-30 | 2025 | 2024 | 2024-04-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.50625 | 0 | 12.15 | 12.15 | Turbine and USS attending for project pending work | Open | 0.46731 |  |  |  | WTG Breakdown Maintenance |  | 0
146 | 2024-04-30 | 2025 | 2024 | 2024-04-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.50625 | 0 | 12.15 | 12.15 | Turbine and USS attending for project pending work | Open | 0.46731 |  |  |  | WTG Breakdown Maintenance |  | 0
147 | 2024-04-30 | 2025 | 2024 | 2024-04-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.50625 | 0 | 12.15 | 12.15 | Turbine and USS attending for project pending work | Open | 0.46731 |  |  |  | WTG Breakdown Maintenance |  | 0
148 | 2024-04-30 | 2025 | 2024 | 2024-04-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.52014 | 0.52014 | 0.68611 | 0 | 3.9833 | 3.9833 | Turbine and USS attending for project pending work | Open | 0.15321 |  |  |  | WTG Breakdown Maintenance |  | 0
149 | 2024-04-30 | 2025 | 2024 | 2024-04-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.52014 | 0.52014 | 0.68611 | 0 | 3.9833 | 3.9833 | Turbine and USS attending for project pending work | Open | 0.15321 |  |  |  | WTG Breakdown Maintenance |  | 0
150 | 2024-04-30 | 2025 | 2024 | 2024-04-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.52014 | 0.52014 | 0.68611 | 0 | 3.9833 | 3.9833 | Turbine and USS attending for project pending work | Open | 0.15321 |  |  |  | WTG Breakdown Maintenance |  | 0
151 | 2024-04-30 | 2025 | 2024 | 2024-04-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.52014 | 0.52014 | 0.68611 | 0 | 3.9833 | 3.9833 | Turbine and USS attending for project pending work | Open | 0.15321 |  |  |  | WTG Breakdown Maintenance |  | 0
152 | 2024-04-30 | 2025 | 2024 | 2024-04-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.52014 | 0.52014 | 0.68611 | 0 | 3.9833 | 3.9833 | Turbine and USS attending for project pending work | Open | 0.15321 |  |  |  | WTG Breakdown Maintenance |  | 0
153 | 2024-04-30 | 2025 | 2024 | 2024-04-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.52014 | 0.52014 | 0.68611 | 0 | 3.9833 | 3.9833 | Turbine and USS attending for project pending work | Open | 0.15321 |  |  |  | WTG Breakdown Maintenance |  | 0
154 | 2024-04-30 | 2025 | 2024 | 2024-04-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.52014 | 0.52014 | 0.68611 | 0 | 3.9833 | 3.9833 | Turbine and USS attending for project pending work | Open | 0.15321 |  |  |  | WTG Breakdown Maintenance |  | 0
155 | 2024-04-30 | 2025 | 2024 | 2024-04-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.52014 | 0.52014 | 0.68611 | 0 | 3.9833 | 3.9833 | Turbine and USS attending for project pending work | Open | 0.15321 |  |  |  | WTG Breakdown Maintenance |  | 0
156 | 2024-04-30 | 2025 | 2024 | 2024-04-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.52014 | 0.52014 | 0.68611 | 0 | 3.9833 | 3.9833 | Turbine and USS attending for project pending work | Open | 0.15321 |  |  |  | WTG Breakdown Maintenance |  | 0
157 | 2024-04-30 | 2025 | 2024 | 2024-04-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.76111 | 0.76111 | 0.99931 | 0 | 5.7167 | 5.7167 | Turbine and USS attending for project pending work | Open | 0.21987 |  |  |  | WTG Breakdown Maintenance |  | 0
158 | 2024-04-30 | 2025 | 2024 | 2024-04-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.76111 | 0.76111 | 0.99931 | 0 | 5.7167 | 5.7167 | Turbine and USS attending for project pending work | Open | 0.21987 |  |  |  | WTG Breakdown Maintenance |  | 0
159 | 2024-04-30 | 2025 | 2024 | 2024-04-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.76111 | 0.76111 | 0.99931 | 0 | 5.7167 | 5.7167 | Turbine and USS attending for project pending work | Open | 0.21987 |  |  |  | WTG Breakdown Maintenance |  | 0
160 | 2024-04-30 | 2025 | 2024 | 2024-04-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.76111 | 0.76111 | 0.99931 | 0 | 5.7167 | 5.7167 | Turbine and USS attending for project pending work | Open | 0.21987 |  |  |  | WTG Breakdown Maintenance |  | 0
161 | 2024-04-30 | 2025 | 2024 | 2024-04-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.76111 | 0.76111 | 0.99931 | 0 | 5.7167 | 5.7167 | Turbine and USS attending for project pending work | Open | 0.21987 |  |  |  | WTG Breakdown Maintenance |  | 0
162 | 2024-04-30 | 2025 | 2024 | 2024-04-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.76111 | 0.76111 | 0.99931 | 0 | 5.7167 | 5.7167 | Turbine and USS attending for project pending work | Open | 0.21987 |  |  |  | WTG Breakdown Maintenance |  | 0
163 | 2024-04-30 | 2025 | 2024 | 2024-04-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.76111 | 0.76111 | 0.99931 | 0 | 5.7167 | 5.7167 | Turbine and USS attending for project pending work | Open | 0.21987 |  |  |  | WTG Breakdown Maintenance |  | 0
164 | 2024-04-30 | 2025 | 2024 | 2024-04-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.76111 | 0.76111 | 0.99931 | 0 | 5.7167 | 5.7167 | Turbine and USS attending for project pending work | Open | 0.21987 |  |  |  | WTG Breakdown Maintenance |  | 0
165 | 2024-04-30 | 2025 | 2024 | 2024-04-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.76111 | 0.76111 | 0.99931 | 0 | 5.7167 | 5.7167 | Turbine and USS attending for project pending work | Open | 0.21987 |  |  |  | WTG Breakdown Maintenance |  | 0
166 | 2024-05-01 | 2025 | 2024 | 2024-05-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.67569 | 0 | 16.2167 | 16.2167 | Turbine and USS attending for project pending work | Open | 0.62372 |  |  |  | WTG Breakdown Maintenance |  | 0
167 | 2024-05-01 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.67569 | 0 | 16.2167 | 16.2167 | Turbine and USS attending for project pending work | Open | 0.62372 |  |  |  | WTG Breakdown Maintenance |  | 0
168 | 2024-05-01 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.67569 | 0 | 16.2167 | 16.2167 | Turbine and USS attending for project pending work | Open | 0.62372 |  |  |  | WTG Breakdown Maintenance |  | 0
169 | 2024-05-01 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.67569 | 0 | 16.2167 | 16.2167 | Turbine and USS attending for project pending work | Open | 0.62372 |  |  |  | WTG Breakdown Maintenance |  | 0
170 | 2024-05-01 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.67569 | 0 | 16.2167 | 16.2167 | Turbine and USS attending for project pending work | Open | 0.62372 |  |  |  | WTG Breakdown Maintenance |  | 0
171 | 2024-05-01 | 2025 | 2024 | 2024-05-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.67569 | 0 | 16.2167 | 16.2167 | Turbine and USS attending for project pending work | Open | 0.62372 |  |  |  | WTG Breakdown Maintenance |  | 0
172 | 2024-05-01 | 2025 | 2024 | 2024-05-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.67569 | 0 | 16.2167 | 16.2167 | Turbine and USS attending for project pending work | Open | 0.62372 |  |  |  | WTG Breakdown Maintenance |  | 0
173 | 2024-05-01 | 2025 | 2024 | 2024-05-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.67569 | 0 | 16.2167 | 16.2167 | Turbine and USS attending for project pending work | Open | 0.62372 |  |  |  | WTG Breakdown Maintenance |  | 0
174 | 2024-05-01 | 2025 | 2024 | 2024-05-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.67569 | 0 | 16.2167 | 16.2167 | Turbine and USS attending for project pending work | Open | 0.62372 |  |  |  | WTG Breakdown Maintenance |  | 0
175 | 2024-05-01 | 2025 | 2024 | 2024-05-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.79514 | 0.79514 | 0.99931 | 0 | 4.9 | 4.9 | Turbine and USS attending for project pending work | Open | 0.18846 |  |  |  | WTG Breakdown Maintenance |  | 0
176 | 2024-05-01 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.79514 | 0.79514 | 0.99931 | 0 | 4.9 | 4.9 | Turbine and USS attending for project pending work | Open | 0.18846 |  |  |  | WTG Breakdown Maintenance |  | 0
177 | 2024-05-01 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.79514 | 0.79514 | 0.99931 | 0 | 4.9 | 4.9 | Turbine and USS attending for project pending work | Open | 0.18846 |  |  |  | WTG Breakdown Maintenance |  | 0
178 | 2024-05-01 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.79514 | 0.79514 | 0.99931 | 0 | 4.9 | 4.9 | Turbine and USS attending for project pending work | Open | 0.18846 |  |  |  | WTG Breakdown Maintenance |  | 0
179 | 2024-05-01 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.79514 | 0.79514 | 0.99931 | 0 | 4.9 | 4.9 | Turbine and USS attending for project pending work | Open | 0.18846 |  |  |  | WTG Breakdown Maintenance |  | 0
180 | 2024-05-01 | 2025 | 2024 | 2024-05-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.79514 | 0.79514 | 0.99931 | 0 | 4.9 | 4.9 | Turbine and USS attending for project pending work | Open | 0.18846 |  |  |  | WTG Breakdown Maintenance |  | 0
181 | 2024-05-01 | 2025 | 2024 | 2024-05-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.79514 | 0.79514 | 0.99931 | 0 | 4.9 | 4.9 | Turbine and USS attending for project pending work | Open | 0.18846 |  |  |  | WTG Breakdown Maintenance |  | 0
182 | 2024-05-01 | 2025 | 2024 | 2024-05-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.79514 | 0.79514 | 0.99931 | 0 | 4.9 | 4.9 | Turbine and USS attending for project pending work | Open | 0.18846 |  |  |  | WTG Breakdown Maintenance |  | 0
183 | 2024-05-01 | 2025 | 2024 | 2024-05-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.79514 | 0.79514 | 0.99931 | 0 | 4.9 | 4.9 | Turbine and USS attending for project pending work | Open | 0.18846 |  |  |  | WTG Breakdown Maintenance |  | 0
184 | 2024-05-02 | 2025 | 2024 | 2024-05-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 | O2_15 | 2602.1917 |  | WTG Breakdown Maintenance | 2604 | 2602.1917
185 | 2024-05-02 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 | O2_15 | 2602.1917 |  | WTG Breakdown Maintenance | 2604 | 2602.1917
186 | 2024-05-02 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 | O2_15 | 2602.1917 |  | WTG Breakdown Maintenance | 2604 | 2602.1917
187 | 2024-05-02 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 | O2_13 | 1398.0285 |  | WTG Breakdown Maintenance | 1399 | 1398.0285
188 | 2024-05-02 | 2025 | 2024 | 2024-05-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 | O2_15 | 2602.1917 |  | WTG Breakdown Maintenance | 2604 | 2602.1917
189 | 2024-05-02 | 2025 | 2024 | 2024-05-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 | O2_20 | 2213.4618 |  | WTG Breakdown Maintenance | 2215 | 2213.4618
190 | 2024-05-02 | 2025 | 2024 | 2024-05-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.74236 | 0 | 17.8167 | 17.8167 | Turbine and USS attending for project pending work | Open | 0.68526 | O2_15 | 1933.1083 |  | WTG Breakdown Maintenance | 2604 | 1933.1083
191 | 2024-05-02 | 2025 | 2024 | 2024-05-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.64931 | 0 | 15.5833 | 15.5833 | Turbine and USS attending for project pending work | Open | 0.59936 | O2_20 | 1438.2118 |  | WTG Breakdown Maintenance | 2215 | 1438.2118
192 | 2024-05-02 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.77083 | 0 | 18.5 | 18.5 | Turbine and USS attending for project pending work | Open | 0.71154 | O2_15 | 2007.25 |  | WTG Breakdown Maintenance | 2604 | 2007.25
193 | 2024-05-02 | 2025 | 2024 | 2024-05-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 2687 | Break down | Auto reset | 0.89306 | 0.89306 | 0.90486 | 0 | 0.28333 | 0.28333 | Auto reset | Close | 0.010897 | O2_15 | 30.7417 |  | WTG Unscheduled Maintenance | 2604 | 30.7417
194 | 2024-05-02 | 2025 | 2024 | 2024-05-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 2687 | Break down | Auto reset | 0.85486 | 0.85486 | 0.87569 | 0 | 0.5 | 0.5 | Auto reset | Close | 0.019231 | O2_13 | 29.1458 |  | WTG Unscheduled Maintenance | 1399 | 29.1458
195 | 2024-05-02 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 2687 | Break down | Auto reset | 0.92708 | 0.92708 | 0.95625 | 0 | 0.7 | 0.7 | Auto reset | Close | 0.026923 | O2_15 | 75.95 |  | WTG Unscheduled Maintenance | 2604 | 75.95
196 | 2024-05-03 | 2025 | 2024 | 2024-05-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.63264 | 0 | 15.1833 | 15.1833 | Turbine and USS attending for project pending work | Open | 0.58397 | O2_15 | 2613.4313 |  | WTG Breakdown Maintenance | 4131 | 2613.4313
197 | 2024-05-03 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.63264 | 0 | 15.1833 | 15.1833 | Turbine and USS attending for project pending work | Open | 0.58397 | O2_15 | 2613.4313 |  | WTG Breakdown Maintenance | 4131 | 2613.4313
198 | 2024-05-03 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.63264 | 0 | 15.1833 | 15.1833 | Turbine and USS attending for project pending work | Open | 0.58397 | O2_15 | 2613.4313 |  | WTG Breakdown Maintenance | 4131 | 2613.4313
199 | 2024-05-03 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.63264 | 0 | 15.1833 | 15.1833 | Turbine and USS attending for project pending work | Open | 0.58397 | O2_13 | 4378.4937 |  | WTG Breakdown Maintenance | 6921 | 4378.4937
200 | 2024-05-03 | 2025 | 2024 | 2024-05-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.63264 | 0 | 15.1833 | 15.1833 | Turbine and USS attending for project pending work | Open | 0.58397 | O2_15 | 2613.4313 |  | WTG Breakdown Maintenance | 4131 | 2613.4313
201 | 2024-05-03 | 2025 | 2024 | 2024-05-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.63264 | 0 | 15.1833 | 15.1833 | Turbine and USS attending for project pending work | Open | 0.58397 | O2_20 | 6003.1104 |  | WTG Breakdown Maintenance | 9489 | 6003.1104
202 | 2024-05-03 | 2025 | 2024 | 2024-05-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.72222 | 0.72222 | 0.99931 | 0 | 6.65 | 6.65 | Turbine and USS attending for project pending work | Open | 0.25577 | O2_15 | 1144.6313 |  | WTG Breakdown Maintenance | 4131 | 1144.6313
203 | 2024-05-03 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.72222 | 0.72222 | 0.99931 | 0 | 6.65 | 6.65 | Turbine and USS attending for project pending work | Open | 0.25577 | O2_15 | 1144.6313 |  | WTG Breakdown Maintenance | 4131 | 1144.6313
204 | 2024-05-03 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.72222 | 0.72222 | 0.99931 | 0 | 6.65 | 6.65 | Turbine and USS attending for project pending work | Open | 0.25577 | O2_13 | 1917.6938 |  | WTG Breakdown Maintenance | 6921 | 1917.6938
205 | 2024-05-03 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.72222 | 0.72222 | 0.99931 | 0 | 6.65 | 6.65 | Turbine and USS attending for project pending work | Open | 0.25577 | O2_13 | 1917.6938 |  | WTG Breakdown Maintenance | 6921 | 1917.6938
206 | 2024-05-03 | 2025 | 2024 | 2024-05-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.72222 | 0.72222 | 0.99931 | 0 | 6.65 | 6.65 | Turbine and USS attending for project pending work | Open | 0.25577 | O2_15 | 1144.6313 |  | WTG Breakdown Maintenance | 4131 | 1144.6313
207 | 2024-05-03 | 2025 | 2024 | 2024-05-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.72222 | 0.72222 | 0.99931 | 0 | 6.65 | 6.65 | Turbine and USS attending for project pending work | Open | 0.25577 | O2_20 | 2629.2438 |  | WTG Breakdown Maintenance | 9489 | 2629.2438
208 | 2024-05-03 | 2025 | 2024 | 2024-05-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.48403 | 0.48403 | 0.52986 | 0 | 1.1 | 1.1 | Turbine attended by senvion project pending work | Close | 0.042308 | O2_15 | 189.3375 |  | WTG Breakdown Maintenance | 4131 | 189.3375
209 | 2024-05-03 | 2025 | 2024 | 2024-05-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 2687 | Break down | Auto reset | 0.56319 | 0.56319 | 0.60347 | 0 | 0.96667 | 0.96667 | Auto reset | Close | 0.037179 | O2_15 | 166.3875 |  | WTG Unscheduled Maintenance | 4131 | 166.3875
210 | 2024-05-03 | 2025 | 2024 | 2024-05-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 2687 | Break down | Auto reset | 0.85 | 0.85 | 0.87917 | 0 | 0.7 | 0.7 | Auto reset | Close | 0.026923 | O2_15 | 120.4875 |  | WTG Unscheduled Maintenance | 4131 | 120.4875
211 | 2024-05-03 | 2025 | 2024 | 2024-05-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.44514 | 0.44514 | 0.53542 | 0 | 2.1667 | 2.1667 | Turbine attended by senvion project pending work | Close | 0.083333 | O2_13 | 624.8125 |  | WTG Breakdown Maintenance | 6921 | 624.8125
212 | 2024-05-03 | 2025 | 2024 | 2024-05-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3095 | Break down | Major BD | 0.72222 | 0.72222 | 0.99931 | 0 | 6.65 | 6.65 | Turbine not started due to offline | Open | 0.25577 | O2_13 | 1144.6313 |  | WTG Unscheduled Maintenance | 4131 | 1144.6313
213 | 2024-05-03 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.48125 | 0.48125 | 0.51806 | 0 | 0.88333 | 0.88333 | Turbine attended by senvion project pending work | Open | 0.033974 | O2_15 | 152.0438 |  | WTG Breakdown Maintenance | 4131 | 152.0438
214 | 2024-05-03 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 2687 | Break down | Auto reset | 0.58819 | 0.58819 | 0.61806 | 0 | 0.71667 | 0.71667 | Auto reset | Close | 0.027564 | O2_15 | 123.3563 |  | WTG Unscheduled Maintenance | 4131 | 123.3563
215 | 2024-05-03 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 2687 | Break down | Auto reset | 0.88472 | 0.88472 | 0.90833 | 0 | 0.56667 | 0.56667 | Auto reset | Close | 0.021795 | O2_15 | 97.5375 |  | WTG Unscheduled Maintenance | 4131 | 97.5375
216 | 2024-05-04 | 2025 | 2024 | 2024-05-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 | O2_20 | 21715.909 |  | WTG Breakdown Maintenance | 21731 | 21715.909
217 | 2024-05-04 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 | O2_20 | 21715.909 |  | WTG Breakdown Maintenance | 21731 | 21715.909
218 | 2024-05-04 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 | O2_20 | 21715.909 |  | WTG Breakdown Maintenance | 21731 | 21715.909
219 | 2024-05-04 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 | O2_20 | 21715.909 |  | WTG Breakdown Maintenance | 21731 | 21715.909
220 | 2024-05-04 | 2025 | 2024 | 2024-05-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 | O2_13 | 11699.8694 |  | WTG Breakdown Maintenance | 11708 | 11699.8694
221 | 2024-05-04 | 2025 | 2024 | 2024-05-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine and USS attending for project pending work | Open | 0.92244 | O2_13 | 11699.8694 |  | WTG Breakdown Maintenance | 11708 | 11699.8694
222 | 2024-05-04 | 2025 | 2024 | 2024-05-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3095 | Break down | Break down | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine not attended due to senvion security ROW | Open | 0.92244 | O2_13 | 11699.8694 |  | WTG Unscheduled Maintenance | 11708 | 11699.8694
223 | 2024-05-04 | 2025 | 2024 | 2024-05-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 3804 | Break down | Break down | 0.65208 | 0.65208 | 0.76319 | 0 | 2.6667 | 2.6667 | Checked and found USS VCB tripped in O/C then checked and found deviation in relay setting then corrected setting and charged VCB | Close | 0.10256 | O2_13 | 1300.8889 |  | WTG Unscheduled Maintenance | 11708 | 1300.8889
224 | 2024-05-05 | 2025 | 2024 | 2024-05-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 826 | Break down | Major BD | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | RPM sensor error troubleshooting WIP | Open | 0.92244 | O2_14 | 2431.3104 |  | WTG Unscheduled Maintenance | 2433 | 2431.3104
225 | 2024-05-05 | 2025 | 2024 | 2024-05-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine stopped by senvion project team for punch point closing | Open | 0.92244 | O2_20 | 26372.6729 |  | WTG Breakdown Maintenance | 26391 | 26372.6729
226 | 2024-05-05 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine stopped by senvion project team for punch point closing | Open | 0.92244 | O2_13 | 16063.8368 |  | WTG Breakdown Maintenance | 16075 | 16063.8368
227 | 2024-05-05 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine stopped by senvion project team for punch point closing | Open | 0.92244 | O2_15 | 5635.084 |  | WTG Breakdown Maintenance | 5639 | 5635.084
228 | 2024-05-05 | 2025 | 2024 | 2024-05-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | CE100001 | Break down | Break down | 0 | 0 | 0.49653 | 0 | 11.9167 | 11.9167 | Turbine stopped by senvion project team for punch point closing and due to senvion security ROW turbine not restored | Open | 0.45833 | O2_15 | 2799.9201 |  | WTG Unscheduled Maintenance | 5639 | 2799.9201
229 | 2024-05-05 | 2025 | 2024 | 2024-05-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 6505 | Break down | Break down | 0.59931 | 0.59931 | 0.77778 | 0 | 4.2833 | 4.2833 | Wind sensor alignment done and started turbine | Close | 0.16474 | O2_15 | 1006.4049 |  | WTG Unscheduled Maintenance | 5639 | 1006.4049
230 | 2024-05-05 | 2025 | 2024 | 2024-05-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 675 | Break down | Break down | 0.9375 | 0.99931 | 0.99931 | 1.4833 | 0 | 1.4833 | Data analysis WIP | Open | 0.057051 | O2_15 | 348.5215 |  | WTG Unscheduled Maintenance | 5639 | 348.5215
231 | 2024-05-05 | 2025 | 2024 | 2024-05-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 696 | Break down | Break down | 0.63264 | 0.63264 | 0.66667 | 0 | 0.81667 | 0.81667 | Checked data then reset | Close | 0.03141 | O2_16 | 898.0271 |  | WTG Unscheduled Maintenance | 26391 | 898.0271
232 | 2024-05-05 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.72639 | 0 | 17.4333 | 17.4333 | Turbine stopped by senvion project team for punch point closing and due to senvion security ROW turbine not restored | Open | 0.67051 | O2_15 | 4096.1069 |  | WTG Breakdown Maintenance | 5639 | 4096.1069
233 | 2024-05-05 | 2025 | 2024 | 2024-05-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.47917 | 0 | 11.5 | 11.5 | Turbine stopped by senvion project team for punch point closing and due to senvion security ROW turbine not restored | Open | 0.44231 | O2_14 | 1165.8125 |  | WTG Breakdown Maintenance | 2433 | 1165.8125
234 | 2024-05-05 | 2025 | 2024 | 2024-05-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 6505 | Break down | Break down | 0.625 | 0.625 | 0.77083 | 0 | 3.5 | 3.5 | Wind sensor alignment done and started turbine | Close | 0.13462 | O2_14 | 354.8125 |  | WTG Unscheduled Maintenance | 2433 | 354.8125
235 | 2024-05-06 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine stopped by senvion project team for punch point closing | Open | 0.92244 | O2_11 | 9003.7431 |  | WTG Breakdown Maintenance | 9010 | 9003.7431
236 | 2024-05-06 | 2025 | 2024 | 2024-05-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine stopped by senvion project team for punch point closing | Open | 0.92244 | O2_20 | 9003.7431 |  | WTG Breakdown Maintenance | 25565 | 25547.2465
237 | 2024-05-06 | 2025 | 2024 | 2024-05-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 826 | Break down | Major BD | 0 | 0 | 0.69444 | 0 | 16.6667 | 16.6667 | Encoder cable connector loose so correct it | Close | 0.64103 | O2_14 | 25547.2465 |  | WTG Unscheduled Maintenance | 9010 | 6256.9444
238 | 2024-05-06 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.71319 | 0.71319 | 0.82917 | 0 | 2.7833 | 2.7833 | Turbine stopped by senvion project team for punch point closing | Close | 0.10705 | O2_15 | 6256.9444 |  | WTG Breakdown Maintenance | 19937 | 2312.1382
239 | 2024-05-06 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Break down | Major BD | 0 | 0 | 0.70833 | 0 | 17 | 17 | Pitch converter Parameter updated and start | Close | 0.65385 | O2_13 | 2312.1382 |  | WTG Unscheduled Maintenance | 23344 | 16535.3333
240 | 2024-05-06 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3804 | Break down | Break down | 0.70069 | 0.70069 | 0.71875 | 0 | 0.43333 | 0.43333 | Checked and found USS VCB tripped in O/C then checked and found deviation in relay setting then corrected setting and charged VCB | Close | 0.016667 | O2_12 | 16535.3333 |  | WTG Unscheduled Maintenance | 3889 | 70.2181
241 | 2024-05-06 | 2025 | 2024 | 2024-05-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.45347 | 0.45347 | 0.60694 | 0 | 3.6833 | 3.6833 | Turbine stopped by senvion project team for punch point closing | Close | 0.14167 | O2_14 | 70.2181 |  | WTG Breakdown Maintenance | 9010 | 1382.7847
242 | 2024-05-06 | 2025 | 2024 | 2024-05-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 675 | Break down | Major BD | 0 | 0 | 0.59375 | 0 | 14.25 | 14.25 | Pitch encoder cable connection check and start | Close | 0.54808 | O2_15 | 1382.7847 |  | WTG Unscheduled Maintenance | 19937 | 11837.5938
243 | 2024-05-07 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine stopped by senvion project team for punch point closing | Open | 0.92244 | O2_15 | 11837.5938 |  | WTG Breakdown Maintenance | 10543 | 10535.6785
244 | 2024-05-07 | 2025 | 2024 | 2024-05-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine stopped by senvion project team for punch point closing | Open | 0.92244 | O2_20 | 15857.9799 |  | WTG Breakdown Maintenance | 15869 | 15857.9799
245 | 2024-05-07 | 2025 | 2024 | 2024-05-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 665 | Break down | Auto reset | 0.45903 | 0.45903 | 0.4625 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0032051 | O2_14 | 48.1389 |  | WTG Unscheduled Maintenance | 13864 | 48.1389
246 | 2024-05-07 | 2025 | 2024 | 2024-05-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 2687 | Break down | Auto reset | 0.46528 | 0.46528 | 0.48264 | 0 | 0.41667 | 0.41667 | Auto reset | Close | 0.016026 | O2_14 | 240.6944 |  | WTG Unscheduled Maintenance | 13864 | 240.6944
247 | 2024-05-07 | 2025 | 2024 | 2024-05-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 2687 | Break down | Auto reset | 0.68403 | 0.68403 | 0.69167 | 0 | 0.18333 | 0.18333 | Auto reset | Close | 0.0070513 | O2_14 | 105.9056 |  | WTG Unscheduled Maintenance | 13864 | 105.9056
248 | 2024-05-07 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6100 | Break down | Auto reset | 0.85625 | 0.85625 | 0.86042 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2_15 | 43.9292 |  | WTG Unscheduled Maintenance | 10543 | 43.9292
249 | 2024-05-07 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6120 | Break down | Auto reset | 0.87569 | 0.87569 | 0.87986 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2_15 | 43.9292 |  | WTG Unscheduled Maintenance | 10543 | 43.9292
250 | 2024-05-07 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6100 | Break down | Auto reset | 0.95278 | 0.95278 | 0.96181 | 0 | 0.21667 | 0.21667 | Auto reset | Close | 0.0083333 | O2_15 | 95.1799 |  | WTG Unscheduled Maintenance | 10543 | 95.1799
251 | 2024-05-07 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Break down | Auto reset | 0.88472 | 0.88472 | 0.88611 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2_13 | 12.5486 |  | WTG Unscheduled Maintenance | 9035 | 12.5486
252 | 2024-05-07 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 172 | Break down | Break down | 0.42639 | 0.42639 | 0.42917 | 0 | 0.066667 | 0.066667 | Checked data then reset | Close | 0.0025641 | O2_12 | 37.8889 |  | WTG Unscheduled Maintenance | 13640 | 37.8889
253 | 2024-05-07 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 172 | Break down | Break down | 0.43333 | 0.43333 | 0.44861 | 0 | 0.36667 | 0.36667 | Checked data then reset | Close | 0.014103 | O2_12 | 208.3889 |  | WTG Unscheduled Maintenance | 13640 | 208.3889
254 | 2024-05-07 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | CE100001 | Break down | Break down | 0.45903 | 0.45903 | 0.63542 | 0 | 4.2333 | 4.2333 | Attend and found rotor brake mechanical valve not not full operate so correct it and start | Close | 0.16282 | O2_12 | 2405.9444 |  | WTG Unscheduled Maintenance | 13640 | 2405.9444
255 | 2024-05-07 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 641 | Break down | Break down | 0.90069 | 0.90069 | 0.99931 | 0 | 2.3667 | 2.3667 | Blade Encoder A issue WIP | Open | 0.091026 | O2_12 | 1345.0556 |  | WTG Unscheduled Maintenance | 13640 | 1345.0556
256 | 2024-05-07 | 2025 | 2024 | 2024-05-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 2687 | Break down | Auto reset | 0.45278 | 0.45278 | 0.48194 | 0 | 0.7 | 0.7 | Auto reset | Close | 0.026923 | O2_15 | 307.5042 |  | WTG Unscheduled Maintenance | 10543 | 307.5042
257 | 2024-05-07 | 2025 | 2024 | 2024-05-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 465 | Break down | Break down | 0.81597 | 0.81597 | 0.81944 | 0 | 0.083333 | 0.083333 | Checked data then reset | Close | 0.0032051 | O2_10 | 39.2257 |  | WTG Unscheduled Maintenance | 11297 | 39.2257
258 | 2024-05-07 | 2025 | 2024 | 2024-05-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 465 | Break down | Break down | 0.87569 | 0.87569 | 0.87917 | 0 | 0.083333 | 0.083333 | Checked data then reset | Close | 0.0032051 | O2_10 | 39.2257 |  | WTG Unscheduled Maintenance | 11297 | 39.2257
259 | 2024-05-08 | 2025 | 2024 | 2024-05-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 2687 | Break down | Auto reset | 0.46806 | 0.46806 | 0.49097 | 0 | 0.55 | 0.55 | Auto reset | Close | 0.021154 | O2_15 | 436.0354 |  | WTG Unscheduled Maintenance | 19027 | 436.0354
260 | 2024-05-08 | 2025 | 2024 | 2024-05-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 2687 | Break down | Auto reset | 0.52361 | 0.52361 | 0.53958 | 0 | 0.38333 | 0.38333 | Auto reset | Close | 0.014744 | O2_15 | 303.9035 |  | WTG Unscheduled Maintenance | 19027 | 303.9035
261 | 2024-05-08 | 2025 | 2024 | 2024-05-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 665 | Break down | Break down | 0.91667 | 0.91667 | 0.97014 | 0 | 1.2833 | 1.2833 | Attend and found Overvoltage protection feedback loose so correct it | Close | 0.049359 | O2_15 | 1017.416 |  | WTG Unscheduled Maintenance | 19027 | 1017.416
262 | 2024-05-08 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 2687 | Break down | Auto reset | 0.55347 | 0.55347 | 0.56389 | 0 | 0.25 | 0.25 | Auto reset | Close | 0.0096154 | O2_12 | 215.7917 |  | WTG Unscheduled Maintenance | 20716 | 215.7917
263 | 2024-05-08 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 2687 | Break down | Auto reset | 0.64583 | 0.64583 | 0.66667 | 0 | 0.5 | 0.5 | Auto reset | Close | 0.019231 | O2_12 | 431.5833 |  | WTG Unscheduled Maintenance | 20716 | 431.5833
264 | 2024-05-08 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6120 | Break down | Auto reset | 0.64583 | 0.64583 | 0.66667 | 0 | 0.5 | 0.5 | Auto reset | Close | 0.019231 | O2_15 | 396.3958 |  | WTG Unscheduled Maintenance | 19027 | 396.3958
265 | 2024-05-08 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6120 | Break down | Auto reset | 0.21111 | 0.21111 | 0.21944 | 0 | 0.2 | 0.2 | Auto reset | Close | 0.0076923 | O2_15 | 158.5583 |  | WTG Unscheduled Maintenance | 19027 | 158.5583
266 | 2024-05-08 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6120 | Break down | Auto reset | 0.34236 | 0.34236 | 0.34653 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2_15 | 79.2792 |  | WTG Unscheduled Maintenance | 19027 | 79.2792
267 | 2024-05-08 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | CE100001 | Break down | Break down | 0.53333 | 0.53333 | 0.53958 | 0 | 0.15 | 0.15 | Attend and checked drag pressure, clean valve and filter of Hyd unit and run | Close | 0.0057692 | O2_15 | 118.9187 |  | WTG Unscheduled Maintenance | 19027 | 118.9187
268 | 2024-05-08 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6120 | Break down | Auto reset | 0.54306 | 0.54306 | 0.61875 | 0 | 1.8167 | 1.8167 | Auto reset | Close | 0.069872 | O2_15 | 1440.2382 |  | WTG Unscheduled Maintenance | 19027 | 1440.2382
269 | 2024-05-08 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 665 | Break down | Major BD | 0 | 0 | 0.85347 | 0 | 20.4833 | 20.4833 | Attend check related circuit and found Blade motor encoder failed so replace it blade calibration done and start | Close | 0.78782 | O2_12 | 17680.5306 |  | WTG Unscheduled Maintenance | 20716 | 17680.5306
270 | 2024-05-08 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Break down | Break down | 0.86458 | 0.86458 | 0.91181 | 0 | 1.1333 | 1.1333 | Converter software update and start | Close | 0.04359 | O2_12 | 978.2556 |  | WTG Unscheduled Maintenance | 20716 | 978.2556
271 | 2024-05-08 | 2025 | 2024 | 2024-05-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 2687 | Break down | Auto reset | 0.65833 | 0.65833 | 0.67708 | 0 | 0.45 | 0.45 | Auto reset | Close | 0.017308 | O2_10 | 307.5375 |  | WTG Unscheduled Maintenance | 16402 | 307.5375
272 | 2024-05-08 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine stopped by senvion project team for punch point closing | Open | 0.92244 | O2_14 | 16531.5118 |  | WTG Breakdown Maintenance | 16543 | 16531.5118
273 | 2024-05-08 | 2025 | 2024 | 2024-05-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine stopped by senvion project team for punch point closing | Open | 0.92244 | O2_20 | 23233.8542 |  | WTG Breakdown Maintenance | 23250 | 23233.8542
274 | 2024-05-09 | 2025 | 2024 | 2024-05-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 665 | Break down | Auto reset | 0.27083 | 0.27083 | 0.29167 | 0 | 0.5 | 0.5 | Auto reset | Close | 0.019231 | O2_14 | 383.1042 |  | WTG Unscheduled Maintenance | 18389 | 383.1042
275 | 2024-05-09 | 2025 | 2024 | 2024-05-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 2687 | Break down | Auto reset | 0.5 | 0.5 | 0.50764 | 0 | 0.18333 | 0.18333 | Auto reset | Close | 0.0070513 | O2_14 | 140.4715 |  | WTG Unscheduled Maintenance | 18389 | 140.4715
276 | 2024-05-09 | 2025 | 2024 | 2024-05-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 2687 | Break down | Auto reset | 0.57361 | 0.57361 | 0.59306 | 0 | 0.46667 | 0.46667 | Auto reset | Close | 0.017949 | O2_14 | 357.5639 |  | WTG Unscheduled Maintenance | 18389 | 357.5639
277 | 2024-05-09 | 2025 | 2024 | 2024-05-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 2687 | Break down | Auto reset | 0.65833 | 0.65833 | 0.67569 | 0 | 0.41667 | 0.41667 | Auto reset | Close | 0.016026 | O2_14 | 319.2535 |  | WTG Unscheduled Maintenance | 18389 | 319.2535
278 | 2024-05-09 | 2025 | 2024 | 2024-05-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 2687 | Break down | Auto reset | 0.72917 | 0.72917 | 0.75 | 0 | 0.5 | 0.5 | Auto reset | Close | 0.019231 | O2_14 | 383.1042 |  | WTG Unscheduled Maintenance | 18389 | 383.1042
279 | 2024-05-09 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 2050 | Break down | Auto reset | 0.15972 | 0.15972 | 0.17014 | 0 | 0.25 | 0.25 | Auto reset | Close | 0.0096154 | O2_15 | 194.5521 |  | WTG Unscheduled Maintenance | 18677 | 194.5521
280 | 2024-05-09 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 2050 | Break down | Auto reset | 0.70417 | 0.70417 | 0.70833 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2_15 | 77.8208 |  | WTG Unscheduled Maintenance | 18677 | 77.8208
281 | 2024-05-09 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 2050 | Break down | Auto reset | 0.76875 | 0.76875 | 0.77569 | 0 | 0.16667 | 0.16667 | Auto reset | Close | 0.0064103 | O2_15 | 129.7014 |  | WTG Unscheduled Maintenance | 18677 | 129.7014
282 | 2024-05-09 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 2050 | Break down | Auto reset | 0.8375 | 0.8375 | 0.84028 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0025641 | O2_15 | 51.8806 |  | WTG Unscheduled Maintenance | 18677 | 51.8806
283 | 2024-05-09 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6120 | Break down | Auto reset | 0.90903 | 0.90903 | 0.92292 | 0 | 0.33333 | 0.33333 | Auto reset | Close | 0.012821 | O2_15 | 259.4028 |  | WTG Unscheduled Maintenance | 18677 | 259.4028
284 | 2024-05-09 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Break down | Auto reset | 0.49028 | 0.49236 | 0.49236 | 0.05 | 0 | 0.05 | Auto reset | Close | 0.0019231 | O2_12 | 49.5646 |  | WTG Unscheduled Maintenance | 23791 | 49.5646
285 | 2024-05-09 | 2025 | 2024 | 2024-05-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 2357 | Break down | Auto reset | 0.11806 | 0.11806 | 0.12847 | 0 | 0.25 | 0.25 | Auto reset | Close | 0.0096154 | O2_15 | 194.5521 |  | WTG Unscheduled Maintenance | 18677 | 194.5521
286 | 2024-05-09 | 2025 | 2024 | 2024-05-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 2357 | Break down | Auto reset | 0.24653 | 0.24653 | 0.25347 | 0 | 0.16667 | 0.16667 | Auto reset | Close | 0.0064103 | O2_15 | 129.7014 |  | WTG Unscheduled Maintenance | 18677 | 129.7014
287 | 2024-05-09 | 2025 | 2024 | 2024-05-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 7002 | Break down | Break down | 0.47917 | 0.47917 | 0.49306 | 0 | 0.33333 | 0.33333 | Remote reset | Close | 0.012821 | O2_15 | 259.4028 |  | WTG Unscheduled Maintenance | 18677 | 259.4028
288 | 2024-05-09 | 2025 | 2024 | 2024-05-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | CE100001 | Break down | Auto reset | 0.57639 | 0.57639 | 0.65278 | 0 | 1.8333 | 1.8333 | Auto reset | Close | 0.070513 | O2_15 | 1426.7153 |  | WTG Unscheduled Maintenance | 18677 | 1426.7153
289 | 2024-05-09 | 2025 | 2024 | 2024-05-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 2687 | Break down | Auto reset | 0.64375 | 0.64375 | 0.66667 | 0 | 0.55 | 0.55 | Auto reset | Close | 0.021154 | O2_14 | 421.4146 |  | WTG Unscheduled Maintenance | 18389 | 421.4146
290 | 2024-05-09 | 2025 | 2024 | 2024-05-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 2687 | Break down | Auto reset | 0.72917 | 0.72917 | 0.75069 | 0 | 0.51667 | 0.51667 | Auto reset | Close | 0.019872 | O2_14 | 395.8743 |  | WTG Unscheduled Maintenance | 18389 | 395.8743
291 | 2024-05-09 | 2025 | 2024 | 2024-05-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 465 | Break down | Auto reset | 0.90139 | 0.90139 | 0.90347 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2_14 | 38.3104 |  | WTG Unscheduled Maintenance | 18389 | 38.3104
292 | 2024-05-09 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine stopped by senvion project team for punch point closing | Open | 0.92244 | O2_14 | 18376.2299 |  | WTG Breakdown Maintenance | 18389 | 18376.2299
293 | 2024-05-09 | 2025 | 2024 | 2024-05-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine stopped by senvion project team for punch point closing | Open | 0.92244 | O2_20 | 26463.6097 |  | WTG Breakdown Maintenance | 26482 | 26463.6097
294 | 2024-05-10 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Break down | Auto reset | 0.49167 | 0.49167 | 0.49306 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2_13 | 29.3042 |  | WTG Unscheduled Maintenance | 21099 | 29.3042
295 | 2024-05-10 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3211 | Break down | Auto reset | 0.62083 | 0.62083 | 0.62153 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | O2_13 | 14.6521 |  | WTG Unscheduled Maintenance | 21099 | 14.6521
296 | 2024-05-10 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 25 | Break down | Ladder issue | 0.83333 | 0.83333 | 0.91736 | 0 | 2.0167 | 2.0167 | WTG manual stop as per project team instruction. | Close | 0.077564 | O2_13 | 1772.9021 |  | WTG Unscheduled Maintenance | 21099 | 1772.9021
297 | 2024-05-10 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Break down | Break down | 0.97708 | 0.97708 | 0.97847 | 0 | 0.033333 | 0.033333 | Reset and started WTG. | Close | 0.0012821 | O2_13 | 29.3042 |  | WTG Unscheduled Maintenance | 21099 | 29.3042
298 | 2024-05-10 | 2025 | 2024 | 2024-05-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 3211 | Break down | Break down | 0.44097 | 0.44097 | 0.44375 | 0 | 0.066667 | 0.066667 | Reset and started WTG. | Close | 0.0025641 | O2_15 | 49.0889 |  | WTG Unscheduled Maintenance | 17672 | 49.0889
299 | 2024-05-10 | 2025 | 2024 | 2024-05-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 25 | Break down | Ladder issue | 0.83333 | 0.83333 | 0.91597 | 0 | 1.9833 | 1.9833 | WTG manual stop as per instruction of project team. | Close | 0.076282 | O2_15 | 1460.3944 |  | WTG Unscheduled Maintenance | 17672 | 1460.3944
300 | 2024-05-10 | 2025 | 2024 | 2024-05-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3061 | Break down | Break down | 0.53403 | 0.53403 | 0.53542 | 0 | 0.033333 | 0.033333 | Reset and started WTG. | Close | 0.0012821 | O2_10 | 1264.5403 |  | WTG Unscheduled Maintenance | 15302 | 21.2528
301 | 2024-05-10 | 2025 | 2024 | 2024-05-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 6012 | Break down | Break down | 0.55208 | 0.55208 | 0.72778 | 0 | 4.2167 | 4.2167 | Attend and found yaw MPCB tripped so charged it and found air in hydraulic ckt so oil building done then reset and started . | Close | 0.16218 | O2_10 | 21.2528 |  | WTG Unscheduled Maintenance | 15302 | 2688.4764
302 | 2024-05-10 | 2025 | 2024 | 2024-05-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 25 | Break down | Ladder issue | 0.85694 | 0.85694 | 0.91528 | 0 | 1.4 | 1.4 | WTG manual stop as per instruction of project team. | Close | 0.053846 | O2_10 | 2688.4764 |  | WTG Unscheduled Maintenance | 15302 | 892.6167
303 | 2024-05-10 | 2025 | 2024 | 2024-05-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 156 | Break down | Break down | 0.34931 | 0.34931 | 0.36667 | 0 | 0.41667 | 0.41667 | Reset and started WTG. | Close | 0.016026 | O2_13 | 366.3021 |  | WTG Unscheduled Maintenance | 21099 | 366.3021
304 | 2024-05-10 | 2025 | 2024 | 2024-05-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 156 | Break down | Ladder issue | 0.725 | 0.725 | 0.99931 | 0 | 6.5833 | 6.5833 | WTG manual stop as per instruction of project team. | Close | 0.25321 | O2_13 | 5419.1806 |  | WTG Unscheduled Maintenance | 21099 | 5787.5729
305 | 2024-05-10 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Break down | Break down | 0.63958 | 0.63958 | 0.64306 | 0 | 0.083333 | 0.083333 | Reset and started WTG. | Close | 0.0032051 | O2_12 | 61.3611 |  | WTG Unscheduled Maintenance | 19756 | 68.5972
306 | 2024-05-10 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6120 | Break down | Auto reset | 0.097917 | 0.097917 | 0.10486 | 0 | 0.16667 | 0.16667 | Auto reset | Close | 0.0064103 | O2_15 | 122.7222 |  | WTG Unscheduled Maintenance | 17672 | 122.7222
307 | 2024-05-10 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6130 | Break down | Break down | 0.20417 | 0.20417 | 0.21389 | 0 | 0.23333 | 0.23333 | Reset and started WTG. | Close | 0.0089744 | O2_15 | 171.8111 |  | WTG Unscheduled Maintenance | 17672 | 171.8111
308 | 2024-05-10 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6120 | Break down | Break down | 0.24444 | 0.24444 | 0.25833 | 0 | 0.33333 | 0.33333 | Reset and started WTG. | Close | 0.012821 | O2_15 | 245.4444 |  | WTG Unscheduled Maintenance | 17672 | 245.4444
309 | 2024-05-10 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6130 | Break down | Auto reset | 0.43542 | 0.43542 | 0.43958 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2_15 | 73.6333 |  | WTG Unscheduled Maintenance | 17672 | 73.6333
310 | 2024-05-10 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6120 | Break down | Auto reset | 0.45 | 0.45 | 0.45278 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0025641 | O2_15 | 49.0889 |  | WTG Unscheduled Maintenance | 17672 | 49.0889
311 | 2024-05-10 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6120 | Break down | Auto reset | 0.68611 | 0.68611 | 0.69167 | 0 | 0.13333 | 0.13333 | Auto reset | Close | 0.0051282 | O2_15 | 98.1778 |  | WTG Unscheduled Maintenance | 17672 | 98.1778
312 | 2024-05-10 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6120 | Break down | Auto reset | 0.71597 | 0.71597 | 0.73125 | 0 | 0.36667 | 0.36667 | Auto reset | Close | 0.014103 | O2_15 | 269.9889 |  | WTG Unscheduled Maintenance | 17672 | 269.9889
313 | 2024-05-10 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6120 | Break down | Auto reset | 0.77639 | 0.77639 | 0.78889 | 0 | 0.3 | 0.3 | Auto reset | Close | 0.011538 | O2_15 | 220.9 |  | WTG Unscheduled Maintenance | 17672 | 220.9
314 | 2024-05-10 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6120 | Break down | Auto reset | 0.82083 | 0.82083 | 0.82361 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0025641 | O2_15 | 49.0889 |  | WTG Unscheduled Maintenance | 17672 | 49.0889
315 | 2024-05-10 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 25 | Break down | Ladder issue | 0.83333 | 0.83333 | 0.99931 | 0 | 3.9833 | 3.9833 | WTG manual stop as per instruction of project team. | Open | 0.15321 | O2_15 | 2933.0611 |  | WTG Unscheduled Maintenance | 17672 | 2933.0611
316 | 2024-05-10 | 2025 | 2024 | 2024-05-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 665 | Break down | Auto reset | 0.30556 | 0.30556 | 0.3125 | 0 | 0.16667 | 0.16667 | Auto reset | Open | 0.0064103 | O2_14 | 131.8819 |  | WTG Unscheduled Maintenance | 18991 | 131.8819
317 | 2024-05-10 | 2025 | 2024 | 2024-05-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 665 | Break down | Auto reset | 0.32153 | 0.32153 | 0.33958 | 0 | 0.43333 | 0.43333 | Auto reset | Close | 0.016667 | O2_14 | 342.8931 |  | WTG Unscheduled Maintenance | 18991 | 342.8931
318 | 2024-05-10 | 2025 | 2024 | 2024-05-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 665 | Break down | Auto reset | 0.34583 | 0.34583 | 0.34931 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0032051 | O2_14 | 65.941 |  | WTG Unscheduled Maintenance | 18991 | 65.941
319 | 2024-05-10 | 2025 | 2024 | 2024-05-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 665 | Break down | Auto reset | 0.36875 | 0.36875 | 0.37222 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0032051 | O2_14 | 65.941 |  | WTG Unscheduled Maintenance | 18991 | 65.941
320 | 2024-05-10 | 2025 | 2024 | 2024-05-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 665 | Break down | Break down | 0.37361 | 0.37361 | 0.56667 | 0 | 4.6333 | 4.6333 | Attend and checked & found feedback of battery cut not proper connected so correct it then reset and started WTG. | Close | 0.17821 | O2_14 | 3666.3181 |  | WTG Unscheduled Maintenance | 18991 | 3666.3181
321 | 2024-05-10 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine stopped by senvion project team for punch point closing | Open | 0.92244 | O2_14 | 18977.8118 |  | WTG Breakdown Maintenance | 18991 | 18977.8118
322 | 2024-05-10 | 2025 | 2024 | 2024-05-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine stopped by senvion project team for punch point closing | Open | 0.92244 | O2_20 | 18977.8118 |  | WTG Breakdown Maintenance | 18991 | 18977.8118
323 | 2024-05-11 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.44653 | 0 | 10.7167 | 10.7167 | Turbine stopped by senvion project team for punch point closing | Open | 0.41218 | O2_14 | 7140.4257 |  | WTG Breakdown Maintenance | 15991 | 7140.4257
324 | 2024-05-11 | 2025 | 2024 | 2024-05-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.44653 | 0 | 10.7167 | 10.7167 | Turbine stopped by senvion project team for punch point closing | Open | 0.41218 | O2_14 | 7140.4257 |  | WTG Breakdown Maintenance | 15991 | 7140.4257
325 | 2024-05-11 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.50903 | 0.50903 | 0.99931 | 0 | 11.7667 | 11.7667 | Turbine stopped by senvion project team for punch point closing | Open | 0.45256 | O2_14 | 7840.0319 |  | WTG Breakdown Maintenance | 15991 | 7840.0319
326 | 2024-05-11 | 2025 | 2024 | 2024-05-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.50903 | 0.50903 | 0.99931 | 0 | 11.7667 | 11.7667 | Turbine stopped by senvion project team for punch point closing | Open | 0.45256 | O2_14 | 7840.0319 |  | WTG Breakdown Maintenance | 15991 | 7840.0319
327 | 2024-05-11 | 2025 | 2024 | 2024-05-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 25 | Manual stop without login | Project pending work | 0 | 0 | 0.44653 | 0 | 10.7167 | 10.7167 | Turbine stopped by senvion project team for punch point closing | Open | 0.41218 | O2_13 | 6182.1771 |  | WTG Unscheduled Maintenance | 13845 | 6182.1771
328 | 2024-05-11 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 25 | Manual stop without login | Project pending work | 0 | 0 | 0.44653 | 0 | 10.7167 | 10.7167 | Turbine stopped by senvion project team for punch point closing | Open | 0.41218 | O2_15 | 6835.8938 |  | WTG Unscheduled Maintenance | 15309 | 6835.8938
329 | 2024-05-11 | 2025 | 2024 | 2024-05-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 25 | Manual stop without login | Project pending work | 0.50903 | 0.50903 | 0.99931 | 0 | 11.7667 | 11.7667 | Turbine stopped by senvion project team for punch point closing | Open | 0.45256 | O2_13 | 6787.8958 |  | WTG Unscheduled Maintenance | 13845 | 6787.8958
330 | 2024-05-11 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 25 | Manual stop without login | Project pending work | 0.50903 | 0.50903 | 0.99931 | 0 | 11.7667 | 11.7667 | Turbine stopped by senvion project team for punch point closing | Open | 0.45256 | O2_15 | 7505.6625 |  | WTG Unscheduled Maintenance | 15309 | 7505.6625
331 | 2024-05-11 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3000 | Break down | Break down | 0.34375 | 0.34375 | 0.34583 | 0 | 0.05 | 0.05 | Reset and started WTG. | Close | 0.0019231 | O2_13 | 28.8438 |  | WTG Unscheduled Maintenance | 13845 | 28.8438
332 | 2024-05-11 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 7002 | Break down | Break down | 0.52153 | 0.52153 | 0.53472 | 0 | 0.31667 | 0.31667 | Reset and started WTG. | Close | 0.012179 | O2_13 | 182.6771 |  | WTG Unscheduled Maintenance | 13845 | 182.6771
333 | 2024-05-11 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 154 | Break down | Break down | 0.61806 | 0.61806 | 0.77847 | 0 | 3.85 | 3.85 | Attend and found rpm sensor cable bend so correct it, sensor gap set proper then started WTG. | Close | 0.14808 | O2_13 | 2220.9688 |  | WTG Unscheduled Maintenance | 13845 | 2220.9688
334 | 2024-05-11 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Break down | Break down | 0.57014 | 0.57014 | 0.57361 | 0 | 0.083333 | 0.083333 | Reset and started WTG. | Close | 0.0032051 | O2_12 | 51.4306 |  | WTG Unscheduled Maintenance | 14812 | 51.4306
335 | 2024-05-11 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Break down | Break down | 0.62569 | 0.62569 | 0.64653 | 0 | 0.5 | 0.5 | Checked & analysis error related data in Scada then reset and started WG. | Close | 0.019231 | O2_12 | 308.5833 |  | WTG Unscheduled Maintenance | 14812 | 308.5833
336 | 2024-05-11 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 5510 | Break down | Break down | 0.67153 | 0.67153 | 0.67639 | 0 | 0.11667 | 0.11667 | Reset and started WTG. | Close | 0.0044872 | O2_12 | 72.0028 |  | WTG Unscheduled Maintenance | 14812 | 72.0028
337 | 2024-05-11 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Break down | Break down | 0.71806 | 0.71806 | 0.72153 | 0 | 0.083333 | 0.083333 | Reset and started WTG. | Close | 0.0032051 | O2_12 | 51.4306 |  | WTG Unscheduled Maintenance | 14812 | 51.4306
338 | 2024-05-11 | 2025 | 2024 | 2024-05-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 2687 | Break down | Auto reset | 0.58889 | 0.58889 | 0.60417 | 0 | 0.36667 | 0.36667 | Auto reset | Close | 0.014103 | O2_14 | 244.3069 |  | WTG Unscheduled Maintenance | 15991 | 244.3069
339 | 2024-05-11 | 2025 | 2024 | 2024-05-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 2687 | Break down | Auto reset | 0.71111 | 0.71111 | 0.74583 | 0 | 0.83333 | 0.83333 | Auto reset | Close | 0.032051 | O2_14 | 555.2431 |  | WTG Unscheduled Maintenance | 15991 | 555.2431
340 | 2024-05-11 | 2025 | 2024 | 2024-05-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3110 | Break down | Break down | 0.54722 | 0.54722 | 0.54861 | 0 | 0.033333 | 0.033333 | Reset and started WTG. | Close | 0.0012821 | O2_14 | 22.2097 |  | WTG Unscheduled Maintenance | 15991 | 22.2097
341 | 2024-05-11 | 2025 | 2024 | 2024-05-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 2687 | Break down | Auto reset | 0.64861 | 0.64861 | 0.66875 | 0 | 0.48333 | 0.48333 | Auto reset | Close | 0.01859 | O2_14 | 322.041 |  | WTG Unscheduled Maintenance | 15991 | 322.041
342 | 2024-05-11 | 2025 | 2024 | 2024-05-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 25 | Break down | Ladder issue | 0.66875 | 0.66875 | 0.71042 | 0 | 1 | 1 | WTG manual stop by project team for abnormality inspection in turbine. | Close | 0.038462 | O2_14 | 666.2917 |  | WTG Unscheduled Maintenance | 15991 | 666.2917
343 | 2024-05-12 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Break down | Break down | 0.33403 | 0.33403 | 0.35278 | 0 | 0.45 | 0.45 | Checked data related error in Scada then reset and started WG. | Close | 0.017308 | O2_13 | 259.5938 |  | WTG Unscheduled Maintenance | 13845 | 259.5938
344 | 2024-05-12 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Break down | Break down | 0.58264 | 0.58264 | 0.58611 | 0 | 0.083333 | 0.083333 | Reset and started WTG. | Close | 0.0032051 | O2_12 | 56.9062 |  | WTG Unscheduled Maintenance | 16389 | 56.9062
345 | 2024-05-12 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Break down | Break down | 0.64931 | 0.64931 | 0.81458 | 0 | 3.9667 | 3.9667 | Attend and checked error related cut and set power supply output properly and tight all related cut connection then take trail found ok so reset and started WTG. | Close | 0.15256 | O2_14 | 2642.9569 |  | WTG Unscheduled Maintenance | 15991 | 2642.9569
346 | 2024-05-12 | 2025 | 2024 | 2024-05-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 2687 | Break down | Auto reset | 0.69792 | 0.69792 | 0.73472 | 0 | 0.88333 | 0.88333 | Auto reset | Close | 0.033974 | O2_14 | 509.5729 |  | WTG Unscheduled Maintenance | 13845 | 509.5729
347 | 2024-05-12 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.39931 | 0 | 9.5833 | 9.5833 | Turbine stopped by senvion project team for punch point closing | Open | 0.36859 | O2_15 | 6112.9688 |  | WTG Breakdown Maintenance | 15309 | 6112.9688
348 | 2024-05-12 | 2025 | 2024 | 2024-05-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.39931 | 0 | 9.5833 | 9.5833 | Turbine stopped by senvion project team for punch point closing | Open | 0.36859 | O2_15 | 6112.9688 |  | WTG Breakdown Maintenance | 15309 | 6112.9688
349 | 2024-05-12 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.45486 | 0.45486 | 0.99931 | 0 | 13.0667 | 13.0667 | Turbine stopped by senvion project team for punch point closing | Open | 0.50256 | O2_15 | 8334.9 |  | WTG Breakdown Maintenance | 15309 | 8334.9
350 | 2024-05-12 | 2025 | 2024 | 2024-05-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.45486 | 0.45486 | 0.99931 | 0 | 13.0667 | 13.0667 | Turbine stopped by senvion project team for punch point closing | Open | 0.50256 | O2_15 | 8334.9 |  | WTG Breakdown Maintenance | 15309 | 8334.9
351 | 2024-05-12 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | CE100001 | Break down | Ladder issue | 0 | 0 | 0.39931 | 0 | 9.5833 | 9.5833 | Turbine stopped by senvion project team for critical observation | Open | 0.36859 | O2_15 | 6112.9688 |  | WTG Unscheduled Maintenance | 15309 | 6112.9688
352 | 2024-05-12 | 2025 | 2024 | 2024-05-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | CE100001 | Break down | Ladder issue | 0 | 0 | 0.39931 | 0 | 9.5833 | 9.5833 | Turbine stopped by senvion project team for critical observation | Open | 0.36859 | O2_15 | 6112.9688 |  | WTG Unscheduled Maintenance | 15309 | 6112.9688
353 | 2024-05-12 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | CE100001 | Break down | Ladder issue | 0.45486 | 0.45486 | 0.99931 | 0 | 13.0667 | 13.0667 | Turbine stopped by senvion project team for critical observation | Open | 0.50256 | O2_15 | 8334.9 |  | WTG Unscheduled Maintenance | 15309 | 8334.9
354 | 2024-05-12 | 2025 | 2024 | 2024-05-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | CE100001 | Break down | Ladder issue | 0.45486 | 0.45486 | 0.99931 | 0 | 13.0667 | 13.0667 | Turbine stopped by senvion project team for critical observation | Open | 0.50256 | O2_15 | 8334.9 |  | WTG Unscheduled Maintenance | 15309 | 8334.9
355 | 2024-05-13 | 2025 | 2024 | 2024-05-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.73264 | 0 | 17.5833 | 17.5833 | Turbine stopped by senvion project team for punch point closing | Open | 0.67628 | O2_15 | 12403.5764 |  | WTG Breakdown Maintenance | 16930 | 12403.5764
356 | 2024-05-13 | 2025 | 2024 | 2024-05-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.73264 | 0 | 17.5833 | 17.5833 | Turbine stopped by senvion project team for punch point closing | Open | 0.67628 | O2_15 | 12403.5764 |  | WTG Breakdown Maintenance | 16930 | 12403.5764
357 | 2024-05-13 | 2025 | 2024 | 2024-05-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.79583 | 0.79583 | 0.99931 | 0 | 4.8833 | 4.8833 | Turbine stopped by senvion project team for punch point closing | Close | 0.18782 | O2_15 | 3444.7847 |  | WTG Breakdown Maintenance | 16930 | 3444.7847
358 | 2024-05-13 | 2025 | 2024 | 2024-05-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0.79583 | 0.79583 | 0.99931 | 0 | 4.8833 | 4.8833 | Turbine stopped by senvion project team for punch point closing | Close | 0.18782 | O2_15 | 3444.7847 |  | WTG Breakdown Maintenance | 16930 | 3444.7847
359 | 2024-05-13 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 64 | Break down | Break down | 0.90833 | 0.90833 | 0.92778 | 0 | 0.46667 | 0.46667 | WTG stop due to high wind at site | Close | 0.017949 | O2_13 | 107.9556 |  | WTG Unscheduled Maintenance | 5552 | 107.9556
360 | 2024-05-13 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Break down | Break down | 0.49236 | 0.49236 | 0.49792 | 0 | 0.13333 | 0.13333 | Reset and started WTG. | Close | 0.0051282 | O2_14 | 100.7278 |  | WTG Unscheduled Maintenance | 18131 | 100.7278
361 | 2024-05-13 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 5550 | Break down | Break down | 0.58333 | 0.58333 | 0.60069 | 0 | 0.41667 | 0.41667 | Reset and started WTG. | Close | 0.016026 | O2_14 | 314.7743 |  | WTG Unscheduled Maintenance | 18131 | 314.7743
362 | 2024-05-13 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 5550 | Break down | Major BD | 0.62361 | 0.62361 | 0.87361 | 0 | 6 | 6 | Attend and found hydraulic oil leakage from brake calliper so replaced 2 no's hose pipe and its connector top-up hydraulic oil set oil drag pressure then reset and started WTG. | Close | 0.23077 | O2_14 | 4532.75 |  | WTG Unscheduled Maintenance | 18131 | 4532.75
363 | 2024-05-13 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 64 | Break down | Break down | 0.92292 | 0.92292 | 0.98889 | 0 | 1.5833 | 1.5833 | WTG stop due to high wind at site | Close | 0.060897 | O2_14 | 1196.1424 |  | WTG Unscheduled Maintenance | 18131 | 1196.1424
364 | 2024-05-13 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 153 | Break down | Break down | 0.98889 | 0.98889 | 0.99931 | 0 | 0.25 | 0.25 | Work continues WIP | Open | 0.0096154 | O2_14 | 188.8646 |  | WTG Unscheduled Maintenance | 18131 | 188.8646
365 | 2024-05-13 | 2025 | 2024 | 2024-05-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 3200 | Break down | Break down | 0.58403 | 0.58403 | 0.59861 | 0 | 0.35 | 0.35 | Reset and started WTG. | Close | 0.013462 | O2_15 | 246.8958 |  | WTG Unscheduled Maintenance | 16930 | 246.8958
366 | 2024-05-13 | 2025 | 2024 | 2024-05-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 1600 | Break down | Break down | 0.90833 | 0.90833 | 0.93333 | 0 | 0.6 | 0.6 | WTG stop due to high wind at site | Close | 0.023077 | O2_15 | 423.25 |  | WTG Unscheduled Maintenance | 16930 | 423.25
367 | 2024-05-13 | 2025 | 2024 | 2024-05-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 2687 | Break down | Auto reset | 0.58958 | 0.58958 | 0.60903 | 0 | 0.46667 | 0.46667 | Auto reset | Close | 0.017949 | O2_14 | 352.5472 |  | WTG Unscheduled Maintenance | 18131 | 352.5472
368 | 2024-05-13 | 2025 | 2024 | 2024-05-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 64 | Break down | Break down | 0.91042 | 0.91042 | 0.94236 | 0 | 0.76667 | 0.76667 | WTG stop due to high wind at site | Close | 0.029487 | O2_14 | 579.1847 |  | WTG Unscheduled Maintenance | 18131 | 579.1847
369 | 2024-05-13 | 2025 | 2024 | 2024-05-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 4540 | Break down | Auto reset | 0.64653 | 0.64653 | 0.65764 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | O2_14 | 201.4556 |  | WTG Unscheduled Maintenance | 18131 | 201.4556
370 | 2024-05-13 | 2025 | 2024 | 2024-05-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 1070 | Break down | Break down | 0.91042 | 0.91042 | 0.91181 | 0 | 0.033333 | 0.033333 | Reset and started WTG. | Close | 0.0012821 | O2_14 | 25.1819 |  | WTG Unscheduled Maintenance | 18131 | 25.1819
371 | 2024-05-13 | 2025 | 2024 | 2024-05-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 64 | Break down | Break down | 0.91667 | 0.91667 | 0.94375 | 0 | 0.65 | 0.65 | WTG stop due to high wind at site | Close | 0.025 | O2_14 | 491.0479 |  | WTG Unscheduled Maintenance | 18131 | 491.0479
372 | 2024-05-13 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | CE100001 | Break down | Ladder issue | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine stopped by senvion project team for Ladder Issue | Open | 0.92244 | O2_15 | 16918.2431 |  | WTG Unscheduled Maintenance | 16930 | 16918.2431
373 | 2024-05-13 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine stopped by senvion project team for punch point closing | Open | 0.92244 | O2_14 | 18118.409 |  | WTG Breakdown Maintenance | 18131 | 18118.409
374 | 2024-05-14 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | CE100001 | Break down | Ladder issue | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine stopped by senvion project team for Ladder Issue | Open | 0.92244 | O2_15 | 15125.4889 |  | WTG Unscheduled Maintenance | 15136 | 15125.4889
375 | 2024-05-14 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine stopped by senvion project team for punch point closing | Open | 0.92244 | O2_03 | 14697.7861 |  | WTG Breakdown Maintenance | 14708 | 14697.7861
376 | 2024-05-14 | 2025 | 2024 | 2024-05-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | CE100001 | Manual Stop | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine stopped by senvion project team for punch point closing | Open | 0.92244 | O2_15 | 15125.4889 |  | WTG Breakdown Maintenance | 15136 | 15125.4889
377 | 2024-05-14 | 2025 | 2024 | 2024-05-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | CE100001 | Break down | Ladder issue | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine stopped by senvion project team for Ladder Issue | Open | 0.92244 | O2_15 | 15125.4889 |  | WTG Unscheduled Maintenance | 15136 | 15125.4889
378 | 2024-05-14 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3211 | Break down | Break down | 0.36667 | 0.36667 | 0.37014 | 0 | 0.083333 | 0.083333 | Reset and started WTG. | Close | 0.0032051 | O2_03 | 51.0694 |  | WTG Unscheduled Maintenance | 14708 | 51.0694
379 | 2024-05-14 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 153 | Break down | Break down | 0.53611 | 0.53611 | 0.56806 | 0 | 0.76667 | 0.76667 | Check data then reset and start | Close | 0.029487 | O2_03 | 469.8389 |  | WTG Unscheduled Maintenance | 14708 | 469.8389
380 | 2024-05-14 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3500 | Break down | ROW issue | 0.84236 | 0.84236 | 0.99931 | 0 | 3.7667 | 3.7667 | WTG stop due to ROW issue VCB trip. | Open | 0.14487 | O2_03 | 2308.3389 |  | WTG Unscheduled Maintenance | 14708 | 2308.3389
381 | 2024-05-14 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 153 | Break down | Major BD | 0 | 0 | 0.57778 | 0 | 13.8667 | 13.8667 | Attend and found yaw limit switch activate so release limit switch and remove cable twist and set limit switch & check cw & ccw yaw then reset and started WTG. | Close | 0.53333 | O2_12 | 9956.2667 |  | WTG Unscheduled Maintenance | 17232 | 9956.2667
382 | 2024-05-14 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Break down | Break down | 0.65208 | 0.65208 | 0.66806 | 0 | 0.38333 | 0.38333 | Reset and started WTG. | Close | 0.014744 | O2_12 | 275.2333 |  | WTG Unscheduled Maintenance | 17232 | 275.2333
383 | 2024-05-14 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Break down | Break down | 0.71458 | 0.71458 | 0.72083 | 0 | 0.15 | 0.15 | Reset and started WTG. | Close | 0.0057692 | O2_12 | 107.7 |  | WTG Unscheduled Maintenance | 17232 | 107.7
384 | 2024-05-14 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3500 | Break down | ROW issue | 0.88542 | 0.88542 | 0.99931 | 0 | 2.7333 | 2.7333 | WTG stop due to ROW issue VCB trip. | Open | 0.10513 | O2_12 | 1962.5333 |  | WTG Unscheduled Maintenance | 17232 | 1962.5333
385 | 2024-05-14 | 2025 | 2024 | 2024-05-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 153 | Break down | Major BD | 0.22708 | 0.22708 | 0.56111 | 0 | 8.0167 | 8.0167 | Attend and found yaw limit switch activate so release limit switch and remove cable twist and set limit switch & check cw & ccw yaw then reset and started WTG. | Close | 0.30833 | O2_03 | 4912.8806 |  | WTG Unscheduled Maintenance | 14708 | 4912.8806
386 | 2024-05-14 | 2025 | 2024 | 2024-05-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 3500 | Break down | ROW issue | 0.85694 | 0.85694 | 0.99931 | 0 | 3.4167 | 3.4167 | WTG stop due to ROW issue VCB trip. | Open | 0.13141 | O2_03 | 2093.8472 |  | WTG Unscheduled Maintenance | 14708 | 2093.8472
387 | 2024-05-14 | 2025 | 2024 | 2024-05-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 2687 | Break down | Auto reset | 0.74236 | 0.74236 | 0.77569 | 0 | 0.8 | 0.8 | Auto reset | Close | 0.030769 | O2_14 | 295.2 |  | WTG Unscheduled Maintenance | 8856 | 295.2
388 | 2024-05-14 | 2025 | 2024 | 2024-05-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 2687 | Break down | Break down | 0.56458 | 0.56458 | 0.575 | 0 | 0.25 | 0.25 | Reset and started WTG. | Close | 0.0096154 | O2_03 | 153.2083 |  | WTG Unscheduled Maintenance | 14708 | 153.2083
389 | 2024-05-14 | 2025 | 2024 | 2024-05-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3500 | Break down | ROW issue | 0.86944 | 0.86944 | 0.99931 | 0 | 3.1167 | 3.1167 | WTG stop due to ROW issue VCB trip. | Open | 0.11987 | O2_03 | 1909.9972 |  | WTG Unscheduled Maintenance | 14708 | 1909.9972
390 | 2024-05-15 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | CE100001 | Break down | Ladder issue | 0 | 0 | 0.70694 | 0 | 16.9667 | 16.9667 | Turbine stopped by senvion project team for Ladder Issue | Open | 0.65256 | O2_03 | 3943.3361 |  | WTG Unscheduled Maintenance | 5578 | 3943.3361
391 | 2024-05-15 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | CE100001 | Break down | Ladder issue | 0 | 0 | 0.70694 | 0 | 16.9667 | 16.9667 | Turbine stopped by senvion project team for component failure | Open | 0.65256 | O2_03 | 3943.3361 |  | WTG Unscheduled Maintenance | 5578 | 3943.3361
392 | 2024-05-15 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | CE100001 | Break down | Ladder issue | 0.74306 | 0.74306 | 0.99931 | 0 | 6.15 | 6.15 | Turbine stopped by senvion project team for Ladder Issue | Open | 0.23654 | O2_03 | 1429.3625 |  | WTG Unscheduled Maintenance | 5578 | 1429.3625
393 | 2024-05-15 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | CE100001 | Break down | Ladder issue | 0.74306 | 0.74306 | 0.99931 | 0 | 6.15 | 6.15 | Turbine stopped by senvion project team for component failure | Open | 0.23654 | O2_03 | 1429.3625 |  | WTG Unscheduled Maintenance | 5578 | 1429.3625
394 | 2024-05-15 | 2025 | 2024 | 2024-05-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | CE100001 | Break down | Ladder issue | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | Turbine stopped by senvion project team for Ladder Issue | Open | 0.92244 | O2_03 | 5574.1264 |  | WTG Unscheduled Maintenance | 5578 | 5574.1264
395 | 2024-05-15 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3455 | Break down | ROW issue | 0 | 0 | 0.46736 | 0 | 11.2167 | 11.2167 | WTG stop due to ROW issue and VCB trip | Close | 0.43141 | O2_03 | 2606.9403 |  | WTG Unscheduled Maintenance | 5578 | 2606.9403
396 | 2024-05-15 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3061 | Break down | Break down | 0.52431 | 0.52431 | 0.52778 | 0 | 0.083333 | 0.083333 | Reset and started WTG. | Close | 0.0032051 | O2_03 | 19.3681 |  | WTG Unscheduled Maintenance | 5578 | 19.3681
397 | 2024-05-15 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3211 | Break down | Auto reset | 0.56389 | 0.56389 | 0.56528 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2_03 | 7.7472 |  | WTG Unscheduled Maintenance | 5578 | 7.7472
398 | 2024-05-15 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3455 | Break down | ROW issue | 0.74236 | 0.74236 | 0.99931 | 0 | 6.1667 | 6.1667 | WTG stop due to ROW issue | Open | 0.23718 | O2_03 | 1433.2361 |  | WTG Unscheduled Maintenance | 5578 | 1433.2361
399 | 2024-05-15 | 2025 | 2024 | 2024-05-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | CE100001 | Break down | Ladder issue | 0 | 0 | 0.62708 | 0 | 15.05 | 15.05 | WTG manual stop as per instruction of project team. | Close | 0.57885 | O2_03 | 3497.8708 |  | WTG Unscheduled Maintenance | 5578 | 3497.8708
400 | 2024-05-15 | 2025 | 2024 | 2024-05-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 6130 | Break down | Auto reset | 0.66319 | 0.66319 | 0.66736 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2_03 | 23.2417 |  | WTG Unscheduled Maintenance | 5578 | 23.2417
401 | 2024-05-15 | 2025 | 2024 | 2024-05-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 58 | Break down | Break down | 0.67847 | 0.67847 | 0.67986 | 0 | 0.033333 | 0.033333 | Reset and started WTG. | Close | 0.0012821 | O2_03 | 7.7472 |  | WTG Unscheduled Maintenance | 5578 | 7.7472
402 | 2024-05-15 | 2025 | 2024 | 2024-05-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 6052 | Break down | Auto reset | 0.68611 | 0.68611 | 0.6875 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2_03 | 7.7472 |  | WTG Unscheduled Maintenance | 5578 | 7.7472
403 | 2024-05-15 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3455 | Break down | ROW issue | 0 | 0 | 0.70694 | 0 | 16.9667 | 16.9667 | WTG stop due to ROW issue and VCB trip | Open | 0.65256 | O2_03 | 3943.3361 |  | WTG Unscheduled Maintenance | 5578 | 3943.3361
404 | 2024-05-15 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3455 | Break down | ROW issue | 0 | 0 | 0.70694 | 0 | 16.9667 | 16.9667 | WTG stop due to ROW issue and VCB trip | Open | 0.65256 | O2_03 | 3943.3361 |  | WTG Unscheduled Maintenance | 5578 | 3943.3361
405 | 2024-05-15 | 2025 | 2024 | 2024-05-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 3455 | Break down | ROW issue | 0.74306 | 0.74306 | 0.99931 | 0 | 6.15 | 6.15 | WTG stop due to ROW issue and VCB trip | Open | 0.23654 | O2_03 | 1429.3625 |  | WTG Unscheduled Maintenance | 5578 | 1429.3625
406 | 2024-05-15 | 2025 | 2024 | 2024-05-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 3455 | Break down | ROW issue | 0.74306 | 0.74306 | 0.99931 | 0 | 6.15 | 6.15 | WTG stop due to ROW issue and VCB trip | Open | 0.23654 | O2_03 | 1429.3625 |  | WTG Unscheduled Maintenance | 5578 | 1429.3625
407 | 2024-05-15 | 2025 | 2024 | 2024-05-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3455 | Break down | ROW issue | 0 | 0 | 0.45625 | 0 | 10.95 | 10.95 | WTG stop due to ROW issue and VCB trip | Close | 0.42115 | O2_03 | 2544.9625 |  | WTG Unscheduled Maintenance | 5578 | 2544.9625
408 | 2024-05-15 | 2025 | 2024 | 2024-05-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 153 | Break down | Break down | 0.78472 | 0.78472 | 0.85278 | 0 | 1.6333 | 1.6333 | Attend remove cable twist and start | Close | 0.062821 | O2_03 | 379.6139 |  | WTG Unscheduled Maintenance | 5578 | 379.6139
409 | 2024-05-15 | 2025 | 2024 | 2024-05-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3455 | Break down | ROW issue | 0.86944 | 0.86944 | 0.99931 | 0 | 3.1167 | 3.1167 | WTG stop due to ROW issue VCB tripped. | Open | 0.11987 | O2_03 | 724.3653 |  | WTG Unscheduled Maintenance | 5578 | 724.3653
410 | 2024-05-16 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3455 | Break down | ROW issue | 0 | 0 | 0.39792 | 0 | 9.55 | 9.55 | WTG stop due to ROW issue VCB tripped. | Close | 0.36731 | O2_16 | 3557.7729 |  | WTG Unscheduled Maintenance | 8941 | 3557.7729
411 | 2024-05-16 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3000 | Break down | Break down | 0.77569 | 0.77569 | 0.80208 | 0 | 0.63333 | 0.63333 | Reset and started WTG. | Close | 0.024359 | O2_16 | 235.9431 |  | WTG Unscheduled Maintenance | 8941 | 235.9431
412 | 2024-05-16 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3000 | Break down | Break down | 0.80347 | 0.80347 | 0.81736 | 0 | 0.33333 | 0.33333 | Reset and started WTG. | Close | 0.012821 | O2_16 | 124.1806 |  | WTG Unscheduled Maintenance | 8941 | 124.1806
413 | 2024-05-16 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3000 | Break down | Break down | 0.81875 | 0.81875 | 0.87014 | 0 | 1.2333 | 1.2333 | Converter parameter update and start | Close | 0.047436 | O2_16 | 459.4681 |  | WTG Unscheduled Maintenance | 8941 | 459.4681
414 | 2024-05-16 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 152 | Break down | Break down | 0.92014 | 0.92014 | 0.93264 | 0 | 0.3 | 0.3 | reboot controller then reset and started WTG. | Close | 0.011538 | O2_16 | 111.7625 |  | WTG Unscheduled Maintenance | 8941 | 111.7625
415 | 2024-05-16 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 152 | Break down | Break down | 0.9625 | 0.9625 | 0.99792 | 0 | 0.85 | 0.85 | Checked error related data then reset and started WTG. | Close | 0.032692 | O2_16 | 316.6604 |  | WTG Unscheduled Maintenance | 8941 | 316.6604
416 | 2024-05-16 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3455 | Break down | ROW issue | 0 | 0 | 0.39792 | 0 | 9.55 | 9.55 | WTG stop due to ROW issue VCB tripped. | Close | 0.36731 | O2_16 | 3557.7729 |  | WTG Unscheduled Maintenance | 8941 | 3557.7729
417 | 2024-05-16 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Break down | Break down | 0.81736 | 0.81736 | 0.81944 | 0 | 0.05 | 0.05 | Reset and started WTG. | Close | 0.0019231 | O2_16 | 18.6271 |  | WTG Unscheduled Maintenance | 8941 | 18.6271
418 | 2024-05-16 | 2025 | 2024 | 2024-05-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 3500 | Break down | ROW issue | 0 | 0 | 0.39792 | 0 | 9.55 | 9.55 | WTG stop due to ROW issue VCB tripped. | Close | 0.36731 | O2_16 | 3557.7729 |  | WTG Unscheduled Maintenance | 8941 | 3557.7729
419 | 2024-05-16 | 2025 | 2024 | 2024-05-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3500 | Break down | ROW issue | 0 | 0 | 0.33333 | 0 | 8 | 8 | WTG stop due to ROW issue VCB tripped. | Close | 0.30769 | O2_16 | 2980.3333 |  | WTG Unscheduled Maintenance | 8941 | 2980.3333
420 | 2024-05-16 | 2025 | 2024 | 2024-05-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3532 | Break down | Auto reset | 0.42014 | 0.42014 | 0.42083 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | O2_16 | 6.209 |  | WTG Unscheduled Maintenance | 8941 | 6.209
421 | 2024-05-16 | 2025 | 2024 | 2024-05-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | Break down | Ladder issue | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | WTG manual stop as per instruction of project team. | Open | 0.92244 | O2_16 | 8934.791 |  | WTG Unscheduled Maintenance | 8941 | 8934.791
422 | 2024-05-16 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | Break down | Ladder issue | 0 | 0 | 0.39792 | 0 | 9.55 | 9.55 | WTG manual stop as per instruction of project team. | Close | 0.36731 | O2_16 | 3557.7729 |  | WTG Unscheduled Maintenance | 8941 | 3557.7729
423 | 2024-05-16 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | Break down | Break down | 0.77569 | 0.77569 | 0.88194 | 0 | 2.55 | 2.55 | Hydraulic unit valve replaced, set pressure and start | Close | 0.098077 | O2_16 | 949.9813 |  | WTG Unscheduled Maintenance | 8941 | 949.9813
424 | 2024-05-16 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 3500 | Break down | Ladder issue | 0 | 0 | 0.39792 | 0 | 9.55 | 9.55 | WTG manual stop as per instruction of project team. | Open | 0.36731 | O2_16 | 3557.7729 |  | WTG Unscheduled Maintenance | 8941 | 3557.7729
425 | 2024-05-16 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | Break down | Ladder issue | 0.77569 | 0.77569 | 0.99931 | 0 | 5.3667 | 5.3667 | WTG manual stop as per instruction of project team. | Open | 0.20641 | O2_16 | 1999.3069 |  | WTG Unscheduled Maintenance | 8941 | 1999.3069
426 | 2024-05-16 | 2025 | 2024 | 2024-05-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 665 | Break down | Major BD | 0.10556 | 0.10556 | 0.39792 | 0 | 7.0167 | 7.0167 | work continue….. | Close | 0.26987 | O2_16 | 2614.0007 |  | WTG Unscheduled Maintenance | 8941 | 2614.0007
427 | 2024-05-16 | 2025 | 2024 | 2024-05-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 665 | Break down | Break down | 0.77569 | 0.77569 | 0.99931 | 0 | 5.3667 | 5.3667 | work continue….. | Close | 0.20641 | O2_16 | 1999.3069 |  | WTG Unscheduled Maintenance | 8941 | 1999.3069
428 | 2024-05-17 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | Break down | Ladder issue | 0 | 0 | 0.66806 | 0 | 16.0333 | 16.0333 | WTG manual stop as per instruction of project team. | Open | 0.61667 | O2_16 | 13084.5361 |  | WTG Unscheduled Maintenance | 19586 | 13084.5361
429 | 2024-05-17 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | Break down | Ladder issue | 0.81806 | 0.81806 | 0.99931 | 0 | 4.35 | 4.35 | WTG manual stop as per instruction of project team. | Open | 0.16731 | O2_16 | 3549.9625 |  | WTG Unscheduled Maintenance | 19586 | 3549.9625
430 | 2024-05-17 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3211 | Break down | Break down | 0.25972 | 0.25972 | 0.26042 | 0 | 0.016667 | 0.016667 | Reset and started WTG. | Close | 0.00064103 | O2_16 | 13.6014 |  | WTG Unscheduled Maintenance | 19586 | 13.6014
431 | 2024-05-17 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3211 | Break down | Break down | 0.3 | 0.3 | 0.30139 | 0 | 0.033333 | 0.033333 | Reset and started WTG. | Close | 0.0012821 | O2_16 | 27.2028 |  | WTG Unscheduled Maintenance | 19586 | 27.2028
432 | 2024-05-17 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 175 | Break down | Break down | 0.45903 | 0.45903 | 0.48403 | 0 | 0.6 | 0.6 | Reset and started WTG. | Close | 0.023077 | O2_16 | 489.65 |  | WTG Unscheduled Maintenance | 19586 | 489.65
433 | 2024-05-17 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | Break down | Break down | 0.61806 | 0.61806 | 0.65972 | 0 | 1 | 1 | WTG manual stop for repeated error SLC SF system monitoring (Speed HC <> SLC) error rectification work, Attend and checked & tight all related cut connection and cleaned RPM sensor then reset and started WTG. | Close | 0.038462 | O2_16 | 816.0833 |  | WTG Unscheduled Maintenance | 19586 | 816.0833
434 | 2024-05-17 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Project pending work | 0.81806 | 0.81806 | 0.99931 | 0 | 4.35 | 4.35 | WTG stop due to 33KV transmission line pole fall-down near (O2-12) WTG during heavy ran and high wind at site. | Open | 0.16731 | O2_16 | 3549.9625 |  | WTG Unscheduled Maintenance | 19586 | 3549.9625
435 | 2024-05-17 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6012 | Break down | Break down | 0.81944 | 0.81944 | 0.85694 | 0 | 0.9 | 0.9 | Attend and found Yaw motor MCB tripped so charged it then reset and started WTG. | Close | 0.034615 | O2_16 | 734.475 |  | WTG Unscheduled Maintenance | 19586 | 734.475
436 | 2024-05-17 | 2025 | 2024 | 2024-05-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 665 | Break down | Major BD | 0 | 0 | 0.55833 | 0 | 13.4 | 13.4 | Attend and replaced breaking resister then reset and started WTG. | Close | 0.51538 | O2_16 | 10935.5167 |  | WTG Unscheduled Maintenance | 19586 | 10935.5167
437 | 2024-05-17 | 2025 | 2024 | 2024-05-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3211 | Break down | Break down | 0.63194 | 0.63194 | 0.63889 | 0 | 0.16667 | 0.16667 | Reset and started WTG. | Close | 0.0064103 | O2_16 | 136.0139 |  | WTG Unscheduled Maintenance | 19586 | 136.0139
438 | 2024-05-17 | 2025 | 2024 | 2024-05-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 58 | Break down | Break down | 0.64444 | 0.64444 | 0.64861 | 0 | 0.1 | 0.1 | Reset and started WTG. | Close | 0.0038462 | O2_16 | 81.6083 |  | WTG Unscheduled Maintenance | 19586 | 81.6083
439 | 2024-05-17 | 2025 | 2024 | 2024-05-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3110 | Break down | Break down | 0.20139 | 0.20139 | 0.21319 | 0 | 0.28333 | 0.28333 | Reset and started WTG. | Close | 0.010897 | O2_16 | 231.2236 |  | WTG Unscheduled Maintenance | 19586 | 231.2236
440 | 2024-05-17 | 2025 | 2024 | 2024-05-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 6130 | Break down | Auto reset | 0.71389 | 0.71389 | 0.71806 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2_16 | 81.6083 |  | WTG Unscheduled Maintenance | 19586 | 81.6083
441 | 2024-05-17 | 2025 | 2024 | 2024-05-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | Break down | Ladder issue | 0 | 0 | 0.47917 | 0 | 11.5 | 11.5 | WTG manual stop as per instruction of project team. | Close | 0.44231 | O2_16 | 9384.9583 |  | WTG Unscheduled Maintenance | 19586 | 9384.9583
442 | 2024-05-17 | 2025 | 2024 | 2024-05-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 2687 | Break down | Break down | 0.63889 | 0.63889 | 0.64167 | 0 | 0.066667 | 0.066667 | Reset and started WTG. | Close | 0.0025641 | O2_16 | 54.4056 |  | WTG Unscheduled Maintenance | 19586 | 54.4056
443 | 2024-05-17 | 2025 | 2024 | 2024-05-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 3211 | Break down | Break down | 0.64861 | 0.64861 | 0.65 | 0 | 0.033333 | 0.033333 | Reset and started WTG. | Close | 0.0012821 | O2_16 | 27.2028 |  | WTG Unscheduled Maintenance | 19586 | 27.2028
444 | 2024-05-17 | 2025 | 2024 | 2024-05-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 665 | Break down | Break down | 0.69514 | 0.69514 | 0.69792 | 0 | 0.066667 | 0.066667 | Reset and started WTG. | Close | 0.0025641 | O2_16 | 54.4056 |  | WTG Unscheduled Maintenance | 19586 | 54.4056
445 | 2024-05-17 | 2025 | 2024 | 2024-05-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 665 | Break down | Break down | 0.7375 | 0.7375 | 0.80486 | 0 | 1.6167 | 1.6167 | Checked error related data then reset and started WTG. | Close | 0.062179 | O2_16 | 1319.3347 |  | WTG Unscheduled Maintenance | 19586 | 1319.3347
446 | 2024-05-17 | 2025 | 2024 | 2024-05-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 665 | Break down | Break down | 0.82639 | 0.82639 | 0.82917 | 0 | 0.066667 | 0.066667 | Reset and started WTG. | Close | 0.0025641 | O2_16 | 54.4056 |  | WTG Unscheduled Maintenance | 19586 | 54.4056
447 | 2024-05-18 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | Break down | Ladder issue | 0 | 0 | 0.81597 | 0 | 19.5833 | 19.5833 | WTG manual stop as per instruction of project team. | Open | 0.75321 | O2_15 | 10696.5799 |  | WTG Unscheduled Maintenance | 13109 | 10696.5799
448 | 2024-05-18 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | Break down | Ladder issue | 0.83681 | 0.83681 | 0.99931 | 0 | 3.9 | 3.9 | WTG manual stop as per instruction of project team. | Open | 0.15 | O2_15 | 2130.2125 |  | WTG Unscheduled Maintenance | 13109 | 2130.2125
449 | 2024-05-18 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Project pending work | 0 | 0 | 0.81597 | 0 | 19.5833 | 19.5833 | WTG stop due to 33KV transmission line pole fall-down near (O2-12) WTG during heavy rain and high wind at site. | Close | 0.75321 | O2_15 | 10696.5799 |  | WTG Unscheduled Maintenance | 13109 | 10696.5799
450 | 2024-05-18 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Break down | Break down | 0.83681 | 0.83681 | 0.89583 | 0 | 1.4167 | 1.4167 | Checked converter parameter, reboot converter then start | Close | 0.054487 | O2_15 | 773.7951 |  | WTG Unscheduled Maintenance | 13109 | 773.7951
451 | 2024-05-18 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Break down | Auto reset | 0.30486 | 0.30486 | 0.30833 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0032051 | O2_15 | 45.5174 |  | WTG Unscheduled Maintenance | 13109 | 45.5174
452 | 2024-05-18 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Break down | Auto reset | 0.41111 | 0.41111 | 0.41319 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2_15 | 27.3104 |  | WTG Unscheduled Maintenance | 13109 | 27.3104
453 | 2024-05-18 | 2025 | 2024 | 2024-05-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3500 | Break down | Break down | 0.86667 | 0.86667 | 0.94444 | 0 | 1.8667 | 1.8667 | VCB charged and start | Close | 0.071795 | O2_15 | 1019.5889 |  | WTG Unscheduled Maintenance | 13109 | 1019.5889
454 | 2024-05-18 | 2025 | 2024 | 2024-05-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3250 | Break down | Break down | 0.64097 | 0.64097 | 0.72222 | 0 | 1.95 | 1.95 | Converter control board connection, CAN cable connection check and start | Close | 0.075 | O2_15 | 1065.1063 |  | WTG Unscheduled Maintenance | 13109 | 1065.1063
455 | 2024-05-18 | 2025 | 2024 | 2024-05-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3250 | Break down | Break down | 0.86458 | 0.86458 | 0.91597 | 0 | 1.2333 | 1.2333 | Coolant temp data check, cooling fan check and start | Close | 0.047436 | O2_15 | 673.6569 |  | WTG Unscheduled Maintenance | 13109 | 673.6569
456 | 2024-05-18 | 2025 | 2024 | 2024-05-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 152 | Break down | Break down | 0.40486 | 0.40486 | 0.42014 | 0 | 0.36667 | 0.36667 | reboot controller then reset and started WTG. | Close | 0.014103 | O2_15 | 200.2764 |  | WTG Unscheduled Maintenance | 13109 | 200.2764
457 | 2024-05-18 | 2025 | 2024 | 2024-05-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | Break down | Major BD | 0.57153 | 0.57153 | 0.83403 | 0 | 6.3 | 6.3 | Attend check related circuit and found pitch chopper resister failed so replace it and start | Close | 0.24231 | O2_15 | 3441.1125 |  | WTG Unscheduled Maintenance | 13109 | 3441.1125
458 | 2024-05-19 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Break down | Break down | 0.47917 | 0.47917 | 0.48125 | 0 | 0.05 | 0.05 | Checked converter data log and parameter then and start the turbine. | Close | 0.0019231 | O2_10 | 80.6875 |  | WTG Unscheduled Maintenance | 38730 | 80.6875
459 | 2024-05-19 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Break down | Break down | 0.63958 | 0.63958 | 0.64236 | 0 | 0.066667 | 0.066667 | Checked converter data log and parameter then and start the turbine. | Close | 0.0025641 | O2_10 | 107.5833 |  | WTG Unscheduled Maintenance | 38730 | 107.5833
460 | 2024-05-19 | 2025 | 2024 | 2024-05-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 175 | Break down | Break down | 0.0625 | 0.0625 | 0.069444 | 0 | 0.16667 | 0.16667 | Checked SLC data log and reset the turbine. | Close | 0.0064103 | O2_10 | 268.9583 |  | WTG Unscheduled Maintenance | 38730 | 268.9583
461 | 2024-05-19 | 2025 | 2024 | 2024-05-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | Break down | Ladder issue | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | WTG manual stop as per instruction of project team. | Open | 0.92244 | O2_10 | 38703.1042 |  | WTG Unscheduled Maintenance | 38730 | 38703.1042
462 | 2024-05-20 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | Break down | Ladder issue | 0 | 0 | 0.93403 | 0 | 22.4167 | 22.4167 | WTG manual stop as per instruction of project team. | Close | 0.86218 | O2_20 | 32303 |  | WTG Unscheduled Maintenance | 34585 | 32303.3507
463 | 2024-05-20 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3500 | Break down | Break down | 0.91944 | 0.91944 | 0.97986 | 0 | 1.45 | 1.45 | Attend and checked related error then found VCB trip. So, charge the VCB then reset and run WTG. | Close | 0.055769 | O2_20 | 2089 |  | WTG Unscheduled Maintenance | 34585 | 2089.5104
464 | 2024-05-20 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3500 | Break down | Break down | 0.94861 | 0.94861 | 1899-12-31 | 0 | 1.2333 | 1.2333 | Attend and checked related error then found VCB trip. So, charge the VCB then WTG resetting and start work in progress. | Open | 0.047436 | O2_20 | 1777 |  | WTG Unscheduled Maintenance | 34585 | 1777.2847
465 | 2024-05-20 | 2025 | 2024 | 2024-05-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.63264 | 0.63264 | 0.72569 | 0 | 2.2333 | 2.2333 | Manual stop for project pending work of power cable clamp installation | Close | 0.085897 | O2_20 | 3170 |  | WTG Breakdown Maintenance | 34585 | 3218.3264
467 | 2024-05-20 | 2025 | 2024 | 2024-05-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 665 | Break down | Break down | 0.75903 | 0.75903 | 0.78681 | 0 | 0.66667 | 0.66667 | Checked data and reset turbine | Close | 0.025641 | O2_20 | 961 |  | WTG Unscheduled Maintenance | 34585 | 960.6944
468 | 2024-05-21 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.60139 | 0.60139 | 0.65764 | 0 | 1.35 | 1.35 | Manual stop for project pending work as well as nacelle temp. repeated error inspection. | Close | 0.051923 | O2_20 | 1945 |  | WTG Breakdown Maintenance | 34585 | 1945.4063
469 | 2024-05-21 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.67778 | 0.67778 | 0.82014 | 0 | 3.4167 | 3.4167 | Manual stop for project pending work as well as nacelle temp. repeated error inspection. | Close | 0.13141 | O2_20 | 1033 |  | WTG Breakdown Maintenance | 34585 | 4923.559
471 | 2024-05-21 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 665 | Break down | Break down | 0.0097222 | 0.0097222 | 0.025 | 0 | 0.36667 | 0.36667 | Checked related error data log then reboot the controller and after that reset the turbine and start the turbine. | Close | 0.014103 | O2_20 | 528 |  | WTG Unscheduled Maintenance | 34585 | 528.3819
472 | 2024-05-21 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 1550 | Break down | Break down | 0.081944 | 0.081944 | 0.12083 | 0 | 0.93333 | 0.93333 | Checked related error data log then reboot the controller and after that reset the turbine and start the turbine. | Close | 0.035897 | O2_20 | 1345 |  | WTG Unscheduled Maintenance | 34585 | 1344.9722
473 | 2024-05-21 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 1550 | Break down | Break down | 0.74236 | 0.74236 | 0.75625 | 0 | 0.33333 | 0.33333 | Checked related error data log then reboot the controller and after that reset the turbine and start the turbine. | Close | 0.012821 | O2_20 | 480 |  | WTG Unscheduled Maintenance | 34585 | 480.3472
474 | 2024-05-21 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3500 | Break down | Break down | 0 | 0 | 0.0034722 | 0 | 0.083333 | 0.083333 | Attend and checked related error then found VCB trip. So, charge the VCB then reset and run WTG. | Close | 0.0032051 | O2_20 | 120 |  | WTG Unscheduled Maintenance | 34585 | 120.0868
475 | 2024-05-21 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 152 | Break down | Break down | 0.67847 | 0.67847 | 0.68611 | 0 | 0.18333 | 0.18333 | After grid resume then checked related error then reset and run the WTG. | Close | 0.0070513 | O2_20 | 264 |  | WTG Unscheduled Maintenance | 34585 | 264.191
476 | 2024-05-21 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Break down | Break down | 0.68958 | 0.68958 | 0.69306 | 0 | 0.083333 | 0.083333 | Checked related error data log then reboot the controller and after that reset the turbine and start the turbine. | Close | 0.0032051 | O2_20 | 120 |  | WTG Unscheduled Maintenance | 34585 | 120.0868
477 | 2024-05-21 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3500 | Break down | Break down | 0 | 0 | 0.079861 | 0 | 1.9167 | 1.9167 | Attend and checked related error then found VCB trip. So, charge the VCB then reset and run WTG. | Close | 0.073718 | O2_20 | 2762 |  | WTG Unscheduled Maintenance | 34585 | 2761.9965
478 | 2024-05-21 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.62153 | 0.62153 | 0.77847 | 0 | 3.7667 | 3.7667 | Manual stop for project pending work as well as ladder clamp fixing work. | Close | 0.14487 | O2_20 | 1249 |  | WTG Breakdown Maintenance | 34585 | 5427.9236
480 | 2024-05-21 | 2025 | 2024 | 2024-05-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 665 | Break down | Break down | 0.67778 | 0.67778 | 0.85903 | 0 | 4.35 | 4.35 | After grid resume then checked related data log so, found encoder pitch chopper resistor failed. So, replaced it with new one then reset and run the WTG. | Close | 0.16731 | O2_20 | 6269 |  | WTG Unscheduled Maintenance | 34585 | 6268.5312
481 | 2024-05-21 | 2025 | 2024 | 2024-05-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3500 | Break down | Break down | 0 | 0 | 0.0048611 | 0 | 0.11667 | 0.11667 | Attend and checked related error then found VCB trip. So, charge the VCB then WTG resetting and start work in progress. | Close | 0.0044872 | O2_20 | 168 |  | WTG Unscheduled Maintenance | 34585 | 168.1215
482 | 2024-05-22 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 2685 | Break down | Break down | 0.68681 | 0.68681 | 0.71944 | 0 | 0.78333 | 0.78333 | Checked related error data log then reset the turbine and start the turbine. | Close | 0.030128 | O2_16 | 1286 |  | WTG Unscheduled Maintenance | 39397 | 1285.8743
483 | 2024-05-22 | 2025 | 2024 | 2024-05-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | Break down | Ladder issue | 0.41944 | 0.41944 | 0.48264 | 0 | 1.5167 | 1.5167 | WTG manually stop for ladder clamp retrofit work. | Close | 0.058333 | O2_16 | 2490 |  | WTG Unscheduled Maintenance | 39397 | 2489.6715
484 | 2024-05-22 | 2025 | 2024 | 2024-05-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | Break down | Break down | 0.56875 | 0.56875 | 0.58472 | 0 | 0.38333 | 0.38333 | WTG manually stop for USS yard transformer LT box closing work. | Close | 0.014744 | O2_16 | 629 |  | WTG Unscheduled Maintenance | 39397 | 629.2576
485 | 2024-05-22 | 2025 | 2024 | 2024-05-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 175 | Break down | Major BD | 0.15764 | 0.15764 | 0.50972 | 0 | 8.45 | 8.45 | Due to not available Scada connectivity, checked all data log and reset & run the WTG. | Close | 0.325 | O2_16 | 13871 |  | WTG Unscheduled Maintenance | 39397 | 13871.0271
487 | 2024-05-22 | 2025 | 2024 | 2024-05-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 175 | Break down | Break down | 0.55625 | 0.55625 | 0.57917 | 0 | 0.55 | 0.55 | Replaced rotor brake pad temp sensor and run turbine | Close | 0.021154 | O2_16 | 903 |  | WTG Unscheduled Maintenance | 39397 | 902.8479
488 | 2024-05-22 | 2025 | 2024 | 2024-05-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 665 | Break down | Break down | 0.89236 | 0.89236 | 0.89583 | 0 | 0.083333 | 0.083333 | Auto reset error after that run the WTG. | Close | 0.0032051 | O2_16 | 137 |  | WTG Unscheduled Maintenance | 39397 | 136.7951
489 | 2024-05-22 | 2025 | 2024 | 2024-05-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 2685 | Break down | Break down | 0.5875 | 0.5875 | 0.59028 | 0 | 0.066667 | 0.066667 | Auto reset error after that run the WTG. | Close | 0.0025641 | O2_16 | 109 |  | WTG Unscheduled Maintenance | 39397 | 109.4361
491 | 2024-05-22 | 2025 | 2024 | 2024-05-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3110 | Break down | Break down | 0.77292 | 0.77292 | 0.80833 | 0 | 0.85 | 0.85 | Attend and checked related cut then replaced rotor RPM sensor after that reset and run the WTG. | Close | 0.032692 | O2_16 | 1395 |  | WTG Unscheduled Maintenance | 39397 | 1395.3104
492 | 2024-05-23 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 0 | Break down | Break down | 0.45694 | 0.45694 | 0.48194 | 0 | 0.6 | 0.6 | Checked related error data log then reset & run the WTG. | Close | 0.023077 | O2_03 | 1173 |  | WTG Unscheduled Maintenance | 46937 | 1173.425
493 | 2024-05-23 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% |  | Break down | Break down | 0.54444 | 0.54444 | 0.54653 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_03 | 98 |  | WTG Unscheduled Maintenance | 46937 | 97.7854
494 | 2024-05-23 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 2687 | Break down | Break down | 0.59097 | 0.59097 | 0.62292 | 0 | 0.76667 | 0.76667 | Checked related error data log then reset & run the WTG. | Close | 0.029487 | O2_03 | 1499 |  | WTG Unscheduled Maintenance | 46937 | 1499.3764
495 | 2024-05-23 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% |  | Break down | Break down | 0.67153 | 0.67153 | 0.69514 | 0 | 0.56667 | 0.56667 | Checked related error data log then reset & run the WTG. | Close | 0.021795 | O2_03 | 1108 |  | WTG Unscheduled Maintenance | 46937 | 1108.2347
496 | 2024-05-23 | 2025 | 2024 | 2024-05-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 5600 | Break down | Break down | 0.24375 | 0.24375 | 0.39653 | 0 | 3.6667 | 3.6667 | Attend and checked related error data log then found hydraulic MPCB tripped. So, MPCB ON it then checked all connection also pressure not build up so, operate flushing mode. After reset & run the WTG. | Close | 0.14103 | O2_03 | 7171 |  | WTG Unscheduled Maintenance | 46937 | 7170.9306
497 | 2024-05-23 | 2025 | 2024 | 2024-05-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 5510 | Break down | Major BD | 0.37847 | 0.37847 | 0.72361 | 0 | 8.2833 | 8.2833 | Attend and checked related error data log, checked all connection, checked all valve. So, found oil filter chock so clean it oil filter and after clean it valve then top up coolant in nacelle and bottom converter cooling system. After complete all work then reset & run the WTG. | Close | 0.31859 | O2_03 | 16200 |  | WTG Unscheduled Maintenance | 46937 | 16199.784
498 | 2024-05-23 | 2025 | 2024 | 2024-05-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 175 | Break down | Break down | 0.6 | 0.6 | 0.63264 | 0 | 0.78333 | 0.78333 | Checked related error data log then reset & run the WTG. | Close | 0.030128 | O2_03 | 1532 |  | WTG Unscheduled Maintenance | 46937 | 1531.9715
499 | 2024-05-23 | 2025 | 2024 | 2024-05-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 696 | Break down | Break down | 0.65208 | 0.65208 | 0.65347 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_03 | 65 |  | WTG Unscheduled Maintenance | 46937 | 65.1903
500 | 2024-05-23 | 2025 | 2024 | 2024-05-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% |  | Break down | Break down | 0.45625 | 0.45625 | 0.47292 | 0 | 0.4 | 0.4 | Checked related error data log then reset & run the WTG. | Close | 0.015385 | O2_03 | 782 |  | WTG Unscheduled Maintenance | 46937 | 782.2833
501 | 2024-05-23 | 2025 | 2024 | 2024-05-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% |  | Break down | Break down | 0.49375 | 0.49375 | 0.5 | 0 | 0.15 | 0.15 | Checked related error data log then reset & run the WTG. | Close | 0.0057692 | O2_03 | 293 |  | WTG Unscheduled Maintenance | 46937 | 293.3562
502 | 2024-05-23 | 2025 | 2024 | 2024-05-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.64236 | 0.64236 | 0.70208 | 0 | 1.4333 | 1.4333 | WTG manually stop by project team for sonic sensor alignment work done. | Close | 0.055128 | O2_03 | 2803 |  | WTG Breakdown Maintenance | 46937 | 2803.1819
503 | 2024-05-23 | 2025 | 2024 | 2024-05-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% |  | Break down | Connectivity issue | 0.38056 | 0.38056 | 0.99097 | 0 | 14.65 | 14.65 | Due to not available Scada connectivity after time physically check WTG so, found in stop condition. So, connect WTG manually then checked all data log and reset & run the WTG. | Close | 0.56346 | O2_03 | 28651 |  | WTG Unscheduled Maintenance | 46937 | 28651.1271
504 | 2024-05-24 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 665 | Break down | Break down | 0.50347 | 0.50347 | 0.6375 | 0 | 3.2167 | 3.2167 | Attend and checked related error data log then checked blade encoder connection then checked nacelle cooling system connection and also tight proper. After complete work then reset & run the WTG. | Close | 0.12372 | O2_20 | 6508 |  | WTG Unscheduled Maintenance | 51211 | 6863.6965
505 | 2024-05-24 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 578 | Break down | Break down | 0.22639 | 0.22639 | 0.23889 | 0 | 0.3 | 0.3 | Checked related error data log then reset & run the WTG. | Close | 0.011538 | O2_20 | 640 |  | WTG Unscheduled Maintenance | 51211 | 640.1375
506 | 2024-05-24 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 175 | Break down | Break down | 0.52014 | 0.52014 | 0.52361 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_20 | 178 |  | WTG Unscheduled Maintenance | 51211 | 177.816
507 | 2024-05-24 | 2025 | 2024 | 2024-05-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 5600 | Break down | Break down | 0.11944 | 0.11944 | 0.24236 | 0 | 2.95 | 2.95 | Attend and checked related error data log then found hydraulic MPCB tripped. So, checked motor current, checked pressure after adjust MPCB setting then MPCB ON it then checked all connection also pressure not build up so, operate flushing mode. After reset & run the WTG. | Close | 0.11346 | O2_20 | 6295 |  | WTG Unscheduled Maintenance | 51211 | 6294.6854
508 | 2024-05-24 | 2025 | 2024 | 2024-05-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 1550 | Break down | Break down | 0.51875 | 0.51875 | 0.52292 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2_20 | 213 |  | WTG Unscheduled Maintenance | 51211 | 213.3792
509 | 2024-05-24 | 2025 | 2024 | 2024-05-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% |  | Break down | Break down | 0.52222 | 0.52222 | 0.52708 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & run the WTG. | Close | 0.0044872 | O2_20 | 249 |  | WTG Unscheduled Maintenance | 51211 | 248.9424
510 | 2024-05-24 | 2025 | 2024 | 2024-05-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 3000 | Break down | Break down | 0.16458 | 0.16458 | 0.22431 | 0 | 1.4333 | 1.4333 | Checked data then reset & run turbine | Close | 0.055128 | O2_20 | 3058 |  | WTG Unscheduled Maintenance | 51211 | 3058.4347
511 | 2024-05-24 | 2025 | 2024 | 2024-05-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 3110 | Break down | Break down | 0.90347 | 0.90347 | 0.90903 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & run the WTG. | Close | 0.0051282 | O2_20 | 284 |  | WTG Unscheduled Maintenance | 51211 | 284.5056
512 | 2024-05-24 | 2025 | 2024 | 2024-05-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 2685 | Break down | Break down | 0.93194 | 0.93194 | 1899-12-31 | 0 | 1.6333 | 1.6333 | Checked related error data log, also checked temp. after system found normal then reset and run the WTG. | Close | 0.062821 | O2_20 | 3485 |  | WTG Unscheduled Maintenance | 51211 | 3485.1931
513 | 2024-05-24 | 2025 | 2024 | 2024-05-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% |  | Break down | Connectivity issue | 0.61389 | 0.61389 | 0.7375 | 0 | 2.9667 | 2.9667 | Due to not available Scada connectivity and also not available vehicle after time physically check WTG so, found in stop condition. So, connect WTG manually then checked all data log and reset & run the WTG. | Close | 0.1141 | O2_20 | 6330 |  | WTG Unscheduled Maintenance | 51211 | 6330.2486
514 | 2024-05-24 | 2025 | 2024 | 2024-05-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 175 | Break down | Connectivity issue | 0.75972 | 0.75972 | 1899-12-31 | 0 | 5.7667 | 5.7667 | Due to not available Scada connectivity after time at 23:30 physically check WTG so, found in stop condition. So, connect WTG manually then checked all error data log and communicate Yogesh Bhai and try to reset the WTG but error does not resolve so further tmr will troubleshoot and run the WTG restore shortly time. | Open | 0.22179 | O2_20 | 12305 |  | WTG Unscheduled Maintenance | 51211 | 12304.8653
515 | 2024-05-25 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | Break down | Ladder issue | 0.50764 | 0.50764 | 0.53819 | 0 | 0.73333 | 0.73333 | WTG manually stop for ladder inspection. | Close | 0.028205 | O2_20 | 1173 |  | WTG Unscheduled Maintenance | 38395 | 1173.1806
516 | 2024-05-25 | 2025 | 2024 | 2024-05-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 6130 | Break down | Break down | 0.55278 | 0.55278 | 0.58333 | 0 | 0.73333 | 0.73333 | Checked related error data log then reset & run the WTG. | Close | 0.028205 | O2_20 | 1173 |  | WTG Unscheduled Maintenance | 38395 | 1173.1806
517 | 2024-05-25 | 2025 | 2024 | 2024-05-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 1600 | Break down | Break down | 0.055556 | 0.055556 | 0.079861 | 0 | 0.58333 | 0.58333 | Checked related error data log then reset & run the WTG. | Close | 0.022436 | O2_20 | 933 |  | WTG Unscheduled Maintenance | 38395 | 933.2118
518 | 2024-05-25 | 2025 | 2024 | 2024-05-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | Break down | Break down | 0.54514 | 0.54514 | 0.62569 | 0 | 1.9333 | 1.9333 | WTG manually stop for power curve issue. Checked cable of load sensor which is malfunctioning so arrange material and plan for install it. | Close | 0.074359 | O2_20 | 3093 |  | WTG Unscheduled Maintenance | 38395 | 3092.9306
519 | 2024-05-25 | 2025 | 2024 | 2024-05-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 175 | Break down | Major BD | 0 | 0 | 0.66806 | 0 | 16.0333 | 16.0333 | Also we are attend in night but required material so arrange material then Attend and checked related error data log then checked yaw contactor and also replaced yaw contactor. After set limit switch position and also done SLC reconfiguration then cable pinch of feedback so correct it. After complete all work then reset & run the WTG. | Close | 0.61667 | O2_20 | 25650 |  | WTG Unscheduled Maintenance | 38395 | 25649.9931
520 | 2024-05-25 | 2025 | 2024 | 2024-05-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.53958 | 0.53958 | 0.67778 | 0 | 3.3167 | 3.3167 | WTG manually stop by project team for done inspection. Also done GEDA observation. | Close | 0.12756 | O2_20 | 5306 |  | WTG Breakdown Maintenance | 38395 | 5305.9757
521 | 2024-05-26 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% |  | Break down | Break down | 0.68264 | 0.68264 | 0.69792 | 0 | 0.36667 | 0.36667 | Checked related error data log then reset & run the WTG. | Close | 0.014103 | O2_20 | 745 |  | WTG Unscheduled Maintenance | 48753 | 744.8375
522 | 2024-05-26 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | Break down | Ladder issue | 0.48333 | 0.48333 | 0.54722 | 0 | 1.5333 | 1.5333 | WTG manually stop for ladder inspection. And also rework of ladder. | Close | 0.058974 | O2_20 | 3115 |  | WTG Unscheduled Maintenance | 48753 | 3114.775
523 | 2024-05-26 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Break down | Break down | 0.83681 | 0.83681 | 0.85417 | 0 | 0.41667 | 0.41667 | Checked related error data log then reset & run the WTG. | Close | 0.016026 | O2_20 | 846 |  | WTG Unscheduled Maintenance | 48753 | 846.4063
524 | 2024-05-26 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3211 | Break down | Break down | 0.92569 | 0.92569 | 0.93333 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & run the WTG. | Close | 0.0070513 | O2_20 | 372 |  | WTG Unscheduled Maintenance | 48753 | 372.4187
525 | 2024-05-26 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 2687 | Break down | Break down | 0.71181 | 0.71181 | 0.73194 | 0 | 0.48333 | 0.48333 | Checked related error data log then reset & run the WTG. | Close | 0.01859 | O2_20 | 982 |  | WTG Unscheduled Maintenance | 48753 | 981.8313
526 | 2024-05-26 | 2025 | 2024 | 2024-05-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% |  | Break down | Break down | 0.47917 | 0.47917 | 0.4875 | 0 | 0.2 | 0.2 | Checked related error data log then reset & run the WTG. | Close | 0.0076923 | O2_20 | 406 |  | WTG Unscheduled Maintenance | 48753 | 406.275
527 | 2024-05-26 | 2025 | 2024 | 2024-05-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 6130 | Break down | Break down | 0.50833 | 0.50833 | 0.5125 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2_20 | 203 |  | WTG Unscheduled Maintenance | 48753 | 203.1375
528 | 2024-05-26 | 2025 | 2024 | 2024-05-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 6130 | Break down | Break down | 0.71736 | 0.71736 | 0.72917 | 0 | 0.28333 | 0.28333 | Checked related error data log then reset & run the WTG. | Close | 0.010897 | O2_20 | 575 |  | WTG Unscheduled Maintenance | 48753 | 575.5563
529 | 2024-05-26 | 2025 | 2024 | 2024-05-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% |  | Break down | Break down | 0.5125 | 0.5125 | 0.51736 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & run the WTG. | Close | 0.0044872 | O2_20 | 237 |  | WTG Unscheduled Maintenance | 48753 | 236.9937
530 | 2024-05-26 | 2025 | 2024 | 2024-05-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | Break down | Break down | 0.66736 | 0.66736 | 0.77986 | 0 | 2.7 | 2.7 | WTG manually stop for power curve rectification work. | Close | 0.10385 | O2_20 | 5484 |  | WTG Unscheduled Maintenance | 48753 | 5484.7125
531 | 2024-05-26 | 2025 | 2024 | 2024-05-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% |  | Break down | Connectivity issue | 0 | 0 | 0.039583 | 0 | 0.95 | 0.95 | Due to not available Scada connectivity after time physically check WTG so, found in stop condition. So, connect WTG manually then checked all data log and reset & run the WTG. | Close | 0.036538 | O2_20 | 1930 |  | WTG Unscheduled Maintenance | 48753 | 1929.8062
532 | 2024-05-26 | 2025 | 2024 | 2024-05-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% |  | Break down | Connectivity issue | 0.1375 | 0.1375 | 0.55486 | 0 | 10.0167 | 10.0167 | Due to not available Scada connectivity after time physically check WTG so, found in stop condition. So, connect WTG manually then checked all data log and reset & run the WTG. | Close | 0.38526 | O2_20 | 20348 |  | WTG Unscheduled Maintenance | 48753 | 20347.6063
533 | 2024-05-26 | 2025 | 2024 | 2024-05-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% |  | Break down | Connectivity issue | 0.72083 | 0.72083 | 0.84653 | 0 | 3.0167 | 3.0167 | Due to not available Scada connectivity after time physically check WTG so, found in stop condition. So, connect WTG manually then checked all data log and reset & run the WTG. | Close | 0.11603 | O2_20 | 6128 |  | WTG Unscheduled Maintenance | 48753 | 6127.9812
534 | 2024-05-27 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 175 | Break down | Break down | 0.013194 | 0.013194 | 0.0375 | 0 | 0.58333 | 0.58333 | Checked related error data log then reset & run the WTG. | Close | 0.022436 | O2_20 | 1031 |  | WTG Unscheduled Maintenance | 42433 | 1031.3576
535 | 2024-05-27 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 675 | Break down | Break down | 0.75556 | 0.75556 | 0.84028 | 0 | 2.0333 | 2.0333 | After grid resume then errors occurred so, attend and checked related error data log , checked all connection and its tightness also all over found ok. So, reset the error log then run the WTG. | Close | 0.078205 | O2_20 | 3595 |  | WTG Unscheduled Maintenance | 42433 | 3595.0181
536 | 2024-05-27 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Break down | Break down | 0.21875 | 0.21875 | 0.22083 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_20 | 88 |  | WTG Unscheduled Maintenance | 42433 | 88.4021
537 | 2024-05-27 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3000 | Break down | Break down | 0.76319 | 0.76319 | 0.78681 | 0 | 0.56667 | 0.56667 | After grid resume so, checked related error data log then reset & run the WTG. | Close | 0.021795 | O2_20 | 1002 |  | WTG Unscheduled Maintenance | 42433 | 1001.8903
538 | 2024-05-27 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 2687 | Break down | Break down | 0.76181 | 0.76181 | 0.78125 | 0 | 0.46667 | 0.46667 | After grid resume so, checked related error data log then reset & run the WTG. | Close | 0.017949 | O2_20 | 825 |  | WTG Unscheduled Maintenance | 42433 | 825.0861
539 | 2024-05-27 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Break down | Break down | 0.92431 | 0.92431 | 0.94097 | 0 | 0.4 | 0.4 | Checked related error data log then reset & run the WTG. | Close | 0.015385 | O2_20 | 707 |  | WTG Unscheduled Maintenance | 42433 | 707.2167
540 | 2024-05-27 | 2025 | 2024 | 2024-05-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 175 | Break down | Break down | 0.013194 | 0.013194 | 0.0375 | 0 | 0.58333 | 0.58333 | Checked related error data log then reset & run the WTG. | Close | 0.022436 | O2_20 | 1031 |  | WTG Unscheduled Maintenance | 42433 | 1031.3576
541 | 2024-05-27 | 2025 | 2024 | 2024-05-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 3010 | Break down | Break down | 0.75764 | 0.75764 | 0.78125 | 0 | 0.56667 | 0.56667 | After grid resume so, checked related error data log then reset & run the WTG. | Close | 0.021795 | O2_20 | 1002 |  | WTG Unscheduled Maintenance | 42433 | 1001.8903
542 | 2024-05-27 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 175 | Break down | Break down | 0.013194 | 0.013194 | 0.0375 | 0 | 0.58333 | 0.58333 | Checked related error data log then reset & run the WTG. | Close | 0.022436 | O2_20 | 1031 |  | WTG Unscheduled Maintenance | 42433 | 1031.3576
543 | 2024-05-27 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6130 | Break down | Break down | 0.51458 | 0.51458 | 0.52222 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & run the WTG. | Close | 0.0070513 | O2_20 | 324 |  | WTG Unscheduled Maintenance | 42433 | 324.141
544 | 2024-05-27 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 696 | Break down | Break down | 0.78056 | 0.78056 | 0.80833 | 0 | 0.66667 | 0.66667 | After grid resume so, checked related error data log then reset & run the WTG. | Close | 0.025641 | O2_20 | 1179 |  | WTG Unscheduled Maintenance | 42433 | 1178.6944
545 | 2024-05-27 | 2025 | 2024 | 2024-05-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 175 | Break down | Break down | 0.013194 | 0.013194 | 0.0375 | 0 | 0.58333 | 0.58333 | Checked related error data log then reset & run the WTG. | Close | 0.022436 | O2_20 | 1031 |  | WTG Unscheduled Maintenance | 42433 | 1031.3576
546 | 2024-05-27 | 2025 | 2024 | 2024-05-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 175 | Break down | Break down | 0.013194 | 0.013194 | 0.0375 | 0 | 0.58333 | 0.58333 | Checked related error data log then reset & run the WTG. | Close | 0.022436 | O2_20 | 1031 |  | WTG Unscheduled Maintenance | 42433 | 1031.3576
547 | 2024-05-27 | 2025 | 2024 | 2024-05-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3010 | Break down | Break down | 0.75764 | 0.75764 | 0.76667 | 0 | 0.21667 | 0.21667 | After grid resume so, checked related error data log then reset & run the WTG. | Close | 0.0083333 | O2_20 | 383 |  | WTG Unscheduled Maintenance | 42433 | 383.0757
548 | 2024-05-27 | 2025 | 2024 | 2024-05-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 175 | Break down | Break down | 0.013194 | 0.013194 | 0.0375 | 0 | 0.58333 | 0.58333 | Checked related error data log then reset & run the WTG. | Close | 0.022436 | O2_20 | 1031 |  | WTG Unscheduled Maintenance | 42433 | 1031.3576
549 | 2024-05-27 | 2025 | 2024 | 2024-05-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 665 | Break down | Break down | 0.093056 | 0.093056 | 0.096528 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_20 | 147 |  | WTG Unscheduled Maintenance | 42433 | 147.3368
550 | 2024-05-27 | 2025 | 2024 | 2024-05-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3010 | Break down | Break down | 0.18958 | 0.18958 | 0.19861 | 0 | 0.21667 | 0.21667 | After grid resume so, checked related error data log then reset & run the WTG. | Close | 0.0083333 | O2_20 | 383 |  | WTG Unscheduled Maintenance | 42433 | 383.0757
551 | 2024-05-27 | 2025 | 2024 | 2024-05-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 175 | Break down | Break down | 0.013194 | 0.013194 | 0.0375 | 0 | 0.58333 | 0.58333 | Checked related error data log then reset & run the WTG. | Close | 0.022436 | O2_20 | 1031 |  | WTG Unscheduled Maintenance | 42433 | 1031.3576
552 | 2024-05-27 | 2025 | 2024 | 2024-05-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 175 | Break down | Break down | 0.013194 | 0.013194 | 0.0375 | 0 | 0.58333 | 0.58333 | Checked related error data log then reset & run the WTG. | Close | 0.022436 | O2_20 | 1031 |  | WTG Unscheduled Maintenance | 42433 | 1031.3576
553 | 2024-05-27 | 2025 | 2024 | 2024-05-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3000 | Break down | Break down | 0.75347 | 0.75347 | 0.80625 | 0 | 1.2667 | 1.2667 | After grid resume so, checked related error data log then reset & run the WTG. | Close | 0.048718 | O2_20 | 2239 |  | WTG Unscheduled Maintenance | 42433 | 2239.5194
554 | 2024-05-28 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 696 | Break down | Break down | 0.15764 | 0.15764 | 0.17153 | 0 | 0.33333 | 0.33333 | Checked related error data log then reset & run the WTG. | Close | 0.012821 | O2_14 | 563 |  | WTG Unscheduled Maintenance | 40537 | 563.0139
555 | 2024-05-28 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3000 | Break down | Break down | 0.71806 | 0.71806 | 0.77014 | 0 | 1.25 | 1.25 | After grid resume so, checked related error data log then reset & run the WTG. | Close | 0.048077 | O2_14 | 2111 |  | WTG Unscheduled Maintenance | 40537 | 2111.3021
556 | 2024-05-28 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 1550 | Break down | Break down | 0.93889 | 0.93889 | 0.95139 | 0 | 0.3 | 0.3 | Checked related error data log then reset & run the WTG. | Close | 0.011538 | O2_14 | 506 |  | WTG Unscheduled Maintenance | 40537 | 506.7125
557 | 2024-05-28 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 1550 | Break down | Break down | 0.96667 | 0.96667 | 0.99097 | 0 | 0.58333 | 0.58333 | Checked related error data log then reset & run the WTG. | Close | 0.022436 | O2_14 | 985 |  | WTG Unscheduled Maintenance | 40537 | 985.2743
558 | 2024-05-28 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Break down | Break down | 0.0020833 | 0.0020833 | 0.014583 | 0 | 0.3 | 0.3 | Checked related error data log then reset & run the WTG. | Close | 0.011538 | O2_14 | 507 |  | WTG Unscheduled Maintenance | 40537 | 506.7125
559 | 2024-05-28 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Break down | Break down | 0.040278 | 0.040278 | 0.045139 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & run the WTG. | Close | 0.0044872 | O2_14 | 197 |  | WTG Unscheduled Maintenance | 40537 | 197.0549
560 | 2024-05-28 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 973 | Break down | Break down | 0.053472 | 0.053472 | 0.061806 | 0 | 0.2 | 0.2 | Checked related error data log then reset & run the WTG. | Close | 0.0076923 | O2_14 | 338 |  | WTG Unscheduled Maintenance | 40537 | 337.8083
561 | 2024-05-28 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Break down | Break down | 0.10139 | 0.10139 | 0.12361 | 0 | 0.53333 | 0.53333 | Checked related error data log then reset & run the WTG. | Close | 0.020513 | O2_14 | 901 |  | WTG Unscheduled Maintenance | 40537 | 900.8222
562 | 2024-05-28 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3061 | Break down | Break down | 0.12847 | 0.12847 | 0.14514 | 0 | 0.4 | 0.4 | Checked related error data log then reset & run the WTG. | Close | 0.015385 | O2_14 | 676 |  | WTG Unscheduled Maintenance | 40537 | 675.6167
563 | 2024-05-28 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 578 | Break down | Break down | 0.20486 | 0.20486 | 0.22292 | 0 | 0.43333 | 0.43333 | Checked related error data log then reset & run the WTG. | Close | 0.016667 | O2_14 | 732 |  | WTG Unscheduled Maintenance | 40537 | 731.9181
564 | 2024-05-28 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 973 | Break down | Break down | 0.23194 | 0.23194 | 0.24306 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_14 | 450 |  | WTG Unscheduled Maintenance | 40537 | 450.4111
565 | 2024-05-28 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Break down | Break down | 0.32847 | 0.32847 | 0.33889 | 0 | 0.25 | 0.25 | Checked related error data log then reset & run the WTG. | Close | 0.0096154 | O2_14 | 422 |  | WTG Unscheduled Maintenance | 40537 | 422.2604
566 | 2024-05-28 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 455 | Break down | Break down | 0.77292 | 0.77292 | 0.79236 | 0 | 0.46667 | 0.46667 | Checked related error data log then reset & run the WTG. | Close | 0.017949 | O2_14 | 788 |  | WTG Unscheduled Maintenance | 40537 | 788.2194
567 | 2024-05-28 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 973 | Break down | Break down | 0.8125 | 0.8125 | 0.84375 | 0 | 0.75 | 0.75 | Checked related error data log then reset & run the WTG. | Open | 0.028846 | O2_14 | 1267 |  | WTG Unscheduled Maintenance | 40537 | 1266.7812
568 | 2024-05-28 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Break down | Break down | 0.8625 | 0.8625 | 0.89514 | 0 | 0.78333 | 0.78333 | Checked related error data log then reset & run the WTG. | Close | 0.030128 | O2_14 | 1323 |  | WTG Unscheduled Maintenance | 40537 | 1323.0826
569 | 2024-05-28 | 2025 | 2024 | 2024-05-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 5700 | Break down | Break down | 0.97431 | 0.97431 | 0.99722 | 0 | 0.55 | 0.55 | Checked related error data log then reset & run the WTG. | Close | 0.021154 | O2_14 | 929 |  | WTG Unscheduled Maintenance | 40537 | 928.9729
570 | 2024-05-28 | 2025 | 2024 | 2024-05-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 1600 | Break down | Break down | 0.076389 | 0.076389 | 0.092361 | 0 | 0.38333 | 0.38333 | Checked related error data log then reset & run the WTG. | Close | 0.014744 | O2_09 | 573 |  | WTG Unscheduled Maintenance | 35853 | 572.6521
571 | 2024-05-28 | 2025 | 2024 | 2024-05-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3110 | Break down | Break down | 0.71806 | 0.71806 | 0.77569 | 0 | 1.3833 | 1.3833 | After grid resume so, checked related error data log then reset & run the WTG. | Close | 0.053205 | O2_09 | 2067 |  | WTG Unscheduled Maintenance | 35853 | 2066.5271
572 | 2024-05-28 | 2025 | 2024 | 2024-05-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 696 | Break down | Break down | 0.00069444 | 0.00069444 | 0.015972 | 0 | 0.36667 | 0.36667 | Checked related error data log then reset & run the WTG. | Close | 0.014103 | O2_16 | 64 |  | WTG Unscheduled Maintenance | 4225 | 64.5486
573 | 2024-05-28 | 2025 | 2024 | 2024-05-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 6130 | Break down | Break down | 0.11319 | 0.11319 | 0.12431 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_03 | 392 |  | WTG Unscheduled Maintenance | 35240 | 391.5556
574 | 2024-05-28 | 2025 | 2024 | 2024-05-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 175 | Break down | Break down | 0.71806 | 0.71806 | 0.75347 | 0 | 0.85 | 0.85 | After grid resume so, checked related error data log then reset & run the WTG. | Close | 0.032692 | O2_03 | 1248 |  | WTG Unscheduled Maintenance | 35240 | 1248.0833
575 | 2024-05-29 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 973 | Break down | Break down | 0.45347 | 0.45347 | 0.45833 | 0 | 0.11667 | 0.11667 | Auto reset error then start WTG. | Close | 0.0044872 | O2_14 | 274 |  | WTG Unscheduled Maintenance | 56520 | 274.75
576 | 2024-05-29 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 1600 | Break down | Break down | 0.47917 | 0.47917 | 0.49653 | 0 | 0.41667 | 0.41667 | Checked related error data log then reset & run the WTG. | Close | 0.016026 | O2_14 | 981 |  | WTG Unscheduled Maintenance | 56520 | 981.25
577 | 2024-05-29 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 973 | Break down | Break down | 0.55347 | 0.55347 | 0.55903 | 0 | 0.13333 | 0.13333 | Auto reset error then start WTG. | Close | 0.0051282 | O2_14 | 314 |  | WTG Unscheduled Maintenance | 56520 | 314
578 | 2024-05-29 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 973 | Break down | Break down | 0.60208 | 0.60208 | 0.60833 | 0 | 0.15 | 0.15 | Auto reset error then start WTG. | Close | 0.0057692 | O2_14 | 353 |  | WTG Unscheduled Maintenance | 56520 | 353.25
579 | 2024-05-29 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 696 | Break down | Break down | 0.76667 | 0.76667 | 0.77292 | 0 | 0.15 | 0.15 | Checked related error data log then reset & run the WTG. | Close | 0.0057692 | O2_14 | 353 |  | WTG Unscheduled Maintenance | 56520 | 353.25
580 | 2024-05-29 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 973 | Break down | Break down | 0.19375 | 0.19375 | 0.19444 | 0 | 0.016667 | 0.016667 | Auto reset error then start WTG. | Close | 0.00064103 | O2_13 | 34 |  | WTG Unscheduled Maintenance | 48390 | 33.6042
581 | 2024-05-29 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 155 | Break down | Break down | 0.37569 | 0.37569 | 0.42569 | 0 | 1.2 | 1.2 | Checked related error data log then reset & run the WTG. | Close | 0.046154 | O2_13 | 2419 |  | WTG Unscheduled Maintenance | 48390 | 2419.5
582 | 2024-05-29 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 973 | Break down | Break down | 0.53611 | 0.53611 | 0.5375 | 0 | 0.033333 | 0.033333 | Auto reset error then start WTG. | Close | 0.0012821 | O2_13 | 67 |  | WTG Unscheduled Maintenance | 48390 | 67.2083
583 | 2024-05-29 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 696 | Break down | Break down | 0.55764 | 0.55764 | 0.575 | 0 | 0.41667 | 0.41667 | Checked related error data log then reset & run the WTG. | Close | 0.016026 | O2_13 | 840 |  | WTG Unscheduled Maintenance | 48390 | 840.1042
584 | 2024-05-29 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 696 | Break down | Break down | 0.65833 | 0.65833 | 0.67361 | 0 | 0.36667 | 0.36667 | Checked related error data log then reset & run the WTG. | Close | 0.014103 | O2_13 | 739 |  | WTG Unscheduled Maintenance | 48390 | 739.2917
585 | 2024-05-29 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Break down | Break down | 0.74722 | 0.74722 | 0.75694 | 0 | 0.23333 | 0.23333 | Checked related error data log then reset & run the WTG. | Close | 0.0089744 | O2_13 | 470 |  | WTG Unscheduled Maintenance | 48390 | 470.4583
586 | 2024-05-29 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 155 | Break down | Break down | 0.81042 | 0.81042 | 0.81875 | 0 | 0.2 | 0.2 | Checked related error data log then reset & run the WTG. | Close | 0.0076923 | O2_13 | 403 |  | WTG Unscheduled Maintenance | 48390 | 403.25
587 | 2024-05-29 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 155 | Break down | Break down | 0.92847 | 0.92847 | 0.93958 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_13 | 537 |  | WTG Unscheduled Maintenance | 48390 | 537.6667
588 | 2024-05-29 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Break down | Break down | 0.52083 | 0.52083 | 0.52986 | 0 | 0.21667 | 0.21667 | Auto reset error then start WTG. | Close | 0.0083333 | O2_12 | 442 |  | WTG Unscheduled Maintenance | 48960 | 442
589 | 2024-05-29 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Break down | Break down | 0.90694 | 0.90694 | 0.90833 | 0 | 0.033333 | 0.033333 | Auto reset error then start WTG. | Close | 0.0012821 | O2_12 | 68 |  | WTG Unscheduled Maintenance | 48960 | 68
590 | 2024-05-29 | 2025 | 2024 | 2024-05-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 696 | Break down | Break down | 0.55972 | 0.55972 | 0.60903 | 0 | 1.1833 | 1.1833 | Checked related error data log then reset & run the WTG. | Close | 0.045513 | O2_11 | 2747 |  | WTG Unscheduled Maintenance | 55708 | 2746.7139
591 | 2024-05-29 | 2025 | 2024 | 2024-05-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 696 | Break down | Break down | 0.67292 | 0.67292 | 0.67847 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & run the WTG. | Close | 0.0051282 | O2_11 | 309 |  | WTG Unscheduled Maintenance | 55708 | 309.4889
592 | 2024-05-29 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 696 | Break down | Break down | 0.56597 | 0.56597 | 0.575 | 0 | 0.21667 | 0.21667 | Checked related error data log then reset & run the WTG. | Close | 0.0083333 | O2_15 | 521 |  | WTG Unscheduled Maintenance | 57664 | 520.5778
593 | 2024-05-29 | 2025 | 2024 | 2024-05-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 696 | Break down | Break down | 0.58958 | 0.58958 | 0.60278 | 0 | 0.31667 | 0.31667 | Checked related error data log then reset & run the WTG. | Close | 0.012179 | O2_15 | 761 |  | WTG Unscheduled Maintenance | 57664 | 760.8444
594 | 2024-05-29 | 2025 | 2024 | 2024-05-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 696 | Break down | Break down | 0.5125 | 0.5125 | 0.51806 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & run the WTG. | Close | 0.0051282 | O2_09 | 267 |  | WTG Unscheduled Maintenance | 48123 | 267.35
595 | 2024-05-29 | 2025 | 2024 | 2024-05-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 696 | Break down | Break down | 0.63819 | 0.63819 | 0.64583 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & run the WTG. | Close | 0.0070513 | O2_10 | 440 |  | WTG Unscheduled Maintenance | 57660 | 440.4583
596 | 2024-05-29 | 2025 | 2024 | 2024-05-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 696 | Break down | Break down | 0.625 | 0.625 | 0.63472 | 0 | 0.23333 | 0.23333 | Checked related error data log then reset & run the WTG. | Close | 0.0089744 | O2_20 | 512 |  | WTG Unscheduled Maintenance | 52664 | 512.0111
597 | 2024-05-29 | 2025 | 2024 | 2024-05-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 455 | Break down | Break down | 0.6625 | 0.6625 | 0.67431 | 0 | 0.28333 | 0.28333 | Checked related error data log then reset & run the WTG. | Close | 0.010897 | O2_20 | 622 |  | WTG Unscheduled Maintenance | 52664 | 621.7278
598 | 2024-05-29 | 2025 | 2024 | 2024-05-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 696 | Break down | Break down | 0.71806 | 0.71806 | 0.72917 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_20 | 585 |  | WTG Unscheduled Maintenance | 52664 | 585.1556
599 | 2024-05-29 | 2025 | 2024 | 2024-05-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 696 | Break down | Break down | 0.18264 | 0.18264 | 0.20208 | 0 | 0.46667 | 0.46667 | Checked related error data log then reset & run the WTG. | Close | 0.017949 | O2_16 | 988 |  | WTG Unscheduled Maintenance | 50789 | 987.5639
600 | 2024-05-29 | 2025 | 2024 | 2024-05-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 973 | Break down | Break down | 0.64028 | 0.64028 | 0.64653 | 0 | 0.15 | 0.15 | Auto reset error then start WTG. | Close | 0.0057692 | O2_16 | 317 |  | WTG Unscheduled Maintenance | 50789 | 317.4312
601 | 2024-05-29 | 2025 | 2024 | 2024-05-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 1600 | Break down | Break down | 0.67431 | 0.67431 | 0.69722 | 0 | 0.55 | 0.55 | Checked related error data log then reset & run the WTG. | Close | 0.021154 | O2_16 | 1164 |  | WTG Unscheduled Maintenance | 50789 | 1163.9146
602 | 2024-05-29 | 2025 | 2024 | 2024-05-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 973 | Break down | Break down | 0.77986 | 0.77986 | 0.78611 | 0 | 0.15 | 0.15 | Auto reset error then start WTG. | Close | 0.0057692 | O2_16 | 317 |  | WTG Unscheduled Maintenance | 50789 | 317.4313
603 | 2024-05-29 | 2025 | 2024 | 2024-05-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 665 | Break down | Break down | 0.035417 | 0.035417 | 0.04375 | 0 | 0.2 | 0.2 | Checked related error data log then reset & run the WTG. | Close | 0.0076923 | O2_03 | 497 |  | WTG Unscheduled Maintenance | 59670 | 497.25
604 | 2024-05-29 | 2025 | 2024 | 2024-05-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 665 | Break down | Break down | 0.17986 | 0.17986 | 0.18889 | 0 | 0.21667 | 0.21667 | Checked related error data log then reset & run the WTG. | Close | 0.0083333 | O2_03 | 538 |  | WTG Unscheduled Maintenance | 59670 | 538.6875
605 | 2024-05-29 | 2025 | 2024 | 2024-05-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 665 | Break down | Break down | 0.31736 | 0.31736 | 0.32083 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_03 | 207 |  | WTG Unscheduled Maintenance | 59670 | 207.1875
606 | 2024-05-29 | 2025 | 2024 | 2024-05-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.37292 | 0.37292 | 0.39306 | 0 | 0.48333 | 0.48333 | Checked related error data log then reset & run the WTG. | Close | 0.01859 | O2_03 | 1202 |  | WTG Unscheduled Maintenance | 59670 | 1201.6875
607 | 2024-05-29 | 2025 | 2024 | 2024-05-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.40208 | 0.40208 | 0.41667 | 0 | 0.35 | 0.35 | Checked related error data log then reset & run the WTG. | Close | 0.013462 | O2_03 | 870 |  | WTG Unscheduled Maintenance | 59670 | 870.1875
608 | 2024-05-29 | 2025 | 2024 | 2024-05-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.4625 | 0.4625 | 0.47847 | 0 | 0.38333 | 0.38333 | Checked related error data log then reset & run the WTG. | Close | 0.014744 | O2_03 | 953 |  | WTG Unscheduled Maintenance | 59670 | 953.0625
609 | 2024-05-29 | 2025 | 2024 | 2024-05-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.49722 | 0.49722 | 0.62778 | 0 | 3.1333 | 3.1333 | Attend for repeated Pitch error so, checked related error data log and also checked cut then replaced chopper resistor of Blade -3 after complete work then reset the WTG and start the WTG. | Close | 0.12051 | O2_03 | 7790 |  | WTG Breakdown Maintenance | 59670 | 7790.25
610 | 2024-05-29 | 2025 | 2024 | 2024-05-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Connectivity issue | 0.37153 | 0.37153 | 0.46875 | 0 | 2.3333 | 2.3333 | Due to not available Scada connectivity after time physically check WTG so, found in stop condition. So, connect WTG manually then checked all data log and reset & run the WTG. | Close | 0.089744 | O2_02 | 1187 |  | WTG Unscheduled Maintenance | 12205 | 1186.5972
611 | 2024-05-29 | 2025 | 2024 | 2024-05-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.5375 | 0.5375 | 0.78333 | 0 | 5.9 | 5.9 | Attend for repeated Wind. Dir. Diff. level 2 error so, checked related error data log, also checked all connection and cut after checked found both wind sensor alignment not proper. So, both wind sensor alignment properly done. After complete all work then checked data and then reset all error log after run the WTG. | Close | 0.22692 | O2_02 | 3000 |  | WTG Breakdown Maintenance | 12205 | 3000.3958
612 | 2024-05-29 | 2025 | 2024 | 2024-05-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Connectivity issue | 0 | 0 | 0.026389 | 0 | 0.63333 | 0.63333 | Due to not available Scada connectivity after time physically check WTG so, found in stop condition. So, connect WTG manually then checked all data log and reset & run the WTG. | Close | 0.024359 | O2_05 | 852 |  | WTG Unscheduled Maintenance | 32307 | 852.5458
613 | 2024-05-29 | 2025 | 2024 | 2024-05-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Connectivity issue | 0.15625 | 0.15625 | 0.46389 | 0 | 7.3833 | 7.3833 | Due to not available Scada connectivity after time physically check WTG so, found in stop condition. So, connect WTG manually then checked all data log and reset & run the WTG. | Close | 0.28397 | O2_05 | 9939 |  | WTG Unscheduled Maintenance | 32307 | 9938.8896
614 | 2024-05-29 | 2025 | 2024 | 2024-05-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 6120 | Uncontrolled yaw movement | Break down | 0.50417 | 0.50417 | 0.74167 | 0 | 5.7 | 5.7 | Attend for repeated Yaw error so, checked all related error data log, also checked all connection and its tightness then checked all HU unit valve and checked pressure switch. Found everything is normal so reset all error data log then run the WTG. | Close | 0.21923 | O2_05 | 7673 |  | WTG Unscheduled Maintenance | 32307 | 7672.9125
615 | 2024-05-30 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.6625 | 0.6625 | 0.66806 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & run the WTG. | Close | 0.0051282 | O2_14 | 214 |  | WTG Unscheduled Maintenance | 38592 | 214.4
616 | 2024-05-30 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 155 | SLC SF system monitoring | Break down | 0.17014 | 0.17014 | 0.18403 | 0 | 0.33333 | 0.33333 | Checked related error data log then reset & run the WTG. | Close | 0.012821 | O2_13 | 490 |  | WTG Unscheduled Maintenance | 35282 | 490.0278
617 | 2024-05-30 | 2025 | 2024 | 2024-05-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.93194 | 0.93194 | 0.94722 | 0 | 0.36667 | 0.36667 | Checked related error data log then reset & run the WTG. | Close | 0.014103 | O2_13 | 539 |  | WTG Unscheduled Maintenance | 35282 | 539.0306
618 | 2024-05-30 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.53472 | 0.53472 | 0.58333 | 0 | 1.1667 | 1.1667 | WTG manually stop for inspection of power curve. Also done blade load sensor calibration. After that reset the all generated error then run the WTG. | Close | 0.044872 | O2_12 | 1866 |  | WTG Breakdown Maintenance | 38380 | 1865.6944
619 | 2024-05-30 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.6375 | 0.6375 | 0.65069 | 0 | 0.31667 | 0.31667 | Checked related error data log then reset & run the WTG. | Close | 0.012179 | O2_12 | 506 |  | WTG Unscheduled Maintenance | 38380 | 506.4028
620 | 2024-05-30 | 2025 | 2024 | 2024-05-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 88 | Outs.temp. nacelle implaus. | Break down | 0.53264 | 0.53264 | 0.6875 | 0 | 3.7167 | 3.7167 | Attend and checked related error data log, also checked all connections and its tightness then checked nacelle outside temp. sensor connection and tight properly. After complete all work then reset all error data log then run the WTG. | Close | 0.14295 | O2_03 | 5764 |  | WTG Unscheduled Maintenance | 37220 | 5763.9306
621 | 2024-05-30 | 2025 | 2024 | 2024-05-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 6120 | Uncontrolled yaw movement | Break down | 0 | 0 | 0.016667 | 0 | 0.4 | 0.4 | Checked related error data log then reset & run the WTG. | Close | 0.015385 | O2_05 | 617 |  | WTG Unscheduled Maintenance | 37037 | 617.2833
622 | 2024-05-30 | 2025 | 2024 | 2024-05-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.065972 | 0.065972 | 0.070139 | 0 | 0.1 | 0.1 | Auto reset error then start WTG. | Close | 0.0038462 | O2_05 | 154 |  | WTG Unscheduled Maintenance | 37037 | 154.3208
623 | 2024-05-30 | 2025 | 2024 | 2024-05-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.19028 | 0.19028 | 0.20764 | 0 | 0.41667 | 0.41667 | Checked related error data log then reset & run the WTG. | Close | 0.016026 | O2_05 | 643 |  | WTG Unscheduled Maintenance | 37037 | 643.0035
624 | 2024-05-30 | 2025 | 2024 | 2024-05-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Connectivity issue | 0.47222 | 0.47222 | 0.77292 | 0 | 7.2167 | 7.2167 | Due to not available Scada connectivity after time physically check WTG so, found in stop condition. So, connect WTG manually then checked all data log and reset & run the WTG. | Close | 0.27756 | O2_05 | 11136 |  | WTG Unscheduled Maintenance | 37037 | 11136.8201
625 | 2024-05-30 | 2025 | 2024 | 2024-05-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 155 | SLC SF system monitoring | Connectivity issue | 0.80972 | 0.80972 | 0.99097 | 0 | 4.35 | 4.35 | Due to not available Scada connectivity after time physically check WTG so, found in stop condition. So, connect WTG manually then checked all data log and reset & run the WTG. | Close | 0.16731 | O2_05 | 6713 |  | WTG Unscheduled Maintenance | 37037 | 6712.9563
626 | 2024-05-31 | 2025 | 2024 | 2024-05-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.61458 | 0.61458 | 0.61944 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & run the WTG. | Close | 0.0044872 | O2_12 | 159 |  | WTG Unscheduled Maintenance | 32626 | 158.5986
627 | 2024-05-31 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 973 | Check blade bend.mom. | Break down | 0.45069 | 0.45069 | 0.45208 | 0 | 0.033333 | 0.033333 | Auto reset error then start WTG. | Close | 0.0012821 | O2_12 | 45 |  | WTG Unscheduled Maintenance | 32626 | 45.3139
628 | 2024-05-31 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 973 | Check blade bend.mom. | Break down | 0.58333 | 0.58333 | 0.58403 | 0 | 0.016667 | 0.016667 | Auto reset error then start WTG. | Close | 0.00064103 | O2_12 | 23 |  | WTG Unscheduled Maintenance | 32626 | 22.6569
629 | 2024-05-31 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.58889 | 0.58889 | 0.59722 | 0 | 0.2 | 0.2 | Checked related error data log then reset & run the WTG. | Close | 0.0076923 | O2_12 | 272 |  | WTG Unscheduled Maintenance | 32626 | 271.8833
630 | 2024-05-31 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 973 | Check blade bend.mom. | Break down | 0.60625 | 0.60625 | 0.60694 | 0 | 0.016667 | 0.016667 | Auto reset error then start WTG. | Close | 0.00064103 | O2_12 | 23 |  | WTG Unscheduled Maintenance | 32626 | 22.6569
631 | 2024-05-31 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 973 | Check blade bend.mom. | Break down | 0.62083 | 0.62083 | 0.62153 | 0 | 0.016667 | 0.016667 | Auto reset error then start WTG. | Close | 0.00064103 | O2_12 | 23 |  | WTG Unscheduled Maintenance | 32626 | 22.6569
632 | 2024-05-31 | 2025 | 2024 | 2024-05-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.625 | 0.625 | 0.75486 | 0 | 3.1167 | 3.1167 | WTG manually stop for repeated error inspection. So, checked repeated errors related cut and error data log also checked all connection and checked power curve issue related connection and its cut. Also checked load sensor and its cable then done its calibration. After complete all work then reset all errors data log and run the WTG. | Close | 0.11987 | O2_12 | 4237 |  | WTG Breakdown Maintenance | 32626 | 4236.8486
633 | 2024-05-31 | 2025 | 2024 | 2024-05-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.23958 | 0.23958 | 0.24653 | 0 | 0.16667 | 0.16667 | Checked related error data log then reset & run the WTG. | Close | 0.0064103 | O2_15 | 228 |  | WTG Unscheduled Maintenance | 32864 | 228.2222
634 | 2024-05-31 | 2025 | 2024 | 2024-05-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 973 | Check blade bend.mom. | Break down | 0.41875 | 0.41875 | 0.41944 | 0 | 0.016667 | 0.016667 | Auto reset error then start WTG. | Close | 0.00064103 | O2_20 | 21 |  | WTG Unscheduled Maintenance | 30256 | 21.0111
635 | 2024-05-31 | 2025 | 2024 | 2024-05-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.42292 | 0.42292 | 0.42986 | 0 | 0.16667 | 0.16667 | Checked related error data log then reset & run the WTG. | Close | 0.0064103 | O2_20 | 210 |  | WTG Unscheduled Maintenance | 30256 | 210.1111
636 | 2024-05-31 | 2025 | 2024 | 2024-05-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.63681 | 0.63681 | 0.64028 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_20 | 105 |  | WTG Unscheduled Maintenance | 30256 | 105.0556
637 | 2024-05-31 | 2025 | 2024 | 2024-05-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.40972 | 0.40972 | 0.42569 | 0 | 0.38333 | 0.38333 | Checked related error data log then reset & run the WTG. | Close | 0.014744 | O2_16 | 482 |  | WTG Unscheduled Maintenance | 30151 | 481.5785
638 | 2024-05-31 | 2025 | 2024 | 2024-05-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.37778 | 0.37778 | 0.54653 | 0 | 4.05 | 4.05 | Attend and checked related error data log also checked its cut and all connection then checked operation of hydraulic valve. Found normal so reset all error then run the WTG. | Close | 0.15577 | O2_05 | 6206 |  | WTG Unscheduled Maintenance | 36776 | 6205.95
639 | 2024-05-31 | 2025 | 2024 | 2024-05-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.65139 | 0.65139 | 0.82292 | 0 | 4.1167 | 4.1167 | Attend and checked related error data log, also checked all connection and its tightness. Found contamination in solenoid valve. So, properly clean it then reset all error log then run the WTG. | Close | 0.15833 | O2_05 | 6308 |  | WTG Unscheduled Maintenance | 36776 | 6308.1056
640 | 2024-06-01 | 2025 | 2024 | 2024-06-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.70625 | 0.70625 | 0.80694 | 0 | 2.4167 | 2.4167 | Attend and checked related error data log, also checked all connection and its tightness. Then found wind sensor alignment some deviation. So, correct it and properly done wind sensor alignment. After complete work then reset all error data log then run the WTG. | Close | 0.092949 | O2_14 | 2909 |  | WTG Unscheduled Maintenance | 28891 | 2909.1632
641 | 2024-06-01 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.60069 | 0.60069 | 0.65278 | 0 | 1.25 | 1.25 | After grid resume so, checked related error data log then reset & run the WTG. | Close | 0.048077 | O2_13 | 138 |  | WTG Unscheduled Maintenance | 28403 | 1479.3229
642 | 2024-06-01 | 2025 | 2024 | 2024-06-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.60069 | 0.60069 | 0.65139 | 0 | 1.2167 | 1.2167 | After grid resume so, checked related error data log then reset & run the WTG. | Close | 0.046795 | O2_09 | 1537 |  | WTG Unscheduled Maintenance | 30319 | 1537.0049
643 | 2024-06-01 | 2025 | 2024 | 2024-06-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.74236 | 0.74236 | 0.76042 | 0 | 0.43333 | 0.43333 | Checked related error data log then reset & run the WTG. | Close | 0.016667 | O2_14 | 522 |  | WTG Unscheduled Maintenance | 28891 | 521.6431
644 | 2024-06-01 | 2025 | 2024 | 2024-06-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.77917 | 0.77917 | 0.84306 | 0 | 1.5333 | 1.5333 | WTG manually stop for O2 project team closing pending points. | Close | 0.058974 | O2_20 | 1297 |  | WTG Breakdown Maintenance | 20302 | 1297.0722
645 | 2024-06-02 | 2025 | 2024 | 2024-06-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.76944 | 0.76944 | 0.8 | 0 | 0.73333 | 0.73333 | After grid resume so, checked related error data log then reset & run the WTG. | Close | 0.028205 | O2_14 | 481 |  | WTG Unscheduled Maintenance | 15751 | 481.2806
646 | 2024-06-02 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.39722 | 0.39722 | 0.41181 | 0 | 0.35 | 0.35 | After grid resume so, checked related error data log then reset & run the WTG. | Close | 0.013462 | O2_12 | 231 |  | WTG Unscheduled Maintenance | 15856 | 231.2333
647 | 2024-06-02 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.52431 | 0.52431 | 0.53264 | 0 | 0.2 | 0.2 | Checked related error data log then reset & run the WTG. | Close | 0.0076923 | O2_12 | 132 |  | WTG Unscheduled Maintenance | 15856 | 132.1333
648 | 2024-06-02 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 2687 | Max. slip ring cell temp. | Break down | 0.70347 | 0.70347 | 0.71042 | 0 | 0.16667 | 0.16667 | Checked related error data log then reset & run the WTG. | Close | 0.0064103 | O2_12 | 110 |  | WTG Unscheduled Maintenance | 15856 | 110.1111
649 | 2024-06-02 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.76944 | 0.76944 | 0.80694 | 0 | 0.9 | 0.9 | After grid resume so, checked related error data log then reset & run the WTG. | Close | 0.034615 | O2_12 | 595 |  | WTG Unscheduled Maintenance | 15856 | 594.6
650 | 2024-06-02 | 2025 | 2024 | 2024-06-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.25556 | 0.25556 | 0.26319 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & run the WTG. | Close | 0.0070513 | O2_15 | 118 |  | WTG Unscheduled Maintenance | 15504 | 118.4333
651 | 2024-06-02 | 2025 | 2024 | 2024-06-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.39722 | 0.39722 | 0.45556 | 0 | 1.4 | 1.4 | After grid resume so, checked related error data log then reset & run the WTG. | Close | 0.053846 | O2_15 | 904 |  | WTG Unscheduled Maintenance | 15504 | 904.4
652 | 2024-06-02 | 2025 | 2024 | 2024-06-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.76944 | 0.76944 | 0.79375 | 0 | 0.58333 | 0.58333 | After grid resume so, checked related error data log then reset & run the WTG. | Close | 0.022436 | O2_15 | 377 |  | WTG Unscheduled Maintenance | 15504 | 376.8333
653 | 2024-06-02 | 2025 | 2024 | 2024-06-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.37222 | 0.37222 | 0.77778 | 0 | 9.7333 | 9.7333 | WTG manually stop for O2 project team closing pending points. | Close | 0.37436 | O2_15 | 6288 |  | WTG Breakdown Maintenance | 15504 | 6287.7333
654 | 2024-06-02 | 2025 | 2024 | 2024-06-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.37222 | 0.37222 | 0.79375 | 0 | 10.1167 | 10.1167 | WTG manually stop for O2 project team closing pending points. | Close | 0.3891 | O2_14 | 6639 |  | WTG Breakdown Maintenance | 15751 | 6639.484
655 | 2024-06-02 | 2025 | 2024 | 2024-06-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.79375 | 0.79375 | 0.80486 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_20 | 178 |  | WTG Unscheduled Maintenance | 16028 | 178.0889
656 | 2024-06-02 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.39722 | 0.39722 | 0.40972 | 0 | 0.3 | 0.3 | After grid resume so, checked related error data log then reset & run the WTG. | Close | 0.011538 | O2_03 | 188 |  | WTG Unscheduled Maintenance | 15044 | 188.05
657 | 2024-06-02 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.76944 | 0.76944 | 0.78403 | 0 | 0.35 | 0.35 | After grid resume so, checked related error data log then reset & run the WTG. | Close | 0.013462 | O2_03 | 219 |  | WTG Unscheduled Maintenance | 15044 | 219.3917
658 | 2024-06-03 | 2025 | 2024 | 2024-06-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 6012 | Overload yaw motors group 2 | Break down | 0.44653 | 0.44653 | 0.50278 | 0 | 1.35 | 1.35 | Attend and checked related error data log, also checked all connection and cut with its tightness then found Yaw motor MPCB trip. So, before switch on set current value in MPCB then switch on. After complete work then reset all errors then run the WTG. | Close | 0.051923 | O2_05 | 760 |  | WTG Unscheduled Maintenance | 13517 | 760.3312
659 | 2024-06-03 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.43403 | 0.43403 | 0.44236 | 0 | 0.2 | 0.2 | Checked related error data log then reset & run the WTG. | Close | 0.0076923 | O2_13 | 145.6167 |  | WTG Unscheduled Maintenance | 17474 | 145.6167
660 | 2024-06-03 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.99028 | 0.99028 | 1899-12-31 | 0 | 0.23333 | 0.23333 | Checked related error data log then reset & run the WTG. | Close | 0.0089744 | O2_13 | 169.8861 |  | WTG Unscheduled Maintenance | 17474 | 169.8861
661 | 2024-06-03 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.55347 | 0.55347 | 0.56667 | 0 | 0.31667 | 0.31667 | Checked related error data log then reset & run the WTG. | Close | 0.012179 | O2_12 | 281.9917 |  | WTG Unscheduled Maintenance | 21372 | 281.9917
662 | 2024-06-03 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.60139 | 0.60139 | 0.6125 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_12 | 237.4667 |  | WTG Unscheduled Maintenance | 21372 | 237.4667
663 | 2024-06-03 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.69306 | 0.69306 | 0.72778 | 0 | 0.83333 | 0.83333 | Checked related error data log then reset & run the WTG. | Close | 0.032051 | O2_12 | 742.0833 |  | WTG Unscheduled Maintenance | 21372 | 742.0833
664 | 2024-06-03 | 2025 | 2024 | 2024-06-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.825 | 0.825 | 0.83819 | 0 | 0.31667 | 0.31667 | Checked related error data log then reset & run the WTG. | Close | 0.012179 | O2_09 | 275.3153 |  | WTG Unscheduled Maintenance | 20866 | 275.3153
665 | 2024-06-03 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.87431 | 0.87431 | 0.88472 | 0 | 0.25 | 0.25 | Checked related error data log then reset & run the WTG. | Close | 0.0096154 | O2_03 | 207 |  | WTG Unscheduled Maintenance | 19872 | 207
666 | 2024-06-03 | 2025 | 2024 | 2024-06-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.70764 | 0.70764 | 0.87431 | 0 | 4 | 4 | WTG manually stop for O2 project team closing pending points. | Close | 0.15385 | O2_16 | 11077 |  | WTG Breakdown Maintenance | 22154 | 3692.3333
667 | 2024-06-04 | 2025 | 2024 | 2024-06-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.76597 | 0.76597 | 0.7875 | 0 | 0.51667 | 0.51667 | After grid resume wtg in error Checked related error data log then found vcb trip so charge vcb than reset & run the WTG. | Close | 0.019872 | O2_12 | 389.6313 |  | WTG Unscheduled Maintenance | 18099 | 389.6313
668 | 2024-06-04 | 2025 | 2024 | 2024-06-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 973 | Check blade bend.mom. | Break down | 0.84792 | 0.84792 | 0.85764 | 0 | 0.23333 | 0.23333 | Checked related error data log then reset & run the WTG. | Close | 0.0089744 | O2_12 | 175.9625 |  | WTG Unscheduled Maintenance | 18099 | 175.9625
669 | 2024-06-04 | 2025 | 2024 | 2024-06-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 578 | Pitch set point slow hold time BP75 | Break down | 0.90139 | 0.90139 | 0.92292 | 0 | 0.51667 | 0.51667 | Checked related error data log then reset & run the WTG. | Close | 0.019872 | O2_12 | 389.6312 |  | WTG Unscheduled Maintenance | 18099 | 389.6312
670 | 2024-06-04 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.041667 | 0.041667 | 0.047917 | 0 | 0.15 | 0.15 | Checked related error data log then reset & run the WTG. | Close | 0.0057692 | O2_11 | 89.5062 |  | WTG Unscheduled Maintenance | 14321 | 89.5062
671 | 2024-06-04 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Connectivity issue | 0.72708 | 0.72708 | 0.77847 | 0 | 1.2333 | 1.2333 | Checked related error data log then found vcb trip so charge vcb than reset & run the WTG.(late start due to connectivity issue due to after grid resume o2 11 vcb) trip | Close | 0.047436 | O2_11 | 735.9403 |  | WTG Unscheduled Maintenance | 14321 | 735.9403
672 | 2024-06-04 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.6125 | 0.6125 | 0.62431 | 0 | 0.28333 | 0.28333 | Checked related error data log then reset & run the WTG. | Close | 0.010897 | O2_11 | 169.0674 |  | WTG Unscheduled Maintenance | 14321 | 169.0674
673 | 2024-06-04 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.7625 | 0.7625 | 0.78056 | 0 | 0.43333 | 0.43333 | Checked related error data log then reset & run the WTG. | Close | 0.016667 | O2_11 | 258.5736 |  | WTG Unscheduled Maintenance | 14321 | 258.5736
674 | 2024-06-04 | 2025 | 2024 | 2024-06-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Break down | 0.70417 | 0.70417 | 0.71528 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_20 | 294.9778 |  | WTG Unscheduled Maintenance | 26548 | 294.9778
675 | 2024-06-04 | 2025 | 2024 | 2024-06-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3060 | Conv. emerg.off type A | Connectivity issue | 0.72708 | 0.72708 | 0.76806 | 0 | 0.98333 | 0.98333 | Checked related error data log then found vcb trip so charge vcb than reset & run the WTG.(late start due to connectivity issue due to after grid resume o2 11 vcb) trip | Close | 0.037821 | O2_09 | 872.5444 |  | WTG Unscheduled Maintenance | 21296 | 872.5444
676 | 2024-06-04 | 2025 | 2024 | 2024-06-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Connectivity issue | 0.72708 | 0.72708 | 0.75 | 0 | 0.55 | 0.55 | Checked related error data log then reset & run the WTG. Late start due to 02 11 VCB trip so connectivity issue after connectivity restore reset and start WTG | Close | 0.021154 | O2_09 | 488.0333 |  | WTG Unscheduled Maintenance | 21296 | 488.0333
677 | 2024-06-04 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Connectivity issue | 0.72708 | 0.72708 | 0.77639 | 0 | 1.1833 | 1.1833 | Checked related error data log then found vcb trip so charge vcb than reset & run the WTG.(late start due to connectivity issue due to after grid resume o2 11 vcb) trip | Close | 0.045513 | O2_03 | 928.4729 |  | WTG Unscheduled Maintenance | 18831 | 928.4729
678 | 2024-06-04 | 2025 | 2024 | 2024-06-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 2340 | Temp. rot.br.pad implaus. | Break down | 0.052083 | 0.052083 | 0.15833 | 0 | 2.55 | 2.55 | attend and check related circuit than check break pad PT100 sensor than check pad gap than nothing found abnormal than reset and start WTG | Close | 0.098077 | O2_03 | 2680.9 |  | WTG Unscheduled Maintenance | 25232 | 2680.9
679 | 2024-06-04 | 2025 | 2024 | 2024-06-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.72708 | 0.72708 | 0.75694 | 0 | 0.71667 | 0.71667 | After grid resume wtg in error so attend and check event than apply hard reboot than reset and start WTG. | Close | 0.027564 | O2_05 | 463.1458 |  | WTG Unscheduled Maintenance | 15510 | 463.1458
680 | 2024-06-04 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.35625 | 0.35625 | 0.72708 | 0 | 8.9 | 8.9 | WTG manually stop for O2 project team closing pending points. | Close | 0.34231 | O2_03 | 6983.1625 |  | WTG Breakdown Maintenance | 18831 | 6983.1625
681 | 2024-06-04 | 2025 | 2024 | 2024-06-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.35625 | 0.35625 | 0.72708 | 0 | 8.9 | 8.9 | WTG manually stop for O2 project team closing pending points. | Close | 0.34231 | O2_12 | 6711.7125 |  | WTG Breakdown Maintenance | 18099 | 6711.7125
682 | 2024-06-04 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.35625 | 0.35625 | 0.72708 | 0 | 8.9 | 8.9 | WTG manually stop for O2 project team closing pending points. | Close | 0.34231 | O2_11 | 5310.7042 |  | WTG Breakdown Maintenance | 14321 | 5310.7042
683 | 2024-06-04 | 2025 | 2024 | 2024-06-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.35625 | 0.35625 | 0.72708 | 0 | 8.9 | 8.9 | WTG manually stop for O2 project team closing pending points. | Close | 0.34231 | O2_09 | 7897.2667 |  | WTG Breakdown Maintenance | 21296 | 7897.2667
684 | 2024-06-04 | 2025 | 2024 | 2024-06-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.35625 | 0.35625 | 0.72708 | 0 | 8.9 | 8.9 | WTG manually stop for O2 project team closing pending points. | Close | 0.34231 | O2_05 | 5751.625 |  | WTG Breakdown Maintenance | 15510 | 5751.625
685 | 2024-06-04 | 2025 | 2024 | 2024-06-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.35625 | 0.35625 | 0.72708 | 0 | 8.9 | 8.9 | WTG manually stop for O2 project team closing pending points. | Close | 0.34231 | O2_02 | 9356.8667 |  | WTG Breakdown Maintenance | 25232 | 9356.8667
686 | 2024-06-05 | 2025 | 2024 | 2024-06-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.36736 | 0.36736 | 0.60486 | 0 | 5.7 | 5.7 | WTG manually stop for O2 project team closing pending points. | Close | 0.21923 | O2_09 | 6197.325 |  | WTG Breakdown Maintenance | 26094 | 6197.325
687 | 2024-06-05 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.36736 | 0.36736 | 0.60486 | 0 | 5.7 | 5.7 | WTG manually stop for O2 project team closing pending points. | Close | 0.21923 | O2_11 | 5998.775 |  | WTG Breakdown Maintenance | 25258 | 5998.775
688 | 2024-06-05 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.70694 | 0.70694 | 0.725 | 0 | 0.43333 | 0.43333 | After grid resume wtg in error so check event than reset and start WTG. | Close | 0.016667 | O2_03 | 375.3569 |  | WTG Unscheduled Maintenance | 20789 | 375.3569
689 | 2024-06-05 | 2025 | 2024 | 2024-06-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.70694 | 0.70694 | 0.725 | 0 | 0.43333 | 0.43333 | After grid resume wtg in error so check event than reset and start WTG. | Close | 0.016667 | O2_15 | 444.9069 |  | WTG Unscheduled Maintenance | 24641 | 444.9069
690 | 2024-06-05 | 2025 | 2024 | 2024-06-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.37361 | 0.37361 | 0.38958 | 0 | 0.38333 | 0.38333 | After grid resume wtg in error so check event than reset and start WTG. | Close | 0.014744 | O2_12 | 328.7562 |  | WTG Unscheduled Maintenance | 20583 | 328.7562
691 | 2024-06-05 | 2025 | 2024 | 2024-06-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.70694 | 0.70694 | 0.725 | 0 | 0.43333 | 0.43333 | After grid resume wtg in error so check event than reset and start WTG. | Close | 0.016667 | O2_12 | 371.6375 |  | WTG Unscheduled Maintenance | 20583 | 371.6375
692 | 2024-06-05 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.70694 | 0.70694 | 0.75833 | 0 | 1.2333 | 1.2333 | After grid resume wtg in error so check event than reset and start WTG. | Close | 0.047436 | O2_11 | 1297.9806 |  | WTG Unscheduled Maintenance | 25258 | 1297.9806
693 | 2024-06-05 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.5 | 0.5 | 0.60486 | 0 | 2.5167 | 2.5167 | WTG manually stop for O2 project team closing pending points and ladder repairing and also power curve rectification work done. | Close | 0.096795 | O2_12 | 2158.3563 |  | WTG Breakdown Maintenance | 20583 | 2158.3563
694 | 2024-06-05 | 2025 | 2024 | 2024-06-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.19375 | 0.19375 | 0.20208 | 0 | 0.2 | 0.2 | Checked related error data log then reset & run the WTG. | Close | 0.0076923 | O2_13 | 184.1667 |  | WTG Unscheduled Maintenance | 22100 | 184.1667
695 | 2024-06-05 | 2025 | 2024 | 2024-06-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.70903 | 0.70903 | 0.72708 | 0 | 0.43333 | 0.43333 | Checked related error data log then reset & run the WTG. | Close | 0.016667 | O2_13 | 399.0278 |  | WTG Unscheduled Maintenance | 22100 | 399.0278
696 | 2024-06-05 | 2025 | 2024 | 2024-06-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.70694 | 0.70694 | 0.74375 | 0 | 0.88333 | 0.88333 | After grid resume wtg in error so attend and check event than reset and start WTG. | Close | 0.033974 | O2_09 | 960.4042 |  | WTG Unscheduled Maintenance | 26094 | 960.4042
697 | 2024-06-05 | 2025 | 2024 | 2024-06-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Connectivity issue | 0.36736 | 0.36736 | 0.44653 | 0 | 1.9 | 1.9 | After grid resume wtg in error so attend and check event than apply hard reboot than reset and start WTG. Late start due to connectivity issue. | Close | 0.073077 | O2_02 | 1988.2708 |  | WTG Unscheduled Maintenance | 25115 | 1988.2708
698 | 2024-06-05 | 2025 | 2024 | 2024-06-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.077778 | 0.077778 | 0.091667 | 0 | 0.33333 | 0.33333 | Checked related error data log then reset & run the WTG. | Close | 0.012821 | O2_05 | 281.5833 |  | WTG Unscheduled Maintenance | 20274 | 281.5833
699 | 2024-06-05 | 2025 | 2024 | 2024-06-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Connectivity issue | 0.36736 | 0.36736 | 0.45347 | 0 | 2.0667 | 2.0667 | After grid resume wtg in error so check event than reset and start WTG. Late start due to connectivity issue. | Close | 0.079487 | O2_05 | 1745.8167 |  | WTG Unscheduled Maintenance | 20274 | 1745.8167
700 | 2024-06-06 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.27014 | 0.27014 | 0.27847 | 0 | 0.2 | 0.2 | Checked related error data log then reset & run the WTG. | Close | 0.0076923 | O2_03 | 177.0417 |  | WTG Unscheduled Maintenance | 21245 | 177.0417
701 | 2024-06-06 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 2521 | Gen.sp.analog <<>> gearb.sp. | Break down | 0.56597 | 0.56597 | 0.57708 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_03 | 236.0556 |  | WTG Unscheduled Maintenance | 21245 | 236.0556
702 | 2024-06-06 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 72 | Outdoor temperature high | Break down | 0.67431 | 0.67431 | 0.71875 | 0 | 1.0667 | 1.0667 | attend and found outside temperature sensor was malfunctioning so check related circuit and refight all related connection than reset and start WTG. | Close | 0.041026 | O2_03 | 944.2222 |  | WTG Unscheduled Maintenance | 21245 | 944.2222
703 | 2024-06-06 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.95417 | 0.95417 | 0.96458 | 0 | 0.25 | 0.25 | Checked related error data log then reset & run the WTG. | Close | 0.0096154 | O2_03 | 221.3021 |  | WTG Unscheduled Maintenance | 21245 | 221.3021
704 | 2024-06-06 | 2025 | 2024 | 2024-06-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 578 | Pitch set point slow hold time BP75 | Break down | 0.88681 | 0.88681 | 0.90347 | 0 | 0.4 | 0.4 | Checked related error data log then reset & run the WTG. | Close | 0.015385 | O2_11 | 326.0833 |  | WTG Unscheduled Maintenance | 19565 | 326.0833
705 | 2024-06-06 | 2025 | 2024 | 2024-06-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | ROW issue | 0.53056 | 0.53056 | 0.57778 | 0 | 1.1333 | 1.1333 | check and found VCB trip by unknown ROW person so charge normally than reset and start WTG | Close | 0.04359 | O2_12 | 997.9472 |  | WTG Unscheduled Maintenance | 21133 | 997.9472
706 | 2024-06-06 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3590 | Overvoltage | Connectivity issue | 0.54097 | 0.54097 | 0.57014 | 0 | 0.7 | 0.7 | checked data then reset and start WTG late reset due connectivity issue. | Close | 0.026923 | O2_13 | 608.5917 |  | WTG Unscheduled Maintenance | 20866 | 608.5917
707 | 2024-06-06 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.70903 | 0.70903 | 0.72014 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_12 | 234.8111 |  | WTG Unscheduled Maintenance | 21133 | 234.8111
708 | 2024-06-06 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.75139 | 0.75139 | 0.7625 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_12 | 234.8111 |  | WTG Unscheduled Maintenance | 21133 | 234.8111
709 | 2024-06-07 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 2687 | Max. slip ring cell temp. | Break down | 0.6 | 0.6 | 0.61389 | 0 | 0.33333 | 0.33333 | Checked related error data log then reset & run the WTG. | Close | 0.012821 | O2_03 | 351.1111 |  | WTG Unscheduled Maintenance | 25280 | 351.1111
710 | 2024-06-07 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 2687 | Max. slip ring cell temp. | Break down | 0.63819 | 0.63819 | 0.64306 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & run the WTG. | Close | 0.0044872 | O2_03 | 115.7236 |  | WTG Unscheduled Maintenance | 23806 | 115.7236
711 | 2024-06-07 | 2025 | 2024 | 2024-06-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 2687 | Max. slip ring cell temp. | Break down | 0.69375 | 0.69375 | 0.70972 | 0 | 0.38333 | 0.38333 | Checked related error data log then reset & run the WTG. | Close | 0.014744 | O2_12 | 380.2347 |  | WTG Unscheduled Maintenance | 23806 | 380.2347
712 | 2024-06-07 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 2828 | Timeout fault gen. lubrication | Break down | 0.33056 | 0.33056 | 0.35694 | 0 | 0.63333 | 0.63333 | Checked related error data log then reset & run the WTG. | Close | 0.024359 | O2_12 | 628.2139 |  | WTG Unscheduled Maintenance | 23806 | 628.2139
713 | 2024-06-07 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3065 | Conv. emerg.off type F | Break down | 0.47153 | 0.47153 | 0.47569 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2_12 | 99.1917 |  | WTG Unscheduled Maintenance | 23806 | 99.1917
714 | 2024-06-07 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.59028 | 0.59028 | 0.59375 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_12 | 82.6597 |  | WTG Unscheduled Maintenance | 23806 | 82.6597
715 | 2024-06-07 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.62431 | 0.62431 | 0.63264 | 0 | 0.2 | 0.2 | Checked related error data log then reset & run the WTG. | Close | 0.0076923 | O2_12 | 198.3833 |  | WTG Unscheduled Maintenance | 23806 | 198.3833
716 | 2024-06-07 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 973 | Check blade bend.mom. | Break down | 0.78681 | 0.78681 | 0.79306 | 0 | 0.15 | 0.15 | Checked related error data log then reset & run the WTG. | Close | 0.0057692 | O2_12 | 148.7875 |  | WTG Unscheduled Maintenance | 23806 | 148.7875
717 | 2024-06-07 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.79306 | 0.79306 | 0.81389 | 0 | 0.5 | 0.5 | Checked related error data log then reset & run the WTG. | Close | 0.019231 | O2_12 | 495.9583 |  | WTG Unscheduled Maintenance | 23806 | 495.9583
718 | 2024-06-07 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.89028 | 0.89028 | 0.89722 | 0 | 0.16667 | 0.16667 | Checked related error data log then reset & run the WTG. | Close | 0.0064103 | O2_12 | 165.3194 |  | WTG Unscheduled Maintenance | 23806 | 165.3194
719 | 2024-06-07 | 2025 | 2024 | 2024-06-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 3065 | Conv. emerg.off type F | Break down | 0.69931 | 0.69931 | 0.71111 | 0 | 0.28333 | 0.28333 | Checked related error data log then reset & run the WTG. | Close | 0.010897 | O2_13 | 188.3104 |  | WTG Unscheduled Maintenance | 15951 | 188.3104
720 | 2024-06-07 | 2025 | 2024 | 2024-06-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.69653 | 0.69653 | 0.70208 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & run the WTG. | Close | 0.0051282 | O2_09 | 138.5278 |  | WTG Unscheduled Maintenance | 24935 | 138.5278
721 | 2024-06-07 | 2025 | 2024 | 2024-06-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Connectivity issue | 0.87431 | 0.87431 | 1899-12-31 | 0 | 3.0167 | 3.0167 | Checked related error data log then reset & run the WTG late reset due to connectivity issue. | Close | 0.11603 | O2_02 | 3385.2028 |  | WTG Unscheduled Maintenance | 26932 | 3385.2028
722 | 2024-06-08 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.60764 | 0.60764 | 0.61944 | 0 | 0.28333 | 0.28333 | WTG manual stop for PPC file configuration. | Close | 0.010897 | O2_03 | 201.4028 |  | WTG Breakdown Maintenance | 17060 | 201.4028
723 | 2024-06-08 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.80625 | 0.80625 | 0.87153 | 0 | 1.5667 | 1.5667 | attend and check related circuit than nothing found abnormal than apply hard reboot than reset and start WTG | Close | 0.060256 | O2_03 | 1113.6389 |  | WTG Unscheduled Maintenance | 17060 | 1113.6389
724 | 2024-06-08 | 2025 | 2024 | 2024-06-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.61736 | 0.61736 | 0.62708 | 0 | 0.23333 | 0.23333 | WTG manual stop for PPC file configuration. | Close | 0.0089744 | O2_11 | 167.3583 |  | WTG Breakdown Maintenance | 17214 | 167.3583
725 | 2024-06-08 | 2025 | 2024 | 2024-06-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.80625 | 0.80625 | 0.81458 | 0 | 0.2 | 0.2 | After grid resume wtg in error so check error data and reset and start WTG | Close | 0.0076923 | O2_11 | 143.45 |  | WTG Unscheduled Maintenance | 17214 | 143.45
726 | 2024-06-08 | 2025 | 2024 | 2024-06-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.37083 | 0.37083 | 0.3875 | 0 | 0.4 | 0.4 | After grid resume wtg in error so check error data and reset and start WTG | Close | 0.015385 | O2_10 | 255.6167 |  | WTG Unscheduled Maintenance | 15337 | 255.6167
727 | 2024-06-08 | 2025 | 2024 | 2024-06-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.62778 | 0.62778 | 0.63681 | 0 | 0.21667 | 0.21667 | WTG manual stop for PPC file configuration. | Close | 0.0083333 | O2_10 | 138.459 |  | WTG Breakdown Maintenance | 15337 | 138.459
728 | 2024-06-08 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.37847 | 0.37847 | 0.39097 | 0 | 0.3 | 0.3 | After gride resume wtg in error so check error data than reset and start WTG | Close | 0.011538 | O2_11 | 215.175 |  | WTG Unscheduled Maintenance | 17214 | 215.175
729 | 2024-06-08 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.63611 | 0.63611 | 0.64653 | 0 | 0.25 | 0.25 | WTG manual stop for PPC file configuration. | Close | 0.0096154 | O2_11 | 179.3125 |  | WTG Breakdown Maintenance | 17214 | 179.3125
730 | 2024-06-08 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.37083 | 0.37083 | 0.39167 | 0 | 0.5 | 0.5 | After grid resume wtg in error so check error data and reset and start WTG | Close | 0.019231 | O2_12 | 318 |  | WTG Unscheduled Maintenance | 15264 | 318
731 | 2024-06-08 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.45833 | 0.45833 | 0.46597 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & run the WTG. | Close | 0.0070513 | O2_12 | 116.6 |  | WTG Unscheduled Maintenance | 15264 | 116.6
732 | 2024-06-08 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.64444 | 0.64444 | 0.65139 | 0 | 0.16667 | 0.16667 | WTG manual stop for PPC file configuration. | Close | 0.0064103 | O2_12 | 106 |  | WTG Breakdown Maintenance | 15264 | 106
733 | 2024-06-08 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.80694 | 0.80694 | 0.82222 | 0 | 0.36667 | 0.36667 | After grid resume wtg in error so check error data and reset and start WTG | Close | 0.014103 | O2_12 | 233.2 |  | WTG Unscheduled Maintenance | 15264 | 233.2
734 | 2024-06-08 | 2025 | 2024 | 2024-06-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.37083 | 0.37083 | 0.39167 | 0 | 0.5 | 0.5 | After grid resume wtg in error so check error data and reset and start WTG | Close | 0.019231 | O2_13 | 340.2708 |  | WTG Unscheduled Maintenance | 16333 | 340.2708
735 | 2024-06-08 | 2025 | 2024 | 2024-06-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.49306 | 0.49306 | 0.49792 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & run the WTG. | Close | 0.0044872 | O2_13 | 79.3965 |  | WTG Unscheduled Maintenance | 16333 | 79.3965
736 | 2024-06-08 | 2025 | 2024 | 2024-06-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.65208 | 0.65208 | 0.67292 | 0 | 0.5 | 0.5 | WTG manual stop for PPC file configuration. | Close | 0.019231 | O2_13 | 340.2708 |  | WTG Breakdown Maintenance | 16333 | 340.2708
737 | 2024-06-08 | 2025 | 2024 | 2024-06-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.80764 | 0.80764 | 0.81597 | 0 | 0.2 | 0.2 | After grid resume wtg in error so check error data and reset and start WTG | Close | 0.0076923 | O2_13 | 136.1083 |  | WTG Unscheduled Maintenance | 16333 | 136.1083
738 | 2024-06-08 | 2025 | 2024 | 2024-06-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.67361 | 0.67361 | 0.68056 | 0 | 0.16667 | 0.16667 | WTG manual stop for PPC file configuration. | Close | 0.0064103 | O2_20 | 124.7847 |  | WTG Breakdown Maintenance | 17969 | 124.7847
739 | 2024-06-08 | 2025 | 2024 | 2024-06-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Break down | 0.77431 | 0.77431 | 0.77917 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & run the WTG. | Close | 0.0044872 | O2_20 | 87.3493 |  | WTG Unscheduled Maintenance | 17969 | 87.3493
740 | 2024-06-08 | 2025 | 2024 | 2024-06-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.98472 | 0.98472 | 1899-12-31 | 0 | 0.36667 | 0.36667 | Checked related error data log then reset & run the WTG. | Close | 0.014103 | O2_20 | 274.5264 |  | WTG Unscheduled Maintenance | 17969 | 274.5264
741 | 2024-06-08 | 2025 | 2024 | 2024-06-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.37083 | 0.37083 | 0.40278 | 0 | 0.76667 | 0.76667 | After grid resume wtg in error so check error data and reset and start WTG | Close | 0.029487 | O2_09 | 485.0125 |  | WTG Unscheduled Maintenance | 15183 | 485.0125
742 | 2024-06-08 | 2025 | 2024 | 2024-06-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.51458 | 0.51458 | 0.52361 | 0 | 0.21667 | 0.21667 | Checked related error data log then reset & run the WTG. | Close | 0.0083333 | O2_09 | 137.0688 |  | WTG Unscheduled Maintenance | 15183 | 137.0688
743 | 2024-06-08 | 2025 | 2024 | 2024-06-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.56528 | 0.56528 | 0.59167 | 0 | 0.63333 | 0.63333 | WTG manual stop for PPC file configuration. | Close | 0.024359 | O2_09 | 400.6625 |  | WTG Breakdown Maintenance | 15183 | 400.6625
744 | 2024-06-08 | 2025 | 2024 | 2024-06-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Break down | 0.80625 | 0.80625 | 0.82639 | 0 | 0.48333 | 0.48333 | After grid resume wtg in error so check error data and reset and start WTG | Close | 0.01859 | O2_09 | 305.7687 |  | WTG Unscheduled Maintenance | 15183 | 305.7687
745 | 2024-06-08 | 2025 | 2024 | 2024-06-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.66458 | 0.66458 | 0.67153 | 0 | 0.16667 | 0.16667 | WTG manual stop for PPC file configuration. | Close | 0.0064103 | O2_20 | 124.7847 |  | WTG Breakdown Maintenance | 17969 | 124.7847
746 | 2024-06-08 | 2025 | 2024 | 2024-06-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.68125 | 0.68125 | 0.68819 | 0 | 0.16667 | 0.16667 | WTG manual stop for PPC file configuration. | Close | 0.0064103 | O2_15 | 110.5625 |  | WTG Breakdown Maintenance | 15921 | 110.5625
747 | 2024-06-08 | 2025 | 2024 | 2024-06-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.37083 | 0.37083 | 0.74028 | 0 | 8.8667 | 8.8667 | WTG stop for OFC cable laying Work. | Close | 0.34103 | O2_05 | 6943.3389 |  | WTG Breakdown Maintenance | 18794 | 6943.3389
748 | 2024-06-08 | 2025 | 2024 | 2024-06-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Connectivity issue | 0.80625 | 0.80625 | 0.83403 | 0 | 0.66667 | 0.66667 | After grid resume wtg in error so check error data and reset and start WTG. Late reset due to connectivity issue | Close | 0.025641 | O2_05 | 522.0556 |  | WTG Unscheduled Maintenance | 18794 | 522.0556
749 | 2024-06-08 | 2025 | 2024 | 2024-06-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.37083 | 0.37083 | 0.74028 | 0 | 8.8667 | 8.8667 | WTG stop for OFC cable laying Work. | Close | 0.34103 | O2_02 | 7191.2361 |  | WTG Breakdown Maintenance | 19465 | 7191.2361
750 | 2024-06-08 | 2025 | 2024 | 2024-06-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.80625 | 0.80625 | 0.81042 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2_02 | 81.1042 |  | WTG Unscheduled Maintenance | 19465 | 81.1042
751 | 2024-06-09 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Connectivity issue | 0.32083 | 0.32083 | 0.34028 | 0 | 0.46667 | 0.46667 | After grid resume wtg in error so check error data and reset and start WTG. Late reset due to connectivity issue | Close | 0.017949 | O2_03 | 317.0222 |  | WTG Unscheduled Maintenance | 16304 | 317.0222
752 | 2024-06-09 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Connectivity issue | 0.38819 | 0.38819 | 0.40625 | 0 | 0.43333 | 0.43333 | After grid resume wtg in error so check error data and reset and start WTG. Late reset due to connectivity issue | Close | 0.016667 | O2_03 | 294.3778 |  | WTG Unscheduled Maintenance | 16304 | 294.3778
753 | 2024-06-09 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Connectivity issue | 0.81111 | 0.81111 | 0.82639 | 0 | 0.36667 | 0.36667 | After grid resume wtg in error so check error data and reset and start WTG. Late reset due to connectivity issue | Close | 0.014103 | O2_03 | 249.0889 |  | WTG Unscheduled Maintenance | 16304 | 249.0889
754 | 2024-06-09 | 2025 | 2024 | 2024-06-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Connectivity issue | 0.32083 | 0.32083 | 0.32917 | 0 | 0.2 | 0.2 | After grid resume wtg in error so check error data and reset and start WTG. Late reset due to connectivity issue | Close | 0.0076923 | O2_10 | 137.2667 |  | WTG Unscheduled Maintenance | 16472 | 137.2667
755 | 2024-06-09 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Connectivity issue | 0.32083 | 0.32083 | 0.33403 | 0 | 0.31667 | 0.31667 | After grid resume wtg in error so check error data and reset and start WTG. Late reset due to connectivity issue | Close | 0.012179 | O2_14 | 222.8674 |  | WTG Unscheduled Maintenance | 16891 | 222.8674
756 | 2024-06-09 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Connectivity issue | 0.38819 | 0.38819 | 0.40069 | 0 | 0.3 | 0.3 | After grid resume wtg in error so check error data and reset and start WTG. Late reset due to connectivity issue | Close | 0.011538 | O2_14 | 211.1375 |  | WTG Unscheduled Maintenance | 16891 | 211.1375
757 | 2024-06-09 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.56458 | 0.56458 | 0.56875 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2_14 | 70.3792 |  | WTG Unscheduled Maintenance | 16891 | 70.3792
758 | 2024-06-09 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.86875 | 0.86875 | 0.88125 | 0 | 0.3 | 0.3 | Checked related error data log then reset & run the WTG. | Close | 0.011538 | O2_14 | 211.1375 |  | WTG Unscheduled Maintenance | 16891 | 211.1375
759 | 2024-06-09 | 2025 | 2024 | 2024-06-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Connectivity issue | 0.32083 | 0.32083 | 0.33403 | 0 | 0.31667 | 0.31667 | After grid resume wtg in error so check error data and reset and start WTG. Late reset due to connectivity issue | Close | 0.012179 | O2_13 | 215.1222 |  | WTG Unscheduled Maintenance | 16304 | 215.1222
760 | 2024-06-09 | 2025 | 2024 | 2024-06-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 3060 | Conv. emerg.off type A | Connectivity issue | 0.38819 | 0.38819 | 0.39375 | 0 | 0.13333 | 0.13333 | After grid resume wtg in error so check error data and reset and start WTG. Late reset due to connectivity issue | Close | 0.0051282 | O2_13 | 90.5778 |  | WTG Unscheduled Maintenance | 16304 | 90.5778
761 | 2024-06-09 | 2025 | 2024 | 2024-06-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Connectivity issue | 0.32083 | 0.32083 | 0.3375 | 0 | 0.4 | 0.4 | After grid resume wtg in error so check error data and reset and start WTG. Late reset due to connectivity issue | Close | 0.015385 | O2_09 | 274.1833 |  | WTG Unscheduled Maintenance | 16451 | 274.1833
762 | 2024-06-09 | 2025 | 2024 | 2024-06-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Connectivity issue | 0.32083 | 0.32083 | 0.32917 | 0 | 0.2 | 0.2 | After grid resume wtg in error so check error data and reset and start WTG. Late reset due to connectivity issue | Close | 0.0076923 | O2_20 | 203.325 |  | WTG Unscheduled Maintenance | 24399 | 203.325
763 | 2024-06-09 | 2025 | 2024 | 2024-06-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.81042 | 0.81042 | 0.81389 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_20 | 84.7188 |  | WTG Unscheduled Maintenance | 24399 | 84.7188
764 | 2024-06-09 | 2025 | 2024 | 2024-06-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.57708 | 0.57708 | 0.57986 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & run the WTG. | Close | 0.0025641 | O2_20 | 67.775 |  | WTG Unscheduled Maintenance | 24399 | 67.775
765 | 2024-06-09 | 2025 | 2024 | 2024-06-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.70417 | 0.70417 | 0.70625 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_20 | 50.8312 |  | WTG Unscheduled Maintenance | 24399 | 50.8312
766 | 2024-06-09 | 2025 | 2024 | 2024-06-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Connectivity issue | 0.81042 | 0.81042 | 0.81389 | 0 | 0.083333 | 0.083333 | After grid resume wtg in error so check error data and reset and start WTG. Late reset due to connectivity issue | Close | 0.0032051 | O2_15 | 54.8611 |  | WTG Unscheduled Maintenance | 15800 | 54.8611
767 | 2024-06-09 | 2025 | 2024 | 2024-06-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.32153 | 0.32153 | 0.99931 | 0 | 16.2667 | 16.2667 | WTG stop for OFC cable laying Work after rain O2-02 pole fell down due to turbine has stopped | Open | 0.62564 | O2_09 | 11150.1222 |  | WTG Breakdown Maintenance | 16451 | 11150.1222
768 | 2024-06-09 | 2025 | 2024 | 2024-06-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.32153 | 0.32153 | 0.99931 | 0 | 16.2667 | 16.2667 | WTG stop for OFC cable laying Work after rain O2-02 pole fell down due to turbine has stopped | Open | 0.62564 | O2_09 | 11150.1222 |  | WTG Breakdown Maintenance | 16451 | 11150.1222
769 | 2024-06-10 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.53333 | 0.53333 | 0.53472 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_03 | 30.4486 |  | WTG Unscheduled Maintenance | 21923 | 30.4486
770 | 2024-06-10 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.84306 | 0.84306 | 0.85347 | 0 | 0.25 | 0.25 | Checked related error data log then reset & run the WTG. | Close | 0.0096154 | O2_03 | 228.3646 |  | WTG Unscheduled Maintenance | 21923 | 228.3646
771 | 2024-06-10 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.47778 | 0.47778 | 0.70417 | 0 | 5.4333 | 5.4333 | attend and replace load sensor check blade calibration and also set wind wane than reset and start WTG | Close | 0.20897 | O2_14 | 4705.9458 |  | WTG Breakdown Maintenance | 20787 | 4705.9458
772 | 2024-06-10 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Connectivity issue | 0.74722 | 0.74722 | 0.75833 | 0 | 0.26667 | 0.26667 | After grid resume wtg in error so check error data and reset and start WTG. Late reset due to connectivity issue | Close | 0.010256 | O2_14 | 230.9667 |  | WTG Unscheduled Maintenance | 20787 | 230.9667
773 | 2024-06-10 | 2025 | 2024 | 2024-06-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Connectivity issue | 0.74722 | 0.74722 | 0.76111 | 0 | 0.33333 | 0.33333 | After grid resume wtg in error so check error data and reset and start WTG. Late reset due to connectivity issue | Close | 0.012821 | O2_13 | 286.1667 |  | WTG Unscheduled Maintenance | 20604 | 286.1667
774 | 2024-06-10 | 2025 | 2024 | 2024-06-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0 | 0 | 0.70417 | 0 | 16.9 | 16.9 | WTG stop for OFC cable laying Work after rain O2-02 pole fell down due to turbine has stopped | Close | 0.65 | O2_12 | 15063.5333 |  | WTG Breakdown Maintenance | 21392 | 15063.5333
775 | 2024-06-10 | 2025 | 2024 | 2024-06-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | WTG stop for OFC cable laying Work after rain O2-02 pole fell down due to turbine has stopped | Open | 0.92244 | O2_02 | 9735.2347 |  | WTG Breakdown Maintenance | 9742 | 9735.2347
776 | 2024-06-11 | 2025 | 2024 | 2024-06-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.38125 | 0.38125 | 0.74722 | 0 | 8.7833 | 8.7833 | WTG stop for OFC cable laying Work after rain O2-02 pole fell down due to turbine has stopped | Close | 0.33782 | O2_12 | 14233.7576 |  | WTG Breakdown Maintenance | 38893 | 14233.7576
777 | 2024-06-11 | 2025 | 2024 | 2024-06-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Connectivity issue | 0.76389 | 0.76389 | 0.79861 | 0 | 0.83333 | 0.83333 | After grid resume wtg in error so check error data and reset and start WTG. Late reset due to connectivity issue | Close | 0.032051 | O2_12 | 1350.4514 |  | WTG Unscheduled Maintenance | 38893 | 1350.4514
778 | 2024-06-11 | 2025 | 2024 | 2024-06-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0 | 0 | 0.99931 | 0 | 23.9833 | 23.9833 | WTG stop for OFC cable laying Work after rain O2-02 pole fell down due to turbine has stopped | Open | 0.92244 | O2_02 | 28067.4951 |  | WTG Breakdown Maintenance | 28087 | 28067.4951
779 | 2024-06-11 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.2 | 0.2 | 0.21597 | 0 | 0.38333 | 0.38333 | Checked related error data log then reset & run the WTG. | Close | 0.014744 | O2_03 | 476.9306 |  | WTG Unscheduled Maintenance | 29860 | 476.9306
780 | 2024-06-11 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Connectivity issue | 0.38125 | 0.38125 | 0.39653 | 0 | 0.36667 | 0.36667 | After grid resume wtg in error so check error data and reset and start WTG. Late reset due to connectivity issue | Close | 0.014103 | O2_03 | 456.1944 |  | WTG Unscheduled Maintenance | 29860 | 456.1944
781 | 2024-06-11 | 2025 | 2024 | 2024-06-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 2828 | Timeout fault gen. lubrication | Break down | 0.19375 | 0.19375 | 0.20278 | 0 | 0.21667 | 0.21667 | Checked related error data log then reset & run the WTG. | Close | 0.0083333 | O2_12 | 351.1174 |  | WTG Unscheduled Maintenance | 38893 | 351.1174
782 | 2024-06-11 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Project pending work | 0.19931 | 0.19931 | 0.20903 | 0 | 0.23333 | 0.23333 | wtg shutdown taken for project pending work and OFC cable laying work | Close | 0.0089744 | O2_14 | 364.3014 |  | WTG Unscheduled Maintenance | 37471 | 364.3014
783 | 2024-06-11 | 2025 | 2024 | 2024-06-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.21458 | 0.21458 | 0.2375 | 0 | 0.55 | 0.55 | Checked related error data log then reset & run the WTG. | Close | 0.021154 | O2_13 | 848.2146 |  | WTG Unscheduled Maintenance | 37013 | 848.2146
784 | 2024-06-11 | 2025 | 2024 | 2024-06-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.65417 | 0.65417 | 0.66111 | 0 | 0.16667 | 0.16667 | Checked related error data log then reset & run the WTG. | Close | 0.0064103 | O2_20 | 314.8819 |  | WTG Unscheduled Maintenance | 45343 | 314.8819
785 | 2024-06-11 | 2025 | 2024 | 2024-06-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Connectivity issue | 0.38125 | 0.38125 | 0.40139 | 0 | 0.48333 | 0.48333 | After grid resume wtg in error so check error data and reset and start WTG. Late reset due to connectivity issue | Close | 0.01859 | O2_09 | 766.909 |  | WTG Unscheduled Maintenance | 38081 | 766.909
786 | 2024-06-11 | 2025 | 2024 | 2024-06-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3396 | Coolant heating 1&2 overload | Break down | 0.82083 | 0.82083 | 0.91806 | 0 | 2.3333 | 2.3333 | after grid resume wtg error so attend and check related circuit than found coolant temperature sensor was malfunctioning so refight and set properly than reset and start wtg | Close | 0.089744 | O2_09 | 3702.3194 |  | WTG Unscheduled Maintenance | 38081 | 3702.3194
787 | 2024-06-12 | 2025 | 2024 | 2024-06-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.425 | 0.425 | 0.79167 | 0 | 8.8 | 8.8 | wtg shutdown taken for project pending work and OFC cable laying work | Close | 0.33846 | O2_05 | 2964.5 |  | WTG Breakdown Maintenance | 8085 | 2964.5
788 | 2024-06-12 | 2025 | 2024 | 2024-06-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Connectivity issue | 0.83611 | 0.83611 | 0.87083 | 0 | 0.83333 | 0.83333 | After grid resume wtg in error so check error data and reset and start WTG.(Late reset due to connectivity issue.) | Close | 0.032051 | O2_05 | 280.7292 |  | WTG Unscheduled Maintenance | 8085 | 280.7292
789 | 2024-06-12 | 2025 | 2024 | 2024-06-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Connectivity issue | 0.88472 | 0.88472 | 0.99931 | 0 | 2.75 | 2.75 | Checked related error data log then reset & run the WTG. Late reset due to connectivity issue. | Close | 0.10577 | O2_05 | 926.4062 |  | WTG Unscheduled Maintenance | 8085 | 926.4062
790 | 2024-06-12 | 2025 | 2024 | 2024-06-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0 | 0 | 0.83681 | 0 | 20.0833 | 20.0833 | wtg shutdown taken for project pending work and OFC cable laying work | Close | 0.77244 | O2_02 | 12323.6354 |  | WTG Breakdown Maintenance | 14727 | 12323.6354
791 | 2024-06-12 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.42639 | 0.42639 | 0.44861 | 0 | 0.53333 | 0.53333 | After grid resume wtg in error so check error data and reset and start WTG. | Close | 0.020513 | O2_03 | 690.0667 |  | WTG Unscheduled Maintenance | 31053 | 690.0667
792 | 2024-06-12 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.64167 | 0.64167 | 0.75694 | 0 | 2.7667 | 2.7667 | WTG stop for repeated error work so attend and check converter CAN connector its cable check resistance value than refix it than reset and start Wtg. | Close | 0.10641 | O2_03 | 3579.7208 |  | WTG Breakdown Maintenance | 31053 | 3579.7208
793 | 2024-06-12 | 2025 | 2024 | 2024-06-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.52083 | 0.52083 | 0.59653 | 0 | 1.8167 | 1.8167 | WTG manual stop for project MCC point closer work | Close | 0.069872 | O2_11 | 2188.7806 |  | WTG Breakdown Maintenance | 28916 | 2188.7806
794 | 2024-06-12 | 2025 | 2024 | 2024-06-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.43194 | 0.43194 | 0.43472 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & run the WTG. | Close | 0.0025641 | O2_11 | 80.3222 |  | WTG Unscheduled Maintenance | 28916 | 80.3222
795 | 2024-06-12 | 2025 | 2024 | 2024-06-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.44306 | 0.44306 | 0.44792 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & run the WTG. | Close | 0.0044872 | O2_11 | 140.5639 |  | WTG Unscheduled Maintenance | 28916 | 140.5639
796 | 2024-06-12 | 2025 | 2024 | 2024-06-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Break down | 0.74583 | 0.74583 | 0.74722 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_10 | 39.5597 |  | WTG Unscheduled Maintenance | 28483 | 39.5597
797 | 2024-06-12 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.69028 | 0.69028 | 0.69236 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_11 | 60.2417 |  | WTG Unscheduled Maintenance | 28916 | 60.2417
798 | 2024-06-12 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.44444 | 0.44444 | 0.50833 | 0 | 1.5333 | 1.5333 | WTG manual stop for project MCC point closer work | Close | 0.058974 | O2_12 | 2128.5222 |  | WTG Breakdown Maintenance | 33316 | 2128.5222
799 | 2024-06-12 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.74306 | 0.74306 | 0.74583 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & run the WTG. | Close | 0.0025641 | O2_12 | 92.5444 |  | WTG Unscheduled Maintenance | 33316 | 92.5444
800 | 2024-06-12 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.77986 | 0.77986 | 0.78125 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_12 | 46.2722 |  | WTG Unscheduled Maintenance | 33316 | 46.2722
801 | 2024-06-12 | 2025 | 2024 | 2024-06-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.73264 | 0.73264 | 0.73472 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_13 | 51.9875 |  | WTG Unscheduled Maintenance | 24954 | 51.9875
802 | 2024-06-12 | 2025 | 2024 | 2024-06-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 1065 | Drive train monitor level 1 | Break down | 0.74236 | 0.74236 | 0.74375 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_13 | 34.6583 |  | WTG Unscheduled Maintenance | 24954 | 34.6583
803 | 2024-06-12 | 2025 | 2024 | 2024-06-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.73958 | 0.73958 | 0.74097 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_20 | 53.8931 |  | WTG Unscheduled Maintenance | 38803 | 53.8931
804 | 2024-06-12 | 2025 | 2024 | 2024-06-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.77292 | 0.77292 | 0.77569 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & run the WTG. | Close | 0.0025641 | O2_20 | 107.7861 |  | WTG Unscheduled Maintenance | 38803 | 107.7861
805 | 2024-06-12 | 2025 | 2024 | 2024-06-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.62222 | 0.62222 | 0.67083 | 0 | 1.1667 | 1.1667 | WTG manual stop for project MCC point closer work | Close | 0.044872 | O2_15 | 1443.3125 |  | WTG Breakdown Maintenance | 29691 | 1443.3125
806 | 2024-06-13 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.17361 | 0.17361 | 0.17569 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_03 | 39.0729 |  | WTG Unscheduled Maintenance | 18755 | 39.0729
807 | 2024-06-13 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.25833 | 0.25833 | 0.26042 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_03 | 39.0729 |  | WTG Unscheduled Maintenance | 18755 | 39.0729
808 | 2024-06-13 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.33889 | 0.33889 | 0.34792 | 0 | 0.21667 | 0.21667 | Checked related error data log then reset & run the WTG. | Close | 0.0083333 | O2_03 | 169.316 |  | WTG Unscheduled Maintenance | 18755 | 169.316
809 | 2024-06-13 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Connectivity issue | 0.68958 | 0.68958 | 0.75694 | 0 | 1.6167 | 1.6167 | After grid resume Connectivity lost restore connectivity and start WTG. | Close | 0.062179 | O2_03 | 1263.3576 |  | WTG Unscheduled Maintenance | 18755 | 1263.3576
810 | 2024-06-13 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down | 0.78542 | 0.78542 | 0.89306 | 0 | 2.5833 | 2.5833 | attend and check hydraulic pressure, pressure valve pressure switch, pressure feedback switch and connection proper refight than reset and start WTG. | Close | 0.099359 | O2_03 | 2018.7674 |  | WTG Unscheduled Maintenance | 18755 | 2018.7674
811 | 2024-06-13 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Connectivity issue | 0.68958 | 0.68958 | 0.75 | 0 | 1.45 | 1.45 | After grid resume Connectivity lost restore connectivity and start WTG. | Close | 0.055769 | O2_11 | 1362.275 |  | WTG Unscheduled Maintenance | 22548 | 1362.275
812 | 2024-06-13 | 2025 | 2024 | 2024-06-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Connectivity issue | 0.68958 | 0.68958 | 0.75 | 0 | 1.45 | 1.45 | After grid resume Connectivity lost restore connectivity and start WTG. | Close | 0.055769 | O2_09 | 741.8563 |  | WTG Unscheduled Maintenance | 12279 | 741.8563
813 | 2024-06-13 | 2025 | 2024 | 2024-06-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.53472 | 0.53472 | 0.53611 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_16 | 47 |  | WTG Unscheduled Maintenance | 33840 | 47
814 | 2024-06-13 | 2025 | 2024 | 2024-06-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0.68958 | 0.68958 | 0.72014 | 0 | 0.73333 | 0.73333 | After grid resume Vcb found trip so charge normally than reset and start WTG.(No connectivity) | Close | 0.028205 | O2_02 | 716.375 |  | WTG Unscheduled Maintenance | 23445 | 716.375
815 | 2024-06-13 | 2025 | 2024 | 2024-06-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.68958 | 0.68958 | 0.73958 | 0 | 1.2 | 1.2 | After grid resume wtg in error so check error data and reset and start WTG.(No connectivity) | Close | 0.046154 | O2_05 | 1162.75 |  | WTG Unscheduled Maintenance | 23255 | 1162.75
816 | 2024-06-14 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.078472 | 0.078472 | 0.080556 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_03 | 58.3 |  | WTG Unscheduled Maintenance | 27984 | 58.3
817 | 2024-06-14 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down | 0.60417 | 0.60417 | 0.76389 | 0 | 3.8333 | 3.8333 | attend for hydraulic error and found solenoid valve connection loose so correct it then check also converter for frequency converter error so check all related circuit than proper shielding done of communication cable than reset and start WTG. | Close | 0.14744 | O2_03 | 4469.6667 |  | WTG Unscheduled Maintenance | 27984 | 4469.6667
818 | 2024-06-14 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down | 0.60417 | 0.70139 | 0.76389 | 2.3333 | 1.5 | 3.8333 | attend for hydraulic error and found solenoid valve connection loose so correct it then check also converter for frequency converter error so check all related circuit than proper shielding done of communication cable than reset and start WTG. | Close | 0.14744 | O2_03 | 4469.6667 |  | WTG Unscheduled Maintenance | 27984 | 4469.6667
819 | 2024-06-14 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3063 | Conv. emerg.off type D | Break down | 0.18542 | 0.18542 | 0.18889 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_13 | 90.5521 |  | WTG Unscheduled Maintenance | 26079 | 90.5521
820 | 2024-06-14 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.38542 | 0.38542 | 0.38958 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2_13 | 108.6625 |  | WTG Unscheduled Maintenance | 26079 | 108.6625
821 | 2024-06-14 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.75972 | 0.75972 | 0.76528 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & run the WTG. | Close | 0.0051282 | O2_13 | 144.8833 |  | WTG Unscheduled Maintenance | 26079 | 144.8833
822 | 2024-06-14 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.33958 | 0.33958 | 0.34306 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_12 | 97.5312 |  | WTG Unscheduled Maintenance | 28089 | 97.5312
823 | 2024-06-14 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.75903 | 0.75903 | 0.76181 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & run the WTG. | Close | 0.0025641 | O2_12 | 78.025 |  | WTG Unscheduled Maintenance | 28089 | 78.025
824 | 2024-06-14 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.77292 | 0.77292 | 0.77778 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & run the WTG. | Close | 0.0044872 | O2_12 | 136.5437 |  | WTG Unscheduled Maintenance | 28089 | 136.5437
825 | 2024-06-14 | 2025 | 2024 | 2024-06-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.55972 | 0.55972 | 0.575 | 0 | 0.36667 | 0.36667 | Checked related error data log then reset & run the WTG. | Close | 0.014103 | O2_13 | 398.4292 |  | WTG Unscheduled Maintenance | 26079 | 398.4292
826 | 2024-06-14 | 2025 | 2024 | 2024-06-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0 | 0 | 0.76597 | 0 | 18.3833 | 18.3833 | wtg shutdown taken for grid commissioning WIP. | Close | 0.70705 | O2_05 | 20724.1444 |  | WTG Breakdown Maintenance | 27056 | 20724.1444
827 | 2024-06-15 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.62708 | 0.62708 | 0.62986 | 0 | 0.066667 | 0.066667 | auto reset | Close | 0.0025641 | O2_03 | 38.1611 |  | WTG Unscheduled Maintenance | 13738 | 38.1611
828 | 2024-06-15 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.65417 | 0.65417 | 0.65764 | 0 | 0.083333 | 0.083333 | auto reset | Close | 0.0032051 | O2_03 | 47.7014 |  | WTG Unscheduled Maintenance | 13738 | 47.7014
829 | 2024-06-15 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.72361 | 0.72361 | 0.72569 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_03 | 28.6208 |  | WTG Unscheduled Maintenance | 13738 | 28.6208
830 | 2024-06-15 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.76389 | 0.76389 | 0.99931 | 0 | 5.65 | 5.65 | wtg in error so attend and check related circuit ,battery voltage ,connection,registers,encoder and its connection and future troubleshooting is WIP | Close | 0.21731 | O2_03 | 3234.1542 |  | WTG Unscheduled Maintenance | 13738 | 3234.1542
831 | 2024-06-15 | 2025 | 2024 | 2024-06-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.48611 | 0.48611 | 0.4875 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_12 | 21.1542 |  | WTG Unscheduled Maintenance | 15231 | 21.1542
832 | 2024-06-15 | 2025 | 2024 | 2024-06-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 2828 | Timeout fault gen. lubrication | Break down | 0.58194 | 0.58194 | 0.59861 | 0 | 0.4 | 0.4 | Checked related error data log then reset & run the WTG. | Close | 0.015385 | O2_12 | 253.85 |  | WTG Unscheduled Maintenance | 15231 | 253.85
833 | 2024-06-15 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.47222 | 0.47222 | 0.61111 | 0 | 3.3333 | 3.3333 | wtg shutdown taken for MCC point closer work from project team | Close | 0.12821 | O2_11 | 2036.9444 |  | WTG Breakdown Maintenance | 14666 | 2036.9444
834 | 2024-06-15 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.78542 | 0.78542 | 0.78889 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_11 | 50.9236 |  | WTG Unscheduled Maintenance | 14666 | 50.9236
835 | 2024-06-15 | 2025 | 2024 | 2024-06-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.019444 | 0.019444 | 0.020833 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_05 | 20.9472 |  | WTG Unscheduled Maintenance | 15082 | 20.9472
836 | 2024-06-15 | 2025 | 2024 | 2024-06-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.77986 | 0.77986 | 0.79167 | 0 | 0.28333 | 0.28333 | Checked related error data log then reset & run the WTG. | Close | 0.010897 | O2_09 | 121.1958 |  | WTG Unscheduled Maintenance | 10266 | 121.1958
837 | 2024-06-15 | 2025 | 2024 | 2024-06-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.85417 | 0.85417 | 0.86806 | 0 | 0.33333 | 0.33333 | Checked related error data log then reset & run the WTG. | Close | 0.012821 | O2_09 | 142.5833 |  | WTG Unscheduled Maintenance | 10266 | 142.5833
838 | 2024-06-15 | 2025 | 2024 | 2024-06-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.88194 | 0.88194 | 0.89514 | 0 | 0.31667 | 0.31667 | Checked related error data log then reset & run the WTG. | Close | 0.012179 | O2_20 | 198.2861 |  | WTG Unscheduled Maintenance | 15028 | 198.2861
839 | 2024-06-15 | 2025 | 2024 | 2024-06-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.55486 | 0.55486 | 0.62292 | 0 | 1.6333 | 1.6333 | wtg shutdown taken for MCC point closer work from project team | Close | 0.062821 | O2_05 | 1026.4139 |  | WTG Breakdown Maintenance | 15082 | 1026.4139
840 | 2024-06-16 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0 | 0 | 0.053472 | 0 | 1.2833 | 1.2833 | wtg in error so attend and check related circuit ,battery voltage ,connection,registers,encoder and its connection than found blade no 2 choper register malfunctioning so replace new one than reset and start WTG. | Close | 0.049359 | O2_03 | 713.266 |  | WTG Unscheduled Maintenance | 13339 | 713.266
841 | 2024-06-16 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.018056 | 0.018056 | 0.049306 | 0 | 0.75 | 0.75 | Checked related error data log then reset & run the WTG. | Close | 0.028846 | O2_13 | 394.5312 |  | WTG Unscheduled Maintenance | 12625 | 394.5312
842 | 2024-06-16 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.41181 | 0.41181 | 0.44444 | 0 | 0.78333 | 0.78333 | Checked related error data log then reset & run the WTG. | Close | 0.030128 | O2_13 | 412.066 |  | WTG Unscheduled Maintenance | 12625 | 412.066
843 | 2024-06-16 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.33542 | 0.33542 | 0.33958 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2_12 | 56.7667 |  | WTG Unscheduled Maintenance | 13624 | 56.7667
844 | 2024-06-16 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.51806 | 0.51806 | 0.58333 | 0 | 1.5667 | 1.5667 | Checked related error data log then reset & run the WTG. | Close | 0.060256 | O2_12 | 889.3444 |  | WTG Unscheduled Maintenance | 13624 | 889.3444
845 | 2024-06-16 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.61667 | 0.61667 | 0.625 | 0 | 0.2 | 0.2 | Checked related error data log then reset & run the WTG. | Close | 0.0076923 | O2_12 | 113.5333 |  | WTG Unscheduled Maintenance | 13624 | 113.5333
846 | 2024-06-16 | 2025 | 2024 | 2024-06-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.46875 | 0.46875 | 0.62153 | 0 | 3.6667 | 3.6667 | wtg shutdown taken for MCC point clouser work from project team | Close | 0.14103 | O2_13 | 1928.8194 |  | WTG Breakdown Maintenance | 12625 | 1928.8194
847 | 2024-06-16 | 2025 | 2024 | 2024-06-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.25 | 0.25 | 0.25972 | 0 | 0.23333 | 0.23333 | Checked related error data log then reset & run the WTG. | Close | 0.0089744 | O2_20 | 137.0736 |  | WTG Unscheduled Maintenance | 14099 | 137.0736
848 | 2024-06-17 | 2025 | 2024 | 2024-06-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.61806 | 0.61806 | 0.62014 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_05 | 27.475 |  | WTG Unscheduled Maintenance | 13188 | 27.475
849 | 2024-06-17 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.023611 | 0.023611 | 0.025694 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_13 | 29.7396 |  | WTG Unscheduled Maintenance | 14275 | 29.7396
850 | 2024-06-17 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3063 | Conv. emerg.off type D | Break down | 0.067361 | 0.067361 | 0.06875 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_13 | 19.8264 |  | WTG Unscheduled Maintenance | 14275 | 19.8264
851 | 2024-06-17 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.28472 | 0.28472 | 0.3 | 0 | 0.36667 | 0.36667 | Checked related error data log then reset & run the WTG. | Close | 0.014103 | O2_13 | 218.0903 |  | WTG Unscheduled Maintenance | 14275 | 218.0903
852 | 2024-06-17 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.50903 | 0.50903 | 0.51806 | 0 | 0.21667 | 0.21667 | Checked related error data log then reset & run the WTG. | Close | 0.0083333 | O2_12 | 129.341 |  | WTG Unscheduled Maintenance | 14327 | 129.341
853 | 2024-06-17 | 2025 | 2024 | 2024-06-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.65833 | 0.65833 | 0.66458 | 0 | 0.15 | 0.15 | Checked related error data log then reset & run the WTG. | Close | 0.0057692 | O2_12 | 89.5437 |  | WTG Unscheduled Maintenance | 14327 | 89.5437
854 | 2024-06-17 | 2025 | 2024 | 2024-06-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 153 | SLC SF max. cable winding | Road issue | 0.68472 | 0.68472 | 0.90556 | 0 | 5.3 | 5.3 | attend and check related circuit than doing yaw position at zero digree than set limit switch setting properly and correct it and also retight all connection than reset and start WTG.(Delay due to road approach issue) | Close | 0.20385 | O2_20 | 2938.4083 |  | WTG Unscheduled Maintenance | 13306 | 2938.4083
855 | 2024-06-17 | 2025 | 2024 | 2024-06-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.68819 | 0.68819 | 0.69236 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2_09 | 65.075 |  | WTG Unscheduled Maintenance | 15618 | 65.075
856 | 2024-06-18 | 2025 | 2024 | 2024-06-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3065 | Conv. emerg.off type F | Break down | 0.56944 | 0.56944 | 0.57153 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_11 | 58.25 |  | WTG Unscheduled Maintenance | 27960 | 58.25
857 | 2024-06-18 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 155 | SLC SF system monitoring | Break down | 0.19444 | 0.19444 | 0.20139 | 0 | 0.16667 | 0.16667 | Checked related error data log then reset & run the WTG. | Close | 0.0064103 | O2_11 | 194.1667 |  | WTG Unscheduled Maintenance | 27960 | 194.1667
858 | 2024-06-18 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.46944 | 0.46944 | 0.59653 | 0 | 3.05 | 3.05 | Manual stop for WTG inspection work | Close | 0.11731 | O2_11 | 3553.25 |  | WTG Breakdown Maintenance | 27960 | 3553.25
859 | 2024-06-18 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Break down | 0.79236 | 0.79236 | 0.80347 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_11 | 310.6667 |  | WTG Unscheduled Maintenance | 27960 | 310.6667
860 | 2024-06-18 | 2025 | 2024 | 2024-06-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.66597 | 0.66597 | 0.67431 | 0 | 0.2 | 0.2 | Checked related error data log then reset & run the WTG. | Close | 0.0076923 | O2_09 | 236.725 |  | WTG Unscheduled Maintenance | 28407 | 236.725
861 | 2024-06-18 | 2025 | 2024 | 2024-06-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Road issue | 0.31389 | 0.31389 | 0.54236 | 0 | 5.4833 | 5.4833 | wtg in error but road was not accesable for vehicale so another vehicale arragemnt than after attend WTG. | Close | 0.2109 | O2_05 | 6283.4431 |  | WTG Unscheduled Maintenance | 27502 | 6283.4431
862 | 2024-06-18 | 2025 | 2024 | 2024-06-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Road issue | 0.54236 | 0.54236 | 0.76667 | 0 | 5.3833 | 5.3833 | attend and check battery voltage monitoring circuit than found monitoring resister value is not ok so arrange and replace with new one than reset and start WTG.(late attend & start Due to road approch issue.) | Close | 0.20705 | O2_05 | 6168.8514 |  | WTG Unscheduled Maintenance | 27502 | 6168.8514 | O2_06 | #VALUE! |  | WTG Unscheduled Maintenance
863 | 2024-06-18 | 2025 | 2024 | 2024-06-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.68472 | 0.68472 | 0.74028 | 0 | 1.3333 | 1.3333 | manual stop for MCC work | Close | 0.20705 | O2_05 | 1527.8889 |  | WTG Breakdown Maintenance | 27502 | 1527.8889
864 | 2024-06-19 | 2025 | 2024 | 2024-06-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.41528 | 0.41528 | 0.41667 | 0 | 0.033333 | 0.033333 | Error occurred due to PLC not completely shutdown before charge feeder, So controller malfunction occurred. | Close | 0.0012821 | O2_02 | 45.6903 |  | WTG Unscheduled Maintenance | 32897 | 45.6903
865 | 2024-06-19 | 2025 | 2024 | 2024-06-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Break down | 0.51944 | 0.51944 | 0.52083 | 0 | 0.033333 | 0.033333 | Error occurred due to PLC not completely shutdown before charge feeder, So controller malfunction occurred. | Close | 0.0012821 | O2_02 | 45.6903 |  | WTG Unscheduled Maintenance | 32897 | 45.6903
866 | 2024-06-19 | 2025 | 2024 | 2024-06-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.59375 | 0.59375 | 0.59722 | 0 | 0.083333 | 0.083333 | Hard reboot PLC then start. | Close | 0.0032051 | O2_02 | 114.2257 |  | WTG Unscheduled Maintenance | 32897 | 114.2257
867 | 2024-06-19 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.425 | 0.425 | 0.42639 | 0 | 0.033333 | 0.033333 | Error occurred due to PLC not completely shutdown before charge feeder, So controller malfunction occurred. | Close | 0.0012821 | O2_03 | 43.5028 |  | WTG Unscheduled Maintenance | 31322 | 43.5028
868 | 2024-06-19 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Break down | 0.44583 | 0.44583 | 0.44722 | 0 | 0.033333 | 0.033333 | Error occurred due to PLC not completely shutdown before charge feeder, So controller malfunction occurred. | Close | 0.0012821 | O2_03 | 43.5028 |  | WTG Unscheduled Maintenance | 31322 | 43.5028
869 | 2024-06-19 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.49444 | 0.49444 | 0.49583 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_03 | 43.5028 |  | WTG Unscheduled Maintenance | 31322 | 43.5028
870 | 2024-06-19 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.54236 | 0.54236 | 0.55139 | 0 | 0.21667 | 0.21667 | Hard reboot PLC then start. | Close | 0.0083333 | O2_03 | 282.7681 |  | WTG Unscheduled Maintenance | 31322 | 282.7681
871 | 2024-06-19 | 2025 | 2024 | 2024-06-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.40903 | 0.40903 | 0.41111 | 0 | 0.05 | 0.05 | Error occurred due to PLC not completely shutdown before charge feeder, So controller malfunction occurred. | Close | 0.0019231 | O2_11 | 58.9542 |  | WTG Unscheduled Maintenance | 28298 | 58.9542
872 | 2024-06-19 | 2025 | 2024 | 2024-06-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Break down | 0.43542 | 0.43542 | 0.43819 | 0 | 0.066667 | 0.066667 | Error occurred due to PLC not completely shutdown before charge feeder, So controller malfunction occurred. | Close | 0.0025641 | O2_11 | 78.6056 |  | WTG Unscheduled Maintenance | 28298 | 78.6056
873 | 2024-06-19 | 2025 | 2024 | 2024-06-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Break down | 0.49306 | 0.49306 | 0.52778 | 0 | 0.83333 | 0.83333 | Error occurred due to PLC not completely shutdown before charge feeder, So controller malfunction occurred. | Close | 0.032051 | O2_11 | 982.5694 |  | WTG Unscheduled Maintenance | 28298 | 982.5694
874 | 2024-06-19 | 2025 | 2024 | 2024-06-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Break down | 0.60417 | 0.60417 | 0.69444 | 0 | 2.1667 | 2.1667 | Hard reboot PLC then start. | Close | 0.083333 | O2_11 | 2554.6806 |  | WTG Unscheduled Maintenance | 28298 | 2554.6806
875 | 2024-06-19 | 2025 | 2024 | 2024-06-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Break down | 0.40347 | 0.40347 | 0.41181 | 0 | 0.2 | 0.2 | Error occurred due to PLC not completely shutdown before charge feeder, So controller malfunction occurred. | Close | 0.0076923 | O2_10 | 203 |  | WTG Unscheduled Maintenance | 24360 | 203
876 | 2024-06-19 | 2025 | 2024 | 2024-06-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.42847 | 0.42847 | 0.43056 | 0 | 0.05 | 0.05 | Error occurred due to PLC not completely shutdown before charge feeder, So controller malfunction occurred. | Close | 0.0019231 | O2_10 | 50.75 |  | WTG Unscheduled Maintenance | 24360 | 50.75
877 | 2024-06-19 | 2025 | 2024 | 2024-06-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.48958 | 0.48958 | 0.60278 | 0 | 2.7167 | 2.7167 | Manual stop for WTG Service inspection work | Close | 0.10449 | O2_10 | 2757.4167 |  | WTG Breakdown Maintenance | 24360 | 2757.4167
878 | 2024-06-19 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.42361 | 0.42361 | 0.425 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_11 | 39.3028 |  | WTG Unscheduled Maintenance | 28298 | 39.3028
879 | 2024-06-19 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.78264 | 0.78264 | 0.81042 | 0 | 0.66667 | 0.66667 | Checked related error data log then reset & run the WTG. | Close | 0.025641 | O2_11 | 786.0556 |  | WTG Unscheduled Maintenance | 28298 | 786.0556
880 | 2024-06-19 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.48403 | 0.48403 | 0.48819 | 0 | 0.1 | 0.1 | Error occurred due to PLC not completely shutdown before charge feeder, So controller malfunction occurred. | Close | 0.0038462 | O2_11 | 117.9083 |  | WTG Unscheduled Maintenance | 28298 | 117.9083
881 | 2024-06-19 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.50486 | 0.50486 | 0.50764 | 0 | 0.066667 | 0.066667 | Error occurred due to PLC not completely shutdown before charge feeder, So controller malfunction occurred. | Close | 0.0025641 | O2_11 | 78.6056 |  | WTG Unscheduled Maintenance | 28298 | 78.6056
882 | 2024-06-19 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Break down | 0.58403 | 0.58403 | 0.63542 | 0 | 1.2333 | 1.2333 | Hard reboot PLC then start. | Close | 0.047436 | O2_11 | 1454.2028 |  | WTG Unscheduled Maintenance | 28298 | 1454.2028
883 | 2024-06-19 | 2025 | 2024 | 2024-06-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Break down | 0.41181 | 0.41181 | 0.42222 | 0 | 0.25 | 0.25 | Error occurred due to PLC not completely shutdown before charge feeder, So controller malfunction occurred. | Close | 0.0096154 | O2_11 | 294.7708 |  | WTG Unscheduled Maintenance | 28298 | 294.7708
884 | 2024-06-19 | 2025 | 2024 | 2024-06-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Break down | 0.47847 | 0.47847 | 0.48958 | 0 | 0.26667 | 0.26667 | Hard reboot PLC then start. | Close | 0.010256 | O2_11 | 314.4222 |  | WTG Unscheduled Maintenance | 28298 | 314.4222
885 | 2024-06-19 | 2025 | 2024 | 2024-06-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.073611 | 0.073611 | 0.075694 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_05 | 63.3458 |  | WTG Unscheduled Maintenance | 30406 | 63.3458
886 | 2024-06-19 | 2025 | 2024 | 2024-06-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.13056 | 0.13056 | 0.13264 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_05 | 63.3458 |  | WTG Unscheduled Maintenance | 30406 | 63.3458
887 | 2024-06-19 | 2025 | 2024 | 2024-06-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.65417 | 0.65417 | 0.65972 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & run the WTG. | Close | 0.0051282 | O2_05 | 168.9222 |  | WTG Unscheduled Maintenance | 30406 | 168.9222
888 | 2024-06-19 | 2025 | 2024 | 2024-06-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.7625 | 0.7625 | 0.76667 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2_09 | 131.2792 |  | WTG Unscheduled Maintenance | 31507 | 131.2792
889 | 2024-06-19 | 2025 | 2024 | 2024-06-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Break down | 0.41042 | 0.41042 | 0.41528 | 0 | 0.11667 | 0.11667 | Error occurred due to PLC not completely shutdown before charge feeder, So controller malfunction occurred. | Close | 0.0044872 | O2_20 | 156.7563 |  | WTG Unscheduled Maintenance | 32247 | 156.7563
890 | 2024-06-19 | 2025 | 2024 | 2024-06-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Break down | 0.48264 | 0.48264 | 0.49444 | 0 | 0.28333 | 0.28333 | Hard reboot PLC then start. | Close | 0.010897 | O2_20 | 380.6938 |  | WTG Unscheduled Maintenance | 32247 | 380.6938
891 | 2024-06-19 | 2025 | 2024 | 2024-06-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.69375 | 0.69375 | 0.70417 | 0 | 0.25 | 0.25 | Checked related error data log then reset & run the WTG. | Close | 0.0096154 | O2_20 | 335.9063 |  | WTG Unscheduled Maintenance | 32247 | 335.9063
892 | 2024-06-19 | 2025 | 2024 | 2024-06-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.45417 | 0.45417 | 0.45694 | 0 | 0.066667 | 0.066667 | Error occurred due to PLC not completely shutdown before charge feeder, So controller malfunction occurred. | Close | 0.0025641 | O2_03 | 87.0056 |  | WTG Unscheduled Maintenance | 31322 | 87.0056
893 | 2024-06-19 | 2025 | 2024 | 2024-06-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.50694 | 0.50694 | 0.51736 | 0 | 0.25 | 0.25 | Error occurred due to PLC not completely shutdown before charge feeder, So controller malfunction occurred. | Close | 0.0096154 | O2_03 | 326.2708 |  | WTG Unscheduled Maintenance | 31322 | 326.2708
894 | 2024-06-19 | 2025 | 2024 | 2024-06-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Break down | 0.54167 | 0.54167 | 0.55764 | 0 | 0.38333 | 0.38333 | Hard reboot PLC then start. | Close | 0.014744 | O2_03 | 500.2819 |  | WTG Unscheduled Maintenance | 31322 | 500.2819
895 | 2024-06-20 | 2025 | 2024 | 2024-06-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 973 | Check blade bend.mom. | Break down | 0.71736 | 0.71736 | 0.71875 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_02 | 50.9917 |  | WTG Unscheduled Maintenance | 36714 | 50.9917
896 | 2024-06-20 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.65139 | 0.65139 | 0.65417 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & run the WTG. | Close | 0.0025641 | O2_03 | 77.7611 |  | WTG Unscheduled Maintenance | 27994 | 77.7611
897 | 2024-06-20 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.43542 | 0.43542 | 0.43958 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2_11 | 145.9167 |  | WTG Unscheduled Maintenance | 35020 | 145.9167
898 | 2024-06-20 | 2025 | 2024 | 2024-06-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 973 | Check blade bend.mom. | Break down | 0.7375 | 0.7375 | 0.73889 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_20 | 40.2597 |  | WTG Unscheduled Maintenance | 28987 | 40.2597
899 | 2024-06-20 | 2025 | 2024 | 2024-06-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.18542 | 0.18542 | 0.18681 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_05 | 47.7042 |  | WTG Unscheduled Maintenance | 34347 | 47.7042
900 | 2024-06-20 | 2025 | 2024 | 2024-06-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.92292 | 0.92292 | 0.925 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_05 | 71.5562 |  | WTG Unscheduled Maintenance | 34347 | 71.5562
901 | 2024-06-20 | 2025 | 2024 | 2024-06-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Break down | 0.69236 | 0.69236 | 0.69375 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_09 | 48.4903 |  | WTG Unscheduled Maintenance | 34913 | 48.4903
902 | 2024-06-20 | 2025 | 2024 | 2024-06-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.74236 | 0.74236 | 0.79306 | 0 | 1.2167 | 1.2167 | attend and check related circuit than found converter colling temprature sensor was malfunctioning so replace with new one than reset and start WTG. | Close | 0.046795 | O2_09 | 1769.8951 |  | WTG Unscheduled Maintenance | 34913 | 1769.8951
903 | 2024-06-20 | 2025 | 2024 | 2024-06-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 4555 | Tower accel. difference | Break down | 0.16736 | 0.16736 | 0.17153 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2_20 | 120.7792 |  | WTG Unscheduled Maintenance | 28987 | 120.7792
904 | 2024-06-20 | 2025 | 2024 | 2024-06-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.59861 | 0.59861 | 0.70208 | 0 | 2.4833 | 2.4833 | attend for rep error so check related circuit and done proper altrasonic sensors alignment than start WTG | Close | 0.095513 | O2_20 | 2999.3493 |  | WTG Breakdown Maintenance | 28987 | 2999.3493
905 | 2024-06-20 | 2025 | 2024 | 2024-06-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Break down | 0.50139 | 0.50139 | 0.5125 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_15 | 343.3111 |  | WTG Unscheduled Maintenance | 30898 | 343.3111
906 | 2024-06-20 | 2025 | 2024 | 2024-06-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.59583 | 0.59583 | 0.59722 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_15 | 42.9139 |  | WTG Unscheduled Maintenance | 30898 | 42.9139
907 | 2024-06-21 | 2025 | 2024 | 2024-06-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.05 | 0.05 | 0.076389 | 0 | 0.63333 | 0.63333 | Checked related error data log then reset & run the WTG. | Close | 0.024359 | O2_05 | 862.125 |  | WTG Unscheduled Maintenance | 32670 | 862.125
908 | 2024-06-21 | 2025 | 2024 | 2024-06-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 650 | Pitch controller communication error | Break down | 0.76111 | 0.76111 | 0.79375 | 0 | 0.78333 | 0.78333 | attend and check related circuit than nothing found abnormal than retight all connection and apply hard reboot than start WTG. | Close | 0.030128 | O2_15 | 1305.5556 |  | WTG Unscheduled Maintenance | 40000 | 1305.5556
909 | 2024-06-21 | 2025 | 2024 | 2024-06-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.42361 | 0.42361 | 0.4375 | 0 | 0.33333 | 0.33333 | Manual stop for project pending work | Close | 0.012821 | O2_09 | 537.2083 |  | WTG Breakdown Maintenance | 38679 | 537.2083
910 | 2024-06-21 | 2025 | 2024 | 2024-06-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.4625 | 0.4625 | 0.47431 | 0 | 0.28333 | 0.28333 | Manual stop for meter sealing work. | Close | 0.010897 | O2_09 | 456.6271 |  | WTG Breakdown Maintenance | 38679 | 456.6271
911 | 2024-06-21 | 2025 | 2024 | 2024-06-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.76111 | 0.76111 | 0.77569 | 0 | 0.35 | 0.35 | Checked related error data log then reset & run the WTG. | Close | 0.013462 | O2_09 | 564.0688 |  | WTG Unscheduled Maintenance | 38679 | 564.0688
912 | 2024-06-21 | 2025 | 2024 | 2024-06-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.79722 | 0.79722 | 0.80833 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_09 | 429.7667 |  | WTG Unscheduled Maintenance | 38679 | 429.7667
913 | 2024-06-21 | 2025 | 2024 | 2024-06-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 1630 | Disc filter adaption implausible | Break down | 0.81736 | 0.81736 | 0.85208 | 0 | 0.83333 | 0.83333 | Checked related error data log then apply soft reboot then reset & run the WTG. | Close | 0.032051 | O2_09 | 1343.0208 |  | WTG Unscheduled Maintenance | 38679 | 1343.0208
914 | 2024-06-21 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 1600 | High gear speed | Break down | 0.78681 | 0.78681 | 0.79792 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_01 | 341.7778 |  | WTG Unscheduled Maintenance | 30760 | 341.7778
915 | 2024-06-21 | 2025 | 2024 | 2024-06-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.61806 | 0.61806 | 0.62222 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2_15 | 166.6667 |  | WTG Unscheduled Maintenance | 40000 | 166.6667
916 | 2024-06-21 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.011111 | 0.011111 | 0.0125 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_13 | 53.7042 |  | WTG Unscheduled Maintenance | 38667 | 53.7042
917 | 2024-06-21 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.15 | 0.15 | 0.15139 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_13 | 52.625 |  | WTG Unscheduled Maintenance | 37890 | 52.625
918 | 2024-06-21 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.59653 | 0.59653 | 0.61389 | 0 | 0.41667 | 0.41667 | Checked related error data log then reset & run the WTG. | Close | 0.016026 | O2_12 | 657.8125 |  | WTG Unscheduled Maintenance | 37890 | 657.8125
919 | 2024-06-21 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.63542 | 0.63542 | 0.64167 | 0 | 0.15 | 0.15 | Checked related error data log then reset & run the WTG. | Close | 0.0057692 | O2_12 | 236.8125 |  | WTG Unscheduled Maintenance | 37890 | 236.8125
920 | 2024-06-21 | 2025 | 2024 | 2024-06-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.64167 | 0.64167 | 0.64306 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_20 | 43.2097 |  | WTG Unscheduled Maintenance | 31111 | 43.2097
921 | 2024-06-22 | 2025 | 2024 | 2024-06-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 2687 | Max. slip ring cell temp. | Break down | 0.58542 | 0.58542 | 0.59653 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_14 | 219.1889 |  | WTG Unscheduled Maintenance | 19727 | 219.1889
922 | 2024-06-22 | 2025 | 2024 | 2024-06-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 2687 | Max. slip ring cell temp. | Break down | 0.70694 | 0.70694 | 0.73611 | 0 | 0.7 | 0.7 | Checked related error data log then reset & run the WTG. | Close | 0.026923 | O2_14 | 575.3708 |  | WTG Unscheduled Maintenance | 19727 | 575.3708
923 | 2024-06-22 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.55833 | 0.55833 | 0.56181 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_12 | 72.4757 |  | WTG Unscheduled Maintenance | 20873 | 72.4757
924 | 2024-06-22 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.64167 | 0.64167 | 0.65486 | 0 | 0.31667 | 0.31667 | Checked related error data log then reset & run the WTG. | Close | 0.012179 | O2_12 | 275.4076 |  | WTG Unscheduled Maintenance | 20873 | 275.4076
925 | 2024-06-22 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.72847 | 0.72847 | 0.74306 | 0 | 0.35 | 0.35 | Checked related error data log then reset & run the WTG. | Close | 0.013462 | O2_12 | 304.3979 |  | WTG Unscheduled Maintenance | 20873 | 304.3979
926 | 2024-06-22 | 2025 | 2024 | 2024-06-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.72986 | 0.72986 | 0.73403 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2_15 | 90.0167 |  | WTG Unscheduled Maintenance | 21604 | 90.0167
927 | 2024-06-22 | 2025 | 2024 | 2024-06-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.93056 | 0.93056 | 0.93681 | 0 | 0.15 | 0.15 | Checked related error data log then reset & run the WTG. | Close | 0.0057692 | O2_15 | 135.025 |  | WTG Unscheduled Maintenance | 21604 | 135.025
928 | 2024-06-22 | 2025 | 2024 | 2024-06-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.49028 | 0.49028 | 0.52917 | 0 | 0.93333 | 0.93333 | wtg Manual stop for lift cable correction work | Close | 0.035897 | O2_20 | 741.65 |  | WTG Breakdown Maintenance | 19071 | 741.65
929 | 2024-06-22 | 2025 | 2024 | 2024-06-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.46111 | 0.46111 | 0.58333 | 0 | 2.9333 | 2.9333 | wtg Manual stop for OMS WTG service audit work | Close | 0.11282 | O2_16 | 2345.2 |  | WTG Breakdown Maintenance | 19188 | 2345.2
930 | 2024-06-22 | 2025 | 2024 | 2024-06-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.34583 | 0.34583 | 0.35 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2_05 | 100.3458 |  | WTG Unscheduled Maintenance | 24083 | 100.3458
931 | 2024-06-22 | 2025 | 2024 | 2024-06-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.81528 | 0.81528 | 0.81667 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_05 | 33.4486 |  | WTG Unscheduled Maintenance | 24083 | 33.4486
932 | 2024-06-22 | 2025 | 2024 | 2024-06-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 3065 | Conv. emerg.off type F | Break down | 0.81528 | 0.81528 | 0.81875 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_09 | 79.8194 |  | WTG Unscheduled Maintenance | 22988 | 79.8194 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
933 | 2024-06-22 | 2025 | 2024 | 2024-06-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0 | 0 | 0.65903 | 0 | 15.8167 | 15.8167 | grid commissioning WIP. | Close | 0.60833 | O2_16 | 12645.425 |  | WTG Breakdown Maintenance | 19188 | 12645.425
934 | 2024-06-23 | 2025 | 2024 | 2024-06-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.62847 | 0.62847 | 0.66597 | 0 | 0.9 | 0.9 | Checked related error data log then apply soft reboot then reset & run the WTG. | Close | 0.034615 | O2_12 | 454.425 |  | WTG Unscheduled Maintenance | 12118 | 454.425
935 | 2024-06-23 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 360 | Timeout systemtest 1 | Break down | 0.62847 | 0.62847 | 0.68056 | 0 | 1.25 | 1.25 | Checked related error data log then apply soft reboot then reset & run the WTG. | Close | 0.048077 | O2_11 | 683.3333 |  | WTG Unscheduled Maintenance | 13120 | 683.3333
936 | 2024-06-23 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.62847 | 0.62847 | 0.66597 | 0 | 0.9 | 0.9 | Checked related error data log then apply soft reboot then reset & run the WTG. | Close | 0.034615 | O2_12 | 454.425 |  | WTG Unscheduled Maintenance | 12118 | 454.425
937 | 2024-06-23 | 2025 | 2024 | 2024-06-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.62847 | 0.62847 | 0.66667 | 0 | 0.91667 | 0.91667 | Checked related error data log then apply soft reboot then reset & run the WTG. | Close | 0.035256 | O2_13 | 494.6562 |  | WTG Unscheduled Maintenance | 12951 | 494.6562
938 | 2024-06-23 | 2025 | 2024 | 2024-06-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.62847 | 0.62847 | 0.66597 | 0 | 0.9 | 0.9 | Checked related error data log then apply soft reboot then reset & run the WTG. | Close | 0.034615 | O2_15 | 485.025 |  | WTG Unscheduled Maintenance | 12934 | 485.025
939 | 2024-06-23 | 2025 | 2024 | 2024-06-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Break down | 0.62847 | 0.62847 | 0.68056 | 0 | 1.25 | 1.25 | Checked related error data log then apply soft reboot then reset & run the WTG. | Close | 0.048077 | O2_09 | 712.9688 |  | WTG Unscheduled Maintenance | 13689 | 712.9688
940 | 2024-06-23 | 2025 | 2024 | 2024-06-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.62847 | 0.62847 | 0.66736 | 0 | 0.93333 | 0.93333 | Checked related error data log then apply soft reboot then reset & run the WTG. | Close | 0.035897 | O2_10 | 424.5889 |  | WTG Unscheduled Maintenance | 10918 | 424.5889
941 | 2024-06-23 | 2025 | 2024 | 2024-06-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 1510 | Low gearbox oil pressure | Break down | 0.67292 | 0.67292 | 0.67847 | 0 | 0.13333 | 0.13333 | auto reset | Close | 0.0051282 | O2_10 | 60.6556 |  | WTG Unscheduled Maintenance | 10918 | 60.6556
942 | 2024-06-23 | 2025 | 2024 | 2024-06-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.62847 | 0.62847 | 0.66736 | 0 | 0.93333 | 0.93333 | Checked related error data log then apply soft reboot then reset & run the WTG. | Close | 0.035897 | O2_20 | 574 |  | WTG Unscheduled Maintenance | 14760 | 574
943 | 2024-06-23 | 2025 | 2024 | 2024-06-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.62847 | 0.62847 | 0.66806 | 0 | 0.95 | 0.95 | Checked related error data log then apply soft reboot then reset & run the WTG. | Close | 0.036538 | O2_16 | 599.2521 |  | WTG Unscheduled Maintenance | 15139 | 599.2521
944 | 2024-06-23 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.62847 | 0.62847 | 0.66528 | 0 | 0.88333 | 0.88333 | Checked related error data log then apply soft reboot then reset & run the WTG. | Close | 0.033974 | O2_03 | 464.6701 |  | WTG Unscheduled Maintenance | 12625 | 464.6701
945 | 2024-06-23 | 2025 | 2024 | 2024-06-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.62847 | 0.62847 | 0.67014 | 0 | 1 | 1 | Checked related error data log then apply soft reboot then reset & run the WTG. | Close | 0.038462 | O2_02 | 747.0417 |  | WTG Unscheduled Maintenance | 17929 | 747.0417
946 | 2024-06-23 | 2025 | 2024 | 2024-06-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3060 | Conv. emerg.off type A | Break down | 0.62847 | 0.62847 | 0.66111 | 0 | 0.78333 | 0.78333 | Checked related error data log then apply soft reboot then reset & run the WTG. | Close | 0.030128 | O2_02 | 585.1826 |  | WTG Unscheduled Maintenance | 17929 | 585.1826
947 | 2024-06-23 | 2025 | 2024 | 2024-06-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.62847 | 0.62847 | 0.64375 | 0 | 0.36667 | 0.36667 | Checked related error data log then apply soft reboot then reset & run the WTG. | Close | 0.014103 | O2_09 | 209.1375 |  | WTG Unscheduled Maintenance | 13689 | 209.1375
948 | 2024-06-23 | 2025 | 2024 | 2024-06-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.77083 | 0.77083 | 0.77292 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_09 | 28.5187 |  | WTG Unscheduled Maintenance | 13689 | 28.5187
949 | 2024-06-23 | 2025 | 2024 | 2024-06-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3060 | Conv. emerg.off type A | Break down | 0.62847 | 0.62847 | 0.68056 | 0 | 1.25 | 1.25 | Checked related error data log then apply soft reboot then reset & run the WTG. | Close | 0.048077 | O2_06 | 82.5 |  | WTG Unscheduled Maintenance | 1584 | 82.5
950 | 2024-06-23 | 2025 | 2024 | 2024-06-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0 | 0 | 0.86181 | 0 | 20.6833 | 20.6833 | grid commissioning WIP. | Close | 0.79551 | O2_21 | 6635.9028 |  | WTG Breakdown Maintenance | 7700 | 6635.9028 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
951 | 2024-06-24 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.3625 | 0.3625 | 0.36389 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_13 | 5.3083 |  | WTG Unscheduled Maintenance | 3822 | 5.3083
952 | 2024-06-24 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.43194 | 0.43194 | 0.44444 | 0 | 0.3 | 0.3 | Checked related error data log then reset & run the WTG. | Close | 0.011538 | O2_12 | 59.6625 |  | WTG Unscheduled Maintenance | 4773 | 59.6625
953 | 2024-06-24 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.50486 | 0.50486 | 0.63681 | 0 | 3.1667 | 3.1667 | wtg Manual stop for OMS WTG service audit work. | Close | 0.12179 | O2_12 | 629.7708 |  | WTG Breakdown Maintenance | 4773 | 629.7708
954 | 2024-06-24 | 2025 | 2024 | 2024-06-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.19028 | 0.19028 | 0.19236 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_05 | 15.575 |  | WTG Unscheduled Maintenance | 7476 | 15.575
955 | 2024-06-24 | 2025 | 2024 | 2024-06-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.49653 | 0.49653 | 0.625 | 0 | 3.0833 | 3.0833 | Manual stop for project pending work | Close | 0.11859 | O2_06 | 493.5903 |  | WTG Breakdown Maintenance | 3842 | 493.5903
956 | 2024-06-25 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.63125 | 0.63125 | 0.69097 | 0 | 1.4333 | 1.4333 | attent and check all communication cable check encoder cable ,retight all connection then reset & run the WTG | Close | 0.055128 | O2_13 | 284.3972 |  | WTG Breakdown Maintenance | 4762 | 284.3972
957 | 2024-06-25 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.78611 | 0.78611 | 0.82708 | 0 | 0.98333 | 0.98333 | Checked related error data log then reset & run the WTG. | Close | 0.037821 | O2_13 | 195.1097 |  | WTG Unscheduled Maintenance | 4762 | 195.1097
958 | 2024-06-25 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 650 | Pitch controller communication error | Break down | 0.85 | 0.85 | 0.86389 | 0 | 0.33333 | 0.33333 | Checked related error data log then apply soft reboot then reset & run the WTG. | Close | 0.012821 | O2_13 | 66.1389 |  | WTG Unscheduled Maintenance | 4762 | 66.1389
959 | 2024-06-25 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.65625 | 0.65625 | 0.65972 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_12 | 20.9896 |  | WTG Unscheduled Maintenance | 6045 | 20.9896
960 | 2024-06-25 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.68819 | 0.68819 | 0.69167 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_12 | 20.9896 |  | WTG Unscheduled Maintenance | 6045 | 20.9896
961 | 2024-06-25 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.83819 | 0.83819 | 0.99375 | 0 | 3.7333 | 3.7333 | attend and check related circuit check and found all 3 blade are communication are missing so check all 3 blade communication cable retight all connection and than nothing found abnormal than apply hard reboot than start WTG. | Close | 0.14359 | O2_12 | 940.3333 |  | WTG Unscheduled Maintenance | 6045 | 940.3333
962 | 2024-06-25 | 2025 | 2024 | 2024-06-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 642 | Sim.angle E enc. <> act.angle 2 | Break down | 0.78611 | 0.78611 | 0.81458 | 0 | 0.68333 | 0.68333 | After grid resume wtg in error is occur so Checked related error data log then apply soft reboot then reset & run the WTG. | Close | 0.026282 | O2_13 | 135.5847 |  | WTG Unscheduled Maintenance | 4762 | 135.5847
963 | 2024-06-25 | 2025 | 2024 | 2024-06-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.20833 | 0.20833 | 0.30347 | 0 | 2.2833 | 2.2833 | Checked related error data log then apply soft reboot then reset & run the WTG. | Close | 0.087821 | O2_05 | 731.1424 |  | WTG Unscheduled Maintenance | 7685 | 731.1424
964 | 2024-06-25 | 2025 | 2024 | 2024-06-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0 | 0 | 0.75278 | 0 | 18.0667 | 18.0667 | grid commissioning WIP. | Close | 0.69487 | O2_06 | 5102.3278 |  | WTG Breakdown Maintenance | 6778 | 5102.3278 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
965 | 2024-06-26 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.52083 | 0.52083 | 0.52361 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & run the WTG. | Close | 0.0025641 | O2_11 | 16.7083 |  | WTG Unscheduled Maintenance | 6015 | 16.7083
966 | 2024-06-26 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 155 | SLC SF system monitoring | Break down | 0.56597 | 0.56597 | 0.57708 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_11 | 66.8333 |  | WTG Unscheduled Maintenance | 6015 | 66.8333
967 | 2024-06-26 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 155 | SLC SF system monitoring | Break down | 0.74583 | 0.74583 | 0.8625 | 0 | 2.8 | 2.8 | attend and set the rotor proximity sensor gap as well as clean grease from the rotor teeth then reset and start wtg. | Close | 0.10769 | O2_11 | 701.75 |  | WTG Unscheduled Maintenance | 6015 | 701.75
968 | 2024-06-26 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.011111 | 0.011111 | 0.015972 | 0 | 0.11667 | 0.11667 | attend Checked related error data log then apply hard reboot then reset & run the WTG. | Close | 0.0044872 | O2_12 | 34.9757 |  | WTG Unscheduled Maintenance | 7195 | 34.9757
969 | 2024-06-26 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.36458 | 0.36458 | 0.36806 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_12 | 24.9826 |  | WTG Unscheduled Maintenance | 7195 | 24.9826
970 | 2024-06-26 | 2025 | 2024 | 2024-06-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 88 | Outs.temp. nacelle implaus. | Break down | 0.57083 | 0.57083 | 0.78611 | 0 | 5.1667 | 5.1667 | attend Checked related ckt and found nacelle outdoor sensor malfunctioning so replace it then reset and start wtg. | Close | 0.19872 | O2_09 | 1520.0764 |  | WTG Unscheduled Maintenance | 7061 | 1520.0764
971 | 2024-06-26 | 2025 | 2024 | 2024-06-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.35556 | 0.35556 | 0.36181 | 0 | 0.15 | 0.15 | Checked related error data log then reset & run the WTG. | Close | 0.0057692 | O2_20 | 58.45 |  | WTG Unscheduled Maintenance | 9352 | 58.45
972 | 2024-06-26 | 2025 | 2024 | 2024-06-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.82917 | 0.82917 | 0.87222 | 0 | 1.0333 | 1.0333 | Checked related error data log then reset & run the WTG. | Close | 0.039744 | O2_20 | 402.6556 |  | WTG Unscheduled Maintenance | 9352 | 402.6556
973 | 2024-06-26 | 2025 | 2024 | 2024-06-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 3061 | Conv. emerg.off type B | Break down | 0.34028 | 0.34028 | 0.34167 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_03 | 10.8056 |  | WTG Unscheduled Maintenance | 7780 | 10.8056
974 | 2024-06-26 | 2025 | 2024 | 2024-06-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3063 | Conv. emerg.off type D | Break down | 0.36458 | 0.36458 | 0.36597 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_05 | 9.3806 |  | WTG Unscheduled Maintenance | 6754 | 9.3806
975 | 2024-06-26 | 2025 | 2024 | 2024-06-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.5375 | 0.5375 | 0.54097 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_09 | 24.5174 |  | WTG Unscheduled Maintenance | 7061 | 24.5174
976 | 2024-06-26 | 2025 | 2024 | 2024-06-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 3065 | Conv. emerg.off type F | Break down | 0.75486 | 0.75486 | 0.75764 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & run the WTG. | Close | 0.0025641 | O2_09 | 19.6139 |  | WTG Unscheduled Maintenance | 7061 | 19.6139
977 | 2024-06-26 | 2025 | 2024 | 2024-06-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.80069 | 0.80069 | 0.91111 | 0 | 2.65 | 2.65 | attend Checked related ckt check hydraulic pressure solenoid valve connection, check & adjust drag pressure then start. | Close | 0.10192 | O2_16 | 994.8542 |  | WTG Unscheduled Maintenance | 9010 | 994.8542
978 | 2024-06-26 | 2025 | 2024 | 2024-06-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 530 | Overload axis 3 | Break down | 0.43264 | 0.43264 | 0.43542 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & run the WTG. | Close | 0.0025641 | O2_09 | 19.6139 |  | WTG Unscheduled Maintenance | 7061 | 19.6139
979 | 2024-06-26 | 2025 | 2024 | 2024-06-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3063 | Conv. emerg.off type D | Break down | 0.50486 | 0.50486 | 0.52778 | 0 | 0.55 | 0.55 | Checked related error data log then reset & run the WTG. | Close | 0.021154 | O2_09 | 161.8146 |  | WTG Unscheduled Maintenance | 7061 | 161.8146
980 | 2024-06-27 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.060417 | 0.060417 | 0.061111 | 0 | 0.016667 | 0.016667 | Checked related error data log then reset & run the WTG. | Close | 0.00064103 | O2_11 | 8.1819 |  | WTG Unscheduled Maintenance | 11782 | 8.1819
981 | 2024-06-27 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.5875 | 0.5875 | 0.58889 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_11 | 18.9167 |  | WTG Unscheduled Maintenance | 13620 | 18.9167
982 | 2024-06-27 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.027778 | 0.027778 | 0.040278 | 0 | 0.3 | 0.3 | Checked related error data log then reset & run the WTG. | Close | 0.011538 | O2_12 | 170.25 |  | WTG Unscheduled Maintenance | 13620 | 170.25
983 | 2024-06-27 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3061 | Conv. emerg.off type B | Break down | 0.18333 | 0.18333 | 0.18542 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_12 | 28.375 |  | WTG Unscheduled Maintenance | 13620 | 28.375
984 | 2024-06-27 | 2025 | 2024 | 2024-06-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.027083 | 0.027083 | 0.040278 | 0 | 0.31667 | 0.31667 | Checked related error data log then reset & run the WTG. | Close | 0.012179 | O2_13 | 174.259 |  | WTG Unscheduled Maintenance | 13207 | 174.259
985 | 2024-06-27 | 2025 | 2024 | 2024-06-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.027778 | 0.027778 | 0.029861 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_15 | 23.1563 |  | WTG Unscheduled Maintenance | 11115 | 23.1563
986 | 2024-06-27 | 2025 | 2024 | 2024-06-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3060 | Conv. emerg.off type A | Break down | 0.31806 | 0.31806 | 0.31944 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_11 | 16.3639 |  | WTG Unscheduled Maintenance | 11782 | 16.3639
987 | 2024-06-27 | 2025 | 2024 | 2024-06-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 153 | SLC SF max. cable winding | Break down | 0.85625 | 0.85625 | 0.98472 | 0 | 3.0833 | 3.0833 | attend and found twist of sensor limit switch trip and also cable twist is higher so removed cable twist and set twist of sensor then reset and start wtg. | Close | 0.11859 | O2_10 | 1490.9201 |  | WTG Unscheduled Maintenance | 11605 | 1490.9201
988 | 2024-06-27 | 2025 | 2024 | 2024-06-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.65764 | 0.65764 | 0.69236 | 0 | 0.83333 | 0.83333 | attend for CAN related error so check CAN communication cable, cannector,proper grounding is ok and found no any abnormality so reset and start WTG. | Close | 0.032051 | O2_05 | 381.6667 |  | WTG Breakdown Maintenance | 10992 | 381.6667
989 | 2024-06-27 | 2025 | 2024 | 2024-06-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.47778 | 0.47778 | 0.68542 | 0 | 4.9833 | 4.9833 | attend and replace chopper register in axis 1 and also done OMS audit work. | Close | 0.19167 | O2_16 | 2655.0785 |  | WTG Breakdown Maintenance | 12787 | 2655.0785
990 | 2024-06-27 | 2025 | 2024 | 2024-06-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3063 | Conv. emerg.off type D | Break down | 0.82292 | 0.82292 | 0.82431 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_16 | 17.7597 |  | WTG Unscheduled Maintenance | 12787 | 17.7597
991 | 2024-06-27 | 2025 | 2024 | 2024-06-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3063 | Conv. emerg.off type D | Break down | 0.92431 | 0.92431 | 0.93542 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_06 | 148.0667 |  | WTG Unscheduled Maintenance | 13326 | 148.0667
992 | 2024-06-28 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.19306 | 0.19306 | 0.19375 | 0 | 0.016667 | 0.016667 | Checked related error data log then reset & run the WTG. | Close | 0.00064103 | O2_11 | 12.7792 |  | WTG Unscheduled Maintenance | 18402 | 12.7792
993 | 2024-06-28 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.62222 | 0.62222 | 0.62431 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_11 | 38.3375 |  | WTG Unscheduled Maintenance | 18402 | 38.3375
994 | 2024-06-28 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.68333 | 0.68333 | 0.68472 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_11 | 25.5583 |  | WTG Unscheduled Maintenance | 18402 | 25.5583
995 | 2024-06-28 | 2025 | 2024 | 2024-06-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.43958 | 0.43958 | 0.45278 | 0 | 0.31667 | 0.31667 | Checked related error data log then reset & run the WTG. | Close | 0.012179 | O2_12 | 246.0236 |  | WTG Unscheduled Maintenance | 18646 | 246.0236
996 | 2024-06-28 | 2025 | 2024 | 2024-06-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down | 0.62569 | 0.62569 | 0.62708 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_16 | 25.0778 |  | WTG Unscheduled Maintenance | 18056 | 25.0778
997 | 2024-06-28 | 2025 | 2024 | 2024-06-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.48681 | 0.48681 | 0.48819 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_20 | 21.1944 |  | WTG Unscheduled Maintenance | 15260 | 21.1944
998 | 2024-06-28 | 2025 | 2024 | 2024-06-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.68681 | 0.68681 | 0.68819 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_16 | 25.0778 |  | WTG Unscheduled Maintenance | 18056 | 25.0778
999 | 2024-06-28 | 2025 | 2024 | 2024-06-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.98889 | 0.98889 | 0.99028 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_16 | 25.0778 |  | WTG Unscheduled Maintenance | 18056 | 25.0778
1000 | 2024-06-29 | 2025 | 2024 | 2024-06-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.44028 | 0.44028 | 0.74861 | 0 | 7.4 | 7.4 | wtg Manual stop for maintenance activity work. | Close | 0.28462 | O2_16 | 9067.1583 |  | WTG Breakdown Maintenance | 29407 | 9067.1583
1001 | 2024-06-29 | 2025 | 2024 | 2024-06-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.040278 | 0.040278 | 0.040972 | 0 | 0.016667 | 0.016667 | Checked related error data log then reset & run the WTG. | Close | 0.00064103 | O2_05 | 17.4674 |  | WTG Unscheduled Maintenance | 25153 | 17.4674
1002 | 2024-06-29 | 2025 | 2024 | 2024-06-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.86875 | 0.86875 | 0.87292 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2_11 | 116.6458 |  | WTG Unscheduled Maintenance | 27995 | 116.6458
1003 | 2024-06-29 | 2025 | 2024 | 2024-06-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.99097 | 0.99097 | 0.99236 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_11 | 38.8819 |  | WTG Unscheduled Maintenance | 27995 | 38.8819
1004 | 2024-06-29 | 2025 | 2024 | 2024-06-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.034028 | 0.034028 | 0.04375 | 0 | 0.23333 | 0.23333 | Checked related error data log then reset & run the WTG. | Close | 0.0089744 | O2_16 | 285.9014 |  | WTG Unscheduled Maintenance | 29407 | 285.9014
1005 | 2024-06-29 | 2025 | 2024 | 2024-06-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.36528 | 0.36528 | 0.36736 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_16 | 61.2646 |  | WTG Unscheduled Maintenance | 29407 | 61.2646
1006 | 2024-06-29 | 2025 | 2024 | 2024-06-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.96042 | 0.96042 | 0.975 | 0 | 0.35 | 0.35 | Checked related error data log then reset & run the WTG. | Close | 0.013462 | O2_16 | 428.8521 |  | WTG Unscheduled Maintenance | 29407 | 428.8521
1007 | 2024-06-29 | 2025 | 2024 | 2024-06-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.98889 | 0.98889 | 0.99028 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_16 | 40.8431 |  | WTG Unscheduled Maintenance | 29407 | 40.8431
1008 | 2024-06-30 | 2025 | 2024 | 2024-06-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.51944 | 0.51944 | 0.52083 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_11 | 37.2486 |  | WTG Unscheduled Maintenance | 26819 | 37.2486
1009 | 2024-06-30 | 2025 | 2024 | 2024-06-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.54444 | 0.54444 | 0.54583 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_05 | 30.9653 |  | WTG Unscheduled Maintenance | 22295 | 30.9653
1010 | 2024-06-30 | 2025 | 2024 | 2024-06-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.62431 | 0.62431 | 0.63194 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & run the WTG. | Close | 0.0070513 | O2_06 | 186.3583 |  | WTG Unscheduled Maintenance | 24396 | 186.3583
1011 | 2024-06-30 | 2025 | 2024 | 2024-06-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.66458 | 0.66458 | 0.66597 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_06 | 33.8833 |  | WTG Unscheduled Maintenance | 24396 | 33.8833
1012 | 2024-06-30 | 2025 | 2024 | 2024-06-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.73542 | 0.73542 | 0.73889 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_06 | 84.7083 |  | WTG Unscheduled Maintenance | 24396 | 84.7083
1013 | 2024-06-30 | 2025 | 2024 | 2024-06-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.023611 | 0.023611 | 0.028472 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & run the WTG. | Close | 0.0044872 | O2_06 | 118.5917 |  | WTG Unscheduled Maintenance | 24396 | 118.5917
1014 | 2024-06-30 | 2025 | 2024 | 2024-06-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 4093 | Rel. air hum. tower base inside too high (in operation) | Break down | 0.15556 | 0.15556 | 0.15625 | 0 | 0.016667 | 0.016667 | Checked related error data log then reset & run the WTG. | Close | 0.00064103 | O2_06 | 16.9417 |  | WTG Unscheduled Maintenance | 24396 | 16.9417
1015 | 2024-06-30 | 2025 | 2024 | 2024-06-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.30486 | 0.30486 | 0.32639 | 0 | 0.51667 | 0.51667 | Checked related error data log then reset & run the WTG. | Close | 0.019872 | O2_06 | 525.1917 |  | WTG Unscheduled Maintenance | 24396 | 525.1917
1016 | 2024-06-30 | 2025 | 2024 | 2024-06-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.46319 | 0.46319 | 0.46806 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & run the WTG. | Close | 0.0044872 | O2_06 | 118.5917 |  | WTG Unscheduled Maintenance | 24396 | 118.5917
1017 | 2024-07-01 | 2025 | 2024 | 2024-07-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.12361 | 0.12361 | 0.125 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_11 | 51.0944 |  | WTG Unscheduled Maintenance | 36788 | 51.0944
1018 | 2024-07-01 | 2025 | 2024 | 2024-07-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.21944 | 0.21944 | 0.22083 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_11 | 51.0944 |  | WTG Unscheduled Maintenance | 36788 | 51.0944
1019 | 2024-07-01 | 2025 | 2024 | 2024-07-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Break down | 0.61528 | 0.61528 | 0.61806 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & run the WTG. | Close | 0.0025641 | O2_12 | 101.7139 |  | WTG Unscheduled Maintenance | 36617 | 101.7139
1020 | 2024-07-01 | 2025 | 2024 | 2024-07-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.00625 | 0.00625 | 0.011111 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & run the WTG. | Close | 0.0044872 | O2_13 | 171.2278 |  | WTG Unscheduled Maintenance | 35224 | 171.2278
1021 | 2024-07-01 | 2025 | 2024 | 2024-07-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 7415 | PLC hardware error | Major BD | 0.22083 | 0.22083 | 0.64583 | 0 | 10.2 | 10.2 | wtg in error but road was not accesable for vehicale so another vehicale arragemnt than after attend WTG. | Close | 0.39231 | O2_02 | 16039.5 |  | WTG Unscheduled Maintenance | 37740 | 16039.5
1022 | 2024-07-01 | 2025 | 2024 | 2024-07-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 7415 | PLC hardware error | Break down | 0.64583 | 0.64583 | 0.67639 | 0 | 0.73333 | 0.73333 | attend and found grid voltage measurement module issue ,due to connector not proper tight so correct it,then reset & run the WTG. | Close | 0.028205 | O2_02 | 1153.1667 |  | WTG Unscheduled Maintenance | 37740 | 1153.1667
1023 | 2024-07-01 | 2025 | 2024 | 2024-07-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.21528 | 0.21528 | 0.21944 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2_05 | 83.5458 |  | WTG Unscheduled Maintenance | 20051 | 83.5458
1024 | 2024-07-01 | 2025 | 2024 | 2024-07-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 172 | SLC MF torque protection | Break down | 0.022917 | 0.022917 | 0.028472 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & run the WTG. | Close | 0.0051282 | O2_09 | 195.0278 |  | WTG Unscheduled Maintenance | 35105 | 195.0278
1025 | 2024-07-01 | 2025 | 2024 | 2024-07-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 4093 | Rel. air hum. tower base inside too high (in operation) | Break down | 0.23889 | 0.23889 | 0.24167 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & run the WTG. | Close | 0.0025641 | O2_06 | 117.3472 |  | WTG Unscheduled Maintenance | 42245 | 117.3472
1026 | 2024-07-02 | 2025 | 2024 | 2024-07-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.50417 | 0.50417 | 0.51806 | 0 | 0.33333 | 0.33333 | Checked related error data log then reset & run the WTG. | Close | 0.012821 | O2_11 | 760.75 |  | WTG Unscheduled Maintenance | 54774 | 760.75
1027 | 2024-07-02 | 2025 | 2024 | 2024-07-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Break down | 0.94861 | 0.94861 | 1899-12-31 | 0 | 1.2333 | 1.2333 | WIP. | Close | 0.047436 | O2_11 | 2814.775 |  | WTG Unscheduled Maintenance | 54774 | 2814.775
1028 | 2024-07-02 | 2025 | 2024 | 2024-07-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.55694 | 0.55694 | 0.60833 | 0 | 1.2333 | 1.2333 | Checked related error data log then reset & run the WTG. | Close | 0.047436 | O2_11 | 2814.775 |  | WTG Unscheduled Maintenance | 54774 | 2814.775
1029 | 2024-07-02 | 2025 | 2024 | 2024-07-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.65972 | 0.65972 | 0.66181 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_11 | 114.1125 |  | WTG Unscheduled Maintenance | 54774 | 114.1125
1030 | 2024-07-02 | 2025 | 2024 | 2024-07-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 642 | Sim.angle E enc. <> act.angle 2 | Break down | 0.70972 | 0.70972 | 0.90833 | 0 | 4.7667 | 4.7667 | attend and check all related circuit found blade 2 encoder cable pinched due to cable tie so remove it then start wtg. | Close | 0.18333 | O2_09 | 10385.9708 |  | WTG Unscheduled Maintenance | 52293 | 10385.9708
1031 | 2024-07-02 | 2025 | 2024 | 2024-07-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.57153 | 0.57153 | 0.60833 | 0 | 0.88333 | 0.88333 | Checked related error data log then apply soft reboot then reset & run the WTG. | Close | 0.033974 | O2_10 | 1829.5674 |  | WTG Unscheduled Maintenance | 49709 | 1829.5674
1032 | 2024-07-02 | 2025 | 2024 | 2024-07-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 578 | Pitch set point slow hold time BP75 | Break down | 0.072917 | 0.072917 | 0.075694 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & run the WTG. | Close | 0.0025641 | O2_06 | 166.3694 |  | WTG Unscheduled Maintenance | 59893 | 166.3694
1033 | 2024-07-02 | 2025 | 2024 | 2024-07-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.3125 | 0.3125 | 0.31319 | 0 | 0.016667 | 0.016667 | Checked related error data log then reset & run the WTG. | Close | 0.00064103 | O2_06 | 41.5924 |  | WTG Unscheduled Maintenance | 59893 | 41.5924
1034 | 2024-07-02 | 2025 | 2024 | 2024-07-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 578 | Pitch set point slow hold time BP75 | Break down | 0.34931 | 0.34931 | 0.35139 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_06 | 124.7771 |  | WTG Unscheduled Maintenance | 59893 | 124.7771
1035 | 2024-07-02 | 2025 | 2024 | 2024-07-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.45764 | 0.45764 | 0.78819 | 0 | 7.9333 | 7.9333 | wtg Manual stop for 1st month maintenance activity work. | Close | 0.30513 | O2_06 | 19797.9639 |  | WTG Breakdown Maintenance | 59893 | 19797.9639
1036 | 2024-07-02 | 2025 | 2024 | 2024-07-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down | 0.10764 | 0.10764 | 0.12153 | 0 | 0.33333 | 0.33333 | Checked related error data log then apply soft reboot then reset & run the WTG. | Close | 0.012821 | O2_02 | 719.4722 |  | WTG Unscheduled Maintenance | 51802 | 719.4722
1037 | 2024-07-02 | 2025 | 2024 | 2024-07-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.51181 | 0.51181 | 0.52222 | 0 | 0.25 | 0.25 | Checked related error data log then reset & run the WTG. | Close | 0.0096154 | O2_05 | 511.9271 |  | WTG Unscheduled Maintenance | 49145 | 511.9271
1038 | 2024-07-02 | 2025 | 2024 | 2024-07-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.82778 | 0.82778 | 0.82917 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_05 | 68.2569 |  | WTG Unscheduled Maintenance | 49145 | 68.2569
1039 | 2024-07-02 | 2025 | 2024 | 2024-07-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.34653 | 0.34653 | 0.35069 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2_20 | 152.3625 |  | WTG Unscheduled Maintenance | 36567 | 152.3625
1040 | 2024-07-02 | 2025 | 2024 | 2024-07-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.81528 | 0.81528 | 0.84097 | 0 | 0.61667 | 0.61667 | Checked related error data log then apply soft reboot then reset & run the WTG. | Close | 0.023718 | O2_20 | 939.5688 |  | WTG Unscheduled Maintenance | 36567 | 939.5688
1041 | 2024-07-02 | 2025 | 2024 | 2024-07-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.048611 | 0.048611 | 0.05 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_20 | 50.7875 |  | WTG Unscheduled Maintenance | 36567 | 50.7875
1042 | 2024-07-02 | 2025 | 2024 | 2024-07-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.79375 | 0.79375 | 0.81736 | 0 | 0.56667 | 0.56667 | Checked related error data log then apply soft reboot then reset & run the WTG. | Close | 0.021795 | O2_20 | 863.3875 |  | WTG Unscheduled Maintenance | 36567 | 863.3875
1043 | 2024-07-03 | 2025 | 2024 | 2024-07-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0.80486 | 0.80486 | 0.87153 | 0 | 1.6 | 1.6 | attend by HT team and found VCB tripped by Unknown person so check then related circuit then no any abnormality so charge the VCB and start wtg. | Close | 0.061538 | O2_12 | 2623.6667 |  | WTG Unscheduled Maintenance | 39355 | 2623.6667
1044 | 2024-07-03 | 2025 | 2024 | 2024-07-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0.8125 | 0.8125 | 0.875 | 0 | 1.5 | 1.5 | attend by HT team and found VCB tripped by Unknown person so check then related circuit then no any abnormality so charge the VCB and start wtg. | Close | 0.057692 | O2_12 | 2459.6875 |  | WTG Unscheduled Maintenance | 39355 | 2459.6875
1045 | 2024-07-03 | 2025 | 2024 | 2024-07-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Major BD | 0 | 0 | 0.52083 | 0 | 12.5 | 12.5 | attend check all related circuit and found encoder of blade 1 defective, so replace it then blade calibration done reset and start wtg. | Close | 0.48077 | O2_12 | 20497.3958 |  | WTG Unscheduled Maintenance | 39355 | 20497.3958
1046 | 2024-07-03 | 2025 | 2024 | 2024-07-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0.8 | 0.8 | 0.8625 | 0 | 1.5 | 1.5 | attend by HT team and found VCB tripped by Unknown person so check then related circuit then no any abnormality so charge the VCB and start wtg. | Close | 0.057692 | O2_12 | 2459.6875 |  | WTG Unscheduled Maintenance | 39355 | 2459.6875
1047 | 2024-07-03 | 2025 | 2024 | 2024-07-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 642 | Sim.angle E enc. <> act.angle 2 | Major BD | 0.58611 | 0.58611 | 1899-12-31 | 0 | 9.9333 | 9.9333 | arrend check related circuit and replace encoder of blade2 and start turbine after thet gain error occurred so troubleshooting WIP | Close | 0.38205 | O2_09 | 19226.7944 |  | WTG Unscheduled Maintenance | 46454 | 19226.7944
1048 | 2024-07-03 | 2025 | 2024 | 2024-07-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.39167 | 0.39167 | 0.73472 | 0 | 8.2333 | 8.2333 | wtg Manual stop for 1st month maintenance activity work. | Close | 0.31667 | O2_06 | 16901.3181 |  | WTG Breakdown Maintenance | 49267 | 16901.3181
1049 | 2024-07-03 | 2025 | 2024 | 2024-07-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 5520 | 4-20mA hydraulic pressure | Major BD | 0.59722 | 0.59722 | 1899-12-31 | 0 | 9.6667 | 9.6667 | road problem, Road is not proper accessible.wip | Close | 0.37179 | O2_05 | 18073.4444 |  | WTG Unscheduled Maintenance | 44872 | 18073.4444
1050 | 2024-07-03 | 2025 | 2024 | 2024-07-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.21528 | 0.21528 | 0.22153 | 0 | 0.15 | 0.15 | Checked related error data log then reset & run the WTG. | Close | 0.0057692 | O2_20 | 183.7187 |  | WTG Unscheduled Maintenance | 29395 | 183.7187
1051 | 2024-07-04 | 2025 | 2024 | 2024-07-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 642 | Sim.angle E enc. <> act.angle 2 | Major BD | 0 | 0 | 0.76319 | 0 | 18.3167 | 18.3167 | attend and replaced Encoder A in axis1 then done calibration after then reset and start wtg. | Close | 0.70449 | O2_09 | 22228.0382 |  | WTG Unscheduled Maintenance | 29125 | 22228.0382
1052 | 2024-07-04 | 2025 | 2024 | 2024-07-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 5520 | 4-20mA hydraulic pressure | Major BD | 0 | 0 | 0.75417 | 0 | 18.1 | 18.1 | Hydraulic pressure input malfunction ,so once input received, then start the turbine. | Close | 0.69615 | O2_05 | 21026.9208 |  | WTG Unscheduled Maintenance | 27881 | 21026.9208
1053 | 2024-07-04 | 2025 | 2024 | 2024-07-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 172 | SLC MF torque protection | Break down | 0.88264 | 0.88264 | 0.88611 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_09 | 101.1285 |  | WTG Unscheduled Maintenance | 29125 | 101.1285
1054 | 2024-07-04 | 2025 | 2024 | 2024-07-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.55764 | 0.55764 | 0.55903 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_16 | 27.3764 |  | WTG Unscheduled Maintenance | 19711 | 27.3764
1055 | 2024-07-04 | 2025 | 2024 | 2024-07-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.85764 | 0.85764 | 0.85972 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_16 | 41.0646 |  | WTG Unscheduled Maintenance | 19711 | 41.0646
1056 | 2024-07-05 | 2025 | 2024 | 2024-07-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.94306 | 0.94306 | 0.94444 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_11 | 27.7278 |  | WTG Unscheduled Maintenance | 19964 | 27.7278
1057 | 2024-07-05 | 2025 | 2024 | 2024-07-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.18889 | 0.18889 | 0.19097 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_11 | 41.5917 |  | WTG Unscheduled Maintenance | 19964 | 41.5917
1058 | 2024-07-05 | 2025 | 2024 | 2024-07-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.34097 | 0.34097 | 0.69444 | 0 | 8.4833 | 8.4833 | wtg Manual stop for 1st month maintenance activity work. | Close | 0.32628 | O2_11 | 7056.7194 |  | WTG Breakdown Maintenance | 19964 | 7056.7194
1059 | 2024-07-05 | 2025 | 2024 | 2024-07-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.33958 | 0.33958 | 0.34167 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_11 | 41.5917 |  | WTG Unscheduled Maintenance | 19964 | 41.5917
1060 | 2024-07-05 | 2025 | 2024 | 2024-07-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Ladder issue | 0.46528 | 0.46528 | 0.75556 | 0 | 6.9667 | 6.9667 | wtg manul stop for ladder replacement work. | Close | 0.26795 | O2_09 | 5910.9264 |  | WTG Breakdown Maintenance | 20363 | 5910.9264
1061 | 2024-07-05 | 2025 | 2024 | 2024-07-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.00069444 | 0.00069444 | 0.0020833 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_05 | 27.8083 |  | WTG Unscheduled Maintenance | 20022 | 27.8083
1062 | 2024-07-05 | 2025 | 2024 | 2024-07-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 172 | SLC MF torque protection | Break down | 0.91181 | 0.91181 | 0.92083 | 0 | 0.21667 | 0.21667 | Checked related error data log then reset & run the WTG. | Close | 0.0083333 | O2_09 | 183.8326 |  | WTG Unscheduled Maintenance | 20363 | 183.8326
1063 | 2024-07-05 | 2025 | 2024 | 2024-07-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.59375 | 0.59375 | 0.62847 | 0 | 0.83333 | 0.83333 | Checked related error data log then reset & run the WTG. | Close | 0.032051 | O2_16 | 644.8264 |  | WTG Unscheduled Maintenance | 18571 | 644.8264
1064 | 2024-07-05 | 2025 | 2024 | 2024-07-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.56736 | 0.56736 | 0.57014 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & run the WTG. | Close | 0.0025641 | O2_16 | 51.5861 |  | WTG Unscheduled Maintenance | 18571 | 51.5861
1065 | 2024-07-05 | 2025 | 2024 | 2024-07-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3063 | Conv. emerg.off type D | Break down | 0.20278 | 0.20278 | 0.20417 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_16 | 25.7931 |  | WTG Unscheduled Maintenance | 18571 | 25.7931
1066 | 2024-07-05 | 2025 | 2024 | 2024-07-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 7002 | Task runtime failure 5ms | Break down | 0.3125 | 0.3125 | 0.32361 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_16 | 206.3444 |  | WTG Unscheduled Maintenance | 18571 | 206.3444
1067 | 2024-07-06 | 2025 | 2024 | 2024-07-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.34653 | 0.34653 | 0.59167 | 0 | 5.8833 | 5.8833 | wtg Manual stop for 1st month maintenance activity work. | Close | 0.22628 | O2_12 | 8778.6688 |  | WTG Breakdown Maintenance | 35811 | 8778.6688
1068 | 2024-07-06 | 2025 | 2024 | 2024-07-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.61111 | 0.61111 | 0.69514 | 0 | 2.0167 | 2.0167 | attend and found wtg is offline so check and found NT255 Bachman power supply module fail. So replace it then start wtg. | Close | 0.077564 | O2_09 | 3571.3486 |  | WTG Unscheduled Maintenance | 42502 | 3571.3486
1069 | 2024-07-06 | 2025 | 2024 | 2024-07-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.25625 | 0.25625 | 0.26528 | 0 | 0.21667 | 0.21667 | Checked related error data log then reset & run the WTG. | Close | 0.0083333 | O2_06 | 281.5944 |  | WTG Unscheduled Maintenance | 31192 | 281.5944
1070 | 2024-07-06 | 2025 | 2024 | 2024-07-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 5520 | 4-20mA hydraulic pressure | Auto reset | 0.44097 | 0.44097 | 0.44167 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | O2_05 | 28.6764 |  | WTG Unscheduled Maintenance | 41294 | 28.6764
1071 | 2024-07-06 | 2025 | 2024 | 2024-07-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.57153 | 0.57153 | 0.57292 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2_05 | 57.3528 |  | WTG Unscheduled Maintenance | 41294 | 57.3528
1072 | 2024-07-06 | 2025 | 2024 | 2024-07-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 172 | SLC MF torque protection | Break down | 0.13819 | 0.13819 | 0.14583 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & run the WTG. | Close | 0.0070513 | O2_09 | 324.6681 |  | WTG Unscheduled Maintenance | 42502 | 324.6681
1073 | 2024-07-06 | 2025 | 2024 | 2024-07-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 172 | SLC MF torque protection | Break down | 0.20764 | 0.20764 | 0.21111 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_09 | 147.5764 |  | WTG Unscheduled Maintenance | 42502 | 147.5764
1074 | 2024-07-06 | 2025 | 2024 | 2024-07-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.42778 | 0.42778 | 0.42917 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_16 | 34.3056 |  | WTG Unscheduled Maintenance | 24700 | 34.3056
1075 | 2024-07-06 | 2025 | 2024 | 2024-07-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.44931 | 0.44931 | 0.60972 | 0 | 3.85 | 3.85 | attend and check chopper resistor of axis2 replace it,then check comm cable from controller to converter tgen start wtg. | Close | 0.14808 | O2_16 | 3962.2917 |  | WTG Breakdown Maintenance | 24700 | 3962.2917
1076 | 2024-07-06 | 2025 | 2024 | 2024-07-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.73542 | 0.73542 | 0.7375 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_16 | 51.4583 |  | WTG Unscheduled Maintenance | 24700 | 51.4583
1077 | 2024-07-06 | 2025 | 2024 | 2024-07-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.72083 | 0.72083 | 0.74583 | 0 | 0.6 | 0.6 | check comm cable from controller to converter, correct cable routine then start wtg. | Close | 0.023077 | O2_16 | 617.5 |  | WTG Breakdown Maintenance | 24700 | 617.5
1078 | 2024-07-06 | 2025 | 2024 | 2024-07-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.026389 | 0.026389 | 0.029167 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & run the WTG. | Close | 0.0025641 | O2_16 | 68.6111 |  | WTG Unscheduled Maintenance | 24700 | 68.6111
1079 | 2024-07-06 | 2025 | 2024 | 2024-07-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.22431 | 0.22431 | 0.22569 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_16 | 34.3056 |  | WTG Unscheduled Maintenance | 24700 | 34.3056
1080 | 2024-07-06 | 2025 | 2024 | 2024-07-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.65694 | 0.65694 | 0.68056 | 0 | 0.56667 | 0.56667 | attend and check comm cable from conroller to converter, correct cable routine then start wtg. | Close | 0.021795 | O2_16 | 583.1944 |  | WTG Breakdown Maintenance | 24700 | 583.1944
1081 | 2024-07-07 | 2025 | 2024 | 2024-07-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.61528 | 0.61528 | 0.61944 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2_09 | 147.1375 |  | WTG Unscheduled Maintenance | 35313 | 147.1375
1082 | 2024-07-07 | 2025 | 2024 | 2024-07-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.5 | 0.5 | 0.61389 | 0 | 2.7333 | 2.7333 | wtg manul stop for service audit punch poin closure work. | Close | 0.10513 | O2_16 | 4007.5222 |  | WTG Breakdown Maintenance | 35188 | 4007.5222
1083 | 2024-07-07 | 2025 | 2024 | 2024-07-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3250 | No power | Break down | 0.17708 | 0.17708 | 0.18681 | 0 | 0.23333 | 0.23333 | Checked related error data log then reset & run the WTG. | Close | 0.0089744 | O2_05 | 350.1944 |  | WTG Unscheduled Maintenance | 36020 | 350.1944
1084 | 2024-07-07 | 2025 | 2024 | 2024-07-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.54583 | 0.54583 | 0.61111 | 0 | 1.5667 | 1.5667 | check temp data once temp within range then started turbine.(plan for attend once turbine accessible by road) | Close | 0.060256 | O2_05 | 2351.3056 |  | WTG Unscheduled Maintenance | 36020 | 2351.3056
1085 | 2024-07-07 | 2025 | 2024 | 2024-07-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 172 | SLC MF torque protection | Break down | 04:48 | 04:48 | 04:50 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_09 | 49.0458 |  | WTG Unscheduled Maintenance | 35313 | 49.0458 | 49.0458 | 49.0458 | 49.0458 | 49.0458
1086 | 2024-07-08 | 2025 | 2024 | 2024-07-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.061806 | 0.061806 | 0.063194 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_11 | 20.8694 |  | WTG Unscheduled Maintenance | 15026 | 20.8694
1087 | 2024-07-08 | 2025 | 2024 | 2024-07-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.49444 | 0.49444 | 0.73611 | 0 | 5.8 | 5.8 | wtg manual stop for service audit punch poin closure work. | Close | 0.22308 | O2_11 | 3631.2833 |  | WTG Breakdown Maintenance | 15026 | 3631.2833
1088 | 2024-07-08 | 2025 | 2024 | 2024-07-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 656 | Error pitch converter 1 | Break down | 0.99097 | 0.99097 | 0.99861 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & run the WTG. | Close | 0.0070513 | O2_11 | 114.7819 |  | WTG Unscheduled Maintenance | 15026 | 114.7819
1089 | 2024-07-08 | 2025 | 2024 | 2024-07-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.39861 | 0.39861 | 0.77431 | 0 | 9.0167 | 9.0167 | wtg Manual stop for 1st month maintenance activity work. | Close | 0.34679 | O2_10 | 5369.8007 |  | WTG Scheduled Maintenance | 14293 | 5369.8007
1090 | 2024-07-08 | 2025 | 2024 | 2024-07-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.48958 | 0.48958 | 0.59167 | 0 | 2.45 | 2.45 | Check and found temp sensor of brakepad malfunctioning, so replaced sensor and start | Close | 0.094231 | O2_09 | 1530.3313 |  | WTG Unscheduled Maintenance | 14991 | 1530.3313
1091 | 2024-07-08 | 2025 | 2024 | 2024-07-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 172 | SLC MF torque protection | Break down | 0.375 | 0.375 | 0.42083 | 0 | 1.1 | 1.1 | Check related data then reset and start | Close | 0.042308 | O2_09 | 687.0875 |  | WTG Unscheduled Maintenance | 14991 | 687.0875
1092 | 2024-07-08 | 2025 | 2024 | 2024-07-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.089583 | 0.089583 | 0.090972 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_18 | 19.9764 |  | WTG Unscheduled Maintenance | 14383 | 19.9764
1093 | 2024-07-08 | 2025 | 2024 | 2024-07-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.81528 | 0.81528 | 0.81667 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_18 | 19.9764 |  | WTG Unscheduled Maintenance | 14383 | 19.9764
1094 | 2024-07-08 | 2025 | 2024 | 2024-07-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.83472 | 0.83472 | 0.8375 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & run the WTG. | Close | 0.0025641 | O2_18 | 39.9528 |  | WTG Unscheduled Maintenance | 14383 | 39.9528
1095 | 2024-07-08 | 2025 | 2024 | 2024-07-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.12153 | 0.12153 | 0.12361 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_18 | 29.9646 |  | WTG Unscheduled Maintenance | 14383 | 29.9646
1096 | 2024-07-09 | 2025 | 2024 | 2024-07-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.22569 | 0.22569 | 0.22986 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2_13 | 42 |  | WTG Unscheduled Maintenance | 10070 | 41.9583
1097 | 2024-07-09 | 2025 | 2024 | 2024-07-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.5375 | 0.5375 | 0.54444 | 0 | 0.16667 | 0.16667 | Checked related error data log then reset & run the WTG. | Close | 0.0064103 | O2_13 | 70 |  | WTG Unscheduled Maintenance | 10070 | 69.9306
1098 | 2024-07-09 | 2025 | 2024 | 2024-07-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.67361 | 0.67361 | 0.67847 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & run the WTG. | Close | 0.0044872 | O2_09 | 52 |  | WTG Unscheduled Maintenance | 10664 | 51.8389
1099 | 2024-07-09 | 2025 | 2024 | 2024-07-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.36458 | 0.36458 | 0.63958 | 0 | 6.6 | 6.6 | WTG manually stop for 1st month maintenance activity. | Close | 0.25385 | O2_14 | 2945 |  | WTG Scheduled Maintenance | 10710 | 2945.25
1100 | 2024-07-09 | 2025 | 2024 | 2024-07-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.11458 | 0.11458 | 0.12083 | 0 | 0.15 | 0.15 | Checked related error data log then reset & run the WTG. | Close | 0.0057692 | O2_06 | 73 |  | WTG Unscheduled Maintenance | 11729 | 73.3063
1101 | 2024-07-09 | 2025 | 2024 | 2024-07-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.12222 | 0.12222 | 0.13333 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_21 | 121 |  | WTG Unscheduled Maintenance | 10892 | 121.0222
1102 | 2024-07-09 | 2025 | 2024 | 2024-07-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 4093 | Rel. air hum. tower base inside too high (in operation) | Break down | 0.97083 | 0.97083 | 0.97917 | 0 | 0.2 | 0.2 | Checked related error data log then reset & run the WTG. | Close | 0.0076923 | O2_21 | 91 |  | WTG Unscheduled Maintenance | 10892 | 90.7667
1103 | 2024-07-10 | 2025 | 2024 | 2024-07-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.50833 | 0.50833 | 0.72708 | 0 | 5.25 | 5.25 | WTG manually stop for punch point closure work. | Close | 0.20192 | O2_13 | 1813 |  | WTG Breakdown Maintenance | 8290 | 1813.4375
1104 | 2024-07-10 | 2025 | 2024 | 2024-07-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.85 | 0.85 | 0.85139 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_13 | 11 |  | WTG Unscheduled Maintenance | 8290 | 11.5139
1105 | 2024-07-10 | 2025 | 2024 | 2024-07-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.475 | 0.475 | 0.47847 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_12 | 23 |  | WTG Unscheduled Maintenance | 6518 | 22.6319
1106 | 2024-07-10 | 2025 | 2024 | 2024-07-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.52292 | 0.52292 | 0.52639 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_12 | 23 |  | WTG Unscheduled Maintenance | 6518 | 22.6319
1107 | 2024-07-10 | 2025 | 2024 | 2024-07-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.56667 | 0.56667 | 0.57153 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & run the WTG. | Close | 0.0044872 | O2_12 | 32 |  | WTG Unscheduled Maintenance | 6518 | 31.6847
1108 | 2024-07-10 | 2025 | 2024 | 2024-07-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.39306 | 0.39306 | 0.66667 | 0 | 6.5667 | 6.5667 | WTG manually stop for 1st month maintenance activity. | Close | 0.25256 | O2_15 | 2506 |  | WTG Scheduled Maintenance | 9159 | 2506.0042
1109 | 2024-07-10 | 2025 | 2024 | 2024-07-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.26597 | 0.26597 | 0.26736 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_09 | 12 |  | WTG Unscheduled Maintenance | 8428 | 11.7056
1110 | 2024-07-10 | 2025 | 2024 | 2024-07-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.26597 | 0.26597 | 0.26736 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_06 | 15 |  | WTG Unscheduled Maintenance | 11058 | 15.3583
1111 | 2024-07-10 | 2025 | 2024 | 2024-07-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.26597 | 0.26597 | 0.26736 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_21 | 15 |  | WTG Unscheduled Maintenance | 10984 | 15.2556
1112 | 2024-07-10 | 2025 | 2024 | 2024-07-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.98542 | 0.98542 | 0.98681 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_21 | 15 |  | WTG Unscheduled Maintenance | 10984 | 15.2556
1113 | 2024-07-10 | 2025 | 2024 | 2024-07-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.57986 | 0.57986 | 0.58333 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_03 | 31 |  | WTG Unscheduled Maintenance | 8906 | 30.9236
1114 | 2024-07-11 | 2025 | 2024 | 2024-07-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.37708 | 0.37708 | 0.66111 | 0 | 6.8167 | 6.8167 | WTG manually stop for 1st month maintenance activity. | Close | 0.26218 | O2_15 | 4518 |  | WTG Scheduled Maintenance | 15908 | 4518.3139
1115 | 2024-07-11 | 2025 | 2024 | 2024-07-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Road issue | 0.2125 | 0.2125 | 0.5 | 0 | 6.9 | 6.9 | turbine approach issue due to road not proper | Close | 0.26538 | O2_05 | 4609 |  | WTG Unscheduled Maintenance | 16031 | 4608.9125
1116 | 2024-07-11 | 2025 | 2024 | 2024-07-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.50069 | 0.50069 | 0.61806 | 0 | 2.8167 | 2.8167 | Attend and checked related error data log then found cooling sysytem temp. sensor malfunctioning. So, correct it then checked carried out for converter load shedding can. After complete work then reset all error data log and run the WTG. | Close | 0.10833 | O2_05 | 1881 |  | WTG Unscheduled Maintenance | 16031 | 1881.416
1117 | 2024-07-11 | 2025 | 2024 | 2024-07-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.50556 | 0.50556 | 0.63958 | 0 | 3.2167 | 3.2167 | WTG manually stop for punch point closure work. | Close | 0.12372 | O2_09 | 2051 |  | WTG Breakdown Maintenance | 15303 | 2051.0271
1118 | 2024-07-12 | 2025 | 2024 | 2024-07-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.30625 | 0.30625 | 0.39583 | 0 | 2.15 | 2.15 | Attend and checked cooling fan connection, CCU function by manual operation then reboot converter and start.(delay due to vehicle issue) | Close | 0.082692 | O2_14 | 2136 |  | WTG Unscheduled Maintenance | 23844 | 2136.025
1119 | 2024-07-12 | 2025 | 2024 | 2024-07-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.39583 | 0.39583 | 0.54167 | 0 | 3.5 | 3.5 | Attend and checked cooling fan connection, CCU function by manual operation then reboot converter and start.(delay due to vehicle issue) | Close | 0.13462 | O2_14 | 3477 |  | WTG Unscheduled Maintenance | 23844 | 3477.25
1120 | 2024-07-12 | 2025 | 2024 | 2024-07-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Break down | 0.73333 | 0.73333 | 0.95139 | 0 | 5.2333 | 5.2333 | Attend and found cooling system MPCB tripped because of transient voltage during E/F of feeder. So correct it and start(delay due to road and vehicle issue) | Close | 0.20128 | O2_14 | 5199 |  | WTG Unscheduled Maintenance | 23844 | 5199.3167
1121 | 2024-07-12 | 2025 | 2024 | 2024-07-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Break down | 0.95139 | 0.95139 | 0.96875 | 0 | 0.41667 | 0.41667 | Attend and found cooling system MPCB tripped because of transient voltage during E/F of feeder. So correct it and start(delay due to road and vehicle issue) | Close | 0.016026 | O2_14 | 414 |  | WTG Unscheduled Maintenance | 23844 | 413.9583
1125 | 2024-07-12 | 2025 | 2024 | 2024-07-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0.20486 | 0.20486 | 0.23889 | 0 | 0.81667 | 0.81667 | After grid resume then checked related error data log then reset & run the WTG. | Close | 0.03141 | O2_11 | 352 |  | WTG Unscheduled Maintenance | 10342 | 351.9153
1126 | 2024-07-12 | 2025 | 2024 | 2024-07-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.43264 | 0.43264 | 0.63333 | 0 | 4.8167 | 4.8167 | WTG manually stop for 1st month maintenance activity. | Close | 0.18526 | O2_11 | 2075 |  | WTG Scheduled Maintenance | 10342 | 2075.5819
1128 | 2024-07-12 | 2025 | 2024 | 2024-07-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0.20486 | 0.20486 | 0.23611 | 0 | 0.75 | 0.75 | After grid resume then checked related error data log then reset & run the WTG. | Close | 0.028846 | O2_15 | 860 |  | WTG Unscheduled Maintenance | 27532 | 860.375
1129 | 2024-07-12 | 2025 | 2024 | 2024-07-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.49306 | 0.49306 | 0.50417 | 0 | 0.26667 | 0.26667 | Manual stop for ladder inspection by project team | Close | 0.010256 | O2_15 | 306 |  | WTG Breakdown Maintenance | 27532 | 305.9111
1131 | 2024-07-12 | 2025 | 2024 | 2024-07-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Connectivity issue | 0.20486 | 0.20486 | 0.26042 | 0 | 1.3333 | 1.3333 | After feeder charge connectivity lost due to O2-15 and O2-05 VCB trip, so restore connectivity and start | Close | 0.051282 | O2_09 | 1638 |  | WTG Unscheduled Maintenance | 29486 | 1638.1111
1132 | 2024-07-12 | 2025 | 2024 | 2024-07-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.61389 | 0.61389 | 0.64931 | 0 | 0.85 | 0.85 | Checked related error data log then reset & run the WTG. | Close | 0.032692 | O2_09 | 1044 |  | WTG Unscheduled Maintenance | 29486 | 1044.2958
1133 | 2024-07-12 | 2025 | 2024 | 2024-07-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.65833 | 0.65833 | 0.66736 | 0 | 0.21667 | 0.21667 | Checked related error data log then reset & run the WTG. | Close | 0.0083333 | O2_09 | 266 |  | WTG Unscheduled Maintenance | 29486 | 266.1931
1134 | 2024-07-12 | 2025 | 2024 | 2024-07-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Road issue | 0.73333 | 0.73333 | 0.92569 | 0 | 4.6167 | 4.6167 | Attend and found cooling system MPCB tripped because of transient voltage during E/F of feeder. So correct it and start(delay due to road and vehicle issue) | Close | 0.17756 | O2_09 | 5672 |  | WTG Unscheduled Maintenance | 29486 | 5671.9597
1135 | 2024-07-12 | 2025 | 2024 | 2024-07-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0.20486 | 0.20486 | 0.2375 | 0 | 0.78333 | 0.78333 | After grid resume then found VCB trip. So charge it then reset and run the WTG. | Close | 0.030128 | O2_10 | 1030 |  | WTG Unscheduled Maintenance | 31545 | 1029.5937
1136 | 2024-07-12 | 2025 | 2024 | 2024-07-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.49653 | 0.49653 | 0.56806 | 0 | 1.7167 | 1.7167 | WTG manually stop for punch point closure work. | Close | 0.066026 | O2_10 | 2256 |  | WTG Breakdown Maintenance | 31545 | 2256.3437
1137 | 2024-07-12 | 2025 | 2024 | 2024-07-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 1600 | High gear speed | Break down | 0.63333 | 0.63333 | 0.64861 | 0 | 0.36667 | 0.36667 | Checked related error data log then reset & run the WTG. | Close | 0.014103 | O2_10 | 482 |  | WTG Unscheduled Maintenance | 31545 | 481.9375
1140 | 2024-07-12 | 2025 | 2024 | 2024-07-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 1600 | High gear speed | Break down | 0.60833 | 0.60833 | 0.62292 | 0 | 0.35 | 0.35 | Checked related error data log then reset & run the WTG. | Close | 0.013462 | O2_03 | 232 |  | WTG Unscheduled Maintenance | 15941 | 232.4729
1142 | 2024-07-12 | 2025 | 2024 | 2024-07-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0.20486 | 0.20486 | 0.39583 | 0 | 4.5833 | 4.5833 | After grid resume then found VCB trip. So charge it. Then Pitch error occurred so attend and reboot controller then start(delay due to vehicle non availability) | Close | 0.17628 | O2_02 | 6047 |  | WTG Unscheduled Maintenance | 31665 | 6047.1354
1143 | 2024-07-12 | 2025 | 2024 | 2024-07-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0.39583 | 0.39583 | 0.45139 | 0 | 1.3333 | 1.3333 | After grid resume then found VCB trip. So charge it. Then Pitch error occurred so attend and reboot controller then start(delay due to vehicle non availability) | Close | 0.051282 | O2_02 | 1759 |  | WTG Unscheduled Maintenance | 31665 | 1759.1667
1144 | 2024-07-12 | 2025 | 2024 | 2024-07-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.20486 | 0.20486 | 0.26319 | 0 | 1.4 | 1.4 | After grid resume then checked related error data log then reset & run the WTG. | Close | 0.053846 | O2_05 | 1489 |  | WTG Unscheduled Maintenance | 25533 | 1489.425
1145 | 2024-07-12 | 2025 | 2024 | 2024-07-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Connectivity issue | 0.20486 | 0.20486 | 0.28125 | 0 | 1.8333 | 1.8333 | After feeder charge connectivity lost due to VCB trip, so restore connectivity and start | Close | 0.070513 | O2_09 | 2252 |  | WTG Unscheduled Maintenance | 29486 | 2252.4028
1146 | 2024-07-13 | 2025 | 2024 | 2024-07-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.81667 | 0.81667 | 0.93264 | 0 | 2.7833 | 2.7833 | After grid resume then error occurred so, so attend and found connector of surgeprotection feedback in converter was loose so correct it and start. | Close | 0.10705 | O2_14 | 4202 |  | WTG Unscheduled Maintenance | 36236 | 4202.3694
1147 | 2024-07-13 | 2025 | 2024 | 2024-07-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.50972 | 0.50972 | 0.51389 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2_12 | 160 |  | WTG Unscheduled Maintenance | 38421 | 160.0875
1148 | 2024-07-13 | 2025 | 2024 | 2024-07-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.54375 | 0.54375 | 0.72361 | 0 | 4.3167 | 4.3167 | WTG manually stop for punch point closure work. | Close | 0.16603 | O2_15 | 6140 |  | WTG Breakdown Maintenance | 34136 | 6139.7389
1149 | 2024-07-13 | 2025 | 2024 | 2024-07-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0.78056 | 0.78056 | 0.86181 | 0 | 1.95 | 1.95 | After grid resume then checked related error data log, checked hydraulic unit and found solenoid valve nob is fully closed condition so, its nob fully open condition then reset & run the WTG. | Close | 0.075 | O2_15 | 2773 |  | WTG Unscheduled Maintenance | 34136 | 2773.55
1150 | 2024-07-13 | 2025 | 2024 | 2024-07-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0.78056 | 0.78056 | 0.81319 | 0 | 0.78333 | 0.78333 | After grid resume then checked related error data log then reset & run the WTG. | Close | 0.030128 | O2_10 | 735 |  | WTG Unscheduled Maintenance | 22535 | 735.5174
1152 | 2024-07-13 | 2025 | 2024 | 2024-07-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 973 | Check blade bend.mom. | Auto reset | 0.11667 | 0.11667 | 0.11875 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2_20 | 71 |  | WTG Unscheduled Maintenance | 34200 | 71.25
1153 | 2024-07-13 | 2025 | 2024 | 2024-07-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.30764 | 0.30764 | 0.39583 | 0 | 2.1167 | 2.1167 | Checked data and reset turbine | Close | 0.08141 | O2_20 | 3372 |  | WTG Unscheduled Maintenance | 34200 | 3016.25
1154 | 2024-07-13 | 2025 | 2024 | 2024-07-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.34722 | 0.34722 | 0.39583 | 0 | 1.1667 | 1.1667 | Checked data and reset turbine | Close | 0.044872 | O2_21 | 2187 |  | WTG Unscheduled Maintenance | 37054 | 1801.2361
1155 | 2024-07-14 | 2025 | 2024 | 2024-07-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.50278 | 0.50278 | 0.50486 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_12 | 57 |  | WTG Unscheduled Maintenance | 27214 | 56.6958
1156 | 2024-07-14 | 2025 | 2024 | 2024-07-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.48264 | 0.48264 | 0.49375 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_03 | 286 |  | WTG Unscheduled Maintenance | 25784 | 286.4889
1157 | 2024-07-14 | 2025 | 2024 | 2024-07-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.56806 | 0.56806 | 0.57708 | 0 | 0.21667 | 0.21667 | Checked related error data log then reset & run the WTG. | Close | 0.0083333 | O2_03 | 233 |  | WTG Unscheduled Maintenance | 25784 | 232.7722
1158 | 2024-07-14 | 2025 | 2024 | 2024-07-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.17292 | 0.17292 | 0.18472 | 0 | 0.28333 | 0.28333 | Checked related error data log then reset & run the WTG. | Close | 0.010897 | O2_06 | 398 |  | WTG Unscheduled Maintenance | 33681 | 397.6229
1159 | 2024-07-14 | 2025 | 2024 | 2024-07-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.41736 | 0.41736 | 0.41875 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_06 | 47 |  | WTG Unscheduled Maintenance | 33681 | 46.7792
1160 | 2024-07-14 | 2025 | 2024 | 2024-07-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.46319 | 0.46319 | 0.46389 | 0 | 0.016667 | 0.016667 | Checked related error data log then reset & run the WTG. | Close | 0.00064103 | O2_06 | 23 |  | WTG Unscheduled Maintenance | 33681 | 23.3896
1161 | 2024-07-15 | 2025 | 2024 | 2024-07-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.91944 | 0.91944 | 0.92083 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2_13 | 16 |  | WTG Unscheduled Maintenance | 11160 | 15.5
1162 | 2024-07-15 | 2025 | 2024 | 2024-07-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Auto reset | 0.59514 | 0.59514 | 0.59861 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0032051 | O2_12 | 42 |  | WTG Unscheduled Maintenance | 12182 | 42.2986
1163 | 2024-07-15 | 2025 | 2024 | 2024-07-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Auto reset | 0.76806 | 0.76806 | 0.77014 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2_12 | 25 |  | WTG Unscheduled Maintenance | 12182 | 25.3792
1164 | 2024-07-15 | 2025 | 2024 | 2024-07-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.39167 | 0.39167 | 0.67708 | 0 | 6.85 | 6.85 | WTG manually stop for 1st month maintenance activity. | Close | 0.26346 | O2_11 | 3356 |  | WTG Scheduled Maintenance | 11760 | 3356.5
1165 | 2024-07-15 | 2025 | 2024 | 2024-07-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3560 | Voltage asymmetry | Break down | 0.50278 | 0.50278 | 0.525 | 0 | 0.53333 | 0.53333 | Attend and checked related error data log and ckt. Then manually reboot UPS system. Then reset all error data log and run the WTG. | Close | 0.020513 | O2_15 | 288 |  | WTG Unscheduled Maintenance | 12957 | 287.9333
1166 | 2024-07-15 | 2025 | 2024 | 2024-07-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.60694 | 0.60694 | 0.69028 | 0 | 2 | 2 | Attend and checked related error data log, also checked related ckt, all connection and its tightness. Found everything ok. So, reset and run the WTG. | Close | 0.076923 | O2_15 | 1080 |  | WTG Unscheduled Maintenance | 12957 | 1079.75
1167 | 2024-07-15 | 2025 | 2024 | 2024-07-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.77153 | 0.77153 | 0.78542 | 0 | 0.33333 | 0.33333 | Checked related error data log then reset & run the WTG. | Close | 0.012821 | O2_09 | 162 |  | WTG Unscheduled Maintenance | 11655 | 161.875
1168 | 2024-07-15 | 2025 | 2024 | 2024-07-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.29722 | 0.29722 | 0.31319 | 0 | 0.38333 | 0.38333 | Checked related error data log then reset & run the WTG. | Close | 0.014744 | O2_03 | 167 |  | WTG Unscheduled Maintenance | 10458 | 167.0375
1169 | 2024-07-15 | 2025 | 2024 | 2024-07-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.77639 | 0.77639 | 0.78889 | 0 | 0.3 | 0.3 | Checked related error data log then reset & run the WTG. | Close | 0.011538 | O2_05 | 173 |  | WTG Unscheduled Maintenance | 13804 | 172.55
1170 | 2024-07-15 | 2025 | 2024 | 2024-07-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.79306 | 0.79306 | 0.79583 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & run the WTG. | Close | 0.0025641 | O2_09 | 32 |  | WTG Unscheduled Maintenance | 11655 | 32.375
1171 | 2024-07-15 | 2025 | 2024 | 2024-07-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Auto reset | 0.68542 | 0.68542 | 0.6875 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2_06 | 32 |  | WTG Unscheduled Maintenance | 15224 | 31.7167
1172 | 2024-07-15 | 2025 | 2024 | 2024-07-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.78889 | 0.78889 | 0.79167 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & run the WTG. | Close | 0.0025641 | O2_06 | 42 |  | WTG Unscheduled Maintenance | 15224 | 42.2889
1173 | 2024-07-15 | 2025 | 2024 | 2024-07-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3063 | Conv. emerg.off type D | Break down | 0.46319 | 0.46319 | 0.46667 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_21 | 35 |  | WTG Unscheduled Maintenance | 10074 | 34.9792
1174 | 2024-07-15 | 2025 | 2024 | 2024-07-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 2520 | Gen.speed analog<>gear.speed | Break down | 0.80903 | 0.80903 | 0.82153 | 0 | 0.3 | 0.3 | Checked related error data log then reset & run the WTG. | Close | 0.011538 | O2_21 | 126 |  | WTG Unscheduled Maintenance | 10074 | 125.925
1175 | 2024-07-15 | 2025 | 2024 | 2024-07-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3063 | Conv. emerg.off type D | Auto reset | 0.30486 | 0.30486 | 0.30625 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2_06 | 21 |  | WTG Unscheduled Maintenance | 15224 | 21.1444
1176 | 2024-07-15 | 2025 | 2024 | 2024-07-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.49306 | 0.49306 | 0.50556 | 0 | 0.3 | 0.3 | Checked related error data log then reset & run the WTG. | Close | 0.011538 | O2_06 | 190 |  | WTG Unscheduled Maintenance | 15224 | 190.3
1177 | 2024-07-15 | 2025 | 2024 | 2024-07-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.78403 | 0.78403 | 0.79236 | 0 | 0.2 | 0.2 | Checked related error data log then reset & run the WTG. | Close | 0.0076923 | O2_06 | 127 |  | WTG Unscheduled Maintenance | 15224 | 126.8667
1178 | 2024-07-16 | 2025 | 2024 | 2024-07-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.99653 | 0.99653 | 0.99792 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_12 | 15 |  | WTG Unscheduled Maintenance | 10738 | 14.9139
1179 | 2024-07-16 | 2025 | 2024 | 2024-07-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.36736 | 0.36736 | 0.58333 | 0 | 5.1833 | 5.1833 | WTG manually stop for 1st month maintenance activity. | Close | 0.19936 | O2_11 | 2387 |  | WTG Scheduled Maintenance | 11053 | 2387.141
1180 | 2024-07-16 | 2025 | 2024 | 2024-07-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.55903 | 0.55903 | 0.73611 | 0 | 4.25 | 4.25 | WTG manually stop for power curve deviation. Found ultrasonic alignment deviation. So, correct it. Also checked voltage measurement ckt in the converter panel to the BOB panel as well as check auxilary transformer connection. After done work then reset and run the WTG. | Close | 0.16346 | O2_15 | 1980 |  | WTG Breakdown Maintenance | 11179 | 1979.6146
1181 | 2024-07-16 | 2025 | 2024 | 2024-07-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 500 | Grid loss | Break down | 0.43056 | 0.43056 | 0.47917 | 0 | 1.1667 | 1.1667 | After grid resume then checked related error data log then reset & run the WTG. | Close | 0.044872 | O2_10 | 471 |  | WTG Unscheduled Maintenance | 9692 | 471.1389
1182 | 2024-07-16 | 2025 | 2024 | 2024-07-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.74097 | 0.74097 | 0.75208 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_03 | 105 |  | WTG Unscheduled Maintenance | 9464 | 105.1556
1183 | 2024-07-16 | 2025 | 2024 | 2024-07-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Road issue | 0.99167 | 0.99167 | 1899-12-31 | 0 | 0.2 | 0.2 | Due to WTG road not accessible. Furthur restoration tommorow. | Open | 0.0076923 | O2_03 | 79 |  | WTG Unscheduled Maintenance | 9464 | 78.8667
1184 | 2024-07-16 | 2025 | 2024 | 2024-07-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.68264 | 0.68264 | 0.68611 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_09 | 31 |  | WTG Unscheduled Maintenance | 9025 | 31.3368
1185 | 2024-07-16 | 2025 | 2024 | 2024-07-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.015278 | 0.015278 | 0.016667 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2_06 | 19 |  | WTG Unscheduled Maintenance | 13803 | 19.1708
1186 | 2024-07-16 | 2025 | 2024 | 2024-07-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Auto reset | 0.24167 | 0.24167 | 0.24306 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2_06 | 19 |  | WTG Unscheduled Maintenance | 13803 | 19.1708
1187 | 2024-07-16 | 2025 | 2024 | 2024-07-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Auto reset | 0.57986 | 0.57986 | 0.58125 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2_21 | 19 |  | WTG Unscheduled Maintenance | 13359 | 18.5542
1188 | 2024-07-16 | 2025 | 2024 | 2024-07-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 4093 | Rel. air hum. tower base inside too high (in operation) | Break down | 0.12986 | 0.12986 | 0.13472 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & run the WTG. | Close | 0.0044872 | O2_06 | 67 |  | WTG Unscheduled Maintenance | 13803 | 67.0979
1189 | 2024-07-16 | 2025 | 2024 | 2024-07-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 4093 | Rel. air hum. tower base inside too high (in operation) | Break down | 0.26181 | 0.26181 | 0.275 | 0 | 0.31667 | 0.31667 | Checked related error data log then reset & run the WTG. | Close | 0.012179 | O2_06 | 182 |  | WTG Unscheduled Maintenance | 13803 | 182.1229
1190 | 2024-07-16 | 2025 | 2024 | 2024-07-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 500 | Grid loss | Road issue | 0.76042 | 0.76042 | 1899-12-31 | 0 | 5.75 | 5.75 | After grid resume then turbine disconnected. Due to heavy rain so WTG road not accessible. | Open | 0.22115 | O2_05 | 3174 |  | WTG Unscheduled Maintenance | 13250 | 3174.4792
1191 | 2024-07-17 | 2025 | 2024 | 2024-07-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Auto reset | 0.32778 | 0.32778 | 0.33125 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0032051 | O2_12 | 42 |  | WTG Unscheduled Maintenance | 11979 | 41.5937
1192 | 2024-07-17 | 2025 | 2024 | 2024-07-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.70556 | 0.70556 | 0.88125 | 0 | 4.2167 | 4.2167 | WTG manually stop forpower curve deviation isues. Replaced GMP232 module. Also checked all 3 blade calibration, BLS cable laying and ultrasonic cable. After done work then reset and run the turbine. | Close | 0.16218 | O2_15 | 2067 |  | WTG Breakdown Maintenance | 11767 | 2067.3965
1193 | 2024-07-17 | 2025 | 2024 | 2024-07-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.44375 | 0.44375 | 0.70833 | 0 | 6.35 | 6.35 | WTG manually stop for 1st month maintenance activity. | Close | 0.24423 | O2_09 | 1614 |  | WTG Scheduled Maintenance | 6099 | 1613.6938
1194 | 2024-07-17 | 2025 | 2024 | 2024-07-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Major BD | 0.70903 | 0.70903 | 1899-12-31 | 0 | 6.9833 | 6.9833 | After done 1st month maintenance activity then error triggered. So, checked error related ckt and then found axis 2 flate 1.7 ohm resister fail. Then material arranging and WTG restoration WIP. | Open | 0.26859 | O2_09 | 1775 |  | WTG Unscheduled Maintenance | 6099 | 1774.6396
1195 | 2024-07-17 | 2025 | 2024 | 2024-07-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Road issue | 0 | 0 | 0.54167 | 0 | 13 | 13 | WTG restoration delay due to location road does not accessible. | Close | 0.5 | O2_03 | 1136 |  | WTG Unscheduled Maintenance | 2098 | 1136.4167
1196 | 2024-07-17 | 2025 | 2024 | 2024-07-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Road issue | 0.54167 | 0.54167 | 0.65694 | 0 | 2.7667 | 2.7667 | Attend and checked related error data log, then found flate resistor fail. So, replaced with new one. After done work then reset and run the turbine. (Delay due to location road does not accessible. | Close | 0.10641 | O2_03 | 242 |  | WTG Unscheduled Maintenance | 2098 | 241.8528
1197 | 2024-07-17 | 2025 | 2024 | 2024-07-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 500 | Grid loss | Road issue | 0 | 0 | 0.58056 | 0 | 13.9333 | 13.9333 | Attend and checked then found VCB tripped. So, charge VCB by BOP person then reset and run the WTG. (Delay due to location road does not accessible.) | Close | 0.5359 | O2_05 | 6353 |  | WTG Unscheduled Maintenance | 10943 | 6353.0194
1198 | 2024-07-17 | 2025 | 2024 | 2024-07-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Auto reset | 0.05625 | 0.05625 | 0.057639 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2_06 | 19 |  | WTG Unscheduled Maintenance | 13778 | 19.1361
1199 | 2024-07-18 | 2025 | 2024 | 2024-07-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Auto reset | 0.26597 | 0.26597 | 0.26806 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2_13 | 20 |  | WTG Unscheduled Maintenance | 9407 | 19.5979
1200 | 2024-07-18 | 2025 | 2024 | 2024-07-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Auto reset | 0.85972 | 0.85972 | 0.86111 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2_13 | 13 |  | WTG Unscheduled Maintenance | 9407 | 13.0653
1201 | 2024-07-18 | 2025 | 2024 | 2024-07-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.3125 | 0.3125 | 0.31528 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset and run the turbine. | Close | 0.0025641 | O2_12 | 31 |  | WTG Unscheduled Maintenance | 11127 | 30.9083
1202 | 2024-07-18 | 2025 | 2024 | 2024-07-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.96528 | 0.96528 | 0.96875 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset and run the turbine. | Close | 0.0032051 | O2_12 | 39 |  | WTG Unscheduled Maintenance | 11127 | 38.6354
1203 | 2024-07-18 | 2025 | 2024 | 2024-07-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.97222 | 0.97222 | 0.99306 | 0 | 0.5 | 0.5 | Checked related error data log then reset and run the turbine. | Close | 0.019231 | O2_12 | 232 |  | WTG Unscheduled Maintenance | 11127 | 231.8125
1204 | 2024-07-18 | 2025 | 2024 | 2024-07-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0 | 0 | 0.079861 | 0 | 1.9167 | 1.9167 | Attend and checked related ckt then found flate DBR resistor faulty. So, replaced with new one then reset and run the turbine. | Close | 0.073718 | O2_09 | 765 |  | WTG Unscheduled Maintenance | 9579 | 764.9896
1205 | 2024-07-18 | 2025 | 2024 | 2024-07-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.47986 | 0.47986 | 0.69236 | 0 | 5.1 | 5.1 | WTG manually stop for 1st month maintenance activity. | Close | 0.19615 | O2_09 | 2036 |  | WTG Scheduled Maintenance | 9579 | 2035.5375
1206 | 2024-07-18 | 2025 | 2024 | 2024-07-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Auto reset | 0.20347 | 0.20347 | 0.20486 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2_05 | 13 |  | WTG Unscheduled Maintenance | 9302 | 12.9194
1207 | 2024-07-18 | 2025 | 2024 | 2024-07-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.68264 | 0.68264 | 0.68333 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | O2_05 | 6 |  | WTG Unscheduled Maintenance | 9302 | 6.4597
1208 | 2024-07-18 | 2025 | 2024 | 2024-07-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.70139 | 0.70139 | 0.70556 | 0 | 0.1 | 0.1 | Checked related error data log then reset and run the turbine. | Close | 0.0038462 | O2_05 | 39 |  | WTG Unscheduled Maintenance | 9302 | 38.7583
1209 | 2024-07-18 | 2025 | 2024 | 2024-07-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.05625 | 0.05625 | 0.057639 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2_06 | 19 |  | WTG Unscheduled Maintenance | 13937 | 19.3569
1210 | 2024-07-18 | 2025 | 2024 | 2024-07-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Auto reset | 0.36944 | 0.36944 | 0.37083 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2_06 | 19 |  | WTG Unscheduled Maintenance | 13937 | 19.3569
1211 | 2024-07-18 | 2025 | 2024 | 2024-07-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.0125 | 0.0125 | 0.013194 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | O2_21 | 9 |  | WTG Unscheduled Maintenance | 13058 | 9.0681
1212 | 2024-07-18 | 2025 | 2024 | 2024-07-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Auto reset | 0.047917 | 0.047917 | 0.049306 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2_21 | 18 |  | WTG Unscheduled Maintenance | 13058 | 18.1361
1213 | 2024-07-18 | 2025 | 2024 | 2024-07-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Auto reset | 0.17292 | 0.17292 | 0.17431 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2_21 | 18 |  | WTG Unscheduled Maintenance | 13058 | 18.1361
1214 | 2024-07-18 | 2025 | 2024 | 2024-07-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.78194 | 0.78194 | 0.825 | 0 | 1.0333 | 1.0333 | Checked related error data log then reset and run the turbine. | Close | 0.039744 | O2_21 | 562 |  | WTG Unscheduled Maintenance | 13058 | 562.2194
1215 | 2024-07-19 | 2025 | 2024 | 2024-07-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.057639 | 0.057639 | 0.065972 | 0 | 0.2 | 0.2 | Checked related error data log then reset and run the turbine. | Close | 0.0076923 | O2_12 | 120 |  | WTG Unscheduled Maintenance | 14447 | 120.3917
1216 | 2024-07-19 | 2025 | 2024 | 2024-07-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.14306 | 0.14306 | 0.15278 | 0 | 0.23333 | 0.23333 | Checked related error data log then reset and run the turbine. | Close | 0.0089744 | O2_12 | 140 |  | WTG Unscheduled Maintenance | 14447 | 140.4569
1217 | 2024-07-19 | 2025 | 2024 | 2024-07-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.47153 | 0.47153 | 0.57569 | 0 | 2.5 | 2.5 | WTG manually stop for 1st month maintenance activity. | Close | 0.096154 | O2_09 | 1319 |  | WTG Scheduled Maintenance | 12661 | 1318.8542
1218 | 2024-07-19 | 2025 | 2024 | 2024-07-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0.41875 | 0.41875 | 0.54167 | 0 | 2.95 | 2.95 | After grid resume then attend and checked related error data log then reboot UPS after then reset & run the WTG. (Delay due to vehicle not available) | Close | 0.11346 | O2_10 | 1710 |  | WTG Unscheduled Maintenance | 13910 | 1709.7708
1219 | 2024-07-19 | 2025 | 2024 | 2024-07-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0.64722 | 0.64722 | 0.74375 | 0 | 2.3167 | 2.3167 | After grid resume then checked related error data log then reset & run the WTG. | Close | 0.089103 | O2_02 | 1063 |  | WTG Unscheduled Maintenance | 11011 | 1062.8674
1220 | 2024-07-19 | 2025 | 2024 | 2024-07-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0.64722 | 0.64722 | 0.74514 | 0 | 2.35 | 2.35 | After grid resume then checked related error data log then reset & run the WTG. | Close | 0.090385 | O2_05 | 987 |  | WTG Unscheduled Maintenance | 10077 | 986.7062
1221 | 2024-07-20 | 2025 | 2024 | 2024-07-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0.10347 | 0.10347 | 0.13542 | 0 | 0.76667 | 0.76667 | After grid resume then found VCB trip. So charge it then reset and run the WTG. | Close | 0.029487 | O2_11 | 344 |  | WTG Unscheduled Maintenance | 10768 | 343.9778
1222 | 2024-07-20 | 2025 | 2024 | 2024-07-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Connectivity issue | 0.10347 | 0.10347 | 0.12986 | 0 | 0.63333 | 0.63333 | After feeder charge connectivity lost due to O2-14 VCB trip, so restore connectivity and start | Close | 0.024359 | O2_15 | 308 |  | WTG Unscheduled Maintenance | 11686 | 308.3806
1223 | 2024-07-20 | 2025 | 2024 | 2024-07-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Connectivity issue | 0.10347 | 0.10347 | 0.12778 | 0 | 0.58333 | 0.58333 | After feeder charge connectivity lost due to O2-14 VCB trip, so restore connectivity and start | Close | 0.022436 | O2_09 | 256 |  | WTG Unscheduled Maintenance | 10549 | 256.3993
1224 | 2024-07-20 | 2025 | 2024 | 2024-07-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Connectivity issue | 0.10347 | 0.10347 | 0.13542 | 0 | 0.76667 | 0.76667 | After feeder charge connectivity lost due to O2-14 VCB trip, so restore connectivity and start | Close | 0.029487 | O2_10 | 358 |  | WTG Unscheduled Maintenance | 11208 | 358.0333
1225 | 2024-07-20 | 2025 | 2024 | 2024-07-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Road issue | 0.63056 | 0.63056 | 1899-12-31 | 0 | 8.8667 | 8.8667 | Due to WTG road not accessible. Once road clear will attend the same | Open | 0.34103 | O2_05 | 3436 |  | WTG Unscheduled Maintenance | 9301 | 3436.2028
1226 | 2024-07-20 | 2025 | 2024 | 2024-07-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Auto reset | 0.43681 | 0.43681 | 0.43889 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2_21 | 19 |  | WTG Unscheduled Maintenance | 9046 | 18.8458
1227 | 2024-07-20 | 2025 | 2024 | 2024-07-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | ROW issue | 0 | 0 | 0.061806 | 0 | 1.4833 | 1.4833 | Found VCB trip by unknown person. So charge it by BOP person then reset and run the WTG. | Close | 0.057051 | O2_06 | 692 |  | WTG Unscheduled Maintenance | 11200 | 692.2222
1228 | 2024-07-20 | 2025 | 2024 | 2024-07-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 4093 | Rel. air hum. tower base inside too high (in operation) | Auto reset | 0.37778 | 0.37778 | 0.38056 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0025641 | O2_06 | 31 |  | WTG Unscheduled Maintenance | 11200 | 31.1111
1229 | 2024-07-21 | 2025 | 2024 | 2024-07-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Auto reset | 0.20417 | 0.20417 | 0.20556 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2_13 | 27 |  | WTG Unscheduled Maintenance | 19578 | 27.1917
1230 | 2024-07-21 | 2025 | 2024 | 2024-07-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Auto reset | 0.50208 | 0.50208 | 0.50556 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0032051 | O2_12 | 72 |  | WTG Unscheduled Maintenance | 20644 | 71.6806
1231 | 2024-07-21 | 2025 | 2024 | 2024-07-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Auto reset | 0.56597 | 0.56597 | 0.56875 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0025641 | O2_12 | 57 |  | WTG Unscheduled Maintenance | 20644 | 57.3444
1232 | 2024-07-21 | 2025 | 2024 | 2024-07-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.57153 | 0.57153 | 0.57708 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & run the WTG. | Close | 0.0051282 | O2_12 | 115 |  | WTG Unscheduled Maintenance | 20644 | 114.6889
1233 | 2024-07-21 | 2025 | 2024 | 2024-07-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Connectivity issue | 0.71875 | 0.71875 | 0.78333 | 0 | 1.55 | 1.55 | During Checked related error data log then turbine connectivity failure and turbine was disconnected. So, attend and checked turbine connectivity and found one pair disconnected so, using spare pair and restore connectivity after then reset & run the WTG. | Close | 0.059615 | O2_16 | 1287 |  | WTG Unscheduled Maintenance | 19930 | 1287.1458
1234 | 2024-07-21 | 2025 | 2024 | 2024-07-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Auto reset | 0.60764 | 0.60764 | 0.61111 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0032051 | O2_03 | 69 |  | WTG Unscheduled Maintenance | 19797 | 68.7396
1235 | 2024-07-21 | 2025 | 2024 | 2024-07-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.95556 | 0.95556 | 0.98125 | 0 | 0.61667 | 0.61667 | Checked related error data log then reset & run the WTG. | Close | 0.023718 | O2_21 | 542 |  | WTG Unscheduled Maintenance | 21099 | 542.1271
1236 | 2024-07-21 | 2025 | 2024 | 2024-07-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Auto reset | 0 | 0 | 0.0020833 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2_06 | 41 |  | WTG Unscheduled Maintenance | 19860 | 41.375
1237 | 2024-07-21 | 2025 | 2024 | 2024-07-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.077778 | 0.077778 | 0.088889 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_06 | 221 |  | WTG Unscheduled Maintenance | 19860 | 220.6667
1238 | 2024-07-21 | 2025 | 2024 | 2024-07-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.575 | 0.575 | 0.60139 | 0 | 0.63333 | 0.63333 | Checked related error data log then reset & run the WTG. | Close | 0.024359 | O2_06 | 524 |  | WTG Unscheduled Maintenance | 19860 | 524.0833
1239 | 2024-07-21 | 2025 | 2024 | 2024-07-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Road issue | 0 | 0 | 1899-12-31 | 0 | 24 | 24 | Due to WTG road not accessible. Once road clear will attend the same | Open | 0.92308 | O2_05 | 21922 |  | WTG Unscheduled Maintenance | 21922 | 21922
1240 | 2024-07-22 | 2025 | 2024 | 2024-07-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Road issue | 0 | 0 | 0.99999 | 0 | 23.9997 | 23.9997 | Due to WTG road not accessible. Once road clear will attend the same | Open | 0.92307 | O2_05 | 29706.6562 |  | WTG Unscheduled Maintenance | 29707 | 29706.6562
1241 | 2024-07-22 | 2025 | 2024 | 2024-07-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.97639 | 0.97639 | 0.98056 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2_20 | 135.9292 |  | WTG Unscheduled Maintenance | 32623 | 135.9292
1242 | 2024-07-22 | 2025 | 2024 | 2024-07-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.70139 | 0.70139 | 0.72569 | 0 | 0.58333 | 0.58333 | Wtg manual stop for project pending work at USS yard. | Close | 0.022436 | O2_03 | 760.4479 |  | WTG Breakdown Maintenance | 31287 | 760.4479
1243 | 2024-07-22 | 2025 | 2024 | 2024-07-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 4093 | Rel. air hum. tower base inside too high (in operation) | Break down | 0.35417 | 0.35417 | 0.40139 | 0 | 1.1333 | 1.1333 | Atend and checkrower fan and found malfunctioning so replacement work tommoroow | Close | 0.04359 | O2_21 | 1597.0083 |  | WTG Unscheduled Maintenance | 33819 | 1597.0083
1244 | 2024-07-22 | 2025 | 2024 | 2024-07-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 4093 | Rel. air hum. tower base inside too high (in operation) | Break down | 0.52917 | 0.52917 | 0.54306 | 0 | 0.33333 | 0.33333 | Checked related error data log then reset & run the WTG. | Close | 0.012821 | O2_21 | 469.7083 |  | WTG Unscheduled Maintenance | 33819 | 469.7083
1245 | 2024-07-22 | 2025 | 2024 | 2024-07-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.47917 | 0.47917 | 0.71042 | 0 | 5.55 | 5.55 | wtg manual stop for OMS audit work. | Close | 0.21346 | O2_05 | 6869.7438 |  | WTG Breakdown Maintenance | 29707 | 6869.7438
1246 | 2024-07-22 | 2025 | 2024 | 2024-07-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Auto reset | 0.70417 | 0.70417 | 0.70694 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0025641 | O2_18 | 82.6278 |  | WTG Unscheduled Maintenance | 29746 | 82.6278
1247 | 2024-07-23 | 2025 | 2024 | 2024-07-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Road issue | 0 | 0 | 0.99999 | 0 | 23.9997 | 23.9997 | Due to WTG road not accessible. Once road clear will attend the same | Open | 0.92307 | O2_05 | 53000.3866 |  | WTG Unscheduled Maintenance | 53001 | 53000.3866
1248 | 2024-07-23 | 2025 | 2024 | 2024-07-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Break down | 0.18264 | 0.18264 | 0.19583 | 0 | 0.31667 | 0.31667 | Checked related error data log then reset & run the WTG. | Close | 0.012179 | O2_12 | 698.4083 |  | WTG Unscheduled Maintenance | 52932 | 698.4083
1249 | 2024-07-23 | 2025 | 2024 | 2024-07-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.19931 | 0.19931 | 0.20903 | 0 | 0.23333 | 0.23333 | Checked related error data log then reset & run the WTG. | Close | 0.0089744 | O2_12 | 514.6167 |  | WTG Unscheduled Maintenance | 52932 | 514.6167
1250 | 2024-07-23 | 2025 | 2024 | 2024-07-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 2355 | Temp. rot.br.pad high | Break down | 0.49306 | 0.49306 | 0.54861 | 0 | 1.3333 | 1.3333 | attend and check scada data than found break pad 2 tep malfunctioning so interchange break pad 1 & 2 sensor than reset and start WTg.(now turbine under observation( | Close | 0.051282 | O2_12 | 2940.6667 |  | WTG Unscheduled Maintenance | 52932 | 2940.6667
1251 | 2024-07-23 | 2025 | 2024 | 2024-07-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.62361 | 0.62361 | 0.62778 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2_12 | 220.55 |  | WTG Unscheduled Maintenance | 52932 | 220.55
1252 | 2024-07-23 | 2025 | 2024 | 2024-07-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.53264 | 0.53264 | 0.53889 | 0 | 0.15 | 0.15 | Checked related error data log then reset & run the WTG. | Close | 0.0057692 | O2_09 | 328.5062 |  | WTG Unscheduled Maintenance | 52561 | 328.5062
1253 | 2024-07-23 | 2025 | 2024 | 2024-07-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.63403 | 0.63403 | 0.63681 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & run the WTG. | Close | 0.0025641 | O2_15 | 134.1444 |  | WTG Unscheduled Maintenance | 48292 | 134.1444
1254 | 2024-07-23 | 2025 | 2024 | 2024-07-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Auto reset | 0.74722 | 0.74722 | 0.74861 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2_15 | 67.0722 |  | WTG Unscheduled Maintenance | 48292 | 67.0722
1255 | 2024-07-23 | 2025 | 2024 | 2024-07-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.64722 | 0.64722 | 0.66389 | 0 | 0.4 | 0.4 | Checked related error data log then reset & run the WTG. | Open | 0.015385 | O2_25 | 947.5167 |  | WTG Unscheduled Maintenance | 56851 | 947.5167
1256 | 2024-07-23 | 2025 | 2024 | 2024-07-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.52639 | 0.52639 | 0.52986 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Open | 0.0032051 | O2_25 | 197.3993 |  | WTG Unscheduled Maintenance | 56851 | 197.3993
1257 | 2024-07-23 | 2025 | 2024 | 2024-07-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.85903 | 0.85903 | 0.86319 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2_06 | 192.2333 |  | WTG Unscheduled Maintenance | 46136 | 192.2333
1258 | 2024-07-23 | 2025 | 2024 | 2024-07-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.64722 | 0.64722 | 0.67917 | 0 | 0.76667 | 0.76667 | Checked related error data log then reset & run the WTG. | Close | 0.029487 | O2_21 | 1602.2056 |  | WTG Unscheduled Maintenance | 50156 | 1602.2056
1259 | 2024-07-23 | 2025 | 2024 | 2024-07-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.55556 | 0.55556 | 0.61181 | 0 | 1.35 | 1.35 | Attend for tiwer base humidity high error so check connection and correct it and start turbine (now turbine under observation) | Close | 0.051923 | O2_21 | 2821.275 |  | WTG Breakdown Maintenance | 50156 | 2821.275
1247 | 2024-07-24 | 2025 | 2024 | 2024-07-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Road issue | 0 | 0 | 0.99999 | 0 | 23.9997 | 23.9997 | Due to WTG road not accessible. Once road clear will attend the same | Open | 0.92307 | O2_05 | 60711.2973 |  | WTG Unscheduled Maintenance | 60712 | 60711.2973
1248 | 2024-07-24 | 2025 | 2024 | 2024-07-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.98264 | 0.98264 | 0.98611 | 0 | 0.31667 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_11 | 211.2917 |  | WTG Unscheduled Maintenance | 60852 | 211.2917
1249 | 2024-07-24 | 2025 | 2024 | 2024-07-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.45139 | 0.45139 | 0.46597 | 0 | 0.23333 | 0.35 | Checked related error data log then reset & run the WTG. | Close | 0.013462 | O2_11 | 887.425 |  | WTG Unscheduled Maintenance | 60852 | 887.425
1250 | 2024-07-24 | 2025 | 2024 | 2024-07-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Break down | 0.18056 | 0.18056 | 0.19514 | 0 | 1.3333 | 0.35 | Checked related error data log then reset & run the WTG. | Close | 0.013462 | O2_09 | 869.0354 |  | WTG Unscheduled Maintenance | 59591 | 869.0354
1251 | 2024-07-24 | 2025 | 2024 | 2024-07-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Auto reset | 0.55069 | 0.55069 | 0.55347 | 0 | 0.1 | 0.066667 | Auto reset | Close | 0.0025641 | O2_09 | 165.5306 |  | WTG Unscheduled Maintenance | 59591 | 165.5306
1252 | 2024-07-24 | 2025 | 2024 | 2024-07-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Auto reset | 0.011806 | 0.011806 | 0.013889 | 0 | 0.15 | 0.05 | Auto reset | Close | 0.0019231 | O2_25 | 111.2167 |  | WTG Unscheduled Maintenance | 53384 | 111.2167
1253 | 2024-07-24 | 2025 | 2024 | 2024-07-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Auto reset | 0.038194 | 0.038194 | 0.040278 | 0 | 0.066667 | 0.05 | Auto reset | Close | 0.0019231 | O2_25 | 111.2167 |  | WTG Unscheduled Maintenance | 53384 | 111.2167
1254 | 2024-07-24 | 2025 | 2024 | 2024-07-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Schedule WTG PM | 0.32778 | 0.32778 | 0.34514 | 0 | 0.033333 | 0.41667 | Checked related error data log then reset & run the WTG. | Close | 0.016026 | O2_25 | 926.8056 |  | WTG Unscheduled Maintenance | 53384 | 926.8056
1255 | 2024-07-24 | 2025 | 2024 | 2024-07-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.50347 | 0.50347 | 0.51042 | 0 | 0.4 | 0.16667 | Wtg stop For project pending work. | Open | 0.0064103 | O2_21 | 414.1806 |  | WTG Breakdown Maintenance | 59642 | 414.1806
1256 | 2024-07-24 | 2025 | 2024 | 2024-07-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.041667 | 0.041667 | 0.17014 | 0 | 0.083333 | 3.0833 | Attend WTG and check related circuit and chck hydrulic Valve and flushing properly than clean and reset and start Turbine | Open | 0.11859 | O2_06 | 7671.3333 |  | WTG Unscheduled Maintenance | 59712 | 7671.3333
1257 | 2024-07-25 | 2025 | 2024 | 2024-07-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Road issue | 0 | 0 | 0.96528 | 0 | 0.083333 | 23.1667 | After road access than attend and check related circuit than replace flate resistor in axis-03 and also hydrulic pressure low error occurred so clean valve and also tower base colling system tep sensor replace and collent top up work done and start Wtg. | Close | 0.89103 | 02_05 | 55961.9792 |  | WTG Unscheduled Maintenance | 57975 | 55961.9792 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
1258 | 2024-07-25 | 2025 | 2024 | 2024-07-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.14722 | 0.14722 | 0.15278 | 0 | 0.083333 | 0.13333 | Checked related error data log then reset & run the WTG. | Close | 0.0051282 | O2_11 | 326.4 |  | WTG Unscheduled Maintenance | 58752 | 326.4
1259 | 2024-07-25 | 2025 | 2024 | 2024-07-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.095833 | 0.095833 | 0.11944 | 0 | 0.083333 | 0.56667 | Checked related error data log then reset & run the WTG. | Close | 0.021795 | O2_11 | 1387.2 |  | WTG Unscheduled Maintenance | 58752 | 1387.2
1260 | 2024-07-25 | 2025 | 2024 | 2024-07-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.13194 | 0.13194 | 0.16111 | 0 | 0.7 | 0.7 | Checked related error data log then reset & run the WTG. | Close | 0.026923 | O2_11 | 1713.6 |  | WTG Unscheduled Maintenance | 58752 | 1713.6
1261 | 2024-07-25 | 2025 | 2024 | 2024-07-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.18403 | 0.18403 | 0.18819 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2_11 | 244.8 |  | WTG Unscheduled Maintenance | 58752 | 244.8
1262 | 2024-07-25 | 2025 | 2024 | 2024-07-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 4540 | Tower oscillation X level 2 | Break down | 0.46597 | 0.46597 | 0.49514 | 0 | 0.7 | 0.7 | Checked related error data log then reset & run the WTG. | Close | 0.026923 | O2_11 | 1713.6 |  | WTG Unscheduled Maintenance | 58752 | 1713.6
1263 | 2024-07-25 | 2025 | 2024 | 2024-07-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.50069 | 0.50069 | 0.50417 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_11 | 204 |  | WTG Unscheduled Maintenance | 58752 | 204
1264 | 2024-07-25 | 2025 | 2024 | 2024-07-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.15278 | 0.15278 | 0.1625 | 0 | 0.23333 | 0.23333 | Checked related error data log then reset & run the WTG. | Close | 0.0089744 | O2_11 | 571.2 |  | WTG Unscheduled Maintenance | 58752 | 571.2
1265 | 2024-07-25 | 2025 | 2024 | 2024-07-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.1 | 0.1 | 0.10486 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & run the WTG. | Close | 0.0044872 | 02_03 | 278.2743 |  | WTG Unscheduled Maintenance | 57245 | 278.2743
1266 | 2024-07-25 | 2025 | 2024 | 2024-07-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.097917 | 0.097917 | 0.099306 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | 02_21 | 84.8597 |  | WTG Unscheduled Maintenance | 61099 | 84.8597
1267 | 2024-07-25 | 2025 | 2024 | 2024-07-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 973 | Check blade bend.mom. | Break down | 0.16389 | 0.16389 | 0.16736 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | 02_21 | 212.1493 |  | WTG Unscheduled Maintenance | 61099 | 212.1493
1268 | 2024-07-25 | 2025 | 2024 | 2024-07-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 1600 | High gear speed | Break down | 0.51458 | 0.51458 | 0.51667 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | 02_21 | 127.2896 |  | WTG Unscheduled Maintenance | 61099 | 127.2896
1269 | 2024-07-25 | 2025 | 2024 | 2024-07-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.028472 | 0.028472 | 0.038889 | 0 | 0.25 | 0.25 | Checked related error data log then reset & run the WTG. | Close | 0.0096154 | O2_11 | 612 |  | WTG Unscheduled Maintenance | 58752 | 612
1270 | 2024-07-25 | 2025 | 2024 | 2024-07-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | ROW issue | 0.61111 | 0.61111 | 0.65625 | 0 | 1.0833 | 1.0833 | attend and check related circuit than found VCB was tripped by vanrajbhai due to senvion project pending paymnet for tractor Hiring , so charge By BOP person than reset and start Turbine. | Close | 0.041667 | O2_11 | 2652 |  | WTG Unscheduled Maintenance | 58752 | 2652
1271 | 2024-07-25 | 2025 | 2024 | 2024-07-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.088889 | 0.088889 | 0.10139 | 0 | 0.3 | 0.3 | Checked related error data log then reset & run the WTG. | Close | 0.011538 | 02_25 | 765.2625 |  | WTG Unscheduled Maintenance | 61221 | 765.2625
1272 | 2024-07-25 | 2025 | 2024 | 2024-07-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.3875 | 0.3875 | 0.39444 | 0 | 0.16667 | 0.16667 | Checked related error data log then reset & run the WTG. | Close | 0.0064103 | 02_21 | 424.2986 |  | WTG Unscheduled Maintenance | 61099 | 424.2986
1273 | 2024-07-25 | 2025 | 2024 | 2024-07-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.39514 | 0.39514 | 0.40069 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & run the WTG. | Close | 0.0051282 | 02_21 | 339.4389 |  | WTG Unscheduled Maintenance | 61099 | 339.4389
1274 | 2024-07-25 | 2025 | 2024 | 2024-07-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD | 0 | 0 | 0.75 | 0 | 18 | 18 | After grid commissioning done start Wtg. | Close | 0.69231 | 02_01 | 43602 |  | WTG Breakdown Maintenance | 58136 | 43602
1275 | 2024-07-26 | 2025 | 2024 | 2024-07-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.49097 | 0.49097 | 0.49931 | 0 | 0.2 | 0.2 | Checked related error data log then reset & run the WTG. | Close | 0.0076923 | O2_05 | 445.1417 |  | WTG Unscheduled Maintenance | 53417 | 445.1417
1276 | 2024-07-26 | 2025 | 2024 | 2024-07-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.27917 | 0.27917 | 0.28264 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_02 | 194.3819 |  | WTG Unscheduled Maintenance | 55982 | 194.3819
1277 | 2024-07-26 | 2025 | 2024 | 2024-07-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.6875 | 0.6875 | 0.71736 | 0 | 0.71667 | 0.71667 | Wtg Manual stop by costomer for Power cable inspection Work. | Close | 0.027564 | O2_02 | 1671.6847 |  | WTG Breakdown Maintenance | 55982 | 1671.6847
1278 | 2024-07-26 | 2025 | 2024 | 2024-07-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.66111 | 0.66111 | 0.66458 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | 02_03 | 177.1042 |  | WTG Unscheduled Maintenance | 51006 | 177.1042
1279 | 2024-07-26 | 2025 | 2024 | 2024-07-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 9211 | External stop IEC | Auto reset | 0.85 | 0.85 | 0.85069 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | 02_03 | 35.4208 |  | WTG Unscheduled Maintenance | 51006 | 35.4208
1280 | 2024-07-26 | 2025 | 2024 | 2024-07-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 9211 | External stop IEC | Auto reset | 0.85 | 0.85 | 0.85069 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | O2_13 | 37.8382 |  | WTG Unscheduled Maintenance | 54487 | 37.8382
1281 | 2024-07-26 | 2025 | 2024 | 2024-07-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 47 | Max. windspeed BP50 | Auto reset | 0.85486 | 0.85486 | 0.85625 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2_13 | 75.6764 |  | WTG Unscheduled Maintenance | 54487 | 75.6764
1282 | 2024-07-26 | 2025 | 2024 | 2024-07-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.5625 | 0.5625 | 0.59722 | 0 | 0.83333 | 0.83333 | Wtg Manual stop by costomer for Power cable inspection Work. | Close | 0.032051 | O2_11 | 1905.3819 |  | WTG Breakdown Maintenance | 54875 | 1905.3819
1283 | 2024-07-26 | 2025 | 2024 | 2024-07-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 9211 | External stop IEC | Auto reset | 0.85 | 0.85 | 0.85069 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | O2_11 | 38.1076 |  | WTG Unscheduled Maintenance | 54875 | 38.1076
1284 | 2024-07-26 | 2025 | 2024 | 2024-07-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.85625 | 0.85625 | 0.85833 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_11 | 114.3229 |  | WTG Unscheduled Maintenance | 54875 | 114.3229
1285 | 2024-07-26 | 2025 | 2024 | 2024-07-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.51042 | 0.51042 | 0.56875 | 0 | 1.4 | 1.4 | Wtg Manual stop by costomer for Power cable inspection Work. | Close | 0.053846 | O2_11 | 3201.0417 |  | WTG Breakdown Maintenance | 54875 | 3201.0417
1286 | 2024-07-26 | 2025 | 2024 | 2024-07-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 550 | Pitch current asymmetry | Break down | 0.28333 | 0.28333 | 0.29306 | 0 | 0.23333 | 0.23333 | Checked related error data log then reset & run the WTG. | Close | 0.0089744 | 02_20 | 503.4944 |  | WTG Unscheduled Maintenance | 51788 | 503.4944
1287 | 2024-07-26 | 2025 | 2024 | 2024-07-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.27361 | 0.27361 | 0.28403 | 0 | 0.25 | 0.25 | Checked related error data log then reset & run the WTG. | Close | 0.0096154 | 02_21 | 566.2812 |  | WTG Unscheduled Maintenance | 54363 | 566.2812
1288 | 2024-07-26 | 2025 | 2024 | 2024-07-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.55625 | 0.55625 | 0.56111 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & run the WTG. | Close | 0.0044872 | O2_18 | 260.6236 |  | WTG Unscheduled Maintenance | 53614 | 260.6236
1289 | 2024-07-26 | 2025 | 2024 | 2024-07-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.56458 | 0.56458 | 0.57014 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & run the WTG. | Close | 0.0051282 | O2_18 | 297.8556 |  | WTG Breakdown Maintenance | 53614 | 297.8556
1290 | 2024-07-26 | 2025 | 2024 | 2024-07-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.044444 | 0.044444 | 0.052778 | 0 | 0.2 | 0.2 | Checked related error data log then reset & run the WTG. | Close | 0.0076923 | 02_01 | 436.8833 |  | WTG Unscheduled Maintenance | 52426 | 436.8833
1291 | 2024-07-26 | 2025 | 2024 | 2024-07-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.070833 | 0.070833 | 0.080556 | 0 | 0.23333 | 0.23333 | Checked related error data log then reset & run the WTG. | Close | 0.0089744 | 02_01 | 509.6972 |  | WTG Unscheduled Maintenance | 52426 | 509.6972
1292 | 2024-07-26 | 2025 | 2024 | 2024-07-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Project pending work | 0.39236 | 0.39236 | 0.50139 | 0 | 2.6167 | 2.6167 | Attend by project team for repeted hydrulic error. | Close | 0.10064 | 02_01 | 5715.8903 |  | WTG Unscheduled Maintenance | 52426 | 5715.8903
1293 | 2024-07-26 | 2025 | 2024 | 2024-07-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Project pending work | 0.54792 | 0.54792 | 0.70139 | 0 | 3.6833 | 3.6833 | Attend by project team for repeted SLC error. | Close | 0.14167 | 02_01 | 8045.9347 |  | WTG Unscheduled Maintenance | 52426 | 8045.9347
1294 | 2024-07-27 | 2025 | 2024 | 2024-07-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Break down | 0.34097 | 0.34097 | 0.54444 | 0 | 4.8833 | 4.8833 | Attend wtg and check related circuit and Found flate resister malfunctioning so replace flate resister in axis no 1 than reset and start WTG. | Close | 0.18782 | 02_09 | 8314.4854 |  | WTG Unscheduled Maintenance | 40863 | 8314.4854
1295 | 2024-07-27 | 2025 | 2024 | 2024-07-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.3125 | 0.3125 | 0.31806 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & run the WTG. | Close | 0.0051282 | 02_21 | 251.9389 |  | WTG Unscheduled Maintenance | 45349 | 251.9389
1296 | 2024-07-27 | 2025 | 2024 | 2024-07-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.41944 | 0.41944 | 0.43056 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | 02_21 | 503.8778 |  | WTG Unscheduled Maintenance | 45349 | 503.8778
1297 | 2024-07-27 | 2025 | 2024 | 2024-07-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.67431 | 0.67431 | 0.68264 | 0 | 0.2 | 0.2 | Checked related error data log then reset & run the WTG. | Close | 0.0076923 | 02_21 | 377.9083 |  | WTG Unscheduled Maintenance | 45349 | 377.9083
1298 | 2024-07-27 | 2025 | 2024 | 2024-07-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.52292 | 0.52292 | 0.55069 | 0 | 0.66667 | 0.66667 | Wtg Manual stop by costomer for Power cable inspection Work. | Close | 0.025641 | 02_13 | 1456.2778 |  | WTG Breakdown Maintenance | 52426 | 1456.2778
1299 | 2024-07-27 | 2025 | 2024 | 2024-07-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.35833 | 0.35833 | 0.37153 | 0 | 0.31667 | 0.31667 | Checked related error data log then reset & run the WTG. | Close | 0.012179 | 02_12 | 586.216 |  | WTG Unscheduled Maintenance | 44429 | 586.216
1300 | 2024-07-27 | 2025 | 2024 | 2024-07-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.44792 | 0.44792 | 0.45208 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | 02_12 | 185.1208 |  | WTG Unscheduled Maintenance | 44429 | 185.1208
1301 | 2024-07-27 | 2025 | 2024 | 2024-07-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.55694 | 0.55694 | 0.58958 | 0 | 0.78333 | 0.78333 | Wtg Manual stop by costomer for Power cable inspection Work. | Close | 0.030128 | 02_12 | 1450.1132 |  | WTG Breakdown Maintenance | 44429 | 1450.1132
1302 | 2024-07-27 | 2025 | 2024 | 2024-07-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.66667 | 0.66667 | 0.67083 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | 02_12 | 185.1208 |  | WTG Unscheduled Maintenance | 44429 | 185.1208
1303 | 2024-07-27 | 2025 | 2024 | 2024-07-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 973 | Check blade bend.mom. | Auto reset | 0.56319 | 0.56319 | 0.56458 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | 02_20 | 55.9931 |  | WTG Unscheduled Maintenance | 40315 | 55.9931
1304 | 2024-07-27 | 2025 | 2024 | 2024-07-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.50208 | 0.50208 | 0.52153 | 0 | 0.46667 | 0.46667 | Checked related error data log then reset & run the WTG. | Close | 0.017949 | 02_01 | 734.9611 |  | WTG Unscheduled Maintenance | 37798 | 734.9611
1305 | 2024-07-27 | 2025 | 2024 | 2024-07-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Project pending work | 0.36667 | 0.36667 | 0.47222 | 0 | 2.5333 | 2.5333 | Attend by project team for repeted Frequency converter not ready error. | Close | 0.097436 | 02_01 | 3989.7889 |  | WTG Unscheduled Maintenance | 37798 | 3989.7889
1306 | 2024-07-28 | 2025 | 2024 | 2024-07-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Auto reset | 0.79861 | 0.79861 | 0.8 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2_21 | 29.5986 |  | WTG Unscheduled Maintenance | 21311 | 29.5986
1307 | 2024-07-28 | 2025 | 2024 | 2024-07-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.48958 | 0.48958 | 0.50278 | 0 | 0.31667 | 0.31667 | Checked related error data log then reset & run the WTG. | Close | 0.012179 | 02_11 | 272.3069 |  | WTG Unscheduled Maintenance | 20638 | 272.3069
1308 | 2024-07-28 | 2025 | 2024 | 2024-07-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.75347 | 0.75347 | 0.77153 | 0 | 0.43333 | 0.43333 | after grid resume Wtg in error so check related data than reset and start6 WTG. | Close | 0.016667 | 02_11 | 372.6306 |  | WTG Unscheduled Maintenance | 20638 | 372.6306
1309 | 2024-07-28 | 2025 | 2024 | 2024-07-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.75556 | 0.75556 | 0.77083 | 0 | 0.36667 | 0.36667 | after grid resume Wtg in error so check related data than apply soft reboot than reset and start6 WTG. | Close | 0.014103 | O2_13 | 421.2847 |  | WTG Unscheduled Maintenance | 27575 | 421.2847
1310 | 2024-07-28 | 2025 | 2024 | 2024-07-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.37986 | 0.37986 | 0.38958 | 0 | 0.23333 | 0.23333 | Checked related error data log then reset & run the WTG. | Close | 0.0089744 | 02_20 | 201.8333 |  | WTG Unscheduled Maintenance | 20760 | 201.8333
1311 | 2024-07-28 | 2025 | 2024 | 2024-07-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 656 | Error pitch converter 1 | Break down | 0.37778 | 0.37778 | 0.39097 | 0 | 0.31667 | 0.31667 | Checked related error data log then reset & run the WTG. | Close | 0.012179 | O2_06 | 271.6208 |  | WTG Unscheduled Maintenance | 20586 | 271.6208
1312 | 2024-07-28 | 2025 | 2024 | 2024-07-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 7002 | Task runtime failure 5ms | Break down | 0.27083 | 0.27083 | 0.28611 | 0 | 0.36667 | 0.36667 | Checked related error data log then reset & run the WTG. | Close | 0.014103 | 02_01 | 295.2583 |  | WTG Unscheduled Maintenance | 19326 | 295.2583
1313 | 2024-07-28 | 2025 | 2024 | 2024-07-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.75347 | 0.75347 | 0.77431 | 0 | 0.5 | 0.5 | after grid resume Wtg in error so check related data than reset and start6 WTG. | Close | 0.019231 | 02_01 | 402.625 |  | WTG Unscheduled Maintenance | 19326 | 402.625
1314 | 2024-07-28 | 2025 | 2024 | 2024-07-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 656 | Error pitch converter 1 | Break down | 0.50347 | 0.50347 | 0.51042 | 0 | 0.16667 | 0.16667 | Checked related error data log then reset & run the WTG. | Close | 0.0064103 | 02_05 | 150.8403 |  | WTG Unscheduled Maintenance | 21721 | 150.8403
1315 | 2024-07-28 | 2025 | 2024 | 2024-07-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.51111 | 0.51111 | 0.51944 | 0 | 0.2 | 0.2 | Checked related error data log then reset & run the WTG. | Close | 0.0076923 | 02_05 | 181.0083 |  | WTG Unscheduled Maintenance | 21721 | 181.0083
1316 | 2024-07-28 | 2025 | 2024 | 2024-07-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.43403 | 0.43403 | 0.43681 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & run the WTG. | Close | 0.0025641 | O2_12 | 62.3278 |  | WTG Unscheduled Maintenance | 22438 | 62.3278
1317 | 2024-07-28 | 2025 | 2024 | 2024-07-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.44444 | 0.44444 | 0.675 | 0 | 5.5333 | 5.5333 | attend and check releted circuit then drail all oil and also open its filter and properly clean it by using blower all oil clean by using gasket then top up all oil then close it filteer after done all oil then close it filtter after done all activity then pressure release switch close it properly then reset and run the wtg after grid resume | Close | 0.21282 | O2_12 | 5173.2056 |  | WTG Unscheduled Maintenance | 22438 | 5173.2056
1318 | 2024-07-28 | 2025 | 2024 | 2024-07-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.75347 | 0.75347 | 0.77778 | 0 | 0.58333 | 0.58333 | after grid resume Wtg in error so check related data than reset and start6 WTG. | Close | 0.022436 | O2_12 | 545.3681 |  | WTG Unscheduled Maintenance | 22438 | 545.3681
1319 | 2024-07-28 | 2025 | 2024 | 2024-07-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.8125 | 0.8125 | 0.8375 | 0 | 0.6 | 0.6 | attend and check releted circuit then drail all oil and also open its filter and properly clean it by using blower all oil clean by using gasket then top up all oil then close it filteer after done all oil then close it filtter after done all activity then pressure release switch close it properly then reset and run the wtg after grid resume | Close | 0.023077 | O2_12 | 560.95 |  | WTG Unscheduled Maintenance | 22438 | 560.95
1320 | 2024-07-28 | 2025 | 2024 | 2024-07-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.85486 | 0.85486 | 0.86736 | 0 | 0.3 | 0.3 | Checked related error data log then reset & run the WTG. | Close | 0.011538 | O2_12 | 280.475 |  | WTG Unscheduled Maintenance | 22438 | 280.475
1321 | 2024-07-28 | 2025 | 2024 | 2024-07-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.88333 | 0.88333 | 0.89653 | 0 | 0.31667 | 0.31667 | Checked related error data log then reset & run the WTG. | Close | 0.012179 | O2_12 | 296.0569 |  | WTG Unscheduled Maintenance | 22438 | 296.0569
1322 | 2024-07-28 | 2025 | 2024 | 2024-07-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.92014 | 0.92014 | 0.93264 | 0 | 0.3 | 0.3 | Checked related error data log then reset & run the WTG. | Close | 0.011538 | O2_12 | 280.475 |  | WTG Unscheduled Maintenance | 22438 | 280.475
1323 | 2024-07-28 | 2025 | 2024 | 2024-07-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.96389 | 0.96389 | 0.98056 | 0 | 0.4 | 0.4 | Checked related error data log then reset & run the WTG. | Close | 0.015385 | O2_12 | 373.9667 |  | WTG Unscheduled Maintenance | 22438 | 373.9667
1324 | 2024-07-29 | 2025 | 2024 | 2024-07-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.020139 | 0.020139 | 0.021528 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_21 | 42.0361 |  | WTG Unscheduled Maintenance | 30266 | 42.0361
1325 | 2024-07-29 | 2025 | 2024 | 2024-07-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.54514 | 0.54514 | 0.58333 | 0 | 0.91667 | 0.91667 | Shutdown taken by customer for USS transformer inspection | Close | 0.035256 | O2_01 | 995.8056 |  | WTG Breakdown Maintenance | 26072 | 995.8056
1326 | 2024-07-29 | 2025 | 2024 | 2024-07-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0.62292 | 0.62292 | 0.67708 | 0 | 1.3 | 1.3 | VCB tripped, so charge and start turbine | Close | 0.05 | O2_01 | 1412.2333 |  | WTG Unscheduled Maintenance | 26072 | 1412.2333
1327 | 2024-07-29 | 2025 | 2024 | 2024-07-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.69722 | 0.69722 | 0.70069 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_13 | 88.7083 |  | WTG Unscheduled Maintenance | 25548 | 88.7083
1328 | 2024-07-29 | 2025 | 2024 | 2024-07-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Break down | 0.82222 | 0.82222 | 0.83333 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_12 | 291.4778 |  | WTG Unscheduled Maintenance | 26233 | 291.4778
1329 | 2024-07-29 | 2025 | 2024 | 2024-07-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.064583 | 0.064583 | 0.068056 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_06 | 101.3576 |  | WTG Unscheduled Maintenance | 29191 | 101.3576
1330 | 2024-07-29 | 2025 | 2024 | 2024-07-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.22917 | 0.22917 | 0.23056 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_06 | 40.5431 |  | WTG Unscheduled Maintenance | 29191 | 40.5431
1331 | 2024-07-29 | 2025 | 2024 | 2024-07-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.36875 | 0.36875 | 0.37431 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & run the WTG. | Close | 0.0051282 | O2_06 | 162.1722 |  | WTG Unscheduled Maintenance | 29191 | 162.1722
1332 | 2024-07-29 | 2025 | 2024 | 2024-07-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.98333 | 0.98333 | 0.98472 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_06 | 40.5431 |  | WTG Unscheduled Maintenance | 29191 | 40.5431
1333 | 2024-07-29 | 2025 | 2024 | 2024-07-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.0083333 | 0.0083333 | 0.0125 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2_11 | 107.4708 |  | WTG Unscheduled Maintenance | 25793 | 107.4708
1334 | 2024-07-29 | 2025 | 2024 | 2024-07-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.1375 | 0.1375 | 0.14722 | 0 | 0.23333 | 0.23333 | Checked related error data log then reset & run the WTG. | Close | 0.0089744 | O2_11 | 250.7653 |  | WTG Unscheduled Maintenance | 25793 | 250.7653
1335 | 2024-07-29 | 2025 | 2024 | 2024-07-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.18333 | 0.18333 | 0.18681 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_11 | 89.559 |  | WTG Unscheduled Maintenance | 25793 | 89.559
1336 | 2024-07-29 | 2025 | 2024 | 2024-07-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.19861 | 0.19861 | 0.20833 | 0 | 0.23333 | 0.23333 | Checked related error data log then reset & run the WTG. | Close | 0.0089744 | O2_11 | 250.7653 |  | WTG Unscheduled Maintenance | 25793 | 250.7653
1337 | 2024-07-29 | 2025 | 2024 | 2024-07-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.22153 | 0.22153 | 0.24931 | 0 | 0.66667 | 0.66667 | Checked related error data log then reset & run the WTG. | Close | 0.025641 | O2_11 | 716.4722 |  | WTG Unscheduled Maintenance | 25793 | 716.4722
1338 | 2024-07-29 | 2025 | 2024 | 2024-07-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.37569 | 0.37569 | 0.39097 | 0 | 0.36667 | 0.36667 | Checked related error data log then reset & run the WTG. | Close | 0.014103 | O2_11 | 394.0597 |  | WTG Unscheduled Maintenance | 25793 | 394.0597
1339 | 2024-07-29 | 2025 | 2024 | 2024-07-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Major BD | 0.40556 | 0.40556 | 0.68472 | 0 | 6.7 | 6.7 | Attend and hydraulic oil flushing done, check & clean oil filter then Hydraulic oil replaced with new oil then take trial and start | Close | 0.25769 | O2_11 | 7200.5458 |  | WTG Unscheduled Maintenance | 25793 | 7200.5458
1340 | 2024-07-29 | 2025 | 2024 | 2024-07-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.75347 | 0.75347 | 0.76736 | 0 | 0.33333 | 0.33333 | Checked related error data log then reset & run the WTG. | Close | 0.012821 | O2_11 | 358.2361 |  | WTG Unscheduled Maintenance | 25793 | 358.2361
1341 | 2024-07-29 | 2025 | 2024 | 2024-07-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.775 | 0.775 | 0.78056 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & run the WTG. | Close | 0.0051282 | O2_11 | 143.2944 |  | WTG Unscheduled Maintenance | 25793 | 143.2944
1342 | 2024-07-29 | 2025 | 2024 | 2024-07-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.79514 | 0.79514 | 0.81389 | 0 | 0.45 | 0.45 | Checked related error data log then reset & run the WTG. | Close | 0.017308 | O2_11 | 483.6188 |  | WTG Unscheduled Maintenance | 25793 | 483.6188
1343 | 2024-07-29 | 2025 | 2024 | 2024-07-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.82361 | 0.82361 | 0.99931 | 0 | 4.2167 | 4.2167 | Attend and again oil flushing done, replaced oil with new oil, pressure switch removed, clean and pressure setting done then start. | Close | 0.16218 | O2_11 | 4531.6868 |  | WTG Unscheduled Maintenance | 25793 | 4531.6868
1344 | 2024-07-30 | 2025 | 2024 | 2024-07-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.56111 | 0.56111 | 0.56458 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_01 | 93.5521 |  | WTG Unscheduled Maintenance | 26943 | 93.5521
1345 | 2024-07-30 | 2025 | 2024 | 2024-07-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.41111 | 0.41111 | 0.68611 | 0 | 6.6 | 6.6 | Manual stop for 1st month maintenance activity | Close | 0.25385 | O2_13 | 6474.6 |  | WTG Scheduled Maintenance | 23544 | 6474.6
1346 | 2024-07-30 | 2025 | 2024 | 2024-07-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0 | 0 | 0.061111 | 0 | 1.4667 | 1.4667 | Attend and again oil flushing done, replaced oil with new oil, pressure switch removed, clean and pressure setting done then start. | Close | 0.05641 | O2_13 | 1438.8 |  | WTG Unscheduled Maintenance | 23544 | 1438.8
1347 | 2024-07-30 | 2025 | 2024 | 2024-07-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.58056 | 0.58056 | 0.59722 | 0 | 0.4 | 0.4 | Manual stop for tower fan mounting correction work | Close | 0.015385 | O2_13 | 392.4 |  | WTG Breakdown Maintenance | 23544 | 392.4
1348 | 2024-07-30 | 2025 | 2024 | 2024-07-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Project pending work | 0.054167 | 0.054167 | 0.05625 | 0 | 0.05 | 0.05 | Manual stop for tower fan mounting correction work | Close | 0.0019231 | O2_06 | 53.8354 |  | WTG Unscheduled Maintenance | 25841 | 53.8354
1349 | 2024-07-30 | 2025 | 2024 | 2024-07-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.99583 | 0.99583 | 0.99861 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & run the WTG. | Close | 0.0025641 | O2_06 | 71.7806 |  | WTG Unscheduled Maintenance | 25841 | 71.7806
1350 | 2024-07-30 | 2025 | 2024 | 2024-07-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.22569 | 0.22569 | 0.22986 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2_06 | 107.6708 |  | WTG Unscheduled Maintenance | 25841 | 107.6708
1351 | 2024-07-31 | 2025 | 2024 | 2024-07-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.063889 | 0.063889 | 0.065972 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_05 | 68.1917 |  | WTG Unscheduled Maintenance | 32732 | 68.1917
1352 | 2024-07-31 | 2025 | 2024 | 2024-07-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.52222 | 0.52222 | 0.52639 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2_05 | 136.3833 |  | WTG Unscheduled Maintenance | 32732 | 136.3833
1353 | 2024-07-31 | 2025 | 2024 | 2024-07-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Break down | 0.72083 | 0.72083 | 0.73194 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_05 | 363.6889 |  | WTG Unscheduled Maintenance | 32732 | 363.6889
1354 | 2024-07-31 | 2025 | 2024 | 2024-07-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.73889 | 0.73889 | 0.74583 | 0 | 0.16667 | 0.16667 | Checked related error data log then reset & run the WTG. | Close | 0.0064103 | O2_05 | 227.3056 |  | WTG Unscheduled Maintenance | 32732 | 227.3056
1355 | 2024-07-31 | 2025 | 2024 | 2024-07-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.0041667 | 0.0041667 | 0.00625 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_21 | 61.9792 |  | WTG Unscheduled Maintenance | 29750 | 61.9792
1356 | 2024-07-31 | 2025 | 2024 | 2024-07-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.70694 | 0.70694 | 0.71736 | 0 | 0.25 | 0.25 | Checked related error data log then reset & run the WTG. | Close | 0.0096154 | O2_21 | 309.8958 |  | WTG Unscheduled Maintenance | 29750 | 309.8958
1357 | 2024-07-31 | 2025 | 2024 | 2024-07-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.67222 | 0.67222 | 0.67639 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2_15 | 118.2333 |  | WTG Unscheduled Maintenance | 28376 | 118.2333
1358 | 2024-07-31 | 2025 | 2024 | 2024-07-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Break down | 0.57778 | 0.57778 | 0.58889 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_14 | 327.6333 |  | WTG Unscheduled Maintenance | 29487 | 327.6333
1359 | 2024-07-31 | 2025 | 2024 | 2024-07-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.42431 | 0.42431 | 0.70833 | 0 | 6.8167 | 6.8167 | Manual stop for 1st month maintenance activity | Close | 0.26218 | O2_14 | 8375.1271 |  | WTG Scheduled Maintenance | 29487 | 8375.1271
1360 | 2024-07-31 | 2025 | 2024 | 2024-07-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.050694 | 0.050694 | 0.051389 | 0 | 0.016667 | 0.016667 | Checked related error data log then reset & run the WTG. | Close | 0.00064103 | O2_21 | 20.6597 |  | WTG Unscheduled Maintenance | 29750 | 20.6597
1361 | 2024-07-31 | 2025 | 2024 | 2024-07-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.39444 | 0.39444 | 0.41667 | 0 | 0.53333 | 0.53333 | Checked related error data log then reset & run the WTG. | Close | 0.020513 | O2_21 | 661.1111 |  | WTG Unscheduled Maintenance | 29750 | 661.1111
1362 | 2024-07-31 | 2025 | 2024 | 2024-07-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Break down | 0.67708 | 0.67708 | 0.68819 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_16 | 287.5889 |  | WTG Unscheduled Maintenance | 25883 | 287.5889
1363 | 2024-07-31 | 2025 | 2024 | 2024-07-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.098611 | 0.098611 | 0.099306 | 0 | 0.016667 | 0.016667 | Checked related error data log then reset & run the WTG. | Close | 0.00064103 | O2_18 | 19.4319 |  | WTG Unscheduled Maintenance | 27982 | 19.4319
1364 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 9211 | External stop IEC | Break down | 0.44861 | 0.44861 | 0.45069 | 0 | 0.05 | 0.05 | Turbine stopped due to PPC testing | Close | 0.0019231 | O2_09 | 94.7396 |  | WTG Unscheduled Maintenance | 45475 | 94.7396
1365 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 7002 | Task runtime failure 5ms | Break down | 0.52083 | 0.52083 | 0.53194 | 0 | 0.26667 | 0.26667 | Turbine stopped due to PPC testing | Close | 0.010256 | O2_09 | 505.2778 |  | WTG Unscheduled Maintenance | 45475 | 505.2778
1366 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.55903 | 0.55903 | 0.57569 | 0 | 0.4 | 0.4 | Checked related error data log then reset & run the WTG. | Close | 0.015385 | O2_09 | 757.9167 |  | WTG Unscheduled Maintenance | 45475 | 757.9167
1367 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.36111 | 0.36111 | 0.37361 | 0 | 0.3 | 0.3 | Checked related error data log then reset & run the WTG. | Close | 0.011538 | O2_05 | 606.7875 |  | WTG Unscheduled Maintenance | 48543 | 606.7875
1368 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.79722 | 0.79722 | 0.84028 | 0 | 1.0333 | 1.0333 | Checked related error data log then reset & run the WTG. | Close | 0.039744 | O2_05 | 2090.0458 |  | WTG Unscheduled Maintenance | 48543 | 2090.0458
1369 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 9211 | External stop IEC | Break down | 0.44722 | 0.44722 | 0.45 | 0 | 0.066667 | 0.066667 | Turbine stopped due to PPC testing | Close | 0.0025641 | O2_09 | 126.3194 |  | WTG Unscheduled Maintenance | 45475 | 126.3194
1370 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 9211 | External stop IEC | Break down | 0.48264 | 0.48264 | 0.48333 | 0 | 0.016667 | 0.016667 | Turbine stopped due to PPC testing | Close | 0.00064103 | O2_09 | 31.5799 |  | WTG Unscheduled Maintenance | 45475 | 31.5799
1371 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 4540 | Tower oscillation X level 2 | Break down | 0.66389 | 0.66389 | 0.67431 | 0 | 0.25 | 0.25 | Checked related error data log then reset & run the WTG. | Close | 0.0096154 | O2_09 | 473.6979 |  | WTG Unscheduled Maintenance | 45475 | 473.6979
1372 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 9211 | External stop IEC | Break down | 0.44444 | 0.44444 | 0.44653 | 0 | 0.05 | 0.05 | Turbine stopped due to PPC testing | Close | 0.0019231 | O2_02 | 96.2 |  | WTG Unscheduled Maintenance | 46176 | 96.2
1373 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 9211 | External stop IEC | Break down | 0.47986 | 0.47986 | 0.48056 | 0 | 0.016667 | 0.016667 | Turbine stopped due to PPC testing | Close | 0.00064103 | O2_02 | 32.0667 |  | WTG Unscheduled Maintenance | 46176 | 32.0667
1374 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.54097 | 0.54097 | 0.54236 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_02 | 64.1333 |  | WTG Unscheduled Maintenance | 46176 | 64.1333
1375 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.54306 | 0.54306 | 0.55069 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & run the WTG. | Close | 0.0070513 | O2_02 | 352.7333 |  | WTG Unscheduled Maintenance | 46176 | 352.7333
1376 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.14861 | 0.14861 | 0.15 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_21 | 61.4347 |  | WTG Unscheduled Maintenance | 44233 | 61.4347
1377 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 9211 | External stop IEC | Break down | 0.44792 | 0.44792 | 0.45 | 0 | 0.05 | 0.05 | Turbine stopped due to PPC testing | Close | 0.0019231 | O2_21 | 92.1521 |  | WTG Unscheduled Maintenance | 44233 | 92.1521
1378 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 9211 | External stop IEC | Break down | 0.48333 | 0.48333 | 0.48403 | 0 | 0.016667 | 0.016667 | Turbine stopped due to PPC testing | Close | 0.00064103 | O2_21 | 30.7174 |  | WTG Unscheduled Maintenance | 44233 | 30.7174
1379 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.49861 | 0.49861 | 0.51389 | 0 | 0.36667 | 0.36667 | Checked related error data log then reset & run the WTG. | Close | 0.014103 | O2_21 | 675.7819 |  | WTG Unscheduled Maintenance | 44233 | 675.7819
1380 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.59028 | 0.59028 | 0.59375 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_21 | 153.5868 |  | WTG Unscheduled Maintenance | 44233 | 153.5868
1381 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 9211 | External stop IEC | Break down | 0.44792 | 0.44792 | 0.45069 | 0 | 0.066667 | 0.066667 | Turbine stopped due to PPC testing | Close | 0.0025641 | O2_01 | 122.4944 |  | WTG Unscheduled Maintenance | 44098 | 122.4944
1382 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.51319 | 0.51319 | 0.51389 | 0 | 0.016667 | 0.016667 | Checked related error data log then reset & run the WTG. | Close | 0.00064103 | O2_01 | 30.6236 |  | WTG Unscheduled Maintenance | 44098 | 30.6236
1383 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 1600 | High gear speed | Break down | 0.54167 | 0.54167 | 0.55625 | 0 | 0.35 | 0.35 | Checked related error data log then reset & run the WTG. | Close | 0.013462 | O2_01 | 643.0958 |  | WTG Unscheduled Maintenance | 44098 | 643.0958
1384 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.5875 | 0.5875 | 0.58889 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_01 | 61.2472 |  | WTG Unscheduled Maintenance | 44098 | 61.2472
1385 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 9211 | External stop IEC | Break down | 0.44792 | 0.44792 | 0.45069 | 0 | 0.066667 | 0.066667 | Turbine stopped due to PPC testing | Close | 0.0025641 | O2_15 | 114.6389 |  | WTG Unscheduled Maintenance | 41270 | 114.6389
1386 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 9211 | External stop IEC | Break down | 0.48333 | 0.48333 | 0.48403 | 0 | 0.016667 | 0.016667 | Turbine stopped due to PPC testing | Close | 0.00064103 | O2_15 | 28.6597 |  | WTG Unscheduled Maintenance | 41270 | 28.6597
1387 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 1600 | High gear speed | Break down | 0.53056 | 0.53056 | 0.54236 | 0 | 0.28333 | 0.28333 | Checked related error data log then reset & run the WTG. | Close | 0.010897 | O2_15 | 487.2153 |  | WTG Unscheduled Maintenance | 41270 | 487.2153
1388 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.68958 | 0.68958 | 0.69375 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2_15 | 171.9583 |  | WTG Unscheduled Maintenance | 41270 | 171.9583
1389 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.42014 | 0.42014 | 0.71528 | 0 | 7.0833 | 7.0833 | Manual stop for 1st month maintenance activity | Close | 0.27244 | O2_14 | 13296.8924 |  | WTG Scheduled Maintenance | 45053 | 13296.8924
1390 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.72986 | 0.72986 | 0.73542 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & run the WTG. | Close | 0.0051282 | O2_14 | 250.2944 |  | WTG Unscheduled Maintenance | 45053 | 250.2944
1391 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.75 | 0.75 | 0.76042 | 0 | 0.25 | 0.25 | Checked related error data log then reset & run the WTG. | Close | 0.0096154 | O2_14 | 469.3021 |  | WTG Unscheduled Maintenance | 45053 | 469.3021
1392 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.77431 | 0.77431 | 0.84028 | 0 | 1.5833 | 1.5833 | Checked related error data log then reset & run the WTG. | Close | 0.060897 | O2_14 | 2972.2465 |  | WTG Unscheduled Maintenance | 45053 | 2972.2465
1393 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.85833 | 0.85833 | 0.97917 | 0 | 2.9 | 2.9 | Attend and Ultrasonic sensor alignment done, checked cable and connector then satrt | Close | 0.11154 | O2_14 | 5443.9042 |  | WTG Unscheduled Maintenance | 45053 | 5443.9042
1394 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.043056 | 0.043056 | 0.04375 | 0 | 0.016667 | 0.016667 | Checked related error data log then reset & run the WTG. | Close | 0.00064103 | O2_14 | 31.2868 |  | WTG Unscheduled Maintenance | 45053 | 31.2868
1395 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.66458 | 0.66458 | 0.68125 | 0 | 0.4 | 0.4 | Checked related error data log then reset & run the WTG. | Close | 0.015385 | O2_14 | 750.8833 |  | WTG Unscheduled Maintenance | 45053 | 750.8833
1396 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 9211 | External stop IEC | Break down | 0.44861 | 0.44861 | 0.45069 | 0 | 0.05 | 0.05 | Turbine stopped due to PPC testing | Close | 0.0019231 | O2_14 | 93.8604 |  | WTG Unscheduled Maintenance | 45053 | 93.8604
1397 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.45347 | 0.45347 | 0.45694 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_14 | 156.434 |  | WTG Unscheduled Maintenance | 45053 | 156.434
1398 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.50764 | 0.50764 | 0.51875 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_14 | 500.5889 |  | WTG Unscheduled Maintenance | 45053 | 500.5889
1399 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 1600 | High gear speed | Break down | 0.53333 | 0.53333 | 0.54306 | 0 | 0.23333 | 0.23333 | Checked related error data log then reset & run the WTG. | Close | 0.0089744 | O2_14 | 438.0153 |  | WTG Unscheduled Maintenance | 45053 | 438.0153
1400 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.59306 | 0.59306 | 0.62361 | 0 | 0.73333 | 0.73333 | Checked related error data log then reset & run the WTG. | Close | 0.028205 | O2_14 | 1376.6194 |  | WTG Unscheduled Maintenance | 45053 | 1376.6194
1401 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.62917 | 0.62917 | 0.63125 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_14 | 93.8604 |  | WTG Unscheduled Maintenance | 45053 | 93.8604
1402 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 9211 | External stop IEC | Break down | 0.44792 | 0.44792 | 0.45 | 0 | 0.05 | 0.05 | Turbine stopped due to PPC testing | Close | 0.0019231 | O2_12 | 94.8167 |  | WTG Unscheduled Maintenance | 45512 | 94.8167
1403 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 1600 | High gear speed | Break down | 0.53194 | 0.53194 | 0.54306 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_12 | 505.6889 |  | WTG Unscheduled Maintenance | 45512 | 505.6889
1404 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.53194 | 0.53194 | 0.54236 | 0 | 0.25 | 0.25 | Checked related error data log then reset & run the WTG. | Close | 0.0096154 | O2_10 | 445.7187 |  | WTG Unscheduled Maintenance | 42789 | 445.7187
1405 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.44028 | 0.44028 | 0.44167 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_18 | 56.4792 |  | WTG Unscheduled Maintenance | 40665 | 56.4792
1406 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 9211 | External stop IEC | Break down | 0.44792 | 0.44792 | 0.45 | 0 | 0.05 | 0.05 | Turbine stopped due to PPC testing | Close | 0.0019231 | O2_18 | 84.7187 |  | WTG Unscheduled Maintenance | 40665 | 84.7187
1407 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 9211 | External stop IEC | Break down | 0.48333 | 0.48333 | 0.48403 | 0 | 0.016667 | 0.016667 | Turbine stopped due to PPC testing | Close | 0.00064103 | O2_18 | 28.2396 |  | WTG Unscheduled Maintenance | 40665 | 28.2396
1408 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 973 | Check blade bend.mom. | Break down | 0.53403 | 0.53403 | 0.53472 | 0 | 0.016667 | 0.016667 | Checked related error data log then reset & run the WTG. | Close | 0.00064103 | O2_18 | 28.2396 |  | WTG Unscheduled Maintenance | 40665 | 28.2396
1409 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 973 | Check blade bend.mom. | Break down | 0.72431 | 0.72431 | 0.725 | 0 | 0.016667 | 0.016667 | Checked related error data log then reset & run the WTG. | Close | 0.00064103 | O2_18 | 28.2396 |  | WTG Unscheduled Maintenance | 40665 | 28.2396
1410 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 9211 | External stop IEC | Break down | 0.44792 | 0.44792 | 0.45 | 0 | 0.05 | 0.05 | Turbine stopped due to PPC testing | Close | 0.0019231 | O2_16 | 78.9458 |  | WTG Unscheduled Maintenance | 37894 | 78.9458
1411 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 9211 | External stop IEC | Break down | 0.48333 | 0.48333 | 0.48403 | 0 | 0.016667 | 0.016667 | Turbine stopped due to PPC testing | Close | 0.00064103 | O2_16 | 26.3153 |  | WTG Unscheduled Maintenance | 37894 | 26.3153
1412 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0.89028 | 0.89028 | 0.94931 | 0 | 1.4167 | 1.4167 | Found VCB trip by unknown person. So charge it by BOP person then reset and run the WTG. | Close | 0.054487 | O2_16 | 2236.7986 |  | WTG Unscheduled Maintenance | 37894 | 2236.7986
1413 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 9211 | External stop IEC | Break down | 0.44792 | 0.44792 | 0.45069 | 0 | 0.066667 | 0.066667 | Turbine stopped due to PPC testing | Close | 0.0025641 | O2_16 | 105.2611 |  | WTG Unscheduled Maintenance | 37894 | 105.2611
1414 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 9211 | External stop IEC | Break down | 0.48333 | 0.48333 | 0.48403 | 0 | 0.016667 | 0.016667 | Turbine stopped due to PPC testing | Close | 0.00064103 | O2_16 | 26.3153 |  | WTG Unscheduled Maintenance | 37894 | 26.3153
1415 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.71667 | 0.71667 | 0.72014 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_06 | 141.4826 |  | WTG Unscheduled Maintenance | 40747 | 141.4826
1416 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.47639 | 0.47639 | 0.64375 | 0 | 4.0167 | 4.0167 | Atend and checked overvoltage protection circuit of Pitch supply, found loose connection of feedback circuit of surge protection so correct it, also found loose silica gel from so remove it then start | Close | 0.15449 | O2_13 | 6711.3479 |  | WTG Unscheduled Maintenance | 40101 | 6711.3479
1417 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.79444 | 0.79444 | 0.84028 | 0 | 1.1 | 1.1 | Checked related error data log then reset & run the WTG. | Close | 0.042308 | O2_13 | 1837.9625 |  | WTG Unscheduled Maintenance | 40101 | 1837.9625
1418 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.41875 | 0.41875 | 0.42639 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & run the WTG. | Close | 0.0070513 | O2_05 | 370.8146 |  | WTG Unscheduled Maintenance | 48543 | 370.8146
1419 | 2024-08-01 | 2025 | 2024 | 2024-08-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.48056 | 0.48056 | 0.71597 | 0 | 5.65 | 5.65 | Atend and checked overvoltage protection circuit of Pitch supply, found loose connection of feedback circuit of surge protection, so correct it then start | Close | 0.21731 | O2_05 | 11427.8313 |  | WTG Unscheduled Maintenance | 48543 | 11427.8313
1420 | 2024-08-02 | 2025 | 2024 | 2024-08-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.55625 | 0.55625 | 0.56667 | 0 | 0.25 | 0.25 | Checked related error data log then reset & run the WTG. | Close | 0.0096154 | O2_09 | 566.8021 |  | WTG Unscheduled Maintenance | 54413 | 566.8021
1421 | 2024-08-02 | 2025 | 2024 | 2024-08-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.076389 | 0.076389 | 0.08125 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & run the WTG. | Close | 0.0044872 | O2_09 | 264.5076 |  | WTG Unscheduled Maintenance | 54413 | 264.5076
1422 | 2024-08-02 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.38542 | 0.38542 | 0.39375 | 0 | 0.2 | 0.2 | Checked related error data log then reset & run the WTG. | Close | 0.0076923 | O2_21 | 407.5917 |  | WTG Unscheduled Maintenance | 48911 | 407.5917
1423 | 2024-08-02 | 2025 | 2024 | 2024-08-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD | 0.45417 | 0.45417 | 0.79375 | 0 | 8.15 | 8.15 | Manual stop for power curve issue inspection, checked blade calibration by laser tool, replaced ultrasonic sensor then alignment done and start | Close | 0.31346 | O2_15 | 18480.8042 |  | WTG Breakdown Maintenance | 54422 | 18480.8042
1424 | 2024-08-02 | 2025 | 2024 | 2024-08-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.81042 | 0.81042 | 0.81597 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & run the WTG. | Close | 0.0051282 | O2_15 | 302.3444 |  | WTG Unscheduled Maintenance | 54422 | 302.3444
1425 | 2024-08-02 | 2025 | 2024 | 2024-08-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.83125 | 0.83125 | 0.83472 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_15 | 188.9653 |  | WTG Unscheduled Maintenance | 54422 | 188.9653
1426 | 2024-08-02 | 2025 | 2024 | 2024-08-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.85833 | 0.85833 | 0.99931 | 0 | 3.3833 | 3.3833 | Attend and ultrasonic sensor cable check, alignment done then start. | Close | 0.13013 | O2_15 | 7671.9903 |  | WTG Unscheduled Maintenance | 54422 | 7671.9903
1427 | 2024-08-02 | 2025 | 2024 | 2024-08-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.41875 | 0.41875 | 0.69931 | 0 | 6.7333 | 6.7333 | Manual stop for 1st month maintenance activity | Close | 0.25897 | O2_13 | 15432.2389 |  | WTG Scheduled Maintenance | 55006 | 15432.2389
1428 | 2024-08-02 | 2025 | 2024 | 2024-08-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Break down | 0.82986 | 0.82986 | 0.84097 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_13 | 611.1778 |  | WTG Unscheduled Maintenance | 55006 | 611.1778
1429 | 2024-08-02 | 2025 | 2024 | 2024-08-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 4540 | Tower oscillation X level 2 | Break down | 0.55208 | 0.55208 | 0.56806 | 0 | 0.38333 | 0.38333 | Checked related error data log then reset & run the WTG. | Close | 0.014744 | O2_13 | 878.5681 |  | WTG Unscheduled Maintenance | 55006 | 878.5681
1430 | 2024-08-02 | 2025 | 2024 | 2024-08-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.13403 | 0.13403 | 0.13472 | 0 | 0.016667 | 0.016667 | Checked related error data log then reset & run the WTG. | Close | 0.00064103 | O2_13 | 38.1986 |  | WTG Unscheduled Maintenance | 55006 | 38.1986
1431 | 2024-08-02 | 2025 | 2024 | 2024-08-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.13542 | 0.13542 | 0.14306 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & run the WTG. | Close | 0.0070513 | O2_13 | 420.1847 |  | WTG Unscheduled Maintenance | 55006 | 420.1847
1432 | 2024-08-02 | 2025 | 2024 | 2024-08-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 973 | Check blade bend.mom. | Break down | 0.089583 | 0.089583 | 0.090278 | 0 | 0.016667 | 0.016667 | Checked related error data log then reset & run the WTG. | Close | 0.00064103 | O2_18 | 33.4847 |  | WTG Unscheduled Maintenance | 48218 | 33.4847
1433 | 2024-08-02 | 2025 | 2024 | 2024-08-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 973 | Check blade bend.mom. | Break down | 0.34444 | 0.34444 | 0.375 | 0 | 0.73333 | 0.73333 | Checked related error data log then reset & run the WTG. | Close | 0.028205 | O2_18 | 1473.3278 |  | WTG Unscheduled Maintenance | 48218 | 1473.3278
1434 | 2024-08-02 | 2025 | 2024 | 2024-08-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 973 | Check blade bend.mom. | Break down | 0.56667 | 0.56667 | 0.56806 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_18 | 66.9694 |  | WTG Unscheduled Maintenance | 48218 | 66.9694
1435 | 2024-08-02 | 2025 | 2024 | 2024-08-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.56736 | 0.56736 | 0.56875 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_18 | 66.9694 |  | WTG Unscheduled Maintenance | 48218 | 66.9694
1436 | 2024-08-02 | 2025 | 2024 | 2024-08-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 4540 | Tower oscillation X level 2 | Break down | 0.48403 | 0.48403 | 0.49514 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_13 | 611.1778 |  | WTG Unscheduled Maintenance | 55006 | 611.1778
1437 | 2024-08-02 | 2025 | 2024 | 2024-08-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.66944 | 0.66944 | 0.67431 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & run the WTG. | Close | 0.0044872 | O2_13 | 267.3903 |  | WTG Unscheduled Maintenance | 55006 | 267.3903
1438 | 2024-08-03 | 2025 | 2024 | 2024-08-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.65486 | 0.65486 | 0.66181 | 0 | 0.16667 | 0.16667 | Checked related error data log then reset & run the WTG. | Close | 0.0064103 | O2_05 | 407.6597 |  | WTG Unscheduled Maintenance | 58703 | 407.6597
1439 | 2024-08-03 | 2025 | 2024 | 2024-08-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.72778 | 0.72778 | 0.73125 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_01 | 199.1215 |  | WTG Unscheduled Maintenance | 57347 | 199.1215
1440 | 2024-08-03 | 2025 | 2024 | 2024-08-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.53611 | 0.53611 | 0.53958 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_01 | 199.1215 |  | WTG Unscheduled Maintenance | 57347 | 199.1215
1441 | 2024-08-03 | 2025 | 2024 | 2024-08-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.61111 | 0.61111 | 0.61736 | 0 | 0.15 | 0.15 | Checked related error data log then reset & run the WTG. | Close | 0.0057692 | O2_01 | 358.4187 |  | WTG Unscheduled Maintenance | 57347 | 358.4187
1442 | 2024-08-03 | 2025 | 2024 | 2024-08-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.61806 | 0.61806 | 0.62639 | 0 | 0.2 | 0.2 | Checked related error data log then reset & run the WTG. | Close | 0.0076923 | O2_01 | 477.8917 |  | WTG Unscheduled Maintenance | 57347 | 477.8917
1443 | 2024-08-03 | 2025 | 2024 | 2024-08-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0 | 0 | 0.01875 | 0 | 0.45 | 0.45 | Checked related error data log then reset & run the WTG. | Close | 0.017308 | O2_15 | 1044.7312 |  | WTG Unscheduled Maintenance | 55719 | 1044.7312
1444 | 2024-08-03 | 2025 | 2024 | 2024-08-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.034722 | 0.034722 | 0.097222 | 0 | 1.5 | 1.5 | Attend and ultrasonic sensor cable check, alignment done of one sensor due to rain second sensor alignment pending | Open | 0.057692 | O2_15 | 3482.4375 |  | WTG Unscheduled Maintenance | 55719 | 3482.4375
1445 | 2024-08-03 | 2025 | 2024 | 2024-08-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.17014 | 0.17014 | 0.17778 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & run the WTG. | Close | 0.0070513 | O2_15 | 425.6313 |  | WTG Unscheduled Maintenance | 55719 | 425.6313
1446 | 2024-08-03 | 2025 | 2024 | 2024-08-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.19861 | 0.19861 | 0.27222 | 0 | 1.7667 | 1.7667 | Ultrasonic second sensor alignment done than start | Open | 0.067949 | O2_15 | 4101.5375 |  | WTG Unscheduled Maintenance | 55719 | 4101.5375
1447 | 2024-08-03 | 2025 | 2024 | 2024-08-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.28958 | 0.28958 | 0.29653 | 0 | 0.16667 | 0.16667 | Checked related error data log then reset & run the WTG. | Close | 0.0064103 | O2_15 | 386.9375 |  | WTG Unscheduled Maintenance | 55719 | 386.9375
1448 | 2024-08-03 | 2025 | 2024 | 2024-08-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.32917 | 0.32917 | 0.35347 | 0 | 0.58333 | 0.58333 | Checked related error data log then reset & run the WTG. | Close | 0.022436 | O2_15 | 1354.2813 |  | WTG Unscheduled Maintenance | 55719 | 1354.2813
1449 | 2024-08-03 | 2025 | 2024 | 2024-08-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.36806 | 0.36806 | 0.55208 | 0 | 4.4167 | 4.4167 | Replaced wind measurement GIO212 mudule, complete cable removed from tray, check for damage then reroutine done of cable and start | Open | 0.16987 | O2_15 | 10253.8438 |  | WTG Unscheduled Maintenance | 55719 | 10253.8438
1450 | 2024-08-03 | 2025 | 2024 | 2024-08-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.58125 | 0.58125 | 0.61806 | 0 | 0.88333 | 0.88333 | Ultrasonic sensor alignment done than start. | Close | 0.033974 | O2_15 | 2050.7687 |  | WTG Unscheduled Maintenance | 55719 | 2050.7687
1451 | 2024-08-03 | 2025 | 2024 | 2024-08-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.88611 | 0.88611 | 0.90139 | 0 | 0.36667 | 0.36667 | Checked related error data log then reset & run the WTG. | Close | 0.014103 | O2_15 | 851.2625 |  | WTG Unscheduled Maintenance | 55719 | 851.2625
1452 | 2024-08-03 | 2025 | 2024 | 2024-08-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 64 | Max. wind speed | Break down | 0.91319 | 0.91319 | 0.92986 | 0 | 0.4 | 0.4 | Checked related error data log then reset & run the WTG. | Close | 0.015385 | O2_15 | 928.65 |  | WTG Unscheduled Maintenance | 55719 | 928.65
1453 | 2024-08-03 | 2025 | 2024 | 2024-08-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Break down | 0.035417 | 0.035417 | 0.046528 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_15 | 619.1 |  | WTG Unscheduled Maintenance | 55719 | 619.1
1454 | 2024-08-03 | 2025 | 2024 | 2024-08-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Break down | 0.49722 | 0.49722 | 0.50833 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_10 | 327.4111 |  | WTG Unscheduled Maintenance | 29467 | 327.4111
1455 | 2024-08-03 | 2025 | 2024 | 2024-08-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.55139 | 0.55139 | 0.55694 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & run the WTG. | Close | 0.0051282 | O2_10 | 163.7056 |  | WTG Unscheduled Maintenance | 29467 | 163.7056
1456 | 2024-08-03 | 2025 | 2024 | 2024-08-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.55278 | 0.55278 | 0.56875 | 0 | 0.38333 | 0.38333 | Checked related error data log then reset & run the WTG. | Close | 0.014744 | O2_20 | 847.3583 |  | WTG Unscheduled Maintenance | 53052 | 847.3583
1457 | 2024-08-03 | 2025 | 2024 | 2024-08-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 973 | Check blade bend.mom. | Break down | 0.68681 | 0.68681 | 0.69792 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_20 | 589.4667 |  | WTG Unscheduled Maintenance | 53052 | 589.4667
1458 | 2024-08-03 | 2025 | 2024 | 2024-08-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.70833 | 0.70833 | 0.70972 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_20 | 73.6833 |  | WTG Unscheduled Maintenance | 53052 | 73.6833
1459 | 2024-08-03 | 2025 | 2024 | 2024-08-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 973 | Check blade bend.mom. | Break down | 0.85 | 0.85 | 0.99931 | 0 | 3.5833 | 3.5833 | Checked related error data log then reset & run the WTG. Delay due to scada issue | Close | 0.13782 | O2_20 | 7920.9583 |  | WTG Unscheduled Maintenance | 53052 | 7920.9583
1460 | 2024-08-03 | 2025 | 2024 | 2024-08-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.093056 | 0.093056 | 0.096528 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_16 | 159.8472 |  | WTG Unscheduled Maintenance | 46036 | 159.8472
1461 | 2024-08-03 | 2025 | 2024 | 2024-08-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.45625 | 0.45625 | 0.47014 | 0 | 0.33333 | 0.33333 | Checked related error data log then reset & run the WTG. | Close | 0.012821 | O2_16 | 639.3889 |  | WTG Unscheduled Maintenance | 46036 | 639.3889
1462 | 2024-08-03 | 2025 | 2024 | 2024-08-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.64653 | 0.64653 | 0.64722 | 0 | 0.016667 | 0.016667 | Checked related error data log then reset & run the WTG. | Close | 0.00064103 | O2_16 | 31.9694 |  | WTG Unscheduled Maintenance | 46036 | 31.9694
1463 | 2024-08-03 | 2025 | 2024 | 2024-08-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.66389 | 0.66389 | 0.66528 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_16 | 63.9389 |  | WTG Unscheduled Maintenance | 46036 | 63.9389
1464 | 2024-08-03 | 2025 | 2024 | 2024-08-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down | 0.74097 | 0.74097 | 0.87847 | 0 | 3.3 | 3.3 | Attend and checked solenoid valve of hydraulic system, checked oil filter, pressure setting reverify, oil bleeding done from HU then start | Close | 0.12692 | O2_06 | 8012.2625 |  | WTG Unscheduled Maintenance | 58271 | 8012.2625
1465 | 2024-08-03 | 2025 | 2024 | 2024-08-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.58403 | 0.58403 | 0.60278 | 0 | 0.45 | 0.45 | Checked related error data log then reset & run the WTG. | Close | 0.017308 | O2_13 | 1071.3 |  | WTG Unscheduled Maintenance | 57136 | 1071.3
1466 | 2024-08-03 | 2025 | 2024 | 2024-08-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.98889 | 0.98889 | 0.99236 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_13 | 198.3889 |  | WTG Unscheduled Maintenance | 57136 | 198.3889
1467 | 2024-08-04 | 2025 | 2024 | 2024-08-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.4625 | 0.4625 | 0.48889 | 0 | 0.63333 | 0.63333 | Manual stop for O2-01 Line jumper open for project work | Close | 0.024359 | O2_09 | 1048.8 |  | WTG Breakdown Maintenance | 39744 | 1048.8
1468 | 2024-08-04 | 2025 | 2024 | 2024-08-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.4625 | 0.4625 | 0.48889 | 0 | 0.63333 | 0.63333 | Manual stop for O2-01 Line jumper open for project work | Close | 0.024359 | O2_09 | 1048.8 |  | WTG Breakdown Maintenance | 39744 | 1048.8
1469 | 2024-08-04 | 2025 | 2024 | 2024-08-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.4625 | 0.4625 | 0.48889 | 0 | 0.63333 | 0.63333 | Manual stop for O2-01 Line jumper open for project work | Close | 0.024359 | O2_09 | 1048.8 |  | WTG Breakdown Maintenance | 39744 | 1048.8
1470 | 2024-08-04 | 2025 | 2024 | 2024-08-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.4625 | 0.4625 | 0.48889 | 0 | 0.63333 | 0.63333 | Manual stop for O2-01 Line jumper open for project work | Close | 0.024359 | O2_09 | 1048.8 |  | WTG Breakdown Maintenance | 39744 | 1048.8
1471 | 2024-08-04 | 2025 | 2024 | 2024-08-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.51042 | 0.51042 | 0.52431 | 0 | 0.33333 | 0.33333 | Manual stop for Parameter update work | Close | 0.012821 | O2_05 | 521.625 |  | WTG Breakdown Maintenance | 37557 | 521.625
1472 | 2024-08-04 | 2025 | 2024 | 2024-08-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Connectivity issue | 0.51042 | 0.51042 | 0.53472 | 0 | 0.58333 | 0.58333 | After Grid resume connectivity lost , so restore the connectivity ans start the WTG | Close | 0.022436 | O2_05 | 912.8438 |  | WTG Unscheduled Maintenance | 37557 | 912.8438
1473 | 2024-08-04 | 2025 | 2024 | 2024-08-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.57917 | 0.57917 | 0.72708 | 0 | 3.55 | 3.55 | Manual stop for parameter update, after that pitch error occurred so check and found battery charging resistor defective so replace it and satrt | Close | 0.13654 | O2_05 | 5555.3062 |  | WTG Breakdown Maintenance | 37557 | 5555.3062
1474 | 2024-08-04 | 2025 | 2024 | 2024-08-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.76389 | 0.76389 | 0.76528 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_05 | 52.1625 |  | WTG Unscheduled Maintenance | 37557 | 52.1625
1475 | 2024-08-04 | 2025 | 2024 | 2024-08-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.52847 | 0.52847 | 0.53194 | 0 | 0.083333 | 0.083333 | Manual stop for Parameter update work | Close | 0.0032051 | O2_09 | 138 |  | WTG Breakdown Maintenance | 39744 | 138
1476 | 2024-08-04 | 2025 | 2024 | 2024-08-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Connectivity issue | 0.50972 | 0.50972 | 0.55278 | 0 | 1.0333 | 1.0333 | After feeder charge connectivity lost, so restore connectivity and start | Close | 0.039744 | O2_02 | 1368.2625 |  | WTG Breakdown Maintenance | 31779 | 1368.2625
1477 | 2024-08-04 | 2025 | 2024 | 2024-08-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.5875 | 0.5875 | 0.59097 | 0 | 0.083333 | 0.083333 | Manual stop for Parameter update work | Close | 0.0032051 | O2_02 | 110.3437 |  | WTG Breakdown Maintenance | 31779 | 110.3437
1478 | 2024-08-04 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 4540 | Tower oscillation X level 2 | Break down | 0.05 | 0.05 | 0.059722 | 0 | 0.23333 | 0.23333 | Checked related error data log then reset & run the WTG. | Close | 0.0089744 | O2_21 | 474.8431 |  | WTG Unscheduled Maintenance | 48841 | 474.8431
1479 | 2024-08-04 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.066667 | 0.066667 | 0.076389 | 0 | 0.23333 | 0.23333 | Checked related error data log then reset & run the WTG. | Close | 0.0089744 | O2_21 | 474.8431 |  | WTG Unscheduled Maintenance | 48841 | 474.8431
1480 | 2024-08-04 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.59583 | 0.59583 | 0.60347 | 0 | 0.18333 | 0.18333 | Manual stop for Parameter update work | Close | 0.0070513 | O2_21 | 373.091 |  | WTG Breakdown Maintenance | 48841 | 373.091
1481 | 2024-08-04 | 2025 | 2024 | 2024-08-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.51042 | 0.51042 | 0.54097 | 0 | 0.73333 | 0.73333 | Manual stop for Parameter update work | Close | 0.028205 | O2_01 | 1194.3861 |  | WTG Breakdown Maintenance | 39089 | 1194.3861
1482 | 2024-08-04 | 2025 | 2024 | 2024-08-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 64 | Max. wind speed | Break down | 0.12778 | 0.12778 | 0.13333 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & run the WTG. | Close | 0.0051282 | O2_15 | 217.6389 |  | WTG Unscheduled Maintenance | 39175 | 217.6389
1483 | 2024-08-04 | 2025 | 2024 | 2024-08-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.57431 | 0.57431 | 0.57847 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2_15 | 163.2292 |  | WTG Unscheduled Maintenance | 39175 | 163.2292
1484 | 2024-08-04 | 2025 | 2024 | 2024-08-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Break down | 0.20903 | 0.20903 | 0.22014 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_14 | 422.2444 |  | WTG Unscheduled Maintenance | 38002 | 422.2444
1485 | 2024-08-04 | 2025 | 2024 | 2024-08-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Connectivity issue | 0.51042 | 0.51042 | 0.55 | 0 | 0.95 | 0.95 | After grid resume Connectivity lost restore connectivity and start WTG. | Close | 0.036538 | O2_14 | 1504.2458 |  | WTG Breakdown Maintenance | 38002 | 1504.2458
1486 | 2024-08-04 | 2025 | 2024 | 2024-08-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.61111 | 0.61111 | 0.61458 | 0 | 0.083333 | 0.083333 | Manual stop for Parameter update work | Close | 0.0032051 | O2_14 | 131.9514 |  | WTG Breakdown Maintenance | 38002 | 131.9514
1487 | 2024-08-04 | 2025 | 2024 | 2024-08-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.51042 | 0.51042 | 0.60208 | 0 | 2.2 | 2.2 | Manual stop for Parameter update work | Close | 0.084615 | O2_14 | 3483.5167 |  | WTG Breakdown Maintenance | 38002 | 3483.5167
1488 | 2024-08-04 | 2025 | 2024 | 2024-08-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Connectivity issue | 0.51042 | 0.51042 | 0.55208 | 0 | 1 | 1 | After grid resume Connectivity lost restore connectivity and start WTG. | Close | 0.038462 | O2_14 | 1583.4167 |  | WTG Breakdown Maintenance | 38002 | 1583.4167
1489 | 2024-08-04 | 2025 | 2024 | 2024-08-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.59167 | 0.59167 | 0.59722 | 0 | 0.13333 | 0.13333 | Manual stop for Parameter update work | Close | 0.0051282 | O2_14 | 211.1222 |  | WTG Breakdown Maintenance | 38002 | 211.1222
1490 | 2024-08-04 | 2025 | 2024 | 2024-08-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Connectivity issue | 0.51042 | 0.51042 | 0.55764 | 0 | 1.1333 | 1.1333 | After grid resume Connectivity lost restore connectivity and start WTG. | Close | 0.04359 | O2_11 | 1764.175 |  | WTG Breakdown Maintenance | 37359 | 1764.175
1491 | 2024-08-04 | 2025 | 2024 | 2024-08-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.63194 | 0.63194 | 0.63889 | 0 | 0.16667 | 0.16667 | Manual stop for Parameter update work | Close | 0.0064103 | O2_11 | 259.4375 |  | WTG Breakdown Maintenance | 37359 | 259.4375
1492 | 2024-08-04 | 2025 | 2024 | 2024-08-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Connectivity issue | 0.51042 | 0.51042 | 0.55486 | 0 | 1.0667 | 1.0667 | After grid resume Connectivity lost restore connectivity and start WTG. | Close | 0.041026 | O2_10 | 1689.0667 |  | WTG Breakdown Maintenance | 38004 | 1689.0667
1493 | 2024-08-04 | 2025 | 2024 | 2024-08-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.6625 | 0.6625 | 0.66528 | 0 | 0.066667 | 0.066667 | Manual stop for Parameter update work | Close | 0.0025641 | O2_10 | 105.5667 |  | WTG Breakdown Maintenance | 38004 | 105.5667
1494 | 2024-08-04 | 2025 | 2024 | 2024-08-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 973 | Check blade bend.mom. | Break down | 0 | 0 | 0.10694 | 0 | 2.5667 | 2.5667 | Checked related error data log then reset & run the WTG. Delay due to scada issue | Close | 0.098718 | O2_20 | 4962.7569 |  | WTG Unscheduled Maintenance | 46405 | 4962.7569
1495 | 2024-08-04 | 2025 | 2024 | 2024-08-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 973 | Check blade bend.mom. | Break down | 0.18819 | 0.18819 | 0.18889 | 0 | 0.016667 | 0.016667 | Checked related error data log then reset & run the WTG. | Close | 0.00064103 | O2_20 | 32.2257 |  | WTG Unscheduled Maintenance | 46405 | 32.2257
1496 | 2024-08-04 | 2025 | 2024 | 2024-08-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 973 | Check blade bend.mom. | Break down | 0.28264 | 0.28264 | 0.28403 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_20 | 64.4514 |  | WTG Unscheduled Maintenance | 46405 | 64.4514
1497 | 2024-08-04 | 2025 | 2024 | 2024-08-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 973 | Check blade bend.mom. | Break down | 0.42153 | 0.42153 | 0.42222 | 0 | 0.016667 | 0.016667 | Checked related error data log then reset & run the WTG. | Close | 0.00064103 | O2_20 | 32.2257 |  | WTG Unscheduled Maintenance | 46405 | 32.2257
1498 | 2024-08-04 | 2025 | 2024 | 2024-08-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.64583 | 0.64583 | 0.64931 | 0 | 0.083333 | 0.083333 | Manual stop for Parameter update work | Close | 0.0032051 | O2_16 | 135.5104 |  | WTG Breakdown Maintenance | 39027 | 135.5104
1499 | 2024-08-04 | 2025 | 2024 | 2024-08-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.65417 | 0.65417 | 0.65903 | 0 | 0.11667 | 0.11667 | Manual stop for Parameter update work | Close | 0.0044872 | O2_16 | 189.7146 |  | WTG Breakdown Maintenance | 39027 | 189.7146
1500 | 2024-08-04 | 2025 | 2024 | 2024-08-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.67014 | 0.67014 | 0.675 | 0 | 0.11667 | 0.11667 | Manual stop for Parameter update work | Close | 0.0044872 | O2_06 | 217.7389 |  | WTG Breakdown Maintenance | 44792 | 217.7389
1501 | 2024-08-04 | 2025 | 2024 | 2024-08-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.67708 | 0.67708 | 0.68125 | 0 | 0.1 | 0.1 | Manual stop for Parameter update work | Close | 0.0038462 | O2_13 | 158.4292 |  | WTG Breakdown Maintenance | 38023 | 158.4292
1502 | 2024-08-04 | 2025 | 2024 | 2024-08-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.77222 | 0.77222 | 0.77778 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & run the WTG. | Close | 0.0051282 | O2_13 | 211.2389 |  | WTG Unscheduled Maintenance | 38023 | 211.2389
1503 | 2024-08-04 | 2025 | 2024 | 2024-08-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Connectivity issue | 0.51042 | 0.51042 | 0.54931 | 0 | 0.93333 | 0.93333 | After grid resume Connectivity lost restore connectivity and start WTG. | Close | 0.035897 | O2_05 | 1460.55 |  | WTG Breakdown Maintenance | 37557 | 1460.55
1504 | 2024-08-04 | 2025 | 2024 | 2024-08-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 4540 | Tower oscillation X level 2 | Break down | 0.59722 | 0.59722 | 0.60764 | 0 | 0.25 | 0.25 | Checked related error data log then reset & run the WTG. | Close | 0.0096154 | O2_05 | 391.2187 |  | WTG Unscheduled Maintenance | 37557 | 391.2187
1505 | 2024-08-04 | 2025 | 2024 | 2024-08-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.68333 | 0.68333 | 0.68819 | 0 | 0.11667 | 0.11667 | Manual stop for Parameter update work | Close | 0.0044872 | O2_05 | 182.5687 |  | WTG Breakdown Maintenance | 37557 | 182.5687
1506 | 2024-08-05 | 2025 | 2024 | 2024-08-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.64444 | 0.64444 | 0.775 | 0 | 3.1333 | 3.1333 | Attend and check related circuit than found break choper resistor failure in axis 2 so replace it with new one than reset and start WTG. | Close | 0.12051 | O2_03 | 4136.7833 |  | WTG Breakdown Maintenance | 31686 | 4136.7833
1507 | 2024-08-05 | 2025 | 2024 | 2024-08-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.63472 | 0.63472 | 0.76389 | 0 | 3.1 | 3.1 | Attend and check related ckt than found ultrasonic sensor 2 cable damage so replaced it with new one than check data of vane position angle found ok so reset and start WTG. | Close | 0.11923 | O2_15 | 3614.3417 |  | WTG Breakdown Maintenance | 27982 | 3614.3417
1508 | 2024-08-05 | 2025 | 2024 | 2024-08-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.65625 | 0.65625 | 0.66042 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2_11 | 129.8208 |  | WTG Unscheduled Maintenance | 31157 | 129.8208
1509 | 2024-08-05 | 2025 | 2024 | 2024-08-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.26528 | 0.26528 | 0.27569 | 0 | 0.25 | 0.25 | Checked related error data log then reset & run the WTG. | Close | 0.0096154 | O2_20 | 287.1458 |  | WTG Unscheduled Maintenance | 27566 | 287.1458
1510 | 2024-08-05 | 2025 | 2024 | 2024-08-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 4093 | Rel. air hum. tower base inside too high (in operation) | Break down | 0.21389 | 0.21389 | 0.21736 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_21 | 116.8333 |  | WTG Unscheduled Maintenance | 33648 | 116.8333
1511 | 2024-08-05 | 2025 | 2024 | 2024-08-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.68333 | 0.68333 | 0.68819 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & run the WTG. | Close | 0.0044872 | O2_21 | 163.5667 |  | WTG Unscheduled Maintenance | 33648 | 163.5667
1512 | 2024-08-06 | 2025 | 2024 | 2024-08-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.35556 | 0.35556 | 0.53958 | 0 | 4.4167 | 4.4167 | Manual stop for 1st month maintenance activity -DAY 1 | Close | 0.16987 | O2_02 | 7747.3854 |  | WTG Scheduled Maintenance | 42099 | 7747.3854
1513 | 2024-08-06 | 2025 | 2024 | 2024-08-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 973 | Check blade bend.mom. | Break down | 0.71875 | 0.71875 | 0.71944 | 0 | 0.016667 | 0.016667 | Checked related error data log then reset & run the WTG. | Close | 0.00064103 | O2_02 | 29.2354 |  | WTG Unscheduled Maintenance | 42099 | 29.2354
1514 | 2024-08-06 | 2025 | 2024 | 2024-08-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 2520 | Gen.speed analog<>gear.speed | Break down | 0.70417 | 0.70417 | 0.70972 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & run the WTG. | Close | 0.0051282 | O2_11 | 215.6667 |  | WTG Unscheduled Maintenance | 38820 | 215.6667
1515 | 2024-08-06 | 2025 | 2024 | 2024-08-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 551 | Pitch motor current too high | Break down | 0.53403 | 0.53403 | 0.53958 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & run the WTG. | Close | 0.0051282 | O2_10 | 210.0556 |  | WTG Unscheduled Maintenance | 37810 | 210.0556
1516 | 2024-08-06 | 2025 | 2024 | 2024-08-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.51875 | 0.51875 | 0.52292 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2_03 | 170.975 |  | WTG Unscheduled Maintenance | 41034 | 170.975
1517 | 2024-08-06 | 2025 | 2024 | 2024-08-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.045139 | 0.045139 | 0.05 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & run the WTG. | Close | 0.0044872 | O2_21 | 186.7979 |  | WTG Unscheduled Maintenance | 38427 | 186.7979
1518 | 2024-08-06 | 2025 | 2024 | 2024-08-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.33681 | 0.33681 | 0.34583 | 0 | 0.21667 | 0.21667 | Checked related error data log then reset & run the WTG. | Close | 0.0083333 | O2_21 | 346.9104 |  | WTG Unscheduled Maintenance | 38427 | 346.9104
1519 | 2024-08-06 | 2025 | 2024 | 2024-08-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.51875 | 0.51875 | 0.52014 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_16 | 4.6833 |  | WTG Unscheduled Maintenance | 3372 | 4.6833
1520 | 2024-08-06 | 2025 | 2024 | 2024-08-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.51597 | 0.51597 | 0.52222 | 0 | 0.15 | 0.15 | Checked related error data log then reset & run the WTG. | Close | 0.0057692 | O2_18 | 225.0562 |  | WTG Unscheduled Maintenance | 36009 | 225.0562
1521 | 2024-08-07 | 2025 | 2024 | 2024-08-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3380 | Coolant temp. high | Road issue | 0.44722 | 0.44722 | 0.99999 | 0 | 13.2664 | 13.2664 | Due to WTG road not accessible. Once road clear will attend the same | Close | 0.51025 | O2_05 | 23398.5934 |  | WTG Unscheduled Maintenance | 42330 | 23398.5934
1522 | 2024-08-07 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.033333 | 0.033333 | 0.036111 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & run the WTG. | Close | 0.0025641 | O2_18 | 110.0389 |  | WTG Unscheduled Maintenance | 39614 | 110.0389
1523 | 2024-08-07 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.32222 | 0.32222 | 0.32778 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & run the WTG. | Close | 0.0051282 | O2_18 | 220.0778 |  | WTG Unscheduled Maintenance | 39614 | 220.0778
1524 | 2024-08-07 | 2025 | 2024 | 2024-08-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.60556 | 0.60556 | 0.60972 | 0 | 0.1 | 0.1 | Manual stop for software update work. | Close | 0.0038462 | O2_11 | 161.6708 |  | WTG Breakdown Maintenance | 38801 | 161.6708
1525 | 2024-08-07 | 2025 | 2024 | 2024-08-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Break down | 0.10764 | 0.10764 | 0.11875 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_10 | 454.5667 |  | WTG Unscheduled Maintenance | 40911 | 454.5667
1526 | 2024-08-07 | 2025 | 2024 | 2024-08-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.61528 | 0.61528 | 0.62361 | 0 | 0.2 | 0.2 | Manual stop for software update work. | Close | 0.0076923 | O2_20 | 326.4417 |  | WTG Breakdown Maintenance | 39173 | 326.4417
1527 | 2024-08-07 | 2025 | 2024 | 2024-08-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.71111 | 0.71111 | 0.71944 | 0 | 0.2 | 0.2 | Checked related error data log then reset & run the WTG. | Close | 0.0076923 | O2_06 | 342.425 |  | WTG Unscheduled Maintenance | 41091 | 342.425
1528 | 2024-08-07 | 2025 | 2024 | 2024-08-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.30208 | 0.30208 | 0.30417 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_18 | 82.5292 |  | WTG Unscheduled Maintenance | 39614 | 82.5292
1529 | 2024-08-07 | 2025 | 2024 | 2024-08-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.46389 | 0.46389 | 0.68194 | 0 | 5.2333 | 5.2333 | attend for repeted pitch error so check related cicuit and measure copper resister value in axis one so found resistor was faulty so replace it and also check can cable and its connection and done properly than reset and start WTG. | Close | 0.20128 | O2_18 | 8638.0528 |  | WTG Breakdown Maintenance | 39614 | 8638.0528
1521 | 2024-08-08 | 2025 | 2024 | 2024-08-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3380 | Coolant temp. high | Road issue | 0 | 0 | 0.99999 | 0 | 23.9997 | 23.9997 | Due to WTG road not accessible. Once road clear will attend the same | Open | 0.92307 | O2_05 | 33527.6119 |  | WTG Unscheduled Maintenance | 33528 | 33527.6119
1522 | 2024-08-08 | 2025 | 2024 | 2024-08-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3370 | Coolant press. low | Break down | 0.63194 | 0.63194 | 0.65556 | 0 | 0.56667 | 0.56667 | attend and check circuit and found pressure switch connection loose so retight proper than reset and start Wtg. | Close | 0.021795 | O2_09 | 797.6778 |  | WTG Unscheduled Maintenance | 33784 | 797.6778
1523 | 2024-08-08 | 2025 | 2024 | 2024-08-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.45903 | 0.45903 | 0.57361 | 0 | 2.75 | 2.75 | attend for repeted error so check related cicuit and than found altrasonic sensor 1 cable not working properly so replace it after both sensor alignment is done properly than check data of van position angle found ok than reset and start WTG. | Close | 0.10577 | O2_11 | 3544.1771 |  | WTG Breakdown Maintenance | 30931 | 3544.1771
1524 | 2024-08-08 | 2025 | 2024 | 2024-08-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.58194 | 0.58194 | 0.64306 | 0 | 1.4667 | 1.4667 | attend for repeted error so check related cicuit and than found altrasonic sensor 1 cable not working properly so replace it after both sensor alignment is done properly than check data of van position angle found ok than reset and start WTG. | Close | 0.05641 | O2_11 | 1890.2278 |  | WTG Breakdown Maintenance | 30931 | 1890.2278
1525 | 2024-08-08 | 2025 | 2024 | 2024-08-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.25903 | 0.25903 | 0.26042 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_11 | 42.9597 |  | WTG Unscheduled Maintenance | 30931 | 42.9597
1526 | 2024-08-08 | 2025 | 2024 | 2024-08-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.46944 | 0.46944 | 0.64861 | 0 | 4.3 | 4.3 | attend for repeted error so check related cicuit and check converter can cable and laying between converter to BOB and also done software upadate in HUB controller than start WTG. | Close | 0.16538 | O2_11 | 5541.8042 |  | WTG Breakdown Maintenance | 30931 | 5541.8042
1527 | 2024-08-08 | 2025 | 2024 | 2024-08-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.84514 | 0.84514 | 0.85069 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & run the WTG. | Close | 0.0051282 | O2_11 | 171.8389 |  | WTG Unscheduled Maintenance | 30931 | 171.8389
1528 | 2024-08-08 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.58056 | 0.58056 | 0.58194 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_18 | 42.8139 |  | WTG Unscheduled Maintenance | 30826 | 42.8139
1529 | 2024-08-08 | 2025 | 2024 | 2024-08-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Break down | 0.75903 | 0.75903 | 0.77014 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_10 | 273.1222 |  | WTG Unscheduled Maintenance | 24581 | 273.1222
1521 | 2024-08-08 | 2025 | 2024 | 2024-08-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 973 | Check blade bend.mom. | Break down | 0.28194 | 0.28194 | 0.28264 | 0 | 0.016667 | 0.016667 | Checked related error data log then reset & run the WTG. | Close | 0.00064103 | O2_20 | 21.1028 |  | WTG Unscheduled Maintenance | 30388 | 21.1028
1522 | 2024-08-08 | 2025 | 2024 | 2024-08-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.89236 | 0.89236 | 0.89375 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_18 | 42.8139 |  | WTG Unscheduled Maintenance | 30826 | 42.8139
1525 | 2024-08-09 | 2025 | 2024 | 2024-08-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3370 | Coolant press. low | Break down | 0.63403 | 0.63403 | 0.71389 | 0 | 1.9167 | 1.9167 | attend and check error related circuit than found collent pressure low so top up collent than reset and start WTG. | Close | 0.073718 | O2_09 | 2794.6597 |  | WTG Unscheduled Maintenance | 34994 | 2794.6597
1526 | 2024-08-09 | 2025 | 2024 | 2024-08-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.75972 | 0.75972 | 0.77431 | 0 | 0.35 | 0.35 | Checked related error data log then reset & run the WTG. | Close | 0.013462 | O2_09 | 510.3292 |  | WTG Unscheduled Maintenance | 34994 | 510.3292
1527 | 2024-08-09 | 2025 | 2024 | 2024-08-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 551 | Pitch motor current too high | Break down | 0.91736 | 0.91736 | 0.92778 | 0 | 0.25 | 0.25 | Checked related error data log then reset & run the WTG. | Close | 0.0096154 | O2_25 | 389.0417 |  | WTG Unscheduled Maintenance | 37348 | 389.0417
1528 | 2024-08-09 | 2025 | 2024 | 2024-08-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 47 | Max. windspeed BP50 | Break down | 0.93194 | 0.93194 | 0.93333 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_25 | 51.8722 |  | WTG Unscheduled Maintenance | 37348 | 51.8722
1529 | 2024-08-09 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.42569 | 0.42569 | 0.42708 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_18 | 45.2625 |  | WTG Unscheduled Maintenance | 32589 | 45.2625
1521 | 2024-08-09 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 2520 | Gen.speed analog<>gear.speed | Break down | 0.87014 | 0.87014 | 0.88125 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_18 | 362.1 |  | WTG Unscheduled Maintenance | 32589 | 362.1
1522 | 2024-08-09 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.89028 | 0.89028 | 0.89514 | 0 | 0.11667 | 0.11667 | manual stop for apply soft reboot due to tower resonence error occurred so after reboot done than reset and start WTG. | Close | 0.0044872 | O2_18 | 158.4188 |  | WTG Breakdown Maintenance | 32589 | 158.4188
1525 | 2024-08-09 | 2025 | 2024 | 2024-08-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.34722 | 0.34722 | 0.34931 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_11 | 69.7 |  | WTG Unscheduled Maintenance | 33456 | 69.7
1526 | 2024-08-09 | 2025 | 2024 | 2024-08-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.58958 | 0.58958 | 0.59583 | 0 | 0.15 | 0.15 | manual stop for apply soft reboot due to rottor break pad temp error occurred so after reboot done than reset and start WTG. | Close | 0.0057692 | O2_11 | 209.1 |  | WTG Unscheduled Maintenance | 33456 | 209.1
1527 | 2024-08-09 | 2025 | 2024 | 2024-08-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.61667 | 0.61667 | 0.73194 | 0 | 2.7667 | 2.7667 | Attend and chcek related circuit than found temp.sensor connection was loose so retight properly than reset and start WTG. | Close | 0.10641 | O2_11 | 3856.7333 |  | WTG Unscheduled Maintenance | 33456 | 3856.7333
1528 | 2024-08-09 | 2025 | 2024 | 2024-08-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.5875 | 0.5875 | 0.76319 | 0 | 4.2167 | 4.2167 | Manual stop for power curve inspection workl so check altrasonic sensor alignment than done proper allignment and also chcek north position than correct it proper position than reset and start WTG.(Blade calibration check pending due to high wind.) | Close | 0.16218 | O2_11 | 5878.0333 |  | WTG Breakdown Maintenance | 33456 | 5878.0333
1529 | 2024-08-09 | 2025 | 2024 | 2024-08-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.77431 | 0.77431 | 0.79236 | 0 | 0.43333 | 0.43333 | Manual stop for power curve inspection workl so check altrasonic sensor alignment than done proper allignment and also chcek north position than correct it proper position than reset and start WTG.(Blade calibration check pending due to high wind.) | Close | 0.016667 | O2_11 | 604.0667 |  | WTG Breakdown Maintenance | 33456 | 604.0667
1521 | 2024-08-09 | 2025 | 2024 | 2024-08-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.20764 | 0.20764 | 0.21181 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2_06 | 128.3167 |  | WTG Unscheduled Maintenance | 30796 | 128.3167
1522 | 2024-08-09 | 2025 | 2024 | 2024-08-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.40833 | 0.40833 | 0.40903 | 0 | 0.016667 | 0.016667 | Checked related error data log then reset & run the WTG. | Close | 0.00064103 | O2_06 | 21.3861 |  | WTG Unscheduled Maintenance | 30796 | 21.3861
1525 | 2024-08-09 | 2025 | 2024 | 2024-08-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 551 | Pitch motor current too high | Break down | 0.92222 | 0.92222 | 0.93333 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_05 | 386.5333 |  | WTG Unscheduled Maintenance | 34788 | 386.5333
1526 | 2024-08-09 | 2025 | 2024 | 2024-08-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3380 | Coolant temp. high | Road issue | 0 | 0 | 0.99999 | 0 | 23.9997 | 23.9997 | Due to WTG road not accessible. Once road clear will attend the same | Open | 0.92307 | O2_05 | 34787.5974 |  | WTG Unscheduled Maintenance | 34788 | 34787.5974
1525 | 2024-08-10 | 2025 | 2024 | 2024-08-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Break down | 0.50903 | 0.50903 | 0.51736 | 0 | 0.2 | 0.2 | after grid resume Wtg in error so Checked related error data log then reset & run the WTG. | Close | 0.0076923 | O2_24 | 370.9667 |  | WTG Unscheduled Maintenance | 44516 | 370.9667
1526 | 2024-08-10 | 2025 | 2024 | 2024-08-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.66667 | 0.66667 | 0.79236 | 0 | 3.0167 | 3.0167 | attend and check related circuit and found chopper resister failure in axiss no 1 so replace it than reset and start WTG. | Close | 0.11603 | O2_24 | 5595.4139 |  | WTG Unscheduled Maintenance | 44516 | 5595.4139
1527 | 2024-08-10 | 2025 | 2024 | 2024-08-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3380 | Coolant temp. high | Road issue | 0 | 0 | 0.49583 | 0 | 11.9 | 11.9 | Due to WTG road not accessible. Once road clear will attend the same | Open | 0.45769 | O2_05 | 18671.5958 |  | WTG Unscheduled Maintenance | 37657 | 18671.5958
1528 | 2024-08-10 | 2025 | 2024 | 2024-08-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3380 | Coolant temp. high | Road issue | 0.50833 | 0.50833 | 0.99999 | 0 | 11.7997 | 11.7997 | Due to WTG road not accessible. Once road clear will attend the same | Open | 0.45384 | O2_05 | 18514.2558 |  | WTG Unscheduled Maintenance | 37657 | 18514.2558
1529 | 2024-08-10 | 2025 | 2024 | 2024-08-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Break down | 0.51736 | 0.51736 | 0.51875 | 0 | 0.033333 | 0.033333 | after grid resume Wtg in error so Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_05 | 52.3014 |  | WTG Unscheduled Maintenance | 37657 | 52.3014
1530 | 2024-08-10 | 2025 | 2024 | 2024-08-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Break down | 0.54167 | 0.54167 | 0.56597 | 0 | 0.58333 | 0.58333 | Attend and check related circuit than nothing found abnormal than apply hard rebbot of ups than reset and start WTG | Close | 0.022436 | O2_05 | 915.2743 |  | WTG Unscheduled Maintenance | 37657 | 915.2743
1531 | 2024-08-10 | 2025 | 2024 | 2024-08-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 47 | Max. windspeed BP50 | Break down | 0.57292 | 0.57292 | 0.58403 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_05 | 418.4111 |  | WTG Unscheduled Maintenance | 37657 | 418.4111
1532 | 2024-08-10 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.17917 | 0.17917 | 0.18125 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_18 | 81.4583 |  | WTG Unscheduled Maintenance | 39100 | 81.4583
1533 | 2024-08-10 | 2025 | 2024 | 2024-08-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.50833 | 0.50833 | 0.5125 | 0 | 0.1 | 0.1 | after grid resume Wtg in error so Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2_03 | 154.0708 |  | WTG Unscheduled Maintenance | 36977 | 154.0708
1534 | 2024-08-10 | 2025 | 2024 | 2024-08-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.50833 | 0.50833 | 0.51319 | 0 | 0.11667 | 0.11667 | after grid resume Wtg in error so Checked related error data log then reset & run the WTG. | Close | 0.0044872 | O2_11 | 186.8368 |  | WTG Unscheduled Maintenance | 38435 | 186.8368
1535 | 2024-08-10 | 2025 | 2024 | 2024-08-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Break down | 0.50833 | 0.50833 | 0.51319 | 0 | 0.11667 | 0.11667 | after grid resume Wtg in error so Checked related error data log then reset & run the WTG. | Close | 0.0044872 | O2_11 | 186.8368 |  | WTG Unscheduled Maintenance | 38435 | 186.8368
1536 | 2024-08-10 | 2025 | 2024 | 2024-08-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.67361 | 0.67361 | 0.68472 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_11 | 427.0556 |  | WTG Unscheduled Maintenance | 38435 | 427.0556
1537 | 2024-08-10 | 2025 | 2024 | 2024-08-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.25486 | 0.25486 | 0.25625 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_11 | 53.3819 |  | WTG Unscheduled Maintenance | 38435 | 53.3819
1538 | 2024-08-10 | 2025 | 2024 | 2024-08-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.50833 | 0.50833 | 0.51389 | 0 | 0.13333 | 0.13333 | after grid resume Wtg in error so Checked related error data log then reset & run the WTG. | Close | 0.0051282 | O2_11 | 213.5278 |  | WTG Unscheduled Maintenance | 38435 | 213.5278
1539 | 2024-08-10 | 2025 | 2024 | 2024-08-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Break down | 0.51319 | 0.51319 | 0.54236 | 0 | 0.7 | 0.7 | Attend and check related circuit than nothing found abnormal than apply hard rebbot of ups than reset and start WTG | Close | 0.026923 | O2_11 | 1121.0208 |  | WTG Unscheduled Maintenance | 38435 | 1121.0208
1540 | 2024-08-10 | 2025 | 2024 | 2024-08-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Break down | 0.50833 | 0.50833 | 0.51806 | 0 | 0.23333 | 0.23333 | after grid resume Wtg in error so Checked related error data log then reset & run the WTG. | Close | 0.0089744 | O2_10 | 412.4653 |  | WTG Unscheduled Maintenance | 42425 | 412.4653
1541 | 2024-08-10 | 2025 | 2024 | 2024-08-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 550 | Pitch current asymmetry | Break down | 0.82708 | 0.82708 | 0.83333 | 0 | 0.15 | 0.15 | Checked related error data log then reset & run the WTG. | Close | 0.0057692 | O2_10 | 265.1563 |  | WTG Unscheduled Maintenance | 42425 | 265.1563
1542 | 2024-08-10 | 2025 | 2024 | 2024-08-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.031944 | 0.031944 | 0.036111 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2_06 | 170.9458 |  | WTG Unscheduled Maintenance | 41027 | 170.9458
1543 | 2024-08-10 | 2025 | 2024 | 2024-08-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.0875 | 0.0875 | 0.10764 | 0 | 0.48333 | 0.48333 | Checked related error data log then reset & run the WTG. | Close | 0.01859 | O2_06 | 826.2382 |  | WTG Unscheduled Maintenance | 41027 | 826.2382
1544 | 2024-08-10 | 2025 | 2024 | 2024-08-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.66319 | 0.66319 | 0.66458 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_15 | 54.8792 |  | WTG Unscheduled Maintenance | 39513 | 54.8792
1545 | 2024-08-10 | 2025 | 2024 | 2024-08-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.70208 | 0.70208 | 0.70347 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_15 | 54.8792 |  | WTG Unscheduled Maintenance | 39513 | 54.8792
1546 | 2024-08-10 | 2025 | 2024 | 2024-08-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 2520 | Gen.speed analog<>gear.speed | Break down | 0.66181 | 0.66181 | 0.66389 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_18 | 81.4583 |  | WTG Unscheduled Maintenance | 39100 | 81.4583
1547 | 2024-08-10 | 2025 | 2024 | 2024-08-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.94375 | 0.94375 | 0.95347 | 0 | 0.23333 | 0.23333 | Checked related error data log then reset & run the WTG. | Close | 0.0089744 | O2_18 | 380.1389 |  | WTG Unscheduled Maintenance | 39100 | 380.1389
1548 | 2024-08-10 | 2025 | 2024 | 2024-08-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Break down | 0.50833 | 0.50833 | 0.54097 | 0 | 0.78333 | 0.78333 | Attend and check related circuit than nothing found abnormal than apply soft rebbot of ups than reset and start WTG | Close | 0.030128 | O2_05 | 1229.0826 |  | WTG Unscheduled Maintenance | 37657 | 1229.0826
1549 | 2024-08-11 | 2025 | 2024 | 2024-08-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 1630 | Disc filter adaption implausible | Break down | 0.53819 | 0.53819 | 0.55 | 0 | 0.28333 | 0.28333 | Checked related error data log then reset & run the WTG. | Close | 0.010897 | O2_24 | 593.9611 |  | WTG Unscheduled Maintenance | 50312 | 593.9611
1550 | 2024-08-11 | 2025 | 2024 | 2024-08-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.68333 | 0.68333 | 0.6875 | 0 | 0.1 | 0.1 | Check error data than nothing found Abnormal than apply soft reboot than reset and start WTG. | Close | 0.0038462 | O2_24 | 209.6333 |  | WTG Unscheduled Maintenance | 50312 | 209.6333
1551 | 2024-08-11 | 2025 | 2024 | 2024-08-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3380 | Coolant temp. high | Road issue | 0 | 0 | 0.99999 | 0 | 23.9997 | 23.9997 | Due to WTG road not accessible. Once road clear will attend the same | Open | 0.92307 | O2_05 | 49183.4307 |  | WTG Unscheduled Maintenance | 49184 | 49183.4307
1552 | 2024-08-11 | 2025 | 2024 | 2024-08-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 4540 | Tower oscillation X level 2 | Break down | 0.4375 | 0.4375 | 0.44861 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_25 | 581.9778 |  | WTG Unscheduled Maintenance | 52378 | 581.9778
1553 | 2024-08-11 | 2025 | 2024 | 2024-08-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.44931 | 0.44931 | 0.45069 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_15 | 68.1403 |  | WTG Unscheduled Maintenance | 49061 | 68.1403
1554 | 2024-08-11 | 2025 | 2024 | 2024-08-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.50278 | 0.50278 | 0.5125 | 0 | 0.23333 | 0.23333 | Checked related error data log then reset & run the WTG. | Close | 0.0089744 | O2_13 | 462.1944 |  | WTG Unscheduled Maintenance | 47540 | 462.1944
1555 | 2024-08-11 | 2025 | 2024 | 2024-08-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 1600 | High gear speed | Break down | 0.79722 | 0.79722 | 0.81111 | 0 | 0.33333 | 0.33333 | Check error data than nothing found Abnormal than apply soft reboot than reset and start WTG. | Close | 0.012821 | O2_13 | 660.2778 |  | WTG Unscheduled Maintenance | 47540 | 660.2778
1556 | 2024-08-11 | 2025 | 2024 | 2024-08-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Break down | 0.40903 | 0.40903 | 0.42014 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_11 | 512.3222 |  | WTG Unscheduled Maintenance | 46109 | 512.3222
1557 | 2024-08-11 | 2025 | 2024 | 2024-08-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.42569 | 0.42569 | 0.42847 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & run the WTG. | Close | 0.0025641 | O2_11 | 128.0806 |  | WTG Unscheduled Maintenance | 46109 | 128.0806
1558 | 2024-08-11 | 2025 | 2024 | 2024-08-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 4540 | Tower oscillation X level 2 | Break down | 0.58611 | 0.58611 | 0.59653 | 0 | 0.25 | 0.25 | Checked related error data log then reset & run the WTG. | Close | 0.0096154 | O2_10 | 528.7292 |  | WTG Unscheduled Maintenance | 50758 | 528.7292
1559 | 2024-08-11 | 2025 | 2024 | 2024-08-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 4555 | Tower accel. difference | Auto reset | 0.90972 | 0.90972 | 0.91389 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2_10 | 211.4917 |  | WTG Unscheduled Maintenance | 50758 | 211.4917
1560 | 2024-08-11 | 2025 | 2024 | 2024-08-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Auto reset | 0.4375 | 0.4375 | 0.43819 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | O2_20 | 30.7958 |  | WTG Unscheduled Maintenance | 44346 | 30.7958
1561 | 2024-08-11 | 2025 | 2024 | 2024-08-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 1600 | High gear speed | Break down | 0.43889 | 0.43889 | 0.45417 | 0 | 0.36667 | 0.36667 | Check error data than nothing found Abnormal than apply soft reboot than reset and start WTG. | Close | 0.014103 | O2_01 | 700.1653 |  | WTG Unscheduled Maintenance | 45829 | 700.1653
1562 | 2024-08-11 | 2025 | 2024 | 2024-08-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.43889 | 0.43889 | 0.44028 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_16 | 64.8236 |  | WTG Unscheduled Maintenance | 46673 | 64.8236
1563 | 2024-08-12 | 2025 | 2024 | 2024-08-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.75694 | 0.75694 | 0.75972 | 0 | 0.066667 | 0.066667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.0025641 | O2_16 | 88.2528 |  | WTG Unscheduled Maintenance | 31771 | 88.2528
1564 | 2024-08-12 | 2025 | 2024 | 2024-08-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3380 | Coolant temp. high | Road issue | 0 | 0 | 0.63819 | 0 | 15.3167 | 15.3167 | Due to WTG road not accessible. Once road clear will attend the same | Open | 0.5891 | O2_05 | 14564.2354 |  | WTG Unscheduled Maintenance | 22821 | 14564.2354
1565 | 2024-08-12 | 2025 | 2024 | 2024-08-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3380 | Coolant temp. high | Road issue | 0.75694 | 0.75694 | 1899-12-31 | 0 | 5.8333 | 5.8333 | Due to WTG road not accessible. Once road clear will attend the same | Open | 0.22436 | O2_05 | 5546.7708 |  | WTG Unscheduled Maintenance | 22821 | 5546.7708
1566 | 2024-08-12 | 2025 | 2024 | 2024-08-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.4125 | 0.4125 | 0.63819 | 0 | 5.4167 | 5.4167 | Manual stop for 1st month maintenance activity(Day-2) | Close | 0.20833 | O2_02 | 0 |  | WTG Scheduled Maintenance | 0 | 0
1567 | 2024-08-12 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Auto reset | 0.39653 | 0.39653 | 0.39861 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2_21 | 69.5 |  | WTG Unscheduled Maintenance | 33360 | 69.5
1568 | 2024-08-12 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.82778 | 0.82778 | 0.85139 | 0 | 0.56667 | 0.56667 | Checked related error data log then reset & run the WTG. | Close | 0.021795 | O2_21 | 787.6667 |  | WTG Unscheduled Maintenance | 33360 | 787.6667
1569 | 2024-08-12 | 2025 | 2024 | 2024-08-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.50903 | 0.50903 | 0.63819 | 0 | 3.1 | 3.1 | Manual stop for ladder replacement work. | Close | 0.11923 | O2_03 | 4000.0333 |  | WTG Breakdown Maintenance | 30968 | 4000.0333
1570 | 2024-08-12 | 2025 | 2024 | 2024-08-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.75694 | 0.75694 | 0.76389 | 0 | 0.16667 | 0.16667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.0064103 | O2_03 | 215.0556 |  | WTG Unscheduled Maintenance | 30968 | 215.0556
1571 | 2024-08-12 | 2025 | 2024 | 2024-08-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.75694 | 0.75694 | 0.76042 | 0 | 0.083333 | 0.083333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.0032051 | O2_15 | 100.309 |  | WTG Unscheduled Maintenance | 28889 | 100.309
1572 | 2024-08-12 | 2025 | 2024 | 2024-08-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.75694 | 0.75694 | 0.76111 | 0 | 0.1 | 0.1 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.0038462 | O2_12 | 132.2042 |  | WTG Unscheduled Maintenance | 31729 | 132.2042
1573 | 2024-08-12 | 2025 | 2024 | 2024-08-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.75694 | 0.75694 | 0.76181 | 0 | 0.11667 | 0.11667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.0044872 | O2_11 | 145.0847 |  | WTG Unscheduled Maintenance | 29846 | 145.0847
1574 | 2024-08-12 | 2025 | 2024 | 2024-08-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.75694 | 0.75694 | 0.76736 | 0 | 0.25 | 0.25 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.0096154 | O2_11 | 310.8958 |  | WTG Unscheduled Maintenance | 29846 | 310.8958
1575 | 2024-08-12 | 2025 | 2024 | 2024-08-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.75694 | 0.75694 | 0.79861 | 0 | 1 | 1 | Attend for grid resume Wtg in error so Checked related error data log then apply hard reboot reset & start the WTG. | Close | 0.038462 | O2_11 | 1243.5833 |  | WTG Unscheduled Maintenance | 29846 | 1243.5833
1576 | 2024-08-12 | 2025 | 2024 | 2024-08-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.75694 | 0.75694 | 0.76319 | 0 | 0.15 | 0.15 | Checked related error data log then reset & run the WTG. | Close | 0.0057692 | O2_11 | 186.5375 |  | WTG Unscheduled Maintenance | 29846 | 186.5375
1577 | 2024-08-12 | 2025 | 2024 | 2024-08-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.088889 | 0.088889 | 0.13194 | 0 | 1.0333 | 1.0333 | Checked related error data log then reset & run the WTG. | Close | 0.039744 | O2_06 | 1319.4806 |  | WTG Unscheduled Maintenance | 30646 | 1319.4806
1578 | 2024-08-12 | 2025 | 2024 | 2024-08-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.39444 | 0.39444 | 0.40347 | 0 | 0.21667 | 0.21667 | Checked related error data log then reset & run the WTG. | Close | 0.0083333 | O2_06 | 276.6653 |  | WTG Unscheduled Maintenance | 30646 | 276.6653
1579 | 2024-08-12 | 2025 | 2024 | 2024-08-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.69028 | 0.69028 | 0.69792 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & run the WTG. | Close | 0.0070513 | O2_06 | 234.1014 |  | WTG Unscheduled Maintenance | 30646 | 234.1014
1580 | 2024-08-12 | 2025 | 2024 | 2024-08-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.75694 | 0.75694 | 0.76111 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2_06 | 127.6917 |  | WTG Unscheduled Maintenance | 30646 | 127.6917
1580 | 2024-08-13 | 2025 | 2024 | 2024-08-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.37778 | 0.37778 | 0.62986 | 0 | 6.05 | 6.05 | Manual stop for 1st month maintenance activity(Day-1) | Close | 0.23269 | O2_09 | 3110.9604 |  | WTG Scheduled Maintenance | 12341 | 3110.9604
1580 | 2024-08-13 | 2025 | 2024 | 2024-08-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3380 | Coolant temp. high | Road issue | 0 | 0 | 0.62986 | 0 | 15.1167 | 15.1167 | Due to WTG road not accessible. Once road clear will attend the same . | Open | 0.58141 | O2_05 | 11081.1465 |  | WTG Unscheduled Maintenance | 17593 | 11081.1465
1580 | 2024-08-13 | 2025 | 2024 | 2024-08-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3380 | Coolant temp. high | Road issue | 0.73333 | 0.73333 | 1899-12-31 | 0 | 6.4 | 6.4 | Due to WTG road not accessible. Once road clear will attend the same. | Open | 0.24615 | O2_05 | 4691.4667 |  | WTG Unscheduled Maintenance | 17593 | 4691.4667
1580 | 2024-08-13 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.09375 | 0.09375 | 0.10417 | 0 | 0.25 | 0.25 | Checked related error data log then reset & run the WTG. | Close | 0.0096154 | O2_21 | 215.125 |  | WTG Unscheduled Maintenance | 20652 | 215.125
1580 | 2024-08-13 | 2025 | 2024 | 2024-08-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.45694 | 0.45694 | 0.62986 | 0 | 4.15 | 4.15 | Manual stop for ladder replacement work. | Close | 0.15962 | O2_03 | 2521.8167 |  | WTG Breakdown Maintenance | 14584 | 2521.8167
1580 | 2024-08-13 | 2025 | 2024 | 2024-08-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.73472 | 0.73472 | 0.7375 | 0 | 0.066667 | 0.066667 | after grid resume Wtg start then battery Test time error is accurs so Checked related error data log then reset & start the WTG. | Close | 0.0025641 | O2_12 | 44.2222 |  | WTG Unscheduled Maintenance | 15920 | 44.2222
1580 | 2024-08-13 | 2025 | 2024 | 2024-08-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Auto reset | 0.61389 | 0.61389 | 0.61736 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0032051 | O2_11 | 49.8715 |  | WTG Unscheduled Maintenance | 14363 | 49.8715
1580 | 2024-08-13 | 2025 | 2024 | 2024-08-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.84028 | 0.84028 | 0.84375 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_11 | 49.8715 |  | WTG Unscheduled Maintenance | 14363 | 49.8715
1580 | 2024-08-13 | 2025 | 2024 | 2024-08-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.47778 | 0.47778 | 0.60625 | 0 | 3.0833 | 3.0833 | attend for check PC deviation work. | Close | 0.11859 | O2_11 | 1845.2465 |  | WTG Breakdown Maintenance | 14363 | 1845.2465
1580 | 2024-08-13 | 2025 | 2024 | 2024-08-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.73333 | 0.73333 | 0.73681 | 0 | 0.083333 | 0.083333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.0032051 | O2_11 | 49.8715 |  | WTG Unscheduled Maintenance | 14363 | 49.8715
1580 | 2024-08-13 | 2025 | 2024 | 2024-08-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.825 | 0.825 | 0.83264 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & run the WTG. | Close | 0.0070513 | O2_06 | 152.075 |  | WTG Unscheduled Maintenance | 19908 | 152.075
1580 | 2024-08-13 | 2025 | 2024 | 2024-08-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.73333 | 0.73333 | 0.73819 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & run the WTG. | Close | 0.0044872 | O2_06 | 96.775 |  | WTG Unscheduled Maintenance | 19908 | 96.775
1581 | 2024-08-14 | 2025 | 2024 | 2024-08-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.41944 | 0.41944 | 0.62917 | 0 | 5.0333 | 5.0333 | Manual stop for 1st month maintenance activity(Day-2) | Close | 0.19359 | O2_09 | 3072.2208 |  | WTG Scheduled Maintenance | 14649 | 3072.2208
1582 | 2024-08-14 | 2025 | 2024 | 2024-08-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3380 | Coolant temp. high | Road issue | 0 | 0 | 1899-12-31 | 0 | 24 | 24 | Due to WTG road not accessible. Once road clear will attend the same . | Open | 0.92308 | O2_05 | 17870 |  | WTG Unscheduled Maintenance | 17870 | 17870
1583 | 2024-08-14 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.30625 | 0.30625 | 0.30764 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_05 | 24.8194 |  | WTG Unscheduled Maintenance | 17870 | 24.8194
1584 | 2024-08-14 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.41181 | 0.41181 | 0.41389 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_21 | 29.1687 |  | WTG Unscheduled Maintenance | 14001 | 29.1687
1585 | 2024-08-14 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.75556 | 0.75556 | 0.75694 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_21 | 19.4458 |  | WTG Unscheduled Maintenance | 14001 | 19.4458
1586 | 2024-08-14 | 2025 | 2024 | 2024-08-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.086806 | 0.086806 | 0.10417 | 0 | 0.41667 | 0.41667 | Checked related error data log then reset & run the WTG. | Close | 0.016026 | O2_12 | 251.3368 |  | WTG Unscheduled Maintenance | 14477 | 251.3368
1587 | 2024-08-14 | 2025 | 2024 | 2024-08-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.071528 | 0.071528 | 0.075 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_16 | 53.6701 |  | WTG Unscheduled Maintenance | 15457 | 53.6701
1588 | 2024-08-14 | 2025 | 2024 | 2024-08-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.38333 | 0.38333 | 0.38681 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_16 | 53.6701 |  | WTG Unscheduled Maintenance | 15457 | 53.6701
1589 | 2024-08-14 | 2025 | 2024 | 2024-08-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.15 | 0.15 | 0.15208 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_06 | 29.7562 |  | WTG Unscheduled Maintenance | 14283 | 29.7562
1590 | 2024-08-14 | 2025 | 2024 | 2024-08-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.39236 | 0.39236 | 0.39375 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_06 | 19.8375 |  | WTG Unscheduled Maintenance | 14283 | 19.8375
1591 | 2024-08-15 | 2025 | 2024 | 2024-08-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3380 | Coolant temp. high | Road issue | 0 | 0 | 1899-12-31 | 0 | 24 | 24 | Due to WTG road not accessible. Once road clear will attend the same . | Close | 0.92308 | O2_05 | 21561 |  | WTG Unscheduled Maintenance | 21561 | 21561
1592 | 2024-08-15 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.1125 | 0.1125 | 0.11806 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & run the WTG. | Close | 0.0051282 | O2_21 | 120.1167 |  | WTG Unscheduled Maintenance | 21621 | 120.1167
1593 | 2024-08-15 | 2025 | 2024 | 2024-08-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.38194 | 0.38194 | 0.38403 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_11 | 38.4646 |  | WTG Unscheduled Maintenance | 18463 | 38.4646
1594 | 2024-08-15 | 2025 | 2024 | 2024-08-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.77778 | 0.77778 | 0.7875 | 0 | 0.23333 | 0.23333 | Checked related error data log then reset & run the WTG. | Close | 0.0089744 | O2_11 | 179.5014 |  | WTG Unscheduled Maintenance | 18463 | 179.5014
1595 | 2024-08-15 | 2025 | 2024 | 2024-08-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.91458 | 0.91458 | 0.97222 | 0 | 1.3833 | 1.3833 | Attend repeated error for Temp. rot.br.pad high so check and found break pad temp sensor malfunctioning so check and all tight cannecsion then start wtg. | Close | 0.053205 | O2_11 | 1064.1868 |  | WTG Breakdown Maintenance | 18463 | 1064.1868
1596 | 2024-08-15 | 2025 | 2024 | 2024-08-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.25972 | 0.25972 | 0.26111 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_21 | 30.0292 |  | WTG Unscheduled Maintenance | 21621 | 30.0292
1597 | 2024-08-15 | 2025 | 2024 | 2024-08-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.04375 | 0.04375 | 0.045833 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_21 | 45.0437 |  | WTG Unscheduled Maintenance | 21621 | 45.0437
1598 | 2024-08-15 | 2025 | 2024 | 2024-08-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.19167 | 0.19167 | 0.19653 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & run the WTG. | Close | 0.0044872 | O2_21 | 105.1021 |  | WTG Unscheduled Maintenance | 21621 | 105.1021
1599 | 2024-08-15 | 2025 | 2024 | 2024-08-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 658 | Error pitch converter 3 | Break down | 0.25486 | 0.25486 | 0.25903 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2_21 | 90.0875 |  | WTG Unscheduled Maintenance | 21621 | 90.0875
1600 | 2024-08-15 | 2025 | 2024 | 2024-08-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.29167 | 0.29167 | 0.29375 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_21 | 45.0437 |  | WTG Unscheduled Maintenance | 21621 | 45.0437
1601 | 2024-08-16 | 2025 | 2024 | 2024-08-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3380 | Coolant temp. high | Road issue | 0 | 0 | 0.6875 | 0 | 16.5 | 16.5 | Due to WTG road not accessible. Once road clear will attend the same . | Close | 0.63462 | O2_05 | 13584.3125 |  | WTG Unscheduled Maintenance | 19759 | 13584.3125
1602 | 2024-08-16 | 2025 | 2024 | 2024-08-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3380 | Coolant temp. high | Break down | 0.6875 | 0.6875 | 0.75347 | 0 | 1.5833 | 1.5833 | Attend check all related circuit and found converter cooling fan contactor faulty so Replaced converter cooling fan contactor and start turbine. | Close | 0.060897 | O2_05 | 1303.5451 |  | WTG Unscheduled Maintenance | 19759 | 1303.5451
1603 | 2024-08-16 | 2025 | 2024 | 2024-08-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.44792 | 0.44792 | 0.74792 | 0 | 7.2 | 7.2 | Manual stop for 1st month maintenance activity(Day-1) | Close | 0.27692 | O2_03 | 5312.1 |  | WTG Scheduled Maintenance | 17707 | 5312.1
1604 | 2024-08-16 | 2025 | 2024 | 2024-08-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.058333 | 0.058333 | 0.060417 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_13 | 32.2 |  | WTG Unscheduled Maintenance | 15456 | 32.2
1605 | 2024-08-16 | 2025 | 2024 | 2024-08-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD | 0.44583 | 0.44583 | 0.78611 | 0 | 8.1667 | 8.1667 | Attend and checked related ckt, also checked Chopper resitor value in Axis no 2 than found faulty so replace it with new one and also check axis 3 chopper resistor value is not ok so replace it with new one.than take trial than undervoltage error occured so check flate resistor value in axis 3 than found value is not ok so replace it than reset and start Wtg. | Close | 0.3141 | O2_20 | 5092.5972 |  | WTG Breakdown Maintenance | 14966 | 5092.5972
1606 | 2024-08-17 | 2025 | 2024 | 2024-08-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.16389 | 0.16389 | 0.17361 | 0 | 0.23333 | 0.23333 | Checked related error data log then reset & run the WTG. | Close | 0.0089744 | O2_05 | 161.5639 |  | WTG Unscheduled Maintenance | 16618 | 161.5639
1607 | 2024-08-17 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.21319 | 0.21319 | 0.21458 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_21 | 23.9792 |  | WTG Unscheduled Maintenance | 17265 | 23.9792
1608 | 2024-08-17 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.52222 | 0.52222 | 0.71667 | 0 | 4.6667 | 4.6667 | attend for power curve inspection work and also replace blade 1 chopper resistor then start wtg. | Close | 0.17949 | O2_21 | 3357.0833 |  | WTG Breakdown Maintenance | 17265 | 3357.0833
1609 | 2024-08-17 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.95278 | 0.95278 | 0.95486 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | O2_21 | 35.9688 |  | WTG Unscheduled Maintenance | 17265 | 35.9688
1610 | 2024-08-17 | 2025 | 2024 | 2024-08-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.39028 | 0.39028 | 0.65347 | 0 | 6.3167 | 6.3167 | Manual stop for 1st month maintenance activity(Day-2) | Close | 0.24295 | O2_03 | 3930.2826 |  | WTG Scheduled Maintenance | 14933 | 3930.2826
1611 | 2024-08-17 | 2025 | 2024 | 2024-08-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.52361 | 0.52361 | 0.59236 | 0 | 1.65 | 1.65 | Manual stop for lift supply cable replacement work by lift and project team | Close | 0.063462 | O2_20 | 1033.1062 |  | WTG Breakdown Maintenance | 15027 | 1033.1062
1612 | 2024-08-17 | 2025 | 2024 | 2024-08-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.93056 | 0.93056 | 0.95625 | 0 | 0.61667 | 0.61667 | Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.023718 | O2_20 | 386.1104 |  | WTG Unscheduled Maintenance | 15027 | 386.1104
1613 | 2024-08-17 | 2025 | 2024 | 2024-08-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.072917 | 0.072917 | 0.074306 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & start WTG. | Close | 0.0012821 | O2_06 | 16.7903 |  | WTG Unscheduled Maintenance | 12089 | 16.7903
1614 | 2024-08-17 | 2025 | 2024 | 2024-08-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.43889 | 0.43889 | 0.44097 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | O2_06 | 25.1854 |  | WTG Unscheduled Maintenance | 12089 | 25.1854
1615 | 2024-08-18 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.60972 | 0.60972 | 0.61111 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & start WTG. | Close | 0.0012821 | O2_21 | 12.9417 |  | WTG Unscheduled Maintenance | 9318 | 12.9417
1616 | 2024-08-18 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.88194 | 0.88194 | 0.88403 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | O2_21 | 19.4125 |  | WTG Unscheduled Maintenance | 9318 | 19.4125
1617 | 2024-08-18 | 2025 | 2024 | 2024-08-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.52361 | 0.52361 | 0.525 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2_11 | 11.6597 |  | WTG Unscheduled Maintenance | 8395 | 11.6597
1618 | 2024-08-18 | 2025 | 2024 | 2024-08-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.50139 | 0.50139 | 0.54444 | 0 | 1.0333 | 1.0333 | Manual stop for bottom Fan Modification work | Close | 0.039744 | O2_11 | 361.4514 |  | WTG Breakdown Maintenance | 8395 | 361.4514
1619 | 2024-08-18 | 2025 | 2024 | 2024-08-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Major BD | 0.70556 | 0.70556 | 1899-12-31 | 0 | 7.0667 | 7.0667 | attend and found switching capacitor contactor is faulty and 500A fuse 2 nos is faulty now troubleshooting and material arrangement work WIP | Close | 0.27179 | O2_11 | 2471.8611 |  | WTG Unscheduled Maintenance | 8395 | 2471.8611
1620 | 2024-08-18 | 2025 | 2024 | 2024-08-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.79514 | 0.79514 | 0.79722 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | O2_06 | 19.5104 |  | WTG Unscheduled Maintenance | 9365 | 19.5104
1621 | 2024-08-19 | 2025 | 2024 | 2024-08-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Major BD | 0 | 0 | 1899-12-31 | 0 | 24 | 24 | attend and replace switching capacitor contactor and 2 nos fuse then take trial and same error occurs so now another troubleshooting and material arrangement work WIP. | Open | 0.92308 | O2_10 | 5141 |  | WTG Unscheduled Maintenance | 5141 | 5141
1622 | 2024-08-19 | 2025 | 2024 | 2024-08-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.41458 | 0.41458 | 0.70694 | 0 | 7.0167 | 7.0167 | Manual stop for 1st month maintenance activity(Day-1) | Close | 0.26987 | O2_21 | 1750.0736 |  | WTG Scheduled Maintenance | 5986 | 1750.0736
1623 | 2024-08-19 | 2025 | 2024 | 2024-08-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.73472 | 0.73472 | 0.74444 | 0 | 0.23333 | 0.23333 | Checked related error data log then reset & start WTG. | Close | 0.0089744 | O2_21 | 58.1972 |  | WTG Unscheduled Maintenance | 5986 | 58.1972
1624 | 2024-08-20 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.36597 | 0.36597 | 0.36736 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & start WTG. | Close | 0.0012821 | O2_21 | 12.5458 |  | WTG Unscheduled Maintenance | 9033 | 12.5458
1625 | 2024-08-20 | 2025 | 2024 | 2024-08-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0.96528 | 0.96528 | 1899-12-31 | 0 | 0.83333 | 0.83333 | WIP | Close | 0.032051 | O2_11 | 277.9167 |  | WTG Unscheduled Maintenance | 8004 | 277.9167
1626 | 2024-08-20 | 2025 | 2024 | 2024-08-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.089583 | 0.089583 | 0.090972 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2_11 | 11.1167 |  | WTG Unscheduled Maintenance | 8004 | 11.1167
1627 | 2024-08-20 | 2025 | 2024 | 2024-08-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.83611 | 0.83611 | 0.83819 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | O2_11 | 16.675 |  | WTG Unscheduled Maintenance | 8004 | 16.675
1628 | 2024-08-20 | 2025 | 2024 | 2024-08-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Major BD | 0 | 0 | 1899-12-31 | 0 | 24 | 24 | another troubleshooting and material arrangement work WIP. | Open | 0.92308 | O2_10 | 6250 |  | WTG Unscheduled Maintenance | 6250 | 6250
1629 | 2024-08-20 | 2025 | 2024 | 2024-08-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.41806 | 0.41806 | 0.67569 | 0 | 6.1833 | 6.1833 | Manual stop for 1st month maintenance activity(Day-2) | Close | 0.23782 | O2_21 | 2327.2521 |  | WTG Scheduled Maintenance | 9033 | 2327.2521
1630 | 2024-08-20 | 2025 | 2024 | 2024-08-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.60347 | 0.60347 | 0.60486 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & start WTG. | Close | 0.0012821 | O2_06 | 19.3736 |  | WTG Unscheduled Maintenance | 13949 | 19.3736
1631 | 2024-08-20 | 2025 | 2024 | 2024-08-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.82917 | 0.82917 | 0.83056 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & start WTG. | Close | 0.0012821 | O2_06 | 19.3736 |  | WTG Unscheduled Maintenance | 13949 | 19.3736
1632 | 2024-08-20 | 2025 | 2024 | 2024-08-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.94931 | 0.94931 | 0.95069 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & start WTG. | Close | 0.0012821 | O2_06 | 19.3736 |  | WTG Unscheduled Maintenance | 13949 | 19.3736
1633 | 2024-08-20 | 2025 | 2024 | 2024-08-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD | 0 | 0 | 0.46458 | 0 | 11.15 | 11.15 | After grid commissioning done start Wtg. | Close | 0.42885 | O2_01 | 4489.7333 |  | WTG Breakdown Maintenance | 9664 | 4489.7333
1634 | 2024-08-21 | 2025 | 2024 | 2024-08-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.0375 | 0.0375 | 0.038194 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | O2_05 | 4.384 |  | WTG Unscheduled Maintenance | 6313 | 4.384
1635 | 2024-08-21 | 2025 | 2024 | 2024-08-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.25208 | 0.25208 | 0.26389 | 0 | 0.28333 | 0.28333 | Checked related error data log then reset & start WTG. | Close | 0.010897 | O2_09 | 53.7389 |  | WTG Unscheduled Maintenance | 4552 | 53.7389
1636 | 2024-08-21 | 2025 | 2024 | 2024-08-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.32778 | 0.32778 | 0.34028 | 0 | 0.3 | 0.3 | Checked related error data log then reset & start WTG. | Close | 0.011538 | O2_02 | 73.625 |  | WTG Unscheduled Maintenance | 5890 | 73.625
1637 | 2024-08-21 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.29236 | 0.29236 | 0.29375 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & start WTG. | Close | 0.0012821 | O2_21 | 6.4875 |  | WTG Unscheduled Maintenance | 4671 | 6.4875
1638 | 2024-08-21 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.59931 | 0.59931 | 0.60069 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & start WTG. | Close | 0.0012821 | O2_21 | 6.4875 |  | WTG Unscheduled Maintenance | 4671 | 6.4875
1639 | 2024-08-21 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.81944 | 0.81944 | 0.82292 | 0 | 0.083333 | 0.083333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.0032051 | O2_21 | 16.2187 |  | WTG Unscheduled Maintenance | 4671 | 16.2187
1640 | 2024-08-21 | 2025 | 2024 | 2024-08-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0 | 0 | 0.0125 | 0 | 0.3 | 0.3 | attend and found VCB trip so check related circuit,check switch yard, check relays no found any abnormality then charged then VCB. | Close | 0.011538 | O2_11 | 55.9 |  | WTG Unscheduled Maintenance | 4472 | 55.9
1641 | 2024-08-21 | 2025 | 2024 | 2024-08-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.27083 | 0.27083 | 0.28472 | 0 | 0.33333 | 0.33333 | Checked related error data log then reset & start WTG. | Close | 0.012821 | O2_14 | 60.2361 |  | WTG Unscheduled Maintenance | 4337 | 60.2361
1642 | 2024-08-21 | 2025 | 2024 | 2024-08-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.069444 | 0.069444 | 0.070833 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & start WTG. | Close | 0.0012821 | O2_11 | 6.2111 |  | WTG Unscheduled Maintenance | 4472 | 6.2111
1643 | 2024-08-21 | 2025 | 2024 | 2024-08-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.50486 | 0.50486 | 0.52917 | 0 | 0.58333 | 0.58333 | Checked related error data log then reset & start WTG. | Close | 0.022436 | O2_11 | 108.6944 |  | WTG Unscheduled Maintenance | 4472 | 108.6944
1644 | 2024-08-21 | 2025 | 2024 | 2024-08-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.25833 | 0.25833 | 0.26597 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & start WTG. | Close | 0.0070513 | O2_11 | 34.1611 |  | WTG Unscheduled Maintenance | 4472 | 34.1611
1645 | 2024-08-21 | 2025 | 2024 | 2024-08-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.25347 | 0.25347 | 0.26458 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & start WTG. | Close | 0.010256 | O2_11 | 49.6889 |  | WTG Unscheduled Maintenance | 4472 | 49.6889
1646 | 2024-08-21 | 2025 | 2024 | 2024-08-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Major BD | 0 | 0 | 0.76736 | 0 | 18.4167 | 18.4167 | Attend and check related circuit with Technical team and Ingeteam suplier team with on call than check Capacitor circuit than check grid filter contector than also check precharge circuit and than check GSC than nothing found abnormal than check than rotor cable remove and Charge MSC than charge than nothing found abnormal replace 2 nos 500A Fuse and Replace 2 nos grid filter contector with Cable than take trial and start Wtg.(Now Wtg under observation) | Close | 0.70833 | O2_14 | 3328.0451 |  | WTG Unscheduled Maintenance | 4337 | 3328.0451
1647 | 2024-08-21 | 2025 | 2024 | 2024-08-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 7025 | Configuration error | Break down | 0.81944 | 0.81944 | 0.83056 | 0 | 0.26667 | 0.26667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.010256 | O2_20 | 54.7889 |  | WTG Unscheduled Maintenance | 4931 | 54.7889
1648 | 2024-08-21 | 2025 | 2024 | 2024-08-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.41944 | 0.41944 | 0.67708 | 0 | 6.1833 | 6.1833 | Manual stop for 1st month maintenance activity(Day-1) | Close | 0.23782 | O2_16 | 1286.6486 |  | WTG Scheduled Maintenance | 4994 | 1286.6486
1649 | 2024-08-21 | 2025 | 2024 | 2024-08-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 7025 | Configuration error | Break down | 0.81944 | 0.81944 | 0.83056 | 0 | 0.26667 | 0.26667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.010256 | O2_16 | 55.4889 |  | WTG Unscheduled Maintenance | 4994 | 55.4889
1650 | 2024-08-21 | 2025 | 2024 | 2024-08-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.81944 | 0.81944 | 0.82569 | 0 | 0.15 | 0.15 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.0057692 | O2_16 | 31.2125 |  | WTG Unscheduled Maintenance | 4994 | 31.2125
1651 | 2024-08-21 | 2025 | 2024 | 2024-08-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.81944 | 0.81944 | 0.82986 | 0 | 0.25 | 0.25 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.0096154 | O2_20 | 51.3646 |  | WTG Unscheduled Maintenance | 4931 | 51.3646
1652 | 2024-08-21 | 2025 | 2024 | 2024-08-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 656 | Error pitch converter 1 | Break down | 0.32986 | 0.32986 | 0.33264 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & start WTG. | Close | 0.0025641 | O2_20 | 13.6972 |  | WTG Unscheduled Maintenance | 4931 | 13.6972
1653 | 2024-08-21 | 2025 | 2024 | 2024-08-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 656 | Error pitch converter 1 | Break down | 0.34236 | 0.34236 | 0.34722 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & start WTG. | Close | 0.0044872 | O2_20 | 23.9701 |  | WTG Unscheduled Maintenance | 4931 | 23.9701
1654 | 2024-08-22 | 2025 | 2024 | 2024-08-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.41806 | 0.41806 | 0.42014 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | O2_05 | 9.5479 |  | WTG Unscheduled Maintenance | 4583 | 9.5479
1655 | 2024-08-22 | 2025 | 2024 | 2024-08-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.67431 | 0.67431 | 0.67569 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & start WTG. | Close | 0.0012821 | O2_02 | 6.8778 |  | WTG Unscheduled Maintenance | 4952 | 6.8778
1656 | 2024-08-22 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.27986 | 0.27986 | 0.28194 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | O2_21 | 6.7125 |  | WTG Unscheduled Maintenance | 3222 | 6.7125
1657 | 2024-08-22 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.46944 | 0.46944 | 0.47222 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & start WTG. | Close | 0.0025641 | O2_21 | 8.95 |  | WTG Unscheduled Maintenance | 3222 | 8.95
1658 | 2024-08-22 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.91875 | 0.91875 | 0.92083 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | O2_21 | 6.7125 |  | WTG Unscheduled Maintenance | 3222 | 6.7125
1659 | 2024-08-22 | 2025 | 2024 | 2024-08-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Major BD | 0.71875 | 0.71875 | 1899-12-31 | 0 | 6.75 | 6.75 | attend and found QA7.2 grid filter contactor failure and 2 nos 500A fuse faulty so now troubleshooting and material arrangement work WIP. | Open | 0.25962 | O2_11 | 767.25 |  | WTG Unscheduled Maintenance | 2728 | 767.25
1660 | 2024-08-22 | 2025 | 2024 | 2024-08-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.36389 | 0.36389 | 0.67708 | 0 | 7.5167 | 7.5167 | Manual stop for 1st month maintenance activity(Day-2) | Close | 0.2891 | O2_06 | 1184.1882 |  | WTG Scheduled Maintenance | 3781 | 1184.1882
1661 | 2024-08-23 | 2025 | 2024 | 2024-08-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.65764 | 0.65764 | 0.67014 | 0 | 0.3 | 0.3 | Checked related error data log then reset & start WTG. | Close | 0.011538 | O2_26 | 78.05 |  | WTG Unscheduled Maintenance | 6244 | 78.05
1662 | 2024-08-23 | 2025 | 2024 | 2024-08-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.83125 | 0.83125 | 1899-12-31 | 0 | 4.05 | 4.05 | wip | Close | 0.15577 | O2_02 | 1333.6312 |  | WTG Unscheduled Maintenance | 7903 | 1333.6312
1663 | 2024-08-23 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.11667 | 0.11667 | 0.11875 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | O2_21 | 11.3708 |  | WTG Unscheduled Maintenance | 5458 | 11.3708
1664 | 2024-08-23 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.23542 | 0.23542 | 0.24028 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & start WTG. | Close | 0.0044872 | O2_21 | 26.5319 |  | WTG Unscheduled Maintenance | 5458 | 26.5319
1665 | 2024-08-23 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.30764 | 0.30764 | 0.30972 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | O2_21 | 11.3708 |  | WTG Unscheduled Maintenance | 5458 | 11.3708
1666 | 2024-08-23 | 2025 | 2024 | 2024-08-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD | 0.47569 | 0.47569 | 0.74028 | 0 | 6.35 | 6.35 | attend and replace 2 no's ladder change completed T2-T3 section and 1 no's ladder change completed T3-T4 section and all sections ladder splicing work completed. | Close | 0.24423 | O2_03 | 1673.4896 |  | WTG Breakdown Maintenance | 6325 | 1673.4896
1667 | 2024-08-23 | 2025 | 2024 | 2024-08-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.575 | 0.575 | 0.57639 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & start WTG. | Close | 0.0012821 | O2_12 | 7.2472 |  | WTG Unscheduled Maintenance | 5218 | 7.2472
1668 | 2024-08-23 | 2025 | 2024 | 2024-08-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.21389 | 0.21389 | 0.21528 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & start WTG. | Close | 0.0012821 | O2_11 | 7.6194 |  | WTG Unscheduled Maintenance | 5486 | 7.6194
1669 | 2024-08-23 | 2025 | 2024 | 2024-08-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.89792 | 0.89792 | 0.89931 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & start WTG. | Close | 0.0012821 | O2_11 | 7.6194 |  | WTG Unscheduled Maintenance | 5486 | 7.6194
1670 | 2024-08-23 | 2025 | 2024 | 2024-08-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Major BD | 0 | 0 | 1899-12-31 | 0 | 24 | 24 | attend and check USS transformer LV side to Converter power cable IR value taken,Capacitors CA1 to CA18 capacitance value taken,Capacitors CA1 to CA18 Group IR value taken,QA7.1 & QA7.2 to FC7.1, FC7.2, FC7.3 cable IR value taken,BC13, BC14, BC15 grid filter current measurement CT terminal resistance value taken. now troubleshooting and material arrangement work WIP. | Open | 0.92308 | O2_14 | 5718 |  | WTG Unscheduled Maintenance | 5718 | 5718
1671 | 2024-08-23 | 2025 | 2024 | 2024-08-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.71181 | 0.71181 | 0.71944 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & start WTG. | Close | 0.0070513 | O2_16 | 49.1486 |  | WTG Unscheduled Maintenance | 6434 | 49.1486
1672 | 2024-08-23 | 2025 | 2024 | 2024-08-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.42083 | 0.42083 | 0.72708 | 0 | 7.35 | 7.35 | Manual stop for 1st month maintenance activity(Day-1) | Close | 0.28269 | O2_16 | 1970.4125 |  | WTG Scheduled Maintenance | 6434 | 1970.4125
1673 | 2024-08-24 | 2025 | 2024 | 2024-08-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.84375 | 0.84375 | 0.85139 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & start WTG. | Close | 0.0070513 | O2_26 | 171.5924 |  | WTG Unscheduled Maintenance | 22463 | 171.5924
1674 | 2024-08-24 | 2025 | 2024 | 2024-08-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.6875 | 0.6875 | 0.68889 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & start WTG. | Close | 0.0012821 | O2_05 | 39.9264 |  | WTG Unscheduled Maintenance | 28747 | 39.9264
1675 | 2024-08-24 | 2025 | 2024 | 2024-08-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0 | 0 | 0.013194 | 0 | 0.31667 | 0.31667 | Attend for high temperature ambient upper Convator error so check and found temperature sensor is malfunction, 140 ohm's value, so we interchange temperature sensor Modual KZ3 upper ambient (6 and 7) cannecsion to lower ambient (2 and 3) cannecsion then Start wtg .so now WTG under observation. | Close | 0.012179 | O2_02 | 396.0312 |  | WTG Unscheduled Maintenance | 30015 | 396.0312
1676 | 2024-08-24 | 2025 | 2024 | 2024-08-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.13889 | 0.13889 | 0.14097 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | O2_02 | 62.5312 |  | WTG Unscheduled Maintenance | 30015 | 62.5312
1677 | 2024-08-24 | 2025 | 2024 | 2024-08-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.42292 | 0.42292 | 0.4375 | 0 | 0.35 | 0.35 | Checked related error data log then reset & start WTG. | Close | 0.013462 | O2_02 | 437.7188 |  | WTG Unscheduled Maintenance | 30015 | 437.7188
1678 | 2024-08-24 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.42361 | 0.42361 | 0.43889 | 0 | 0.36667 | 0.36667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.014103 | O2_21 | 327.25 |  | WTG Unscheduled Maintenance | 21420 | 327.25
1679 | 2024-08-24 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.58056 | 0.58056 | 0.58403 | 0 | 0.083333 | 0.083333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.0032051 | O2_21 | 74.375 |  | WTG Unscheduled Maintenance | 21420 | 74.375
1680 | 2024-08-24 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.73611 | 0.73611 | 0.76319 | 0 | 0.65 | 0.65 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.025 | O2_21 | 580.125 |  | WTG Unscheduled Maintenance | 21420 | 580.125
1681 | 2024-08-24 | 2025 | 2024 | 2024-08-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Major BD | 0 | 0 | 0.87986 | 0 | 21.1167 | 21.1167 | attend and check ingeteme supplier guideline check and replace 500A fuse and grid filter contactor with Cable than take trial and start Wtg.(Now Wtg under observation). | Close | 0.81218 | O2_14 | 24159.2264 |  | WTG Unscheduled Maintenance | 27458 | 24159.2264
1682 | 2024-08-24 | 2025 | 2024 | 2024-08-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.42361 | 0.42361 | 0.49653 | 0 | 1.75 | 1.75 | after grid resume Wtg in error so Checked related error data log another troubleshooting work apply hard reboot then start wtg. | Close | 0.067308 | O2_20 | 1526.875 |  | WTG Unscheduled Maintenance | 20940 | 1526.875
1683 | 2024-08-24 | 2025 | 2024 | 2024-08-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.58056 | 0.58056 | 0.58542 | 0 | 0.11667 | 0.11667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.0044872 | O2_20 | 101.7917 |  | WTG Unscheduled Maintenance | 20940 | 101.7917
1684 | 2024-08-24 | 2025 | 2024 | 2024-08-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Connectivity issue | 0.73611 | 0.73611 | 0.85069 | 0 | 2.75 | 2.75 | after grid resume late reset due to connectivity loss for O2-24 VCB trip,(late reset due to heavy rain and approach road problem) | Close | 0.10577 | O2_20 | 2399.375 |  | WTG Unscheduled Maintenance | 20940 | 2399.375
1685 | 2024-08-24 | 2025 | 2024 | 2024-08-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.42361 | 0.42361 | 0.4375 | 0 | 0.33333 | 0.33333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.012821 | O2_21 | 297.5 |  | WTG Unscheduled Maintenance | 21420 | 297.5
1686 | 2024-08-24 | 2025 | 2024 | 2024-08-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.58056 | 0.58056 | 0.5875 | 0 | 0.16667 | 0.16667 | Checked related error data log then reset & start WTG. | Close | 0.0064103 | O2_21 | 148.75 |  | WTG Unscheduled Maintenance | 21420 | 148.75
1687 | 2024-08-24 | 2025 | 2024 | 2024-08-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.73611 | 0.73611 | 0.74792 | 0 | 0.28333 | 0.28333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.010897 | O2_21 | 252.875 |  | WTG Unscheduled Maintenance | 21420 | 252.875
1688 | 2024-08-24 | 2025 | 2024 | 2024-08-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.42361 | 0.42361 | 0.43125 | 0 | 0.18333 | 0.18333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.0070513 | O2_16 | 146.2236 |  | WTG Unscheduled Maintenance | 19142 | 146.2236
1689 | 2024-08-24 | 2025 | 2024 | 2024-08-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.58056 | 0.58056 | 0.58611 | 0 | 0.13333 | 0.13333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.0051282 | O2_16 | 106.3444 |  | WTG Unscheduled Maintenance | 19142 | 106.3444
1690 | 2024-08-24 | 2025 | 2024 | 2024-08-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Connectivity issue | 0.73611 | 0.73611 | 0.85 | 0 | 2.7333 | 2.7333 | after grid resume late reset due to connectivity loss for O2-24 VCB trip,(late reset due to heavy rain and approach road problem) | Close | 0.10513 | O2_16 | 2180.0611 |  | WTG Unscheduled Maintenance | 19142 | 2180.0611
1691 | 2024-08-24 | 2025 | 2024 | 2024-08-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.42361 | 0.42361 | 0.43611 | 0 | 0.3 | 0.3 | Checked related error data log then reset & start WTG. | Close | 0.011538 | O2_20 | 261.75 |  | WTG Unscheduled Maintenance | 20940 | 261.75
1692 | 2024-08-24 | 2025 | 2024 | 2024-08-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Break down | 0.58056 | 0.58056 | 0.68472 | 0 | 2.5 | 2.5 | after grid resume Wtg in error so attend and replace blade 1 chopper register and Dynamic breaking register then wtg is not start due to f# 2 shutdown. | Close | 0.096154 | O2_20 | 2181.25 |  | WTG Unscheduled Maintenance | 20940 | 2181.25
1693 | 2024-08-24 | 2025 | 2024 | 2024-08-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Road issue | 0.73611 | 0.73611 | 0.85625 | 0 | 2.8833 | 2.8833 | after grid resume VCB trip, so attend by HT team check all releted circuit no nay abnormality so charge VCB then start wtg. (late attend due to heavy rain and approach road problem) | Close | 0.1109 | O2_20 | 2515.7083 |  | WTG Unscheduled Maintenance | 20940 | 2515.7083
1694 | 2024-08-24 | 2025 | 2024 | 2024-08-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.18611 | 0.18611 | 0.18958 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & start WTG. | Close | 0.0032051 | O2_01 | 88.7361 |  | WTG Unscheduled Maintenance | 25556 | 88.7361
1695 | 2024-08-24 | 2025 | 2024 | 2024-08-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.24931 | 0.24931 | 0.27222 | 0 | 0.55 | 0.55 | grid voltage is very high 714 v so tap down on PSS the voltage is normal then Start wtg now WTG in production | Close | 0.021154 | O2_01 | 585.6583 |  | WTG Unscheduled Maintenance | 25556 | 585.6583
1696 | 2024-08-25 | 2025 | 2024 | 2024-08-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Environment | 0.67014 | 0.67014 | 1899-12-31 | 0 | 7.9167 | 7.9167 | not attend due to heavy rain at site and approach road problem. | Open | 0.30449 | O2_02 | 20695.816 |  | WTG Unscheduled Maintenance | 62741 | 20695.816
1697 | 2024-08-25 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 4540 | Tower oscillation X level 2 | Break down | 0.79236 | 0.79236 | 0.80833 | 0 | 0.38333 | 0.38333 | after Tower oscillation normal then Checked related error data log then reset & start WTG. | Close | 0.014744 | O2_21 | 968.1882 |  | WTG Unscheduled Maintenance | 60617 | 968.1882
1698 | 2024-08-25 | 2025 | 2024 | 2024-08-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.47014 | 0.47014 | 0.47431 | 0 | 0.1 | 0.1 | Checked related error data log then reset & start WTG. | Close | 0.0038462 | O2_11 | 248.7583 |  | WTG Unscheduled Maintenance | 59702 | 248.7583
1699 | 2024-08-25 | 2025 | 2024 | 2024-08-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.091667 | 0.091667 | 0.094444 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & start WTG. | Close | 0.0025641 | O2_11 | 165.8389 |  | WTG Unscheduled Maintenance | 59702 | 165.8389
1700 | 2024-08-25 | 2025 | 2024 | 2024-08-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.77222 | 0.77222 | 0.78333 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & start WTG. | Close | 0.010256 | O2_11 | 663.3556 |  | WTG Unscheduled Maintenance | 59702 | 663.3556
1701 | 2024-08-25 | 2025 | 2024 | 2024-08-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.52222 | 0.52222 | 0.54167 | 0 | 0.46667 | 0.46667 | attend for converter inspection done using IR thermometer with ingeteam no any abnormal temperature rise obseeves. | Close | 0.017949 | O2_11 | 1160.8722 |  | WTG Breakdown Maintenance | 59702 | 1160.8722
1702 | 2024-08-25 | 2025 | 2024 | 2024-08-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 4540 | Tower oscillation X level 2 | Break down | 0.8375 | 0.8375 | 0.84097 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & start WTG. | Close | 0.0032051 | O2_21 | 210.4757 |  | WTG Unscheduled Maintenance | 60617 | 210.4757
1703 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Road issue | 0 | 0 | 0.99999 | 0 | 23.9997 | 23.9997 | Due to road approch issue unable to attend the wtg and heavy rain | Close | 0.92307 | O2_02 | 40613.5299 |  | WTG Unscheduled Maintenance | 40614 | 40613.5299
1704 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Road issue | 0.87153 | 0.87153 | 1899-12-31 | 0 | 3.0833 | 3.0833 | Due to road approch issue unable to attend the wtg and VCB tripped | Open | 0.11859 | O2_05 | 5217.7708 |  | WTG Breakdown Maintenance | 40614 | 5217.7708
1705 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 537 | Incorrect Error Code | Break down | 0.40903 | 0.40903 | 0.41528 | 0 | 0.15 | 0.15 | Checked related error data log then reset & start WTG. | Close | 0.0057692 | O2_26 | 220.6125 |  | WTG Unscheduled Maintenance | 35298 | 220.6125
1706 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.57292 | 0.57292 | 0.58542 | 0 | 0.3 | 0.3 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.011538 | O2_26 | 441.225 |  | WTG Unscheduled Maintenance | 35298 | 441.225
1707 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.88194 | 0.88194 | 0.90347 | 0 | 0.51667 | 0.51667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.019872 | O2_26 | 759.8875 |  | WTG Unscheduled Maintenance | 35298 | 759.8875
1708 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.46875 | 0.46875 | 0.47083 | 0 | 0.05 | 0.05 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.0019231 | O2_09 | 86.8333 |  | WTG Unscheduled Maintenance | 41680 | 86.8333
1709 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.88194 | 0.88194 | 0.92639 | 0 | 1.0667 | 1.0667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.041026 | O2_09 | 1852.4444 |  | WTG Unscheduled Maintenance | 41680 | 1852.4444
1710 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.46875 | 0.46875 | 0.48819 | 0 | 0.46667 | 0.46667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.017949 | O2_21 | 665.4083 |  | WTG Unscheduled Maintenance | 34221 | 665.4083
1711 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.57292 | 0.57292 | 0.59097 | 0 | 0.43333 | 0.43333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.016667 | O2_21 | 617.8792 |  | WTG Unscheduled Maintenance | 34221 | 617.8792
1712 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.88194 | 0.88194 | 1899-12-31 | 0 | 2.8333 | 2.8333 | wip | Close | 0.10897 | O2_21 | 4039.9792 |  | WTG Unscheduled Maintenance | 34221 | 4039.9792
1713 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.88194 | 0.88194 | 0.90069 | 0 | 0.45 | 0.45 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.017308 | O2_03 | 765.6 |  | WTG Unscheduled Maintenance | 40832 | 765.6
1714 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 455 | Repeating error BP52 | Break down | 0.38611 | 0.38611 | 0.39306 | 0 | 0.16667 | 0.16667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.0064103 | O2_11 | 277.4375 |  | WTG Unscheduled Maintenance | 39951 | 277.4375
1715 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 455 | Repeating error BP52 | Break down | 0.88194 | 0.88194 | 0.92847 | 0 | 1.1167 | 1.1167 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.042949 | O2_11 | 1858.8313 |  | WTG Unscheduled Maintenance | 39951 | 1858.8313
1716 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.46875 | 0.46875 | 0.47014 | 0 | 0.033333 | 0.033333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.0012821 | O2_12 | 43.7542 |  | WTG Unscheduled Maintenance | 31503 | 43.7542
1717 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Others | 0.60486 | 0.60486 | 0.65486 | 0 | 1.2 | 1.2 | wtg manual stop for load shedding by SCDC | Close | 0.046154 | O2_12 | 1575.15 |  | WTG Breakdown Maintenance | 31503 | 1575.15
1718 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.88194 | 0.88194 | 0.88889 | 0 | 0.16667 | 0.16667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.0064103 | O2_12 | 218.7708 |  | WTG Unscheduled Maintenance | 31503 | 218.7708
1719 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.91042 | 0.91042 | 0.91181 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & start WTG. | Close | 0.0012821 | O2_12 | 43.7542 |  | WTG Unscheduled Maintenance | 31503 | 43.7542
1720 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.46875 | 0.46875 | 0.47153 | 0 | 0.066667 | 0.066667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.0025641 | O2_11 | 110.975 |  | WTG Unscheduled Maintenance | 39951 | 110.975
1721 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 518 | Pitch limit switch 3 | Environment | 0.57292 | 0.57292 | 0.65486 | 0 | 1.9667 | 1.9667 | not attend due to heavy rain at site and approach road problem. | Close | 0.075641 | O2_11 | 3273.7625 |  | WTG Unscheduled Maintenance | 39951 | 3273.7625
1722 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 518 | Pitch limit switch 3 | Environment | 0.88194 | 0.88194 | 1899-12-31 | 0 | 2.8333 | 2.8333 | not attend due to heavy rain at site and approach road problem. | Close | 0.10897 | O2_11 | 4716.4375 |  | WTG Unscheduled Maintenance | 39951 | 4716.4375
1723 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.46875 | 0.46875 | 0.47083 | 0 | 0.05 | 0.05 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.0019231 | O2_11 | 83.2312 |  | WTG Unscheduled Maintenance | 39951 | 83.2312
1724 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.88194 | 0.88194 | 0.89306 | 0 | 0.26667 | 0.26667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.010256 | O2_11 | 443.9 |  | WTG Unscheduled Maintenance | 39951 | 443.9
1725 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.46875 | 0.46875 | 0.47083 | 0 | 0.05 | 0.05 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.0019231 | O2_11 | 83.2312 |  | WTG Unscheduled Maintenance | 39951 | 83.2312
1726 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.88194 | 0.88194 | 0.90278 | 0 | 0.5 | 0.5 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.019231 | O2_11 | 832.3125 |  | WTG Unscheduled Maintenance | 39951 | 832.3125
1727 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.46875 | 0.46875 | 0.48056 | 0 | 0.28333 | 0.28333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.010897 | O2_11 | 471.6438 |  | WTG Unscheduled Maintenance | 39951 | 471.6438
1728 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.57292 | 0.57292 | 0.57639 | 0 | 0.083333 | 0.083333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.0032051 | O2_11 | 138.7187 |  | WTG Unscheduled Maintenance | 39951 | 138.7187
1729 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.62569 | 0.62569 | 0.65486 | 0 | 0.7 | 0.7 | attend for converter inspection done using IR thermometer with ingeteam no any abnormal temperature rise observation. | Close | 0.026923 | O2_11 | 1165.2375 |  | WTG Breakdown Maintenance | 39951 | 1165.2375
1730 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.88194 | 0.88194 | 0.91667 | 0 | 0.83333 | 0.83333 | after grid resume VCB trip cherge VCB then start wtg. | Close | 0.032051 | O2_11 | 1387.1875 |  | WTG Unscheduled Maintenance | 39951 | 1387.1875
1731 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.91667 | 0.91667 | 0.92847 | 0 | 0.28333 | 0.28333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.010897 | O2_11 | 471.6438 |  | WTG Unscheduled Maintenance | 39951 | 471.6438
1732 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.46875 | 0.46875 | 0.47153 | 0 | 0.066667 | 0.066667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.0025641 | O2_21 | 95.0583 |  | WTG Unscheduled Maintenance | 34221 | 95.0583
1733 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.88194 | 0.88194 | 0.89028 | 0 | 0.2 | 0.2 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.0076923 | O2_21 | 285.175 |  | WTG Unscheduled Maintenance | 34221 | 285.175
1734 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.46875 | 0.46875 | 0.47847 | 0 | 0.23333 | 0.23333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.0089744 | O2_21 | 332.7042 |  | WTG Unscheduled Maintenance | 34221 | 332.7042
1735 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.57292 | 0.57292 | 0.58889 | 0 | 0.38333 | 0.38333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.014744 | O2_21 | 546.5854 |  | WTG Unscheduled Maintenance | 34221 | 546.5854
1736 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.88194 | 0.88194 | 0.94444 | 0 | 1.5 | 1.5 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.057692 | O2_21 | 2138.8125 |  | WTG Unscheduled Maintenance | 34221 | 2138.8125
1737 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 1600 | High gear speed | Break down | 0.16042 | 0.16042 | 0.16597 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & start WTG. | Close | 0.0051282 | O2_21 | 190.1167 |  | WTG Unscheduled Maintenance | 34221 | 190.1167
1738 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 455 | Repeating error BP52 | Break down | 0.38889 | 0.38889 | 0.39236 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & start WTG. | Close | 0.0032051 | O2_21 | 118.8229 |  | WTG Unscheduled Maintenance | 34221 | 118.8229
1739 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.46875 | 0.46875 | 0.47708 | 0 | 0.2 | 0.2 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.0076923 | O2_21 | 285.175 |  | WTG Unscheduled Maintenance | 34221 | 285.175
1740 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.57292 | 0.57292 | 0.57569 | 0 | 0.066667 | 0.066667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.0025641 | O2_21 | 95.0583 |  | WTG Unscheduled Maintenance | 34221 | 95.0583
1741 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.88194 | 0.88194 | 0.89167 | 0 | 0.23333 | 0.23333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.0089744 | O2_21 | 332.7042 |  | WTG Unscheduled Maintenance | 34221 | 332.7042
1742 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.46875 | 0.46875 | 0.48264 | 0 | 0.33333 | 0.33333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.012821 | O2_21 | 475.2917 |  | WTG Unscheduled Maintenance | 34221 | 475.2917
1743 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.57292 | 0.57292 | 0.59375 | 0 | 0.5 | 0.5 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.019231 | O2_21 | 712.9375 |  | WTG Unscheduled Maintenance | 34221 | 712.9375
1744 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.88194 | 0.88194 | 1899-12-31 | 0 | 2.8333 | 2.8333 | wip | Close | 0.10897 | O2_21 | 4039.9792 |  | WTG Unscheduled Maintenance | 34221 | 4039.9792
1745 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.46875 | 0.46875 | 0.47361 | 0 | 0.11667 | 0.11667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.0044872 | O2_21 | 166.3521 |  | WTG Unscheduled Maintenance | 34221 | 166.3521
1746 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.57292 | 0.57292 | 0.58125 | 0 | 0.2 | 0.2 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.0076923 | O2_21 | 285.175 |  | WTG Unscheduled Maintenance | 34221 | 285.175
1747 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Others | 0.60139 | 0.60139 | 0.65486 | 0 | 1.2833 | 1.2833 | wtg manual stop for load shedding by SCDC | Close | 0.049359 | O2_21 | 1829.8729 |  | WTG Breakdown Maintenance | 34221 | 1829.8729
1748 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.88194 | 0.88194 | 0.90347 | 0 | 0.51667 | 0.51667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.019872 | O2_21 | 736.7021 |  | WTG Unscheduled Maintenance | 34221 | 736.7021
1749 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down | 0.97361 | 0.97361 | 0.98819 | 0 | 0.35 | 0.35 | Checked related error data log then reset & start WTG. | Close | 0.013462 | O2_21 | 499.0563 |  | WTG Unscheduled Maintenance | 34221 | 499.0563
1750 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.46875 | 0.46875 | 0.47639 | 0 | 0.18333 | 0.18333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.0070513 | O2_21 | 261.4104 |  | WTG Unscheduled Maintenance | 34221 | 261.4104
1751 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.57292 | 0.57292 | 0.58819 | 0 | 0.36667 | 0.36667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.014103 | O2_21 | 522.8208 |  | WTG Unscheduled Maintenance | 34221 | 522.8208
1752 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.88194 | 0.88194 | 0.93264 | 0 | 1.2167 | 1.2167 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.046795 | O2_21 | 1734.8146 |  | WTG Unscheduled Maintenance | 34221 | 1734.8146
1753 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.88194 | 0.88194 | 0.94514 | 0 | 1.5167 | 1.5167 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.058333 | O2_21 | 2162.5771 |  | WTG Unscheduled Maintenance | 34221 | 2162.5771
1754 | 2024-08-27 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0 | 0 | 0.022917 | 0 | 0.55 | 0.55 | after grid resume Wtg is not cannected to scada so attend and Checked related error data log then apply hard reboot then reset & start the WTG. | Close | 0.021154 | O2_21 | 1372.4792 |  | WTG Unscheduled Maintenance | 59890 | 1372.4792
1755 | 2024-08-27 | 2025 | 2024 | 2024-08-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0 | 0 | 0.061806 | 0 | 1.4833 | 1.4833 | after grid resume Wtg is not cannected to scada so attend and Checked related error data log then apply hard reboot then reset & start the WTG. | Close | 0.057051 | O2_06 | 4021.0076 |  | WTG Unscheduled Maintenance | 65059 | 4021.0076
1756 | 2024-08-27 | 2025 | 2024 | 2024-08-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.31597 | 0.31597 | 0.31806 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | O2_06 | 135.5396 |  | WTG Unscheduled Maintenance | 65059 | 135.5396
1757 | 2024-08-27 | 2025 | 2024 | 2024-08-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Break down | 0.0083333 | 0.0083333 | 0.01875 | 0 | 0.25 | 0.25 | Checked related error data log apply soft reboot reset & start the WTG. | Close | 0.0096154 | O2_03 | 676.2917 |  | WTG Unscheduled Maintenance | 64924 | 676.2917
1758 | 2024-08-27 | 2025 | 2024 | 2024-08-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Break down | 0.21042 | 0.21042 | 0.22153 | 0 | 0.26667 | 0.26667 | Checked related error data log apply soft reboot reset & start the WTG. | Close | 0.010256 | O2_03 | 721.3778 |  | WTG Unscheduled Maintenance | 64924 | 721.3778
1759 | 2024-08-27 | 2025 | 2024 | 2024-08-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.25694 | 0.25694 | 0.26667 | 0 | 0.23333 | 0.23333 | Checked related error data log then reset & start WTG. | Close | 0.0089744 | O2_11 | 605.5097 |  | WTG Unscheduled Maintenance | 62281 | 605.5097
1760 | 2024-08-27 | 2025 | 2024 | 2024-08-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 4540 | Tower oscillation X level 2 | Break down | 0.086111 | 0.086111 | 0.097222 | 0 | 0.26667 | 0.26667 | Checked related error data log apply soft reboot reset & start the WTG. | Close | 0.010256 | O2_10 | 720.1 |  | WTG Unscheduled Maintenance | 64809 | 720.1
1761 | 2024-08-27 | 2025 | 2024 | 2024-08-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down | 0.21319 | 0.21319 | 0.21806 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & start WTG. | Close | 0.0044872 | O2_10 | 315.0438 |  | WTG Unscheduled Maintenance | 64809 | 315.0438
1762 | 2024-08-27 | 2025 | 2024 | 2024-08-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down | 0.68125 | 0.68125 | 0.69236 | 0 | 0.26667 | 0.26667 | Checked related error data log apply soft reboot reset & start the WTG. | Close | 0.010256 | O2_11 | 692.0111 |  | WTG Unscheduled Maintenance | 62281 | 692.0111
1763 | 2024-08-27 | 2025 | 2024 | 2024-08-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Break down | 0.067361 | 0.067361 | 0.078472 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & start WTG. | Close | 0.010256 | O2_20 | 726.8667 |  | WTG Unscheduled Maintenance | 65418 | 726.8667
1764 | 2024-08-27 | 2025 | 2024 | 2024-08-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Break down | 0.3375 | 0.3375 | 0.34861 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & start WTG. | Close | 0.010256 | O2_20 | 726.8667 |  | WTG Unscheduled Maintenance | 65418 | 726.8667
1765 | 2024-08-27 | 2025 | 2024 | 2024-08-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Break down | 0.33889 | 0.33889 | 0.34931 | 0 | 0.25 | 0.25 | Checked related error data log then reset & start WTG. | Close | 0.0096154 | O2_20 | 681.4375 |  | WTG Unscheduled Maintenance | 65418 | 681.4375
1766 | 2024-08-27 | 2025 | 2024 | 2024-08-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Break down | 0.47083 | 0.47083 | 0.48194 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & start WTG. | Close | 0.010256 | O2_20 | 726.8667 |  | WTG Unscheduled Maintenance | 65418 | 726.8667
1767 | 2024-08-27 | 2025 | 2024 | 2024-08-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Environment | 0.32083 | 0.32083 | 1899-12-31 | 0 | 16.3 | 16.3 | not attend due to heavy rain at site and high wind. | Open | 0.62692 | O2_01 | 45420.6292 |  | WTG Unscheduled Maintenance | 66877 | 45420.6292
1768 | 2024-08-27 | 2025 | 2024 | 2024-08-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down | 0.71944 | 0.71944 | 0.73333 | 0 | 0.33333 | 0.33333 | Checked related error data log apply soft reboot reset & start the WTG. | Close | 0.012821 | O2_01 | 928.8472 |  | WTG Unscheduled Maintenance | 66877 | 928.8472
1769 | 2024-08-27 | 2025 | 2024 | 2024-08-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 4540 | Tower oscillation X level 2 | Break down | 0.86319 | 0.86319 | 0.87014 | 0 | 0.16667 | 0.16667 | Checked related error data log then reset & start WTG. | Close | 0.0064103 | O2_01 | 464.4236 |  | WTG Unscheduled Maintenance | 66877 | 464.4236
1770 | 2024-08-27 | 2025 | 2024 | 2024-08-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 518 | Pitch limit switch 3 | Environment | 0 | 0 | 1899-12-31 | 0 | 24 | 24 | not attend due to heavy rain at site and approach road problem. | Open | 0.92308 | O2_11 | 62281 |  | WTG Unscheduled Maintenance | 62281 | 62281
1771 | 2024-08-27 | 2025 | 2024 | 2024-08-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Road issue | 0 | 0 | 1899-12-31 | 0 | 24 | 24 | not attend due to heavy rain at site and approach road problem. | Open | 0.92308 | O2_02 | 17578 |  | WTG Unscheduled Maintenance | 17578 | 17578
1772 | 2024-08-27 | 2025 | 2024 | 2024-08-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Connectivity issue | 0 | 0 | 0.72153 | 0 | 17.3167 | 17.3167 | wtg is not cannected scada so cannectivity restoration work done then start wtg (late attend due to heavy rain at site and approach road problem) | Close | 0.66603 | O2_05 | 0 |  | WTG Unscheduled Maintenance | 0 | 0
1773 | 2024-08-28 | 2025 | 2024 | 2024-08-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.59028 | 0.59028 | 0.59167 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & start WTG. | Close | 0.0012821 | O2_26 | 84.0653 |  | WTG Unscheduled Maintenance | 60527 | 84.0653
1774 | 2024-08-28 | 2025 | 2024 | 2024-08-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down | 0.62639 | 0.62639 | 0.64514 | 0 | 0.45 | 0.45 | Checked related error data log apply soft reboot reset & start the WTG. | Close | 0.017308 | O2_26 | 1134.8813 |  | WTG Unscheduled Maintenance | 60527 | 1134.8813
1775 | 2024-08-28 | 2025 | 2024 | 2024-08-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down | 0.68472 | 0.68472 | 0.69722 | 0 | 0.3 | 0.3 | Checked related error data log apply soft reboot reset & start the WTG. | Close | 0.011538 | O2_26 | 756.5875 |  | WTG Unscheduled Maintenance | 60527 | 756.5875
1776 | 2024-08-28 | 2025 | 2024 | 2024-08-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.54444 | 0.54444 | 0.56181 | 0 | 0.41667 | 0.41667 | Checked related error data log apply soft reboot reset & start the WTG. | Close | 0.016026 | O2_05 | 318.4722 |  | WTG Unscheduled Maintenance | 18344 | 318.4722
1777 | 2024-08-28 | 2025 | 2024 | 2024-08-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.56667 | 0.56667 | 0.57431 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & start WTG. | Close | 0.0070513 | O2_05 | 140.1278 |  | WTG Unscheduled Maintenance | 18344 | 140.1278
1778 | 2024-08-28 | 2025 | 2024 | 2024-08-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.62292 | 0.62292 | 0.63958 | 0 | 0.4 | 0.4 | Checked related error data log apply soft reboot reset & start the WTG. | Close | 0.015385 | O2_05 | 305.7333 |  | WTG Unscheduled Maintenance | 18344 | 305.7333
1779 | 2024-08-28 | 2025 | 2024 | 2024-08-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.90069 | 0.90069 | 0.91736 | 0 | 0.4 | 0.4 | Checked related error data log apply soft reboot reset & start the WTG. | Close | 0.015385 | O2_05 | 305.7333 |  | WTG Unscheduled Maintenance | 18344 | 305.7333
1780 | 2024-08-28 | 2025 | 2024 | 2024-08-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 1055 | Max. drivetrain oscillations | Break down | 0.56528 | 0.56528 | 0.56806 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & start WTG. | Close | 0.0025641 | O2_09 | 166.4889 |  | WTG Unscheduled Maintenance | 59936 | 166.4889
1781 | 2024-08-28 | 2025 | 2024 | 2024-08-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 1055 | Max. drivetrain oscillations | Break down | 0.61319 | 0.61319 | 0.62083 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & start WTG. | Close | 0.0070513 | O2_09 | 457.8444 |  | WTG Unscheduled Maintenance | 59936 | 457.8444
1782 | 2024-08-28 | 2025 | 2024 | 2024-08-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.87431 | 0.87431 | 0.89861 | 0 | 0.58333 | 0.58333 | Checked related error data log apply soft reboot reset & start the WTG. | Close | 0.022436 | O2_09 | 1456.7778 |  | WTG Unscheduled Maintenance | 59936 | 1456.7778
1783 | 2024-08-28 | 2025 | 2024 | 2024-08-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Major BD | 0 | 0 | 0.68056 | 0 | 16.3333 | 16.3333 | attend and found VCB trip so check all related circuit found no any abnormality so charge VCB . | Close | 0.62821 | O2_02 | 37646.9722 |  | WTG Unscheduled Maintenance | 55318 | 37646.9722
1784 | 2024-08-28 | 2025 | 2024 | 2024-08-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Road issue | 0.68056 | 0.68056 | 0.71736 | 0 | 0.88333 | 0.88333 | then VCB cherge. attend check all related circuit found temp. sensor faulty so replace it and start wtg.(late attend due to heavy rain at site and approach road problem.) | Close | 0.033974 | O2_02 | 2036.0097 |  | WTG Unscheduled Maintenance | 55318 | 2036.0097
1785 | 2024-08-28 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 1055 | Max. drivetrain oscillations | Break down | 0.37986 | 0.37986 | 0.40417 | 0 | 0.58333 | 0.58333 | Checked related error data log apply soft reboot reset & start the WTG. | Close | 0.022436 | O2_21 | 1590.191 |  | WTG Unscheduled Maintenance | 65425 | 1590.191
1786 | 2024-08-28 | 2025 | 2024 | 2024-08-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 4540 | Tower oscillation X level 2 | Break down | 0.52778 | 0.52778 | 0.53819 | 0 | 0.25 | 0.25 | Checked related error data log then reset & start WTG. | Close | 0.0096154 | O2_21 | 681.5104 |  | WTG Unscheduled Maintenance | 65425 | 681.5104
1787 | 2024-08-28 | 2025 | 2024 | 2024-08-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down | 0.57292 | 0.57292 | 0.58056 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & start WTG. | Close | 0.0070513 | O2_03 | 471.0521 |  | WTG Unscheduled Maintenance | 61665 | 471.0521
1788 | 2024-08-28 | 2025 | 2024 | 2024-08-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down | 0.63681 | 0.63681 | 0.64444 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & start WTG. | Close | 0.0070513 | O2_11 | 493.3653 |  | WTG Unscheduled Maintenance | 64586 | 493.3653
1789 | 2024-08-28 | 2025 | 2024 | 2024-08-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Break down | 0.48403 | 0.48403 | 0.49514 | 0 | 0.26667 | 0.26667 | Checked related error data log apply soft reboot reset & start the WTG. | Close | 0.010256 | O2_13 | 713.3444 |  | WTG Unscheduled Maintenance | 64201 | 713.3444
1790 | 2024-08-28 | 2025 | 2024 | 2024-08-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 4540 | Tower oscillation X level 2 | Break down | 0.50347 | 0.50347 | 0.51458 | 0 | 0.26667 | 0.26667 | Checked related error data log apply soft reboot reset & start the WTG. | Close | 0.010256 | O2_13 | 713.3444 |  | WTG Unscheduled Maintenance | 64201 | 713.3444
1791 | 2024-08-28 | 2025 | 2024 | 2024-08-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down | 0.53681 | 0.53681 | 0.54514 | 0 | 0.2 | 0.2 | Checked related error data log apply soft reboot reset & start the WTG. | Close | 0.0076923 | O2_13 | 535.0083 |  | WTG Unscheduled Maintenance | 64201 | 535.0083
1792 | 2024-08-28 | 2025 | 2024 | 2024-08-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down | 0.6 | 0.6 | 0.60486 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & start WTG. | Close | 0.0044872 | O2_13 | 312.0882 |  | WTG Unscheduled Maintenance | 64201 | 312.0882
1793 | 2024-08-28 | 2025 | 2024 | 2024-08-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.55903 | 0.55903 | 0.5625 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & start WTG. | Close | 0.0032051 | O2_15 | 186.7292 |  | WTG Unscheduled Maintenance | 53778 | 186.7292
1794 | 2024-08-28 | 2025 | 2024 | 2024-08-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.39583 | 0.39583 | 0.53056 | 0 | 3.2333 | 3.2333 | attend and check all releted found top panel all modual are not ON so check and found 24v is missing so correct it then start wtg. | Close | 0.12436 | O2_14 | 8645.7986 |  | WTG Unscheduled Maintenance | 64175 | 8645.7986
1795 | 2024-08-28 | 2025 | 2024 | 2024-08-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down | 0.58333 | 0.58333 | 0.59306 | 0 | 0.23333 | 0.23333 | Checked related error data log apply soft reboot reset & start the WTG. | Close | 0.0089744 | O2_14 | 623.9236 |  | WTG Unscheduled Maintenance | 64175 | 623.9236
1796 | 2024-08-28 | 2025 | 2024 | 2024-08-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down | 0.6375 | 0.6375 | 0.64653 | 0 | 0.21667 | 0.21667 | Checked related error data log apply soft reboot reset & start the WTG. | Close | 0.0083333 | O2_14 | 579.3576 |  | WTG Unscheduled Maintenance | 64175 | 579.3576
1797 | 2024-08-28 | 2025 | 2024 | 2024-08-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.38264 | 0.38264 | 0.40417 | 0 | 0.51667 | 0.51667 | Checked related error data log apply soft reboot reset & start the WTG. | Close | 0.019872 | O2_20 | 1169.9056 |  | WTG Unscheduled Maintenance | 54344 | 1169.9056
1798 | 2024-08-28 | 2025 | 2024 | 2024-08-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down | 0.52431 | 0.52431 | 0.53125 | 0 | 0.16667 | 0.16667 | Checked related error data log then reset & start WTG. | Close | 0.0064103 | O2_20 | 377.3889 |  | WTG Unscheduled Maintenance | 54344 | 377.3889
1799 | 2024-08-28 | 2025 | 2024 | 2024-08-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.094444 | 0.094444 | 0.10069 | 0 | 0.15 | 0.15 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.0057692 | O2_20 | 339.65 |  | WTG Unscheduled Maintenance | 54344 | 339.65
1800 | 2024-08-28 | 2025 | 2024 | 2024-08-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 7025 | Configuration error | Break down | 0.094444 | 0.094444 | 0.097917 | 0 | 0.083333 | 0.083333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.0032051 | O2_20 | 188.6944 |  | WTG Unscheduled Maintenance | 54344 | 188.6944
1801 | 2024-08-28 | 2025 | 2024 | 2024-08-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down | 0.575 | 0.575 | 0.57917 | 0 | 0.1 | 0.1 | Checked related error data log then reset & start WTG. | Close | 0.0038462 | O2_20 | 226.4333 |  | WTG Unscheduled Maintenance | 54344 | 226.4333
1802 | 2024-08-28 | 2025 | 2024 | 2024-08-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down | 0.59861 | 0.59861 | 0.60417 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & start WTG. | Close | 0.0051282 | O2_01 | 341.1944 |  | WTG Unscheduled Maintenance | 61415 | 341.1944
1803 | 2024-08-28 | 2025 | 2024 | 2024-08-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 518 | Pitch limit switch 3 | Road issue | 0 | 0 | 1899-12-31 | 0 | 24 | 24 | not attend due to heavy rain at site and approach road problem. | Open | 0.92308 | O2_11 | 64586 |  | WTG Unscheduled Maintenance | 64586 | 64586
1804 | 2024-08-28 | 2025 | 2024 | 2024-08-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Environment | 0 | 0 | 1899-12-31 | 0 | 24 | 24 | not attend due to heavy rain at site and high wind. | Open | 0.92308 | O2_24 | 63437 |  | WTG Unscheduled Maintenance | 63437 | 63437
1805 | 2024-08-28 | 2025 | 2024 | 2024-08-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.094444 | 0.094444 | 0.11806 | 0 | 0.56667 | 0.56667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Open | 0.021795 | O2_24 | 1497.8181 |  | WTG Unscheduled Maintenance | 63437 | 1497.8181
1806 | 2024-08-29 | 2025 | 2024 | 2024-08-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 518 | Pitch limit switch 3 | Environment | 0 | 0 | 0.58333 | 0 | 14 | 14 | not attend due to heavy rain at site and approach road problem. | Close | 0.53846 | O2_13 | 39487 |  | WTG Unscheduled Maintenance | 67692 | 39487
1807 | 2024-08-29 | 2025 | 2024 | 2024-08-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 518 | Pitch limit switch 3 | Break down | 0.58333 | 0.58333 | 0.68056 | 0 | 2.3333 | 2.3333 | Attend and checked related ckt then found battery lug burn out in axis 3. So, remove battery and replaced with new one. Then reset all data log and start the WTG. | Close | 0.089744 | O2_13 | 6581.1667 |  | WTG Unscheduled Maintenance | 67692 | 6581.1667
1808 | 2024-08-29 | 2025 | 2024 | 2024-08-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down | 0.59931 | 0.59931 | 0.80694 | 0 | 4.9833 | 4.9833 | Attend and checked related ckt and data log then checked HU system found filter damage so remove it and reset all data log then run the WTG. | Close | 0.19167 | O2_06 | 13769.9882 |  | WTG Unscheduled Maintenance | 66317 | 13769.9882
1809 | 2024-08-29 | 2025 | 2024 | 2024-08-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Environment | 0 | 0 | 1899-12-31 | 0 | 24 | 24 | not attend due to heavy rain at site and high wind. | Close | 0.92308 | O2_05 | 64101 |  | WTG Unscheduled Maintenance | 64101 | 64101
1810 | 2024-08-29 | 2025 | 2024 | 2024-08-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 567 | Pitch too slow BP52 | Break down | 0.89722 | 0.89722 | 0.90278 | 0 | 0.13333 | 0.13333 | Checked related error data log apply soft reboot reset & start the WTG. | Close | 0.0051282 | O2_05 | 356.1167 |  | WTG Unscheduled Maintenance | 64101 | 356.1167
1811 | 2024-08-29 | 2025 | 2024 | 2024-08-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 1600 | High gear speed | Break down | 0.0083333 | 0.0083333 | 0.020139 | 0 | 0.28333 | 0.28333 | Checked related error data log apply soft reboot reset & start the WTG. | Close | 0.010897 | O2_05 | 756.7479 |  | WTG Unscheduled Maintenance | 64101 | 756.7479
1811 | 2024-08-29 | 2025 | 2024 | 2024-08-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD | 0 | 0 | 0.52361 | 0 | 12.5667 | 12.5667 | wtg grid commissioning work done then start wtg | Close | 0.48333 | O2_02 | 32802.1417 |  | WTG Breakdown Maintenance | 62646 | 32802.1417
1811 | 2024-08-29 | 2025 | 2024 | 2024-08-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Auto reset | 0.15833 | 0.15833 | 0.15972 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2_02 | 87.0083 |  | WTG Unscheduled Maintenance | 62646 | 87.0083
1812 | 2024-08-29 | 2025 | 2024 | 2024-08-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 1600 | High gear speed | Break down | 0.59514 | 0.59514 | 0.61667 | 0 | 0.51667 | 0.51667 | Checked related error data log apply soft reboot reset & start the WTG. | Close | 0.019872 | O2_13 | 1457.2583 |  | WTG Unscheduled Maintenance | 67692 | 1457.2583
1813 | 2024-08-29 | 2025 | 2024 | 2024-08-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 4540 | Tower oscillation X level 2 | Break down | 0.42847 | 0.42847 | 0.43611 | 0 | 0.18333 | 0.18333 | Checked related error data log apply soft reboot reset & start the WTG. | Close | 0.0070513 | O2_20 | 439.5493 |  | WTG Unscheduled Maintenance | 57541 | 439.5493
1814 | 2024-08-29 | 2025 | 2024 | 2024-08-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.46667 | 0.46667 | 0.47361 | 0 | 0.16667 | 0.16667 | Checked related error data log apply soft reboot reset & start the WTG. | Close | 0.0064103 | O2_16 | 414.7569 |  | WTG Unscheduled Maintenance | 59725 | 414.7569
1815 | 2024-08-29 | 2025 | 2024 | 2024-08-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.41319 | 0.41319 | 0.41944 | 0 | 0.15 | 0.15 | Checked related error data log apply soft reboot reset & start the WTG. | Close | 0.0057692 | O2_16 | 373.2813 |  | WTG Unscheduled Maintenance | 59725 | 373.2813
1816 | 2024-08-29 | 2025 | 2024 | 2024-08-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 567 | Pitch too slow BP52 | Break down | 0.56806 | 0.56806 | 0.57917 | 0 | 0.26667 | 0.26667 | Checked related error data log apply soft reboot reset & start the WTG. | Close | 0.010256 | O2_18 | 582.5222 |  | WTG Unscheduled Maintenance | 52427 | 582.5222
1817 | 2024-08-29 | 2025 | 2024 | 2024-08-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down | 0.51111 | 0.51111 | 0.52014 | 0 | 0.21667 | 0.21667 | Checked related error data log apply soft reboot reset & start the WTG. | Close | 0.0083333 | O2_18 | 473.2993 |  | WTG Unscheduled Maintenance | 52427 | 473.2993
1818 | 2024-08-29 | 2025 | 2024 | 2024-08-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down | 0.91875 | 0.91875 | 0.94514 | 0 | 0.63333 | 0.63333 | Checked related error data log apply soft reboot reset & start the WTG. | Close | 0.024359 | O2_01 | 1668.0153 |  | WTG Unscheduled Maintenance | 63209 | 1668.0153
1819 | 2024-08-29 | 2025 | 2024 | 2024-08-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.85417 | 0.85417 | 0.85833 | 0 | 0.1 | 0.1 | Checked related error data log apply soft reboot reset & start the WTG. | Close | 0.0038462 | O2_01 | 263.3708 |  | WTG Unscheduled Maintenance | 63209 | 263.3708
1820 | 2024-08-29 | 2025 | 2024 | 2024-08-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.57292 | 0.57292 | 0.58125 | 0 | 0.2 | 0.2 | Checked related error data log apply soft reboot reset & start the WTG. | Close | 0.0076923 | O2_01 | 526.7417 |  | WTG Unscheduled Maintenance | 63209 | 526.7417
1821 | 2024-08-29 | 2025 | 2024 | 2024-08-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 1600 | High gear speed | Break down | 0.36111 | 0.36111 | 0.37361 | 0 | 0.3 | 0.3 | Checked related error data log apply soft reboot reset & start the WTG. | Close | 0.011538 | O2_01 | 790.1125 |  | WTG Unscheduled Maintenance | 63209 | 790.1125
1822 | 2024-08-30 | 2025 | 2024 | 2024-08-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 551 | Pitch motor current too high | Break down | 0.053472 | 0.053472 | 0.09375 | 0 | 0.96667 | 0.96667 | Checked related error data log apply soft reboot reset & start the WTG. | Close | 0.037179 | O2_10 | 1316.6806 |  | WTG Unscheduled Maintenance | 32690 | 1316.6806
1823 | 2024-08-30 | 2025 | 2024 | 2024-08-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 780 | Error bridging start-up | Break down | 0.95347 | 0.95347 | 0.96875 | 0 | 0.36667 | 0.36667 | Checked related error data log apply soft reboot reset & start the WTG. | Close | 0.014103 | O2_10 | 499.4306 |  | WTG Unscheduled Maintenance | 32690 | 499.4306
1823 | 2024-08-30 | 2025 | 2024 | 2024-08-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3570 | Grid error | Project pending work | 0.53958 | 0.53958 | 1899-12-31 | 0 | 11.05 | 11.05 | wtg manual stop for by project team for O2_07 & O2_04 line jumper opening and ofc cable laying work. | Close | 0.425 | O2_02 | 15626.5417 |  | WTG Unscheduled Maintenance | 33940 | 15626.5417
1824 | 2024-08-30 | 2025 | 2024 | 2024-08-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0 | 0 | 0.1875 | 0 | 4.5 | 4.5 | Attend and checked related error data log then checked all three blades and all axis connection found 230v mcb axis 1 machanism not working so replaced it. Then checked resistance found axis 1 chopper resistor so replaced with new one. Then reset all data log and run the turbine under observation. | Close | 0.17308 | O2_05 | 6061.5 |  | WTG Unscheduled Maintenance | 32328 | 6061.5
1825 | 2024-08-30 | 2025 | 2024 | 2024-08-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 88 | Outs.temp. nacelle implaus. | Break down | 0.25 | 0.25 | 0.27639 | 0 | 0.63333 | 0.63333 | Checked related error data log apply soft reboot reset & start the WTG. | Close | 0.024359 | O2_01 | 894.0028 |  | WTG Unscheduled Maintenance | 33878 | 894.0028
1826 | 2024-08-30 | 2025 | 2024 | 2024-08-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.51389 | 0.51389 | 0.68819 | 0 | 4.1833 | 4.1833 | Attend and checked outside naccele temp. related error data log then found naccele outside temp. malfunctioning. So, interchage to bottom temp. sensor. Also checked blade 2 high current related data and ckt so found 1nos. 4amps rectifier fuse failure so, replaced it. After done all activity then reset all data and run the turbine. | Close | 0.1609 | O2_01 | 5905.1236 |  | WTG Breakdown Maintenance | 33878 | 5905.1236
1827 | 2024-08-30 | 2025 | 2024 | 2024-08-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 65 | Absence of wind during run-up | Break down | 0.97222 | 0.97222 | 1899-12-31 | 0 | 0.66667 | 0.66667 | Attend and checked related data and furthur turbine restoration work in progress. | Close | 0.025641 | O2_01 | 941.0556 |  | WTG Unscheduled Maintenance | 33878 | 941.0556
1828 | 2024-08-31 | 2025 | 2024 | 2024-08-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.61181 | 0.61181 | 0.69444 | 0 | 1.9833 | 1.9833 | WTG manual stop for power curve rectification work. So, done rectification then reset and run the turbine. | Close | 0.076282 | O2_13 | 704.4139 |  | WTG Breakdown Maintenance | 8524 | 704.4139
1829 | 2024-08-31 | 2025 | 2024 | 2024-08-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Ladder issue | 0.47569 | 0.47569 | 0.5125 | 0 | 0.88333 | 0.88333 | WTG manual stop for ladder replacement work. | Close | 0.033974 | O2_10 | 307.1056 |  | WTG Breakdown Maintenance | 8344 | 307.1056
1830 | 2024-08-31 | 2025 | 2024 | 2024-08-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Ladder issue | 0.55 | 0.55 | 0.75903 | 0 | 5.0167 | 5.0167 | WTG manual stop for ladder replacement work. | Close | 0.19295 | O2_10 | 1744.1278 |  | WTG Breakdown Maintenance | 8344 | 1744.1278
1831 | 2024-08-31 | 2025 | 2024 | 2024-08-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.58264 | 0.58264 | 0.68819 | 0 | 2.5333 | 2.5333 | Attend and checked related ckt then found axis 3 chopper resistor failure. So, replaced it with new one then reset and run the turbine. | Close | 0.097436 | O2_06 | 1175.7833 |  | WTG Unscheduled Maintenance | 11139 | 1175.7833
1831 | 2024-08-31 | 2025 | 2024 | 2024-08-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3570 | Grid error | Project pending work | 0 | 0 | 1899-12-31 | 0 | 24 | 24 | wtg manual stop for by project team for O2_07 & O2_04 line jumper opening and ofc cable laying work. | Close | 0.92308 | O2_02 | 9061 |  | WTG Unscheduled Maintenance | 9061 | 9061
1832 | 2024-08-31 | 2025 | 2024 | 2024-08-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0 | 0 | 0.22222 | 0 | 5.3333 | 5.3333 | Attend and checked related error data log and also checked all ckt. Checked all DIO input respect to ckt diagram, also measure 24vdc. Checked all 3 blade connection and also chcked center box connection then center box found lots of silica gel inside. So, remove it and proper clean it. Then reset all data but after that battery charger all axis error occured so chcked all input connection then found center boc rotary switch inside silica gel stuck and its machanism not working properly. So proper clean it then reset and run the turbine. | Close | 0.20513 | O2_01 | 1656.4444 |  | WTG Unscheduled Maintenance | 7454 | 1656.4444
1833 | 2024-08-31 | 2025 | 2024 | 2024-08-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down | 0.72917 | 0.72917 | 0.80208 | 0 | 1.75 | 1.75 | Attend and checked respective ckt and error data log. Then checked error related hydraulic unit and its connection and valve. Doing properly flushing then checked pressure and its build up. So, reset and run the turbine under observation. | Close | 0.067308 | O2_01 | 543.5208 |  | WTG Unscheduled Maintenance | 7454 | 543.5208
1834 | 2024-09-01 | 2025 | 2024 | 2024-09-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 1600 | High gear speed | Break down | 0.95 | 0.95 | 0.97569 | 0 | 0.61667 | 0.61667 | Checked related error data log apply soft reboot reset & start the WTG. | Close | 0.023718 | O2_05 | 303 |  | WTG Unscheduled Maintenance | 11790 | 302.9375
1834 | 2024-09-01 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Project pending work | 0 | 0 | 1899-12-31 | 0 | 24 | 24 | wtg manual stop for by project team for O2_07 & O2_04 line jumper opening and ofc cable laying work. | Close | 0.92308 | O2_02 | 303 |  | WTG Unscheduled Maintenance | 11910 | 11910
1835 | 2024-09-01 | 2025 | 2024 | 2024-09-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Break down | 0.020833 | 0.020833 | 0.022222 | 0 | 0.033333 | 0.033333 | Checked related error data log apply soft reboot reset & start the WTG. | Close | 0.0012821 | O2_11 | 13 |  | WTG Unscheduled Maintenance | 9039 | 12.5542
1836 | 2024-09-01 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 4093 | Rel. air hum. tower base inside too high (in operation) | Break down | 0.23125 | 0.23125 | 0.23681 | 0 | 0.13333 | 0.13333 | Checked related error data log apply soft reboot reset & start the WTG. | Close | 0.0051282 | O2_06 | 76 |  | WTG Unscheduled Maintenance | 13600 | 75.5556
1837 | 2024-09-02 | 2025 | 2024 | 2024-09-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Break down | 0.30139 | 0.30139 | 0.30347 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | O2_05 | 20.7583 |  | WTG Unscheduled Maintenance | 9964 | 20.7583
1838 | 2024-09-02 | 2025 | 2024 | 2024-09-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.039583 | 0.039583 | 0.040972 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & start WTG. | Close | 0.0012821 | O2_11 | 9.6167 |  | WTG Unscheduled Maintenance | 6924 | 9.6167
1838 | 2024-09-02 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Project pending work | 0 | 0 | 0.45139 | 0 | 10.8333 | 10.8333 | wtg manual stop for by project team for O2_07 & O2_04 line jumper opening and ofc cable laying work. | Close | 0.41667 | O2_02 | 4941.3542 |  | WTG Unscheduled Maintenance | 10947 | 4941.3542
1838 | 2024-09-02 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Project pending work | 0.70139 | 0.70139 | 1899-12-31 | 0 | 7.1667 | 7.1667 | wtg manual stop for by project team for O2_07 & O2_04 line jumper opening and ofc cable laying work. | Close | 0.27564 | O2_02 | 3268.8958 |  | WTG Unscheduled Maintenance | 10947 | 3268.8958
1839 | 2024-09-02 | 2025 | 2024 | 2024-09-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.71181 | 0.71181 | 0.74375 | 0 | 0.76667 | 0.76667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.029487 | O2_13 | 224.1222 |  | WTG Unscheduled Maintenance | 7016 | 224.1222
1840 | 2024-09-02 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 4093 | Rel. air hum. tower base inside too high (in operation) | Break down | 0.26736 | 0.26736 | 0.29306 | 0 | 0.61667 | 0.61667 | Checked related error data log then reset & start WTG. | Close | 0.023718 | O2_06 | 240.0889 |  | WTG Unscheduled Maintenance | 9344 | 240.0889
1841 | 2024-09-02 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Break down | 0.98264 | 0.98264 | 0.98611 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & start WTG. | Close | 0.0032051 | O2_06 | 32.4444 |  | WTG Unscheduled Maintenance | 9344 | 32.4444
1842 | 2024-09-02 | 2025 | 2024 | 2024-09-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.71181 | 0.71181 | 0.8625 | 0 | 3.6167 | 3.6167 | After grid resume then error occurred so, attend and checked related ckt then found F5 SPD feedback connection loos. So, tight it also checked UPSnfeedback related ckt then reset and run the turbine. | Close | 0.1391 | O2_01 | 1251.9694 |  | WTG Unscheduled Maintenance | 8308 | 1251.9694
1843 | 2024-09-02 | 2025 | 2024 | 2024-09-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.95139 | 0.95139 | 1899-12-31 | 0 | 1.1667 | 1.1667 | Attend and checked related error data log and also checked all ckt. Checked all DIO input respect to ckt diagram, also measure 24vdc. Checked all 3 blade connection and also chcked center box connection then center box found lots of silica gel inside. So, remove it and proper clean it. Then reset all data but after that battery charger all axis error occured so chcked all input connection then found center boc rotary switch inside silica gel stuck and its machanism not working properly. Furthur turbine restoration work in progress... | Open | 0.044872 | O2_01 | 403.8611 |  | WTG Unscheduled Maintenance | 8308 | 403.8611
1844 | 2024-09-03 | 2025 | 2024 | 2024-09-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Ladder issue | 0.54097 | 0.54097 | 0.81181 | 0 | 6.5 | 6.5 | Manual stop By project team for ladder rectification Work | Close | 0.25 | O2_02 | 3931.6875 |  | WTG Breakdown Maintenance | 14517 | 3931.6875
1845 | 2024-09-03 | 2025 | 2024 | 2024-09-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.49028 | 0.49028 | 0.52292 | 0 | 0.78333 | 0.78333 | Manual stop By project team for pending work | Close | 0.030128 | O2_26 | 485.1444 |  | WTG Breakdown Maintenance | 14864 | 485.1444
1846 | 2024-09-03 | 2025 | 2024 | 2024-09-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.87292 | 0.87292 | 0.87431 | 0 | 0.033333 | 0.033333 | Auto reseted | Close | 0.0012821 | O2_05 | 16.0583 |  | WTG Unscheduled Maintenance | 11562 | 16.0583
1847 | 2024-09-03 | 2025 | 2024 | 2024-09-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.014583 | 0.014583 | 0.038194 | 0 | 0.56667 | 0.56667 | Check error data than reset and start Wtg. | Close | 0.021795 | O2_09 | 288.6222 |  | WTG Unscheduled Maintenance | 12224 | 288.6222
1848 | 2024-09-03 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.16806 | 0.16806 | 0.16944 | 0 | 0.033333 | 0.033333 | Check error data than reset and start Wtg. | Close | 0.0012821 | O2_18 | 14.5042 |  | WTG Unscheduled Maintenance | 10443 | 14.5042
1849 | 2024-09-03 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 4093 | Rel. air hum. tower base inside too high (in operation) | Break down | 0.33611 | 0.33611 | 0.37083 | 0 | 0.83333 | 0.83333 | Check error data than reset and start Wtg. | Close | 0.032051 | O2_18 | 362.6042 |  | WTG Unscheduled Maintenance | 10443 | 362.6042
1850 | 2024-09-03 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.46319 | 0.46319 | 0.47153 | 0 | 0.2 | 0.2 | Check error data than apply soft reboot than reset and start WTG. | Close | 0.0076923 | O2_18 | 87.025 |  | WTG Unscheduled Maintenance | 10443 | 87.025
1851 | 2024-09-03 | 2025 | 2024 | 2024-09-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Break down | 0.93958 | 0.93958 | 0.96389 | 0 | 0.58333 | 0.58333 | After grid resume Wtg in error so check data and reset and start WTG | Close | 0.022436 | O2_13 | 266.0729 |  | WTG Unscheduled Maintenance | 10947 | 266.0729
1852 | 2024-09-03 | 2025 | 2024 | 2024-09-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.0069444 | 0.0069444 | 0.0097222 | 0 | 0.066667 | 0.066667 | Check error data than reset and start Wtg. | Close | 0.0025641 | O2_14 | 30.5083 |  | WTG Unscheduled Maintenance | 10983 | 30.5083
1853 | 2024-09-03 | 2025 | 2024 | 2024-09-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.93958 | 0.93958 | 0.96389 | 0 | 0.58333 | 0.58333 | After grid resume Wtg in error so check data and reset and start WTG | Close | 0.022436 | O2_14 | 266.9479 |  | WTG Unscheduled Maintenance | 10983 | 266.9479
1854 | 2024-09-03 | 2025 | 2024 | 2024-09-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.93958 | 0.93958 | 0.96458 | 0 | 0.6 | 0.6 | After grid resume Wtg in error so check data and reset and start WTG | Close | 0.023077 | O2_12 | 271.575 |  | WTG Unscheduled Maintenance | 10863 | 271.575
1855 | 2024-09-03 | 2025 | 2024 | 2024-09-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 4555 | Tower accel. difference | Break down | 0.90417 | 0.90417 | 0.90833 | 0 | 0.1 | 0.1 | Auto reseted | Close | 0.0038462 | O2_10 | 40.1 |  | WTG Unscheduled Maintenance | 9624 | 40.1
1856 | 2024-09-03 | 2025 | 2024 | 2024-09-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Break down | 0.93958 | 0.93958 | 0.96597 | 0 | 0.63333 | 0.63333 | After grid resume Wtg in error so check data and reset and start WTG | Close | 0.024359 | O2_10 | 253.9667 |  | WTG Unscheduled Maintenance | 9624 | 253.9667
1857 | 2024-09-03 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.20278 | 0.20278 | 0.20417 | 0 | 0.033333 | 0.033333 | Check error data than apply soft reboot than reset and start WTG. | Close | 0.0012821 | O2_06 | 15.6236 |  | WTG Unscheduled Maintenance | 11249 | 15.6236
1858 | 2024-09-03 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.86736 | 0.86736 | 0.95833 | 0 | 2.1833 | 2.1833 | Attend and check related circuit than nothing found abnormal than apply soft reboot than reset and start WTG. | Close | 0.083974 | O2_06 | 1023.3465 |  | WTG Unscheduled Maintenance | 11249 | 1023.3465
1859 | 2024-09-03 | 2025 | 2024 | 2024-09-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.44653 | 0.44653 | 0.63542 | 0 | 4.5333 | 4.5333 | Wtg stop for 1st month maintenance day-2 | Close | 0.17436 | O2_06 | 2124.8111 |  | WTG Scheduled Maintenance | 11249 | 2124.8111
1860 | 2024-09-03 | 2025 | 2024 | 2024-09-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.95903 | 0.95903 | 0.97569 | 0 | 0.4 | 0.4 | Check error data than apply soft reboot than reset and start WTG. | Close | 0.015385 | O2_20 | 202.1667 |  | WTG Unscheduled Maintenance | 12130 | 202.1667
1860 | 2024-09-03 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Project pending work | 0 | 0 | 0.50139 | 0 | 12.0333 | 12.0333 | wtg manual stop for by project team for O2_07 & O2_04 line jumper opening and ofc cable laying work complete then start wtg | Close | 0.46282 | O2_02 | 7278.6625 |  | WTG Unscheduled Maintenance | 14517 | 7278.6625
1860 | 2024-09-03 | 2025 | 2024 | 2024-09-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0 | 0 | 0.59792 | 0 | 14.35 | 14.35 | wtg grid commissioning work done then start wtg | Close | 0.55192 | O2_02 | 8679.9562 |  | WTG Breakdown Maintenance | 14517 | 8679.9562
1861 | 2024-09-03 | 2025 | 2024 | 2024-09-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.93958 | 0.93958 | 0.96458 | 0 | 0.6 | 0.6 | After grid resume Wtg in error so check data and reset and start WTG | Close | 0.023077 | O2_02 | 362.925 |  | WTG Unscheduled Maintenance | 14517 | 362.925
1862 | 2024-09-03 | 2025 | 2024 | 2024-09-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Major BD | 0 | 0 | 0.92569 | 0 | 22.2167 | 22.2167 | Attend and check related circuit than furthur troublshooting WIP….. | Open | 0.85449 | O2_01 | 11652.6417 |  | WTG Unscheduled Maintenance | 12588 | 11652.6417
1863 | 2024-09-03 | 2025 | 2024 | 2024-09-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.93889 | 0.93889 | 0.99999 | 0 | 1.4664 | 1.4664 | Attend and check related circuit than furthur troublshooting WIP….. | Open | 0.0564 | O2_01 | 769.121 |  | WTG Unscheduled Maintenance | 12588 | 769.121
1864 | 2024-09-04 | 2025 | 2024 | 2024-09-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.32569 | 0.32569 | 0.32778 | 0 | 0.05 | 0.05 | Check error data than reset and start Wtg. | Close | 0.0019231 | O2_05 | 39.7 |  | WTG Unscheduled Maintenance | 19056 | 39.7
1865 | 2024-09-04 | 2025 | 2024 | 2024-09-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.33125 | 0.33125 | 0.33333 | 0 | 0.05 | 0.05 | Check error data than reset and start Wtg. | Close | 0.0019231 | O2_05 | 39.7 |  | WTG Unscheduled Maintenance | 19056 | 39.7
1866 | 2024-09-04 | 2025 | 2024 | 2024-09-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.52847 | 0.52847 | 0.7375 | 0 | 5.0167 | 5.0167 | Attend and replace ledder splicing work done by project team | Close | 0.19295 | O2_11 | 3197.4979 |  | WTG Breakdown Maintenance | 15297 | 3197.4979
1867 | 2024-09-04 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 25 | Manual stop without login | Schedule WTG PM | 0.4 | 0.4 | 0.69444 | 0 | 7.0667 | 7.0667 | Wtg stop for 1st month maintenance day-1 | Close | 0.27179 | O2_18 | 5272.0278 |  | WTG Unscheduled Maintenance | 17905 | 5272.0278
1867 | 2024-09-04 | 2025 | 2024 | 2024-09-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Schedule WTG PM | 0.072917 | 0.072917 | 0.47708 | 0 | 9.7 | 9.7 | Check error data than apply soft reboot than reset and start WTG.(late reset due to no connectivity) | Close | 0.37308 | O2_18 | 7236.6042 |  | WTG Unscheduled Maintenance | 17905 | 7236.6042
1868 | 2024-09-04 | 2025 | 2024 | 2024-09-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.41181 | 0.41181 | 0.41319 | 0 | 0.033333 | 0.033333 | Check error data than reset and start Wtg. | Close | 0.0012821 | O2_14 | 21.4708 |  | WTG Unscheduled Maintenance | 15459 | 21.4708
1869 | 2024-09-04 | 2025 | 2024 | 2024-09-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.93264 | 0.93264 | 0.93403 | 0 | 0.033333 | 0.033333 | Check error data than reset and start Wtg. | Close | 0.0012821 | O2_14 | 21.4708 |  | WTG Unscheduled Maintenance | 15459 | 21.4708
1870 | 2024-09-04 | 2025 | 2024 | 2024-09-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.99375 | 0.99375 | 1899-12-31 | 0 | 0.15 | 0.15 | Check error data than reset and start Wtg. | Close | 0.0057692 | O2_14 | 96.6187 |  | WTG Unscheduled Maintenance | 15459 | 96.6187
1871 | 2024-09-04 | 2025 | 2024 | 2024-09-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.33264 | 0.33264 | 0.34167 | 0 | 0.21667 | 0.21667 | Check error data than reset and start Wtg. | Close | 0.0083333 | O2_11 | 138.0979 |  | WTG Unscheduled Maintenance | 15297 | 138.0979
1872 | 2024-09-04 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.12361 | 0.12361 | 0.21944 | 0 | 2.3 | 2.3 | Check error data than apply soft reboot than reset and start WTG. | Close | 0.088462 | O2_06 | 1067.4875 |  | WTG Unscheduled Maintenance | 11139 | 1067.4875
1873 | 2024-09-04 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 4093 | Rel. air hum. tower base inside too high (in operation) | Break down | 0.34653 | 0.34653 | 0.38819 | 0 | 1 | 1 | Check error data than reset and start Wtg. | Close | 0.038462 | O2_06 | 464.125 |  | WTG Unscheduled Maintenance | 11139 | 464.125
1874 | 2024-09-04 | 2025 | 2024 | 2024-09-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.49167 | 0.49167 | 0.56597 | 0 | 1.7833 | 1.7833 | Check error data than reset and start Wtg. | Close | 0.06859 | O2_06 | 827.6896 |  | WTG Breakdown Maintenance | 11139 | 827.6896
1875 | 2024-09-04 | 2025 | 2024 | 2024-09-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.29792 | 0.29792 | 0.32708 | 0 | 0.7 | 0.7 | Check error data than apply soft reboot than reset and start WTG. | Close | 0.026923 | O2_14 | 450.8875 |  | WTG Unscheduled Maintenance | 15459 | 450.8875
1876 | 2024-09-04 | 2025 | 2024 | 2024-09-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Major BD | 0 | 0 | 0.58333 | 0 | 14 | 14 | Attend and check related circuit than found Axis 3 PPD Faulty so replace witn new one. | Close | 0.53846 | O2_01 | 9979.0833 |  | WTG Unscheduled Maintenance | 17107 | 9979.0833
1877 | 2024-09-05 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.46042 | 0.46042 | 0.67014 | 0 | 5.0333 | 5.0333 | Wtg stop for 1st month maintenance day-2 | Close | 0.19359 | O2_18 | 3400.4361 |  | WTG Scheduled Maintenance | 16214 | 3400.4361
1878 | 2024-09-05 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.055556 | 0.055556 | 0.05625 | 0 | 0.016667 | 0.016667 | Check error data than reset and start Wtg. | Close | 0.00064103 | O2_18 | 11.2597 |  | WTG Unscheduled Maintenance | 16214 | 11.2597
1879 | 2024-09-05 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.27639 | 0.27639 | 0.27778 | 0 | 0.033333 | 0.033333 | Check error data than reset and start Wtg. | Close | 0.0012821 | O2_18 | 22.5194 |  | WTG Unscheduled Maintenance | 16214 | 22.5194
1879 | 2024-09-05 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Road issue | 0.70278 | 0.70278 | 0.99653 | 0 | 7.05 | 7.05 | Wtg in error but coonectivity is not available and also road not approchable. | Close | 0.27115 | O2_18 | 4762.8625 |  | WTG Unscheduled Maintenance | 16214 | 4762.8625
1879 | 2024-09-05 | 2025 | 2024 | 2024-09-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Road issue | 0.57986 | 0.57986 | 0.99653 | 0 | 10 | 10 | Wtg in error but coonectivity is not available and also road not approchable. | Close | 0.38462 | O2_18 | 6755.8333 |  | WTG Unscheduled Maintenance | 16214 | 6755.8333
1880 | 2024-09-05 | 2025 | 2024 | 2024-09-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 1600 | High gear speed | Break down | 0.60833 | 0.60833 | 0.61597 | 0 | 0.18333 | 0.18333 | Check error data than reset and start Wtg. | Close | 0.0070513 | O2_14 | 153.2285 |  | WTG Unscheduled Maintenance | 20059 | 153.2285
1881 | 2024-09-05 | 2025 | 2024 | 2024-09-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0 | 0 | 0.0041667 | 0 | 0.1 | 0.1 | Check error data than reset and start Wtg. | Close | 0.0038462 | O2_14 | 83.5792 |  | WTG Unscheduled Maintenance | 20059 | 83.5792
1882 | 2024-09-05 | 2025 | 2024 | 2024-09-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.77986 | 0.77986 | 0.78125 | 0 | 0.033333 | 0.033333 | Check error data than reset and start Wtg. | Close | 0.0012821 | O2_14 | 27.8597 |  | WTG Unscheduled Maintenance | 20059 | 27.8597
1883 | 2024-09-05 | 2025 | 2024 | 2024-09-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Ladder issue | 0.48125 | 0.48125 | 0.75486 | 0 | 6.5667 | 6.5667 | WTG Attend and Ladder Splicing work by Project Team | Close | 0.25256 | O2_12 | 7837.5903 |  | WTG Breakdown Maintenance | 28645 | 7837.5903
1884 | 2024-09-05 | 2025 | 2024 | 2024-09-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 551 | Pitch motor current too high | Break down | 0.86597 | 0.86597 | 0.86736 | 0 | 0.033333 | 0.033333 | Check error data than reset and start Wtg. | Close | 0.0012821 | O2_10 | 33.5222 |  | WTG Unscheduled Maintenance | 24136 | 33.5222
1885 | 2024-09-05 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 4093 | Rel. air hum. tower base inside too high (in operation) | Break down | 0.19028 | 0.19028 | 0.19236 | 0 | 0.05 | 0.05 | Check error data than reset and start Wtg. | Close | 0.0019231 | O2_06 | 50.0604 |  | WTG Unscheduled Maintenance | 24029 | 50.0604
1886 | 2024-09-05 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3063 | Conv. emerg.off type D | Break down | 0.22917 | 0.22917 | 0.2375 | 0 | 0.2 | 0.2 | Check error data than reset and start Wtg. | Close | 0.0076923 | O2_06 | 200.2417 |  | WTG Unscheduled Maintenance | 24029 | 200.2417
1887 | 2024-09-05 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 4093 | Rel. air hum. tower base inside too high (in operation) | Break down | 0.36528 | 0.36528 | 0.38125 | 0 | 0.38333 | 0.38333 | Check error data than reset and start Wtg. | Close | 0.014744 | O2_06 | 383.7965 |  | WTG Unscheduled Maintenance | 24029 | 383.7965
1888 | 2024-09-05 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.53542 | 0.53542 | 0.57917 | 0 | 1.05 | 1.05 | Attend and project pending work done than start wtg | Close | 0.040385 | O2_06 | 1051.2688 |  | WTG Breakdown Maintenance | 24029 | 1051.2688
1889 | 2024-09-05 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.70833 | 0.70833 | 0.78125 | 0 | 1.75 | 1.75 | Check error data than apply soft reboot than reset and start WTG. | Close | 0.067308 | O2_06 | 1752.1146 |  | WTG Unscheduled Maintenance | 24029 | 1752.1146
1890 | 2024-09-05 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Road issue | 0.78403 | 0.78403 | 1899-12-31 | 0 | 5.1833 | 5.1833 | WTG not attending due to Road not approchable | Open | 0.19936 | O2_06 | 5189.5965 |  | WTG Unscheduled Maintenance | 24029 | 5189.5965
1891 | 2024-09-05 | 2025 | 2024 | 2024-09-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.26528 | 0.26528 | 0.26667 | 0 | 0.033333 | 0.033333 | Check error data than reset and start Wtg. | Close | 0.0012821 | O2_06 | 33.3736 |  | WTG Unscheduled Maintenance | 24029 | 33.3736
1992 | 2024-09-05 | 2025 | 2024 | 2024-09-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.82917 | 0.82917 | 0.83056 | 0 | 0.033333 | 0.033333 | Check error data than reset and start Wtg. | Close | 0.0012821 | O2_06 | 33.3736 |  | WTG Unscheduled Maintenance | 24029 | 33.3736
1993 | 2024-09-06 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Road issue | 0.12014 | 0.12014 | 0.41528 | 0 | 7.0833 | 7.0833 | Wtg in error but coonectivity is not available and also road not approchable. | Close | 0.27244 | O2_07 | 2807.3611 |  | WTG Unscheduled Maintenance | 9512 | 2807.3611
1994 | 2024-09-06 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.55208 | 0.55208 | 0.55347 | 0 | 0.033333 | 0.033333 | Check error data than reset and start Wtg. | Close | 0.0012821 | O2_07 | 13.2111 |  | WTG Unscheduled Maintenance | 9512 | 13.2111
1995 | 2024-09-06 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.85486 | 0.85486 | 0.85625 | 0 | 0.033333 | 0.033333 | Check error data than reset and start Wtg. | Close | 0.0012821 | O2_07 | 13.2111 |  | WTG Unscheduled Maintenance | 9512 | 13.2111
1996 | 2024-09-06 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.39792 | 0.39792 | 0.39931 | 0 | 0.033333 | 0.033333 | Check error data than reset and start Wtg. | Close | 0.0012821 | O2_18 | 1.5361 |  | WTG Unscheduled Maintenance | 1106 | 1.5361
1997 | 2024-09-06 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Break down | 0.48264 | 0.48264 | 0.48958 | 0 | 0.16667 | 0.16667 | Check error data than reset and start Wtg. | Close | 0.0064103 | O2_18 | 7.6806 |  | WTG Unscheduled Maintenance | 1106 | 7.6806
1998 | 2024-09-06 | 2025 | 2024 | 2024-09-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Connectivity issue | 0 | 0 | 0.41667 | 0 | 10 | 10 | Wtg stop By project team due to connectivity issue | Close | 0.38462 | O2_04 | 4928.3333 |  | WTG Breakdown Maintenance | 11828 | 4928.3333
1999 | 2024-09-06 | 2025 | 2024 | 2024-09-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.48264 | 0.48264 | 0.54653 | 0 | 1.5333 | 1.5333 | after grid resume Wtg in error but coonectivity is not available so late start. | Close | 0.058974 | O2_04 | 755.6778 |  | WTG Unscheduled Maintenance | 11828 | 755.6778
2000 | 2024-09-06 | 2025 | 2024 | 2024-09-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Break down | 0.48264 | 0.48264 | 0.55347 | 0 | 1.7 | 1.7 | after grid resume Wtg in error soattend and check related circuit than apply soft rebbot than reset and start WTG. | Close | 0.065385 | O2_12 | 1784.8583 |  | WTG Unscheduled Maintenance | 25198 | 1784.8583
2001 | 2024-09-06 | 2025 | 2024 | 2024-09-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Ladder issue | 0.52431 | 0.52431 | 0.68194 | 0 | 3.7833 | 3.7833 | Wtg manual stop by project team for ladder rectification work. | Close | 0.14551 | O2_12 | 3972.1847 |  | WTG Breakdown Maintenance | 25198 | 3972.1847
2002 | 2024-09-06 | 2025 | 2024 | 2024-09-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Break down | 0.48264 | 0.48264 | 0.51042 | 0 | 0.66667 | 0.66667 | after grid resume Wtg in error soattend and check related circuit than apply soft rebbot than reset and start WTG. | Close | 0.025641 | O2_20 | 701.3611 |  | WTG Unscheduled Maintenance | 25249 | 701.3611
2003 | 2024-09-06 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Road issue | 0 | 0 | 0.25 | 0 | 6 | 6 | wtg in error but turbine road was not approchable so plane to attend in early morning. | Close | 0.23077 | 02_21 | 7461 |  | WTG Unscheduled Maintenance | 29844 | 7461
2004 | 2024-09-06 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.25 | 0.25 | 0.29444 | 0 | 1.0667 | 1.0667 | attend and check related circuit than nothing found abnormal than apply hard rebbot of UPS than reset and start WTG. | Close | 0.041026 | 02_21 | 1326.4 |  | WTG Unscheduled Maintenance | 29844 | 1326.4
2005 | 2024-09-06 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Major BD | 0.35139 | 0.35139 | 0.99999 | 0 | 15.5664 | 15.5664 | attend and check related circuit pitch motor and encode b connection and also cable routing than further troublshooting WIP. | Open | 0.59871 | 02_21 | 19356.8046 |  | WTG Unscheduled Maintenance | 29844 | 19356.8046
2006 | 2024-09-06 | 2025 | 2024 | 2024-09-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.48264 | 0.48264 | 0.51181 | 0 | 0.7 | 0.7 | after grid resume Wtg in error soattend and check related circuit than apply soft rebbot than reset and start WTG. | Close | 0.026923 | O2_16 | 751.975 |  | WTG Unscheduled Maintenance | 25782 | 751.975
2007 | 2024-09-06 | 2025 | 2024 | 2024-09-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD | 0.48264 | 0.48264 | 0.75 | 0 | 6.4167 | 6.4167 | after grid resumeVcb was tripp and check by BOP team than replace triping coil than start WTG. | Close | 0.24679 | O2_20 | 6750.6007 |  | WTG Breakdown Maintenance | 25249 | 6750.6007
2008 | 2024-09-06 | 2025 | 2024 | 2024-09-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Major BD | 0.75 | 0.75 | 0.99999 | 0 | 5.9997 | 5.9997 | After VCB charge by Bop team than WTG in error so attend and check related circuit than found pitch no 2 flate resister value not ok so replacement WIP | Open | 0.23076 | O2_20 | 6311.9578 |  | WTG Unscheduled Maintenance | 25249 | 6311.9578
2009 | 2024-09-06 | 2025 | 2024 | 2024-09-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.34583 | 0.34583 | 0.35 | 0 | 0.1 | 0.1 | Check error data than reset and start Wtg. | Close | 0.0038462 | O2_05 | 109.1042 |  | WTG Unscheduled Maintenance | 26185 | 109.1042
2010 | 2024-09-06 | 2025 | 2024 | 2024-09-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.48264 | 0.48264 | 0.65903 | 0 | 4.2333 | 4.2333 | Wtg stop for 1st month mentenence of Day 1 | Close | 0.16282 | O2_05 | 4618.7431 |  | WTG Scheduled Maintenance | 26185 | 4618.7431
2011 | 2024-09-06 | 2025 | 2024 | 2024-09-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.58958 | 0.58958 | 0.61597 | 0 | 0.63333 | 0.63333 | Check error data than reset and start Wtg. | Close | 0.024359 | O2_05 | 671.8083 |  | WTG Unscheduled Maintenance | 25458 | 671.8083
2012 | 2024-09-06 | 2025 | 2024 | 2024-09-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3060 | Conv. emerg.off type A | Break down | 0.73889 | 0.73889 | 0.75694 | 0 | 0.43333 | 0.43333 | after grid resume wtg in error so check data than apply soft rebbot than reset and start WTG. | Close | 0.016667 | O2_05 | 459.6583 |  | WTG Unscheduled Maintenance | 25458 | 459.6583
2013 | 2024-09-07 | 2025 | 2024 | 2024-09-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.55486 | 0.55486 | 0.55694 | 0 | 0.05 | 0.05 | Check error data than reset and start Wtg. | Close | 0.0019231 | O2_05 | 35.5542 |  | WTG Unscheduled Maintenance | 17066 | 35.5542
2014 | 2024-09-07 | 2025 | 2024 | 2024-09-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.6625 | 0.6625 | 0.66319 | 0 | 0.016667 | 0.016667 | Check error data than reset and start Wtg. | Close | 0.00064103 | O2_05 | 11.8514 |  | WTG Unscheduled Maintenance | 17066 | 11.8514
2015 | 2024-09-07 | 2025 | 2024 | 2024-09-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.96806 | 0.96806 | 0.97153 | 0 | 0.083333 | 0.083333 | Check error data than reset and start Wtg. | Close | 0.0032051 | O2_05 | 59.2569 |  | WTG Unscheduled Maintenance | 17066 | 59.2569
2016 | 2024-09-07 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.15764 | 0.15764 | 0.15903 | 0 | 0.033333 | 0.033333 | Check error data than reset and start Wtg. | Close | 0.0012821 | O2_07 | 16.1111 |  | WTG Unscheduled Maintenance | 11600 | 16.1111
2017 | 2024-09-07 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.32431 | 0.32431 | 0.34792 | 0 | 0.56667 | 0.56667 | Check error data than reset and start Wtg. | Close | 0.021795 | O2_07 | 273.8889 |  | WTG Unscheduled Maintenance | 11600 | 273.8889
2018 | 2024-09-07 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.75 | 0.75 | 0.75208 | 0 | 0.05 | 0.05 | Check error data than reset and start Wtg. | Close | 0.0019231 | O2_18 | 27.6771 |  | WTG Unscheduled Maintenance | 13285 | 27.6771
2019 | 2024-09-07 | 2025 | 2024 | 2024-09-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.49792 | 0.49792 | 0.49931 | 0 | 0.033333 | 0.033333 | Check error data than reset and start Wtg. | Close | 0.0012821 | O2_12 | 23.9208 |  | WTG Unscheduled Maintenance | 17223 | 23.9208
2020 | 2024-09-07 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0 | 0 | 0.11181 | 0 | 2.6833 | 2.6833 | attend and check related circuit pitch motor and encoder b blade connection and also check than found Angel encoder cable fauly so replace it than reset and start WTG. | Close | 0.10321 | O2_12 | 1925.6271 |  | WTG Unscheduled Maintenance | 17223 | 1925.6271
2021 | 2024-09-07 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 4093 | Rel. air hum. tower base inside too high (in operation) | Break down | 0.27778 | 0.27778 | 0.28472 | 0 | 0.16667 | 0.16667 | Check error data than reset and start Wtg. | Close | 0.0064103 | O2_02 | 120.9722 |  | WTG Unscheduled Maintenance | 17420 | 120.9722
2022 | 2024-09-07 | 2025 | 2024 | 2024-09-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Break down | 0 | 0 | 0.034028 | 0 | 0.81667 | 0.81667 | After VCB charge by Bop team than WTG in error so attend and check related circuit than found pitch no 2 flate resister value not ok so replacement with new one than start WTG. | Close | 0.03141 | O2_18 | 364.7097 |  | WTG Unscheduled Maintenance | 10718 | 364.7097
2023 | 2024-09-07 | 2025 | 2024 | 2024-09-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.045139 | 0.045139 | 0.047222 | 0 | 0.05 | 0.05 | Check error data than reset and start Wtg. | Close | 0.0019231 | O2_14 | 32.8812 |  | WTG Unscheduled Maintenance | 15783 | 32.8812
2024 | 2024-09-07 | 2025 | 2024 | 2024-09-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.051389 | 0.051389 | 0.053472 | 0 | 0.05 | 0.05 | Check error data than reset and start Wtg. | Close | 0.0019231 | O2_14 | 32.8812 |  | WTG Unscheduled Maintenance | 15783 | 32.8812
2025 | 2024-09-07 | 2025 | 2024 | 2024-09-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.059722 | 0.059722 | 0.11181 | 0 | 1.25 | 1.25 | Attend and check error related ckt than retight all connection and start WTG. | Close | 0.048077 | O2_14 | 822.0312 |  | WTG Unscheduled Maintenance | 15783 | 822.0312
2026 | 2024-09-07 | 2025 | 2024 | 2024-09-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.42292 | 0.42292 | 0.6125 | 0 | 4.55 | 4.55 | Wtg stop for 1st month mentenence of Day 2 | Close | 0.175 | O2_02 | 3302.5417 |  | WTG Scheduled Maintenance | 17420 | 3302.5417
2027 | 2024-09-07 | 2025 | 2024 | 2024-09-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.11181 | 0.11181 | 0.11319 | 0 | 0.033333 | 0.033333 | Check error data than reset and start Wtg. | Close | 0.0012821 | O2_01 | 20.4181 |  | WTG Unscheduled Maintenance | 14701 | 20.4181
2028 | 2024-09-07 | 2025 | 2024 | 2024-09-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.61736 | 0.61736 | 0.61875 | 0 | 0.033333 | 0.033333 | Check error data than reset and start Wtg. | Close | 0.0012821 | O2_01 | 20.4181 |  | WTG Unscheduled Maintenance | 14701 | 20.4181
2029 | 2024-09-07 | 2025 | 2024 | 2024-09-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.90625 | 0.90625 | 0.90764 | 0 | 0.033333 | 0.033333 | Check error data than reset and start Wtg. | Close | 0.0012821 | O2_01 | 20.4181 |  | WTG Unscheduled Maintenance | 14701 | 20.4181
2030 | 2024-09-08 | 2025 | 2024 | 2024-09-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.45417 | 0.45417 | 0.45903 | 0 | 0.11667 | 0.11667 | Check error data than reset and start Wtg. | Close | 0.0044872 | O2_05 | 45.5486 |  | WTG Unscheduled Maintenance | 9370 | 45.5486
2031 | 2024-09-08 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.69097 | 0.69097 | 0.73056 | 0 | 0.95 | 0.95 | after grid resume wtg in error(preheating) so check data log than reset and start WTG. | Close | 0.036538 | O2_21 | 247.1583 |  | WTG Unscheduled Maintenance | 6244 | 247.1583
2032 | 2024-09-08 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.41458 | 0.41458 | 0.66181 | 0 | 5.9333 | 5.9333 | Project Pending work O2-18,O2-06,o2-21 33kv line Jumper opening | Close | 0.22821 | O2_21 | 1543.6556 |  | WTG Breakdown Maintenance | 6244 | 1543.6556
2033 | 2024-09-08 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.69097 | 0.69097 | 0.72986 | 0 | 0.93333 | 0.93333 | after grid resume wtg in error(preheating) so check data log than reset and start WTG. | Close | 0.035897 | O2_21 | 242.8222 |  | WTG Unscheduled Maintenance | 6244 | 242.8222
2034 | 2024-09-08 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.41458 | 0.41458 | 0.66181 | 0 | 5.9333 | 5.9333 | Project Pending work O2-18,O2-06,o2-21 33kv line Jumper opening | Close | 0.22821 | O2_21 | 1543.6556 |  | WTG Breakdown Maintenance | 6244 | 1543.6556
2035 | 2024-09-08 | 2025 | 2024 | 2024-09-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.69097 | 0.69097 | 0.72917 | 0 | 0.91667 | 0.91667 | after grid resume wtg in error(preheating) so check data log than reset and start WTG. | Close | 0.035256 | O2_06 | 269.2326 |  | WTG Unscheduled Maintenance | 7049 | 269.2326
2036 | 2024-09-08 | 2025 | 2024 | 2024-09-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.41458 | 0.41458 | 0.66181 | 0 | 5.9333 | 5.9333 | Project Pending work O2-18,O2-06,o2-21 33kv line Jumper opening | Close | 0.22821 | O2_06 | 1742.6694 |  | WTG Breakdown Maintenance | 7049 | 1742.6694
2037 | 2024-09-08 | 2025 | 2024 | 2024-09-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.13889 | 0.13889 | 0.18056 | 0 | 1 | 1 | Checked related error data log check data than apply soft rebbot than reset and start WTG. | Close | 0.038462 | O2_01 | 359.375 |  | WTG Unscheduled Maintenance | 8625 | 359.375
2038 | 2024-09-08 | 2025 | 2024 | 2024-09-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.20556 | 0.20556 | 0.22917 | 0 | 0.56667 | 0.56667 | Checked related error data log check data than apply soft rebbot than reset and start WTG. | Close | 0.021795 | O2_01 | 203.6458 |  | WTG Unscheduled Maintenance | 8625 | 203.6458
2039 | 2024-09-09 | 2025 | 2024 | 2024-09-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.40625 | 0.40625 | 0.42361 | 0 | 0.41667 | 0.41667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.016026 | O2_26 | 216.441 |  | WTG Unscheduled Maintenance | 12467 | 216.441
2040 | 2024-09-09 | 2025 | 2024 | 2024-09-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.40625 | 0.40625 | 0.60417 | 0 | 4.75 | 4.75 | Project Pending work O2-25,O2-02,o2-05 33kv line Jumper opening | Close | 0.18269 | O2_05 | 2406.2708 |  | WTG Breakdown Maintenance | 12158 | 2406.2708
2041 | 2024-09-09 | 2025 | 2024 | 2024-09-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.63194 | 0.63194 | 0.67847 | 0 | 1.1167 | 1.1167 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.042949 | O2_05 | 565.6847 |  | WTG Unscheduled Maintenance | 12158 | 565.6847
2042 | 2024-09-09 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.38125 | 0.38125 | 0.43125 | 0 | 1.2 | 1.2 | Checked related error data log apply soft reboot reset & start the WTG. | Close | 0.046154 | O2_24 | 828 |  | WTG Unscheduled Maintenance | 16560 | 828
2043 | 2024-09-09 | 2025 | 2024 | 2024-09-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.40625 | 0.40625 | 0.60417 | 0 | 4.75 | 4.75 | Project Pending work O2-25,O2-02,o2-05 33kv line Jumper opening | Close | 0.18269 | O2_02 | 2438.9271 |  | WTG Breakdown Maintenance | 12323 | 2438.9271
2044 | 2024-09-09 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 650 | Pitch controller communication error | Break down | 0.37847 | 0.37847 | 0.54167 | 0 | 3.9167 | 3.9167 | Checked related error data log apply Hard reboot reset & start the WTG. | Close | 0.15064 | O2_21 | 1735.8993 |  | WTG Unscheduled Maintenance | 10637 | 1735.8993
2045 | 2024-09-09 | 2025 | 2024 | 2024-09-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.38194 | 0.38194 | 0.425 | 0 | 1.0333 | 1.0333 | Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.039744 | O2_04 | 713 |  | WTG Unscheduled Maintenance | 16560 | 713
2046 | 2024-09-09 | 2025 | 2024 | 2024-09-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0.88611 | 0.88611 | 0.95556 | 0 | 1.6667 | 1.6667 | attend and found VCB tripped by Unknown person so check all releted circuit found no any abnormality so cherge VCB then start WTG. | Close | 0.064103 | O2_04 | 1150 |  | WTG Unscheduled Maintenance | 16560 | 1150
2047 | 2024-09-09 | 2025 | 2024 | 2024-09-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 155 | Incorrect Error Code | Break down | 0.40625 | 0.40625 | 0.41528 | 0 | 0.21667 | 0.21667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.0083333 | O2_03 | 107.2229 |  | WTG Unscheduled Maintenance | 11877 | 107.2229
2048 | 2024-09-09 | 2025 | 2024 | 2024-09-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.40625 | 0.40625 | 0.41667 | 0 | 0.25 | 0.25 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.0096154 | O2_11 | 111.7083 |  | WTG Unscheduled Maintenance | 10724 | 111.7083
2049 | 2024-09-09 | 2025 | 2024 | 2024-09-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 155 | Incorrect Error Code | Break down | 0.40625 | 0.40625 | 0.41667 | 0 | 0.25 | 0.25 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.0096154 | O2_12 | 97.6875 |  | WTG Unscheduled Maintenance | 9378 | 97.6875
2050 | 2024-09-09 | 2025 | 2024 | 2024-09-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.40625 | 0.40625 | 0.48472 | 0 | 1.8833 | 1.8833 | Checked related error data log apply Hard reboot then reset & start the WTG. | Close | 0.072436 | O2_11 | 841.5361 |  | WTG Unscheduled Maintenance | 10724 | 841.5361
2051 | 2024-09-09 | 2025 | 2024 | 2024-09-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 155 | Incorrect Error Code | Break down | 0.63194 | 0.63194 | 0.64583 | 0 | 0.33333 | 0.33333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.012821 | O2_11 | 148.9444 |  | WTG Unscheduled Maintenance | 10724 | 148.9444
2052 | 2024-09-09 | 2025 | 2024 | 2024-09-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.40625 | 0.40625 | 0.41806 | 0 | 0.28333 | 0.28333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.010897 | O2_11 | 126.6028 |  | WTG Unscheduled Maintenance | 10724 | 126.6028
2053 | 2024-09-09 | 2025 | 2024 | 2024-09-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.40625 | 0.40625 | 0.41806 | 0 | 0.28333 | 0.28333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.010897 | O2_11 | 126.6028 |  | WTG Unscheduled Maintenance | 10724 | 126.6028
2054 | 2024-09-09 | 2025 | 2024 | 2024-09-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.40625 | 0.40625 | 0.41806 | 0 | 0.28333 | 0.28333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.010897 | O2_11 | 126.6028 |  | WTG Unscheduled Maintenance | 10724 | 126.6028
2055 | 2024-09-09 | 2025 | 2024 | 2024-09-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.37847 | 0.37847 | 0.42083 | 0 | 1.0167 | 1.0167 | Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.039103 | O2_20 | 483.0014 |  | WTG Unscheduled Maintenance | 11402 | 483.0014
2056 | 2024-09-09 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.37847 | 0.37847 | 0.43194 | 0 | 1.2833 | 1.2833 | Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.049359 | O2_06 | 685.1931 |  | WTG Unscheduled Maintenance | 12814 | 685.1931
2057 | 2024-09-09 | 2025 | 2024 | 2024-09-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.37847 | 0.37847 | 0.47917 | 0 | 2.4167 | 2.4167 | Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.092949 | O2_16 | 1327.0521 |  | WTG Unscheduled Maintenance | 13179 | 1327.0521
2058 | 2024-09-09 | 2025 | 2024 | 2024-09-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.37847 | 0.37847 | 0.44861 | 0 | 1.6833 | 1.6833 | Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.064744 | O2_06 | 898.7597 |  | WTG Unscheduled Maintenance | 12814 | 898.7597
2059 | 2024-09-09 | 2025 | 2024 | 2024-09-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.37847 | 0.37847 | 0.69097 | 0 | 7.5 | 7.5 | Wtg stop for 1st month mentenence of Day 1 | Close | 0.28846 | O2_20 | 3563.125 |  | WTG Scheduled Maintenance | 11402 | 3563.125
2060 | 2024-09-09 | 2025 | 2024 | 2024-09-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.40625 | 0.40625 | 0.60417 | 0 | 4.75 | 4.75 | Project Pending work O2-25,O2-02,o2-05 33kv line Jumper opening | Close | 0.18269 | O2_05 | 2406.2708 |  | WTG Breakdown Maintenance | 12158 | 2406.2708
2061 | 2024-09-09 | 2025 | 2024 | 2024-09-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.40625 | 0.40625 | 0.425 | 0 | 0.45 | 0.45 | after grid resume Wtg in error so Checked related error data log then apply soft reboot reset & start the WTG. | Close | 0.017308 | O2_01 | 246.0187 |  | WTG Unscheduled Maintenance | 13121 | 246.0187
2062 | 2024-09-09 | 2025 | 2024 | 2024-09-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 650 | Pitch controller communication error | Break down | 0.67569 | 0.67569 | 0.67986 | 0 | 0.1 | 0.1 | Check error data than reset and start Wtg. | Close | 0.0038462 | O2_01 | 54.6708 |  | WTG Unscheduled Maintenance | 13121 | 54.6708
2063 | 2024-09-10 | 2025 | 2024 | 2024-09-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.65625 | 0.65625 | 0.67708 | 0 | 0.5 | 0.5 | wtg manul stop for project pending point closer work. | Close | 0.019231 | O2_09 | 339.8333 |  | WTG Breakdown Maintenance | 16312 | 339.8333
2064 | 2024-09-10 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.10903 | 0.10903 | 0.12778 | 0 | 0.45 | 0.45 | Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.017308 | O2_21 | 224.2875 |  | WTG Unscheduled Maintenance | 11962 | 224.2875
2065 | 2024-09-10 | 2025 | 2024 | 2024-09-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0.90139 | 0.90139 | 0.98056 | 0 | 1.9 | 1.9 | attend and found VCB tripped by Unknown person so check all releted circuit found no any abnormality so cherge VCB then start WTG. | Close | 0.073077 | O2_04 | 1593.2292 |  | WTG Unscheduled Maintenance | 20125 | 1593.2292
2066 | 2024-09-10 | 2025 | 2024 | 2024-09-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0.99375 | 0.99375 | 1899-12-31 | 0 | 0.15 | 0.15 | attend and found VCB tripped by Unknown person so check all releted circuit found no any abnormality so cherge VCB then start WTG. | Close | 0.0057692 | O2_04 | 125.7812 |  | WTG Unscheduled Maintenance | 20125 | 125.7812
2067 | 2024-09-10 | 2025 | 2024 | 2024-09-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Ladder issue | 0.46667 | 0.46667 | 0.79236 | 0 | 7.8167 | 7.8167 | WTG manual stop for ladder replacement work. | Close | 0.30064 | O2_12 | 5031.0021 |  | WTG Breakdown Maintenance | 15447 | 5031.0021
2068 | 2024-09-10 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.39514 | 0.39514 | 0.40903 | 0 | 0.33333 | 0.33333 | Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.012821 | O2_06 | 219.8889 |  | WTG Unscheduled Maintenance | 15832 | 219.8889
2069 | 2024-09-10 | 2025 | 2024 | 2024-09-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.41667 | 0.41667 | 0.64028 | 0 | 5.3667 | 5.3667 | Wtg stop for 1st month mentenence of Day 2 | Close | 0.20641 | O2_20 | 3757.1139 |  | WTG Scheduled Maintenance | 16802 | 3757.1139
2070 | 2024-09-11 | 2025 | 2024 | 2024-09-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.53611 | 0.53611 | 0.57639 | 0 | 0.96667 | 0.96667 | wtg stop for project pending work. | Close | 0.037179 | O2-09 | 772.8097 |  | WTG Breakdown Maintenance | 19187 | 772.8097
2071 | 2024-09-11 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.10139 | 0.10139 | 0.10347 | 0 | 0.05 | 0.05 | check data and reset and start WTG. | Close | 0.0019231 | O2-07 | 34 |  | WTG Unscheduled Maintenance | 16320 | 34
2072 | 2024-09-11 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.58681 | 0.58681 | 0.58819 | 0 | 0.033333 | 0.033333 | check data and reset and start WTG. | Close | 0.0012821 | O2-18 | 27.125 |  | WTG Unscheduled Maintenance | 19530 | 27.125
2073 | 2024-09-11 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.90625 | 0.90625 | 0.90764 | 0 | 0.033333 | 0.033333 | check data and reset and start WTG. | Close | 0.0012821 | O2-18 | 27.125 |  | WTG Unscheduled Maintenance | 19530 | 27.125
2074 | 2024-09-11 | 2025 | 2024 | 2024-09-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Project pending work | 0.053472 | 0.053472 | 0.05625 | 0 | 0.066667 | 0.066667 | wtg stop for project pending work. | Close | 0.0025641 | O2_04 | 58.7028 |  | WTG Unscheduled Maintenance | 21133 | 58.7028
2075 | 2024-09-11 | 2025 | 2024 | 2024-09-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0.83542 | 0.83542 | 0.91806 | 0 | 1.9833 | 1.9833 | Check By Bop team and found VCB was trip so charge and after check data than reset and start WTG | Close | 0.076282 | O2_04 | 1746.4076 |  | WTG Unscheduled Maintenance | 21133 | 1746.4076
2076 | 2024-09-11 | 2025 | 2024 | 2024-09-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Ladder issue | 0.49028 | 0.49028 | 0.60625 | 0 | 2.7833 | 2.7833 | WTG manual stop for ladder replacement work. | Close | 0.10705 | O2-15 | 2107.7951 |  | WTG Breakdown Maintenance | 18175 | 2107.7951
2077 | 2024-09-11 | 2025 | 2024 | 2024-09-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.35069 | 0.35069 | 0.35208 | 0 | 0.033333 | 0.033333 | check data and reset and start WTG. | Close | 0.0012821 | O2-11 | 22.7167 |  | WTG Unscheduled Maintenance | 16356 | 22.7167
2078 | 2024-09-11 | 2025 | 2024 | 2024-09-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.56181 | 0.56181 | 0.5875 | 0 | 0.61667 | 0.61667 | wtg stop for O2 project pending work. | Close | 0.023718 | O2-24 | 446.184 |  | WTG Breakdown Maintenance | 17365 | 446.184
2079 | 2024-09-11 | 2025 | 2024 | 2024-09-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0.65764 | 0.65764 | 0.65903 | 0 | 0.033333 | 0.033333 | check data and reset and start WTG. | Close | 0.0012821 | O2-18 | 27.125 |  | WTG Unscheduled Maintenance | 19530 | 27.125
2080 | 2024-09-11 | 2025 | 2024 | 2024-09-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.57083 | 0.57083 | 0.58125 | 0 | 0.25 | 0.25 | check data and reset and start WTG. | Close | 0.0096154 | O2-01 | 188.8958 |  | WTG Unscheduled Maintenance | 18134 | 188.8958
2081 | 2024-09-12 | 2025 | 2024 | 2024-09-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.55972 | 0.55972 | 0.5875 | 0 | 0.66667 | 0.66667 | check data and reset and start WTG. | Close | 0.025641 | O2-25 | 891.9722 |  | WTG Unscheduled Maintenance | 32111 | 891.9722
2082 | 2024-09-12 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.31736 | 0.31736 | 0.325 | 0 | 0.18333 | 0.18333 | check data and reset and start WTG. | Close | 0.0070513 | O2-07 | 206.2194 |  | WTG Unscheduled Maintenance | 26996 | 206.2194
2083 | 2024-09-12 | 2025 | 2024 | 2024-09-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Road issue | 0.73125 | 0.73125 | 0.775 | 0 | 1.05 | 1.05 | Wtg in error but road was not accesable for vehicale so another vehicale arragemnt WIP. | Close | 0.040385 | O2-04 | 1284.2813 |  | WTG Unscheduled Maintenance | 29355 | 1284.2813
2084 | 2024-09-12 | 2025 | 2024 | 2024-09-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Road issue | 0.775 | 0.775 | 0.875 | 0 | 2.4 | 2.4 | Wtg in error but road was not accesable for vehicale so another vehicale arragemnt WIP. | Close | 0.092308 | O2-04 | 2935.5 |  | WTG Unscheduled Maintenance | 29355 | 2935.5
2085 | 2024-09-12 | 2025 | 2024 | 2024-09-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.875 | 0.875 | 0.94583 | 0 | 1.7 | 1.7 | After vehical arrngement done and attend and check related circuit than found Yaw contector FB connection was loose than retight properly than take trial than nothing found abnormal than reset and start WTG. | Close | 0.065385 | O2-04 | 2079.3125 |  | WTG Unscheduled Maintenance | 29355 | 2079.3125
2086 | 2024-09-12 | 2025 | 2024 | 2024-09-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0.91319 | 0.91319 | 0.99999 | 0 | 2.0831 | 2.0831 | attend and found VCB tripped by Unknown person so check all releted circuit found no any abnormality so cherge VCB then start WTG. | Close | 0.080118 | O2-04 | 2547.8373 |  | WTG Unscheduled Maintenance | 29355 | 2547.8373
2087 | 2024-09-12 | 2025 | 2024 | 2024-09-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Ladder issue | 0.49097 | 0.49097 | 0.63056 | 0 | 3.35 | 3.35 | WTG manual stop for ladder replacement work. | Close | 0.12885 | O2-24 | 4236.2146 |  | WTG Breakdown Maintenance | 30349 | 4236.2146
2088 | 2024-09-12 | 2025 | 2024 | 2024-09-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.42986 | 0.42986 | 0.68194 | 0 | 6.05 | 6.05 | Wtg stop for 1st month mentenence of Day 2 | Close | 0.23269 | O2-01 | 5471.2167 |  | WTG Scheduled Maintenance | 21704 | 5471.2167
2089 | 2024-09-12 | 2025 | 2024 | 2024-09-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 551 | Pitch motor current too high | Break down | 0.019444 | 0.019444 | 0.045833 | 0 | 0.63333 | 0.63333 | check data and reset and start WTG. | Close | 0.024359 | O2-01 | 572.7444 |  | WTG Unscheduled Maintenance | 21704 | 572.7444
2090 | 2024-09-13 | 2025 | 2024 | 2024-09-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 1630 | Disc filter adaption implausible | Break down | 0.6375 | 0.6375 | 0.64444 | 0 | 0.16667 | 0.16667 | check data and reset and start WTG. | Close | 0.0064103 | O2-25 | 198.3611 |  | WTG Unscheduled Maintenance | 28564 | 198.3611
2091 | 2024-09-13 | 2025 | 2024 | 2024-09-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.022917 | 0.022917 | 0.024306 | 0 | 0.033333 | 0.033333 | check data and reset and start WTG. | Close | 0.0012821 | O2-05 | 42.0264 |  | WTG Unscheduled Maintenance | 30259 | 42.0264
2092 | 2024-09-13 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.31181 | 0.31181 | 0.32222 | 0 | 0.25 | 0.25 | check data and than nothing found abnpormal than apply soft reboot than reset and start WTG. | Close | 0.0096154 | O2-07 | 228.9583 |  | WTG Unscheduled Maintenance | 21980 | 228.9583
2093 | 2024-09-13 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.35069 | 0.35069 | 0.35208 | 0 | 0.033333 | 0.033333 | check data and reset and start WTG. | Close | 0.0012821 | O2-07 | 30.5278 |  | WTG Unscheduled Maintenance | 21980 | 30.5278
2094 | 2024-09-13 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.93056 | 0.93056 | 0.93264 | 0 | 0.05 | 0.05 | check data and reset and start WTG. | Close | 0.0019231 | O2-07 | 45.7917 |  | WTG Unscheduled Maintenance | 21980 | 45.7917
2095 | 2024-09-13 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Break down | 0.975 | 0.975 | 0.99999 | 0 | 0.59972 | 0.59972 | After grid resume wtg in error so further troublshooting WIP. | Close | 0.023066 | O2-18 | 702.9744 |  | WTG Unscheduled Maintenance | 28132 | 702.9744
2096 | 2024-09-13 | 2025 | 2024 | 2024-09-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0 | 0 | 0.075 | 0 | 1.8 | 1.8 | attend and found VCB tripped by Unknown person so check all releted circuit found no any abnormality so cherge VCB then start WTG. | Close | 0.069231 | O2_04 | 1771.725 |  | WTG Unscheduled Maintenance | 23623 | 1771.725
2097 | 2024-09-13 | 2025 | 2024 | 2024-09-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0.92083 | 0.92083 | 0.95347 | 0 | 0.78333 | 0.78333 | attend and found VCB tripped by Unknown person so check all releted circuit found no any abnormality so cherge VCB then start WTG. | Close | 0.030128 | O2_04 | 771.0285 |  | WTG Unscheduled Maintenance | 23623 | 771.0285
2098 | 2024-09-13 | 2025 | 2024 | 2024-09-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0.95347 | 0.95347 | 0.99999 | 0 | 1.1164 | 1.1164 | attend and found VCB tripped by Unknown person so check all releted circuit found no any abnormality so cherge VCB then start WTG. | Close | 0.042938 | O2_04 | 1098.8523 |  | WTG Unscheduled Maintenance | 23623 | 1098.8523
2099 | 2024-09-13 | 2025 | 2024 | 2024-09-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.71319 | 0.71319 | 0.71736 | 0 | 0.1 | 0.1 | check data and reset and start WTG. | Close | 0.0038462 | O2-15 | 104.4708 |  | WTG Unscheduled Maintenance | 25073 | 104.4708
2100 | 2024-09-13 | 2025 | 2024 | 2024-09-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.45347 | 0.45347 | 0.45694 | 0 | 0.083333 | 0.083333 | check data and reset and start WTG. | Close | 0.0032051 | O2-11 | 96.7083 |  | WTG Unscheduled Maintenance | 27852 | 96.7083
2101 | 2024-09-13 | 2025 | 2024 | 2024-09-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Ladder issue | 0.49236 | 0.49236 | 0.625 | 0 | 3.1833 | 3.1833 | Wtg stop by project team for ladder replacement work | Close | 0.12244 | O2-11 | 3694.2583 |  | WTG Breakdown Maintenance | 27852 | 3694.2583
2102 | 2024-09-13 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.11736 | 0.11736 | 0.11875 | 0 | 0.033333 | 0.033333 | check data and reset and start WTG. | Close | 0.0012821 | O2-06 | 38.1764 |  | WTG Unscheduled Maintenance | 27487 | 38.1764
2103 | 2024-09-13 | 2025 | 2024 | 2024-09-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.18611 | 0.18611 | 0.1875 | 0 | 0.033333 | 0.033333 | check data and reset and start WTG. | Close | 0.0012821 | O2-01 | 37.5167 |  | WTG Unscheduled Maintenance | 27012 | 37.5167
2104 | 2024-09-13 | 2025 | 2024 | 2024-09-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.29653 | 0.29653 | 0.34028 | 0 | 1.05 | 1.05 | check data and reset and start WTG. | Close | 0.040385 | O2-01 | 1181.775 |  | WTG Unscheduled Maintenance | 27012 | 1181.775
2105 | 2024-09-13 | 2025 | 2024 | 2024-09-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.41667 | 0.41667 | 0.60764 | 0 | 4.5833 | 4.5833 | Wtg manual stop for 1st month maintenance activity work Day 2. and also rep error troublshooting work done. | Close | 0.17628 | O2-01 | 5158.5417 |  | WTG Scheduled Maintenance | 27012 | 5158.5417
2105 | 2024-09-13 | 2025 | 2024 | 2024-09-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.73056 | 0.73056 | 0.73472 | 0 | 0.1 | 0.1 | check data and reset and start WTG. | Close | 0.0038462 | O2-01 | 112.55 |  | WTG Unscheduled Maintenance | 27012 | 112.55
2106 | 2024-09-13 | 2025 | 2024 | 2024-09-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Major BD | 0.44097 | 0.44097 | 0.99999 | 0 | 13.4164 | 13.4164 | Attend and check related circuit check hydrulic pressure and its 9.1 & 9.7 valve than clean and flushing than take trial but error not solve so further troublesooting WIP. | Open | 0.51601 | O2-20 | 13882.0494 |  | WTG Unscheduled Maintenance | 24833 | 13882.0494
2107 | 2024-09-13 | 2025 | 2024 | 2024-09-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 550 | Pitch current asymmetry | Break down | 0.78125 | 0.78125 | 0.78264 | 0 | 0.033333 | 0.033333 | check data and reset and start WTG. | Close | 0.0012821 | O2-01 | 37.5167 |  | WTG Unscheduled Maintenance | 27012 | 37.5167 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
2108 | 2024-09-14 | 2025 | 2024 | 2024-09-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Ladder issue | 0.48056 | 0.48056 | 0.70833 | 0 | 5.4667 | 5.4667 | Wtg stop by project team for ladder replacement work | Close | 0.21026 | O2-20 | 5032.0667 |  | WTG Breakdown Maintenance | 22092 | 5032.0667
2109 | 2024-09-14 | 2025 | 2024 | 2024-09-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.60486 | 0.60486 | 0.66458 | 0 | 1.4333 | 1.4333 | check data and reset and start WTG. | Close | 0.055128 | O2-26 | 1330.2528 |  | WTG Unscheduled Maintenance | 22274 | 1330.2528
2110 | 2024-09-14 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.16667 | 0.16667 | 0.17292 | 0 | 0.15 | 0.15 | check data and reset and start WTG. | Close | 0.0057692 | O2-07 | 90.0125 |  | WTG Unscheduled Maintenance | 14402 | 90.0125
2111 | 2024-09-14 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.080556 | 0.080556 | 0.086111 | 0 | 0.13333 | 0.13333 | check data and reset and start WTG. | Close | 0.0051282 | O2-18 | 142.1444 |  | WTG Unscheduled Maintenance | 25586 | 142.1444
2112 | 2024-09-14 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.17847 | 0.17847 | 0.17986 | 0 | 0.033333 | 0.033333 | check data and reset and start WTG. | Close | 0.0012821 | O2-18 | 35.5361 |  | WTG Unscheduled Maintenance | 25586 | 35.5361
2113 | 2024-09-14 | 2025 | 2024 | 2024-09-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0.011806 | 0.011806 | 0.019444 | 0 | 0.18333 | 0.18333 | attend and found VCB tripped by Unknown person so check all releted circuit found no any abnormality so cherge VCB then start WTG. | Close | 0.0070513 | O2-04 | 149.4701 |  | WTG Unscheduled Maintenance | 19567 | 149.4701
2114 | 2024-09-14 | 2025 | 2024 | 2024-09-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0.83681 | 0.83681 | 0.91389 | 0 | 1.85 | 1.85 | attend and found VCB tripped by Unknown person so check all releted circuit found no any abnormality so cherge VCB then start WTG. | Close | 0.071154 | O2-04 | 1508.2896 |  | WTG Unscheduled Maintenance | 19567 | 1508.2896
2115 | 2024-09-14 | 2025 | 2024 | 2024-09-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0.97778 | 0.97778 | 0.99097 | 0 | 0.31667 | 0.31667 | attend and found VCB tripped by Unknown person so check all releted circuit found no any abnormality so cherge VCB then start WTG. | Close | 0.012179 | O2-04 | 258.1757 |  | WTG Unscheduled Maintenance | 19567 | 258.1757
2116 | 2024-09-14 | 2025 | 2024 | 2024-09-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.0083333 | 0.0083333 | 0.011806 | 0 | 0.083333 | 0.083333 | check data and reset and start WTG. | Close | 0.0032051 | O2-14 | 75.4132 |  | WTG Unscheduled Maintenance | 21719 | 75.4132
2117 | 2024-09-14 | 2025 | 2024 | 2024-09-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 7002 | Task runtime failure 5ms | Break down | 0.27083 | 0.27083 | 0.28194 | 0 | 0.26667 | 0.26667 | check data and reset and start WTG. | Close | 0.010256 | O2-10 | 251.9889 |  | WTG Unscheduled Maintenance | 22679 | 251.9889
2118 | 2024-09-14 | 2025 | 2024 | 2024-09-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.22847 | 0.22847 | 0.23056 | 0 | 0.05 | 0.05 | check data and reset and start WTG. | Close | 0.0019231 | O2-06 | 49.1479 |  | WTG Unscheduled Maintenance | 23591 | 49.1479
2119 | 2024-09-14 | 2025 | 2024 | 2024-09-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3063 | Conv. emerg.off type D | Break down | 0.56597 | 0.56597 | 0.57083 | 0 | 0.11667 | 0.11667 | check data and reset and start WTG. | Close | 0.0044872 | O2-06 | 114.6785 |  | WTG Unscheduled Maintenance | 23591 | 114.6785
2120 | 2024-09-14 | 2025 | 2024 | 2024-09-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down | 0.78056 | 0.78056 | 1899-12-31 | 0 | 5.2667 | 5.2667 | WIP | Close | 0.20256 | O2-14 | 4766.1139 |  | WTG Unscheduled Maintenance | 21719 | 4766.1139
2121 | 2024-09-14 | 2025 | 2024 | 2024-09-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 551 | Pitch motor current too high | Break down | 0.84097 | 0.84097 | 0.89167 | 0 | 1.2167 | 1.2167 | check data and reset and start WTG. | Close | 0.046795 | O2-05 | 1148.7868 |  | WTG Unscheduled Maintenance | 22661 | 1148.7868
2122 | 2024-09-14 | 2025 | 2024 | 2024-09-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.44722 | 0.44722 | 0.47292 | 0 | 0.61667 | 0.61667 | check data and reset and start WTG. | Close | 0.023718 | O2-01 | 488.9396 |  | WTG Unscheduled Maintenance | 19029 | 488.9396
2123 | 2024-09-15 | 2025 | 2024 | 2024-09-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.32083 | 0.32083 | 0.325 | 0 | 0.1 | 0.1 | check data and reset and start WTG. | Close | 0.0038462 | O2-05 | 87.3542 |  | WTG Unscheduled Maintenance | 20965 | 87.3542
2124 | 2024-09-15 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.30139 | 0.30139 | 0.30347 | 0 | 0.05 | 0.05 | check data and reset and start WTG. | Close | 0.0019231 | O2-07 | 30.6437 |  | WTG Unscheduled Maintenance | 14709 | 30.6437
2125 | 2024-09-15 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.13542 | 0.13542 | 0.13889 | 0 | 0.083333 | 0.083333 | check data and reset and start WTG. | Close | 0.0032051 | O2-18 | 79.3438 |  | WTG Unscheduled Maintenance | 22851 | 79.3438
2126 | 2024-09-15 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.37292 | 0.37292 | 0.37431 | 0 | 0.033333 | 0.033333 | check data and reset and start WTG. | Close | 0.0012821 | O2-18 | 31.7375 |  | WTG Unscheduled Maintenance | 22851 | 31.7375
2127 | 2024-09-15 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.41319 | 0.41319 | 0.42917 | 0 | 0.38333 | 0.38333 | check data and reset and start WTG. | Close | 0.014744 | O2-18 | 364.9812 |  | WTG Unscheduled Maintenance | 22851 | 364.9812
2128 | 2024-09-15 | 2025 | 2024 | 2024-09-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0.53264 | 0.53264 | 0.60972 | 0 | 1.85 | 1.85 | attend and check than found than VCB was trip so charge by BOP team than reset and start WTG. | Close | 0.071154 | O2-04 | 1700.3042 |  | WTG Unscheduled Maintenance | 22058 | 1700.3042
2129 | 2024-09-15 | 2025 | 2024 | 2024-09-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0.83056 | 0.83056 | 0.91875 | 0 | 2.1167 | 2.1167 | attend and check than found than VCB was trip so charge by BOP team than reset and start WTG. | Close | 0.08141 | O2-04 | 1945.3931 |  | WTG Unscheduled Maintenance | 22058 | 1945.3931
2130 | 2024-09-15 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.070833 | 0.070833 | 0.084028 | 0 | 0.31667 | 0.31667 | check data and reset and start WTG. | Close | 0.012179 | O2-06 | 303.8549 |  | WTG Unscheduled Maintenance | 23029 | 303.8549
2131 | 2024-09-15 | 2025 | 2024 | 2024-09-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.48125 | 0.48125 | 0.48542 | 0 | 0.1 | 0.1 | check data and reset and start WTG. | Close | 0.0038462 | O2-06 | 95.9542 |  | WTG Unscheduled Maintenance | 23029 | 95.9542
2132 | 2024-09-15 | 2025 | 2024 | 2024-09-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down | 0 | 0 | 0.03125 | 0 | 0.75 | 0.75 | Hydraulic unit in 9.3 , 9.15, 9.1, and A1 A2 VALVE During absorb so reemove its and clean with blowerand after refiling all valve then taken trail but same error, so we set pressure 175 Bar with use of pressure gauge and taken trail but same error occured. we changre hydrolic oil with new one after taken trail and start wtg ( n0w wtg running under observation) | Close | 0.028846 | O2-14 | 571.625 |  | WTG Unscheduled Maintenance | 18292 | 571.625
2133 | 2024-09-15 | 2025 | 2024 | 2024-09-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Major BD | 0.36458 | 0.36458 | 1899-12-31 | 0 | 15.25 | 15.25 | WIP | Open | 0.58654 | O2-14 | 11623.0417 |  | WTG Unscheduled Maintenance | 18292 | 11623.0417
2134 | 2024-09-15 | 2025 | 2024 | 2024-09-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.56736 | 0.56736 | 0.57014 | 0 | 0.066667 | 0.066667 | check data and reset and start WTG. | Close | 0.0025641 | O2-01 | 50.7417 |  | WTG Unscheduled Maintenance | 18267 | 50.7417
2135 | 2024-09-16 | 2025 | 2024 | 2024-09-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 21 | Manual stop - remote | Break down | 0.64583 | 0.64583 | 0.64931 | 0 | 0.083333 | 0.083333 | EPC Software updated work | Close | 0.0032051 | O2_26 | 57.8333 |  | WTG Breakdown Maintenance | 16656 | 57.8333
2136 | 2024-09-16 | 2025 | 2024 | 2024-09-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.088889 | 0.088889 | 0.095139 | 0 | 0.15 | 0.15 | check data and reset and start WTG. | Close | 0.0057692 | O2_05 | 117.6687 |  | WTG Unscheduled Maintenance | 18827 | 117.6687
2137 | 2024-09-16 | 2025 | 2024 | 2024-09-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 21 | Manual stop - remote | Break down | 0.65347 | 0.65347 | 0.66111 | 0 | 0.18333 | 0.18333 | EPC Software updated work | Close | 0.0070513 | O2_05 | 143.8174 |  | WTG Breakdown Maintenance | 18827 | 143.8174
2138 | 2024-09-16 | 2025 | 2024 | 2024-09-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Road issue | 0.84167 | 0.84167 | 1899-12-31 | 0 | 3.8 | 3.8 | Road approach issue | Close | 0.14615 | O2_05 | 2980.9417 |  | WTG Unscheduled Maintenance | 18827 | 2980.9417
2139 | 2024-09-16 | 2025 | 2024 | 2024-09-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 21 | Manual stop - remote | Break down | 0.6625 | 0.6625 | 0.66806 | 0 | 0.13333 | 0.13333 | EPC Software updated work | Close | 0.0051282 | O2_09 | 96.4833 |  | WTG Breakdown Maintenance | 17367 | 96.4833
2140 | 2024-09-16 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.015278 | 0.015278 | 0.016667 | 0 | 0.033333 | 0.033333 | check data and reset and start WTG. | Close | 0.0012821 | O2_07 | 18.7556 |  | WTG Unscheduled Maintenance | 13504 | 18.7556
2141 | 2024-09-16 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.65347 | 0.65347 | 0.65556 | 0 | 0.05 | 0.05 | check data and reset and start WTG. | Close | 0.0019231 | O2_07 | 28.1333 |  | WTG Unscheduled Maintenance | 13504 | 28.1333
2142 | 2024-09-16 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.67639 | 0.67639 | 0.67778 | 0 | 0.033333 | 0.033333 | check data and reset and start WTG. | Close | 0.0012821 | O2_07 | 18.7556 |  | WTG Unscheduled Maintenance | 13504 | 18.7556
2143 | 2024-09-16 | 2025 | 2024 | 2024-09-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 21 | Manual stop - remote | Break down | 0.66944 | 0.66944 | 0.67569 | 0 | 0.15 | 0.15 | EPC Software updated work | Close | 0.0057692 | O2_02 | 106.7188 |  | WTG Breakdown Maintenance | 17075 | 106.7188
2144 | 2024-09-16 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.20903 | 0.20903 | 0.21111 | 0 | 0.05 | 0.05 | check data and reset and start WTG. | Close | 0.0019231 | O2_21 | 31.1167 |  | WTG Unscheduled Maintenance | 14936 | 31.1167
2145 | 2024-09-16 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.48056 | 0.48056 | 0.48403 | 0 | 0.083333 | 0.083333 | check data and reset and start WTG. | Close | 0.0032051 | O2_21 | 51.8611 |  | WTG Unscheduled Maintenance | 14936 | 51.8611
2146 | 2024-09-16 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 21 | Manual stop - remote | Break down | 0.68056 | 0.68056 | 0.68611 | 0 | 0.13333 | 0.13333 | EPC Software updated work | Close | 0.0051282 | O2_21 | 82.9778 |  | WTG Breakdown Maintenance | 14936 | 82.9778
2147 | 2024-09-16 | 2025 | 2024 | 2024-09-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 21 | Manual stop - remote | Break down | 0.068056 | 0.068056 | 0.073611 | 0 | 0.13333 | 0.13333 | EPC Software updated work | Close | 0.0051282 | O2_04 | 121.1167 |  | WTG Breakdown Maintenance | 21801 | 121.1167
2148 | 2024-09-16 | 2025 | 2024 | 2024-09-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0.45694 | 0.45694 | 0.54514 | 0 | 2.1167 | 2.1167 | attend and check than found than VCB was trip so charge by BOP team than reset and start WTG. | Close | 0.08141 | O2_04 | 1922.7271 |  | WTG Unscheduled Maintenance | 21801 | 1922.7271
2149 | 2024-09-16 | 2025 | 2024 | 2024-09-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0.84236 | 0.84236 | 0.94306 | 0 | 2.4167 | 2.4167 | attend and check than found than VCB was trip so charge by BOP team than reset and start WTG. | Close | 0.092949 | O2_04 | 2195.2396 |  | WTG Unscheduled Maintenance | 21801 | 2195.2396
2150 | 2024-09-16 | 2025 | 2024 | 2024-09-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 21 | Manual stop - remote | Break down | 0.68819 | 0.68819 | 0.69236 | 0 | 0.1 | 0.1 | EPC Software updated work | Close | 0.0038462 | O2_03 | 71.1958 |  | WTG Breakdown Maintenance | 17087 | 71.1958
2151 | 2024-09-16 | 2025 | 2024 | 2024-09-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 21 | Manual stop - remote | Break down | 0.69583 | 0.69583 | 0.7 | 0 | 0.1 | 0.1 | EPC Software updated work | Close | 0.0038462 | O2_15 | 65.1083 |  | WTG Breakdown Maintenance | 15626 | 65.1083
2152 | 2024-09-16 | 2025 | 2024 | 2024-09-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 21 | Manual stop - remote | Break down | 0.69583 | 0.69583 | 0.7 | 0 | 0.1 | 0.1 | EPC Software updated work | Close | 0.0038462 | O2_12 | 65.4625 |  | WTG Breakdown Maintenance | 15711 | 65.4625
2153 | 2024-09-16 | 2025 | 2024 | 2024-09-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.74375 | 0.74375 | 0.89375 | 0 | 3.6 | 3.6 | attend and found 24v FA1 SPD loose connection so tight trhen reset and start WTG. | Close | 0.13846 | O2_12 | 2356.65 |  | WTG Unscheduled Maintenance | 15711 | 2356.65
2154 | 2024-09-16 | 2025 | 2024 | 2024-09-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.27431 | 0.27431 | 0.27569 | 0 | 0.033333 | 0.033333 | check data and reset and start WTG. | Close | 0.0012821 | O2_14 | 23.9681 |  | WTG Unscheduled Maintenance | 17257 | 23.9681
2155 | 2024-09-16 | 2025 | 2024 | 2024-09-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.45208 | 0.45208 | 0.45347 | 0 | 0.033333 | 0.033333 | check data and reset and start WTG. | Close | 0.0012821 | O2_14 | 23.9681 |  | WTG Unscheduled Maintenance | 17257 | 23.9681
2156 | 2024-09-16 | 2025 | 2024 | 2024-09-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 21 | Manual stop - remote | Break down | 0.71806 | 0.71806 | 0.72222 | 0 | 0.1 | 0.1 | EPC Software updated work | Close | 0.0038462 | O2_11 | 71.9042 |  | WTG Breakdown Maintenance | 17257 | 71.9042
2157 | 2024-09-16 | 2025 | 2024 | 2024-09-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 21 | Manual stop - remote | Break down | 0.72222 | 0.72222 | 0.72778 | 0 | 0.13333 | 0.13333 | EPC Software updated work | Close | 0.0051282 | O2_12 | 87.2833 |  | WTG Breakdown Maintenance | 15711 | 87.2833
2158 | 2024-09-16 | 2025 | 2024 | 2024-09-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 21 | Manual stop - remote | Break down | 0.010417 | 0.010417 | 0.043056 | 0 | 0.78333 | 0.78333 | HPU Inspectin work | Close | 0.030128 | O2_10 | 474.4715 |  | WTG Breakdown Maintenance | 14537 | 474.4715
2159 | 2024-09-16 | 2025 | 2024 | 2024-09-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 21 | Manual stop - remote | Break down | 0.73125 | 0.73125 | 0.73611 | 0 | 0.11667 | 0.11667 | EPC Software updated work | Close | 0.0044872 | O2_10 | 70.666 |  | WTG Breakdown Maintenance | 14537 | 70.666
2160 | 2024-09-16 | 2025 | 2024 | 2024-09-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 21 | Manual stop - remote | Break down | 0.73542 | 0.73542 | 0.74306 | 0 | 0.18333 | 0.18333 | EPC Software updated work | Close | 0.0070513 | O2_21 | 114.0944 |  | WTG Breakdown Maintenance | 14936 | 114.0944
2161 | 2024-09-16 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.37431 | 0.37431 | 0.37569 | 0 | 0.033333 | 0.033333 | check data and reset and start WTG. | Close | 0.0012821 | O2_06 | 20.7444 |  | WTG Unscheduled Maintenance | 14936 | 20.7444
2162 | 2024-09-16 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 21 | Manual stop - remote | Break down | 0.74583 | 0.74583 | 0.75 | 0 | 0.1 | 0.1 | EPC Software updated work | Close | 0.0038462 | O2_06 | 62.2333 |  | WTG Breakdown Maintenance | 14936 | 62.2333
2163 | 2024-09-16 | 2025 | 2024 | 2024-09-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 21 | Manual stop - remote | Break down | 0.74583 | 0.74583 | 0.75 | 0 | 0.1 | 0.1 | EPC Software updated work | Close | 0.0038462 | O2_24 | 24.6542 |  | WTG Breakdown Maintenance | 5917 | 24.6542
2164 | 2024-09-16 | 2025 | 2024 | 2024-09-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.59514 | 0.59514 | 0.59722 | 0 | 0.05 | 0.05 | check data and reset and start WTG. | Close | 0.0019231 | O2_06 | 46.1875 |  | WTG Unscheduled Maintenance | 22170 | 46.1875
2165 | 2024-09-16 | 2025 | 2024 | 2024-09-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 21 | Manual stop - remote | Major BD | 0 | 0 | 0.74167 | 0 | 17.8 | 17.8 | 02-24 WTG AFTER REPLACE 9.1 valve manual yawing time check pressure is not down suddenly so then start wg | Close | 0.68462 | O2_20 | 13014.025 |  | WTG Breakdown Maintenance | 17547 | 13014.025
2166 | 2024-09-16 | 2025 | 2024 | 2024-09-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.47778 | 0.47778 | 0.55 | 0 | 1.7333 | 1.7333 | attend for pitch motor over current ) so check all releted circuit found blade 2 rectifire both fuse are faulty so replace it and no any abnormal so reset and start wtg | Close | 0.066667 | O2_25 | 1413.9667 |  | WTG Breakdown Maintenance | 19578 | 1413.9667
2167 | 2024-09-16 | 2025 | 2024 | 2024-09-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 650 | Pitch controller communication error | Break down | 0.78681 | 0.78681 | 0.80694 | 0 | 0.48333 | 0.48333 | check data and reset and start WTG. | Close | 0.01859 | O2_01 | 360.3049 |  | WTG Unscheduled Maintenance | 17891 | 360.3049
2168 | 2024-09-17 | 2025 | 2024 | 2024-09-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.25417 | 0.25417 | 0.25972 | 0 | 0.13333 | 0.13333 | check data and reset and start WTG. | Close | 0.0051282 | O2_26 | 34.9056 |  | WTG Unscheduled Maintenance | 6283 | 34.9056
2169 | 2024-09-17 | 2025 | 2024 | 2024-09-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Road issue | 0.16944 | 0.16944 | 1899-12-31 | 0 | 19.9333 | 19.9333 | Road approach issue | Open | 0.76667 | O2_05 | 6205.0806 |  | WTG Unscheduled Maintenance | 7471 | 6205.0806
2170 | 2024-09-17 | 2025 | 2024 | 2024-09-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.57361 | 0.57361 | 0.59236 | 0 | 0.45 | 0.45 | Project Pending WORK | Close | 0.017308 | O2_09 | 129.8063 |  | WTG Breakdown Maintenance | 6923 | 129.8063
2171 | 2024-09-17 | 2025 | 2024 | 2024-09-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.77639 | 0.77639 | 0.78681 | 0 | 0.25 | 0.25 | check data and reset and start WTG. | Close | 0.0096154 | O2_25 | 72.8021 |  | WTG Unscheduled Maintenance | 6989 | 72.8021
2172 | 2024-09-17 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 7025 | Configuration error | Break down | 0.21875 | 0.21875 | 0.22083 | 0 | 0.05 | 0.05 | Configuration error | Close | 0.0019231 | O2_18 | 20.8187 |  | WTG Unscheduled Maintenance | 9993 | 20.8187
2173 | 2024-09-17 | 2025 | 2024 | 2024-09-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Break down | 0.22708 | 0.22708 | 0.24028 | 0 | 0.31667 | 0.31667 | Apply Hard reebut after then reset and start wtg. | Close | 0.012179 | O2_15 | 96.0028 |  | WTG Unscheduled Maintenance | 7276 | 96.0028
2174 | 2024-09-17 | 2025 | 2024 | 2024-09-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Break down | 0.23333 | 0.23333 | 0.2375 | 0 | 0.1 | 0.1 | Apply Hard reebut after then reset and start wtg. | Close | 0.0038462 | O2_13 | 28.9208 |  | WTG Unscheduled Maintenance | 6941 | 28.9208
2175 | 2024-09-17 | 2025 | 2024 | 2024-09-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 650 | Pitch controller communication error | Break down | 0.24028 | 0.24028 | 0.24583 | 0 | 0.13333 | 0.13333 | Apply Hard reebut after then reset and start wtg. | Close | 0.0051282 | O2_10 | 36.8444 |  | WTG Unscheduled Maintenance | 6632 | 36.8444
2176 | 2024-09-17 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.51944 | 0.51944 | 0.53194 | 0 | 0.3 | 0.3 | check data and reset and start WTG. | Close | 0.011538 | O2_06 | 134.7 |  | WTG Unscheduled Maintenance | 10776 | 134.7
2177 | 2024-09-17 | 2025 | 2024 | 2024-09-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 159 | SLC SF emergency stop | Break down | 0.25208 | 0.25208 | 0.25764 | 0 | 0.13333 | 0.13333 | check data and reset and start WTG. | Close | 0.0051282 | O2_05 | 41.5056 |  | WTG Unscheduled Maintenance | 7471 | 41.5056
2178 | 2024-09-17 | 2025 | 2024 | 2024-09-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3171 | Incorrect Error Code | Break down | 0.27639 | 0.27639 | 0.27778 | 0 | 0.033333 | 0.033333 | check data and reset and start WTG. | Close | 0.0012821 | O2_01 | 9.5347 |  | WTG Unscheduled Maintenance | 6865 | 9.5347
2179 | 2024-09-18 | 2025 | 2024 | 2024-09-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Road issue | 0 | 0 | 1899-12-31 | 0 | 24 | 24 | Road approach issue | Open | 0.92308 | O2-05 | 13595 |  | WTG Unscheduled Maintenance | 13595 | 13595
2180 | 2024-09-18 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.39583 | 0.39583 | 0.39861 | 0 | 0.066667 | 0.066667 | check data and reset and start WTG. | Close | 0.0025641 | O2-07 | 27.3583 |  | WTG Unscheduled Maintenance | 9849 | 27.3583
2181 | 2024-09-18 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.89444 | 0.89444 | 0.89653 | 0 | 0.05 | 0.05 | check data and reset and start WTG. | Close | 0.0019231 | O2-18 | 20.1875 |  | WTG Unscheduled Maintenance | 9690 | 20.1875
2182 | 2024-09-18 | 2025 | 2024 | 2024-09-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.26806 | 0.26806 | 0.27014 | 0 | 0.05 | 0.05 | check data and reset and start WTG. | Close | 0.0019231 | O2-14 | 19.4917 |  | WTG Unscheduled Maintenance | 9356 | 19.4917
2183 | 2024-09-18 | 2025 | 2024 | 2024-09-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.33542 | 0.33542 | 0.37778 | 0 | 1.0167 | 1.0167 | check data and reset and start WTG. | Close | 0.039103 | O2-11 | 363.1618 |  | WTG Unscheduled Maintenance | 8573 | 363.1618
2184 | 2024-09-18 | 2025 | 2024 | 2024-09-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.39236 | 0.39236 | 0.55139 | 0 | 3.8167 | 3.8167 | Attend and check than found coolnet pump MPCB Trip so check related circuit then check motor and take rediator coolnet motor valve then found ok than check cable routing and its found ok TRA XD010 Connection than found losses so retight properly then reset and start wtg. | Close | 0.14679 | O2-11 | 1363.3451 |  | WTG Unscheduled Maintenance | 8573 | 1363.3451
2185 | 2024-09-18 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.084722 | 0.084722 | 0.086806 | 0 | 0.05 | 0.05 | check data and reset and start WTG. | Close | 0.0019231 | O2-06 | 20.7937 |  | WTG Unscheduled Maintenance | 9981 | 20.7937
2186 | 2024-09-18 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.45764 | 0.45764 | 0.47014 | 0 | 0.3 | 0.3 | check data and reset and start WTG. | Close | 0.011538 | O2-06 | 124.7625 |  | WTG Unscheduled Maintenance | 9981 | 124.7625
2187 | 2024-09-18 | 2025 | 2024 | 2024-09-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.475 | 0.475 | 0.74931 | 0 | 6.5833 | 6.5833 | WTG Maintance work 3rd Day and OMS Audit Work | Close | 0.25321 | O2-18 | 2658.0208 |  | WTG Scheduled Maintenance | 9690 | 2658.0208
2188 | 2024-09-18 | 2025 | 2024 | 2024-09-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.42917 | 0.42917 | 0.46875 | 0 | 0.95 | 0.95 | check data and reset and start WTG. | Close | 0.036538 | O2-01 | 377.4667 |  | WTG Unscheduled Maintenance | 9536 | 377.4667
2189 | 2024-09-18 | 2025 | 2024 | 2024-09-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.70833 | 0.70833 | 0.71528 | 0 | 0.16667 | 0.16667 | check data and reset and start WTG. | Close | 0.0064103 | O2-01 | 66.2222 |  | WTG Unscheduled Maintenance | 9536 | 66.2222
2190 | 2024-09-19 | 2025 | 2024 | 2024-09-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Road issue | 0 | 0 | 1899-12-31 | 0 | 24 | 24 | Road approach issue | Open | 0.92308 | O2-05 | 16071 |  | WTG Unscheduled Maintenance | 16071 | 16071
2191 | 2024-09-19 | 2025 | 2024 | 2024-09-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.50903 | 0.50903 | 0.73125 | 0 | 5.3333 | 5.3333 | WTG Maintance work 3rd Day AND WIND DIFF WARNNING CLEAR SO CHECK Both ULTRASONIC RELIAGMENT chck all cable laying found no any abnormall on cable laying found left side ultrasonic minor deviation is normal | Close | 0.20513 | O2-09 | 2379.5556 |  | WTG Scheduled Maintenance | 10708 | 2379.5556
2192 | 2024-09-19 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.17014 | 0.17014 | 0.17153 | 0 | 0.033333 | 0.033333 | check data and reset and start WTG. | Close | 0.0012821 | O2-07 | 18.4986 |  | WTG Unscheduled Maintenance | 13319 | 18.4986
2193 | 2024-09-19 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.83958 | 0.83958 | 0.84097 | 0 | 0.033333 | 0.033333 | check data and reset and start WTG. | Close | 0.0012821 | O2-07 | 18.4986 |  | WTG Unscheduled Maintenance | 13319 | 18.4986
2194 | 2024-09-19 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.61389 | 0.61389 | 0.67639 | 0 | 1.5 | 1.5 | attend for rep frequency control (CAN Load sheding) so check cable and its connector and refix properly from cable tray and apply proper cable shidhing and refix connector then reset and star wtg | Close | 0.057692 | O2-21 | 838.8125 |  | WTG Breakdown Maintenance | 13421 | 838.8125 | [6 empty] | Load shedding
2195 | 2024-09-19 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.81944 | 0.81944 | 0.82083 | 0 | 0.033333 | 0.033333 | check data and reset and start WTG. | Close | 0.0012821 | O2-06 | 16.7194 |  | WTG Unscheduled Maintenance | 12038 | 16.7194
2196 | 2024-09-19 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 4093 | Rel. air hum. tower base inside too high (in operation) | Break down | 0.34931 | 0.34931 | 0.35417 | 0 | 0.11667 | 0.11667 | check data and reset and start WTG. | Close | 0.0044872 | O2-06 | 58.5181 |  | WTG Unscheduled Maintenance | 12038 | 58.5181
2197 | 2024-09-19 | 2025 | 2024 | 2024-09-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.50278 | 0.50278 | 0.51806 | 0 | 0.36667 | 0.36667 | WTG MANUAL STOP FOR MCC Reverification work Project team | Close | 0.014103 | O2-13 | 174.1972 |  | WTG Breakdown Maintenance | 11402 | 174.1972
2198 | 2024-09-19 | 2025 | 2024 | 2024-09-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.015278 | 0.015278 | 0.01875 | 0 | 0.083333 | 0.083333 | check data and reset and start WTG. | Close | 0.0032051 | O2-06 | 41.7986 |  | WTG Unscheduled Maintenance | 12038 | 41.7986
2199 | 2024-09-20 | 2025 | 2024 | 2024-09-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Break down | 0.85556 | 0.85556 | 0.86042 | 0 | 0.11667 | 0.11667 | check data and reset and start WTG. | Close | 0.0044872 | O2-26 | 71.2931 |  | WTG Unscheduled Maintenance | 14666 | 71.2931
2200 | 2024-09-20 | 2025 | 2024 | 2024-09-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Road issue | 0 | 0 | 0.60417 | 0 | 14.5 | 14.5 | Road approach issue | Open | 0.55769 | O2-05 | 11545.0208 |  | WTG Unscheduled Maintenance | 19109 | 11545.0208
2201 | 2024-09-20 | 2025 | 2024 | 2024-09-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Break down | 0.60417 | 0.60417 | 0.70833 | 0 | 2.5 | 2.5 | Attend and wtg trouble shuting work | Close | 0.096154 | O2-05 | 1990.5208 |  | WTG Unscheduled Maintenance | 19109 | 1990.5208
2202 | 2024-09-20 | 2025 | 2024 | 2024-09-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Road issue | 0.81944 | 0.81944 | 1899-12-31 | 0 | 4.3333 | 4.3333 | Road approach issue | Close | 0.16667 | O2-05 | 3450.2361 |  | WTG Unscheduled Maintenance | 19109 | 3450.2361
2203 | 2024-09-20 | 2025 | 2024 | 2024-09-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.43542 | 0.43542 | 0.70833 | 0 | 6.55 | 6.55 | WTG Maintance work 3rd Day and OMS Audit Work | Close | 0.25192 | O2-12 | 3742.5063 |  | WTG Scheduled Maintenance | 13713 | 3742.5063
2204 | 2024-09-20 | 2025 | 2024 | 2024-09-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 6690 | Icing (stop) | Break down | 0.84375 | 0.84375 | 1899-12-31 | 0 | 3.75 | 3.75 | Material arrangment work and wtg wip | Close | 0.14423 | O2-12 | 2142.6562 |  | WTG Unscheduled Maintenance | 13713 | 2142.6562
2205 | 2024-09-20 | 2025 | 2024 | 2024-09-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.5125 | 0.5125 | 0.54306 | 0 | 0.73333 | 0.73333 | Manual stop for rep error by project team | Close | 0.028205 | O2-01 | 449.3806 |  | WTG Breakdown Maintenance | 14707 | 449.3806
2206 | 2024-09-20 | 2025 | 2024 | 2024-09-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.045833 | 0.045833 | 0.047917 | 0 | 0.05 | 0.05 | check data and reset and start WTG. | Close | 0.0019231 | O2-01 | 30.6396 |  | WTG Unscheduled Maintenance | 14707 | 30.6396
2207 | 2024-09-20 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.33472 | 0.33472 | 0.33611 | 0 | 0.033333 | 0.033333 | check data and reset and start WTG. | Close | 0.0012821 | O2-18 | 22.3986 |  | WTG Unscheduled Maintenance | 16127 | 22.3986
2208 | 2024-09-20 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.34306 | 0.34306 | 0.34514 | 0 | 0.05 | 0.05 | check data and reset and start WTG. | Close | 0.0019231 | O2-18 | 33.5979 |  | WTG Unscheduled Maintenance | 16127 | 33.5979
2209 | 2024-09-20 | 2025 | 2024 | 2024-09-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 650 | Pitch controller communication error | Break down | 0.69444 | 0.69444 | 0.69583 | 0 | 0.033333 | 0.033333 | check data and reset and start WTG. | Close | 0.0012821 | O2-04 | 24.8611 |  | WTG Unscheduled Maintenance | 17900 | 24.8611
2210 | 2024-09-20 | 2025 | 2024 | 2024-09-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.31944 | 0.31944 | 0.32153 | 0 | 0.05 | 0.05 | check data and reset and start WTG. | Close | 0.0019231 | O2-14 | 15.9938 |  | WTG Unscheduled Maintenance | 7677 | 15.9938
2211 | 2024-09-20 | 2025 | 2024 | 2024-09-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 650 | Pitch controller communication error | Break down | 0.042361 | 0.042361 | 0.045139 | 0 | 0.066667 | 0.066667 | check data and reset and start WTG. | Close | 0.0025641 | O2-11 | 37.6611 |  | WTG Unscheduled Maintenance | 13558 | 37.6611
2212 | 2024-09-20 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.50278 | 0.50278 | 0.50417 | 0 | 0.033333 | 0.033333 | check data and reset and start WTG. | Close | 0.0012821 | O2-06 | 21.0681 |  | WTG Unscheduled Maintenance | 15169 | 21.0681
2213 | 2024-09-20 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.67569 | 0.67569 | 0.69167 | 0 | 0.38333 | 0.38333 | check data and reset and start WTG. | Close | 0.014744 | O2-06 | 242.2826 |  | WTG Unscheduled Maintenance | 15169 | 242.2826
2214 | 2024-09-20 | 2025 | 2024 | 2024-09-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.56597 | 0.56597 | 0.56944 | 0 | 0.083333 | 0.083333 | check data and reset and start WTG. | Close | 0.0032051 | O2-06 | 52.6701 |  | WTG Unscheduled Maintenance | 15169 | 52.6701
2215 | 2024-09-21 | 2025 | 2024 | 2024-09-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Road issue | 0 | 0 | 0.38194 | 0 | 9.1667 | 9.1667 | Road approach issue | Open | 0.35256 | O2-05 | 6708.4722 |  | WTG Unscheduled Maintenance | 17564 | 6708.4722
2216 | 2024-09-21 | 2025 | 2024 | 2024-09-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Major BD | 0.45139 | 0.45139 | 0.84375 | 0 | 9.4167 | 9.4167 | WTG TRUBL SHUTING WORK AFTER FOUND M1 Module faulty | Open | 0.36218 | O2-05 | 6891.4306 |  | WTG Unscheduled Maintenance | 17564 | 6891.4306
2217 | 2024-09-21 | 2025 | 2024 | 2024-09-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Road issue | 0.84375 | 0.84375 | 1899-12-31 | 0 | 3.75 | 3.75 | Road approach issue | Open | 0.14423 | O2-05 | 2744.375 |  | WTG Unscheduled Maintenance | 17564 | 2744.375
2218 | 2024-09-21 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.33889 | 0.33889 | 0.34028 | 0 | 0.033333 | 0.033333 | check data and reset and start WTG. | Close | 0.0012821 | O2-07 | 26.3611 |  | WTG Unscheduled Maintenance | 18980 | 26.3611
2219 | 2024-09-21 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.37083 | 0.37083 | 0.37292 | 0 | 0.05 | 0.05 | check data and reset and start WTG. | Close | 0.0019231 | O2-07 | 39.5417 |  | WTG Unscheduled Maintenance | 18980 | 39.5417
2220 | 2024-09-21 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 1705 | Max. temp. gear bearing 1 | Break down | 0.014583 | 0.014583 | 0.022222 | 0 | 0.18333 | 0.18333 | check data and reset and start WTG. | Close | 0.0070513 | O2-21 | 136.9042 |  | WTG Unscheduled Maintenance | 17922 | 136.9042
2221 | 2024-09-21 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 1705 | Max. temp. gear bearing 1 | Break down | 0.088889 | 0.088889 | 0.10069 | 0 | 0.28333 | 0.28333 | check data and reset and start WTG. | Close | 0.010897 | O2-21 | 211.5792 |  | WTG Unscheduled Maintenance | 17922 | 211.5792
2222 | 2024-09-21 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 1705 | Max. temp. gear bearing 1 | Break down | 0.18264 | 0.18264 | 0.28333 | 0 | 2.4167 | 2.4167 | Attend and wtg check gear bearing temp sensor 1 and 2 value check so ok and all connection retight and check nacel coolant pressure value 3.5 bar ok after trail so ok | Close | 0.092949 | O2-21 | 1804.6458 |  | WTG Unscheduled Maintenance | 17922 | 1804.6458
2223 | 2024-09-21 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.46944 | 0.46944 | 0.52917 | 0 | 1.4333 | 1.4333 | wtg error rectification work | Close | 0.055128 | O2-21 | 1070.3417 |  | WTG Breakdown Maintenance | 17922 | 1070.3417
2224 | 2024-09-21 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.77569 | 0.77569 | 0.77708 | 0 | 0.033333 | 0.033333 | check data and reset and start WTG. | Close | 0.0012821 | O2-21 | 24.8917 |  | WTG Unscheduled Maintenance | 17922 | 24.8917
2225 | 2024-09-21 | 2025 | 2024 | 2024-09-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.55139 | 0.55139 | 0.55278 | 0 | 0.033333 | 0.033333 | check data and reset and start WTG. | Close | 0.0012821 | O2-15 | 21.4528 |  | WTG Unscheduled Maintenance | 15446 | 21.4528
2226 | 2024-09-21 | 2025 | 2024 | 2024-09-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 6690 | Icing (stop) | Break down | 0 | 0 | 0.23403 | 0 | 5.6167 | 5.6167 | Attend wtg wind vane altrasonic cable with shildring continuty check so ok after all cable properly lugging and apply sleev after wind vane aliment done after trail so ok after then start wtg | Close | 0.21603 | O2-12 | 3571.4979 |  | WTG Unscheduled Maintenance | 15261 | 3571.4979
2227 | 2024-09-21 | 2025 | 2024 | 2024-09-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.60903 | 0.60903 | 0.62639 | 0 | 0.41667 | 0.41667 | wtg error rectification work | Close | 0.016026 | O2-12 | 264.9479 |  | WTG Breakdown Maintenance | 15261 | 264.9479
2228 | 2024-09-21 | 2025 | 2024 | 2024-09-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 650 | Pitch controller communication error | Break down | 0.45208 | 0.45208 | 0.4625 | 0 | 0.25 | 0.25 | check data and reset and start WTG. | Close | 0.0096154 | O2-21 | 186.6875 |  | WTG Unscheduled Maintenance | 17922 | 186.6875
2229 | 2024-09-21 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.46597 | 0.46597 | 0.46875 | 0 | 0.066667 | 0.066667 | check data and reset and start WTG. | Close | 0.0025641 | O2-06 | 32.7028 |  | WTG Unscheduled Maintenance | 11773 | 32.7028
2230 | 2024-09-21 | 2025 | 2024 | 2024-09-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down | 0.53333 | 0.53333 | 0.53819 | 0 | 0.11667 | 0.11667 | check data and reset and start WTG. | Close | 0.0044872 | O2-01 | 71.9639 |  | WTG Unscheduled Maintenance | 14804 | 71.9639
2231 | 2024-09-22 | 2025 | 2024 | 2024-09-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Road issue | 0 | 0 | 0.3125 | 0 | 7.5 | 7.5 | Road approach issue | Close | 0.28846 | O2_05 | 4713.4375 |  | WTG Unscheduled Maintenance | 15083 | 4713.4375
2232 | 2024-09-22 | 2025 | 2024 | 2024-09-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Break down | 0.3125 | 0.3125 | 0.52083 | 0 | 5 | 5 | attend and found M1 modual in error so check all releted circuit found M1 software is corrupted so replace M1 mudual and reinstall sofware and some error accurs so replace programable card then reset and start WTG. | Close | 0.19231 | O2_05 | 3142.2917 |  | WTG Unscheduled Maintenance | 15083 | 3142.2917
2233 | 2024-09-22 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.45903 | 0.45903 | 0.46042 | 0 | 0.033333 | 0.033333 | check data and reset and start WTG. | Close | 0.0012821 | O2_07 | 17.1111 |  | WTG Unscheduled Maintenance | 12320 | 17.1111
2234 | 2024-09-22 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.87778 | 0.87778 | 0.87917 | 0 | 0.033333 | 0.033333 | check data and reset and start WTG. | Close | 0.0012821 | O2_07 | 17.1111 |  | WTG Unscheduled Maintenance | 12320 | 17.1111
2235 | 2024-09-22 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.50208 | 0.50208 | 0.50417 | 0 | 0.05 | 0.05 | check data and reset and start WTG. | Close | 0.0019231 | O2_21 | 22.5083 |  | WTG Unscheduled Maintenance | 10804 | 22.5083
2236 | 2024-09-22 | 2025 | 2024 | 2024-09-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.15139 | 0.15139 | 0.15278 | 0 | 0.033333 | 0.033333 | check data and reset and start WTG. | Close | 0.0012821 | O2_14 | 15.3278 |  | WTG Unscheduled Maintenance | 11036 | 15.3278
2237 | 2024-09-22 | 2025 | 2024 | 2024-09-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.22639 | 0.22639 | 0.22847 | 0 | 0.05 | 0.05 | check data and reset and start WTG. | Close | 0.0019231 | O2_14 | 22.9917 |  | WTG Unscheduled Maintenance | 11036 | 22.9917
2238 | 2024-09-22 | 2025 | 2024 | 2024-09-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.72431 | 0.72431 | 0.72639 | 0 | 0.05 | 0.05 | check data and reset and start WTG. | Close | 0.0019231 | O2_14 | 22.9917 |  | WTG Unscheduled Maintenance | 11036 | 22.9917
2239 | 2024-09-22 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.63958 | 0.63958 | 0.65139 | 0 | 0.28333 | 0.28333 | check data and reset and start WTG. | Close | 0.010897 | O2_06 | 166.2104 |  | WTG Unscheduled Maintenance | 14079 | 166.2104
2240 | 2024-09-22 | 2025 | 2024 | 2024-09-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.028472 | 0.028472 | 0.11667 | 0 | 2.1167 | 2.1167 | Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.08141 | O2_26 | 957.3507 |  | WTG Unscheduled Maintenance | 10855 | 957.3507
2241 | 2024-09-23 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.029861 | 0.029861 | 0.054167 | 0 | 0.58333 | 0.58333 | Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.022436 | O2_07 | 376.8576 |  | WTG Unscheduled Maintenance | 15505 | 376.8576
2242 | 2024-09-23 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.32153 | 0.32153 | 0.32361 | 0 | 0.05 | 0.05 | check data and reset and start WTG. | Close | 0.0019231 | O2_07 | 32.3021 |  | WTG Unscheduled Maintenance | 15505 | 32.3021
2243 | 2024-09-23 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.34514 | 0.34514 | 0.34722 | 0 | 0.05 | 0.05 | check data and reset and start WTG. | Close | 0.0019231 | O2_07 | 32.3021 |  | WTG Unscheduled Maintenance | 15505 | 32.3021
2244 | 2024-09-23 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.32847 | 0.32847 | 0.32986 | 0 | 0.033333 | 0.033333 | check data and reset and start WTG. | Close | 0.0012821 | O2_21 | 24.1014 |  | WTG Unscheduled Maintenance | 17353 | 24.1014
2245 | 2024-09-23 | 2025 | 2024 | 2024-09-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.43889 | 0.43889 | 0.73264 | 0 | 7.05 | 7.05 | WTG manual stop for Maintance work 3rd Day | Close | 0.27115 | O2_15 | 4435.9187 |  | WTG Scheduled Maintenance | 15101 | 4435.9187
2246 | 2024-09-23 | 2025 | 2024 | 2024-09-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.19583 | 0.19583 | 0.20486 | 0 | 0.21667 | 0.21667 | Check error data than reset and start Wtg. | Close | 0.0083333 | O2_14 | 137.6375 |  | WTG Unscheduled Maintenance | 15246 | 137.6375
2247 | 2024-09-23 | 2025 | 2024 | 2024-09-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.027083 | 0.027083 | 0.051389 | 0 | 0.58333 | 0.58333 | Check error data than reset and start Wtg. | Close | 0.022436 | O2_21 | 421.7743 |  | WTG Unscheduled Maintenance | 17353 | 421.7743
2248 | 2024-09-23 | 2025 | 2024 | 2024-09-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.080556 | 0.080556 | 0.091667 | 0 | 0.26667 | 0.26667 | Check error data than reset and start Wtg. | Close | 0.010256 | O2_21 | 192.8111 |  | WTG Unscheduled Maintenance | 17353 | 192.8111
2249 | 2024-09-23 | 2025 | 2024 | 2024-09-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.10625 | 0.10625 | 0.13472 | 0 | 0.68333 | 0.68333 | Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.026282 | O2_21 | 494.0785 |  | WTG Unscheduled Maintenance | 17353 | 494.0785
2250 | 2024-09-23 | 2025 | 2024 | 2024-09-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.14514 | 0.14514 | 0.15139 | 0 | 0.15 | 0.15 | Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.0057692 | O2_21 | 108.4562 |  | WTG Unscheduled Maintenance | 17353 | 108.4562
2251 | 2024-09-23 | 2025 | 2024 | 2024-09-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.21111 | 0.21111 | 0.22361 | 0 | 0.3 | 0.3 | Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.011538 | O2_21 | 216.9125 |  | WTG Unscheduled Maintenance | 17353 | 216.9125
2252 | 2024-09-23 | 2025 | 2024 | 2024-09-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.29583 | 0.29583 | 0.30486 | 0 | 0.21667 | 0.21667 | Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.0083333 | O2_21 | 156.659 |  | WTG Unscheduled Maintenance | 17353 | 156.659
2253 | 2024-09-23 | 2025 | 2024 | 2024-09-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.88681 | 0.88681 | 0.89653 | 0 | 0.23333 | 0.23333 | Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.0089744 | O2_21 | 168.7097 |  | WTG Unscheduled Maintenance | 17353 | 168.7097
2254 | 2024-09-23 | 2025 | 2024 | 2024-09-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 1065 | Drive train monitor level 1 | Break down | 0.93681 | 0.93681 | 0.97014 | 0 | 0.8 | 0.8 | Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.030769 | O2_21 | 578.4333 |  | WTG Unscheduled Maintenance | 17353 | 578.4333
2255 | 2024-09-23 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.31806 | 0.31806 | 0.31944 | 0 | 0.033333 | 0.033333 | Check error data than reset and start Wtg. | Close | 0.0012821 | O2_06 | 19.6556 |  | WTG Unscheduled Maintenance | 14152 | 19.6556
2256 | 2024-09-23 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.35694 | 0.35694 | 0.36111 | 0 | 0.1 | 0.1 | Check error data than reset and start Wtg. | Close | 0.0038462 | O2_06 | 58.9667 |  | WTG Unscheduled Maintenance | 14152 | 58.9667
2257 | 2024-09-23 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.60417 | 0.60417 | 0.60556 | 0 | 0.033333 | 0.033333 | Check error data than reset and start Wtg. | Close | 0.0012821 | O2_06 | 19.6556 |  | WTG Unscheduled Maintenance | 14152 | 19.6556
2258 | 2024-09-23 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.79931 | 0.79931 | 0.80417 | 0 | 0.11667 | 0.11667 | Check error data than reset and start Wtg. | Close | 0.0044872 | O2_06 | 68.7944 |  | WTG Unscheduled Maintenance | 14152 | 68.7944
2259 | 2024-09-23 | 2025 | 2024 | 2024-09-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.63611 | 0.63611 | 0.64931 | 0 | 0.31667 | 0.31667 | WTG manual stop for visit by visitors | Close | 0.012179 | O2_25 | 245.8653 |  | WTG Breakdown Maintenance | 18634 | 245.8653
2260 | 2024-09-23 | 2025 | 2024 | 2024-09-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.5625 | 0.5625 | 0.56736 | 0 | 0.11667 | 0.11667 | Check error data than reset and start Wtg. | Close | 0.0044872 | O2_01 | 68.2257 |  | WTG Unscheduled Maintenance | 14035 | 68.2257
2261 | 2024-09-23 | 2025 | 2024 | 2024-09-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.57222 | 0.57222 | 0.57917 | 0 | 0.16667 | 0.16667 | Check error data than reset and start Wtg. | Close | 0.0064103 | O2_01 | 97.4653 |  | WTG Unscheduled Maintenance | 14035 | 97.4653
2262 | 2024-09-23 | 2025 | 2024 | 2024-09-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Break down | 0.58472 | 0.58472 | 0.76042 | 0 | 4.2167 | 4.2167 | attend and Wtg check flat resistor axis No:01 so Value Not Ok after Replace New flat Resistor reset Wtg return Pitch power supply failure error found after check all axis and check all Connection so found Main switch Single phase power cut off after main sweetch connection properly retigh after properly supply ok after reset Wtg and start wtg. | Close | 0.16218 | O2_01 | 2465.8715 |  | WTG Unscheduled Maintenance | 14035 | 2465.8715
2263 | 2024-09-23 | 2025 | 2024 | 2024-09-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.6875 | 0.6875 | 0.73958 | 0 | 1.25 | 1.25 | Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.048077 | O2_26 | 656.6146 |  | WTG Unscheduled Maintenance | 12607 | 656.6146
2264 | 2024-09-24 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.077778 | 0.077778 | 0.079861 | 0 | 0.05 | 0.05 | Check error data than reset and start Wtg. | Close | 0.0019231 | O2_21 | 40.575 |  | WTG Unscheduled Maintenance | 19476 | 40.575
2265 | 2024-09-24 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.18819 | 0.18819 | 0.18958 | 0 | 0.033333 | 0.033333 | Check error data than reset and start Wtg. | Close | 0.0012821 | O2_21 | 27.05 |  | WTG Unscheduled Maintenance | 19476 | 27.05
2266 | 2024-09-24 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.73542 | 0.73542 | 0.74722 | 0 | 0.28333 | 0.28333 | Check error data than reset and start Wtg. | Close | 0.010897 | O2_21 | 229.925 |  | WTG Unscheduled Maintenance | 19476 | 229.925
2267 | 2024-09-24 | 2025 | 2024 | 2024-09-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.56458 | 0.56458 | 0.57083 | 0 | 0.15 | 0.15 | Check error data than reset and start Wtg. | Close | 0.0057692 | O2_12 | 99.375 |  | WTG Unscheduled Maintenance | 15900 | 99.375
2268 | 2024-09-24 | 2025 | 2024 | 2024-09-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.61042 | 0.61042 | 0.775 | 0 | 3.95 | 3.95 | Attend and found top box 400v HUB supply MPCB FC001 trip so checke HUB side and nacelle side cable continuity is ok so charge MPCB then start wtg | Close | 0.15192 | O2_11 | 2619.8375 |  | WTG Unscheduled Maintenance | 15918 | 2619.8375
2269 | 2024-09-24 | 2025 | 2024 | 2024-09-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.90833 | 0.90833 | 1899-12-31 | 0 | 2.2 | 2.2 | WIP | Open | 0.084615 | O2_11 | 1459.15 |  | WTG Unscheduled Maintenance | 15918 | 1459.15
2270 | 2024-09-24 | 2025 | 2024 | 2024-09-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.45903 | 0.45903 | 0.70417 | 0 | 5.8833 | 5.8833 | WTG manual stop for Maintance work 3rd Day | Close | 0.22628 | O2_10 | 3922.7125 |  | WTG Scheduled Maintenance | 16002 | 3922.7125
2271 | 2024-09-24 | 2025 | 2024 | 2024-09-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Break down | 0.0020833 | 0.0020833 | 0.022222 | 0 | 0.48333 | 0.48333 | Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.01859 | O2_21 | 392.225 |  | WTG Unscheduled Maintenance | 19476 | 392.225
2272 | 2024-09-24 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.0069444 | 0.0069444 | 0.022917 | 0 | 0.38333 | 0.38333 | Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.014744 | O2_06 | 258.8458 |  | WTG Unscheduled Maintenance | 16206 | 258.8458
2273 | 2024-09-24 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.086111 | 0.086111 | 0.10764 | 0 | 0.51667 | 0.51667 | Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.019872 | O2_06 | 348.8792 |  | WTG Unscheduled Maintenance | 16206 | 348.8792
2274 | 2024-09-24 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.27083 | 0.27083 | 0.27431 | 0 | 0.083333 | 0.083333 | Check error data than reset and start Wtg. | Close | 0.0032051 | O2_06 | 56.2708 |  | WTG Unscheduled Maintenance | 16206 | 56.2708
2275 | 2024-09-24 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.50208 | 0.50208 | 0.575 | 0 | 1.75 | 1.75 | WTG manual stop for rep error inspection work. | Close | 0.067308 | O2_06 | 1181.6875 |  | WTG Breakdown Maintenance | 16206 | 1181.6875
2276 | 2024-09-24 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.59444 | 0.59444 | 0.60208 | 0 | 0.18333 | 0.18333 | Check error data than reset and start Wtg. | Close | 0.0070513 | O2_06 | 123.7958 |  | WTG Unscheduled Maintenance | 16206 | 123.7958
2277 | 2024-09-24 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.98125 | 0.98125 | 0.98264 | 0 | 0.033333 | 0.033333 | Check error data than reset and start Wtg. | Close | 0.0012821 | O2_06 | 22.5083 |  | WTG Unscheduled Maintenance | 16206 | 22.5083
2278 | 2024-09-24 | 2025 | 2024 | 2024-09-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.67361 | 0.67361 | 0.75 | 0 | 1.8333 | 1.8333 | WTG manual stop for project pending work by O2 project team | Close | 0.070513 | O2_26 | 1383.3264 |  | WTG Breakdown Maintenance | 18109 | 1383.3264
2279 | 2024-09-24 | 2025 | 2024 | 2024-09-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.89236 | 0.89236 | 1899-12-31 | 0 | 2.5833 | 2.5833 | wip | Open | 0.099359 | O2_26 | 1949.2326 |  | WTG Unscheduled Maintenance | 18109 | 1949.2326
2280 | 2024-09-25 | 2025 | 2024 | 2024-09-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.47778 | 0.47778 | 0.77639 | 0 | 7.1667 | 7.1667 | wtg manual stop for project pending work. | Close | 0.27564 | O2_04 | 7408.2431 |  | WTG Breakdown Maintenance | 24809 | 7408.2431
2281 | 2024-09-25 | 2025 | 2024 | 2024-09-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Major BD | 0 | 0 | 1899-12-31 | 0 | 24 | 24 | Attend and found 400v Hub MPCB (FC001) Trip so check and found MPCB 1 phase in ground so interchange cable with neutral cable, both sides Hub and nacelle ,then start wtg now second time MPCB trip so check and found one another cable are ground in HUB rotated time. Required Hub Slipring WTr so Material arrangement work WIP. | Open | 0.92308 | O2_11 | 21782 |  | WTG Unscheduled Maintenance | 21782 | 21782
2282 | 2024-09-25 | 2025 | 2024 | 2024-09-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.58333 | 0.58333 | 0.59444 | 0 | 0.26667 | 0.26667 | WTG stop by costomer for inspection work . | Close | 0.010256 | O2_10 | 224.3667 |  | WTG Breakdown Maintenance | 20193 | 224.3667
2283 | 2024-09-25 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.62431 | 0.62431 | 0.71806 | 0 | 2.25 | 2.25 | Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.086538 | O2_06 | 1958.4375 |  | WTG Unscheduled Maintenance | 20890 | 1958.4375
2284 | 2024-09-25 | 2025 | 2024 | 2024-09-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.52847 | 0.52847 | 0.69514 | 0 | 4 | 4 | wtg manual stop for service audit work. | Close | 0.15385 | O2_06 | 3481.6667 |  | WTG Breakdown Maintenance | 20890 | 3481.6667
2285 | 2024-09-25 | 2025 | 2024 | 2024-09-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.42222 | 0.42222 | 0.43403 | 0 | 0.28333 | 0.28333 | Check error data than reset and start Wtg. | Close | 0.010897 | O2_01 | 249.1681 |  | WTG Unscheduled Maintenance | 21106 | 249.1681
2286 | 2024-09-25 | 2025 | 2024 | 2024-09-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.88958 | 0.88958 | 0.91736 | 0 | 0.66667 | 0.66667 | Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.025641 | O2_01 | 586.2778 |  | WTG Unscheduled Maintenance | 21106 | 586.2778
2287 | 2024-09-25 | 2025 | 2024 | 2024-09-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0 | 0 | 0.14861 | 0 | 3.5667 | 3.5667 | atten and chechk all releted ckt and found HUB central box found silica so removed it apply hard reboot then start wtg. | Close | 0.13718 | O2_26 | 2680.35 |  | WTG Unscheduled Maintenance | 18036 | 2680.35
2288 | 2024-09-25 | 2025 | 2024 | 2024-09-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.71736 | 0.71736 | 0.73264 | 0 | 0.36667 | 0.36667 | wtg stop for software update work | Close | 0.014103 | O2_26 | 275.55 |  | WTG Breakdown Maintenance | 18036 | 275.55
2289 | 2024-09-25 | 2025 | 2024 | 2024-09-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.92708 | 0.92708 | 0.99306 | 0 | 1.5833 | 1.5833 | Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.060897 | O2_26 | 1189.875 |  | WTG Unscheduled Maintenance | 18036 | 1189.875
2290 | 2024-09-26 | 2025 | 2024 | 2024-09-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3060 | Conv. emerg.off type A | Break down | 0.81319 | 0.81319 | 0.84583 | 0 | 0.78333 | 0.78333 | Checked related error data log fond grid jurk so apply soft reboot then reset & start the WTG. | Close | 0.030128 | O2_09 | 505.2826 |  | WTG Unscheduled Maintenance | 15481 | 505.2826
2291 | 2024-09-26 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.38611 | 0.38611 | 0.3875 | 0 | 0.033333 | 0.033333 | Check error data than reset and start Wtg. | Close | 0.0012821 | O2_07 | 7.1806 |  | WTG Unscheduled Maintenance | 5170 | 7.1806
2292 | 2024-09-26 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.84722 | 0.84722 | 0.85764 | 0 | 0.25 | 0.25 | after grid resume Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.0096154 | O2_07 | 53.8542 |  | WTG Unscheduled Maintenance | 5170 | 53.8542
2293 | 2024-09-26 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.13889 | 0.13889 | 0.15903 | 0 | 0.48333 | 0.48333 | after grid resume Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.01859 | O2_21 | 203.8861 |  | WTG Unscheduled Maintenance | 10124 | 203.8861
2294 | 2024-09-26 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.24931 | 0.24931 | 0.25139 | 0 | 0.05 | 0.05 | Check error data than reset and start Wtg. | Close | 0.0019231 | O2_21 | 21.0917 |  | WTG Unscheduled Maintenance | 10124 | 21.0917
2295 | 2024-09-26 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.52986 | 0.52986 | 0.56597 | 0 | 0.86667 | 0.86667 | Check error data than reset and start Wtg. | Close | 0.033333 | O2_21 | 365.5889 |  | WTG Unscheduled Maintenance | 10124 | 365.5889
2296 | 2024-09-26 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.59653 | 0.59653 | 0.66944 | 0 | 1.75 | 1.75 | Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.067308 | O2_21 | 738.2083 |  | WTG Unscheduled Maintenance | 10124 | 738.2083
2297 | 2024-09-26 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.84722 | 0.84722 | 0.85694 | 0 | 0.23333 | 0.23333 | after grid resume Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.0089744 | O2_21 | 98.4278 |  | WTG Unscheduled Maintenance | 10124 | 98.4278
2298 | 2024-09-26 | 2025 | 2024 | 2024-09-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.13889 | 0.13889 | 0.31042 | 0 | 4.1167 | 4.1167 | after grid resume error is occurs and wtg is not cannected in SCADA so chechk and found wtg software side issues so check and correct it then start WTG. | Close | 0.15833 | O2_04 | 2356.4486 |  | WTG Unscheduled Maintenance | 13738 | 2356.4486
2299 | 2024-09-26 | 2025 | 2024 | 2024-09-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.49444 | 0.49444 | 0.76944 | 0 | 6.6 | 6.6 | wtg manual stop for project pending work. | Close | 0.25385 | O2_04 | 3777.95 |  | WTG Breakdown Maintenance | 13738 | 3777.95
2300 | 2024-09-26 | 2025 | 2024 | 2024-09-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Major BD | 0 | 0 | 0.83333 | 0 | 20 | 20 | attend removed slipring cable found cable ground so replace it WIP. | Close | 0.76923 | O2_11 | 12128.3333 |  | WTG Unscheduled Maintenance | 14554 | 12128.3333
2301 | 2024-09-26 | 2025 | 2024 | 2024-09-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.83333 | 0.83333 | 1899-12-31 | 0 | 4 | 4 | attend removed slipring cable found cable ground so replace time environmtent condition is not suitable so now work is stop | Close | 0.15385 | O2_11 | 2425.6667 |  | WTG Unscheduled Maintenance | 14554 | 2425.6667
2302 | 2024-09-26 | 2025 | 2024 | 2024-09-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down | 0.82569 | 0.82569 | 0.84375 | 0 | 0.43333 | 0.43333 | Checked related error data log fond grid jurk so apply soft reboot then reset & start the WTG. | Close | 0.016667 | O2_12 | 267.8542 |  | WTG Unscheduled Maintenance | 14835 | 267.8542
2303 | 2024-09-26 | 2025 | 2024 | 2024-09-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.54097 | 0.54097 | 0.54514 | 0 | 0.1 | 0.1 | WTG stop by costomer for inspection work . | Close | 0.0038462 | O2_10 | 51.8333 |  | WTG Breakdown Maintenance | 12440 | 51.8333
2304 | 2024-09-26 | 2025 | 2024 | 2024-09-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Road issue | 0.13889 | 0.13889 | 0.29167 | 0 | 3.6667 | 3.6667 | wtg not attending due to Road not approchable and heavy rain and lighting. | Close | 0.14103 | O2_21 | 1546.7222 |  | WTG Unscheduled Maintenance | 10124 | 1546.7222
2305 | 2024-09-26 | 2025 | 2024 | 2024-09-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.29167 | 0.29167 | 0.45139 | 0 | 3.8333 | 3.8333 | attend wtg after grid resume Checked related error data log apply hard reboot then reset & start the WTG. | Close | 0.14744 | O2_21 | 1617.0278 |  | WTG Unscheduled Maintenance | 10124 | 1617.0278
2306 | 2024-09-26 | 2025 | 2024 | 2024-09-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.84722 | 0.84722 | 0.86875 | 0 | 0.51667 | 0.51667 | after grid resume Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.019872 | O2_21 | 217.9472 |  | WTG Unscheduled Maintenance | 10124 | 217.9472
2307 | 2024-09-26 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Major BD | 0.13889 | 0.13889 | 0.83542 | 0 | 16.7167 | 16.7167 | after grid resume Checked related error data log found wtg have a software side issues so wtg handover software teame. | Close | 0.64295 | O2_06 | 7429.1653 |  | WTG Unscheduled Maintenance | 10666 | 7429.1653
2308 | 2024-09-26 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Road issue | 0.84722 | 0.84722 | 1899-12-31 | 0 | 3.6667 | 3.6667 | troubleshooting time environmtent condition is not suitable,Road not approchable and heavy rain and lighting.so now work is stop, | Close | 0.14103 | O2_06 | 1629.5278 |  | WTG Unscheduled Maintenance | 10666 | 1629.5278
2309 | 2024-09-26 | 2025 | 2024 | 2024-09-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.13889 | 0.13889 | 0.15417 | 0 | 0.36667 | 0.36667 | after grid resume Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.014103 | O2_24 | 201.575 |  | WTG Unscheduled Maintenance | 13194 | 201.575
2310 | 2024-09-26 | 2025 | 2024 | 2024-09-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.84722 | 0.84722 | 0.85417 | 0 | 0.16667 | 0.16667 | after grid resume Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.0064103 | O2_24 | 91.625 |  | WTG Unscheduled Maintenance | 13194 | 91.625
2311 | 2024-09-26 | 2025 | 2024 | 2024-09-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.13889 | 0.13889 | 0.15417 | 0 | 0.36667 | 0.36667 | after grid resume Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.014103 | O2_06 | 162.9528 |  | WTG Unscheduled Maintenance | 10666 | 162.9528
2312 | 2024-09-26 | 2025 | 2024 | 2024-09-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.84722 | 0.84722 | 0.85278 | 0 | 0.13333 | 0.13333 | after grid resume Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.0051282 | O2_06 | 59.2556 |  | WTG Unscheduled Maintenance | 10666 | 59.2556
2313 | 2024-09-26 | 2025 | 2024 | 2024-09-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.13889 | 0.13889 | 0.16111 | 0 | 0.53333 | 0.53333 | after grid resume Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.020513 | O2_20 | 300.2222 |  | WTG Unscheduled Maintenance | 13510 | 300.2222
2314 | 2024-09-26 | 2025 | 2024 | 2024-09-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down | 0.82014 | 0.82014 | 0.83542 | 0 | 0.36667 | 0.36667 | Checked related error data log fond grid jurk so apply soft reboot then reset & start the WTG. | Close | 0.014103 | O2_20 | 206.4028 |  | WTG Unscheduled Maintenance | 13510 | 206.4028
2315 | 2024-09-26 | 2025 | 2024 | 2024-09-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down | 0.83333 | 0.83333 | 0.85208 | 0 | 0.45 | 0.45 | after grid resume Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.017308 | O2_20 | 253.3125 |  | WTG Unscheduled Maintenance | 13510 | 253.3125
2316 | 2024-09-26 | 2025 | 2024 | 2024-09-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.55903 | 0.55903 | 0.5625 | 0 | 0.083333 | 0.083333 | WTG stop by costomer for inspection work . | Close | 0.0032051 | O2_25 | 63.9687 |  | WTG Breakdown Maintenance | 18423 | 63.9687
2317 | 2024-09-26 | 2025 | 2024 | 2024-09-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.74514 | 0.74514 | 0.75903 | 0 | 0.33333 | 0.33333 | Checked related error data log fond grid jurk so apply soft reboot then reset & start the WTG. | Close | 0.012821 | O2_26 | 255.875 |  | WTG Unscheduled Maintenance | 18423 | 255.875
2318 | 2024-09-26 | 2025 | 2024 | 2024-09-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.86875 | 0.86875 | 0.87569 | 0 | 0.16667 | 0.16667 | Checked related error data log so apply soft reboot then reset & start the WTG. | Close | 0.0064103 | O2_26 | 127.9375 |  | WTG Unscheduled Maintenance | 18423 | 127.9375
2319 | 2024-09-26 | 2025 | 2024 | 2024-09-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.81667 | 0.81667 | 0.84167 | 0 | 0.6 | 0.6 | Checked related error data log so apply soft reboot then reset & start the WTG. | Close | 0.023077 | O2_02 | 455.4 |  | WTG Unscheduled Maintenance | 18216 | 455.4
2320 | 2024-09-27 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.28403 | 0.28403 | 0.28542 | 0 | 0.033333 | 0.033333 | Check error data than reset and start Wtg. | Close | 0.0012821 | O2_07 | 36.5292 |  | WTG Unscheduled Maintenance | 26301 | 36.5292
2321 | 2024-09-27 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 2521 | Gen.sp.analog <<>> gearb.sp. | Break down | 0.42639 | 0.42639 | 0.4375 | 0 | 0.26667 | 0.26667 | Auto reseted | Close | 0.010256 | O2_07 | 292.2333 |  | WTG Unscheduled Maintenance | 26301 | 292.2333
2322 | 2024-09-27 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Break down | 0.72917 | 0.72917 | 0.95486 | 0 | 5.4167 | 5.4167 | attend and Checked related error found axis 2 (1.7 ohms) flat resister faulty so replace with new one then start WTG. | Close | 0.20833 | O2_07 | 5935.9896 |  | WTG Unscheduled Maintenance | 26301 | 5935.9896
2323 | 2024-09-27 | 2025 | 2024 | 2024-09-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.10417 | 0.10417 | 0.10625 | 0 | 0.05 | 0.05 | Check error data than reset and start Wtg. | Close | 0.0019231 | O2_14 | 66.2437 |  | WTG Unscheduled Maintenance | 31797 | 66.2437
2324 | 2024-09-27 | 2025 | 2024 | 2024-09-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 1130 | Acceleration detector drivetrain | Break down | 0.8375 | 0.8375 | 0.85347 | 0 | 0.38333 | 0.38333 | Checked related error data log so apply soft reboot then reset & start the WTG. | Close | 0.014744 | O2_14 | 507.8687 |  | WTG Unscheduled Maintenance | 31797 | 507.8687
2325 | 2024-09-27 | 2025 | 2024 | 2024-09-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Major BD | 0 | 0 | 0.70139 | 0 | 16.8333 | 16.8333 | Attend and check related circuit than found slipring cable cut inside so remoce and refix properly than take trial than frequency converter error so top up coolant and CAN cable connection retught than reset and start Wtg. | Close | 0.64744 | O2_11 | 21415.5069 |  | WTG Unscheduled Maintenance | 30533 | 21415.5069
2326 | 2024-09-27 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Environment | 0 | 0 | 0.29167 | 0 | 7 | 7 | environmtent condition is not suitable,Road not approchable and heavy rain and lighting.so now work is stop, | Close | 0.26923 | O2_06 | 10158.75 |  | WTG Unscheduled Maintenance | 34830 | 10158.75
2327 | 2024-09-27 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Major BD | 0.29167 | 0.29167 | 0.72847 | 0 | 10.4833 | 10.4833 | attend for Pitch initialization error so check related circuit than nothing found abnoram than update software of MX220 amd also SLC programing and MC212 software update work Done than take trial and reset and start Wtg. | Close | 0.40321 | O2_06 | 15213.9375 |  | WTG Unscheduled Maintenance | 34830 | 15213.9375
2328 | 2024-09-27 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.98333 | 0.98333 | 0.98958 | 0 | 0.15 | 0.15 | Check error data than reset and start Wtg. | Close | 0.0057692 | O2_06 | 217.6875 |  | WTG Unscheduled Maintenance | 34830 | 217.6875
2329 | 2024-09-27 | 2025 | 2024 | 2024-09-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.59028 | 0.59028 | 0.59514 | 0 | 0.11667 | 0.11667 | Check error data than reset and start Wtg. | Close | 0.0044872 | O2_01 | 146.0375 |  | WTG Unscheduled Maintenance | 30042 | 146.0375
2330 | 2024-09-27 | 2025 | 2024 | 2024-09-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.49583 | 0.49583 | 0.70833 | 0 | 5.1 | 5.1 | wtg manual stop by project team for project pending work (rotor bolt replacement work) | Close | 0.19615 | O2_04 | 4524.7625 |  | WTG Breakdown Maintenance | 21293 | 4524.7625
2331 | 2024-09-28 | 2025 | 2024 | 2024-09-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 657 | Error pitch converter 2 | Break down | 0.45417 | 0.45417 | 0.45972 | 0 | 0.13333 | 0.13333 | Check error data than reset and start Wtg. | Close | 0.0051282 | O2_26 | 100.7611 |  | WTG Unscheduled Maintenance | 18137 | 100.7611
2332 | 2024-09-28 | 2025 | 2024 | 2024-09-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.63403 | 0.63403 | 0.63542 | 0 | 0.033333 | 0.033333 | auto reseted | Close | 0.0012821 | O2_05 | 29.8681 |  | WTG Unscheduled Maintenance | 21505 | 29.8681
2333 | 2024-09-28 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.56597 | 0.56597 | 0.63194 | 0 | 1.5833 | 1.5833 | wtg manual stop for project pending work | Close | 0.060897 | O2_07 | 1184.5972 |  | WTG Breakdown Maintenance | 17956 | 1184.5972
2334 | 2024-09-28 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.67014 | 0.67014 | 0.67153 | 0 | 0.033333 | 0.033333 | Check error data than reset and start Wtg. | Close | 0.0012821 | O2_21 | 23.5444 |  | WTG Unscheduled Maintenance | 16952 | 23.5444
2335 | 2024-09-28 | 2025 | 2024 | 2024-09-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.95972 | 0.95972 | 0.96319 | 0 | 0.083333 | 0.083333 | Check error data than reset and start Wtg. | Close | 0.0032051 | O2_03 | 66.559 |  | WTG Unscheduled Maintenance | 19169 | 66.559
2336 | 2024-09-28 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.18889 | 0.18889 | 0.19722 | 0 | 0.2 | 0.2 | Check error data than reset and start Wtg. | Close | 0.0076923 | O2_06 | 154.075 |  | WTG Unscheduled Maintenance | 18489 | 154.075
2337 | 2024-09-28 | 2025 | 2024 | 2024-09-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 4093 | Rel. air hum. tower base inside too high (in operation) | Break down | 0.32639 | 0.32639 | 0.33264 | 0 | 0.15 | 0.15 | Check error data than reset and start Wtg. | Close | 0.0057692 | O2_06 | 115.5562 |  | WTG Unscheduled Maintenance | 18489 | 115.5562
2338 | 2024-09-28 | 2025 | 2024 | 2024-09-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.20694 | 0.20694 | 0.20833 | 0 | 0.033333 | 0.033333 | Check error data than reset and start Wtg. | Close | 0.0012821 | O2_06 | 25.6792 |  | WTG Unscheduled Maintenance | 18489 | 25.6792
2339 | 2024-09-28 | 2025 | 2024 | 2024-09-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.26111 | 0.26111 | 0.2625 | 0 | 0.033333 | 0.033333 | Check error data than reset and start Wtg. | Close | 0.0012821 | O2_06 | 25.6792 |  | WTG Unscheduled Maintenance | 18489 | 25.6792
2340 | 2024-09-29 | 2025 | 2024 | 2024-09-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.73958 | 0.73958 | 0.74514 | 0 | 0.13333 | 0.13333 | after grid resume Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.0051282 | O2_26 | 29.0944 |  | WTG Unscheduled Maintenance | 5237 | 29.0944
2341 | 2024-09-29 | 2025 | 2024 | 2024-09-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 657 | Error pitch converter 2 | Break down | 0.75208 | 0.75208 | 0.75764 | 0 | 0.13333 | 0.13333 | Check error data than reset and start Wtg. | Close | 0.0051282 | O2_26 | 29.0944 |  | WTG Unscheduled Maintenance | 5237 | 29.0944
2342 | 2024-09-29 | 2025 | 2024 | 2024-09-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.51736 | 0.51736 | 0.52083 | 0 | 0.083333 | 0.083333 | Check error data than reset and start Wtg. | Close | 0.0032051 | O2_05 | 25.3785 |  | WTG Unscheduled Maintenance | 7309 | 25.3785
2343 | 2024-09-29 | 2025 | 2024 | 2024-09-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.73958 | 0.73958 | 0.74306 | 0 | 0.083333 | 0.083333 | after grid resume Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.0032051 | O2_09 | 18.8681 |  | WTG Unscheduled Maintenance | 5434 | 18.8681
2344 | 2024-09-29 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.23889 | 0.23889 | 0.24028 | 0 | 0.033333 | 0.033333 | Check error data than reset and start Wtg. | Close | 0.0012821 | O2_07 | 10.2681 |  | WTG Unscheduled Maintenance | 7393 | 10.2681
2345 | 2024-09-29 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.38889 | 0.38889 | 0.39097 | 0 | 0.05 | 0.05 | Check error data than reset and start Wtg. | Close | 0.0019231 | O2_07 | 15.4021 |  | WTG Unscheduled Maintenance | 7393 | 15.4021
2346 | 2024-09-29 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.42986 | 0.42986 | 0.43472 | 0 | 0.11667 | 0.11667 | Check error data than reset and start Wtg. | Close | 0.0044872 | O2_07 | 35.9382 |  | WTG Unscheduled Maintenance | 7393 | 35.9382
2347 | 2024-09-29 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.49514 | 0.49514 | 0.50069 | 0 | 0.13333 | 0.13333 | Check error data than reset and start Wtg. | Close | 0.0051282 | O2_07 | 41.0722 |  | WTG Unscheduled Maintenance | 7393 | 41.0722
2348 | 2024-09-29 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.28333 | 0.28333 | 0.29167 | 0 | 0.2 | 0.2 | Check error data than reset and start Wtg. | Close | 0.0076923 | O2_21 | 39.8583 |  | WTG Unscheduled Maintenance | 4783 | 39.8583
2349 | 2024-09-29 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.73958 | 0.73958 | 0.74653 | 0 | 0.16667 | 0.16667 | after grid resume Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.0064103 | O2_21 | 33.2153 |  | WTG Unscheduled Maintenance | 4783 | 33.2153
2350 | 2024-09-29 | 2025 | 2024 | 2024-09-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.73958 | 0.73958 | 0.74583 | 0 | 0.15 | 0.15 | after grid resume Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.0057692 | O2_03 | 35.0062 |  | WTG Unscheduled Maintenance | 5601 | 35.0062
2351 | 2024-09-29 | 2025 | 2024 | 2024-09-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.73958 | 0.73958 | 0.74722 | 0 | 0.18333 | 0.18333 | after grid resume Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.0070513 | O2_15 | 38.034 |  | WTG Unscheduled Maintenance | 4979 | 38.034
2352 | 2024-09-29 | 2025 | 2024 | 2024-09-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.73958 | 0.73958 | 0.74792 | 0 | 0.2 | 0.2 | after grid resume Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.0076923 | O2_12 | 45.0167 |  | WTG Unscheduled Maintenance | 5402 | 45.0167
2353 | 2024-09-29 | 2025 | 2024 | 2024-09-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.73958 | 0.73958 | 0.74861 | 0 | 0.21667 | 0.21667 | after grid resume Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.0083333 | O2_14 | 46.7368 |  | WTG Unscheduled Maintenance | 5177 | 46.7368
2354 | 2024-09-29 | 2025 | 2024 | 2024-09-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.73958 | 0.73958 | 0.74861 | 0 | 0.21667 | 0.21667 | after grid resume Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.0083333 | O2_11 | 46.7187 |  | WTG Unscheduled Maintenance | 5175 | 46.7187
2355 | 2024-09-29 | 2025 | 2024 | 2024-09-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.73958 | 0.73958 | 0.74861 | 0 | 0.21667 | 0.21667 | after grid resume Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.0083333 | O2_12 | 48.7681 |  | WTG Unscheduled Maintenance | 5402 | 48.7681
2356 | 2024-09-29 | 2025 | 2024 | 2024-09-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.73958 | 0.73958 | 0.75 | 0 | 0.25 | 0.25 | after grid resume Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.0096154 | O2_10 | 44.375 |  | WTG Unscheduled Maintenance | 4260 | 44.375
2357 | 2024-09-29 | 2025 | 2024 | 2024-09-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.73958 | 0.73958 | 0.74931 | 0 | 0.23333 | 0.23333 | after grid resume Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.0089744 | O2_21 | 46.5014 |  | WTG Unscheduled Maintenance | 4783 | 46.5014
2358 | 2024-09-29 | 2025 | 2024 | 2024-09-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.73958 | 0.73958 | 0.75556 | 0 | 0.38333 | 0.38333 | after grid resume Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.014744 | O2_24 | 75.4847 |  | WTG Unscheduled Maintenance | 4726 | 75.4847
2359 | 2024-09-29 | 2025 | 2024 | 2024-09-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.73958 | 0.73958 | 0.75556 | 0 | 0.38333 | 0.38333 | after grid resume Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.014744 | O2_06 | 87.5437 |  | WTG Unscheduled Maintenance | 5481 | 87.5437
2360 | 2024-09-29 | 2025 | 2024 | 2024-09-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.73958 | 0.73958 | 0.75139 | 0 | 0.28333 | 0.28333 | after grid resume Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.010897 | O2_20 | 65.2611 |  | WTG Unscheduled Maintenance | 5528 | 65.2611
2361 | 2024-09-29 | 2025 | 2024 | 2024-09-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.73958 | 0.73958 | 0.75764 | 0 | 0.43333 | 0.43333 | after grid resume Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.016667 | O2_25 | 139.1181 |  | WTG Unscheduled Maintenance | 7705 | 139.1181
2362 | 2024-09-29 | 2025 | 2024 | 2024-09-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.73958 | 0.73958 | 0.75903 | 0 | 0.46667 | 0.46667 | after grid resume Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.017949 | O2_01 | 117.7556 |  | WTG Unscheduled Maintenance | 6056 | 117.7556
2363 | 2024-09-29 | 2025 | 2024 | 2024-09-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.73958 | 0.73958 | 0.76042 | 0 | 0.5 | 0.5 | after grid resume Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.019231 | O2_26 | 109.1042 |  | WTG Unscheduled Maintenance | 5237 | 109.1042
2364 | 2024-09-29 | 2025 | 2024 | 2024-09-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.73958 | 0.73958 | 0.74931 | 0 | 0.23333 | 0.23333 | after grid resume Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.0089744 | O2_26 | 50.9153 |  | WTG Unscheduled Maintenance | 5237 | 50.9153
2365 | 2024-09-30 | 2025 | 2024 | 2024-09-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.70625 | 0.70625 | 0.71181 | 0 | 0.13333 | 0.13333 | Check error data than reset and start Wtg. | Close | 0.0051282 | O2_26 | 43.3333 |  | WTG Unscheduled Maintenance | 7800 | 43.3333
2366 | 2024-09-30 | 2025 | 2024 | 2024-09-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.60139 | 0.60139 | 0.60278 | 0 | 0.033333 | 0.033333 | Check error data than reset and start Wtg. | Close | 0.0012821 | O2_05 | 15.2236 |  | WTG Unscheduled Maintenance | 10961 | 15.2236
2367 | 2024-09-30 | 2025 | 2024 | 2024-09-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.97639 | 0.97639 | 0.97778 | 0 | 0.033333 | 0.033333 | Check error data than reset and start Wtg. | Close | 0.0012821 | O2_05 | 15.2236 |  | WTG Unscheduled Maintenance | 10961 | 15.2236
2368 | 2024-09-30 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.0027778 | 0.0027778 | 0.0048611 | 0 | 0.05 | 0.05 | Check error data than reset and start Wtg. | Close | 0.0019231 | O2_07 | 20.5625 |  | WTG Unscheduled Maintenance | 9870 | 20.5625
2369 | 2024-09-30 | 2025 | 2024 | 2024-09-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.55972 | 0.55972 | 0.56181 | 0 | 0.05 | 0.05 | Check error data than reset and start Wtg. | Close | 0.0019231 | O2_07 | 20.5625 |  | WTG Unscheduled Maintenance | 9870 | 20.5625
2370 | 2024-09-30 | 2025 | 2024 | 2024-09-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.88681 | 0.88681 | 0.8875 | 0 | 0.016667 | 0.016667 | auto reseted | Close | 0.00064103 | O2_21 | 7.5382 |  | WTG Unscheduled Maintenance | 10855 | 7.5382
2371 | 2024-09-30 | 2025 | 2024 | 2024-09-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.65972 | 0.65972 | 0.66736 | 0 | 0.18333 | 0.18333 | wtg manual stop for software update work | Close | 0.0070513 | O2_04 | 86.4111 |  | WTG Breakdown Maintenance | 11312 | 86.4111
2372 | 2024-09-30 | 2025 | 2024 | 2024-09-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.45139 | 0.45139 | 0.69792 | 0 | 5.9167 | 5.9167 | wtg manual stop for WTG Maintance work 3rd Day. | Close | 0.22756 | O2_11 | 1873.8576 |  | WTG scheduled Maintenance | 7601 | 1873.8576
2373 | 2024-09-30 | 2025 | 2024 | 2024-09-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Road issue | 0.87292 | 0.87292 | 0.95833 | 0 | 2.05 | 2.05 | approach Road issue | Close | 0.078846 | O2_12 | 769.0063 |  | WTG Unscheduled Maintenance | 9003 | 769.0063
2374 | 2024-09-30 | 2025 | 2024 | 2024-09-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.95833 | 0.95833 | 1899-12-31 | 0 | 1 | 1 | WIP | Close | 0.038462 | O2_12 | 375.125 |  | WTG Unscheduled Maintenance | 9003 | 375.125
2375 | 2024-09-30 | 2025 | 2024 | 2024-09-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.63542 | 0.63542 | 0.63681 | 0 | 0.033333 | 0.033333 | Check error data than reset and start Wtg. | Close | 0.0012821 | O2_06 | 15.3236 |  | WTG Unscheduled Maintenance | 11033 | 15.3236
2376 | 2024-09-30 | 2025 | 2024 | 2024-09-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.88611 | 0.88611 | 0.88681 | 0 | 0.016667 | 0.016667 | auto reseted | Close | 0.00064103 | O2_06 | 7.6618 |  | WTG Unscheduled Maintenance | 11033 | 7.6618
2377 | 2024-09-30 | 2025 | 2024 | 2024-09-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.1875 | 0.1875 | 0.18958 | 0 | 0.05 | 0.05 | Check error data than reset and start Wtg. | Close | 0.0019231 | O2_01 | 16.3 |  | WTG Unscheduled Maintenance | 7824 | 16.3
2378 | 2024-09-30 | 2025 | 2024 | 2024-09-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.2625 | 0.2625 | 0.26389 | 0 | 0.033333 | 0.033333 | auto reseted | Close | 0.0012821 | O2_01 | 10.8667 |  | WTG Unscheduled Maintenance | 7824 | 10.8667
2379 | 2024-10-01 | 2025 | 2024 | 2024-10-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Scheadule WTG PM | 0.39444 | 0.39444 | 0.56111 | 0 | 4 | 4 | wtg manual stop for HT yard HYPM work | Close | 0.15385 | O2-26 | 808.3333 |  | WTG scheduled Maintenance | 4850 | 808.3333
2380 | 2024-10-01 | 2025 | 2024 | 2024-10-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.61458 | 0.61458 | 0.66181 | 0 | 1.1333 | 1.1333 | wtg manual stop for project pending work | Close | 0.04359 | O2-26 | 229.0278 |  | WTG Breakdown Maintenance | 4850 | 229.0278
2381 | 2024-10-01 | 2025 | 2024 | 2024-10-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.23056 | 0.23056 | 0.23125 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | O2-05 | 4.7271 |  | WTG Unscheduled Maintenance | 6807 | 4.7271 | [6 empty] | Auto reset
2382 | 2024-10-01 | 2025 | 2024 | 2024-10-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.71875 | 0.71875 | 0.72708 | 0 | 0.2 | 0.2 | after grid resume Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.0076923 | O2-21 | 47.6333 |  | WTG Unscheduled Maintenance | 5716 | 47.6333 | [6 empty] | Break down
2383 | 2024-10-01 | 2025 | 2024 | 2024-10-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Auto reset | 0.90278 | 0.90278 | 0.90417 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2-21 | 7.9389 |  | WTG Unscheduled Maintenance | 5716 | 7.9389 | [6 empty] | ROW issue
2384 | 2024-10-01 | 2025 | 2024 | 2024-10-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.71875 | 0.71875 | 0.73056 | 0 | 0.28333 | 0.28333 | after grid resume Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.010897 | O2-04 | 85.4014 |  | WTG Unscheduled Maintenance | 7234 | 85.4014 | [6 empty] | Road issue
2385 | 2024-10-01 | 2025 | 2024 | 2024-10-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.44167 | 0.44167 | 0.63542 | 0 | 4.65 | 4.65 | wtg manual stop for WTG Maintance work 3rd Day. | Close | 0.17885 | O2-12 | 922.25 |  | WTG scheduled Maintenance | 4760 | 922.25 | [6 empty] | Major BD
2386 | 2024-10-01 | 2025 | 2024 | 2024-10-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.44583 | 0.44583 | 0.44722 | 0 | 0.033333 | 0.033333 | Check error data than reset and start Wtg. | Close | 0.0012821 | O2-14 | 6.5069 |  | WTG Unscheduled Maintenance | 4685 | 6.5069 | [6 empty] | Ladder issue
2387 | 2024-10-01 | 2025 | 2024 | 2024-10-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0 | 0 | 0.020139 | 0 | 0.48333 | 0.48333 | atten ahen nd check all releted ckt found 24v missing on CCU so check and found SPD on loose so proper fix it then start wtg. | Close | 0.01859 | O2-12 | 95.8611 |  | WTG Unscheduled Maintenance | 4760 | 95.8611 | [6 empty] | Project pending work
2388 | 2024-10-01 | 2025 | 2024 | 2024-10-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.71875 | 0.71875 | 0.72639 | 0 | 0.18333 | 0.18333 | after grid resume Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.0070513 | O2-21 | 43.6639 |  | WTG Unscheduled Maintenance | 5716 | 43.6639 | [6 empty] | Schedule WTG PM
2389 | 2024-10-01 | 2025 | 2024 | 2024-10-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 4093 | Rel. air hum. tower base inside too high (in operation) | Break down | 0.30486 | 0.30486 | 0.3125 | 0 | 0.18333 | 0.18333 | Check error data than reset and start Wtg. | Close | 0.0070513 | O2-06 | 52.9528 |  | WTG Unscheduled Maintenance | 6932 | 52.9528 | [6 empty] | WTR
2390 | 2024-10-01 | 2025 | 2024 | 2024-10-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.71875 | 0.71875 | 0.73333 | 0 | 0.35 | 0.35 | after grid resume Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.013462 | O2-06 | 101.0917 |  | WTG Unscheduled Maintenance | 6932 | 101.0917 | [6 empty] | Connectivity issue
2391 | 2024-10-01 | 2025 | 2024 | 2024-10-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.71875 | 0.71875 | 0.72917 | 0 | 0.25 | 0.25 | after grid resume Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.0096154 | O2-20 | 51.5208 |  | WTG Unscheduled Maintenance | 4946 | 51.5208 | [6 empty] | Others
2392 | 2024-10-01 | 2025 | 2024 | 2024-10-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule USS PM | 0.59375 | 0.59375 | 0.69444 | 0 | 2.4167 | 2.4167 | wtg manual stop for HT yard HYPM work | Close | 0.092949 | O2-20 | 498.0347 |  | WTG scheduled Maintenance | 4946 | 498.0347 | [6 empty] | Environment
2393 | 2024-10-02 | 2025 | 2024 | 2024-10-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.50833 | 0.50833 | 0.50903 | 0 | 0.016667 | 0.016667 | Check error data than reset and start Wtg. | Close | 0.00064103 | O2_05 | 3.6076 |  | WTG Unscheduled Maintenance | 5195 | 3.6076 | [6 empty] | Blade cleaning work
2394 | 2024-10-02 | 2025 | 2024 | 2024-10-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.85833 | 0.85833 | 0.85972 | 0 | 0.033333 | 0.033333 | Check error data than reset and start Wtg. | Close | 0.0012821 | O2_05 | 7.2153 |  | WTG Unscheduled Maintenance | 5195 | 7.2153 | [6 empty] | Load Shedding
2395 | 2024-10-02 | 2025 | 2024 | 2024-10-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.50694 | 0.50694 | 0.50833 | 0 | 0.033333 | 0.033333 | Check error data than reset and start Wtg. | Close | 0.0012821 | O2_09 | 5.9653 |  | WTG Unscheduled Maintenance | 4295 | 5.9653 | [6 empty] | Customer
2396 | 2024-10-02 | 2025 | 2024 | 2024-10-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.042361 | 0.042361 | 0.04375 | 0 | 0.033333 | 0.033333 | Check error data than reset and start Wtg. | Close | 0.0012821 | O2_07 | 7.4264 |  | WTG Unscheduled Maintenance | 5347 | 7.4264
2397 | 2024-10-02 | 2025 | 2024 | 2024-10-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.44306 | 0.44306 | 0.60347 | 0 | 3.85 | 3.85 | wtg manual stop for WTG Maintance work 3rd Day. | Close | 0.14808 | O2_14 | 627.7104 |  | WTG scheduled Maintenance | 3913 | 627.7104
2398 | 2024-10-02 | 2025 | 2024 | 2024-10-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 4093 | Rel. air hum. tower base inside too high (in operation) | Break down | 0.30486 | 0.30486 | 0.3125 | 0 | 0.18333 | 0.18333 | Check error data than reset and start Wtg. | Close | 0.0070513 | O2_06 | 49.3014 |  | WTG Unscheduled Maintenance | 6454 | 49.3014
2399 | 2024-10-02 | 2025 | 2024 | 2024-10-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.475 | 0.475 | 0.57083 | 0 | 2.3 | 2.3 | wtg manual stop for project pending work and blade 2 chopper resistor replacement work. | Close | 0.088462 | O2_06 | 618.5083 |  | WTG Breakdown Maintenance | 6454 | 618.5083
2400 | 2024-10-02 | 2025 | 2024 | 2024-10-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.50903 | 0.50903 | 0.51319 | 0 | 0.1 | 0.1 | Check error data than reset and start Wtg. | Close | 0.0038462 | O2_01 | 18.675 |  | WTG Unscheduled Maintenance | 4482 | 18.675
2401 | 2024-10-03 | 2025 | 2024 | 2024-10-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.42292 | 0.42292 | 0.66528 | 0 | 5.8167 | 5.8167 | wtg manual stop for WTG Maintance work 3rd Day.Check ckt Error related than blade axis 2 chhoper resister faulty so replace with new then reset and start turbine(Activity during with maintenance) | Close | 0.22372 | O2_26 | 2577.5104 |  | WTG scheduled Maintenance | 10635 | 2577.5104
2402 | 2024-10-03 | 2025 | 2024 | 2024-10-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.15833 | 0.15833 | 0.15903 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | O2_05 | 13.1903 |  | WTG Unscheduled Maintenance | 18994 | 13.1903
2403 | 2024-10-03 | 2025 | 2024 | 2024-10-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.46806 | 0.46806 | 0.52431 | 0 | 1.35 | 1.35 | wtg manual stop for project pending work | Close | 0.051923 | O2_21 | 795.2063 |  | WTG Breakdown Maintenance | 14137 | 795.2063
2404 | 2024-10-03 | 2025 | 2024 | 2024-10-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.56944 | 0.56944 | 0.57083 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_21 | 19.6347 |  | WTG Unscheduled Maintenance | 14137 | 19.6347
2405 | 2024-10-03 | 2025 | 2024 | 2024-10-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.5 | 0.5 | 0.75903 | 0 | 6.2167 | 6.2167 | wtg manual stop by project team tramformar WTR work. | Close | 0.2391 | O2_15 | 2934.2667 |  | WTG Breakdown Maintenance | 11328 | 2934.2667
2406 | 2024-10-03 | 2025 | 2024 | 2024-10-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.23958 | 0.23958 | 0.24583 | 0 | 0.15 | 0.15 | after grid resume Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.0057692 | O2_21 | 88.3562 |  | WTG Unscheduled Maintenance | 14137 | 88.3562
2407 | 2024-10-03 | 2025 | 2024 | 2024-10-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.50625 | 0.50625 | 0.50764 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_06 | 22.8014 |  | WTG Unscheduled Maintenance | 16417 | 22.8014
2408 | 2024-10-03 | 2025 | 2024 | 2024-10-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.53194 | 0.53194 | 0.53403 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_06 | 34.2021 |  | WTG Unscheduled Maintenance | 16417 | 34.2021
2409 | 2024-10-03 | 2025 | 2024 | 2024-10-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.23958 | 0.23958 | 0.24375 | 0 | 0.1 | 0.1 | after grid resume Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.0038462 | O2_06 | 68.4042 |  | WTG Unscheduled Maintenance | 16417 | 68.4042
2410 | 2024-10-03 | 2025 | 2024 | 2024-10-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.23958 | 0.23958 | 0.24375 | 0 | 0.1 | 0.1 | after grid resume Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.0038462 | O2_20 | 54.7833 |  | WTG Unscheduled Maintenance | 13148 | 54.7833
2411 | 2024-10-03 | 2025 | 2024 | 2024-10-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 7002 | Task runtime failure 5ms | Break down | 0.60417 | 0.60417 | 0.61528 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2_25 | 185.3778 |  | WTG Unscheduled Maintenance | 16684 | 185.3778
2412 | 2024-10-03 | 2025 | 2024 | 2024-10-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.47917 | 0.47917 | 0.62847 | 0 | 3.5833 | 3.5833 | Checke Error related data scada so found NO RM bringing limit switches feedback not received so Attend and check circuit so found silica gel stuck in contactor KF012 connection so remove it as well as collect silica from CB then reset and start turbine. | Close | 0.13782 | O2_01 | 1951.8715 |  | WTG Unscheduled Maintenance | 13073 | 1951.8715
2413 | 2024-10-04 | 2025 | 2024 | 2024-10-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.22222 | 0.22222 | 0.22361 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_21 | 19.5278 |  | WTG Unscheduled Maintenance | 14060 | 19.5278
2414 | 2024-10-04 | 2025 | 2024 | 2024-10-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.47917 | 0.47917 | 0.54028 | 0 | 1.4667 | 1.4667 | wtg manual stop for project pending work. | Close | 0.05641 | O2_21 | 859.2222 |  | WTG Breakdown Maintenance | 14060 | 859.2222
2415 | 2024-10-04 | 2025 | 2024 | 2024-10-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.55903 | 0.55903 | 0.56111 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_21 | 29.2917 |  | WTG Unscheduled Maintenance | 14060 | 29.2917
2416 | 2024-10-04 | 2025 | 2024 | 2024-10-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.13611 | 0.13611 | 0.1375 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_14 | 22.8167 |  | WTG Unscheduled Maintenance | 16428 | 22.8167
2417 | 2024-10-04 | 2025 | 2024 | 2024-10-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.68125 | 0.68125 | 0.79861 | 0 | 2.8167 | 2.8167 | wtg manual stop for repeated error and wtg inspection work. | Close | 0.10833 | O2_11 | 1721.8049 |  | WTG Breakdown Maintenance | 14671 | 1721.8049
2418 | 2024-10-04 | 2025 | 2024 | 2024-10-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.069444 | 0.069444 | 0.070833 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_06 | 24.0347 |  | WTG Unscheduled Maintenance | 17305 | 24.0347
2419 | 2024-10-04 | 2025 | 2024 | 2024-10-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.48819 | 0.48819 | 0.52083 | 0 | 0.78333 | 0.78333 | wtg manual stop for project pending work. | Close | 0.030128 | O2_06 | 564.816 |  | WTG Breakdown Maintenance | 17305 | 564.816
2420 | 2024-10-04 | 2025 | 2024 | 2024-10-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.42778 | 0.42778 | 0.70556 | 0 | 6.6667 | 6.6667 | wtg manual stop for WTG Maintanance work 3rd Day | Close | 0.25641 | O2_24 | 4590 |  | WTG scheduled Maintenance | 16524 | 4590
2421 | 2024-10-04 | 2025 | 2024 | 2024-10-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.33472 | 0.33472 | 0.33542 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | O2_01 | 12.3042 |  | WTG Unscheduled Maintenance | 17718 | 12.3042
2422 | 2024-10-04 | 2025 | 2024 | 2024-10-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.55347 | 0.55347 | 0.55486 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_01 | 24.6083 |  | WTG Unscheduled Maintenance | 17718 | 24.6083
2423 | 2024-10-04 | 2025 | 2024 | 2024-10-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.775 | 0.775 | 0.77639 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_01 | 24.6083 |  | WTG Unscheduled Maintenance | 17718 | 24.6083
2424 | 2024-10-04 | 2025 | 2024 | 2024-10-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.78194 | 0.78194 | 0.78333 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_01 | 24.6083 |  | WTG Unscheduled Maintenance | 17718 | 24.6083
2425 | 2024-10-05 | 2025 | 2024 | 2024-10-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.78194 | 0.78194 | 0.78333 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_01 | 14.2278 |  | WTG Unscheduled Maintenance | 10244 | 14.2278
2426 | 2024-10-05 | 2025 | 2024 | 2024-10-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.93125 | 0.93125 | 0.93264 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_07 | 16.0056 |  | WTG Unscheduled Maintenance | 11524 | 16.0056
2427 | 2024-10-05 | 2025 | 2024 | 2024-10-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.49167 | 0.49167 | 0.49306 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_02 | 18.6903 |  | WTG Unscheduled Maintenance | 13457 | 18.6903
2428 | 2024-10-05 | 2025 | 2024 | 2024-10-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.0048611 | 0.0048611 | 0.0069444 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_21 | 15.7729 |  | WTG Unscheduled Maintenance | 7571 | 15.7729
2429 | 2024-10-05 | 2025 | 2024 | 2024-10-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.044444 | 0.044444 | 0.046528 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_21 | 15.7729 |  | WTG Unscheduled Maintenance | 7571 | 15.7729
2430 | 2024-10-05 | 2025 | 2024 | 2024-10-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 5550 | Low hydraulic oil level | Break down | 0.16875 | 0.16875 | 0.37708 | 0 | 5 | 5 | Attend and found HP Unit top side minor leakage so recorrect it and oil top up than reset and start WTG. | Close | 0.19231 | O2_03 | 1748.75 |  | WTG Unscheduled Maintenance | 8394 | 1748.75
2431 | 2024-10-05 | 2025 | 2024 | 2024-10-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule USS PM | 0.50278 | 0.50278 | 0.62361 | 0 | 2.9 | 2.9 | wtg manual stop for HT yard HYPM work | Close | 0.11154 | O2_12 | 860.3333 |  | WTG scheduled Maintenance | 7120 | 860.3333
2432 | 2024-10-05 | 2025 | 2024 | 2024-10-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.48889 | 0.48889 | 0.49097 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_11 | 14.5729 |  | WTG Unscheduled Maintenance | 6995 | 14.5729
2433 | 2024-10-05 | 2025 | 2024 | 2024-10-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule USS PM | 0.35069 | 0.35069 | 0.49444 | 0 | 3.45 | 3.45 | wtg manual stop for HT yard HYPM work | Close | 0.13269 | O2_12 | 1023.5 |  | WTG scheduled Maintenance | 7120 | 1023.5
2434 | 2024-10-05 | 2025 | 2024 | 2024-10-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 4093 | Rel. air hum. tower base inside too high (in operation) | Break down | 0.34167 | 0.34167 | 0.34583 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2_06 | 49.4042 |  | WTG Unscheduled Maintenance | 11857 | 49.4042
2435 | 2024-10-06 | 2025 | 2024 | 2024-10-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.55417 | 0.55417 | 0.55556 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_05 | 6.2028 |  | WTG Unscheduled Maintenance | 4466 | 6.2028
2436 | 2024-10-06 | 2025 | 2024 | 2024-10-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.17222 | 0.17222 | 0.17431 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_07 | 6.9583 |  | WTG Unscheduled Maintenance | 3340 | 6.9583
2437 | 2024-10-06 | 2025 | 2024 | 2024-10-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3060 | Conv. emerg.off type A | Break down | 0.69792 | 0.69792 | 0.75208 | 0 | 1.3 | 1.3 | VCB Tripped so check it than no any abnormality than Charge Vcb. | Close | 0.05 | O2_07 | 180.9167 |  | WTG Unscheduled Maintenance | 3340 | 180.9167
2438 | 2024-10-06 | 2025 | 2024 | 2024-10-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.56181 | 0.56181 | 0.56319 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_02 | 6.6639 |  | WTG Unscheduled Maintenance | 4798 | 6.6639
2439 | 2024-10-06 | 2025 | 2024 | 2024-10-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.76944 | 0.76944 | 0.77083 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_21 | 6.2556 |  | WTG Unscheduled Maintenance | 4504 | 6.2556
2442 | 2024-10-06 | 2025 | 2024 | 2024-10-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.49653 | 0.49653 | 0.49931 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & run the WTG. | Close | 0.0025641 | O2_21 | 12.5111 |  | WTG Unscheduled Maintenance | 4504 | 12.5111
2443 | 2024-10-06 | 2025 | 2024 | 2024-10-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down | 0.65694 | 0.65694 | 0.65764 | 0 | 0.016667 | 0.016667 | Checked related error data log then reset & run the WTG. | Close | 0.00064103 | O2_21 | 3.1278 |  | WTG Unscheduled Maintenance | 4504 | 3.1278
2444 | 2024-10-06 | 2025 | 2024 | 2024-10-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.97083 | 0.97083 | 0.97222 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_06 | 6.8861 |  | WTG Unscheduled Maintenance | 4958 | 6.8861
2445 | 2024-10-06 | 2025 | 2024 | 2024-10-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.25556 | 0.25556 | 0.25694 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_06 | 6.8861 |  | WTG Unscheduled Maintenance | 4958 | 6.8861
2446 | 2024-10-06 | 2025 | 2024 | 2024-10-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.22917 | 0.22917 | 0.24236 | 0 | 0.31667 | 0.31667 | Checked related error data log then reset & run the WTG. | Close | 0.012179 | O2_25 | 61.8424 |  | WTG Unscheduled Maintenance | 4687 | 61.8424
2447 | 2024-10-06 | 2025 | 2024 | 2024-10-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.12431 | 0.12431 | 0.125 | 0 | 0.016667 | 0.016667 | Checked related error data log then reset & run the WTG. | Close | 0.00064103 | O2_01 | 2.8931 |  | WTG Unscheduled Maintenance | 4166 | 2.8931
2448 | 2024-10-06 | 2025 | 2024 | 2024-10-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.75972 | 0.75972 | 0.76111 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_01 | 5.7861 |  | WTG Unscheduled Maintenance | 4166 | 5.7861
2449 | 2024-10-07 | 2025 | 2024 | 2024-10-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 1630 | Disc filter adaption implausible | Break down | 0.45347 | 0.45347 | 0.45694 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_26 | 52.6076 |  | WTG Unscheduled Maintenance | 15151 | 52.6076
2450 | 2024-10-07 | 2025 | 2024 | 2024-10-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 1630 | Disc filter adaption implausible | Break down | 0.51806 | 0.51806 | 0.52222 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2_26 | 63.1292 |  | WTG Unscheduled Maintenance | 15151 | 63.1292
2451 | 2024-10-07 | 2025 | 2024 | 2024-10-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 1630 | Disc filter adaption implausible | Break down | 0.5875 | 0.5875 | 0.59375 | 0 | 0.15 | 0.15 | Checked related error data log then reset & run the WTG. | Close | 0.0057692 | O2_26 | 94.6937 |  | WTG Unscheduled Maintenance | 15151 | 94.6937
2452 | 2024-10-07 | 2025 | 2024 | 2024-10-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 1630 | Disc filter adaption implausible | Break down | 0.70417 | 0.70417 | 0.80208 | 0 | 2.35 | 2.35 | Attend for repeated error check rotor disc sensor gap is ok 2.5mm so check sensor cap connection found no any abnormal condition so minor sensor gap set than reset and start WTG now under Obesravation | Close | 0.090385 | O2_26 | 1483.5354 |  | WTG Unscheduled Maintenance | 15151 | 1483.5354
2453 | 2024-10-07 | 2025 | 2024 | 2024-10-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.48889 | 0.48889 | 0.49097 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_05 | 34.2771 |  | WTG Unscheduled Maintenance | 16453 | 34.2771
2454 | 2024-10-07 | 2025 | 2024 | 2024-10-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.63889 | 0.63889 | 0.64028 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_05 | 22.8514 |  | WTG Unscheduled Maintenance | 16453 | 22.8514
2455 | 2024-10-07 | 2025 | 2024 | 2024-10-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.38958 | 0.38958 | 0.39097 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_07 | 18.3153 |  | WTG Unscheduled Maintenance | 13187 | 18.3153
2456 | 2024-10-07 | 2025 | 2024 | 2024-10-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.80208 | 0.80208 | 0.80417 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_21 | 23.1333 |  | WTG Unscheduled Maintenance | 11104 | 23.1333
2457 | 2024-10-07 | 2025 | 2024 | 2024-10-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule USS PM | 0.35278 | 0.35278 | 0.4875 | 0 | 3.2333 | 3.2333 | wtg manual stop for HT yard HYPM work | Close | 0.12436 | O2_15 | 1626.3667 |  | WTG scheduled Maintenance | 12072 | 1626.3667
2458 | 2024-10-07 | 2025 | 2024 | 2024-10-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.30764 | 0.30764 | 0.30903 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_14 | 18.0708 |  | WTG Unscheduled Maintenance | 13011 | 18.0708
2459 | 2024-10-07 | 2025 | 2024 | 2024-10-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.575 | 0.575 | 0.57639 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_14 | 18.0708 |  | WTG Unscheduled Maintenance | 13011 | 18.0708
2460 | 2024-10-07 | 2025 | 2024 | 2024-10-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule USS PM | 0.50278 | 0.50278 | 0.61528 | 0 | 2.7 | 2.7 | wtg manual stop for HT yard HYPM work | Close | 0.10385 | O2_10 | 1280.25 |  | WTG scheduled Maintenance | 11380 | 1280.25
2461 | 2024-10-07 | 2025 | 2024 | 2024-10-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.57083 | 0.57083 | 0.59306 | 0 | 0.53333 | 0.53333 | wtg manual stop for WTG Maintanance work 3rd Day but F#2 S/D for project pending work so WTG maintenance plan cancel and start Wtg. | Close | 0.020513 | O2_21 | 246.7556 |  | WTG scheduled Maintenance | 11104 | 246.7556
2462 | 2024-10-07 | 2025 | 2024 | 2024-10-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.56389 | 0.56389 | 0.57014 | 0 | 0.15 | 0.15 | Checked related error data log then reset & run the WTG. | Close | 0.0057692 | O2_06 | 58.8562 |  | WTG Unscheduled Maintenance | 9417 | 58.8562
2463 | 2024-10-08 | 2025 | 2024 | 2024-10-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 1630 | Disc filter adaption implausible | Break down | 0.10278 | 0.10278 | 0.10833 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & run the WTG. | Close | 0.0051282 | O2_26 | 39.75 |  | WTG Unscheduled Maintenance | 7155 | 39.75
2464 | 2024-10-08 | 2025 | 2024 | 2024-10-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 1630 | Disc filter adaption implausible | Break down | 0.15069 | 0.15069 | 0.15139 | 0 | 0.016667 | 0.016667 | Checked related error data log then reset & run the WTG. | Close | 0.00064103 | O2_26 | 4.9687 |  | WTG Unscheduled Maintenance | 7155 | 4.9687
2465 | 2024-10-08 | 2025 | 2024 | 2024-10-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.16042 | 0.16042 | 0.16111 | 0 | 0.016667 | 0.016667 | Checked related error data log then reset & run the WTG. | Close | 0.00064103 | O2_05 | 6.1437 |  | WTG Unscheduled Maintenance | 8847 | 6.1437
2466 | 2024-10-08 | 2025 | 2024 | 2024-10-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.87222 | 0.87222 | 0.87431 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_05 | 18.4312 |  | WTG Unscheduled Maintenance | 8847 | 18.4312
2467 | 2024-10-08 | 2025 | 2024 | 2024-10-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.27778 | 0.27778 | 0.27917 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_07 | 10.2444 |  | WTG Unscheduled Maintenance | 7376 | 10.2444
2468 | 2024-10-08 | 2025 | 2024 | 2024-10-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.67986 | 0.67986 | 0.68125 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_03 | 10.6903 |  | WTG Unscheduled Maintenance | 7697 | 10.6903
2469 | 2024-10-08 | 2025 | 2024 | 2024-10-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.68333 | 0.68333 | 0.68403 | 0 | 0.016667 | 0.016667 | Checked related error data log then reset & run the WTG. | Close | 0.00064103 | O2_03 | 5.3451 |  | WTG Unscheduled Maintenance | 7697 | 5.3451
2470 | 2024-10-08 | 2025 | 2024 | 2024-10-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.10417 | 0.10417 | 0.10903 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & run the WTG. | Close | 0.0044872 | O2_15 | 38.7139 |  | WTG Unscheduled Maintenance | 7964 | 38.7139
2471 | 2024-10-08 | 2025 | 2024 | 2024-10-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.040972 | 0.040972 | 0.04375 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & run the WTG. | Close | 0.0025641 | O2_14 | 19.4722 |  | WTG Unscheduled Maintenance | 7010 | 19.4722
2472 | 2024-10-08 | 2025 | 2024 | 2024-10-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.26111 | 0.26111 | 0.3125 | 0 | 1.2333 | 1.2333 | Checked related error data log then check all perameter than reset & run the WTG. | Close | 0.047436 | O2_14 | 360.2361 |  | WTG Unscheduled Maintenance | 7010 | 360.2361
2473 | 2024-10-08 | 2025 | 2024 | 2024-10-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.34306 | 0.34306 | 0.34444 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_14 | 9.7361 |  | WTG Unscheduled Maintenance | 7010 | 9.7361
2474 | 2024-10-08 | 2025 | 2024 | 2024-10-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 88 | Outs.temp. nacelle implaus. | Break down | 0.6375 | 0.6375 | 0.65278 | 0 | 0.36667 | 0.36667 | Checked related error data log then reset & run the WTG. | Close | 0.014103 | O2_12 | 122.1458 |  | WTG Unscheduled Maintenance | 7995 | 122.1458
2475 | 2024-10-08 | 2025 | 2024 | 2024-10-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 88 | Outs.temp. nacelle implaus. | Break down | 0.66111 | 0.66111 | 0.69792 | 0 | 0.88333 | 0.88333 | Attend and check error related ckt than found out door sensor connection loose so tight it than reset and start WTG. | Close | 0.033974 | O2_12 | 294.2604 |  | WTG Unscheduled Maintenance | 7995 | 294.2604
2476 | 2024-10-08 | 2025 | 2024 | 2024-10-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.43056 | 0.43056 | 0.71111 | 0 | 6.7333 | 6.7333 | wtg manual stop for WTG Maintanance work 3rd Day. | Close | 0.25897 | O2_21 | 2993.5278 |  | WTG scheduled Maintenance | 10670 | 2993.5278
2477 | 2024-10-08 | 2025 | 2024 | 2024-10-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.27778 | 0.27778 | 0.29375 | 0 | 0.38333 | 0.38333 | Checked related error data log then check all perameter than reset & run the WTG. | Close | 0.014744 | O2_06 | 178.4097 |  | WTG Unscheduled Maintenance | 11170 | 178.4097
2478 | 2024-10-08 | 2025 | 2024 | 2024-10-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.25069 | 0.25069 | 0.25139 | 0 | 0.016667 | 0.016667 | Checked related error data log then reset & run the WTG. | Close | 0.00064103 | O2_06 | 7.7569 |  | WTG Unscheduled Maintenance | 11170 | 7.7569
2479 | 2024-10-08 | 2025 | 2024 | 2024-10-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 2687 | Max. slip ring cell temp. | Break down | 0.62708 | 0.62708 | 0.67361 | 0 | 1.1167 | 1.1167 | Checked related error data log then check all perameter than reset & run the WTG. | Close | 0.042949 | O2_20 | 306.8042 |  | WTG Unscheduled Maintenance | 6594 | 306.8042
2480 | 2024-10-08 | 2025 | 2024 | 2024-10-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.071528 | 0.071528 | 0.072917 | 0 | 0.033333 | 0.033333 | Checked related error data log then check all perameter than reset & run the WTG. | Close | 0.0012821 | O2_01 | 12.4236 |  | WTG Unscheduled Maintenance | 8945 | 12.4236
2481 | 2024-10-08 | 2025 | 2024 | 2024-10-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.14306 | 0.14306 | 0.14444 | 0 | 0.033333 | 0.033333 | Checked related error data log then check all perameter than reset & run the WTG. | Close | 0.0012821 | O2_01 | 12.4236 |  | WTG Unscheduled Maintenance | 8945 | 12.4236
2482 | 2024-10-08 | 2025 | 2024 | 2024-10-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.27986 | 0.27986 | 0.3125 | 0 | 0.78333 | 0.78333 | Checked related error data log then check all perameter than reset & run the WTG. | Close | 0.030128 | O2_01 | 291.9549 |  | WTG Unscheduled Maintenance | 8945 | 291.9549
2483 | 2024-10-09 | 2025 | 2024 | 2024-10-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.038889 | 0.038889 | 0.040278 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_05 | 8.9181 |  | WTG Unscheduled Maintenance | 6421 | 8.9181
2484 | 2024-10-09 | 2025 | 2024 | 2024-10-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.10069 | 0.10069 | 0.10208 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_05 | 8.9181 |  | WTG Unscheduled Maintenance | 6421 | 8.9181
2485 | 2024-10-09 | 2025 | 2024 | 2024-10-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.29653 | 0.29653 | 0.29722 | 0 | 0.016667 | 0.016667 | Checked related error data log then reset & run the WTG. | Close | 0.00064103 | O2_05 | 4.459 |  | WTG Unscheduled Maintenance | 6421 | 4.459
2486 | 2024-10-09 | 2025 | 2024 | 2024-10-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.68819 | 0.68819 | 0.68889 | 0 | 0.016667 | 0.016667 | Checked related error data log then reset & run the WTG. | Close | 0.00064103 | O2_05 | 4.459 |  | WTG Unscheduled Maintenance | 6421 | 4.459
2487 | 2024-10-09 | 2025 | 2024 | 2024-10-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.25069 | 0.25069 | 0.25417 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_09 | 20.7847 |  | WTG Unscheduled Maintenance | 5986 | 20.7847
2488 | 2024-10-09 | 2025 | 2024 | 2024-10-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 642 | Sim.angle E enc. <> act.angle 2 | Break down | 0.94514 | 0.94514 | 0.94653 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_04 | 7.3208 |  | WTG Unscheduled Maintenance | 5271 | 7.3208
2489 | 2024-10-09 | 2025 | 2024 | 2024-10-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.94722 | 0.94722 | 0.96736 | 0 | 0.48333 | 0.48333 | Checked related error data log then check all perameter than reset & run the WTG. | Close | 0.01859 | O2_04 | 106.1521 |  | WTG Unscheduled Maintenance | 5271 | 106.1521
2490 | 2024-10-09 | 2025 | 2024 | 2024-10-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 3065 | Conv. emerg.off type F | Auto reset | 0.63542 | 0.63542 | 0.63681 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2_03 | 9.8444 |  | WTG Unscheduled Maintenance | 7088 | 9.8444
2491 | 2024-10-09 | 2025 | 2024 | 2024-10-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 3065 | Conv. emerg.off type F | Auto reset | 0.67153 | 0.67153 | 0.67292 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2_03 | 9.8444 |  | WTG Unscheduled Maintenance | 7088 | 9.8444
2492 | 2024-10-09 | 2025 | 2024 | 2024-10-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 3065 | Conv. emerg.off type F | Auto reset | 0.67431 | 0.67431 | 0.67639 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2_03 | 14.7667 |  | WTG Unscheduled Maintenance | 7088 | 14.7667
2493 | 2024-10-09 | 2025 | 2024 | 2024-10-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 3065 | Conv. emerg.off type F | Auto reset | 0.67708 | 0.67708 | 0.67847 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2_03 | 9.8444 |  | WTG Unscheduled Maintenance | 7088 | 9.8444
2494 | 2024-10-09 | 2025 | 2024 | 2024-10-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 3065 | Conv. emerg.off type F | Auto reset | 0.6875 | 0.6875 | 0.68889 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2_03 | 9.8444 |  | WTG Unscheduled Maintenance | 7088 | 9.8444
2495 | 2024-10-09 | 2025 | 2024 | 2024-10-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 3065 | Conv. emerg.off type F | Auto reset | 0.69028 | 0.69028 | 0.69167 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2_03 | 9.8444 |  | WTG Unscheduled Maintenance | 7088 | 9.8444
2496 | 2024-10-09 | 2025 | 2024 | 2024-10-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 3065 | Conv. emerg.off type F | Road issue | 0.69306 | 0.69306 | 0.83056 | 0 | 3.3 | 3.3 | WTG road not approchablse so waiting for the Tector | Close | 0.12692 | O2_03 | 974.6 |  | WTG Unscheduled Maintenance | 7088 | 974.6
2497 | 2024-10-09 | 2025 | 2024 | 2024-10-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 3065 | Conv. emerg.off type F | Break down | 0.83056 | 0.83056 | 0.85139 | 0 | 0.5 | 0.5 | Attend and Check encoder connection in CCU and converter TB but nothing found abnormal so check encoder connector and shielding so encoder connector found minor loose so tight it then reset and start Turbine. | Close | 0.019231 | O2_03 | 147.6667 |  | WTG Unscheduled Maintenance | 7088 | 147.6667
2498 | 2024-10-09 | 2025 | 2024 | 2024-10-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.25486 | 0.25486 | 0.25625 | 0 | 0.033333 | 0.033333 | Checked related error data log then check all perameter than reset & run the WTG. | Close | 0.0012821 | O2_14 | 7.5292 |  | WTG Unscheduled Maintenance | 5421 | 7.5292
2499 | 2024-10-09 | 2025 | 2024 | 2024-10-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.46736 | 0.46736 | 0.46806 | 0 | 0.016667 | 0.016667 | Checked related error data log then check all perameter than reset & run the WTG. | Close | 0.00064103 | O2_14 | 3.7646 |  | WTG Unscheduled Maintenance | 5421 | 3.7646
2500 | 2024-10-09 | 2025 | 2024 | 2024-10-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.70347 | 0.70347 | 0.75625 | 0 | 1.2667 | 1.2667 | WTG stop for inspection and converter CAN connection & Software inspection work | Close | 0.048718 | O2_11 | 323.4222 |  | WTG Breakdown Maintenance | 6128 | 323.4222
2501 | 2024-10-09 | 2025 | 2024 | 2024-10-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.41667 | 0.41667 | 0.70486 | 0 | 6.9167 | 6.9167 | wtg manual stop for WTG Maintanance work 3rd Day. | Close | 0.26603 | O2_06 | 992.5417 |  | WTG scheduled Maintenance | 3444 | 992.5417
2502 | 2024-10-09 | 2025 | 2024 | 2024-10-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.15833 | 0.15833 | 0.16042 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2_06 | 7.175 |  | WTG Unscheduled Maintenance | 3444 | 7.175
2503 | 2024-10-09 | 2025 | 2024 | 2024-10-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.16389 | 0.16389 | 0.16528 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_01 | 10.3583 |  | WTG Unscheduled Maintenance | 7458 | 10.3583
2504 | 2024-10-10 | 2025 | 2024 | 2024-10-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.97431 | 0.97431 | 0.97917 | 0 | 0.11667 | 0.11667 | Checked related error data log then check all perameter than reset & run the WTG. | Close | 0.0044872 | O2_07 | 49.8507 |  | WTG Unscheduled Maintenance | 10255 | 49.8507
2505 | 2024-10-10 | 2025 | 2024 | 2024-10-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.43542 | 0.43542 | 0.70139 | 0 | 6.3833 | 6.3833 | wtg manual stop for WTG Maintanance work 3rd Day. | Close | 0.24551 | O2_21 | 5284.0701 |  | WTG scheduled Maintenance | 19867 | 5284.0701
2506 | 2024-10-10 | 2025 | 2024 | 2024-10-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Break down | 0.23333 | 0.23333 | 0.45903 | 0 | 5.4167 | 5.4167 | Attend and check error related ckt found battery box 1 input missing so attend check error related ckt than found RA007 1.7 ohm flate Resister faulty so arrange spare and replace it than reset and start turbine. | Close | 0.20833 | O2_04 | 2704.2708 |  | WTG Unscheduled Maintenance | 11982 | 2704.2708
2507 | 2024-10-10 | 2025 | 2024 | 2024-10-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.31319 | 0.31319 | 0.32153 | 0 | 0.2 | 0.2 | Checked related error data log then check all perameter than reset & run the WTG. | Close | 0.0076923 | O2_26 | 108.725 |  | WTG Unscheduled Maintenance | 13047 | 108.725
2508 | 2024-10-10 | 2025 | 2024 | 2024-10-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.56875 | 0.56875 | 0.58958 | 0 | 0.5 | 0.5 | wtg manual stop for project pending work. | Close | 0.019231 | O2_11 | 264.7708 |  | WTG Breakdown Maintenance | 12709 | 264.7708
2509 | 2024-10-10 | 2025 | 2024 | 2024-10-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.47847 | 0.47847 | 0.48264 | 0 | 0.1 | 0.1 | Checked related error data log then check all perameter than reset & run the WTG. | Close | 0.0038462 | O2_01 | 69.0125 |  | WTG Unscheduled Maintenance | 16563 | 69.0125
2510 | 2024-10-10 | 2025 | 2024 | 2024-10-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.51111 | 0.51111 | 0.525 | 0 | 0.33333 | 0.33333 | Checked related error data log then reset & run the WTG. | Close | 0.012821 | O2_01 | 230.0417 |  | WTG Unscheduled Maintenance | 16563 | 230.0417
2511 | 2024-10-10 | 2025 | 2024 | 2024-10-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down | 0.57153 | 0.57153 | 0.57431 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & run the WTG. | Close | 0.0025641 | O2_01 | 46.0083 |  | WTG Unscheduled Maintenance | 16563 | 46.0083
2512 | 2024-10-11 | 2025 | 2024 | 2024-10-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.64792 | 0.64792 | 0.75 | 0 | 2.45 | 2.45 | check error related ckt so found K24 Relay malfunctionso K24 Realy interchange withK30 FOR Observation purpose also check conv repeated error related insection then reset and start wtg | Close | 0.094231 | O2_09 | 2496.2437 |  | WTG Unscheduled Maintenance | 24453 | 2496.2437
2513 | 2024-10-11 | 2025 | 2024 | 2024-10-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.44306 | 0.44306 | 0.45833 | 0 | 0.36667 | 0.36667 | Wtg stof for Converter Error Rectification work | Close | 0.014103 | O2_07 | 337.6389 |  | WTG Breakdown Maintenance | 22100 | 337.6389
2514 | 2024-10-11 | 2025 | 2024 | 2024-10-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.68611 | 0.68611 | 0.73056 | 0 | 1.0667 | 1.0667 | Checked related error data log then reset & run the WTG. | Close | 0.041026 | O2_07 | 982.2222 |  | WTG Unscheduled Maintenance | 22100 | 982.2222
2515 | 2024-10-11 | 2025 | 2024 | 2024-10-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.80764 | 0.80764 | 0.80903 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_07 | 30.6944 |  | WTG Unscheduled Maintenance | 22100 | 30.6944
2516 | 2024-10-11 | 2025 | 2024 | 2024-10-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.39653 | 0.39653 | 0.40139 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & run the WTG. | Close | 0.0044872 | O2_26 | 108.7674 |  | WTG Unscheduled Maintenance | 22375 | 108.7674
2517 | 2024-10-11 | 2025 | 2024 | 2024-10-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.53056 | 0.53056 | 0.63472 | 0 | 2.5 | 2.5 | Wtg stof for Converter Error Rectification work | Close | 0.096154 | O2_14 | 2299.5833 |  | WTG Breakdown Maintenance | 22076 | 2299.5833
2518 | 2024-10-11 | 2025 | 2024 | 2024-10-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.61111 | 0.61111 | 0.6125 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2_06 | 46.625 |  | WTG Unscheduled Maintenance | 33570 | 46.625
2519 | 2024-10-11 | 2025 | 2024 | 2024-10-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.88958 | 0.88958 | 0.89306 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2_01 | 99.2847 |  | WTG Unscheduled Maintenance | 28594 | 99.2847
2520 | 2024-10-11 | 2025 | 2024 | 2024-10-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 6007 | Overload yaw motors group 1 | Break down | 0.0076389 | 0.0076389 | 0.091667 | 0 | 2.0167 | 2.0167 | Attend and check error related ckt then found yaw MPCB trip so check all connection then charge MPCB THEN RESET AND STARTWTG. | Close | 0.077564 | O2_20 | 1938.941 |  | WTG Unscheduled Maintenance | 23075 | 1938.941
2521 | 2024-10-11 | 2025 | 2024 | 2024-10-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.43333 | 0.43333 | 0.66944 | 0 | 5.6667 | 5.6667 | wtg manual stop for WTG Maintanance work 3rd Day. | Close | 0.21795 | O2_20 | 5448.2639 |  | WTG scheduled Maintenance | 23075 | 5448.2639
2522 | 2024-10-12 | 2025 | 2024 | 2024-10-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.094444 | 0.094444 | 0.095833 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-05 | 16.95 |  | WTG Unscheduled Maintenance | 12204 | 16.95
2523 | 2024-10-12 | 2025 | 2024 | 2024-10-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.96597 | 0.96597 | 0.96736 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-05 | 16.95 |  | WTG Unscheduled Maintenance | 12204 | 16.95
2524 | 2024-10-12 | 2025 | 2024 | 2024-10-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.96528 | 0.96528 | 0.96736 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-09 | 27.5687 |  | WTG Unscheduled Maintenance | 13233 | 27.5687
2525 | 2024-10-12 | 2025 | 2024 | 2024-10-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.17708 | 0.17708 | 0.17917 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-07 | 24.6396 |  | WTG Unscheduled Maintenance | 11827 | 24.6396
2526 | 2024-10-12 | 2025 | 2024 | 2024-10-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.32431 | 0.32431 | 0.32569 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-07 | 16.4264 |  | WTG Unscheduled Maintenance | 11827 | 16.4264
2527 | 2024-10-12 | 2025 | 2024 | 2024-10-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.51736 | 0.51736 | 0.55972 | 0 | 1.0167 | 1.0167 | Project Pending Work | Close | 0.039103 | O2-07 | 501.0049 |  | WTG Breakdown Maintenance | 11827 | 501.0049
2528 | 2024-10-12 | 2025 | 2024 | 2024-10-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.69097 | 0.69097 | 0.69236 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-21 | 24.5069 |  | WTG Unscheduled Maintenance | 17645 | 24.5069
2529 | 2024-10-12 | 2025 | 2024 | 2024-10-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.67847 | 0.67847 | 0.74306 | 0 | 1.55 | 1.55 | Wtg stof for Converter Error Rectification work | Close | 0.059615 | O2-12 | 951.9583 |  | WTG Breakdown Maintenance | 14740 | 951.9583
2530 | 2024-10-12 | 2025 | 2024 | 2024-10-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.84375 | 0.84375 | 0.86597 | 0 | 0.53333 | 0.53333 | Checked related error data log then reset & run the WTG. | Close | 0.020513 | O2-06 | 406.8 |  | WTG Unscheduled Maintenance | 18306 | 406.8
2531 | 2024-10-12 | 2025 | 2024 | 2024-10-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.94653 | 0.94653 | 0.95069 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2-06 | 76.275 |  | WTG Unscheduled Maintenance | 18306 | 76.275
2532 | 2024-10-12 | 2025 | 2024 | 2024-10-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.46806 | 0.46806 | 0.49028 | 0 | 0.53333 | 0.53333 | Wtg stof for Converter Error Rectification work | Close | 0.020513 | O2-06 | 406.8 |  | WTG Breakdown Maintenance | 18306 | 406.8
2533 | 2024-10-12 | 2025 | 2024 | 2024-10-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.39375 | 0.39375 | 0.64861 | 0 | 6.1167 | 6.1167 | wtg manual stop for WTG Maintanance work 3rd Day. Warning showing pressure drop hyd system so check 9.1 valve but nothing found (filter already removed from system ) After that found 9.1 valve in close condition so recorrect it . Also drain all hydraulic oil which is in very bad condition so top up new hydraulic oil. Now pressure drop hyd system waring not there turbine is under observation for that particular warning. | Close | 0.23526 | O2-01 | 3830.5625 |  | WTG scheduled Maintenance | 15030 | 3830.5625
2534 | 2024-10-12 | 2025 | 2024 | 2024-10-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.96667 | 0.96667 | 0.96806 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-01 | 20.875 |  | WTG Unscheduled Maintenance | 15030 | 20.875
2535 | 2024-10-13 | 2025 | 2024 | 2024-10-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.77083 | 0.77083 | 0.99931 | 0 | 5.4833 | 5.4833 | Attend and After error check related ckt than Check axis-2 encoder A cable malfuntioning so further Troublushooting WIP, | Close | 0.2109 | O2-04 | 1094.1535 |  | WTG Unscheduled Maintenance | 4789 | 1094.1535
2536 | 2024-10-13 | 2025 | 2024 | 2024-10-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.17014 | 0.17014 | 0.17153 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-11 | 6.9667 |  | WTG Unscheduled Maintenance | 5016 | 6.9667
2537 | 2024-10-13 | 2025 | 2024 | 2024-10-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.0027778 | 0.0027778 | 0.0041667 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-06 | 9.5111 |  | WTG Unscheduled Maintenance | 6848 | 9.5111
2538 | 2024-10-13 | 2025 | 2024 | 2024-10-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.74306 | 0.74306 | 0.74444 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-06 | 9.5111 |  | WTG Unscheduled Maintenance | 6848 | 9.5111
2539 | 2024-10-13 | 2025 | 2024 | 2024-10-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.61181 | 0.61181 | 0.66181 | 0 | 1.2 | 1.2 | WTG in error so attend check related ckt than nothing found abnormal so apply hard rebbot than reset and start WTG. | Close | 0.046154 | O2-20 | 270.1 |  | WTG Unscheduled Maintenance | 5402 | 270.1
2540 | 2024-10-13 | 2025 | 2024 | 2024-10-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.96319 | 0.96319 | 0.96458 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-05 | 9.4361 |  | WTG Unscheduled Maintenance | 6794 | 9.4361
2541 | 2024-10-13 | 2025 | 2024 | 2024-10-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.18542 | 0.18542 | 0.18681 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-07 | 4.9653 |  | WTG Unscheduled Maintenance | 3575 | 4.9653
2542 | 2024-10-13 | 2025 | 2024 | 2024-10-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0 | 0 | 0.76806 | 0 | 18.4333 | 18.4333 | wtg manual stop for zeda c ommitioning after zeda done than staret WTG. | Close | 0.70897 | O2-07 | 2745.7986 |  | WTG Breakdown Maintenance | 3575 | 2745.7986
2543 | 2024-10-14 | 2025 | 2024 | 2024-10-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.27292 | 0.27292 | 0.27431 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-05 | 9.1014 |  | WTG Unscheduled Maintenance | 6553 | 9.1014
2544 | 2024-10-14 | 2025 | 2024 | 2024-10-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.95694 | 0.95694 | 0.95833 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-05 | 9.1014 |  | WTG Unscheduled Maintenance | 6553 | 9.1014
2545 | 2024-10-14 | 2025 | 2024 | 2024-10-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Major BD | 0 | 0 | 0.30139 | 0 | 7.2333 | 7.2333 | Attend and check related all connection and PPD After Found Blade no 2 AllConnection check and tight after trouble shuting time found Blade Encoder cable connector 8 Number Pin Connection Open After arrange Soldring iron and cable after soldring done then reset and start wtg | Close | 0.27821 | O2-04 | 1968.0694 |  | WTG Unscheduled Maintenance | 6530 | 1968.0694
2546 | 2024-10-14 | 2025 | 2024 | 2024-10-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.67917 | 0.67917 | 0.68542 | 0 | 0.15 | 0.15 | Checked related error data log then reset & run the WTG. | Close | 0.0057692 | O2-26 | 38.2375 |  | WTG Unscheduled Maintenance | 6118 | 38.2375
2547 | 2024-10-14 | 2025 | 2024 | 2024-10-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.93403 | 0.93403 | 0.93472 | 0 | 0.016667 | 0.016667 | Checked related error data log then reset & run the WTG. | Close | 0.00064103 | O2-15 | 4.1319 |  | WTG Unscheduled Maintenance | 5950 | 4.1319
2548 | 2024-10-14 | 2025 | 2024 | 2024-10-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.36875 | 0.36875 | 0.38194 | 0 | 0.31667 | 0.31667 | Checked related error data log then reset & run the WTG. | Close | 0.012179 | O2-06 | 102.2437 |  | WTG Unscheduled Maintenance | 7749 | 102.2437
2549 | 2024-10-14 | 2025 | 2024 | 2024-10-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.65347 | 0.65347 | 0.65625 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & run the WTG. | Close | 0.0025641 | O2-06 | 21.525 |  | WTG Unscheduled Maintenance | 7749 | 21.525
2550 | 2024-10-14 | 2025 | 2024 | 2024-10-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.82361 | 0.82361 | 0.85347 | 0 | 0.71667 | 0.71667 | Checked related error data log then reset & run the WTG. | Close | 0.027564 | O2-06 | 231.3938 |  | WTG Unscheduled Maintenance | 7749 | 231.3938
2551 | 2024-10-14 | 2025 | 2024 | 2024-10-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.84444 | 0.84444 | 0.84583 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-16 | 8.4181 |  | WTG Unscheduled Maintenance | 6061 | 8.4181
2552 | 2024-10-14 | 2025 | 2024 | 2024-10-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.43611 | 0.43611 | 0.59792 | 0 | 3.8833 | 3.8833 | wtg manual stop for WTG Maintanance work 3rd Day. | Close | 0.14936 | O2-25 | 1172.9285 |  | WTG scheduled Maintenance | 7249 | 1172.9285
2553 | 2024-10-14 | 2025 | 2024 | 2024-10-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.23611 | 0.23611 | 0.24097 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & run the WTG. | Close | 0.0044872 | O2-01 | 35.8264 |  | WTG Unscheduled Maintenance | 7370 | 35.8264
2554 | 2024-10-14 | 2025 | 2024 | 2024-10-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.24931 | 0.24931 | 0.25764 | 0 | 0.2 | 0.2 | Checked related error data log then reset & run the WTG. | Close | 0.0076923 | O2-01 | 61.4167 |  | WTG Unscheduled Maintenance | 7370 | 61.4167
2555 | 2024-10-14 | 2025 | 2024 | 2024-10-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.72431 | 0.72431 | 0.72847 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2-01 | 30.7083 |  | WTG Unscheduled Maintenance | 7370 | 30.7083
2556 | 2024-10-15 | 2025 | 2024 | 2024-10-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Break down | 0.87014 | 0.87014 | 0.87431 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2-26 | 9.2292 |  | WTG Unscheduled Maintenance | 2215 | 9.2292
2557 | 2024-10-15 | 2025 | 2024 | 2024-10-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.86458 | 0.86458 | 0.87153 | 0 | 0.16667 | 0.16667 | Checked related error data log then reset & run the WTG. | Close | 0.0064103 | O2-05 | 12.3889 |  | WTG Unscheduled Maintenance | 1784 | 12.3889
2558 | 2024-10-15 | 2025 | 2024 | 2024-10-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.85694 | 0.85694 | 0.85833 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-09 | 3.5708 |  | WTG Unscheduled Maintenance | 2571 | 3.5708
2559 | 2024-10-15 | 2025 | 2024 | 2024-10-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.21389 | 0.21389 | 0.21528 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-07 | 2.1292 |  | WTG Unscheduled Maintenance | 1533 | 2.1292
2560 | 2024-10-15 | 2025 | 2024 | 2024-10-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.3 | 0.3 | 0.30208 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-07 | 3.1937 |  | WTG Unscheduled Maintenance | 1533 | 3.1937
2561 | 2024-10-15 | 2025 | 2024 | 2024-10-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.98542 | 0.98542 | 0.98681 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-07 | 2.1292 |  | WTG Unscheduled Maintenance | 1533 | 2.1292
2562 | 2024-10-15 | 2025 | 2024 | 2024-10-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.99375 | 0.99375 | 0.99653 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & run the WTG. | Close | 0.0025641 | O2-07 | 4.2583 |  | WTG Unscheduled Maintenance | 1533 | 4.2583
2564 | 2024-10-15 | 2025 | 2024 | 2024-10-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.86875 | 0.86875 | 0.87014 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-21 | 1.4958 |  | WTG Unscheduled Maintenance | 1077 | 1.4958
2565 | 2024-10-15 | 2025 | 2024 | 2024-10-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Connectivity issue | 0.82431 | 0.82431 | 0.87431 | 0 | 1.2 | 1.2 | late start due to connectivity issue | Close | 0.046154 | O2-26 | 110.75 |  | WTG Breakdown Maintenance | 2215 | 110.75
2566 | 2024-10-15 | 2025 | 2024 | 2024-10-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Connectivity issue | 0.82431 | 0.82431 | 0.83542 | 0 | 0.26667 | 0.26667 | late start due to connectivity issue | Close | 0.010256 | O2-03 | 26.7 |  | WTG Breakdown Maintenance | 2403 | 26.7
2567 | 2024-10-15 | 2025 | 2024 | 2024-10-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.20486 | 0.20486 | 0.20694 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-15 | 3.7187 |  | WTG Unscheduled Maintenance | 1785 | 3.7187
2568 | 2024-10-15 | 2025 | 2024 | 2024-10-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.21597 | 0.21597 | 0.21806 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-15 | 3.7187 |  | WTG Unscheduled Maintenance | 1785 | 3.7187
2569 | 2024-10-15 | 2025 | 2024 | 2024-10-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.92708 | 0.92708 | 0.92847 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-15 | 2.4792 |  | WTG Unscheduled Maintenance | 1785 | 2.4792
2570 | 2024-10-15 | 2025 | 2024 | 2024-10-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.87153 | 0.87153 | 0.87292 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-14 | 2.7625 |  | WTG Unscheduled Maintenance | 1989 | 2.7625
2571 | 2024-10-15 | 2025 | 2024 | 2024-10-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Connectivity issue | 0.82431 | 0.82431 | 0.82708 | 0 | 0.066667 | 0.066667 | late start due to connectivity issue | Close | 0.0025641 | O2-12 | 5.4417 |  | WTG Breakdown Maintenance | 1959 | 5.4417
2573 | 2024-10-15 | 2025 | 2024 | 2024-10-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Connectivity issue | 0.82431 | 0.82431 | 0.83611 | 0 | 0.28333 | 0.28333 | Late star due t oconnectivity issue | Close | 0.010897 | O2-21 | 12.7146 |  | WTG Breakdown Maintenance | 1077 | 12.7146
2574 | 2024-10-15 | 2025 | 2024 | 2024-10-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.84097 | 0.84097 | 0.84722 | 0 | 0.15 | 0.15 | Checked related error data log then reset & run the WTG. | Close | 0.0057692 | O2-06 | 4.8875 |  | WTG Unscheduled Maintenance | 782 | 4.8875
2575 | 2024-10-15 | 2025 | 2024 | 2024-10-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.84861 | 0.84861 | 0.85486 | 0 | 0.15 | 0.15 | Checked related error data log then reset & run the WTG. | Close | 0.0057692 | O2-06 | 4.8875 |  | WTG Unscheduled Maintenance | 782 | 4.8875
2577 | 2024-10-15 | 2025 | 2024 | 2024-10-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Connectivity issue | 0.82431 | 0.82431 | 0.83542 | 0 | 0.26667 | 0.26667 | late start due to connectivity issue | Close | 0.010256 | O2-24 | 18.5778 |  | WTG Breakdown Maintenance | 1672 | 18.5778
2579 | 2024-10-15 | 2025 | 2024 | 2024-10-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Connectivity issue | 0.82431 | 0.82431 | 0.86597 | 0 | 1 | 1 | late start due to connectivity issue | Close | 0.038462 | O2-25 | 102.125 |  | WTG Breakdown Maintenance | 2451 | 102.125
2580 | 2024-10-15 | 2025 | 2024 | 2024-10-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.18264 | 0.18264 | 0.18333 | 0 | 0.016667 | 0.016667 | Checked related error data log then reset & run the WTG. | Close | 0.00064103 | O2-01 | 1.5389 |  | WTG Unscheduled Maintenance | 2216 | 1.5389
2581 | 2024-10-16 | 2025 | 2024 | 2024-10-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.50694 | 0.50694 | 0.50972 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & run the WTG. | Close | 0.0025641 | O2-05 | 20.5028 |  | WTG Unscheduled Maintenance | 7381 | 20.5028
2582 | 2024-10-16 | 2025 | 2024 | 2024-10-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.7625 | 0.7625 | 0.76458 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-05 | 15.3771 |  | WTG Unscheduled Maintenance | 7381 | 15.3771
2583 | 2024-10-16 | 2025 | 2024 | 2024-10-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down | 0.065278 | 0.065278 | 0.27917 | 0 | 5.1333 | 5.1333 | Attend and check releted ckt. So found 9.1 valve and 9.3 valve inside contaminition so properly clean it with using blower also check A1 &A2 LINES. FOUND A1 INSIDE NOT Avalilable after reemove avail after trail but not resolve error so replace 9.1 valve and after check pressure normal and normally maintain and also normaly build up after then reset and start wtg | Close | 0.19744 | O2-21 | 841.8667 |  | WTG Unscheduled Maintenance | 3936 | 841.8667
2584 | 2024-10-16 | 2025 | 2024 | 2024-10-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down | 0.99722 | 0.99722 | 0.99931 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-21 | 8.2 |  | WTG Unscheduled Maintenance | 3936 | 8.2
2585 | 2024-10-16 | 2025 | 2024 | 2024-10-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.68542 | 0.68542 | 0.69861 | 0 | 0.31667 | 0.31667 | Checked related error data log then reset & run the WTG. | Close | 0.012179 | O2-26 | 114.2375 |  | WTG Unscheduled Maintenance | 8658 | 114.2375
2586 | 2024-10-16 | 2025 | 2024 | 2024-10-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.44028 | 0.44028 | 0.79722 | 0 | 8.5667 | 8.5667 | wtg manual stop for WTG Maintanance work 3rd Day. | Close | 0.32949 | O2-03 | 2804.5125 |  | WTG scheduled Maintenance | 7857 | 2804.5125
2587 | 2024-10-16 | 2025 | 2024 | 2024-10-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.015972 | 0.015972 | 0.018056 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-15 | 14.2396 |  | WTG Unscheduled Maintenance | 6835 | 14.2396
2588 | 2024-10-16 | 2025 | 2024 | 2024-10-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.11319 | 0.11319 | 0.12639 | 0 | 0.31667 | 0.31667 | Checked related error data log then reset & run the WTG. | Close | 0.012179 | O2-15 | 90.184 |  | WTG Unscheduled Maintenance | 6835 | 90.184
2589 | 2024-10-16 | 2025 | 2024 | 2024-10-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.22917 | 0.22917 | 0.23056 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-15 | 9.4931 |  | WTG Unscheduled Maintenance | 6835 | 9.4931
2590 | 2024-10-16 | 2025 | 2024 | 2024-10-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.24792 | 0.24792 | 0.25208 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2-15 | 28.4792 |  | WTG Unscheduled Maintenance | 6835 | 28.4792
2591 | 2024-10-16 | 2025 | 2024 | 2024-10-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.38056 | 0.38056 | 0.54792 | 0 | 4.0167 | 4.0167 | check error related data in scada so found inductor cell temp jump so attend it check error releted circuit so found inductor cell temp sensor BT6 Connection loose so tight it then reset and start wtg. | Close | 0.15449 | O2-15 | 1143.9132 |  | WTG Unscheduled Maintenance | 6835 | 1143.9132
2592 | 2024-10-16 | 2025 | 2024 | 2024-10-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.47292 | 0.47292 | 0.76528 | 0 | 7.0167 | 7.0167 | Turbani Manual stop for broken rotor bolt remove work | Close | 0.26987 | O2-14 | 2175.459 |  | WTG Breakdown Maintenance | 7441 | 2175.459
2593 | 2024-10-16 | 2025 | 2024 | 2024-10-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.74653 | 0.74653 | 0.89167 | 0 | 3.4833 | 3.4833 | Check error releted data in scADA so found coolant unit tempvalue malfunction so attend it check error related circuit so found loos connection so tigh it then reset and start wtg | Close | 0.13397 | O2-11 | 1121.0528 |  | WTG Unscheduled Maintenance | 7724 | 1121.0528
2594 | 2024-10-16 | 2025 | 2024 | 2024-10-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 88 | Outs.temp. nacelle implaus. | Break down | 0.57292 | 0.57292 | 0.67708 | 0 | 2.5 | 2.5 | Check error related data in scada so found nacelle outdoor temp sensor value difference more than 3 degree so attend check error related circuit so found 1 nos temp sensor faulty so replace it then reset and start wtg | Close | 0.096154 | O2-09 | 561.0417 |  | WTG Unscheduled Maintenance | 5386 | 561.0417
2596 | 2024-10-16 | 2025 | 2024 | 2024-10-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.25486 | 0.25486 | 0.25833 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2-06 | 7.6563 |  | WTG Unscheduled Maintenance | 2205 | 7.6563
2597 | 2024-10-17 | 2025 | 2024 | 2024-10-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.025694 | 0.025694 | 0.027083 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-05 | 10.5528 |  | WTG Unscheduled Maintenance | 7598 | 10.5528
2598 | 2024-10-17 | 2025 | 2024 | 2024-10-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.12778 | 0.12778 | 0.12917 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-05 | 10.5528 |  | WTG Unscheduled Maintenance | 7598 | 10.5528
2599 | 2024-10-17 | 2025 | 2024 | 2024-10-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.66458 | 0.66458 | 0.71458 | 0 | 1.2 | 1.2 | After grid resume time Not Singnal Converter RFO (CAN) After single available then reset and start wtg | Close | 0.046154 | O2-07 | 208.8 |  | WTG Unscheduled Maintenance | 4176 | 208.8
2600 | 2024-10-17 | 2025 | 2024 | 2024-10-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.66458 | 0.66458 | 0.72569 | 0 | 1.4667 | 1.4667 | After grid resume time Not Singnal Converter RFO (CAN) After single available then reset and start wtg | Close | 0.05641 | O2-21 | 343.5056 |  | WTG Unscheduled Maintenance | 5621 | 343.5056
2601 | 2024-10-17 | 2025 | 2024 | 2024-10-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.45694 | 0.45694 | 0.5625 | 0 | 2.5333 | 2.5333 | Turbine Manual stop for broken rotor bolt remove work | Close | 0.097436 | O2-14 | 529.6778 |  | WTG Breakdown Maintenance | 5018 | 529.6778
2602 | 2024-10-17 | 2025 | 2024 | 2024-10-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.016667 | 0.016667 | 0.020139 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2-11 | 17.9063 |  | WTG Unscheduled Maintenance | 5157 | 17.9063
2603 | 2024-10-17 | 2025 | 2024 | 2024-10-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.040972 | 0.040972 | 0.045833 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & run the WTG. | Close | 0.0044872 | O2-11 | 25.0687 |  | WTG Unscheduled Maintenance | 5157 | 25.0687
2604 | 2024-10-17 | 2025 | 2024 | 2024-10-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.34931 | 0.34931 | 0.35833 | 0 | 0.21667 | 0.21667 | Checked related error data log then reset & run the WTG. | Close | 0.0083333 | O2-11 | 46.5563 |  | WTG Unscheduled Maintenance | 5157 | 46.5563
2605 | 2024-10-17 | 2025 | 2024 | 2024-10-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.66458 | 0.66458 | 0.69375 | 0 | 0.7 | 0.7 | After grid resume time Not Singnal Converter RFO (CAN) After single available then reset and start wtg | Close | 0.026923 | O2-06 | 164.5 |  | WTG Unscheduled Maintenance | 5640 | 164.5
2606 | 2024-10-17 | 2025 | 2024 | 2024-10-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.66458 | 0.66458 | 0.70625 | 0 | 1 | 1 | After grid resume time Not Singnal Converter RFO (CAN) After single available then reset and start wtg | Close | 0.038462 | O2-16 | 229.9167 |  | WTG Unscheduled Maintenance | 5518 | 229.9167
2607 | 2024-10-17 | 2025 | 2024 | 2024-10-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.051389 | 0.051389 | 0.053472 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-06 | 11.75 |  | WTG Unscheduled Maintenance | 5640 | 11.75
2608 | 2024-10-17 | 2025 | 2024 | 2024-10-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.43472 | 0.43472 | 0.43681 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-06 | 11.75 |  | WTG Unscheduled Maintenance | 5640 | 11.75
2609 | 2024-10-17 | 2025 | 2024 | 2024-10-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.66458 | 0.66458 | 0.71042 | 0 | 1.1 | 1.1 | Checked related error data log then reset & run the WTG. | Close | 0.042308 | O2-06 | 258.5 |  | WTG Unscheduled Maintenance | 5640 | 258.5
2610 | 2024-10-17 | 2025 | 2024 | 2024-10-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.63542 | 0.63542 | 0.72083 | 0 | 2.05 | 2.05 | Tower base bolt testing work | Close | 0.078846 | O2-25 | 680.9417 |  | WTG scheduled Maintenance | 7972 | 680.9417
2611 | 2024-10-17 | 2025 | 2024 | 2024-10-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.11319 | 0.11319 | 0.11458 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-01 | 9.6681 |  | WTG Unscheduled Maintenance | 6961 | 9.6681
2612 | 2024-10-17 | 2025 | 2024 | 2024-10-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.054861 | 0.054861 | 0.075694 | 0 | 0.5 | 0.5 | Checked related error data log then reset & run the WTG. | Close | 0.019231 | O2-11 | 107.4375 |  | WTG Unscheduled Maintenance | 5157 | 107.4375
2613 | 2024-10-18 | 2025 | 2024 | 2024-10-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 7025 | Configuration error | Break down | 0.75139 | 0.75139 | 0.76806 | 0 | 0.4 | 0.4 | After grid resume time error after solustion center to Hard Reebut apply after then reset and start wtg | Close | 0.015385 | O2-26 | 72.2 |  | WTG Unscheduled Maintenance | 4332 | 72.2
2614 | 2024-10-18 | 2025 | 2024 | 2024-10-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.75139 | 0.75139 | 0.78264 | 0 | 0.75 | 0.75 | After grid resume time Not Singnal Converter RFO (CAN) After single available then reset and start wtg | Close | 0.028846 | O2-05 | 117.1562 |  | WTG Unscheduled Maintenance | 3749 | 117.1562
2615 | 2024-10-18 | 2025 | 2024 | 2024-10-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.75139 | 0.75139 | 0.80486 | 0 | 1.2833 | 1.2833 | After grid resume time Not Singnal Converter RFO (CAN) After single available then reset and start wtg | Close | 0.049359 | O2-09 | 268.5375 |  | WTG Unscheduled Maintenance | 5022 | 268.5375
2616 | 2024-10-18 | 2025 | 2024 | 2024-10-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.39306 | 0.39306 | 0.71458 | 0 | 7.7167 | 7.7167 | WTG 1 ST Month Mainttanance work | Close | 0.29679 | O2-07 | 1802.1632 |  | WTG Scheduled Maintenance | 5605 | 1802.1632
2617 | 2024-10-18 | 2025 | 2024 | 2024-10-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.75139 | 0.75139 | 0.76875 | 0 | 0.41667 | 0.41667 | After grid resume time error after solustion center to Hard Reebut apply after then reset and start wtg | Close | 0.016026 | O2-15 | 55.7465 |  | WTG Unscheduled Maintenance | 3211 | 55.7465
2618 | 2024-10-18 | 2025 | 2024 | 2024-10-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.75139 | 0.75139 | 0.79653 | 0 | 1.0833 | 1.0833 | After grid resume time Not Singnal Converter RFO (CAN) After single available then reset and start wtg | Close | 0.041667 | O2-14 | 162.9514 |  | WTG Unscheduled Maintenance | 3610 | 162.9514
2619 | 2024-10-18 | 2025 | 2024 | 2024-10-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.81667 | 0.81667 | 0.81875 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-11 | 7.7354 |  | WTG Unscheduled Maintenance | 3713 | 7.7354
2620 | 2024-10-18 | 2025 | 2024 | 2024-10-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 650 | Pitch controller communication error | Break down | 0.76597 | 0.76597 | 0.77014 | 0 | 0.1 | 0.1 | After grid time error after solustion center to hard reebut apply after then start wtg | Close | 0.0038462 | O2-10 | 14.7458 |  | WTG Unscheduled Maintenance | 3539 | 14.7458
2621 | 2024-10-18 | 2025 | 2024 | 2024-10-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.36597 | 0.36597 | 0.36736 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-06 | 9.1958 |  | WTG Unscheduled Maintenance | 6621 | 9.1958
2622 | 2024-10-18 | 2025 | 2024 | 2024-10-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.84236 | 0.84236 | 0.84375 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-06 | 9.1958 |  | WTG Unscheduled Maintenance | 6621 | 9.1958
2623 | 2024-10-18 | 2025 | 2024 | 2024-10-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.61111 | 0.61111 | 0.63056 | 0 | 0.46667 | 0.46667 | WTG Manual stop for project punch point closing work | Close | 0.017949 | O2-16 | 132.8833 |  | WTG Breakdown Maintenance | 6834 | 132.8833
2624 | 2024-10-18 | 2025 | 2024 | 2024-10-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.19861 | 0.19861 | 0.20069 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-06 | 13.7938 |  | WTG Unscheduled Maintenance | 6621 | 13.7938
2625 | 2024-10-18 | 2025 | 2024 | 2024-10-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.56181 | 0.56181 | 0.56667 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & run the WTG. | Close | 0.0044872 | O2-06 | 32.1854 |  | WTG Unscheduled Maintenance | 6621 | 32.1854
2626 | 2024-10-18 | 2025 | 2024 | 2024-10-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.44653 | 0.44653 | 0.45556 | 0 | 0.21667 | 0.21667 | Checked related error data log then reset & run the WTG. | Close | 0.0083333 | O2-06 | 59.7729 |  | WTG Unscheduled Maintenance | 6621 | 59.7729
2627 | 2024-10-18 | 2025 | 2024 | 2024-10-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 7002 | Task runtime failure 5ms | Break down | 0.76736 | 0.76736 | 0.77153 | 0 | 0.1 | 0.1 | After grid time error after solustion center to hard reebut apply after then start wtg | Close | 0.0038462 | O2-25 | 21.8875 |  | WTG Unscheduled Maintenance | 5253 | 21.8875
2628 | 2024-10-18 | 2025 | 2024 | 2024-10-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.75139 | 0.75139 | 0.80694 | 0 | 1.3333 | 1.3333 | After grid resume time Not Singnal Converter RFO (CAN) After single available then reset and start wtg | Close | 0.051282 | O2-01 | 246.5 |  | WTG Unscheduled Maintenance | 4437 | 246.5
2629 | 2024-10-19 | 2025 | 2024 | 2024-10-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.59375 | 0.59375 | 0.59792 | 0 | 0.1 | 0.1 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0038462 | O2-26 | 27.7917 |  | WTG Unscheduled Maintenance | 6670 | 27.7917
2630 | 2024-10-19 | 2025 | 2024 | 2024-10-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.59375 | 0.59375 | 0.63819 | 0 | 1.0667 | 1.0667 | After grid resume time Not Singnal Converter RFO (CAN) After single available then reset and start wtg | Close | 0.041026 | O2-05 | 340.6222 |  | WTG Unscheduled Maintenance | 7664 | 340.6222
2631 | 2024-10-19 | 2025 | 2024 | 2024-10-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.65833 | 0.65833 | 0.6625 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2-05 | 31.9333 |  | WTG Unscheduled Maintenance | 7664 | 31.9333
2632 | 2024-10-19 | 2025 | 2024 | 2024-10-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.67431 | 0.67431 | 0.68472 | 0 | 0.25 | 0.25 | Checked related error data log then reset & run the WTG. | Close | 0.0096154 | O2-05 | 79.8333 |  | WTG Unscheduled Maintenance | 7664 | 79.8333
2633 | 2024-10-19 | 2025 | 2024 | 2024-10-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.69097 | 0.69097 | 0.69306 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-05 | 15.9667 |  | WTG Unscheduled Maintenance | 7664 | 15.9667
2634 | 2024-10-19 | 2025 | 2024 | 2024-10-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.59375 | 0.59375 | 0.65347 | 0 | 1.4333 | 1.4333 | After grid resume time Not Singnal Converter RFO (CAN) After single available then reset and start wtg | Close | 0.055128 | O2-09 | 447.4389 |  | WTG Unscheduled Maintenance | 7492 | 447.4389
2635 | 2024-10-19 | 2025 | 2024 | 2024-10-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Auto reset | 0.25972 | 0.25972 | 0.26111 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2-07 | 6.3014 |  | WTG Unscheduled Maintenance | 4537 | 6.3014
2636 | 2024-10-19 | 2025 | 2024 | 2024-10-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.38403 | 0.38403 | 0.64236 | 0 | 6.2 | 6.2 | WTG 1 ST Month Mainttanance work( 2 day) | Close | 0.23846 | O2-07 | 1172.0583 |  | WTG scheduled Maintenance | 4537 | 1172.0583
2637 | 2024-10-19 | 2025 | 2024 | 2024-10-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.6875 | 0.6875 | 0.68958 | 0 | 0.05 | 0.05 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0019231 | O2-07 | 9.4521 |  | WTG Unscheduled Maintenance | 4537 | 9.4521
2638 | 2024-10-19 | 2025 | 2024 | 2024-10-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Auto reset | 0.81875 | 0.81875 | 0.82083 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2-07 | 9.4521 |  | WTG Unscheduled Maintenance | 4537 | 9.4521
2639 | 2024-10-19 | 2025 | 2024 | 2024-10-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down | 0.65486 | 0.65486 | 0.66806 | 0 | 0.31667 | 0.31667 | Checked related error data log then reset & run the WTG. | Close | 0.012179 | O2-02 | 81.2778 |  | WTG Unscheduled Maintenance | 6160 | 81.2778
2640 | 2024-10-19 | 2025 | 2024 | 2024-10-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3060 | Conv. emerg.off type A | Break down | 0.6875 | 0.6875 | 0.69028 | 0 | 0.066667 | 0.066667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0025641 | O2-21 | 14.2444 |  | WTG Unscheduled Maintenance | 5128 | 14.2444
2641 | 2024-10-19 | 2025 | 2024 | 2024-10-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.92222 | 0.92222 | 0.92361 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-21 | 7.1222 |  | WTG Unscheduled Maintenance | 5128 | 7.1222
2642 | 2024-10-19 | 2025 | 2024 | 2024-10-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.6875 | 0.6875 | 0.69097 | 0 | 0.083333 | 0.083333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0032051 | O2-04 | 17.8681 |  | WTG Unscheduled Maintenance | 5146 | 17.8681
2643 | 2024-10-19 | 2025 | 2024 | 2024-10-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.59375 | 0.59375 | 0.60486 | 0 | 0.26667 | 0.26667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.010256 | O2-03 | 84.9667 |  | WTG Unscheduled Maintenance | 7647 | 84.9667
2644 | 2024-10-19 | 2025 | 2024 | 2024-10-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.59375 | 0.59375 | 0.63958 | 0 | 1.1 | 1.1 | After grid resume time Not Singnal Converter RFO (CAN) After single available then reset and start wtg | Close | 0.042308 | O2-14 | 337.1958 |  | WTG Unscheduled Maintenance | 7357 | 337.1958
2645 | 2024-10-19 | 2025 | 2024 | 2024-10-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.65417 | 0.65417 | 0.65833 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2-14 | 30.6542 |  | WTG Unscheduled Maintenance | 7357 | 30.6542
2646 | 2024-10-19 | 2025 | 2024 | 2024-10-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.62222 | 0.62222 | 0.62361 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2-10 | 9.9667 |  | WTG Unscheduled Maintenance | 7176 | 9.9667
2647 | 2024-10-19 | 2025 | 2024 | 2024-10-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3063 | Conv. emerg.off type D | Auto reset | 0.56319 | 0.56319 | 0.56528 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2-06 | 9.9146 |  | WTG Unscheduled Maintenance | 4759 | 9.9146
2648 | 2024-10-19 | 2025 | 2024 | 2024-10-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.6875 | 0.6875 | 0.69792 | 0 | 0.25 | 0.25 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0096154 | O2-06 | 49.5729 |  | WTG Unscheduled Maintenance | 4759 | 49.5729
2649 | 2024-10-19 | 2025 | 2024 | 2024-10-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.51528 | 0.51528 | 0.55694 | 0 | 1 | 1 | WTG Manual stop for project pendind work . | Close | 0.038462 | O2-06 | 198.2917 |  | WTG Breakdown Maintenance | 4759 | 198.2917
2650 | 2024-10-19 | 2025 | 2024 | 2024-10-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.76042 | 0.76042 | 0.76389 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2-06 | 16.5243 |  | WTG Unscheduled Maintenance | 4759 | 16.5243
2651 | 2024-10-19 | 2025 | 2024 | 2024-10-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.59375 | 0.59375 | 0.60208 | 0 | 0.2 | 0.2 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0076923 | O2-25 | 78.0417 |  | WTG Unscheduled Maintenance | 9365 | 78.0417
2652 | 2024-10-19 | 2025 | 2024 | 2024-10-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down | 0.65833 | 0.65833 | 0.67361 | 0 | 0.36667 | 0.36667 | Checked related error data log then reset & run the WTG. | Close | 0.014103 | O2-01 | 135.2847 |  | WTG Unscheduled Maintenance | 8855 | 135.2847
2653 | 2024-10-20 | 2025 | 2024 | 2024-10-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 650 | Pitch controller communication error | Break down | 0.63194 | 0.63194 | 0.64167 | 0 | 0.23333 | 0.23333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0089744 | O2-05 | 28.7972 |  | WTG Unscheduled Maintenance | 2962 | 28.7972
2654 | 2024-10-20 | 2025 | 2024 | 2024-10-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.65069 | 0.65069 | 0.65556 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & run the WTG. | Close | 0.0044872 | O2-05 | 14.3986 |  | WTG Unscheduled Maintenance | 2962 | 14.3986
2655 | 2024-10-20 | 2025 | 2024 | 2024-10-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.63194 | 0.63194 | 0.65764 | 0 | 0.61667 | 0.61667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.023718 | O2-26 | 70.3257 |  | WTG Unscheduled Maintenance | 2737 | 70.3257
2656 | 2024-10-20 | 2025 | 2024 | 2024-10-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.63194 | 0.63194 | 0.63889 | 0 | 0.16667 | 0.16667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0064103 | O2-03 | 24.4444 |  | WTG Unscheduled Maintenance | 3520 | 24.4444
2657 | 2024-10-20 | 2025 | 2024 | 2024-10-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.63194 | 0.63194 | 0.6375 | 0 | 0.13333 | 0.13333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0051282 | O2-15 | 12.8667 |  | WTG Unscheduled Maintenance | 2316 | 12.8667
2658 | 2024-10-20 | 2025 | 2024 | 2024-10-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.63194 | 0.63194 | 0.63819 | 0 | 0.15 | 0.15 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0057692 | O2-12 | 16.7375 |  | WTG Unscheduled Maintenance | 2678 | 16.7375
2659 | 2024-10-20 | 2025 | 2024 | 2024-10-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.63194 | 0.63194 | 0.63958 | 0 | 0.18333 | 0.18333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0070513 | O2-14 | 18.1958 |  | WTG Unscheduled Maintenance | 2382 | 18.1958
2660 | 2024-10-20 | 2025 | 2024 | 2024-10-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.64792 | 0.64792 | 0.65 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-11 | 5.3229 |  | WTG Unscheduled Maintenance | 2555 | 5.3229
2661 | 2024-10-20 | 2025 | 2024 | 2024-10-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.65625 | 0.65625 | 0.65833 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-11 | 5.3229 |  | WTG Unscheduled Maintenance | 2555 | 5.3229
2662 | 2024-10-20 | 2025 | 2024 | 2024-10-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.63194 | 0.63194 | 0.63472 | 0 | 0.066667 | 0.066667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0025641 | O2-10 | 7.1361 |  | WTG Unscheduled Maintenance | 2569 | 7.1361
2663 | 2024-10-20 | 2025 | 2024 | 2024-10-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 2520 | Gen.speed analog<>gear.speed | Break down | 0.61181 | 0.61181 | 0.62222 | 0 | 0.25 | 0.25 | Checked related error data log then reset & run the WTG. | Close | 0.0096154 | O2-06 | 50.8125 |  | WTG Unscheduled Maintenance | 4878 | 50.8125
2664 | 2024-10-20 | 2025 | 2024 | 2024-10-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.61111 | 0.61111 | 0.61319 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-06 | 10.1625 |  | WTG Unscheduled Maintenance | 4878 | 10.1625
2665 | 2024-10-20 | 2025 | 2024 | 2024-10-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Auto reset | 0.69861 | 0.69861 | 0.7 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2-06 | 6.775 |  | WTG Unscheduled Maintenance | 4878 | 6.775
2666 | 2024-10-20 | 2025 | 2024 | 2024-10-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.63194 | 0.63194 | 0.65 | 0 | 0.43333 | 0.43333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.016667 | O2-25 | 48.8403 |  | WTG Unscheduled Maintenance | 2705 | 48.8403
2667 | 2024-10-20 | 2025 | 2024 | 2024-10-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.63194 | 0.63194 | 0.65 | 0 | 0.43333 | 0.43333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.016667 | O2-01 | 73.2153 |  | WTG Unscheduled Maintenance | 4055 | 73.2153
2668 | 2024-10-21 | 2025 | 2024 | 2024-10-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Auto reset | 0.72153 | 0.72153 | 0.72292 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2-07 | 2.4125 |  | WTG Unscheduled Maintenance | 1737 | 2.4125
2669 | 2024-10-21 | 2025 | 2024 | 2024-10-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.41319 | 0.41319 | 0.50972 | 0 | 2.3167 | 2.3167 | Wtg stop for 1st month mentenence Day-1 | Close | 0.089103 | O2-04 | 232.9215 |  | WTG Scheduled Maintenance | 2413 | 232.9215
2670 | 2024-10-21 | 2025 | 2024 | 2024-10-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.575 | 0.575 | 0.74167 | 0 | 4 | 4 | Wtg stop for 1st month mentenence Day-1 | Close | 0.15385 | O2-04 | 402.1667 |  | WTG Scheduled Maintenance | 2413 | 402.1667
2671 | 2024-10-21 | 2025 | 2024 | 2024-10-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.33958 | 0.33958 | 0.34167 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-26 | 6.0771 |  | WTG Unscheduled Maintenance | 2917 | 6.0771
2672 | 2024-10-21 | 2025 | 2024 | 2024-10-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.27014 | 0.27014 | 0.27153 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-11 | 3.6917 |  | WTG Unscheduled Maintenance | 2658 | 3.6917
2673 | 2024-10-21 | 2025 | 2024 | 2024-10-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.6375 | 0.6375 | 0.63958 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-11 | 5.5375 |  | WTG Unscheduled Maintenance | 2658 | 5.5375
2674 | 2024-10-21 | 2025 | 2024 | 2024-10-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.95972 | 0.95972 | 0.99999 | 0 | 0.96639 | 0.96639 | After wtg in error so attend and check related circuit and check all center box connection so further troublsooting WIP.. | Close | 0.037169 | O2-21 | 141.8981 |  | WTG Unscheduled Maintenance | 3524 | 141.8981
2675 | 2024-10-21 | 2025 | 2024 | 2024-10-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.61944 | 0.61944 | 0.75417 | 0 | 3.2333 | 3.2333 | Wyg attend for rep cooling error so attend and replace coolent motor on top unit and also replace coolent motor in bottom unit than reset and start WTG.(Now turbine under observation). | Close | 0.12436 | O2-08 | 369.8125 |  | WTG Breakdown Maintenance | 2745 | 369.8125
2676 | 2024-10-22 | 2025 | 2024 | 2024-10-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 6210 | Max. cable twistangle | Break down | 0.19653 | 0.19653 | 0.31319 | 0 | 2.8 | 2.8 | Attend and remove cable twist and set twist of sensor then reset and start wtg | Close | 0.10769 | O2-21 | 388.15 |  | WTG Unscheduled Maintenance | 3327 | 388.15
2677 | 2024-10-22 | 2025 | 2024 | 2024-10-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.40139 | 0.40139 | 0.66875 | 0 | 6.4167 | 6.4167 | Wtg stop for 1st month mentenence work ( Day-2) | Close | 0.24679 | O2-04 | 733.1042 |  | WTG Scheduled Maintenance | 2742 | 733.1042
2678 | 2024-10-22 | 2025 | 2024 | 2024-10-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD | 0.53194 | 0.53194 | 0.85833 | 0 | 7.8333 | 7.8333 | Attend for Power curve checking work so replace Both untrasolnic cable with codute and proper routing and also ultrasonic alignment work Done.-than after check Naccele coolent pressure diffrece error than found pressure transmeter malfunctioning so replace With new one than refilling coolnet and pressure value comes normal.-than replace Naccele coolent motor due to abnormal sound is comes so replace it with new one which is comes against NCR.-Also Check BLS cable routing.-And also remove Cables from top panele as per Engineering guidence.then start wtg. | Close | 0.30128 | O2-12 | 899.8542 |  | WTG Breakdown Maintenance | 2757 | 899.8542
2679 | 2024-10-22 | 2025 | 2024 | 2024-10-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.13194 | 0.13194 | 0.13403 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-06 | 6.2167 |  | WTG Unscheduled Maintenance | 2984 | 6.2167
2680 | 2024-10-22 | 2025 | 2024 | 2024-10-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.018056 | 0.018056 | 0.019444 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-07 | 4.1014 |  | WTG Unscheduled Maintenance | 2953 | 4.1014
2681 | 2024-10-22 | 2025 | 2024 | 2024-10-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.0034722 | 0.0034722 | 0.23333 | 0 | 5.5167 | 5.5167 | Attend check all related circuit check 24v on SPD and found FA001 SPD loose connection so tight it then no any abnormality so reset and start wtg now WTG under observation. | Close | 0.21218 | O2-06 | 685.9056 |  | WTG Unscheduled Maintenance | 2984 | 685.9056
2682 | 2024-10-22 | 2025 | 2024 | 2024-10-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.56181 | 0.56181 | 0.625 | 0 | 1.5167 | 1.5167 | WTG Manual stop for project pendind work . | Close | 0.058333 | O2-06 | 188.5722 |  | WTG Breakdown Maintenance | 2984 | 188.5722
2683 | 2024-10-22 | 2025 | 2024 | 2024-10-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.52014 | 0.52014 | 0.52222 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-20 | 5.5312 |  | WTG Unscheduled Maintenance | 2655 | 5.5312 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
2684 | 2024-10-23 | 2025 | 2024 | 2024-10-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.99722 | 0.99722 | 0.99931 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-07 | 11.3396 |  | WTG Unscheduled Maintenance | 5443 | 11.3396
2685 | 2024-10-23 | 2025 | 2024 | 2024-10-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.58611 | 0.58611 | 0.5875 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-21 | 8.5875 |  | WTG Unscheduled Maintenance | 6183 | 8.5875
2686 | 2024-10-23 | 2025 | 2024 | 2024-10-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.89583 | 0.89583 | 0.89792 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-21 | 12.8812 |  | WTG Unscheduled Maintenance | 6183 | 12.8812
2687 | 2024-10-23 | 2025 | 2024 | 2024-10-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.43889 | 0.43889 | 0.74236 | 0 | 7.2833 | 7.2833 | wtg manual stop for Repeated Error Inspection Work done | Close | 0.28013 | O2-12 | 1876.3688 |  | WTG Breakdown Maintenance | 6183 | 1876.3688
2688 | 2024-10-23 | 2025 | 2024 | 2024-10-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.35278 | 0.35278 | 0.47847 | 0 | 3.0167 | 3.0167 | wtg manual stop for first Month Maintenance Pending point activity | Close | 0.11603 | O2-21 | 975.3889 |  | WTG Scheduled Maintenance | 7760 | 975.3889
2689 | 2024-10-23 | 2025 | 2024 | 2024-10-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.57986 | 0.57986 | 0.58125 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-06 | 8.8083 |  | WTG Unscheduled Maintenance | 6342 | 8.8083
2690 | 2024-10-23 | 2025 | 2024 | 2024-10-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.7 | 0.7 | 0.70208 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-06 | 13.2125 |  | WTG Unscheduled Maintenance | 6342 | 13.2125
2691 | 2024-10-23 | 2025 | 2024 | 2024-10-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.64861 | 0.64861 | 0.72014 | 0 | 1.7167 | 1.7167 | wtg manual stop for first Month Maintenance Pending point activity | Close | 0.066026 | O2-20 | 406.4924 |  | WTG Scheduled Maintenance | 5683 | 406.4924
2692 | 2024-10-24 | 2025 | 2024 | 2024-10-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.97431 | 0.97431 | 0.98958 | 0 | 0.36667 | 0.36667 | Checked related error data log then reset & run the WTG. | Close | 0.014103 | O2-05 | 147.0181 |  | WTG Unscheduled Maintenance | 9623 | 147.0181
2693 | 2024-10-24 | 2025 | 2024 | 2024-10-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.97361 | 0.97361 | 0.98819 | 0 | 0.35 | 0.35 | Checked related error data log then reset & run the WTG. | Close | 0.013462 | O2-09 | 194.2063 |  | WTG Unscheduled Maintenance | 13317 | 194.2063
2694 | 2024-10-24 | 2025 | 2024 | 2024-10-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.41389 | 0.41389 | 0.74167 | 0 | 7.8667 | 7.8667 | Wtg stop for 1st month Maintenance work ( Day-1) | Close | 0.30256 | O2-26 | 2914.6 |  | WTG Scheduled Maintenance | 8892 | 2914.6
2695 | 2024-10-24 | 2025 | 2024 | 2024-10-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 7002 | Task runtime failure 5ms | Break down | 0.8125 | 0.8125 | 0.83264 | 0 | 0.48333 | 0.48333 | Checked related error data log then reset & run the WTG. | Close | 0.01859 | O2-11 | 220.3799 |  | WTG Unscheduled Maintenance | 10943 | 220.3799
2696 | 2024-10-24 | 2025 | 2024 | 2024-10-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.48333 | 0.48333 | 0.68333 | 0 | 4.8 | 4.8 | wtg manual stop foe rep error Inspection work | Close | 0.18462 | O2-01 | 2365.4 |  | WTG Breakdown Maintenance | 11827 | 2365.4
2697 | 2024-10-24 | 2025 | 2024 | 2024-10-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.61458 | 0.61458 | 0.62986 | 0 | 0.36667 | 0.36667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.014103 | O2-07 | 76.8319 |  | WTG Unscheduled Maintenance | 5029 | 76.8319
2698 | 2024-10-24 | 2025 | 2024 | 2024-10-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.61458 | 0.61458 | 0.61806 | 0 | 0.083333 | 0.083333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0032051 | O2-21 | 27.0799 |  | WTG Unscheduled Maintenance | 7799 | 27.0799
2699 | 2024-10-24 | 2025 | 2024 | 2024-10-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.61458 | 0.61458 | 0.62361 | 0 | 0.21667 | 0.21667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0083333 | O2-04 | 57.3715 |  | WTG Unscheduled Maintenance | 6355 | 57.3715
2700 | 2024-10-24 | 2025 | 2024 | 2024-10-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.61458 | 0.61458 | 0.61736 | 0 | 0.066667 | 0.066667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0025641 | O2-21 | 21.6639 |  | WTG Unscheduled Maintenance | 7799 | 21.6639
2701 | 2024-10-24 | 2025 | 2024 | 2024-10-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.78889 | 0.78889 | 0.81458 | 0 | 0.61667 | 0.61667 | Checked related error data log then reset & run the WTG. | Close | 0.023718 | O2-06 | 199.466 |  | WTG Unscheduled Maintenance | 7763 | 199.466
2702 | 2024-10-24 | 2025 | 2024 | 2024-10-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.61458 | 0.61458 | 0.63056 | 0 | 0.38333 | 0.38333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.014744 | O2-06 | 123.9924 |  | WTG Unscheduled Maintenance | 7763 | 123.9924
2703 | 2024-10-24 | 2025 | 2024 | 2024-10-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.61458 | 0.61458 | 0.62014 | 0 | 0.13333 | 0.13333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0051282 | O2-24 | 46.0278 |  | WTG Unscheduled Maintenance | 8285 | 46.0278
2704 | 2024-10-24 | 2025 | 2024 | 2024-10-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.61458 | 0.61458 | 0.64861 | 0 | 0.81667 | 0.81667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot and Error is not resolved so Another troubleshooting work WIP | Close | 0.03141 | O2-06 | 264.1576 |  | WTG Unscheduled Maintenance | 7763 | 264.1576
2705 | 2024-10-24 | 2025 | 2024 | 2024-10-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.72569 | 0.72569 | 0.72778 | 0 | 0.05 | 0.05 | after grid resume Wtg in error so Checked related error data log then apply hard reboot then reset & start the WTG. | Close | 0.0019231 | O2-06 | 16.1729 |  | WTG Unscheduled Maintenance | 7763 | 16.1729
2706 | 2024-10-24 | 2025 | 2024 | 2024-10-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.33194 | 0.33194 | 0.33611 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2-06 | 32.3458 |  | WTG Unscheduled Maintenance | 7763 | 32.3458
2707 | 2024-10-24 | 2025 | 2024 | 2024-10-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.61458 | 0.61458 | 0.63194 | 0 | 0.41667 | 0.41667 | after grid resume Wtg in error so Checked related error data log then apply hard reboot then reset & start the WTG. | Close | 0.016026 | O2-06 | 134.7743 |  | WTG Unscheduled Maintenance | 7763 | 134.7743
2708 | 2024-10-24 | 2025 | 2024 | 2024-10-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 650 | Pitch controller communication error | Break down | 0.72569 | 0.72569 | 0.72917 | 0 | 0.083333 | 0.083333 | after grid resume Wtg in error so Checked related error data log then apply hard reboot then reset & start the WTG. | Close | 0.0032051 | O2-06 | 26.9549 |  | WTG Unscheduled Maintenance | 7763 | 26.9549
2709 | 2024-10-24 | 2025 | 2024 | 2024-10-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.61458 | 0.61458 | 0.64861 | 0 | 0.81667 | 0.81667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot and Error is not resolved so Another troubleshooting work WIP | Close | 0.03141 | O2-20 | 245.1701 |  | WTG Unscheduled Maintenance | 7205 | 245.1701
2710 | 2024-10-24 | 2025 | 2024 | 2024-10-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.72569 | 0.72569 | 0.72917 | 0 | 0.083333 | 0.083333 | after grid resume Wtg in error so Checked related error data log then apply hard reboot then reset & start the WTG. | Close | 0.0032051 | O2-20 | 25.0174 |  | WTG Unscheduled Maintenance | 7205 | 25.0174
2711 | 2024-10-25 | 2025 | 2024 | 2024-10-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 650 | Pitch controller communication error | Break down | 0.024306 | 0.024306 | 0.039583 | 0 | 0.36667 | 0.36667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.014103 | O2-21 | 122.0542 |  | WTG Unscheduled Maintenance | 7989 | 122.0542
2712 | 2024-10-25 | 2025 | 2024 | 2024-10-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 650 | Pitch controller communication error | Break down | 0.11458 | 0.11458 | 0.12014 | 0 | 0.13333 | 0.13333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0051282 | O2-21 | 44.3833 |  | WTG Unscheduled Maintenance | 7989 | 44.3833
2713 | 2024-10-25 | 2025 | 2024 | 2024-10-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 650 | Pitch controller communication error | Break down | 0.59028 | 0.59028 | 0.60625 | 0 | 0.38333 | 0.38333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.014744 | O2-21 | 127.6021 |  | WTG Unscheduled Maintenance | 7989 | 127.6021
2714 | 2024-10-25 | 2025 | 2024 | 2024-10-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.024306 | 0.024306 | 0.033333 | 0 | 0.21667 | 0.21667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0083333 | O2-04 | 66.2188 |  | WTG Unscheduled Maintenance | 7335 | 66.2188
2715 | 2024-10-25 | 2025 | 2024 | 2024-10-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.11458 | 0.11458 | 0.12431 | 0 | 0.23333 | 0.23333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0089744 | O2-04 | 71.3125 |  | WTG Unscheduled Maintenance | 7335 | 71.3125
2716 | 2024-10-25 | 2025 | 2024 | 2024-10-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.30069 | 0.30069 | 0.30903 | 0 | 0.2 | 0.2 | Checked related error data log then reset & run the WTG. | Close | 0.0076923 | O2-26 | 86.275 |  | WTG Unscheduled Maintenance | 10353 | 86.275
2717 | 2024-10-25 | 2025 | 2024 | 2024-10-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.42153 | 0.42153 | 0.68611 | 0 | 6.35 | 6.35 | Wtg manual stop for 1st month Maintenance work ( Day-2) | Close | 0.24423 | O2-26 | 2739.2312 |  | WTG Scheduled Maintenance | 10353 | 2739.2312
2718 | 2024-10-25 | 2025 | 2024 | 2024-10-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.81736 | 0.81736 | 1899-12-31 | 0 | 4.3833 | 4.3833 | wip | Close | 0.16859 | O2-26 | 1890.8604 |  | WTG Unscheduled Maintenance | 10353 | 1890.8604
2719 | 2024-10-25 | 2025 | 2024 | 2024-10-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.60486 | 0.60486 | 0.60833 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2-03 | 39.8125 |  | WTG Unscheduled Maintenance | 11466 | 39.8125
2720 | 2024-10-25 | 2025 | 2024 | 2024-10-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.024306 | 0.024306 | 0.038194 | 0 | 0.33333 | 0.33333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.012821 | O2-21 | 110.9583 |  | WTG Unscheduled Maintenance | 7989 | 110.9583
2721 | 2024-10-25 | 2025 | 2024 | 2024-10-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.10069 | 0.10069 | 0.12153 | 0 | 0.5 | 0.5 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.019231 | O2-21 | 166.4375 |  | WTG Unscheduled Maintenance | 7989 | 166.4375
2722 | 2024-10-25 | 2025 | 2024 | 2024-10-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.59028 | 0.59028 | 0.60208 | 0 | 0.28333 | 0.28333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.010897 | O2-21 | 94.3146 |  | WTG Unscheduled Maintenance | 7989 | 94.3146
2723 | 2024-10-25 | 2025 | 2024 | 2024-10-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.024306 | 0.024306 | 0.040278 | 0 | 0.38333 | 0.38333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.014744 | O2-06 | 122.491 |  | WTG Unscheduled Maintenance | 7669 | 122.491
2724 | 2024-10-25 | 2025 | 2024 | 2024-10-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.11458 | 0.11458 | 0.12361 | 0 | 0.21667 | 0.21667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0083333 | O2-06 | 69.234 |  | WTG Unscheduled Maintenance | 7669 | 69.234
2725 | 2024-10-25 | 2025 | 2024 | 2024-10-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.024306 | 0.024306 | 0.043056 | 0 | 0.45 | 0.45 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.017308 | O2-21 | 149.7937 |  | WTG Unscheduled Maintenance | 7989 | 149.7937
2726 | 2024-10-25 | 2025 | 2024 | 2024-10-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.11458 | 0.11458 | 0.13542 | 0 | 0.5 | 0.5 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.019231 | O2-21 | 166.4375 |  | WTG Unscheduled Maintenance | 7989 | 166.4375
2727 | 2024-10-25 | 2025 | 2024 | 2024-10-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.59028 | 0.59028 | 0.60625 | 0 | 0.38333 | 0.38333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.014744 | O2-21 | 127.6021 |  | WTG Unscheduled Maintenance | 7989 | 127.6021
2728 | 2024-10-25 | 2025 | 2024 | 2024-10-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.024306 | 0.024306 | 0.038194 | 0 | 0.33333 | 0.33333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.012821 | O2-24 | 97.8194 |  | WTG Unscheduled Maintenance | 7043 | 97.8194
2729 | 2024-10-25 | 2025 | 2024 | 2024-10-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.10069 | 0.10069 | 0.12917 | 0 | 0.68333 | 0.68333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.026282 | O2-24 | 200.5299 |  | WTG Unscheduled Maintenance | 7043 | 200.5299
2730 | 2024-10-25 | 2025 | 2024 | 2024-10-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.024306 | 0.024306 | 0.038194 | 0 | 0.33333 | 0.33333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.012821 | O2-24 | 97.8194 |  | WTG Unscheduled Maintenance | 7043 | 97.8194
2731 | 2024-10-25 | 2025 | 2024 | 2024-10-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.11458 | 0.11458 | 0.12569 | 0 | 0.26667 | 0.26667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.010256 | O2-06 | 85.2111 |  | WTG Unscheduled Maintenance | 7669 | 85.2111
2732 | 2024-10-25 | 2025 | 2024 | 2024-10-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.59028 | 0.59028 | 0.60069 | 0 | 0.25 | 0.25 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0096154 | O2-06 | 79.8854 |  | WTG Unscheduled Maintenance | 7669 | 79.8854
2733 | 2024-10-25 | 2025 | 2024 | 2024-10-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.024306 | 0.024306 | 0.0375 | 0 | 0.31667 | 0.31667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.012179 | O2-06 | 101.1882 |  | WTG Unscheduled Maintenance | 7669 | 101.1882
2734 | 2024-10-25 | 2025 | 2024 | 2024-10-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3060 | Conv. emerg.off type A | Break down | 0.11458 | 0.11458 | 0.12986 | 0 | 0.36667 | 0.36667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.014103 | O2-06 | 117.1653 |  | WTG Unscheduled Maintenance | 7669 | 117.1653
2735 | 2024-10-25 | 2025 | 2024 | 2024-10-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.024306 | 0.024306 | 0.035417 | 0 | 0.26667 | 0.26667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.010256 | O2-20 | 102.5111 |  | WTG Unscheduled Maintenance | 9226 | 102.5111
2736 | 2024-10-25 | 2025 | 2024 | 2024-10-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.11458 | 0.11458 | 0.12778 | 0 | 0.31667 | 0.31667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.012179 | O2-20 | 121.7319 |  | WTG Unscheduled Maintenance | 9226 | 121.7319
2737 | 2024-10-25 | 2025 | 2024 | 2024-10-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.51667 | 0.51667 | 0.53819 | 0 | 0.51667 | 0.51667 | wtg manul stop for rep error inspections work | Close | 0.019872 | O2-20 | 198.6153 |  | WTG Breakdown Maintenance | 9226 | 198.6153
2738 | 2024-10-25 | 2025 | 2024 | 2024-10-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.59028 | 0.59028 | 0.60069 | 0 | 0.25 | 0.25 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0096154 | O2-20 | 96.1042 |  | WTG Unscheduled Maintenance | 9226 | 96.1042
2739 | 2024-10-26 | 2025 | 2024 | 2024-10-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Connectivity issue | 0.39931 | 0.39931 | 0.42222 | 0 | 0.55 | 0.55 | after grid resume Wtg in error so Checked related error data log then reset and start(late start due to O2 08 vcb was tripped so connectivity lost.) | Close | 0.021154 | O2-26 | 15.5375 |  | WTG Unscheduled Maintenance | 678 | 15.5375
2740 | 2024-10-26 | 2025 | 2024 | 2024-10-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Connectivity issue | 0.76389 | 0.76389 | 0.82222 | 0 | 1.4 | 1.4 | after grid resume Wtg in error so Checked related error data log then reset and start(late start due to O2 08 vcb was tripped so connectivity lost.) | Close | 0.053846 | O2-26 | 39.55 |  | WTG Unscheduled Maintenance | 678 | 39.55
2741 | 2024-10-26 | 2025 | 2024 | 2024-10-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Connectivity issue | 0.39931 | 0.39931 | 0.41944 | 0 | 0.48333 | 0.48333 | after grid resume Wtg in error so Checked related error data log then reset and start(late start due to O2 08 vcb was tripped so connectivity lost.) | Close | 0.01859 | O2-05 | 13.7951 |  | WTG Unscheduled Maintenance | 685 | 13.7951
2742 | 2024-10-26 | 2025 | 2024 | 2024-10-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Connectivity issue | 0.76389 | 0.76389 | 0.80972 | 0 | 1.1 | 1.1 | after grid resume Wtg in error so Checked related error data log then reset and start(late start due to O2 08 vcb was tripped so connectivity lost.) | Close | 0.042308 | O2-05 | 31.3958 |  | WTG Unscheduled Maintenance | 685 | 31.3958
2743 | 2024-10-26 | 2025 | 2024 | 2024-10-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Connectivity issue | 0.39931 | 0.39931 | 0.42014 | 0 | 0.5 | 0.5 | after grid resume Wtg in error so Checked related error data log then reset and start(late start due to O2 08 vcb was tripped so connectivity lost.) | Close | 0.019231 | O2-09 | 19.4375 |  | WTG Unscheduled Maintenance | 933 | 19.4375
2744 | 2024-10-26 | 2025 | 2024 | 2024-10-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Connectivity issue | 0.76389 | 0.76389 | 0.80903 | 0 | 1.0833 | 1.0833 | after grid resume Wtg in error so Checked related error data log then reset and start(late start due to O2 08 vcb was tripped so connectivity lost.) | Close | 0.041667 | O2-09 | 42.1146 |  | WTG Unscheduled Maintenance | 933 | 42.1146
2745 | 2024-10-26 | 2025 | 2024 | 2024-10-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.35139 | 0.35139 | 0.35278 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-07 | 0.9625 |  | WTG Unscheduled Maintenance | 693 | 0.9625
2746 | 2024-10-26 | 2025 | 2024 | 2024-10-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Connectivity issue | 0.39931 | 0.39931 | 0.44375 | 0 | 1.0667 | 1.0667 | after grid resume Wtg in error so Checked related error data log then reset and start(late start due to O2 08 vcb was tripped so connectivity lost.) | Close | 0.041026 | O2-02 | 30.4 |  | WTG Unscheduled Maintenance | 684 | 30.4
2747 | 2024-10-26 | 2025 | 2024 | 2024-10-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.45139 | 0.45139 | 0.62361 | 0 | 4.1333 | 4.1333 | Wtg stop for 1st month mentenence Day-3 | Close | 0.15897 | O2-02 | 117.8 |  | WTG Scheduled Maintenance | 684 | 117.8
2748 | 2024-10-26 | 2025 | 2024 | 2024-10-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Connectivity issue | 0.76389 | 0.76389 | 0.81111 | 0 | 1.1333 | 1.1333 | after grid resume Wtg in error so Checked related error data log then reset and start(late start due to O2 08 vcb was tripped so connectivity lost.) | Close | 0.04359 | O2-02 | 32.3 |  | WTG Unscheduled Maintenance | 684 | 32.3
2749 | 2024-10-26 | 2025 | 2024 | 2024-10-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 1.1574e-05 | 1.1574e-05 | 0.048611 | 0 | 1.1664 | 1.1664 | attend and check related circuit and found Fc008 24v connection loose in axis 1 so retight and reset and start wtg | Close | 0.044861 | O2-26 | 32.9505 |  | WTG Unscheduled Maintenance | 678 | 32.9505
2750 | 2024-10-26 | 2025 | 2024 | 2024-10-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 550 | Pitch current asymmetry | Break down | 0.82847 | 0.82847 | 0.99999 | 0 | 4.1164 | 4.1164 | WTg In error so check related circuit in axis 2 check 24v supply than nothning found abnormal so further troublshooting WIP | open | 0.15832 | O2-26 | 116.288 |  | WTG Unscheduled Maintenance | 678 | 116.288
2751 | 2024-10-26 | 2025 | 2024 | 2024-10-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Connectivity issue | 0.76389 | 0.76389 | 0.77569 | 0 | 0.28333 | 0.28333 | after grid resume Wtg in error so Checked related error data log then reset and start(late start due to O2 08 vcb was tripped so connectivity lost.) | Close | 0.010897 | O2-03 | 8.0632 |  | WTG Unscheduled Maintenance | 683 | 8.0632
2752 | 2024-10-26 | 2025 | 2024 | 2024-10-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Break down | 0.39931 | 0.39931 | 0.40139 | 0 | 0.05 | 0.05 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0019231 | O2-15 | 1.6375 |  | WTG Unscheduled Maintenance | 786 | 1.6375
2753 | 2024-10-26 | 2025 | 2024 | 2024-10-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Break down | 0.39931 | 0.39931 | 0.40556 | 0 | 0.15 | 0.15 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0057692 | O2-14 | 4.0187 |  | WTG Unscheduled Maintenance | 643 | 4.0187
2754 | 2024-10-26 | 2025 | 2024 | 2024-10-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.39931 | 0.39931 | 0.40417 | 0 | 0.11667 | 0.11667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0044872 | O2-12 | 4.7542 |  | WTG Unscheduled Maintenance | 978 | 4.7542
2755 | 2024-10-26 | 2025 | 2024 | 2024-10-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Break down | 0.76389 | 0.76389 | 0.78681 | 0 | 0.55 | 0.55 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.021154 | O2-12 | 22.4125 |  | WTG Unscheduled Maintenance | 978 | 22.4125
2756 | 2024-10-26 | 2025 | 2024 | 2024-10-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.74028 | 0.74028 | 0.74167 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-06 | 1.4944 |  | WTG Unscheduled Maintenance | 1076 | 1.4944
2757 | 2024-10-26 | 2025 | 2024 | 2024-10-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Connectivity issue | 0.39931 | 0.39931 | 0.42361 | 0 | 0.58333 | 0.58333 | after grid resume Wtg in error so Checked related error data log then reset and start(late start due to O2 08 vcb was tripped so connectivity lost.) | Close | 0.022436 | O2-25 | 18.3993 |  | WTG Unscheduled Maintenance | 757 | 18.3993
2758 | 2024-10-26 | 2025 | 2024 | 2024-10-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Connectivity issue | 0.59028 | 0.59028 | 0.82222 | 0 | 5.5667 | 5.5667 | after grid resume Wtg in error so Checked related error data log then reset and start(late start due to O2 08 vcb was tripped so connectivity lost.) | Close | 0.2141 | O2-25 | 175.5819 |  | WTG Unscheduled Maintenance | 757 | 175.5819
2759 | 2024-10-26 | 2025 | 2024 | 2024-10-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Major BD | 0.39931 | 0.39931 | 0.6375 | 0 | 5.7167 | 5.7167 | after grid resume wtg in error so check related circuit than check blad limit switch connection and retight all connection and apply hard rebbot than reset and startWTg. | Close | 0.21987 | O2-01 | 190.7937 |  | WTG Unscheduled Maintenance | 801 | 190.7937
2760 | 2024-10-26 | 2025 | 2024 | 2024-10-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.76389 | 0.76389 | 0.82708 | 0 | 1.5167 | 1.5167 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.058333 | O2-01 | 50.6187 |  | WTG Unscheduled Maintenance | 801 | 50.6187
2761 | 2024-10-26 | 2025 | 2024 | 2024-10-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0 | 0 | 0.90764 | 0 | 21.7833 | 21.7833 | After Geda commissioning done than start WTG. | Close | 0.83782 | O2-11 | 661.6687 |  | WTG Breakdown Maintenance | 729 | 661.6687
2762 | 2024-10-27 | 2025 | 2024 | 2024-10-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.072222 | 0.072222 | 0.073611 | 0 | 0.033333 | 0.033333 | auto reset | Close | 0.0012821 | O2-05 | 11.2264 |  | WTG Unscheduled Maintenance | 8083 | 11.2264
2763 | 2024-10-27 | 2025 | 2024 | 2024-10-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.30903 | 0.30903 | 0.77917 | 0 | 11.2833 | 11.2833 | Wtg manual stop for 1st month Maintenance work | Close | 0.43397 | O2-05 | 3800.1326 |  | WTG Scheduled Maintenance | 8083 | 3800.1326
2764 | 2024-10-27 | 2025 | 2024 | 2024-10-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 550 | Pitch current asymmetry | Break down | 0 | 0 | 0.088889 | 0 | 2.1333 | 2.1333 | During troubleshooting found axis2 blade angle 92 and so manual pitching and recalibrations done and blade engle Limit Switch NO NC contact retight then start wtg. | Close | 0.082051 | O2-26 | 623.9111 |  | WTG Unscheduled Maintenance | 7019 | 623.9111
2765 | 2024-10-27 | 2025 | 2024 | 2024-10-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Major BD | 0.12153 | 0.12153 | 0.65 | 0 | 12.6833 | 12.6833 | attend and found hydraulic unit is not Build up Pressure so check found 9.1 valve is faulty so material arrangement for another site and replace it then start WTG. | Close | 0.48782 | O2-26 | 3709.3465 |  | WTG Unscheduled Maintenance | 7019 | 3709.3465
2766 | 2024-10-27 | 2025 | 2024 | 2024-10-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 88 | Outs.temp. nacelle implaus. | Break down | 0.54583 | 0.54583 | 0.72431 | 0 | 4.2833 | 4.2833 | attend and found nacelle out door temp sansor on Loose connections so tight it then start wg.(Late attend due to multiple breakdown on site ) | Close | 0.16474 | O2-12 | 1169.1715 |  | WTG Unscheduled Maintenance | 6551 | 1169.1715
2767 | 2024-10-27 | 2025 | 2024 | 2024-10-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.093056 | 0.093056 | 0.13819 | 0 | 1.0833 | 1.0833 | After VCB charge time Converter RFO (CAN) Singnal not come so After single available then reset and start wtg | Close | 0.041667 | O2-06 | 251.6042 |  | WTG Unscheduled Maintenance | 5574 | 251.6042
2768 | 2024-10-27 | 2025 | 2024 | 2024-10-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 2687 | Max. slip ring cell temp. | Break down | 0.55347 | 0.55347 | 0.60208 | 0 | 1.1667 | 1.1667 | after slipring cell temp is normal then start wtg | Close | 0.044872 | O2-06 | 270.9583 |  | WTG Unscheduled Maintenance | 5574 | 270.9583
2769 | 2024-10-27 | 2025 | 2024 | 2024-10-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 2687 | Max. slip ring cell temp. | Break down | 0.55556 | 0.55556 | 0.6 | 0 | 1.0667 | 1.0667 | after slipring cell temp is normal then start wtg | Close | 0.041026 | O2-01 | 325.9111 |  | WTG Unscheduled Maintenance | 7333 | 325.9111
2770 | 2024-10-27 | 2025 | 2024 | 2024-10-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3555 | Current asymmetry | Project pending work | 0.20833 | 0.20833 | 0.48333 | 0 | 6.6 | 6.6 | attend by project team check and found power panel CT cannections is loose so tight then start wtg.now wtg . | Close | 0.25385 | O2-11 | 1542.75 |  | WTG Unscheduled Maintenance | 5610 | 1542.75
2771 | 2024-10-27 | 2025 | 2024 | 2024-10-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3555 | Current asymmetry | Project pending work | 0.65139 | 0.65139 | 0.71736 | 0 | 1.5833 | 1.5833 | wtg manul stop for project team for repeated error inspections work | Close | 0.060897 | O2-11 | 370.1042 |  | WTG Unscheduled Maintenance | 5610 | 370.1042
2772 | 2024-10-28 | 2025 | 2024 | 2024-10-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Auto reset | 0.76042 | 0.76042 | 0.7625 | 0 | 0.05 | 0.05 | auto reset | Close | 0.0019231 | O2-07 | 16.4062 |  | WTG Unscheduled Maintenance | 7875 | 16.4062
2773 | 2024-10-28 | 2025 | 2024 | 2024-10-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.86806 | 0.86806 | 0.86944 | 0 | 0.033333 | 0.033333 | auto reset | Close | 0.0012821 | O2-07 | 10.9375 |  | WTG Unscheduled Maintenance | 7875 | 10.9375
2774 | 2024-10-28 | 2025 | 2024 | 2024-10-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 155 | Incorrect Error Code | Break down | 0.60764 | 0.60764 | 0.61389 | 0 | 0.15 | 0.15 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0057692 | O2-21 | 62.2375 |  | WTG Unscheduled Maintenance | 9958 | 62.2375
2775 | 2024-10-28 | 2025 | 2024 | 2024-10-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.60764 | 0.60764 | 0.625 | 0 | 0.41667 | 0.41667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.016026 | O2-21 | 172.8819 |  | WTG Unscheduled Maintenance | 9958 | 172.8819
2776 | 2024-10-28 | 2025 | 2024 | 2024-10-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.60764 | 0.60764 | 0.625 | 0 | 0.41667 | 0.41667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.016026 | O2-07 | 136.7188 |  | WTG Unscheduled Maintenance | 7875 | 136.7188
2777 | 2024-10-28 | 2025 | 2024 | 2024-10-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.60764 | 0.60764 | 0.62014 | 0 | 0.3 | 0.3 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.011538 | O2-24 | 136.3625 |  | WTG Unscheduled Maintenance | 10909 | 136.3625
2778 | 2024-10-28 | 2025 | 2024 | 2024-10-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.60764 | 0.60764 | 0.61806 | 0 | 0.25 | 0.25 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0096154 | O2-06 | 116.8542 |  | WTG Unscheduled Maintenance | 11218 | 116.8542
2779 | 2024-10-28 | 2025 | 2024 | 2024-10-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.019444 | 0.019444 | 0.021528 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-06 | 23.3708 |  | WTG Unscheduled Maintenance | 11218 | 23.3708
2780 | 2024-10-28 | 2025 | 2024 | 2024-10-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.15903 | 0.15903 | 0.17292 | 0 | 0.33333 | 0.33333 | Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.012821 | O2-06 | 155.8056 |  | WTG Unscheduled Maintenance | 11218 | 155.8056
2781 | 2024-10-28 | 2025 | 2024 | 2024-10-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.60764 | 0.60764 | 0.61875 | 0 | 0.26667 | 0.26667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.010256 | O2-06 | 124.6444 |  | WTG Unscheduled Maintenance | 11218 | 124.6444
2782 | 2024-10-28 | 2025 | 2024 | 2024-10-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 2687 | Max. slip ring cell temp. | Break down | 0.44306 | 0.44306 | 0.48681 | 0 | 1.05 | 1.05 | after slipring cell temp is normal then start wtg | Close | 0.040385 | O2-11 | 499.1 |  | WTG Unscheduled Maintenance | 11408 | 499.1
2783 | 2024-10-28 | 2025 | 2024 | 2024-10-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 1731 | Oil temperature gearbox input high | Break down | 0.67292 | 0.67292 | 0.86458 | 0 | 4.6 | 4.6 | Attend by commissioning team check temperature sensor ohm's value is ok check cable laying Found module side cable is not proper fix it so fix it proper then reset and start wtg. | Close | 0.17692 | O2-11 | 2186.5333 |  | WTG Unscheduled Maintenance | 11408 | 2186.5333
2784 | 2024-10-28 | 2025 | 2024 | 2024-10-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 2687 | Max. slip ring cell temp. | Break down | 0.43125 | 0.43125 | 0.47153 | 0 | 0.96667 | 0.96667 | after slipring cell temp is normal then start wtg | Close | 0.037179 | O2-20 | 411.5181 |  | WTG Unscheduled Maintenance | 10217 | 411.5181
2785 | 2024-10-28 | 2025 | 2024 | 2024-10-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.60764 | 0.60764 | 0.61944 | 0 | 0.28333 | 0.28333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.010897 | O2-20 | 120.6174 |  | WTG Unscheduled Maintenance | 10217 | 120.6174
2786 | 2024-10-29 | 2025 | 2024 | 2024-10-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.31736 | 0.31736 | 0.325 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & run the WTG. | Close | 0.0070513 | O2-26 | 57.6889 |  | WTG Unscheduled Maintenance | 7552 | 57.6889
2787 | 2024-10-29 | 2025 | 2024 | 2024-10-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Auto reset | 0.60556 | 0.60556 | 0.60694 | 0 | 0.033333 | 0.033333 | auto reset | Close | 0.0012821 | O2-05 | 15.2014 |  | WTG Unscheduled Maintenance | 10945 | 15.2014
2788 | 2024-10-29 | 2025 | 2024 | 2024-10-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.62778 | 0.62778 | 0.63125 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2-07 | 25.5972 |  | WTG Unscheduled Maintenance | 7372 | 25.5972
2789 | 2024-10-29 | 2025 | 2024 | 2024-10-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.42778 | 0.42778 | 0.51319 | 0 | 2.05 | 2.05 | Wtg manual stop for 1st month Maintenance pending work. | Close | 0.078846 | O2-04 | 777.4625 |  | WTG Scheduled Maintenance | 9102 | 777.4625
2790 | 2024-10-29 | 2025 | 2024 | 2024-10-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.31319 | 0.31319 | 0.31458 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-11 | 8.6472 |  | WTG Unscheduled Maintenance | 6226 | 8.6472
2791 | 2024-10-29 | 2025 | 2024 | 2024-10-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 1732 | Max. oil temperature gearbox input | Break down | 0.52083 | 0.52083 | 0.64028 | 0 | 2.8667 | 2.8667 | Attend by commissioning team check temperature sensor ohm's value is ok so found modual malfunctioning so apply Soft reboot Then reset and Start WTG | Close | 0.11026 | O2-11 | 743.6611 |  | WTG Unscheduled Maintenance | 6226 | 743.6611
2792 | 2024-10-29 | 2025 | 2024 | 2024-10-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.72917 | 0.72917 | 0.76667 | 0 | 0.9 | 0.9 | Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.034615 | O2-01 | 323.4375 |  | WTG Unscheduled Maintenance | 8625 | 323.4375
2793 | 2024-10-29 | 2025 | 2024 | 2024-10-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.80278 | 0.80278 | 0.83194 | 0 | 0.7 | 0.7 | Checked related error data log then so apply manual DO and found all Condition is ok so reset & start WTG. | Close | 0.026923 | O2-01 | 251.5625 |  | WTG Unscheduled Maintenance | 8625 | 251.5625
2794 | 2024-10-30 | 2025 | 2024 | 2024-10-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.67431 | 0.67431 | 0.67639 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-10 | 10.7521 |  | WTG Unscheduled Maintenance | 5161 | 10.7521
2795 | 2024-10-30 | 2025 | 2024 | 2024-10-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.68333 | 0.68333 | 0.68542 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-10 | 10.7521 |  | WTG Unscheduled Maintenance | 5161 | 10.7521
2796 | 2024-10-30 | 2025 | 2024 | 2024-10-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 2687 | Max. slip ring cell temp. | Break down | 0.47986 | 0.47986 | 0.48403 | 0 | 0.1 | 0.1 | after slipring cell temp is normal then start wtg | Close | 0.0038462 | O2-06 | 20.1 |  | WTG Unscheduled Maintenance | 4824 | 20.1
2797 | 2024-10-31 | 2025 | 2024 | 2024-10-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Auto reset | 0.96944 | 0.96944 | 0.97153 | 0 | 0.05 | 0.05 | auto reset | Close | 0.0019231 | O2-05 | 27.3312 |  | WTG Unscheduled Maintenance | 13119 | 27.3312
2798 | 2024-10-31 | 2025 | 2024 | 2024-10-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.37569 | 0.37569 | 0.37778 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-10 | 25.2229 |  | WTG Unscheduled Maintenance | 12107 | 25.2229
2799 | 2024-10-31 | 2025 | 2024 | 2024-10-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.38403 | 0.38403 | 0.38681 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & run the WTG. | Close | 0.0025641 | O2-10 | 33.6306 |  | WTG Unscheduled Maintenance | 12107 | 33.6306
2800 | 2024-10-31 | 2025 | 2024 | 2024-10-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.39444 | 0.39444 | 0.43542 | 0 | 0.98333 | 0.98333 | Checked related error data log and all Ingeteam Perameter check by Engineering team then apply soft reboot then reset & start the WTG. | Close | 0.037821 | O2-10 | 496.0507 |  | WTG Unscheduled Maintenance | 12107 | 496.0507
2801 | 2024-10-31 | 2025 | 2024 | 2024-10-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.24444 | 0.24444 | 0.24583 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-06 | 11.6194 |  | WTG Unscheduled Maintenance | 8366 | 11.6194
2802 | 2024-10-31 | 2025 | 2024 | 2024-10-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.15972 | 0.15972 | 0.16111 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-11 | 17.2222 |  | WTG Unscheduled Maintenance | 12400 | 17.2222
2803 | 2024-11-01 | 2025 | 2024 | 2024-11-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.38958 | 0.38958 | 0.39097 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-05 | 9.6583 |  | WTG Unscheduled Maintenance | 6954 | 9.6583
2804 | 2024-11-01 | 2025 | 2024 | 2024-11-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.10347 | 0.10347 | 0.10556 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-07 | 8.7521 |  | WTG Unscheduled Maintenance | 4201 | 8.7521
2805 | 2024-11-01 | 2025 | 2024 | 2024-11-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.31528 | 0.31528 | 0.31667 | 0 | 0.033333 | 0.033333 | auto reset | Close | 0.0012821 | O2-07 | 5.8347 |  | WTG Unscheduled Maintenance | 4201 | 5.8347
2806 | 2024-11-01 | 2025 | 2024 | 2024-11-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.60903 | 0.60903 | 0.61111 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-07 | 8.7521 |  | WTG Unscheduled Maintenance | 4201 | 8.7521
2807 | 2024-11-01 | 2025 | 2024 | 2024-11-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 6056 | High yaw load | Break down | 0.50347 | 0.50347 | 0.50625 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & run the WTG. | Close | 0.0025641 | O2-03 | 22.5639 |  | WTG Unscheduled Maintenance | 8123 | 22.5639
2808 | 2024-11-01 | 2025 | 2024 | 2024-11-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 2687 | Max. slip ring cell temp. | Break down | 0.52222 | 0.52222 | 0.55278 | 0 | 0.73333 | 0.73333 | after slipring cell temp is normal then start wtg | Close | 0.028205 | O2-03 | 248.2028 |  | WTG Unscheduled Maintenance | 8123 | 248.2028
2809 | 2024-11-01 | 2025 | 2024 | 2024-11-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 2687 | Max. slip ring cell temp. | Break down | 0.94722 | 0.94722 | 0.96319 | 0 | 0.38333 | 0.38333 | after slipring cell temp is normal then start wtg | Close | 0.014744 | O2-03 | 129.7424 |  | WTG Unscheduled Maintenance | 8123 | 129.7424
2810 | 2024-11-01 | 2025 | 2024 | 2024-11-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.81458 | 0.81458 | 0.81597 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-14 | 8.7444 |  | WTG Unscheduled Maintenance | 6296 | 8.7444
2811 | 2024-11-01 | 2025 | 2024 | 2024-11-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.12361 | 0.12361 | 0.12569 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-06 | 8.0146 |  | WTG Unscheduled Maintenance | 3847 | 8.0146
2812 | 2024-11-01 | 2025 | 2024 | 2024-11-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.14722 | 0.14722 | 0.15347 | 0 | 0.15 | 0.15 | Checked related error data log then reset & run the WTG. | Close | 0.0057692 | O2-06 | 24.0438 |  | WTG Unscheduled Maintenance | 3847 | 24.0438
2813 | 2024-11-01 | 2025 | 2024 | 2024-11-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.42917 | 0.42917 | 0.43056 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-06 | 5.3431 |  | WTG Unscheduled Maintenance | 3847 | 5.3431
2814 | 2024-11-01 | 2025 | 2024 | 2024-11-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.76875 | 0.76875 | 0.77014 | 0 | 0.033333 | 0.033333 | auto reset | Close | 0.0012821 | O2-11 | 9.9056 |  | WTG Unscheduled Maintenance | 7132 | 9.9056
2815 | 2024-11-01 | 2025 | 2024 | 2024-11-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.79722 | 0.79722 | 0.79792 | 0 | 0.016667 | 0.016667 | auto reset | Close | 0.00064103 | O2-11 | 4.9528 |  | WTG Unscheduled Maintenance | 7132 | 4.9528
2816 | 2024-11-01 | 2025 | 2024 | 2024-11-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 2687 | Max. slip ring cell temp. | Break down | 0.49514 | 0.49514 | 0.55764 | 0 | 1.5 | 1.5 | after slipring cell temp is normal then start wtg | Close | 0.057692 | O2-20 | 300.1875 |  | WTG Unscheduled Maintenance | 4803 | 300.1875
2817 | 2024-11-01 | 2025 | 2024 | 2024-11-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 2687 | Max. slip ring cell temp. | Break down | 0.89028 | 0.89028 | 0.90625 | 0 | 0.38333 | 0.38333 | after slipring cell temp is normal then start wtg | Close | 0.014744 | O2-20 | 76.7146 |  | WTG Unscheduled Maintenance | 4803 | 76.7146
2818 | 2024-11-02 | 2025 | 2024 | 2024-11-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Break down | 0.54653 | 0.54653 | 0.55556 | 0 | 0.21667 | 0.21667 | Checked related error data log then reset & run the WTG. | Close | 0.0083333 | O2-04 | 13.7132 |  | WTG Unscheduled Maintenance | 1519 | 13.7132
2819 | 2024-11-02 | 2025 | 2024 | 2024-11-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.23819 | 0.23819 | 0.25278 | 0 | 0.35 | 0.35 | Checked related error data log then reset & run the WTG. | Close | 0.013462 | O2-06 | 15.4729 |  | WTG Unscheduled Maintenance | 1061 | 15.4729
2820 | 2024-11-02 | 2025 | 2024 | 2024-11-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.71528 | 0.71528 | 0.72431 | 0 | 0.21667 | 0.21667 | Checked related error data log then reset & run the WTG. | Close | 0.0083333 | O2-01 | 16.9181 |  | WTG Unscheduled Maintenance | 1874 | 16.9181
2821 | 2024-11-03 | 2025 | 2024 | 2024-11-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.32292 | 0.32292 | 0.33194 | 0 | 0.21667 | 0.21667 | Checked related error data log then reset & run the WTG. | Close | 0.0083333 | O2-26 | 13.316 |  | WTG Unscheduled Maintenance | 1475 | 13.316
2822 | 2024-11-03 | 2025 | 2024 | 2024-11-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.98681 | 0.98681 | 0.98819 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-21 | 3.5792 |  | WTG Unscheduled Maintenance | 2577 | 3.5792
2823 | 2024-11-03 | 2025 | 2024 | 2024-11-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Break down | 0.32222 | 0.32222 | 0.34306 | 0 | 0.5 | 0.5 | Checked related error data log then reset & run the WTG. | Close | 0.019231 | O2-26 | 30.7292 |  | WTG Unscheduled Maintenance | 1475 | 30.7292
2824 | 2024-11-03 | 2025 | 2024 | 2024-11-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Break down | 0.35 | 0.35 | 0.38264 | 0 | 0.78333 | 0.78333 | Checked related error data log then reset & run the WTG. | Close | 0.030128 | O2-26 | 48.1424 |  | WTG Unscheduled Maintenance | 1475 | 48.1424
2825 | 2024-11-03 | 2025 | 2024 | 2024-11-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Break down | 0.38542 | 0.38542 | 0.39514 | 0 | 0.23333 | 0.23333 | Checked related error data log Reboot then reset & run the WTG. | Close | 0.0089744 | O2-26 | 14.3403 |  | WTG Unscheduled Maintenance | 1475 | 14.3403
2826 | 2024-11-03 | 2025 | 2024 | 2024-11-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.49653 | 0.49653 | 0.53264 | 0 | 0.86667 | 0.86667 | Checked related error data log than discuss with Ingteam person than Reboot then reset & run the WTG. | Close | 0.033333 | O2-15 | 65.7583 |  | WTG Unscheduled Maintenance | 1821 | 65.7583
2827 | 2024-11-03 | 2025 | 2024 | 2024-11-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.32431 | 0.32431 | 0.33542 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2-12 | 23.6 |  | WTG Unscheduled Maintenance | 2124 | 23.6
2828 | 2024-11-03 | 2025 | 2024 | 2024-11-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.31458 | 0.31458 | 0.31667 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-06 | 5.8646 |  | WTG Unscheduled Maintenance | 2815 | 5.8646
2829 | 2024-11-03 | 2025 | 2024 | 2024-11-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.72708 | 0.72708 | 0.72847 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-06 | 3.9097 |  | WTG Unscheduled Maintenance | 2815 | 3.9097
2830 | 2024-11-04 | 2025 | 2024 | 2024-11-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.029861 | 0.029861 | 0.031944 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-05 | 2.9125 |  | WTG Unscheduled Maintenance | 1398 | 2.9125
2831 | 2024-11-04 | 2025 | 2024 | 2024-11-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.08125 | 0.08125 | 0.088194 | 0 | 0.16667 | 0.16667 | Checked related error data log then reset & run the WTG. | Close | 0.0064103 | O2-04 | 10.6944 |  | WTG Unscheduled Maintenance | 1540 | 10.6944
2832 | 2024-11-04 | 2025 | 2024 | 2024-11-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.48125 | 0.48125 | 0.48264 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-15 | 2.0431 |  | WTG Unscheduled Maintenance | 1471 | 2.0431
2833 | 2024-11-04 | 2025 | 2024 | 2024-11-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.5625 | 0.5625 | 0.56389 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-15 | 2.0431 |  | WTG Unscheduled Maintenance | 1471 | 2.0431
2834 | 2024-11-04 | 2025 | 2024 | 2024-11-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 2687 | Max. slip ring cell temp. | Break down | 0.77292 | 0.77292 | 0.80417 | 0 | 0.75 | 0.75 | after slipring cell temp is normal then start wtg | Close | 0.028846 | O2-06 | 56.3438 |  | WTG Unscheduled Maintenance | 1803 | 56.3438
2835 | 2024-11-04 | 2025 | 2024 | 2024-11-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.77014 | 0.77014 | 0.77083 | 0 | 0.016667 | 0.016667 | auto reset | Close | 0.00064103 | O2-11 | 0.74167 |  | WTG Unscheduled Maintenance | 1068 | 0.74167
2836 | 2024-11-05 | 2025 | 2024 | 2024-11-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.4625 | 0.4625 | 0.54653 | 0 | 2.0167 | 2.0167 | WTG Manual stop for Converter new software testing work and also coolent pressure low so coolent fill up than reset and start WTG. | Close | 0.077564 | O2-26 | 803.9778 |  | WTG Breakdown Maintenance | 9568 | 803.9778
2837 | 2024-11-05 | 2025 | 2024 | 2024-11-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Auto reset | 0.022917 | 0.022917 | 0.024306 | 0 | 0.033333 | 0.033333 | auto reset | Close | 0.0012821 | O2-05 | 11.5569 |  | WTG Unscheduled Maintenance | 8321 | 11.5569
2838 | 2024-11-05 | 2025 | 2024 | 2024-11-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.16667 | 0.16667 | 0.16736 | 0 | 0.016667 | 0.016667 | auto reset | Close | 0.00064103 | O2-05 | 5.7785 |  | WTG Unscheduled Maintenance | 8321 | 5.7785
2839 | 2024-11-05 | 2025 | 2024 | 2024-11-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.38403 | 0.38403 | 0.39583 | 0 | 0.28333 | 0.28333 | Checked related error data log then reset & run the WTG. | Close | 0.010897 | O2-07 | 102.6493 |  | WTG Unscheduled Maintenance | 8695 | 102.6493
2840 | 2024-11-05 | 2025 | 2024 | 2024-11-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.60764 | 0.60764 | 0.60903 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-07 | 12.0764 |  | WTG Unscheduled Maintenance | 8695 | 12.0764
2841 | 2024-11-05 | 2025 | 2024 | 2024-11-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.20417 | 0.20417 | 0.20486 | 0 | 0.016667 | 0.016667 | auto reset | Close | 0.00064103 | O2-14 | 5.4882 |  | WTG Unscheduled Maintenance | 7903 | 5.4882
2842 | 2024-11-05 | 2025 | 2024 | 2024-11-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.58264 | 0.58264 | 0.58403 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-14 | 10.9764 |  | WTG Unscheduled Maintenance | 7903 | 10.9764
2843 | 2024-11-05 | 2025 | 2024 | 2024-11-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Break down | 0.25 | 0.25 | 0.39583 | 0 | 3.5 | 3.5 | Attend and check error related ckt than found axis 3 Flat resistor faulty so replace with new one. | Close | 0.13462 | O2-06 | 812.4375 |  | WTG Unscheduled Maintenance | 5571 | 812.4375
2844 | 2024-11-05 | 2025 | 2024 | 2024-11-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.84375 | 0.84375 | 0.84514 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-06 | 7.7375 |  | WTG Unscheduled Maintenance | 5571 | 7.7375
2845 | 2024-11-05 | 2025 | 2024 | 2024-11-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.059722 | 0.059722 | 0.061111 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-06 | 7.7375 |  | WTG Unscheduled Maintenance | 5571 | 7.7375
2846 | 2024-11-05 | 2025 | 2024 | 2024-11-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.81875 | 0.81875 | 0.82014 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-06 | 7.7375 |  | WTG Unscheduled Maintenance | 5571 | 7.7375
2847 | 2024-11-05 | 2025 | 2024 | 2024-11-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.30625 | 0.30625 | 0.31944 | 0 | 0.31667 | 0.31667 | Checked related error data log then reset & run the WTG. | Close | 0.012179 | O2-06 | 73.5062 |  | WTG Unscheduled Maintenance | 5571 | 73.5062
2848 | 2024-11-05 | 2025 | 2024 | 2024-11-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 2687 | Max. slip ring cell temp. | Break down | 0.61111 | 0.61111 | 0.70625 | 0 | 2.2833 | 2.2833 | Attend and check error related ckt than found loose connection in TB so retight it than reset and start WTG. | Close | 0.087821 | O2-06 | 530.0187 |  | WTG Unscheduled Maintenance | 5571 | 530.0187
2849 | 2024-11-05 | 2025 | 2024 | 2024-11-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.038889 | 0.038889 | 0.041667 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & run the WTG. | Close | 0.0025641 | O2-11 | 22.1639 |  | WTG Unscheduled Maintenance | 7979 | 22.1639
2850 | 2024-11-05 | 2025 | 2024 | 2024-11-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.18056 | 0.18056 | 0.20486 | 0 | 0.58333 | 0.58333 | Checked related error data log and check perameter than reboot then reset & run the WTG. | Close | 0.022436 | O2-11 | 193.934 |  | WTG Unscheduled Maintenance | 7979 | 193.934
2851 | 2024-11-05 | 2025 | 2024 | 2024-11-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 550 | Pitch current asymmetry | Break down | 0.20556 | 0.20556 | 0.22153 | 0 | 0.38333 | 0.38333 | Checked related error data log and check perameter than reboot then reset & run the WTG. | Close | 0.014744 | O2-11 | 127.4424 |  | WTG Unscheduled Maintenance | 7979 | 127.4424
2852 | 2024-11-05 | 2025 | 2024 | 2024-11-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.30903 | 0.30903 | 0.31944 | 0 | 0.25 | 0.25 | Checked related error data log then reset & run the WTG. | Close | 0.0096154 | O2-11 | 83.1146 |  | WTG Unscheduled Maintenance | 7979 | 83.1146
2853 | 2024-11-05 | 2025 | 2024 | 2024-11-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.35972 | 0.35972 | 0.36111 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-11 | 11.0819 |  | WTG Unscheduled Maintenance | 7979 | 11.0819
2854 | 2024-11-06 | 2025 | 2024 | 2024-11-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.59722 | 0.59722 | 0.59861 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-05 | 17.1389 |  | WTG Unscheduled Maintenance | 12340 | 17.1389
2855 | 2024-11-06 | 2025 | 2024 | 2024-11-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.60625 | 0.60625 | 0.60764 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-05 | 17.1389 |  | WTG Unscheduled Maintenance | 12340 | 17.1389
2856 | 2024-11-06 | 2025 | 2024 | 2024-11-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.17153 | 0.17153 | 0.17292 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-07 | 11.8986 |  | WTG Unscheduled Maintenance | 8567 | 11.8986
2857 | 2024-11-06 | 2025 | 2024 | 2024-11-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.62014 | 0.62014 | 0.62083 | 0 | 0.016667 | 0.016667 | auto reset | Close | 0.00064103 | O2-07 | 5.9493 |  | WTG Unscheduled Maintenance | 8567 | 5.9493
2858 | 2024-11-06 | 2025 | 2024 | 2024-11-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.90764 | 0.90764 | 0.90903 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-21 | 11.3167 |  | WTG Unscheduled Maintenance | 8148 | 11.3167
2858 | 2024-11-06 | 2025 | 2024 | 2024-11-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.45625 | 0.45625 | 0.60833 | 0 | 3.65 | 3.65 | Wtg Manual stop for Nacelle position warning check and found sensor 6 Degree out so set properly and slip ring cell temprature error check ckt than reset and start WTG | Close | 0.14038 | O2-03 | 1991.2271 |  | WTG Breakdown Maintenance | 13093 | 1991.2271
2859 | 2024-11-06 | 2025 | 2024 | 2024-11-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.44375 | 0.44375 | 0.50972 | 0 | 1.5833 | 1.5833 | WTG Manual stop for Converter new software testing work than reset and start WTG. | Close | 0.060897 | O2-12 | 719.0312 |  | WTG Breakdown Maintenance | 10899 | 719.0312
2860 | 2024-11-06 | 2025 | 2024 | 2024-11-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.48333 | 0.48333 | 0.48472 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-06 | 10.2708 |  | WTG Unscheduled Maintenance | 7395 | 10.2708
2861 | 2024-11-06 | 2025 | 2024 | 2024-11-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Major BD | 0.48889 | 0.48889 | 0.78333 | 0 | 7.0667 | 7.0667 | Attend and found axis 3 Encoder connector cable broken so correct it and also rectification error pitch exis 2 current asymmetry error and max slipring cell temp and repeated error CAN communication error than reset and start WTG. | Close | 0.27179 | O2-11 | 3261.2667 |  | WTG Unscheduled Maintenance | 11076 | 3261.2667
2862 | 2024-11-06 | 2025 | 2024 | 2024-11-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.77083 | 0.77083 | 0.77986 | 0 | 0.21667 | 0.21667 | Checked related error data log then reset & run the WTG. | Close | 0.0083333 | O2-20 | 78.9389 |  | WTG Unscheduled Maintenance | 8744 | 78.9389
2863 | 2024-11-06 | 2025 | 2024 | 2024-11-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.37361 | 0.37361 | 0.38681 | 0 | 0.31667 | 0.31667 | Checked related error data log then reset & run the WTG. | Close | 0.012179 | O2-01 | 177.3069 |  | WTG Unscheduled Maintenance | 13438 | 177.3069
2864 | 2024-11-07 | 2025 | 2024 | 2024-11-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.79931 | 0.79931 | 0.80069 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-05 | 15.4597 |  | WTG Unscheduled Maintenance | 11131 | 15.4597
2865 | 2024-11-07 | 2025 | 2024 | 2024-11-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.96528 | 0.96528 | 0.96667 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-05 | 15.4597 |  | WTG Unscheduled Maintenance | 11131 | 15.4597
2866 | 2024-11-07 | 2025 | 2024 | 2024-11-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.038194 | 0.038194 | 0.040278 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-07 | 15.2375 |  | WTG Unscheduled Maintenance | 7314 | 15.2375
2867 | 2024-11-07 | 2025 | 2024 | 2024-11-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.64583 | 0.64583 | 0.66875 | 0 | 0.55 | 0.55 | Checked related error data log and check perameter than reboot then reset & run the WTG. | Close | 0.021154 | O2-04 | 202.1021 |  | WTG Unscheduled Maintenance | 8819 | 202.1021
2868 | 2024-11-07 | 2025 | 2024 | 2024-11-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.41875 | 0.41875 | 0.42986 | 0 | 0.26667 | 0.26667 | Checked related error data log and check perameter than reboot then reset & run the WTG. | Close | 0.010256 | O2-06 | 105.3 |  | WTG Unscheduled Maintenance | 9477 | 105.3
2869 | 2024-11-07 | 2025 | 2024 | 2024-11-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.44514 | 0.44514 | 0.44653 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-06 | 13.1625 |  | WTG Unscheduled Maintenance | 9477 | 13.1625
2870 | 2024-11-07 | 2025 | 2024 | 2024-11-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.82292 | 0.82292 | 0.83125 | 0 | 0.2 | 0.2 | Checked related error data log then reset & run the WTG. | Close | 0.0076923 | O2-06 | 78.975 |  | WTG Unscheduled Maintenance | 9477 | 78.975
2871 | 2024-11-07 | 2025 | 2024 | 2024-11-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.38958 | 0.38958 | 0.39097 | 0 | 0.033333 | 0.033333 | auto reset | Close | 0.0012821 | O2-06 | 13.1625 |  | WTG Unscheduled Maintenance | 9477 | 13.1625
2872 | 2024-11-07 | 2025 | 2024 | 2024-11-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.63611 | 0.63611 | 0.73611 | 0 | 2.4 | 2.4 | WTG Manual stop for Converter new software testing work than reset and start WTG. | Close | 0.092308 | O2-06 | 947.7 |  | WTG Breakdown Maintenance | 9477 | 947.7
2873 | 2024-11-07 | 2025 | 2024 | 2024-11-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.49375 | 0.49375 | 0.61806 | 0 | 2.9833 | 2.9833 | WTG Manual stop for Converter new software testing work than reset and start WTG. | Close | 0.11474 | O2-11 | 1332.6799 |  | WTG Breakdown Maintenance | 10721 | 1332.6799
2874 | 2024-11-07 | 2025 | 2024 | 2024-11-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.85903 | 0.85903 | 0.86042 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-11 | 14.8903 |  | WTG Unscheduled Maintenance | 10721 | 14.8903
2875 | 2024-11-07 | 2025 | 2024 | 2024-11-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 525 | Overload axis 2 | Break down | 0.86111 | 0.86111 | 0.86528 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2-11 | 44.6708 |  | WTG Unscheduled Maintenance | 10721 | 44.6708
2876 | 2024-11-07 | 2025 | 2024 | 2024-11-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 525 | Overload axis 2 | Break down | 0.87778 | 0.87778 | 0.89931 | 0 | 0.51667 | 0.51667 | Checked related error data log then reset & run the WTG. | Close | 0.019872 | O2-11 | 230.7993 |  | WTG Unscheduled Maintenance | 10721 | 230.7993
2877 | 2024-11-07 | 2025 | 2024 | 2024-11-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 525 | Overload axis 2 | Break down | 0.90139 | 0.90139 | 0.91458 | 0 | 0.31667 | 0.31667 | Checked related error data log and check perameter than reboot then reset & run the WTG. | Close | 0.012179 | O2-11 | 141.4576 |  | WTG Unscheduled Maintenance | 10721 | 141.4576
2878 | 2024-11-07 | 2025 | 2024 | 2024-11-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 2687 | Max. slip ring cell temp. | Break down | 0.53264 | 0.53264 | 0.65417 | 0 | 2.9167 | 2.9167 | Attend and check error related ckt than found loose connection so retight it and no any abnormality so reset and start WTG. | Close | 0.11218 | O2-20 | 1275.0694 |  | WTG Unscheduled Maintenance | 10492 | 1275.0694
2879 | 2024-11-07 | 2025 | 2024 | 2024-11-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 551 | Pitch motor current too high | Break down | 0.30486 | 0.30486 | 0.3375 | 0 | 0.78333 | 0.78333 | Checked related error data log and check perameter than reboot then reset & run the WTG. | Close | 0.030128 | O2-25 | 357.1347 |  | WTG Unscheduled Maintenance | 10942 | 357.1347
2880 | 2024-11-07 | 2025 | 2024 | 2024-11-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.51736 | 0.51736 | 0.61111 | 0 | 2.25 | 2.25 | WTG manual stop for Repeted inspection work than reset and start WTG. | Close | 0.086538 | O2-01 | 1297.2188 |  | WTG Breakdown Maintenance | 13837 | 1297.2188
2881 | 2024-11-07 | 2025 | 2024 | 2024-11-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.64583 | 0.64583 | 0.72917 | 0 | 2 | 2 | WTG stop for Blade Inspection Work than reset and start WTG. | Close | 0.076923 | O2-01 | 1153.0833 |  | WTG Breakdown Maintenance | 13837 | 1153.0833
2882 | 2024-11-08 | 2025 | 2024 | 2024-11-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.62014 | 0.62014 | 0.64792 | 0 | 0.66667 | 0.66667 | Checked related error data log then reset & run the WTG. | Close | 0.025641 | O2-05 | 88.8889 |  | WTG Unscheduled Maintenance | 3200 | 88.8889
2883 | 2024-11-08 | 2025 | 2024 | 2024-11-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.9375 | 0.9375 | 0.94236 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & run the WTG. | Close | 0.0044872 | O2-09 | 19.5611 |  | WTG Unscheduled Maintenance | 4024 | 19.5611
2884 | 2024-11-08 | 2025 | 2024 | 2024-11-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3063 | Conv. emerg.off type D | Break down | 0.71042 | 0.71042 | 0.71181 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-21 | 2.6861 |  | WTG Unscheduled Maintenance | 1934 | 2.6861
2885 | 2024-11-08 | 2025 | 2024 | 2024-11-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.42292 | 0.42292 | 0.46458 | 0 | 1 | 1 | WTG stop for Blade Inspection Work than reset and start WTG. | Close | 0.038462 | O2-12 | 111.7083 |  | WTG Breakdown Maintenance | 2681 | 111.7083
2886 | 2024-11-08 | 2025 | 2024 | 2024-11-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.2625 | 0.2625 | 0.26389 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-14 | 3.2042 |  | WTG Unscheduled Maintenance | 2307 | 3.2042
2887 | 2024-11-08 | 2025 | 2024 | 2024-11-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.49722 | 0.49722 | 0.51806 | 0 | 0.5 | 0.5 | WTG stop for Blade Inspection Work than reset and start WTG. | Close | 0.019231 | O2-14 | 48.0625 |  | WTG Breakdown Maintenance | 2307 | 48.0625
2888 | 2024-11-08 | 2025 | 2024 | 2024-11-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.72639 | 0.72639 | 0.72778 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-14 | 3.2042 |  | WTG Unscheduled Maintenance | 2307 | 3.2042
2890 | 2024-11-08 | 2025 | 2024 | 2024-11-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.43611 | 0.43611 | 0.46944 | 0 | 0.8 | 0.8 | Checked related error data log then reset & run the WTG. | Close | 0.030769 | O2-06 | 52.3 |  | WTG Unscheduled Maintenance | 1569 | 52.3
2891 | 2024-11-08 | 2025 | 2024 | 2024-11-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.38194 | 0.38194 | 0.39514 | 0 | 0.31667 | 0.31667 | Checked related error data log then reset & run the WTG. | Close | 0.012179 | O2-11 | 32.1944 |  | WTG Unscheduled Maintenance | 2440 | 32.1944
2892 | 2024-11-08 | 2025 | 2024 | 2024-11-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 643 | Sim.angle E enc. <> act.angle 3 | Break down | 0.65417 | 0.65417 | 0.66389 | 0 | 0.23333 | 0.23333 | Checked related error data log then reset & run the WTG. | Close | 0.0089744 | O2-11 | 23.7222 |  | WTG Unscheduled Maintenance | 2440 | 23.7222
2893 | 2024-11-08 | 2025 | 2024 | 2024-11-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 642 | Sim.angle E enc. <> act.angle 2 | Major BD | 0.67292 | 0.67292 | 1899-12-31 | 0 | 7.85 | 7.85 | attend and found Axis 3. Encoder cable connector side Broken. So material arrangement work for another side. Wip. | Close | 0.30192 | O2-11 | 798.0833 |  | WTG Unscheduled Maintenance | 2440 | 798.0833
2894 | 2024-11-09 | 2025 | 2024 | 2024-11-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.31389 | 0.31389 | 0.31597 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-07 | 19.1771 |  | WTG Unscheduled Maintenance | 9205 | 19.1771
2895 | 2024-11-09 | 2025 | 2024 | 2024-11-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.51528 | 0.51528 | 0.51667 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-07 | 12.7847 |  | WTG Unscheduled Maintenance | 9205 | 12.7847
2896 | 2024-11-09 | 2025 | 2024 | 2024-11-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Major BD | 0.020139 | 0.020139 | 0.33333 | 0 | 7.5167 | 7.5167 | attend and check and found hydralic pressure is not hold so check hydraulic system pressure 9.1 walll and Re adjustment and clean then reset and start wtg. | Close | 0.2891 | O2-02 | 4155.4639 |  | WTG Unscheduled Maintenance | 13268 | 4155.4639
2897 | 2024-11-09 | 2025 | 2024 | 2024-11-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.64236 | 0.64236 | 0.64375 | 0 | 0.033333 | 0.033333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0012821 | O2-04 | 14.3403 |  | WTG Unscheduled Maintenance | 10325 | 14.3403
2898 | 2024-11-09 | 2025 | 2024 | 2024-11-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.47778 | 0.47778 | 0.47917 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-14 | 14.0167 |  | WTG Unscheduled Maintenance | 10092 | 14.0167
2899 | 2024-11-09 | 2025 | 2024 | 2024-11-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.85069 | 0.85069 | 0.85278 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-14 | 21.025 |  | WTG Unscheduled Maintenance | 10092 | 21.025
2900 | 2024-11-09 | 2025 | 2024 | 2024-11-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.64236 | 0.64236 | 0.64444 | 0 | 0.05 | 0.05 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0019231 | O2-21 | 16.0271 |  | WTG Unscheduled Maintenance | 7693 | 16.0271
2901 | 2024-11-09 | 2025 | 2024 | 2024-11-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.68819 | 0.68819 | 0.69306 | 0 | 0.11667 | 0.11667 | WTG stop for PPC Software updated Work than reset and start WTG. | Close | 0.0044872 | O2-06 | 37.975 |  | WTG Breakdown Maintenance | 7812 | 37.975
2902 | 2024-11-09 | 2025 | 2024 | 2024-11-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 650 | Pitch controller communication error | Break down | 0.64236 | 0.64236 | 0.65139 | 0 | 0.21667 | 0.21667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0083333 | O2-07 | 83.1007 |  | WTG Unscheduled Maintenance | 9205 | 83.1007
2903 | 2024-11-09 | 2025 | 2024 | 2024-11-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 643 | Sim.angle E enc. <> act.angle 3 | Major BD | 0 | 0 | 0.70625 | 0 | 16.95 | 16.95 | attend and check snapshot than check encoder A cable and cable routing than take continuity than found cable was cut inside connector on encoder side and than arrange new cable from mahuva than replace than calibration Done than trial time sim angele pitch conv.3 error occured so check than found Encode A was faulty so replace it than again blade calibration Done than reset and start wtg. | Close | 0.65192 | O2-11 | 7426.2188 |  | WTG Unscheduled Maintenance | 10515 | 7426.2188
2904 | 2024-11-09 | 2025 | 2024 | 2024-11-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 551 | Pitch motor current too high | Break down | 0.34861 | 0.34861 | 0.36597 | 0 | 0.41667 | 0.41667 | Checked related error data log then reset & run the WTG. | Close | 0.016026 | O2-25 | 213.0035 |  | WTG Unscheduled Maintenance | 12269 | 213.0035
2905 | 2024-11-10 | 2025 | 2024 | 2024-11-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.6125 | 0.6125 | 0.61389 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-07 | 5.5875 |  | WTG Unscheduled Maintenance | 4023 | 5.5875
2906 | 2024-11-10 | 2025 | 2024 | 2024-11-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.39236 | 0.39236 | 0.42569 | 0 | 0.8 | 0.8 | Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.030769 | O2-26 | 164.4 |  | WTG Unscheduled Maintenance | 4932 | 164.4
2907 | 2024-11-10 | 2025 | 2024 | 2024-11-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.47292 | 0.47292 | 0.475 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-06 | 7.0917 |  | WTG Unscheduled Maintenance | 3404 | 7.0917
2908 | 2024-11-10 | 2025 | 2024 | 2024-11-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.58125 | 0.58125 | 0.58403 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & run the WTG. | Close | 0.0025641 | O2-06 | 9.4556 |  | WTG Unscheduled Maintenance | 3404 | 9.4556
2909 | 2024-11-10 | 2025 | 2024 | 2024-11-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.56736 | 0.56736 | 0.57639 | 0 | 0.21667 | 0.21667 | Checked related error data log then reset & run the WTG. | Close | 0.0083333 | O2-06 | 30.7306 |  | WTG Unscheduled Maintenance | 3404 | 30.7306
2910 | 2024-11-10 | 2025 | 2024 | 2024-11-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.59097 | 0.59097 | 0.59306 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-11 | 6.5333 |  | WTG Unscheduled Maintenance | 3136 | 6.5333
2911 | 2024-11-10 | 2025 | 2024 | 2024-11-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 2687 | Max. slip ring cell temp. | Break down | 0.71111 | 0.71111 | 0.73056 | 0 | 0.46667 | 0.46667 | after slipring cell temp is normal then start wtg | Close | 0.017949 | O2-20 | 60.6083 |  | WTG Unscheduled Maintenance | 3117 | 60.6083
2912 | 2024-11-10 | 2025 | 2024 | 2024-11-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down | 0.33264 | 0.33264 | 0.33472 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-25 | 10.5875 |  | WTG Unscheduled Maintenance | 5082 | 10.5875
2913 | 2024-11-11 | 2025 | 2024 | 2024-11-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 3065 | Conv. emerg.off type F | Break down | 0.59931 | 0.59931 | 0.60347 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2-26 | 25.9542 |  | WTG Unscheduled Maintenance | 6229 | 25.9542
2914 | 2024-11-11 | 2025 | 2024 | 2024-11-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.33056 | 0.33056 | 0.33194 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-05 | 6.6292 |  | WTG Unscheduled Maintenance | 4773 | 6.6292
2915 | 2024-11-11 | 2025 | 2024 | 2024-11-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 7002 | Task runtime failure 5ms | Break down | 0.47917 | 0.47917 | 0.49444 | 0 | 0.36667 | 0.36667 | Checked related error data log then reset & run the WTG. | Close | 0.014103 | O2-05 | 72.9208 |  | WTG Unscheduled Maintenance | 4773 | 72.9208
2916 | 2024-11-11 | 2025 | 2024 | 2024-11-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.62639 | 0.62639 | 0.62778 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-07 | 6.3194 |  | WTG Unscheduled Maintenance | 4550 | 6.3194
2917 | 2024-11-11 | 2025 | 2024 | 2024-11-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.36528 | 0.36528 | 0.36667 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-21 | 6.7375 |  | WTG Unscheduled Maintenance | 4851 | 6.7375
2918 | 2024-11-11 | 2025 | 2024 | 2024-11-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.54583 | 0.54583 | 0.54653 | 0 | 0.016667 | 0.016667 | auto reset | Close | 0.00064103 | O2-21 | 3.3687 |  | WTG Unscheduled Maintenance | 4851 | 3.3687
2919 | 2024-11-11 | 2025 | 2024 | 2024-11-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.8125 | 0.8125 | 0.825 | 0 | 0.3 | 0.3 | Checked related error data log then reset & run the WTG. | Close | 0.011538 | O2-04 | 53.0375 |  | WTG Unscheduled Maintenance | 4243 | 53.0375
2920 | 2024-11-11 | 2025 | 2024 | 2024-11-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.74167 | 0.74167 | 0.74792 | 0 | 0.15 | 0.15 | WTG Manual stop for software update work than reset and start WTG. | Close | 0.0057692 | O2-12 | 33.5812 |  | WTG Breakdown Maintenance | 5373 | 33.5812
2921 | 2024-11-11 | 2025 | 2024 | 2024-11-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.72083 | 0.72083 | 0.73194 | 0 | 0.26667 | 0.26667 | WTG Manual stop for software update work than reset and start WTG. | Close | 0.010256 | O2-11 | 52.1111 |  | WTG Breakdown Maintenance | 4690 | 52.1111
2922 | 2024-11-11 | 2025 | 2024 | 2024-11-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.52153 | 0.52153 | 0.54167 | 0 | 0.48333 | 0.48333 | WTG Manual stop for software update work than reset and start WTG. | Close | 0.01859 | O2-12 | 108.2062 |  | WTG Breakdown Maintenance | 5373 | 108.2062
2923 | 2024-11-11 | 2025 | 2024 | 2024-11-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.57153 | 0.57153 | 0.60556 | 0 | 0.81667 | 0.81667 | WTG Manual stop for software update work than reset and start WTG. | Close | 0.03141 | O2-12 | 182.8312 |  | WTG Breakdown Maintenance | 5373 | 182.8312
2924 | 2024-11-11 | 2025 | 2024 | 2024-11-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.77083 | 0.77083 | 0.87986 | 0 | 2.6167 | 2.6167 | Checked related error data log then reset & run the WTG.( late reset due to fleetpro is not show in live data and not connected in fleetpro) | Close | 0.10064 | O2-24 | 459.4431 |  | WTG Unscheduled Maintenance | 4214 | 459.4431
2925 | 2024-11-11 | 2025 | 2024 | 2024-11-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.65208 | 0.65208 | 0.65347 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-06 | 6.3833 |  | WTG Unscheduled Maintenance | 4596 | 6.3833
2926 | 2024-11-11 | 2025 | 2024 | 2024-11-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.38125 | 0.38125 | 0.38264 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-06 | 6.3833 |  | WTG Unscheduled Maintenance | 4596 | 6.3833
2927 | 2024-11-11 | 2025 | 2024 | 2024-11-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.42361 | 0.42361 | 0.42847 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & run the WTG. | Close | 0.0044872 | O2-06 | 22.3417 |  | WTG Unscheduled Maintenance | 4596 | 22.3417
2928 | 2024-11-11 | 2025 | 2024 | 2024-11-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.60347 | 0.60347 | 0.64444 | 0 | 0.98333 | 0.98333 | WTG Manual stop for project pending work than reset and start WTG. | Close | 0.037821 | O2-11 | 192.1597 |  | WTG Breakdown Maintenance | 4690 | 192.1597
2929 | 2024-11-11 | 2025 | 2024 | 2024-11-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.65694 | 0.65694 | 0.66111 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2-11 | 19.5417 |  | WTG Unscheduled Maintenance | 4690 | 19.5417
2930 | 2024-11-11 | 2025 | 2024 | 2024-11-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.70278 | 0.70278 | 0.71111 | 0 | 0.2 | 0.2 | WTG Manual stop for software update work than reset and start WTG. | Close | 0.0076923 | O2-20 | 32.975 |  | WTG Breakdown Maintenance | 3957 | 32.975
2931 | 2024-11-12 | 2025 | 2024 | 2024-11-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.54097 | 0.54097 | 0.54583 | 0 | 0.11667 | 0.11667 | WTG Manual stop for software update work than reset and start WTG. | Close | 0.0044872 | O2-05 | 26.8771 |  | WTG Breakdown Maintenance | 5529 | 26.8771
2932 | 2024-11-12 | 2025 | 2024 | 2024-11-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.44583 | 0.44583 | 0.44722 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-07 | 6.9792 |  | WTG Unscheduled Maintenance | 5025 | 6.9792
2933 | 2024-11-12 | 2025 | 2024 | 2024-11-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.54306 | 0.54306 | 0.54861 | 0 | 0.13333 | 0.13333 | WTG Manual stop for software update work than reset and start WTG. | Close | 0.0051282 | O2-07 | 27.9167 |  | WTG Breakdown Maintenance | 5025 | 27.9167
2934 | 2024-11-12 | 2025 | 2024 | 2024-11-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.54167 | 0.54167 | 0.55139 | 0 | 0.23333 | 0.23333 | WTG Manual stop for software update work than reset and start WTG. | Close | 0.0089744 | O2-21 | 58.9069 |  | WTG Breakdown Maintenance | 6059 | 58.9069
2935 | 2024-11-12 | 2025 | 2024 | 2024-11-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Break down | 0.44653 | 0.44653 | 0.44722 | 0 | 0.016667 | 0.016667 | auto reset | Close | 0.00064103 | O2-04 | 3.5521 |  | WTG Unscheduled Maintenance | 5115 | 3.5521
2936 | 2024-11-12 | 2025 | 2024 | 2024-11-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.058333 | 0.058333 | 0.059722 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-14 | 6.9403 |  | WTG Unscheduled Maintenance | 4997 | 6.9403
2937 | 2024-11-12 | 2025 | 2024 | 2024-11-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.54444 | 0.54444 | 0.54931 | 0 | 0.11667 | 0.11667 | WTG Manual stop for software update work than reset and start WTG. | Close | 0.0044872 | O2-14 | 24.291 |  | WTG Breakdown Maintenance | 4997 | 24.291
2938 | 2024-11-12 | 2025 | 2024 | 2024-11-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.60417 | 0.60417 | 0.64653 | 0 | 1.0167 | 1.0167 | WTG Manual stop for software update work than reset and start WTG. | Close | 0.039103 | O2-12 | 251.9639 |  | WTG Breakdown Maintenance | 5948 | 251.9639
2939 | 2024-11-12 | 2025 | 2024 | 2024-11-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.70139 | 0.70139 | 0.71597 | 0 | 0.35 | 0.35 | WTG Manual stop for software update work than reset and start WTG. | Close | 0.013462 | O2-12 | 86.7417 |  | WTG Breakdown Maintenance | 5948 | 86.7417
2940 | 2024-11-12 | 2025 | 2024 | 2024-11-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.53403 | 0.53403 | 0.53889 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & run the WTG. | Close | 0.0044872 | O2-06 | 29.4049 |  | WTG Unscheduled Maintenance | 6049 | 29.4049
2941 | 2024-11-12 | 2025 | 2024 | 2024-11-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.54514 | 0.54514 | 0.55208 | 0 | 0.16667 | 0.16667 | WTG Manual stop for software update work than reset and start WTG. | Close | 0.0064103 | O2-06 | 42.0069 |  | WTG Breakdown Maintenance | 6049 | 42.0069
2942 | 2024-11-12 | 2025 | 2024 | 2024-11-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.54861 | 0.54861 | 0.55347 | 0 | 0.11667 | 0.11667 | WTG Manual stop for software update work than reset and start WTG. | Close | 0.0044872 | O2-06 | 29.4049 |  | WTG Breakdown Maintenance | 6049 | 29.4049
2943 | 2024-11-12 | 2025 | 2024 | 2024-11-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.35972 | 0.35972 | 0.36875 | 0 | 0.21667 | 0.21667 | Checked related error data log then reset & run the WTG. | Close | 0.0083333 | O2-06 | 54.609 |  | WTG Unscheduled Maintenance | 6049 | 54.609
2944 | 2024-11-12 | 2025 | 2024 | 2024-11-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.55556 | 0.55556 | 0.56181 | 0 | 0.15 | 0.15 | WTG Manual stop for software update work than reset and start WTG. | Close | 0.0057692 | O2-06 | 37.8062 |  | WTG Breakdown Maintenance | 6049 | 37.8062
2945 | 2024-11-12 | 2025 | 2024 | 2024-11-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.18819 | 0.18819 | 0.18958 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-11 | 6.4347 |  | WTG Unscheduled Maintenance | 4633 | 6.4347
2946 | 2024-11-12 | 2025 | 2024 | 2024-11-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.55764 | 0.55764 | 0.56458 | 0 | 0.16667 | 0.16667 | WTG Manual stop for software update work than reset and start WTG. | Close | 0.0064103 | O2-11 | 32.1736 |  | WTG Breakdown Maintenance | 4633 | 32.1736
2947 | 2024-11-12 | 2025 | 2024 | 2024-11-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.55486 | 0.55486 | 0.56042 | 0 | 0.13333 | 0.13333 | WTG Manual stop for software update work than reset and start WTG. | Close | 0.0051282 | O2-01 | 35.8222 |  | WTG Breakdown Maintenance | 6448 | 35.8222
2948 | 2024-11-12 | 2025 | 2024 | 2024-11-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.6 | 0.6 | 0.60208 | 0 | 0.05 | 0.05 | auto reset | Close | 0.0019231 | O2-01 | 13.4333 |  | WTG Unscheduled Maintenance | 6448 | 13.4333
2948 | 2024-11-13 | 2025 | 2024 | 2024-11-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 3065 | Conv. emerg.off type F | Break down | 0.67014 | 0.67014 | 0.67222 | 0 | 0.05 | 0.05 | auto reset | Close | 0.0019231 | O2-26 | 14.8771 |  | WTG Unscheduled Maintenance | 7141 | 14.8771
2948 | 2024-11-13 | 2025 | 2024 | 2024-11-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.85278 | 0.85278 | 0.85486 | 0 | 0.05 | 0.05 | auto reset | Close | 0.0019231 | O2-05 | 15.1854 |  | WTG Unscheduled Maintenance | 7289 | 15.1854
2948 | 2024-11-13 | 2025 | 2024 | 2024-11-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.86528 | 0.86528 | 0.86875 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2-05 | 25.309 |  | WTG Unscheduled Maintenance | 7289 | 25.309
2948 | 2024-11-13 | 2025 | 2024 | 2024-11-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.44653 | 0.44653 | 0.56389 | 0 | 2.8167 | 2.8167 | WTG Manual stop for O&M seevice audit work than reset and start WTG. | Close | 0.10833 | O2-21 | 975.8576 |  | WTG Breakdown Maintenance | 8315 | 975.8576
2948 | 2024-11-13 | 2025 | 2024 | 2024-11-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.59653 | 0.59653 | 0.65625 | 0 | 1.4333 | 1.4333 | WTG Manual stop for O&M seevice audit work than reset and start WTG. | Close | 0.055128 | O2-06 | 453.5306 |  | WTG Breakdown Maintenance | 7594 | 453.5306
2948 | 2024-11-13 | 2025 | 2024 | 2024-11-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.054861 | 0.054861 | 0.056944 | 0 | 0.05 | 0.05 | auto reset | Close | 0.0019231 | O2-07 | 13.7437 |  | WTG Unscheduled Maintenance | 6597 | 13.7437
2948 | 2024-11-13 | 2025 | 2024 | 2024-11-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.059028 | 0.059028 | 0.069444 | 0 | 0.25 | 0.25 | Checked related error data log then reset & run the WTG. | Close | 0.0096154 | O2-07 | 68.7188 |  | WTG Unscheduled Maintenance | 6597 | 68.7188
2948 | 2024-11-13 | 2025 | 2024 | 2024-11-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.72361 | 0.72361 | 0.73611 | 0 | 0.3 | 0.3 | WTG Manual stop for software update work than reset and start WTG. | Close | 0.011538 | O2-24 | 80.3125 |  | WTG Breakdown Maintenance | 6425 | 80.3125
2948 | 2024-11-13 | 2025 | 2024 | 2024-11-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.41667 | 0.41667 | 0.42083 | 0 | 0.1 | 0.1 | auto reset | Close | 0.0038462 | O2-06 | 31.6417 |  | WTG Unscheduled Maintenance | 7594 | 31.6417
2949 | 2024-11-14 | 2025 | 2024 | 2024-11-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.58889 | 0.58889 | 0.71597 | 0 | 3.05 | 3.05 | WTG Manual stop for O&M service audit work than reset and start WTG. | Close | 0.11731 | O2-03 | 1341.3646 |  | WTG Breakdown Maintenance | 10555 | 1341.3646
2950 | 2024-11-14 | 2025 | 2024 | 2024-11-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.60069 | 0.60069 | 0.63542 | 0 | 0.83333 | 0.83333 | WTG Manual stop for convertor software testing work than reset and start WTG. | Close | 0.032051 | O2-12 | 392.5694 |  | WTG Breakdown Maintenance | 11306 | 392.5694
2951 | 2024-11-14 | 2025 | 2024 | 2024-11-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.51389 | 0.51389 | 0.57778 | 0 | 1.5333 | 1.5333 | WTG Manual stop for converter Inspection work so inspection time Converter related error occurs so check and found no any abnormality Apply hard reboot than reset and start WTG. | Close | 0.058974 | O2-10 | 669.4278 |  | WTG Breakdown Maintenance | 10478 | 669.4278
2952 | 2024-11-14 | 2025 | 2024 | 2024-11-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.50278 | 0.50278 | 0.52153 | 0 | 0.45 | 0.45 | WTG Manual stop for convertor software testing work than reset and start WTG. | Close | 0.017308 | O2-24 | 218.1 |  | WTG Breakdown Maintenance | 11632 | 218.1
2953 | 2024-11-14 | 2025 | 2024 | 2024-11-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.4125 | 0.4125 | 0.41319 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | O2-06 | 9.966 |  | WTG Unscheduled Maintenance | 14351 | 9.966
2954 | 2024-11-14 | 2025 | 2024 | 2024-11-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.52778 | 0.52778 | 0.53194 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-06 | 59.7958 |  | WTG Unscheduled Maintenance | 14351 | 59.7958
2955 | 2024-11-14 | 2025 | 2024 | 2024-11-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 2687 | Max. slip ring cell temp. | Break down | 0.66458 | 0.66458 | 0.70347 | 0 | 0.93333 | 0.93333 | after slipring cell temp is normal then start wtg | Close | 0.035897 | O2-20 | 426.6111 |  | WTG Unscheduled Maintenance | 10970 | 426.6111
2956 | 2024-11-14 | 2025 | 2024 | 2024-11-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.32361 | 0.32361 | 0.32569 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-01 | 23.0312 |  | WTG Unscheduled Maintenance | 11055 | 23.0312
2957 | 2024-11-14 | 2025 | 2024 | 2024-11-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.34583 | 0.34583 | 0.35417 | 0 | 0.2 | 0.2 | Checked related error data log then reset & run the WTG. | Close | 0.0076923 | O2-01 | 92.125 |  | WTG Unscheduled Maintenance | 11055 | 92.125
2957 | 2024-11-15 | 2025 | 2024 | 2024-11-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.45278 | 0.45278 | 0.57083 | 0 | 2.8333 | 2.8333 | WTG Manual stop for repeated error and found converter coolant Pressure switch malfunctioning so replace it And top up coolant than reset and start WTG. | Close | 0.10897 | O2-21 | 623.5694 |  | WTG Breakdown Maintenance | 5282 | 623.5694
2957 | 2024-11-15 | 2025 | 2024 | 2024-11-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Break down | 0.55139 | 0.55139 | 0.55417 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & run the WTG. | Close | 0.0025641 | O2-04 | 5.6722 |  | WTG Unscheduled Maintenance | 2042 | 5.6722
2957 | 2024-11-15 | 2025 | 2024 | 2024-11-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.53542 | 0.53542 | 0.53889 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2-26 | 11.6771 |  | WTG Unscheduled Maintenance | 3363 | 11.6771
2957 | 2024-11-15 | 2025 | 2024 | 2024-11-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.24792 | 0.24792 | 0.25 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-03 | 8.1333 |  | WTG Unscheduled Maintenance | 3904 | 8.1333
2957 | 2024-11-15 | 2025 | 2024 | 2024-11-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD | 0.63889 | 0.63889 | 0.89444 | 0 | 6.1333 | 6.1333 | attend for converter Related repeated error so check all related circuit found loose connections in converter panel and also check Another repeated error then reset and start wtg | Close | 0.2359 | O2-03 | 997.6889 |  | WTG Breakdown Maintenance | 3904 | 997.6889
2957 | 2024-11-15 | 2025 | 2024 | 2024-11-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.59097 | 0.59097 | 0.59306 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-15 | 10.3062 |  | WTG Unscheduled Maintenance | 4947 | 10.3062
2957 | 2024-11-15 | 2025 | 2024 | 2024-11-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.65625 | 0.65625 | 0.65833 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-15 | 10.3062 |  | WTG Unscheduled Maintenance | 4947 | 10.3062
2957 | 2024-11-15 | 2025 | 2024 | 2024-11-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.50278 | 0.50278 | 0.59444 | 0 | 2.2 | 2.2 | WTG Manual stop for O&M service audit work than reset and start WTG. | Close | 0.084615 | O2-21 | 484.1833 |  | WTG Breakdown Maintenance | 5282 | 484.1833
2957 | 2024-11-15 | 2025 | 2024 | 2024-11-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.47153 | 0.47153 | 0.58958 | 0 | 2.8333 | 2.8333 | WTG Manual stop for project pending work than reset and start WTG. | Close | 0.10897 | O2-24 | 495.2431 |  | WTG Breakdown Maintenance | 4195 | 495.2431
2958 | 2024-11-16 | 2025 | 2024 | 2024-11-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.74583 | 0.74583 | 0.74792 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-15 | 5.3937 |  | WTG Unscheduled Maintenance | 2589 | 5.3937
2959 | 2024-11-16 | 2025 | 2024 | 2024-11-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.48333 | 0.48333 | 0.61181 | 0 | 3.0833 | 3.0833 | WTG Manual stop for audit punch point closing work than reset and start WTG. | Close | 0.11859 | O2-12 | 396.2083 |  | WTG Breakdown Maintenance | 3084 | 396.2083
2960 | 2024-11-16 | 2025 | 2024 | 2024-11-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.54931 | 0.54931 | 0.69583 | 0 | 3.5167 | 3.5167 | wtg manual stop for power curve inspection work. attend and check altrasonic sensor and replace with new one and also alignment done and check 10 min data than found ok and also taken slipring cell temp sensor resistance value and naccele outdoor temp sensor resistance value than reset and start Wtg. | Close | 0.13526 | O2-12 | 451.8917 |  | WTG Breakdown Maintenance | 3084 | 451.8917
2961 | 2024-11-16 | 2025 | 2024 | 2024-11-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.37222 | 0.37222 | 0.37708 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & run the WTG. | Close | 0.0044872 | O2-07 | 12.7944 |  | WTG Unscheduled Maintenance | 2632 | 12.7944
2962 | 2024-11-16 | 2025 | 2024 | 2024-11-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.96181 | 0.96181 | 0.97431 | 0 | 0.3 | 0.3 | Checked related error data log then reset & run the WTG. | Close | 0.011538 | O2-07 | 32.9 |  | WTG Unscheduled Maintenance | 2632 | 32.9
2963 | 2024-11-17 | 2025 | 2024 | 2024-11-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Break down | 0.425 | 0.425 | 0.4375 | 0 | 0.3 | 0.3 | Checked related error data log then reset & run the WTG. | Close | 0.011538 | O2-26 | 159.3125 |  | WTG Unscheduled Maintenance | 12745 | 159.3125
2964 | 2024-11-17 | 2025 | 2024 | 2024-11-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.44236 | 0.44236 | 0.52153 | 0 | 1.9 | 1.9 | attend and check all Related Circuit found Silica gel in contractor So removed and no any abnormality so take trial then start wtg. | Close | 0.073077 | O2-26 | 1008.9792 |  | WTG Unscheduled Maintenance | 12745 | 1008.9792
2965 | 2024-11-17 | 2025 | 2024 | 2024-11-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Major BD | 0.5625 | 0.5625 | 1899-12-31 | 0 | 10.5 | 10.5 | Another Troubleshooting WIP | open | 0.40385 | O2-11 | 4377.1875 |  | WTG Unscheduled Maintenance | 10005 | 4377.1875
2966 | 2024-11-17 | 2025 | 2024 | 2024-11-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.45556 | 0.45556 | 0.60208 | 0 | 3.5167 | 3.5167 | WTG Manual stop for project pending work than reset and start WTG. | Close | 0.13526 | O2-12 | 1656.6431 |  | WTG Breakdown Maintenance | 11306 | 1656.6431
2967 | 2024-11-17 | 2025 | 2024 | 2024-11-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.098611 | 0.098611 | 0.22639 | 0 | 3.0667 | 3.0667 | attend and check all Related Circuit found break pad temp sensor on loose connections so Correct it, then reset and start wtg. | Close | 0.11795 | O2-07 | 1396.2278 |  | WTG Unscheduled Maintenance | 10927 | 1396.2278 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
2968 | 2024-11-18 | 2025 | 2024 | 2024-11-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Road issue | 0.28403 | 0.28403 | 0.50694 | 0 | 5.35 | 5.35 | Road is not approchable and also Disconnect from SCADA | Close | 0.20577 | O2-05 | 3200.6375 |  | WTG Unscheduled Maintenance | 14358 | 3200.6375
2969 | 2024-11-18 | 2025 | 2024 | 2024-11-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Road issue | 0.50694 | 0.50694 | 0.78056 | 0 | 6.5667 | 6.5667 | Attend And WTG Check Error Related Circuit After found UPS connection Loose After All Conection tight and trail so ok after then start wtg | Close | 0.25256 | O2-05 | 3928.5083 |  | WTG Unscheduled Maintenance | 14358 | 3928.5083
2970 | 2024-11-18 | 2025 | 2024 | 2024-11-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 650 | Pitch controller communication error | Break down | 0.011111 | 0.011111 | 0.021528 | 0 | 0.25 | 0.25 | Checked related error data log then reset & run the WTG. | Close | 0.0096154 | O2-11 | 109.8646 |  | WTG Unscheduled Maintenance | 10547 | 109.8646
2971 | 2024-11-18 | 2025 | 2024 | 2024-11-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.75694 | 0.75694 | 0.78264 | 0 | 0.61667 | 0.61667 | WTG Manual stop for convertor software testing work than reset and start WTG. | Close | 0.023718 | O2-11 | 270.9993 |  | WTG Breakdown Maintenance | 10547 | 270.9993
2972 | 2024-11-18 | 2025 | 2024 | 2024-11-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.49931 | 0.49931 | 0.59375 | 0 | 2.2667 | 2.2667 | WTG Manual stop for project pending work than reset and start WTG. | Close | 0.087179 | O2-06 | 1222.3 |  | WTG Breakdown Maintenance | 12942 | 1222.3
2973 | 2024-11-19 | 2025 | 2024 | 2024-11-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.32847 | 0.32847 | 0.33264 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2-07 | 46.6792 |  | WTG Unscheduled Maintenance | 11203 | 46.6792
2974 | 2024-11-19 | 2025 | 2024 | 2024-11-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.38819 | 0.38819 | 0.40417 | 0 | 0.38333 | 0.38333 | Checked related error data log then reset & run the WTG. | Close | 0.014744 | O2-04 | 149.2285 |  | WTG Unscheduled Maintenance | 9343 | 149.2285
2976 | 2024-11-19 | 2025 | 2024 | 2024-11-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.44792 | 0.44792 | 0.54583 | 0 | 2.35 | 2.35 | WTG Manual stop for repeated error and found converter coolant Pressure Law it And top up coolant than reset and start WTG. | Close | 0.090385 | O2-11 | 880.1729 |  | WTG Breakdown Maintenance | 8989 | 880.1729
2977 | 2024-11-19 | 2025 | 2024 | 2024-11-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.51389 | 0.51389 | 0.66667 | 0 | 3.6667 | 3.6667 | WTG Manual stop for convertor software testing work than reset and start WTG. | Close | 0.14103 | O2-12 | 1702.0972 |  | WTG Breakdown Maintenance | 11141 | 1702.0972
2978 | 2024-11-19 | 2025 | 2024 | 2024-11-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.66806 | 0.66806 | 0.73403 | 0 | 1.5833 | 1.5833 | WTG Manual stop for repeated error and found converter coolant Pressure Law it And top up coolant than reset and start WTG. | Close | 0.060897 | O2-07 | 739.0868 |  | WTG Breakdown Maintenance | 11203 | 739.0868
2979 | 2024-11-19 | 2025 | 2024 | 2024-11-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.52153 | 0.52153 | 0.61597 | 0 | 2.2667 | 2.2667 | WTG Manual stop for project pending work than reset and start WTG. | Close | 0.087179 | O2-03 | 1198.0278 |  | WTG Breakdown Maintenance | 12685 | 1198.0278
2980 | 2024-11-19 | 2025 | 2024 | 2024-11-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 550 | Pitch current asymmetry | Break down | 0.56667 | 0.56667 | 0.57847 | 0 | 0.28333 | 0.28333 | Checked related error data log then reset & run the WTG. | Close | 0.010897 | O2-11 | 106.1201 |  | WTG Unscheduled Maintenance | 8989 | 106.1201
2981 | 2024-11-20 | 2025 | 2024 | 2024-11-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Break down | 0.33264 | 0.33264 | 0.54583 | 0 | 5.1167 | 5.1167 | Attend and found flate resistor faulty so replace it and also check repeted error blade bearing lubrication faulty so check and found lubar grease level sensor cable on loose connection so tight it and also check repeated error pitch 2 current asymmetry so check pitch break resister , check pitch motor power cable Laying are ok then check QA003 connector found loose connection so tight it then reset and start wtg now wtg under observation. | Close | 0.19679 | O2-11 | 1708.7535 |  | WTG Unscheduled Maintenance | 8015 | 1708.7535
2982 | 2024-11-20 | 2025 | 2024 | 2024-11-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.50486 | 0.50486 | 0.51181 | 0 | 0.16667 | 0.16667 | WTG Manual stop for convertor software testing work than reset and start WTG. | Close | 0.0064103 | O2-20 | 47.2917 |  | WTG Breakdown Maintenance | 6810 | 47.2917
2983 | 2024-11-21 | 2025 | 2024 | 2024-11-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.45486 | 0.45486 | 0.59583 | 0 | 3.3833 | 3.3833 | wtg stop for Rep Error Releted inspection work Done after start wtg | Close | 0.13013 | O-21 | 1453.1417 |  | WTG Breakdown Maintenance | 10308 | 1453.1417
2984 | 2024-11-21 | 2025 | 2024 | 2024-11-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Break down | 0.63958 | 0.63958 | 0.85764 | 0 | 5.2333 | 5.2333 | Attend and check Encoder A cable and Connector SO found Connector loos after tight all Connection and Connector after cable rooting Properly after trail so ok after then reset and start wtg | Close | 0.20128 | O-04 | 1748.3694 |  | WTG Unscheduled Maintenance | 8018 | 1748.3694
2985 | 2024-11-21 | 2025 | 2024 | 2024-11-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.44653 | 0.44653 | 0.49583 | 0 | 1.1833 | 1.1833 | Attend and wtg check all Connection and surge arrester connection loose after all connection tight after trail and reset wtg | Close | 0.045513 | O2-06 | 479.0035 |  | WTG Unscheduled Maintenance | 9715 | 479.0035
2986 | 2024-11-21 | 2025 | 2024 | 2024-11-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.49583 | 0.49583 | 0.64514 | 0 | 3.5833 | 3.5833 | Project Pending Punch Point closing work | Close | 0.13782 | O2-06 | 1450.5035 |  | WTG Breakdown Maintenance | 9715 | 1450.5035
2987 | 2024-11-22 | 2025 | 2024 | 2024-11-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.50764 | 0.50764 | 0.69097 | 0 | 4.4 | 4.4 | Project Pending Punch Point closing work | Close | 0.16923 | O2-12 | 1383.25 |  | WTG Breakdown Maintenance | 7545 | 1383.25
2988 | 2024-11-22 | 2025 | 2024 | 2024-11-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.58472 | 0.58472 | 0.65486 | 0 | 1.6833 | 1.6833 | WTG Stop for converter connectivity checking work | Close | 0.064744 | O2-06 | 637.9833 |  | WTG Breakdown Maintenance | 9096 | 637.9833
2989 | 2024-11-22 | 2025 | 2024 | 2024-11-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Major BD | 0.72153 | 0.72153 | 1899-12-31 | 0 | 6.6833 | 6.6833 | Attend and WTG Check hydralic UNIT and check reletedet circuit so found 9.1 valve faulty so arrnge other site Replace 9.1 Valve after trail so ok then reset and start wtg | Close | 0.25705 | O2-26 | 2198.8167 |  | WTG Unscheduled Maintenance | 7896 | 2198.8167
2990 | 2024-11-23 | 2025 | 2024 | 2024-11-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down | 0 | 0 | 0.026389 | 0 | 0.63333 | 0.63333 | Attendand wtg Hydraulic pump oil refiling work done Also HPU UNIT WTR Completed done after reset and start wtg | Close | 0.024359 | O2-26 | 103.9722 |  | WTG Unscheduled Maintenance | 3940 | 103.9722
2991 | 2024-11-23 | 2025 | 2024 | 2024-11-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.27431 | 0.27431 | 0.42361 | 0 | 3.5833 | 3.5833 | Attend And wtg Check convertor cooling system so found PRV Coolant liquid leakge minor after all pipe tight and clean coolant after trail so ok then reset and start wtg under observation | Close | 0.13782 | O2-05 | 596.3264 |  | WTG Breakdown Maintenance | 3994 | 596.3264
2930 | 2024-11-24 | 2025 | 2024 | 2024-11-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Break down | 0.79583 | 0.79583 | 0.80347 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & run the WTG. | Close | 0.0070513 | O2-26 | 29.8528 |  | WTG Unscheduled Maintenance | 3908 | 29.8528
2931 | 2024-11-24 | 2025 | 2024 | 2024-11-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.77778 | 0.77778 | 0.85972 | 0 | 1.9667 | 1.9667 | WTG Manual stop after grid time convereter RFO Singnal not show in systeam after show singnal after reset and start wtg | Close | 0.075641 | O2-09 | 430.8639 |  | WTG Breakdown Maintenance | 5258 | 430.8639
2932 | 2024-11-24 | 2025 | 2024 | 2024-11-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.94792 | 0.94792 | 0.99722 | 0 | 1.1833 | 1.1833 | WTG Manual stop after grid time convereter RFO Singnal not show in systeam after show singnal after reset and start wtg | Close | 0.045513 | O2-21 | 162.9549 |  | WTG Breakdown Maintenance | 3305 | 162.9549
2933 | 2024-11-24 | 2025 | 2024 | 2024-11-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.77778 | 0.77778 | 0.86181 | 0 | 2.0167 | 2.0167 | WTG Manual stop after grid time convereter RFO Singnal not show in systeam after show singnal after reset and start wtg | Close | 0.077564 | O2-11 | 232.3368 |  | WTG Breakdown Maintenance | 2765 | 232.3368
2934 | 2024-11-24 | 2025 | 2024 | 2024-11-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.77778 | 0.77778 | 0.87778 | 0 | 2.4 | 2.4 | WTG Manual stop after grid time convereter RFO Singnal not show in systeam after show singnal after reset and start wtg | Close | 0.092308 | O2-01 | 493.3 |  | WTG Breakdown Maintenance | 4933 | 493.3
2935 | 2024-11-24 | 2025 | 2024 | 2024-11-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.94792 | 0.94792 | 0.99861 | 0 | 1.2167 | 1.2167 | WTG Manual stop after grid time convereter RFO Singnal not show in systeam after show singnal after reset and start wtg | Close | 0.046795 | O2-06 | 169.7757 |  | WTG Breakdown Maintenance | 3349 | 169.7757
2936 | 2024-11-24 | 2025 | 2024 | 2024-11-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Connectivity issue | 0.94792 | 0.94792 | 1899-12-31 | 0 | 1.25 | 1.25 | Disconnect to SCADA Because O2-21 VCB Off no connect O2-22 WTG | Close | 0.048077 | O2-06 | 174.4271 |  | WTG Breakdown Maintenance | 3349 | 174.4271
2937 | 2024-11-24 | 2025 | 2024 | 2024-11-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Connectivity issue | 0.94792 | 0.94792 | 1899-12-31 | 0 | 1.25 | 1.25 | Disconnect to SCADA Because 02-24 VCB Off no connect WTG | Close | 0.048077 | O2-24 | 161.9271 |  | WTG Breakdown Maintenance | 3109 | 161.9271
2938 | 2024-11-24 | 2025 | 2024 | 2024-11-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Connectivity issue | 0.94792 | 0.94792 | 1899-12-31 | 0 | 1.25 | 1.25 | Disconnect to SCADA Because 02-24 VCB Off no connect WTG | Close | 0.048077 | O2-21 | 172.1354 |  | WTG Breakdown Maintenance | 3305 | 172.1354
2939 | 2024-11-25 | 2025 | 2024 | 2024-11-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Connectivity issue | 0 | 0 | 0.027778 | 0 | 0.66667 | 0.66667 | Late start wtg Disconect to SCADA O2-24 VCB Off | Close | 0.025641 | O2-24 | 419.1389 |  | WTG Breakdown Maintenance | 15089 | 419.1389
2940 | 2024-11-25 | 2025 | 2024 | 2024-11-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.49097 | 0.49097 | 0.68194 | 0 | 4.5833 | 4.5833 | Project Pending Punch Point closing work | Close | 0.17628 | O2-24 | 2881.5799 |  | WTG Breakdown Maintenance | 15089 | 2881.5799
2941 | 2024-11-25 | 2025 | 2024 | 2024-11-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.59722 | 0.59722 | 0.71181 | 0 | 2.75 | 2.75 | WTG Manual stop for Rep Error inspection work done | Close | 0.10577 | O2-21 | 1948.2604 |  | WTG Breakdown Maintenance | 17003 | 1948.2604
2942 | 2024-11-25 | 2025 | 2024 | 2024-11-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.64792 | 0.64792 | 0.725 | 0 | 1.85 | 1.85 | WTG Manual stop for software checking work | Close | 0.071154 | O2-12 | 1236.1854 |  | WTG Breakdown Maintenance | 16037 | 1236.1854
2943 | 2024-11-25 | 2025 | 2024 | 2024-11-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.0083333 | 0.0083333 | 0.017361 | 0 | 0.21667 | 0.21667 | Checked related error data log then reset & run the WTG. | Close | 0.0083333 | O2-05 | 183.6611 |  | WTG Breakdown Maintenance | 20344 | 183.6611
2944 | 2024-11-25 | 2025 | 2024 | 2024-11-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.81944 | 0.81944 | 0.9 | 0 | 1.9333 | 1.9333 | WTG Manual stop after grid time convereter RFO Singnal not show in systeam after show singnal after reset and start wtg | Close | 0.074359 | O2-07 | 435.4028 |  | WTG Breakdown Maintenance | 5405 | 435.4028
2945 | 2024-11-25 | 2025 | 2024 | 2024-11-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Connectivity issue | 0 | 0 | 0.029861 | 0 | 0.71667 | 0.71667 | Late start wtg Disconect to SCADA O2-24 VCB Off | Close | 0.027564 | O2-21 | 507.7285 |  | WTG Breakdown Maintenance | 17003 | 507.7285
2946 | 2024-11-25 | 2025 | 2024 | 2024-11-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Connectivity issue | 0 | 0 | 0.075 | 0 | 1.8 | 1.8 | Late start wtg Disconect to SCADA O2-21 VCB Off | Close | 0.069231 | O2-06 | 1099.2 |  | WTG Breakdown Maintenance | 14656 | 1099.2
2947 | 2024-11-25 | 2025 | 2024 | 2024-11-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0 | 0 | 0.075 | 0 | 1.8 | 1.8 | VCB charge afterWTG Manual stop after grid time convereter RFO Singnal not show in systeam after show singnal after reset and start wtg | Close | 0.069231 | O2-06 | 1099.2 |  | WTG Breakdown Maintenance | 14656 | 1099.2
2948 | 2024-11-25 | 2025 | 2024 | 2024-11-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3060 | Conv. emerg.off type A | Break down | 0.82153 | 0.82153 | 0.84514 | 0 | 0.56667 | 0.56667 | Checked related error data log then reset & run the WTG. | Close | 0.021795 | O2-06 | 346.0444 |  | WTG Unscheduled Maintenance | 14656 | 346.0444
2949 | 2024-11-25 | 2025 | 2024 | 2024-11-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Break down | 0 | 0 | 0.032639 | 0 | 0.78333 | 0.78333 | After grid time error so reset and start wtg | Close | 0.030128 | O2-20 | 326.7479 |  | WTG Unscheduled Maintenance | 10011 | 326.7479
2950 | 2024-11-25 | 2025 | 2024 | 2024-11-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.82153 | 0.82153 | 0.86736 | 0 | 1.1 | 1.1 | After grid time error so reset and start wtg | Close | 0.042308 | O2-07 | 247.7292 |  | WTG Unscheduled Maintenance | 5405 | 247.7292
2951 | 2024-11-26 | 2025 | 2024 | 2024-11-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.70278 | 0.70278 | 0.70694 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2-05 | 91.7583 |  | WTG Unscheduled Maintenance | 22022 | 91.7583
2952 | 2024-11-26 | 2025 | 2024 | 2024-11-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.49028 | 0.49028 | 0.56944 | 0 | 1.9 | 1.9 | Rep Error Inspection work & Blade inspection Work | Close | 0.073077 | O2-03 | 1366.2583 |  | WTG Breakdown Maintenance | 17258 | 1366.2583
2953 | 2024-11-26 | 2025 | 2024 | 2024-11-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.17986 | 0.17986 | 0.18125 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-07 | 26.8944 |  | WTG Unscheduled Maintenance | 19364 | 26.8944
2954 | 2024-11-26 | 2025 | 2024 | 2024-11-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.4375 | 0.4375 | 0.44097 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2-07 | 67.2361 |  | WTG Unscheduled Maintenance | 19364 | 67.2361
2955 | 2024-11-26 | 2025 | 2024 | 2024-11-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 551 | Pitch motor current too high | Break down | 0.58958 | 0.58958 | 0.59444 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & run the WTG. | Close | 0.0044872 | O2-25 | 110.3569 |  | WTG Unscheduled Maintenance | 22702 | 110.3569
2956 | 2024-11-27 | 2025 | 2024 | 2024-11-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.49375 | 0.49375 | 0.69792 | 0 | 4.9 | 4.9 | Project Pending Punch Point closing work | Close | 0.18846 | O2-26 | 3028.6083 |  | WTG Breakdown Maintenance | 14834 | 3028.6083
2957 | 2024-11-27 | 2025 | 2024 | 2024-11-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Break down | 0.72222 | 0.72222 | 0.80625 | 0 | 2.0167 | 2.0167 | attend and wtg so found flate resistor Faulty Axis No:3 After Replace Flate resistor then reset and start wtg | Close | 0.077564 | O2-11 | 812.7167 |  | WTG Unscheduled Maintenance | 9672 | 812.7167
2958 | 2024-11-28 | 2025 | 2024 | 2024-11-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.48611 | 0.48611 | 0.72917 | 0 | 5.8333 | 5.8333 | Project Pending Punch Point closing work | Close | 0.22436 | O2-09 | 2716.6319 |  | WTG Breakdown Maintenance | 11177 | 2716.6319
2959 | 2024-11-28 | 2025 | 2024 | 2024-11-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.35417 | 0.35417 | 0.55903 | 0 | 4.9167 | 4.9167 | Attend and WTG check Converter connector deep switch check and connection proper tight after Repeted error occurred work Nacell Coolant pressure law so after 5 Liters coolant TOP UP After trail so ok then reset and start wtg | Close | 0.1891 | O2-15 | 2571.8264 |  | WTG Unscheduled Maintenance | 12554 | 2571.8264
2960 | 2024-11-28 | 2025 | 2024 | 2024-11-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.69444 | 0.69444 | 0.74167 | 0 | 1.1333 | 1.1333 | WTG stop for Lift Inspection work | Close | 0.04359 | O2-14 | 470.0972 |  | WTG Breakdown Maintenance | 9955 | 470.0972
2961 | 2024-11-28 | 2025 | 2024 | 2024-11-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.63542 | 0.63542 | 0.66944 | 0 | 0.81667 | 0.81667 | WTG stop for Lift Inspection work | Close | 0.03141 | O2-15 | 427.1847 |  | WTG Breakdown Maintenance | 12554 | 427.1847
2962 | 2024-11-28 | 2025 | 2024 | 2024-11-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.61944 | 0.61944 | 0.66667 | 0 | 1.1333 | 1.1333 | WTG stop For Blade inspection work | Close | 0.04359 | O2-20 | 532.6667 |  | WTG Breakdown Maintenance | 11280 | 532.6667
2963 | 2024-11-29 | 2025 | 2024 | 2024-11-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.54167 | 0.54167 | 0.54583 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2-02 | 99.7125 |  | WTG Unscheduled Maintenance | 23931 | 99.7125
2964 | 2024-11-29 | 2025 | 2024 | 2024-11-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.4375 | 0.4375 | 0.58056 | 0 | 3.4333 | 3.4333 | Project Pending Punch Point closing work | Close | 0.13205 | O2-04 | 2769.9847 |  | WTG Breakdown Maintenance | 19363 | 2769.9847
2966 | 2024-11-29 | 2025 | 2024 | 2024-11-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.49236 | 0.49236 | 0.49444 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-15 | 46.5437 |  | WTG Unscheduled Maintenance | 22341 | 46.5437
2967 | 2024-11-29 | 2025 | 2024 | 2024-11-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.53333 | 0.53333 | 0.53611 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & run the WTG. | Close | 0.0025641 | O2-06 | 76.2778 |  | WTG Unscheduled Maintenance | 27460 | 76.2778
2968 | 2024-11-29 | 2025 | 2024 | 2024-11-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.71667 | 0.71667 | 0.72083 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2-06 | 114.4167 |  | WTG Unscheduled Maintenance | 27460 | 114.4167
2970 | 2024-11-29 | 2025 | 2024 | 2024-11-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 551 | Pitch motor current too high | Break down | 0.52986 | 0.52986 | 0.53125 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-25 | 22.3458 |  | WTG Unscheduled Maintenance | 16089 | 22.3458
2971 | 2024-11-29 | 2025 | 2024 | 2024-11-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 551 | Pitch motor current too high | Major BD | 0.53958 | 0.53958 | 0.86458 | 0 | 7.8 | 7.8 | Attend wtg check Axis-02 Pitch Motor And Winding and check Pitch Brake value so ok All connection check Axia-02 After Rectifier Fuse Check so 1 Pc Faulty found so Replace New fuse After trail so ok after reset and start wtg | Close | 0.3 | O2-25 | 5228.925 |  | WTG Unscheduled Maintenance | 16089 | 5228.925
2972 | 2024-11-30 | 2025 | 2024 | 2024-11-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.56042 | 0.56042 | 0.57222 | 0 | 0.28333 | 0.28333 | Checked related error data log then reset & run the WTG. | Close | 0.010897 | O2-02 | 383.5035 |  | WTG Unscheduled Maintenance | 32485 | 383.5035
2973 | 2024-11-30 | 2025 | 2024 | 2024-11-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.55139 | 0.55139 | 0.55556 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2-04 | 126.0333 |  | WTG Unscheduled Maintenance | 30248 | 126.0333
2974 | 2024-11-30 | 2025 | 2024 | 2024-11-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 159 | SLC SF emergency stop | Break down | 0.27222 | 0.27222 | 0.40972 | 0 | 3.3 | 3.3 | Attend and check related circuit than check CCU And its connection then check DIO280 Module then found 24 v supply connection loose so retight than rest and start wtg | Close | 0.12692 | O2-15 | 4362.7375 |  | WTG Unscheduled Maintenance | 31729 | 4362.7375
2975 | 2024-11-30 | 2025 | 2024 | 2024-11-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.42361 | 0.42361 | 0.59861 | 0 | 4.2 | 4.2 | Project Pending Punch Point closing work | Close | 0.16154 | O2-15 | 5552.575 |  | WTG Breakdown Maintenance | 31729 | 5552.575
2976 | 2024-11-30 | 2025 | 2024 | 2024-11-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down | 0.37153 | 0.37153 | 0.58056 | 0 | 5.0167 | 5.0167 | Attend and wtg Replace Hydraulic Pump 9.1 valve and Hydrolic Pump Oil Refilling Work Done Also HPU Unit WTR Work Done after reset and start wtg | Close | 0.19295 | O2-21 | 7626.5875 |  | WTG Unscheduled Maintenance | 36486 | 7626.5875
2977 | 2024-11-30 | 2025 | 2024 | 2024-11-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.47083 | 0.47083 | 0.47639 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & run the WTG. | Close | 0.0051282 | O2-06 | 202.8278 |  | WTG Unscheduled Maintenance | 36509 | 202.8278
2978 | 2024-11-30 | 2025 | 2024 | 2024-11-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.53194 | 0.53194 | 0.5375 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & run the WTG. | Close | 0.0051282 | O2-06 | 202.8278 |  | WTG Unscheduled Maintenance | 36509 | 202.8278
2979 | 2024-11-30 | 2025 | 2024 | 2024-11-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.64931 | 0.64931 | 0.65347 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2-01 | 136.2708 |  | WTG Unscheduled Maintenance | 32705 | 136.2708
2980 | 2024-12-01 | 2025 | 2024 | 2024-12-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.19167 | 0.19167 | 0.24167 | 0 | 1.2 | 1.2 | WTG Manual stop Feeder -01 load High after load normal then reset and start wtg | Close | 0.046154 | O2-26 | 1308 |  | WTG Breakdown Maintenance | 26160 | 1308
2981 | 2024-12-01 | 2025 | 2024 | 2024-12-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Connectivity issue | 0.79375 | 0.79375 | 0.81875 | 0 | 0.6 | 0.6 | WTG Disconnect to SCADA after Connect then reset and start wtg | Close | 0.023077 | O2-26 | 654 |  | WTG Breakdown Maintenance | 26160 | 654
2982 | 2024-12-01 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Connectivity issue | 0.79375 | 0.79375 | 0.84236 | 0 | 1.1667 | 1.1667 | WTG Disconnect to SCADA after Connect then reset and start wtg | Close | 0.044872 | O2-05 | 1279.5903 |  | WTG Breakdown Maintenance | 26323 | 1279.5903
2983 | 2024-12-01 | 2025 | 2024 | 2024-12-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Connectivity issue | 0.79375 | 0.79375 | 0.83542 | 0 | 1 | 1 | WTG Disconnect to SCADA after Connect then reset and start wtg | Close | 0.038462 | O2-26 | 1090 |  | WTG Breakdown Maintenance | 26160 | 1090
2984 | 2024-12-01 | 2025 | 2024 | 2024-12-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.097222 | 0.097222 | 0.13542 | 0 | 0.91667 | 0.91667 | WTG Manual stop Feeder -01 load High after load normal then reset and start wtg | Close | 0.035256 | O2-12 | 1011.1597 |  | WTG Breakdown Maintenance | 26474 | 1011.1597
2985 | 2024-12-01 | 2025 | 2024 | 2024-12-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Connectivity issue | 0.79375 | 0.79375 | 0.82847 | 0 | 0.83333 | 0.83333 | WTG Disconnect to SCADA after Connect then reset and start wtg | Close | 0.032051 | O2-12 | 919.2361 |  | WTG Breakdown Maintenance | 26474 | 919.2361
2986 | 2024-12-01 | 2025 | 2024 | 2024-12-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.064583 | 0.064583 | 0.070833 | 0 | 0.15 | 0.15 | Checked related error data log then reset & run the WTG. | Close | 0.0057692 | O2-15 | 180.6625 |  | WTG Unscheduled Maintenance | 28906 | 180.6625
2987 | 2024-12-01 | 2025 | 2024 | 2024-12-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.085417 | 0.085417 | 0.090972 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & run the WTG. | Close | 0.0051282 | O2-15 | 160.5889 |  | WTG Unscheduled Maintenance | 28906 | 160.5889
2988 | 2024-12-01 | 2025 | 2024 | 2024-12-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.18542 | 0.18542 | 0.18958 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2-06 | 140.0708 |  | WTG Unscheduled Maintenance | 33617 | 140.0708
2989 | 2024-12-01 | 2025 | 2024 | 2024-12-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Connectivity issue | 0.79375 | 0.79375 | 0.81944 | 0 | 0.61667 | 0.61667 | WTG Disconnect to SCADA after Connect then reset and start wtg | Close | 0.023718 | O2-11 | 361.9063 |  | WTG Breakdown Maintenance | 14085 | 361.9063
2990 | 2024-12-01 | 2025 | 2024 | 2024-12-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Connectivity issue | 0.79375 | 0.79375 | 0.84306 | 0 | 1.1833 | 1.1833 | WTG Disconnect to SCADA after Connect then reset and start wtg | Close | 0.045513 | O2-01 | 1255.3688 |  | WTG Breakdown Maintenance | 25461 | 1255.3688
2991 | 2024-12-02 | 2025 | 2024 | 2024-12-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.80208 | 0.80208 | 0.8375 | 0 | 0.85 | 0.85 | CHEcked related error data log then Temp normal after reset & run the WTG. | Close | 0.032692 | O2-09 | 985.3271 |  | WTG Unscheduled Maintenance | 27821 | 985.3271
2992 | 2024-12-02 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.41528 | 0.41528 | 0.67292 | 0 | 6.1833 | 6.1833 | Project Pending Punch Point closing work | Close | 0.23782 | O2-02 | 7980.8799 |  | WTG Breakdown Maintenance | 30977 | 7980.8799
2993 | 2024-12-02 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.92361 | 0.92361 | 1899-12-31 | 0 | 1.8333 | 1.8333 | Attend and wtg check wind vane connection check and tight after wind vane 2 and 1 aligment properly after trail so ok after reset and start wtg | Close | 0.070513 | O2-02 | 2366.2986 |  | WTG Unscheduled Maintenance | 30977 | 2366.2986
2994 | 2024-12-02 | 2025 | 2024 | 2024-12-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3125 | Timeout ready for connection | Break down | 0.74653 | 0.74653 | 0.79444 | 0 | 1.15 | 1.15 | Attend and wtg checK ALL connection amd Retight all Connection DFIG panell and control panel after trail so ok after reset and start wtg | Close | 0.044231 | O2-01 | 1480.0021 |  | WTG Unscheduled Maintenance | 30887 | 1480.0021
2995 | 2024-12-03 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.98264 | 0.98264 | 1899-12-31 | 0 | 0.41667 | 0.41667 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.016026 | O2-05 | 425.4861 |  | WTG Breakdown Maintenance | 24508 | 425.4861
2996 | 2024-12-03 | 2025 | 2024 | 2024-12-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 5506 | Rot.br. press. high | Break down | 0.36389 | 0.36389 | 0.47778 | 0 | 2.7333 | 2.7333 | Attend and wtg inspection of rotor brake pressure valve then clean it and again refil it then reset and start turbine | Close | 0.10513 | O2-07 | 2374.8111 |  | WTG Unscheduled Maintenance | 20852 | 2374.8111
2997 | 2024-12-03 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0 | 0 | 0.030556 | 0 | 0.73333 | 0.73333 | Attend and wtg check wind vane connection check and tight after wind vane 2 and 1 aligment properly after trail so ok after reset and start wtg | Close | 0.028205 | O2-02 | 780.2361 |  | WTG Unscheduled Maintenance | 25535 | 780.2361
2998 | 2024-12-03 | 2025 | 2024 | 2024-12-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Major BD | 0.30139 | 0.30139 | 0.58958 | 0 | 6.9167 | 6.9167 | Check error related circuit so found control cable cut by rabbit so correct in then rotor brake pad error occurred so inspected it then reset and start wtg | Close | 0.26603 | O2-15 | 7959.066 |  | WTG Unscheduled Maintenance | 27617 | 7959.066
2999 | 2024-12-03 | 2025 | 2024 | 2024-12-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 5506 | Rot.br. press. high | Break down | 0.43333 | 0.43333 | 0.62917 | 0 | 4.7 | 4.7 | Attend and wtg inspection of rotor brake releted all valve then check and clean it then take trail and reset and start wtg | Close | 0.18077 | O2-21 | 5914.3625 |  | WTG Unscheduled Maintenance | 30201 | 5914.3625
3000 | 2024-12-03 | 2025 | 2024 | 2024-12-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.93333 | 0.93333 | 0.94167 | 0 | 0.2 | 0.2 | CHECK Error related data so ok after reset and start wtg | Close | 0.0076923 | O2-21 | 251.675 |  | WTG Unscheduled Maintenance | 30201 | 251.675
3001 | 2024-12-04 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.075 | 0.075 | 0.082639 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & run the WTG. | Close | 0.0070513 | O2-05 | 290.4993 |  | WTG Unscheduled Maintenance | 38029 | 290.4993
3002 | 2024-12-04 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.13125 | 0.13125 | 0.14028 | 0 | 0.21667 | 0.21667 | Checked related error data log then reset & run the WTG. | Close | 0.0083333 | O2-05 | 343.3174 |  | WTG Unscheduled Maintenance | 38029 | 343.3174
3003 | 2024-12-04 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0 | 0 | 0.011111 | 0 | 0.26667 | 0.26667 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.010256 | O2-05 | 422.5444 |  | WTG Breakdown Maintenance | 38029 | 422.5444
3004 | 2024-12-04 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.14861 | 0.14861 | 0.24722 | 0 | 2.3667 | 2.3667 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.091026 | O2-05 | 3750.0819 |  | WTG Breakdown Maintenance | 38029 | 3750.0819
3005 | 2024-12-04 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.28611 | 0.28611 | 0.33889 | 0 | 1.2667 | 1.2667 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.048718 | O2-05 | 2007.0861 |  | WTG Breakdown Maintenance | 38029 | 2007.0861
3006 | 2024-12-04 | 2025 | 2024 | 2024-12-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.49583 | 0.49583 | 0.50069 | 0 | 0.11667 | 0.11667 | wtg stop for Software update work | Close | 0.0044872 | O2-09 | 177.8049 |  | WTG Breakdown Maintenance | 36577 | 177.8049
3007 | 2024-12-04 | 2025 | 2024 | 2024-12-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.74653 | 0.74653 | 0.75486 | 0 | 0.2 | 0.2 | WTG software update Work done than start wtg | Close | 0.0076923 | O2-26 | 331.8417 |  | WTG Breakdown Maintenance | 39821 | 331.8417
3008 | 2024-12-04 | 2025 | 2024 | 2024-12-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.69653 | 0.69653 | 0.74931 | 0 | 1.2667 | 1.2667 | After CAN RFO signal coming than start WTG. | Close | 0.048718 | O2-07 | 1698.3889 |  | WTG Unscheduled Maintenance | 32180 | 1698.3889
3009 | 2024-12-04 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.64375 | 0.64375 | 0.65069 | 0 | 0.16667 | 0.16667 | WTG software update Work done than start wtg | Close | 0.0064103 | O2-02 | 173.8542 |  | WTG Breakdown Maintenance | 25035 | 173.8542
3010 | 2024-12-04 | 2025 | 2024 | 2024-12-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.16181 | 0.16181 | 0.20694 | 0 | 1.0833 | 1.0833 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.041667 | O2-26 | 1797.4757 |  | WTG Breakdown Maintenance | 39821 | 1797.4757
3011 | 2024-12-04 | 2025 | 2024 | 2024-12-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.60625 | 0.60625 | 0.72222 | 0 | 2.7833 | 2.7833 | Project Pending Punch Point closing work | Close | 0.10705 | O2-03 | 4610.2438 |  | WTG Breakdown Maintenance | 39753 | 4610.2438
3012 | 2024-12-04 | 2025 | 2024 | 2024-12-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.72222 | 0.72222 | 0.73264 | 0 | 0.25 | 0.25 | wtg stop for Software update work | Close | 0.0096154 | O2-03 | 414.0937 |  | WTG Breakdown Maintenance | 39753 | 414.0937
3013 | 2024-12-04 | 2025 | 2024 | 2024-12-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.18403 | 0.18403 | 0.19375 | 0 | 0.23333 | 0.23333 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.0089744 | O2-15 | 368.5986 |  | WTG Breakdown Maintenance | 37913 | 368.5986
3014 | 2024-12-04 | 2025 | 2024 | 2024-12-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.16389 | 0.16389 | 0.17153 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & run the WTG. | Close | 0.0070513 | O2-12 | 288.0778 |  | WTG Unscheduled Maintenance | 37712 | 288.0778
3015 | 2024-12-04 | 2025 | 2024 | 2024-12-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.19028 | 0.19028 | 0.19792 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & run the WTG. | Close | 0.0070513 | O2-12 | 288.0778 |  | WTG Unscheduled Maintenance | 37712 | 288.0778
3016 | 2024-12-04 | 2025 | 2024 | 2024-12-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.21597 | 0.21597 | 0.22361 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & run the WTG. | Close | 0.0070513 | O2-12 | 288.0778 |  | WTG Unscheduled Maintenance | 37712 | 288.0778
3017 | 2024-12-04 | 2025 | 2024 | 2024-12-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.25625 | 0.25625 | 0.32778 | 0 | 1.7167 | 1.7167 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.066026 | O2-12 | 2697.4556 |  | WTG Breakdown Maintenance | 37712 | 2697.4556
3018 | 2024-12-04 | 2025 | 2024 | 2024-12-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.69653 | 0.69653 | 0.74931 | 0 | 1.2667 | 1.2667 | After CAN RFO signal coming than start WTG. | Close | 0.048718 | O2-06 | 1974.2583 |  | WTG Unscheduled Maintenance | 37407 | 1974.2583
3019 | 2024-12-04 | 2025 | 2024 | 2024-12-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.69653 | 0.69653 | 0.74792 | 0 | 1.2333 | 1.2333 | After CAN RFO signal coming than start WTG. | Close | 0.047436 | O2-06 | 1922.3042 |  | WTG Unscheduled Maintenance | 37407 | 1922.3042
3020 | 2024-12-04 | 2025 | 2024 | 2024-12-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.33333 | 0.33333 | 0.33681 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2-06 | 129.8854 |  | WTG Unscheduled Maintenance | 37407 | 129.8854
3021 | 2024-12-04 | 2025 | 2024 | 2024-12-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.69653 | 0.69653 | 0.75625 | 0 | 1.4333 | 1.4333 | After CAN RFO signal coming than start WTG. | Close | 0.055128 | O2-06 | 2234.0292 |  | WTG Unscheduled Maintenance | 37407 | 2234.0292
3022 | 2024-12-04 | 2025 | 2024 | 2024-12-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 525 | Overload axis 2 | Break down | 0.077083 | 0.077083 | 0.12431 | 0 | 1.1333 | 1.1333 | Checked related error data log then reset & run the WTG. | Close | 0.04359 | O2-11 | 1311.1722 |  | WTG Unscheduled Maintenance | 27766 | 1311.1722
3023 | 2024-12-04 | 2025 | 2024 | 2024-12-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.56806 | 0.56806 | 0.68681 | 0 | 2.85 | 2.85 | Attend and check error related ckt than check all Axis 1 connection than found Pitch motor 1 Motor encoder connector loose so tight it than reset and start WTG. | Close | 0.10962 | O2-11 | 3297.2125 |  | WTG Unscheduled Maintenance | 27766 | 3297.2125
3024 | 2024-12-04 | 2025 | 2024 | 2024-12-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.68125 | 0.68125 | 0.68819 | 0 | 0.16667 | 0.16667 | WTG software update Work done than start wtg | Close | 0.0064103 | O2-25 | 280.3125 |  | WTG Breakdown Maintenance | 40365 | 280.3125
3025 | 2024-12-04 | 2025 | 2024 | 2024-12-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.64861 | 0.64861 | 0.65556 | 0 | 0.16667 | 0.16667 | Checked related error data log then reset & run the WTG. | Close | 0.0064103 | O2-01 | 271.3403 |  | WTG Unscheduled Maintenance | 39073 | 271.3403
3026 | 2024-12-05 | 2025 | 2024 | 2024-12-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 158 | SLC SF max. rotor brake pad temp. | Break down | 0.48403 | 0.48403 | 0.50208 | 0 | 0.43333 | 0.43333 | Checked related error data log then reset & run the WTG. | Close | 0.016667 | O2-09 | 513.6264 |  | WTG Unscheduled Maintenance | 28447 | 513.6264
3027 | 2024-12-05 | 2025 | 2024 | 2024-12-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 158 | SLC SF max. rotor brake pad temp. | Break down | 0.50764 | 0.50764 | 0.51597 | 0 | 0.2 | 0.2 | Checked related error data log then reset & run the WTG. | Close | 0.0076923 | O2-09 | 237.0583 |  | WTG Unscheduled Maintenance | 28447 | 237.0583
3028 | 2024-12-05 | 2025 | 2024 | 2024-12-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 158 | SLC SF max. rotor brake pad temp. | Break down | 0.58194 | 0.58194 | 0.67847 | 0 | 2.3167 | 2.3167 | Attend and check error related CKT than found faulty rotor brake Pad 1 sensor faulty so replace with new one than start WTG. | Close | 0.089103 | O2-09 | 2745.9257 |  | WTG Unscheduled Maintenance | 28447 | 2745.9257
3029 | 2024-12-05 | 2025 | 2024 | 2024-12-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.17361 | 0.17361 | 0.17847 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & run the WTG. | Close | 0.0044872 | O2-15 | 115.8646 |  | WTG Unscheduled Maintenance | 23835 | 115.8646
3030 | 2024-12-05 | 2025 | 2024 | 2024-12-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.46875 | 0.46875 | 0.48264 | 0 | 0.33333 | 0.33333 | WTG software update Work done than wip, | Close | 0.012821 | O2-10 | 320.8333 |  | WTG Breakdown Maintenance | 23100 | 320.8333
3031 | 2024-12-05 | 2025 | 2024 | 2024-12-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.48333 | 0.48333 | 0.63333 | 0 | 3.6 | 3.6 | After Project Pending Punch Point closing work done than start WTG. | Close | 0.13846 | O2-10 | 3465 |  | WTG Breakdown Maintenance | 23100 | 3465
3032 | 2024-12-05 | 2025 | 2024 | 2024-12-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.49028 | 0.49028 | 0.50139 | 0 | 0.26667 | 0.26667 | WTG software update Work done than reset and start WTG. | Close | 0.010256 | O2-21 | 308.5 |  | WTG Breakdown Maintenance | 27765 | 308.5
3033 | 2024-12-05 | 2025 | 2024 | 2024-12-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.44861 | 0.44861 | 0.47222 | 0 | 0.56667 | 0.56667 | WTG software update Work done than reset and start WTG. | Close | 0.021795 | O2-24 | 584.1153 |  | WTG Breakdown Maintenance | 24739 | 584.1153
3034 | 2024-12-06 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.46597 | 0.46597 | 0.46875 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & run the WTG. | Close | 0.0025641 | O2-02 | 55.7611 |  | WTG Unscheduled Maintenance | 20074 | 55.7611
3035 | 2024-12-06 | 2025 | 2024 | 2024-12-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.48542 | 0.48542 | 0.60694 | 0 | 2.9167 | 2.9167 | Project Pending Punch Point closing work done than start WTG. | Close | 0.11218 | O2-21 | 2003.0208 |  | WTG Breakdown Maintenance | 16482 | 2003.0208
3036 | 2024-12-06 | 2025 | 2024 | 2024-12-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.052083 | 0.052083 | 0.056944 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & run the WTG. | Close | 0.0044872 | O2-26 | 114.0028 |  | WTG Unscheduled Maintenance | 23452 | 114.0028
3037 | 2024-12-06 | 2025 | 2024 | 2024-12-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 158 | SLC SF max. rotor brake pad temp. | Break down | 0.64236 | 0.64236 | 0.65625 | 0 | 0.33333 | 0.33333 | Checked related error data log then reset & run the WTG. | Close | 0.012821 | O2-03 | 316.6111 |  | WTG Unscheduled Maintenance | 22796 | 316.6111
3038 | 2024-12-06 | 2025 | 2024 | 2024-12-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 158 | SLC SF max. rotor brake pad temp. | Break down | 0.69583 | 0.69583 | 0.77847 | 0 | 1.9833 | 1.9833 | Attend and check error related CKT than found faulty rotor brake Pad 1 sensor faulty so replace with new one than start WTG. | Close | 0.076282 | O2-03 | 1883.8361 |  | WTG Unscheduled Maintenance | 22796 | 1883.8361
3039 | 2024-12-06 | 2025 | 2024 | 2024-12-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.67292 | 0.67292 | 0.68889 | 0 | 0.38333 | 0.38333 | WTG software update Work done than reset and start WTG. | Close | 0.014744 | O2-03 | 364.1028 |  | WTG Breakdown Maintenance | 22796 | 364.1028
3040 | 2024-12-06 | 2025 | 2024 | 2024-12-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.60556 | 0.60556 | 0.63056 | 0 | 0.6 | 0.6 | WTG stop For Blade inspection work done than start WTG. | Close | 0.023077 | O2-12 | 562.05 |  | WTG Breakdown Maintenance | 22482 | 562.05
3041 | 2024-12-06 | 2025 | 2024 | 2024-12-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.67222 | 0.67222 | 0.67708 | 0 | 0.11667 | 0.11667 | WTG software update Work done than reset and start WTG. | Close | 0.0044872 | O2-11 | 107.7222 |  | WTG Breakdown Maintenance | 22160 | 107.7222
3042 | 2024-12-06 | 2025 | 2024 | 2024-12-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.43056 | 0.43056 | 0.46528 | 0 | 0.83333 | 0.83333 | WTG stop For Blade inspection work done than start WTG. | Close | 0.032051 | O2-06 | 496.25 |  | WTG Breakdown Maintenance | 14292 | 496.25
3043 | 2024-12-06 | 2025 | 2024 | 2024-12-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.69236 | 0.69236 | 0.69444 | 0 | 0.05 | 0.05 | WTG software update Work done than reset and start WTG. | Close | 0.0019231 | O2-24 | 43.85 |  | WTG Breakdown Maintenance | 21048 | 43.85
3044 | 2024-12-06 | 2025 | 2024 | 2024-12-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.62083 | 0.62083 | 0.62847 | 0 | 0.18333 | 0.18333 | WTG software update Work done than wip, | Close | 0.0070513 | O2-20 | 143.0611 |  | WTG Breakdown Maintenance | 18728 | 143.0611
3045 | 2024-12-06 | 2025 | 2024 | 2024-12-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.62847 | 0.62847 | 0.66042 | 0 | 0.76667 | 0.76667 | WTG Stop for Customer safety Audit done than Start WTG. | Close | 0.029487 | O2-20 | 598.2556 |  | WTG Breakdown Maintenance | 18728 | 598.2556
3046 | 2024-12-07 | 2025 | 2024 | 2024-12-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.48403 | 0.48403 | 0.48611 | 0 | 0.05 | 0.05 | WTG software update Work done than reset and start WTG. | Close | 0.0019231 | O2-26 | 8.5271 |  | WTG Breakdown Maintenance | 4093 | 8.5271
3047 | 2024-12-07 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.51181 | 0.51181 | 0.5125 | 0 | 0.016667 | 0.016667 | WTG software update Work done than reset and start WTG. | Close | 0.00064103 | O2-05 | 3.5444 |  | WTG Breakdown Maintenance | 5104 | 3.5444
3048 | 2024-12-07 | 2025 | 2024 | 2024-12-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.48681 | 0.48681 | 0.48819 | 0 | 0.033333 | 0.033333 | WTG software update Work done than reset and start WTG. | Close | 0.0012821 | O2-09 | 6.5722 |  | WTG Breakdown Maintenance | 4732 | 6.5722
3049 | 2024-12-07 | 2025 | 2024 | 2024-12-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.54236 | 0.54236 | 0.54514 | 0 | 0.066667 | 0.066667 | WTG software update Work done than reset and start WTG. | Close | 0.0025641 | O2-07 | 10.9222 |  | WTG Breakdown Maintenance | 3932 | 10.9222
3050 | 2024-12-07 | 2025 | 2024 | 2024-12-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 1316 | Timeout fault rotor bear. lubr. | Break down | 0.54583 | 0.54583 | 0.61042 | 0 | 1.55 | 1.55 | Checked related error data log and apply soft reboot then reset & run the WTG. | Close | 0.059615 | O2-07 | 253.9417 |  | WTG Unscheduled Maintenance | 3932 | 253.9417
3051 | 2024-12-07 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.56042 | 0.56042 | 0.56181 | 0 | 0.033333 | 0.033333 | WTG software update Work done than reset and start WTG. | Close | 0.0012821 | O2-02 | 6.7764 |  | WTG Breakdown Maintenance | 4879 | 6.7764
3052 | 2024-12-07 | 2025 | 2024 | 2024-12-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.54653 | 0.54653 | 0.54861 | 0 | 0.05 | 0.05 | WTG software update Work done than reset and start WTG. | Close | 0.0019231 | O2-21 | 6.3396 |  | WTG Breakdown Maintenance | 3043 | 6.3396
3053 | 2024-12-07 | 2025 | 2024 | 2024-12-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.48958 | 0.48958 | 0.49097 | 0 | 0.033333 | 0.033333 | WTG software update Work done than reset and start WTG. | Close | 0.0012821 | O2-04 | 7.4833 |  | WTG Breakdown Maintenance | 5388 | 7.4833
3054 | 2024-12-07 | 2025 | 2024 | 2024-12-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.49167 | 0.49167 | 0.49306 | 0 | 0.033333 | 0.033333 | WTG software update Work done than reset and start WTG. | Close | 0.0012821 | O2-26 | 5.6847 |  | WTG Breakdown Maintenance | 4093 | 5.6847
3055 | 2024-12-07 | 2025 | 2024 | 2024-12-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.55069 | 0.55069 | 0.55139 | 0 | 0.016667 | 0.016667 | WTG software update Work done than reset and start WTG. | Close | 0.00064103 | O2-14 | 3.5958 |  | WTG Breakdown Maintenance | 5178 | 3.5958
3056 | 2024-12-07 | 2025 | 2024 | 2024-12-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.49375 | 0.49375 | 0.49583 | 0 | 0.05 | 0.05 | WTG software update Work done than reset and start WTG. | Close | 0.0019231 | O2-12 | 8.0958 |  | WTG Breakdown Maintenance | 3886 | 8.0958
3057 | 2024-12-07 | 2025 | 2024 | 2024-12-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.49583 | 0.49583 | 0.49792 | 0 | 0.05 | 0.05 | WTG software update Work done than reset and start WTG. | Close | 0.0019231 | O2-10 | 8.9896 |  | WTG Breakdown Maintenance | 4315 | 8.9896
3058 | 2024-12-07 | 2025 | 2024 | 2024-12-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.49861 | 0.49861 | 0.49931 | 0 | 0.016667 | 0.016667 | WTG software update Work done than reset and start WTG. | Close | 0.00064103 | O2-21 | 2.1132 |  | WTG Breakdown Maintenance | 3043 | 2.1132
3059 | 2024-12-07 | 2025 | 2024 | 2024-12-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.5 | 0.5 | 0.50208 | 0 | 0.05 | 0.05 | WTG software update Work done than reset and start WTG. | Close | 0.0019231 | O2-06 | 9.6292 |  | WTG Breakdown Maintenance | 4622 | 9.6292
3060 | 2024-12-07 | 2025 | 2024 | 2024-12-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.48125 | 0.48125 | 0.72014 | 0 | 5.7333 | 5.7333 | Project Pending Punch Point closing work, Top up coolant 15 Ltr on converter and nacalle coolant unit and found axis 3 20 ohm chopper resistor faulty so replace it than start WTG. | Close | 0.22051 | O2-06 | 1104.1444 |  | WTG Breakdown Maintenance | 4622 | 1104.1444
3061 | 2024-12-07 | 2025 | 2024 | 2024-12-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.52569 | 0.52569 | 0.52708 | 0 | 0.033333 | 0.033333 | WTG software update Work done than reset and start WTG. | Close | 0.0012821 | O2-06 | 6.4194 |  | WTG Breakdown Maintenance | 4622 | 6.4194
3062 | 2024-12-07 | 2025 | 2024 | 2024-12-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.50764 | 0.50764 | 0.50903 | 0 | 0.033333 | 0.033333 | WTG software update Work done than reset and start WTG. | Close | 0.0012821 | O2-11 | 7.5028 |  | WTG Breakdown Maintenance | 5402 | 7.5028
3063 | 2024-12-07 | 2025 | 2024 | 2024-12-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.55069 | 0.55069 | 0.55347 | 0 | 0.066667 | 0.066667 | WTG software update Work done than reset and start WTG. | Close | 0.0025641 | O2-25 | 14.4139 |  | WTG Breakdown Maintenance | 5189 | 14.4139
3064 | 2024-12-07 | 2025 | 2024 | 2024-12-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.50972 | 0.50972 | 0.51111 | 0 | 0.033333 | 0.033333 | WTG software update Work done than reset and start WTG. | Close | 0.0012821 | O2-01 | 6.2542 |  | WTG Breakdown Maintenance | 4503 | 6.2542
3065 | 2024-12-08 | 2025 | 2024 | 2024-12-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.58194 | 0.58194 | 0.64583 | 0 | 1.5333 | 1.5333 | WTG Disconnect from Scada so check it than attend WTG and new software upload than apply reboot than rset and start WTG. | Close | 0.058974 | O2-26 | 886.2667 |  | WTG Breakdown Maintenance | 13872 | 886.2667
3066 | 2024-12-08 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Road issue | 0 | 0 | 0.99999 | 0 | 23.9997 | 23.9997 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | Close | 0.92307 | O2-05 | 11386.8682 |  | WTG Unscheduled Maintenance | 11387 | 11386.8682
3067 | 2024-12-08 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.57708 | 0.57708 | 0.69167 | 0 | 2.75 | 2.75 | After Feeder Charge error occurred so attend and check error related ckt than found loose connnector axis 1 motor encoder so retight it than reset and start WTG. | Close | 0.10577 | O2-02 | 0 |  | WTG Unscheduled Maintenance | 0 | 0
3068 | 2024-12-08 | 2025 | 2024 | 2024-12-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.0048611 | 0.0048611 | 0.14306 | 0 | 3.3167 | 3.3167 | WTG Disconnect from Scada so check it than attend WTG and new software upload than apply reboot than rset and start WTG. | Close | 0.12756 | O2-11 | 2019.0208 |  | WTG Breakdown Maintenance | 14610 | 2019.0208
3069 | 2024-12-08 | 2025 | 2024 | 2024-12-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.046528 | 0.046528 | 0.063889 | 0 | 0.41667 | 0.41667 | WTG Manual stop after grid time convertor RFO Signal not show in system after show signal after reset and start wtg | Close | 0.016026 | O2-01 | 228.2465 |  | WTG Breakdown Maintenance | 13147 | 228.2465
3070 | 2024-12-08 | 2025 | 2024 | 2024-12-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.67292 | 0.67292 | 0.67431 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-01 | 18.2597 |  | WTG Unscheduled Maintenance | 13147 | 18.2597 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
3071 | 2024-12-09 | 2025 | 2024 | 2024-12-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.18819 | 0.18819 | 0.31389 | 0 | 3.0167 | 3.0167 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.11603 | O2-26 | 4942.5569 |  | WTG Breakdown Maintenance | 39322 | 4942.5569
3072 | 2024-12-09 | 2025 | 2024 | 2024-12-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.15625 | 0.15625 | 0.23264 | 0 | 1.8333 | 1.8333 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.070513 | O2-11 | 3138.9722 |  | WTG Breakdown Maintenance | 41092 | 3138.9722
3073 | 2024-12-09 | 2025 | 2024 | 2024-12-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.26458 | 0.26458 | 0.28264 | 0 | 0.43333 | 0.43333 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.016667 | O2-11 | 741.9389 |  | WTG Breakdown Maintenance | 41092 | 741.9389
3074 | 2024-12-09 | 2025 | 2024 | 2024-12-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.44306 | 0.44306 | 0.45208 | 0 | 0.21667 | 0.21667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-13 and disconnected to scada. | Close | 0.0083333 | O2-26 | 354.9903 |  | WTG Unscheduled Maintenance | 39322 | 354.9903
3075 | 2024-12-09 | 2025 | 2024 | 2024-12-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.83819 | 0.83819 | 0.85556 | 0 | 0.41667 | 0.41667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-26 and disconnected to scada. | Close | 0.016026 | O2-26 | 682.6736 |  | WTG Unscheduled Maintenance | 39322 | 682.6736
3076 | 2024-12-09 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | ROW issue | 0 | 0 | 0.41042 | 0 | 9.85 | 9.85 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable & Also ROW issue. | open | 0.37885 | O2-05 | 15299.9229 |  | WTG Unscheduled Maintenance | 37279 | 15299.9229
3077 | 2024-12-09 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | ROW issue | 0.44306 | 0.44306 | 0.82153 | 0 | 9.0833 | 9.0833 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable & Also ROW issue. | open | 0.34936 | O2-05 | 14109.066 |  | WTG Unscheduled Maintenance | 37279 | 14109.066
3078 | 2024-12-09 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | ROW issue | 0.83819 | 0.83819 | 1899-12-31 | 0 | 3.8833 | 3.8833 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable & Also ROW issue. | open | 0.14936 | O2-05 | 6031.9493 |  | WTG Unscheduled Maintenance | 37279 | 6031.9493
3079 | 2024-12-09 | 2025 | 2024 | 2024-12-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 7025 | Configuration error | Break down | 0.44306 | 0.44306 | 0.45764 | 0 | 0.35 | 0.35 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-13 and disconnected to scada. | Close | 0.013462 | O2-09 | 649.775 |  | WTG Unscheduled Maintenance | 44556 | 649.775
3080 | 2024-12-09 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.44306 | 0.44306 | 0.46806 | 0 | 0.6 | 0.6 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-13 and disconnected to scada. | Close | 0.023077 | O2-02 | 0 |  | WTG Unscheduled Maintenance | 0 | 0
3081 | 2024-12-09 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 158 | SLC SF max. rotor brake pad temp. | Break down | 0.83819 | 0.83819 | 0.87222 | 0 | 0.81667 | 0.81667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-26 and disconnected to scada. | Close | 0.03141 | O2-02 | 0 |  | WTG Unscheduled Maintenance | 0 | 0
3082 | 2024-12-09 | 2025 | 2024 | 2024-12-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 158 | SLC SF max. rotor brake pad temp. | Break down | 0.44306 | 0.44306 | 0.45347 | 0 | 0.25 | 0.25 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-13 and disconnected to scada. | Close | 0.0096154 | O2-26 | 409.6042 |  | WTG Unscheduled Maintenance | 39322 | 409.6042
3083 | 2024-12-09 | 2025 | 2024 | 2024-12-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Break down | 0.44306 | 0.44306 | 0.45278 | 0 | 0.23333 | 0.23333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-13 and disconnected to scada. | Close | 0.0089744 | O2-03 | 428.4 |  | WTG Unscheduled Maintenance | 44064 | 428.4
3084 | 2024-12-09 | 2025 | 2024 | 2024-12-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 158 | SLC SF max. rotor brake pad temp. | Break down | 0.44306 | 0.44306 | 0.45833 | 0 | 0.36667 | 0.36667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.014103 | O2-15 | 594.4889 |  | WTG Unscheduled Maintenance | 38912 | 594.4889
3085 | 2024-12-09 | 2025 | 2024 | 2024-12-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 158 | SLC SF max. rotor brake pad temp. | Break down | 0.83819 | 0.83819 | 0.89306 | 0 | 1.3167 | 1.3167 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.050641 | O2-15 | 2134.7556 |  | WTG Unscheduled Maintenance | 38912 | 2134.7556
3086 | 2024-12-09 | 2025 | 2024 | 2024-12-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 158 | SLC SF max. rotor brake pad temp. | Break down | 0.44306 | 0.44306 | 0.46389 | 0 | 0.5 | 0.5 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-13 and disconnected to scada. | Close | 0.019231 | O2-12 | 865.5417 |  | WTG Unscheduled Maintenance | 41546 | 865.5417
3087 | 2024-12-09 | 2025 | 2024 | 2024-12-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.46736 | 0.46736 | 0.60625 | 0 | 3.3333 | 3.3333 | Project Pending Punch Point closing work done than start WTG. | Close | 0.12821 | O2-21 | 5570.2778 |  | WTG Breakdown Maintenance | 40106 | 5570.2778
3088 | 2024-12-09 | 2025 | 2024 | 2024-12-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 158 | SLC SF max. rotor brake pad temp. | Break down | 0.44306 | 0.44306 | 0.45556 | 0 | 0.3 | 0.3 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-13 and disconnected to scada. | Close | 0.011538 | O2-11 | 513.65 |  | WTG Unscheduled Maintenance | 41092 | 513.65
3089 | 2024-12-09 | 2025 | 2024 | 2024-12-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 158 | SLC SF max. rotor brake pad temp. | Break down | 0.44306 | 0.44306 | 0.45833 | 0 | 0.36667 | 0.36667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-13 and disconnected to scada. | Close | 0.014103 | O2-25 | 615.4958 |  | WTG Unscheduled Maintenance | 40287 | 615.4958
3090 | 2024-12-09 | 2025 | 2024 | 2024-12-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 158 | SLC SF max. rotor brake pad temp. | Break down | 0.83819 | 0.83819 | 0.85903 | 0 | 0.5 | 0.5 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-26 and disconnected to scada. | Close | 0.019231 | O2-25 | 839.3125 |  | WTG Unscheduled Maintenance | 40287 | 839.3125
3091 | 2024-12-09 | 2025 | 2024 | 2024-12-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 158 | SLC SF max. rotor brake pad temp. | Break down | 0.44306 | 0.44306 | 0.47292 | 0 | 0.71667 | 0.71667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-13 and disconnected to scada. | Close | 0.027564 | O2-01 | 922.4396 |  | WTG Unscheduled Maintenance | 30891 | 922.4396
3092 | 2024-12-10 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Road issue | 0 | 0 | 0.99999 | 0 | 23.9997 | 23.9997 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | open | 0.92307 | O2-05 | 44941.4798 |  | WTG Unscheduled Maintenance | 44942 | 44941.4798
3093 | 2024-12-10 | 2025 | 2024 | 2024-12-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.18264 | 0.18264 | 0.32639 | 0 | 3.45 | 3.45 | attend and found hopewind convertor panel fan not working so check and found k16 relay is Malfunctioning so carect it then start wtg | Close | 0.13269 | O2-07 | 5863.85 |  | WTG Unscheduled Maintenance | 40792 | 5863.85
3094 | 2024-12-10 | 2025 | 2024 | 2024-12-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.10486 | 0.10486 | 0.10903 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2-21 | 196.075 |  | WTG Unscheduled Maintenance | 47058 | 196.075
3095 | 2024-12-10 | 2025 | 2024 | 2024-12-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.19444 | 0.19444 | 0.26111 | 0 | 1.6 | 1.6 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.061538 | O2-15 | 2485.4 |  | WTG Breakdown Maintenance | 37281 | 2485.4
3096 | 2024-12-10 | 2025 | 2024 | 2024-12-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 6007 | Overload yaw motors group 1 | Break down | 0.43264 | 0.43264 | 0.51944 | 0 | 2.0833 | 2.0833 | attend and found yaw motor MCB trip and so check and found loose cannections on MCB so tight and start wtg | Close | 0.080128 | O2-12 | 3894.0972 |  | WTG Unscheduled Maintenance | 44860 | 3894.0972
3097 | 2024-12-10 | 2025 | 2024 | 2024-12-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.017361 | 0.017361 | 0.04375 | 0 | 0.63333 | 0.63333 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.024359 | O2-10 | 1010.325 |  | WTG Breakdown Maintenance | 38286 | 1010.325
3098 | 2024-12-10 | 2025 | 2024 | 2024-12-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.090972 | 0.090972 | 0.12361 | 0 | 0.78333 | 0.78333 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.030128 | O2-10 | 1249.6125 |  | WTG Breakdown Maintenance | 38286 | 1249.6125
3099 | 2024-12-10 | 2025 | 2024 | 2024-12-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.16667 | 0.16667 | 0.21944 | 0 | 1.2667 | 1.2667 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.048718 | O2-10 | 2020.65 |  | WTG Breakdown Maintenance | 38286 | 2020.65
3100 | 2024-12-10 | 2025 | 2024 | 2024-12-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.10486 | 0.10486 | 0.11042 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & run the WTG. | Close | 0.0051282 | O2-21 | 261.4333 |  | WTG Unscheduled Maintenance | 47058 | 261.4333
3101 | 2024-12-10 | 2025 | 2024 | 2024-12-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.058333 | 0.058333 | 0.0625 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2-06 | 184.1333 |  | WTG Unscheduled Maintenance | 44192 | 184.1333
3102 | 2024-12-10 | 2025 | 2024 | 2024-12-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.59583 | 0.59583 | 0.60625 | 0 | 0.25 | 0.25 | Checked related error data log then reset & run the WTG. | Close | 0.0096154 | O2-06 | 460.3333 |  | WTG Unscheduled Maintenance | 44192 | 460.3333
3103 | 2024-12-10 | 2025 | 2024 | 2024-12-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.070833 | 0.070833 | 0.086111 | 0 | 0.36667 | 0.36667 | Checked related error data log then reset & run the WTG. | Close | 0.014103 | O2-06 | 675.1556 |  | WTG Unscheduled Maintenance | 44192 | 675.1556
3104 | 2024-12-11 | 2025 | 2024 | 2024-12-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 157 | SLC SF max. tower oscillation | Break down | 0.19792 | 0.19792 | 0.27083 | 0 | 1.75 | 1.75 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-23 and disconnected to scada. | Close | 0.067308 | O2-26 | 1687.875 |  | WTG Unscheduled Maintenance | 23148 | 1687.875
3105 | 2024-12-11 | 2025 | 2024 | 2024-12-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.66111 | 0.66111 | 0.67778 | 0 | 0.4 | 0.4 | WTG Manual stop for blade inspection work | Close | 0.015385 | O2-26 | 385.8 |  | WTG Breakdown Maintenance | 23148 | 385.8
3106 | 2024-12-11 | 2025 | 2024 | 2024-12-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 7025 | Configuration error | Break down | 0.86458 | 0.86458 | 0.92847 | 0 | 1.5333 | 1.5333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-26 and disconnected to scada. | Close | 0.058974 | O2-26 | 1478.9 |  | WTG Unscheduled Maintenance | 23148 | 1478.9
3107 | 2024-12-11 | 2025 | 2024 | 2024-12-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Break down | 0.97431 | 0.97431 | 1899-12-31 | 0 | 0.61667 | 0.61667 | WIP | Close | 0.023718 | O2-26 | 594.775 |  | WTG Unscheduled Maintenance | 23148 | 594.775
3108 | 2024-12-11 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Road issue | 0 | 0 | 0.17361 | 0 | 4.1667 | 4.1667 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | Close | 0.16026 | O2-05 | 4225.6944 |  | WTG Unscheduled Maintenance | 24340 | 4225.6944
3109 | 2024-12-11 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Road issue | 0.19792 | 0.19792 | 0.84583 | 0 | 15.55 | 15.55 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | Close | 0.59808 | O2-05 | 15770.2917 |  | WTG Unscheduled Maintenance | 24340 | 15770.2917
3110 | 2024-12-11 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Road issue | 0.86458 | 0.86458 | 0.99999 | 0 | 3.2497 | 3.2497 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | Close | 0.12499 | O2-05 | 3295.76 |  | WTG Unscheduled Maintenance | 24340 | 3295.76
3111 | 2024-12-11 | 2025 | 2024 | 2024-12-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Connectivity issue | 0.19792 | 0.19792 | 0.27083 | 0 | 1.75 | 1.75 | after grid resume Wtg is disconnected to scada for VCB trip O2-23 | Close | 0.067308 | O2-09 | 1819.7812 |  | WTG Unscheduled Maintenance | 24957 | 1819.7812
3112 | 2024-12-11 | 2025 | 2024 | 2024-12-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.27083 | 0.27083 | 0.35278 | 0 | 1.9667 | 1.9667 | after grid resume Wtg in error so Checked related error data log then apply hard reboot then reset & start the WTG. Late reset due to VCB trip O2-23 and disconnected to scada. | Close | 0.075641 | O2-09 | 2045.0875 |  | WTG Unscheduled Maintenance | 24957 | 2045.0875
3113 | 2024-12-11 | 2025 | 2024 | 2024-12-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 155 | Incorrect Error Code | Break down | 0.86458 | 0.86458 | 0.90625 | 0 | 1 | 1 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-09 and disconnected to scada. | Close | 0.038462 | O2-09 | 1039.875 |  | WTG Unscheduled Maintenance | 24957 | 1039.875
3114 | 2024-12-11 | 2025 | 2024 | 2024-12-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.12569 | 0.12569 | 0.13264 | 0 | 0.16667 | 0.16667 | Checked related error data log then reset & run the WTG. | Close | 0.0064103 | O2-07 | 214.5486 |  | WTG Unscheduled Maintenance | 30895 | 214.5486
3115 | 2024-12-11 | 2025 | 2024 | 2024-12-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 5506 | Rot.br. press. high | Break down | 0.13333 | 0.13333 | 0.13681 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2-07 | 107.2743 |  | WTG Unscheduled Maintenance | 30895 | 107.2743
3116 | 2024-12-11 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Connectivity issue | 0.19792 | 0.19792 | 0.27083 | 0 | 1.75 | 1.75 | after grid resume Wtg is disconnected to scada for VCB trip O2-23 | Close | 0.067308 | O2-02 | 0 |  | WTG Unscheduled Maintenance | 0 | 0
3117 | 2024-12-11 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.27083 | 0.27083 | 0.27847 | 0 | 0.18333 | 0.18333 | after grid resume Wtg in error so Checked related error data log then apply hard reboot then reset & start the WTG. Late reset due to VCB trip O2-23 and disconnected to scada. | Close | 0.0070513 | O2-02 | 0 |  | WTG Unscheduled Maintenance | 0 | 0
3118 | 2024-12-11 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Connectivity issue | 0.86458 | 0.86458 | 0.925 | 0 | 1.45 | 1.45 | after grid resume Wtg is disconnected to scada for VCB trip O2-26 | Close | 0.055769 | O2-02 | 0 |  | WTG Unscheduled Maintenance | 0 | 0
3119 | 2024-12-11 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.925 | 0.925 | 0.94375 | 0 | 0.45 | 0.45 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-26 and disconnected to scada. | Close | 0.017308 | O2-02 | 0 |  | WTG Unscheduled Maintenance | 0 | 0
3120 | 2024-12-11 | 2025 | 2024 | 2024-12-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.19792 | 0.19792 | 0.27083 | 0 | 1.75 | 1.75 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-23 and disconnected to scada. | Close | 0.067308 | O2-26 | 1687.875 |  | WTG Unscheduled Maintenance | 23148 | 1687.875
3121 | 2024-12-11 | 2025 | 2024 | 2024-12-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Connectivity issue | 0.86458 | 0.86458 | 0.90625 | 0 | 1 | 1 | after grid resume Wtg is disconnected to scada for VCB trip O2-09 | Close | 0.038462 | O2-26 | 964.5 |  | WTG Unscheduled Maintenance | 23148 | 964.5
3122 | 2024-12-11 | 2025 | 2024 | 2024-12-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Break down | 0.90625 | 0.90625 | 0.97222 | 0 | 1.5833 | 1.5833 | after grid resume Wtg in error so Checked related error data log and ckt then found MCB trip so charge MCB then start wtg. | Close | 0.060897 | O2-26 | 1527.125 |  | WTG Unscheduled Maintenance | 23148 | 1527.125
3123 | 2024-12-11 | 2025 | 2024 | 2024-12-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 7025 | Configuration error | Break down | 0.19792 | 0.19792 | 0.25 | 0 | 1.25 | 1.25 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-23 and disconnected to scada. | Close | 0.048077 | O2-03 | 1118.6458 |  | WTG Unscheduled Maintenance | 21478 | 1118.6458
3124 | 2024-12-11 | 2025 | 2024 | 2024-12-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 7025 | Configuration error | Break down | 0.86458 | 0.86458 | 0.86736 | 0 | 0.066667 | 0.066667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0025641 | O2-15 | 76.1306 |  | WTG Unscheduled Maintenance | 27407 | 76.1306
3125 | 2024-12-11 | 2025 | 2024 | 2024-12-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.86458 | 0.86458 | 0.88403 | 0 | 0.46667 | 0.46667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-13 and disconnected to scada. | Close | 0.017949 | O2-12 | 558.5417 |  | WTG Unscheduled Maintenance | 28725 | 558.5417
3126 | 2024-12-11 | 2025 | 2024 | 2024-12-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.86458 | 0.86458 | 0.90625 | 0 | 1 | 1 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-13 and disconnected to scada. | Close | 0.038462 | O2-14 | 972.6667 |  | WTG Unscheduled Maintenance | 23344 | 972.6667
3127 | 2024-12-11 | 2025 | 2024 | 2024-12-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Break down | 0.89167 | 0.89167 | 0.99792 | 0 | 2.55 | 2.55 | after grid resume Wtg in error so Checked related error data log and ckt then found MCB trip in nacelle so charge MCB then start wtg. | Close | 0.098077 | O2-12 | 3052.0312 |  | WTG Unscheduled Maintenance | 28725 | 3052.0312
3128 | 2024-12-11 | 2025 | 2024 | 2024-12-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 170 | SLC MF brake request HC | Break down | 0.35417 | 0.35417 | 0.40972 | 0 | 1.3333 | 1.3333 | Checked related error data log then reset & run the WTG. | Close | 0.051282 | O2-07 | 1716.3889 |  | WTG Unscheduled Maintenance | 30895 | 1716.3889
3129 | 2024-12-11 | 2025 | 2024 | 2024-12-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.45 | 0.45 | 0.68542 | 0 | 5.65 | 5.65 | Project Pending Punch Point closing work | Close | 0.21731 | O2-07 | 7273.1979 |  | WTG Breakdown Maintenance | 30895 | 7273.1979
3130 | 2024-12-11 | 2025 | 2024 | 2024-12-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 7025 | Configuration error | Break down | 0.19792 | 0.19792 | 0.27083 | 0 | 1.75 | 1.75 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-23 and disconnected to scada. | Close | 0.067308 | O2-25 | 1646.6042 |  | WTG Unscheduled Maintenance | 22582 | 1646.6042
3131 | 2024-12-11 | 2025 | 2024 | 2024-12-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 7025 | Configuration error | Break down | 0.86458 | 0.86458 | 0.93681 | 0 | 1.7333 | 1.7333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-26 and disconnected to scada. | Close | 0.066667 | O2-25 | 1630.9222 |  | WTG Unscheduled Maintenance | 22582 | 1630.9222
3132 | 2024-12-11 | 2025 | 2024 | 2024-12-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 7025 | Configuration error | Break down | 0.19792 | 0.19792 | 0.26042 | 0 | 1.5 | 1.5 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-23 and disconnected to scada. | Close | 0.057692 | O2-01 | 1230.875 |  | WTG Unscheduled Maintenance | 19694 | 1230.875
3133 | 2024-12-11 | 2025 | 2024 | 2024-12-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.92431 | 0.92431 | 0.95694 | 0 | 0.78333 | 0.78333 | after grid resume Wtg is disconnected to scada for VCB trip O2-26 | Close | 0.030128 | O2-26 | 755.525 |  | WTG Breakdown Maintenance | 23148 | 755.525
3134 | 2024-12-11 | 2025 | 2024 | 2024-12-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.15 | 0.15 | 0.16806 | 0 | 0.43333 | 0.43333 | Checked related error data log then reset & run the WTG. | Close | 0.016667 | O2-26 | 417.95 |  | WTG Unscheduled Maintenance | 23148 | 417.95
3135 | 2024-12-11 | 2025 | 2024 | 2024-12-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.84306 | 0.84306 | 0.86111 | 0 | 0.43333 | 0.43333 | Checked related error data log then reset & run the WTG. | Close | 0.016667 | O2-25 | 407.7306 |  | WTG Unscheduled Maintenance | 22582 | 407.7306
3136 | 2024-12-11 | 2025 | 2024 | 2024-12-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.053472 | 0.053472 | 0.11875 | 0 | 1.5667 | 1.5667 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.060256 | O2-12 | 1875.1042 |  | WTG Breakdown Maintenance | 28725 | 1875.1042
3136 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Break down | 0 | 0 | 0.029167 | 0 | 0.7 | 0.7 | after grid resume Wtg in error so Checked related error data log and ckt then found MCB trip so charge MCB then start wtg. | Close | 0.026923 | O2-26 | 726.8917 |  | WTG Unscheduled Maintenance | 24922 | 726.8917
3136 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.21528 | 0.21528 | 0.25 | 0 | 0.83333 | 0.83333 | after grid resume Wtg is disconnected to scada for VCB trip O2-26 | Close | 0.032051 | O2-26 | 865.3472 |  | WTG Unscheduled Maintenance | 24922 | 865.3472
3136 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.25 | 0.25 | 0.26181 | 0 | 0.28333 | 0.28333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-26 and disconnected to scada. | Close | 0.010897 | O2-26 | 294.2181 |  | WTG Unscheduled Maintenance | 24922 | 294.2181
3136 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.54167 | 0.54167 | 0.56458 | 0 | 0.55 | 0.55 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-08 and disconnected to scada. | Close | 0.021154 | O2-26 | 571.1292 |  | WTG Unscheduled Maintenance | 24922 | 571.1292
3136 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.91667 | 0.91667 | 0.97778 | 0 | 1.4667 | 1.4667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-26 and disconnected to scada. | Close | 0.05641 | O2-26 | 1523.0111 |  | WTG Unscheduled Maintenance | 24922 | 1523.0111
3136 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Road issue | 0 | 0 | 0.19792 | 0 | 4.75 | 4.75 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | open | 0.18269 | O2-05 | 4031.5625 |  | WTG Unscheduled Maintenance | 20370 | 4031.5625
3136 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Road issue | 0.21528 | 0.21528 | 0.42708 | 0 | 5.0833 | 5.0833 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | open | 0.19551 | O2-05 | 4314.4792 |  | WTG Unscheduled Maintenance | 20370 | 4314.4792
3136 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Road issue | 0.54167 | 0.54167 | 0.91667 | 0 | 9 | 9 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | open | 0.34615 | O2-05 | 7638.75 |  | WTG Unscheduled Maintenance | 20370 | 7638.75
3136 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Road issue | 0.91667 | 0.91667 | 0.99999 | 0 | 1.9997 | 1.9997 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | open | 0.076912 | O2-05 | 1697.2642 |  | WTG Unscheduled Maintenance | 20370 | 1697.2642
3136 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 7025 | Configuration error | Break down | 0.21528 | 0.21528 | 0.24028 | 0 | 0.6 | 0.6 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-23 and disconnected to scada. | Close | 0.023077 | O2-09 | 680.35 |  | WTG Unscheduled Maintenance | 27214 | 680.35
3136 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 7025 | Configuration error | Break down | 0.93056 | 0.93056 | 0.95833 | 0 | 0.66667 | 0.66667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-23 and disconnected to scada. | Close | 0.025641 | O2-09 | 755.9444 |  | WTG Unscheduled Maintenance | 27214 | 755.9444
3136 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.21528 | 0.21528 | 0.24931 | 0 | 0.81667 | 0.81667 | after grid resume Wtg is disconnected to scada for VCB trip O2-26 | Close | 0.03141 | O2-25 | 932.9056 |  | WTG Unscheduled Maintenance | 27416 | 932.9056
3136 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.24931 | 0.24931 | 0.325 | 0 | 1.8167 | 1.8167 | after gtid resume wtg is not cannected so check and found 02-05 software file is corrupted so re update software file then reset and start wtg. | Close | 0.069872 | O2-25 | 2075.2389 |  | WTG Unscheduled Maintenance | 27416 | 2075.2389
3136 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 7025 | Configuration error | Break down | 0.93056 | 0.93056 | 0.96736 | 0 | 0.88333 | 0.88333 | after grid resume Wtg is disconnected to scada for VCB trip O2-26 | Close | 0.033974 | O2-25 | 1009.0611 |  | WTG Unscheduled Maintenance | 27416 | 1009.0611
3136 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 7025 | Configuration error | Break down | 0.96736 | 0.96736 | 0.99792 | 0 | 0.73333 | 0.73333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG | Close | 0.028205 | O2-25 | 837.7111 |  | WTG Unscheduled Maintenance | 27416 | 837.7111
3136 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 7025 | Configuration error | Break down | 0.21528 | 0.21528 | 0.23681 | 0 | 0.51667 | 0.51667 | after grid resume Wtg is disconnected to scada for VCB trip O2-23 | Close | 0.019872 | O2-26 | 536.5153 |  | WTG Unscheduled Maintenance | 24922 | 536.5153
3136 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 7025 | Configuration error | Break down | 0.93056 | 0.93056 | 0.95764 | 0 | 0.65 | 0.65 | after grid resume Wtg is disconnected to scada for VCB trip O2-23 | Close | 0.025 | O2-26 | 674.9708 |  | WTG Unscheduled Maintenance | 24922 | 674.9708
3136 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 7025 | Configuration error | Break down | 0.21528 | 0.21528 | 0.23681 | 0 | 0.51667 | 0.51667 | after grid resume Wtg is disconnected to scada for VCB trip O2-23 | Close | 0.019872 | O2-03 | 630.2687 |  | WTG Unscheduled Maintenance | 29277 | 630.2687
3136 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 7025 | Configuration error | Break down | 0.93056 | 0.93056 | 0.95764 | 0 | 0.65 | 0.65 | after grid resume Wtg is disconnected to scada for VCB trip O2-23 | Close | 0.025 | O2-03 | 792.9188 |  | WTG Unscheduled Maintenance | 29277 | 792.9188
3136 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 7025 | Configuration error | Break down | 0.93056 | 0.93056 | 0.93611 | 0 | 0.13333 | 0.13333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0051282 | O2-15 | 128.3722 |  | WTG Unscheduled Maintenance | 23107 | 128.3722
3136 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.21528 | 0.21528 | 0.22083 | 0 | 0.13333 | 0.13333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG.Late reset due to VCB trip O2-13 and disconnected to scada. | Close | 0.0051282 | O2-12 | 155.3889 |  | WTG Unscheduled Maintenance | 27970 | 155.3889
3136 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.93056 | 0.93056 | 0.94097 | 0 | 0.25 | 0.25 | after grid resume Wtg is disconnected to scada for VCB trip O2-13 | Close | 0.0096154 | O2-12 | 291.3542 |  | WTG Unscheduled Maintenance | 27970 | 291.3542
3136 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.21528 | 0.21528 | 0.225 | 0 | 0.23333 | 0.23333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-13 and disconnected to scada. | Close | 0.0089744 | O2-14 | 218.5069 |  | WTG Unscheduled Maintenance | 22475 | 218.5069
3136 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.93056 | 0.93056 | 0.94097 | 0 | 0.25 | 0.25 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-13 and disconnected to scada. | Close | 0.0096154 | O2-14 | 234.1146 |  | WTG Unscheduled Maintenance | 22475 | 234.1146
3136 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.75 | 0.75 | 0.81875 | 0 | 1.65 | 1.65 | WTG manual stop for shoftware updated work. | Close | 0.063462 | O2-12 | 1922.9375 |  | WTG Breakdown Maintenance | 27970 | 1922.9375
3136 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.93056 | 0.93056 | 0.94792 | 0 | 0.41667 | 0.41667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.016026 | O2-12 | 485.5903 |  | WTG Unscheduled Maintenance | 27970 | 485.5903
3136 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.93056 | 0.93056 | 0.93472 | 0 | 0.1 | 0.1 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0038462 | O2-10 | 119.9417 |  | WTG Unscheduled Maintenance | 28786 | 119.9417
3136 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.54167 | 0.54167 | 0.55208 | 0 | 0.25 | 0.25 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0096154 | O2-06 | 230.75 |  | WTG Unscheduled Maintenance | 22152 | 230.75
3136 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.23681 | 0.23681 | 0.24583 | 0 | 0.21667 | 0.21667 | after VCB charge Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0083333 | O2-11 | 244.3729 |  | WTG Unscheduled Maintenance | 27069 | 244.3729
3136 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.54167 | 0.54167 | 0.61528 | 0 | 1.7667 | 1.7667 | after gtid resume wtg is not cannected so check and found 02-23 software file is corrupted so re update software file then reset and start wtg. | Close | 0.067949 | O2-11 | 1992.5792 |  | WTG Unscheduled Maintenance | 27069 | 1992.5792
3136 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.58333 | 0.58333 | 0.71458 | 0 | 3.15 | 3.15 | WTG manual stop for Project Pending Punch Point closing work | Close | 0.12115 | O2-20 | 4088.3062 |  | WTG Breakdown Maintenance | 31149 | 4088.3062
3136 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.21528 | 0.21528 | 0.24931 | 0 | 0.81667 | 0.81667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-26 and disconnected to scada. | Close | 0.03141 | O2-25 | 932.9056 |  | WTG Unscheduled Maintenance | 27416 | 932.9056
3136 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.54167 | 0.54167 | 0.56181 | 0 | 0.48333 | 0.48333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.01859 | O2-25 | 552.1278 |  | WTG Unscheduled Maintenance | 27416 | 552.1278
3136 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.93056 | 0.93056 | 0.96736 | 0 | 0.88333 | 0.88333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-26 and disconnected to scada. | Close | 0.033974 | O2-25 | 1009.0611 |  | WTG Unscheduled Maintenance | 27416 | 1009.0611
3136 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.96736 | 0.96736 | 0.99583 | 0 | 0.68333 | 0.68333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.026282 | O2-25 | 780.5944 |  | WTG Unscheduled Maintenance | 27416 | 780.5944
3136 | 2024-12-13 | 2025 | 2024 | 2024-12-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.13194 | 0.13194 | 0.19097 | 0 | 1.4167 | 1.4167 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-11 and disconnected to scada. | Close | 0.054487 | O2-26 | 2744.3785 |  | WTG Unscheduled Maintenance | 46493 | 2744.3785
3136 | 2024-12-13 | 2025 | 2024 | 2024-12-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 7415 | PLC hardware error | Break down | 0.36528 | 0.36528 | 0.43194 | 0 | 1.6 | 1.6 | Attend and found mouse is insade the panel and cut for AIO modual cable so removed it and rejoint it then reset and start wtg. | Close | 0.061538 | O2-26 | 3099.5333 |  | WTG Unscheduled Maintenance | 46493 | 3099.5333
3136 | 2024-12-13 | 2025 | 2024 | 2024-12-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.46319 | 0.46319 | 0.46944 | 0 | 0.15 | 0.15 | Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0057692 | O2-26 | 290.5812 |  | WTG Unscheduled Maintenance | 46493 | 290.5812
3136 | 2024-12-13 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Road issue | 0 | 0 | 0.10903 | 0 | 2.6167 | 2.6167 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | open | 0.10064 | O2-05 | 3826.766 |  | WTG Unscheduled Maintenance | 35099 | 3826.766
3136 | 2024-12-13 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Road issue | 0.13194 | 0.13194 | 0.99999 | 0 | 20.8331 | 20.8331 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | open | 0.80127 | O2-05 | 30467.4757 |  | WTG Unscheduled Maintenance | 35099 | 30467.4757
3136 | 2024-12-13 | 2025 | 2024 | 2024-12-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.13194 | 0.13194 | 0.19097 | 0 | 1.4167 | 1.4167 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-11 and disconnected to scada. | Close | 0.054487 | O2-09 | 2817.3958 |  | WTG Unscheduled Maintenance | 47730 | 2817.3958
3136 | 2024-12-13 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 7025 | Configuration error | Break down | 0.13194 | 0.13194 | 0.19097 | 0 | 1.4167 | 1.4167 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-11 and disconnected to scada. | Close | 0.054487 | O2-25 | 2945.191 |  | WTG Unscheduled Maintenance | 49895 | 2945.191
3136 | 2024-12-13 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 7025 | Configuration error | Break down | 0.19097 | 0.19097 | 0.20139 | 0 | 0.25 | 0.25 | Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0096154 | O2-25 | 519.7396 |  | WTG Unscheduled Maintenance | 49895 | 519.7396
3136 | 2024-12-13 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.24444 | 0.24444 | 0.29861 | 0 | 1.3 | 1.3 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.05 | O2-25 | 2702.6458 |  | WTG Breakdown Maintenance | 49895 | 2702.6458
3136 | 2024-12-13 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.91806 | 0.91806 | 0.94306 | 0 | 0.6 | 0.6 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.023077 | O2-25 | 1247.375 |  | WTG Breakdown Maintenance | 49895 | 1247.375
3136 | 2024-12-13 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.95764 | 0.95764 | 1899-12-31 | 0 | 1.0167 | 1.0167 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.039103 | O2-25 | 2113.6076 |  | WTG Breakdown Maintenance | 49895 | 2113.6076
3136 | 2024-12-13 | 2025 | 2024 | 2024-12-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.13194 | 0.13194 | 0.19097 | 0 | 1.4167 | 1.4167 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-11 and disconnected to scada. | Close | 0.054487 | O2-26 | 2744.3785 |  | WTG Unscheduled Maintenance | 46493 | 2744.3785
3136 | 2024-12-13 | 2025 | 2024 | 2024-12-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.49097 | 0.49097 | 0.49167 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | O2-26 | 32.2868 |  | WTG Unscheduled Maintenance | 46493 | 32.2868
3136 | 2024-12-13 | 2025 | 2024 | 2024-12-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.61875 | 0.61875 | 0.62292 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2-26 | 193.7208 |  | WTG Unscheduled Maintenance | 46493 | 193.7208
3136 | 2024-12-13 | 2025 | 2024 | 2024-12-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 7025 | Configuration error | Break down | 0.13194 | 0.13194 | 0.19097 | 0 | 1.4167 | 1.4167 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-11 and disconnected to scada. | Close | 0.054487 | O2-03 | 2854.1111 |  | WTG Unscheduled Maintenance | 48352 | 2854.1111
3136 | 2024-12-13 | 2025 | 2024 | 2024-12-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.39861 | 0.39861 | 0.40208 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2-03 | 167.8889 |  | WTG Unscheduled Maintenance | 48352 | 167.8889
3136 | 2024-12-13 | 2025 | 2024 | 2024-12-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.43125 | 0.43125 | 0.43889 | 0 | 0.18333 | 0.18333 | Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0070513 | O2-03 | 369.3556 |  | WTG Unscheduled Maintenance | 48352 | 369.3556
3136 | 2024-12-13 | 2025 | 2024 | 2024-12-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.22083 | 0.22083 | 0.37222 | 0 | 3.6333 | 3.6333 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.13974 | O2-12 | 7075.6139 |  | WTG Breakdown Maintenance | 46738 | 7075.6139
3136 | 2024-12-13 | 2025 | 2024 | 2024-12-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.4625 | 0.4625 | 0.49861 | 0 | 0.86667 | 0.86667 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.033333 | O2-12 | 1687.7611 |  | WTG Breakdown Maintenance | 46738 | 1687.7611
3136 | 2024-12-13 | 2025 | 2024 | 2024-12-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Break down | 0.85972 | 0.85972 | 0.87083 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & run the WTG. | Close | 0.010256 | O2-12 | 519.3111 |  | WTG Unscheduled Maintenance | 46738 | 519.3111
3136 | 2024-12-13 | 2025 | 2024 | 2024-12-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.94097 | 0.94097 | 0.94861 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & run the WTG. | Close | 0.0070513 | O2-12 | 357.0264 |  | WTG Unscheduled Maintenance | 46738 | 357.0264
3136 | 2024-12-13 | 2025 | 2024 | 2024-12-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.13194 | 0.13194 | 0.19097 | 0 | 1.4167 | 1.4167 | after grid resume Wtg is disconnected to scada for VCB trip O2-11 | Close | 0.054487 | O2-14 | 2867.0382 |  | WTG Unscheduled Maintenance | 48571 | 2867.0382
3136 | 2024-12-13 | 2025 | 2024 | 2024-12-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.19097 | 0.19097 | 0.20486 | 0 | 0.33333 | 0.33333 | Checked related error data log then reset & run the WTG. | Close | 0.012821 | O2-14 | 674.5972 |  | WTG Unscheduled Maintenance | 48571 | 674.5972
3136 | 2024-12-13 | 2025 | 2024 | 2024-12-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.18403 | 0.18403 | 0.20069 | 0 | 0.4 | 0.4 | Checked related error data log then reset & run the WTG. | Close | 0.015385 | O2-11 | 368.5833 |  | WTG Unscheduled Maintenance | 22115 | 368.5833
3136 | 2024-12-13 | 2025 | 2024 | 2024-12-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Break down | 0.45625 | 0.45625 | 0.46181 | 0 | 0.13333 | 0.13333 | Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0051282 | O2-12 | 259.6556 |  | WTG Unscheduled Maintenance | 46738 | 259.6556
3136 | 2024-12-13 | 2025 | 2024 | 2024-12-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Break down | 0.44236 | 0.44236 | 0.44931 | 0 | 0.16667 | 0.16667 | Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0064103 | O2-10 | 294.8333 |  | WTG Unscheduled Maintenance | 42456 | 294.8333
3136 | 2024-12-13 | 2025 | 2024 | 2024-12-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.43125 | 0.43125 | 0.44028 | 0 | 0.21667 | 0.21667 | Checked related error data log then reset & run the WTG. | Close | 0.0083333 | O2-07 | 460.8319 |  | WTG Unscheduled Maintenance | 51046 | 460.8319
3136 | 2024-12-13 | 2025 | 2024 | 2024-12-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.37778 | 0.37778 | 0.37986 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-06 | 107.2229 |  | WTG Unscheduled Maintenance | 51467 | 107.2229
3136 | 2024-12-13 | 2025 | 2024 | 2024-12-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.64306 | 0.64306 | 0.65694 | 0 | 0.33333 | 0.33333 | Checked related error data log then reset & run the WTG. | Close | 0.012821 | O2-06 | 714.8194 |  | WTG Unscheduled Maintenance | 51467 | 714.8194
3136 | 2024-12-13 | 2025 | 2024 | 2024-12-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.13194 | 0.13194 | 0.19097 | 0 | 1.4167 | 1.4167 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-11 and disconnected to scada. | Close | 0.054487 | O2-11 | 1305.3993 |  | WTG Unscheduled Maintenance | 22115 | 1305.3993
3136 | 2024-12-13 | 2025 | 2024 | 2024-12-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.13194 | 0.13194 | 0.19097 | 0 | 1.4167 | 1.4167 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-11 and disconnected to scada. | Close | 0.054487 | O2-25 | 2945.191 |  | WTG Unscheduled Maintenance | 49895 | 2945.191
3136 | 2024-12-13 | 2025 | 2024 | 2024-12-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.13194 | 0.13194 | 0.19097 | 0 | 1.4167 | 1.4167 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-11 and disconnected to scada. | Close | 0.054487 | O2-01 | 2143.7118 |  | WTG Unscheduled Maintenance | 36317 | 2143.7118
3136 | 2024-12-13 | 2025 | 2024 | 2024-12-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.19097 | 0.19097 | 0.20556 | 0 | 0.35 | 0.35 | Checked related error data log then reset & run the WTG. | Close | 0.013462 | O2-01 | 529.6229 |  | WTG Unscheduled Maintenance | 36317 | 529.6229
3136 | 2024-12-14 | 2025 | 2024 | 2024-12-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.65417 | 0.65417 | 0.67361 | 0 | 0.46667 | 0.46667 | WTG Manual stop for inpection work. | Close | 0.017949 | O2-26 | 675.8306 |  | WTG Breakdown Maintenance | 34757 | 675.8306
3136 | 2024-12-14 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Road issue | 0 | 0 | 0.99999 | 0 | 23.9997 | 23.9997 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | open | 0.92307 | O2-05 | 18482.7861 |  | WTG Unscheduled Maintenance | 18483 | 18482.7861
3136 | 2024-12-14 | 2025 | 2024 | 2024-12-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 5506 | Rot.br. press. high | Break down | 0.64722 | 0.64722 | 0.66736 | 0 | 0.48333 | 0.48333 | Checked related error data log then reset & run the WTG. | Close | 0.01859 | O2-07 | 682.7687 |  | WTG Unscheduled Maintenance | 33903 | 682.7687
3136 | 2024-12-14 | 2025 | 2024 | 2024-12-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 5506 | Rot.br. press. high | Break down | 0.67014 | 0.67014 | 0.77778 | 0 | 2.5833 | 2.5833 | attend and check hydraulic pressure,pressure valve pressure switch,pressure feedback switch and connection proper retight than reset and start WTG. | Close | 0.099359 | O2-07 | 3649.2813 |  | WTG Unscheduled Maintenance | 33903 | 3649.2813
3136 | 2024-12-14 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0 | 0 | 0.30833 | 0 | 7.4 | 7.4 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.28462 | O2-25 | 12846.4 |  | WTG Breakdown Maintenance | 41664 | 12846.4
3136 | 2024-12-14 | 2025 | 2024 | 2024-12-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 6115 | Yaw sensor A defect | Break down | 0.027778 | 0.027778 | 0.03125 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & run the WTG. | Close | 0.0032051 | O2-12 | 134.0208 |  | WTG Unscheduled Maintenance | 38598 | 134.0208
3136 | 2024-12-14 | 2025 | 2024 | 2024-12-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.22431 | 0.22431 | 0.27639 | 0 | 1.25 | 1.25 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.048077 | O2-12 | 2010.3125 |  | WTG Breakdown Maintenance | 38598 | 2010.3125
3136 | 2024-12-14 | 2025 | 2024 | 2024-12-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.77431 | 0.77431 | 1899-12-31 | 0 | 5.4167 | 5.4167 | wtg manual stop for material interchanging work | Close | 0.20833 | O2-10 | 8978.5764 |  | WTG Breakdown Maintenance | 39782 | 8978.5764
3136 | 2024-12-14 | 2025 | 2024 | 2024-12-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.64583 | 0.64583 | 0.69236 | 0 | 1.1167 | 1.1167 | After grid resume time Not Singnal Converter RFO (CAN) After single available then reset and start wtg | Close | 0.042949 | O2-06 | 1638.5687 |  | WTG Unscheduled Maintenance | 35217 | 1638.5687
3136 | 2024-12-14 | 2025 | 2024 | 2024-12-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.64583 | 0.64583 | 0.64861 | 0 | 0.066667 | 0.066667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0025641 | O2-24 | 98.5889 |  | WTG Unscheduled Maintenance | 35492 | 98.5889
3136 | 2024-12-14 | 2025 | 2024 | 2024-12-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.66667 | 0.66667 | 0.71875 | 0 | 1.25 | 1.25 | After grid resume time Not Singnal Converter RFO (CAN) After single available then reset and start wtg | Close | 0.048077 | O2-06 | 1834.2188 |  | WTG Unscheduled Maintenance | 35217 | 1834.2188
3136 | 2024-12-14 | 2025 | 2024 | 2024-12-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.66042 | 0.66042 | 0.69861 | 0 | 0.91667 | 0.91667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.035256 | O2-06 | 1345.0937 |  | WTG Unscheduled Maintenance | 35217 | 1345.0937
3136 | 2024-12-14 | 2025 | 2024 | 2024-12-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.64097 | 0.64097 | 0.66181 | 0 | 0.5 | 0.5 | WTG Manual stop for inpection work. | Close | 0.019231 | O2-01 | 809.25 |  | WTG Breakdown Maintenance | 38844 | 809.25
3136 | 2024-12-15 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Road issue | 0 | 0 | 0.56944 | 0 | 13.6667 | 13.6667 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | open | 0.52564 | O2-05 | 10636.6528 |  | WTG Unscheduled Maintenance | 18679 | 10636.6528
3136 | 2024-12-15 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Road issue | 0.59375 | 0.59375 | 1899-12-31 | 0 | 9.75 | 9.75 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | open | 0.375 | O2-05 | 7588.3438 |  | WTG Unscheduled Maintenance | 18679 | 7588.3438
3136 | 2024-12-15 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 7025 | Configuration error | Break down | 0.59375 | 0.59375 | 0.60417 | 0 | 0.25 | 0.25 | after grid resume Wtg in error so Checked related error data log then apply soft reboot and software updated then reset & start the WTG. | Close | 0.0096154 | O2-25 | 218.1875 |  | WTG Unscheduled Maintenance | 20946 | 218.1875
3136 | 2024-12-15 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.79514 | 0.79514 | 0.79653 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-25 | 29.0917 |  | WTG Unscheduled Maintenance | 20946 | 29.0917
3136 | 2024-12-15 | 2025 | 2024 | 2024-12-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.52292 | 0.52292 | 0.65764 | 0 | 3.2333 | 3.2333 | wtg manual stop for software update. Softweare update time softwar is corrupted so call IT team and update software then reset and start wtg. | Close | 0.12436 | O2-21 | 3343.5361 |  | WTG Breakdown Maintenance | 24818 | 3343.5361
3136 | 2024-12-15 | 2025 | 2024 | 2024-12-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.59375 | 0.59375 | 0.6 | 0 | 0.15 | 0.15 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0057692 | O2-26 | 110.85 |  | WTG Unscheduled Maintenance | 17736 | 110.85
3136 | 2024-12-15 | 2025 | 2024 | 2024-12-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.48958 | 0.48958 | 0.49097 | 0 | 0.033333 | 0.033333 | wtg manul stop for software updated then reset & start the WTG. | Close | 0.0012821 | O2-03 | 24.9583 |  | WTG Breakdown Maintenance | 17970 | 24.9583
3136 | 2024-12-15 | 2025 | 2024 | 2024-12-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.48056 | 0.48056 | 0.48333 | 0 | 0.066667 | 0.066667 | wtg manul stop for software updated then reset & start the WTG. | Close | 0.0025641 | O2-12 | 51.5722 |  | WTG Breakdown Maintenance | 18566 | 51.5722
3136 | 2024-12-15 | 2025 | 2024 | 2024-12-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.59375 | 0.59375 | 0.77014 | 0 | 4.2333 | 4.2333 | after grid resume Wtg in error so attend found axis 3 blade calibration out so recalibration then reset and start wtg. | Close | 0.16282 | O2-12 | 3274.8361 |  | WTG Unscheduled Maintenance | 18566 | 3274.8361
3136 | 2024-12-15 | 2025 | 2024 | 2024-12-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.46944 | 0.46944 | 0.47431 | 0 | 0.11667 | 0.11667 | wtg manul stop for software updated then reset & start the WTG. | Close | 0.0044872 | O2-11 | 71.0743 |  | WTG Breakdown Maintenance | 14621 | 71.0743
3136 | 2024-12-15 | 2025 | 2024 | 2024-12-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0 | 0 | 0.45139 | 0 | 10.8333 | 10.8333 | wtg manual stop for material interchanging work done then reset and start wtg. | Close | 0.41667 | O2-10 | 8779.9653 |  | WTG Breakdown Maintenance | 19451 | 8779.9653
3136 | 2024-12-15 | 2025 | 2024 | 2024-12-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.3875 | 0.3875 | 0.76667 | 0 | 9.1 | 9.1 | Wtg stop for 1st month Maintenance work. | Close | 0.35 | O2-07 | 7146.5333 |  | WTG Scheduled Maintenance | 18848 | 7146.5333
3136 | 2024-12-15 | 2025 | 2024 | 2024-12-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.48681 | 0.48681 | 0.48819 | 0 | 0.033333 | 0.033333 | wtg manul stop for software updated then reset & start the WTG. | Close | 0.0012821 | O2-24 | 31.8306 |  | WTG Breakdown Maintenance | 22918 | 31.8306
3136 | 2024-12-15 | 2025 | 2024 | 2024-12-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.59375 | 0.59375 | 0.60833 | 0 | 0.35 | 0.35 | after grid resume Wtg in error so Checked related error data log then apply soft reboot and software updated then reset & start the WTG. | Close | 0.013462 | O2-24 | 334.2208 |  | WTG Unscheduled Maintenance | 22918 | 334.2208
3136 | 2024-12-16 | 2025 | 2024 | 2024-12-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 7025 | Configuration error | Break down | 0.44097 | 0.44097 | 0.44792 | 0 | 0.16667 | 0.16667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot and then reset & start the WTG. | Close | 0.0064103 | O2-26 | 81.375 |  | WTG Unscheduled Maintenance | 11718 | 81.375
3136 | 2024-12-16 | 2025 | 2024 | 2024-12-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 7025 | Configuration error | Break down | 0.49306 | 0.49306 | 0.49722 | 0 | 0.1 | 0.1 | after grid resume Wtg in error so Checked related error data log then apply soft reboot and then reset & start the WTG. | Close | 0.0038462 | O2-26 | 48.825 |  | WTG Unscheduled Maintenance | 11718 | 48.825
3136 | 2024-12-16 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Road issue | 0 | 0 | 0.21528 | 0 | 5.1667 | 5.1667 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | OPEN | 0.19872 | O2-05 | 2472.6806 |  | WTG Unscheduled Maintenance | 11486 | 2472.6806
3136 | 2024-12-16 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Road issue | 0.23264 | 0.23264 | 0.41944 | 0 | 4.4833 | 4.4833 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | OPEN | 0.17244 | O2-05 | 2145.6486 |  | WTG Unscheduled Maintenance | 11486 | 2145.6486
3136 | 2024-12-16 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Road issue | 0.44097 | 0.44097 | 0.47569 | 0 | 0.83333 | 0.83333 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | OPEN | 0.032051 | O2-05 | 398.8194 |  | WTG Unscheduled Maintenance | 11486 | 398.8194
3136 | 2024-12-16 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Road issue | 0.49306 | 0.49306 | 0.99999 | 0 | 12.1664 | 12.1664 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | OPEN | 0.46794 | O2-05 | 5822.6309 |  | WTG Unscheduled Maintenance | 11486 | 5822.6309
3136 | 2024-12-16 | 2025 | 2024 | 2024-12-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.47153 | 0.47153 | 0.47292 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2-07 | 15.2514 |  | WTG Unscheduled Maintenance | 10981 | 15.2514
3136 | 2024-12-16 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 7025 | Configuration error | Break down | 0.23264 | 0.23264 | 0.23958 | 0 | 0.16667 | 0.16667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot and then reset & start the WTG. | Close | 0.0064103 | O2-25 | 64.8472 |  | WTG Unscheduled Maintenance | 9338 | 64.8472
3136 | 2024-12-16 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 7025 | Configuration error | Break down | 0.44097 | 0.44097 | 0.45486 | 0 | 0.33333 | 0.33333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot and then reset & start the WTG. | Close | 0.012821 | O2-25 | 129.6944 |  | WTG Unscheduled Maintenance | 9338 | 129.6944
3136 | 2024-12-16 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 7025 | Configuration error | Break down | 0.49306 | 0.49306 | 0.5 | 0 | 0.16667 | 0.16667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot and then reset & start the WTG. | Close | 0.0064103 | O2-25 | 64.8472 |  | WTG Unscheduled Maintenance | 9338 | 64.8472
3136 | 2024-12-16 | 2025 | 2024 | 2024-12-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.23264 | 0.23264 | 0.23611 | 0 | 0.083333 | 0.083333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot and then reset & start the WTG. | Close | 0.0032051 | O2-26 | 40.6875 |  | WTG Unscheduled Maintenance | 11718 | 40.6875
3136 | 2024-12-16 | 2025 | 2024 | 2024-12-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 7002 | Task runtime failure 5ms | Break down | 0.44097 | 0.44097 | 0.45347 | 0 | 0.3 | 0.3 | after grid resume Wtg in error so Checked related error data log then apply soft reboot and then reset & start the WTG. | Close | 0.011538 | O2-26 | 146.475 |  | WTG Unscheduled Maintenance | 11718 | 146.475
3136 | 2024-12-16 | 2025 | 2024 | 2024-12-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.49306 | 0.49306 | 0.49861 | 0 | 0.13333 | 0.13333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot and then reset & start the WTG. | Close | 0.0051282 | O2-26 | 65.1 |  | WTG Unscheduled Maintenance | 11718 | 65.1
3136 | 2024-12-16 | 2025 | 2024 | 2024-12-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 7025 | Configuration error | Break down | 0.23264 | 0.23264 | 0.23889 | 0 | 0.15 | 0.15 | after grid resume Wtg in error so Checked related error data log then apply soft reboot and then reset & start the WTG. | Close | 0.0057692 | O2-03 | 76.6125 |  | WTG Unscheduled Maintenance | 12258 | 76.6125
3136 | 2024-12-16 | 2025 | 2024 | 2024-12-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 7025 | Configuration error | Break down | 0.23264 | 0.23264 | 0.23958 | 0 | 0.16667 | 0.16667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot and then reset & start the WTG. | Close | 0.0064103 | O2-15 | 74.8819 |  | WTG Unscheduled Maintenance | 10783 | 74.8819
3136 | 2024-12-16 | 2025 | 2024 | 2024-12-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 7025 | Configuration error | Break down | 0.23264 | 0.23264 | 0.24028 | 0 | 0.18333 | 0.18333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot and then reset & start the WTG. | Close | 0.0070513 | O2-15 | 82.3701 |  | WTG Unscheduled Maintenance | 10783 | 82.3701
3136 | 2024-12-16 | 2025 | 2024 | 2024-12-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 7025 | Configuration error | Break down | 0.23264 | 0.23264 | 0.24097 | 0 | 0.2 | 0.2 | after grid resume Wtg in error so Checked related error data log then apply soft reboot and then reset & start the WTG. | Close | 0.0076923 | O2-14 | 74.1917 |  | WTG Unscheduled Maintenance | 8903 | 74.1917
3136 | 2024-12-16 | 2025 | 2024 | 2024-12-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 7025 | Configuration error | Break down | 0.23264 | 0.23264 | 0.24167 | 0 | 0.21667 | 0.21667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot and then reset & start the WTG. | Close | 0.0083333 | O2-11 | 83.2812 |  | WTG Unscheduled Maintenance | 9225 | 83.2812
3136 | 2024-12-16 | 2025 | 2024 | 2024-12-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 7025 | Configuration error | Break down | 0.23264 | 0.23264 | 0.24236 | 0 | 0.23333 | 0.23333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot and then reset & start the WTG. | Close | 0.0089744 | O2-12 | 104.5236 |  | WTG Unscheduled Maintenance | 10751 | 104.5236
3136 | 2024-12-16 | 2025 | 2024 | 2024-12-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.23264 | 0.23264 | 0.24375 | 0 | 0.26667 | 0.26667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot and then reset & start the WTG. | Close | 0.010256 | O2-10 | 119.0778 |  | WTG Unscheduled Maintenance | 10717 | 119.0778
3136 | 2024-12-16 | 2025 | 2024 | 2024-12-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.43542 | 0.43542 | 0.73056 | 0 | 7.0833 | 7.0833 | Wtg stop for 1st month Maintenance work. | Close | 0.27244 | O2-06 | 2966.1458 |  | WTG Scheduled Maintenance | 10050 | 2966.1458
3136 | 2024-12-16 | 2025 | 2024 | 2024-12-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 7002 | Task runtime failure 5ms | Break down | 0.23264 | 0.23264 | 0.24444 | 0 | 0.28333 | 0.28333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot and then reset & start the WTG. | Close | 0.010897 | O2-11 | 108.9062 |  | WTG Unscheduled Maintenance | 9225 | 108.9062
3136 | 2024-12-16 | 2025 | 2024 | 2024-12-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.23264 | 0.23264 | 0.36042 | 0 | 3.0667 | 3.0667 | after grid resume Wtg in error so attend and found axis 2 FC006 MCB trip so check all related crk and interchange contactor and retight all cannections then start wtg. | Close | 0.11795 | O2-25 | 1193.1889 |  | WTG Unscheduled Maintenance | 9338 | 1193.1889
3136 | 2024-12-16 | 2025 | 2024 | 2024-12-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.44097 | 0.44097 | 0.45208 | 0 | 0.26667 | 0.26667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot and then reset & start the WTG. | Close | 0.010256 | O2-25 | 103.7556 |  | WTG Unscheduled Maintenance | 9338 | 103.7556
3136 | 2024-12-16 | 2025 | 2024 | 2024-12-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.73819 | 0.73819 | 0.84514 | 0 | 2.5667 | 2.5667 | after grid resume Wtg in error so attend and found axis 2 FC006 MCB trip so check all related crk and interchange MCB and retight all cannections then start wtg. | Close | 0.098718 | O2-25 | 998.6472 |  | WTG Unscheduled Maintenance | 9338 | 998.6472
3136 | 2024-12-16 | 2025 | 2024 | 2024-12-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.23264 | 0.23264 | 0.25139 | 0 | 0.45 | 0.45 | after grid resume Wtg in error so Checked related error data log then apply soft reboot and then reset & start the WTG. | Close | 0.017308 | O2-01 | 243.9 |  | WTG Unscheduled Maintenance | 13008 | 243.9
3136 | 2024-12-16 | 2025 | 2024 | 2024-12-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.44097 | 0.44097 | 0.45694 | 0 | 0.38333 | 0.38333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot and then reset & start the WTG. | Close | 0.014744 | O2-01 | 207.7667 |  | WTG Unscheduled Maintenance | 13008 | 207.7667
3136 | 2024-12-17 | 2025 | 2024 | 2024-12-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 5506 | Rot.br. press. high | Break down | 0.42708 | 0.42708 | 0.47917 | 0 | 1.25 | 1.25 | after grid resume Wtg in error so Checked related error data log then attend and check 9.1 valve cleane and check pressure for oil is ok then apply soft reboot and then reset & start the WTG. | Close | 0.048077 | O2-07 | 663.5938 |  | WTG Unscheduled Maintenance | 12741 | 663.5938
3136 | 2024-12-17 | 2025 | 2024 | 2024-12-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 5506 | Rot.br. press. high | Break down | 0.51389 | 0.51389 | 0.54861 | 0 | 0.83333 | 0.83333 | after grid resume Wtg in error so Checked related error data log then attend and check 9.1 valve cleane and check pressure for oil is ok then apply soft reboot and then reset & start the WTG. | Close | 0.032051 | O2-07 | 442.3958 |  | WTG Unscheduled Maintenance | 12741 | 442.3958
3136 | 2024-12-17 | 2025 | 2024 | 2024-12-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 5506 | Rot.br. press. high | Break down | 0.78125 | 0.78125 | 0.85069 | 0 | 1.6667 | 1.6667 | after grid resume Wtg in error so Checked related error data log then attend and check 9.1 valve cleane and orifis and check pressure for oil is ok then apply soft reboot and then reset & start the WTG. | Close | 0.064103 | O2-07 | 884.7917 |  | WTG Unscheduled Maintenance | 12741 | 884.7917
3136 | 2024-12-17 | 2025 | 2024 | 2024-12-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.30556 | 0.30556 | 0.31458 | 0 | 0.21667 | 0.21667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot and then reset & start the WTG. | Close | 0.0083333 | O2-26 | 161.9583 |  | WTG Unscheduled Maintenance | 17940 | 161.9583
3136 | 2024-12-17 | 2025 | 2024 | 2024-12-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.30556 | 0.30556 | 0.30764 | 0 | 0.05 | 0.05 | after grid resume Wtg in error so Checked related error data log then apply soft reboot and then reset & start the WTG. | Close | 0.0019231 | O2-12 | 36.0437 |  | WTG Unscheduled Maintenance | 17301 | 36.0437
3136 | 2024-12-17 | 2025 | 2024 | 2024-12-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Major BD | 0.42708 | 0.42708 | 0.66667 | 0 | 5.75 | 5.75 | after grid resume Wtg in error so attend and check axis number 1 limit switch 95 connection and 24 voltage supply after blade calibration done after trail ok then reset & start the WTG. | Close | 0.22115 | O2-07 | 3052.5312 |  | WTG Unscheduled Maintenance | 12741 | 3052.5312
3136 | 2024-12-17 | 2025 | 2024 | 2024-12-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 7415 | PLC hardware error | Major BD | 0.42708 | 0.42708 | 0.72361 | 0 | 7.1167 | 7.1167 | after grid resume WTG sofware corrupted so technical team and software team are troubleshoot and resolve it then apply soft reboot and then reset & start the WTG. | Close | 0.27372 | O2-07 | 3778.0604 |  | WTG Unscheduled Maintenance | 12741 | 3778.0604
3136 | 2024-12-17 | 2025 | 2024 | 2024-12-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.40278 | 0.40278 | 0.70625 | 0 | 7.2833 | 7.2833 | Wtg stop for 1st month Maintenance work. | Close | 0.28013 | O2-11 | 5319.2611 |  | WTG Scheduled Maintenance | 17528 | 5319.2611
3136 | 2024-12-17 | 2025 | 2024 | 2024-12-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.30556 | 0.30556 | 0.3125 | 0 | 0.16667 | 0.16667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot and then reset & start the WTG. | Close | 0.0064103 | O2-01 | 149.1181 |  | WTG Unscheduled Maintenance | 21473 | 149.1181
3137 | 2024-12-17 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Road issue | 0.30556 | 0.30556 | 0.375 | 0 | 1.6667 | 1.6667 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | open | 0.064103 | O2-05 | 1078.2639 |  | WTG Unscheduled Maintenance | 15527 | 1078.2639
3138 | 2024-12-17 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Road issue | 0.42708 | 0.42708 | 0.99999 | 0 | 13.7497 | 13.7497 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | open | 0.52884 | O2-05 | 8895.4974 |  | WTG Unscheduled Maintenance | 15527 | 8895.4974
3138 | 2024-12-18 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Road issue | 0 | 0 | 0.74444 | 0 | 17.8667 | 17.8667 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | open | 0.68718 | O2-05 | 7541.9667 |  | WTG Unscheduled Maintenance | 10131 | 7541.9667
3138 | 2024-12-18 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Road issue | 0.76736 | 0.76736 | 0.99999 | 0 | 5.5831 | 5.5831 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | open | 0.21473 | O2-05 | 2356.7473 |  | WTG Unscheduled Maintenance | 10131 | 2356.7473
3138 | 2024-12-18 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.028472 | 0.028472 | 0.032639 | 0 | 0.1 | 0.1 | Checked related error data log then reset & run the WTG. | Close | 0.0038462 | O2-25 | 51.8292 |  | WTG Unscheduled Maintenance | 12439 | 51.8292
3138 | 2024-12-18 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.036111 | 0.036111 | 0.038194 | 0 | 0.05 | 0.05 | Checked related error data log then reset & run the WTG. | Close | 0.0019231 | O2-25 | 25.9146 |  | WTG Unscheduled Maintenance | 12439 | 25.9146
3138 | 2024-12-18 | 2025 | 2024 | 2024-12-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.76736 | 0.76736 | 0.77639 | 0 | 0.21667 | 0.21667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot and then reset & start the WTG. | Close | 0.0083333 | O2-26 | 104.659 |  | WTG Unscheduled Maintenance | 11593 | 104.659
3138 | 2024-12-18 | 2025 | 2024 | 2024-12-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.63194 | 0.63194 | 0.63472 | 0 | 0.066667 | 0.066667 | wtg stop for Software update work | Close | 0.0025641 | O2-15 | 27.625 |  | WTG Breakdown Maintenance | 9945 | 27.625
3138 | 2024-12-18 | 2025 | 2024 | 2024-12-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.76736 | 0.76736 | 0.77014 | 0 | 0.066667 | 0.066667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot and then reset & start the WTG. | Close | 0.0025641 | O2-15 | 27.625 |  | WTG Unscheduled Maintenance | 9945 | 27.625
3138 | 2024-12-18 | 2025 | 2024 | 2024-12-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.66944 | 0.66944 | 0.675 | 0 | 0.13333 | 0.13333 | wtg stop for Software update work | Close | 0.0051282 | O2-11 | 63.2611 |  | WTG Breakdown Maintenance | 11387 | 63.2611
3138 | 2024-12-18 | 2025 | 2024 | 2024-12-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.6875 | 0.6875 | 0.69097 | 0 | 0.083333 | 0.083333 | wtg stop for Software update work | Close | 0.0032051 | O2-12 | 35.7917 |  | WTG Breakdown Maintenance | 10308 | 35.7917
3138 | 2024-12-18 | 2025 | 2024 | 2024-12-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.76736 | 0.76736 | 0.77083 | 0 | 0.083333 | 0.083333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot and then reset & start the WTG. | Close | 0.0032051 | O2-12 | 35.7917 |  | WTG Unscheduled Maintenance | 10308 | 35.7917
3138 | 2024-12-18 | 2025 | 2024 | 2024-12-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0 | 0 | 0.70625 | 0 | 16.95 | 16.95 | wtg stop for project pending work. | Close | 0.65192 | O2-22 | 6991.875 |  | WTG Breakdown Maintenance | 9900 | 6991.875
3138 | 2024-12-18 | 2025 | 2024 | 2024-12-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.44236 | 0.44236 | 0.525 | 0 | 1.9833 | 1.9833 | Wtg stop for 1st month Maintenance work. | Close | 0.076282 | O2-07 | 755.7326 |  | WTG Scheduled Maintenance | 9145 | 755.7326
3138 | 2024-12-18 | 2025 | 2024 | 2024-12-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.70833 | 0.70833 | 0.7125 | 0 | 0.1 | 0.1 | wtg stop for Software update work | Close | 0.0038462 | O2-20 | 36.4625 |  | WTG Breakdown Maintenance | 8751 | 36.4625
3138 | 2024-12-18 | 2025 | 2024 | 2024-12-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.76736 | 0.76736 | 0.79653 | 0 | 0.7 | 0.7 | after grid resume Wtg in error so Checked related error data log then apply soft reboot and then reset & start the WTG. | Close | 0.026923 | O2-25 | 362.8042 |  | WTG Unscheduled Maintenance | 12439 | 362.8042
3138 | 2024-12-18 | 2025 | 2024 | 2024-12-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.76736 | 0.76736 | 0.77153 | 0 | 0.1 | 0.1 | after grid resume Wtg in error so Checked related error data log then apply soft reboot and then reset & start the WTG. | Close | 0.0038462 | O2-01 | 57.3042 |  | WTG Unscheduled Maintenance | 13753 | 57.3042
3139 | 2024-12-19 | 2025 | 2024 | 2024-12-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.49306 | 0.49306 | 0.84722 | 0 | 8.5 | 8.5 | wtg stop for project pending work. | Close | 0.32692 | O2-02 | 4871.2083 |  | WTG Breakdown Maintenance | 13754 | 4871.2083
3140 | 2024-12-19 | 2025 | 2024 | 2024-12-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.84792 | 0.84792 | 0.99999 | 0 | 3.6497 | 3.6497 | after project work complet than found chopper resister found faulty so replace it than check ClS system warning so solve it than rotor break pressure high error occurred than Further Troubl shooting WIP. | Close | 0.14037 | O2-03 | 2091.747 |  | WTG Breakdown Maintenance | 13755 | 2091.747
3141 | 2024-12-19 | 2025 | 2024 | 2024-12-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.56458 | 0.56458 | 0.56597 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & run the WTG. | Close | 0.0012821 | O2-04 | 19.1056 |  | WTG Unscheduled Maintenance | 13756 | 19.1056
3142 | 2024-12-19 | 2025 | 2024 | 2024-12-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.60833 | 0.60833 | 0.61806 | 0 | 0.23333 | 0.23333 | Checked related error data log then reset & run the WTG. | Close | 0.0089744 | O2-05 | 133.7486 |  | WTG Unscheduled Maintenance | 13757 | 133.7486
3143 | 2024-12-19 | 2025 | 2024 | 2024-12-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.52222 | 0.52222 | 0.60417 | 0 | 1.9667 | 1.9667 | Shutdoun taken by O2 project team for MOG work. | Close | 0.075641 | O2-06 | 1127.3917 |  | WTG Breakdown Maintenance | 13758 | 1127.3917
3144 | 2024-12-19 | 2025 | 2024 | 2024-12-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.084028 | 0.084028 | 0.088889 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & run the WTG. | Close | 0.0044872 | O2-07 | 66.884 |  | WTG Unscheduled Maintenance | 13759 | 66.884
3145 | 2024-12-19 | 2025 | 2024 | 2024-12-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Major BD | 0.45208 | 0.45208 | 0.99999 | 0 | 13.1497 | 13.1497 | After grid resume VCB trip so charge by BOP team than restore WTG | Close | 0.50576 | O2-08 | 7539.1741 |  | WTG Unscheduled Maintenance | 13760 | 7539.1741
3146 | 2024-12-19 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | ROW issue | 0 | 0 | 0.93125 | 0 | 22.35 | 22.35 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | open | 0.85962 | O2-09 | 12814.9313 |  | WTG Unscheduled Maintenance | 13761 | 12814.9313
3147 | 2024-12-19 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | ROW issue | 0.95208 | 0.95208 | 0.99999 | 0 | 1.1497 | 1.1497 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | open | 0.04422 | O2-10 | 659.2699 |  | WTG Unscheduled Maintenance | 13762 | 659.2699
3148 | 2024-12-20 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Break down | 0 | 0 | 0.045139 | 0 | 1.0833 | 1.0833 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | open | 0.041667 | O2-05 | 1125.6285 |  | WTG Unscheduled Maintenance | 24937 | 1125.6285
3149 | 2024-12-20 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Break down | 0.0625 | 0.0625 | 0.94236 | 0 | 21.1167 | 21.1167 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | open | 0.81218 | O2-05 | 21941.0965 |  | WTG Unscheduled Maintenance | 24937 | 21941.0965
3150 | 2024-12-20 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Break down | 0.96528 | 0.96528 | 1899-12-31 | 0 | 0.83333 | 0.83333 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | open | 0.032051 | O2-05 | 865.8681 |  | WTG Unscheduled Maintenance | 24937 | 865.8681
3151 | 2024-12-20 | 2025 | 2024 | 2024-12-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.0625 | 0.0625 | 0.077778 | 0 | 0.36667 | 0.36667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-13 and disconnected to scada. | Close | 0.014103 | O2-26 | 346.8819 |  | WTG Unscheduled Maintenance | 22705 | 346.8819
3152 | 2024-12-20 | 2025 | 2024 | 2024-12-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.77431 | 0.77431 | 0.77569 | 0 | 0.033333 | 0.033333 | wtg stop for Software update work | Close | 0.0012821 | O2-26 | 31.5347 |  | WTG Breakdown Maintenance | 22705 | 31.5347
3153 | 2024-12-20 | 2025 | 2024 | 2024-12-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.96528 | 0.96528 | 1899-12-31 | 0 | 0.83333 | 0.83333 | after grid resume Wtg in disconnected to scada. VCB trip O2-08 | Close | 0.032051 | O2-26 | 788.3681 |  | WTG Unscheduled Maintenance | 22705 | 788.3681
3154 | 2024-12-20 | 2025 | 2024 | 2024-12-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.0625 | 0.0625 | 0.10069 | 0 | 0.91667 | 0.91667 | after grid resume Wtg in disconnected to scada. VCB trip O2-13 | Close | 0.035256 | O2-09 | 959.75 |  | WTG Unscheduled Maintenance | 25128 | 959.75
3155 | 2024-12-20 | 2025 | 2024 | 2024-12-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.09375 | 0.09375 | 0.10347 | 0 | 0.23333 | 0.23333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0089744 | O2-09 | 244.3 |  | WTG Unscheduled Maintenance | 25128 | 244.3
3156 | 2024-12-20 | 2025 | 2024 | 2024-12-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.96528 | 0.96528 | 0.97778 | 0 | 0.3 | 0.3 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.011538 | O2-09 | 314.1 |  | WTG Unscheduled Maintenance | 25128 | 314.1
3157 | 2024-12-20 | 2025 | 2024 | 2024-12-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 5506 | Rot.br. press. high | Break down | 0 | 0 | 0.24861 | 0 | 5.9667 | 5.9667 | attend and do WTR Hydraulic pressure and take trial and error is accure so check and found orifish is faulty so replace it then reset and strart wtg. | Close | 0.22949 | O2-07 | 5180.8069 |  | WTG Unscheduled Maintenance | 20839 | 5180.8069
3158 | 2024-12-20 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.0625 | 0.0625 | 0.097222 | 0 | 0.83333 | 0.83333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-08 and disconnected to scada. | Close | 0.032051 | O2-25 | 881.2847 |  | WTG Unscheduled Maintenance | 25381 | 881.2847
3159 | 2024-12-20 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.79097 | 0.79097 | 0.82014 | 0 | 0.7 | 0.7 | wtg stop for Software update work | Close | 0.026923 | O2-25 | 740.2792 |  | WTG Breakdown Maintenance | 25381 | 740.2792
3160 | 2024-12-20 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.95278 | 0.95278 | 1899-12-31 | 0 | 1.1333 | 1.1333 | after grid resume Wtg in disconnected to scada. VCB trip O2-08 | Close | 0.04359 | O2-25 | 1198.5472 |  | WTG Unscheduled Maintenance | 25381 | 1198.5472
3161 | 2024-12-20 | 2025 | 2024 | 2024-12-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.0625 | 0.0625 | 0.10069 | 0 | 0.91667 | 0.91667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-13 and disconnected to scada. | Close | 0.035256 | O2-03 | 940.8819 |  | WTG Unscheduled Maintenance | 24634 | 940.8819
3162 | 2024-12-20 | 2025 | 2024 | 2024-12-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.94236 | 0.94236 | 0.97778 | 0 | 0.85 | 0.85 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-13 and disconnected to scada. | Close | 0.032692 | O2-03 | 872.4542 |  | WTG Unscheduled Maintenance | 24634 | 872.4542
3163 | 2024-12-20 | 2025 | 2024 | 2024-12-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.0625 | 0.0625 | 0.072917 | 0 | 0.25 | 0.25 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0096154 | O2-15 | 295.5938 |  | WTG Unscheduled Maintenance | 28377 | 295.5938
3164 | 2024-12-20 | 2025 | 2024 | 2024-12-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.0625 | 0.0625 | 0.10069 | 0 | 0.91667 | 0.91667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-13 and disconnected to scada. | Close | 0.035256 | O2-14 | 873.4688 |  | WTG Unscheduled Maintenance | 22869 | 873.4688
3165 | 2024-12-20 | 2025 | 2024 | 2024-12-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.0625 | 0.0625 | 0.10069 | 0 | 0.91667 | 0.91667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-13 and disconnected to scada. | Close | 0.035256 | O2-11 | 957.4965 |  | WTG Unscheduled Maintenance | 25069 | 957.4965
3166 | 2024-12-20 | 2025 | 2024 | 2024-12-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.0625 | 0.0625 | 0.072917 | 0 | 0.25 | 0.25 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. | Close | 0.0096154 | O2-12 | 276.9375 |  | WTG Unscheduled Maintenance | 26586 | 276.9375
3167 | 2024-12-20 | 2025 | 2024 | 2024-12-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.0625 | 0.0625 | 0.10069 | 0 | 0.91667 | 0.91667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-13 and disconnected to scada. | Close | 0.035256 | O2-10 | 1135.0625 |  | WTG Unscheduled Maintenance | 29718 | 1135.0625
3168 | 2024-12-20 | 2025 | 2024 | 2024-12-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.96528 | 0.96528 | 0.97778 | 0 | 0.3 | 0.3 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-13 and disconnected to scada. | Close | 0.011538 | O2-12 | 332.325 |  | WTG Unscheduled Maintenance | 26586 | 332.325
3169 | 2024-12-20 | 2025 | 2024 | 2024-12-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.96528 | 0.96528 | 0.97778 | 0 | 0.3 | 0.3 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-13 and disconnected to scada. | Close | 0.011538 | O2-14 | 285.8625 |  | WTG Unscheduled Maintenance | 22869 | 285.8625
3170 | 2024-12-20 | 2025 | 2024 | 2024-12-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.96528 | 0.96528 | 0.97778 | 0 | 0.3 | 0.3 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-13 and disconnected to scada. | Close | 0.011538 | O2-11 | 313.3625 |  | WTG Unscheduled Maintenance | 25069 | 313.3625
3171 | 2024-12-20 | 2025 | 2024 | 2024-12-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.96528 | 0.96528 | 0.97778 | 0 | 0.3 | 0.3 | after grid resume Wtg in disconnected to scada. VCB trip O2-13 | Close | 0.011538 | O2-12 | 332.325 |  | WTG Unscheduled Maintenance | 26586 | 332.325
3172 | 2024-12-20 | 2025 | 2024 | 2024-12-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.97778 | 0.97778 | 1899-12-31 | 0 | 0.53333 | 0.53333 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-13 and disconnected to scada. | Close | 0.020513 | O2-12 | 590.8 |  | WTG Unscheduled Maintenance | 26586 | 590.8
3173 | 2024-12-20 | 2025 | 2024 | 2024-12-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.96528 | 0.96528 | 0.97778 | 0 | 0.3 | 0.3 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-13 and disconnected to scada. | Close | 0.011538 | O2-10 | 371.475 |  | WTG Unscheduled Maintenance | 29718 | 371.475
3174 | 2024-12-20 | 2025 | 2024 | 2024-12-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.96528 | 0.96528 | 0.97778 | 0 | 0.3 | 0.3 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-13 and disconnected to scada. | Close | 0.011538 | O2-11 | 313.3625 |  | WTG Unscheduled Maintenance | 25069 | 313.3625
3175 | 2024-12-20 | 2025 | 2024 | 2024-12-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.43056 | 0.43056 | 0.43333 | 0 | 0.066667 | 0.066667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-13 and disconnected to scada. | Close | 0.0025641 | O2-20 | 79.3861 |  | WTG Unscheduled Maintenance | 28579 | 79.3861
3176 | 2024-12-20 | 2025 | 2024 | 2024-12-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0 | 0 | 0.045139 | 0 | 1.0833 | 1.0833 | wip | Close | 0.041667 | O2-25 | 1145.6701 |  | WTG Unscheduled Maintenance | 25381 | 1145.6701
3177 | 2024-12-20 | 2025 | 2024 | 2024-12-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.0625 | 0.0625 | 0.17361 | 0 | 2.6667 | 2.6667 | attend and found HUB aix2 MCB trip so check and found no any abnormality so cherge MCB then start wtg | Close | 0.10256 | O2-25 | 2820.1111 |  | WTG Unscheduled Maintenance | 25381 | 2820.1111
3178 | 2024-12-20 | 2025 | 2024 | 2024-12-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.96528 | 0.96528 | 0.99931 | 0 | 0.81667 | 0.81667 | after grid resume Wtg in error so Checked related error data log then apply soft reboot then reset & start the WTG. Late reset due to VCB trip O2-08 and disconnected to scada. | Close | 0.03141 | O2-25 | 863.659 |  | WTG Unscheduled Maintenance | 25381 | 863.659
3179 | 2024-12-20 | 2025 | 2024 | 2024-12-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.96528 | 0.96528 | 1899-12-31 | 0 | 0.83333 | 0.83333 | after grid resume Wtg in disconnected to scada. VCB trip O2-08 | Close | 0.032051 | O2-01 | 885.5208 |  | WTG Unscheduled Maintenance | 25503 | 885.5208
3180 | 2024-12-21 | 2025 | 2024 | 2024-12-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.28819 | 0.28819 | 0.32083 | 0 | 0.78333 | 0.78333 | after grid resume Wtg in disconnected to scada. VCB trip O2-08 | Close | 0.030128 | O2-26 | 257.1618 |  | WTG Unscheduled Maintenance | 7879 | 257.1618
3181 | 2024-12-21 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Road issue | 0 | 0 | 0.27778 | 0 | 6.6667 | 6.6667 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | open | 0.25641 | O2-05 | 2159.4444 |  | WTG Unscheduled Maintenance | 7774 | 2159.4444
3182 | 2024-12-21 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Road issue | 0.28819 | 0.28819 | 0.68056 | 0 | 9.4167 | 9.4167 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | open | 0.36218 | O2-05 | 3050.2153 |  | WTG Unscheduled Maintenance | 7774 | 3050.2153
3183 | 2024-12-21 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Road issue | 0.73958 | 0.73958 | 1899-12-31 | 0 | 6.25 | 6.25 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | open | 0.24038 | O2-05 | 2024.4792 |  | WTG Unscheduled Maintenance | 7774 | 2024.4792
3184 | 2024-12-21 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.28819 | 0.28819 | 0.34375 | 0 | 1.3333 | 1.3333 | after grid resume Wtg in disconnected to scada. VCB trip O2-08 | Close | 0.051282 | O2-25 | 529.9444 |  | WTG Unscheduled Maintenance | 9539 | 529.9444
3185 | 2024-12-21 | 2025 | 2024 | 2024-12-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.28819 | 0.28819 | 0.31319 | 0 | 0.6 | 0.6 | after grid resume Wtg in disconnected to scada. VCB trip O2-08 | Close | 0.023077 | O2-01 | 228.425 |  | WTG Unscheduled Maintenance | 9137 | 228.425
3186 | 2024-12-21 | 2025 | 2024 | 2024-12-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.49514 | 0.49514 | 0.55625 | 0 | 1.4667 | 1.4667 | Attend and WTG So check Panel and all connecttion RFO Releted so ok after all connection tight after then reset and start wtg | Close | 0.05641 | O2-06 | 166.2222 |  | WTG Unscheduled Maintenance | 2720 | 166.2222
3187 | 2024-12-21 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.28819 | 0.28819 | 0.34097 | 0 | 1.2667 | 1.2667 | after grid resume Wtg in disconnected to scada. VCB trip O2-08 | Close | 0.048718 | O2-25 | 503.4472 |  | WTG Unscheduled Maintenance | 9539 | 503.4472
3188 | 2024-12-21 | 2025 | 2024 | 2024-12-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.28819 | 0.28819 | 0.3125 | 0 | 0.58333 | 0.58333 | after grid resume Wtg in disconnected to scada. VCB trip O2-08 | Close | 0.022436 | O2-25 | 231.8507 |  | WTG Unscheduled Maintenance | 9539 | 231.8507
3189 | 2024-12-21 | 2025 | 2024 | 2024-12-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.49514 | 0.49514 | 0.53264 | 0 | 0.9 | 0.9 | Attend and wtg check Module and connection after retight and reset and start wtg | Close | 0.034615 | O2-22 | 182.025 |  | WTG Unscheduled Maintenance | 4854 | 182.025
3190 | 2024-12-22 | 2025 | 2024 | 2024-12-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Connectivity issue | 0.39375 | 0.39375 | 0.41806 | 0 | 0.58333 | 0.58333 | after grid resume Wtg in disconnected to scada. VCB trip O2-08 | Close | 0.022436 | O2-26 | 120.4097 |  | WTG Unscheduled Maintenance | 4954 | 120.4097
3191 | 2024-12-22 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.60069 | 0.60069 | 0.84514 | 0 | 5.8667 | 5.8667 | Check error related ckt but Nothing found Abnormal so remove and rifix temp sensor connection then shown normal temp in scada so reset and start wtg | Close | 0.22564 | O2-25 | 789.8 |  | WTG Unscheduled Maintenance | 3231 | 789.8
3192 | 2024-12-22 | 2025 | 2024 | 2024-12-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 525 | Overload axis 2 | Major BD | 0.60069 | 0.60069 | 0.98819 | 0 | 9.3 | 9.3 | Attend and wtg check releated circuit so axis no 2 MCB tripped after interchange for axis Number 1 ( QA001) And Axis Number 3 IQA006)After trail so ok reset and start wtg | Close | 0.35769 | O2-25 | 1252.0125 |  | WTG Unscheduled Maintenance | 3231 | 1252.0125
3193 | 2024-12-22 | 2025 | 2024 | 2024-12-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.94236 | 0.94236 | 0.95417 | 0 | 0.28333 | 0.28333 | after grid resume Wtg in disconnected to scada. VCB trip O2-08 | Close | 0.010897 | O2-01 | 64.8597 |  | WTG Unscheduled Maintenance | 5494 | 64.8597
3194 | 2024-12-22 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Road issue | 0 | 0 | 0.36806 | 0 | 8.8333 | 8.8333 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | open | 0.33974 | O2-05 | 895.8472 |  | WTG Unscheduled Maintenance | 2434 | 895.8472
3195 | 2024-12-22 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Road issue | 0.60069 | 0.60069 | 0.91806 | 0 | 7.6167 | 7.6167 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | open | 0.29295 | O2-05 | 772.4569 |  | WTG Unscheduled Maintenance | 2434 | 772.4569
3196 | 2024-12-22 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Road issue | 0.94236 | 0.94236 | 1899-12-31 | 0 | 1.3833 | 1.3833 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | open | 0.053205 | O2-05 | 140.2931 |  | WTG Unscheduled Maintenance | 2434 | 140.2931
3197 | 2024-12-22 | 2025 | 2024 | 2024-12-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.49306 | 0.49306 | 0.66667 | 0 | 4.1667 | 4.1667 | Attend and Check All connection and so found coonnection loose in fan body after tight all connection after then reset and start wtg | Close | 0.16026 | O2-04 | 1575.5208 |  | WTG Unscheduled Maintenance | 9075 | 1575.5208
3198 | 2024-12-22 | 2025 | 2024 | 2024-12-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.74167 | 0.74167 | 0.8 | 0 | 1.4 | 1.4 | Attend And wtg so UPS Shutdown after check all connection check and tight after TRAIL SO Ok after reset and start wtg | Close | 0.053846 | O2-04 | 529.375 |  | WTG Unscheduled Maintenance | 9075 | 529.375
3199 | 2024-12-22 | 2025 | 2024 | 2024-12-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD | 0.60069 | 0.60069 | 0.61389 | 0 | 0.31667 | 0.31667 | after grid resume Wtg in disconnected to scada. VCB trip O2-08 | Close | 0.012179 | O2-26 | 65.3653 |  | WTG Breakdown Maintenance | 4954 | 65.3653
3200 | 2024-12-22 | 2025 | 2024 | 2024-12-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.39375 | 0.39375 | 0.41806 | 0 | 0.58333 | 0.58333 | after grid resume Wtg in disconnected to scada. VCB trip O2-08 | Close | 0.022436 | O2-01 | 133.5347 |  | WTG Breakdown Maintenance | 5494 | 133.5347
3201 | 2024-12-22 | 2025 | 2024 | 2024-12-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.39375 | 0.39375 | 0.41944 | 0 | 0.61667 | 0.61667 | after grid resume Wtg in disconnected to scada. VCB trip O2-08 | Close | 0.023718 | O2-25 | 83.0188 |  | WTG Breakdown Maintenance | 3231 | 83.0188
3202 | 2024-12-23 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Road issue | 0 | 0 | 0.055556 | 0 | 1.3333 | 1.3333 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | open | 0.051282 | O2-05 | 310.0556 |  | WTG Unscheduled Maintenance | 5581 | 310.0556
3203 | 2024-12-23 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Road issue | 0.070833 | 0.070833 | 0.29236 | 0 | 5.3167 | 5.3167 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | open | 0.20449 | O2-05 | 1236.3465 |  | WTG Unscheduled Maintenance | 5581 | 1236.3465
3204 | 2024-12-23 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Road issue | 0.31597 | 0.31597 | 0.80347 | 0 | 11.7 | 11.7 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | open | 0.45 | O2-05 | 2720.7375 |  | WTG Unscheduled Maintenance | 5581 | 2720.7375
3205 | 2024-12-23 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Road issue | 0.90903 | 0.90903 | 1899-12-31 | 0 | 2.1833 | 2.1833 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | open | 0.083974 | O2-05 | 507.716 |  | WTG Unscheduled Maintenance | 5581 | 507.716
3206 | 2024-12-23 | 2025 | 2024 | 2024-12-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 525 | Overload axis 2 | Break down | 0.34028 | 0.34028 | 0.37917 | 0 | 0.93333 | 0.93333 | Check Data log after so Normal then Reset and start wtg | Close | 0.035897 | O2-25 | 245.0778 |  | WTG Unscheduled Maintenance | 6302 | 245.0778
3207 | 2024-12-23 | 2025 | 2024 | 2024-12-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 525 | Overload axis 2 | Break down | 0.69097 | 0.69097 | 0.82361 | 0 | 3.1833 | 3.1833 | Attend And wtg check releted circuit SO OK After Contactor Interchange Axis no 3 and 1 | Close | 0.12244 | O2-25 | 835.8903 |  | WTG Unscheduled Maintenance | 6302 | 835.8903
3208 | 2024-12-23 | 2025 | 2024 | 2024-12-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 470 | Repeating error BP180 | Break down | 0.86806 | 0.86806 | 0.96667 | 0 | 2.3667 | 2.3667 | Attend and wtg check All Connection and after tight All Connection then reset And start wtg | Close | 0.091026 | O2-12 | 732.5819 |  | WTG Unscheduled Maintenance | 7429 | 732.5819
3209 | 2024-12-23 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.6875 | 0.6875 | 0.72431 | 0 | 0.88333 | 0.88333 | after grid resume Wtg in disconnected to scada. VCB trip O2-08 | Close | 0.033974 | O2-25 | 231.9486 |  | WTG Unscheduled Maintenance | 6302 | 231.9486
3210 | 2024-12-23 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.73611 | 0.73611 | 0.73819 | 0 | 0.05 | 0.05 | Check Data log after so Normal then Reset and start wtg | Close | 0.0019231 | O2-25 | 13.1292 |  | WTG Unscheduled Maintenance | 6302 | 13.1292
3211 | 2024-12-23 | 2025 | 2024 | 2024-12-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 650 | Pitch controller communication error | Break down | 0.31597 | 0.31597 | 0.34097 | 0 | 0.6 | 0.6 | Check Data log after so Normal then Reset and start wtg | Close | 0.023077 | O2-01 | 0 |  | WTG Unscheduled Maintenance | 0 | 0
3212 | 2024-12-23 | 2025 | 2024 | 2024-12-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.34028 | 0.34028 | 0.37917 | 0 | 0.93333 | 0.93333 | Check Data log after so Normal then Reset and start wtg | Close | 0.035897 | O2-26 | 257.9889 |  | WTG Unscheduled Maintenance | 6634 | 257.9889
3213 | 2024-12-23 | 2025 | 2024 | 2024-12-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.41528 | 0.41528 | 0.65972 | 0 | 5.8667 | 5.8667 | Attend And WTG check All Module so found M1 Not RUN Condition after Intechange m1 Module for O2.25 After check but not RUN Module WIP | Close | 0.22564 | O2-26 | 1621.6444 |  | WTG Unscheduled Maintenance | 6634 | 1621.6444
3214 | 2024-12-23 | 2025 | 2024 | 2024-12-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Major BD | 0.6875 | 0.6875 | 1899-12-31 | 0 | 7.5 | 7.5 | Attend And WTG check All Module so found M1 Not RUN Condition after Intechange m1 Module for O2.25 After check but not RUN Module WIP | Close | 0.28846 | O2-26 | 2073.125 |  | WTG Unscheduled Maintenance | 6634 | 2073.125
3215 | 2024-12-23 | 2025 | 2024 | 2024-12-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.086806 | 0.086806 | 0.11389 | 0 | 0.65 | 0.65 | After CAN RFO signal coming than start WTG. | Close | 0.025 | O2-11 | 177.7479 |  | WTG Unscheduled Maintenance | 6563 | 177.7479
3216 | 2024-12-23 | 2025 | 2024 | 2024-12-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.84167 | 0.84167 | 0.8625 | 0 | 0.5 | 0.5 | Check Data log after so Normal then Reset and start wtg | Close | 0.019231 | O2-01 | 0 |  | WTG Unscheduled Maintenance | 0 | 0
3217 | 2024-12-23 | 2025 | 2024 | 2024-12-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Break down | 0.82569 | 0.82569 | 0.94653 | 0 | 2.9 | 2.9 | Attend and wtg check reletad circuit so All connection TIGHT After reset and start wtg | Close | 0.11154 | O2-12 | 897.6708 |  | WTG Unscheduled Maintenance | 7429 | 897.6708
3218 | 2024-12-23 | 2025 | 2024 | 2024-12-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 650 | Pitch controller communication error | Break down | 0.82569 | 0.82569 | 0.85833 | 0 | 0.78333 | 0.78333 | after grid resume Wtg in disconnected to scada. VCB trip O2-11 | Close | 0.030128 | O2-01 | 0 |  | WTG Unscheduled Maintenance | 0 | 0
3219 | 2024-12-23 | 2025 | 2024 | 2024-12-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 650 | Pitch controller communication error | Break down | 0.82569 | 0.82569 | 0.88403 | 0 | 1.4 | 1.4 | after grid resume Wtg in disconnected to scada. VCB trip O2-11 | Close | 0.053846 | O2-03 | 630.7 |  | WTG Unscheduled Maintenance | 10812 | 630.7
3220 | 2024-12-23 | 2025 | 2024 | 2024-12-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.68194 | 0.68194 | 0.73889 | 0 | 1.3667 | 1.3667 | Conv pre heating mode after complete start | Close | 0.052564 | O2-01 | 0 |  | WTG Breakdown Maintenance | 0 | 0
3221 | 2024-12-23 | 2025 | 2024 | 2024-12-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.58333 | 0.58333 | 0.68403 | 0 | 2.4167 | 2.4167 | Project Pending Punch Point closing work | Close | 0.092949 | O2-14 | 674.3507 |  | WTG Breakdown Maintenance | 6697 | 674.3507
3222 | 2024-12-24 | 2025 | 2024 | 2024-12-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.44931 | 0.44931 | 0.45833 | 0 | 0.21667 | 0.21667 | Check Data log after so Normal then Reset and start wtg | Close | 0.0083333 | O2-21 | 148.3625 |  | WTG Unscheduled Maintenance | 16434 | 148.3625
3223 | 2024-12-24 | 2025 | 2024 | 2024-12-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.27083 | 0.27083 | 0.27847 | 0 | 0.18333 | 0.18333 | Check Data log after so Normal then Reset and start wtg | Close | 0.0070513 | O2-26 | 202.8583 |  | WTG Unscheduled Maintenance | 26556 | 202.8583
3224 | 2024-12-24 | 2025 | 2024 | 2024-12-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.6 | 0.6 | 0.62222 | 0 | 0.53333 | 0.53333 | Rep Error Inspection work (Project Team ) | Close | 0.020513 | O2-04 | 476.8222 |  | WTG Breakdown Maintenance | 21457 | 476.8222
3225 | 2024-12-24 | 2025 | 2024 | 2024-12-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Major BD | 0 | 0 | 0.88194 | 0 | 21.1667 | 21.1667 | After grid resume time error not connect to SAM And solution center so attend and check connection than programing done and but mudule not come in to run mode so we put fresh commissionning pakage but same issue occurred so we arrange new MC212 WITH Card and pogram but key licence not available of new module and take time to come licence from HO so we arrnge MC210 Module with card from tithawa than program it and replace than start wtg | Close | 0.8141 | O2-26 | 23420.9167 |  | WTG Unscheduled Maintenance | 26556 | 23420.9167
3226 | 2024-12-24 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Road issue | 0 | 0 | 1899-12-31 | 0 | 24 | 24 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | open | 0.92308 | O2-05 | 25176 |  | WTG Unscheduled Maintenance | 25176 | 25176
3227 | 2024-12-25 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Road issue | 0 | 0 | 0.24861 | 0 | 5.9667 | 5.9667 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | open | 0.22949 | O2-05 | 5612.1472 |  | WTG Unscheduled Maintenance | 22574 | 5612.1472
3228 | 2024-12-25 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Road issue | 0.26806 | 0.26806 | 0.77014 | 0 | 12.05 | 12.05 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | open | 0.46346 | O2-05 | 11334.0292 |  | WTG Unscheduled Maintenance | 22574 | 11334.0292
3229 | 2024-12-25 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Road issue | 0.79097 | 0.79097 | 1899-12-31 | 0 | 5.0167 | 5.0167 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | open | 0.19295 | O2-05 | 4718.5931 |  | WTG Unscheduled Maintenance | 22574 | 4718.5931
3230 | 2024-12-25 | 2025 | 2024 | 2024-12-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.79097 | 0.79097 | 0.82847 | 0 | 0.9 | 0.9 | after grid resume Wtg in disconnected to scada. VCB trip O2-11 | Close | 0.034615 | O2-09 | 853.8 |  | WTG Unscheduled Maintenance | 22768 | 853.8
3231 | 2024-12-25 | 2025 | 2024 | 2024-12-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.95486 | 0.95486 | 0.99722 | 0 | 1.0167 | 1.0167 | After CAN RFO signal coming than start WTG. | Close | 0.039103 | O2-07 | 558.4042 |  | WTG Unscheduled Maintenance | 13182 | 558.4042
3232 | 2024-12-25 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Connectivity issue | 0.26806 | 0.26806 | 0.32639 | 0 | 1.4 | 1.4 | after grid resume Wtg in disconnected to scada. VCB trip O2-08 | Close | 0.053846 | O2-25 | 1034.8333 |  | WTG Unscheduled Maintenance | 17740 | 1034.8333
3233 | 2024-12-25 | 2025 | 2024 | 2024-12-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Connectivity issue | 0.26806 | 0.26806 | 0.31111 | 0 | 1.0333 | 1.0333 | after grid resume Wtg in disconnected to scada. VCB trip O2-08 | Close | 0.039744 | O2-03 | 984.1208 |  | WTG Unscheduled Maintenance | 22857 | 984.1208
3234 | 2024-12-25 | 2025 | 2024 | 2024-12-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Connectivity issue | 0.26806 | 0.26806 | 0.28611 | 0 | 0.43333 | 0.43333 | after grid resume Wtg in disconnected to scada. VCB trip O2-13 | Close | 0.016667 | O2-12 | 386.6958 |  | WTG Unscheduled Maintenance | 21417 | 386.6958
3235 | 2024-12-25 | 2025 | 2024 | 2024-12-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 525 | Overload axis 2 | Break down | 0.79097 | 0.79097 | 0.95417 | 0 | 3.9167 | 3.9167 | Attend and wtg check Axis no 2 so found MCB Trip after trublshooting check all circuit releted contector check check 24 V Supply so ok after tight all connection after trail so ok after then reset and start wtg | Close | 0.15064 | O2-25 | 2895.0694 |  | WTG Unscheduled Maintenance | 17740 | 2895.0694
3236 | 2024-12-25 | 2025 | 2024 | 2024-12-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.85417 | 0.85417 | 0.9625 | 0 | 2.6 | 2.6 | Attend and wtg check pitch releted circuit check All Axis check and connection tight after trail so ok after then reset and start wtg | Close | 0.1 | O2-06 | 1601.7083 |  | WTG Unscheduled Maintenance | 14785 | 1601.7083
3237 | 2024-12-25 | 2025 | 2024 | 2024-12-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.85417 | 0.85417 | 0.98472 | 0 | 3.1333 | 3.1333 | Atten and wtg check releted circuit so check all connection for ingetem and check all CM202 Connector connection check and all connection retight after trail so ok after then reset and start wtf | Close | 0.12051 | O2-22 | 2093.3278 |  | WTG Unscheduled Maintenance | 16034 | 2093.3278
3238 | 2024-12-25 | 2025 | 2024 | 2024-12-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.95486 | 0.95486 | 0.99861 | 0 | 1.05 | 1.05 | After CAN RFO signal coming than start WTG. | Close | 0.040385 | O2-06 | 646.8437 |  | WTG Unscheduled Maintenance | 14785 | 646.8437
3239 | 2024-12-25 | 2025 | 2024 | 2024-12-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.95486 | 0.95486 | 0.98125 | 0 | 0.63333 | 0.63333 | After CAN RFO signal coming than start WTG. | Close | 0.024359 | O2-06 | 390.1597 |  | WTG Unscheduled Maintenance | 14785 | 390.1597
3240 | 2024-12-25 | 2025 | 2024 | 2024-12-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.79097 | 0.79097 | 0.84028 | 0 | 1.1833 | 1.1833 | after grid resume Wtg in disconnected to scada. VCB trip O2-13 | Close | 0.045513 | O2-12 | 1055.9771 |  | WTG Unscheduled Maintenance | 21417 | 1055.9771
3241 | 2024-12-26 | 2025 | 2024 | 2024-12-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.52431 | 0.52431 | 0.76875 | 0 | 5.8667 | 5.8667 | Manual stop for Project Pending work | Close | 0.22564 | O2-25 | 4577.2222 |  | WTG Breakdown Maintenance | 18725 | 4577.2222
3242 | 2024-12-26 | 2025 | 2024 | 2024-12-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.57986 | 0.57986 | 0.69236 | 0 | 2.7 | 2.7 | Attend and wtg check releted circuit after check perameter and cable twist physhical after match to Sam so ok after trail so ok after reset and start wtg. | Close | 0.10385 | O2-26 | 1772.6625 |  | WTG Unscheduled Maintenance | 15757 | 1772.6625
3243 | 2024-12-26 | 2025 | 2024 | 2024-12-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Major BD | 0.72917 | 0.72917 | 1899-12-31 | 0 | 6.5 | 6.5 | Attend wtg check bottom panel so ok after top Hub Module check and pograming done after arrange new modle for other site | Close | 0.25 | O2-22 | 4139.6875 |  | WTG Unscheduled Maintenance | 15285 | 4139.6875
3244 | 2024-12-26 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.77708 | 0.77708 | 0.84931 | 0 | 1.7333 | 1.7333 | after grid resume Wtg in disconnected to scada. VCB trip O2-08 | Close | 0.066667 | O2-25 | 1352.3611 |  | WTG Unscheduled Maintenance | 18725 | 1352.3611
3245 | 2024-12-26 | 2025 | 2024 | 2024-12-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.77708 | 0.77708 | 0.83819 | 0 | 1.4667 | 1.4667 | after grid resume Wtg in disconnected to scada. VCB trip O2-08 | Close | 0.05641 | O2-25 | 1144.3056 |  | WTG Unscheduled Maintenance | 18725 | 1144.3056
3246 | 2024-12-26 | 2025 | 2024 | 2024-12-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.77708 | 0.77708 | 0.80556 | 0 | 0.68333 | 0.68333 | after grid resume Wtg in disconnected to scada. VCB trip O2-08 | Close | 0.026282 | O2-01 | 456.4097 |  | WTG Unscheduled Maintenance | 16030 | 456.4097
3247 | 2024-12-26 | 2025 | 2024 | 2024-12-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.78819 | 0.78819 | 0.85347 | 0 | 1.5667 | 1.5667 | after grid resume Wtg in disconnected to scada. VCB trip O2-08 | Close | 0.060256 | O2-26 | 1028.5819 |  | WTG Unscheduled Maintenance | 15757 | 1028.5819
3248 | 2024-12-26 | 2025 | 2024 | 2024-12-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.77708 | 0.77708 | 0.8 | 0 | 0.55 | 0.55 | after grid resume Wtg in disconnected to scada. VCB trip O2-08 | Close | 0.021154 | O2-26 | 361.0979 |  | WTG Unscheduled Maintenance | 15757 | 361.0979
3249 | 2024-12-26 | 2025 | 2024 | 2024-12-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0 | 0 | 0.016667 | 0 | 0.4 | 0.4 | After CAN RFO signal coming than start WTG. | Close | 0.015385 | O2-07 | 162.6167 |  | WTG Unscheduled Maintenance | 9757 | 162.6167
3250 | 2024-12-26 | 2025 | 2024 | 2024-12-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down | 0.84167 | 0.84167 | 0.93889 | 0 | 2.3333 | 2.3333 | Attend and wtg check releted error after UPS All conection check found Ups off so after restor ups and charge after reset and start wtg | Close | 0.089744 | O2-04 | 1204.7778 |  | WTG Unscheduled Maintenance | 12392 | 1204.7778
3251 | 2024-12-26 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Road issue | 0 | 0 | 0.75069 | 0 | 18.0167 | 18.0167 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | open | 0.69295 | O2-05 | 13249.7569 |  | WTG Unscheduled Maintenance | 17650 | 13249.7569
3252 | 2024-12-26 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Road issue | 0.77708 | 0.77708 | 1899-12-31 | 0 | 5.35 | 5.35 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | open | 0.20577 | O2-05 | 3934.4792 |  | WTG Unscheduled Maintenance | 17650 | 3934.4792
3253 | 2024-12-27 | 2025 | 2024 | 2024-12-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.48264 | 0.48264 | 0.65972 | 0 | 4.25 | 4.25 | Project Pending Punch Point closing work | Close | 0.16346 | O2-11 | 2512.2812 |  | WTG Breakdown Maintenance | 14187 | 2512.2812
3254 | 2024-12-27 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Road issue | 0 | 0 | 0.71111 | 0 | 17.0667 | 17.0667 | WTG stop Pump cooling Sys.Overload error occurred in down condition due to road not approchable | open | 0.65641 | O2-05 | 14124.0889 |  | WTG Unscheduled Maintenance | 19862 | 14124.0889
3255 | 2024-12-27 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Break down | 0.74444 | 0.74444 | 0.75139 | 0 | 0.16667 | 0.16667 | Attend and wtg check releted wtg so fillup coolant and Coolant Motor MCB tripped after charge MCB and start wtg | Close | 0.0064103 | O2-05 | 137.9306 |  | WTG Unscheduled Maintenance | 19862 | 137.9306
3256 | 2024-12-27 | 2025 | 2024 | 2024-12-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0.36458 | 0.36458 | 0.41528 | 0 | 1.2167 | 1.2167 | Attend and wtg check bottom panel so found UPS Tripped after check all connection and tight all connection after trail so ok after reset and start wtg | Close | 0.046795 | O2-04 | 692.2326 |  | WTG Unscheduled Maintenance | 13655 | 692.2326
3257 | 2024-12-27 | 2025 | 2024 | 2024-12-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.56528 | 0.56528 | 0.56944 | 0 | 0.1 | 0.1 | Check Data log after so Normal then Reset and start wtg | Close | 0.0038462 | O2-15 | 72.3125 |  | WTG Unscheduled Maintenance | 17355 | 72.3125
3258 | 2024-12-27 | 2025 | 2024 | 2024-12-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 650 | Pitch controller communication error | Break down | 0.73681 | 0.73681 | 0.74236 | 0 | 0.13333 | 0.13333 | Check Data log after so Normal then Reset and start wtg | Close | 0.0051282 | O2-12 | 77.3444 |  | WTG Unscheduled Maintenance | 13922 | 77.3444
3259 | 2024-12-27 | 2025 | 2024 | 2024-12-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Major BD | 0 | 0 | 0.375 | 0 | 9 | 9 | further trublshooting and material arrngment other site | open | 0.34615 | O2-22 | 4079.25 |  | WTG Unscheduled Maintenance | 10878 | 4079.25
3260 | 2024-12-27 | 2025 | 2024 | 2024-12-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Major BD | 0.76806 | 0.76806 | 1899-12-31 | 0 | 5.5667 | 5.5667 | further trublshooting and material arrngment other site | open | 0.2141 | O2-22 | 2523.0917 |  | WTG Unscheduled Maintenance | 10878 | 2523.0917
3261 | 2024-12-27 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0.74444 | 0.75486 | 0.75486 | 0.25 | 0 | 0.25 | Disconnect to scada after check UPS charge after error reset and start wtg | Close | 0.0096154 | O2-02 | 70.7083 |  | WTG Unscheduled Maintenance | 6788 | 70.7083
3262 | 2024-12-27 | 2025 | 2024 | 2024-12-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0.74444 | 0.76875 | 0.76875 | 0.58333 | 0 | 0.58333 | Disconnect to scada after check UPS charge after error reset and start wtg | Close | 0.022436 | O2-26 | 345.3333 |  | WTG Unscheduled Maintenance | 14208 | 345.3333
3263 | 2024-12-27 | 2025 | 2024 | 2024-12-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Connectivity issue | 0.77639 | 0.77639 | 0.82361 | 0 | 1.1333 | 1.1333 | After grid resume time error after reset and start wtg VCB OF For O2-21 | Close | 0.04359 | O2-06 | 427.2194 |  | WTG Unscheduled Maintenance | 9047 | 427.2194
3264 | 2024-12-27 | 2025 | 2024 | 2024-12-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Connectivity issue | 0.80972 | 0.80972 | 0.84792 | 0 | 0.91667 | 0.91667 | After grid resume time error after reset and start wtg VCB OF For O2-21 | Close | 0.035256 | O2-06 | 345.5451 |  | WTG Unscheduled Maintenance | 9047 | 345.5451
3265 | 2024-12-27 | 2025 | 2024 | 2024-12-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Connectivity issue | 0.81111 | 0.81111 | 0.85 | 0 | 0.93333 | 0.93333 | After grid resume time error after reset and start wtg VCB OF For O2-21 | Close | 0.035897 | O2-06 | 351.8278 |  | WTG Unscheduled Maintenance | 9047 | 351.8278
3266 | 2024-12-27 | 2025 | 2024 | 2024-12-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Connectivity issue | 0.76736 | 0.76736 | 0.80556 | 0 | 0.91667 | 0.91667 | after grid resume Wtg in disconnected to scada. VCB trip O2-08 | Close | 0.035256 | O2-01 | 743.0729 |  | WTG Unscheduled Maintenance | 19455 | 743.0729
3267 | 2024-12-27 | 2025 | 2024 | 2024-12-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 525 | Overload axis 2 | Break down | 0.80625 | 0.80625 | 0.84861 | 0 | 1.0167 | 1.0167 | Attend and wtg so check asix no 2 Pitch Releted MCB Tripped after check all connection and retight after trail so ok after then reset and start wtg | Close | 0.039103 | O2-01 | 824.1354 |  | WTG Unscheduled Maintenance | 19455 | 824.1354
3268 | 2024-12-28 | 2025 | 2024 | 2024-12-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.45486 | 0.45486 | 0.66667 | 0 | 5.0833 | 5.0833 | Project punch point verification work + blade axis-2 chhopper 2 nos replace after reset and start wtg | Close | 0.19551 | O2-01 | 4722.8403 |  | WTG Breakdown Maintenance | 22298 | 4722.8403
3269 | 2024-12-28 | 2025 | 2024 | 2024-12-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.5 | 0.5 | 0.90556 | 0 | 9.7333 | 9.7333 | WTR-0638-Extentionof transformer Winding strips after error for LOW Hydralic pressure error troublshuting for WIP | Close | 0.37436 | O2-12 | 9277.8944 |  | WTG Breakdown Maintenance | 22877 | 9277.8944
3270 | 2024-12-28 | 2025 | 2024 | 2024-12-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Major BD | 0 | 0 | 0.375 | 0 | 9 | 9 | FUrther trublshooting FOR Engineering team Work in pogress | open | 0.34615 | O2-22 | 6736.875 |  | WTG Unscheduled Maintenance | 17965 | 6736.875
3271 | 2024-12-28 | 2025 | 2024 | 2024-12-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.76458 | 0.76458 | 1899-12-31 | 0 | 5.65 | 5.65 | FUrther trublshooting FOR Engineering team Work in pogress | open | 0.21731 | O2-22 | 4229.2604 |  | WTG Unscheduled Maintenance | 17965 | 4229.2604
3272 | 2024-12-28 | 2025 | 2024 | 2024-12-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Major BD | 0.75694 | 0.75694 | 0.80347 | 0 | 1.1167 | 1.1167 | After grid resume time error after reset and start wtg VCB OF For O2-21 | Close | 0.042949 | O2-06 | 890.2625 |  | WTG Unscheduled Maintenance | 19134 | 890.2625
3273 | 2024-12-28 | 2025 | 2024 | 2024-12-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 650 | Pitch controller communication error | Break down | 0.16944 | 0.16944 | 0.2 | 0 | 0.73333 | 0.73333 | Check Data log after so Normal then Reset and start wtg | Close | 0.028205 | O2-06 | 584.65 |  | WTG Unscheduled Maintenance | 19134 | 584.65
3274 | 2024-12-28 | 2025 | 2024 | 2024-12-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down | 0.90556 | 0.90556 | 1899-12-31 | 0 | 2.2667 | 2.2667 | Attend and wtg check oil level and check all valv after arrange new 9.1 valv work in pogresh | open | 0.087179 | O2-12 | 2160.6056 |  | WTG Unscheduled Maintenance | 22877 | 2160.6056
3275 | 2024-12-29 | 2025 | 2024 | 2024-12-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Major BD | 0 | 0 | 0.37778 | 0 | 9.0667 | 9.0667 | FUrther trublshooting FOR Engineering team Work in pogress | Close | 0.34872 | O2-22 | 7663.2222 |  | WTG Unscheduled Maintenance | 20285 | 7663.2222
3276 | 2024-12-29 | 2025 | 2024 | 2024-12-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Major BD | 0.74444 | 0.74444 | 0.91667 | 0 | 4.1333 | 4.1333 | Attend and check than found software error so apply new software than check but same error occurred so our technical team analyss and update software parameter than take trial than start WTG(now turbine under observation) | Close | 0.15897 | O2-22 | 3493.5278 |  | WTG Unscheduled Maintenance | 20285 | 3493.5278
3277 | 2024-12-29 | 2025 | 2024 | 2024-12-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Major BD | 0 | 0 | 0.65833 | 0 | 15.8 | 15.8 | attend And check than found 400v cable interchange on bottom transformer in WTR work so we reconnected phase4 sequend and charge VCB but vcb not charge so call BOP team and check it than Charge vcb than start WTG. | Close | 0.60769 | O2-12 | 14483.9917 |  | WTG Unscheduled Maintenance | 22001 | 14483.9917
3278 | 2024-12-29 | 2025 | 2024 | 2024-12-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Break down | 0.34236 | 0.34236 | 0.34792 | 0 | 0.13333 | 0.13333 | Check Data log after so Normal then Reset and start wtg | Close | 0.0051282 | O2-24 | 107.0556 |  | WTG Unscheduled Maintenance | 19270 | 107.0556
3279 | 2024-12-29 | 2025 | 2024 | 2024-12-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Break down | 0.4125 | 0.4125 | 0.45 | 0 | 0.9 | 0.9 | After grid resume time error occurred so after reset and start wtg | Close | 0.034615 | O2-22 | 760.6875 |  | WTG Unscheduled Maintenance | 20285 | 760.6875
3280 | 2024-12-29 | 2025 | 2024 | 2024-12-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Break down | 0.74444 | 0.74444 | 0.78472 | 0 | 0.96667 | 0.96667 | After grid resume time error occurred so after reset and start wtg | Close | 0.037179 | O2-22 | 817.0347 |  | WTG Unscheduled Maintenance | 20285 | 817.0347
3281 | 2024-12-29 | 2025 | 2024 | 2024-12-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.74444 | 0.74444 | 0.79167 | 0 | 1.1333 | 1.1333 | After grid resume time error occurred so apply soft rebbot and reset and start WTG | Close | 0.04359 | O2-21 | 870.0694 |  | WTG Unscheduled Maintenance | 18425 | 870.0694
3282 | 2024-12-30 | 2025 | 2024 | 2024-12-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Connectivity issue | 0.54861 | 0.54861 | 0.62014 | 0 | 1.7167 | 1.7167 | Due to O2 24 Jumper open so Turbine is discoonected From Scada so connectivity not available after connectivity comes than start Turbine. | Close | 0.066026 | O2-22 | 1352.9479 |  | WTG Breakdown Maintenance | 18915 | 1352.9479
3283 | 2024-12-30 | 2025 | 2024 | 2024-12-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Connectivity issue | 0.54861 | 0.54861 | 0.62014 | 0 | 1.7167 | 1.7167 | Due to O2 24 Jumper open so Turbine is discoonected From Scada so connectivity not available after connectivity comes than start Turbine. | Close | 0.066026 | O2-24 | 1421.8292 |  | WTG Breakdown Maintenance | 19878 | 1421.8292
3284 | 2024-12-30 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Break down | 0.54861 | 0.54861 | 0.57292 | 0 | 0.58333 | 0.58333 | After grid resume time error occurred so apply soft rebbot and reset and start WTG | Close | 0.022436 | O2-02 | 542.3299 |  | WTG Unscheduled Maintenance | 22313 | 542.3299
3285 | 2024-12-30 | 2025 | 2024 | 2024-12-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 158 | SLC SF max. rotor brake pad temp. | Break down | 0.098611 | 0.098611 | 0.11458 | 0 | 0.38333 | 0.38333 | Check Data log after Temp comes Normal then Reset and start wtg | Close | 0.014744 | O2-04 | 254.1819 |  | WTG Unscheduled Maintenance | 15914 | 254.1819
3286 | 2024-12-30 | 2025 | 2024 | 2024-12-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Break down | 0.39653 | 0.39653 | 0.48889 | 0 | 2.2167 | 2.2167 | attend and check related circuit than nothing found abnormal than apply hard reboot pf UPS and also coolent refilling done and reset and start WTG. | Close | 0.085256 | O2-26 | 1802.7042 |  | WTG Unscheduled Maintenance | 19518 | 1802.7042
3287 | 2024-12-30 | 2025 | 2024 | 2024-12-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.54861 | 0.54861 | 0.56667 | 0 | 0.43333 | 0.43333 | After grid resume time error occurred so Check data than found Encoder angle value is malfunctioning so apply hard reboot of UPS than reste and start WTG. | Close | 0.016667 | O2-12 | 314.7083 |  | WTG Unscheduled Maintenance | 17430 | 314.7083
3288 | 2024-12-30 | 2025 | 2024 | 2024-12-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down | 0.57639 | 0.57639 | 0.57778 | 0 | 0.033333 | 0.033333 | Check Data log after so Normal then Reset and start wtg | Close | 0.0012821 | O2-11 | 15.3097 |  | WTG Unscheduled Maintenance | 11023 | 15.3097
3289 | 2024-12-30 | 2025 | 2024 | 2024-12-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 550 | Pitch current asymmetry | Break down | 0.35347 | 0.35347 | 0.35764 | 0 | 0.1 | 0.1 | Check Data log after so Normal then Reset and start wtg | Close | 0.0038462 | O2-22 | 78.8125 |  | WTG Unscheduled Maintenance | 18915 | 78.8125
3290 | 2024-12-30 | 2025 | 2024 | 2024-12-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 658 | Error pitch converter 3 | Auto reset | 0.85764 | 0.85764 | 0.85833 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | O2-21 | 13.5521 |  | WTG Unscheduled Maintenance | 19515 | 13.5521
3291 | 2024-12-30 | 2025 | 2024 | 2024-12-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Break down | 0.54861 | 0.54861 | 0.57569 | 0 | 0.65 | 0.65 | After grid resume time error occurred so apply soft rebbot and reset and start WTG | Close | 0.025 | O2-18 | 481.4875 |  | WTG Unscheduled Maintenance | 17778 | 481.4875
3292 | 2024-12-30 | 2025 | 2024 | 2024-12-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Break down | 0.65764 | 0.65764 | 0.69306 | 0 | 0.85 | 0.85 | After grid resume time error occurred so apply soft rebbot and reset and start WTG | Close | 0.032692 | O2-18 | 629.6375 |  | WTG Unscheduled Maintenance | 17778 | 629.6375
3293 | 2024-12-30 | 2025 | 2024 | 2024-12-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.54861 | 0.54861 | 0.68611 | 0 | 3.3 | 3.3 | Attend And wtg check releted circuit Than found MCB was trip in axis 2 check all contector and mcb connection than retight all connection and apply hard reboot than reset and start WTG. | Close | 0.12692 | O2-05 | 2996.2625 |  | WTG Unscheduled Maintenance | 21791 | 2996.2625
3294 | 2024-12-31 | 2025 | 2024 | 2024-12-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.77153 | 0.77153 | 0.77431 | 0 | 0.066667 | 0.066667 | Rough Blade Parameter,Herk 10 and CM202 driver file software update work done than start WTG. | Close | 0.0025641 | O2-05 | 28.6556 |  | WTG Breakdown Maintenance | 10316 | 28.6556
3295 | 2024-12-31 | 2025 | 2024 | 2024-12-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.77431 | 0.77431 | 0.77778 | 0 | 0.083333 | 0.083333 | Rough Blade Parameter,Herk 10 and CM202 driver file software update work done than start WTG. | Close | 0.0032051 | O2-26 | 293.7194 |  | WTG Breakdown Maintenance | 9778 | 33.9514
3296 | 2024-12-31 | 2025 | 2024 | 2024-12-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.77639 | 0.77639 | 0.78125 | 0 | 0.11667 | 0.11667 | Rough Blade Parameter,Herk 10 and CM202 driver file software update work done than start WTG. | Close | 0.0044872 | O2-03 | 57.3111 |  | WTG Breakdown Maintenance | 11845 | 57.5799
3297 | 2024-12-31 | 2025 | 2024 | 2024-12-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.37778 | 0.37778 | 0.39097 | 0 | 0.31667 | 0.31667 | After Grid Jurk Check Data log after so Normal then apply soft reboot than Reset and start wtg | Close | 0.012179 | O2-15 | 284.6875 |  | WTG Unscheduled Maintenance | 7466 | 98.5097
3298 | 2024-12-31 | 2025 | 2024 | 2024-12-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.58194 | 0.58194 | 0.58681 | 0 | 0.11667 | 0.11667 | Rough Blade Parameter,Herk 10 and CM202 driver file software update work done than start WTG. | Close | 0.0044872 | O2-12 | 44.2847 |  | WTG Breakdown Maintenance | 7466 | 36.2931
3299 | 2024-12-31 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.32083 | 0.32083 | 0.32292 | 0 | 0.05 | 0.05 | Check Data log after so Normal then Reset and start wtg | Close | 0.0019231 | O2-14 | 38.1306 |  | WTG Unscheduled Maintenance | 10224 | 21.3
3300 | 2024-12-31 | 2025 | 2024 | 2024-12-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.79583 | 0.79583 | 0.79861 | 0 | 0.066667 | 0.066667 | Rough Blade Parameter,Herk 10 and CM202 driver file software update work done than start WTG. | Close | 0.0025641 | O2-11 | 528.3806 |  | WTG Breakdown Maintenance | 10224 | 28.4
3301 | 2024-12-31 | 2025 | 2024 | 2024-12-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.37778 | 0.37778 | 0.40625 | 0 | 0.68333 | 0.68333 | After Grid Jurk Check Data log after so Normal then apply soft reboot than Reset and start wtg | Close | 0.026282 | O2-26 | 58.6278 |  | WTG Unscheduled Maintenance | 10316 | 293.7194
3302 | 2024-12-31 | 2025 | 2024 | 2024-12-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.58889 | 0.58889 | 0.59444 | 0 | 0.13333 | 0.13333 | Rough Blade Parameter,Herk 10 and CM202 driver file software update work done than start WTG. | Close | 0.0051282 | O2-03 | 25.7986 |  | WTG Breakdown Maintenance | 10316 | 57.3111
3303 | 2024-12-31 | 2025 | 2024 | 2024-12-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.37778 | 0.37778 | 0.40903 | 0 | 0.75 | 0.75 | After Grid Jurk Check Data log after so Normal then apply soft reboot than Reset and start wtg | Close | 0.028846 | O2-15 | 35.5 |  | WTG Unscheduled Maintenance | 9110 | 284.6875
3304 | 2024-12-31 | 2025 | 2024 | 2024-12-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.59583 | 0.59583 | 0.60069 | 0 | 0.11667 | 0.11667 | Rough Blade Parameter,Herk 10 and CM202 driver file software update work done than start WTG. | Close | 0.0044872 | O2-12 | 57.7889 |  | WTG Breakdown Maintenance | 9110 | 44.2847
3305 | 2024-12-31 | 2025 | 2024 | 2024-12-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.78333 | 0.78333 | 0.78819 | 0 | 0.11667 | 0.11667 | Rough Blade Parameter,Herk 10 and CM202 driver file software update work done than start WTG. | Close | 0.0044872 | O2-14 | 45.4368 |  | WTG Breakdown Maintenance | 7844 | 38.1306
3306 | 2024-12-31 | 2025 | 2024 | 2024-12-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.79167 | 0.79167 | 0.85903 | 0 | 1.6167 | 1.6167 | Attend and reinstall M1 software than reset and start WTG. | Close | 0.062179 | O2-11 | 31.1083 |  | WTG Unscheduled Maintenance | 7844 | 528.3806
3307 | 2024-12-31 | 2025 | 2024 | 2024-12-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.78611 | 0.78611 | 0.79167 | 0 | 0.13333 | 0.13333 | Rough Blade Parameter,Herk 10 and CM202 driver file software update work done than start WTG. | Close | 0.0051282 | O2-12 | 39.9826 |  | WTG Breakdown Maintenance | 10553 | 58.6278
3308 | 2024-12-31 | 2025 | 2024 | 2024-12-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.78819 | 0.78819 | 0.79167 | 0 | 0.083333 | 0.083333 | Rough Blade Parameter,Herk 10 and CM202 driver file software update work done than start WTG. | Close | 0.0032051 | O2-10 | 272.6208 |  | WTG Breakdown Maintenance | 7430 | 25.7986
3309 | 2024-12-31 | 2025 | 2024 | 2024-12-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.75833 | 0.75833 | 0.76181 | 0 | 0.083333 | 0.083333 | Rough Blade Parameter,Herk 10 and CM202 driver file software update work done than start WTG. | Close | 0.0032051 | O2-21 | 38.9458 |  | WTG Breakdown Maintenance | 10224 | 35.5
3310 | 2024-12-31 | 2025 | 2024 | 2024-12-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.79306 | 0.79306 | 0.79792 | 0 | 0.11667 | 0.11667 | Rough Blade Parameter,Herk 10 and CM202 driver file software update work done than start WTG. | Close | 0.0044872 | O2-22 | 220.0618 |  | WTG Breakdown Maintenance | 11888 | 57.7889
3311 | 2024-12-31 | 2025 | 2024 | 2024-12-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.76458 | 0.76458 | 0.76944 | 0 | 0.11667 | 0.11667 | Rough Blade Parameter,Herk 10 and CM202 driver file software update work done than start WTG. | Close | 0.0044872 | O2-06 | 37.5715 |  | WTG Breakdown Maintenance | 9347 | 45.4368
3312 | 2024-12-31 | 2025 | 2024 | 2024-12-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.76736 | 0.76736 | 0.77153 | 0 | 0.1 | 0.1 | Rough Blade Parameter,Herk 10 and CM202 driver file software update work done than start WTG. | Close | 0.0038462 | O2-07 | 322.1063 |  | WTG Breakdown Maintenance | 7466 | 31.1083
3313 | 2024-12-31 | 2025 | 2024 | 2024-12-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.79653 | 0.79653 | 0.8 | 0 | 0.083333 | 0.083333 | Rough Blade Parameter,Herk 10 and CM202 driver file software update work done than start WTG. | Close | 0.0032051 | O2-24 | 62.85 |  | WTG Breakdown Maintenance | 11515 | 39.9826
3314 | 2024-12-31 | 2025 | 2024 | 2024-12-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.37778 | 0.37778 | 0.40694 | 0 | 0.7 | 0.7 | After Grid Jurk Check Data log after so Normal then apply soft reboot than Reset and start wtg | Close | 0.026923 | O2-06 | 329.5389 |  | WTG Unscheduled Maintenance | 9347 | 272.6208
3315 | 2024-12-31 | 2025 | 2024 | 2024-12-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.82361 | 0.82361 | 0.82778 | 0 | 0.1 | 0.1 | Rough Blade Parameter,Herk 10 and CM202 driver file software update work done than start WTG. | Close | 0.0038462 | O2-06 | 50.1472 |  | WTG Breakdown Maintenance | 9347 | 38.9458
3316 | 2024-12-31 | 2025 | 2024 | 2024-12-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.37778 | 0.37778 | 0.40625 | 0 | 0.68333 | 0.68333 | After Grid Jurk Check Data log after so Normal then apply soft reboot than Reset and start wtg | Close | 0.026282 | O2-11 | 353.7049 |  | WTG Unscheduled Maintenance | 7729 | 220.0618
3317 | 2024-12-31 | 2025 | 2024 | 2024-12-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.61042 | 0.61042 | 0.61528 | 0 | 0.11667 | 0.11667 | Rough Blade Parameter,Herk 10 and CM202 driver file software update work done than start WTG. | Close | 0.0044872 | O2-20 | 65.8056 |  | WTG Breakdown Maintenance | 7729 | 37.5715
3318 | 2024-12-31 | 2025 | 2024 | 2024-12-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.37778 | 0.37778 | 0.40625 | 0 | 0.68333 | 0.68333 | After Grid Jurk Check Data log after so Normal then apply soft reboot than Reset and start wtg | Close | 0.026282 | O2-01 | 344.7444 |  | WTG Unscheduled Maintenance | 11313 | 322.1063
3319 | 2024-12-31 | 2025 | 2024 | 2024-12-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.61736 | 0.61736 | 0.62292 | 0 | 0.13333 | 0.13333 | Rough Blade Parameter,Herk 10 and CM202 driver file software update work done than start WTG. | Close | 0.0051282 | O2-01 | 59.9556 |  | WTG Breakdown Maintenance | 11313 | 62.85
3320 | 2024-12-31 | 2025 | 2024 | 2024-12-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.37778 | 0.37778 | 0.40972 | 0 | 0.76667 | 0.76667 | After Grid Jurk Check Data log after so Normal then apply soft reboot than Reset and start wtg | Close | 0.029487 | O2-26 | 284.7361 |  | WTG Unscheduled Maintenance | 10316 | 329.5389
3321 | 2024-12-31 | 2025 | 2024 | 2024-12-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.62431 | 0.62431 | 0.62917 | 0 | 0.11667 | 0.11667 | Rough Blade Parameter,Herk 10 and CM202 driver file software update work done than start WTG. | Close | 0.0044872 | O2-26 | 38.3299 |  | WTG Breakdown Maintenance | 10316 | 50.1472
3322 | 2024-12-31 | 2025 | 2024 | 2024-12-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.37778 | 0.37778 | 0.40764 | 0 | 0.71667 | 0.71667 | After Grid Jurk Check Data log after so Normal then apply soft reboot than Reset and start wtg | Close | 0.027564 | O2-09 | 56.3333 |  | WTG Unscheduled Maintenance | 11845 | 353.7049
3323 | 2024-12-31 | 2025 | 2024 | 2024-12-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.62708 | 0.62708 | 0.63264 | 0 | 0.13333 | 0.13333 | Rough Blade Parameter,Herk 10 and CM202 driver file software update work done than start WTG. | Close | 0.0051282 | O2-09 | 297.3403 |  | WTG Breakdown Maintenance | 11845 | 65.8056
3324 | 2024-12-31 | 2025 | 2024 | 2024-12-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.40417 | 0.40417 | 0.43611 | 0 | 0.76667 | 0.76667 | After Grid Jurk Check Data log after so Normal then apply soft reboot than Reset and start wtg | Close | 0.029487 | O2-25 | 37.9583 |  | WTG Unscheduled Maintenance | 10792 | 344.7444
3325 | 2024-12-31 | 2025 | 2024 | 2024-12-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.64861 | 0.64861 | 0.65417 | 0 | 0.13333 | 0.13333 | Rough Blade Parameter,Herk 10 and CM202 driver file software update work done than start WTG. | Close | 0.0051282 | O2-25 | 27.2361 |  | WTG Breakdown Maintenance | 10792 | 59.9556
3326 | 2024-12-31 | 2025 | 2024 | 2024-12-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.40833 | 0.40833 | 0.44444 | 0 | 0.86667 | 0.86667 | After Grid Jurk Check Data log after so Normal then apply soft reboot than Reset and start wtg | Close | 0.033333 | O2-04 | 32.2042 |  | WTG Unscheduled Maintenance | 7885 | 284.7361
3327 | 2024-12-31 | 2025 | 2024 | 2024-12-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.65486 | 0.65486 | 0.65972 | 0 | 0.11667 | 0.11667 | Rough Blade Parameter,Herk 10 and CM202 driver file software update work done than start WTG. | Close | 0.0044872 | O2-04 | 38.3299 |  | WTG Breakdown Maintenance | 7885 | 38.3299
3328 | 2024-12-31 | 2025 | 2024 | 2024-12-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.79861 | 0.79861 | 0.80417 | 0 | 0.13333 | 0.13333 | Rough Blade Parameter,Herk 10 and CM202 driver file software update work done than start WTG. | Close | 0.0051282 | O2-03 | 56.3333 |  | WTG Breakdown Maintenance | 10140 | 56.3333
3329 | 2024-12-31 | 2025 | 2024 | 2024-12-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.37778 | 0.37778 | 0.41042 | 0 | 0.78333 | 0.78333 | After Grid Jurk Check Data log after so Normal then apply soft reboot than Reset and start wtg | Close | 0.030128 | O2-15 | 297.3403 |  | WTG Unscheduled Maintenance | 9110 | 297.3403
3330 | 2024-12-31 | 2025 | 2024 | 2024-12-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.64028 | 0.64028 | 0.64444 | 0 | 0.1 | 0.1 | Rough Blade Parameter,Herk 10 and CM202 driver file software update work done than start WTG. | Close | 0.0038462 | O2-15 | 37.9583 |  | WTG Breakdown Maintenance | 9110 | 37.9583
3331 | 2024-12-31 | 2025 | 2024 | 2024-12-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.80556 | 0.80556 | 0.80903 | 0 | 0.083333 | 0.083333 | Rough Blade Parameter,Herk 10 and CM202 driver file software update work done than start WTG. | Close | 0.0032051 | O2-14 | 27.2361 |  | WTG Breakdown Maintenance | 7844 | 27.2361
3332 | 2024-12-31 | 2025 | 2024 | 2024-12-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.80764 | 0.80764 | 0.81181 | 0 | 0.1 | 0.1 | Rough Blade Parameter,Herk 10 and CM202 driver file software update work done than start WTG. | Close | 0.0038462 | O2-11 | 32.2042 |  | WTG Breakdown Maintenance | 7729 | 32.2042
3333 | 2025-01-01 | 2025 | 2025 | 2025-01-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.74861 | 0.74861 | 0.79861 | 0 | 1.2 | 1.2 | After RFO signal coming than Start WTG. | Close | 0.046154 | O2-05 | 584.1 |  | WTG Unscheduled Maintenance | 11682 | 584.1
3334 | 2025-01-01 | 2025 | 2025 | 2025-01-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.74861 | 0.74861 | 0.8 | 0 | 1.2333 | 1.2333 | After RFO signal coming than Start WTG. | Close | 0.047436 | O2-23 | 478.6875 |  | WTG Unscheduled Maintenance | 9315 | 478.6875
3335 | 2025-01-01 | 2025 | 2025 | 2025-01-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.74861 | 0.74861 | 0.80069 | 0 | 1.25 | 1.25 | After RFO signal coming than Start WTG. | Close | 0.048077 | O2-22 | 612.6563 |  | WTG Unscheduled Maintenance | 11763 | 612.6563
3336 | 2025-01-01 | 2025 | 2025 | 2025-01-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.64861 | 0.64861 | 0.67986 | 0 | 0.75 | 0.75 | Check Data log and all perameter check then apply soft reboot than Reset and start wtg | Close | 0.028846 | O2-06 | 337.7812 |  | WTG Unscheduled Maintenance | 10809 | 337.7812
3337 | 2025-01-01 | 2025 | 2025 | 2025-01-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.74861 | 0.74861 | 0.80208 | 0 | 1.2833 | 1.2833 | After RFO signal coming than Start WTG. | Close | 0.049359 | O2-23 | 498.0938 |  | WTG Unscheduled Maintenance | 9315 | 498.0938
3338 | 2025-01-01 | 2025 | 2025 | 2025-01-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.74861 | 0.74861 | 0.80417 | 0 | 1.3333 | 1.3333 | After RFO signal coming than Start WTG. | Close | 0.051282 | O2-11 | 333.5 |  | WTG Unscheduled Maintenance | 6003 | 333.5
3339 | 2025-01-02 | 2025 | 2025 | 2025-01-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Project pending work | 0.43403 | 0.43403 | 0.72569 | 0 | 7 | 7 | O2-04 Jumper open for project pending work (section Isolator Fixing work) of O2 project team. | Close | 0.26923 | O2-07 | 1290.0417 |  | WTG Unscheduled Maintenance | 4423 | 1290.0417
3340 | 2025-01-02 | 2025 | 2025 | 2025-01-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.79167 | 0.79167 | 0.8375 | 0 | 1.1 | 1.1 | After Grid charge RFO signal coming than Start WTG. | Close | 0.042308 | O2-07 | 202.7208 |  | WTG Unscheduled Maintenance | 4423 | 202.7208
3341 | 2025-01-02 | 2025 | 2025 | 2025-01-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.79167 | 0.79167 | 1899-12-31 | 0 | 5 | 5 | After Feeder chagre WTG not connected to Scada so attend wtg and check error related ckt than found MC202 Module in Error mode than check all perameter than wip, | Close | 0.19231 | O2-18 | 813.5417 |  | WTG Unscheduled Maintenance | 3905 | 813.5417
3342 | 2025-01-02 | 2025 | 2025 | 2025-01-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Project pending work | 0.43403 | 0.43403 | 0.72569 | 0 | 7 | 7 | O2-07 Jumper open for project pending work (section Isolator Fixing work) of O2 project team. | Close | 0.26923 | O2-04 | 993.4167 |  | WTG Unscheduled Maintenance | 3406 | 993.4167
3343 | 2025-01-02 | 2025 | 2025 | 2025-01-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.5625 | 0.5625 | 0.70833 | 0 | 3.5 | 3.5 | Attend and check related ckt than check encoder supply connector and check 24 V supply connection loose so retight and reset than start WTG. | Close | 0.13462 | O2-03 | 570.6458 |  | WTG Unscheduled Maintenance | 3913 | 570.6458
3344 | 2025-01-02 | 2025 | 2025 | 2025-01-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.25694 | 0.25694 | 0.31458 | 0 | 1.3833 | 1.3833 | After grid resume time error occurred so apply soft reboot and reset and start WTG | Close | 0.053205 | O2-13 | 226.4632 |  | WTG Unscheduled Maintenance | 3929 | 226.4632
3345 | 2025-01-02 | 2025 | 2025 | 2025-01-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.56181 | 0.56181 | 1899-12-31 | 0 | 10.5167 | 10.5167 | Attend and check Error related ckt than found in DFIG panel Capacitor switching contactor,fuse and cable blown so material Arrengement wip WTG in stop Condition. | Close | 0.40449 | O2-10 | 1670.8354 |  | WTG Unscheduled Maintenance | 3813 | 1670.8354
3346 | 2025-01-02 | 2025 | 2025 | 2025-01-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Project pending work | 0.43403 | 0.43403 | 0.72569 | 0 | 7 | 7 | O2-19 Jumper open for project pending work (section Isolator Fixing work) of O2 project team. | Close | 0.26923 | O2-26 | 1218.2917 |  | WTG Unscheduled Maintenance | 4177 | 1218.2917
3347 | 2025-01-02 | 2025 | 2025 | 2025-01-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.79167 | 0.79167 | 0.82153 | 0 | 0.71667 | 0.71667 | Attend and Bottom Cooling system unit inspection with supplier than start WTG. | Close | 0.027564 | O2-26 | 124.7299 |  | WTG Breakdown Maintenance | 4177 | 124.7299
3348 | 2025-01-02 | 2025 | 2025 | 2025-01-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.5 | 0.5 | 0.6125 | 0 | 2.7 | 2.7 | WTG Stop for Project punch point closing work. | Close | 0.10385 | O2-21 | 676.8 |  | WTG Breakdown Maintenance | 6016 | 676.8
3349 | 2025-01-02 | 2025 | 2025 | 2025-01-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.46597 | 0.46597 | 0.53819 | 0 | 1.7333 | 1.7333 | Attend and Bottom Cooling system unit inspection with supplier than start WTG. | Close | 0.066667 | O2-15 | 299.9389 |  | WTG Breakdown Maintenance | 4153 | 299.9389
3350 | 2025-01-03 | 2025 | 2025 | 2025-01-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0.44236 | 0.44236 | 0.71389 | 0 | 6.5167 | 6.5167 | O2-06 Jumper open for project pending work (section Isolator Fixing work) of O2 project team. | Close | 0.25064 | O2-21 | 231.6132 |  | WTG Unscheduled Maintenance | 853 | 231.6132
3351 | 2025-01-03 | 2025 | 2025 | 2025-01-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.44236 | 0.44236 | 0.46736 | 0 | 0.6 | 0.6 | WTG Stop for convertor Inspection Work. | Close | 0.023077 | O2-04 | 14.975 |  | WTG Breakdown Maintenance | 599 | 14.975
3352 | 2025-01-03 | 2025 | 2025 | 2025-01-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 687 | Power failure pitch | Break down | 0.56389 | 0.56389 | 0.71389 | 0 | 3.6 | 3.6 | Attend and check error related ckt than found 400V mcb trip so check all connection related ckt also check Slip ring cable continuety and top to bottom power cable inspection work done than wip, | Close | 0.13846 | O2-04 | 89.85 |  | WTG Unscheduled Maintenance | 599 | 89.85
3353 | 2025-01-03 | 2025 | 2025 | 2025-01-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 687 | Power failure pitch | Break down | 0.73472 | 0.73472 | 0.77778 | 0 | 1.0333 | 1.0333 | After Grid resume error related ckt than found 400V mcb trip so check all connection related ckt also check Slip ring cable continuety and top to bottom power cable inspection work done than start WTG. | Close | 0.039744 | O2-04 | 25.7903 |  | WTG Unscheduled Maintenance | 599 | 25.7903
3354 | 2025-01-03 | 2025 | 2025 | 2025-01-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down | 0.1625 | 0.1625 | 0.16458 | 0 | 0.05 | 0.05 | Check Data log after so Normal then Reset and start wtg | Close | 0.0019231 | O2-14 | 1.1625 |  | WTG Unscheduled Maintenance | 558 | 1.1625
3355 | 2025-01-03 | 2025 | 2025 | 2025-01-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0 | 0 | 1899-12-31 | 0 | 24 | 24 | Attend and check Error related ckt than found in DFIG panel Capacitor switching contactor,fuse and cable blown so material Arrengement wip WTG in stop Condition. | Close | 0.92308 | O2-10 | 754 |  | WTG Unscheduled Maintenance | 754 | 754
3356 | 2025-01-03 | 2025 | 2025 | 2025-01-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.675 | 0.675 | 0.71389 | 0 | 0.93333 | 0.93333 | WTG Stop for convertor Inspection Work. | Close | 0.035897 | O2-21 | 33.1722 |  | WTG Breakdown Maintenance | 853 | 33.1722
3357 | 2025-01-03 | 2025 | 2025 | 2025-01-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0.44236 | 0.44236 | 0.71389 | 0 | 6.5167 | 6.5167 | O2-17 Jumper open for project pending work (section Isolator Fixing work) of O2 project team. | Close | 0.25064 | O2-22 | 202.5597 |  | WTG Unscheduled Maintenance | 746 | 202.5597
3358 | 2025-01-03 | 2025 | 2025 | 2025-01-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.73472 | 0.73472 | 0.80556 | 0 | 1.7 | 1.7 | After grid charge error occurred so check error related ckt than tight all connection than reset and start WTG. | Close | 0.065385 | O2-22 | 52.8417 |  | WTG Unscheduled Maintenance | 746 | 52.8417
3359 | 2025-01-03 | 2025 | 2025 | 2025-01-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0.44236 | 0.44236 | 0.71389 | 0 | 6.5167 | 6.5167 | O2-18 Jumper open for project pending work (section Isolator Fixing work) of O2 project team. | Close | 0.25064 | O2-06 | 281.0313 |  | WTG Unscheduled Maintenance | 1035 | 281.0313
3360 | 2025-01-03 | 2025 | 2025 | 2025-01-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.73472 | 0.73472 | 0.79861 | 0 | 1.5333 | 1.5333 | After Grid charge RFO signal coming than Start WTG. | Close | 0.058974 | O2-06 | 66.125 |  | WTG Unscheduled Maintenance | 1035 | 66.125
3361 | 2025-01-03 | 2025 | 2025 | 2025-01-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0.44236 | 0.44236 | 0.71389 | 0 | 6.5167 | 6.5167 | O2-21 Jumper open for project pending work (section Isolator Fixing work) of O2 project team. | Close | 0.25064 | O2-06 | 281.0313 |  | WTG Unscheduled Maintenance | 1035 | 281.0313
3362 | 2025-01-03 | 2025 | 2025 | 2025-01-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.73472 | 0.73472 | 0.81667 | 0 | 1.9667 | 1.9667 | After Grid charge RFO signal coming than Start WTG. | Close | 0.075641 | O2-06 | 84.8125 |  | WTG Unscheduled Maintenance | 1035 | 84.8125
3363 | 2025-01-03 | 2025 | 2025 | 2025-01-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Break down | 0.44236 | 0.44236 | 0.71389 | 0 | 6.5167 | 6.5167 | O2-22 Jumper open for project pending work (section Isolator Fixing work) of O2 project team. | Close | 0.25064 | O2-06 | 281.0313 |  | WTG Unscheduled Maintenance | 1035 | 281.0313
3364 | 2025-01-03 | 2025 | 2025 | 2025-01-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.73472 | 0.73472 | 0.82222 | 0 | 2.1 | 2.1 | After Grid charge RFO signal coming than Start WTG. | Close | 0.080769 | O2-06 | 90.5625 |  | WTG Unscheduled Maintenance | 1035 | 90.5625
3365 | 2025-01-03 | 2025 | 2025 | 2025-01-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.5 | 0.5 | 0.54653 | 0 | 1.1167 | 1.1167 | WTG Stop for Project punch point closing work. | Close | 0.042949 | O2-11 | 25.5437 |  | WTG Breakdown Maintenance | 549 | 25.5437
3366 | 2025-01-03 | 2025 | 2025 | 2025-01-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0 | 0 | 0.013889 | 0 | 0.33333 | 0.33333 | After Feeder chagre WTG not connected to Scada so attend wtg and check error related ckt than found MC202 Module in Error mode than check all perameter than Reinstall software than start WTG. | Close | 0.012821 | O2-21 | 11.8472 |  | WTG Unscheduled Maintenance | 853 | 11.8472
3367 | 2025-01-04 | 2025 | 2025 | 2025-01-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 687 | Power failure pitch | Major BD | 0.30764 | 0.30764 | 0.62153 | 0 | 7.5333 | 7.5333 | Attend and check ckt than found 400V Pitch MCB trip so check ckt related all connection than reset nad start WTG. | Close | 0.28974 | O2-04 | 1475.5917 |  | WTG Unscheduled Maintenance | 4701 | 1475.5917
3368 | 2025-01-04 | 2025 | 2025 | 2025-01-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 687 | Power failure pitch | Break down | 0.65903 | 0.65903 | 0.71806 | 0 | 1.4167 | 1.4167 | Attend and check ckt than found 400V Pitch MCB trip so check ckt related all connection than reset nad start WTG. | Close | 0.054487 | O2-04 | 277.4896 |  | WTG Unscheduled Maintenance | 4701 | 277.4896
3370 | 2025-01-04 | 2025 | 2025 | 2025-01-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.74306 | 0.74306 | 0.83333 | 0 | 2.1667 | 2.1667 | Attend and check ckt than found coolent low so top up coolent than reset and start WTG. | Close | 0.083333 | O2-26 | 306.3125 |  | WTG Unscheduled Maintenance | 3393 | 306.3125
3371 | 2025-01-04 | 2025 | 2025 | 2025-01-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3502 | Timeout grid error | Break down | 0.22917 | 0.22917 | 0.3625 | 0 | 3.2 | 3.2 | Attend and check error related ckt than voltage check of transformer than vcb trip and charge so found no any abnormality than start WTG. | Close | 0.12308 | O2-15 | 0 |  | WTG Unscheduled Maintenance | 0 | 0
3372 | 2025-01-04 | 2025 | 2025 | 2025-01-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Major BD | 0 | 0 | 1899-12-31 | 0 | 24 | 24 | Attend and check Error related ckt than found in DFIG panel Capacitor switching contactor,fuse and cable blown so material Arrengement wip WTG in stop Condition also today Slipring WTR 646 activity done by team. | Close | 0.92308 | O2-10 | 4930 |  | WTG Unscheduled Maintenance | 4930 | 4930
3373 | 2025-01-04 | 2025 | 2025 | 2025-01-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.72778 | 0.72778 | 0.76736 | 0 | 0.95 | 0.95 | After grid charge error occurred so check error related ckt than tight all connection than reset and start WTG. | Close | 0.036538 | O2-22 | 71.25 |  | WTG Unscheduled Maintenance | 1800 | 71.25
3374 | 2025-01-04 | 2025 | 2025 | 2025-01-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.72917 | 0.72917 | 0.77778 | 0 | 1.1667 | 1.1667 | After Grid charge RFO signal coming than Start WTG. | Close | 0.044872 | O2-06 | 113.3611 |  | WTG Unscheduled Maintenance | 2332 | 113.3611
3375 | 2025-01-04 | 2025 | 2025 | 2025-01-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.72917 | 0.72917 | 0.79792 | 0 | 1.65 | 1.65 | After Grid charge RFO signal coming than Start WTG. | Close | 0.063462 | O2-06 | 160.325 |  | WTG Unscheduled Maintenance | 2332 | 160.325
3376 | 2025-01-04 | 2025 | 2025 | 2025-01-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.72917 | 0.72917 | 0.79931 | 0 | 1.6833 | 1.6833 | After Grid charge RFO signal coming than Start WTG. | Close | 0.064744 | O2-06 | 163.5639 |  | WTG Unscheduled Maintenance | 2332 | 163.5639
3377 | 2025-01-04 | 2025 | 2025 | 2025-01-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.95625 | 0.95625 | 1899-12-31 | 0 | 1.05 | 1.05 | After grid error occurred so attend the wtg and check ckt than apply reboot than Wip, | Close | 0.040385 | O2-12 | 185.9375 |  | WTG Unscheduled Maintenance | 4250 | 185.9375
3378 | 2025-01-05 | 2025 | 2025 | 2025-01-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.53681 | 0.53681 | 0.60556 | 0 | 1.65 | 1.65 | After Grid resume Blade 3 Encoder value malfunction so hard Reboot controller than reset and start WTG. | Close | 0.063462 | O2-02 | 1410.475 |  | WTG Unscheduled Maintenance | 20516 | 1410.475
3379 | 2025-01-05 | 2025 | 2025 | 2025-01-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0 | 0 | 0.01875 | 0 | 0.45 | 0.45 | After Grid resume Blade 3 Encoder value malfunction so hard Reboot controller than reset and start WTG. | Close | 0.017308 | O2-23 | 197.25 |  | WTG Unscheduled Maintenance | 10520 | 197.25
3380 | 2025-01-05 | 2025 | 2025 | 2025-01-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0 | 0 | 0.50417 | 0 | 12.1 | 12.1 | Attend and replace 3 nos.500A fuse, Grid filter contector 7.1 & 7.2 with cable and as per technical team instruction we do first take test trial pricharge than charge grid filter than take test GSC two time take generation trial and that time yaw motor current high stop than wip, | Close | 0.46538 | O2-10 | 9084.075 |  | WTG Unscheduled Maintenance | 18018 | 9084.075
3381 | 2025-01-05 | 2025 | 2025 | 2025-01-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 6007 | Overload yaw motors group 1 | Break down | 0.53681 | 0.53681 | 0.65625 | 0 | 2.8667 | 2.8667 | after Grid resume we continue check yaw current high stop error check related ckt than check break and supply than found yaw Caliper was stuck so pressure down from hydrolic unit and air release than reset and start WTG. | Close | 0.11026 | O2-10 | 2152.15 |  | WTG Unscheduled Maintenance | 18018 | 2152.15
3382 | 2025-01-05 | 2025 | 2025 | 2025-01-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.80417 | 0.80417 | 0.90625 | 0 | 2.45 | 2.45 | After Grid resume Blade 3 Encoder value malfunction so hard Reboot controller than reset and start WTG. | Close | 0.094231 | O2-10 | 1839.3375 |  | WTG Unscheduled Maintenance | 18018 | 1839.3375
3383 | 2025-01-05 | 2025 | 2025 | 2025-01-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 610 | Max. temp. motor axis 3 | Break down | 0.41528 | 0.41528 | 0.49583 | 0 | 1.9333 | 1.9333 | After Grid resume check blade 3 motor temp sensor and it's value found normal so remove and refix connection then temp. occurred normal so reset and start WTG. | Close | 0.074359 | O2-06 | 1834.1694 |  | WTG Unscheduled Maintenance | 22769 | 1834.1694
3384 | 2025-01-06 | 2025 | 2025 | 2025-01-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Connectivity issue | 0.95069 | 0.95069 | 0.98958 | 0 | 0.93333 | 0.93333 | After grid resume turbine is disconnected so after connected then reset and start WTG. | Close | 0.035897 | O2-14 | 937.4944 |  | WTG Unscheduled Maintenance | 24107 | 937.4944
3385 | 2025-01-06 | 2025 | 2025 | 2025-01-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Connectivity issue | 0.95069 | 0.95069 | 0.98958 | 0 | 0.93333 | 0.93333 | After grid resume turbine is disconnected so after connected then reset and start WTG. | Close | 0.035897 | O2-13 | 923.0667 |  | WTG Unscheduled Maintenance | 23736 | 923.0667
3386 | 2025-01-06 | 2025 | 2025 | 2025-01-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Break down | 0.95069 | 0.95069 | 0.98611 | 0 | 0.85 | 0.85 | After grid resume turbineiS error and encoder engel is malfunctioning so apply hard reboot and reset and start WTG. | Close | 0.032692 | O2-13 | 840.65 |  | WTG Unscheduled Maintenance | 23736 | 840.65
3387 | 2025-01-06 | 2025 | 2025 | 2025-01-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Connectivity issue | 0.70833 | 0.70833 | 0.72778 | 0 | 0.46667 | 0.46667 | AFTER Feeder shutdown clear than wtg in Disconnected due to O2 21 VCB tripped so After charge than reset and start WTG. | Close | 0.017949 | O2-22 | 574.1167 |  | WTG Unscheduled Maintenance | 29526 | 574.1167
3388 | 2025-01-06 | 2025 | 2025 | 2025-01-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Connectivity issue | 0.70833 | 0.70833 | 0.75278 | 0 | 1.0667 | 1.0667 | AFTER Feeder shutdown clear than wtg in Disconnected due to O2 21 VCB tripped so After charge than reset and start WTG. | Close | 0.041026 | O2-17 | 1462.7556 |  | WTG Unscheduled Maintenance | 32912 | 1462.7556
3389 | 2025-01-06 | 2025 | 2025 | 2025-01-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Connectivity issue | 0.95069 | 0.95069 | 0.99999 | 0 | 1.1831 | 1.1831 | AFTER Feeder shutdown clear than wtg in Disconnected so VCB charge WIP. | Close | 0.045502 | O2-26 | 1140.712 |  | WTG Unscheduled Maintenance | 23141 | 1140.712
3390 | 2025-01-06 | 2025 | 2025 | 2025-01-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 551 | Pitch motor current too high | Break down | 0.18889 | 0.18889 | 0.22917 | 0 | 0.96667 | 0.96667 | attend and check related circuit than FC08 MCB was tripped so retight all connection and charge it and reset and start WTG. | Close | 0.037179 | O2-26 | 932.0681 |  | WTG Unscheduled Maintenance | 23141 | 932.0681
3391 | 2025-01-06 | 2025 | 2025 | 2025-01-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Connectivity issue | 0.95069 | 0.95069 | 0.99999 | 0 | 1.1831 | 1.1831 | Late start Due to connectivity is not availbale of this turbine | Close | 0.045502 | O2-25 | 598.8233 |  | WTG Unscheduled Maintenance | 12148 | 598.8233
3392 | 2025-01-06 | 2025 | 2025 | 2025-01-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Connectivity issue | 0.95069 | 0.95069 | 0.99999 | 0 | 1.1831 | 1.1831 | Late start Due to connectivity is not availbale of this turbine | Close | 0.045502 | O2-25 | 598.8233 |  | WTG Unscheduled Maintenance | 12148 | 598.8233
3393 | 2025-01-06 | 2025 | 2025 | 2025-01-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Connectivity issue | 0.95069 | 0.95069 | 0.99999 | 0 | 1.1831 | 1.1831 | Late start Due to connectivity is not availbale of this turbine | Close | 0.045502 | O2-26 | 598.8233 |  | WTG Unscheduled Maintenance | 12148 | 598.8233
3394 | 2025-01-06 | 2025 | 2025 | 2025-01-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Connectivity issue | 0.95069 | 0.95069 | 0.99999 | 0 | 1.1831 | 1.1831 | Late start Due to connectivity is not availbale of this turbine | Close | 0.045502 | O2-03 | 1355.9295 |  | WTG Unscheduled Maintenance | 27507 | 1355.9295
3395 | 2025-01-06 | 2025 | 2025 | 2025-01-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Connectivity issue | 0.95069 | 0.95069 | 0.99999 | 0 | 1.1831 | 1.1831 | Late start Due to connectivity is not availbale of this turbine | Close | 0.045502 | O2-26 | 1140.712 |  | WTG Unscheduled Maintenance | 23141 | 1140.712
3396 | 2025-01-06 | 2025 | 2025 | 2025-01-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Connectivity issue | 0.95069 | 0.95069 | 0.99999 | 0 | 1.1831 | 1.1831 | Late start Due to connectivity is not availbale of this turbine | Close | 0.045502 | O2-26 | 1140.712 |  | WTG Unscheduled Maintenance | 23141 | 1140.712
3397 | 2025-01-06 | 2025 | 2025 | 2025-01-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 7415 | PLC hardware error | Break down | 0.23611 | 0.23611 | 0.45278 | 0 | 5.2 | 5.2 | After Grid resume Blade 3 Encoder value malfunction so hard Reboot controller than reset and start WTG. | Close | 0.2 | O2-25 | 2632.0667 |  | WTG Unscheduled Maintenance | 12148 | 2632.0667
3398 | 2025-01-06 | 2025 | 2025 | 2025-01-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 7415 | PLC hardware error | Break down | 0.50139 | 0.50139 | 0.64514 | 0 | 3.45 | 3.45 | After Grid resume Blade 3 Encoder value malfunction so hard Reboot controller than reset and start WTG. | Close | 0.13269 | O2-25 | 1746.275 |  | WTG Unscheduled Maintenance | 12148 | 1746.275
3399 | 2025-01-06 | 2025 | 2025 | 2025-01-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 7415 | PLC hardware error | Break down | 0.67708 | 0.67708 | 0.7125 | 0 | 0.85 | 0.85 | After Grid resume Blade 3 Encoder value malfunction so hard Reboot controller than reset and start WTG. | Close | 0.032692 | O2-25 | 430.2417 |  | WTG Unscheduled Maintenance | 12148 | 430.2417
3400 | 2025-01-06 | 2025 | 2025 | 2025-01-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 7415 | PLC hardware error | Break down | 0.75694 | 0.75694 | 0.89167 | 0 | 3.2333 | 3.2333 | After Grid resume Blade 3 Encoder value malfunction so hard Reboot controller than reset and start WTG. | Close | 0.12436 | O2-25 | 1636.6056 |  | WTG Unscheduled Maintenance | 12148 | 1636.6056
3401 | 2025-01-06 | 2025 | 2025 | 2025-01-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 7415 | PLC hardware error | Break down | 0.89167 | 0.89167 | 0.99999 | 0 | 2.5997 | 2.5997 | After Grid resume Blade 3 Encoder value malfunction so hard Reboot controller than reset and start WTG. | Close | 0.099989 | O2-25 | 1315.8927 |  | WTG Unscheduled Maintenance | 12148 | 1315.8927
3402 | 2025-01-07 | 2025 | 2025 | 2025-01-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.72778 | 0.72778 | 0.73264 | 0 | 0.11667 | 0.11667 | Check Data log after reset and start wtg | Close | 0.0044872 | O2-25 | 156.8486 |  | WTG Unscheduled Maintenance | 32266 | 156.8486
3403 | 2025-01-07 | 2025 | 2025 | 2025-01-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.64792 | 0.64792 | 0.65208 | 0 | 0.1 | 0.1 | Check Data log after reset and start wtg | Close | 0.0038462 | O2-26 | 119.1375 |  | WTG Unscheduled Maintenance | 28593 | 119.1375
3404 | 2025-01-07 | 2025 | 2025 | 2025-01-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.068056 | 0.068056 | 0.09375 | 0 | 0.61667 | 0.61667 | Check error related circuit so found control cable cut by rabbit so troubleshooting work in progress | Close | 0.023718 | O2-09 | 758.8083 |  | WTG Unscheduled Maintenance | 29532 | 758.8083
3405 | 2025-01-07 | 2025 | 2025 | 2025-01-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Connectivity issue | 0.068056 | 0.068056 | 0.1125 | 0 | 1.0667 | 1.0667 | Late start Due to connectivity is not availbale of this turbine | Close | 0.041026 | O2-25 | 1434.0444 |  | WTG Unscheduled Maintenance | 32266 | 1434.0444
3406 | 2025-01-07 | 2025 | 2025 | 2025-01-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Connectivity issue | 0.068056 | 0.068056 | 0.11528 | 0 | 1.1333 | 1.1333 | Late start Due to connectivity is not availbale of this turbine | Close | 0.04359 | O2-03 | 1517.1083 |  | WTG Unscheduled Maintenance | 32127 | 1517.1083
3407 | 2025-01-07 | 2025 | 2025 | 2025-01-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.36389 | 0.36389 | 0.38333 | 0 | 0.46667 | 0.46667 | WTG Manual stop for BOP Reletead work after plan cancle so Reset and start wtg | Close | 0.017949 | O2-11 | 538.65 |  | WTG Breakdown Maintenance | 27702 | 538.65
3408 | 2025-01-07 | 2025 | 2025 | 2025-01-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.36389 | 0.36389 | 0.38333 | 0 | 0.46667 | 0.46667 | WTG Manual stop for BOP Reletead work after plan cancle so Reset and start wtg | Close | 0.017949 | O2-12 | 628.6194 |  | WTG Breakdown Maintenance | 32329 | 628.6194
3409 | 2025-01-07 | 2025 | 2025 | 2025-01-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.36389 | 0.36389 | 0.38333 | 0 | 0.46667 | 0.46667 | WTG Manual stop for BOP Reletead work after plan cancle so Reset and start wtg | Close | 0.017949 | O2-11 | 538.65 |  | WTG Breakdown Maintenance | 27702 | 538.65
3410 | 2025-01-07 | 2025 | 2025 | 2025-01-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.36389 | 0.36389 | 0.38333 | 0 | 0.46667 | 0.46667 | WTG Manual stop for BOP Reletead work after plan cancle so Reset and start wtg | Close | 0.017949 | O2-11 | 538.65 |  | WTG Breakdown Maintenance | 27702 | 538.65
3411 | 2025-01-07 | 2025 | 2025 | 2025-01-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.36389 | 0.36389 | 0.38333 | 0 | 0.46667 | 0.46667 | WTG Manual stop for BOP Reletead work after plan cancle so Reset and start wtg | Close | 0.017949 | O2-11 | 538.65 |  | WTG Breakdown Maintenance | 27702 | 538.65
3412 | 2025-01-07 | 2025 | 2025 | 2025-01-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.36389 | 0.36389 | 0.38333 | 0 | 0.46667 | 0.46667 | WTG Manual stop for BOP Reletead work after plan cancle so Reset and start wtg | Close | 0.017949 | O2-12 | 628.6194 |  | WTG Breakdown Maintenance | 32329 | 628.6194
3413 | 2025-01-07 | 2025 | 2025 | 2025-01-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.36389 | 0.36389 | 0.38333 | 0 | 0.46667 | 0.46667 | WTG Manual stop for BOP Reletead work after plan cancle so Reset and start wtg | Close | 0.017949 | O2-25 | 627.3944 |  | WTG Breakdown Maintenance | 32266 | 627.3944
3414 | 2025-01-07 | 2025 | 2025 | 2025-01-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 6007 | Overload yaw motors group 1 | Break down | 0.65625 | 0.65625 | 0.71528 | 0 | 1.4167 | 1.4167 | Attend and check Yaw brake caliper and Check Hydralic unit WIP | Close | 0.054487 | O2-12 | 1908.309 |  | WTG Unscheduled Maintenance | 32329 | 1908.309
3415 | 2025-01-07 | 2025 | 2025 | 2025-01-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 6007 | Overload yaw motors group 1 | Break down | 0.75 | 0.75 | 0.80347 | 0 | 1.2833 | 1.2833 | Attend and check Yaw brake caliper and Check Hydralic unit WIP | Close | 0.049359 | O2-12 | 1728.7035 |  | WTG Unscheduled Maintenance | 32329 | 1728.7035
3416 | 2025-01-07 | 2025 | 2025 | 2025-01-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 6007 | Overload yaw motors group 1 | Break down | 0.84028 | 0.84028 | 0.91667 | 0 | 1.8333 | 1.8333 | Attend and check Yaw brake caliper and Check Hydralic unit WIP | Close | 0.070513 | O2-12 | 2469.5764 |  | WTG Unscheduled Maintenance | 32329 | 2469.5764
3417 | 2025-01-07 | 2025 | 2025 | 2025-01-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 7415 | PLC hardware error | Break down | 0 | 0 | 0.0076389 | 0 | 0.18333 | 0.18333 | After Troubleshoot and found M1 , Busbar and DIO212 Are Faulty By Rat Cut cable on bottom cantrol panel so replace it take trail so ok then reset and start wtg | Close | 0.0070513 | O2-25 | 246.4764 |  | WTG Unscheduled Maintenance | 32266 | 246.4764
3418 | 2025-01-07 | 2025 | 2025 | 2025-01-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 7415 | PLC hardware error | Major BD | 0.068056 | 0.068056 | 0.65625 | 0 | 14.1167 | 14.1167 | After Troubleshoot and found M1 , Busbar and DIO212 Are Faulty By Rat Cut cable on bottom cantrol panel so replace it take trail so ok then reset and start wtg | Close | 0.54295 | O2-25 | 18978.6819 |  | WTG Unscheduled Maintenance | 32266 | 18978.6819 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
3419 | 2025-01-08 | 2025 | 2025 | 2025-01-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 7415 | PLC hardware error | Major BD | 0.38472 | 0.38472 | 0.44236 | 0 | 1.3833 | 1.3833 | After Feeder Attend and check error related ckt than apply hard reboot than reset and start WTG. | Close | 0.053205 | O2-26 | 943.9521 |  | WTG Unscheduled Maintenance | 16377 | 943.9521
3420 | 2025-01-08 | 2025 | 2025 | 2025-01-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Major BD | 0.54514 | 0.54514 | 0.79931 | 0 | 6.1 | 6.1 | After troubleshoot and found Hydrolic pressure not proper built up so clean 9.1 and 9.7 valve then reset and start WTG. | Close | 0.23462 | O2-07 | 6036.4583 |  | WTG Unscheduled Maintenance | 23750 | 6036.4583
3421 | 2025-01-08 | 2025 | 2025 | 2025-01-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.89444 | 0.89444 | 1899-12-31 | 0 | 2.5333 | 2.5333 | After feeder error occurred so attend and check error related ckt than wip, | Close | 0.097436 | O2-02 | 3033.2444 |  | WTG Unscheduled Maintenance | 28736 | 3033.2444
3422 | 2025-01-08 | 2025 | 2025 | 2025-01-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 6007 | Overload yaw motors group 1 | Break down | 0 | 0 | 0.097222 | 0 | 2.3333 | 2.3333 | Attend and wtg check hydraulic unit valve and pressure release after trail so ok then reset and start WTG. | Close | 0.089744 | O2-10 | 2306.0139 |  | WTG Unscheduled Maintenance | 23719 | 2306.0139
3423 | 2025-01-08 | 2025 | 2025 | 2025-01-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Major BD | 0.0625 | 0.0625 | 0.45833 | 0 | 9.5 | 9.5 | Attend and check after troubleshoot and found FA03 surge arrester FB cable found loose so tight it then reset and start WTG. | Close | 0.36538 | O2-26 | 6482.5625 |  | WTG Unscheduled Maintenance | 16377 | 6482.5625
3424 | 2025-01-08 | 2025 | 2025 | 2025-01-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.62847 | 0.62847 | 0.675 | 0 | 1.1167 | 1.1167 | Attend and check error related ckt than wip | Close | 0.042949 | O2-01 | 950.9347 |  | WTG Unscheduled Maintenance | 20438 | 950.9347
3425 | 2025-01-08 | 2025 | 2025 | 2025-01-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.69722 | 0.69722 | 0.73681 | 0 | 0.95 | 0.95 | Attend and check error related ckt than wip | Close | 0.036538 | O2-01 | 809.0042 |  | WTG Unscheduled Maintenance | 20438 | 809.0042
3426 | 2025-01-08 | 2025 | 2025 | 2025-01-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.76944 | 0.76944 | 0.7875 | 0 | 0.43333 | 0.43333 | Attend and check error related ckt than found K46 relay malfunctioning so interchange with K44 than retight all connection than reset and start WTG. | Close | 0.016667 | O2-01 | 369.0194 |  | WTG Unscheduled Maintenance | 20438 | 369.0194
3427 | 2025-01-09 | 2025 | 2025 | 2025-01-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 650 | Pitch controller communication error | Break down | 0.82778 | 0.82778 | 0.83125 | 0 | 0.083333 | 0.083333 | Check Data log after reset and start wtg | Close | 0.0032051 | O2-07 | 24.5278 |  | WTG Unscheduled Maintenance | 7064 | 24.5278
3428 | 2025-01-09 | 2025 | 2025 | 2025-01-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0 | 0 | 0.072917 | 0 | 1.75 | 1.75 | After Feeder resume error occurred so Attend and check error related ckt than apply hard reboot than reset and start WTG. | Close | 0.067308 | O2-02 | 935.375 |  | WTG Unscheduled Maintenance | 12828 | 935.375
3429 | 2025-01-09 | 2025 | 2025 | 2025-01-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.42153 | 0.42153 | 0.42847 | 0 | 0.16667 | 0.16667 | Software Update work done than start WTG. | Close | 0.0064103 | O2-21 | 132.1111 |  | WTG Breakdown Maintenance | 19024 | 132.1111
3430 | 2025-01-09 | 2025 | 2025 | 2025-01-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD | 0.47014 | 0.47014 | 1899-12-31 | 0 | 12.7167 | 12.7167 | WTG stop for Preventive work Slip ring Modification work WIP, | Close | 0.4891 | O2-04 | 6008.0951 |  | WTG Breakdown Maintenance | 11339 | 6008.0951
3431 | 2025-01-09 | 2025 | 2025 | 2025-01-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.50347 | 0.50347 | 0.54722 | 0 | 1.05 | 1.05 | Check Data log and all perameter check then apply soft reboot than Reset and start wtg | Close | 0.040385 | O2-26 | 476.9625 |  | WTG Unscheduled Maintenance | 10902 | 476.9625
3432 | 2025-01-09 | 2025 | 2025 | 2025-01-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.78542 | 0.78542 | 0.82778 | 0 | 1.0167 | 1.0167 | Attend and check error related ckt than wip, | Close | 0.039103 | O2-26 | 461.8208 |  | WTG Unscheduled Maintenance | 10902 | 461.8208
3433 | 2025-01-09 | 2025 | 2025 | 2025-01-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.91528 | 0.93125 | 0.99583 | 0.38333 | 1.55 | 1.9333 | After Grid resume found coolent pressure low so fill up than reset and start WTG. | Close | 0.074359 | O2-26 | 878.2167 |  | WTG Unscheduled Maintenance | 10902 | 878.2167
3434 | 2025-01-09 | 2025 | 2025 | 2025-01-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.52569 | 0.52569 | 0.55208 | 0 | 0.63333 | 0.63333 | Check Data log and all perameter check then apply soft reboot than Reset and start wtg | Close | 0.024359 | O2-12 | 367.5972 |  | WTG Unscheduled Maintenance | 13930 | 367.5972
3435 | 2025-01-10 | 2025 | 2025 | 2025-01-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.25 | 0.25 | 0.29861 | 0 | 1.1667 | 1.1667 | After Feeder resume error occurred so Attend and check error related ckt than apply hard reboot Of UPS than reset and start WTG. | Close | 0.044872 | O2-09 | 540.6042 |  | WTG Unscheduled Maintenance | 11121 | 540.6042
3436 | 2025-01-10 | 2025 | 2025 | 2025-01-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR | 0 | 0 | 0.62014 | 0 | 14.8833 | 14.8833 | WTG stop for Preventive work Slip ring Modification work Also Rep Error troublsooting work. | Close | 0.57244 | O2-05 | 5279.8625 |  | WTG Breakdown Maintenance | 8514 | 5279.8625
3437 | 2025-01-10 | 2025 | 2025 | 2025-01-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 3065 | Conv. emerg.off type F | Break down | 0.59375 | 0.59375 | 0.6 | 0 | 0.15 | 0.15 | Auto reset | Close | 0.0057692 | O2-24 | 75.0125 |  | WTG Unscheduled Maintenance | 12002 | 75.0125
3438 | 2025-01-10 | 2025 | 2025 | 2025-01-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 2828 | Timeout fault gen. lubrication | Break down | 0.57917 | 0.57917 | 0.58681 | 0 | 0.18333 | 0.18333 | Wtg In error so chcek related circuit and check IN sam than apply Manual Dio Apply than input comes ok than reset and start WTG. | Close | 0.0070513 | O2-08 | 85.7771 |  | WTG Unscheduled Maintenance | 11229 | 85.7771
3439 | 2025-01-10 | 2025 | 2025 | 2025-01-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.93889 | 0.93889 | 0.97569 | 0 | 0.88333 | 0.88333 | Attend and check than found Coolent low so refill and reset and start WTG. | Close | 0.033974 | O2-08 | 413.2896 |  | WTG Unscheduled Maintenance | 11229 | 413.2896
3440 | 2025-01-10 | 2025 | 2025 | 2025-01-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Connectivity issue | 0.25 | 0.25 | 0.275 | 0 | 0.6 | 0.6 | After Feeder resume error occurred so Attend and check error related ckt than apply hard reboot Of UPS than reset and start WTG.(Late start Due to connectivity issue after grid resume.) | Close | 0.023077 | O2-08 | 280.725 |  | WTG Unscheduled Maintenance | 11229 | 280.725
3441 | 2025-01-10 | 2025 | 2025 | 2025-01-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.56806 | 0.625 | 0.99999 | 1.3667 | 8.9997 | 10.3664 | Attend and check related circuit than check all Cards and K46 relay and also interchange K46 relau with another relay but error not solve so further troublshooting WIP with technical team and Suplier. | open | 0.39871 | O2-08 | 4850.1742 |  | WTG Unscheduled Maintenance | 11229 | 4850.1742
3442 | 2025-01-11 | 2025 | 2025 | 2025-01-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 2828 | Timeout fault gen. lubrication | Break down | 0.15069 | 0.31667 | 0.31667 | 3.9833 | 0 | 3.9833 | Attend and wtg check Releted circuit check 230 V Supply 24 v supply after Check Motor and check fuse so faulty fuse after replace then reset and start wtg | Close | 0.15321 | O2-03 | 1590.1799 |  | WTG Unscheduled Maintenance | 9581 | 1590.1799
3443 | 2025-01-11 | 2025 | 2025 | 2025-01-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Major BD | 0 | 0.625 | 0.625 | 15 | 0 | 15 | Attend and wtg Replace Hope wind Card replace and softwer upadeted after reset and start wtg | Close | 0.57692 | O2-01 | 6570.625 |  | WTG Unscheduled Maintenance | 10513 | 6570.625
3444 | 2025-01-11 | 2025 | 2025 | 2025-01-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.65208 | 0.84306 | 0.84306 | 4.5833 | 0 | 4.5833 | Attend wtg check releted circuit and perameter upadeting work wtg wip | Close | 0.17628 | O2-01 | 2007.691 |  | WTG Unscheduled Maintenance | 10513 | 2007.691
3445 | 2025-01-11 | 2025 | 2025 | 2025-01-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.87083 | 0.89167 | 0.89167 | 0.5 | 0 | 0.5 | Attend wtg check releted circuit and perameter upadeting work wtg wip | Close | 0.019231 | O2-01 | 219.0208 |  | WTG Unscheduled Maintenance | 10513 | 219.0208
3446 | 2025-01-11 | 2025 | 2025 | 2025-01-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.94444 | 1899-12-31 | 1899-12-31 | 1.3333 | 0 | 1.3333 | Attend wtg check releted circuit and perameter upadeting work wtg wip | open | 0.051282 | O2-01 | 584.0556 |  | WTG Unscheduled Maintenance | 10513 | 584.0556
3447 | 2025-01-11 | 2025 | 2025 | 2025-01-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.5 | 0.63333 | 0.63333 | 3.2 | 0 | 3.2 | WTG Prevantive work | Close | 0.12308 | O2-11 | 1145.7333 |  | WTG Breakdown Maintenance | 8593 | 1145.7333
3448 | 2025-01-12 | 2025 | 2025 | 2025-01-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.63125 | 0.63125 | 0.63542 | 0 | 0.1 | 0.1 | Check Data log after reset and start wtg | Close | 0.0038462 | O2-26 | 135.5083 |  | WTG Unscheduled Maintenance | 32522 | 135.5083
3449 | 2025-01-12 | 2025 | 2025 | 2025-01-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.89931 | 0.89931 | 1899-12-31 | 0 | 2.4167 | 2.4167 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.092949 | O2-15 | 3407.0972 |  | WTG Breakdown Maintenance | 33836 | 3407.0972
3450 | 2025-01-12 | 2025 | 2025 | 2025-01-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.65486 | 0.65486 | 0.65903 | 0 | 0.1 | 0.1 | Check Data log after reset and start wtg | Close | 0.0038462 | O2-21 | 101.9875 |  | WTG Unscheduled Maintenance | 24477 | 101.9875
3451 | 2025-01-12 | 2025 | 2025 | 2025-01-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.027778 | 0.027778 | 0.19583 | 0 | 4.0333 | 4.0333 | Turbine Stop for material cannibalize work than start WTG. | Close | 0.15513 | O2-11 | 5289.3806 |  | WTG Breakdown Maintenance | 31474 | 5289.3806
3452 | 2025-01-12 | 2025 | 2025 | 2025-01-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.45139 | 0.45139 | 0.46458 | 0 | 0.31667 | 0.31667 | Check Data log after reset and start wtg | Close | 0.012179 | O2-11 | 415.2819 |  | WTG Unscheduled Maintenance | 31474 | 415.2819
3453 | 2025-01-12 | 2025 | 2025 | 2025-01-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0 | 0 | 0.070139 | 0 | 1.6833 | 1.6833 | Attend and check error related ckt than replace MU1,GU1 and Interface card than update firmware and parameter then reset and start WTG. | Close | 0.064744 | O2-08 | 1793.8021 |  | WTG Unscheduled Maintenance | 25575 | 1793.8021
3454 | 2025-01-13 | 2025 | 2025 | 2025-01-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0 | 0 | 0.12847 | 0 | 3.0833 | 3.0833 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.11859 | O2-03 | 5159.059 |  | WTG Breakdown Maintenance | 40157 | 5159.059
3455 | 2025-01-13 | 2025 | 2025 | 2025-01-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0 | 0 | 0.05 | 0 | 1.2 | 1.2 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.046154 | O2-11 | 1652.5 |  | WTG Breakdown Maintenance | 33050 | 1652.5
3456 | 2025-01-13 | 2025 | 2025 | 2025-01-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 643 | Sim.angle E enc. <> act.angle 3 | Major BD | 0.079167 | 0.13681 | 0.74861 | 1.3833 | 14.6833 | 16.0667 | Attend check Error Releted ckt so found PPD Failure in blade 3 so attend it and replace with then after take trail time error occurred so troubleshooting it and found blade 2 flat 1.7 ohm resister failure then take trail again error occurred in blade so troubleshooting it and found silica stuck in blade 3 contact so rectify it and then take trail sucessfully it and then turbine put in to operation. | Close | 0.61795 | O2-26 | 28618.0806 |  | WTG Unscheduled Maintenance | 42749 | 28618.0806
3457 | 2025-01-13 | 2025 | 2025 | 2025-01-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.60208 | 0.60208 | 0.63056 | 0 | 0.68333 | 0.68333 | Check Data log after reset and start wtg | Close | 0.026282 | O2-01 | 1106.2313 |  | WTG Unscheduled Maintenance | 38853 | 1106.2313
3458 | 2025-01-13 | 2025 | 2025 | 2025-01-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.26042 | 0.27778 | 0.28819 | 0.41667 | 0.25 | 0.66667 | Attend and wtg apply Hard reebut then reset and start wtg | Close | 0.025641 | O2-12 | 1104 |  | WTG Unscheduled Maintenance | 39744 | 1104
3459 | 2025-01-13 | 2025 | 2025 | 2025-01-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 2828 | Timeout fault gen. lubrication | Break down | 0.49306 | 0.49306 | 0.49861 | 0 | 0.13333 | 0.13333 | Check Data log after reset and start wtg | Close | 0.0051282 | O2-03 | 223.0944 |  | WTG Unscheduled Maintenance | 40157 | 223.0944
3460 | 2025-01-13 | 2025 | 2025 | 2025-01-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.60208 | 0.60208 | 0.62986 | 0 | 0.66667 | 0.66667 | Check Data log after reset and start wtg | Close | 0.025641 | O2-11 | 918.0556 |  | WTG Unscheduled Maintenance | 33050 | 918.0556
3461 | 2025-01-13 | 2025 | 2025 | 2025-01-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.73125 | 0.73125 | 0.73542 | 0 | 0.1 | 0.1 | Check Data log after reset and start wtg | Close | 0.0038462 | O2-06 | 159.4583 |  | WTG Unscheduled Maintenance | 38270 | 159.4583
3462 | 2025-01-13 | 2025 | 2025 | 2025-01-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.65069 | 0.65069 | 0.65625 | 0 | 0.13333 | 0.13333 | Check Data log after reset and start wtg | Close | 0.0051282 | O2-06 | 212.6111 |  | WTG Unscheduled Maintenance | 38270 | 212.6111
3463 | 2025-01-13 | 2025 | 2025 | 2025-01-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.63403 | 0.63403 | 0.63819 | 0 | 0.1 | 0.1 | Check Data log after reset and start wtg | Close | 0.0038462 | O2-06 | 159.4583 |  | WTG Unscheduled Maintenance | 38270 | 159.4583
3464 | 2025-01-14 | 2025 | 2025 | 2025-01-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 1510 | Low gearbox oil pressure | Major BD | 0.62847 | 0.64583 | 1899-12-31 | 0.41667 | 8.5 | 8.9167 | attend and found gearbox pump motor coupler damage so now material arrangement work wip. | open | 0.34295 | O2-03 | 9744.059 |  | WTG Unscheduled Maintenance | 26227 | 9744.059
3465 | 2025-01-14 | 2025 | 2025 | 2025-01-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.43958 | 0.43958 | 0.45556 | 0 | 0.38333 | 0.38333 | Check Data log after reset and start wtg | Close | 0.014744 | O2-23 | 370.6035 |  | WTG Unscheduled Maintenance | 23203 | 370.6035
3466 | 2025-01-14 | 2025 | 2025 | 2025-01-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.58333 | 0.58333 | 0.73333 | 0 | 3.6 | 3.6 | Check Data log after reset and start wtg | Close | 0.13846 | O2-23 | 3480.45 |  | WTG Unscheduled Maintenance | 23203 | 3480.45
3467 | 2025-01-14 | 2025 | 2025 | 2025-01-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.74028 | 0.74028 | 0.775 | 0 | 0.83333 | 0.83333 | Check Data log after reset and start wtg | Close | 0.032051 | O2-23 | 805.6597 |  | WTG Unscheduled Maintenance | 23203 | 805.6597
3468 | 2025-01-14 | 2025 | 2025 | 2025-01-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.43958 | 0.43958 | 0.45486 | 0 | 0.36667 | 0.36667 | Check Data log after reset and start wtg | Close | 0.014103 | O2-26 | 455.5375 |  | WTG Unscheduled Maintenance | 29817 | 455.5375
3469 | 2025-01-14 | 2025 | 2025 | 2025-01-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.63403 | 0.63403 | 0.72847 | 0 | 2.2667 | 2.2667 | Check Data log after reset and start wtg | Close | 0.087179 | O2-26 | 2816.05 |  | WTG Unscheduled Maintenance | 29817 | 2816.05
3470 | 2025-01-14 | 2025 | 2025 | 2025-01-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.74028 | 0.74028 | 0.77292 | 0 | 0.78333 | 0.78333 | Check Data log after reset and start wtg | Close | 0.030128 | O2-26 | 973.1937 |  | WTG Unscheduled Maintenance | 29817 | 973.1937
3471 | 2025-01-15 | 2025 | 2025 | 2025-01-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 1510 | Low gearbox oil pressure | Break down | 0 | 0 | 0.92083 | 0 | 22.1 | 22.1 | Material arrangement for another site then attend and replace gearbox pump motor coupler then start WTG. | Close | 0.85 | O2-09 | 21723.3792 |  | WTG Unscheduled Maintenance | 23591 | 21723.3792
3472 | 2025-01-15 | 2025 | 2025 | 2025-01-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.35972 | 0.35972 | 0.36736 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & start WTG. | Close | 0.0070513 | O2-02 | 189.7118 |  | WTG Unscheduled Maintenance | 24835 | 189.7118
3473 | 2025-01-15 | 2025 | 2025 | 2025-01-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 2828 | Timeout fault gen. lubrication | Break down | 0.63889 | 0.63889 | 0.66944 | 0 | 0.73333 | 0.73333 | Checked related error data log then reset & start WTG. | Close | 0.028205 | O2-03 | 69.6667 |  | WTG Unscheduled Maintenance | 2280 | 69.6667
3474 | 2025-01-15 | 2025 | 2025 | 2025-01-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.25972 | 0.25972 | 0.26042 | 0 | 0.016667 | 0.016667 | Checked related error data log then reset & start WTG. | Close | 0.00064103 | O2-21 | 11.766 |  | WTG Unscheduled Maintenance | 16943 | 11.766
3475 | 2025-01-15 | 2025 | 2025 | 2025-01-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.26528 | 0.26528 | 0.26597 | 0 | 0.016667 | 0.016667 | Checked related error data log then reset & start WTG. | Close | 0.00064103 | O2-06 | 10.9236 |  | WTG Unscheduled Maintenance | 15730 | 10.9236
3476 | 2025-01-15 | 2025 | 2025 | 2025-01-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 7003 | Task runtime failure 10 ms | Break down | 0.020833 | 0.020833 | 0.024306 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & start WTG. | Close | 0.0032051 | O2-06 | 54.6181 |  | WTG Unscheduled Maintenance | 15730 | 54.6181
3477 | 2025-01-15 | 2025 | 2025 | 2025-01-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.67361 | 0.67361 | 0.67708 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & start WTG. | Close | 0.0032051 | O2-11 | 77.9097 |  | WTG Unscheduled Maintenance | 22438 | 77.9097
3478 | 2025-01-15 | 2025 | 2025 | 2025-01-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.67361 | 0.67361 | 0.67847 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & start WTG. | Close | 0.0044872 | O2-01 | 131.8528 |  | WTG Unscheduled Maintenance | 27124 | 131.8528
3479 | 2025-01-15 | 2025 | 2025 | 2025-01-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Others | 0.49583 | 0.49583 | 0.50903 | 0 | 0.31667 | 0.31667 | wtg manual stop for customer audit work | Close | 0.012179 | O2-01 | 357.8861 |  | WTG Breakdown Maintenance | 27124 | 357.8861
3480 | 2025-01-16 | 2025 | 2025 | 2025-01-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.047917 | 0.047917 | 0.11181 | 0 | 1.5333 | 1.5333 | Checked related error data log then reset & start WTG.(late reset due to internet connectivity not avalable on PSS and FLLTPRO is not working.) | Close | 0.058974 | O2-05 | 1882.3583 |  | WTG Unscheduled Maintenance | 29463 | 1882.3583
3481 | 2025-01-16 | 2025 | 2025 | 2025-01-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.92986 | 0.92986 | 0.93542 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & start WTG. | Close | 0.0051282 | O2-05 | 163.6833 |  | WTG Unscheduled Maintenance | 29463 | 163.6833
3482 | 2025-01-16 | 2025 | 2025 | 2025-01-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.95208 | 0.95208 | 0.95486 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & start WTG. | Close | 0.0025641 | O2-05 | 81.8417 |  | WTG Unscheduled Maintenance | 29463 | 81.8417
3483 | 2025-01-16 | 2025 | 2025 | 2025-01-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.96181 | 0.96181 | 1899-12-31 | 0 | 0.91667 | 0.91667 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.035256 | O2-05 | 1125.3229 |  | WTG Breakdown Maintenance | 29463 | 1125.3229
3484 | 2025-01-16 | 2025 | 2025 | 2025-01-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.19583 | 0.19583 | 0.20694 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & start WTG. | Close | 0.010256 | O2-02 | 416.4222 |  | WTG Unscheduled Maintenance | 37478 | 416.4222
3485 | 2025-01-16 | 2025 | 2025 | 2025-01-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 1065 | Drive train monitor level 1 | Break down | 0.22569 | 0.22569 | 0.22708 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & start WTG. | Close | 0.0012821 | O2-02 | 52.0528 |  | WTG Unscheduled Maintenance | 37478 | 52.0528
3486 | 2025-01-16 | 2025 | 2025 | 2025-01-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 1065 | Drive train monitor level 1 | Break down | 0.28194 | 0.28194 | 0.28681 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & start WTG. | Close | 0.0044872 | O2-02 | 182.1847 |  | WTG Unscheduled Maintenance | 37478 | 182.1847
3487 | 2025-01-16 | 2025 | 2025 | 2025-01-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Break down | 0.37708 | 0.37708 | 0.41181 | 0 | 0.83333 | 0.83333 | Checked related error data log then reset & start WTG. | Close | 0.032051 | O2-02 | 1301.3194 |  | WTG Unscheduled Maintenance | 37478 | 1301.3194
3488 | 2025-01-16 | 2025 | 2025 | 2025-01-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Break down | 0.62986 | 0.63194 | 0.65833 | 0.05 | 0.63333 | 0.68333 | attend and connection tight and all cable check after trail so ok then reset and start WTG. | Close | 0.026282 | O2-02 | 1067.0819 |  | WTG Unscheduled Maintenance | 37478 | 1067.0819
3489 | 2025-01-16 | 2025 | 2025 | 2025-01-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.14028 | 0.14028 | 0.20208 | 0 | 1.4833 | 1.4833 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.057051 | O2-03 | 2779.7667 |  | WTG Breakdown Maintenance | 44976 | 2779.7667
3490 | 2025-01-16 | 2025 | 2025 | 2025-01-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.28403 | 0.28403 | 0.35069 | 0 | 1.6 | 1.6 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.061538 | O2-03 | 2998.4 |  | WTG Breakdown Maintenance | 44976 | 2998.4
3491 | 2025-01-16 | 2025 | 2025 | 2025-01-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.97917 | 0.97917 | 1899-12-31 | 0 | 0.5 | 0.5 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.019231 | O2-03 | 937 |  | WTG Breakdown Maintenance | 44976 | 937
3492 | 2025-01-16 | 2025 | 2025 | 2025-01-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.59444 | 0.59444 | 0.62986 | 0 | 0.85 | 0.85 | wtg manual stop Genarator Bearing Inspection work. | Close | 0.032692 | O2-03 | 1592.9 |  | WTG Breakdown Maintenance | 44976 | 1592.9
3493 | 2025-01-16 | 2025 | 2025 | 2025-01-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.6 | 0.6 | 0.60208 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2-21 | 79.7271 |  | WTG Unscheduled Maintenance | 38269 | 79.7271
3494 | 2025-01-16 | 2025 | 2025 | 2025-01-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.59375 | 0.59375 | 0.6 | 0 | 0.15 | 0.15 | Checked related error data log then reset & start WTG. | Close | 0.0057692 | O2-22 | 243.7687 |  | WTG Unscheduled Maintenance | 39003 | 243.7687
3495 | 2025-01-16 | 2025 | 2025 | 2025-01-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.63611 | 0.63611 | 0.6375 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & start WTG. | Close | 0.0012821 | O2-06 | 50.9042 |  | WTG Unscheduled Maintenance | 36651 | 50.9042
3496 | 2025-01-16 | 2025 | 2025 | 2025-01-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.43958 | 0.43958 | 0.44375 | 0 | 0.1 | 0.1 | Checked related error data log then reset & start WTG. | Close | 0.0038462 | O2-06 | 152.7125 |  | WTG Unscheduled Maintenance | 36651 | 152.7125
3497 | 2025-01-16 | 2025 | 2025 | 2025-01-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.51806 | 0.51806 | 0.52014 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | O2-06 | 76.3562 |  | WTG Unscheduled Maintenance | 36651 | 76.3562
3498 | 2025-01-16 | 2025 | 2025 | 2025-01-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.97153 | 0.97153 | 0.97569 | 0 | 0.1 | 0.1 | Checked related error data log then reset & start WTG. | Close | 0.0038462 | O2-25 | 181.875 |  | WTG Unscheduled Maintenance | 43650 | 181.875
3499 | 2025-01-17 | 2025 | 2025 | 2025-01-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 1065 | Drive train monitor level 1 | Break down | 0.038889 | 0.038889 | 0.040278 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & start WTG. | Close | 0.0012821 | O2-26 | 45.6 |  | WTG Unscheduled Maintenance | 32832 | 45.6
3500 | 2025-01-17 | 2025 | 2025 | 2025-01-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.13264 | 0.13542 | 0.13958 | 0.066667 | 0.1 | 0.16667 | attend Wtg in error so Checked related error data log then apply hard reboot then reset & start the WTG | Close | 0.0064103 | O2-26 | 228 |  | WTG Unscheduled Maintenance | 32832 | 228
3501 | 2025-01-17 | 2025 | 2025 | 2025-01-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0 | 0 | 0.36042 | 0 | 8.65 | 8.65 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.33269 | O2-05 | 11479.9917 |  | WTG Breakdown Maintenance | 31852 | 11479.9917
3502 | 2025-01-17 | 2025 | 2025 | 2025-01-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0 | 0 | 0.22569 | 0 | 5.4167 | 5.4167 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.20833 | O2-03 | 6589.375 |  | WTG Breakdown Maintenance | 29196 | 6589.375
3503 | 2025-01-17 | 2025 | 2025 | 2025-01-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.22708 | 0.22708 | 0.29583 | 0 | 1.65 | 1.65 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.063462 | O2-25 | 1819.3313 |  | WTG Breakdown Maintenance | 26463 | 1819.3313
3504 | 2025-01-17 | 2025 | 2025 | 2025-01-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.31458 | 0.31458 | 0.33681 | 0 | 0.53333 | 0.53333 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.020513 | O2-25 | 588.0667 |  | WTG Breakdown Maintenance | 26463 | 588.0667
3505 | 2025-01-18 | 2025 | 2025 | 2025-01-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR | 0.49028 | 0.49028 | 0.51042 | 0 | 0.48333 | 0.48333 | WTG manual stop for WTR 630 work | Close | 0.01859 | O2-26 | 178.0882 |  | WTG Breakdown Maintenance | 8843 | 178.0882
3506 | 2025-01-18 | 2025 | 2025 | 2025-01-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 88 | Outs.temp. nacelle implaus. | Break down | 0.60139 | 0.60139 | 0.62014 | 0 | 0.45 | 0.45 | Checked related error data log then reset & start WTG. | Close | 0.017308 | O2-26 | 165.8063 |  | WTG Unscheduled Maintenance | 8843 | 165.8063
3507 | 2025-01-18 | 2025 | 2025 | 2025-01-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR | 0.51806 | 0.51806 | 0.53819 | 0 | 0.48333 | 0.48333 | WTG manual stop for WTR 630 work | Close | 0.01859 | O2-01 | 217.1375 |  | WTG Breakdown Maintenance | 10782 | 217.1375
3508 | 2025-01-18 | 2025 | 2025 | 2025-01-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.57639 | 0.57639 | 0.65972 | 0 | 2 | 2 | WTG manual stop for SCADA restoration work | Close | 0.076923 | O2-24 | 698.1667 |  | WTG Breakdown Maintenance | 8378 | 698.1667
3509 | 2025-01-18 | 2025 | 2025 | 2025-01-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 72 | Outdoor temperature high | Break down | 0.61458 | 0.61458 | 0.74167 | 0 | 3.05 | 3.05 | attend and check all releted circuit and found loose connection on sensor cable so tight it then start WTG. | Close | 0.11731 | O2-11 | 886.5333 |  | WTG Unscheduled Maintenance | 6976 | 886.5333
3510 | 2025-01-18 | 2025 | 2025 | 2025-01-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 7415 | PLC hardware error | Break down | 0.76736 | 0.76736 | 0.83681 | 0 | 1.6667 | 1.6667 | after grid resume M1 24v supply is come so apply hard reboot then reset and start WTG. | Close | 0.064103 | O2-22 | 767.1528 |  | WTG Unscheduled Maintenance | 11047 | 767.1528
3511 | 2025-01-19 | 2025 | 2025 | 2025-01-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.39375 | 0.39375 | 0.51042 | 0 | 2.8 | 2.8 | WTG manual stop for sofware error rectifications work. | Close | 0.10769 | O2-24 | 468.7667 |  | WTG Breakdown Maintenance | 4018 | 468.7667
3512 | 2025-01-19 | 2025 | 2025 | 2025-01-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Blade cleaning work | 0.47222 | 0.47222 | 0.86736 | 0 | 9.4833 | 9.4833 | WTG manual stop for blade cleaning work. | Close | 0.36474 | O2-20 | 1803.4139 |  | WTG Breakdown Maintenance | 4564 | 1803.4139
3513 | 2025-01-19 | 2025 | 2025 | 2025-01-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.625 | 0.625 | 0.64236 | 0 | 0.41667 | 0.41667 | WTG manual stop for repeated error inspection work and found outdoor temp sensor faulty so replace it and start wtg. | Close | 0.016026 | O2-26 | 104.3229 |  | WTG Breakdown Maintenance | 6009 | 104.3229
3513 | 2025-01-19 | 2025 | 2025 | 2025-01-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 7415 | PLC hardware error | Break down | 0.39375 | 0.39375 | 0.41389 | 0 | 0.48333 | 0.48333 | after grid resume M1 24v supply is come so apply hard reboot then reset and start WTG. | Close | 0.01859 | O2-22 | 130.0167 |  | WTG Unscheduled Maintenance | 6456 | 130.0167
3514 | 2025-01-20 | 2025 | 2025 | 2025-01-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.65972 | 0.65972 | 0.71111 | 0 | 1.2333 | 1.2333 | After Grid charge RFO signal coming than Start WTG. | Close | 0.047436 | O2-07 | 107.7625 |  | WTG Unscheduled Maintenance | 2097 | 107.7625
3515 | 2025-01-20 | 2025 | 2025 | 2025-01-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Blade cleaning work | 0.4375 | 0.4375 | 0.76389 | 0 | 7.8333 | 7.8333 | WTG manual stop for blade cleaning work. | Close | 0.30128 | O2-15 | 556.4931 |  | WTG Breakdown Maintenance | 1705 | 556.4931
3516 | 2025-01-20 | 2025 | 2025 | 2025-01-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.425 | 0.425 | 0.73264 | 0 | 7.3833 | 7.3833 | Wtg stop for 1st month Maintenance work. | Close | 0.28397 | O2-22 | 840.7771 |  | WTG Scheduled Maintenance | 2733 | 840.7771
3517 | 2025-01-20 | 2025 | 2025 | 2025-01-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.48472 | 0.48472 | 0.50347 | 0 | 0.45 | 0.45 | WTG manual stop for WTR 630 work | Close | 0.017308 | O2-24 | 59.175 |  | WTG Breakdown Maintenance | 3156 | 59.175
3518 | 2025-01-20 | 2025 | 2025 | 2025-01-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 2828 | Timeout fault gen. lubrication | Break down | 0.022917 | 0.022917 | 0.034028 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & start WTG. | Close | 0.010256 | O2-03 | 19.3444 |  | WTG Unscheduled Maintenance | 1741 | 19.3444 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
3518 | 2025-01-21 | 2025 | 2025 | 2025-01-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.42361 | 0.42361 | 0.79097 | 0 | 8.8167 | 8.8167 | Wtg stop for 1st month Maintenance work. | Close | 0.3391 | O2-22 | 1805.2125 |  | WTG Breakdown Maintenance | 4914 | 1805.2125
3518 | 2025-01-21 | 2025 | 2025 | 2025-01-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.47708 | 0.47708 | 0.51597 | 0 | 0.93333 | 0.93333 | WTG manual stop for WTR 630 work | Close | 0.035897 | O2-12 | 186.9778 |  | WTG Breakdown Maintenance | 4808 | 186.9778
3518 | 2025-01-21 | 2025 | 2025 | 2025-01-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.45139 | 0.45139 | 0.47014 | 0 | 0.45 | 0.45 | WTG manual stop for WTR 630 work | Close | 0.017308 | O2-12 | 90.15 |  | WTG Breakdown Maintenance | 4808 | 90.15
3518 | 2025-01-21 | 2025 | 2025 | 2025-01-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.50625 | 0.50625 | 0.53125 | 0 | 0.6 | 0.6 | WTG manual stop for WTR 630 work | Close | 0.023077 | O2-06 | 82.425 |  | WTG Breakdown Maintenance | 3297 | 82.425
3518 | 2025-01-21 | 2025 | 2025 | 2025-01-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Blade cleaning work | 0.42361 | 0.42361 | 0.89722 | 0 | 11.3667 | 11.3667 | WTG manual stop for blade cleaning work. | Close | 0.43718 | O2-24 | 3183.1403 |  | WTG Breakdown Maintenance | 6721 | 3183.1403
3518 | 2025-01-22 | 2025 | 2025 | 2025-01-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD | 0.46042 | 0.46042 | 1899-12-31 | 0 | 12.95 | 12.95 | WTG manual stop for generator bearing inspection work done and confirm by engineering team and now generator bearing replacement work WIP. | open | 0.49808 | O2-03 | 5896.5667 |  | WTG Breakdown Maintenance | 10928 | 5896.5667
3518 | 2025-01-22 | 2025 | 2025 | 2025-01-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Blade cleaning work | 0.44653 | 0.44653 | 0.76042 | 0 | 7.5333 | 7.5333 | WTG manual stop for blade cleaning work. | Close | 0.28974 | O2-21 | 3094.0028 |  | WTG Breakdown Maintenance | 9857 | 3094.0028
3518 | 2025-01-22 | 2025 | 2025 | 2025-01-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down | 0.78125 | 0.875 | 0.98958 | 2.25 | 2.75 | 5 | attend found hydraulic oil leval is low so top up oil and apply manual DO and release air then all condition is normal then start WTG. | Close | 0.19231 | O2-22 | 2086.0417 |  | WTG Unscheduled Maintenance | 10013 | 2086.0417
3518 | 2025-01-22 | 2025 | 2025 | 2025-01-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down | 0.039583 | 0.039583 | 0.053472 | 0 | 0.33333 | 0.33333 | Checked related error data log apply manual DO hydtaulic unit and flushing mode then reset and start WTG. | Close | 0.012821 | O2-11 | 155.6806 |  | WTG Unscheduled Maintenance | 11209 | 155.6806
3518 | 2025-01-22 | 2025 | 2025 | 2025-01-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.73403 | 0.73403 | 0.75069 | 0 | 0.4 | 0.4 | Checked related error data log then reset & start WTG. | Close | 0.015385 | O2-24 | 354.3 |  | WTG Unscheduled Maintenance | 21258 | 354.3
3519 | 2025-01-23 | 2025 | 2025 | 2025-01-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.45208 | 0.45208 | 0.48333 | 0 | 0.75 | 0.75 | WTG manual stop for WTR 655 work wip | Close | 0.028846 | O2-26 | 194.1562 |  | WTG Breakdown Maintenance | 6213 | 194.1562
3520 | 2025-01-23 | 2025 | 2025 | 2025-01-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.55347 | 0.55347 | 0.56806 | 0 | 0.35 | 0.35 | WTG manual stop for WTR 655 work | Close | 0.013462 | O2-26 | 90.6062 |  | WTG Breakdown Maintenance | 6213 | 90.6062
3521 | 2025-01-23 | 2025 | 2025 | 2025-01-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD | 0 | 0.35417 | 0.48333 | 8.5 | 3.1 | 11.6 | WTG manual stop for generator bearing replacement work WIP | Close | 0.44615 | O2-03 | 3174.5333 |  | WTG Breakdown Maintenance | 6568 | 3174.5333
3522 | 2025-01-23 | 2025 | 2025 | 2025-01-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD | 0.55347 | 0.55347 | 0.73611 | 0 | 4.3833 | 4.3833 | WTG manual stop for generator bearing replacement work done then start wtg | Close | 0.16859 | O2-03 | 1199.5722 |  | WTG Breakdown Maintenance | 6568 | 1199.5722
3523 | 2025-01-23 | 2025 | 2025 | 2025-01-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.55347 | 0.55347 | 0.62431 | 0 | 1.7 | 1.7 | After Grid resume Blade 3 Encoder value malfunction so hard Reboot controller than reset and start WTG. | Close | 0.065385 | O2-09 | 468.5625 |  | WTG Unscheduled Maintenance | 6615 | 468.5625
3524 | 2025-01-23 | 2025 | 2025 | 2025-01-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down | 0.42361 | 0.44792 | 0.48333 | 0.58333 | 0.85 | 1.4333 | attend found hydraulic oil 9.1 valv is faulty so do WTR for hydraulic unit WIP | Close | 0.055128 | O2-14 | 260.5083 |  | WTG Unscheduled Maintenance | 4362 | 260.5083
3525 | 2025-01-23 | 2025 | 2025 | 2025-01-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down | 0.55347 | 0.55347 | 0.67292 | 0 | 2.8667 | 2.8667 | attend found hydraulic oil 9.1 valv is faulty so do WTR for hydraulic unit then start wtg. | Close | 0.11026 | O2-14 | 521.0167 |  | WTG Unscheduled Maintenance | 4362 | 521.0167
3526 | 2025-01-23 | 2025 | 2025 | 2025-01-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.92847 | 0.92847 | 0.94931 | 0 | 0.5 | 0.5 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.019231 | O2-11 | 103.3542 |  | WTG Breakdown Maintenance | 4961 | 103.3542
3527 | 2025-01-23 | 2025 | 2025 | 2025-01-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.97222 | 0.97222 | 0.98611 | 0 | 0.33333 | 0.33333 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.012821 | O2-11 | 68.9028 |  | WTG Breakdown Maintenance | 4961 | 68.9028
3528 | 2025-01-23 | 2025 | 2025 | 2025-01-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3390 | Cool.sys. pump man.oper. | Break down | 0.97222 | 0.99931 | 0.99999 | 0.65 | 0.016389 | 0.66639 | after grid resume error is occurs so wtg rectfications work WIP | open | 0.02563 | O2-25 | 179.6196 |  | WTG Unscheduled Maintenance | 6469 | 179.6196
3529 | 2025-01-24 | 2025 | 2025 | 2025-01-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.022222 | 0.022222 | 0.033333 | 0 | 0.26667 | 0.26667 | after grid resume Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.010256 | O2-09 | 478.0778 |  | WTG Unscheduled Maintenance | 43027 | 478.0778
3530 | 2025-01-24 | 2025 | 2025 | 2025-01-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.0625 | 0.0625 | 0.18889 | 0 | 3.0333 | 3.0333 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.11667 | O2-11 | 4379.8806 |  | WTG Breakdown Maintenance | 34654 | 4379.8806
3531 | 2025-01-24 | 2025 | 2025 | 2025-01-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.022222 | 0.022222 | 0.055556 | 0 | 0.8 | 0.8 | after grid resume Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.030769 | O2-12 | 1192.3 |  | WTG Unscheduled Maintenance | 35769 | 1192.3
3532 | 2025-01-24 | 2025 | 2025 | 2025-01-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3390 | Cool.sys. pump man.oper. | Break down | 0.022222 | 0.010417 | 0.0625 | -0.28333 | 1.25 | 0.96667 | Attend and found MCB trip for TBC panel pump motot so check all releted ckt found no any abnormality so charge MCB and start WTG. | Close | 0.037179 | O2-25 | 1465.3458 |  | WTG Unscheduled Maintenance | 36381 | 1465.3458
3533 | 2025-01-24 | 2025 | 2025 | 2025-01-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.0625 | 0.0625 | 0.09375 | 0 | 0.75 | 0.75 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.028846 | O2-25 | 1136.9062 |  | WTG Breakdown Maintenance | 36381 | 1136.9062
3534 | 2025-01-25 | 2025 | 2025 | 2025-01-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.40139 | 0.40139 | 0.44792 | 0 | 1.1167 | 1.1167 | after grid resume base box not ready for operation error so attend wtg and hard reboot then reset & start the WTG. | Close | 0.042949 | O2-22 | 1132.5792 |  | WTG Unscheduled Maintenance | 24342 | 1132.5792
3535 | 2025-01-25 | 2025 | 2025 | 2025-01-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.40139 | 0.40139 | 0.41458 | 0 | 0.31667 | 0.31667 | after grid resume Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.012179 | O2-21 | 301.7174 |  | WTG Unscheduled Maintenance | 22867 | 301.7174
3536 | 2025-01-25 | 2025 | 2025 | 2025-01-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Blade cleaning work | 0.43056 | 0.43056 | 0.65278 | 0 | 5.3333 | 5.3333 | WTG manual stop for blade cleaning work. | Close | 0.20513 | O2-10 | 6716.8889 |  | WTG Breakdown Maintenance | 30226 | 6716.8889
3537 | 2025-01-25 | 2025 | 2025 | 2025-01-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Blade cleaning work | 0.67986 | 0.67986 | 0.8625 | 0 | 4.3833 | 4.3833 | WTG manual stop for blade cleaning work. | Close | 0.16859 | O2-10 | 5520.4431 |  | WTG Breakdown Maintenance | 30226 | 5520.4431
3538 | 2025-01-25 | 2025 | 2025 | 2025-01-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR | 0.46111 | 0.46111 | 0.47847 | 0 | 0.41667 | 0.41667 | WTG manual stop for WTR 630 work | Close | 0.016026 | O2-12 | 336.9097 |  | WTG Breakdown Maintenance | 19406 | 336.9097
3539 | 2025-01-25 | 2025 | 2025 | 2025-01-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.46181 | 0.46181 | 0.64167 | 0 | 4.3167 | 4.3167 | WTG manual stop for lift reparing work | Close | 0.16603 | O2-26 | 3864.1361 |  | WTG Breakdown Maintenance | 21484 | 3864.1361
3540 | 2025-01-25 | 2025 | 2025 | 2025-01-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Connectivity issue | 0.40139 | 0.40139 | 0.41806 | 0 | 0.4 | 0.4 | after grid resume Checked related error data log apply soft reboot then reset & start the WTG. | Close | 0.015385 | O2-20 | 395.6667 |  | WTG Unscheduled Maintenance | 23740 | 395.6667
3541 | 2025-01-25 | 2025 | 2025 | 2025-01-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Connectivity issue | 0.024306 | 0.024306 | 0.038194 | 0 | 0.33333 | 0.33333 | after grid resume feeder-1 all wtg are discannected from scada because O2-13 and O2-14 VCB trip. | Close | 0.012821 | O2-26 | 298.3889 |  | WTG Unscheduled Maintenance | 21484 | 298.3889
3542 | 2025-01-25 | 2025 | 2025 | 2025-01-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Connectivity issue | 0.024306 | 0.024306 | 0.038194 | 0 | 0.33333 | 0.33333 | after grid resume feeder-1 all wtg are discannected from scada because O2-13 and O2-14 VCB trip. | Close | 0.012821 | O2-09 | 305.7778 |  | WTG Unscheduled Maintenance | 22016 | 305.7778
3543 | 2025-01-25 | 2025 | 2025 | 2025-01-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Connectivity issue | 0.024306 | 0.024306 | 0.038194 | 0 | 0.33333 | 0.33333 | after grid resume feeder-1 all wtg are discannected from scada because O2-13 and O2-14 VCB trip. | Close | 0.012821 | O2-02 | 344.9028 |  | WTG Unscheduled Maintenance | 24833 | 344.9028
3544 | 2025-01-25 | 2025 | 2025 | 2025-01-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Connectivity issue | 0.024306 | 0.024306 | 0.038194 | 0 | 0.33333 | 0.33333 | after grid resume feeder-1 all wtg are discannected from scada because O2-13 and O2-14 VCB trip. | Close | 0.012821 | O2-26 | 298.3889 |  | WTG Unscheduled Maintenance | 21484 | 298.3889
3545 | 2025-01-25 | 2025 | 2025 | 2025-01-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Connectivity issue | 0.024306 | 0.024306 | 0.038194 | 0 | 0.33333 | 0.33333 | after grid resume feeder-1 all wtg are discannected from scada because O2-13 and O2-14 VCB trip. | Close | 0.012821 | O2-15 | 259.25 |  | WTG Unscheduled Maintenance | 18666 | 259.25
3546 | 2025-01-25 | 2025 | 2025 | 2025-01-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Connectivity issue | 0.024306 | 0.024306 | 0.038194 | 0 | 0.33333 | 0.33333 | after grid resume feeder-1 all wtg are discannected from scada because O2-13 and O2-14 VCB trip. | Close | 0.012821 | O2-14 | 222.3056 |  | WTG Unscheduled Maintenance | 16006 | 222.3056
3547 | 2025-01-25 | 2025 | 2025 | 2025-01-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Connectivity issue | 0.024306 | 0.024306 | 0.038194 | 0 | 0.33333 | 0.33333 | after grid resume feeder-1 all wtg are discannected from scada because O2-13 and O2-14 VCB trip. | Close | 0.012821 | O2-01 | 270.2639 |  | WTG Unscheduled Maintenance | 19459 | 270.2639
3548 | 2025-01-26 | 2025 | 2025 | 2025-01-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.39653 | 0.39653 | 0.39861 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2-02 | 25.6417 |  | WTG Unscheduled Maintenance | 12308 | 25.6417
3549 | 2025-01-26 | 2025 | 2025 | 2025-01-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Blade cleaning work | 0.44583 | 0.44583 | 0.80347 | 0 | 8.5833 | 8.5833 | WTG manual stop for blade cleaning work. | Close | 0.33013 | O2-14 | 3033.8507 |  | WTG Breakdown Maintenance | 8483 | 3033.8507
3550 | 2025-01-26 | 2025 | 2025 | 2025-01-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.60139 | 0.60139 | 0.61319 | 0 | 0.28333 | 0.28333 | Checked related error data log then reset & start WTG. | Close | 0.010897 | O2-12 | 113.0618 |  | WTG Unscheduled Maintenance | 9577 | 113.0618
3551 | 2025-01-26 | 2025 | 2025 | 2025-01-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.77014 | 0.79167 | 0.84375 | 0.51667 | 1.25 | 1.7667 | attend and check and found loose connection in FA001 so tight it and start WTG | Close | 0.067949 | O2-22 | 576.1542 |  | WTG Unscheduled Maintenance | 7827 | 576.1542
3552 | 2025-01-26 | 2025 | 2025 | 2025-01-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.42361 | 0.42361 | 0.43403 | 0 | 0.25 | 0.25 | Checked related error data log then reset & start WTG. | Close | 0.0096154 | O2-24 | 177.0938 |  | WTG Unscheduled Maintenance | 17001 | 177.0938
3553 | 2025-01-26 | 2025 | 2025 | 2025-01-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.84931 | 0.84931 | 0.85347 | 0 | 0.1 | 0.1 | Checked related error data log then reset & start WTG. | Close | 0.0038462 | O2-24 | 70.8375 |  | WTG Unscheduled Maintenance | 17001 | 70.8375
3554 | 2025-01-27 | 2025 | 2025 | 2025-01-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Break down | 0.38889 | 0.38889 | 0.40208 | 0 | 0.31667 | 0.31667 | Checked related error data log then reset & start WTG. | Close | 0.012179 | O2-26 | 54.4403 |  | WTG Unscheduled Maintenance | 4126 | 54.4403
3555 | 2025-01-27 | 2025 | 2025 | 2025-01-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR | 0.48056 | 0.48056 | 0.54236 | 0 | 1.4833 | 1.4833 | WTG manual stop for WTR 630 and WTR 655 work. | Close | 0.057051 | O2-07 | 262.241 |  | WTG Breakdown Maintenance | 4243 | 262.241
3556 | 2025-01-27 | 2025 | 2025 | 2025-01-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.95347 | 0.97917 | 1899-12-31 | 0.61667 | 0.5 | 1.1167 | Attend and check error related ckt than found encoder value abnormal than wip, | Close | 0.042949 | O2-02 | 234.3604 |  | WTG Unscheduled Maintenance | 5037 | 234.3604
3557 | 2025-01-27 | 2025 | 2025 | 2025-01-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR | 0.47708 | 0.47708 | 0.51111 | 0 | 0.81667 | 0.81667 | WTG manual stop for WTR 630 work | Close | 0.03141 | O2-26 | 140.3986 |  | WTG Breakdown Maintenance | 4126 | 140.3986
3558 | 2025-01-27 | 2025 | 2025 | 2025-01-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.84931 | 0.90972 | 0.92778 | 1.45 | 0.43333 | 1.8833 | After Grid Resume turbine disconnected to scada so check by BOP team found VCB not tripped than attend and check error related ckt so found main controller module in error mode so wip, | Close | 0.072436 | O2-11 | 266.0993 |  | WTG Unscheduled Maintenance | 3391 | 266.0993
3559 | 2025-01-27 | 2025 | 2025 | 2025-01-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.95347 | 0.95347 | 1899-12-31 | 0 | 1.1167 | 1.1167 | After Grid Resume turbine disconnected to scada so check by BOP team found VCB not tripped than attend and check error related ckt so found main controller module in error mode so wip, | Close | 0.042949 | O2-11 | 157.7757 |  | WTG Unscheduled Maintenance | 3391 | 157.7757
3560 | 2025-01-27 | 2025 | 2025 | 2025-01-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.69306 | 0.69306 | 0.70278 | 0 | 0.23333 | 0.23333 | Checked related error data log then reset & start WTG. | Close | 0.0089744 | O2-06 | 24.4222 |  | WTG Unscheduled Maintenance | 2512 | 24.4222
3561 | 2025-01-27 | 2025 | 2025 | 2025-01-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Blade cleaning work | 0.44097 | 0.44097 | 0.76042 | 0 | 7.6667 | 7.6667 | WTG manual stop for blade cleaning work. | Close | 0.29487 | O2-07 | 1355.4028 |  | WTG Breakdown Maintenance | 4243 | 1355.4028
3562 | 2025-01-27 | 2025 | 2025 | 2025-01-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.68958 | 0.68958 | 0.69583 | 0 | 0.15 | 0.15 | Checked related error data log then reset & start WTG. | Close | 0.0057692 | O2-24 | 42.9187 |  | WTG Unscheduled Maintenance | 6867 | 42.9187
3563 | 2025-01-27 | 2025 | 2025 | 2025-01-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.71597 | 0.71597 | 0.72569 | 0 | 0.23333 | 0.23333 | Checked related error data log then reset & start WTG. | Close | 0.0089744 | O2-06 | 24.4222 |  | WTG Unscheduled Maintenance | 2512 | 24.4222
3564 | 2025-01-28 | 2025 | 2025 | 2025-01-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.46875 | 0.46875 | 0.56875 | 0 | 2.4 | 2.4 | WTG manual stop for Convertor supplier inspection work. | Close | 0.092308 | O2-26 | 236.8 |  | WTG Breakdown Maintenance | 2368 | 236.8
3565 | 2025-01-28 | 2025 | 2025 | 2025-01-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0 | 0 | 0.036111 | 0 | 0.86667 | 0.86667 | Attend and check error related ckt than found encoder value abnormal than apply hard reboot than start WTG. | Close | 0.033333 | O2-02 | 76.7361 |  | WTG Unscheduled Maintenance | 2125 | 76.7361
3566 | 2025-01-28 | 2025 | 2025 | 2025-01-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR | 0.46181 | 0.46181 | 0.55139 | 0 | 2.15 | 2.15 | WTG manual stop for WTR 655 work. | Close | 0.082692 | O2-02 | 190.3646 |  | WTG Breakdown Maintenance | 2125 | 190.3646
3567 | 2025-01-28 | 2025 | 2025 | 2025-01-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Blade cleaning work | 0.42986 | 0.42986 | 0.84375 | 0 | 9.9333 | 9.9333 | WTG manual stop for blade cleaning work. | Close | 0.38205 | O2-12 | 1589.3333 |  | WTG Breakdown Maintenance | 3840 | 1589.3333
3568 | 2025-01-28 | 2025 | 2025 | 2025-01-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0 | 0 | 0.019444 | 0 | 0.46667 | 0.46667 | After Grid Resume turbine disconnected to scada so check by BOP team found VCB not tripped than attend and check error related ckt so found main controller module in error mode so reinstall software than start WTG. | Close | 0.017949 | O2-11 | 51.5667 |  | WTG Unscheduled Maintenance | 2652 | 51.5667
3569 | 2025-01-28 | 2025 | 2025 | 2025-01-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.58958 | 0.58958 | 0.59097 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & start WTG. | Close | 0.0012821 | O2-22 | 2.5847 |  | WTG Unscheduled Maintenance | 1861 | 2.5847
3570 | 2025-01-28 | 2025 | 2025 | 2025-01-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.52361 | 0.60417 | 0.64931 | 1.9333 | 1.0833 | 3.0167 | After Feeder charge bottom controller software crash so reinsert new software than start WTG. | Close | 0.11603 | O2-07 | 185.1479 |  | WTG Unscheduled Maintenance | 1473 | 185.1479
3571 | 2025-01-28 | 2025 | 2025 | 2025-01-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.75347 | 0.75347 | 0.82986 | 0 | 1.8333 | 1.8333 | WTG main Controller is not proper Data show so reinstall software then reset and start WTG. | Close | 0.070513 | O2-24 | 207.9306 |  | WTG Breakdown Maintenance | 2722 | 207.9306
3572 | 2025-01-28 | 2025 | 2025 | 2025-01-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.84444 | 0.84444 | 0.84653 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | O2-24 | 5.6708 |  | WTG Unscheduled Maintenance | 2722 | 5.6708
3573 | 2025-01-28 | 2025 | 2025 | 2025-01-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.85694 | 0.85694 | 0.86111 | 0 | 0.1 | 0.1 | Checked related error data log then reset & start WTG. | Close | 0.0038462 | O2-24 | 11.3417 |  | WTG Unscheduled Maintenance | 2722 | 11.3417
3574 | 2025-01-29 | 2025 | 2025 | 2025-01-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.48819 | 0.48819 | 0.5 | 0 | 0.28333 | 0.28333 | Checked related error data log then reset & start WTG. | Close | 0.010897 | O2-26 | 43.8813 |  | WTG Unscheduled Maintenance | 3717 | 43.8813
3575 | 2025-01-29 | 2025 | 2025 | 2025-01-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.52292 | 0.52292 | 0.52569 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & start WTG. | Close | 0.0025641 | O2-26 | 10.325 |  | WTG Unscheduled Maintenance | 3717 | 10.325
3576 | 2025-01-29 | 2025 | 2025 | 2025-01-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.69236 | 0.72917 | 0.75694 | 0.88333 | 0.66667 | 1.55 | After Feeder charge bottom controller software crash so reinsert new software than start WTG. | Close | 0.059615 | O2-05 | 250.0021 |  | WTG Unscheduled Maintenance | 3871 | 250.0021
3577 | 2025-01-29 | 2025 | 2025 | 2025-01-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Blade cleaning work | 0.41319 | 0.41319 | 0.66458 | 0 | 6.0333 | 6.0333 | WTG manual stop for blade cleaning work wip, | Close | 0.23205 | O2-26 | 934.4125 |  | WTG Breakdown Maintenance | 3717 | 934.4125
3578 | 2025-01-29 | 2025 | 2025 | 2025-01-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Blade cleaning work | 0.69236 | 0.69236 | 0.77708 | 0 | 2.0333 | 2.0333 | WTG manual stop for blade cleaning work wip, | Close | 0.078205 | O2-26 | 314.9125 |  | WTG Breakdown Maintenance | 3717 | 314.9125
3579 | 2025-01-29 | 2025 | 2025 | 2025-01-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Blade cleaning work | 0.79097 | 0.79097 | 0.85417 | 0 | 1.5167 | 1.5167 | WTG manual stop for blade cleaning work done than Batt. undervoltage/overvoltage error occurred so wip, | Close | 0.058333 | O2-26 | 234.8937 |  | WTG Breakdown Maintenance | 3717 | 234.8937
3580 | 2025-01-29 | 2025 | 2025 | 2025-01-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Break down | 0.85417 | 0.95833 | 1899-12-31 | 2.5 | 1 | 3.5 | After grid attend and check error related ckt than found Axis-3 Flat resistor faulty so replace with new one than wip, | Close | 0.13462 | O2-26 | 542.0625 |  | WTG Unscheduled Maintenance | 3717 | 542.0625
3581 | 2025-01-29 | 2025 | 2025 | 2025-01-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.79097 | 0.8125 | 0.85417 | 0.51667 | 1 | 1.5167 | After grid resume attend and check error related ckt than found encoder value abnormal than apply hard reboot than start WTG. | Close | 0.058333 | O2-12 | 686.4181 |  | WTG Unscheduled Maintenance | 10862 | 686.4181
3582 | 2025-01-29 | 2025 | 2025 | 2025-01-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.79097 | 0.82292 | 0.84375 | 0.76667 | 0.5 | 1.2667 | After grid resume attend and check error related ckt than found encoder value abnormal than apply hard reboot than start WTG. | Close | 0.048718 | O2-10 | 287.1639 |  | WTG Unscheduled Maintenance | 5441 | 287.1639
3583 | 2025-01-29 | 2025 | 2025 | 2025-01-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.21111 | 0.21111 | 0.21528 | 0 | 0.1 | 0.1 | Checked related error data log then reset & start WTG. | Close | 0.0038462 | O2-22 | 17.0042 |  | WTG Unscheduled Maintenance | 4081 | 17.0042
3584 | 2025-01-29 | 2025 | 2025 | 2025-01-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.77639 | 0.79167 | 0.80139 | 0.36667 | 0.23333 | 0.6 | after grid resume base box not ready for operation error so attend wtg and hard reboot then reset & start the WTG. | Close | 0.023077 | O2-22 | 102.025 |  | WTG Unscheduled Maintenance | 4081 | 102.025
3585 | 2025-01-29 | 2025 | 2025 | 2025-01-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.63889 | 0.63889 | 0.68056 | 0 | 1 | 1 | WTG manual stop for convertor Coolent temprature sensor replacement work. | Close | 0.038462 | O2-24 | 388.6667 |  | WTG Unscheduled Maintenance | 9328 | 388.6667
3586 | 2025-01-29 | 2025 | 2025 | 2025-01-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.79097 | 0.85417 | 0.87361 | 1.5167 | 0.46667 | 1.9833 | After Grid resume attend and check ckt than apply hard reboot than wip, | Close | 0.076282 | O2-11 | 873.8236 |  | WTG Unscheduled Maintenance | 10574 | 873.8236
3587 | 2025-01-29 | 2025 | 2025 | 2025-01-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.88958 | 0.88958 | 0.89375 | 0 | 0.1 | 0.1 | After Grid resume attend and check ckt than apply hard reboot than reset and start WTG. | Close | 0.0038462 | O2-11 | 44.0583 |  | WTG Unscheduled Maintenance | 10574 | 44.0583
3588 | 2025-01-29 | 2025 | 2025 | 2025-01-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.45833 | 0.45833 | 0.54861 | 0 | 2.1667 | 2.1667 | WTG manual stop for Ingeteam Convertor Supplier inspection work. | Close | 0.083333 | O2-20 | 555.8403 |  | WTG Breakdown Maintenance | 6157 | 555.8403
3589 | 2025-01-30 | 2025 | 2025 | 2025-01-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.47222 | 0.47222 | 0.53819 | 0 | 1.5833 | 1.5833 | WTG stop for Repeat error inspection work done than start WTG. | Close | 0.060897 | O2-09 | 586.8229 |  | WTG Breakdown Maintenance | 8895 | 586.8229
3590 | 2025-01-30 | 2025 | 2025 | 2025-01-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Break down | 0 | 0 | 0.026389 | 0 | 0.63333 | 0.63333 | After grid attend and check error related ckt than found Axis-3 Flat resistor faulty so replace with new one than start WTG. | Close | 0.024359 | O2-26 | 200.7139 |  | WTG Unscheduled Maintenance | 7606 | 200.7139
3591 | 2025-01-30 | 2025 | 2025 | 2025-01-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.79861 | 0.80556 | 0.82083 | 0.16667 | 0.36667 | 0.53333 | Attend and found convertor cooling fan MCB trip so check all error releted ckt found no any abnormality so reset and start WTG now wtg under observation. | Close | 0.020513 | O2-12 | 341.4 |  | WTG Unscheduled Maintenance | 15363 | 341.4
3592 | 2025-01-30 | 2025 | 2025 | 2025-01-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.85417 | 0.85417 | 0.86875 | 0 | 0.35 | 0.35 | Checked related error data log then reset & start WTG. | Close | 0.013462 | O2-12 | 224.0438 |  | WTG Unscheduled Maintenance | 15363 | 224.0438
3593 | 2025-01-30 | 2025 | 2025 | 2025-01-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.93056 | 0.93056 | 0.95833 | 0 | 0.66667 | 0.66667 | Attend and found convertor cooling fan MCB trip so check all error releted ckt also correct mcb setting than reset and start WTG. | Close | 0.025641 | O2-12 | 426.75 |  | WTG Unscheduled Maintenance | 15363 | 426.75
3594 | 2025-01-30 | 2025 | 2025 | 2025-01-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 4555 | Tower accel. difference | Break down | 0.36319 | 0.36319 | 0.36736 | 0 | 0.1 | 0.1 | Checked related error data log then reset & start WTG. | Close | 0.0038462 | O2-10 | 56.0542 |  | WTG Unscheduled Maintenance | 13453 | 56.0542
3595 | 2025-01-30 | 2025 | 2025 | 2025-01-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.19444 | 0.19444 | 0.20278 | 0 | 0.2 | 0.2 | Checked related error data log then reset & start WTG. | Close | 0.0076923 | O2-24 | 108.7083 |  | WTG Unscheduled Maintenance | 13045 | 108.7083
3596 | 2025-01-30 | 2025 | 2025 | 2025-01-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.52083 | 0.52083 | 0.71528 | 0 | 4.6667 | 4.6667 | Bottom penal Ispection work done than start WTG. | Close | 0.17949 | O2-24 | 2536.5278 |  | WTG Breakdown Maintenance | 13045 | 2536.5278
3597 | 2025-01-30 | 2025 | 2025 | 2025-01-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.98889 | 0.98889 | 1899-12-31 | 0 | 0.26667 | 0.26667 | WTG Manual stop for Softwate releted work wip, | Close | 0.010256 | O2-24 | 144.9444 |  | WTG Breakdown Maintenance | 13045 | 144.9444
3598 | 2025-01-30 | 2025 | 2025 | 2025-01-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Blade cleaning work | 0.43056 | 0.43056 | 0.61806 | 0 | 4.5 | 4.5 | WTG manual stop for blade cleaning work wip, | Close | 0.17308 | O2-25 | 1522.125 |  | WTG Breakdown Maintenance | 8118 | 1522.125
3599 | 2025-01-30 | 2025 | 2025 | 2025-01-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Blade cleaning work | 0.66181 | 0.66181 | 0.80208 | 0 | 3.3667 | 3.3667 | WTG manual stop for blade cleaning work. | Close | 0.12949 | O2-25 | 1138.775 |  | WTG Breakdown Maintenance | 8118 | 1138.775
3600 | 2025-01-31 | 2025 | 2025 | 2025-01-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Blade cleaning work | 0.42014 | 0.42014 | 0.78125 | 0 | 8.6667 | 8.6667 | WTG manual stop for blade cleaning work. | Close | 0.33333 | O2-26 | 2472.5278 |  | WTG Breakdown Maintenance | 6847 | 2472.5278
3601 | 2025-01-31 | 2025 | 2025 | 2025-01-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0 | 0 | 0.0125 | 0 | 0.3 | 0.3 | WTG Manual stop for Softwate releted work . | Close | 0.011538 | O2-24 | 206.0375 |  | WTG Breakdown Maintenance | 16483 | 206.0375
3602 | 2025-01-31 | 2025 | 2025 | 2025-01-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.38889 | 0.38889 | 0.46389 | 0 | 1.8 | 1.8 | WTG main Controller is not proper Data show so reinstall software then wip, | Close | 0.069231 | O2-24 | 1236.225 |  | WTG Breakdown Maintenance | 16483 | 1236.225
3603 | 2025-01-31 | 2025 | 2025 | 2025-01-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR | 0.46458 | 0.46458 | 0.51736 | 0 | 1.2667 | 1.2667 | After Software work done than WTR 655 work done than start WTG. | Close | 0.048718 | O2-24 | 869.9361 |  | WTG Breakdown Maintenance | 16483 | 869.9361
3604 | 2025-01-31 | 2025 | 2025 | 2025-01-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Major BD | 0.5 | 0.57292 | 0.77292 | 1.75 | 4.8 | 6.55 | Turbine atttend and check ckt at that time found some meterial failure like contectro and fuse and cable so now we will arreng meterial work wip, | Close | 0.25192 | O2-22 | 1909.5979 |  | WTG Unscheduled Maintenance | 6997 | 1909.5979
3605 | 2025-01-31 | 2025 | 2025 | 2025-01-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Major BD | 0.79792 | 0.79792 | 1899-12-31 | 0 | 4.85 | 4.85 | After grid resume check ckt at that time found some meterial failure like contectro and fuse and cable so now we will arreng meterial work wip, | Close | 0.18654 | O2-22 | 1413.9771 |  | WTG Unscheduled Maintenance | 6997 | 1413.9771
3606 | 2025-02-01 | 2025 | 2025 | 2025-02-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.44583 | 0.44583 | 0.44792 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | O2-15 | 40.8167 |  | WTG Unscheduled Maintenance | 19592 | 40.8167
3607 | 2025-02-01 | 2025 | 2025 | 2025-02-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Major BD | 0 | 0.79167 | 0.90694 | 19 | 2.7667 | 21.7667 | Attend and arrenge material than replace grid filter contector 2 nos. and also replace link wire contector to fuse than check precharge ckt and take tria than nothing abnormal than reset and start WTG. | Close | 0.83718 | O2-22 | 11446.5458 |  | WTG Unscheduled Maintenance | 12621 | 11446.5458
3608 | 2025-02-01 | 2025 | 2025 | 2025-02-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Blade cleaning work | 0.43056 | 0.43056 | 0.76736 | 0 | 8.0833 | 8.0833 | WTG manual stop for blade cleaning work. | Close | 0.3109 | O2-11 | 6494.9583 |  | WTG Breakdown Maintenance | 19284 | 6494.9583
3609 | 2025-02-01 | 2025 | 2025 | 2025-02-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 551 | Pitch motor current too high | Break down | 0.16389 | 0.16389 | 0.17431 | 0 | 0.25 | 0.25 | Checked related error data log then reset & start WTG. | Close | 0.0096154 | O2-25 | 236.3229 |  | WTG Unscheduled Maintenance | 22687 | 236.3229
3610 | 2025-02-01 | 2025 | 2025 | 2025-02-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.19444 | 0.19444 | 0.20833 | 0 | 0.33333 | 0.33333 | Checked related error data log then reset & start WTG. | Close | 0.012821 | O2-24 | 303.9583 |  | WTG Unscheduled Maintenance | 21885 | 303.9583
3611 | 2025-02-01 | 2025 | 2025 | 2025-02-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.63403 | 0.63403 | 0.64653 | 0 | 0.3 | 0.3 | Checked related error data log then reset & start WTG. | Close | 0.011538 | O2-24 | 273.5625 |  | WTG Unscheduled Maintenance | 21885 | 273.5625
3612 | 2025-02-02 | 2025 | 2025 | 2025-02-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Blade cleaning work | 0.44444 | 0.44444 | 0.77778 | 0 | 8 | 8 | WTG manual stop for blade cleaning work. | Close | 0.30769 | O2-21 | 564.6667 |  | WTG Breakdown Maintenance | 1694 | 564.6667
3613 | 2025-02-02 | 2025 | 2025 | 2025-02-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.28681 | 0.28681 | 0.28889 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | O2-15 | 9.025 |  | WTG Unscheduled Maintenance | 4332 | 9.025
3614 | 2025-02-02 | 2025 | 2025 | 2025-02-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.48472 | 0.48472 | 0.49167 | 0 | 0.16667 | 0.16667 | Checked related error data log then reset & start WTG. | Close | 0.0064103 | O2-24 | 24.1736 |  | WTG Unscheduled Maintenance | 3481 | 24.1736
3615 | 2025-02-02 | 2025 | 2025 | 2025-02-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.93333 | 0.93333 | 0.93819 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & start WTG. | Close | 0.0044872 | O2-24 | 16.9215 |  | WTG Unscheduled Maintenance | 3481 | 16.9215
3616 | 2025-02-03 | 2025 | 2025 | 2025-02-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 4555 | Tower accel. difference | Break down | 0.016667 | 0.016667 | 0.018056 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & start WTG. | Close | 0.0012821 | O2-05 | 4.1375 |  | WTG Unscheduled Maintenance | 2979 | 4.1375
3617 | 2025-02-03 | 2025 | 2025 | 2025-02-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Blade cleaning work | 0.44167 | 0.44167 | 0.74306 | 0 | 7.2333 | 7.2333 | WTG manual stop for blade cleaning work. | Close | 0.27821 | O2-06 | 959.9236 |  | WTG Breakdown Maintenance | 3185 | 959.9236
3618 | 2025-02-03 | 2025 | 2025 | 2025-02-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.34722 | 0.34722 | 0.35972 | 0 | 0.3 | 0.3 | Checked related error data log then reset & start WTG. | Close | 0.011538 | O2-24 | 43.4 |  | WTG Unscheduled Maintenance | 3472 | 43.4
3619 | 2025-02-03 | 2025 | 2025 | 2025-02-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.76319 | 0.76319 | 0.76875 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & start WTG. | Close | 0.0051282 | O2-24 | 19.2889 |  | WTG Unscheduled Maintenance | 3472 | 19.2889
3620 | 2025-02-03 | 2025 | 2025 | 2025-02-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.53403 | 0.53403 | 0.53958 | 0 | 0.13333 | 0.13333 | WTG manual stop for SCADA Synchronization Work. | Close | 0.0051282 | O2-20 | 18.1611 |  | WTG Breakdown Maintenance | 3269 | 18.1611
3621 | 2025-02-03 | 2025 | 2025 | 2025-02-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 551 | Pitch motor current too high | Break down | 0.82986 | 0.82986 | 0.83819 | 0 | 0.2 | 0.2 | Checked related error data log then reset & start WTG. | Close | 0.0076923 | O2-25 | 38.2167 |  | WTG Unscheduled Maintenance | 4586 | 38.2167
3622 | 2025-02-04 | 2025 | 2025 | 2025-02-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 2521 | Gen.sp.analog <<>> gearb.sp. | Break down | 0.38681 | 0.38681 | 0.38889 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | O2-02 | 29.2687 |  | WTG Unscheduled Maintenance | 14049 | 29.2687
3623 | 2025-02-04 | 2025 | 2025 | 2025-02-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 656 | Error pitch converter 1 | Break down | 0.64236 | 0.64236 | 0.64375 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & start WTG. | Close | 0.0012821 | O2-26 | 19.6819 |  | WTG Unscheduled Maintenance | 14171 | 19.6819
3624 | 2025-02-04 | 2025 | 2025 | 2025-02-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Blade cleaning work | 0.55208 | 0.55208 | 0.69097 | 0 | 3.3333 | 3.3333 | Turbine stop for blade cleaning work but suddenly wind speed increse and skylift wire rope gone into HT yard so Pospond activity and plane to tomorrow it. | Close | 0.12821 | O2-03 | 2117.0833 |  | WTG Breakdown Maintenance | 15243 | 2117.0833
3625 | 2025-02-04 | 2025 | 2025 | 2025-02-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.55208 | 0.55208 | 0.59097 | 0 | 0.93333 | 0.93333 | After Grid resume check error related ckt than found encoder value abnormal than apply hard reboot than start WTG. | Close | 0.035897 | O2-12 | 771.0111 |  | WTG Unscheduled Maintenance | 19826 | 771.0111
3626 | 2025-02-04 | 2025 | 2025 | 2025-02-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 7002 | Task runtime failure 5ms | Break down | 0.41667 | 0.41667 | 0.43264 | 0 | 0.38333 | 0.38333 | Checked related error data log then reset & start WTG. | Close | 0.014744 | O2-21 | 176.2215 |  | WTG Unscheduled Maintenance | 11033 | 176.2215
3627 | 2025-02-04 | 2025 | 2025 | 2025-02-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.18403 | 0.18403 | 0.18958 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & start WTG. | Close | 0.0051282 | O2-24 | 118.1556 |  | WTG Unscheduled Maintenance | 21268 | 118.1556
3628 | 2025-02-04 | 2025 | 2025 | 2025-02-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.53264 | 0.53264 | 0.53958 | 0 | 0.16667 | 0.16667 | Checked related error data log then reset & start WTG. | Close | 0.0064103 | O2-24 | 147.6944 |  | WTG Unscheduled Maintenance | 21268 | 147.6944
3629 | 2025-02-04 | 2025 | 2025 | 2025-02-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.97569 | 0.97569 | 0.98264 | 0 | 0.16667 | 0.16667 | Checked related error data log then reset & start WTG. | Close | 0.0064103 | O2-24 | 147.6944 |  | WTG Unscheduled Maintenance | 21268 | 147.6944
3630 | 2025-02-04 | 2025 | 2025 | 2025-02-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 551 | Pitch motor current too high | Major BD | 0.225 | 0.26389 | 0.49861 | 0.93333 | 5.6333 | 6.5667 | Attend and check error related ckt than troubleshooting done than found axis 2 Pitch motor failure than other site material arrengment wip, | Close | 0.25256 | O2-05 | 4245.8972 |  | WTG Unscheduled Maintenance | 15518 | 4245.8972
3631 | 2025-02-04 | 2025 | 2025 | 2025-02-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 551 | Pitch motor current too high | Major BD | 0.55208 | 0.55208 | 0.92847 | 0 | 9.0333 | 9.0333 | After feeder resume and check error related ckt than troubleshooting done than found axis 2 Pitch motor failure than other site material arrengment wip, | Close | 0.34744 | O2-05 | 5840.8028 |  | WTG Unscheduled Maintenance | 15518 | 5840.8028
3632 | 2025-02-04 | 2025 | 2025 | 2025-02-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 551 | Pitch motor current too high | Major BD | 0.94653 | 0.94653 | 0.95694 | 0 | 0.25 | 0.25 | After feeder resume and check error related ckt than troubleshooting done than found axis 2 Pitch motor failure than other site material arrengment wip, | Close | 0.0096154 | O2-05 | 161.6458 |  | WTG Unscheduled Maintenance | 15518 | 161.6458
3633 | 2025-02-05 | 2025 | 2025 | 2025-02-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Blade cleaning work | 0.48125 | 0.48125 | 0.85069 | 0 | 8.8667 | 8.8667 | WTG manual stop for blade cleaning work. | Close | 0.34103 | O2-03 | 7469.7972 |  | WTG Breakdown Maintenance | 20219 | 7469.7972
3634 | 2025-02-05 | 2025 | 2025 | 2025-02-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.6625 | 0.6625 | 0.66458 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | O2-15 | 59.9583 |  | WTG Unscheduled Maintenance | 28780 | 59.9583
3635 | 2025-02-05 | 2025 | 2025 | 2025-02-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0 | 0 | 0.011806 | 0 | 0.28333 | 0.28333 | After Grid resume check error related ckt than found encoder value abnormal than apply hard reboot than start WTG. | Close | 0.010897 | O2-12 | 310.4507 |  | WTG Unscheduled Maintenance | 26297 | 310.4507
3636 | 2025-02-05 | 2025 | 2025 | 2025-02-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 4555 | Tower accel. difference | Break down | 0.41111 | 0.41111 | 0.41458 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & start WTG. | Close | 0.0032051 | O2-07 | 66.0833 |  | WTG Unscheduled Maintenance | 19032 | 66.0833
3637 | 2025-02-05 | 2025 | 2025 | 2025-02-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD | 0.60417 | 0.60417 | 0.99653 | 0 | 9.4167 | 9.4167 | Turbine stop SLC Warning MC212 Module and upadet software but at that time error occurred so call to techanical team and resolve this issue after reset and take generation trail but at that time pitch error occurred so attend check so found 1.7 ohm flat resister failure so replace it then reset and start wtg | Close | 0.36218 | O2-24 | 8516.1979 |  | WTG Breakdown Maintenance | 21705 | 8516.1979
3638 | 2025-02-05 | 2025 | 2025 | 2025-02-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.57778 | 0.57778 | 0.58125 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & start WTG. | Close | 0.0032051 | O2-06 | 89.441 |  | WTG Unscheduled Maintenance | 25759 | 89.441
3639 | 2025-02-05 | 2025 | 2025 | 2025-02-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 551 | Pitch motor current too high | Break down | 0 | 0 | 0.20903 | 0 | 5.0167 | 5.0167 | attend and check error related ckt than found Axis-2 pitch motor failure so replace with new one and start wtg | Close | 0.19295 | O2-01 | 6201.4361 |  | WTG Unscheduled Maintenance | 29668 | 6201.4361
3640 | 2025-02-06 | 2025 | 2025 | 2025-02-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.4875 | 0.4875 | 0.53611 | 0 | 1.1667 | 1.1667 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.044872 | O2-26 | 1793.6528 |  | WTG Breakdown Maintenance | 36898 | 1793.6528
3641 | 2025-02-06 | 2025 | 2025 | 2025-02-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.93194 | 0.93194 | 0.94792 | 0 | 0.38333 | 0.38333 | Checked related error data log then reset & start WTG. | Close | 0.014744 | O2-26 | 589.3431 |  | WTG Unscheduled Maintenance | 36898 | 589.3431
3642 | 2025-02-06 | 2025 | 2025 | 2025-02-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.52083 | 0.52083 | 0.52639 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & start WTG. | Close | 0.0051282 | O2-05 | 262.65 |  | WTG Unscheduled Maintenance | 47277 | 262.65
3643 | 2025-02-06 | 2025 | 2025 | 2025-02-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.83889 | 0.83889 | 0.86667 | 0 | 0.66667 | 0.66667 | Checked related error data log then reset & start WTG. | Close | 0.025641 | O2-05 | 1313.25 |  | WTG Unscheduled Maintenance | 47277 | 1313.25
3644 | 2025-02-06 | 2025 | 2025 | 2025-02-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 6012 | Overload yaw motors group 2 | Break down | 0.52222 | 0.57431 | 0.6375 | 1.25 | 1.5167 | 2.7667 | attend and check error related ckt than found Yaw MPCB waas tripped so check connection and retight all connection than charge and take trial than nothing found abnormal than reset and start WTG. | Close | 0.10641 | O2-21 | 4903.8014 |  | WTG Unscheduled Maintenance | 42539 | 4903.8014
3645 | 2025-02-06 | 2025 | 2025 | 2025-02-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.93194 | 0.93194 | 0.94306 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & start WTG. | Close | 0.010256 | O2-26 | 409.9778 |  | WTG Unscheduled Maintenance | 36898 | 409.9778
3646 | 2025-02-06 | 2025 | 2025 | 2025-02-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.061111 | 0.061111 | 0.32361 | 0 | 6.3 | 6.3 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.24231 | O2-03 | 12315.7125 |  | WTG Breakdown Maintenance | 46917 | 12315.7125
3647 | 2025-02-06 | 2025 | 2025 | 2025-02-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Break down | 0.99861 | 0.99861 | 0.99999 | 0 | 0.033056 | 0.033056 | Wtg in error than check data and found grid jurk so further Troublshooting WIP | Close | 0.0012714 | O2-15 | 79.1653 |  | WTG Unscheduled Maintenance | 57478 | 79.1653
3648 | 2025-02-06 | 2025 | 2025 | 2025-02-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 550 | Pitch current asymmetry | Break down | 0.96806 | 0.96806 | 0.97222 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-14 | 177.3125 |  | WTG Unscheduled Maintenance | 42555 | 177.3125
3649 | 2025-02-06 | 2025 | 2025 | 2025-02-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.072222 | 0.072222 | 0.0875 | 0 | 0.36667 | 0.36667 | WTG in error so check data than apply soft reboot than reset and start WTG. | Close | 0.014103 | O2-22 | 675.1097 |  | WTG Unscheduled Maintenance | 44189 | 675.1097
3650 | 2025-02-06 | 2025 | 2025 | 2025-02-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Break down | 0.10278 | 0.10278 | 0.10417 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & start WTG. | Close | 0.0012821 | O2-22 | 61.3736 |  | WTG Unscheduled Maintenance | 44189 | 61.3736
3651 | 2025-02-06 | 2025 | 2025 | 2025-02-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 1065 | Drive train monitor level 1 | Break down | 0.21389 | 0.21389 | 0.21528 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2-22 | 61.3736 |  | WTG Unscheduled Maintenance | 44189 | 61.3736
3652 | 2025-02-06 | 2025 | 2025 | 2025-02-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Break down | 0.061111 | 0.061111 | 0.0875 | 0 | 0.63333 | 0.63333 | Checked related error data log then reset & start WTG. | Close | 0.024359 | O2-22 | 1166.0986 |  | WTG Unscheduled Maintenance | 44189 | 1166.0986
3653 | 2025-02-06 | 2025 | 2025 | 2025-02-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 7002 | Task runtime failure 5ms | Break down | 0.22778 | 0.22778 | 0.23333 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & start WTG. | Close | 0.0051282 | O2-22 | 245.4944 |  | WTG Unscheduled Maintenance | 44189 | 245.4944
3654 | 2025-02-06 | 2025 | 2025 | 2025-02-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.24653 | 0.24653 | 0.25556 | 0 | 0.21667 | 0.21667 | Checked related error data log then reset & start WTG. | Close | 0.0083333 | O2-22 | 398.9285 |  | WTG Unscheduled Maintenance | 44189 | 398.9285
3655 | 2025-02-06 | 2025 | 2025 | 2025-02-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Break down | 0.40347 | 0.40347 | 0.42639 | 0 | 0.55 | 0.55 | After auto reset than we attend and check than apply hard reboot than reset and start wtg | Close | 0.021154 | O2-22 | 1012.6646 |  | WTG Unscheduled Maintenance | 44189 | 1012.6646
3656 | 2025-02-06 | 2025 | 2025 | 2025-02-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.92847 | 0.92847 | 0.96389 | 0 | 0.85 | 0.85 | check data and found than Encoder angle Malfunctioning so appoly Hard rebbot of Ups than reset and start WTG. | Close | 0.032692 | O2-11 | 1891.8521 |  | WTG Unscheduled Maintenance | 53417 | 1891.8521
3657 | 2025-02-06 | 2025 | 2025 | 2025-02-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.25972 | 0.25972 | 0.26667 | 0 | 0.16667 | 0.16667 | Auto reset | Close | 0.0064103 | O2-20 | 363.9167 |  | WTG Unscheduled Maintenance | 52404 | 363.9167
3658 | 2025-02-06 | 2025 | 2025 | 2025-02-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Break down | 0.93194 | 0.97917 | 0.99999 | 1.1333 | 0.49972 | 1.6331 | Wtg in Error so attend and check related circuit than check contector and its connection and also check limit switch connection than further troublsooting WIP | Close | 0.06281 | O2-01 | 3757.7969 |  | WTG Unscheduled Maintenance | 55226 | 3757.7969
3659 | 2025-02-06 | 2025 | 2025 | 2025-02-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.072917 | 0.072917 | 0.24097 | 0 | 4.0333 | 4.0333 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.15513 | O2-01 | 9281.0361 |  | WTG Breakdown Maintenance | 55226 | 9281.0361
3659 | 2025-02-07 | 2025 | 2025 | 2025-02-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.91528 | 0.91528 | 0.91667 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & start WTG. | Close | 0.0012821 | O2-05 | 50.2056 |  | WTG Unscheduled Maintenance | 36148 | 50.2056
3659 | 2025-02-07 | 2025 | 2025 | 2025-02-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.97639 | 0.97639 | 0.98194 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & start WTG. | Close | 0.0051282 | O2-05 | 200.8222 |  | WTG Unscheduled Maintenance | 36148 | 200.8222
3659 | 2025-02-07 | 2025 | 2025 | 2025-02-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.093056 | 0.14028 | 0.18403 | 1.1333 | 1.05 | 2.1833 | attend turbine and Hard Reboot it after reset and start wtg | Close | 0.083974 | O2-02 | 3971.3014 |  | WTG Unscheduled Maintenance | 43654 | 3971.3014
3659 | 2025-02-07 | 2025 | 2025 | 2025-02-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.044444 | 0.044444 | 0.049306 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & start WTG. | Close | 0.0044872 | O2-26 | 207.6035 |  | WTG Unscheduled Maintenance | 42707 | 207.6035
3659 | 2025-02-07 | 2025 | 2025 | 2025-02-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.10347 | 0.10347 | 0.35 | 0 | 5.9167 | 5.9167 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.22756 | O2-03 | 9433.1389 |  | WTG Breakdown Maintenance | 38264 | 9433.1389
3659 | 2025-02-07 | 2025 | 2025 | 2025-02-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.01875 | 0.01875 | 0.050694 | 0 | 0.76667 | 0.76667 | check data and found than Encoder angle Malfunctioning so appoly Hard rebbot of Ups than reset and start WTG. | Close | 0.029487 | O2-15 | 1530.4903 |  | WTG Unscheduled Maintenance | 47911 | 1530.4903
3660 | 2025-02-07 | 2025 | 2025 | 2025-02-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.34375 | 0.34375 | 0.44306 | 0 | 2.3833 | 2.3833 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.091667 | O2-11 | 4380.666 |  | WTG Breakdown Maintenance | 44113 | 4380.666
3661 | 2025-02-07 | 2025 | 2025 | 2025-02-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 3555 | Current asymmetry | Break down | 0.72153 | 0.72153 | 0.72292 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2-12 | 67.6806 |  | WTG Unscheduled Maintenance | 48730 | 67.6806
3662 | 2025-02-07 | 2025 | 2025 | 2025-02-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.43472 | 0.43472 | 0.44514 | 0 | 0.25 | 0.25 | Checked related error data log then reset & start WTG. | Close | 0.0096154 | O2-22 | 440.8958 |  | WTG Unscheduled Maintenance | 42326 | 440.8958
3663 | 2025-02-07 | 2025 | 2025 | 2025-02-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.48056 | 0.48056 | 0.48542 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & start WTG. | Close | 0.0044872 | O2-06 | 241.325 |  | WTG Unscheduled Maintenance | 49644 | 241.325
3664 | 2025-02-07 | 2025 | 2025 | 2025-02-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.52083 | 0.52083 | 0.525 | 0 | 0.1 | 0.1 | Checked related error data log then reset & start WTG. | Close | 0.0038462 | O2-06 | 206.85 |  | WTG Unscheduled Maintenance | 49644 | 206.85
3665 | 2025-02-07 | 2025 | 2025 | 2025-02-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0 | 0 | 0.10417 | 0 | 2.5 | 2.5 | Attend and wtg check Battery voltage and flate resistorcheck so ok after blade calibration done after trail so ok then reset and start wtg. | Close | 0.096154 | O2-01 | 4979.1667 |  | WTG Unscheduled Maintenance | 47800 | 4979.1667
3666 | 2025-02-07 | 2025 | 2025 | 2025-02-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.10417 | 0.10417 | 0.34722 | 0 | 5.8333 | 5.8333 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.22436 | O2-01 | 11618.0556 |  | WTG Breakdown Maintenance | 47800 | 11618.0556
3667 | 2025-02-07 | 2025 | 2025 | 2025-02-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Major BD | 0.34722 | 0.39931 | 0.65764 | 1.25 | 6.2 | 7.45 | Attend and check All Releted circuit found QA011 contactor faulty so material arrangment then replace it and start wtg | Close | 0.28654 | O2-01 | 14837.9167 |  | WTG Unscheduled Maintenance | 47800 | 14837.9167
3668 | 2025-02-07 | 2025 | 2025 | 2025-02-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 650 | Pitch controller communication error | Break down | 0.066667 | 0.066667 | 0.073611 | 0 | 0.16667 | 0.16667 | Checked related error data log then reset & start WTG. | Close | 0.0064103 | O2-02 | 303.1528 |  | WTG Unscheduled Maintenance | 43654 | 303.1528
3669 | 2025-02-08 | 2025 | 2025 | 2025-02-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 650 | Pitch controller communication error | Break down | 0.0069444 | 0.0069444 | 0.0097222 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0025641 | O2-26 | 30.0139 |  | WTG Unscheduled Maintenance | 10805 | 30.0139
3670 | 2025-02-08 | 2025 | 2025 | 2025-02-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 3270 | Converter torque monitor level 0 | Break down | 0.11389 | 0.12708 | 0.15625 | 0.31667 | 0.7 | 1.0167 | attend turbine and Hard Reboot it after reset and start wtg | Close | 0.039103 | O2-26 | 457.7118 |  | WTG Unscheduled Maintenance | 10805 | 457.7118
3671 | 2025-02-08 | 2025 | 2025 | 2025-02-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.047222 | 0.047222 | 0.077778 | 0 | 0.73333 | 0.73333 | Checked related error data log then reset & start WTG. | Close | 0.028205 | O2-05 | 405.8389 |  | WTG Unscheduled Maintenance | 13282 | 405.8389
3672 | 2025-02-08 | 2025 | 2025 | 2025-02-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Blade cleaning work | 0.47222 | 0.47222 | 0.84722 | 0 | 9 | 9 | WTG manual stop for blade cleaning work. | Close | 0.34615 | O2-02 | 2975.25 |  | WTG Breakdown Maintenance | 7934 | 2975.25
3673 | 2025-02-08 | 2025 | 2025 | 2025-02-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 3270 | Converter torque monitor level 0 | Break down | 0.10417 | 0.11597 | 0.13333 | 0.28333 | 0.41667 | 0.7 | attend turbine and Hard Reboot it after reset and start wtg | Close | 0.026923 | O2-26 | 315.1458 |  | WTG Unscheduled Maintenance | 10805 | 315.1458
3674 | 2025-02-08 | 2025 | 2025 | 2025-02-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.064583 | 0.064583 | 0.072222 | 0 | 0.18333 | 0.18333 | Auto reset | Close | 0.0070513 | O2-12 | 125.866 |  | WTG Unscheduled Maintenance | 16477 | 125.866
3675 | 2025-02-08 | 2025 | 2025 | 2025-02-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.60625 | 0.60625 | 0.6125 | 0 | 0.15 | 0.15 | Auto reset | Close | 0.0057692 | O2-11 | 72.875 |  | WTG Unscheduled Maintenance | 11660 | 72.875
3676 | 2025-02-08 | 2025 | 2025 | 2025-02-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.036111 | 0.036111 | 0.052083 | 0 | 0.38333 | 0.38333 | Checked related error data log then reset & start WTG. | Close | 0.014744 | O2-22 | 203.9174 |  | WTG Unscheduled Maintenance | 12767 | 203.9174
3677 | 2025-02-08 | 2025 | 2025 | 2025-02-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Major BD | 0.065972 | 0.17222 | 0.97569 | 2.55 | 19.2833 | 21.8333 | Attend and wtg check Axis no 2 so found MCB Trip after trublshooting check all circuit releted contector check check 24 V Supply so ok after Check Rectifire After interchange for Axis no 2 to Axis no 1 After check Diode value not ok Axis no 2 After arrnge material. | Close | 0.83974 | O2-01 | 10310.7917 |  | WTG Unscheduled Maintenance | 11334 | 10310.7917
3678 | 2025-02-09 | 2025 | 2025 | 2025-02-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Blade cleaning work | 0.47361 | 0.47361 | 0.84028 | 0 | 8.8 | 8.8 | WTG manual stop for blade cleaning work. | Close | 0.33846 | O2-07 | 735.1667 |  | WTG Breakdown Maintenance | 2005 | 735.1667
3679 | 2025-02-09 | 2025 | 2025 | 2025-02-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.24653 | 0.24653 | 0.27639 | 0 | 0.71667 | 0.71667 | Material Arrange and Replace Diode Axis No 2 Then reset and start wtg | Close | 0.027564 | O2-01 | 124.0729 |  | WTG Breakdown Maintenance | 4155 | 124.0729
3680 | 2025-02-09 | 2025 | 2025 | 2025-02-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Major BD | 0.60764 | 0.63194 | 1899-12-31 | 0.58333 | 8.8333 | 9.4167 | Attend and wtg check all valve and check oil so ok after check pressure so trubulshooting wip | open | 0.36218 | O2-22 | 1266.5417 |  | WTG Unscheduled Maintenance | 3228 | 1266.5417
3681 | 2025-02-10 | 2025 | 2025 | 2025-02-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Blade cleaning work | 0.45278 | 0.45278 | 0.84722 | 0 | 9.4667 | 9.4667 | WTG manual stop for blade cleaning work. | Close | 0.3641 | O2-04 | 2051.5056 |  | WTG Breakdown Maintenance | 5201 | 2051.5056
3682 | 2025-02-10 | 2025 | 2025 | 2025-02-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.18542 | 0.18542 | 0.1875 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2-14 | 8.0146 |  | WTG Unscheduled Maintenance | 3847 | 8.0146
3683 | 2025-02-10 | 2025 | 2025 | 2025-02-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.85903 | 0.85903 | 0.86111 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2-11 | 9.9292 |  | WTG Unscheduled Maintenance | 4766 | 9.9292
3684 | 2025-02-10 | 2025 | 2025 | 2025-02-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down | 0 | 0.41181 | 0.57986 | 9.8833 | 4.0333 | 13.9167 | After Material Arrangement HPU Unit for Another site then replace it then start wtg snd also WTR 672. | Close | 0.53526 | O2-22 | 1475.7465 |  | WTG Unscheduled Maintenance | 2545 | 1475.7465
3685 | 2025-02-10 | 2025 | 2025 | 2025-02-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.27083 | 0.42917 | 0.45833 | 3.8 | 0.7 | 4.5 | Attend and wtg after troubleshoot and found FA05 Surge arrester FB Cable found loose so tight then reset and start wtg | Close | 0.17308 | O2-07 | 252.5625 |  | WTG Unscheduled Maintenance | 1347 | 252.5625
3686 | 2025-02-11 | 2025 | 2025 | 2025-02-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 3555 | Current asymmetry | Auto reset | 0.45486 | 0.45486 | 0.45625 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2-26 | 18.2111 |  | WTG Unscheduled Maintenance | 13112 | 18.2111
3687 | 2025-02-11 | 2025 | 2025 | 2025-02-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 650 | Pitch controller communication error | Break down | 0.19653 | 0.19653 | 0.20139 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & start WTG. | Close | 0.0044872 | O2-05 | 104.7181 |  | WTG Unscheduled Maintenance | 21542 | 104.7181
3688 | 2025-02-11 | 2025 | 2025 | 2025-02-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Blade cleaning work | 0.46181 | 0.46181 | 0.78958 | 0 | 7.8667 | 7.8667 | WTG manual stop for blade cleaning work. | Close | 0.30256 | O2-09 | 5606.3111 |  | WTG Breakdown Maintenance | 17104 | 5606.3111
3689 | 2025-02-11 | 2025 | 2025 | 2025-02-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Major BD | 0.58333 | 0.62986 | 0.9875 | 1.1167 | 8.5833 | 9.7 | Attend and wtg found 1 nos yaw caliper oil leakage after oil arrest in temperry then reset and start wtg | Close | 0.37308 | O2-07 | 7179.6167 |  | WTG Unscheduled Maintenance | 17764 | 7179.6167
3690 | 2025-02-11 | 2025 | 2025 | 2025-02-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Auto reset | 0.20556 | 0.20556 | 0.20694 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2-02 | 24.5264 |  | WTG Unscheduled Maintenance | 17659 | 24.5264
3691 | 2025-02-11 | 2025 | 2025 | 2025-02-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.35208 | 0.35208 | 0.35486 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0025641 | O2-11 | 41.6361 |  | WTG Unscheduled Maintenance | 14989 | 41.6361
3692 | 2025-02-11 | 2025 | 2025 | 2025-02-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.42847 | 0.42847 | 0.43056 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2-11 | 31.2271 |  | WTG Unscheduled Maintenance | 14989 | 31.2271
3693 | 2025-02-11 | 2025 | 2025 | 2025-02-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Major BD | 0.44792 | 0.50139 | 0.78889 | 1.2833 | 6.9 | 8.1833 | Attend and check Related ckt so found QA 7.2 Grid filter contactor stuck so we remove all cable so found QA 7.2.4 AND 7.2.6 Cable born out also check QA 7.1 Contactor cable between capacitor to contactor , contactor to fuse found two nos cable burn then we taken all capacitor value found all normal then we have replace QA 7.2 CONTACTOR And two nos cable between contactor to fuse . then we perform a perform a precharge grid filter and GSC test found all value normal so we started the turbine | Close | 0.31474 | O2-21 | 4524.7014 |  | WTG Unscheduled Maintenance | 13270 | 4524.7014
3694 | 2025-02-11 | 2025 | 2025 | 2025-02-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 551 | Pitch motor current too high | Break down | 0.083333 | 0.13542 | 0.16319 | 1.25 | 0.66667 | 1.9167 | Attend and wtg check related circuit and found axis no 3 rectifier fuse faulty then replace fuse and manually pitching and check motor current found current is normal then reset and start wtg | Close | 0.073718 | O2-01 | 1486.8542 |  | WTG Unscheduled Maintenance | 18618 | 1486.8542
3695 | 2025-02-12 | 2025 | 2025 | 2025-02-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.018056 | 0.018056 | 0.03125 | 0 | 0.31667 | 0.31667 | Checked related error data log then reset & start WTG. | Close | 0.012179 | O2-05 | 251.6972 |  | WTG Unscheduled Maintenance | 19076 | 251.6972
3696 | 2025-02-12 | 2025 | 2025 | 2025-02-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.16667 | 0.16667 | 0.25694 | 0 | 2.1667 | 2.1667 | Attend and wtg apply Hard reebut then reset and start wtg | Close | 0.083333 | O2-09 | 1141.1111 |  | WTG Unscheduled Maintenance | 12640 | 1141.1111
3697 | 2025-02-12 | 2025 | 2025 | 2025-02-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.059722 | 0.059722 | 0.065972 | 0 | 0.15 | 0.15 | Checked related error data log then reset & start WTG. | Close | 0.0057692 | O2-07 | 91.125 |  | WTG Unscheduled Maintenance | 14580 | 91.125
3698 | 2025-02-12 | 2025 | 2025 | 2025-02-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR | 0.65 | 0.65 | 0.65278 | 0 | 0.066667 | 0.066667 | WTR674 Software upadeting work done after reset and start wtg | Close | 0.0025641 | O2-02 | 40.325 |  | WTG Breakdown Maintenance | 14517 | 40.325
3699 | 2025-02-12 | 2025 | 2025 | 2025-02-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR | 0.63264 | 0.63264 | 0.63472 | 0 | 0.05 | 0.05 | WTR674 Software upadeting work done after reset and start wtg | Close | 0.0019231 | O2-26 | 23.5646 |  | WTG Breakdown Maintenance | 11311 | 23.5646
3700 | 2025-02-12 | 2025 | 2025 | 2025-02-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR | 0.64028 | 0.64028 | 0.64306 | 0 | 0.066667 | 0.066667 | WTR674 Software upadeting work done after reset and start wtg | Close | 0.0025641 | O2-26 | 31.4194 |  | WTG Breakdown Maintenance | 11311 | 31.4194
3701 | 2025-02-12 | 2025 | 2025 | 2025-02-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR | 0.64444 | 0.64444 | 0.64653 | 0 | 0.05 | 0.05 | WTR674 Software upadeting work done after reset and start wtg | Close | 0.0019231 | O2-03 | 30.3583 |  | WTG Breakdown Maintenance | 14572 | 30.3583
3702 | 2025-02-12 | 2025 | 2025 | 2025-02-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR | 0.64792 | 0.64792 | 0.65069 | 0 | 0.066667 | 0.066667 | WTR674 Software upadeting work done after reset and start wtg | Close | 0.0025641 | O2-15 | 35.7806 |  | WTG Breakdown Maintenance | 12881 | 35.7806
3703 | 2025-02-12 | 2025 | 2025 | 2025-02-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.50556 | 0.50556 | 0.50972 | 0 | 0.1 | 0.1 | Checked related error data log then reset & start WTG. | Close | 0.0038462 | O2-12 | 59.0375 |  | WTG Unscheduled Maintenance | 14169 | 59.0375
3704 | 2025-02-12 | 2025 | 2025 | 2025-02-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR | 0.65139 | 0.65139 | 0.65278 | 0 | 0.033333 | 0.033333 | WTR674 Software upadeting work done after reset and start wtg | Close | 0.0012821 | O2-12 | 19.6792 |  | WTG Breakdown Maintenance | 14169 | 19.6792
3705 | 2025-02-12 | 2025 | 2025 | 2025-02-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.18889 | 0.18889 | 0.19306 | 0 | 0.1 | 0.1 | Checked related error data log then reset & start WTG. | Close | 0.0038462 | O2-14 | 44.775 |  | WTG Unscheduled Maintenance | 10746 | 44.775
3706 | 2025-02-12 | 2025 | 2025 | 2025-02-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR | 0.65417 | 0.65417 | 0.65764 | 0 | 0.083333 | 0.083333 | WTR674 Software upadeting work done after reset and start wtg | Close | 0.0032051 | O2-14 | 37.3125 |  | WTG Breakdown Maintenance | 10746 | 37.3125
3707 | 2025-02-12 | 2025 | 2025 | 2025-02-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.57917 | 0.57917 | 0.58125 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2-11 | 32.7417 |  | WTG Unscheduled Maintenance | 15716 | 32.7417
3708 | 2025-02-12 | 2025 | 2025 | 2025-02-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.50278 | 0.50278 | 0.51042 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & start WTG. | Close | 0.0070513 | O2-12 | 108.2354 |  | WTG Unscheduled Maintenance | 14169 | 108.2354
3709 | 2025-02-12 | 2025 | 2025 | 2025-02-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR | 0.57847 | 0.57847 | 0.64028 | 0 | 1.4833 | 1.4833 | Project Pending Work done then reset and start wtg | Close | 0.057051 | O2-05 | 1179.0028 |  | WTG Breakdown Maintenance | 19076 | 1179.0028
3710 | 2025-02-12 | 2025 | 2025 | 2025-02-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR | 0.65972 | 0.65972 | 0.66319 | 0 | 0.083333 | 0.083333 | WTR674 Software upadeting work done after reset and start wtg | Close | 0.0032051 | O2-10 | 47.4826 |  | WTG Breakdown Maintenance | 13675 | 47.4826
3711 | 2025-02-12 | 2025 | 2025 | 2025-02-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.49653 | 0.49653 | 0.53125 | 0 | 0.83333 | 0.83333 | Bottom Penal inspection work and coolant fill up work done after reset and start wtg | Close | 0.032051 | O2-21 | 378.8542 |  | WTG Breakdown Maintenance | 10911 | 378.8542
3712 | 2025-02-12 | 2025 | 2025 | 2025-02-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR | 0.6625 | 0.6625 | 0.66528 | 0 | 0.066667 | 0.066667 | WTR674 Software upadeting work done after reset and start wtg | Close | 0.0025641 | O2-21 | 30.3083 |  | WTG Breakdown Maintenance | 10911 | 30.3083
3713 | 2025-02-12 | 2025 | 2025 | 2025-02-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR | 0.66667 | 0.66667 | 0.66875 | 0 | 0.05 | 0.05 | WTR674 Software upadeting work done after reset and start wtg | Close | 0.0019231 | O2-06 | 22.9125 |  | WTG Breakdown Maintenance | 10998 | 22.9125
3714 | 2025-02-12 | 2025 | 2025 | 2025-02-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR | 0.67083 | 0.67083 | 0.67292 | 0 | 0.05 | 0.05 | WTR674 Software upadeting work done after reset and start wtg | Close | 0.0019231 | O2-07 | 30.375 |  | WTG Breakdown Maintenance | 14580 | 30.375
3715 | 2025-02-12 | 2025 | 2025 | 2025-02-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR | 0.67361 | 0.67361 | 0.67708 | 0 | 0.083333 | 0.083333 | WTR674 Software upadeting work done after reset and start wtg | Close | 0.0032051 | O2-24 | 59.941 |  | WTG Breakdown Maintenance | 17263 | 59.941
3716 | 2025-02-12 | 2025 | 2025 | 2025-02-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Blade cleaning work | 0.43472 | 0.43472 | 0.80208 | 0 | 8.8167 | 8.8167 | WTG manual stop for blade cleaning work. | Close | 0.3391 | O2-06 | 4040.2375 |  | WTG Breakdown Maintenance | 10998 | 4040.2375
3717 | 2025-02-12 | 2025 | 2025 | 2025-02-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR | 0.67639 | 0.67639 | 0.67847 | 0 | 0.05 | 0.05 | WTR674 Software upadeting work done after reset and start wtg | Close | 0.0019231 | O2-11 | 32.7417 |  | WTG Breakdown Maintenance | 15716 | 32.7417
3718 | 2025-02-12 | 2025 | 2025 | 2025-02-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR | 0.67917 | 0.67917 | 0.68125 | 0 | 0.05 | 0.05 | WTR674 Software upadeting work done after reset and start wtg | Close | 0.0019231 | O2-20 | 32.1896 |  | WTG Breakdown Maintenance | 15451 | 32.1896
3719 | 2025-02-12 | 2025 | 2025 | 2025-02-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR | 0.68194 | 0.68194 | 0.68472 | 0 | 0.066667 | 0.066667 | WTR674 Software upadeting work done after reset and start wtg | Close | 0.0025641 | O2-01 | 42.5222 |  | WTG Breakdown Maintenance | 15308 | 42.5222
3720 | 2025-02-13 | 2025 | 2025 | 2025-02-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.58542 | 0.58542 | 0.58819 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0025641 | O2-15 | 35.9667 |  | WTG Unscheduled Maintenance | 12948 | 35.9667
3721 | 2025-02-13 | 2025 | 2025 | 2025-02-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.44931 | 0.44931 | 0.46111 | 0 | 0.28333 | 0.28333 | Checked related error data log then reset & start WTG. | Close | 0.010897 | O2-11 | 167.7451 |  | WTG Unscheduled Maintenance | 14209 | 167.7451
3722 | 2025-02-13 | 2025 | 2025 | 2025-02-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.82222 | 0.82222 | 0.82431 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2-11 | 29.6021 |  | WTG Unscheduled Maintenance | 14209 | 29.6021
3723 | 2025-02-13 | 2025 | 2025 | 2025-02-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Blade cleaning work | 0.46875 | 0.46875 | 0.7125 | 0 | 5.85 | 5.85 | WTG manual stop for blade cleaning work. | Close | 0.225 | O2-06 | 2578.1438 |  | WTG Breakdown Maintenance | 10577 | 2578.1438
3724 | 2025-02-13 | 2025 | 2025 | 2025-02-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR | 0.60417 | 0.60417 | 0.70833 | 0 | 2.5 | 2.5 | Attend and WTR 655 & WTR 642 WORK Completed Than reset and start wtg. | Close | 0.096154 | O2-06 | 1101.7708 |  | WTG Breakdown Maintenance | 10577 | 1101.7708
3725 | 2025-02-13 | 2025 | 2025 | 2025-02-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Blade cleaning work | 0.73056 | 0.73056 | 0.86806 | 0 | 3.3 | 3.3 | WTG manual stop for blade cleaning work. | Close | 0.12692 | O2-11 | 1953.7375 |  | WTG Breakdown Maintenance | 14209 | 1953.7375
3726 | 2025-02-14 | 2025 | 2025 | 2025-02-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.0069444 | 0.0069444 | 0.034722 | 0 | 0.66667 | 0.66667 | Attend wtg coolant fillup after reset and start wtg | Close | 0.025641 | O2-14 | 180.3889 |  | WTG Breakdown Maintenance | 6494 | 180.3889
3727 | 2025-02-14 | 2025 | 2025 | 2025-02-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.065972 | 0.065972 | 0.09375 | 0 | 0.66667 | 0.66667 | Attend wtg coolant fillup after reset and start wtg | Close | 0.025641 | O2-22 | 168.3333 |  | WTG Breakdown Maintenance | 6060 | 168.3333
3728 | 2025-02-14 | 2025 | 2025 | 2025-02-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR | 0.49236 | 0.49236 | 0.63472 | 0 | 3.4167 | 3.4167 | Generator bearing inspection work and WTR Work | Close | 0.13141 | O2-24 | 945.4201 |  | WTG Breakdown Maintenance | 6641 | 945.4201
3729 | 2025-02-14 | 2025 | 2025 | 2025-02-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Blade cleaning work | 0.4375 | 0.4375 | 0.79722 | 0 | 8.6333 | 8.6333 | WTG manual stop for blade cleaning work. | Close | 0.33205 | O2-01 | 3210.1611 |  | WTG Breakdown Maintenance | 8924 | 3210.1611
3730 | 2025-02-14 | 2025 | 2025 | 2025-02-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.82083 | 0.82083 | 0.82292 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | O2-02 | 16.0854 |  | WTG Unscheduled Maintenance | 7721 | 16.0854
3731 | 2025-02-14 | 2025 | 2025 | 2025-02-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.35139 | 0.35139 | 0.35347 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2-11 | 14.6667 |  | WTG Unscheduled Maintenance | 7040 | 14.6667
3732 | 2025-02-14 | 2025 | 2025 | 2025-02-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 650 | Pitch controller communication error | Auto reset | 0.48403 | 0.48403 | 0.4875 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0032051 | O2-11 | 24.4444 |  | WTG Unscheduled Maintenance | 7040 | 24.4444
3733 | 2025-02-14 | 2025 | 2025 | 2025-02-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Break down | 0.078472 | 0.078472 | 0.090278 | 0 | 0.28333 | 0.28333 | Checked related error data log then reset & start WTG. | Close | 0.010897 | O2-22 | 71.5417 |  | WTG Unscheduled Maintenance | 6060 | 71.5417
3734 | 2025-02-15 | 2025 | 2025 | 2025-02-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Auto reset | 0.13333 | 0.13333 | 0.13542 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2-26 | 55.3021 |  | WTG Unscheduled Maintenance | 26545 | 55.3021
3735 | 2025-02-15 | 2025 | 2025 | 2025-02-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.051389 | 0.051389 | 0.05625 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & start WTG. | Close | 0.0044872 | O2-05 | 143.5778 |  | WTG Unscheduled Maintenance | 29536 | 143.5778
3736 | 2025-02-15 | 2025 | 2025 | 2025-02-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 650 | Pitch controller communication error | Auto reset | 0.097917 | 0.097917 | 0.10069 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0025641 | O2-05 | 82.0444 |  | WTG Unscheduled Maintenance | 29536 | 82.0444
3737 | 2025-02-15 | 2025 | 2025 | 2025-02-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 650 | Pitch controller communication error | Break down | 0.13889 | 0.13889 | 0.15208 | 0 | 0.31667 | 0.31667 | Checked related error data log then reset & start WTG. | Close | 0.012179 | O2-09 | 346.8556 |  | WTG Unscheduled Maintenance | 26288 | 346.8556
3738 | 2025-02-15 | 2025 | 2025 | 2025-02-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Break down | 0.12153 | 0.17361 | 0.19306 | 1.25 | 0.46667 | 1.7167 | Attend wtg And apply Hard reboot it after reset and start wtg | Close | 0.066026 | O2-02 | 1820.0243 |  | WTG Unscheduled Maintenance | 25445 | 1820.0243
3739 | 2025-02-15 | 2025 | 2025 | 2025-02-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.88194 | 0.925 | 0.94861 | 1.0333 | 0.56667 | 1.6 | Attend and wtg check communication cable and connection after tight all connection after trail so ok then start wtg | Close | 0.061538 | O2-02 | 1696.3333 |  | WTG Unscheduled Maintenance | 25445 | 1696.3333
3740 | 2025-02-15 | 2025 | 2025 | 2025-02-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.095139 | 0.095139 | 0.12639 | 0 | 0.75 | 0.75 | wtg manual stop for Bearing inspection and Reading work done after reset and start wtg | Close | 0.028846 | O2-21 | 880.3438 |  | WTG Breakdown Maintenance | 28171 | 880.3438
3741 | 2025-02-15 | 2025 | 2025 | 2025-02-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Break down | 0.13472 | 0.13472 | 0.14861 | 0 | 0.33333 | 0.33333 | Checked related error data log then reset & start WTG. | Close | 0.012821 | O2-26 | 368.6806 |  | WTG Unscheduled Maintenance | 26545 | 368.6806
3742 | 2025-02-15 | 2025 | 2025 | 2025-02-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.68889 | 0.71597 | 0.75 | 0.65 | 0.81667 | 1.4667 | Attend and check related circuit than check overvoltage protection circuit than check surge arrestor than found 24v feedback connection was loos so retight properly than reset and start wtg. | Close | 0.05641 | O2-03 | 1739.7111 |  | WTG Unscheduled Maintenance | 28468 | 1739.7111
3743 | 2025-02-15 | 2025 | 2025 | 2025-02-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 652 | Pitch controller initialisation error | Break down | 0.48403 | 0.48403 | 0.48958 | 0 | 0.13333 | 0.13333 | Auto reset | Close | 0.0051282 | O2-22 | 158.2278 |  | WTG Unscheduled Maintenance | 28481 | 158.2278
3744 | 2025-02-15 | 2025 | 2025 | 2025-02-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Break down | 0.11806 | 0.14236 | 0.16667 | 0.58333 | 0.58333 | 1.1667 | Attend wtg And apply Hard reboot it after reset and start wtg | Close | 0.044872 | O2-01 | 1532.8542 |  | WTG Unscheduled Maintenance | 31533 | 1532.8542
3745 | 2025-02-16 | 2025 | 2025 | 2025-02-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.38958 | 0.38958 | 0.82292 | 0 | 10.4 | 10.4 | WTG Stop for ladder replacment work for Project team | Close | 0.4 | O2-05 | 14243.2333 |  | WTG Breakdown Maintenance | 32869 | 14243.2333
3746 | 2025-02-16 | 2025 | 2025 | 2025-02-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 4273 | Overload cooling pump | Break down | 0.66111 | 0.68056 | 0.75 | 0.46667 | 1.6667 | 2.1333 | Attend and wtg check panel so found MPCB Tripped after charge then reset and start wtg | Close | 0.082051 | O2-26 | 2184 |  | WTG Unscheduled Maintenance | 24570 | 2184
3747 | 2025-02-17 | 2025 | 2025 | 2025-02-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 4273 | Overload cooling pump | Major BD | 0.33889 | 0.41667 | 0.82917 | 1.8667 | 9.9 | 11.7667 | Replace coolant motor after trail so ok then reset and start wrf | Close | 0.45256 | O2-26 | 8918.1528 |  | WTG Unscheduled Maintenance | 18190 | 8918.1528
3748 | 2025-02-17 | 2025 | 2025 | 2025-02-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Project pending work | 0.44514 | 0.44514 | 0.63681 | 0 | 4.6 | 4.6 | Ladder spicing & Reling replacment work | Close | 0.17692 | O2-05 | 5016.4917 |  | WTG Breakdown Maintenance | 26173 | 5016.4917
3749 | 2025-02-17 | 2025 | 2025 | 2025-02-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 650 | Pitch controller communication error | Break down | 0.80556 | 0.80556 | 0.80833 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0025641 | O2-11 | 55.9667 |  | WTG Unscheduled Maintenance | 20148 | 55.9667
3749 | 2025-02-18 | 2025 | 2025 | 2025-02-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.90625 | 0.96111 | 1899-12-31 | 1.3167 | 0.93333 | 2.25 | WTG restoration work WIP | open | 0.086538 | O2-15 | 1888.5 |  | WTG Unscheduled Maintenance | 20144 | 1888.5
3749 | 2025-02-19 | 2025 | 2025 | 2025-02-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Major BD | 0 | 0 | 0.30694 | 0 | 7.3667 | 7.3667 | WTG restoration work WIP | Close | 0.28333 | O2-09 | 7161.3208 |  | WTG Unscheduled Maintenance | 23331 | 7161.3208
3749 | 2025-02-19 | 2025 | 2025 | 2025-02-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Major BD | 0.32361 | 0.32361 | 0.80903 | 0 | 11.65 | 11.65 | attend and found SPD F2 (2nos),FA001 (2nos) and F5 (1nos) faulty so replace and start turbine at that time power supply pitch error occurred so check and found FA001 hub 400V supply MCB tripped and found R phase grounding so Attend and perform WTR 646 then reset and start turbine. | Close | 0.44808 | O2-09 | 11325.2563 |  | WTG Unscheduled Maintenance | 23331 | 11325.2563
3749 | 2025-02-19 | 2025 | 2025 | 2025-02-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.4375 | 0.4375 | 0.61458 | 0 | 4.25 | 4.25 | wtg stop for project pending work. | Close | 0.16346 | O2-05 | 3846.25 |  | WTG Breakdown Maintenance | 21720 | 3846.25
3749 | 2025-02-19 | 2025 | 2025 | 2025-02-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.54861 | 0.54861 | 0.74306 | 0 | 4.6667 | 4.6667 | wtg stop for sky lift TPI work. | Close | 0.17949 | O2-15 | 4211.8611 |  | WTG Breakdown Maintenance | 21661 | 4211.8611
3749 | 2025-02-19 | 2025 | 2025 | 2025-02-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.20208 | 0.20208 | 0.23333 | 0 | 0.75 | 0.75 | Checked related error data log then reset & start WTG. | Close | 0.028846 | O2-26 | 662.625 |  | WTG Unscheduled Maintenance | 21204 | 662.625
3749 | 2025-02-19 | 2025 | 2025 | 2025-02-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.15972 | 0.15972 | 0.18958 | 0 | 0.71667 | 0.71667 | Checked related error data log then reset & start WTG. | Close | 0.027564 | O2-05 | 648.5833 |  | WTG Unscheduled Maintenance | 21720 | 648.5833
3749 | 2025-02-19 | 2025 | 2025 | 2025-02-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.19583 | 0.19583 | 0.19931 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0032051 | O2-05 | 75.4167 |  | WTG Unscheduled Maintenance | 21720 | 75.4167
3749 | 2025-02-19 | 2025 | 2025 | 2025-02-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Break down | 0.33889 | 0.33889 | 0.35 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & start WTG. | Close | 0.010256 | O2-07 | 209.8111 |  | WTG Unscheduled Maintenance | 18883 | 209.8111
3749 | 2025-02-19 | 2025 | 2025 | 2025-02-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.83333 | 0.83333 | 0.84722 | 0 | 0.33333 | 0.33333 | Checked related error data log then reset & start WTG. | Close | 0.012821 | O2-04 | 317.2639 |  | WTG Unscheduled Maintenance | 22843 | 317.2639
3750 | 2025-02-20 | 2025 | 2025 | 2025-02-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.47917 | 0.47917 | 0.58333 | 0 | 2.5 | 2.5 | WTG manual stop for OMS audit work. | Close | 0.096154 | O2-05 | 2508.5417 |  | WTG Breakdown Maintenance | 24082 | 2508.5417
3751 | 2025-02-20 | 2025 | 2025 | 2025-02-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Break down | 0.40278 | 0.40278 | 0.42014 | 0 | 0.41667 | 0.41667 | Attend wtg And apply Hard reboot it after reset and start wtg | Close | 0.016026 | O2-02 | 356.9097 |  | WTG Unscheduled Maintenance | 20558 | 356.9097
3752 | 2025-02-20 | 2025 | 2025 | 2025-02-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD | 0.40972 | 0.40972 | 1899-12-31 | 0 | 14.1667 | 14.1667 | WTG manual stop for Blade repairing work.today skylift installing work and damage area surface grinding work done and first layer removing work complated. | Close | 0.54487 | O2-15 | 10503.9931 |  | WTG Breakdown Maintenance | 17795 | 10503.9931
3753 | 2025-02-21 | 2025 | 2025 | 2025-02-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.4875 | 0.4875 | 0.5625 | 0 | 1.8 | 1.8 | Attend and check ckt than found Blade-2 Chopper resistor faulty so replace it then reset and start wtg | Close | 0.069231 | O2-06 | 798.6 |  | WTG Breakdown Maintenance | 10648 | 798.6
3754 | 2025-02-21 | 2025 | 2025 | 2025-02-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD | 0 | 0 | 4:10 | 0 | 4.1667 | 4.1667 | today grinding work , Heating apply for Layer after first layer Completed work today. | open | 0.16026 | O2-15 | 2409.375 |  | WTG Breakdown Maintenance | 13878 | 2409.375
3755 | 2025-02-21 | 2025 | 2025 | 2025-02-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD | 0.18542 | 0.18542 | 24:00 | 0 | 19.5497 | 19.5497 | today grinding work , Heating apply for Layer after first layer Completed work today. | open | 0.75191 | O2-15 | 11304.6269 |  | WTG Breakdown Maintenance | 13878 | 11304.6269
3756 | 2025-02-21 | 2025 | 2025 | 2025-02-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 156 | SLC SF overspeed | Break down | 0.18542 | 0.18542 | 0.19792 | 0 | 0.3 | 0.3 | After grid resume and Checked related error data log then apply shoft reboot then reset & start WTG. | Close | 0.011538 | O2-01 | 179.8 |  | WTG Unscheduled Maintenance | 14384 | 179.8
3757 | 2025-02-22 | 2025 | 2025 | 2025-02-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD | 0 | 0 | 0.85556 | 0 | 20.5333 | 20.5333 | Today grinding work ,1 layer apply , Putty apply and Paint apply Completed work then Reset and Start wtg. | Close | 0.78974 | O2-15 | 5366.9 |  | WTG Breakdown Maintenance | 6273 | 5366.9
3758 | 2025-02-23 | 2025 | 2025 | 2025-02-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD | 0.42917 | 0.42917 | 1899-12-31 | 0 | 13.7 | 13.7 | WTG manual stop for Blade repairing work. | OPEN | 0.52692 | O2-07 | 4084.3125 |  | WTG Breakdown Maintenance | 7155 | 4084.3125
3759 | 2025-02-23 | 2025 | 2025 | 2025-02-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.84097 | 0.93542 | 1899-12-31 | 2.2667 | 1.55 | 3.8167 | WTG stop for vibration came from genarator DE bearing side so now WTG under breakdown WIP. | OPEN | 0.14679 | O2-24 | 1521.1007 |  | WTG Unscheduled Maintenance | 9565 | 1521.1007
3760 | 2025-02-23 | 2025 | 2025 | 2025-02-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.58194 | 0.58194 | 0.58958 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & start WTG. | Close | 0.0070513 | O2-01 | 93.0035 |  | WTG Unscheduled Maintenance | 12175 | 93.0035
3761 | 2025-02-23 | 2025 | 2025 | 2025-02-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.78403 | 0.78403 | 0.79097 | 0 | 0.16667 | 0.16667 | Checked related error data log then reset & start WTG. | Close | 0.0064103 | O2-01 | 84.5486 |  | WTG Unscheduled Maintenance | 12175 | 84.5486
3762 | 2025-02-24 | 2025 | 2025 | 2025-02-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD | 0 | 0 | 0.99999 | 0 | 23.9997 | 23.9997 | WTG manual stop for Blade repairing work.Today heating and grinding done, lamination and vaccum ream apply , champharing also done. | open | 0.92307 | O2-07 | 10137.8827 |  | WTG Breakdown Maintenance | 10138 | 10137.8827
3763 | 2025-02-24 | 2025 | 2025 | 2025-02-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD | 0 | 0 | 0.99999 | 0 | 23.9997 | 23.9997 | WTG stop for vibration came from genarator DE bearing side SO Generator Bearing replacement and restoration work WIP. | Close | 0.92307 | O2-24 | 10218.8817 |  | WTG Breakdown Maintenance | 10219 | 10218.8817
3764 | 2025-02-24 | 2025 | 2025 | 2025-02-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Connectivity issue | 0.97014 | 0.97014 | 0.98333 | 0 | 0.31667 | 0.31667 | after grid resume Checked related error data log then reset & start WTG.lat reset due to O2-13 VCB trip and no connectivity from SCADA. | Close | 0.012179 | O2-03 | 138.9639 |  | WTG Unscheduled Maintenance | 10532 | 138.9639
3765 | 2025-02-24 | 2025 | 2025 | 2025-02-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Connectivity issue | 0.97014 | 0.97014 | 0.98333 | 0 | 0.31667 | 0.31667 | after grid resume Checked related error data log then reset & start WTG.lat reset due to O2-13 VCB trip and no connectivity from SCADA. | Close | 0.012179 | O2-11 | 101.2674 |  | WTG Unscheduled Maintenance | 7675 | 101.2674
3766 | 2025-02-25 | 2025 | 2025 | 2025-02-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD | 0 | 0 | 0.62153 | 0 | 14.9167 | 14.9167 | Blade repairing work done and start wtg. | Close | 0.57372 | O2-04 | 13751.9236 |  | WTG Breakdown Maintenance | 22126 | 13751.9236
3767 | 2025-02-25 | 2025 | 2025 | 2025-02-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD | 0 | 0 | 0.99999 | 0 | 23.9997 | 23.9997 | generator bearing replacement work done. Take trial time genarator encoder related error occurs so check encoder and found encoder is faulty so now material arrangement from other site WIP. | open | 0.92307 | O2-20 | 24135.7206 |  | WTG Breakdown Maintenance | 24136 | 24135.7206
3768 | 2025-02-25 | 2025 | 2025 | 2025-02-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Connectivity issue | 0.0375 | 0.0375 | 0.059722 | 0 | 0.53333 | 0.53333 | after grid resume Checked related error data log then reset & start WTG.lat reset due to O2-08 VCB trip and no connectivity from SCADA. | Close | 0.020513 | O2-09 | 484.4889 |  | WTG Unscheduled Maintenance | 21802 | 484.4889
3769 | 2025-02-25 | 2025 | 2025 | 2025-02-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Connectivity issue | 0.0375 | 0.0375 | 0.059722 | 0 | 0.53333 | 0.53333 | after grid resume Checked related error data log then reset & start WTG.lat reset due to O2-08 VCB trip and no connectivity from SCADA. | Close | 0.020513 | O2-23 | 407.7556 |  | WTG Unscheduled Maintenance | 18349 | 407.7556
3770 | 2025-02-26 | 2025 | 2025 | 2025-02-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 660 | Limit switches error 91° | Break down | 0.036806 | 0.036806 | 0.064583 | 0 | 0.66667 | 0.66667 | after grid resume Checked related error data log WIP | Close | 0.025641 | O2-26 | 131.6389 |  | WTG Unscheduled Maintenance | 4739 | 131.6389
3771 | 2025-02-26 | 2025 | 2025 | 2025-02-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 660 | Limit switches error 91° | Break down | 0.10903 | 0.10903 | 0.11458 | 0 | 0.13333 | 0.13333 | after grid resume Checked related error data log then reset & start WTG. | Close | 0.0051282 | O2-26 | 26.3278 |  | WTG Unscheduled Maintenance | 4739 | 26.3278
3772 | 2025-02-26 | 2025 | 2025 | 2025-02-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD | 0 | 0.375 | 0.48958 | 9 | 2.75 | 11.75 | genarator encoder material arrangement from other site then after replace it then start WTG. | Close | 0.45192 | O2-24 | 7800.5312 |  | WTG Breakdown Maintenance | 15933 | 7800.5312
3773 | 2025-02-26 | 2025 | 2025 | 2025-02-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.10903 | 0.10903 | 0.12847 | 0 | 0.46667 | 0.46667 | after grid resume Checked related error data log then reset & start WTG.lat reset due to O2-13 VCB trip and no connectivity from SCADA. | Close | 0.017949 | O2-03 | 113.5944 |  | WTG Unscheduled Maintenance | 5842 | 113.5944
3774 | 2025-02-26 | 2025 | 2025 | 2025-02-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.10903 | 0.10903 | 0.12847 | 0 | 0.46667 | 0.46667 | after grid resume Checked related error data log then reset & start WTG.lat reset due to O2-13 VCB trip and no connectivity from SCADA. | Close | 0.017949 | O2-12 | 114.6444 |  | WTG Unscheduled Maintenance | 5896 | 114.6444
3775 | 2025-02-26 | 2025 | 2025 | 2025-02-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.10903 | 0.10903 | 0.12847 | 0 | 0.46667 | 0.46667 | after grid resume Checked related error data log then reset & start WTG.lat reset due to O2-13 VCB trip and no connectivity from SCADA. | Close | 0.017949 | O2-14 | 77.7778 |  | WTG Unscheduled Maintenance | 4000 | 77.7778
3776 | 2025-02-26 | 2025 | 2025 | 2025-02-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.10903 | 0.10903 | 0.12847 | 0 | 0.46667 | 0.46667 | after grid resume Checked related error data log then reset & start WTG.lat reset due to O2-13 VCB trip and no connectivity from SCADA. | Close | 0.017949 | O2-11 | 114.1194 |  | WTG Unscheduled Maintenance | 5869 | 114.1194
3777 | 2025-02-26 | 2025 | 2025 | 2025-02-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD | 0.35556 | 0.35556 | 0.85069 | 0 | 11.8833 | 11.8833 | Blade repairing work.Today apply pest than grinding work ,Heating work, Heating apply Completed work today. | OPEN | 0.45705 | O2-06 | 10596.9625 |  | WTG Breakdown Maintenance | 21402 | 10596.9625
3778 | 2025-02-26 | 2025 | 2025 | 2025-02-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD | 0.87361 | 0.87361 | 0.95903 | 0 | 2.05 | 2.05 | Blade repairing work.Today apply pest than grinding work ,Heating work, Heating apply Completed work today. | OPEN | 0.078846 | O2-06 | 1828.0875 |  | WTG Breakdown Maintenance | 21402 | 1828.0875
3779 | 2025-02-26 | 2025 | 2025 | 2025-02-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 5550 | Low hydraulic oil level | Break down | 0.6125 | 0.64583 | 0.74097 | 0.8 | 2.2833 | 3.0833 | Attend and Wtg check Oil level so oil level law After Oil top and Check all Pipe so ok after trail then Reset and Start wtg. | Close | 0.11859 | O2-20 | 310.9028 |  | WTG Unscheduled Maintenance | 2420 | 310.9028
3780 | 2025-02-26 | 2025 | 2025 | 2025-02-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.87361 | 0.87361 | 0.94097 | 0 | 1.6167 | 1.6167 | After grid resume and Checked related error data log then apply hard reboot then reset & start WTG. | Close | 0.062179 | O2-12 | 397.1611 |  | WTG Unscheduled Maintenance | 5896 | 397.1611
3781 | 2025-02-26 | 2025 | 2025 | 2025-02-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.87361 | 0.87361 | 0.95278 | 0 | 1.9 | 1.9 | After grid resume and Checked related error data log then apply hard reboot then reset & start WTG. | Close | 0.073077 | O2-10 | 618.3708 |  | WTG Unscheduled Maintenance | 7811 | 618.3708
3782 | 2025-02-27 | 2025 | 2025 | 2025-02-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD | 0 | 0 | 0.79167 | 0 | 19 | 19 | Blade repairing work.Today 1 Layer Apply ,Heating Completed , Lamination Completed,Paint apply and work completed then Reset and start wtg. | Close | 0.73077 | O2-06 | 8986.2083 |  | WTG Breakdown Maintenance | 11351 | 8986.2083
3783 | 2025-02-27 | 2025 | 2025 | 2025-02-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.1625 | 0.1625 | 0.21389 | 0 | 1.2333 | 1.2333 | After grid resume and Checked related error data log then apply hard reboot then reset & start WTG. | Close | 0.047436 | O2-10 | 461.8833 |  | WTG Unscheduled Maintenance | 8988 | 461.8833
3784 | 2025-02-27 | 2025 | 2025 | 2025-02-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.47222 | 0.47222 | 0.56458 | 0 | 2.2167 | 2.2167 | wtg Manual stop for Project Pending work | Close | 0.085256 | O2-05 | 891.0076 |  | WTG Breakdown Maintenance | 9647 | 891.0076
3785 | 2025-02-28 | 2025 | 2025 | 2025-02-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.77361 | 0.77361 | 0.82639 | 0 | 1.2667 | 1.2667 | After Grid charge RFO signal coming than Start WTG. | Close | 0.048718 | O2-05 | 825.8139 |  | WTG Unscheduled Maintenance | 15647 | 825.8139
3786 | 2025-02-28 | 2025 | 2025 | 2025-02-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.2875 | 0.3125 | 0.33194 | 0.6 | 0.46667 | 1.0667 | After grid resume and Checked related error data log then apply hard reboot then reset & start WTG. | Close | 0.041026 | O2-09 | 584.6667 |  | WTG Unscheduled Maintenance | 13155 | 584.6667
3787 | 2025-02-28 | 2025 | 2025 | 2025-02-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.77361 | 0.77361 | 0.825 | 0 | 1.2333 | 1.2333 | After Grid charge RFO signal coming than Start WTG. | Close | 0.047436 | O2-09 | 676.0208 |  | WTG Unscheduled Maintenance | 13155 | 676.0208
3788 | 2025-02-28 | 2025 | 2025 | 2025-02-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.77083 | 0.77083 | 0.825 | 0 | 1.3 | 1.3 | After Grid charge RFO signal coming than Start WTG. | Close | 0.05 | O2-07 | 1068.5458 |  | WTG Unscheduled Maintenance | 19727 | 1068.5458
3789 | 2025-02-28 | 2025 | 2025 | 2025-02-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.77083 | 0.77083 | 0.79097 | 0 | 0.48333 | 0.48333 | After Grid charge RFO signal coming than Start WTG. | Close | 0.01859 | O2-21 | 369.7299 |  | WTG Unscheduled Maintenance | 18359 | 369.7299
3790 | 2025-02-28 | 2025 | 2025 | 2025-02-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.24167 | 0.24167 | 0.24931 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & start WTG. | Close | 0.0070513 | O2-26 | 71.7674 |  | WTG Unscheduled Maintenance | 9395 | 71.7674
3791 | 2025-02-28 | 2025 | 2025 | 2025-02-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.090278 | 0.13542 | 0.16667 | 1.0833 | 0.75 | 1.8333 | Attend and check wtg in converter error so check data from SAM and found Fan error so attend ansd check error related ckt than check feedback connection and also K14 relay relay than check connector than nothing abnormal found so check Fan remove and check manually rotation than wip, | Close | 0.070513 | O2-15 | 1077.7708 |  | WTG Unscheduled Maintenance | 14109 | 1077.7708
3792 | 2025-02-28 | 2025 | 2025 | 2025-02-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.19236 | 0.19236 | 0.25 | 0 | 1.3833 | 1.3833 | After Grid resume check manually Fan rotation than abnormal sound comes from Fan so replace with new fan than reset and take trial than start WTG. | Close | 0.053205 | O2-15 | 813.2271 |  | WTG Unscheduled Maintenance | 14109 | 813.2271
3793 | 2025-02-28 | 2025 | 2025 | 2025-02-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.77361 | 0.81111 | 0.85417 | 0.9 | 1.0333 | 1.9333 | Turbine stop for attend Service Generator brush so check and found Erthing Brush wear out so replace it than reset and start WTG. | Close | 0.074359 | O2-12 | 1255.2972 |  | WTG Breakdown Maintenance | 15583 | 1255.2972
3794 | 2025-02-28 | 2025 | 2025 | 2025-02-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.77361 | 0.77361 | 0.82639 | 0 | 1.2667 | 1.2667 | After Grid charge RFO signal coming than Start WTG. | Close | 0.048718 | O2-14 | 690.2806 |  | WTG Unscheduled Maintenance | 13079 | 690.2806
3795 | 2025-02-28 | 2025 | 2025 | 2025-02-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.77361 | 0.78472 | 0.79653 | 0.26667 | 0.28333 | 0.55 | After grid resume and Checked related error data log then apply hard reboot then reset & start WTG. | Close | 0.021154 | O2-12 | 357.1104 |  | WTG Unscheduled Maintenance | 15583 | 357.1104
3796 | 2025-02-28 | 2025 | 2025 | 2025-02-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.77083 | 0.77083 | 0.82222 | 0 | 1.2333 | 1.2333 | After Grid charge RFO signal coming than Start WTG. | Close | 0.047436 | O2-06 | 917.5486 |  | WTG Unscheduled Maintenance | 17855 | 917.5486
3797 | 2025-02-28 | 2025 | 2025 | 2025-02-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.77083 | 0.77083 | 0.82292 | 0 | 1.25 | 1.25 | After Grid charge RFO signal coming than Start WTG. | Close | 0.048077 | O2-06 | 929.9479 |  | WTG Unscheduled Maintenance | 17855 | 929.9479
3798 | 2025-02-28 | 2025 | 2025 | 2025-02-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.77083 | 0.77083 | 0.825 | 0 | 1.3 | 1.3 | After Grid charge RFO signal coming than Start WTG. | Close | 0.05 | O2-06 | 967.1458 |  | WTG Unscheduled Maintenance | 17855 | 967.1458
3799 | 2025-02-28 | 2025 | 2025 | 2025-02-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.77361 | 0.77361 | 0.82569 | 0 | 1.25 | 1.25 | After Grid charge RFO signal coming than Start WTG. | Close | 0.048077 | O2-11 | 723.6458 |  | WTG Unscheduled Maintenance | 13894 | 723.6458
3800 | 2025-02-28 | 2025 | 2025 | 2025-02-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down | 0.77708 | 0.77708 | 0.77917 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | O2-20 | 42.0292 |  | WTG Unscheduled Maintenance | 20174 | 42.0292
3801 | 2025-02-28 | 2025 | 2025 | 2025-02-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 2340 | Temp. rot.br.pad implaus. | Break down | 0.13056 | 0.13056 | 0.16667 | 0 | 0.86667 | 0.86667 | Checked related error data log then check in sam temprature data than grid down so wip, | Close | 0.033333 | O2-01 | 540.5472 |  | WTG Unscheduled Maintenance | 14969 | 540.5472
3802 | 2025-02-28 | 2025 | 2025 | 2025-02-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 2340 | Temp. rot.br.pad implaus. | Break down | 0.19236 | 0.19236 | 0.21319 | 0 | 0.5 | 0.5 | After Grid resume than check temprature and apply soft reboot than reset and start WTG. | Close | 0.019231 | O2-01 | 311.8542 |  | WTG Unscheduled Maintenance | 14969 | 311.8542
3803 | 2025-02-28 | 2025 | 2025 | 2025-02-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.77361 | 0.77361 | 0.82569 | 0 | 1.25 | 1.25 | After Grid charge RFO signal coming than Start WTG. | Close | 0.048077 | O2-01 | 779.6354 |  | WTG Unscheduled Maintenance | 14969 | 779.6354
3804 | 2025-03-01 | 2025 | 2025 | 2025-03-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.34306 | 0.34306 | 0.35069 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & start WTG. | Close | 0.0070513 | O2-26 | 112.9486 |  | WTG Unscheduled Maintenance | 14786 | 112.9486
3805 | 2025-03-01 | 2025 | 2025 | 2025-03-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down | 0.17361 | 0.17361 | 0.17639 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & start WTG. | Close | 0.0025641 | O2-02 | 63.2611 |  | WTG Unscheduled Maintenance | 22774 | 63.2611
3806 | 2025-03-01 | 2025 | 2025 | 2025-03-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down | 0.35833 | 0.35833 | 0.36111 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & start WTG. | Close | 0.0025641 | O2-02 | 63.2611 |  | WTG Unscheduled Maintenance | 22774 | 63.2611
3807 | 2025-03-01 | 2025 | 2025 | 2025-03-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.31319 | 0.31319 | 0.31806 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & start WTG. | Close | 0.0044872 | O2-26 | 71.8764 |  | WTG Unscheduled Maintenance | 14786 | 71.8764
3808 | 2025-03-01 | 2025 | 2025 | 2025-03-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 550 | Pitch current asymmetry | Major BD | 0.076389 | 0.12153 | 0.34444 | 1.0833 | 5.35 | 6.4333 | Attend and check error related ckt than found Axis-3 Chopper resistor faulty so arrange it than replace it after fault clear Overload axis-3 error occurred so check ckt than found loose connection of pitch motor brake supply so retight it than reset and start WTG. | Close | 0.24744 | O2-22 | 6732.7514 |  | WTG Unscheduled Maintenance | 25117 | 6732.7514
3809 | 2025-03-01 | 2025 | 2025 | 2025-03-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD | 0.42639 | 0.42639 | 1899-12-31 | 0 | 13.7667 | 13.7667 | Blade Repairing work WIP,(Today SKY Lift Installed complated,Grinding Completed,Paint remove Defect Cutting done and Pest Apply) | Close | 0.52949 | O2-06 | 13867.0486 |  | WTG Breakdown Maintenance | 24175 | 13867.0486
3810 | 2025-03-02 | 2025 | 2025 | 2025-03-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.14722 | 0.14722 | 0.15486 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & start WTG. | Close | 0.0070513 | O2-26 | 68.2688 |  | WTG Unscheduled Maintenance | 8937 | 68.2688
3811 | 2025-03-02 | 2025 | 2025 | 2025-03-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.92847 | 0.92847 | 0.95694 | 0 | 0.68333 | 0.68333 | After grid resume and Checked related error data log then apply hard reboot then reset & start WTG. | Close | 0.026282 | O2-09 | 348.8986 |  | WTG Unscheduled Maintenance | 12254 | 348.8986
3812 | 2025-03-02 | 2025 | 2025 | 2025-03-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.92847 | 0.92847 | 0.97222 | 0 | 1.05 | 1.05 | After grid resume and Checked related error data log then apply hard reboot then reset & start WTG. | Close | 0.040385 | O2-12 | 563.675 |  | WTG Unscheduled Maintenance | 12884 | 563.675
3813 | 2025-03-02 | 2025 | 2025 | 2025-03-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.1125 | 0.1125 | 0.14653 | 0 | 0.81667 | 0.81667 | After grid resume and Checked related error data log then apply hard reboot then reset & start WTG. | Close | 0.03141 | O2-12 | 438.4139 |  | WTG Unscheduled Maintenance | 12884 | 438.4139
3814 | 2025-03-02 | 2025 | 2025 | 2025-03-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.31111 | 0.31111 | 0.36111 | 0 | 1.2 | 1.2 | After grid resume and Checked related error data log then apply hard reboot then reset & start WTG. | Close | 0.046154 | O2-10 | 591.7 |  | WTG Unscheduled Maintenance | 11834 | 591.7
3815 | 2025-03-02 | 2025 | 2025 | 2025-03-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD | 0 | 0.32639 | 0.45069 | 7.8333 | 2.9833 | 10.8167 | Blade repairing work wip,(Today 2 leyar Complated,pest level,pest heating,vaccume copmpleted, after putty apply ,putty shedding completed,paint apply) | Close | 0.41603 | O2-06 | 6042.9111 |  | WTG Breakdown Maintenance | 13408 | 6042.9111
3816 | 2025-03-02 | 2025 | 2025 | 2025-03-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD | 0.47569 | 0.47569 | 0.79167 | 0 | 7.5833 | 7.5833 | After grid resume Blade repairing work done then start WTG.(Today 2 leyar Complated,pest level,pest heating,vaccume copmpleted, after putty apply ,putty shedding completed,paint apply) | Close | 0.29167 | O2-06 | 4236.5556 |  | WTG Breakdown Maintenance | 13408 | 4236.5556
3817 | 2025-03-02 | 2025 | 2025 | 2025-03-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down | 0.54583 | 0.54583 | 0.54792 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | O2-20 | 33.7938 |  | WTG Unscheduled Maintenance | 16221 | 33.7938
3818 | 2025-03-03 | 2025 | 2025 | 2025-03-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.081944 | 0.081944 | 0.089583 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & start WTG. | Close | 0.0070513 | O2-26 | 90.9257 |  | WTG Unscheduled Maintenance | 11903 | 90.9257
3819 | 2025-03-03 | 2025 | 2025 | 2025-03-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.12569 | 0.12569 | 0.13333 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & start WTG. | Close | 0.0070513 | O2-26 | 90.9257 |  | WTG Unscheduled Maintenance | 11903 | 90.9257
3820 | 2025-03-03 | 2025 | 2025 | 2025-03-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.47917 | 0.47917 | 0.60417 | 0 | 3 | 3 | WTG Manual stop for Generator Slipring Inspection work done than WIP, | Close | 0.11538 | O2-12 | 2938.875 |  | WTG Breakdown Maintenance | 23511 | 2938.875
3821 | 2025-03-03 | 2025 | 2025 | 2025-03-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.60417 | 0.60417 | 0.67014 | 0 | 1.5833 | 1.5833 | After Customer Audit done than reset and start WTG. | Close | 0.060897 | O2-12 | 1551.0729 |  | WTG Breakdown Maintenance | 23511 | 1551.0729
3822 | 2025-03-03 | 2025 | 2025 | 2025-03-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.25208 | 0.25208 | 0.25278 | 0 | 0.016667 | 0.016667 | Checked related error data log then reset & start WTG. | Close | 0.00064103 | O2-22 | 12.5854 |  | WTG Unscheduled Maintenance | 18123 | 12.5854
3823 | 2025-03-03 | 2025 | 2025 | 2025-03-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 172 | SLC MF torque protection | Break down | 0.024306 | 0.024306 | 0.028472 | 0 | 0.1 | 0.1 | Checked related error data log then reset & start WTG. | Close | 0.0038462 | O2-01 | 90.325 |  | WTG Unscheduled Maintenance | 21678 | 90.325
3824 | 2025-03-03 | 2025 | 2025 | 2025-03-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.24167 | 0.24167 | 0.25069 | 0 | 0.21667 | 0.21667 | Checked related error data log then reset & start WTG. | Close | 0.0083333 | O2-01 | 195.7042 |  | WTG Unscheduled Maintenance | 21678 | 195.7042
3825 | 2025-03-04 | 2025 | 2025 | 2025-03-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 305 | Brake control | Break down | 0.25417 | 0.25417 | 0.32014 | 0 | 1.5833 | 1.5833 | After grid resume and Checked related error data log then apply hard reboot then reset & start WTG. | Close | 0.060897 | O2-26 | 2244.375 |  | WTG Unscheduled Maintenance | 34020 | 2244.375
3826 | 2025-03-04 | 2025 | 2025 | 2025-03-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.48681 | 0.48681 | 0.49514 | 0 | 0.2 | 0.2 | Turbine unexpectedly stop through PPC after problem solve then reset and start WTG. | Close | 0.0076923 | O2-26 | 283.5 |  | WTG Breakdown Maintenance | 34020 | 283.5
3827 | 2025-03-04 | 2025 | 2025 | 2025-03-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.48681 | 0.48681 | 0.49514 | 0 | 0.2 | 0.2 | Turbine unexpectedly stop through PPC after problem solve then reset and start WTG. | Close | 0.0076923 | O2-05 | 353.1583 |  | WTG Breakdown Maintenance | 42379 | 353.1583
3828 | 2025-03-04 | 2025 | 2025 | 2025-03-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.53264 | 0.53264 | 0.53611 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & start WTG. | Close | 0.0032051 | O2-05 | 147.1493 |  | WTG Unscheduled Maintenance | 42379 | 147.1493
3829 | 2025-03-04 | 2025 | 2025 | 2025-03-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.25417 | 0.25417 | 0.34583 | 0 | 2.2 | 2.2 | After grid resume and Checked related error data log then apply hard reboot then reset & start WTG. | Close | 0.084615 | O2-09 | 2887.0417 |  | WTG Unscheduled Maintenance | 31495 | 2887.0417
3830 | 2025-03-04 | 2025 | 2025 | 2025-03-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.48681 | 0.48681 | 0.49514 | 0 | 0.2 | 0.2 | Turbine unexpectedly stop through PPC after problem solve then reset and start WTG. | Close | 0.0076923 | O2-07 | 412.4583 |  | WTG Breakdown Maintenance | 49495 | 412.4583
3831 | 2025-03-04 | 2025 | 2025 | 2025-03-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.48681 | 0.48681 | 0.49514 | 0 | 0.2 | 0.2 | Turbine unexpectedly stop through PPC after problem solve then reset and start WTG. | Close | 0.0076923 | O2-02 | 298.2 |  | WTG Breakdown Maintenance | 35784 | 298.2
3832 | 2025-03-04 | 2025 | 2025 | 2025-03-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.66875 | 0.66875 | 0.67292 | 0 | 0.1 | 0.1 | Checked related error data log then reset & start WTG. | Close | 0.0038462 | O2-02 | 149.1 |  | WTG Unscheduled Maintenance | 35784 | 149.1
3833 | 2025-03-04 | 2025 | 2025 | 2025-03-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.48681 | 0.48681 | 0.49653 | 0 | 0.23333 | 0.23333 | Turbine unexpectedly stop through PPC after problem solve then reset and start WTG. | Close | 0.0089744 | O2-21 | 411.9694 |  | WTG Breakdown Maintenance | 42374 | 411.9694
3834 | 2025-03-04 | 2025 | 2025 | 2025-03-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.48681 | 0.48681 | 0.49653 | 0 | 0.23333 | 0.23333 | Turbine unexpectedly stop through PPC after problem solve then reset and start WTG. | Close | 0.0089744 | O2-04 | 476.5542 |  | WTG Breakdown Maintenance | 49017 | 476.5542
3835 | 2025-03-04 | 2025 | 2025 | 2025-03-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.44653 | 0.44653 | 0.46944 | 0 | 0.55 | 0.55 | Checked related error data log then reset & start WTG. | Close | 0.021154 | O2-26 | 779.625 |  | WTG Unscheduled Maintenance | 34020 | 779.625
3836 | 2025-03-04 | 2025 | 2025 | 2025-03-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.48681 | 0.48681 | 0.49792 | 0 | 0.26667 | 0.26667 | Turbine unexpectedly stop through PPC after problem solve then reset and start WTG. | Close | 0.010256 | O2-26 | 378 |  | WTG Breakdown Maintenance | 34020 | 378
3837 | 2025-03-04 | 2025 | 2025 | 2025-03-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.42639 | 0.42639 | 0.45972 | 0 | 0.8 | 0.8 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.030769 | O2-03 | 1064.1 |  | WTG Breakdown Maintenance | 31923 | 1064.1
3838 | 2025-03-04 | 2025 | 2025 | 2025-03-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.48681 | 0.48681 | 0.49792 | 0 | 0.26667 | 0.26667 | Turbine unexpectedly stop through PPC after problem solve then reset and start WTG. | Close | 0.010256 | O2-03 | 354.7 |  | WTG Breakdown Maintenance | 31923 | 354.7
3839 | 2025-03-04 | 2025 | 2025 | 2025-03-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Break down | 0.42639 | 0.42639 | 0.46806 | 0 | 1 | 1 | Checked related error data log then apply hard reboot then reset & start WTG. | Close | 0.038462 | O2-15 | 1447.125 |  | WTG Unscheduled Maintenance | 34731 | 1447.125
3840 | 2025-03-04 | 2025 | 2025 | 2025-03-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.48681 | 0.48681 | 0.53125 | 0 | 1.0667 | 1.0667 | Turbine unexpectedly stop through PPC after problem solve then reset and start WTG. | Close | 0.041026 | O2-15 | 1543.6 |  | WTG Breakdown Maintenance | 34731 | 1543.6
3841 | 2025-03-04 | 2025 | 2025 | 2025-03-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.41597 | 0.41597 | 0.46111 | 0 | 1.0833 | 1.0833 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.041667 | O2-12 | 1754.5035 |  | WTG Breakdown Maintenance | 38869 | 1754.5035
3842 | 2025-03-04 | 2025 | 2025 | 2025-03-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.46111 | 0.46111 | 0.57639 | 0 | 2.7667 | 2.7667 | Turbine stop for YPM work but suddenly wind increase so unable to material taken from winch after that YPM Cancel and Start Turbine. | Close | 0.10641 | O2-12 | 4480.7319 |  | WTG Breakdown Maintenance | 38869 | 4480.7319
3843 | 2025-03-04 | 2025 | 2025 | 2025-03-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.48681 | 0.48681 | 0.49931 | 0 | 0.3 | 0.3 | Turbine unexpectedly stop through PPC after problem solve then reset and start WTG. | Close | 0.011538 | O2-14 | 352.3625 |  | WTG Breakdown Maintenance | 28189 | 352.3625
3844 | 2025-03-04 | 2025 | 2025 | 2025-03-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.41528 | 0.41528 | 0.45694 | 0 | 1 | 1 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.038462 | O2-11 | 1283.25 |  | WTG Breakdown Maintenance | 30798 | 1283.25
3845 | 2025-03-04 | 2025 | 2025 | 2025-03-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.48681 | 0.48681 | 0.5 | 0 | 0.31667 | 0.31667 | Turbine unexpectedly stop through PPC after problem solve then reset and start WTG. | Close | 0.012179 | O2-11 | 406.3625 |  | WTG Breakdown Maintenance | 30798 | 406.3625
3846 | 2025-03-04 | 2025 | 2025 | 2025-03-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.61597 | 0.61597 | 0.62014 | 0 | 0.1 | 0.1 | Checked related error data log then reset & start WTG. | Close | 0.0038462 | O2-11 | 128.325 |  | WTG Unscheduled Maintenance | 30798 | 128.325
3847 | 2025-03-04 | 2025 | 2025 | 2025-03-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.12917 | 0.12917 | 0.15833 | 0 | 0.7 | 0.7 | After grid resume and Checked related error data log then apply hard reboot then reset & start WTG. | Close | 0.026923 | O2-12 | 1133.6792 |  | WTG Unscheduled Maintenance | 38869 | 1133.6792
3848 | 2025-03-04 | 2025 | 2025 | 2025-03-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.25417 | 0.25417 | 0.28819 | 0 | 0.81667 | 0.81667 | After grid resume and Checked related error data log then apply hard reboot then reset & start WTG. | Close | 0.03141 | O2-12 | 1322.6257 |  | WTG Unscheduled Maintenance | 38869 | 1322.6257
3849 | 2025-03-04 | 2025 | 2025 | 2025-03-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.48681 | 0.48681 | 0.57014 | 0 | 2 | 2 | Turbine unexpectedly stop through PPC after problem solve then reset and start WTG. | Close | 0.076923 | O2-12 | 3239.0833 |  | WTG Breakdown Maintenance | 38869 | 3239.0833
3850 | 2025-03-04 | 2025 | 2025 | 2025-03-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.48681 | 0.48681 | 0.54375 | 0 | 1.3667 | 1.3667 | Turbine unexpectedly stop through PPC after problem solve then reset and start WTG. | Close | 0.052564 | O2-10 | 1968.1708 |  | WTG Breakdown Maintenance | 34563 | 1968.1708
3851 | 2025-03-04 | 2025 | 2025 | 2025-03-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.48681 | 0.48681 | 0.59167 | 0 | 2.5167 | 2.5167 | Turbine unexpectedly stop through PPC after problem solve then reset and start WTG. | Close | 0.096795 | O2-21 | 4443.3847 |  | WTG Breakdown Maintenance | 42374 | 4443.3847
3852 | 2025-03-04 | 2025 | 2025 | 2025-03-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 657 | Error pitch converter 2 | Break down | 0.19097 | 0.19097 | 0.20417 | 0 | 0.31667 | 0.31667 | Checked related error data log then reset & start WTG. | Close | 0.012179 | O2-22 | 682.0604 |  | WTG Unscheduled Maintenance | 51693 | 682.0604
3853 | 2025-03-04 | 2025 | 2025 | 2025-03-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.48681 | 0.48681 | 0.50764 | 0 | 0.5 | 0.5 | Turbine unexpectedly stop through PPC after problem solve then reset and start WTG. | Close | 0.019231 | O2-22 | 1076.9375 |  | WTG Breakdown Maintenance | 51693 | 1076.9375
3854 | 2025-03-04 | 2025 | 2025 | 2025-03-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.48681 | 0.48681 | 0.56111 | 0 | 1.7833 | 1.7833 | Turbine unexpectedly stop through PPC after problem solve then reset and start WTG. | Close | 0.06859 | O2-06 | 3362.1035 |  | WTG Breakdown Maintenance | 45247 | 3362.1035
3855 | 2025-03-04 | 2025 | 2025 | 2025-03-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.48681 | 0.48681 | 0.51042 | 0 | 0.56667 | 0.56667 | Turbine unexpectedly stop through PPC after problem solve then reset and start WTG. | Close | 0.021795 | O2-07 | 1168.6319 |  | WTG Breakdown Maintenance | 49495 | 1168.6319
3856 | 2025-03-04 | 2025 | 2025 | 2025-03-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.48681 | 0.48681 | 0.51042 | 0 | 0.56667 | 0.56667 | Turbine unexpectedly stop through PPC after problem solve then reset and start WTG. | Close | 0.021795 | O2-24 | 1048.6639 |  | WTG Breakdown Maintenance | 44414 | 1048.6639
3857 | 2025-03-04 | 2025 | 2025 | 2025-03-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.13264 | 0.13264 | 0.14028 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & start WTG. | Close | 0.0070513 | O2-06 | 345.6368 |  | WTG Unscheduled Maintenance | 45247 | 345.6368
3858 | 2025-03-04 | 2025 | 2025 | 2025-03-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.48681 | 0.48681 | 0.525 | 0 | 0.91667 | 0.91667 | Turbine unexpectedly stop through PPC after problem solve then reset and start WTG. | Close | 0.035256 | O2-06 | 1728.184 |  | WTG Breakdown Maintenance | 45247 | 1728.184
3859 | 2025-03-04 | 2025 | 2025 | 2025-03-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.48681 | 0.48681 | 0.50972 | 0 | 0.55 | 0.55 | Turbine unexpectedly stop through PPC after problem solve then reset and start WTG. | Close | 0.021154 | O2-06 | 1036.9104 |  | WTG Breakdown Maintenance | 45247 | 1036.9104
3860 | 2025-03-04 | 2025 | 2025 | 2025-03-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.48194 | 0.48194 | 0.48681 | 0 | 0.11667 | 0.11667 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.0044872 | O2-11 | 149.7125 |  | WTG Breakdown Maintenance | 30798 | 149.7125
3861 | 2025-03-04 | 2025 | 2025 | 2025-03-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.48681 | 0.48681 | 0.50347 | 0 | 0.4 | 0.4 | Turbine unexpectedly stop through PPC after problem solve then reset and start WTG. | Close | 0.015385 | O2-11 | 513.3 |  | WTG Breakdown Maintenance | 30798 | 513.3
3862 | 2025-03-04 | 2025 | 2025 | 2025-03-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.48681 | 0.48681 | 0.55139 | 0 | 1.55 | 1.55 | Turbine unexpectedly stop through PPC after problem solve then reset and start WTG. | Close | 0.059615 | O2-20 | 3090.4417 |  | WTG Breakdown Maintenance | 47852 | 3090.4417
3863 | 2025-03-04 | 2025 | 2025 | 2025-03-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.48681 | 0.48681 | 0.50208 | 0 | 0.36667 | 0.36667 | Turbine unexpectedly stop through PPC after problem solve then reset and start WTG. | Close | 0.014103 | O2-01 | 540.3444 |  | WTG Breakdown Maintenance | 35368 | 540.3444
3864 | 2025-03-04 | 2025 | 2025 | 2025-03-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.48681 | 0.48681 | 0.50486 | 0 | 0.43333 | 0.43333 | Turbine unexpectedly stop through PPC after problem solve then reset and start WTG. | Close | 0.016667 | O2-01 | 638.5889 |  | WTG Breakdown Maintenance | 35368 | 638.5889
3865 | 2025-03-05 | 2025 | 2025 | 2025-03-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.41458 | 0.41458 | 0.42083 | 0 | 0.15 | 0.15 | Checked related error data log then reset & start WTG. | Close | 0.0057692 | O2-05 | 226.0625 |  | WTG Unscheduled Maintenance | 36170 | 226.0625
3866 | 2025-03-05 | 2025 | 2025 | 2025-03-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Connectivity issue | 0.52222 | 0.52222 | 0.57292 | 0 | 1.2167 | 1.2167 | Turbine late reset due to O2-14 stop for USS yard YPM work so connectivity not available after connectivity come than start WTG. | Close | 0.046795 | O2-05 | 1833.6181 |  | WTG Unscheduled Maintenance | 36170 | 1833.6181
3867 | 2025-03-05 | 2025 | 2025 | 2025-03-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.55833 | 0.55833 | 0.5625 | 0 | 0.1 | 0.1 | Checked related error data log then reset & start WTG. | Close | 0.0038462 | O2-04 | 147.6667 |  | WTG Unscheduled Maintenance | 35440 | 147.6667
3868 | 2025-03-05 | 2025 | 2025 | 2025-03-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.064583 | 0.064583 | 0.10694 | 0 | 1.0167 | 1.0167 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.039103 | O2-03 | 1517.375 |  | WTG Breakdown Maintenance | 35820 | 1517.375
3869 | 2025-03-05 | 2025 | 2025 | 2025-03-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.12986 | 0.12986 | 0.22083 | 0 | 2.1833 | 2.1833 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.083974 | O2-03 | 3258.625 |  | WTG Breakdown Maintenance | 35820 | 3258.625
3870 | 2025-03-05 | 2025 | 2025 | 2025-03-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.24653 | 0.24653 | 0.26042 | 0 | 0.33333 | 0.33333 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.012821 | O2-03 | 497.5 |  | WTG Breakdown Maintenance | 35820 | 497.5
3871 | 2025-03-05 | 2025 | 2025 | 2025-03-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.076389 | 0.076389 | 0.089583 | 0 | 0.31667 | 0.31667 | Checked related error data log then reset & start WTG. | Close | 0.012179 | O2-15 | 411.3104 |  | WTG Unscheduled Maintenance | 31173 | 411.3104
3872 | 2025-03-05 | 2025 | 2025 | 2025-03-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.10139 | 0.10139 | 0.10694 | 0 | 0.13333 | 0.13333 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.0051282 | O2-15 | 173.1833 |  | WTG Breakdown Maintenance | 31173 | 173.1833
3873 | 2025-03-05 | 2025 | 2025 | 2025-03-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.12986 | 0.12986 | 0.17361 | 0 | 1.05 | 1.05 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.040385 | O2-15 | 1363.8187 |  | WTG Breakdown Maintenance | 31173 | 1363.8187
3874 | 2025-03-05 | 2025 | 2025 | 2025-03-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.28542 | 0.28542 | 0.42917 | 0 | 3.45 | 3.45 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.13269 | O2-15 | 4481.1187 |  | WTG Breakdown Maintenance | 31173 | 4481.1187
3875 | 2025-03-05 | 2025 | 2025 | 2025-03-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.71111 | 0.71111 | 0.71389 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & start WTG. | Close | 0.0025641 | O2-14 | 77.2417 |  | WTG Unscheduled Maintenance | 27807 | 77.2417
3876 | 2025-03-05 | 2025 | 2025 | 2025-03-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.022222 | 0.022222 | 0.026389 | 0 | 0.1 | 0.1 | Checked related error data log then reset & start WTG. | Close | 0.0038462 | O2-21 | 181.7708 |  | WTG Unscheduled Maintenance | 43625 | 181.7708
3877 | 2025-03-05 | 2025 | 2025 | 2025-03-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.43194 | 0.43194 | 0.43333 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & start WTG. | Close | 0.0012821 | O2-21 | 60.5903 |  | WTG Unscheduled Maintenance | 43625 | 60.5903
3878 | 2025-03-05 | 2025 | 2025 | 2025-03-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 657 | Error pitch converter 2 | Break down | 0.09375 | 0.09375 | 0.1 | 0 | 0.15 | 0.15 | Checked related error data log then reset & start WTG. | Close | 0.0057692 | O2-22 | 288.425 |  | WTG Unscheduled Maintenance | 46148 | 288.425
3879 | 2025-03-05 | 2025 | 2025 | 2025-03-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.62292 | 0.62292 | 0.625 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | O2-22 | 96.1417 |  | WTG Unscheduled Maintenance | 46148 | 96.1417
3880 | 2025-03-05 | 2025 | 2025 | 2025-03-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 172 | SLC MF torque protection | Break down | 0.50347 | 0.50347 | 0.57778 | 0 | 1.7833 | 1.7833 | Turbine late reset due to O2-14 stop for USS yard YPM work so connectivity not available after connectivity come than start WTG. | Close | 0.06859 | O2-01 | 2515.3917 |  | WTG Unscheduled Maintenance | 33852 | 2515.3917
3881 | 2025-03-05 | 2025 | 2025 | 2025-03-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.58403 | 0.58403 | 0.58819 | 0 | 0.1 | 0.1 | Checked related error data log then reset & start WTG. | Close | 0.0038462 | O2-01 | 141.05 |  | WTG Unscheduled Maintenance | 33852 | 141.05
3882 | 2025-03-05 | 2025 | 2025 | 2025-03-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.18819 | 0.18819 | 0.22083 | 0 | 0.78333 | 0.78333 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.030128 | O2-01 | 1104.8917 |  | WTG Breakdown Maintenance | 33852 | 1104.8917
3883 | 2025-03-05 | 2025 | 2025 | 2025-03-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.24653 | 0.24653 | 0.31944 | 0 | 1.75 | 1.75 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.067308 | O2-01 | 2468.375 |  | WTG Breakdown Maintenance | 33852 | 2468.375
3884 | 2025-03-05 | 2025 | 2025 | 2025-03-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.34028 | 0.34028 | 0.43264 | 0 | 2.2167 | 2.2167 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.085256 | O2-01 | 3126.6083 |  | WTG Breakdown Maintenance | 33852 | 3126.6083
3885 | 2025-03-05 | 2025 | 2025 | 2025-03-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 2355 | Temp. rot.br.pad high | Connectivity issue | 0.44861 | 0.44861 | 0.5 | 0 | 1.2333 | 1.2333 | Turbine late Attend due to O2-14 stop for USS yard YPM work so connectivity not available after connectivity come wtg in error mode so wip, | Close | 0.047436 | O2-01 | 1739.6167 |  | WTG Unscheduled Maintenance | 33852 | 1739.6167
3886 | 2025-03-05 | 2025 | 2025 | 2025-03-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 2355 | Temp. rot.br.pad high | Break down | 0.5 | 0.5 | 0.68889 | 0 | 4.5333 | 4.5333 | Attend and check Brake pad and check Temprature sensor so ok after clean Brake pad and after check Hydrolic unit found ok so reset and start WTG. | Close | 0.17436 | O2-01 | 6394.2667 |  | WTG Unscheduled Maintenance | 33852 | 6394.2667
3886 | 2025-03-06 | 2025 | 2025 | 2025-03-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 1705 | Max. temp. gear bearing 1 | Break down | 0.16806 | 0.21458 | 0.72847 | 1.1167 | 12.3333 | 13.45 | Attend and check error related ckt than found Nacalle Coolent motor faulty so arrenge from other site than replace with new one than reset and start WTG. | Close | 0.51731 | O2-11 | 10397.9708 |  | WTG Unscheduled Maintenance | 18554 | 10397.9708
3886 | 2025-03-06 | 2025 | 2025 | 2025-03-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.46597 | 0.46597 | 0.71806 | 0 | 6.05 | 6.05 | Attend WTG and replace Brake caliper and also WTR 642, WTR 655 and WTR 672 perform then start WTG. | Close | 0.23269 | O2-01 | 4488.0917 |  | WTG Breakdown Maintenance | 17804 | 4488.0917
3886 | 2025-03-07 | 2025 | 2025 | 2025-03-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.4 | 0.4 | 0.72014 | 0 | 7.6833 | 7.6833 | WTG stop for YPM day-1 activity wip, | Close | 0.29551 | O2-12 | 1672.0854 |  | WTG Scheduled Maintenance | 5223 | 1672.0854
3886 | 2025-03-07 | 2025 | 2025 | 2025-03-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.73264 | 0.73264 | 0.79444 | 0 | 1.4833 | 1.4833 | After grid resume YPM Day-1 Activity complated than Start WTG. | Close | 0.057051 | O2-12 | 322.8104 |  | WTG Scheduled Maintenance | 5223 | 322.8104
3886 | 2025-03-07 | 2025 | 2025 | 2025-03-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.37014 | 0.39583 | 0.43681 | 0.61667 | 0.98333 | 1.6 | After grid resume and Checked related error data log then apply hard reboot then reset & start WTG. | Close | 0.061538 | O2-10 | 470.8 |  | WTG Unscheduled Maintenance | 7062 | 470.8
3886 | 2025-03-07 | 2025 | 2025 | 2025-03-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.25903 | 0.25903 | 0.26319 | 0 | 0.1 | 0.1 | Checked related error data log then reset & start WTG. | Close | 0.0038462 | O2-06 | 30.2625 |  | WTG Unscheduled Maintenance | 7263 | 30.2625
3887 | 2025-03-08 | 2025 | 2025 | 2025-03-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.034028 | 0.034028 | 0.042361 | 0 | 0.2 | 0.2 | Checked related error data log then reset & start WTG. | Close | 0.0076923 | O2-26 | 98.5417 |  | WTG Unscheduled Maintenance | 11825 | 98.5417
3888 | 2025-03-08 | 2025 | 2025 | 2025-03-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.93264 | 0.93264 | 0.94028 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & start WTG. | Close | 0.0070513 | O2-26 | 90.3299 |  | WTG Unscheduled Maintenance | 11825 | 90.3299
3889 | 2025-03-08 | 2025 | 2025 | 2025-03-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.43472 | 0.43472 | 0.69167 | 0 | 6.1667 | 6.1667 | WTG stop for YPM day-2 activity complate than start WTG. | Close | 0.23718 | O2-12 | 3982.125 |  | WTG Scheduled Maintenance | 15498 | 3982.125
3890 | 2025-03-08 | 2025 | 2025 | 2025-03-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.63958 | 0.63958 | 0.64375 | 0 | 0.1 | 0.1 | Checked related error data log then reset & start WTG. | Close | 0.0038462 | O2-21 | 40.1167 |  | WTG Unscheduled Maintenance | 9628 | 40.1167
3891 | 2025-03-08 | 2025 | 2025 | 2025-03-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.32292 | 0.32292 | 0.39861 | 0 | 1.8167 | 1.8167 | After RFO signal coming than Start WTG. | Close | 0.069872 | O2-06 | 683.2938 |  | WTG Unscheduled Maintenance | 9027 | 683.2938
3892 | 2025-03-08 | 2025 | 2025 | 2025-03-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 172 | SLC MF torque protection | Break down | 0.64097 | 0.64097 | 0.64861 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & start WTG. | Close | 0.0070513 | O2-01 | 115.0187 |  | WTG Unscheduled Maintenance | 15057 | 115.0187
3893 | 2025-03-09 | 2025 | 2025 | 2025-03-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.16389 | 0.16389 | 0.17153 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & start WTG. | Close | 0.0070513 | O2-26 | 71.4313 |  | WTG Unscheduled Maintenance | 9351 | 71.4313
3894 | 2025-03-09 | 2025 | 2025 | 2025-03-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.23611 | 0.23611 | 0.24375 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & start WTG. | Close | 0.0070513 | O2-26 | 71.4313 |  | WTG Unscheduled Maintenance | 9351 | 71.4313
3895 | 2025-03-10 | 2025 | 2025 | 2025-03-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.54167 | 0.54167 | 0.55347 | 0 | 0.28333 | 0.28333 | Checked related error data log then reset & start WTG. | Close | 0.010897 | O2-11 | 69.4757 |  | WTG Unscheduled Maintenance | 5885 | 69.4757
3896 | 2025-03-10 | 2025 | 2025 | 2025-03-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.87222 | 0.87222 | 0.87569 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & start WTG. | Close | 0.0032051 | O2-01 | 28.0625 |  | WTG Unscheduled Maintenance | 8082 | 28.0625
3897 | 2025-03-10 | 2025 | 2025 | 2025-03-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 172 | SLC MF torque protection | Break down | 0.34236 | 0.34236 | 0.34722 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & start WTG. | Close | 0.0044872 | O2-01 | 39.2875 |  | WTG Unscheduled Maintenance | 8082 | 39.2875
3898 | 2025-03-10 | 2025 | 2025 | 2025-03-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 172 | SLC MF torque protection | Break down | 0.66319 | 0.66319 | 0.66736 | 0 | 0.1 | 0.1 | Checked related error data log then reset & start WTG. | Close | 0.0038462 | O2-01 | 33.675 |  | WTG Unscheduled Maintenance | 8082 | 33.675
3899 | 2025-03-11 | 2025 | 2025 | 2025-03-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.0625 | 0.0625 | 0.080556 | 0 | 0.43333 | 0.43333 | After grid resume and Checked related error data log then apply shoft reboot then reset & start WTG. | Close | 0.016667 | O2-10 | 127.4361 |  | WTG Unscheduled Maintenance | 7058 | 127.4361
3900 | 2025-03-11 | 2025 | 2025 | 2025-03-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.20139 | 0.20139 | 0.21667 | 0 | 0.36667 | 0.36667 | After grid resume and Checked related error data log then apply shoft reboot then reset & start WTG. | Close | 0.014103 | O2-12 | 69.9569 |  | WTG Unscheduled Maintenance | 4579 | 69.9569
3901 | 2025-03-11 | 2025 | 2025 | 2025-03-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.34097 | 0.34097 | 0.36458 | 0 | 0.56667 | 0.56667 | After grid resume and Checked related error data log then reset & start WTG.( lat reset due to O2-13 VCB trip so wtg discannected from SCADA) | Close | 0.021795 | O2-03 | 112.8847 |  | WTG Unscheduled Maintenance | 4781 | 112.8847
3902 | 2025-03-11 | 2025 | 2025 | 2025-03-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.34097 | 0.34097 | 0.36458 | 0 | 0.56667 | 0.56667 | After grid resume and Checked related error data log then reset & start WTG.( lat reset due to O2-13 VCB trip so wtg discannected from SCADA) | Close | 0.021795 | O2-12 | 108.1153 |  | WTG Unscheduled Maintenance | 4579 | 108.1153
3903 | 2025-03-11 | 2025 | 2025 | 2025-03-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.34097 | 0.34097 | 0.36458 | 0 | 0.56667 | 0.56667 | After grid resume and Checked related error data log then reset & start WTG.( lat reset due to O2-13 VCB trip so wtg discannected from SCADA) | Close | 0.021795 | O2-14 | 131.325 |  | WTG Unscheduled Maintenance | 5562 | 131.325
3904 | 2025-03-11 | 2025 | 2025 | 2025-03-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.34097 | 0.34097 | 0.36458 | 0 | 0.56667 | 0.56667 | After grid resume and Checked related error data log then reset & start WTG.( lat reset due to O2-13 VCB trip so wtg discannected from SCADA) | Close | 0.021795 | O2-11 | 91.1861 |  | WTG Unscheduled Maintenance | 3862 | 91.1861
3905 | 2025-03-11 | 2025 | 2025 | 2025-03-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.34097 | 0.34097 | 0.37917 | 0 | 0.91667 | 0.91667 | After grid resume and Checked related error data log then reset & start WTG.( lat reset due to O2-08 VCB trip so wtg discannected from SCADA) | Close | 0.035256 | O2-01 | 188.184 |  | WTG Unscheduled Maintenance | 4927 | 188.184
3906 | 2025-03-11 | 2025 | 2025 | 2025-03-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.41389 | 0.41389 | 0.7625 | 0 | 8.3667 | 8.3667 | WTG stop for YPM day-1 activity complate than start WTG. | Close | 0.32179 | O2-14 | 1938.975 |  | WTG Scheduled Maintenance | 5562 | 1938.975
3907 | 2025-03-11 | 2025 | 2025 | 2025-03-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 88 | Outs.temp. nacelle implaus. | Break down | 0.62569 | 0.62569 | 0.63819 | 0 | 0.3 | 0.3 | Auto reset | Close | 0.011538 | O2-07 | 116.8 |  | WTG Unscheduled Maintenance | 9344 | 116.8
3908 | 2025-03-11 | 2025 | 2025 | 2025-03-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.72361 | 0.72361 | 0.80903 | 0 | 2.05 | 2.05 | check and found no any abnormality Apply hard reboot than reset and start WTG. | Close | 0.078846 | O2-02 | 408.5479 |  | WTG Unscheduled Maintenance | 4783 | 408.5479
3909 | 2025-03-11 | 2025 | 2025 | 2025-03-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.95833 | 0.95833 | 0.96875 | 0 | 0.25 | 0.25 | Checked related error data log then reset & start WTG. | Close | 0.0096154 | O2-01 | 51.3229 |  | WTG Unscheduled Maintenance | 4927 | 51.3229
3910 | 2025-03-11 | 2025 | 2025 | 2025-03-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.71458 | 0.71458 | 0.73472 | 0 | 0.48333 | 0.48333 | Checked related error data log then reset & start WTG. | Close | 0.01859 | O2-10 | 142.1403 |  | WTG Unscheduled Maintenance | 7058 | 142.1403
3911 | 2025-03-11 | 2025 | 2025 | 2025-03-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.79167 | 0.86111 | 0.90278 | 1.6667 | 1 | 2.6667 | Attend and WTG check releted circuit so found FA001 Surgerrstor Connection loose after all connection tight then reset and start WTG. | Close | 0.10256 | O2-10 | 784.2222 |  | WTG Unscheduled Maintenance | 7058 | 784.2222
3912 | 2025-03-12 | 2025 | 2025 | 2025-03-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.39931 | 0.39931 | 0.60417 | 0 | 4.9167 | 4.9167 | WTG stop for YPM day-2 activity complate than start WTG. | Close | 0.1891 | O2-14 | 3603.7118 |  | WTG Scheduled Maintenance | 17591 | 3603.7118
3913 | 2025-03-12 | 2025 | 2025 | 2025-03-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.60347 | 0.60347 | 0.65417 | 0 | 1.2167 | 1.2167 | wtg manual stop for Rep error inspection work stop | Close | 0.046795 | O2-11 | 984.8917 |  | WTG Breakdown Maintenance | 19428 | 984.8917
3914 | 2025-03-12 | 2025 | 2025 | 2025-03-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 88 | Outs.temp. nacelle implaus. | Break down | 0.56875 | 0.56875 | 0.59653 | 0 | 0.66667 | 0.66667 | Checked related error data log then reset & start WTG. | Close | 0.025641 | O2-07 | 318.5 |  | WTG Unscheduled Maintenance | 11466 | 318.5
3915 | 2025-03-12 | 2025 | 2025 | 2025-03-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.4125 | 0.4125 | 0.41458 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | O2-02 | 34.4104 |  | WTG Unscheduled Maintenance | 16517 | 34.4104
3916 | 2025-03-12 | 2025 | 2025 | 2025-03-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.70347 | 0.70347 | 0.75972 | 0 | 1.35 | 1.35 | Checked related error data log then shoft reboot than reset and start WTG. | Close | 0.051923 | O2-02 | 929.0812 |  | WTG Unscheduled Maintenance | 16517 | 929.0812
3917 | 2025-03-12 | 2025 | 2025 | 2025-03-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.22917 | 0.22917 | 0.23819 | 0 | 0.21667 | 0.21667 | Checked related error data log then reset & start WTG. | Close | 0.0083333 | O2-22 | 128.7542 |  | WTG Unscheduled Maintenance | 14262 | 128.7542
3918 | 2025-03-12 | 2025 | 2025 | 2025-03-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.16042 | 0.16042 | 0.16806 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & start WTG. | Close | 0.0070513 | O2-01 | 165.6646 |  | WTG Unscheduled Maintenance | 21687 | 165.6646
3919 | 2025-03-12 | 2025 | 2025 | 2025-03-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.22083 | 0.22083 | 0.23889 | 0 | 0.43333 | 0.43333 | Checked related error data log then reset & start WTG. | Close | 0.016667 | O2-01 | 391.5708 |  | WTG Unscheduled Maintenance | 21687 | 391.5708
3920 | 2025-03-13 | 2025 | 2025 | 2025-03-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.91528 | 0.91528 | 0.99583 | 0 | 1.9333 | 1.9333 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.074359 | O2-12 | 2748.8778 |  | WTG Breakdown Maintenance | 34124 | 2748.8778
3921 | 2025-03-13 | 2025 | 2025 | 2025-03-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.90625 | 0.90625 | 0.9375 | 0 | 0.75 | 0.75 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.028846 | O2-26 | 651.9375 |  | WTG Breakdown Maintenance | 20862 | 651.9375
3922 | 2025-03-13 | 2025 | 2025 | 2025-03-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.72778 | 0.77083 | 0.82431 | 1.0333 | 1.2833 | 2.3167 | Attend and WTG check releted circuit so found FA001 Surgerrstor Connection loose after all connection tight then reset and start WTG. | Close | 0.089103 | O2-07 | 2742.3542 |  | WTG Unscheduled Maintenance | 28410 | 2742.3542
3923 | 2025-03-13 | 2025 | 2025 | 2025-03-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.095139 | 0.095139 | 0.10556 | 0 | 0.25 | 0.25 | Checked related error data log then reset & start WTG. | Close | 0.0096154 | O2-02 | 319.6458 |  | WTG Unscheduled Maintenance | 30686 | 319.6458
3924 | 2025-03-13 | 2025 | 2025 | 2025-03-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.64028 | 0.64028 | 0.64514 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & start WTG. | Close | 0.0044872 | O2-02 | 149.1681 |  | WTG Unscheduled Maintenance | 30686 | 149.1681
3925 | 2025-03-13 | 2025 | 2025 | 2025-03-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.625 | 0.625 | 0.62917 | 0 | 0.1 | 0.1 | Checked related error data log then reset & start WTG. | Close | 0.0038462 | O2-14 | 130.2708 |  | WTG Unscheduled Maintenance | 31265 | 130.2708
3926 | 2025-03-13 | 2025 | 2025 | 2025-03-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Break down | 0.65278 | 0.65278 | 0.66389 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & start WTG. | Close | 0.010256 | O2-11 | 320.4444 |  | WTG Unscheduled Maintenance | 28840 | 320.4444
3927 | 2025-03-13 | 2025 | 2025 | 2025-03-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.92986 | 0.92986 | 0.93681 | 0 | 0.16667 | 0.16667 | Checked related error data log then reset & start WTG. | Close | 0.0064103 | O2-22 | 214.6389 |  | WTG Unscheduled Maintenance | 30908 | 214.6389
3928 | 2025-03-13 | 2025 | 2025 | 2025-03-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.44306 | 0.44306 | 0.45139 | 0 | 0.2 | 0.2 | Checked related error data log then reset & start WTG. | Close | 0.0076923 | O2-06 | 240.9083 |  | WTG Unscheduled Maintenance | 28909 | 240.9083
3929 | 2025-03-13 | 2025 | 2025 | 2025-03-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.72014 | 0.72014 | 0.725 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & start WTG. | Close | 0.0044872 | O2-24 | 162.9299 |  | WTG Unscheduled Maintenance | 33517 | 162.9299
3930 | 2025-03-13 | 2025 | 2025 | 2025-03-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.76736 | 0.76736 | 0.77917 | 0 | 0.28333 | 0.28333 | Checked related error data log then reset & start WTG. | Close | 0.010897 | O2-24 | 395.6868 |  | WTG Unscheduled Maintenance | 33517 | 395.6868
3931 | 2025-03-13 | 2025 | 2025 | 2025-03-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.036806 | 0.036806 | 0.038889 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | O2-11 | 60.0833 |  | WTG Unscheduled Maintenance | 28840 | 60.0833
3932 | 2025-03-13 | 2025 | 2025 | 2025-03-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 172 | SLC MF torque protection | Break down | 0.68958 | 0.68958 | 0.69514 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & start WTG. | Close | 0.0051282 | O2-01 | 174.8111 |  | WTG Unscheduled Maintenance | 31466 | 174.8111
3933 | 2025-03-13 | 2025 | 2025 | 2025-03-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.0375 | 0.0375 | 0.039583 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | O2-01 | 65.5542 |  | WTG Unscheduled Maintenance | 31466 | 65.5542
3934 | 2025-03-14 | 2025 | 2025 | 2025-03-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.1 | 0.1 | 0.12222 | 0 | 0.53333 | 0.53333 | Checked related error data log then reset & start WTG. | Close | 0.020513 | O2-26 | 493.6444 |  | WTG Unscheduled Maintenance | 22214 | 493.6444
3935 | 2025-03-14 | 2025 | 2025 | 2025-03-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.13194 | 0.13194 | 0.13958 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & start WTG. | Close | 0.0070513 | O2-26 | 169.6903 |  | WTG Unscheduled Maintenance | 22214 | 169.6903
3936 | 2025-03-14 | 2025 | 2025 | 2025-03-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.6 | 0.6 | 0.60486 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & start WTG. | Close | 0.0044872 | O2-05 | 178.2424 |  | WTG Unscheduled Maintenance | 36667 | 178.2424
3937 | 2025-03-14 | 2025 | 2025 | 2025-03-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3560 | Voltage asymmetry | Break down | 0.43056 | 0.43056 | 0.52639 | 0 | 2.3 | 2.3 | due to grid voltage unbalanced from TR. So please check by BOP team wip | open | 0.088462 | O2-15 | 2467.9 |  | WTG Unscheduled Maintenance | 25752 | 2467.9
3938 | 2025-03-14 | 2025 | 2025 | 2025-03-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Break down | 0.52639 | 0.52639 | 0.59375 | 0 | 1.6167 | 1.6167 | Checked related error data log then found no any abnormality Apply shoft reboot than reset and start WTG. | Close | 0.062179 | O2-15 | 1734.6833 |  | WTG Unscheduled Maintenance | 25752 | 1734.6833
3939 | 2025-03-14 | 2025 | 2025 | 2025-03-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.61389 | 0.61389 | 0.63542 | 0 | 0.51667 | 0.51667 | Checked related error data log then reset & start WTG. | Close | 0.019872 | O2-14 | 471.2 |  | WTG Unscheduled Maintenance | 21888 | 471.2
3940 | 2025-03-14 | 2025 | 2025 | 2025-03-01 | 1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Break down | 0.56528 | 0.56528 | 0.57778 | 0 | 0.3 | 0.3 | Checked related error data log then reset & start WTG. | Close | 0.011538 | O2-24 | 337.75 |  | WTG Unscheduled Maintenance | 27020 | 337.75
3941 | 2025-03-14 | 2025 | 2025 | 2025-03-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 6012 | Overload yaw motors group 2 | Break down | 0.44583 | 0.44583 | 0.48819 | 0 | 1.0167 | 1.0167 | Checked related error data log then found no any abnormality Apply shoft reboot than reset and start WTG. | Close | 0.039103 | O2-01 | 1165.3965 |  | WTG Unscheduled Maintenance | 27511 | 1165.3965
3942 | 2025-03-14 | 2025 | 2025 | 2025-03-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 6012 | Overload yaw motors group 2 | Break down | 0.66389 | 0.6875 | 0.72292 | 0.56667 | 0.85 | 1.4167 | attend and found yaw motor FB loose cannections on Contector so tight and start wtg | Close | 0.054487 | O2-01 | 1623.9132 |  | WTG Unscheduled Maintenance | 27511 | 1623.9132
3943 | 2025-03-14 | 2025 | 2025 | 2025-03-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 6012 | Overload yaw motors group 2 | Break down | 0.60625 | 0.60625 | 0.64792 | 0 | 1 | 1 | Checked related error data log then found no any abnormality Apply shoft reboot than reset and start WTG. | Close | 0.038462 | O2-01 | 1146.2917 |  | WTG Unscheduled Maintenance | 27511 | 1146.2917
3944 | 2025-03-15 | 2025 | 2025 | 2025-03-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3560 | Voltage asymmetry | Break down | 0.41319 | 0.44792 | 0.74931 | 0.83333 | 7.2333 | 8.0667 | due to grid voltage unbalanced from TR. So please check by BOP team wip | Close | 0.31026 | O2-15 | 4142.9056 |  | WTG Unscheduled Maintenance | 12326 | 4142.9056
3945 | 2025-03-15 | 2025 | 2025 | 2025-03-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 2521 | Gen.sp.analog <<>> gearb.sp. | Break down | 0.55069 | 0.55069 | 0.55278 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2-02 | 35.0729 |  | WTG Unscheduled Maintenance | 16835 | 35.0729
3946 | 2025-03-15 | 2025 | 2025 | 2025-03-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.69167 | 0.69167 | 0.69306 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & start WTG. | Close | 0.0012821 | O2-02 | 23.3819 |  | WTG Unscheduled Maintenance | 16835 | 23.3819
3947 | 2025-03-15 | 2025 | 2025 | 2025-03-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.41042 | 0.41042 | 0.5125 | 0 | 2.45 | 2.45 | attend and found hub luber supply connections loose so tight it then start WTG. | Close | 0.094231 | O2-06 | 1354.6458 |  | WTG Unscheduled Maintenance | 13270 | 1354.6458
3948 | 2025-03-16 | 2025 | 2025 | 2025-03-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6115 | Yaw sensor A defect | Break down | 0.20139 | 0.27431 | 0.31944 | 1.75 | 1.0833 | 2.8333 | Attend and wtg check Releted circuit so found Yaw Sensor Connection loose after all connection tight then reset and start wtg. | Close | 0.10897 | O2-07 | 2309.2847 |  | WTG Unscheduled Maintenance | 19561 | 2309.2847
3949 | 2025-03-16 | 2025 | 2025 | 2025-03-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.24028 | 0.24028 | 0.25833 | 0 | 0.43333 | 0.43333 | Checked related error data log then reset & start WTG. | Close | 0.016667 | O2-26 | 296.1292 |  | WTG Unscheduled Maintenance | 16401 | 296.1292
3950 | 2025-03-16 | 2025 | 2025 | 2025-03-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 551 | Pitch motor current too high | Break down | 0.31042 | 0.31042 | 0.3125 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | O2-10 | 42.9042 |  | WTG Unscheduled Maintenance | 20594 | 42.9042
3951 | 2025-03-16 | 2025 | 2025 | 2025-03-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.19444 | 0.19444 | 0.2 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & start WTG. | Close | 0.0051282 | O2-01 | 124.0722 |  | WTG Unscheduled Maintenance | 22333 | 124.0722
3952 | 2025-03-16 | 2025 | 2025 | 2025-03-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 172 | SLC MF torque protection | Break down | 0.34583 | 0.34583 | 0.34931 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & start WTG. | Close | 0.0032051 | O2-01 | 77.5451 |  | WTG Unscheduled Maintenance | 22333 | 77.5451
3953 | 2025-03-17 | 2025 | 2025 | 2025-03-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Auto reset | 0.31736 | 0.31736 | 0.32222 | 0 | 0.11667 | 0.11667 | Auto reset | Close | 0.0044872 | O2-26 | 48.9222 |  | WTG Unscheduled Maintenance | 10064 | 48.9222
3954 | 2025-03-17 | 2025 | 2025 | 2025-03-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.0069444 | 0.038194 | 0.076389 | 0.75 | 0.91667 | 1.6667 | Attend and wtg check releted circuit check all connection found CM202 Error Mode After check all connection and converter comunication connector tight after trail so ok then reset and start wtg. | Close | 0.064103 | O2-02 | 1049.8611 |  | WTG Unscheduled Maintenance | 15118 | 1049.8611
3955 | 2025-03-17 | 2025 | 2025 | 2025-03-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.39792 | 0.39792 | 0.72014 | 0 | 7.7333 | 7.7333 | WTG stop for YPM day-1 activity complate than start WTG. | Close | 0.29744 | O2-11 | 4234 |  | WTG Scheduled Maintenance | 13140 | 4234
3956 | 2025-03-17 | 2025 | 2025 | 2025-03-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.65694 | 0.65694 | 0.65833 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2-10 | 17.7875 |  | WTG Unscheduled Maintenance | 12807 | 17.7875
3957 | 2025-03-17 | 2025 | 2025 | 2025-03-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.66736 | 0.66736 | 0.67014 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0025641 | O2-10 | 35.575 |  | WTG Unscheduled Maintenance | 12807 | 35.575
3958 | 2025-03-17 | 2025 | 2025 | 2025-03-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 153 | SLC SF max. cable winding | Break down | 0.92153 | 0.92153 | 0.92778 | 0 | 0.15 | 0.15 | Checked related error data log then reset & start WTG. | Close | 0.0057692 | O2-07 | 77.5438 |  | WTG Unscheduled Maintenance | 12407 | 77.5438
3959 | 2025-03-18 | 2025 | 2025 | 2025-03-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.79444 | 0.79444 | 0.83194 | 0 | 0.9 | 0.9 | After grid Resume time Converter RFO Single Note so after so and Reset and start wtg | Close | 0.034615 | O2-05 | 403.6125 |  | WTG Unscheduled Maintenance | 10763 | 403.6125
3960 | 2025-03-18 | 2025 | 2025 | 2025-03-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.79444 | 0.79444 | 0.83889 | 0 | 1.0667 | 1.0667 | After grid Resume time Converter RFO Single Note so after so and Reset and start wtg | Close | 0.041026 | O2-09 | 502.3111 |  | WTG Unscheduled Maintenance | 11302 | 502.3111
3961 | 2025-03-18 | 2025 | 2025 | 2025-03-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.79583 | 0.79583 | 0.84097 | 0 | 1.0833 | 1.0833 | After grid Resume time Converter RFO Single Note so after so and Reset and start wtg | Close | 0.041667 | O2-07 | 258.5104 |  | WTG Unscheduled Maintenance | 5727 | 258.5104
3962 | 2025-03-18 | 2025 | 2025 | 2025-03-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.79583 | 0.79583 | 0.81944 | 0 | 0.56667 | 0.56667 | After grid Resume time Converter RFO Single Note so after so and Reset and start wtg | Close | 0.021795 | O2-21 | 92.6028 |  | WTG Unscheduled Maintenance | 3922 | 92.6028
3963 | 2025-03-18 | 2025 | 2025 | 2025-03-01 | 1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.79444 | 0.79444 | 0.84028 | 0 | 1.1 | 1.1 | After grid Resume time Converter RFO Single Note so after so and Reset and start wtg | Close | 0.042308 | O2-14 | 350.4875 |  | WTG Unscheduled Maintenance | 7647 | 350.4875
3964 | 2025-03-18 | 2025 | 2025 | 2025-03-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.79583 | 0.79583 | 0.84167 | 0 | 1.1 | 1.1 | After grid Resume time Converter RFO Single Note so after so and Reset and start wtg | Close | 0.042308 | O2-06 | 235.4458 |  | WTG Unscheduled Maintenance | 5137 | 235.4458
3965 | 2025-03-18 | 2025 | 2025 | 2025-03-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.79583 | 0.79583 | 0.86319 | 0 | 1.6167 | 1.6167 | After grid Resume time Converter RFO Single Note so after so and Reset and start wtg | Close | 0.062179 | O2-06 | 346.034 |  | WTG Unscheduled Maintenance | 5137 | 346.034
3966 | 2025-03-18 | 2025 | 2025 | 2025-03-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.79583 | 0.79583 | 0.86319 | 0 | 1.6167 | 1.6167 | After grid Resume time Converter RFO Single Note so after so and Reset and start wtg | Close | 0.062179 | O2-06 | 346.034 |  | WTG Unscheduled Maintenance | 5137 | 346.034
3967 | 2025-03-18 | 2025 | 2025 | 2025-03-01 | 1 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.79444 | 0.79444 | 0.84375 | 0 | 1.1833 | 1.1833 | After grid Resume time Converter RFO Single Note so after so and Reset and start wtg | Close | 0.045513 | O2-11 | 484.6243 |  | WTG Unscheduled Maintenance | 9829 | 484.6243
3968 | 2025-03-18 | 2025 | 2025 | 2025-03-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.79444 | 0.79444 | 0.84583 | 0 | 1.2333 | 1.2333 | After grid Resume time Converter RFO Single Note so after so and Reset and start wtg | Close | 0.047436 | O2-01 | 595.1347 |  | WTG Unscheduled Maintenance | 11581 | 595.1347
3969 | 2025-03-18 | 2025 | 2025 | 2025-03-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.79444 | 0.79444 | 0.86667 | 0 | 1.7333 | 1.7333 | Attend and wtg check Bottom Panel and Converter Panel check panel limit switch connection tigh after trail so ok then reset and start wtg | Close | 0.066667 | O2-01 | 836.4056 |  | WTG Unscheduled Maintenance | 11581 | 836.4056
3970 | 2025-03-18 | 2025 | 2025 | 2025-03-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 2810 | Service generator brushes | Break down | 0.79444 | 0.82917 | 0.8375 | 0.83333 | 0.2 | 1.0333 | Attend and wtg check generator sleepring Earthing brush check so not ok after replace then reset and start wtg | Close | 0.039744 | O2-11 | 423.1931 |  | WTG Unscheduled Maintenance | 9829 | 423.1931
3971 | 2025-03-18 | 2025 | 2025 | 2025-03-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Auto reset | 0.28611 | 0.28611 | 0.28889 | 0 | 0.066667 | 0.066667 | Auto Reset | Close | 0.0025641 | O2-26 | 23.7139 |  | WTG Unscheduled Maintenance | 8537 | 23.7139
3972 | 2025-03-19 | 2025 | 2025 | 2025-03-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.40486 | 0.40486 | 0.67361 | 0 | 6.45 | 6.45 | WTG stop for YPM day-2 activity complate than start WTG. | Close | 0.24808 | O2-11 | 5567.6938 |  | WTG Scheduled Maintenance | 20717 | 5567.6938
3973 | 2025-03-19 | 2025 | 2025 | 2025-03-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Others | 0.51944 | 0.51944 | 0.56806 | 0 | 1.1667 | 1.1667 | WTG Stop for Customer Instruction work compeleted after Reset and start wtg | Close | 0.044872 | O2-01 | 997.9375 |  | WTG Breakdown Maintenance | 20529 | 997.9375
3974 | 2025-03-19 | 2025 | 2025 | 2025-03-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Auto reset | 0.20278 | 0.20278 | 0.20556 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0025641 | O2-02 | 71.6611 |  | WTG Unscheduled Maintenance | 25798 | 71.6611
3975 | 2025-03-19 | 2025 | 2025 | 2025-03-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 2521 | Gen.sp.analog <<>> gearb.sp. | Auto reset | 0.75486 | 0.75486 | 0.75694 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2-02 | 53.7458 |  | WTG Unscheduled Maintenance | 25798 | 53.7458
3976 | 2025-03-19 | 2025 | 2025 | 2025-03-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 6056 | High yaw load | Auto reset | 0.625 | 0.625 | 0.62708 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2-10 | 37.7417 |  | WTG Unscheduled Maintenance | 18116 | 37.7417
3977 | 2025-03-19 | 2025 | 2025 | 2025-03-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Auto reset | 0.91319 | 0.91319 | 0.91597 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0025641 | O2-06 | 56.45 |  | WTG Unscheduled Maintenance | 20322 | 56.45
3978 | 2025-03-19 | 2025 | 2025 | 2025-03-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 172 | SLC MF torque protection | Break down | 0.28889 | 0.28889 | 0.29306 | 0 | 0.1 | 0.1 | Checked related error data log then reset & start WTG. | Close | 0.0038462 | O2-01 | 85.5375 |  | WTG Unscheduled Maintenance | 20529 | 85.5375
3979 | 2025-03-19 | 2025 | 2025 | 2025-03-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 172 | SLC MF torque protection | Break down | 0.81111 | 0.81111 | 0.82083 | 0 | 0.23333 | 0.23333 | Checked related error data log then reset & start WTG. | Close | 0.0089744 | O2-01 | 199.5875 |  | WTG Unscheduled Maintenance | 20529 | 199.5875
3980 | 2025-03-19 | 2025 | 2025 | 2025-03-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.66528 | 0.66528 | 0.66944 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-01 | 85.5375 |  | WTG Unscheduled Maintenance | 20529 | 85.5375
3981 | 2025-03-20 | 2025 | 2025 | 2025-03-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.046528 | 0.046528 | 0.05 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0032051 | O2-09 | 95.1215 |  | WTG Unscheduled Maintenance | 27395 | 95.1215
3982 | 2025-03-20 | 2025 | 2025 | 2025-03-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.059028 | 0.059028 | 0.063194 | 0 | 0.1 | 0.1 | Checked related error data log then reset & start WTG. | Close | 0.0038462 | O2-02 | 132.55 |  | WTG Unscheduled Maintenance | 31812 | 132.55
3983 | 2025-03-20 | 2025 | 2025 | 2025-03-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Auto reset | 0.33264 | 0.33264 | 0.33542 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0025641 | O2-02 | 88.3667 |  | WTG Unscheduled Maintenance | 31812 | 88.3667
3984 | 2025-03-20 | 2025 | 2025 | 2025-03-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Auto reset | 0.25347 | 0.25347 | 0.25625 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0025641 | O2-26 | 62.4889 |  | WTG Unscheduled Maintenance | 22496 | 62.4889
3985 | 2025-03-20 | 2025 | 2025 | 2025-03-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Auto reset | 0.84375 | 0.84375 | 0.85139 | 0 | 0.18333 | 0.18333 | Auto reset | Close | 0.0070513 | O2-26 | 171.8444 |  | WTG Unscheduled Maintenance | 22496 | 171.8444
3986 | 2025-03-20 | 2025 | 2025 | 2025-03-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.076389 | 0.076389 | 0.079861 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & start WTG. | Close | 0.0032051 | O2-15 | 105.1181 |  | WTG Unscheduled Maintenance | 30274 | 105.1181
3987 | 2025-03-20 | 2025 | 2025 | 2025-03-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 2810 | Service generator brushes | Major BD | 0.47569 | 0.47569 | 1899-12-31 | 0 | 12.5833 | 12.5833 | Attend Turbine and check related circuit than found Brush was warn out so check slipring track and also check brush holder and its mouning than nothing found so now we connect with our technical P&T Team and also supplier for further troubleshooting.. | open | 0.48397 | O2-11 | 15833.5035 |  | WTG Unscheduled Maintenance | 30199 | 15833.5035
3988 | 2025-03-20 | 2025 | 2025 | 2025-03-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.40972 | 0.40972 | 0.75694 | 0 | 8.3333 | 8.3333 | WTG stop for YPM day-1 activity complate than start WTG. | Close | 0.32051 | O2-12 | 9807.6389 |  | WTG Scheduled Maintenance | 28246 | 9807.6389
3989 | 2025-03-20 | 2025 | 2025 | 2025-03-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down | 0.96042 | 0.96042 | 0.96458 | 0 | 0.1 | 0.1 | Check Releated Errorflushing on after check so ok after reset and start wtg | Close | 0.0038462 | O2-21 | 115.1458 |  | WTG Unscheduled Maintenance | 27635 | 115.1458
3990 | 2025-03-20 | 2025 | 2025 | 2025-03-01 | 1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.12431 | 0.12431 | 0.12639 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2-01 | 60.0875 |  | WTG Unscheduled Maintenance | 28842 | 60.0875
3991 | 2025-03-21 | 2025 | 2025 | 2025-03-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 2810 | Service generator brushes | Major BD | 0 | 0 | 0.75694 | 0 | 18.1667 | 18.1667 | As per guide our techanical team and supply we have clean earthing brush track and change brush.(WTG Under Observation) | Close | 0.69872 | O2-11 | 10213.4514 |  | WTG Unscheduled Maintenance | 13493 | 10213.4514
3992 | 2025-03-21 | 2025 | 2025 | 2025-03-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.38611 | 0.38611 | 0.65972 | 0 | 6.5667 | 6.5667 | WTG stop for YPM day-2 activity complate than start WTG. | Close | 0.25256 | O2-12 | 4433.0472 |  | WTG Scheduled Maintenance | 16202 | 4433.0472
3993 | 2025-03-21 | 2025 | 2025 | 2025-03-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Auto reset | 0.33403 | 0.33403 | 0.34306 | 0 | 0.21667 | 0.21667 | Auto reset | Close | 0.0083333 | O2-26 | 161.1007 |  | WTG Unscheduled Maintenance | 17845 | 161.1007
3994 | 2025-03-21 | 2025 | 2025 | 2025-03-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.68125 | 0.68125 | 0.68333 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2-10 | 34.5625 |  | WTG Unscheduled Maintenance | 16590 | 34.5625
3995 | 2025-03-21 | 2025 | 2025 | 2025-03-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down | 0.11458 | 0.11458 | 0.11806 | 0 | 0.083333 | 0.083333 | Chech Data log after flushing and after then reset and start wtg. | Close | 0.0032051 | O2-21 | 78.2743 |  | WTG Unscheduled Maintenance | 22543 | 78.2743
3996 | 2025-03-21 | 2025 | 2025 | 2025-03-01 | 1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down | 0.46528 | 0.46528 | 0.62153 | 0 | 3.75 | 3.75 | attend and wtg check valv and check orifish and clean 9.1 valv after trail so ok then reset and start wtg | Close | 0.14423 | O2-21 | 3522.3438 |  | WTG Unscheduled Maintenance | 22543 | 3522.3438
3997 | 2025-03-21 | 2025 | 2025 | 2025-03-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Break down | 0.85417 | 0.93403 | 0.99653 | 1.9167 | 1.5 | 3.4167 | Attend and wtg check related circuit and found axis no 2 flate resiator failure after replace new then reset and start wtg. | Close | 0.13141 | O2-06 | 2945.7361 |  | WTG Unscheduled Maintenance | 20692 | 2945.7361
3998 | 2025-03-21 | 2025 | 2025 | 2025-03-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 153 | SLC SF max. cable winding | Break down | 0.92153 | 0.92153 | 0.94722 | 0 | 0.61667 | 0.61667 | Check data log so yaw cable twist is high after cable twist remove after trail so ok then reset and start wtg | Close | 0.023718 | O2-07 | 479.7153 |  | WTG Unscheduled Maintenance | 18670 | 479.7153
3999 | 2025-03-21 | 2025 | 2025 | 2025-03-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 172 | SLC MF torque protection | Break down | 0.90417 | 0.90417 | 0.92222 | 0 | 0.43333 | 0.43333 | Checked related error data log then reset & start WTG. | Close | 0.016667 | O2-01 | 304.6333 |  | WTG Unscheduled Maintenance | 16872 | 304.6333
4000 | 2025-03-22 | 2025 | 2025 | 2025-03-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.40139 | 0.40139 | 0.73264 | 0 | 7.95 | 7.95 | WTG stop for YPM day-1 activity complate than start WTG. | Close | 0.30577 | O2-02 | 3083.275 |  | WTG Scheduled Maintenance | 9308 | 3083.275
4001 | 2025-03-22 | 2025 | 2025 | 2025-03-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.038194 | 0.038194 | 0.069444 | 0 | 0.75 | 0.75 | WTG STOP WTG INSPECTION Work After reset and start wtg | Close | 0.028846 | O2-11 | 205.1875 |  | WTG Breakdown Maintenance | 6566 | 205.1875
4002 | 2025-03-22 | 2025 | 2025 | 2025-03-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 153 | SLC SF max. cable winding | Break down | 0.94583 | 0.94583 | 0.99653 | 0 | 1.2167 | 1.2167 | Attend and wtg check Set point after yawing 0 degree after trail so ok then reset and start wtg | Close | 0.046795 | O2-07 | 348.3215 |  | WTG Unscheduled Maintenance | 6871 | 348.3215
4003 | 2025-03-22 | 2025 | 2025 | 2025-03-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.80833 | 0.80833 | 0.85417 | 0 | 1.1 | 1.1 | check Converter so RFO Singnal Not show after So Singnal RFO After then reset and start wtg | Close | 0.042308 | O2-06 | 325.6458 |  | WTG Unscheduled Maintenance | 7105 | 325.6458
4004 | 2025-03-22 | 2025 | 2025 | 2025-03-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 172 | SLC MF torque protection | Auto reset | 0.89236 | 0.89236 | 0.89444 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2-01 | 14.75 |  | WTG Unscheduled Maintenance | 7080 | 14.75
4005 | 2025-03-23 | 2025 | 2025 | 2025-03-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.53542 | 0.53542 | 0.53958 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-26 | 51.975 |  | WTG Unscheduled Maintenance | 12474 | 51.975
4006 | 2025-03-23 | 2025 | 2025 | 2025-03-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.65833 | 0.65833 | 0.65972 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2-11 | 14.6389 |  | WTG Unscheduled Maintenance | 10540 | 14.6389
4007 | 2025-03-23 | 2025 | 2025 | 2025-03-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.28542 | 0.28542 | 0.2875 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2-06 | 24.1417 |  | WTG Unscheduled Maintenance | 11588 | 24.1417
4008 | 2025-03-23 | 2025 | 2025 | 2025-03-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 153 | SLC SF max. cable winding | Break down | 0.0013889 | 0.0013889 | 0.016667 | 0 | 0.36667 | 0.36667 | Attend and wtg yaw cable twist Removed after trail so ok then reset and start wtg. | Close | 0.014103 | O2-07 | 131.7708 |  | WTG Unscheduled Maintenance | 8625 | 131.7708
4009 | 2025-03-23 | 2025 | 2025 | 2025-03-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.85833 | 0.85833 | 0.87014 | 0 | 0.28333 | 0.28333 | Checked related error data log then reset & start WTG. | Close | 0.010897 | O2-01 | 165.8444 |  | WTG Unscheduled Maintenance | 14048 | 165.8444
4010 | 2025-03-24 | 2025 | 2025 | 2025-03-01 | 1 | O2_09 | TQGXIIPL | GEDA | 3.846% | 6056 | High yaw load | Break down | 0.56944 | 0.56944 | 0.57153 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | O2-03 | 23.2042 |  | WTG Unscheduled Maintenance | 11138 | 23.2042
4011 | 2025-03-24 | 2025 | 2025 | 2025-03-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 153 | SLC SF max. cable winding | Break down | 0.86111 | 0.91667 | 1899-12-31 | 1.3333 | 2 | 3.3333 | Attend and check error related ckt than wtg yaw cable twist sensor all connection check and retight than cable twist removed than wip, | Close | 0.12821 | O2-07 | 1102.2222 |  | WTG Unscheduled Maintenance | 7936 | 1102.2222
4012 | 2025-03-24 | 2025 | 2025 | 2025-03-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.65972 | 0.65972 | 0.66111 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2-20 | 12.3514 |  | WTG Unscheduled Maintenance | 8893 | 12.3514
4013 | 2025-03-24 | 2025 | 2025 | 2025-03-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 172 | SLC MF torque protection | Break down | 0.32361 | 0.32361 | 0.34375 | 0 | 0.48333 | 0.48333 | Checked related error data log then reset & start WTG. | Close | 0.01859 | O2-01 | 215.0632 |  | WTG Unscheduled Maintenance | 10679 | 215.0632
4014 | 2025-03-24 | 2025 | 2025 | 2025-03-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 172 | SLC MF torque protection | Break down | 0.99444 | 0.99444 | 0.99792 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & start WTG. | Close | 0.0032051 | O2-01 | 37.0799 |  | WTG Unscheduled Maintenance | 10679 | 37.0799
4015 | 2025-03-25 | 2025 | 2025 | 2025-03-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 58 | Wind dir.dev. level 2 | Break down | 0.61597 | 0.61597 | 0.61667 | 0 | 0.016667 | 0.016667 | Checked related error data log then reset & start WTG. | Close | 0.00064103 | O2-05 | 16.6431 |  | WTG Unscheduled Maintenance | 23966 | 16.6431
4016 | 2025-03-25 | 2025 | 2025 | 2025-03-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.41944 | 0.41944 | 0.71597 | 0 | 7.1167 | 7.1167 | WTG stop for YPM day-2 activity complate than start WTG. | Close | 0.27372 | O2-02 | 6889.2299 |  | WTG Scheduled Maintenance | 23233 | 6889.2299
4017 | 2025-03-25 | 2025 | 2025 | 2025-03-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 153 | SLC SF max. cable winding | Break down | 0.074306 | 0.074306 | 0.10278 | 0 | 0.68333 | 0.68333 | WTG stop and Yaw cable twist 0 degree done than reset and start WTG. | Close | 0.026282 | O2-26 | 582.9972 |  | WTG Unscheduled Maintenance | 20476 | 582.9972
4018 | 2025-03-25 | 2025 | 2025 | 2025-03-01 | 1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 6625 | Check vane! | Break down | 0.86806 | 0.86806 | 0.89375 | 0 | 0.61667 | 0.61667 | Checked related error data log then check error related all perameter than reset & start WTG. | Close | 0.023718 | O2-12 | 563.1194 |  | WTG Unscheduled Maintenance | 21916 | 563.1194
4019 | 2025-03-25 | 2025 | 2025 | 2025-03-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Others | 0.625 | 0.625 | 0.63403 | 0 | 0.21667 | 0.21667 | WTG stop for Customer Audit work. | Close | 0.0083333 | O2-11 | 154.5014 |  | WTG Breakdown Maintenance | 17114 | 154.5014
4020 | 2025-03-25 | 2025 | 2025 | 2025-03-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.52431 | 0.52431 | 0.52569 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2-22 | 35.8389 |  | WTG Unscheduled Maintenance | 25804 | 35.8389
4021 | 2025-03-25 | 2025 | 2025 | 2025-03-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.24653 | 0.24653 | 0.25833 | 0 | 0.28333 | 0.28333 | Checked related error data log then check error related all perameter than reset & start WTG. | Close | 0.010897 | O2-06 | 257.7625 |  | WTG Unscheduled Maintenance | 21834 | 257.7625
4022 | 2025-03-25 | 2025 | 2025 | 2025-03-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.35208 | 0.35208 | 0.36319 | 0 | 0.26667 | 0.26667 | Checked related error data log then check error related all perameter than reset & start WTG. | Close | 0.010256 | O2-06 | 242.6 |  | WTG Unscheduled Maintenance | 21834 | 242.6
4023 | 2025-03-25 | 2025 | 2025 | 2025-03-01 | 1 | O2_21 | TQGXIIPL | GEDA | 3.846% | 58 | Wind dir.dev. level 2 | Break down | 0.81736 | 0.81736 | 0.81875 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & start WTG. | Close | 0.0012821 | O2-06 | 30.325 |  | WTG Unscheduled Maintenance | 21834 | 30.325
4024 | 2025-03-25 | 2025 | 2025 | 2025-03-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Others | 0.66181 | 0.66181 | 0.66458 | 0 | 0.066667 | 0.066667 | WTG stop for Customer Audit work. | Close | 0.0025641 | O2-20 | 62.8667 |  | WTG Breakdown Maintenance | 22632 | 62.8667
4025 | 2025-03-25 | 2025 | 2025 | 2025-03-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 172 | SLC MF torque protection | Break down | 0.025694 | 0.025694 | 0.040278 | 0 | 0.35 | 0.35 | Checked related error data log then check error related all perameter than reset & start WTG. | Close | 0.013462 | O2-01 | 384.6063 |  | WTG Unscheduled Maintenance | 26373 | 384.6063
4026 | 2025-03-25 | 2025 | 2025 | 2025-03-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 153 | SLC SF max. cable winding | Break down | 0 | 0 | 0.055556 | 0 | 1.3333 | 1.3333 | Attend and check error related ckt than wtg yaw cable twist sensor all connection check and retight than cable twist removed than reset and Start WTG. | Close | 0.051282 | O2-07 | 440.8889 |  | WTG Unscheduled Maintenance | 7936 | 440.8889
4027 | 2025-03-25 | 2025 | 2025 | 2025-03-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 153 | SLC SF max. cable winding | Break down | 0.82292 | 0.89583 | 1899-12-31 | 1.75 | 2.5 | 4.25 | Attend and check error related ckt than found Yaw Cable twist Main CW-CCW switch main Screw Mechanism not properly working so wip, | Close | 0.16346 | O2-07 | 1405.3333 |  | WTG Unscheduled Maintenance | 7936 | 1405.3333
4028 | 2025-03-26 | 2025 | 2025 | 2025-03-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Break down | 0.32986 | 0.40972 | 0.475 | 1.9167 | 1.5667 | 3.4833 | Attend and check error related ckt and found 1.7 Ohm Flat Resistor faulty so replace it and start WTG. | Close | 0.13397 | O2-26 | 2818.3069 |  | WTG Unscheduled Maintenance | 19418 | 2818.3069
4029 | 2025-03-26 | 2025 | 2025 | 2025-03-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Blade cleaning work | 0.48611 | 0.48611 | 0.8125 | 0 | 7.8333 | 7.8333 | WTG manual stop for blade cleaning work , one blade completed | Close | 0.30128 | O2-05 | 8534.7431 |  | WTG Breakdown Maintenance | 26149 | 8534.7431
4030 | 2025-03-26 | 2025 | 2025 | 2025-03-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.47014 | 0.47014 | 0.47222 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | O2-02 | 45.0479 |  | WTG Unscheduled Maintenance | 21623 | 45.0479
4031 | 2025-03-26 | 2025 | 2025 | 2025-03-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.48333 | 0.48333 | 0.4875 | 0 | 0.1 | 0.1 | Checked related error data log then check error related all perameter than apply soft reboot & start WTG. | Close | 0.0038462 | O2-02 | 90.0958 |  | WTG Unscheduled Maintenance | 21623 | 90.0958
4032 | 2025-03-26 | 2025 | 2025 | 2025-03-01 | 1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.64583 | 0.64583 | 0.65 | 0 | 0.1 | 0.1 | Checked related error data log then reset & start WTG. | Close | 0.0038462 | O2-21 | 100.1792 |  | WTG Unscheduled Maintenance | 24043 | 100.1792
4033 | 2025-03-26 | 2025 | 2025 | 2025-03-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.53125 | 0.53125 | 0.53264 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & start WTG. | Close | 0.0012821 | O2-15 | 26.3069 |  | WTG Unscheduled Maintenance | 18941 | 26.3069
4034 | 2025-03-26 | 2025 | 2025 | 2025-03-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 2810 | Service generator brushes | Break down | 0.77847 | 0.80208 | 0.82778 | 0.56667 | 0.61667 | 1.1833 | Attend and wtg check found Brush was warn out so check slipring track and also check brush holder and found Brush wear out so replace then reset and start wtg | Close | 0.045513 | O2-11 | 920.5347 |  | WTG Unscheduled Maintenance | 18670 | 920.5347
4035 | 2025-03-26 | 2025 | 2025 | 2025-03-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.85556 | 0.85556 | 0.88264 | 0 | 0.65 | 0.65 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.025 | O2-11 | 505.6458 |  | WTG Breakdown Maintenance | 18670 | 505.6458
4036 | 2025-03-26 | 2025 | 2025 | 2025-03-01 | 1 | O2_19 | TQGXIIPL | GEDA | 3.846% | 153 | SLC SF max. cable winding | Break down | 0 | 0 | 0.061806 | 0 | 1.4833 | 1.4833 | Attend and check error related ckt than found Yaw Cable twist Main CW-CCW switch main Screw Mechanism not properly working so Yaw cable twist sensor replace than reset and start WTG. | Close | 0.057051 | O2-07 | 1292.416 |  | WTG Unscheduled Maintenance | 20911 | 1292.416
4037 | 2025-03-26 | 2025 | 2025 | 2025-03-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 172 | SLC MF torque protection | Break down | 0.50347 | 0.50347 | 0.56597 | 0 | 1.5 | 1.5 | Attend and check error related ckt than clean rotor Brake pad and also check brake pad thickness and rotor brake pad temp.sensor connection check found ok than reset and start WTG. | Close | 0.057692 | O2-01 | 1311.625 |  | WTG Unscheduled Maintenance | 20986 | 1311.625
4038 | 2025-03-27 | 2025 | 2025 | 2025-03-01 | 1 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Blade cleaning work | 0.44097 | 0.44097 | 0.86667 | 0 | 10.2167 | 10.2167 | WTG manual stop for blade cleaning work. | Close | 0.39295 | O2-05 | 9999.1368 |  | WTG Breakdown Maintenance | 23489 | 9999.1368
4039 | 2025-03-27 | 2025 | 2025 | 2025-03-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.22292 | 0.22292 | 0.22639 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & start WTG. | Close | 0.0032051 | O2-02 | 62.2812 |  | WTG Unscheduled Maintenance | 17937 | 62.2812
4040 | 2025-03-27 | 2025 | 2025 | 2025-03-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.47431 | 0.47431 | 0.49375 | 0 | 0.46667 | 0.46667 | Checked related error data log then check error related all perameter than apply soft reboot & start WTG. | Close | 0.017949 | O2-02 | 348.775 |  | WTG Unscheduled Maintenance | 17937 | 348.775
4041 | 2025-03-27 | 2025 | 2025 | 2025-03-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 2810 | Service generator brushes | Break down | 0.34028 | 0.38542 | 0.5625 | 1.0833 | 4.25 | 5.3333 | Attend and wtg check found Brush was warn out so check slipring track and clean it and also check brush holder and found Brush wear out so replace then reset and start wtg | Close | 0.20513 | O2-11 | 4203.7778 |  | WTG Unscheduled Maintenance | 18917 | 4203.7778
4042 | 2025-03-27 | 2025 | 2025 | 2025-03-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.59792 | 0.59792 | 0.6 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | O2-06 | 43.8979 |  | WTG Unscheduled Maintenance | 21071 | 43.8979
4042 | 2025-03-28 | 2025 | 2025 | 2025-03-01 | 1 | O2_01 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.59583 | 0.59583 | 0.6 | 0 | 0.1 | 0.1 | Checked related error data log then reset & start WTG. | Close | 0.0038462 | O2-26 | 111.0333 |  | WTG Unscheduled Maintenance | 26648 | 111.0333
4042 | 2025-03-28 | 2025 | 2025 | 2025-03-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 2810 | Service generator brushes | Major BD | 0.34028 | 0.45833 | 0.74375 | 2.8333 | 6.85 | 9.6833 | Attend and check surface area for roughness, use 400mm Grit emery cloth and clean it smoothly the surface cleaned with Emery paper,check run out and phase out by Dial gauge.Interchange both earthing brush springs with O2-14 and replace earthing brush than start WTG. | Close | 0.37244 | O2-11 | 11635.7354 |  | WTG Unscheduled Maintenance | 28839 | 11635.7354
4042 | 2025-03-28 | 2025 | 2025 | 2025-03-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | ROW issue | 0.46528 | 0.46528 | 0.64722 | 0 | 4.3667 | 4.3667 | WTG stop for Blade Cleaning work but ROW Issue Blade cleanning work Cancel. | Close | 0.16795 | O2-12 | 5123.9194 |  | WTG Breakdown Maintenance | 28162 | 5123.9194
4042 | 2025-03-28 | 2025 | 2025 | 2025-03-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.56528 | 0.56528 | 0.56944 | 0 | 0.1 | 0.1 | Checked related error data log then reset & start WTG. | Close | 0.0038462 | O2-01 | 123.0333 |  | WTG Unscheduled Maintenance | 29528 | 123.0333
4043 | 2025-03-29 | 2025 | 2025 | 2025-03-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.6125 | 0.6125 | 0.61667 | 0 | 0.1 | 0.1 | Checked related error data log then reset & start WTG. | Close | 0.0038462 | O2-07 | 112.8958 |  | WTG Unscheduled Maintenance | 27095 | 112.8958
4044 | 2025-03-29 | 2025 | 2025 | 2025-03-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.17708 | 0.17708 | 0.18333 | 0 | 0.15 | 0.15 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.0057692 | O2-02 | 217.7562 |  | WTG Breakdown Maintenance | 34841 | 217.7562
4045 | 2025-03-29 | 2025 | 2025 | 2025-03-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.1 | 0.1 | 0.125 | 0 | 0.6 | 0.6 | Checked related error data log then check error related all perameter than apply soft reboot & start WTG. | Close | 0.023077 | O2-02 | 871.025 |  | WTG Unscheduled Maintenance | 34841 | 871.025
4046 | 2025-03-29 | 2025 | 2025 | 2025-03-01 | 1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.46944 | 0.46944 | 0.47361 | 0 | 0.1 | 0.1 | Auto Reset | Close | 0.0038462 | O2-04 | 121.4 |  | WTG Unscheduled Maintenance | 29136 | 121.4
4047 | 2025-03-29 | 2025 | 2025 | 2025-03-01 | 1 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.43194 | 0.43194 | 0.49792 | 0 | 1.5833 | 1.5833 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.060897 | O2-15 | 2208.1562 |  | WTG Breakdown Maintenance | 33471 | 2208.1562
4048 | 2025-03-29 | 2025 | 2025 | 2025-03-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.13333 | 0.13333 | 0.27361 | 0 | 3.3667 | 3.3667 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.12949 | O2-11 | 4636.1806 |  | WTG Breakdown Maintenance | 33050 | 4636.1806
4049 | 2025-03-29 | 2025 | 2025 | 2025-03-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.8625 | 0.8625 | 0.86667 | 0 | 0.1 | 0.1 | Auto Reset | Close | 0.0038462 | O2-11 | 137.7083 |  | WTG Unscheduled Maintenance | 33050 | 137.7083
4050 | 2025-03-29 | 2025 | 2025 | 2025-03-01 | 1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.14097 | 0.14097 | 0.29306 | 0 | 3.65 | 3.65 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.14038 | O2-12 | 5038.9771 |  | WTG Breakdown Maintenance | 33133 | 5038.9771
4051 | 2025-03-29 | 2025 | 2025 | 2025-03-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 550 | Pitch current asymmetry | Break down | 0.35417 | 0.35417 | 0.35625 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | O2-10 | 64.9687 |  | WTG Unscheduled Maintenance | 31185 | 64.9687
4052 | 2025-03-29 | 2025 | 2025 | 2025-03-01 | 1 | O2_17 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Blade cleaning work | 0.41875 | 0.41875 | 0.82222 | 0 | 9.6833 | 9.6833 | WTG manual stop for blade cleaning work. | Close | 0.37244 | O2-22 | 13232.6785 |  | WTG Breakdown Maintenance | 32797 | 13232.6785
4053 | 2025-03-29 | 2025 | 2025 | 2025-03-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.75556 | 0.75556 | 0.76042 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & start WTG. | Close | 0.0044872 | O2-06 | 140.0194 |  | WTG Unscheduled Maintenance | 28804 | 140.0194
4054 | 2025-03-29 | 2025 | 2025 | 2025-03-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.50833 | 0.50833 | 0.5125 | 0 | 0.1 | 0.1 | Checked related error data log then reset & start WTG. | Close | 0.0038462 | O2-06 | 120.0167 |  | WTG Unscheduled Maintenance | 28804 | 120.0167
4055 | 2025-03-29 | 2025 | 2025 | 2025-03-01 | 1 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.60903 | 0.60903 | 0.61042 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & start WTG. | Close | 0.0012821 | O2-06 | 40.0056 |  | WTG Unscheduled Maintenance | 28804 | 40.0056
4056 | 2025-03-29 | 2025 | 2025 | 2025-03-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.28194 | 0.28194 | 0.28958 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & start WTG. | Close | 0.0070513 | O2-20 | 237.7451 |  | WTG Unscheduled Maintenance | 31123 | 237.7451
4057 | 2025-03-29 | 2025 | 2025 | 2025-03-01 | 1 | O2_24 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.30972 | 0.30972 | 0.31736 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & start WTG. | Close | 0.0070513 | O2-20 | 237.7451 |  | WTG Unscheduled Maintenance | 31123 | 237.7451
4058 | 2025-03-30 | 2025 | 2025 | 2025-03-01 | 1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.14028 | 0.14028 | 0.14792 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & start WTG. | Close | 0.0070513 | O2-26 | 193.6535 |  | WTG Unscheduled Maintenance | 25351 | 193.6535
4059 | 2025-03-30 | 2025 | 2025 | 2025-03-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.099306 | 0.099306 | 0.15208 | 0 | 1.2667 | 1.2667 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.048718 | O2-11 | 1294.2694 |  | WTG Breakdown Maintenance | 24523 | 1294.2694
4060 | 2025-03-30 | 2025 | 2025 | 2025-03-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.93194 | 0.93194 | 1899-12-31 | 0 | 1.6333 | 1.6333 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.062821 | O2-11 | 1668.9264 |  | WTG Breakdown Maintenance | 24523 | 1668.9264
4061 | 2025-03-30 | 2025 | 2025 | 2025-03-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.32431 | 0.32431 | 0.32639 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | O2-06 | 32.5937 |  | WTG Unscheduled Maintenance | 15645 | 32.5937
4062 | 2025-03-30 | 2025 | 2025 | 2025-03-01 | 1 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.13958 | 0.13958 | 0.15625 | 0 | 0.4 | 0.4 | Checked related error data log then check error related all perameters then appllied soft reboot & started WTG. | Close | 0.015385 | O2-01 | 460.6167 |  | WTG Unscheduled Maintenance | 27637 | 460.6167
4063 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | 1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 551 | Pitch motor current too high | Break down | 0.11319 | 0.11319 | 0.12222 | 0 | 0.21667 | 0.21667 | Checked related error data log then check error related all perameter than apply soft reboot & started WTG. | Close | 0.0083333 | O2-09 | 253.9243 |  | WTG Unscheduled Maintenance | 28127 | 253.9243
4064 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | 1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.46528 | 0.46528 | 0.62569 | 0 | 3.85 | 3.85 | Attend and check Hydrolic system and found 1 nos Yaw Caliper cylinder not working Properly then replace with new Yaw Caliper then started WTG. | Close | 0.14808 | O2-07 | 3392.8125 |  | WTG Breakdown Maintenance | 21150 | 3392.8125
4065 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | 1 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Auto reset | 0.90347 | 0.90347 | 0.90556 | 0 | 0.05 | 0.05 | Auto Reset | Close | 0.0019231 | O2-02 | 49.5687 |  | WTG Unscheduled Maintenance | 23793 | 49.5687
4066 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0 | 0 | 0.0097222 | 0 | 0.23333 | 0.23333 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.0089744 | O2-11 | 258.9222 |  | WTG Breakdown Maintenance | 26632 | 258.9222
4067 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.075 | 0.075 | 0.079167 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | O2-11 | 110.9667 |  | WTG Unscheduled Maintenance | 26632 | 110.9667
4068 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | 1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.64375 | 0.64375 | 0.77153 | 0 | 3.0667 | 3.0667 | Turbine stop for Generator slip ring earthing carbon Brush inspection work at that time found carbon brush wear out so replace new carbon brush with take in track shape then reset and started Turbine. | Close | 0.11795 | O2-11 | 3402.9778 |  | WTG Breakdown Maintenance | 26632 | 3402.9778
4069 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | 1 | O2_15 | TQGXIIPL | GEDA | 3.846% | 551 | Pitch motor current too high | Break down | 0.35417 | 0.35417 | 0.35694 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & started WTG. | Close | 0.0025641 | O2-10 | 76.5639 |  | WTG Unscheduled Maintenance | 27563 | 76.5639
4070 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.31042 | 0.31042 | 0.31736 | 0 | 0.16667 | 0.16667 | Checked related error data log then reset & started WTG. | Close | 0.0064103 | O2-06 | 155.6389 |  | WTG Unscheduled Maintenance | 22412 | 155.6389
4071 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | 1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.55903 | 0.55903 | 0.56458 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & started WTG. | Close | 0.0051282 | O2-06 | 124.5111 |  | WTG Unscheduled Maintenance | 22412 | 124.5111
4072 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | 2 | O2_02 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.22014 | 0.22014 | 0.22292 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & started WTG. | Close | 0.0025641 | O2-05 | 68.4056 |  | WTG Unscheduled Maintenance | 24626 | 68.4056
4073 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | 2 | O2_02 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.77917 | 0.77917 | 0.7875 | 0 | 0.2 | 0.2 | Checked related error data log then reset & started WTG. | Close | 0.0076923 | O2-05 | 205.2167 |  | WTG Unscheduled Maintenance | 24626 | 205.2167
4074 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6007 | Overload yaw motors group 1 | Break down | 0.59583 | 0.59583 | 0.60556 | 0 | 0.23333 | 0.23333 | Checked related error data log then reset & started WTG. | Close | 0.0089744 | O2-07 | 158.3361 |  | WTG Unscheduled Maintenance | 16286 | 158.3361
4075 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6007 | Overload yaw motors group 1 | Break down | 0.64236 | 0.64583 | 0.66042 | 0.083333 | 0.35 | 0.43333 | Attend and check error related ckt than found Yaw MPCB Feedback connection loose so tight it than reset and started WTG. | Close | 0.016667 | O2-07 | 294.0528 |  | WTG Unscheduled Maintenance | 16286 | 294.0528
4076 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.39097 | 0.39097 | 0.75 | 0 | 8.6167 | 8.6167 | WTG stop for YPM day-1 activity complate than started WTG. | Close | 0.33141 | O2-15 | 8380.7854 |  | WTG Scheduled Maintenance | 23343 | 8380.7854
4077 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.29514 | 0.29514 | 0.29653 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & started WTG. | Close | 0.0012821 | O2-11 | 29.9708 |  | WTG Unscheduled Maintenance | 21579 | 29.9708
4078 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.88194 | 0.88194 | 0.88333 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & started WTG. | Close | 0.0012821 | O2-06 | 26.6667 |  | WTG Unscheduled Maintenance | 19200 | 26.6667
4079 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.50278 | 0.50278 | 0.50694 | 0 | 0.1 | 0.1 | Check Event log and check Data log after Reset and started wtg | Close | 0.0038462 | O2-26 | 52.825 |  | WTG Unscheduled Maintenance | 12678 | 52.825
4080 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | 2 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.48958 | 0.48958 | 0.49306 | 0 | 0.083333 | 0.083333 | Check Event and check Converter Data log after Reset and started wtg | Close | 0.0032051 | O2-05 | 44.2778 |  | WTG Unscheduled Maintenance | 12752 | 44.2778
4081 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | 2 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.74375 | 0.74375 | 0.74583 | 0 | 0.05 | 0.05 | check event log after check voltage and current data after so ok then reset and started wtg. | Close | 0.0019231 | O2-05 | 26.5667 |  | WTG Unscheduled Maintenance | 12752 | 26.5667
4082 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.74375 | 0.74375 | 0.74514 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2-07 | 10.275 |  | WTG Unscheduled Maintenance | 7398 | 10.275
4083 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Auto reset | 0.4875 | 0.4875 | 0.48958 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2-02 | 19.3521 |  | WTG Unscheduled Maintenance | 9289 | 19.3521
4084 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6056 | High yaw load | Auto reset | 0.64653 | 0.64653 | 0.64861 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | O2-02 | 19.3521 |  | WTG Unscheduled Maintenance | 9289 | 19.3521
4085 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.35 | 0.35 | 0.36667 | 0 | 0.4 | 0.4 | Check Event log and check Nacelle Hydralic Presure value and apply flushing mode on after check value after reset and started wtg | Close | 0.015385 | O2-26 | 211.3 |  | WTG Unscheduled Maintenance | 12678 | 211.3
4086 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 656 | Error pitch converter 1 | Break down | 0.32292 | 0.32292 | 0.34236 | 0 | 0.46667 | 0.46667 | check Event log and check pitch converter 1 Data check snapshot and open hub and check Motor current value so ok after reset and started wtg. | Close | 0.017949 | O2-15 | 258.5722 |  | WTG Unscheduled Maintenance | 13298 | 258.5722
4087 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.4 | 0.4 | 0.64583 | 0 | 5.9 | 5.9 | WTG stop for YPM day-2 activity complate than started WTG. | Close | 0.22692 | O2-15 | 3269.0917 |  | WTG Scheduled Maintenance | 13298 | 3269.0917
4088 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.30764 | 0.30764 | 0.31181 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | O2-11 | 50.05 |  | WTG Unscheduled Maintenance | 12012 | 50.05
4089 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Auto reset | 0.16875 | 0.16875 | 0.17014 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2-22 | 13.0625 |  | WTG Unscheduled Maintenance | 9405 | 13.0625
4090 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.74375 | 0.74375 | 0.74722 | 0 | 0.083333 | 0.083333 | Check Event and check Converter Data log after Reset and started wtg | Close | 0.0032051 | O2-06 | 37.2812 |  | WTG Unscheduled Maintenance | 10737 | 37.2812
4091 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.74375 | 0.74375 | 0.74514 | 0 | 0.033333 | 0.033333 | Check Event and check Converter Data log after Reset and started wtg | Close | 0.0012821 | O2-11 | 16.6833 |  | WTG Unscheduled Maintenance | 12012 | 16.6833
4092 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 6007 | Overload yaw motors group 1 | Break down | 0.56806 | 0.60833 | 0.64167 | 0.96667 | 0.8 | 1.7667 | Attend and wtg check MPCB Check Motor and check all connection so found MPCB Connection loose after then all connection tight after tack trail all candion ok then reset and started wtg. | Close | 0.067949 | O2-01 | 1132.875 |  | WTG Unscheduled Maintenance | 15390 | 1132.875
4093 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | 2 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.74375 | 0.74375 | 0.74722 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & started WTG. | Close | 0.0032051 | O2-01 | 53.4375 |  | WTG Unscheduled Maintenance | 15390 | 53.4375 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
4094 | 2025-04-03 | 2025 | 2025 | 2025-04-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.38125 | 0.38125 | 0.77778 | 0 | 9.5167 | 9.5167 | WTG stop for YPM day-1 activity complate than started WTG. | Close | 0.36603 | O2-26 | 5419.3451 |  | WTG Scheduled Maintenance | 13667 | 5419.3451
4095 | 2025-04-03 | 2025 | 2025 | 2025-04-01 | 2 | O2_07 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.5 | 0.5 | 0.50278 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & started WTG. | Close | 0.0025641 | O2-04 | 33.0722 |  | WTG Unscheduled Maintenance | 11906 | 33.0722
4096 | 2025-04-03 | 2025 | 2025 | 2025-04-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 153 | SLC SF max. cable winding | Break down | 0.94097 | 0.94097 | 0.95694 | 0 | 0.38333 | 0.38333 | Check Data log and all Perameter check and Nacell angle check and check Angle of twist after Removed cable twist after trail so ok then started wtg. | Close | 0.014744 | O2-26 | 218.2924 |  | WTG Unscheduled Maintenance | 13667 | 218.2924
4097 | 2025-04-03 | 2025 | 2025 | 2025-04-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Auto reset | 0.45903 | 0.45903 | 0.45972 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | O2-15 | 11.2097 |  | WTG Unscheduled Maintenance | 16142 | 11.2097
4098 | 2025-04-03 | 2025 | 2025 | 2025-04-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Auto reset | 0.46736 | 0.46736 | 0.46806 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | O2-15 | 11.2097 |  | WTG Unscheduled Maintenance | 16142 | 11.2097
4099 | 2025-04-03 | 2025 | 2025 | 2025-04-01 | 2 | O2_14 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.52778 | 0.52778 | 0.53681 | 0 | 0.21667 | 0.21667 | check Data log and converter Data check after so ok then reset and started wtg. | Close | 0.0083333 | O2-12 | 130.5868 |  | WTG Unscheduled Maintenance | 14465 | 130.5868
4100 | 2025-04-03 | 2025 | 2025 | 2025-04-01 | 2 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.44792 | 0.44792 | 0.66111 | 0 | 5.1167 | 5.1167 | Attend and check related ckt so found QA 7.1 Grid filter contactor burnout and 2 nos fuse faulty after Replaced all cable between contactor to fuse and contactor to capacitor . Then we taken all capacitor value found all normal . Then we have replaced both QA7.1 And QA7.2 Contactor and all 6 nos cable between contactor to fuse and fuse to capacitor and 2 nos fuse after complete all cable rooting properly we have perform a precharge , grid filter and GSC Test found all values normal so we started the turbine. | Close | 0.19679 | O2-21 | 2486.9132 |  | WTG Unscheduled Maintenance | 11665 | 2486.9132
4101 | 2025-04-04 | 2025 | 2025 | 2025-04-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 5550 | Low hydraulic oil level | Break down | 0.17083 | 0.17083 | 0.2625 | 0 | 2.2 | 2.2 | Attend and wtg check releted circuit and check all valve and after oil top up after trail so ok then reset and started wtg. | Close | 0.084615 | O2-26 | 654.775 |  | WTG Unscheduled Maintenance | 7143 | 654.775
4102 | 2025-04-04 | 2025 | 2025 | 2025-04-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.40972 | 0.40972 | 0.64097 | 0 | 5.55 | 5.55 | WTG stop for YPM day-2 activity complate than started WTG. | Close | 0.21346 | O2-26 | 1651.8188 |  | WTG Scheduled Maintenance | 7143 | 1651.8188
4103 | 2025-04-04 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Auto reset | 0.21181 | 0.21181 | 0.21389 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2-02 | 28.0292 |  | WTG Unscheduled Maintenance | 13454 | 28.0292
4104 | 2025-04-04 | 2025 | 2025 | 2025-04-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Auto reset | 0.0625 | 0.0625 | 0.070139 | 0 | 0.18333 | 0.18333 | Auto reset | Close | 0.0070513 | O2-26 | 54.5646 |  | WTG Unscheduled Maintenance | 7143 | 54.5646
4105 | 2025-04-04 | 2025 | 2025 | 2025-04-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.094444 | 0.094444 | 0.11181 | 0 | 0.41667 | 0.41667 | Checked related error data log then reset & started WTG. | Close | 0.016026 | O2-26 | 124.0104 |  | WTG Unscheduled Maintenance | 7143 | 124.0104
4106 | 2025-04-04 | 2025 | 2025 | 2025-04-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 153 | SLC SF max. cable winding | Break down | 0.95417 | 0.95417 | 1899-12-31 | 0 | 1.1 | 1.1 | Check Data log and all Perameter check and Nacell angle check and check Angle of twist after Removed cable twist after trail so ok then started wtg. | Close | 0.042308 | O2-26 | 327.3875 |  | WTG Unscheduled Maintenance | 7143 | 327.3875
4107 | 2025-04-04 | 2025 | 2025 | 2025-04-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down | 0.19167 | 0.19167 | 0.34375 | 0 | 3.65 | 3.65 | Attend and wtg check Hydraulic Pump 9.1 Valve and Hydraulic oil top up after check all pipe and flushing mode on and check pressure so ok after trail then reset and started wtg. | Close | 0.14038 | O2-14 | 1482.2042 |  | WTG Unscheduled Maintenance | 9746 | 1482.2042
4108 | 2025-04-04 | 2025 | 2025 | 2025-04-01 | 2 | O2_24 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.48819 | 0.48819 | 0.48958 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2-20 | 15.1403 |  | WTG Unscheduled Maintenance | 10901 | 15.1403
4109 | 2025-04-04 | 2025 | 2025 | 2025-04-01 | 2 | O2_24 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down | 0.81597 | 0.81597 | 1899-12-31 | 0 | 4.4167 | 4.4167 | Attend and wtg check Hydraulic unit valve and check pressure and check all valv after replace 9.1 valv and top up hydraulic oil wtg working pogress | open | 0.16987 | O2-20 | 2006.0868 |  | WTG Unscheduled Maintenance | 10901 | 2006.0868
4110 | 2025-04-05 | 2025 | 2025 | 2025-04-01 | 2 | O2_03 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.25972 | 0.25972 | 0.62083 | 0 | 8.6667 | 8.6667 | WTG stop for YPM day-1 activity complate than started WTG. | Close | 0.33333 | O2-09 | 3911.5556 |  | WTG Scheduled Maintenance | 10832 | 3911.5556
4111 | 2025-04-05 | 2025 | 2025 | 2025-04-01 | 2 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.92361 | 0.92361 | 0.94722 | 0 | 0.56667 | 0.56667 | Check Data log and all Perameter check and Nacell angle check and check Angle of twist after Removed cable twist after trail so ok then started wtg. | Close | 0.021795 | O2-04 | 229.8069 |  | WTG Unscheduled Maintenance | 9733 | 229.8069
4112 | 2025-04-05 | 2025 | 2025 | 2025-04-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 153 | SLC SF max. cable winding | Break down | 0 | 0 | 0.061806 | 0 | 1.4833 | 1.4833 | Check Data log and all Perameter check and Nacell angle check and check Angle of twist after Removed cable twist after trail so ok then started wtg. | Close | 0.057051 | O2-26 | 536.6576 |  | WTG Unscheduled Maintenance | 8683 | 536.6576
4113 | 2025-04-05 | 2025 | 2025 | 2025-04-01 | 2 | O2_14 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Auto reset | 0.29653 | 0.29653 | 0.29722 | 0 | 0.016667 | 0.016667 | auto reset | Close | 0.00064103 | O2-12 | 6.3285 |  | WTG Unscheduled Maintenance | 9113 | 6.3285
4114 | 2025-04-05 | 2025 | 2025 | 2025-04-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Auto reset | 0.37292 | 0.37292 | 0.375 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2-11 | 20.4792 |  | WTG Unscheduled Maintenance | 9830 | 20.4792
4115 | 2025-04-05 | 2025 | 2025 | 2025-04-01 | 2 | O2_24 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Major BD | 0 | 0 | 0.69792 | 0 | 16.75 | 16.75 | Attend and check than hydraulic oil level than found ok than check 9.1 Valve than check pressure value devuation in SAM than found pressure is suddenly drop so replace 9.1 valve and fluxing but same error occureded so check all other valve than check Accumulator than set rotor pressure proper than take trail than nothing abnormal so reset and start turbine. | Close | 0.64423 | O2-20 | 5388.6146 |  | WTG Unscheduled Maintenance | 7721 | 5388.6146
4116 | 2025-04-05 | 2025 | 2025 | 2025-04-01 | 2 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Auto reset | 0.37292 | 0.37292 | 0.375 | 0 | 0.05 | 0.05 | Auto Reset | Close | 0.0019231 | O2-01 | 22.4375 |  | WTG Unscheduled Maintenance | 10770 | 22.4375
4117 | 2025-04-06 | 2025 | 2025 | 2025-04-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Auto reset | 0.28889 | 0.28889 | 0.29653 | 0 | 0.18333 | 0.18333 | Auto Reset | Close | 0.0070513 | O2-26 | 113.4757 |  | WTG Unscheduled Maintenance | 14855 | 113.4757
4118 | 2025-04-06 | 2025 | 2025 | 2025-04-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Auto reset | 0.375 | 0.375 | 0.38264 | 0 | 0.18333 | 0.18333 | Auto Reset | Close | 0.0070513 | O2-26 | 113.4757 |  | WTG Unscheduled Maintenance | 14855 | 113.4757
4119 | 2025-04-06 | 2025 | 2025 | 2025-04-01 | 2 | O2_03 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.40278 | 0.40278 | 0.63333 | 0 | 5.5333 | 5.5333 | WTG stop for YPM day-2 activity complate than started WTG. | Close | 0.21282 | O2-09 | 4417.2139 |  | WTG Scheduled Maintenance | 19159 | 4417.2139
4120 | 2025-04-06 | 2025 | 2025 | 2025-04-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.56944 | 0.56944 | 0.59097 | 0 | 0.51667 | 0.51667 | Check Data log and check hydraulic pressure check by sam and apply Manually oil flushing after Manual Yawing CW Check pressure ok after reset and started WTG. | Close | 0.019872 | O2-07 | 585.3618 |  | WTG Unscheduled Maintenance | 27191 | 585.3618
4121 | 2025-04-06 | 2025 | 2025 | 2025-04-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.73681 | 0.73681 | 0.76111 | 0 | 0.58333 | 0.58333 | Check Data log and check hydraulic pressure check by sam and apply Manually oil flushing after Manual Yawing CW Check pressure ok after reset and started WTG. | Close | 0.022436 | O2-07 | 660.8924 |  | WTG Unscheduled Maintenance | 27191 | 660.8924
4122 | 2025-04-06 | 2025 | 2025 | 2025-04-01 | 2 | O2_06 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.43125 | 0.43125 | 0.43542 | 0 | 0.1 | 0.1 | Auto Reset | Close | 0.0038462 | O2-21 | 99.4375 |  | WTG Unscheduled Maintenance | 23865 | 99.4375
4123 | 2025-04-06 | 2025 | 2025 | 2025-04-01 | 2 | O2_07 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.44167 | 0.44167 | 0.45972 | 0 | 0.43333 | 0.43333 | Checked related error data log then reset & started WTG. | Close | 0.016667 | O2-04 | 516.1722 |  | WTG Unscheduled Maintenance | 28588 | 516.1722
4124 | 2025-04-06 | 2025 | 2025 | 2025-04-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Auto reset | 0.25833 | 0.25833 | 0.26597 | 0 | 0.18333 | 0.18333 | Auto Reset | Close | 0.0070513 | O2-26 | 113.4757 |  | WTG Unscheduled Maintenance | 14855 | 113.4757
4125 | 2025-04-06 | 2025 | 2025 | 2025-04-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.10278 | 0.10278 | 0.10556 | 0 | 0.066667 | 0.066667 | Auto Reset | Close | 0.0025641 | O2-15 | 66.725 |  | WTG Unscheduled Maintenance | 24021 | 66.725
4126 | 2025-04-06 | 2025 | 2025 | 2025-04-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.11944 | 0.11944 | 0.12361 | 0 | 0.1 | 0.1 | Auto Reset | Close | 0.0038462 | O2-14 | 86.2917 |  | WTG Unscheduled Maintenance | 20710 | 86.2917
4127 | 2025-04-06 | 2025 | 2025 | 2025-04-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.43056 | 0.43056 | 0.48472 | 0 | 1.3 | 1.3 | Wtg Manual Stop for slip ring inspection work after reset and started wtg | Close | 0.05 | O2-11 | 1169.7292 |  | WTG Breakdown Maintenance | 21595 | 1169.7292
4128 | 2025-04-06 | 2025 | 2025 | 2025-04-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 657 | Error pitch converter 2 | Auto reset | 0.49861 | 0.49861 | 0.5 | 0 | 0.033333 | 0.033333 | Auto Reset | Close | 0.0012821 | O2-22 | 41.1111 |  | WTG Unscheduled Maintenance | 29600 | 41.1111
4129 | 2025-04-06 | 2025 | 2025 | 2025-04-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.80139 | 0.80139 | 0.81181 | 0 | 0.25 | 0.25 | Check event log and check converter Data after trail so ok then reset and started wtg | Close | 0.0096154 | O2-06 | 254.6771 |  | WTG Unscheduled Maintenance | 24449 | 254.6771
4130 | 2025-04-06 | 2025 | 2025 | 2025-04-01 | 2 | O2_20 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.82153 | 0.82153 | 0.85486 | 0 | 0.8 | 0.8 | Check Event log and Converter Data check after SO FOUND coolant Temp High after Temp Normal and started wtg | Close | 0.030769 | O2-24 | 819.4 |  | WTG Unscheduled Maintenance | 24582 | 819.4
4131 | 2025-04-06 | 2025 | 2025 | 2025-04-01 | 2 | O2_21 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Break down | 0.38889 | 0.38889 | 0.40694 | 0 | 0.43333 | 0.43333 | Check Event LOG And Hub Event check after Reboot and trail so ok then reset and started wtg | Close | 0.016667 | O2-06 | 441.4403 |  | WTG Unscheduled Maintenance | 24449 | 441.4403
4132 | 2025-04-06 | 2025 | 2025 | 2025-04-01 | 2 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.52639 | 0.52639 | 0.53056 | 0 | 0.1 | 0.1 | Auto Reset | Close | 0.0038462 | O2-06 | 101.8708 |  | WTG Unscheduled Maintenance | 24449 | 101.8708
4133 | 2025-04-06 | 2025 | 2025 | 2025-04-01 | 2 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.64792 | 0.64792 | 0.65556 | 0 | 0.18333 | 0.18333 | Auto Reset | Close | 0.0070513 | O2-06 | 186.7632 |  | WTG Unscheduled Maintenance | 24449 | 186.7632
4134 | 2025-04-06 | 2025 | 2025 | 2025-04-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.79653 | 0.79653 | 0.79792 | 0 | 0.033333 | 0.033333 | Auto Reset | Close | 0.0012821 | O2-11 | 29.9931 |  | WTG Unscheduled Maintenance | 21595 | 29.9931
4135 | 2025-04-07 | 2025 | 2025 | 2025-04-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.16181 | 0.16181 | 0.32292 | 0 | 3.8667 | 3.8667 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.14872 | O2-11 | 4654.9833 |  | WTG Unscheduled Maintenance | 28893 | 4654.9833
4136 | 2025-04-07 | 2025 | 2025 | 2025-04-01 | 2 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.20069 | 0.20069 | 0.27014 | 0 | 1.6667 | 1.6667 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.064103 | O2-12 | 2073.75 |  | WTG Unscheduled Maintenance | 29862 | 2073.75
4137 | 2025-04-07 | 2025 | 2025 | 2025-04-01 | 2 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.29583 | 0.29583 | 0.32292 | 0 | 0.65 | 0.65 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.025 | O2-12 | 808.7625 |  | WTG Unscheduled Maintenance | 29862 | 808.7625
4138 | 2025-04-07 | 2025 | 2025 | 2025-04-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.81528 | 0.81528 | 0.85 | 0 | 0.83333 | 0.83333 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.032051 | O2-11 | 1003.2292 |  | WTG Unscheduled Maintenance | 28893 | 1003.2292
4139 | 2025-04-07 | 2025 | 2025 | 2025-04-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.85694 | 0.85694 | 0.87569 | 0 | 0.45 | 0.45 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.017308 | O2-01 | 582.15 |  | WTG Breakdown Maintenance | 31048 | 582.15
4140 | 2025-04-07 | 2025 | 2025 | 2025-04-01 | 2 | O2_03 | TQGXIIPL | GEDA | 3.846% | 551 | Pitch motor current too high | Auto reset | 0.21528 | 0.21528 | 0.21736 | 0 | 0.05 | 0.05 | Auto Reset | Close | 0.0019231 | O2-09 | 54.525 |  | WTG Unscheduled Maintenance | 26172 | 54.525
4141 | 2025-04-07 | 2025 | 2025 | 2025-04-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.56042 | 0.56042 | 0.57708 | 0 | 0.4 | 0.4 | Check event log and check hydraulic pressure after flushing mode on after check and trail so ok then reset and start wtg. | Close | 0.015385 | O2-07 | 605.1 |  | WTG Unscheduled Maintenance | 36306 | 605.1
4142 | 2025-04-07 | 2025 | 2025 | 2025-04-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Auto reset | 0.68958 | 0.68958 | 0.69167 | 0 | 0.05 | 0.05 | Auto Reset | Close | 0.0019231 | O2-07 | 75.6375 |  | WTG Unscheduled Maintenance | 36306 | 75.6375
4143 | 2025-04-07 | 2025 | 2025 | 2025-04-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.78403 | 0.78403 | 0.79514 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & started WTG. | Close | 0.010256 | O2-07 | 403.4 |  | WTG Unscheduled Maintenance | 36306 | 403.4
4144 | 2025-04-07 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down | 0.325 | 0.325 | 0.33889 | 0 | 0.33333 | 0.33333 | After grid resume time error occurred check event log then reset and started wtg. | Close | 0.012821 | O2-02 | 554.6528 |  | WTG Unscheduled Maintenance | 39935 | 554.6528
4145 | 2025-04-07 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 2521 | Gen.sp.analog <<>> gearb.sp. | Auto reset | 0.73889 | 0.73889 | 0.74028 | 0 | 0.033333 | 0.033333 | Auto Reset | Close | 0.0012821 | O2-02 | 55.4653 |  | WTG Unscheduled Maintenance | 39935 | 55.4653
4146 | 2025-04-07 | 2025 | 2025 | 2025-04-01 | 2 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.46667 | 0.46667 | 0.72083 | 0 | 6.1 | 6.1 | WTG stop for YPM day-1 activity complate than started WTG. | Close | 0.23462 | O2-03 | 7421.9208 |  | WTG Scheduled Maintenance | 29201 | 7421.9208
4147 | 2025-04-07 | 2025 | 2025 | 2025-04-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down | 0.325 | 0.325 | 0.32847 | 0 | 0.083333 | 0.083333 | After grid resume time error occurred check event log then reset and started wtg. | Close | 0.0032051 | O2-12 | 103.6875 |  | WTG Unscheduled Maintenance | 29862 | 103.6875
4148 | 2025-04-07 | 2025 | 2025 | 2025-04-01 | 2 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.55556 | 0.55556 | 0.55694 | 0 | 0.033333 | 0.033333 | Auto Reset | Close | 0.0012821 | O2-10 | 40.9667 |  | WTG Unscheduled Maintenance | 29496 | 40.9667
4149 | 2025-04-07 | 2025 | 2025 | 2025-04-01 | 2 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.61111 | 0.61111 | 0.6125 | 0 | 0.033333 | 0.033333 | Auto Reset | Close | 0.0012821 | O2-10 | 40.9667 |  | WTG Unscheduled Maintenance | 29496 | 40.9667
4150 | 2025-04-07 | 2025 | 2025 | 2025-04-01 | 2 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.30903 | 0.30903 | 0.3125 | 0 | 0.083333 | 0.083333 | Auto Reset | Close | 0.0032051 | O2-21 | 123.3785 |  | WTG Unscheduled Maintenance | 35533 | 123.3785
4151 | 2025-04-07 | 2025 | 2025 | 2025-04-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.80278 | 0.80278 | 0.80972 | 0 | 0.16667 | 0.16667 | Check event log and check converter Data after trail so ok then reset and started wtg | Close | 0.0064103 | O2-06 | 235.75 |  | WTG Unscheduled Maintenance | 33948 | 235.75
4152 | 2025-04-07 | 2025 | 2025 | 2025-04-01 | 2 | O2_20 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.14653 | 0.14653 | 0.15139 | 0 | 0.11667 | 0.11667 | Auto Reset | Close | 0.0044872 | O2-24 | 174.1493 |  | WTG Unscheduled Maintenance | 35825 | 174.1493
4153 | 2025-04-07 | 2025 | 2025 | 2025-04-01 | 2 | O2_20 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.26736 | 0.26736 | 0.27153 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | O2-24 | 149.2708 |  | WTG Unscheduled Maintenance | 35825 | 149.2708
4154 | 2025-04-07 | 2025 | 2025 | 2025-04-01 | 2 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.5 | 0.5 | 0.52431 | 0 | 0.58333 | 0.58333 | Attend and WTG Check temp sensor , fan conditions and connection Replace Panel filter then started Turbine. | Close | 0.022436 | O2-24 | 870.7465 |  | WTG Breakdown Maintenance | 35825 | 870.7465
4155 | 2025-04-07 | 2025 | 2025 | 2025-04-01 | 2 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.47639 | 0.47639 | 0.48056 | 0 | 0.1 | 0.1 | Auto Reset | Close | 0.0038462 | O2-06 | 141.45 |  | WTG Unscheduled Maintenance | 33948 | 141.45
4156 | 2025-04-07 | 2025 | 2025 | 2025-04-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down | 0.82361 | 0.82361 | 0.83889 | 0 | 0.36667 | 0.36667 | Checked related error data log then reset & started WTG. | Close | 0.014103 | O2-01 | 474.3444 |  | WTG Unscheduled Maintenance | 31048 | 474.3444
4157 | 2025-04-07 | 2025 | 2025 | 2025-04-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 650 | Pitch controller communication error | Break down | 0.86667 | 0.86667 | 0.87569 | 0 | 0.21667 | 0.21667 | check event log and check all data after reboot and check so ok then reset and started wtg | Close | 0.0083333 | O2-01 | 280.2944 |  | WTG Unscheduled Maintenance | 31048 | 280.2944
4158 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | 2 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.37569 | 0.37569 | 0.37917 | 0 | 0.083333 | 0.083333 | Check event log and check converter Data after trail so ok then reset and started wtg | Close | 0.0032051 | O2-05 | 103.0764 |  | WTG Unscheduled Maintenance | 29686 | 103.0764
4159 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | 2 | O2_03 | TQGXIIPL | GEDA | 3.846% | 551 | Pitch motor current too high | Break down | 0.29514 | 0.29514 | 0.30556 | 0 | 0.25 | 0.25 | Check event log and check Hub event and check current motor so ok after reset and started wtg | Close | 0.0096154 | O2-09 | 241.0938 |  | WTG Unscheduled Maintenance | 23145 | 241.0938
4160 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.54861 | 0.54861 | 0.55556 | 0 | 0.16667 | 0.16667 | Checked related error data log then reset & started WTG. | Close | 0.0064103 | O2-07 | 221.4167 |  | WTG Unscheduled Maintenance | 31884 | 221.4167
4161 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6300 | Yaw error | Auto reset | 0.65 | 0.65 | 0.65069 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | O2-07 | 22.1417 |  | WTG Unscheduled Maintenance | 31884 | 22.1417
4162 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.73958 | 0.74097 | 0.77431 | 0.033333 | 0.8 | 0.83333 | We Have attened turbine and check in hydraulic system oil level system pressure 9.1 valv conditions found all normal after we check 9.8 valve pressure with gauge found deviation. So correct its and taken trail then started turbine. | Close | 0.032051 | O2-07 | 1107.0833 |  | WTG Unscheduled Maintenance | 31884 | 1107.0833
4163 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.13611 | 0.13611 | 0.13819 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2-02 | 81.0688 |  | WTG Unscheduled Maintenance | 38913 | 81.0688
4164 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.17708 | 0.17708 | 0.23958 | 0 | 1.5 | 1.5 | Attend and wtg check filter and clean after check converter fan condition check so ok after temp sensor connection check and tight then reset and start wtg | Close | 0.057692 | O2-02 | 2432.0625 |  | WTG Unscheduled Maintenance | 38913 | 2432.0625
4165 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.47917 | 0.47917 | 0.55556 | 0 | 1.8333 | 1.8333 | we have attend turbine and check in converter temp sensor value , sensor connection and conditions after taken trail of turbine found temp in noirmal range so started turbine. | Close | 0.070513 | O2-02 | 2972.5208 |  | WTG Unscheduled Maintenance | 38913 | 2972.5208
4166 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Auto reset | 0.27986 | 0.27986 | 0.2875 | 0 | 0.18333 | 0.18333 | Auto reset | Close | 0.0070513 | O2-26 | 182.9972 |  | WTG Unscheduled Maintenance | 23956 | 182.9972
4167 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.87014 | 0.87014 | 0.87222 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2-26 | 49.9083 |  | WTG Unscheduled Maintenance | 23956 | 49.9083
4168 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.90972 | 0.94097 | 0.99306 | 0.75 | 1.25 | 2 | Attend wtg check related circuit than check overvoltage protaction circuit than check surge arrestor and connection than found 24V feedback connection was loose so retight properly than reset and start wtg | Close | 0.076923 | O2-12 | 2727.5 |  | WTG Unscheduled Maintenance | 32730 | 2727.5
4169 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | 2 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.84097 | 0.84097 | 0.84514 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | O2-21 | 134.1625 |  | WTG Unscheduled Maintenance | 32199 | 134.1625
4170 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 2521 | Gen.sp.analog <<>> gearb.sp. | Break down | 0.81667 | 0.81667 | 0.825 | 0 | 0.2 | 0.2 | check event log and check all data after reboot and check so ok then reset and started wtg | Close | 0.0076923 | O2-06 | 263.575 |  | WTG Unscheduled Maintenance | 31629 | 263.575
4171 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | 2 | O2_20 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.60417 | 0.60417 | 0.61389 | 0 | 0.23333 | 0.23333 | Check event log and check converter Data after trail so ok then reset and started wtg | Close | 0.0089744 | O2-24 | 334.8722 |  | WTG Unscheduled Maintenance | 34444 | 334.8722
4172 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.37569 | 0.37569 | 0.37778 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2-11 | 56.5208 |  | WTG Unscheduled Maintenance | 27130 | 56.5208
4173 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.10764 | 0.10764 | 0.11667 | 0 | 0.21667 | 0.21667 | Checked related error data log then reset & started WTG. | Close | 0.0083333 | O2-01 | 297.2937 |  | WTG Unscheduled Maintenance | 32931 | 297.2937
4174 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | 2 | O2_26 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Auto reset | 0.10278 | 0.10278 | 0.11042 | 0 | 0.18333 | 0.18333 | Auto reset | Close | 0.0070513 | O2-01 | 251.5563 |  | WTG Unscheduled Maintenance | 32931 | 251.5563
4175 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | 2 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.37569 | 0.37569 | 0.37778 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2-01 | 68.6062 |  | WTG Unscheduled Maintenance | 32931 | 68.6062
4176 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.12083 | 0.12083 | 0.14097 | 0 | 0.48333 | 0.48333 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.01859 | O2-11 | 546.3681 |  | WTG Breakdown Maintenance | 27130 | 546.3681
4177 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.12153 | 0.12153 | 0.13403 | 0 | 0.3 | 0.3 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.011538 | O2-01 | 411.6375 |  | WTG Breakdown Maintenance | 32931 | 411.6375
4178 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | 2 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.29167 | 0.29167 | 0.54167 | 0 | 6 | 6 | WTG stop for YPM day-2 activity complate than started WTG. | Close | 0.23077 | O2-03 | 7630.75 |  | WTG Scheduled Maintenance | 30523 | 7630.75
4179 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.79792 | 0.79792 | 0.875 | 0 | 1.85 | 1.85 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.071154 | O2-11 | 2091.2708 |  | WTG Breakdown Maintenance | 27130 | 2091.2708
4180 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.82222 | 0.82222 | 0.85417 | 0 | 0.76667 | 0.76667 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.029487 | O2-26 | 765.2611 |  | WTG Breakdown Maintenance | 23956 | 765.2611
4181 | 2025-04-09 | 2025 | 2025 | 2025-04-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Auto reset | 0.070833 | 0.070833 | 0.078472 | 0 | 0.18333 | 0.18333 | Auto reset | Close | 0.0070513 | O2-26 | 179.9722 |  | WTG Unscheduled Maintenance | 23560 | 179.9722
4182 | 2025-04-09 | 2025 | 2025 | 2025-04-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6056 | High yaw load | Auto reset | 0.60694 | 0.60694 | 0.60903 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2-07 | 59.25 |  | WTG Unscheduled Maintenance | 28440 | 59.25
4183 | 2025-04-09 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.3125 | 0.36806 | 0.40139 | 1.3333 | 0.8 | 2.1333 | Attend wtg check inductor cell temp increase so cannibalize temp sensor connection wid another temp sensor ( Now turbine running under observation ) | Close | 0.082051 | O2-02 | 3198.6667 |  | WTG Unscheduled Maintenance | 35985 | 3198.6667
4184 | 2025-04-09 | 2025 | 2025 | 2025-04-01 | 2 | O2_06 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.68403 | 0.68403 | 0.68819 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-21 | 120.7708 |  | WTG Unscheduled Maintenance | 28985 | 120.7708
4185 | 2025-04-09 | 2025 | 2025 | 2025-04-01 | 2 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3065 | Conv. emerg.off type F | Break down | 0.60417 | 0.60417 | 0.61736 | 0 | 0.31667 | 0.31667 | Check event log and check converter Data after trail so ok then reset and started wtg | Close | 0.012179 | O2-21 | 382.441 |  | WTG Unscheduled Maintenance | 28985 | 382.441
4186 | 2025-04-09 | 2025 | 2025 | 2025-04-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Auto reset | 0.64861 | 0.64861 | 0.65069 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2-06 | 59.5292 |  | WTG Unscheduled Maintenance | 28574 | 59.5292
4187 | 2025-04-09 | 2025 | 2025 | 2025-04-01 | 2 | O2_20 | TQGXIIPL | GEDA | 3.846% | 6056 | High yaw load | Auto reset | 0.65 | 0.65 | 0.65139 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2-24 | 44.6431 |  | WTG Unscheduled Maintenance | 32143 | 44.6431
4188 | 2025-04-09 | 2025 | 2025 | 2025-04-01 | 2 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.63819 | 0.63819 | 0.64236 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-06 | 119.0583 |  | WTG Unscheduled Maintenance | 28574 | 119.0583
4189 | 2025-04-09 | 2025 | 2025 | 2025-04-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Break down | 0.8125 | 0.83333 | 1899-12-31 | 0.5 | 4 | 4.5 | Attend And check related circuit found MPCB Trip so we check motor winding connection and found Motor Bearing jam after arrange motor for Mahuva site WIP | open | 0.17308 | O2-11 | 5131.875 |  | WTG Unscheduled Maintenance | 27370 | 5131.875
4190 | 2025-04-09 | 2025 | 2025 | 2025-04-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.15278 | 0.15278 | 0.15764 | 0 | 0.11667 | 0.11667 | Check event log and check converter Data after trail so ok then reset and started wtg | Close | 0.0044872 | O2-01 | 139.4312 |  | WTG Unscheduled Maintenance | 28683 | 139.4312
4191 | 2025-04-10 | 2025 | 2025 | 2025-04-01 | 2 | O2_02 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.63403 | 0.63403 | 0.63681 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & started WTG. | Close | 0.0025641 | O2-05 | 115.4639 |  | WTG Unscheduled Maintenance | 41567 | 115.4639
4192 | 2025-04-10 | 2025 | 2025 | 2025-04-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down | 0.76319 | 0.76319 | 0.76875 | 0 | 0.13333 | 0.13333 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.0051282 | O2-05 | 230.9278 |  | WTG Unscheduled Maintenance | 41567 | 230.9278
4193 | 2025-04-10 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.53333 | 0.53333 | 0.53472 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & started WTG. | Close | 0.0012821 | O2-02 | 62.7542 |  | WTG Unscheduled Maintenance | 45183 | 62.7542
4194 | 2025-04-10 | 2025 | 2025 | 2025-04-01 | 2 | O2_06 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.57153 | 0.57153 | 0.57778 | 0 | 0.15 | 0.15 | Checked related error data log then reset & started WTG. | Close | 0.0057692 | O2-18 | 207.6125 |  | WTG Unscheduled Maintenance | 33218 | 207.6125
4195 | 2025-04-10 | 2025 | 2025 | 2025-04-01 | 2 | O2_06 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down | 0.79514 | 0.79514 | 0.81528 | 0 | 0.48333 | 0.48333 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.01859 | O2-18 | 668.9736 |  | WTG Unscheduled Maintenance | 33218 | 668.9736
4196 | 2025-04-10 | 2025 | 2025 | 2025-04-01 | 2 | O2_07 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.14306 | 0.14306 | 0.14722 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-19 | 193.2292 |  | WTG Unscheduled Maintenance | 46375 | 193.2292
4197 | 2025-04-10 | 2025 | 2025 | 2025-04-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.14375 | 0.14375 | 0.15139 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & started WTG. | Close | 0.0070513 | O2-01 | 288.9486 |  | WTG Unscheduled Maintenance | 37826 | 288.9486
4198 | 2025-04-10 | 2025 | 2025 | 2025-04-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.39861 | 0.39861 | 0.40625 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & started WTG. | Close | 0.0070513 | O2-01 | 288.9486 |  | WTG Unscheduled Maintenance | 37826 | 288.9486
4199 | 2025-04-10 | 2025 | 2025 | 2025-04-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.72431 | 0.72431 | 0.8125 | 0 | 2.1167 | 2.1167 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.08141 | O2-01 | 3336.0431 |  | WTG Breakdown Maintenance | 37826 | 3336.0431
4200 | 2025-04-10 | 2025 | 2025 | 2025-04-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.57708 | 0.57708 | 0.58125 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-12 | 161.2458 |  | WTG Unscheduled Maintenance | 38699 | 161.2458
4201 | 2025-04-10 | 2025 | 2025 | 2025-04-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down | 0.79653 | 0.79653 | 0.80833 | 0 | 0.28333 | 0.28333 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.010897 | O2-11 | 417.9993 |  | WTG Unscheduled Maintenance | 35407 | 417.9993
4202 | 2025-04-10 | 2025 | 2025 | 2025-04-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.58472 | 0.58472 | 0.58889 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-14 | 153.0208 |  | WTG Unscheduled Maintenance | 36725 | 153.0208
4203 | 2025-04-10 | 2025 | 2025 | 2025-04-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.65972 | 0.65972 | 0.675 | 0 | 0.36667 | 0.36667 | check event log and check all data after reboot and check so ok then reset and started wtg | Close | 0.014103 | O2-14 | 561.0764 |  | WTG Unscheduled Maintenance | 36725 | 561.0764
4204 | 2025-04-10 | 2025 | 2025 | 2025-04-01 | 2 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.71111 | 0.71111 | 0.71944 | 0 | 0.2 | 0.2 | Checked related error data log then reset & started WTG. | Close | 0.0076923 | O2-10 | 297.3833 |  | WTG Unscheduled Maintenance | 35686 | 297.3833
4205 | 2025-04-10 | 2025 | 2025 | 2025-04-01 | 2 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.73333 | 0.73333 | 0.78889 | 0 | 1.3333 | 1.3333 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.051282 | O2-10 | 1982.5556 |  | WTG Breakdown Maintenance | 35686 | 1982.5556
4206 | 2025-04-10 | 2025 | 2025 | 2025-04-01 | 2 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.67014 | 0.67014 | 0.67639 | 0 | 0.15 | 0.15 | Checked related error data log then reset & started WTG. | Close | 0.0057692 | O2-20 | 254.8313 |  | WTG Unscheduled Maintenance | 40773 | 254.8313
4207 | 2025-04-10 | 2025 | 2025 | 2025-04-01 | 2 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.69583 | 0.69583 | 0.70903 | 0 | 0.31667 | 0.31667 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.012179 | O2-20 | 537.9771 |  | WTG Unscheduled Maintenance | 40773 | 537.9771
4208 | 2025-04-10 | 2025 | 2025 | 2025-04-01 | 2 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.73403 | 0.73403 | 0.74028 | 0 | 0.15 | 0.15 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.0057692 | O2-20 | 254.8313 |  | WTG Unscheduled Maintenance | 40773 | 254.8313
4209 | 2025-04-10 | 2025 | 2025 | 2025-04-01 | 2 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.75972 | 0.75972 | 0.77431 | 0 | 0.35 | 0.35 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.013462 | O2-20 | 594.6063 |  | WTG Unscheduled Maintenance | 40773 | 594.6063
4210 | 2025-04-10 | 2025 | 2025 | 2025-04-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.37778 | 0.37778 | 0.38125 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & started WTG. | Close | 0.0032051 | O2-06 | 131.5625 |  | WTG Unscheduled Maintenance | 37890 | 131.5625
4111 | 2025-04-10 | 2025 | 2025 | 2025-04-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.75972 | 0.75972 | 0.77361 | 0 | 0.33333 | 0.33333 | check event log and check all data after reboot and check so ok then reset and started wtg | Close | 0.012821 | O2-06 | 526.25 |  | WTG Unscheduled Maintenance | 37890 | 526.25
4212 | 2025-04-10 | 2025 | 2025 | 2025-04-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.77986 | 0.77986 | 0.81875 | 0 | 0.93333 | 0.93333 | check event log and check all data after reboot and check so ok then reset and started wtg | Close | 0.035897 | O2-06 | 1473.5 |  | WTG Unscheduled Maintenance | 37890 | 1473.5
4213 | 2025-04-10 | 2025 | 2025 | 2025-04-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down | 0.67083 | 0.67083 | 0.67708 | 0 | 0.15 | 0.15 | Checked related error data log then reset & started WTG. | Close | 0.0057692 | O2-07 | 266.8625 |  | WTG Unscheduled Maintenance | 42698 | 266.8625
4214 | 2025-04-10 | 2025 | 2025 | 2025-04-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.75833 | 0.75833 | 0.76736 | 0 | 0.21667 | 0.21667 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.0083333 | O2-07 | 385.4681 |  | WTG Unscheduled Maintenance | 42698 | 385.4681
4215 | 2025-04-10 | 2025 | 2025 | 2025-04-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.80625 | 0.80625 | 0.81111 | 0 | 0.11667 | 0.11667 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.0044872 | O2-07 | 207.5597 |  | WTG Unscheduled Maintenance | 42698 | 207.5597
4216 | 2025-04-10 | 2025 | 2025 | 2025-04-01 | 2 | O2_21 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.60764 | 0.60764 | 0.61181 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-18 | 138.4083 |  | WTG Unscheduled Maintenance | 33218 | 138.4083
4217 | 2025-04-10 | 2025 | 2025 | 2025-04-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Break down | 0 | 0 | 0.17986 | 0 | 4.3167 | 4.3167 | Attend And check related circuit found MPCB Trip so we check motor winding connection and found Motor Bearing jam after arrange motor and replace Motor than started WTG. | Close | 0.16603 | O2-08 | 5141.6896 |  | WTG Breakdown Maintenance | 28587 | 5141.6896
4218 | 2025-04-10 | 2025 | 2025 | 2025-04-01 | 2 | O2_26 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.16736 | 0.16736 | 0.17569 | 0 | 0.2 | 0.2 | Checked related error data log then reset & started WTG. | Close | 0.0076923 | O2-08 | 238.225 |  | WTG Unscheduled Maintenance | 28587 | 238.225
4219 | 2025-04-11 | 2025 | 2025 | 2025-04-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.53819 | 0.53819 | 0.54236 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-26 | 174.475 |  | WTG Unscheduled Maintenance | 41874 | 174.475
4220 | 2025-04-11 | 2025 | 2025 | 2025-04-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.59444 | 0.59444 | 0.60417 | 0 | 0.23333 | 0.23333 | Checked related error data log then reset & started WTG. | Close | 0.0089744 | O2-26 | 407.1083 |  | WTG Unscheduled Maintenance | 41874 | 407.1083
4221 | 2025-04-11 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.625 | 0.625 | 0.62917 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-02 | 205.6125 |  | WTG Unscheduled Maintenance | 49347 | 205.6125 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
4222 | 2025-04-11 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.90625 | 0.90625 | 0.91181 | 0 | 0.13333 | 0.13333 | check event log and check all data after reboot and check so ok then reset and started wtg | Close | 0.0051282 | O2-02 | 274.15 |  | WTG Unscheduled Maintenance | 49347 | 274.15
4223 | 2025-04-11 | 2025 | 2025 | 2025-04-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.425 | 0.425 | 0.44375 | 0 | 0.45 | 0.45 | check event log and check all data after reboot and check so ok then reset and started wtg | Close | 0.017308 | O2-26 | 785.1375 |  | WTG Unscheduled Maintenance | 41874 | 785.1375
4224 | 2025-04-11 | 2025 | 2025 | 2025-04-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.72153 | 0.72153 | 0.72569 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-26 | 174.475 |  | WTG Unscheduled Maintenance | 41874 | 174.475
4225 | 2025-04-11 | 2025 | 2025 | 2025-04-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.55972 | 0.55972 | 0.56389 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-15 | 169.4417 |  | WTG Unscheduled Maintenance | 40666 | 169.4417
4226 | 2025-04-11 | 2025 | 2025 | 2025-04-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6056 | High yaw load | Auto reset | 0.57083 | 0.57083 | 0.57292 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2-11 | 77.7167 |  | WTG Unscheduled Maintenance | 37304 | 77.7167
4227 | 2025-04-11 | 2025 | 2025 | 2025-04-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.61111 | 0.61111 | 0.61528 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-11 | 155.4333 |  | WTG Unscheduled Maintenance | 37304 | 155.4333
4228 | 2025-04-11 | 2025 | 2025 | 2025-04-01 | 2 | O2_14 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Major BD | 0.045139 | 0.10417 | 0.32431 | 1.4167 | 5.2833 | 6.7 | Attend and check error related ckt than found Slipring cable short with the Ground than we use temparory Earthing cable for restore the Turbine and plan for the further rectification work in day Shift. | Close | 0.25769 | O2-12 | 11996.6292 |  | WTG Unscheduled Maintenance | 42973 | 11996.6292
4229 | 2025-04-11 | 2025 | 2025 | 2025-04-01 | 2 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR | 0.44583 | 0.44583 | 1899-12-31 | 0 | 13.3 | 13.3 | Turbine stop for Slipring 646 WTR Work WIP, | Close | 0.51154 | O2-12 | 23814.2042 |  | WTG Scheduled Maintenance | 42973 | 23814.2042
4230 | 2025-04-11 | 2025 | 2025 | 2025-04-01 | 2 | O2_16 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.69722 | 0.69722 | 0.70139 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-21 | 167.2167 |  | WTG Unscheduled Maintenance | 40132 | 167.2167
4231 | 2025-04-11 | 2025 | 2025 | 2025-04-01 | 2 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.78333 | 0.78333 | 0.79583 | 0 | 0.3 | 0.3 | check event log and check all data after reboot and check so ok then reset and started wtg | Close | 0.011538 | O2-21 | 501.65 |  | WTG Unscheduled Maintenance | 40132 | 501.65
4232 | 2025-04-11 | 2025 | 2025 | 2025-04-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.55347 | 0.55347 | 0.55556 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | O2-22 | 82.5458 |  | WTG Unscheduled Maintenance | 39622 | 82.5458
4233 | 2025-04-11 | 2025 | 2025 | 2025-04-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.059028 | 0.059028 | 0.067361 | 0 | 0.2 | 0.2 | check event log and check all data after reboot and check so ok then reset and started wtg | Close | 0.0076923 | O2-06 | 331.3667 |  | WTG Unscheduled Maintenance | 39764 | 331.3667
4234 | 2025-04-11 | 2025 | 2025 | 2025-04-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.62986 | 0.62986 | 0.63194 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | O2-06 | 82.8417 |  | WTG Unscheduled Maintenance | 39764 | 82.8417
4235 | 2025-04-11 | 2025 | 2025 | 2025-04-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.64792 | 0.64792 | 0.65208 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-06 | 165.6833 |  | WTG Unscheduled Maintenance | 39764 | 165.6833
4236 | 2025-04-11 | 2025 | 2025 | 2025-04-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.56806 | 0.56806 | 0.57222 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-11 | 155.4333 |  | WTG Unscheduled Maintenance | 37304 | 155.4333
4237 | 2025-04-11 | 2025 | 2025 | 2025-04-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.63958 | 0.63958 | 0.64444 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & started WTG. | Close | 0.0044872 | O2-11 | 181.3389 |  | WTG Unscheduled Maintenance | 37304 | 181.3389
4238 | 2025-04-11 | 2025 | 2025 | 2025-04-01 | 2 | O2_24 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.57639 | 0.57639 | 0.58056 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-20 | 167.4583 |  | WTG Unscheduled Maintenance | 40190 | 167.4583
4239 | 2025-04-11 | 2025 | 2025 | 2025-04-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.48264 | 0.48264 | 0.48681 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-01 | 172.6958 |  | WTG Unscheduled Maintenance | 41447 | 172.6958
4240 | 2025-04-12 | 2025 | 2025 | 2025-04-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.44306 | 0.44306 | 0.47917 | 0 | 0.86667 | 0.86667 | Turbine stop for Software Update Work. | Close | 0.033333 | O2-08 | 253.7889 |  | WTG Unscheduled Maintenance | 7028 | 253.7889
4241 | 2025-04-12 | 2025 | 2025 | 2025-04-01 | 2 | O2_03 | TQGXIIPL | GEDA | 3.846% | 741 | Battery drive trigger by HC | Break down | 0.31389 | 0.31389 | 0.35 | 0 | 0.86667 | 0.86667 | check event log and check all data after reboot and check so ok then reset and started wtg | Close | 0.033333 | O2-09 | 265.2361 |  | WTG Unscheduled Maintenance | 7345 | 265.2361
4242 | 2025-04-12 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.48264 | 0.48264 | 0.49097 | 0 | 0.2 | 0.2 | Turbine stop for Software Update Work. | Close | 0.0076923 | O2-02 | 74.5667 |  | WTG Unscheduled Maintenance | 8948 | 74.5667
4243 | 2025-04-12 | 2025 | 2025 | 2025-04-01 | 2 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR | 0 | 0 | 0.20139 | 0 | 4.8333 | 4.8333 | After done Slipring WTR 646 than reset and started WTG. | Close | 0.1859 | O2-12 | 1567.8125 |  | WTG Scheduled Maintenance | 7785 | 1567.8125
4244 | 2025-04-13 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.91042 | 0.91042 | 0.91667 | 0 | 0.15 | 0.15 | Checked related error data log then reset & started WTG. | Close | 0.0057692 | O2-02 | 178.85 |  | WTG Unscheduled Maintenance | 28616 | 178.85
4245 | 2025-04-13 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.95069 | 0.95069 | 0.95347 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & started WTG. | Close | 0.0025641 | O2-02 | 79.4889 |  | WTG Unscheduled Maintenance | 28616 | 79.4889
4246 | 2025-04-13 | 2025 | 2025 | 2025-04-01 | 2 | O2_06 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.31389 | 0.31389 | 0.32153 | 0 | 0.18333 | 0.18333 | Auto reset | Close | 0.0070513 | O2-21 | 178.4139 |  | WTG Unscheduled Maintenance | 23356 | 178.4139
4247 | 2025-04-13 | 2025 | 2025 | 2025-04-01 | 2 | O2_06 | TQGXIIPL | GEDA | 3.846% | 6056 | High yaw load | Break down | 0.63403 | 0.63403 | 0.63611 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | O2-21 | 48.6583 |  | WTG Unscheduled Maintenance | 23356 | 48.6583
4248 | 2025-04-13 | 2025 | 2025 | 2025-04-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Auto reset | 0.34167 | 0.34167 | 0.34931 | 0 | 0.18333 | 0.18333 | Auto reset | Close | 0.0070513 | O2-26 | 191.1632 |  | WTG Unscheduled Maintenance | 25025 | 191.1632
4249 | 2025-04-13 | 2025 | 2025 | 2025-04-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.77431 | 0.77431 | 0.89167 | 0 | 2.8167 | 2.8167 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.10833 | O2-26 | 2936.9618 |  | WTG Breakdown Maintenance | 25025 | 2936.9618
4250 | 2025-04-13 | 2025 | 2025 | 2025-04-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.89097 | 0.89097 | 1899-12-31 | 0 | 2.6167 | 2.6167 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.10064 | O2-26 | 2728.4201 |  | WTG Breakdown Maintenance | 25025 | 2728.4201
4251 | 2025-04-13 | 2025 | 2025 | 2025-04-01 | 2 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.65278 | 0.65278 | 0.66111 | 0 | 0.2 | 0.2 | WTG Manual stop for Software Updated Work. | Close | 0.0076923 | O2-03 | 214.2083 |  | WTG Breakdown Maintenance | 25705 | 214.2083
4252 | 2025-04-13 | 2025 | 2025 | 2025-04-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Auto reset | 0.325 | 0.325 | 0.33264 | 0 | 0.18333 | 0.18333 | Auto reset | Close | 0.0070513 | O2-15 | 157.766 |  | WTG Unscheduled Maintenance | 20653 | 157.766
4253 | 2025-04-13 | 2025 | 2025 | 2025-04-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.31111 | 0.31111 | 0.31319 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | O2-12 | 52.4792 |  | WTG Unscheduled Maintenance | 25190 | 52.4792
4254 | 2025-04-13 | 2025 | 2025 | 2025-04-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.31667 | 0.31667 | 0.32014 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & started WTG. | Close | 0.0032051 | O2-12 | 87.4653 |  | WTG Unscheduled Maintenance | 25190 | 87.4653
4255 | 2025-04-13 | 2025 | 2025 | 2025-04-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.32639 | 0.32639 | 0.33194 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & started WTG. | Close | 0.0051282 | O2-12 | 139.9444 |  | WTG Unscheduled Maintenance | 25190 | 139.9444
4256 | 2025-04-13 | 2025 | 2025 | 2025-04-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.67222 | 0.67222 | 0.69375 | 0 | 0.51667 | 0.51667 | WTG Manual stop for Software Updated Work. | Close | 0.019872 | O2-12 | 542.2847 |  | WTG Breakdown Maintenance | 25190 | 542.2847
4257 | 2025-04-13 | 2025 | 2025 | 2025-04-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.31319 | 0.31319 | 0.31597 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & started WTG. | Close | 0.0025641 | O2-11 | 65.8278 |  | WTG Unscheduled Maintenance | 23698 | 65.8278
4258 | 2025-04-13 | 2025 | 2025 | 2025-04-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.32014 | 0.32014 | 0.32292 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & started WTG. | Close | 0.0025641 | O2-11 | 65.8278 |  | WTG Unscheduled Maintenance | 23698 | 65.8278
4259 | 2025-04-13 | 2025 | 2025 | 2025-04-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.69722 | 0.69722 | 0.70139 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | O2-11 | 98.7417 |  | WTG Unscheduled Maintenance | 23698 | 98.7417
4260 | 2025-04-13 | 2025 | 2025 | 2025-04-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.76875 | 0.76875 | 0.80625 | 0 | 0.9 | 0.9 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.034615 | O2-11 | 888.675 |  | WTG Breakdown Maintenance | 23698 | 888.675
4261 | 2025-04-13 | 2025 | 2025 | 2025-04-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.84236 | 0.84236 | 1899-12-31 | 0 | 3.7833 | 3.7833 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.14551 | O2-11 | 3735.7264 |  | WTG Breakdown Maintenance | 23698 | 3735.7264
4262 | 2025-04-13 | 2025 | 2025 | 2025-04-01 | 2 | O2_14 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.31319 | 0.31319 | 0.31667 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & started WTG. | Close | 0.0032051 | O2-12 | 87.4653 |  | WTG Unscheduled Maintenance | 25190 | 87.4653
4263 | 2025-04-13 | 2025 | 2025 | 2025-04-01 | 2 | O2_14 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.31944 | 0.31944 | 0.32569 | 0 | 0.15 | 0.15 | Checked related error data log then reset & started WTG. | Close | 0.0057692 | O2-12 | 157.4375 |  | WTG Unscheduled Maintenance | 25190 | 157.4375
4264 | 2025-04-13 | 2025 | 2025 | 2025-04-01 | 2 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.63819 | 0.63819 | 0.65694 | 0 | 0.45 | 0.45 | WTG Manual stop for Software Updated Work. | Close | 0.017308 | O2-12 | 472.3125 |  | WTG Breakdown Maintenance | 25190 | 472.3125
4265 | 2025-04-13 | 2025 | 2025 | 2025-04-01 | 2 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.33403 | 0.33403 | 0.62986 | 0 | 7.1 | 7.1 | WTG stop for YPM day-1 activity complate than started WTG. | Close | 0.27308 | O2-10 | 7664.7458 |  | WTG Scheduled Maintenance | 25909 | 7664.7458
4266 | 2025-04-13 | 2025 | 2025 | 2025-04-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.91319 | 0.91319 | 0.91944 | 0 | 0.15 | 0.15 | Checked related error data log then reset & started WTG. | Close | 0.0057692 | O2-22 | 149.2375 |  | WTG Unscheduled Maintenance | 23878 | 149.2375
4267 | 2025-04-13 | 2025 | 2025 | 2025-04-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.30486 | 0.30486 | 0.30764 | 0 | 0.066667 | 0.066667 | after grid resume error is occurs so Checked related error data log then reset & started WTG. | Close | 0.0025641 | O2-06 | 65.3361 |  | WTG Unscheduled Maintenance | 23521 | 65.3361
4268 | 2025-04-13 | 2025 | 2025 | 2025-04-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.85625 | 0.85625 | 0.86181 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & started WTG. | Close | 0.0051282 | O2-06 | 130.6722 |  | WTG Unscheduled Maintenance | 23521 | 130.6722
4269 | 2025-04-13 | 2025 | 2025 | 2025-04-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.88125 | 0.88125 | 0.9 | 0 | 0.45 | 0.45 | Checked related error data log then reset & started WTG. | Close | 0.017308 | O2-06 | 441.0188 |  | WTG Unscheduled Maintenance | 23521 | 441.0188
4270 | 2025-04-13 | 2025 | 2025 | 2025-04-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.97292 | 0.97292 | 0.97708 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | O2-06 | 98.0042 |  | WTG Unscheduled Maintenance | 23521 | 98.0042
4271 | 2025-04-13 | 2025 | 2025 | 2025-04-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.31042 | 0.31042 | 0.32708 | 0 | 0.4 | 0.4 | after grid resume error is occurs so Checked related error data log then reset & started WTG. | Close | 0.015385 | O2-07 | 367.2667 |  | WTG Unscheduled Maintenance | 22036 | 367.2667
4272 | 2025-04-13 | 2025 | 2025 | 2025-04-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.32708 | 0.38542 | 0.44653 | 1.4 | 1.4667 | 2.8667 | WTG Manual stop for Software Updated Work. | Close | 0.11026 | O2-07 | 2632.0778 |  | WTG Breakdown Maintenance | 22036 | 2632.0778
4273 | 2025-04-13 | 2025 | 2025 | 2025-04-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 53 | Wind dir.dev. level 1 | Break down | 0.66042 | 0.66042 | 0.6625 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | O2-07 | 45.9083 |  | WTG Unscheduled Maintenance | 22036 | 45.9083
4274 | 2025-04-13 | 2025 | 2025 | 2025-04-01 | 2 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.29444 | 0.29444 | 0.3625 | 0 | 1.6333 | 1.6333 | After grid Resume time Converter RFO Single Note so after so and Reset and start wtg | Close | 0.062821 | O2-06 | 1600.7347 |  | WTG Unscheduled Maintenance | 23521 | 1600.7347
4275 | 2025-04-13 | 2025 | 2025 | 2025-04-01 | 2 | O2_24 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.30833 | 0.33194 | 0.38542 | 0.56667 | 1.2833 | 1.85 | Attend and check ckt than found FA01 Surge arrestor feedback connection loose so tight it than started Turbine. | Close | 0.071154 | O2-20 | 1883.9938 |  | WTG Unscheduled Maintenance | 24441 | 1883.9938
4276 | 2025-04-13 | 2025 | 2025 | 2025-04-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.91667 | 0.91667 | 0.92083 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | O2-01 | 110.3708 |  | WTG Unscheduled Maintenance | 26489 | 110.3708
4277 | 2025-04-13 | 2025 | 2025 | 2025-04-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.98264 | 0.98264 | 0.98403 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & started WTG. | Close | 0.0012821 | O2-01 | 36.7903 |  | WTG Unscheduled Maintenance | 26489 | 36.7903
4278 | 2025-04-14 | 2025 | 2025 | 2025-04-01 | 2 | O2_02 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.34167 | 0.34167 | 0.34583 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | O2-05 | 227.1917 |  | WTG Unscheduled Maintenance | 54526 | 227.1917
4279 | 2025-04-14 | 2025 | 2025 | 2025-04-01 | 2 | O2_02 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.50417 | 0.50417 | 0.50972 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & started WTG. | Close | 0.0051282 | O2-05 | 302.9222 |  | WTG Unscheduled Maintenance | 54526 | 302.9222
4280 | 2025-04-14 | 2025 | 2025 | 2025-04-01 | 2 | O2_03 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Connectivity issue | 0.16597 | 0.16597 | 0.20486 | 0 | 0.93333 | 0.93333 | Checked related error data log then reset & started WTG.lat reset due to all WTGs is not cannected in feetpro because internet connectivity breakdown. | Close | 0.035897 | O2-09 | 1752.2556 |  | WTG Unscheduled Maintenance | 45058 | 1752.2556
4281 | 2025-04-14 | 2025 | 2025 | 2025-04-01 | 2 | O2_03 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.69583 | 0.69583 | 0.79097 | 0 | 2.2833 | 2.2833 | attend and check all releted circuit. Check sensor cable laying is ok. check break pad 2 temp sensor found loose cannections so tight it then start WTG. | Close | 0.087821 | O2-09 | 4286.7681 |  | WTG Unscheduled Maintenance | 45058 | 4286.7681
4282 | 2025-04-14 | 2025 | 2025 | 2025-04-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down | 0.78333 | 0.78333 | 0.79028 | 0 | 0.16667 | 0.16667 | Checked related error data log then reset & started WTG. | Close | 0.0064103 | O2-07 | 367.0486 |  | WTG Unscheduled Maintenance | 52855 | 367.0486
4283 | 2025-04-14 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.49931 | 0.49931 | 0.50347 | 0 | 0.1 | 0.1 | Checked related error data log then apply manual DO found all condition is ok then reset & started WTG. | Close | 0.0038462 | O2-02 | 227.4458 |  | WTG Unscheduled Maintenance | 54587 | 227.4458
4284 | 2025-04-14 | 2025 | 2025 | 2025-04-01 | 2 | O2_07 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.3375 | 0.3375 | 0.33958 | 0 | 0.05 | 0.05 | Checked related error data log then apply manual DO found all condition is ok then reset & started WTG. | Close | 0.0019231 | O2-04 | 114.9 |  | WTG Unscheduled Maintenance | 55152 | 114.9
4285 | 2025-04-14 | 2025 | 2025 | 2025-04-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0 | 0 | 0.046528 | 0 | 1.1167 | 1.1167 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.042949 | O2-26 | 2166.1007 |  | WTG Breakdown Maintenance | 46555 | 2166.1007
4286 | 2025-04-14 | 2025 | 2025 | 2025-04-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.48819 | 0.48819 | 0.49931 | 0 | 0.26667 | 0.26667 | Checked related error data log then apply manual DO found all condition is ok then reset & started WTG. | Close | 0.010256 | O2-26 | 517.2778 |  | WTG Unscheduled Maintenance | 46555 | 517.2778
4287 | 2025-04-14 | 2025 | 2025 | 2025-04-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down | 0.74444 | 0.74444 | 0.75556 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & started WTG. | Close | 0.010256 | O2-14 | 462.3444 |  | WTG Unscheduled Maintenance | 41611 | 462.3444
4288 | 2025-04-14 | 2025 | 2025 | 2025-04-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0 | 0 | 0.026389 | 0 | 0.63333 | 0.63333 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.024359 | O2-11 | 1238.325 |  | WTG Breakdown Maintenance | 46926 | 1238.325
4289 | 2025-04-14 | 2025 | 2025 | 2025-04-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.79583 | 0.79583 | 0.95417 | 0 | 3.8 | 3.8 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.14615 | O2-11 | 7429.95 |  | WTG Breakdown Maintenance | 46926 | 7429.95
4290 | 2025-04-14 | 2025 | 2025 | 2025-04-01 | 2 | O2_14 | TQGXIIPL | GEDA | 3.846% | 4540 | Tower oscillation X level 2 | Break down | 0.56181 | 0.56181 | 0.57292 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & started WTG. | Close | 0.010256 | O2-12 | 492.3222 |  | WTG Unscheduled Maintenance | 44309 | 492.3222
4291 | 2025-04-14 | 2025 | 2025 | 2025-04-01 | 2 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.28889 | 0.29583 | 0.50208 | 0.16667 | 4.95 | 5.1167 | WTG stop for YPM day-2 activity and software updated than started WTG. | Close | 0.19679 | O2-10 | 9009.8104 |  | WTG Scheduled Maintenance | 42261 | 9009.8104
4292 | 2025-04-14 | 2025 | 2025 | 2025-04-01 | 2 | O2_16 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.52014 | 0.52014 | 0.52431 | 0 | 0.1 | 0.1 | Checked related error data log then apply manual DO found all condition is ok then reset & started WTG. | Close | 0.0038462 | O2-21 | 182.0792 |  | WTG Unscheduled Maintenance | 43699 | 182.0792
4293 | 2025-04-14 | 2025 | 2025 | 2025-04-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.14167 | 0.14167 | 0.15556 | 0 | 0.33333 | 0.33333 | Checked related error data log then reset & started WTG. | Close | 0.012821 | O2-22 | 682.5556 |  | WTG Unscheduled Maintenance | 49144 | 682.5556
4294 | 2025-04-14 | 2025 | 2025 | 2025-04-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.17431 | 0.17431 | 0.17847 | 0 | 0.1 | 0.1 | Checked related error data log then apply soft reboot then reset & started WTG. | Close | 0.0038462 | O2-22 | 204.7667 |  | WTG Breakdown Maintenance | 49144 | 204.7667
4295 | 2025-04-14 | 2025 | 2025 | 2025-04-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.70903 | 0.70903 | 0.75694 | 0 | 1.15 | 1.15 | Checked related error data log then check wind direction and wind difference data apply DO yawing and check difference is ok so reset & started WTG.now wtg under observation | Close | 0.044231 | O2-22 | 2354.8167 |  | WTG Unscheduled Maintenance | 49144 | 2354.8167
4296 | 2025-04-14 | 2025 | 2025 | 2025-04-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.62708 | 0.62708 | 0.63125 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | O2-06 | 183.2458 |  | WTG Unscheduled Maintenance | 43979 | 183.2458
4297 | 2025-04-14 | 2025 | 2025 | 2025-04-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down | 0.73056 | 0.73056 | 0.75903 | 0 | 0.68333 | 0.68333 | Checked related error data log then apply manual DO cooling pump then reset & started WTG. | Close | 0.026282 | O2-07 | 1504.8993 |  | WTG Unscheduled Maintenance | 52855 | 1504.8993
4298 | 2025-04-14 | 2025 | 2025 | 2025-04-01 | 2 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.53333 | 0.53333 | 0.5375 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | O2-06 | 183.2458 |  | WTG Unscheduled Maintenance | 43979 | 183.2458
4299 | 2025-04-14 | 2025 | 2025 | 2025-04-01 | 2 | O2_24 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.65694 | 0.65694 | 0.65972 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & started WTG. | Close | 0.0025641 | O2-20 | 132.9639 |  | WTG Unscheduled Maintenance | 47867 | 132.9639
4300 | 2025-04-14 | 2025 | 2025 | 2025-04-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.0097222 | 0.0097222 | 0.018056 | 0 | 0.2 | 0.2 | Checked related error data log then apply soft reboot then reset & started WTG. | Close | 0.0076923 | O2-01 | 412.45 |  | WTG Unscheduled Maintenance | 49494 | 412.45
4301 | 2025-04-14 | 2025 | 2025 | 2025-04-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.41667 | 0.41667 | 0.43472 | 0 | 0.43333 | 0.43333 | WTG Manual stop for Software Updated Work. | Close | 0.016667 | O2-01 | 893.6417 |  | WTG Breakdown Maintenance | 49494 | 893.6417
4302 | 2025-04-14 | 2025 | 2025 | 2025-04-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down | 0.70625 | 0.70625 | 0.75208 | 0 | 1.1 | 1.1 | Checked related error data log then apply manual DO cooling pump then reset & started WTG. | Close | 0.042308 | O2-01 | 2268.475 |  | WTG Unscheduled Maintenance | 49494 | 2268.475
4303 | 2025-04-14 | 2025 | 2025 | 2025-04-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.76736 | 0.76736 | 0.96319 | 0 | 4.7 | 4.7 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.18077 | O2-01 | 9692.575 |  | WTG Breakdown Maintenance | 49494 | 9692.575
4304 | 2025-04-15 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.11181 | 0.11181 | 0.11736 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & started WTG. | Close | 0.0051282 | O2-02 | 269.6944 |  | WTG Unscheduled Maintenance | 48545 | 269.6944
4305 | 2025-04-15 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.12153 | 0.12153 | 0.12986 | 0 | 0.2 | 0.2 | Checked related error data log then reset & started WTG. | Close | 0.0076923 | O2-02 | 404.5417 |  | WTG Unscheduled Maintenance | 48545 | 404.5417
4306 | 2025-04-15 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.14583 | 0.14583 | 0.34931 | 0 | 4.8833 | 4.8833 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.18782 | O2-02 | 9877.559 |  | WTG Breakdown Maintenance | 48545 | 9877.559
4307 | 2025-04-15 | 2025 | 2025 | 2025-04-01 | 2 | O2_06 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.36597 | 0.36597 | 0.37014 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-21 | 191.7083 |  | WTG Unscheduled Maintenance | 46010 | 191.7083
4308 | 2025-04-15 | 2025 | 2025 | 2025-04-01 | 2 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.13056 | 0.13056 | 0.34583 | 0 | 5.1667 | 5.1667 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.19872 | O2-03 | 8443.8403 |  | WTG Breakdown Maintenance | 39223 | 8443.8403
4309 | 2025-04-15 | 2025 | 2025 | 2025-04-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.53889 | 0.53889 | 0.56111 | 0 | 0.53333 | 0.53333 | attend and Check rotor brake pads temp sensor condition,cable layout, measure temp value and found loose connection in TB.So re tight and started turbine. | Close | 0.020513 | O2-15 | 994.1333 |  | WTG Breakdown Maintenance | 44736 | 994.1333
4310 | 2025-04-15 | 2025 | 2025 | 2025-04-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.66944 | 0.66944 | 0.67292 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0032051 | O2-15 | 155.3333 |  | WTG Unscheduled Maintenance | 44736 | 155.3333
4311 | 2025-04-15 | 2025 | 2025 | 2025-04-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.58611 | 0.58611 | 0.59028 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-12 | 169.425 |  | WTG Unscheduled Maintenance | 40662 | 169.425
4312 | 2025-04-15 | 2025 | 2025 | 2025-04-01 | 2 | O2_16 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.29306 | 0.30069 | 0.53333 | 0.18333 | 5.5833 | 5.7667 | WTG stop for YPM day-1 activity and software updated than started WTG. | Close | 0.22179 | O2-21 | 11055.1806 |  | WTG Scheduled Maintenance | 46010 | 11055.1806
4313 | 2025-04-15 | 2025 | 2025 | 2025-04-01 | 2 | O2_16 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.62986 | 0.62986 | 0.63403 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | O2-21 | 191.7083 |  | WTG Unscheduled Maintenance | 46010 | 191.7083
4314 | 2025-04-15 | 2025 | 2025 | 2025-04-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.18333 | 0.18333 | 0.19514 | 0 | 0.28333 | 0.28333 | Checked related error data log then reset & started WTG. | Close | 0.010897 | O2-22 | 591.2694 |  | WTG Unscheduled Maintenance | 50084 | 591.2694
4315 | 2025-04-15 | 2025 | 2025 | 2025-04-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD | 0.35556 | 0.37222 | 1899-12-31 | 0.4 | 15.0667 | 15.4667 | WTG manual stop for Blade repairing work.today skylift installing work and damage area surface Measuring and grinding work done and first layer removing work complated and new paste apply & cuting. | open | 0.59487 | O2-22 | 32276.3556 |  | WTG Breakdown Maintenance | 50084 | 32276.3556
4316 | 2025-04-15 | 2025 | 2025 | 2025-04-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down | 0.79861 | 0.79861 | 0.80764 | 0 | 0.21667 | 0.21667 | Checked related error data log then reset & started WTG. | Close | 0.0083333 | O2-07 | 398.5583 |  | WTG Unscheduled Maintenance | 44148 | 398.5583
4317 | 2025-04-15 | 2025 | 2025 | 2025-04-01 | 2 | O2_24 | TQGXIIPL | GEDA | 3.846% | 58 | Wind dir.dev. level 2 | Break down | 0.62361 | 0.62361 | 0.62569 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2-20 | 98.0583 |  | WTG Unscheduled Maintenance | 47068 | 98.0583
4318 | 2025-04-15 | 2025 | 2025 | 2025-04-01 | 2 | O2_24 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.98889 | 0.98889 | 1899-12-31 | 0 | 0.26667 | 0.26667 | attend for generator slipring earthing brush replacement work wip. | open | 0.010256 | O2-20 | 522.9778 |  | WTG Breakdown Maintenance | 47068 | 522.9778
4319 | 2025-04-15 | 2025 | 2025 | 2025-04-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 6012 | Overload yaw motors group 2 | Break down | 0.59653 | 0.63542 | 0.73958 | 0.93333 | 2.5 | 3.4333 | attend and check all releted circuit check all yaw motor winding is ok check all yaw motor break is ok so check and found yaw motor contactor on loose cannection so tight it and started wtg. Now wtg under observations. | Close | 0.13205 | O2-01 | 6654.0861 |  | WTG Unscheduled Maintenance | 46514 | 6654.0861
4320 | 2025-04-16 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.78125 | 0.78125 | 0.81181 | 0 | 0.73333 | 0.73333 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.028205 | O2-02 | 1330.725 |  | WTG Breakdown Maintenance | 43551 | 1330.725
4321 | 2025-04-16 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.85694 | 0.85694 | 0.86528 | 0 | 0.2 | 0.2 | Checked related error data log then reset & started WTG. | Close | 0.0076923 | O2-02 | 362.925 |  | WTG Unscheduled Maintenance | 43551 | 362.925
4322 | 2025-04-16 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.98681 | 0.98681 | 0.99236 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & started WTG. | Close | 0.0051282 | O2-02 | 241.95 |  | WTG Unscheduled Maintenance | 43551 | 241.95
4323 | 2025-04-16 | 2025 | 2025 | 2025-04-01 | 2 | O2_06 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Auto reset | 0.75694 | 0.75694 | 0.75972 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0025641 | O2-21 | 114.4583 |  | WTG Unscheduled Maintenance | 41205 | 114.4583
4324 | 2025-04-16 | 2025 | 2025 | 2025-04-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.47986 | 0.47986 | 0.675 | 0 | 4.6833 | 4.6833 | We have attended turbine for Rep converter temp and Nacelle coolant pressure low check and fill up coolant, Nacelle radiator cleaning with water and Converter in top up coolant,Fan filter replaced, check fan working condition, it's temp sensor circuit then start wtg under observation. | Close | 0.18013 | O2-26 | 7386.0069 |  | WTG Breakdown Maintenance | 37850 | 7386.0069
4325 | 2025-04-16 | 2025 | 2025 | 2025-04-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.70556 | 0.70556 | 0.75208 | 0 | 1.1167 | 1.1167 | then bottom radiator clean with water, check it's working condition.Then reset and started turbine. | Close | 0.042949 | O2-26 | 1761.0764 |  | WTG Breakdown Maintenance | 37850 | 1761.0764
4326 | 2025-04-16 | 2025 | 2025 | 2025-04-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Auto reset | 0.79653 | 0.79653 | 0.80417 | 0 | 0.18333 | 0.18333 | Auto reset | Close | 0.0070513 | O2-14 | 234.5903 |  | WTG Unscheduled Maintenance | 30710 | 234.5903
4327 | 2025-04-16 | 2025 | 2025 | 2025-04-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.66042 | 0.66042 | 0.70278 | 0 | 1.0167 | 1.0167 | WTG Manual stop for blade inspection work. | Close | 0.039103 | O2-11 | 1571.1736 |  | WTG Breakdown Maintenance | 37090 | 1571.1736
4328 | 2025-04-16 | 2025 | 2025 | 2025-04-01 | 2 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.73958 | 0.73958 | 0.76597 | 0 | 0.63333 | 0.63333 | WTG Manual stop for blade inspection work. | Close | 0.024359 | O2-12 | 901.3389 |  | WTG Breakdown Maintenance | 34156 | 901.3389
4329 | 2025-04-16 | 2025 | 2025 | 2025-04-01 | 2 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.76597 | 0.76597 | 0.79792 | 0 | 0.76667 | 0.76667 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.029487 | O2-12 | 1091.0944 |  | WTG Breakdown Maintenance | 34156 | 1091.0944
4330 | 2025-04-16 | 2025 | 2025 | 2025-04-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD | 0 | 0 | 0.90278 | 0 | 21.6667 | 21.6667 | WTG manual stop for Blade repairing work.today we work in blade on Pest leaving and grinding champaring and lamination and curing and heating then putty apply and putty sending work completed then last paint apply then start wtg. | Close | 0.83333 | O2-22 | 41581.9444 |  | WTG Breakdown Maintenance | 46060 | 41581.9444
4331 | 2025-04-16 | 2025 | 2025 | 2025-04-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.475 | 0.475 | 0.72222 | 0 | 5.9333 | 5.9333 | Repeated Conv error (rotor leckage current and encoder error) ocuured so plan to inspection Turbine , Check and visual inspection of Hopewind converter panel components and connection but nothing found abnormal so check Generator slip ring at that time found earthing carbon brush fully wear out and some hot spot mark on Power brush track so clean Power and earthing brush track and do smooth it as well as replace earthing brush and Generator RPM encoder connector loose at yaw platform so correct it the reset and start turbine. | Close | 0.22821 | O2-06 | 10371.4667 |  | WTG Breakdown Maintenance | 41952 | 10371.4667
4332 | 2025-04-16 | 2025 | 2025 | 2025-04-01 | 2 | O2_24 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0 | 0 | 0.043056 | 0 | 1.0333 | 1.0333 | attend for generator slipring earthing brush replacement work done then started wtg. | Close | 0.039744 | O2-20 | 1711.8889 |  | WTG Breakdown Maintenance | 39760 | 1711.8889
4333 | 2025-04-16 | 2025 | 2025 | 2025-04-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down | 0.79375 | 0.79375 | 0.80556 | 0 | 0.28333 | 0.28333 | Checked related error data log then reset & started WTG. | Close | 0.010897 | O2-01 | 468.5271 |  | WTG Unscheduled Maintenance | 39687 | 468.5271
4334 | 2025-04-16 | 2025 | 2025 | 2025-04-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.82639 | 0.82639 | 0.83819 | 0 | 0.28333 | 0.28333 | Checked related error data log then reset & started WTG. | Close | 0.010897 | O2-01 | 468.5271 |  | WTG Unscheduled Maintenance | 39687 | 468.5271
4335 | 2025-04-16 | 2025 | 2025 | 2025-04-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.87153 | 0.87153 | 0.87986 | 0 | 0.2 | 0.2 | Checked related error data log then reset & started WTG. | Close | 0.0076923 | O2-01 | 330.725 |  | WTG Unscheduled Maintenance | 39687 | 330.725
4336 | 2025-04-16 | 2025 | 2025 | 2025-04-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.88611 | 0.88611 | 0.96806 | 0 | 1.9667 | 1.9667 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.075641 | O2-01 | 3252.1292 |  | WTG Breakdown Maintenance | 39687 | 3252.1292
4337 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.61806 | 0.61806 | 0.62431 | 0 | 0.15 | 0.15 | WTG Manual stop for Software Updated Work. | Close | 0.0057692 | O2-26 | 225.6875 |  | WTG Breakdown Maintenance | 36110 | 225.6875
4338 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | 2 | O2_02 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.19028 | 0.19028 | 0.19167 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & started WTG. | Close | 0.0012821 | O2-05 | 53.5611 |  | WTG Unscheduled Maintenance | 38564 | 53.5611
4339 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | 2 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.2875 | 0.29028 | 0.57917 | 0.066667 | 6.9333 | 7 | WTG stop for YPM day-1 activity complate than started WTG. | Close | 0.26923 | O2-05 | 11247.8333 |  | WTG Scheduled Maintenance | 38564 | 11247.8333
4340 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | 2 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.81597 | 0.81597 | 0.82222 | 0 | 0.15 | 0.15 | WTG Manual stop for Software Updated Work. | Close | 0.0057692 | O2-05 | 241.025 |  | WTG Breakdown Maintenance | 38564 | 241.025
4341 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.77847 | 0.77847 | 0.78681 | 0 | 0.2 | 0.2 | WTG Manual stop for Software Updated Work. | Close | 0.0076923 | O2-07 | 304.8917 |  | WTG Breakdown Maintenance | 36587 | 304.8917
4342 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.15139 | 0.15139 | 0.15833 | 0 | 0.16667 | 0.16667 | Checked related error data log then reset & started WTG. | Close | 0.0064103 | O2-02 | 258.8542 |  | WTG Unscheduled Maintenance | 37275 | 258.8542
4343 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.18333 | 0.18333 | 0.19653 | 0 | 0.31667 | 0.31667 | Checked related error data log then reset & started WTG. | Close | 0.012179 | O2-02 | 491.8229 |  | WTG Unscheduled Maintenance | 37275 | 491.8229
4344 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.46042 | 0.46042 | 0.50972 | 0 | 1.1833 | 1.1833 | Checked related error data log then found temp sensor malfunctioning so reboot PLC then reset & started WTG. | Close | 0.045513 | O2-02 | 1837.8646 |  | WTG Unscheduled Maintenance | 37275 | 1837.8646
4345 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | 2 | O2_07 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.78542 | 0.78542 | 0.79306 | 0 | 0.18333 | 0.18333 | WTG Manual stop for Software Updated Work. | Close | 0.0070513 | O2-04 | 309.4208 |  | WTG Breakdown Maintenance | 40506 | 309.4208
4346 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6056 | High yaw load | Auto reset | 0.62708 | 0.62708 | 0.62917 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2-26 | 75.2292 |  | WTG Unscheduled Maintenance | 36110 | 75.2292
4347 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.75 | 0.75 | 0.75694 | 0 | 0.16667 | 0.16667 | WTG Manual stop for Software Updated Work. | Close | 0.0064103 | O2-26 | 250.7639 |  | WTG Breakdown Maintenance | 36110 | 250.7639
4348 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6056 | High yaw load | Auto reset | 0.57708 | 0.57708 | 0.57847 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2-15 | 45.0319 |  | WTG Unscheduled Maintenance | 32423 | 45.0319
4349 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.72361 | 0.72361 | 0.72917 | 0 | 0.13333 | 0.13333 | WTG Manual stop for Software Updated Work. | Close | 0.0051282 | O2-15 | 180.1278 |  | WTG Breakdown Maintenance | 32423 | 180.1278
4350 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.30694 | 0.30694 | 0.31528 | 0 | 0.2 | 0.2 | Checked related error data log then reset & started WTG. | Close | 0.0076923 | O2-12 | 231.3667 |  | WTG Unscheduled Maintenance | 27764 | 231.3667
4351 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.59861 | 0.59861 | 0.61111 | 0 | 0.3 | 0.3 | Checked related error data log then reset & started WTG. | Close | 0.011538 | O2-12 | 347.05 |  | WTG Unscheduled Maintenance | 27764 | 347.05
4352 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.82431 | 0.82431 | 0.89097 | 0 | 1.6 | 1.6 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.061538 | O2-14 | 1987.2 |  | WTG Breakdown Maintenance | 29808 | 1987.2
4353 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.58403 | 0.58403 | 0.58819 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | O2-11 | 136.6083 |  | WTG Unscheduled Maintenance | 32786 | 136.6083
4354 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.79236 | 0.79236 | 0.80069 | 0 | 0.2 | 0.2 | WTG Manual stop for Software Updated Work. | Close | 0.0076923 | O2-11 | 273.2167 |  | WTG Breakdown Maintenance | 32786 | 273.2167
4355 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | 2 | O2_14 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Break down | 0.64792 | 0.64792 | 0.66597 | 0 | 0.43333 | 0.43333 | Checked related error data log then reset & started WTG. | Close | 0.016667 | O2-12 | 501.2944 |  | WTG Unscheduled Maintenance | 27764 | 501.2944
4356 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | 2 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.80139 | 0.80139 | 0.80694 | 0 | 0.13333 | 0.13333 | WTG Manual stop for Software Updated Work. | Close | 0.0051282 | O2-10 | 142.4667 |  | WTG Breakdown Maintenance | 25644 | 142.4667
4357 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.61875 | 0.61875 | 0.62014 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2-22 | 52.0931 |  | WTG Unscheduled Maintenance | 37507 | 52.0931
4358 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.79931 | 0.79931 | 0.80625 | 0 | 0.16667 | 0.16667 | WTG Manual stop for Software Updated Work. | Close | 0.0064103 | O2-22 | 260.4653 |  | WTG Breakdown Maintenance | 37507 | 260.4653
4359 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.6875 | 0.6875 | 0.69236 | 0 | 0.11667 | 0.11667 | WTG Manual stop for Software Updated Work. | Close | 0.0044872 | O2-07 | 177.8535 |  | WTG Breakdown Maintenance | 36587 | 177.8535
4360 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | 2 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.80556 | 0.80556 | 0.81181 | 0 | 0.15 | 0.15 | WTG Manual stop for Software Updated Work. | Close | 0.0057692 | O2-24 | 200.7187 |  | WTG Breakdown Maintenance | 32115 | 200.7187
4361 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | 2 | O2_21 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down | 0.2 | 0.2 | 0.20764 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & started WTG. | Close | 0.0070513 | O2-06 | 261.1201 |  | WTG Unscheduled Maintenance | 34183 | 261.1201
4362 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | 2 | O2_21 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.82361 | 0.82361 | 0.82986 | 0 | 0.15 | 0.15 | WTG Manual stop for Software Updated Work. | Close | 0.0057692 | O2-06 | 213.6438 |  | WTG Breakdown Maintenance | 34183 | 213.6438
4363 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | 2 | O2_22 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.78194 | 0.78194 | 0.78819 | 0 | 0.15 | 0.15 | WTG Manual stop for Software Updated Work. | Close | 0.0057692 | O2-06 | 213.6437 |  | WTG Breakdown Maintenance | 34183 | 213.6437
4364 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | 2 | O2_24 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.76597 | 0.76597 | 0.78194 | 0 | 0.38333 | 0.38333 | WTG Manual stop for Software Updated Work. | Close | 0.014744 | O2-20 | 530.4535 |  | WTG Breakdown Maintenance | 33211 | 530.4535
4365 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | 2 | O2_24 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.96736 | 0.96736 | 1899-12-31 | 0 | 0.78333 | 0.78333 | attend for generator slipring earthing brush replacement work wip. | open | 0.030128 | O2-20 | 1083.9701 |  | WTG Breakdown Maintenance | 33211 | 1083.9701
4366 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.16597 | 0.16597 | 0.18542 | 0 | 0.46667 | 0.46667 | Checked related error data log then reset & started WTG. | Close | 0.017949 | O2-01 | 716.3917 |  | WTG Unscheduled Maintenance | 36843 | 716.3917
4367 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.77014 | 0.77014 | 0.775 | 0 | 0.11667 | 0.11667 | WTG Manual stop for Software Updated Work. | Close | 0.0044872 | O2-01 | 179.0979 |  | WTG Breakdown Maintenance | 36843 | 179.0979
4368 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.86736 | 0.86736 | 0.90972 | 0 | 1.0167 | 1.0167 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.039103 | O2-01 | 1560.7104 |  | WTG Breakdown Maintenance | 36843 | 1560.7104
4369 | 2025-04-18 | 2025 | 2025 | 2025-04-01 | 2 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.27153 | 0.27639 | 0.51458 | 0.11667 | 5.7167 | 5.8333 | WTG stop for YPM day-2 activity and software updated than started WTG. | Close | 0.22436 | O2-05 | 8340.6944 |  | WTG Scheduled Maintenance | 34316 | 8340.6944
4370 | 2025-04-18 | 2025 | 2025 | 2025-04-01 | 2 | O2_03 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Break down | 0.55208 | 0.55208 | 0.56319 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & started WTG. | Close | 0.010256 | O2-09 | 345.9778 |  | WTG Unscheduled Maintenance | 31138 | 345.9778
4371 | 2025-04-18 | 2025 | 2025 | 2025-04-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Break down | 0.68889 | 0.68889 | 0.7 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & started WTG. | Close | 0.010256 | O2-07 | 504.8667 |  | WTG Unscheduled Maintenance | 45438 | 504.8667
4372 | 2025-04-18 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.15347 | 0.15347 | 0.15764 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | O2-02 | 145.4667 |  | WTG Unscheduled Maintenance | 34912 | 145.4667
4373 | 2025-04-18 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.16667 | 0.16667 | 0.2 | 0 | 0.8 | 0.8 | Checked related error data log then found high temp ambient upper converter error the temp sensor malfunction so then reset & started WTG. | Close | 0.030769 | O2-02 | 1163.7333 |  | WTG Unscheduled Maintenance | 34912 | 1163.7333
4374 | 2025-04-18 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.4125 | 0.41875 | 0.46458 | 0.15 | 1.1 | 1.25 | attend and check all related circuit and found temp ambient upper converter sensor on loose cannectinon so tight it then software updated started WTG. | Close | 0.048077 | O2-02 | 1818.3333 |  | WTG Unscheduled Maintenance | 34912 | 1818.3333
4375 | 2025-04-18 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.76806 | 0.76806 | 0.83472 | 0 | 1.6 | 1.6 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.061538 | O2-02 | 2327.4667 |  | WTG Breakdown Maintenance | 34912 | 2327.4667
4376 | 2025-04-18 | 2025 | 2025 | 2025-04-01 | 2 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.70694 | 0.70694 | 0.72778 | 0 | 0.5 | 0.5 | WTG Manual stop for Software Updated Work. | Close | 0.019231 | O2-21 | 659.625 |  | WTG Breakdown Maintenance | 31662 | 659.625
4377 | 2025-04-18 | 2025 | 2025 | 2025-04-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.0013889 | 0.0013889 | 0.026389 | 0 | 0.6 | 0.6 | Checked related error data log then reset & started WTG. | Close | 0.023077 | O2-12 | 771.65 |  | WTG Unscheduled Maintenance | 30866 | 771.65
4378 | 2025-04-18 | 2025 | 2025 | 2025-04-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.58542 | 0.58542 | 0.62778 | 0 | 1.0167 | 1.0167 | Checked related error data log then found PPD pitch angle is diff so apply reboot then reset & started WTG. | Close | 0.039103 | O2-12 | 1307.5181 |  | WTG Unscheduled Maintenance | 30866 | 1307.5181
4379 | 2025-04-18 | 2025 | 2025 | 2025-04-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.46528 | 0.46528 | 0.50069 | 0 | 0.85 | 0.85 | Checked related error data log then reset & started WTG. | Close | 0.032692 | O2-22 | 1288.0687 |  | WTG Unscheduled Maintenance | 36369 | 1288.0687
4380 | 2025-04-18 | 2025 | 2025 | 2025-04-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.60833 | 0.60833 | 0.6125 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | O2-06 | 117.6875 |  | WTG Unscheduled Maintenance | 28245 | 117.6875
4381 | 2025-04-18 | 2025 | 2025 | 2025-04-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Break down | 0.33194 | 0.33194 | 0.34306 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & started WTG. | Close | 0.010256 | O2-07 | 504.8667 |  | WTG Unscheduled Maintenance | 45438 | 504.8667
4382 | 2025-04-18 | 2025 | 2025 | 2025-04-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Break down | 0.36319 | 0.36319 | 0.36736 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | O2-07 | 189.325 |  | WTG Unscheduled Maintenance | 45438 | 189.325
4383 | 2025-04-18 | 2025 | 2025 | 2025-04-01 | 2 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.60764 | 0.60764 | 0.61181 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | O2-06 | 117.6875 |  | WTG Unscheduled Maintenance | 28245 | 117.6875
4384 | 2025-04-18 | 2025 | 2025 | 2025-04-01 | 2 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.63681 | 0.63681 | 0.64931 | 0 | 0.3 | 0.3 | Checked related error data log then reset & started WTG. | Close | 0.011538 | O2-06 | 353.0625 |  | WTG Unscheduled Maintenance | 28245 | 353.0625
4385 | 2025-04-18 | 2025 | 2025 | 2025-04-01 | 2 | O2_24 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0 | 0 | 0.15625 | 0 | 3.75 | 3.75 | attend and check generator slipring and found earthing brush are wear out so clean earthing track and measure by dial gauge take reading and replace brush then start wtg now turbine running under observation | Close | 0.14423 | O2-20 | 5437.6562 |  | WTG Unscheduled Maintenance | 34801 | 5437.6562
4386 | 2025-04-18 | 2025 | 2025 | 2025-04-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.73472 | 0.73472 | 0.74722 | 0 | 0.3 | 0.3 | Checked related error data log then reset & started WTG. | Close | 0.011538 | O2-01 | 428.675 |  | WTG Unscheduled Maintenance | 34294 | 428.675
4387 | 2025-04-18 | 2025 | 2025 | 2025-04-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.75833 | 0.75833 | 0.86528 | 0 | 2.5667 | 2.5667 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.098718 | O2-01 | 3667.5528 |  | WTG Breakdown Maintenance | 34294 | 3667.5528
4388 | 2025-04-18 | 2025 | 2025 | 2025-04-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.90208 | 0.90208 | 0.9375 | 0 | 0.85 | 0.85 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.032692 | O2-01 | 1214.5792 |  | WTG Breakdown Maintenance | 34294 | 1214.5792
4389 | 2025-04-19 | 2025 | 2025 | 2025-04-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.71667 | 0.71667 | 0.73125 | 0 | 0.35 | 0.35 | Checked related error data log then reset & started WTG. | Close | 0.013462 | O2-26 | 666.4729 |  | WTG Unscheduled Maintenance | 45701 | 666.4729
4390 | 2025-04-19 | 2025 | 2025 | 2025-04-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.75764 | 0.75764 | 0.86042 | 0 | 2.4667 | 2.4667 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.094872 | O2-26 | 4697.0472 |  | WTG Breakdown Maintenance | 45701 | 4697.0472
4391 | 2025-04-19 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.72569 | 0.72569 | 0.73542 | 0 | 0.23333 | 0.23333 | Checked related error data log then reset & started WTG. | Close | 0.0089744 | O2-02 | 521.3639 |  | WTG Unscheduled Maintenance | 53626 | 521.3639
4392 | 2025-04-19 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.75 | 0.75 | 0.77917 | 0 | 0.7 | 0.7 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.026923 | O2-02 | 1564.0917 |  | WTG Breakdown Maintenance | 53626 | 1564.0917
4393 | 2025-04-19 | 2025 | 2025 | 2025-04-01 | 2 | O2_06 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down | 0.71389 | 0.71389 | 0.71597 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | O2-21 | 95.0687 |  | WTG Unscheduled Maintenance | 45633 | 95.0687
4394 | 2025-04-19 | 2025 | 2025 | 2025-04-01 | 2 | O2_07 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Break down | 0.51667 | 0.51667 | 0.52778 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & started WTG. | Close | 0.010256 | O2-04 | 568.6444 |  | WTG Unscheduled Maintenance | 51178 | 568.6444
4395 | 2025-04-19 | 2025 | 2025 | 2025-04-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.68264 | 0.68264 | 0.69375 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & started WTG. | Close | 0.010256 | O2-26 | 507.7889 |  | WTG Unscheduled Maintenance | 45701 | 507.7889
4396 | 2025-04-19 | 2025 | 2025 | 2025-04-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.60347 | 0.60347 | 0.60764 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | O2-12 | 186.2167 |  | WTG Unscheduled Maintenance | 44692 | 186.2167
4397 | 2025-04-19 | 2025 | 2025 | 2025-04-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down | 0.70208 | 0.70208 | 0.70417 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | O2-14 | 88.2396 |  | WTG Unscheduled Maintenance | 42355 | 88.2396
4398 | 2025-04-19 | 2025 | 2025 | 2025-04-01 | 2 | O2_14 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Break down | 0.525 | 0.525 | 0.53264 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & started WTG. | Close | 0.0070513 | O2-12 | 341.3972 |  | WTG Unscheduled Maintenance | 44692 | 341.3972
4399 | 2025-04-19 | 2025 | 2025 | 2025-04-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.2875 | 0.2875 | 0.65069 | 0 | 8.7167 | 8.7167 | WTG stop for YPM day-1 activity complate than started WTG. | Close | 0.33526 | O2-06 | 16871.8347 |  | WTG Scheduled Maintenance | 46454 | 16871.8347
4400 | 2025-04-19 | 2025 | 2025 | 2025-04-01 | 2 | O2_20 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Break down | 0.54097 | 0.54097 | 0.55208 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & started WTG. | Close | 0.010256 | O2-24 | 508.8444 |  | WTG Unscheduled Maintenance | 45796 | 508.8444
4401 | 2025-04-19 | 2025 | 2025 | 2025-04-01 | 2 | O2_21 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.44167 | 0.44167 | 0.44583 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | O2-06 | 193.5583 |  | WTG Unscheduled Maintenance | 46454 | 193.5583
4402 | 2025-04-19 | 2025 | 2025 | 2025-04-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Break down | 0.61736 | 0.61736 | 0.62847 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & started WTG. | Close | 0.010256 | O2-11 | 505.8667 |  | WTG Unscheduled Maintenance | 45528 | 505.8667
4403 | 2025-04-19 | 2025 | 2025 | 2025-04-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.4375 | 0.4375 | 0.46458 | 0 | 0.65 | 0.65 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.025 | O2-01 | 1056.9813 |  | WTG Breakdown Maintenance | 39027 | 1056.9813
4404 | 2025-04-19 | 2025 | 2025 | 2025-04-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.70486 | 0.70486 | 0.88194 | 0 | 4.25 | 4.25 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.16346 | O2-01 | 6911.0312 |  | WTG Breakdown Maintenance | 39027 | 6911.0312
4405 | 2025-04-20 | 2025 | 2025 | 2025-04-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.93264 | 0.97778 | 0.99999 | 1.0833 | 0.53306 | 1.6164 | wtg manual stop for converter coolant temp high wip. | open | 0.062169 | O2-26 | 1504.3866 |  | WTG Unscheduled Maintenance | 22337 | 1504.3866
4406 | 2025-04-20 | 2025 | 2025 | 2025-04-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.64236 | 0.64236 | 0.64653 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-07 | 110.4792 |  | WTG Unscheduled Maintenance | 26515 | 110.4792
4407 | 2025-04-20 | 2025 | 2025 | 2025-04-01 | 2 | O2_07 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.60208 | 0.60208 | 0.60694 | 0 | 0.11667 | 0.11667 | Auto reset | Close | 0.0044872 | O2-04 | 149.5083 |  | WTG Unscheduled Maintenance | 30756 | 149.5083
4408 | 2025-04-20 | 2025 | 2025 | 2025-04-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.66875 | 0.66875 | 0.67361 | 0 | 0.11667 | 0.11667 | WTG Manual stop for Software Updated Work. | Close | 0.0044872 | O2-26 | 108.5826 |  | WTG Breakdown Maintenance | 22337 | 108.5826
4409 | 2025-04-20 | 2025 | 2025 | 2025-04-01 | 2 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.61667 | 0.61667 | 0.625 | 0 | 0.2 | 0.2 | WTG Manual stop for Software Updated Work. | Close | 0.0076923 | O2-03 | 189.7417 |  | WTG Breakdown Maintenance | 22769 | 189.7417
4410 | 2025-04-20 | 2025 | 2025 | 2025-04-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.68333 | 0.68333 | 0.68819 | 0 | 0.11667 | 0.11667 | WTG Manual stop for Software Updated Work. | Close | 0.0044872 | O2-12 | 131.6437 |  | WTG Breakdown Maintenance | 27081 | 131.6437
4411 | 2025-04-20 | 2025 | 2025 | 2025-04-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.73125 | 0.73125 | 0.74861 | 0 | 0.41667 | 0.41667 | WTG Manual stop for Software Updated Work. | Close | 0.016026 | O2-14 | 441.5278 |  | WTG Breakdown Maintenance | 25432 | 441.5278
4412 | 2025-04-20 | 2025 | 2025 | 2025-04-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.58125 | 0.58125 | 0.58542 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | O2-11 | 114.0167 |  | WTG Unscheduled Maintenance | 27364 | 114.0167
4413 | 2025-04-20 | 2025 | 2025 | 2025-04-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.65139 | 0.65139 | 0.66319 | 0 | 0.28333 | 0.28333 | WTG Manual stop for Software Updated Work. | Close | 0.010897 | O2-11 | 323.0472 |  | WTG Breakdown Maintenance | 27364 | 323.0472
4414 | 2025-04-20 | 2025 | 2025 | 2025-04-01 | 2 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.67639 | 0.67639 | 0.68056 | 0 | 0.1 | 0.1 | WTG Manual stop for Software Updated Work. | Close | 0.0038462 | O2-12 | 112.8375 |  | WTG Breakdown Maintenance | 27081 | 112.8375
4415 | 2025-04-20 | 2025 | 2025 | 2025-04-01 | 2 | O2_16 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.62014 | 0.62014 | 0.62639 | 0 | 0.15 | 0.15 | WTG Manual stop for Software Updated Work. | Close | 0.0057692 | O2-21 | 187.0375 |  | WTG Breakdown Maintenance | 29926 | 187.0375
4416 | 2025-04-20 | 2025 | 2025 | 2025-04-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.49375 | 0.49375 | 0.50139 | 0 | 0.18333 | 0.18333 | WTG Manual stop for Software Updated Work. | Close | 0.0070513 | O2-22 | 220.7181 |  | WTG Breakdown Maintenance | 28894 | 220.7181
4417 | 2025-04-20 | 2025 | 2025 | 2025-04-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.57222 | 0.57222 | 0.57778 | 0 | 0.13333 | 0.13333 | WTG Manual stop for Software Updated Work. | Close | 0.0051282 | O2-22 | 160.5222 |  | WTG Breakdown Maintenance | 28894 | 160.5222
4418 | 2025-04-20 | 2025 | 2025 | 2025-04-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.27847 | 0.28403 | 0.54375 | 0.13333 | 6.2333 | 6.3667 | WTG stop for YPM day-2 activity complate than started WTG. | Close | 0.24487 | O2-06 | 8007.9403 |  | WTG Scheduled Maintenance | 30187 | 8007.9403
4419 | 2025-04-20 | 2025 | 2025 | 2025-04-01 | 2 | O2_22 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.53681 | 0.53681 | 0.54375 | 0 | 0.16667 | 0.16667 | WTG Manual stop for Software Updated Work. | Close | 0.0064103 | O2-06 | 209.6319 |  | WTG Breakdown Maintenance | 30187 | 209.6319
4420 | 2025-04-20 | 2025 | 2025 | 2025-04-01 | 2 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.72569 | 0.72569 | 0.72986 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-06 | 125.7792 |  | WTG Unscheduled Maintenance | 30187 | 125.7792
4421 | 2025-04-20 | 2025 | 2025 | 2025-04-01 | 2 | O2_24 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.375 | 0.375 | 0.38819 | 0 | 0.31667 | 0.31667 | Checked related error data log then reset & started WTG. | Close | 0.012179 | O2-20 | 374.4979 |  | WTG Unscheduled Maintenance | 28383 | 374.4979
4422 | 2025-04-20 | 2025 | 2025 | 2025-04-01 | 2 | O2_26 | TQGXIIPL | GEDA | 3.846% | 658 | Error pitch converter 3 | Break down | 0.31181 | 0.31181 | 0.32361 | 0 | 0.28333 | 0.28333 | Checked related error data log then reset & started WTG. | Close | 0.010897 | O2-01 | 294.1826 |  | WTG Unscheduled Maintenance | 24919 | 294.1826
4423 | 2025-04-21 | 2025 | 2025 | 2025-04-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0 | 0 | 0.0097222 | 0 | 0.23333 | 0.23333 | wtg manual stop for converter coolant temp high so check and found coolanr MPCB trip and cable cut by mouse so correct it then started wtg. | Close | 0.0089744 | O2-26 | 72.3917 |  | WTG Unscheduled Maintenance | 7446 | 72.3917
4424 | 2025-04-21 | 2025 | 2025 | 2025-04-01 | 2 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.79861 | 0.79861 | 0.83056 | 0 | 0.76667 | 0.76667 | After grid Resume time Converter RFO Single Note so after so and Reset and start wtg | Close | 0.029487 | O2-05 | 389.5306 |  | WTG Unscheduled Maintenance | 12194 | 389.5306
4425 | 2025-04-21 | 2025 | 2025 | 2025-04-01 | 2 | O2_06 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.70694 | 0.70694 | 0.71181 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & started WTG. | Close | 0.0044872 | O2-21 | 45.2569 |  | WTG Unscheduled Maintenance | 9310 | 45.2569
4426 | 2025-04-21 | 2025 | 2025 | 2025-04-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 650 | Pitch controller communication error | Break down | 0.79861 | 0.79861 | 0.83264 | 0 | 0.81667 | 0.81667 | Checked related error data log then apply softreboot then reset & started WTG. | Close | 0.03141 | O2-12 | 325.816 |  | WTG Unscheduled Maintenance | 9575 | 325.816
4427 | 2025-04-21 | 2025 | 2025 | 2025-04-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.85833 | 0.9375 | 0.99999 | 1.9 | 1.4997 | 3.3997 | attend check all related circuit and found Hub panel entry point len cable is damage so replace it and take Wtg trial 30 mini after error it occurs so check all 3 axis len cable entry point found no any abnormality so discuss with commissioning team,wtg restoration wip | open | 0.13076 | O2-12 | 1356.3475 |  | WTG Unscheduled Maintenance | 9575 | 1356.3475
4428 | 2025-04-21 | 2025 | 2025 | 2025-04-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 643 | Sim.angle E enc. <> act.angle 3 | Break down | 0.39653 | 0.44444 | 0.52083 | 1.15 | 1.8333 | 2.9833 | after grid resume error is occurs so attend check all all 3 axis blade calibration is ok so check pitch encode A and B and found pitch encoder connector loose so tight it then started wtg. | Close | 0.11474 | O2-14 | 1132.0507 |  | WTG Unscheduled Maintenance | 9107 | 1132.0507
4429 | 2025-04-21 | 2025 | 2025 | 2025-04-01 | 2 | O2_14 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Break down | 0.79861 | 0.79861 | 0.82222 | 0 | 0.56667 | 0.56667 | Checked related error data log then apply softreboot then reset & started WTG. | Close | 0.021795 | O2-12 | 226.0764 |  | WTG Unscheduled Maintenance | 9575 | 226.0764
4430 | 2025-04-21 | 2025 | 2025 | 2025-04-01 | 2 | O2_16 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.28611 | 0.29236 | 0.54861 | 0.15 | 6.15 | 6.3 | WTG stop for YPM day-2 activity complate than started WTG. | Close | 0.24231 | O2-21 | 2443.875 |  | WTG Scheduled Maintenance | 9310 | 2443.875
4431 | 2025-04-22 | 2025 | 2025 | 2025-04-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.65833 | 0.65833 | 0.66806 | 0 | 0.23333 | 0.23333 | Checked related error data log then reset & started WTG. | Close | 0.0089744 | O2-26 | 119.1069 |  | WTG Unscheduled Maintenance | 12251 | 119.1069
4432 | 2025-04-22 | 2025 | 2025 | 2025-04-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.75625 | 0.78472 | 0.80764 | 0.68333 | 0.55 | 1.2333 | attend and check and found coverter cooling fan MPCB trip so check all releted circuit no any abnormality so interchange MPCB then start wtg. Now wtg under observation. | Close | 0.047436 | O2-26 | 629.5653 |  | WTG Unscheduled Maintenance | 12251 | 629.5653
4433 | 2025-04-22 | 2025 | 2025 | 2025-04-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0 | 0 | 0.021528 | 0 | 0.51667 | 0.51667 | attend and check releted circuit check Hub panel entry point len cable is damage so replace it take Wtg trial | Close | 0.019872 | O2-12 | 270.9271 |  | WTG Unscheduled Maintenance | 12585 | 270.9271
4434 | 2025-04-22 | 2025 | 2025 | 2025-04-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.042361 | 0.042361 | 0.2125 | 0 | 4.0833 | 4.0833 | 30 mini after error it occurs so check all 3 axis len cable entry point found no any abnormality so take Wtg trial | Close | 0.15705 | O2-12 | 2141.1979 |  | WTG Unscheduled Maintenance | 12585 | 2141.1979
4435 | 2025-04-22 | 2025 | 2025 | 2025-04-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Major BD | 0.25 | 0.25 | 0.99999 | 0 | 17.9997 | 17.9997 | after error it occurs so discuss with commissioning team and check and found all 3 axis len cable is not connected as per wtg wiring diagram so correct it WIP | OPEN | 0.6923 | O2-12 | 9438.6043 |  | WTG Unscheduled Maintenance | 12585 | 9438.6043
4436 | 2025-04-22 | 2025 | 2025 | 2025-04-01 | 2 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.54722 | 0.54722 | 0.55139 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-06 | 44.1625 |  | WTG Unscheduled Maintenance | 10599 | 44.1625
4437 | 2025-04-23 | 2025 | 2025 | 2025-04-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Break down | 0.18611 | 0.18611 | 0.19722 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & started WTG. | Close | 0.010256 | O2-26 | 145.7 |  | WTG Unscheduled Maintenance | 13113 | 145.7
4438 | 2025-04-23 | 2025 | 2025 | 2025-04-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Auto reset | 0.22569 | 0.22569 | 0.23681 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | O2-26 | 145.7 |  | WTG Unscheduled Maintenance | 13113 | 145.7
4439 | 2025-04-23 | 2025 | 2025 | 2025-04-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0 | 0 | 0.23264 | 0 | 5.5833 | 5.5833 | Attend and check all Communication Cables and replace and also Check FO cable and connection and than take trial but same error occured so reprogramming of HUb module MX220 and interchange PPD between blade 1&3 than recalibration of all 3 blades than reset and start turbine(Now Turbine under observation). | Close | 0.21474 | O2-12 | 4361.7465 |  | WTG Unscheduled Maintenance | 18749 | 4361.7465
4440 | 2025-04-23 | 2025 | 2025 | 2025-04-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.4375 | 0.48403 | 0.64931 | 1.1167 | 3.9667 | 5.0833 | We have check In SAM Event found Pitch communication loss to 1,2 and 3 also check in Snap and found Encode value deviation.So We have Attend turbine and check all Communication Cables Connector and clean properly and refixed and Further We have interchage Communication module to Mx220 module cable with BLS and Replace MX220 Module with new one and Install new Base package.After Programming Complete We Calibration all 3 blade and properly all cable laying complete we have Taken trail turbine.After No any abnormal absorb so started WTG. | Close | 0.19551 | O2-12 | 3971.1424 |  | WTG Unscheduled Maintenance | 18749 | 3971.1424
4441 | 2025-04-23 | 2025 | 2025 | 2025-04-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD | 0.40417 | 0.40417 | 0.76458 | 0 | 8.65 | 8.65 | WTG Manual stop for Blade-3 VG installation work done than started wtg. | Close | 0.33269 | O2-06 | 6550.2125 |  | WTG Breakdown Maintenance | 18174 | 6550.2125
4442 | 2025-04-24 | 2025 | 2025 | 2025-04-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD | 0.47222 | 0.47222 | 0.77639 | 0 | 7.3 | 7.3 | Wtg manual stop for wtg Lift FTU work. | Close | 0.28077 | O2-22 | 6144.4708 |  | WTG Breakdown Maintenance | 20201 | 6144.4708
4443 | 2025-04-24 | 2025 | 2025 | 2025-04-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD | 0.38472 | 0.38472 | 0.69028 | 0 | 7.3333 | 7.3333 | WTG Manual stop for Blade-2 VG installation work done than started wtg. | Close | 0.28205 | O2-06 | 5623.75 |  | WTG Breakdown Maintenance | 18405 | 5623.75
4444 | 2025-04-24 | 2025 | 2025 | 2025-04-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.69653 | 0.69653 | 0.69861 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | O2-11 | 34.4979 |  | WTG Unscheduled Maintenance | 16559 | 34.4979
4445 | 2025-04-24 | 2025 | 2025 | 2025-04-01 | 2 | O2_24 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.575 | 0.575 | 0.57917 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-20 | 76.9083 |  | WTG Unscheduled Maintenance | 18458 | 76.9083
4445 | 2025-04-25 | 2025 | 2025 | 2025-04-01 | 2 | O2_03 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.78403 | 0.78403 | 0.80972 | 0 | 0.61667 | 0.61667 | Checked related error data log then check parameter then apply soft reboot then reset & started WTG. | Close | 0.023718 | O2-09 | 600.0938 |  | WTG Unscheduled Maintenance | 23355 | 600.0938
4445 | 2025-04-25 | 2025 | 2025 | 2025-04-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 630 | Overload fan pitch motor | Break down | 0.019444 | 0.070833 | 0.125 | 1.2333 | 1.3 | 2.5333 | attend and check all related circuit and found axis1 pitch motor cooling MPCB FC002 trip so check and found cooling fan cannection bolt is loose so tight it then start wtg. | Close | 0.097436 | O2-07 | 2693.9889 |  | WTG Unscheduled Maintenance | 25522 | 2693.9889
4445 | 2025-04-25 | 2025 | 2025 | 2025-04-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3250 | No power | Auto reset | 0.17917 | 0.17917 | 0.17986 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | O2-07 | 17.7236 |  | WTG Unscheduled Maintenance | 25522 | 17.7236
4445 | 2025-04-25 | 2025 | 2025 | 2025-04-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.21736 | 0.21736 | 0.22014 | 0 | 0.066667 | 0.066667 | attend and check and found converter cooling fan MPCB triped so check no any abnormality so stert MPCB then started wtg. | Close | 0.0025641 | O2-07 | 70.8944 |  | WTG Unscheduled Maintenance | 25522 | 70.8944
4445 | 2025-04-25 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down | 0.16181 | 0.19167 | 0.21111 | 0.71667 | 0.46667 | 1.1833 | attend and check all related circuit and check CAND cable all related cable no any abnormality so apply hard reboot then started wtg. | Close | 0.045513 | O2-02 | 1498.1 |  | WTG Unscheduled Maintenance | 30384 | 1498.1
4445 | 2025-04-25 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 7017 | Parameter outside limits stop | Break down | 0.80903 | 0.80903 | 0.83819 | 0 | 0.7 | 0.7 | Checked related error data log then check parameter no any abnormality apply soft reboot then reset & started WTG. | Close | 0.026923 | O2-02 | 886.2 |  | WTG Unscheduled Maintenance | 30384 | 886.2
4445 | 2025-04-25 | 2025 | 2025 | 2025-04-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.85278 | 0.85278 | 0.87569 | 0 | 0.55 | 0.55 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.021154 | O2-14 | 449.8542 |  | WTG Breakdown Maintenance | 19630 | 449.8542
4445 | 2025-04-25 | 2025 | 2025 | 2025-04-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.6375 | 0.6375 | 0.64167 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | O2-11 | 86.7042 |  | WTG Unscheduled Maintenance | 20809 | 86.7042
4445 | 2025-04-25 | 2025 | 2025 | 2025-04-01 | 2 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.65486 | 0.66528 | 0.71181 | 0.25 | 1.1167 | 1.3667 | Wtg manual stop for wtg Lift FTU work. | Close | 0.052564 | O2-12 | 1086.4431 |  | WTG Breakdown Maintenance | 19079 | 1086.4431
4445 | 2025-04-25 | 2025 | 2025 | 2025-04-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD | 0.37639 | 0.37639 | 0.72292 | 0 | 8.3167 | 8.3167 | WTG Manual stop for Blade-1 VG installation work done than started wtg. | Close | 0.31987 | O2-06 | 8481.2674 |  | WTG Breakdown Maintenance | 24475 | 8481.2674
4445 | 2025-04-25 | 2025 | 2025 | 2025-04-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.83056 | 0.83056 | 0.83264 | 0 | 0.05 | 0.05 | Wtg manual stop for parameter check then start wtg | Close | 0.0019231 | O2-06 | 50.9896 |  | WTG Breakdown Maintenance | 24475 | 50.9896
4445 | 2025-04-25 | 2025 | 2025 | 2025-04-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 60 | Wind > power | Break down | 0.84792 | 0.84792 | 0.85347 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & started WTG. | Close | 0.0051282 | O2-06 | 135.9722 |  | WTG Unscheduled Maintenance | 24475 | 135.9722
4445 | 2025-04-25 | 2025 | 2025 | 2025-04-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 60 | Wind > power | Break down | 0.86944 | 0.86944 | 0.88125 | 0 | 0.28333 | 0.28333 | Checked related error data log check parameter by L2 team then reset & started WTG. | Close | 0.010897 | O2-06 | 288.941 |  | WTG Unscheduled Maintenance | 24475 | 288.941
4445 | 2025-04-25 | 2025 | 2025 | 2025-04-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 60 | Wind > power | Break down | 0.89722 | 0.89722 | 0.91528 | 0 | 0.43333 | 0.43333 | Checked related error data log check parameter by L2 team then reset & started WTG. | Close | 0.016667 | O2-06 | 441.9097 |  | WTG Unscheduled Maintenance | 24475 | 441.9097
4445 | 2025-04-25 | 2025 | 2025 | 2025-04-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.91806 | 0.91806 | 0.92569 | 0 | 0.18333 | 0.18333 | WTG Manual stop for Turbine Manual stop for PPC parameter checking work | Close | 0.0070513 | O2-06 | 186.9618 |  | WTG Breakdown Maintenance | 24475 | 186.9618
4445 | 2025-04-25 | 2025 | 2025 | 2025-04-01 | 2 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.30764 | 0.30764 | 0.625 | 0 | 7.6167 | 7.6167 | WTG stop for YPM day-1 activity complate than started WTG. | Close | 0.29295 | O2-24 | 7143.7986 |  | WTG Scheduled Maintenance | 22510 | 7143.7986
4446 | 2025-04-26 | 2025 | 2025 | 2025-04-01 | 2 | O2_03 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Break down | 0.46042 | 0.46042 | 0.46736 | 0 | 0.16667 | 0.16667 | Checked related error data log then reset & started WTG. | Close | 0.0064103 | O2-09 | 148.2014 |  | WTG Unscheduled Maintenance | 21341 | 148.2014
4447 | 2025-04-26 | 2025 | 2025 | 2025-04-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.67431 | 0.67431 | 0.67847 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | O2-07 | 133.95 |  | WTG Unscheduled Maintenance | 32148 | 133.95
4448 | 2025-04-26 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.79931 | 0.79931 | 0.90486 | 0 | 2.5333 | 2.5333 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.097436 | O2-02 | 3175.85 |  | WTG Breakdown Maintenance | 30087 | 3175.85
4449 | 2025-04-26 | 2025 | 2025 | 2025-04-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.68958 | 0.68958 | 0.74653 | 0 | 1.3667 | 1.3667 | Wtg manual stop for wtg Lift FTU work. | Close | 0.052564 | O2-15 | 1212.5181 |  | WTG Breakdown Maintenance | 21293 | 1212.5181
4450 | 2025-04-26 | 2025 | 2025 | 2025-04-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.61528 | 0.61528 | 0.66667 | 0 | 1.2333 | 1.2333 | Wtg manual stop for wtg Lift FTU work. | Close | 0.047436 | O2-12 | 1096.7417 |  | WTG Breakdown Maintenance | 21342 | 1096.7417
4451 | 2025-04-26 | 2025 | 2025 | 2025-04-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.45 | 0.45 | 0.5 | 0 | 1.2 | 1.2 | Wtg manual stop for wtg Lift FTU work. | Close | 0.046154 | O2-11 | 1031.55 |  | WTG Breakdown Maintenance | 20631 | 1031.55
4452 | 2025-04-26 | 2025 | 2025 | 2025-04-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.5 | 0.5 | 0.55208 | 0 | 1.25 | 1.25 | WTG stop for Customer Audit work. | Close | 0.048077 | O2-11 | 1074.5313 |  | WTG Breakdown Maintenance | 20631 | 1074.5313
4453 | 2025-04-26 | 2025 | 2025 | 2025-04-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.56667 | 0.56667 | 0.6 | 0 | 0.8 | 0.8 | WTG stop for Customer Audit work. | Close | 0.030769 | O2-11 | 687.7 |  | WTG Breakdown Maintenance | 20631 | 687.7
4454 | 2025-04-26 | 2025 | 2025 | 2025-04-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD | 0.39167 | 0.39167 | 0.675 | 0 | 6.8 | 6.8 | WTG Manual stop for Blade-3 VG installation work done than started wtg. | Close | 0.26154 | O2-22 | 8197.4 |  | WTG Breakdown Maintenance | 28932 | 8197.4
4455 | 2025-04-26 | 2025 | 2025 | 2025-04-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.58264 | 0.58264 | 0.58889 | 0 | 0.15 | 0.15 | Wtg manual stop for parameter check then apply soft reboot then reset & started WTG. | Close | 0.0057692 | O2-06 | 162.3687 |  | WTG Breakdown Maintenance | 25979 | 162.3687
4456 | 2025-04-26 | 2025 | 2025 | 2025-04-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 60 | Wind > power | Break down | 0.74931 | 0.74931 | 0.76806 | 0 | 0.45 | 0.45 | Checked related error data log check parameterthen reset & started WTG. | Close | 0.017308 | O2-06 | 487.1063 |  | WTG Unscheduled Maintenance | 25979 | 487.1063
4457 | 2025-04-26 | 2025 | 2025 | 2025-04-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Auto reset | 0.89931 | 0.89931 | 0.90069 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2-07 | 44.65 |  | WTG Unscheduled Maintenance | 32148 | 44.65
4458 | 2025-04-26 | 2025 | 2025 | 2025-04-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 3800 | Circuit breaker | Break down | 0.90625 | 0.99931 | 0.99999 | 2.2333 | 0.016389 | 2.2497 | attend and found bottom power panel ACB trip and 1 nos 500A fuse is faulty. So this fault is machine side fault so check generator stator and rotor carbon brush and slipring is all condition is ok so check IR value ACB and ingeteam person traubleshooting WIP. | Close | 0.086528 | O2-07 | 3013.5029 |  | WTG Unscheduled Maintenance | 32148 | 3013.5029
4459 | 2025-04-26 | 2025 | 2025 | 2025-04-01 | 2 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.26528 | 0.26528 | 0.48472 | 0 | 5.2667 | 5.2667 | WTG stop for YPM day-1 activity complate than started WTG. | Close | 0.20256 | O2-24 | 5088.9167 |  | WTG Scheduled Maintenance | 23190 | 5088.9167
4460 | 2025-04-26 | 2025 | 2025 | 2025-04-01 | 2 | O2_20 | TQGXIIPL | GEDA | 3.846% | 643 | Sim.angle E enc. <> act.angle 3 | Break down | 0.49653 | 0.49653 | 0.49861 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | O2-24 | 48.3125 |  | WTG Unscheduled Maintenance | 23190 | 48.3125
4461 | 2025-04-26 | 2025 | 2025 | 2025-04-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.51389 | 0.51389 | 0.51806 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-11 | 85.9625 |  | WTG Unscheduled Maintenance | 20631 | 85.9625
4462 | 2025-04-26 | 2025 | 2025 | 2025-04-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.75694 | 0.75694 | 0.88542 | 0 | 3.0833 | 3.0833 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.11859 | O2-01 | 3035.1562 |  | WTG Breakdown Maintenance | 23625 | 3035.1562
4463 | 2025-04-27 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3210 | Frequency converter load rejection | Break down | 0.23056 | 0.23056 | 0.23264 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | O2-02 | 57.7521 |  | WTG Unscheduled Maintenance | 27721 | 57.7521
4464 | 2025-04-27 | 2025 | 2025 | 2025-04-01 | 2 | O2_07 | TQGXIIPL | GEDA | 3.846% | 6300 | Yaw error | Break down | 0.80833 | 0.80833 | 0.81319 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & started WTG. | Close | 0.0044872 | O2-04 | 125.7229 |  | WTG Unscheduled Maintenance | 25863 | 125.7229
4465 | 2025-04-27 | 2025 | 2025 | 2025-04-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 643 | Sim.angle E enc. <> act.angle 3 | Break down | 0.49931 | 0.49931 | 0.50764 | 0 | 0.2 | 0.2 | Checked related error data log then apply soft reboot then reset & started WTG. | Close | 0.0076923 | O2-14 | 148.5917 |  | WTG Unscheduled Maintenance | 17831 | 148.5917
4466 | 2025-04-27 | 2025 | 2025 | 2025-04-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD | 0.31667 | 0.31667 | 0.62361 | 0 | 7.3667 | 7.3667 | WTG Manual stop for Blade-1 VG installation work done than started wtg. | Close | 0.28333 | O2-22 | 7415.7778 |  | WTG Breakdown Maintenance | 24160 | 7415.7778
4467 | 2025-04-27 | 2025 | 2025 | 2025-04-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 3800 | Circuit breaker | Major BD | 0 | 0.15556 | 0.60694 | 3.7333 | 10.8333 | 14.5667 | attend for WTG stop in Grid loss error(Circuit breaker(Grid loss without grid loss auxiliary power) so we attend turbine and check Sam data and also check physically and check converter panel and found ACB was trip so check Busbar and its connections and also check power cable and stator and rotor and Also take Busbar IR but nothing found abnormalities so now we check ACB and its setting with our technical team and supplier and set ACB settings and also re-tight all connection than reset and take trial than nothing found abnormal so start WTG.(now turbine under observation). | Close | 0.56026 | O2-07 | 14140.5917 |  | WTG Unscheduled Maintenance | 23298 | 14140.5917
4468 | 2025-04-27 | 2025 | 2025 | 2025-04-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.70972 | 0.70972 | 0.73194 | 0 | 0.53333 | 0.53333 | attend wtg for power panel inspection work. | Close | 0.020513 | O2-07 | 517.7333 |  | WTG Breakdown Maintenance | 23298 | 517.7333
4469 | 2025-04-27 | 2025 | 2025 | 2025-04-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.38125 | 0.38125 | 0.38333 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | O2-11 | 38.5333 |  | WTG Unscheduled Maintenance | 18496 | 38.5333
4470 | 2025-04-27 | 2025 | 2025 | 2025-04-01 | 2 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.38125 | 0.38125 | 0.38333 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | O2-01 | 45.1188 |  | WTG Unscheduled Maintenance | 21657 | 45.1188
4471 | 2025-04-28 | 2025 | 2025 | 2025-04-01 | 2 | O2_02 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.47361 | 0.47361 | 0.47778 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-05 | 120.5875 |  | WTG Unscheduled Maintenance | 28941 | 120.5875
4472 | 2025-04-28 | 2025 | 2025 | 2025-04-01 | 2 | O2_03 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Break down | 0.775 | 0.775 | 0.77986 | 0 | 0.11667 | 0.11667 | After Grid error occurred so Checked related error data log then apply soft reboot & started WTG. | Close | 0.0044872 | O2-09 | 115.0285 |  | WTG Unscheduled Maintenance | 23663 | 115.0285
4473 | 2025-04-28 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.47431 | 0.47431 | 0.47639 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | O2-02 | 70.2604 |  | WTG Unscheduled Maintenance | 33725 | 70.2604
4474 | 2025-04-28 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.74861 | 0.74861 | 0.75278 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-02 | 140.5208 |  | WTG Unscheduled Maintenance | 33725 | 140.5208
4475 | 2025-04-28 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.85764 | 0.85764 | 0.92639 | 0 | 1.65 | 1.65 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.063462 | O2-02 | 2318.5938 |  | WTG Breakdown Maintenance | 33725 | 2318.5938
4476 | 2025-04-28 | 2025 | 2025 | 2025-04-01 | 2 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.28472 | 0.28472 | 0.60833 | 0 | 7.7667 | 7.7667 | WTG stop for YPM day-1 activity complate and Lift FTU work done than started WTG. | Close | 0.29872 | O2-21 | 7029.1569 |  | WTG Scheduled Maintenance | 21721 | 7029.1569
4477 | 2025-04-28 | 2025 | 2025 | 2025-04-01 | 2 | O2_06 | TQGXIIPL | GEDA | 3.846% | 6056 | High yaw load | Break down | 0.66181 | 0.66181 | 0.66319 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & started WTG. | Close | 0.0012821 | O2-21 | 30.1681 |  | WTG Unscheduled Maintenance | 21721 | 30.1681
4478 | 2025-04-28 | 2025 | 2025 | 2025-04-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.78681 | 0.78681 | 0.84028 | 0 | 1.2833 | 1.2833 | WTG Manual stop for load shedding due to feeder-01 overloading issue + Lift FTU work done than start WTG. | Close | 0.049359 | O2-14 | 1078.6417 |  | WTG Breakdown Maintenance | 20172 | 1078.6417
4479 | 2025-04-28 | 2025 | 2025 | 2025-04-01 | 2 | O2_16 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.69792 | 0.69792 | 0.72708 | 0 | 0.7 | 0.7 | Wtg manual stop for wtg Lift FTU work. | Close | 0.026923 | O2-21 | 633.5292 |  | WTG Breakdown Maintenance | 21721 | 633.5292
4480 | 2025-04-28 | 2025 | 2025 | 2025-04-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 551 | Pitch motor current too high | Break down | 0.25208 | 0.25208 | 0.25556 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & started WTG. | Close | 0.0032051 | O2-22 | 99.5312 |  | WTG Unscheduled Maintenance | 28665 | 99.5312
4481 | 2025-04-28 | 2025 | 2025 | 2025-04-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD | 0.35278 | 0.35278 | 0.69097 | 0 | 8.1167 | 8.1167 | WTG Manual stop for Blade-2 VG installation work done than started wtg. | Close | 0.31218 | O2-22 | 9694.3437 |  | WTG Breakdown Maintenance | 28665 | 9694.3437
4482 | 2025-04-28 | 2025 | 2025 | 2025-04-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.87778 | 0.87778 | 0.87917 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & started WTG. | Close | 0.0012821 | O2-22 | 39.8125 |  | WTG Unscheduled Maintenance | 28665 | 39.8125
4483 | 2025-04-28 | 2025 | 2025 | 2025-04-01 | 2 | O2_20 | TQGXIIPL | GEDA | 3.846% | 7017 | Parameter outside limits stop | Break down | 0.78542 | 0.78542 | 0.79375 | 0 | 0.2 | 0.2 | Checked related error data log then apply soft reboot then reset & started WTG. | Close | 0.0076923 | O2-24 | 210.925 |  | WTG Unscheduled Maintenance | 25311 | 210.925
4484 | 2025-04-28 | 2025 | 2025 | 2025-04-01 | 2 | O2_21 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.62917 | 0.62917 | 0.66528 | 0 | 0.86667 | 0.86667 | Wtg manual stop for wtg Lift FTU work. | Close | 0.033333 | O2-06 | 677.1556 |  | WTG Breakdown Maintenance | 18752 | 677.1556
4485 | 2025-04-28 | 2025 | 2025 | 2025-04-01 | 2 | O2_22 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.46181 | 0.46181 | 0.50347 | 0 | 1 | 1 | WTG stop for Customer Audit work than WIP, | Close | 0.038462 | O2-06 | 781.3333 |  | WTG Breakdown Maintenance | 18752 | 781.3333
4486 | 2025-04-28 | 2025 | 2025 | 2025-04-01 | 2 | O2_22 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.50347 | 0.50347 | 0.53681 | 0 | 0.8 | 0.8 | Wtg manual stop for wtg Lift FTU work. | Close | 0.030769 | O2-06 | 625.0667 |  | WTG Breakdown Maintenance | 18752 | 625.0667
4487 | 2025-04-28 | 2025 | 2025 | 2025-04-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Break down | 0.76597 | 0.76597 | 0.77222 | 0 | 0.15 | 0.15 | After Grid error occurred so Checked related error data log then apply soft reboot & started WTG. | Close | 0.0057692 | O2-11 | 141.75 |  | WTG Unscheduled Maintenance | 22680 | 141.75
4488 | 2025-04-28 | 2025 | 2025 | 2025-04-01 | 2 | O2_24 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.67361 | 0.67361 | 0.67778 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-20 | 101.9292 |  | WTG Unscheduled Maintenance | 24463 | 101.9292
4489 | 2025-04-29 | 2025 | 2025 | 2025-04-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.58681 | 0.58681 | 0.60486 | 0 | 0.43333 | 0.43333 | Wtg manual stop for wtg Lift FTU work. | Close | 0.016667 | O2-26 | 730.8167 |  | WTG Breakdown Maintenance | 40476 | 730.8167
4490 | 2025-04-29 | 2025 | 2025 | 2025-04-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 159 | SLC SF emergency stop | Break down | 0.96528 | 0.96528 | 1899-12-31 | 0 | 0.83333 | 0.83333 | WTG disconnect from Scada so Attend and check error related ckt than found UPS supply output MCB tripped so wip, | Close | 0.032051 | O2-26 | 1405.4167 |  | WTG Unscheduled Maintenance | 40476 | 1405.4167
4491 | 2025-04-29 | 2025 | 2025 | 2025-04-01 | 2 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.71042 | 0.71042 | 0.73542 | 0 | 0.6 | 0.6 | Wtg manual stop for wtg Lift FTU work. | Close | 0.023077 | O2-05 | 946.775 |  | WTG Breakdown Maintenance | 37871 | 946.775
4492 | 2025-04-29 | 2025 | 2025 | 2025-04-01 | 2 | O2_03 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Break down | 0.5 | 0.5 | 0.67361 | 0 | 4.1667 | 4.1667 | Attend and check event in SAM found pitch error also check in snap and found Encoder value deviation so we have attend turbine and check QA001 contector manually oparate found L2 and L3 cable loose so check All NO/NC auxiliry switch and found one nos NC switch not working properly and check voltage found normal then we have taken trial turbine after no any abnormality so started Turbine. | Close | 0.16026 | O2-09 | 7095.6597 |  | WTG Breakdown Maintenance | 40871 | 7095.6597
4493 | 2025-04-29 | 2025 | 2025 | 2025-04-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.66667 | 0.66667 | 0.69028 | 0 | 0.56667 | 0.56667 | Wtg manual stop for wtg Lift FTU work. | Close | 0.021795 | O2-07 | 1117.325 |  | WTG Breakdown Maintenance | 47322 | 1117.325
4494 | 2025-04-29 | 2025 | 2025 | 2025-04-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down | 0.75208 | 0.75208 | 0.75694 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & started WTG. | Close | 0.0044872 | O2-07 | 230.0375 |  | WTG Unscheduled Maintenance | 47322 | 230.0375
4495 | 2025-04-29 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.86458 | 0.86458 | 1899-12-31 | 0 | 3.25 | 3.25 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.125 | O2-02 | 6362.8229 |  | WTG Breakdown Maintenance | 46987 | 6362.8229
4496 | 2025-04-29 | 2025 | 2025 | 2025-04-01 | 2 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.28889 | 0.28889 | 0.57917 | 0 | 6.9667 | 6.9667 | WTG stop for YPM day-2 activity complate than started WTG. | Close | 0.26795 | O2-21 | 10393.9764 |  | WTG Scheduled Maintenance | 35807 | 10393.9764
4497 | 2025-04-29 | 2025 | 2025 | 2025-04-01 | 2 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.61042 | 0.61042 | 0.61528 | 0 | 0.11667 | 0.11667 | Checked related error data log then apply soft reboot then reset & started WTG. | Close | 0.0044872 | O2-21 | 174.0618 |  | WTG Unscheduled Maintenance | 35807 | 174.0618
4498 | 2025-04-29 | 2025 | 2025 | 2025-04-01 | 2 | O2_07 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.32639 | 0.32639 | 0.33056 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-04 | 198.5875 |  | WTG Unscheduled Maintenance | 47661 | 198.5875
4499 | 2025-04-29 | 2025 | 2025 | 2025-04-01 | 2 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.74792 | 0.74792 | 0.78125 | 0 | 0.8 | 0.8 | Checked related error data log then apply soft reboot then reset & started WTG. | Close | 0.030769 | O2-04 | 1588.7 |  | WTG Unscheduled Maintenance | 47661 | 1588.7
4500 | 2025-04-29 | 2025 | 2025 | 2025-04-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.55278 | 0.55278 | 0.55694 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-26 | 168.65 |  | WTG Unscheduled Maintenance | 40476 | 168.65
4501 | 2025-04-29 | 2025 | 2025 | 2025-04-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.61042 | 0.61042 | 0.61806 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & started WTG. | Close | 0.0070513 | O2-26 | 309.1917 |  | WTG Unscheduled Maintenance | 40476 | 309.1917
4502 | 2025-04-29 | 2025 | 2025 | 2025-04-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.525 | 0.525 | 0.52917 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-15 | 168.3958 |  | WTG Unscheduled Maintenance | 40415 | 168.3958
4503 | 2025-04-29 | 2025 | 2025 | 2025-04-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down | 0.50833 | 0.50833 | 0.51944 | 0 | 0.26667 | 0.26667 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.010256 | O2-14 | 402.7 |  | WTG Unscheduled Maintenance | 36243 | 402.7
4504 | 2025-04-29 | 2025 | 2025 | 2025-04-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.45972 | 0.45972 | 0.46389 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-11 | 159.9208 |  | WTG Unscheduled Maintenance | 38381 | 159.9208
4505 | 2025-04-29 | 2025 | 2025 | 2025-04-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.48056 | 0.48056 | 0.49514 | 0 | 0.35 | 0.35 | Checked related error data log then reset & started WTG. | Close | 0.013462 | O2-11 | 559.7229 |  | WTG Unscheduled Maintenance | 38381 | 559.7229
4506 | 2025-04-29 | 2025 | 2025 | 2025-04-01 | 2 | O2_14 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.51667 | 0.51667 | 0.52014 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & started WTG. | Close | 0.0032051 | O2-12 | 127.0694 |  | WTG Unscheduled Maintenance | 36596 | 127.0694
4507 | 2025-04-29 | 2025 | 2025 | 2025-04-01 | 2 | O2_15 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.35903 | 0.35903 | 0.36319 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-10 | 140.3042 |  | WTG Unscheduled Maintenance | 33673 | 140.3042
4508 | 2025-04-29 | 2025 | 2025 | 2025-04-01 | 2 | O2_15 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.69028 | 0.69028 | 0.70694 | 0 | 0.4 | 0.4 | Checked related error data log then apply soft reboot then reset & started WTG. | Close | 0.015385 | O2-10 | 561.2167 |  | WTG Unscheduled Maintenance | 33673 | 561.2167
4509 | 2025-04-29 | 2025 | 2025 | 2025-04-01 | 2 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.64861 | 0.64861 | 0.65417 | 0 | 0.13333 | 0.13333 | Checked related error data log then apply soft reboot then reset & started WTG. | Close | 0.0051282 | O2-21 | 198.9278 |  | WTG Unscheduled Maintenance | 35807 | 198.9278
4510 | 2025-04-29 | 2025 | 2025 | 2025-04-01 | 2 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.67292 | 0.67292 | 0.67708 | 0 | 0.1 | 0.1 | Checked related error data log then apply soft reboot then reset & started WTG. | Close | 0.0038462 | O2-21 | 149.1958 |  | WTG Unscheduled Maintenance | 35807 | 149.1958
4511 | 2025-04-29 | 2025 | 2025 | 2025-04-01 | 2 | O2_16 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.69514 | 0.69514 | 0.69931 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-21 | 149.1958 |  | WTG Unscheduled Maintenance | 35807 | 149.1958
4512 | 2025-04-29 | 2025 | 2025 | 2025-04-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.62292 | 0.62292 | 0.62431 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & started WTG. | Close | 0.0012821 | O2-22 | 57.5472 |  | WTG Unscheduled Maintenance | 41434 | 57.5472
4513 | 2025-04-29 | 2025 | 2025 | 2025-04-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.64653 | 0.64653 | 0.65069 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-22 | 172.6417 |  | WTG Unscheduled Maintenance | 41434 | 172.6417
4514 | 2025-04-29 | 2025 | 2025 | 2025-04-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.74514 | 0.74514 | 0.77222 | 0 | 0.65 | 0.65 | Checked related error data log then apply soft reboot then reset & started WTG. | Close | 0.025 | O2-22 | 1122.1708 |  | WTG Unscheduled Maintenance | 41434 | 1122.1708
4515 | 2025-04-29 | 2025 | 2025 | 2025-04-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down | 0.51181 | 0.51181 | 0.51736 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & started WTG. | Close | 0.0051282 | O2-07 | 262.9 |  | WTG Unscheduled Maintenance | 47322 | 262.9
4516 | 2025-04-29 | 2025 | 2025 | 2025-04-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down | 0.73125 | 0.73125 | 0.74722 | 0 | 0.38333 | 0.38333 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.014744 | O2-07 | 755.8375 |  | WTG Unscheduled Maintenance | 47322 | 755.8375
4517 | 2025-04-29 | 2025 | 2025 | 2025-04-01 | 2 | O2_21 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.61389 | 0.61389 | 0.61806 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-06 | 125.8458 |  | WTG Unscheduled Maintenance | 30203 | 125.8458
4518 | 2025-04-29 | 2025 | 2025 | 2025-04-01 | 2 | O2_22 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down | 0.83958 | 0.83958 | 0.85625 | 0 | 0.4 | 0.4 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.015385 | O2-06 | 503.3833 |  | WTG Unscheduled Maintenance | 30203 | 503.3833
4519 | 2025-04-29 | 2025 | 2025 | 2025-04-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down | 0.76944 | 0.76944 | 0.78611 | 0 | 0.4 | 0.4 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.015385 | O2-11 | 639.6833 |  | WTG Unscheduled Maintenance | 38381 | 639.6833
4520 | 2025-04-29 | 2025 | 2025 | 2025-04-01 | 2 | O2_24 | TQGXIIPL | GEDA | 3.846% | 6056 | High yaw load | Break down | 0.57083 | 0.57083 | 0.57292 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | O2-20 | 87.3437 |  | WTG Unscheduled Maintenance | 41925 | 87.3437
4521 | 2025-04-29 | 2025 | 2025 | 2025-04-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.75694 | 0.75694 | 1899-12-31 | 0 | 5.8333 | 5.8333 | WTG Manual stop for load shedding due to feeder-01 overloading issue + Lift FTU work done than start WTG. | Close | 0.22436 | O2-01 | 9479.6528 |  | WTG Breakdown Maintenance | 39002 | 9479.6528
4522 | 2025-04-29 | 2025 | 2025 | 2025-04-01 | 2 | O2_26 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.65139 | 0.65139 | 0.66736 | 0 | 0.38333 | 0.38333 | Checked related error data log then apply soft reboot then reset & started WTG. | Close | 0.014744 | O2-01 | 622.9486 |  | WTG Unscheduled Maintenance | 39002 | 622.9486
4523 | 2025-04-29 | 2025 | 2025 | 2025-04-01 | 2 | O2_26 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.675 | 0.675 | 0.67917 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-01 | 162.5083 |  | WTG Unscheduled Maintenance | 39002 | 162.5083
4524 | 2025-04-30 | 2025 | 2025 | 2025-04-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 159 | SLC SF emergency stop | Break down | 0 | 0 | 0.11111 | 0 | 2.6667 | 2.6667 | WTG disconnect from Scada so Attend and check error related ckt than found UPS supply output MCB tripped so check all connection in panel found ok than reset and started WTG. | Close | 0.10256 | O2-26 | 4259.2222 |  | WTG Unscheduled Maintenance | 38333 | 4259.2222
4525 | 2025-04-30 | 2025 | 2025 | 2025-04-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 159 | SLC SF emergency stop | Break down | 0.14583 | 0.14583 | 0.1875 | 0 | 1 | 1 | WTG disconnect from Scada so Attend and check error related ckt than found UPS supply output MCB tripped so check all connection in panel found ok than reset and started WTG. | Close | 0.038462 | O2-26 | 1597.2083 |  | WTG Unscheduled Maintenance | 38333 | 1597.2083
4526 | 2025-04-30 | 2025 | 2025 | 2025-04-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.9 | 0.9 | 0.95139 | 0 | 1.2333 | 1.2333 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.047436 | O2-26 | 1969.8903 |  | WTG Breakdown Maintenance | 38333 | 1969.8903
4527 | 2025-04-30 | 2025 | 2025 | 2025-04-01 | 2 | O2_02 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.575 | 0.575 | 0.57639 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & started WTG. | Close | 0.0012821 | O2-05 | 51.9833 |  | WTG Unscheduled Maintenance | 37428 | 51.9833
4528 | 2025-04-30 | 2025 | 2025 | 2025-04-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.34861 | 0.34861 | 0.35278 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-07 | 181.6458 |  | WTG Unscheduled Maintenance | 43595 | 181.6458
4529 | 2025-04-30 | 2025 | 2025 | 2025-04-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.38125 | 0.38125 | 0.38264 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & started WTG. | Close | 0.0012821 | O2-07 | 60.5486 |  | WTG Unscheduled Maintenance | 43595 | 60.5486
4530 | 2025-04-30 | 2025 | 2025 | 2025-04-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.49722 | 0.49722 | 0.50139 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-07 | 181.6458 |  | WTG Unscheduled Maintenance | 43595 | 181.6458
4531 | 2025-04-30 | 2025 | 2025 | 2025-04-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down | 0.7625 | 0.7625 | 0.78056 | 0 | 0.43333 | 0.43333 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.016667 | O2-07 | 787.1319 |  | WTG Unscheduled Maintenance | 43595 | 787.1319
4532 | 2025-04-30 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0 | 0 | 0.038194 | 0 | 0.91667 | 0.91667 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.035256 | O2-02 | 1794.2222 |  | WTG Breakdown Maintenance | 46976 | 1794.2222
4533 | 2025-04-30 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.77986 | 0.77986 | 0.78403 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-02 | 195.7333 |  | WTG Unscheduled Maintenance | 46976 | 195.7333
4534 | 2025-04-30 | 2025 | 2025 | 2025-04-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.89444 | 0.89444 | 0.97222 | 0 | 1.8667 | 1.8667 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.071795 | O2-02 | 3653.6889 |  | WTG Breakdown Maintenance | 46976 | 3653.6889
4535 | 2025-04-30 | 2025 | 2025 | 2025-04-01 | 2 | O2_06 | TQGXIIPL | GEDA | 3.846% | 6056 | High yaw load | Break down | 0.60903 | 0.60903 | 0.61111 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | O2-21 | 72.7021 |  | WTG Unscheduled Maintenance | 34897 | 72.7021
4536 | 2025-04-30 | 2025 | 2025 | 2025-04-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.44444 | 0.44444 | 0.47569 | 0 | 0.75 | 0.75 | Wtg manual stop for wtg Lift FTU work. | Close | 0.028846 | O2-26 | 1197.9062 |  | WTG Breakdown Maintenance | 38333 | 1197.9062
4537 | 2025-04-30 | 2025 | 2025 | 2025-04-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.68333 | 0.68333 | 0.6875 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-26 | 159.7208 |  | WTG Unscheduled Maintenance | 38333 | 159.7208
4538 | 2025-04-30 | 2025 | 2025 | 2025-04-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.75694 | 0.75694 | 0.84931 | 0 | 2.2167 | 2.2167 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.085256 | O2-26 | 3540.4785 |  | WTG Unscheduled Maintenance | 38333 | 3540.4785
4539 | 2025-04-30 | 2025 | 2025 | 2025-04-01 | 2 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.69306 | 0.69306 | 0.72153 | 0 | 0.68333 | 0.68333 | Wtg manual stop for wtg Lift FTU work. | Close | 0.026282 | O2-03 | 1015.2056 |  | WTG Breakdown Maintenance | 35656 | 1015.2056
4540 | 2025-04-30 | 2025 | 2025 | 2025-04-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.70625 | 0.70625 | 0.71042 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-15 | 162.6167 |  | WTG Unscheduled Maintenance | 39028 | 162.6167
4541 | 2025-04-30 | 2025 | 2025 | 2025-04-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 643 | Sim.angle E enc. <> act.angle 3 | Break down | 0.45556 | 0.45556 | 0.57292 | 0 | 2.8167 | 2.8167 | Attend WTG for repeated error Sim angle 3 so check all related ckt and found QA001 contactor auxiliary 23 and 24 on loose connection so tight it and apply manually Pitching no any abnormality so reset and started WTG. | Close | 0.10833 | O2-14 | 4119.375 |  | WTG Breakdown Maintenance | 35100 | 4119.375
4542 | 2025-04-30 | 2025 | 2025 | 2025-04-01 | 2 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.60208 | 0.60208 | 0.625 | 0 | 0.55 | 0.55 | Wtg manual stop for wtg Lift FTU work. | Close | 0.021154 | O2-10 | 774.9271 |  | WTG Breakdown Maintenance | 33815 | 774.9271
4543 | 2025-04-30 | 2025 | 2025 | 2025-04-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.64931 | 0.64931 | 0.65625 | 0 | 0.16667 | 0.16667 | Checked related error data log then reset & started WTG. | Close | 0.0064103 | O2-22 | 281.4375 |  | WTG Unscheduled Maintenance | 40527 | 281.4375
4544 | 2025-04-30 | 2025 | 2025 | 2025-04-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.73333 | 0.73333 | 0.73542 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | O2-22 | 84.4313 |  | WTG Unscheduled Maintenance | 40527 | 84.4313
4545 | 2025-04-30 | 2025 | 2025 | 2025-04-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 2355 | Temp. rot.br.pad high | Break down | 0.072222 | 0.072222 | 0.076389 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | O2-06 | 167.4792 |  | WTG Unscheduled Maintenance | 40195 | 167.4792
4546 | 2025-04-30 | 2025 | 2025 | 2025-04-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 2355 | Temp. rot.br.pad high | Break down | 0.94514 | 0.94514 | 0.95417 | 0 | 0.21667 | 0.21667 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.0083333 | O2-06 | 362.8715 |  | WTG Unscheduled Maintenance | 40195 | 362.8715
4547 | 2025-04-30 | 2025 | 2025 | 2025-04-01 | 2 | O2_21 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.66458 | 0.66458 | 0.66875 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-06 | 167.4792 |  | WTG Unscheduled Maintenance | 40195 | 167.4792
4548 | 2025-04-30 | 2025 | 2025 | 2025-04-01 | 2 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.53056 | 0.53056 | 0.53472 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-06 | 167.4792 |  | WTG Unscheduled Maintenance | 40195 | 167.4792
4549 | 2025-04-30 | 2025 | 2025 | 2025-04-01 | 2 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.61528 | 0.61528 | 0.61736 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | O2-06 | 83.7396 |  | WTG Unscheduled Maintenance | 40195 | 83.7396
4550 | 2025-04-30 | 2025 | 2025 | 2025-04-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.65208 | 0.65208 | 0.67708 | 0 | 0.6 | 0.6 | Wtg manual stop for wtg Lift FTU work. | Close | 0.023077 | O2-11 | 999.525 |  | WTG Breakdown Maintenance | 39981 | 999.525
4551 | 2025-04-30 | 2025 | 2025 | 2025-04-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0 | 0 | 0.016667 | 0 | 0.4 | 0.4 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.015385 | O2-01 | 512.7667 |  | WTG Breakdown Maintenance | 30766 | 512.7667
4552 | 2025-04-30 | 2025 | 2025 | 2025-04-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.74444 | 0.74444 | 0.81319 | 0 | 1.65 | 1.65 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.063462 | O2-01 | 2115.1625 |  | WTG Breakdown Maintenance | 30766 | 2115.1625
4553 | 2025-04-30 | 2025 | 2025 | 2025-04-01 | 2 | O2_26 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.49792 | 0.49792 | 0.51181 | 0 | 0.33333 | 0.33333 | Wtg manual stop for wtg Lift FTU work. | Close | 0.012821 | O2-01 | 427.3056 |  | WTG Breakdown Maintenance | 30766 | 427.3056
4554 | 2025-04-30 | 2025 | 2025 | 2025-04-01 | 2 | O2_26 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.56528 | 0.56528 | 0.57361 | 0 | 0.2 | 0.2 | Checked related error data log then reset & started WTG. | Close | 0.0076923 | O2-01 | 256.3833 |  | WTG Unscheduled Maintenance | 30766 | 256.3833
4555 | 2025-05-01 | 2025 | 2025 | 2025-05-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.60833 | 0.60833 | 0.6125 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-07 | 190.975 |  | WTG Unscheduled Maintenance | 45834 | 190.975
4556 | 2025-05-01 | 2025 | 2025 | 2025-05-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.44514 | 0.44514 | 0.47569 | 0 | 0.73333 | 0.73333 | Wtg manual stop for wtg Lift FTU work. | Close | 0.028205 | O2-02 | 1517.6944 |  | WTG Breakdown Maintenance | 49670 | 1517.6944
4557 | 2025-05-01 | 2025 | 2025 | 2025-05-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.61944 | 0.61944 | 0.62083 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & started WTG. | Close | 0.0012821 | O2-02 | 68.9861 |  | WTG Unscheduled Maintenance | 49670 | 68.9861
4558 | 2025-05-01 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.60069 | 0.60069 | 0.60486 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-26 | 186.1417 |  | WTG Unscheduled Maintenance | 44674 | 186.1417
4559 | 2025-05-01 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.61111 | 0.61111 | 0.61319 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | O2-26 | 93.0708 |  | WTG Unscheduled Maintenance | 44674 | 93.0708
4560 | 2025-05-01 | 2025 | 2025 | 2025-05-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.63542 | 0.63542 | 0.63681 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & started WTG. | Close | 0.0012821 | O2-14 | 53.5236 |  | WTG Unscheduled Maintenance | 38537 | 53.5236
4561 | 2025-05-01 | 2025 | 2025 | 2025-05-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down | 0.78333 | 0.78333 | 0.79861 | 0 | 0.36667 | 0.36667 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.014103 | O2-14 | 588.7597 |  | WTG Unscheduled Maintenance | 38537 | 588.7597
4562 | 2025-05-01 | 2025 | 2025 | 2025-05-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.42431 | 0.42431 | 0.57292 | 0 | 3.5667 | 3.5667 | Attend for WTG Repeated error (Wind dire.diff.level 2) so check wind vane connection after wind vane 1 & 2 alignment properly after trail so ok then reset and start WTG. | Close | 0.13718 | O2-22 | 7062.5944 |  | WTG Breakdown Maintenance | 47524 | 7062.5944
4563 | 2025-05-01 | 2025 | 2025 | 2025-05-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 2355 | Temp. rot.br.pad high | Break down | 0.14444 | 0.14444 | 0.16806 | 0 | 0.56667 | 0.56667 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.021795 | O2-06 | 1099.0264 |  | WTG Unscheduled Maintenance | 46547 | 1099.0264
4564 | 2025-05-01 | 2025 | 2025 | 2025-05-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.57222 | 0.57222 | 0.57569 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & started WTG. | Close | 0.0032051 | O2-07 | 159.1458 |  | WTG Unscheduled Maintenance | 45834 | 159.1458
4565 | 2025-05-01 | 2025 | 2025 | 2025-05-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down | 0.71319 | 0.71319 | 0.72917 | 0 | 0.38333 | 0.38333 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.014744 | O2-07 | 732.0708 |  | WTG Unscheduled Maintenance | 45834 | 732.0708
4566 | 2025-05-01 | 2025 | 2025 | 2025-05-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down | 0.82431 | 0.82431 | 0.84444 | 0 | 0.48333 | 0.48333 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.01859 | O2-07 | 923.0458 |  | WTG Unscheduled Maintenance | 45834 | 923.0458
4567 | 2025-05-01 | 2025 | 2025 | 2025-05-01 | 2 | O2_20 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.53403 | 0.53403 | 0.53819 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-24 | 172.4375 |  | WTG Unscheduled Maintenance | 41385 | 172.4375
4568 | 2025-05-01 | 2025 | 2025 | 2025-05-01 | 2 | O2_20 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.58889 | 0.58889 | 0.59792 | 0 | 0.21667 | 0.21667 | Checked related error data log then reset & started WTG. | Close | 0.0083333 | O2-24 | 373.6146 |  | WTG Unscheduled Maintenance | 41385 | 373.6146
4569 | 2025-05-01 | 2025 | 2025 | 2025-05-01 | 2 | O2_21 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.31319 | 0.31319 | 0.31736 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-06 | 193.9458 |  | WTG Unscheduled Maintenance | 46547 | 193.9458
4570 | 2025-05-01 | 2025 | 2025 | 2025-05-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.44236 | 0.44236 | 0.44653 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-11 | 168.8167 |  | WTG Unscheduled Maintenance | 40516 | 168.8167
4571 | 2025-05-01 | 2025 | 2025 | 2025-05-01 | 2 | O2_24 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.64722 | 0.64722 | 0.68611 | 0 | 0.93333 | 0.93333 | Wtg manual stop for wtg Lift FTU work. | Close | 0.035897 | O2-20 | 1708.4278 |  | WTG Breakdown Maintenance | 43931 | 1708.4278
4572 | 2025-05-02 | 2025 | 2025 | 2025-05-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.68056 | 0.68056 | 0.68472 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-07 | 110.7542 |  | WTG Unscheduled Maintenance | 26581 | 110.7542
4573 | 2025-05-02 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 58 | Wind dir.dev. level 2 | Break down | 0.58681 | 0.58681 | 0.58889 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | O2-26 | 53.3917 |  | WTG Unscheduled Maintenance | 25628 | 53.3917
4574 | 2025-05-02 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.56319 | 0.56319 | 0.56736 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-26 | 106.7833 |  | WTG Unscheduled Maintenance | 25628 | 106.7833
4575 | 2025-05-02 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.6125 | 0.6125 | 0.62778 | 0 | 0.36667 | 0.36667 | In turbine error occurred during bettry test Rotor br. Buff.volt too low so check related error data log and all perameter then apply soft reboot than started Turbine. | Close | 0.014103 | O2-26 | 391.5389 |  | WTG Unscheduled Maintenance | 25628 | 391.5389
4576 | 2025-05-02 | 2025 | 2025 | 2025-05-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.52361 | 0.52361 | 0.52778 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-12 | 108.1417 |  | WTG Unscheduled Maintenance | 25954 | 108.1417
4577 | 2025-05-02 | 2025 | 2025 | 2025-05-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6056 | High yaw load | Break down | 0.66111 | 0.66111 | 0.66319 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | O2-11 | 55.4312 |  | WTG Unscheduled Maintenance | 26607 | 55.4312
4578 | 2025-05-02 | 2025 | 2025 | 2025-05-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.48472 | 0.48472 | 0.48611 | 0 | 0.033333 | 0.033333 | After Software Update work done than start WTG. | Close | 0.0012821 | O2-22 | 40.0181 |  | WTG Unscheduled Maintenance | 28813 | 40.0181
4579 | 2025-05-02 | 2025 | 2025 | 2025-05-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 172 | SLC MF torque protection | Break down | 0.071528 | 0.071528 | 0.0875 | 0 | 0.38333 | 0.38333 | Checked related error data log then apply soft reboot then reset & started WTG. | Close | 0.014744 | O2-06 | 463.9611 |  | WTG Unscheduled Maintenance | 29048 | 463.9611
4580 | 2025-05-02 | 2025 | 2025 | 2025-05-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.4875 | 0.4875 | 0.48958 | 0 | 0.05 | 0.05 | After Software Update work done than start WTG. | Close | 0.0019231 | O2-06 | 60.5167 |  | WTG Breakdown Maintenance | 29048 | 60.5167
4581 | 2025-05-02 | 2025 | 2025 | 2025-05-01 | 2 | O2_21 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.30972 | 0.30972 | 0.6875 | 0 | 9.0667 | 9.0667 | WTG stop for YPM activity and replace axis 1 (1.7 ohm)Flat resistor then work complated than started WTG. | Close | 0.34872 | O2-06 | 10973.6889 |  | WTG Scheduled Maintenance | 29048 | 10973.6889
4582 | 2025-05-02 | 2025 | 2025 | 2025-05-01 | 2 | O2_26 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.625 | 0.625 | 0.62917 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | O2-01 | 123.7583 |  | WTG Unscheduled Maintenance | 29702 | 123.7583
4583 | 2025-05-02 | 2025 | 2025 | 2025-05-01 | 2 | O2_26 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.73472 | 0.73472 | 0.74444 | 0 | 0.23333 | 0.23333 | Checked related error data log then reset & started WTG. | Close | 0.0089744 | O2-01 | 288.7694 |  | WTG Unscheduled Maintenance | 29702 | 288.7694
4584 | 2025-05-03 | 2025 | 2025 | 2025-05-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 7002 | Task runtime failure 5ms | Break down | 0.16667 | 0.16667 | 0.17153 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & started WTG. | Close | 0.0044872 | O2-26 | 211.191 |  | WTG Unscheduled Maintenance | 43445 | 211.191
4585 | 2025-05-03 | 2025 | 2025 | 2025-05-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.75069 | 0.75069 | 0.91667 | 0 | 3.9833 | 3.9833 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.15321 | O2-26 | 7210.6632 |  | WTG Breakdown Maintenance | 43445 | 7210.6632
4586 | 2025-05-03 | 2025 | 2025 | 2025-05-01 | 2 | O2_02 | TQGXIIPL | GEDA | 3.846% | 550 | Pitch current asymmetry | Auto reset | 0.17569 | 0.17569 | 0.17778 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2-05 | 105.3938 |  | WTG Unscheduled Maintenance | 50589 | 105.3938
4587 | 2025-05-03 | 2025 | 2025 | 2025-05-01 | 2 | O2_06 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.60833 | 0.60833 | 0.62083 | 0 | 0.3 | 0.3 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.011538 | O2-21 | 589.75 |  | WTG Unscheduled Maintenance | 47180 | 589.75
4588 | 2025-05-03 | 2025 | 2025 | 2025-05-01 | 2 | O2_06 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.67639 | 0.69028 | 0.71528 | 0.33333 | 0.6 | 0.93333 | Attend turbine check connection of rotor brake pad 01 sensor its ohmic value , then remove sensor from pad check physical condition then refixed properly . Then check the temp value found normal so take the trail of the turbine and started . | Close | 0.035897 | O2-21 | 1834.7778 |  | WTG Breakdown Maintenance | 47180 | 1834.7778
4589 | 2025-05-03 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.35903 | 0.35903 | 0.3625 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & started WTG. | Close | 0.0032051 | O2-26 | 150.8507 |  | WTG Unscheduled Maintenance | 43445 | 150.8507
4590 | 2025-05-03 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.67639 | 0.67639 | 0.68125 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & started WTG. | Close | 0.0044872 | O2-26 | 211.191 |  | WTG Unscheduled Maintenance | 43445 | 211.191
4591 | 2025-05-03 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.99444 | 0.99444 | 0.99792 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0032051 | O2-26 | 150.8507 |  | WTG Unscheduled Maintenance | 43445 | 150.8507
4592 | 2025-05-03 | 2025 | 2025 | 2025-05-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.625 | 0.625 | 0.62917 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-12 | 179.3708 |  | WTG Unscheduled Maintenance | 43049 | 179.3708
4593 | 2025-05-03 | 2025 | 2025 | 2025-05-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.66736 | 0.66736 | 0.67014 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0025641 | O2-11 | 115.6028 |  | WTG Unscheduled Maintenance | 41617 | 115.6028
4594 | 2025-05-03 | 2025 | 2025 | 2025-05-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Auto reset | 0.63194 | 0.63194 | 0.64028 | 0 | 0.2 | 0.2 | Auto reset | Close | 0.0076923 | O2-06 | 328.8083 |  | WTG Unscheduled Maintenance | 39457 | 328.8083
4595 | 2025-05-03 | 2025 | 2025 | 2025-05-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.77778 | 0.77778 | 0.84306 | 0 | 1.5667 | 1.5667 | Attend and check error related ckt than clean rotor Brake pad and also check brake pad thickness and rotor brake pad temp.sensor connection check found ok than reset and start WTG. | Close | 0.060256 | O2-06 | 2575.6653 |  | WTG Breakdown Maintenance | 39457 | 2575.6653
4596 | 2025-05-03 | 2025 | 2025 | 2025-05-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down | 0.68333 | 0.68333 | 0.69722 | 0 | 0.33333 | 0.33333 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.012821 | O2-07 | 587.5833 |  | WTG Unscheduled Maintenance | 42306 | 587.5833
4597 | 2025-05-03 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.69792 | 0.69792 | 0.9 | 0 | 4.85 | 4.85 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.18654 | O2-26 | 8779.5104 |  | WTG Breakdown Maintenance | 43445 | 8779.5104
4598 | 2025-05-03 | 2025 | 2025 | 2025-05-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.68125 | 0.68125 | 0.68611 | 0 | 0.11667 | 0.11667 | Auto reset | Close | 0.0044872 | O2-11 | 202.3049 |  | WTG Unscheduled Maintenance | 41617 | 202.3049
4599 | 2025-05-03 | 2025 | 2025 | 2025-05-01 | 2 | O2_24 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.30347 | 0.30347 | 0.85764 | 0 | 13.3 | 13.3 | WTG stop for YPM activity complated than started WTG. | Close | 0.51154 | O2-20 | 24626.0583 |  | WTG Scheduled Maintenance | 44438 | 24626.0583
4600 | 2025-05-03 | 2025 | 2025 | 2025-05-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 550 | Pitch current asymmetry | Break down | 0.097917 | 0.097917 | 0.11042 | 0 | 0.3 | 0.3 | Checked related error data log then reset & started WTG. | Close | 0.011538 | O2-01 | 363.55 |  | WTG Breakdown Maintenance | 29084 | 363.55
4601 | 2025-05-03 | 2025 | 2025 | 2025-05-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.68819 | 0.68819 | 0.69236 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-01 | 121.1833 |  | WTG Unscheduled Maintenance | 29084 | 121.1833
4602 | 2025-05-03 | 2025 | 2025 | 2025-05-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.70625 | 0.70625 | 0.75 | 0 | 1.05 | 1.05 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.040385 | O2-01 | 1272.425 |  | WTG Breakdown Maintenance | 29084 | 1272.425
4603 | 2025-05-04 | 2025 | 2025 | 2025-05-01 | 2 | O2_03 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Auto reset | 0.45833 | 0.45833 | 0.46319 | 0 | 0.11667 | 0.11667 | Auto reset | Close | 0.0044872 | O2-09 | 138.2938 |  | WTG Unscheduled Maintenance | 28449 | 138.2938
4604 | 2025-05-04 | 2025 | 2025 | 2025-05-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.69028 | 0.69028 | 0.69444 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-07 | 98.7583 |  | WTG Unscheduled Maintenance | 23702 | 98.7583
4605 | 2025-05-04 | 2025 | 2025 | 2025-05-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Auto reset | 0.69722 | 0.69722 | 0.69861 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2-02 | 40.5194 |  | WTG Unscheduled Maintenance | 29174 | 40.5194
4606 | 2025-05-04 | 2025 | 2025 | 2025-05-01 | 2 | O2_06 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Auto reset | 0.61528 | 0.61528 | 0.61667 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2-21 | 42.8708 |  | WTG Unscheduled Maintenance | 30867 | 42.8708
4607 | 2025-05-04 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.011111 | 0.011111 | 0.013194 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2-26 | 64.2187 |  | WTG Unscheduled Maintenance | 30825 | 64.2187
4608 | 2025-05-04 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.72708 | 0.72708 | 0.85417 | 0 | 3.05 | 3.05 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.11731 | O2-26 | 3917.3437 |  | WTG Breakdown Maintenance | 30825 | 3917.3437
4609 | 2025-05-04 | 2025 | 2025 | 2025-05-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.71181 | 0.71181 | 0.71597 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-15 | 115.8667 |  | WTG Unscheduled Maintenance | 27808 | 115.8667
4610 | 2025-05-04 | 2025 | 2025 | 2025-05-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.55 | 0.55 | 0.55139 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2-12 | 41.0389 |  | WTG Unscheduled Maintenance | 29548 | 41.0389
4611 | 2025-05-04 | 2025 | 2025 | 2025-05-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.73681 | 0.73681 | 0.74097 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-12 | 123.1167 |  | WTG Unscheduled Maintenance | 29548 | 123.1167
4612 | 2025-05-04 | 2025 | 2025 | 2025-05-01 | 2 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.23611 | 0.28194 | 0.39931 | 1.1 | 2.8167 | 3.9167 | Attend for WTG stop in Circuit breaker Error (Grid loss without grid loss auxiliary power) so we attend turbine and check Sam data and also check physically and check converter panel and found ACB was trip so check Busbar and its connections and also check power cable and stator and rotor and Also take Busbar but nothing found abnormalities so now we check ACB and its setting with our technical team and set ACB setting also re-tight all connection than reset and take trial than nothing found abnormal so start WTG.(now turbine under observation). | Close | 0.15064 | O2-21 | 5037.3229 |  | WTG Breakdown Maintenance | 30867 | 5037.3229
4613 | 2025-05-04 | 2025 | 2025 | 2025-05-01 | 2 | O2_16 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.42153 | 0.42153 | 0.43056 | 0 | 0.21667 | 0.21667 | Checked related error data log then reset & started WTG. | Close | 0.0083333 | O2-21 | 278.6604 |  | WTG Unscheduled Maintenance | 30867 | 278.6604
4614 | 2025-05-04 | 2025 | 2025 | 2025-05-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.72153 | 0.72153 | 0.73542 | 0 | 0.33333 | 0.33333 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.012821 | O2-22 | 389.9583 |  | WTG Unscheduled Maintenance | 28077 | 389.9583
4615 | 2025-05-04 | 2025 | 2025 | 2025-05-01 | 2 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.63264 | 0.63264 | 0.63681 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-06 | 120.1333 |  | WTG Unscheduled Maintenance | 28832 | 120.1333
4616 | 2025-05-04 | 2025 | 2025 | 2025-05-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.70625 | 0.70625 | 0.71042 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-11 | 116.8208 |  | WTG Unscheduled Maintenance | 28037 | 116.8208
4617 | 2025-05-04 | 2025 | 2025 | 2025-05-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM | 0.30833 | 0.30833 | 0.73681 | 0 | 10.2833 | 10.2833 | WTG stop for YPM activity complated than started WTG. | Close | 0.39551 | O2-01 | 7701.3597 |  | WTG Scheduled Maintenance | 17974 | 7701.3597
4618 | 2025-05-04 | 2025 | 2025 | 2025-05-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.72292 | 0.72292 | 0.86319 | 0 | 3.3667 | 3.3667 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.12949 | O2-26 | 4324.0625 |  | WTG Breakdown Maintenance | 30825 | 4324.0625
4619 | 2025-05-04 | 2025 | 2025 | 2025-05-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Auto reset | 0.95486 | 0.95486 | 0.95694 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2-02 | 60.7792 |  | WTG Unscheduled Maintenance | 29174 | 60.7792
4620 | 2025-05-05 | 2025 | 2025 | 2025-05-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.64028 | 0.64028 | 0.75 | 0 | 2.6333 | 2.6333 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.10128 | O2-26 | 3424.8694 |  | WTG Breakdown Maintenance | 31214 | 3424.8694
4621 | 2025-05-05 | 2025 | 2025 | 2025-05-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.78542 | 0.78542 | 0.87153 | 0 | 2.0667 | 2.0667 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.079487 | O2-26 | 2687.8722 |  | WTG Breakdown Maintenance | 31214 | 2687.8722
4622 | 2025-05-05 | 2025 | 2025 | 2025-05-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Auto reset | 0.64306 | 0.64306 | 0.64444 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2-02 | 43.8319 |  | WTG Unscheduled Maintenance | 31559 | 43.8319
4623 | 2025-05-05 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.62014 | 0.62014 | 0.62431 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-26 | 130.0583 |  | WTG Unscheduled Maintenance | 31214 | 130.0583
4624 | 2025-05-05 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.67986 | 0.67986 | 0.68194 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2-26 | 65.0292 |  | WTG Unscheduled Maintenance | 31214 | 65.0292
4625 | 2025-05-05 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.72361 | 0.72361 | 0.72778 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-26 | 130.0583 |  | WTG Unscheduled Maintenance | 31214 | 130.0583
4626 | 2025-05-05 | 2025 | 2025 | 2025-05-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.64444 | 0.64444 | 0.74792 | 0 | 2.4833 | 2.4833 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.095513 | O2-12 | 3241.9917 |  | WTG Breakdown Maintenance | 31332 | 3241.9917
4627 | 2025-05-05 | 2025 | 2025 | 2025-05-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.79653 | 0.79653 | 0.86389 | 0 | 1.6167 | 1.6167 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.062179 | O2-12 | 2110.5583 |  | WTG Breakdown Maintenance | 31332 | 2110.5583
4628 | 2025-05-05 | 2025 | 2025 | 2025-05-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.63125 | 0.63125 | 0.63542 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-14 | 123.7542 |  | WTG Unscheduled Maintenance | 29701 | 123.7542
4629 | 2025-05-05 | 2025 | 2025 | 2025-05-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Auto reset | 0.64375 | 0.64375 | 0.64722 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0032051 | O2-22 | 89.9028 |  | WTG Unscheduled Maintenance | 25892 | 89.9028
4630 | 2025-05-05 | 2025 | 2025 | 2025-05-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.77431 | 0.77431 | 0.78611 | 0 | 0.28333 | 0.28333 | Checked related error data log then reset & started WTG. | Close | 0.010897 | O2-22 | 305.6694 |  | WTG Unscheduled Maintenance | 25892 | 305.6694
4631 | 2025-05-05 | 2025 | 2025 | 2025-05-01 | 2 | O2_20 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.69653 | 0.69653 | 0.70069 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-24 | 127.1458 |  | WTG Unscheduled Maintenance | 30515 | 127.1458
4632 | 2025-05-05 | 2025 | 2025 | 2025-05-01 | 2 | O2_22 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.54583 | 0.54583 | 0.55417 | 0 | 0.2 | 0.2 | Checked related error data log then reset & started WTG. | Close | 0.0076923 | O2-06 | 257.5333 |  | WTG Unscheduled Maintenance | 30904 | 257.5333
4633 | 2025-05-05 | 2025 | 2025 | 2025-05-01 | 2 | O2_26 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.59792 | 0.59792 | 0.60139 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0032051 | O2-01 | 65.3993 |  | WTG Unscheduled Maintenance | 18835 | 65.3993
4634 | 2025-05-06 | 2025 | 2025 | 2025-05-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 64 | Max. wind speed | Environment | 0.00625 | 0.00625 | 0.01875 | 0 | 0.3 | 0.3 | Auto reset | Close | 0.011538 | O2-26 | 136.575 |  | WTG Unscheduled Maintenance | 10926 | 136.575
4635 | 2025-05-06 | 2025 | 2025 | 2025-05-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.32153 | 0.32153 | 0.33194 | 0 | 0.25 | 0.25 | Checked related error data log then reset & started WTG. | Close | 0.0096154 | O2-26 | 113.8125 |  | WTG Breakdown Maintenance | 10926 | 113.8125
4636 | 2025-05-06 | 2025 | 2025 | 2025-05-01 | 2 | O2_03 | TQGXIIPL | GEDA | 3.846% | 64 | Max. wind speed | Environment | 0.64514 | 0.64514 | 0.6625 | 0 | 0.41667 | 0.41667 | Auto reset | Close | 0.016026 | O2-09 | 264.6701 |  | WTG Unscheduled Maintenance | 15245 | 264.6701
4637 | 2025-05-06 | 2025 | 2025 | 2025-05-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 5550 | Low hydraulic oil level | Break down | 0.60625 | 0.60625 | 0.64653 | 0 | 0.96667 | 0.96667 | wtg wip | Close | 0.037179 | O2-07 | 756.9403 |  | WTG Breakdown Maintenance | 18793 | 756.9403
4638 | 2025-05-06 | 2025 | 2025 | 2025-05-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 5550 | Low hydraulic oil level | Break down | 0.74375 | 0.74375 | 0.89375 | 0 | 3.6 | 3.6 | Attend and wtg oil top then reset and started wtg | Close | 0.13846 | O2-07 | 2818.95 |  | WTG Breakdown Maintenance | 18793 | 2818.95
4639 | 2025-05-06 | 2025 | 2025 | 2025-05-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 567 | Pitch too slow BP52 | Break down | 0.019444 | 0.019444 | 0.026389 | 0 | 0.16667 | 0.16667 | Auto reset | Close | 0.0064103 | O2-02 | 104.7986 |  | WTG Unscheduled Maintenance | 15091 | 104.7986
4640 | 2025-05-06 | 2025 | 2025 | 2025-05-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 2520 | Gen.speed analog<>gear.speed | Break down | 0.65972 | 0.65972 | 0.66111 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2-02 | 20.9597 |  | WTG Unscheduled Maintenance | 15091 | 20.9597
4641 | 2025-05-06 | 2025 | 2025 | 2025-05-01 | 2 | O2_07 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.91736 | 0.91736 | 0.91806 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | O2-04 | 10.4736 |  | WTG Unscheduled Maintenance | 15082 | 10.4736
4642 | 2025-05-06 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.026389 | 0.026389 | 0.048611 | 0 | 0.53333 | 0.53333 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.020513 | O2-26 | 242.8 |  | WTG Breakdown Maintenance | 10926 | 242.8
4643 | 2025-05-06 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6007 | Overload yaw motors group 1 | Auto reset | 0.052083 | 0.065278 | 0.086111 | 0.31667 | 0.5 | 0.81667 | Attend and wtg check Releted circuit so found Yaw MPCB TRIP Connection loose after all connection tight then reset and start wtg. | Close | 0.03141 | O2-26 | 371.7875 |  | WTG Breakdown Maintenance | 10926 | 371.7875
4644 | 2025-05-06 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.55278 | 0.55278 | 0.55694 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-26 | 45.525 |  | WTG Unscheduled Maintenance | 10926 | 45.525
4645 | 2025-05-06 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.64792 | 0.64792 | 0.6625 | 0 | 0.35 | 0.35 | Auto reset | Close | 0.013462 | O2-26 | 159.3375 |  | WTG Unscheduled Maintenance | 10926 | 159.3375
4646 | 2025-05-06 | 2025 | 2025 | 2025-05-01 | 2 | O2_09 | TQGXIIPL | GEDA | 3.846% | 64 | Max. wind speed | Environment | 0.63125 | 0.63125 | 0.63264 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2-03 | 21.2528 |  | WTG Unscheduled Maintenance | 15302 | 21.2528
4647 | 2025-05-06 | 2025 | 2025 | 2025-05-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 64 | Max. wind speed | Environment | 0.63403 | 0.63403 | 0.63819 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-15 | 74.8375 |  | WTG Unscheduled Maintenance | 17961 | 74.8375
4648 | 2025-05-06 | 2025 | 2025 | 2025-05-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.65 | 0.65 | 0.65417 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-15 | 74.8375 |  | WTG Unscheduled Maintenance | 17961 | 74.8375
4649 | 2025-05-06 | 2025 | 2025 | 2025-05-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 64 | Max. wind speed | Environment | 0.625 | 0.625 | 0.63472 | 0 | 0.23333 | 0.23333 | Auto reset | Close | 0.0089744 | O2-12 | 152.3569 |  | WTG Unscheduled Maintenance | 15671 | 152.3569
4650 | 2025-05-06 | 2025 | 2025 | 2025-05-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 64 | Max. wind speed | Environment | 0.62917 | 0.62917 | 0.64306 | 0 | 0.33333 | 0.33333 | Auto reset | Close | 0.012821 | O2-14 | 233.1667 |  | WTG Unscheduled Maintenance | 16788 | 233.1667
4651 | 2025-05-06 | 2025 | 2025 | 2025-05-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.47708 | 0.47708 | 0.48125 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-11 | 68.5792 |  | WTG Unscheduled Maintenance | 16459 | 68.5792
4652 | 2025-05-06 | 2025 | 2025 | 2025-05-01 | 2 | O2_15 | TQGXIIPL | GEDA | 3.846% | 6056 | High yaw load | Auto reset | 0.63889 | 0.63889 | 0.64097 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2-10 | 38.55 |  | WTG Unscheduled Maintenance | 18504 | 38.55
4652 | 2025-05-06 | 2025 | 2025 | 2025-05-01 | 2 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Major BD | 0.045833 | 0.045833 | 0.64653 | 0 | 14.4167 | 14.4167 | Attend And check releated circuit so found ACB Tripped so we check all cable check stator and rotor connection check and all fuse check,CT Check troubleshooting WIP | Close | 0.55449 | O2-21 | 14207.0243 |  | WTG Breakdown Maintenance | 23651 | 14207.0243
4653 | 2025-05-06 | 2025 | 2025 | 2025-05-01 | 2 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Road issue | 0.86736 | 0.86736 | 1899-12-31 | 0 | 3.1833 | 3.1833 | WTG Road approached issue | OPEN | 0.12244 | O2-21 | 3137.0424 |  | WTG Unscheduled Maintenance | 23651 | 3137.0424
4654 | 2025-05-06 | 2025 | 2025 | 2025-05-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Auto reset | 0.63958 | 0.63958 | 0.64306 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0032051 | O2-22 | 73.8924 |  | WTG Unscheduled Maintenance | 21281 | 73.8924
4655 | 2025-05-06 | 2025 | 2025 | 2025-05-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 53 | Wind dir.dev. level 1 | Auto reset | 0.0083333 | 0.0083333 | 0.010417 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2-11 | 34.2896 |  | WTG Unscheduled Maintenance | 16459 | 34.2896
4656 | 2025-05-06 | 2025 | 2025 | 2025-05-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 64 | Max. wind speed | Auto reset | 0.62986 | 0.62986 | 0.63125 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2-11 | 22.8597 |  | WTG Unscheduled Maintenance | 16459 | 22.8597
4657 | 2025-05-06 | 2025 | 2025 | 2025-05-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.64722 | 0.64722 | 0.65139 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-11 | 68.5792 |  | WTG Unscheduled Maintenance | 16459 | 68.5792
4658 | 2025-05-06 | 2025 | 2025 | 2025-05-01 | 2 | O2_24 | TQGXIIPL | GEDA | 3.846% | 5506 | Rot.br. press. high | Major BD | 0.04375 | 0.04375 | 0.64653 | 0 | 14.4667 | 14.4667 | Rotor Break Pressure High so attend Turbine and check Related circuit Check HPU all valve and check all Valve setting also check Hydrolic Unit oil level is ok Found than taken trail but same error occurred so Disccusion with Enginnering team and found Accumulator Pressure low so Further reffilling. | Close | 0.55641 | O2-20 | 14792.1667 |  | WTG Breakdown Maintenance | 24540 | 14792.1667
4659 | 2025-05-06 | 2025 | 2025 | 2025-05-01 | 2 | O2_24 | TQGXIIPL | GEDA | 3.846% | 5506 | Rot.br. press. high | Major BD | 0.74375 | 0.74375 | 1899-12-31 | 0 | 6.15 | 6.15 | Rotor Break Pressure High so attend Turbine and check Related circuit Check HPU all valve and check all Valve setting also check Hydrolic Unit oil level is ok Found than taken trail but same error occurred so Disccusion with Enginnering team and found Accumulator Pressure low so Further reffilling. | OPEN | 0.23654 | O2-20 | 6288.375 |  | WTG Breakdown Maintenance | 24540 | 6288.375
4660 | 2025-05-06 | 2025 | 2025 | 2025-05-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 58 | Wind dir.dev. level 2 | Auto reset | 0.62153 | 0.62153 | 0.625 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0032051 | O2-01 | 35.2951 |  | WTG Unscheduled Maintenance | 10165 | 35.2951
4661 | 2025-05-06 | 2025 | 2025 | 2025-05-01 | 2 | O2_26 | TQGXIIPL | GEDA | 3.846% | 6012 | Overload yaw motors group 2 | Break down | 0.027778 | 0.099306 | 0.11667 | 1.7167 | 0.41667 | 2.1333 | Attend and wtg check Releted circuit so found Yaw MPCB TRIP After on MPCB after all connection tight then reset and start wtg. | Close | 0.082051 | O2-01 | 903.5556 |  | WTG Breakdown Maintenance | 10165 | 903.5556
4662 | 2025-05-06 | 2025 | 2025 | 2025-05-01 | 2 | O2_26 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Break down | 0.30208 | 0.30208 | 0.35903 | 0 | 1.3667 | 1.3667 | Checked related error data log then reset & started WTG. | Close | 0.052564 | O2-01 | 578.8403 |  | WTG Unscheduled Maintenance | 10165 | 578.8403
4663 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 2390 | Brake due to sudden sys.failure | Break down | 0.089583 | 0.089583 | 0.1375 | 0 | 1.15 | 1.15 | Let start wtg Due to wtg Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) | Close | 0.044231 | O2-26 | 726.7042 |  | WTG Unscheduled Maintenance | 15166 | 726.7042
4664 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.51389 | 0.51389 | 0.59583 | 0 | 1.9667 | 1.9667 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.075641 | O2-26 | 1242.7694 |  | WTG Unscheduled Maintenance | 15166 | 1242.7694
4665 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | 2 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down | 0.090278 | 0.090278 | 0.13819 | 0 | 1.15 | 1.15 | Late start wtg due to disconnect to scada O2-25 VCB Tripped after charge VCB And connect wtg reset and start wtg | Close | 0.044231 | O2-05 | 809.1208 |  | WTG Unscheduled Maintenance | 16886 | 809.1208
4666 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | 2 | O2_03 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Major BD | 0.20139 | 0.20139 | 0.62153 | 0 | 10.0833 | 10.0833 | We have check in sam Found pitch error also chech in snap and check QA001 CONTACTOR all connection and retight it than check ALL NO/NC Auxiliary switch and found NC &NO switch not working properly so replace all switch and check then have trail taken by turbine after no any abnormal absorb so started wtg. | Close | 0.38782 | O2-09 | 6355.0208 |  | WTG Breakdown Maintenance | 15126 | 6355.0208
4667 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down | 0.10347 | 0.10347 | 0.15278 | 0 | 1.1833 | 1.1833 | Late start wtg due to disconnect to scada O2-25 VCB Tripped after charge VCB And connect wtg reset and start wtg | Close | 0.045513 | O2-02 | 836.4688 |  | WTG Unscheduled Maintenance | 16965 | 836.4688
4668 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down | 0.090278 | 0.090278 | 0.14028 | 0 | 1.2 | 1.2 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) after Checked related error data log then reset & started WTG. | Close | 0.046154 | O2-26 | 758.3 |  | WTG Unscheduled Maintenance | 15166 | 758.3
4669 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | 2 | O2_09 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down | 0.090278 | 0.090278 | 0.14167 | 0 | 1.2333 | 1.2333 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) after Checked related error data log then reset & started WTG. | Close | 0.047436 | O2-03 | 95.1722 |  | WTG Unscheduled Maintenance | 1852 | 95.1722
4670 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down | 0.090278 | 0.090278 | 0.14444 | 0 | 1.3 | 1.3 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) after Checked related error data log then reset & started WTG. | Close | 0.05 | O2-15 | 793.0542 |  | WTG Unscheduled Maintenance | 14641 | 793.0542
4671 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down | 0.090278 | 0.090278 | 0.092361 | 0 | 0.05 | 0.05 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) after Checked related error data log then reset & started WTG. | Close | 0.0019231 | O2-12 | 23.8438 |  | WTG Unscheduled Maintenance | 11445 | 23.8438
4672 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down | 0.70694 | 0.70694 | 0.72778 | 0 | 0.5 | 0.5 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) after Checked related error data log then reset & started WTG. | Close | 0.019231 | O2-12 | 238.4375 |  | WTG Unscheduled Maintenance | 11445 | 238.4375
4673 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down | 0.090278 | 0.090278 | 0.097222 | 0 | 0.16667 | 0.16667 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) after Checked related error data log then reset & started WTG. | Close | 0.0064103 | O2-14 | 103.1667 |  | WTG Unscheduled Maintenance | 14856 | 103.1667
4674 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 5516 | Rot.br. press. low | Break down | 0.15486 | 0.15486 | 0.36111 | 0 | 4.95 | 4.95 | WTG Road approached issue | Close | 0.19038 | O2-14 | 3064.05 |  | WTG Unscheduled Maintenance | 14856 | 3064.05
4675 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 5516 | Rot.br. press. low | Break down | 0.36111 | 0.36111 | 0.37639 | 0 | 0.36667 | 0.36667 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) Attend wtg apply hard reboot after check hydrolic presure so ok after trail so ok then reset and started wtg. | Close | 0.014103 | O2-14 | 226.9667 |  | WTG Unscheduled Maintenance | 14856 | 226.9667
4676 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.097222 | 0.097222 | 0.11528 | 0 | 0.43333 | 0.43333 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) after Checked related error data log then reset & started WTG. | Close | 0.016667 | O2-14 | 268.2333 |  | WTG Unscheduled Maintenance | 14856 | 268.2333
4677 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.70694 | 0.70694 | 0.72847 | 0 | 0.51667 | 0.51667 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) after Checked related error data log then reset & started WTG. | Close | 0.019872 | O2-14 | 319.8167 |  | WTG Unscheduled Maintenance | 14856 | 319.8167
4678 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 5516 | Rot.br. press. low | Break down | 0.72847 | 0.72847 | 0.73056 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2-14 | 30.95 |  | WTG Unscheduled Maintenance | 14856 | 30.95
4679 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.099306 | 0.099306 | 0.14583 | 0 | 1.1167 | 1.1167 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) after Checked related error data log then reset & started WTG. | Close | 0.042949 | O2-11 | 676.7465 |  | WTG Unscheduled Maintenance | 14545 | 676.7465
4680 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.70694 | 0.70694 | 0.72847 | 0 | 0.51667 | 0.51667 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) after Checked related error data log then reset & started WTG. | Close | 0.019872 | O2-11 | 313.1215 |  | WTG Unscheduled Maintenance | 14545 | 313.1215
4682 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | 2 | O2_14 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.10556 | 0.10556 | 0.14653 | 0 | 0.98333 | 0.98333 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) after Checked related error data log then reset & started WTG. | Close | 0.037821 | O2-12 | 468.9271 |  | WTG Unscheduled Maintenance | 11445 | 468.9271
4683 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | 2 | O2_14 | TQGXIIPL | GEDA | 3.846% | 642 | Sim.angle E enc. <> act.angle 2 | Break down | 0.70694 | 0.70694 | 0.72917 | 0 | 0.53333 | 0.53333 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) wip | Close | 0.020513 | O2-12 | 254.3333 |  | WTG Unscheduled Maintenance | 11445 | 254.3333
4684 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | 2 | O2_14 | TQGXIIPL | GEDA | 3.846% | 642 | Sim.angle E enc. <> act.angle 2 | Break down | 0.72917 | 0.72917 | 0.74792 | 0 | 0.45 | 0.45 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) after Checked related error data log then reset & started WTG. | Close | 0.017308 | O2-12 | 214.5938 |  | WTG Unscheduled Maintenance | 11445 | 214.5938
4685 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | 2 | O2_15 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.090278 | 0.090278 | 0.14514 | 0 | 1.3167 | 1.3167 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) after Checked related error data log then reset & started WTG. | Close | 0.050641 | O2-10 | 805.1965 |  | WTG Unscheduled Maintenance | 14677 | 805.1965
4686 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | 2 | O2_15 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.70694 | 0.70694 | 0.72986 | 0 | 0.55 | 0.55 | Due to WTG Disconnect to SCADA (Heavy rain and lighting at site and multiple activity at site) wip | Close | 0.021154 | O2-10 | 336.3479 |  | WTG Unscheduled Maintenance | 14677 | 336.3479
4687 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | 2 | O2_15 | TQGXIIPL | GEDA | 3.846% | 741 | Battery drive trigger by HC | Break down | 0.73264 | 0.73264 | 0.80069 | 0 | 1.6333 | 1.6333 | Checked related error data log then apply shoft reboot then reset & started WTG. | Close | 0.062821 | O2-10 | 998.8514 |  | WTG Unscheduled Maintenance | 14677 | 998.8514
4688 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | 2 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Major BD | 0 | 0 | 0.73958 | 0 | 17.75 | 17.75 | attend turbine check converter panel in ACB feedback ckt, ACB physical condition, check main Contactor and it's working condition, check further power cable all joints, junction box all joints and taken all power cable IR value, check stator and rotor box and it's connection also taken generator IR value but nothing found abnormal.So taken trail but again error occured.So discuss with our L2 team and Supplier check in converter panel MSC and GSC stack and perform all test and all test pass successful. So after as per supply suggested we have interchange ACB control card with other turbine and Error shift in other turbine. So now O2.16 Started and O2.20 Stop now material arranging work in progress. | Close | 0.68269 | O2-21 | 16067.4479 |  | WTG Breakdown Maintenance | 21725 | 16067.4479
4689 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.80972 | 0.80972 | 0.94097 | 0 | 3.15 | 3.15 | Late wtg start Due to WTG Disconnect to SCADA after Checked related error data log then reset & started WTG. | Close | 0.12115 | O2-22 | 2557.4062 |  | WTG Unscheduled Maintenance | 19485 | 2557.4062
4690 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | 2 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD | 0.71875 | 0.71875 | 0.97881 | 0 | 6.2414 | 6.2414 | wtg manual stop for component testing work wip | open | 0.24005 | O2-24 | 2708.7628 |  | WTG Breakdown Maintenance | 10416 | 2708.7628
4691 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down | 0.090278 | 0.090278 | 0.14236 | 0 | 1.25 | 1.25 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) after Checked related error data log then reset & started WTG. | Close | 0.048077 | O2-11 | 757.5521 |  | WTG Unscheduled Maintenance | 14545 | 757.5521
4692 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 4093 | Rel. air hum. tower base inside too high (in operation) | Break down | 0.26944 | 0.26944 | 0.37569 | 0 | 2.55 | 2.55 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) | Close | 0.098077 | O2-11 | 1545.4062 |  | WTG Unscheduled Maintenance | 14545 | 1545.4062
4693 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.70694 | 0.70694 | 0.73264 | 0 | 0.61667 | 0.61667 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) after Checked related error data log then reset & started WTG. | Close | 0.023718 | O2-11 | 373.7257 |  | WTG Unscheduled Maintenance | 14545 | 373.7257
4694 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | 2 | O2_24 | TQGXIIPL | GEDA | 3.846% | 5506 | Rot.br. press. high | Major BD | 0 | 0 | 0.46597 | 0 | 11.1833 | 11.1833 | Disccusion with Engineering team and found Accumulator Pressure low so arrange material for anothar side and replace Accumulato then start wtg. | Close | 0.43013 | O2-20 | 9038.4632 |  | WTG Unscheduled Maintenance | 19397 | 9038.4632
4695 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down | 0.70694 | 0.70694 | 0.73472 | 0 | 0.66667 | 0.66667 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) after Checked related error data log then reset & started WTG. | Close | 0.025641 | O2-01 | 314.4167 |  | WTG Unscheduled Maintenance | 11319 | 314.4167
4696 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down | 0.13194 | 0.13194 | 0.14931 | 0 | 0.41667 | 0.41667 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) after Checked related error data log then reset & started WTG. | Close | 0.016026 | O2-01 | 196.5104 |  | WTG Unscheduled Maintenance | 11319 | 196.5104
4697 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.51736 | 0.51736 | 0.53542 | 0 | 0.43333 | 0.43333 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.016667 | O2-01 | 204.3708 |  | WTG Unscheduled Maintenance | 11319 | 204.3708
4698 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | 2 | O2_26 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.70694 | 0.70694 | 0.73542 | 0 | 0.68333 | 0.68333 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) after Checked related error data log then reset & started WTG. | Close | 0.026282 | O2-01 | 322.2771 |  | WTG Unscheduled Maintenance | 11319 | 322.2771
4699 | 2025-05-08 | 2025 | 2025 | 2025-05-01 | 2 | O2_03 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Auto reset | 0.79167 | 0.79167 | 0.79375 | 0 | 0.05 | 0.05 | Auto reset. | Close | 0.0019231 | O2-09 | 13.4667 |  | WTG Unscheduled Maintenance | 6464 | 13.4667
4700 | 2025-05-08 | 2025 | 2025 | 2025-05-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 578 | Pitch set point slow hold time BP75 | Auto reset | 0.84097 | 0.84097 | 0.84236 | 0 | 0.033333 | 0.033333 | Auto reset. | Close | 0.0012821 | O2-11 | 9.8528 |  | WTG Unscheduled Maintenance | 7094 | 9.8528
4701 | 2025-05-08 | 2025 | 2025 | 2025-05-01 | 2 | O2_14 | TQGXIIPL | GEDA | 3.846% | 72 | Outdoor temperature high | Break down | 0.84236 | 0.84236 | 0.85694 | 0 | 0.35 | 0.35 | Check temperature value, after temperature normlize started WTG. | Close | 0.013462 | O2-12 | 97.9417 |  | WTG Unscheduled Maintenance | 6716 | 97.9417
4702 | 2025-05-08 | 2025 | 2025 | 2025-05-01 | 2 | O2_16 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.65625 | 0.65625 | 0.67639 | 0 | 0.48333 | 0.48333 | WTG stopped for material cannibalize work. | Close | 0.01859 | O2-21 | 156.3583 |  | WTG Breakdown Maintenance | 7764 | 156.3583
4703 | 2025-05-08 | 2025 | 2025 | 2025-05-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Auto reset | 0.50278 | 0.50278 | 0.50486 | 0 | 0.05 | 0.05 | Auto reset. | Close | 0.0019231 | O2-22 | 16.1104 |  | WTG Unscheduled Maintenance | 7733 | 16.1104
4704 | 2025-05-08 | 2025 | 2025 | 2025-05-01 | 2 | O2_20 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0 | 0 | 0.15556 | 0 | 3.7333 | 3.7333 | Arrange material than replaced trip unit card and trial takken and started WTG. | Close | 0.14359 | O2-24 | 1457.5556 |  | WTG Breakdown Maintenance | 9370 | 1457.5556
4705 | 2025-05-08 | 2025 | 2025 | 2025-05-01 | 2 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.63889 | 0.63889 | 0.69861 | 0 | 1.4333 | 1.4333 | WTG stopped for material cannibalize work. | Close | 0.055128 | O2-24 | 559.5972 |  | WTG Breakdown Maintenance | 9370 | 559.5972
4706 | 2025-05-08 | 2025 | 2025 | 2025-05-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Break down | 0.79167 | 0.90764 | 0.96806 | 2.7833 | 1.45 | 4.2333 | Attend wtg check releted circuit so found Blade no 1 1.7 ohm Flat resistor faulty after replace then reset and started wtg. | Close | 0.16282 | O2-11 | 1251.3028 |  | WTG Breakdown Maintenance | 7094 | 1251.3028
4707 | 2025-05-08 | 2025 | 2025 | 2025-05-01 | 2 | O2_26 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Auto reset | 0.79028 | 0.79028 | 0.79306 | 0 | 0.066667 | 0.066667 | Auto reset. | Close | 0.0025641 | O2-01 | 21.0417 |  | WTG Unscheduled Maintenance | 7575 | 21.0417
4708 | 2025-05-09 | 2025 | 2025 | 2025-05-01 | 2 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.59792 | 0.59792 | 0.59931 | 0 | 0.033333 | 0.033333 | WTG Manual stop for Software Updated Work. | Close | 0.0012821 | O2-05 | 16.1986 |  | WTG Breakdown Maintenance | 11663 | 16.1986
4709 | 2025-05-09 | 2025 | 2025 | 2025-05-01 | 2 | O2_03 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.60069 | 0.60069 | 0.60208 | 0 | 0.033333 | 0.033333 | WTG Manual stop for Software Updated Work. | Close | 0.0012821 | O2-09 | 12.1944 |  | WTG Breakdown Maintenance | 8780 | 12.1944
4710 | 2025-05-09 | 2025 | 2025 | 2025-05-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.60972 | 0.60972 | 0.61181 | 0 | 0.05 | 0.05 | WTG Manual stop for Software Updated Work. | Close | 0.0019231 | O2-07 | 9.9521 |  | WTG Breakdown Maintenance | 4777 | 9.9521
4711 | 2025-05-09 | 2025 | 2025 | 2025-05-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.62014 | 0.62014 | 0.62153 | 0 | 0.033333 | 0.033333 | WTG Manual stop for Software Updated Work. | Close | 0.0012821 | O2-02 | 17.3736 |  | WTG Breakdown Maintenance | 12509 | 17.3736
4712 | 2025-05-09 | 2025 | 2025 | 2025-05-01 | 2 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.60417 | 0.60417 | 0.60556 | 0 | 0.033333 | 0.033333 | WTG Manual stop for Software Updated Work. | Close | 0.0012821 | O2-21 | 7.4819 |  | WTG Breakdown Maintenance | 5387 | 7.4819
4713 | 2025-05-09 | 2025 | 2025 | 2025-05-01 | 2 | O2_07 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.63333 | 0.63333 | 0.64236 | 0 | 0.21667 | 0.21667 | WTG Manual stop for Software Updated Work. | Close | 0.0083333 | O2-04 | 47.9917 |  | WTG Breakdown Maintenance | 5316 | 47.9917
4714 | 2025-05-09 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.64653 | 0.64653 | 0.64792 | 0 | 0.033333 | 0.033333 | WTG Manual stop for Software Updated Work. | Close | 0.0012821 | O2-26 | 13.5319 |  | WTG Breakdown Maintenance | 9743 | 13.5319
4715 | 2025-05-09 | 2025 | 2025 | 2025-05-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.58542 | 0.58542 | 0.58681 | 0 | 0.033333 | 0.033333 | WTG Manual stop for Software Updated Work. | Close | 0.0012821 | O2-26 | 13.5319 |  | WTG Breakdown Maintenance | 9743 | 13.5319
4716 | 2025-05-09 | 2025 | 2025 | 2025-05-01 | 2 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.64931 | 0.64931 | 0.65069 | 0 | 0.033333 | 0.033333 | WTG Manual stop for Software Updated Work. | Close | 0.0012821 | O2-03 | 12.7875 |  | WTG Breakdown Maintenance | 9207 | 12.7875
4717 | 2025-05-09 | 2025 | 2025 | 2025-05-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.65139 | 0.65139 | 0.66042 | 0 | 0.21667 | 0.21667 | WTG Manual stop for Software Updated Work. | Close | 0.0083333 | O2-15 | 90.6389 |  | WTG Breakdown Maintenance | 10040 | 90.6389
4718 | 2025-05-09 | 2025 | 2025 | 2025-05-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 741 | Battery drive trigger by HC | Auto reset | 0.46597 | 0.46597 | 0.46944 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0032051 | O2-12 | 35.8403 |  | WTG Unscheduled Maintenance | 10322 | 35.8403
4719 | 2025-05-09 | 2025 | 2025 | 2025-05-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.65972 | 0.65972 | 0.66181 | 0 | 0.05 | 0.05 | WTG Manual stop for Software Updated Work. | Close | 0.0019231 | O2-12 | 21.5042 |  | WTG Breakdown Maintenance | 10322 | 21.5042
4720 | 2025-05-09 | 2025 | 2025 | 2025-05-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.6625 | 0.6625 | 0.66458 | 0 | 0.05 | 0.05 | WTG Manual stop for Software Updated Work. | Close | 0.0019231 | O2-14 | 21.4354 |  | WTG Breakdown Maintenance | 10289 | 21.4354
4721 | 2025-05-09 | 2025 | 2025 | 2025-05-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.66528 | 0.66528 | 0.66736 | 0 | 0.05 | 0.05 | WTG Manual stop for Software Updated Work. | Close | 0.0019231 | O2-11 | 19.525 |  | WTG Breakdown Maintenance | 9372 | 19.525
4722 | 2025-05-09 | 2025 | 2025 | 2025-05-01 | 2 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.66806 | 0.66806 | 0.67083 | 0 | 0.066667 | 0.066667 | WTG Manual stop for Software Updated Work. | Close | 0.0025641 | O2-12 | 28.6722 |  | WTG Breakdown Maintenance | 10322 | 28.6722
4723 | 2025-05-09 | 2025 | 2025 | 2025-05-01 | 2 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.67153 | 0.67153 | 0.67431 | 0 | 0.066667 | 0.066667 | WTG Manual stop for Software Updated Work. | Close | 0.0025641 | O2-10 | 26.0389 |  | WTG Breakdown Maintenance | 9374 | 26.0389
4724 | 2025-05-09 | 2025 | 2025 | 2025-05-01 | 2 | O2_16 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.675 | 0.675 | 0.67708 | 0 | 0.05 | 0.05 | WTG Manual stop for Software Updated Work. | Close | 0.0019231 | O2-21 | 11.2229 |  | WTG Breakdown Maintenance | 5387 | 11.2229
4725 | 2025-05-09 | 2025 | 2025 | 2025-05-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.67708 | 0.67708 | 0.68056 | 0 | 0.083333 | 0.083333 | WTG Manual stop for Software Updated Work. | Close | 0.0032051 | O2-07 | 16.5868 |  | WTG Breakdown Maintenance | 4777 | 16.5868
4726 | 2025-05-09 | 2025 | 2025 | 2025-05-01 | 2 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.67778 | 0.67778 | 0.68681 | 0 | 0.21667 | 0.21667 | WTG Manual stop for Software Updated Work. | Close | 0.0083333 | O2-24 | 63.6639 |  | WTG Breakdown Maintenance | 7052 | 63.6639
4727 | 2025-05-09 | 2025 | 2025 | 2025-05-01 | 2 | O2_21 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.69722 | 0.69722 | 0.69861 | 0 | 0.033333 | 0.033333 | WTG Manual stop for Software Updated Work. | Close | 0.0012821 | O2-06 | 9.5708 |  | WTG Breakdown Maintenance | 6891 | 9.5708
4728 | 2025-05-09 | 2025 | 2025 | 2025-05-01 | 2 | O2_22 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.70347 | 0.70347 | 0.70556 | 0 | 0.05 | 0.05 | WTG Manual stop for Software Updated Work. | Close | 0.0019231 | O2-06 | 14.3562 |  | WTG Breakdown Maintenance | 6891 | 14.3562
4729 | 2025-05-09 | 2025 | 2025 | 2025-05-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 6056 | High yaw load | Auto reset | 0.55 | 0.55 | 0.55208 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2-11 | 19.525 |  | WTG Breakdown Maintenance | 9372 | 19.525
4730 | 2025-05-09 | 2025 | 2025 | 2025-05-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.6875 | 0.6875 | 0.68958 | 0 | 0.05 | 0.05 | WTG Manual stop for Software Updated Work. | Close | 0.0019231 | O2-11 | 19.525 |  | WTG Unscheduled Maintenance | 9372 | 19.525
4731 | 2025-05-09 | 2025 | 2025 | 2025-05-01 | 2 | O2_24 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.68819 | 0.68819 | 0.69028 | 0 | 0.05 | 0.05 | WTG Manual stop for Software Updated Work. | Close | 0.0019231 | O2-20 | 13.7437 |  | WTG Breakdown Maintenance | 6597 | 13.7437
4732 | 2025-05-09 | 2025 | 2025 | 2025-05-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.69028 | 0.69028 | 0.69236 | 0 | 0.05 | 0.05 | WTG Manual stop for Software Updated Work. | Close | 0.0019231 | O2-01 | 19.0167 |  | WTG Breakdown Maintenance | 9128 | 19.0167
4733 | 2025-05-09 | 2025 | 2025 | 2025-05-01 | 2 | O2_26 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.69028 | 0.69028 | 0.69236 | 0 | 0.05 | 0.05 | WTG Manual stop for Software Updated Work. | Close | 0.0019231 | O2-01 | 19.0167 |  | WTG Breakdown Maintenance | 9128 | 19.0167
4734 | 2025-05-10 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6210 | Max. cable twistangle | Break down | 0.18819 | 0.18819 | 0.24583 | 0 | 1.3833 | 1.3833 | Checked related error data log then apply shoft reboot and removed cable twist then reset & started WTG. | Close | 0.053205 | O2-26 | 816.6854 |  | WTG Breakdown Maintenance | 14169 | 816.6854
4735 | 2025-05-10 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.46389 | 0.46389 | 0.61458 | 0 | 3.6167 | 3.6167 | Attend and wtg Nacell Position Sensor fault warning and repeated error (wind Dir.diff.Level 1) so check and found wind sensor alignment not proper so wind sensor aligment properly done and also check axis 1 flat resistor faulty so replace it and check yaw releted repeated error, check and found yaw sensor switch setting is not proper so correct it then reset and started wtg. | Close | 0.1391 | O2-26 | 2135.1896 |  | WTG Breakdown Maintenance | 14169 | 2135.1896
4736 | 2025-05-10 | 2025 | 2025 | 2025-05-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.50278 | 0.50278 | 0.54167 | 0 | 0.93333 | 0.93333 | Attend and check ckt then blade axis 2 chopper resistor found faulty so replacement work WIP | Close | 0.035897 | O2-22 | 585.9778 |  | WTG Breakdown Maintenance | 15068 | 585.9778
4737 | 2025-05-10 | 2025 | 2025 | 2025-05-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.69375 | 0.69375 | 0.71875 | 0 | 0.6 | 0.6 | After grid time replace chopper resistor work done after trail then reset and started wtg | Close | 0.023077 | O2-22 | 376.7 |  | WTG Breakdown Maintenance | 15068 | 376.7
4738 | 2025-05-10 | 2025 | 2025 | 2025-05-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down | 0.12847 | 0.15417 | 0.21528 | 0.61667 | 1.4667 | 2.0833 | Attend and wtg check hydraulic oil so ok after replace 9.1 valve after check hydraulic pressure values so ok then reset and started wtg. | Close | 0.080128 | O2-11 | 1145.3125 |  | WTG Breakdown Maintenance | 13194 | 1145.3125
4739 | 2025-05-11 | 2025 | 2025 | 2025-05-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.69653 | 0.69653 | 0.71944 | 0 | 0.55 | 0.55 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.021154 | O2-26 | 229.7854 |  | WTG Unscheduled Maintenance | 10027 | 229.7854
4740 | 2025-05-11 | 2025 | 2025 | 2025-05-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Others | 0.72639 | 0.72639 | 0.7375 | 0 | 0.26667 | 0.26667 | Late start wtg dut to BOP Suggestions after reset and started wtg | Close | 0.010256 | O2-07 | 136.8222 |  | WTG Breakdown Maintenance | 12314 | 136.8222
4741 | 2025-05-11 | 2025 | 2025 | 2025-05-01 | 2 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Others | 0.72639 | 0.72639 | 0.73472 | 0 | 0.2 | 0.2 | Late start wtg dut to BOP Suggestions after reset and started wtg | Close | 0.0076923 | O2-21 | 78.3667 |  | WTG Breakdown Maintenance | 9404 | 78.3667
4742 | 2025-05-11 | 2025 | 2025 | 2025-05-01 | 2 | O2_07 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Others | 0.72639 | 0.72639 | 0.73681 | 0 | 0.25 | 0.25 | Late start wtg dut to BOP Suggestions after reset and started wtg | Close | 0.0096154 | O2-04 | 155.6667 |  | WTG Breakdown Maintenance | 14944 | 155.6667
4743 | 2025-05-11 | 2025 | 2025 | 2025-05-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 5506 | Rot.br. press. high | Break down | 0.76597 | 0.76597 | 1899-12-31 | 0 | 5.6167 | 5.6167 | Attend wtg check hydralic unit and check all valve so ok after check accumulator both so found accumulator Pressure low so wtg WIP | OPEN | 0.21603 | O2-14 | 2437.3993 |  | WTG Breakdown Maintenance | 10415 | 2437.3993
4744 | 2025-05-11 | 2025 | 2025 | 2025-05-01 | 2 | O2_16 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.72639 | 0.72639 | 0.76042 | 0 | 0.81667 | 0.81667 | Attend wtg check Pitch data AND Check all blade angle so ok After trail so ok then reset and started wtg. | Close | 0.03141 | O2-21 | 319.9972 |  | WTG Breakdown Maintenance | 9404 | 319.9972
4745 | 2025-05-11 | 2025 | 2025 | 2025-05-01 | 2 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Others | 0.72639 | 0.72639 | 0.75069 | 0 | 0.58333 | 0.58333 | Late start wtg dut to BOP Suggestions after reset and started wtg | Close | 0.022436 | O2-06 | 292.8819 |  | WTG Breakdown Maintenance | 12050 | 292.8819
4746 | 2025-05-11 | 2025 | 2025 | 2025-05-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 660 | Limit switches error 91° | Break down | 0.80625 | 0.80625 | 0.91528 | 0 | 2.6167 | 2.6167 | Check Data in SCADA so found blade 1 91 limit switch connection loose so tight it then reset and started wtg. | Close | 0.10064 | O2-07 | 1342.5681 |  | WTG Breakdown Maintenance | 12314 | 1342.5681
4747 | 2025-05-11 | 2025 | 2025 | 2025-05-01 | 2 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Others | 0.72639 | 0.72639 | 0.73611 | 0 | 0.23333 | 0.23333 | Late start wtg dut to BOP Suggestions after reset and started wtg | Close | 0.0089744 | O2-24 | 97.6014 |  | WTG Breakdown Maintenance | 10039 | 97.6014
4748 | 2025-05-11 | 2025 | 2025 | 2025-05-01 | 2 | O2_22 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Others | 0.72639 | 0.72639 | 0.75 | 0 | 0.56667 | 0.56667 | Late start wtg dut to BOP Suggestions after reset and started wtg | Close | 0.021795 | O2-06 | 284.5139 |  | WTG Breakdown Maintenance | 12050 | 284.5139
4749 | 2025-05-11 | 2025 | 2025 | 2025-05-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 159 | SLC SF emergency stop | Break down | 0.58819 | 0.58819 | 0.6625 | 0 | 1.7833 | 1.7833 | Check error related CKT Found Bottom Emergency button connection found loose in BOB FS2 Panel so correct it then reset and started wtg | Close | 0.06859 | O2-11 | 754.9444 |  | WTG Breakdown Maintenance | 10160 | 754.9444
4750 | 2025-05-11 | 2025 | 2025 | 2025-05-01 | 2 | O2_26 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.69722 | 0.69722 | 0.71875 | 0 | 0.51667 | 0.51667 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.019872 | O2-01 | 253.6833 |  | WTG Breakdown Maintenance | 11784 | 253.6833
4751 | 2025-05-12 | 2025 | 2025 | 2025-05-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.65347 | 0.65347 | 0.66389 | 0 | 0.25 | 0.25 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.0096154 | O2-26 | 138.7708 |  | WTG Breakdown Maintenance | 13322 | 138.7708
4752 | 2025-05-12 | 2025 | 2025 | 2025-05-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.67361 | 0.67361 | 0.67778 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-26 | 55.5083 |  | WTG Unscheduled Maintenance | 13322 | 55.5083
4753 | 2025-05-12 | 2025 | 2025 | 2025-05-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 5506 | Rot.br. press. high | Break down | 0 | 0 | 0.12014 | 0 | 2.8833 | 2.8833 | After Filling Nitrogen accumulator pressure set than trail taken and started wtg | Close | 0.1109 | O2-14 | 1350.1208 |  | WTG Breakdown Maintenance | 11238 | 1350.1208
4754 | 2025-05-12 | 2025 | 2025 | 2025-05-01 | 2 | O2_20 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Auto reset | 0.44653 | 0.44653 | 0.44792 | 0 | 0.033333 | 0.033333 | Auto Reset | Close | 0.0012821 | O2-24 | 14.4931 |  | WTG Unscheduled Maintenance | 10435 | 14.4931
4755 | 2025-05-12 | 2025 | 2025 | 2025-05-01 | 2 | O2_22 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Auto reset | 0.7375 | 0.7375 | 0.73958 | 0 | 0.05 | 0.05 | Auto Reset | Close | 0.0019231 | O2-06 | 23.3917 |  | WTG Unscheduled Maintenance | 11228 | 23.3917
4756 | 2025-05-12 | 2025 | 2025 | 2025-05-01 | 2 | O2_26 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.65417 | 0.65417 | 0.66389 | 0 | 0.23333 | 0.23333 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.0089744 | O2-01 | 128.1292 |  | WTG Breakdown Maintenance | 13179 | 128.1292
4757 | 2025-05-13 | 2025 | 2025 | 2025-05-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR | 0.37778 | 0.37778 | 0.75 | 0 | 8.9333 | 8.9333 | WTG manual stop for Slipring WTR 646,658,629,633 work. | Close | 0.34359 | O2-26 | 5917.5889 |  | WTG Breakdown Maintenance | 15898 | 5917.5889
4758 | 2025-05-13 | 2025 | 2025 | 2025-05-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 2521 | Gen.sp.analog <<>> gearb.sp. | Auto reset | 0.62361 | 0.62361 | 0.62569 | 0 | 0.05 | 0.05 | AUTO Reset | Close | 0.0019231 | O2-02 | 39.325 |  | WTG Unscheduled Maintenance | 18876 | 39.325
4759 | 2025-05-13 | 2025 | 2025 | 2025-05-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.85278 | 0.85278 | 0.87153 | 0 | 0.45 | 0.45 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.017308 | O2-01 | 297.3188 |  | WTG Unscheduled Maintenance | 15857 | 297.3188
4760 | 2025-05-14 | 2025 | 2025 | 2025-05-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR | 0.70903 | 0.72708 | 0.74792 | 0.43333 | 0.5 | 0.93333 | WTG Manual stop for WTR 656 work. | Close | 0.035897 | O2-26 | 600.9889 |  | WTG Unscheduled Maintenance | 15454 | 600.9889
4761 | 2025-05-14 | 2025 | 2025 | 2025-05-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset | 0.34792 | 0.34792 | 0.35069 | 0 | 0.066667 | 0.066667 | AUTO Reset | Close | 0.0025641 | O2-02 | 51.6194 |  | WTG Unscheduled Maintenance | 18583 | 51.6194
4762 | 2025-05-14 | 2025 | 2025 | 2025-05-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.80278 | 0.80278 | 0.85069 | 0 | 1.15 | 1.15 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.044231 | O2-02 | 890.4354 |  | WTG Unscheduled Maintenance | 18583 | 890.4354
4763 | 2025-05-14 | 2025 | 2025 | 2025-05-01 | 2 | O2_09 | TQGXIIPL | GEDA | 3.846% | 88 | Outs.temp. nacelle implaus. | Auto reset | 0.65417 | 0.65417 | 0.65625 | 0 | 0.05 | 0.05 | Auto Reset | Close | 0.0019231 | O2-03 | 29.3333 |  | WTG Unscheduled Maintenance | 14080 | 29.3333
4764 | 2025-05-14 | 2025 | 2025 | 2025-05-01 | 2 | O2_09 | TQGXIIPL | GEDA | 3.846% | 6690 | Icing (stop) | Auto reset | 0.65833 | 0.65833 | 0.66111 | 0 | 0.066667 | 0.066667 | Auto Reset | Close | 0.0025641 | O2-03 | 39.1111 |  | WTG Unscheduled Maintenance | 14080 | 39.1111
4765 | 2025-05-14 | 2025 | 2025 | 2025-05-01 | 2 | O2_09 | TQGXIIPL | GEDA | 3.846% | 88 | Outs.temp. nacelle implaus. | Break down | 0.67917 | 0.67917 | 0.71181 | 0 | 0.78333 | 0.78333 | Checked related error data log then reset & start WTG. | Close | 0.030128 | O2-03 | 459.5556 |  | WTG Unscheduled Maintenance | 14080 | 459.5556
4766 | 2025-05-14 | 2025 | 2025 | 2025-05-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Break down | 0.79375 | 0.79375 | 0.80278 | 0 | 0.21667 | 0.21667 | Checked related error data log then reset & start WTG. | Close | 0.0083333 | O2-15 | 136.9785 |  | WTG Unscheduled Maintenance | 15173 | 136.9785
4767 | 2025-05-14 | 2025 | 2025 | 2025-05-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.44236 | 0.44236 | 0.44306 | 0 | 0.016667 | 0.016667 | Auto Reset | Close | 0.00064103 | O2-14 | 10.2083 |  | WTG Unscheduled Maintenance | 14700 | 10.2083
4768 | 2025-05-14 | 2025 | 2025 | 2025-05-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR | 0.62153 | 0.62153 | 0.69236 | 0 | 1.7 | 1.7 | WTG Manual stop for WTR 629,658,656 work. | Close | 0.065385 | O2-11 | 1004.4875 |  | WTG Unscheduled Maintenance | 14181 | 1004.4875
4769 | 2025-05-14 | 2025 | 2025 | 2025-05-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Break down | 0.79167 | 0.79167 | 0.80208 | 0 | 0.25 | 0.25 | Checked related error data log then reset & start WTG. | Close | 0.0096154 | O2-11 | 147.7188 |  | WTG Unscheduled Maintenance | 14181 | 147.7188
4770 | 2025-05-14 | 2025 | 2025 | 2025-05-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.79236 | 0.79236 | 0.80347 | 0 | 0.26667 | 0.26667 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.010256 | O2-01 | 181.3222 |  | WTG Unscheduled Maintenance | 16319 | 181.3222
4771 | 2025-05-14 | 2025 | 2025 | 2025-05-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.80833 | 0.80833 | 0.83333 | 0 | 0.6 | 0.6 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.023077 | O2-01 | 407.975 |  | WTG Unscheduled Maintenance | 16319 | 407.975
4772 | 2025-05-15 | 2025 | 2025 | 2025-05-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.76875 | 0.76875 | 0.77292 | 0 | 0.1 | 0.1 | Checked related error data log then reset & start WTG. | Close | 0.0038462 | O2-26 | 46.0667 |  | WTG Unscheduled Maintenance | 11056 | 46.0667
4773 | 2025-05-15 | 2025 | 2025 | 2025-05-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.12708 | 0.12708 | 0.15 | 0 | 0.55 | 0.55 | Checked related error data log then reset & start WTG. | Close | 0.021154 | O2-02 | 315.2188 |  | WTG Unscheduled Maintenance | 13755 | 315.2188
4774 | 2025-05-15 | 2025 | 2025 | 2025-05-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR | 0.45764 | 0.45764 | 0.77361 | 0 | 7.5833 | 7.5833 | WTG Manual stop for WTR 646,633,656,658,629 work. | Close | 0.29167 | O2-02 | 4346.1979 |  | WTG Breakdown Maintenance | 13755 | 4346.1979
4775 | 2025-05-15 | 2025 | 2025 | 2025-05-01 | 2 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3800 | Circuit breaker | Major BD | 0.11597 | 0.11597 | 0.5375 | 0 | 10.1167 | 10.1167 | attend and check data in Sam and also conver data and default restore than check physicaly ACB and it's settings and than check CT connection and take it's Ohm value than value found ok so check ACB setting and set them and also control card relay supply check and rebooted and reset as per Engineering team instruction than reset and start wtg.Now Turbine under observation. | Close | 0.3891 | O2-04 | 4521.7285 |  | WTG Breakdown Maintenance | 10727 | 4521.7285
4776 | 2025-05-15 | 2025 | 2025 | 2025-05-01 | 2 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3800 | Circuit breaker | Break down | 0.93056 | 0.93056 | 0.99999 | 0 | 1.6664 | 1.6664 | atten WTG and found ACB smart trip unit is malfunctioning so we interchange for O2-20 WIP. | Close | 0.064092 | O2-04 | 744.8064 |  | WTG Breakdown Maintenance | 10727 | 744.8064
4777 | 2025-05-15 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.82639 | 0.82639 | 0.84167 | 0 | 0.36667 | 0.36667 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.014103 | O2-26 | 168.9111 |  | WTG Unscheduled Maintenance | 11056 | 168.9111
4778 | 2025-05-15 | 2025 | 2025 | 2025-05-01 | 2 | O2_15 | TQGXIIPL | GEDA | 3.846% | 58 | Wind dir.dev. level 2 | Break down | 0.71042 | 0.71042 | 0.7125 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | O2-10 | 19.2937 |  | WTG Unscheduled Maintenance | 9261 | 19.2937
4779 | 2025-05-15 | 2025 | 2025 | 2025-05-01 | 2 | O2_16 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down | 0.775 | 0.775 | 0.77708 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | O2-21 | 18.2979 |  | WTG Unscheduled Maintenance | 8783 | 18.2979
4780 | 2025-05-15 | 2025 | 2025 | 2025-05-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.82153 | 0.82153 | 0.84583 | 0 | 0.58333 | 0.58333 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.022436 | O2-11 | 235.2535 |  | WTG Unscheduled Maintenance | 9679 | 235.2535
4781 | 2025-05-16 | 2025 | 2025 | 2025-05-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.71042 | 0.71042 | 0.7125 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | O2-26 | 37.2958 |  | WTG Unscheduled Maintenance | 17902 | 37.2958
4782 | 2025-05-16 | 2025 | 2025 | 2025-05-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.76667 | 0.76667 | 0.79167 | 0 | 0.6 | 0.6 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.023077 | O2-26 | 447.55 |  | WTG Unscheduled Maintenance | 17902 | 447.55
4783 | 2025-05-16 | 2025 | 2025 | 2025-05-01 | 2 | O2_02 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Break down | 0.69931 | 0.69931 | 0.71042 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & start WTG. | Close | 0.010256 | O2-05 | 195.9556 |  | WTG Unscheduled Maintenance | 17636 | 195.9556
4784 | 2025-05-16 | 2025 | 2025 | 2025-05-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Break down | 0.71458 | 0.71458 | 0.71875 | 0 | 0.1 | 0.1 | Checked related error data log then reset & start WTG. | Close | 0.0038462 | O2-02 | 76.9708 |  | WTG Unscheduled Maintenance | 18473 | 76.9708
4785 | 2025-05-16 | 2025 | 2025 | 2025-05-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.74722 | 0.74722 | 0.74861 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & start WTG. | Close | 0.0012821 | O2-02 | 25.6569 |  | WTG Unscheduled Maintenance | 18473 | 25.6569
4786 | 2025-05-16 | 2025 | 2025 | 2025-05-01 | 2 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3800 | Circuit breaker | Major BD | 0 | 0 | 0.69444 | 0 | 16.6667 | 16.6667 | ACB smart trip unit Material arrangement for another site WIP | OPEN | 0.64103 | O2-04 | 9255.5556 |  | WTG Breakdown Maintenance | 13328 | 9255.5556
4787 | 2025-05-16 | 2025 | 2025 | 2025-05-01 | 2 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3800 | Circuit breaker | Major BD | 0.79931 | 0.79931 | 0.99999 | 0 | 4.8164 | 4.8164 | ACB smart trip unit Material arrangement for another site WIP | OPEN | 0.18525 | O2-04 | 2674.7013 |  | WTG Breakdown Maintenance | 13328 | 2674.7013
4788 | 2025-05-16 | 2025 | 2025 | 2025-05-01 | 2 | O2_09 | TQGXIIPL | GEDA | 3.846% | 6690 | Icing (stop) | Major BD | 0.63681 | 0.63681 | 0.99999 | 0 | 8.7164 | 8.7164 | Turbine stop in icing (Stop) Error Occurred.But at that time turbine running shown in Fleetpro and status as online but physical in breakdown.Due to data freeze from the server so turbine stop. | Close | 0.33525 | O2-03 | 6247.4717 |  | WTG Unscheduled Maintenance | 17202 | 6247.4717
4789 | 2025-05-16 | 2025 | 2025 | 2025-05-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 53 | Wind dir.dev. level 1 | Auto reset | 0.7 | 0.7 | 0.70139 | 0 | 0.033333 | 0.033333 | Auto Reset | Close | 0.0012821 | O2-12 | 23.1514 |  | WTG Unscheduled Maintenance | 16669 | 23.1514
4790 | 2025-05-16 | 2025 | 2025 | 2025-05-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.75 | 0.75 | 0.75556 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & start WTG. | Close | 0.0051282 | O2-12 | 92.6056 |  | WTG Unscheduled Maintenance | 16669 | 92.6056
4791 | 2025-05-16 | 2025 | 2025 | 2025-05-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR | 0.45347 | 0.45347 | 0.54722 | 0 | 2.25 | 2.25 | WTG Manual stop for WTR 633,656,658,629 work. | Close | 0.086538 | O2-11 | 1612.5938 |  | WTG Scheduled Maintenance | 17201 | 1612.5938
4792 | 2025-05-16 | 2025 | 2025 | 2025-05-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 53 | Wind dir.dev. level 1 | Auto reset | 0.69722 | 0.69722 | 0.69861 | 0 | 0.033333 | 0.033333 | Auto Reset | Close | 0.0012821 | O2-11 | 23.8903 |  | WTG Unscheduled Maintenance | 17201 | 23.8903
4793 | 2025-05-16 | 2025 | 2025 | 2025-05-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.76597 | 0.76597 | 0.76875 | 0 | 0.066667 | 0.066667 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.0025641 | O2-11 | 47.7806 |  | WTG Unscheduled Maintenance | 17201 | 47.7806
4794 | 2025-05-16 | 2025 | 2025 | 2025-05-01 | 2 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.039583 | 0.039583 | 0.072222 | 0 | 0.78333 | 0.78333 | wtg manual stop for material cannibalize work | Close | 0.030128 | O2-24 | 490.5951 |  | WTG Breakdown Maintenance | 15031 | 490.5951
4795 | 2025-05-16 | 2025 | 2025 | 2025-05-01 | 2 | O2_20 | TQGXIIPL | GEDA | 3.846% | 643 | Sim.angle E enc. <> act.angle 3 | Break down | 0.77847 | 0.77847 | 0.77917 | 0 | 0.016667 | 0.016667 | after grid resume error occurs so Checked related error data log then reset & start WTG. | Close | 0.00064103 | O2-24 | 10.4382 |  | WTG Unscheduled Maintenance | 15031 | 10.4382
4796 | 2025-05-16 | 2025 | 2025 | 2025-05-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 1731 | Oil temperature gearbox input high | Break down | 0.19375 | 0.19375 | 0.20139 | 0 | 0.18333 | 0.18333 | Checked related error data log then found sensor is malfunctioning so apply shoft reboot then reset & start WTG. | Close | 0.0070513 | O2-11 | 131.3965 |  | WTG Unscheduled Maintenance | 17201 | 131.3965
4797 | 2025-05-16 | 2025 | 2025 | 2025-05-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 58 | Wind dir.dev. level 2 | Auto reset | 0.74514 | 0.74514 | 0.74583 | 0 | 0.016667 | 0.016667 | Auto Reset | Close | 0.00064103 | O2-11 | 11.9451 |  | WTG Unscheduled Maintenance | 17201 | 11.9451
4798 | 2025-05-16 | 2025 | 2025 | 2025-05-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.77361 | 0.77361 | 0.79236 | 0 | 0.45 | 0.45 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.017308 | O2-01 | 287.3062 |  | WTG Unscheduled Maintenance | 15323 | 287.3062
4799 | 2025-05-17 | 2025 | 2025 | 2025-05-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down | 0.39444 | 0.39444 | 0.39653 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | O2-02 | 28.8354 |  | WTG Unscheduled Maintenance | 13841 | 28.8354
4800 | 2025-05-17 | 2025 | 2025 | 2025-05-01 | 2 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3800 | Circuit breaker | Major BD | 0 | 0 | 0.28056 | 0 | 6.7333 | 6.7333 | ACB smart trip unit Material arrangement for another site WIP | Close | 0.25897 | O2-04 | 3986.1333 |  | WTG Breakdown Maintenance | 14208 | 3986.1333
4801 | 2025-05-17 | 2025 | 2025 | 2025-05-01 | 2 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3800 | Circuit breaker | Major BD | 0.28958 | 0.28958 | 0.74306 | 0 | 10.8833 | 10.8833 | ACB smart trip unit Material arrangement for another site then replace it then start wtg. | Close | 0.41859 | O2-04 | 6442.9333 |  | WTG Breakdown Maintenance | 14208 | 6442.9333
4802 | 2025-05-17 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.55486 | 0.55486 | 0.55903 | 0 | 0.1 | 0.1 | Checked related error data log then reset & start WTG. | Close | 0.0038462 | O2-26 | 52.2042 |  | WTG Unscheduled Maintenance | 12529 | 52.2042
4803 | 2025-05-17 | 2025 | 2025 | 2025-05-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 7002 | Task runtime failure 5ms | Break down | 0.79167 | 0.79167 | 0.80139 | 0 | 0.23333 | 0.23333 | Checked related error data log then reset & start WTG. | Close | 0.0089744 | O2-12 | 118.9417 |  | WTG Unscheduled Maintenance | 12234 | 118.9417
4804 | 2025-05-17 | 2025 | 2025 | 2025-05-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR | 0.63958 | 0.63958 | 0.67778 | 0 | 0.91667 | 0.91667 | WTG Manual stop for WTR 633,656,658,629 work. | Close | 0.035256 | O2-07 | 252.5799 |  | WTG Breakdown Maintenance | 6613 | 252.5799
4804 | 2025-05-17 | 2025 | 2025 | 2025-05-01 | 2 | O2_09 | TQGXIIPL | GEDA | 3.846% | 6690 | Icing (stop) | Major BD | 0 | 0 | 0.99999 | 0 | 23.9997 | 23.9997 | Turbine stop in icing (Stop) Error Occurred.But at that time turbine running shown in Fleetpro and status as online but physical in breakdown.Due to data freeze from the server so turbine stop. | Close | 0.92307 | O2-03 | 13635.8422 |  | WTG Unscheduled Maintenance | 13636 | 13635.8422
4805 | 2025-05-18 | 2025 | 2025 | 2025-05-01 | 2 | O2_07 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.875 | 0.875 | 0.87639 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & start WTG. | Close | 0.0012821 | O2-04 | 18.8222 |  | WTG Unscheduled Maintenance | 13552 | 18.8222
4806 | 2025-05-18 | 2025 | 2025 | 2025-05-01 | 2 | O2_09 | TQGXIIPL | GEDA | 3.846% | 6690 | Icing (stop) | Major BD | 0 | 0 | 0.31528 | 0 | 7.5667 | 7.5667 | Turbine stop in icing (Stop) Error Occurred.But at that time turbine running shown in Fleetpro and status as online but physical in breakdown.Due to data freeze from the server so turbine stop. So cannected wtg (Farm) reset then start WTG. | Close | 0.29103 | O2-03 | 4002.1361 |  | WTG Unscheduled Maintenance | 12694 | 4002.1361
4807 | 2025-05-18 | 2025 | 2025 | 2025-05-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 1130 | Acceleration detector drivetrain | Auto reset | 0.10833 | 0.10833 | 0.10972 | 0 | 0.033333 | 0.033333 | Auto Reset | Close | 0.0012821 | O2-14 | 16.1972 |  | WTG Unscheduled Maintenance | 11662 | 16.1972
4808 | 2025-05-18 | 2025 | 2025 | 2025-05-01 | 2 | O2_15 | TQGXIIPL | GEDA | 3.846% | 642 | Sim.angle E enc. <> act.angle 2 | Break down | 0.51806 | 0.56458 | 0.58056 | 1.1167 | 0.38333 | 1.5 | after grid resume error is occurs so We have check in SAM error related data then attend turbine check blade 02 in converter side connection and found loose connection so re tight properly then started Turbine. | Close | 0.057692 | O2-10 | 829.5 |  | WTG Breakdown Maintenance | 13272 | 829.5
4809 | 2025-05-18 | 2025 | 2025 | 2025-05-01 | 2 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.54792 | 0.54792 | 0.55208 | 0 | 0.1 | 0.1 | Checked related error data log then reset & start WTG. | Close | 0.0038462 | O2-06 | 58.8583 |  | WTG Unscheduled Maintenance | 14126 | 58.8583
4810 | 2025-05-18 | 2025 | 2025 | 2025-05-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.65764 | 0.65764 | 0.65833 | 0 | 0.016667 | 0.016667 | Auto Reset | Close | 0.00064103 | O2-11 | 8.6097 |  | WTG Unscheduled Maintenance | 12398 | 8.6097
4810 | 2025-05-19 | 2025 | 2025 | 2025-05-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | ROW issue | 0.72917 | 0.72917 | 0.73611 | 0 | 0.16667 | 0.16667 | WTG Manual stop for Feeder#1 Shutdown taking by BOP team but Feeder#1 Shutdown postponed due to ROW issue. | Close | 0.0064103 | O2-26 | 99.8472 |  | WTG Unscheduled Maintenance | 14378 | 99.8472
4810 | 2025-05-19 | 2025 | 2025 | 2025-05-01 | 2 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | ROW issue | 0.72917 | 0.72917 | 0.73611 | 0 | 0.16667 | 0.16667 | WTG Manual stop for Feeder#1 Shutdown taking by BOP team but Feeder#1 Shutdown postponed due to ROW issue. | Close | 0.0064103 | O2-05 | 115.4236 |  | WTG Unscheduled Maintenance | 16621 | 115.4236
4810 | 2025-05-19 | 2025 | 2025 | 2025-05-01 | 2 | O2_03 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | ROW issue | 0.72917 | 0.72917 | 0.73611 | 0 | 0.16667 | 0.16667 | WTG Manual stop for Feeder#1 Shutdown taking by BOP team but Feeder#1 Shutdown postponed due to ROW issue. | Close | 0.0064103 | O2-09 | 109.2222 |  | WTG Unscheduled Maintenance | 15728 | 109.2222
4810 | 2025-05-19 | 2025 | 2025 | 2025-05-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | ROW issue | 0.72917 | 0.72917 | 0.73611 | 0 | 0.16667 | 0.16667 | WTG Manual stop for Feeder#1 Shutdown taking by BOP team but Feeder#1 Shutdown postponed due to ROW issue. | Close | 0.0064103 | O2-02 | 125.0139 |  | WTG Unscheduled Maintenance | 18002 | 125.0139
4810 | 2025-05-19 | 2025 | 2025 | 2025-05-01 | 2 | O2_07 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.072917 | 0.072917 | 0.074306 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & start WTG. | Close | 0.0012821 | O2-04 | 22.4486 |  | WTG Unscheduled Maintenance | 16163 | 22.4486
4810 | 2025-05-19 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | ROW issue | 0.72917 | 0.72917 | 0.73611 | 0 | 0.16667 | 0.16667 | WTG Manual stop for Feeder#1 Shutdown taking by BOP team but Feeder#1 Shutdown postponed due to ROW issue. | Close | 0.0064103 | O2-26 | 99.8472 |  | WTG Unscheduled Maintenance | 14378 | 99.8472
4810 | 2025-05-19 | 2025 | 2025 | 2025-05-01 | 2 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | ROW issue | 0.72917 | 0.72917 | 0.73611 | 0 | 0.16667 | 0.16667 | WTG Manual stop for Feeder#1 Shutdown taking by BOP team but Feeder#1 Shutdown postponed due to ROW issue. | Close | 0.0064103 | O2-03 | 92.5972 |  | WTG Unscheduled Maintenance | 13334 | 92.5972
4810 | 2025-05-19 | 2025 | 2025 | 2025-05-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | ROW issue | 0.72917 | 0.72917 | 0.73611 | 0 | 0.16667 | 0.16667 | WTG Manual stop for Feeder#1 Shutdown taking by BOP team but Feeder#1 Shutdown postponed due to ROW issue. | Close | 0.0064103 | O2-15 | 95.8889 |  | WTG Unscheduled Maintenance | 13808 | 95.8889
4810 | 2025-05-19 | 2025 | 2025 | 2025-05-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | ROW issue | 0.72917 | 0.72917 | 0.73611 | 0 | 0.16667 | 0.16667 | WTG Manual stop for Feeder#1 Shutdown taking by BOP team but Feeder#1 Shutdown postponed due to ROW issue. | Close | 0.0064103 | O2-12 | 94.4444 |  | WTG Unscheduled Maintenance | 13600 | 94.4444
4810 | 2025-05-19 | 2025 | 2025 | 2025-05-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | ROW issue | 0.72917 | 0.72917 | 0.73611 | 0 | 0.16667 | 0.16667 | WTG Manual stop for Feeder#1 Shutdown taking by BOP team but Feeder#1 Shutdown postponed due to ROW issue. | Close | 0.0064103 | O2-14 | 98.2014 |  | WTG Unscheduled Maintenance | 14141 | 98.2014
4810 | 2025-05-19 | 2025 | 2025 | 2025-05-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | ROW issue | 0.72917 | 0.72917 | 0.73611 | 0 | 0.16667 | 0.16667 | WTG Manual stop for Feeder#1 Shutdown taking by BOP team but Feeder#1 Shutdown postponed due to ROW issue. | Close | 0.0064103 | O2-11 | 87.8958 |  | WTG Unscheduled Maintenance | 12657 | 87.8958
4810 | 2025-05-19 | 2025 | 2025 | 2025-05-01 | 2 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | ROW issue | 0.72917 | 0.72917 | 0.73611 | 0 | 0.16667 | 0.16667 | WTG Manual stop for Feeder#1 Shutdown taking by BOP team but Feeder#1 Shutdown postponed due to ROW issue. | Close | 0.0064103 | O2-12 | 94.4444 |  | WTG Unscheduled Maintenance | 13600 | 94.4444
4810 | 2025-05-19 | 2025 | 2025 | 2025-05-01 | 2 | O2_15 | TQGXIIPL | GEDA | 3.846% | 4555 | Tower accel. difference | Auto reset | 0.12847 | 0.12847 | 0.13264 | 0 | 0.1 | 0.1 | Auto Reset | Close | 0.0038462 | O2-10 | 60.4 |  | WTG Unscheduled Maintenance | 14496 | 60.4
4810 | 2025-05-19 | 2025 | 2025 | 2025-05-01 | 2 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | ROW issue | 0.72917 | 0.72917 | 0.73611 | 0 | 0.16667 | 0.16667 | WTG Manual stop for Feeder#1 Shutdown taking by BOP team but Feeder#1 Shutdown postponed due to ROW issue. | Close | 0.0064103 | O2-10 | 100.6667 |  | WTG Unscheduled Maintenance | 14496 | 100.6667
4810 | 2025-05-19 | 2025 | 2025 | 2025-05-01 | 2 | O2_22 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.52917 | 0.52917 | 0.625 | 0 | 2.3 | 2.3 | Attend Wtg and Anomaly related work like Blade calibration and ultrasonic value found deviation so alignment done than occurred error Battery under voltage/over voltage so check and found axis 3 flat resistor faulty so arrenge it and replace. | Close | 0.088462 | O2-06 | 1504.3917 |  | WTG Breakdown Maintenance | 15698 | 1504.3917
4810 | 2025-05-19 | 2025 | 2025 | 2025-05-01 | 2 | O2_22 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR | 0.625 | 0.625 | 0.75347 | 0 | 3.0833 | 3.0833 | WTR 656,658,629 and 633 performing work done then start wtg. | Close | 0.11859 | O2-06 | 2016.7569 |  | WTG Breakdown Maintenance | 15698 | 2016.7569
4810 | 2025-05-19 | 2025 | 2025 | 2025-05-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | ROW issue | 0.72917 | 0.72917 | 0.73611 | 0 | 0.16667 | 0.16667 | WTG Manual stop for Feeder#1 Shutdown taking by BOP team but Feeder#1 Shutdown postponed due to ROW issue. | Close | 0.0064103 | O2-11 | 87.8958 |  | WTG Unscheduled Maintenance | 12657 | 87.8958
4810 | 2025-05-19 | 2025 | 2025 | 2025-05-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | ROW issue | 0.72917 | 0.72917 | 0.73611 | 0 | 0.16667 | 0.16667 | WTG Manual stop for Feeder#1 Shutdown taking by BOP team but Feeder#1 Shutdown postponed due to ROW issue. | Close | 0.0064103 | O2-01 | 108.0417 |  | WTG Unscheduled Maintenance | 15558 | 108.0417
4810 | 2025-05-19 | 2025 | 2025 | 2025-05-01 | 2 | O2_26 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | ROW issue | 0.72917 | 0.72917 | 0.73611 | 0 | 0.16667 | 0.16667 | WTG Manual stop for Feeder#1 Shutdown taking by BOP team but Feeder#1 Shutdown postponed due to ROW issue. | Close | 0.0064103 | O2-01 | 108.0417 |  | WTG Unscheduled Maintenance | 15558 | 108.0417
4811 | 2025-05-20 | 2025 | 2025 | 2025-05-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.70972 | 0.70972 | 0.71597 | 0 | 0.15 | 0.15 | Checked related error data log then reset & start WTG. | Close | 0.0057692 | O2-07 | 79.2937 |  | WTG Unscheduled Maintenance | 12687 | 79.2937
4812 | 2025-05-20 | 2025 | 2025 | 2025-05-01 | 2 | O2_06 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.54236 | 0.54236 | 0.54653 | 0 | 0.1 | 0.1 | Auto Reset | Close | 0.0038462 | O2-21 | 58.0583 |  | WTG Unscheduled Maintenance | 13934 | 58.0583
4813 | 2025-05-20 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.71736 | 0.71736 | 0.76042 | 0 | 1.0333 | 1.0333 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.039744 | O2-26 | 607.2125 |  | WTG Unscheduled Maintenance | 14103 | 607.2125
4814 | 2025-05-20 | 2025 | 2025 | 2025-05-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.73264 | 0.73264 | 0.73681 | 0 | 0.1 | 0.1 | Auto Reset | Close | 0.0038462 | O2-15 | 62.4792 |  | WTG Unscheduled Maintenance | 14995 | 62.4792
4815 | 2025-05-20 | 2025 | 2025 | 2025-05-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.37083 | 0.37083 | 0.45833 | 0 | 2.1 | 2.1 | Attend and Wtg check Converter 230 V AC Supply check UPS connection check Feedback connection check all connection tight after trail so ok then Reset and started Wtg. | Close | 0.080769 | O2-14 | 1205.6625 |  | WTG Breakdown Maintenance | 13779 | 1205.6625
4816 | 2025-05-20 | 2025 | 2025 | 2025-05-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR | 0.48056 | 0.48056 | 0.54931 | 0 | 1.65 | 1.65 | WTG Manual stop for WTR 656,658,633 and 629 Performing and started Wtg. | Close | 0.063462 | O2-14 | 947.3063 |  | WTG Breakdown Maintenance | 13779 | 947.3063
4817 | 2025-05-20 | 2025 | 2025 | 2025-05-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 1510 | Low gearbox oil pressure | Break down | 0.89514 | 0.89514 | 0.89722 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | O2-11 | 26.3187 |  | WTG Unscheduled Maintenance | 12633 | 26.3187
4818 | 2025-05-20 | 2025 | 2025 | 2025-05-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.66319 | 0.66319 | 0.66458 | 0 | 0.033333 | 0.033333 | Checked related error data log apply shoft reboot then reset & start WTG. | Close | 0.0012821 | O2-22 | 27.5222 |  | WTG Unscheduled Maintenance | 19816 | 27.5222
4821 | 2025-05-20 | 2025 | 2025 | 2025-05-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.71944 | 0.71944 | 0.75694 | 0 | 0.9 | 0.9 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.034615 | O2-01 | 500.775 |  | WTG Unscheduled Maintenance | 13354 | 500.775
4822 | 2025-05-20 | 2025 | 2025 | 2025-05-01 | 2 | O2_26 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.37083 | 0.37083 | 0.38264 | 0 | 0.28333 | 0.28333 | after grid resume error is occurs so Checked related error data log apply shoft reboot then reset & start WTG. | Close | 0.010897 | O2-01 | 157.6514 |  | WTG Unscheduled Maintenance | 13354 | 157.6514
4823 | 2025-05-21 | 2025 | 2025 | 2025-05-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.80278 | 0.80278 | 0.81736 | 0 | 0.35 | 0.35 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.013462 | O2-26 | 77.6417 |  | WTG Unscheduled Maintenance | 5324 | 77.6417
4824 | 2025-05-21 | 2025 | 2025 | 2025-05-01 | 2 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.80278 | 0.80278 | 0.83333 | 0 | 0.73333 | 0.73333 | After Grid charge RFO signal coming than Start WTG. | Close | 0.028205 | O2-05 | 207.6861 |  | WTG Unscheduled Maintenance | 6797 | 207.6861
4825 | 2025-05-21 | 2025 | 2025 | 2025-05-01 | 2 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.80278 | 0.80278 | 0.83056 | 0 | 0.66667 | 0.66667 | After Grid charge RFO signal coming than Start WTG. | Close | 0.025641 | O2-09 | 159.1667 |  | WTG Unscheduled Maintenance | 5730 | 159.1667
4826 | 2025-05-21 | 2025 | 2025 | 2025-05-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down | 0.79861 | 0.79861 | 0.85417 | 0 | 1.3333 | 1.3333 | after grid resume error is occurs so Checked related error data log then reset & start WTG. | Close | 0.051282 | O2-07 | 458.8333 |  | WTG Unscheduled Maintenance | 8259 | 458.8333
4827 | 2025-05-21 | 2025 | 2025 | 2025-05-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.80278 | 0.80278 | 0.83542 | 0 | 0.78333 | 0.78333 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.030128 | O2-02 | 224.2292 |  | WTG Unscheduled Maintenance | 6870 | 224.2292
4828 | 2025-05-21 | 2025 | 2025 | 2025-05-01 | 2 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.79861 | 0.79861 | 0.83194 | 0 | 0.8 | 0.8 | After Grid charge RFO signal coming than Start WTG. | Close | 0.030769 | O2-21 | 314.0667 |  | WTG Unscheduled Maintenance | 9422 | 314.0667
4829 | 2025-05-21 | 2025 | 2025 | 2025-05-01 | 2 | O2_07 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.79861 | 0.79861 | 0.85486 | 0 | 1.35 | 1.35 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.051923 | O2-04 | 491.9625 |  | WTG Unscheduled Maintenance | 8746 | 491.9625
4830 | 2025-05-21 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.80278 | 0.80278 | 0.81944 | 0 | 0.4 | 0.4 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.015385 | O2-26 | 88.7333 |  | WTG Unscheduled Maintenance | 5324 | 88.7333
4831 | 2025-05-21 | 2025 | 2025 | 2025-05-01 | 2 | O2_09 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down | 0.80278 | 0.80278 | 0.82083 | 0 | 0.43333 | 0.43333 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.016667 | O2-03 | 90.0611 |  | WTG Unscheduled Maintenance | 4988 | 90.0611
4832 | 2025-05-21 | 2025 | 2025 | 2025-05-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down | 0.80278 | 0.80278 | 0.82083 | 0 | 0.43333 | 0.43333 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.016667 | O2-15 | 109.3264 |  | WTG Unscheduled Maintenance | 6055 | 109.3264
4833 | 2025-05-21 | 2025 | 2025 | 2025-05-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.80278 | 0.80278 | 0.82153 | 0 | 0.45 | 0.45 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.017308 | O2-12 | 94.65 |  | WTG Unscheduled Maintenance | 5048 | 94.65
4834 | 2025-05-21 | 2025 | 2025 | 2025-05-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.80278 | 0.80278 | 0.83264 | 0 | 0.71667 | 0.71667 | After Grid charge RFO signal coming than Start WTG. | Close | 0.027564 | O2-14 | 146.8868 |  | WTG Unscheduled Maintenance | 4919 | 146.8868
4835 | 2025-05-21 | 2025 | 2025 | 2025-05-01 | 2 | O2_14 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.80278 | 0.80278 | 0.82292 | 0 | 0.48333 | 0.48333 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.01859 | O2-12 | 101.6611 |  | WTG Unscheduled Maintenance | 5048 | 101.6611
4836 | 2025-05-21 | 2025 | 2025 | 2025-05-01 | 2 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down | 0.80278 | 0.80278 | 0.82292 | 0 | 0.48333 | 0.48333 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.01859 | O2-10 | 94.7535 |  | WTG Unscheduled Maintenance | 4705 | 94.7535
4837 | 2025-05-21 | 2025 | 2025 | 2025-05-01 | 2 | O2_16 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.79861 | 0.85069 | 0.86458 | 1.25 | 0.33333 | 1.5833 | after grid resume error is occurs so attend Checked related error data log then apply hard reboot then reset & start WTG | Close | 0.060897 | O2-21 | 621.5903 |  | WTG Breakdown Maintenance | 9422 | 621.5903
4838 | 2025-05-21 | 2025 | 2025 | 2025-05-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.79861 | 0.79861 | 0.82361 | 0 | 0.6 | 0.6 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.023077 | O2-22 | 347.025 |  | WTG Unscheduled Maintenance | 13881 | 347.025
4839 | 2025-05-21 | 2025 | 2025 | 2025-05-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.79861 | 0.88264 | 0.89306 | 2.0167 | 0.25 | 2.2667 | after grid resume error is occurs so attend Checked related error data log then apply hard reboot then reset & start WTG | Close | 0.087179 | O2-06 | 1139.3778 |  | WTG Breakdown Maintenance | 12064 | 1139.3778
4840 | 2025-05-21 | 2025 | 2025 | 2025-05-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down | 0.79861 | 0.79861 | 0.85556 | 0 | 1.3667 | 1.3667 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.052564 | O2-07 | 470.3042 |  | WTG Unscheduled Maintenance | 8259 | 470.3042
4841 | 2025-05-21 | 2025 | 2025 | 2025-05-01 | 2 | O2_20 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.79861 | 0.79861 | 0.825 | 0 | 0.63333 | 0.63333 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.024359 | O2-24 | 208.9208 |  | WTG Unscheduled Maintenance | 7917 | 208.9208
4842 | 2025-05-21 | 2025 | 2025 | 2025-05-01 | 2 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.79861 | 0.79861 | 0.86875 | 0 | 1.6833 | 1.6833 | After Grid charge RFO signal coming than Start WTG. | Close | 0.064744 | O2-06 | 846.1556 |  | WTG Unscheduled Maintenance | 12064 | 846.1556
4843 | 2025-05-21 | 2025 | 2025 | 2025-05-01 | 2 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down | 0.79861 | 0.79861 | 0.84514 | 0 | 1.1167 | 1.1167 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.042949 | O2-06 | 561.3111 |  | WTG Unscheduled Maintenance | 12064 | 561.3111
4844 | 2025-05-21 | 2025 | 2025 | 2025-05-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.80278 | 0.80278 | 0.83125 | 0 | 0.68333 | 0.68333 | After Grid charge RFO signal coming than Start WTG. | Close | 0.026282 | O2-11 | 140.425 |  | WTG Unscheduled Maintenance | 4932 | 140.425
4845 | 2025-05-21 | 2025 | 2025 | 2025-05-01 | 2 | O2_24 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.79861 | 0.79861 | 0.82639 | 0 | 0.66667 | 0.66667 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.025641 | O2-20 | 214.9444 |  | WTG Unscheduled Maintenance | 7738 | 214.9444
4846 | 2025-05-21 | 2025 | 2025 | 2025-05-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down | 0.80278 | 0.80278 | 0.82708 | 0 | 0.58333 | 0.58333 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.022436 | O2-01 | 141.0451 |  | WTG Unscheduled Maintenance | 5803 | 141.0451
4847 | 2025-05-21 | 2025 | 2025 | 2025-05-01 | 2 | O2_26 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down | 0.80278 | 0.80278 | 0.83472 | 0 | 0.76667 | 0.76667 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.029487 | O2-01 | 185.3736 |  | WTG Unscheduled Maintenance | 5803 | 185.3736
4848 | 2025-05-22 | 2025 | 2025 | 2025-05-01 | 2 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.79236 | 0.79236 | 0.82083 | 0 | 0.68333 | 0.68333 | After Grid charge RFO signal coming than Start WTG. | Close | 0.026282 | O2-05 | 165.5375 |  | WTG Unscheduled Maintenance | 5814 | 165.5375
4849 | 2025-05-22 | 2025 | 2025 | 2025-05-01 | 2 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.79236 | 0.79236 | 0.81944 | 0 | 0.65 | 0.65 | After Grid charge RFO signal coming than Start WTG. | Close | 0.025 | O2-09 | 125.9646 |  | WTG Unscheduled Maintenance | 4651 | 125.9646
4850 | 2025-05-22 | 2025 | 2025 | 2025-05-01 | 2 | O2_03 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Break down | 0.82153 | 0.82153 | 0.83819 | 0 | 0.4 | 0.4 | Checked related error data log then apply shoft reboot then reset & start WTG | Close | 0.015385 | O2-09 | 77.5167 |  | WTG Unscheduled Maintenance | 4651 | 77.5167
4851 | 2025-05-22 | 2025 | 2025 | 2025-05-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down | 0.79236 | 0.79236 | 0.80764 | 0 | 0.36667 | 0.36667 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.014103 | O2-02 | 65.0986 |  | WTG Unscheduled Maintenance | 4261 | 65.0986
4852 | 2025-05-22 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 643 | Sim.angle E enc. <> act.angle 3 | Break down | 0.79236 | 0.79236 | 0.81389 | 0 | 0.51667 | 0.51667 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.019872 | O2-26 | 70.4174 |  | WTG Unscheduled Maintenance | 3271 | 70.4174
4853 | 2025-05-22 | 2025 | 2025 | 2025-05-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down | 0.47431 | 0.47431 | 0.49236 | 0 | 0.43333 | 0.43333 | after grid resume error is occurs so Checked related error data log then reset & start WTG(Late start due to disconnected from scada due to jumer open at O2 14 ) | Close | 0.016667 | O2-15 | 94.6833 |  | WTG Unscheduled Maintenance | 5244 | 94.6833
4854 | 2025-05-22 | 2025 | 2025 | 2025-05-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.79236 | 0.79236 | 0.82083 | 0 | 0.68333 | 0.68333 | After Grid charge RFO signal coming than Start WTG. | Close | 0.026282 | O2-14 | 138.6313 |  | WTG Unscheduled Maintenance | 4869 | 138.6313
4855 | 2025-05-22 | 2025 | 2025 | 2025-05-01 | 2 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down | 0.47431 | 0.47431 | 0.49236 | 0 | 0.43333 | 0.43333 | after grid resume error is occurs so Checked related error data log then reset & start WTG(Late start due to disconnected from scada due to jumer open at O2 14 ) | Close | 0.016667 | O2-10 | 88.9778 |  | WTG Unscheduled Maintenance | 4928 | 88.9778
4856 | 2025-05-22 | 2025 | 2025 | 2025-05-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.79236 | 0.79236 | 0.82431 | 0 | 0.76667 | 0.76667 | After Grid charge RFO signal coming than Start WTG. | Close | 0.029487 | O2-11 | 158.0292 |  | WTG Unscheduled Maintenance | 4947 | 158.0292
4857 | 2025-05-22 | 2025 | 2025 | 2025-05-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.79236 | 0.79236 | 0.82986 | 0 | 0.9 | 0.9 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.034615 | O2-01 | 199.6875 |  | WTG Unscheduled Maintenance | 5325 | 199.6875
4858 | 2025-05-22 | 2025 | 2025 | 2025-05-01 | 2 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.79236 | 0.79236 | 0.82014 | 0 | 0.66667 | 0.66667 | After Grid charge RFO signal coming than Start WTG. | Close | 0.025641 | O2-01 | 147.9167 |  | WTG Unscheduled Maintenance | 5325 | 147.9167
4859 | 2025-05-23 | 2025 | 2025 | 2025-05-01 | 2 | O2_03 | TQGXIIPL | GEDA | 3.846% | 53 | Wind dir.dev. level 1 | Auto reset | 0.72431 | 0.72431 | 0.72639 | 0 | 0.05 | 0.05 | Auto Reset | Close | 0.0019231 | O2-09 | 27.7187 |  | WTG Unscheduled Maintenance | 13305 | 27.7187
4860 | 2025-05-23 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 3555 | Current asymmetry | Auto reset | 0.39167 | 0.39167 | 0.39931 | 0 | 0.18333 | 0.18333 | Auto Reset | Close | 0.0070513 | O2-26 | 93.4694 |  | WTG Unscheduled Maintenance | 12236 | 93.4694
4861 | 2025-05-23 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.73611 | 0.73611 | 0.74792 | 0 | 0.28333 | 0.28333 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.010897 | O2-26 | 144.4528 |  | WTG Unscheduled Maintenance | 12236 | 144.4528
4862 | 2025-05-23 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.80694 | 0.80694 | 0.82153 | 0 | 0.35 | 0.35 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.013462 | O2-26 | 178.4417 |  | WTG Unscheduled Maintenance | 12236 | 178.4417
4863 | 2025-05-23 | 2025 | 2025 | 2025-05-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Auto reset | 0.72431 | 0.72431 | 0.725 | 0 | 0.016667 | 0.016667 | Auto Reset | Close | 0.00064103 | O2-15 | 9.6326 |  | WTG Unscheduled Maintenance | 13871 | 9.6326
4864 | 2025-05-23 | 2025 | 2025 | 2025-05-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.82639 | 0.82639 | 0.82778 | 0 | 0.033333 | 0.033333 | Auto Reset | Close | 0.0012821 | O2-11 | 21.5361 |  | WTG Unscheduled Maintenance | 15506 | 21.5361
4865 | 2025-05-23 | 2025 | 2025 | 2025-05-01 | 2 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3532 | Min. voltage cut in | Auto reset | 0.29931 | 0.29931 | 0.3 | 0 | 0.016667 | 0.016667 | Auto Reset | Close | 0.00064103 | O2-10 | 8.7764 |  | WTG Unscheduled Maintenance | 12638 | 8.7764
4866 | 2025-05-23 | 2025 | 2025 | 2025-05-01 | 2 | O2_16 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Break down | 0.82083 | 0.82083 | 0.82361 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & start WTG. | Close | 0.0025641 | O2-21 | 34.4389 |  | WTG Unscheduled Maintenance | 12398 | 34.4389
4867 | 2025-05-23 | 2025 | 2025 | 2025-05-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.84653 | 0.84653 | 0.84792 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & start WTG. | Close | 0.0012821 | O2-22 | 20.5569 |  | WTG Unscheduled Maintenance | 14801 | 20.5569
4868 | 2025-05-23 | 2025 | 2025 | 2025-05-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 58 | Wind dir.dev. level 2 | Auto reset | 0.71389 | 0.71389 | 0.71528 | 0 | 0.033333 | 0.033333 | Auto Reset | Close | 0.0012821 | O2-06 | 20.3667 |  | WTG Unscheduled Maintenance | 14664 | 20.3667
4869 | 2025-05-23 | 2025 | 2025 | 2025-05-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Auto reset | 0.82431 | 0.82431 | 0.82639 | 0 | 0.05 | 0.05 | Auto Reset | Close | 0.0019231 | O2-07 | 25.5917 |  | WTG Unscheduled Maintenance | 12284 | 25.5917
4870 | 2025-05-23 | 2025 | 2025 | 2025-05-01 | 2 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.73056 | 0.73056 | 0.73194 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & start WTG. | Close | 0.0012821 | O2-06 | 20.3667 |  | WTG Unscheduled Maintenance | 14664 | 20.3667
4871 | 2025-05-23 | 2025 | 2025 | 2025-05-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.73542 | 0.73542 | 0.74792 | 0 | 0.3 | 0.3 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.011538 | O2-01 | 170.85 |  | WTG Unscheduled Maintenance | 13668 | 170.85
4872 | 2025-05-23 | 2025 | 2025 | 2025-05-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.80556 | 0.80556 | 0.82222 | 0 | 0.4 | 0.4 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.015385 | O2-01 | 227.8 |  | WTG Unscheduled Maintenance | 13668 | 227.8
4873 | 2025-05-24 | 2025 | 2025 | 2025-05-01 | 2 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.76944 | 0.76944 | 0.79722 | 0 | 0.66667 | 0.66667 | After Grid charge RFO signal coming than Start WTG. | Close | 0.025641 | O2-05 | 914.8611 |  | WTG Unscheduled Maintenance | 32935 | 914.8611
4874 | 2025-05-24 | 2025 | 2025 | 2025-05-01 | 2 | O2_03 | TQGXIIPL | GEDA | 3.846% | 550 | Pitch current asymmetry | Break down | 0.44097 | 0.44097 | 0.45278 | 0 | 0.28333 | 0.28333 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.010897 | O2-09 | 323.2125 |  | WTG Unscheduled Maintenance | 27378 | 323.2125
4875 | 2025-05-24 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.80139 | 0.80139 | 0.99999 | 0 | 4.7664 | 4.7664 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | open | 0.18332 | O2-26 | 5090.3047 |  | WTG Unscheduled Maintenance | 25631 | 5090.3047
4876 | 2025-05-24 | 2025 | 2025 | 2025-05-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.62222 | 0.62222 | 0.62569 | 0 | 0.083333 | 0.083333 | Auto Reset | Close | 0.0032051 | O2-12 | 50.8542 |  | WTG Unscheduled Maintenance | 14646 | 50.8542
4877 | 2025-05-24 | 2025 | 2025 | 2025-05-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.78194 | 0.78194 | 0.80417 | 0 | 0.53333 | 0.53333 | after grid resume error is occurs so attend Checked related error data log then apply hard reboot then reset & start WTG | Close | 0.020513 | O2-14 | 629.7111 |  | WTG Breakdown Maintenance | 28337 | 629.7111
4878 | 2025-05-24 | 2025 | 2025 | 2025-05-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.80764 | 0.80764 | 0.93542 | 0 | 3.0667 | 3.0667 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.11795 | O2-14 | 3620.8389 |  | WTG Unscheduled Maintenance | 28337 | 3620.8389
4879 | 2025-05-24 | 2025 | 2025 | 2025-05-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.95 | 0.95 | 0.99999 | 0 | 1.1997 | 1.1997 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | open | 0.046143 | O2-14 | 1416.522 |  | WTG Unscheduled Maintenance | 28337 | 1416.522
4880 | 2025-05-24 | 2025 | 2025 | 2025-05-01 | 2 | O2_14 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.68542 | 0.68542 | 0.68958 | 0 | 0.1 | 0.1 | Auto Reset | Close | 0.0038462 | O2-12 | 61.025 |  | WTG Unscheduled Maintenance | 14646 | 61.025
4881 | 2025-05-24 | 2025 | 2025 | 2025-05-01 | 2 | O2_15 | TQGXIIPL | GEDA | 3.846% | 642 | Sim.angle E enc. <> act.angle 2 | Break down | 0.76944 | 0.76944 | 0.78403 | 0 | 0.35 | 0.35 | after grid resume error is occurs so attend Checked related error data log then apply shoft reboot then reset & start WTG | Close | 0.013462 | O2-10 | 421.7208 |  | WTG Unscheduled Maintenance | 28918 | 421.7208
4882 | 2025-05-24 | 2025 | 2025 | 2025-05-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 1731 | Oil temperature gearbox input high | Break down | 0.475 | 0.475 | 0.48681 | 0 | 0.28333 | 0.28333 | Checked related error data log then apply shoft reboot then reset & start WTG. | Close | 0.010897 | O2-11 | 334.5222 |  | WTG Unscheduled Maintenance | 28336 | 334.5222
4883 | 2025-05-24 | 2025 | 2025 | 2025-05-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.31528 | 0.31528 | 0.33194 | 0 | 0.4 | 0.4 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.015385 | O2-01 | 464.45 |  | WTG Unscheduled Maintenance | 27867 | 464.45
4884 | 2025-05-24 | 2025 | 2025 | 2025-05-01 | 2 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.76944 | 0.76944 | 0.79722 | 0 | 0.66667 | 0.66667 | After Grid charge RFO signal coming than Start WTG. | Close | 0.025641 | O2-01 | 774.0833 |  | WTG Unscheduled Maintenance | 27867 | 774.0833
4885 | 2025-05-25 | 2025 | 2025 | 2025-05-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.34861 | 0.34931 | 0.34931 | 0.016667 | 0 | 0.016667 | Auto Reset | Close | 0.00064103 | O2-26 | 23.1806 |  | WTG Unscheduled Maintenance | 33380 | 23.1806
4886 | 2025-05-25 | 2025 | 2025 | 2025-05-01 | 2 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.70625 | 0.73611 | 0.73611 | 0.71667 | 0 | 0.71667 | After Grid charge RFO signal coming than Start WTG. | Close | 0.027564 | O2-05 | 913.0333 |  | WTG Breakdown Maintenance | 30576 | 913.0333
4887 | 2025-05-25 | 2025 | 2025 | 2025-05-01 | 2 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.65069 | 0.6625 | 0.6625 | 0.28333 | 0 | 0.28333 | WTG stopped for material cannibalize work. | Close | 0.010897 | O2-21 | 224.8132 |  | WTG Unscheduled Maintenance | 19043 | 224.8132
4888 | 2025-05-25 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0 | 0.14444 | 0.14444 | 3.4667 | 0 | 3.4667 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.13333 | O2-26 | 4821.5556 |  | WTG Unscheduled Maintenance | 33380 | 4821.5556
4889 | 2025-05-25 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.31458 | 0.36111 | 0.36111 | 1.1167 | 0 | 1.1167 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.042949 | O2-26 | 1553.0972 |  | WTG Unscheduled Maintenance | 33380 | 1553.0972
4890 | 2025-05-25 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.17847 | 0.18264 | 0.18264 | 0.1 | 0 | 0.1 | Auto reset | Close | 0.0038462 | O2-26 | 139.0833 |  | WTG Unscheduled Maintenance | 33380 | 139.0833
4891 | 2025-05-25 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.81736 | 0.96389 | 0.96389 | 3.5167 | 0 | 3.5167 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.13526 | O2-26 | 4891.0972 |  | WTG Unscheduled Maintenance | 33380 | 4891.0972
4892 | 2025-05-25 | 2025 | 2025 | 2025-05-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0 | 0.055556 | 0.055556 | 1.3333 | 0 | 1.3333 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.051282 | O2-14 | 1891.9444 |  | WTG Unscheduled Maintenance | 34055 | 1891.9444
4893 | 2025-05-25 | 2025 | 2025 | 2025-05-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Auto reset | 0.05625 | 0.059722 | 0.059722 | 0.083333 | 0 | 0.083333 | Auto Reset | Close | 0.0032051 | O2-14 | 118.2465 |  | WTG Unscheduled Maintenance | 34055 | 118.2465
4894 | 2025-05-25 | 2025 | 2025 | 2025-05-01 | 2 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Major BD | 0.59097 | 0.65625 | 0.99722 | 1.5667 | 8.1833 | 9.75 | Attend and wtg check related circuit check Converter cable check Power panel check control panel after check Stator cable rotor cable and check slipring so found Rotor cable minor Damage after arranging material 3M Tap apply and after trail so ok then reset and started wtg. | Close | 0.375 | O2-06 | 15254.2812 |  | WTG Breakdown Maintenance | 37549 | 15254.2812
4895 | 2025-05-25 | 2025 | 2025 | 2025-05-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.82708 | 0.93333 | 0.93333 | 2.55 | 0 | 2.55 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.098077 | O2-01 | 3349.3188 |  | WTG Unscheduled Maintenance | 31523 | 3349.3188
4896 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 58 | Wind dir.dev. level 2 | Auto reset | 0.00625 | 0.0083333 | 0.0083333 | 0.05 | 0 | 0.05 | Auto reset | Close | 0.0019231 | O2-26 | 62.4687 |  | WTG Unscheduled Maintenance | 29985 | 62.4687
4897 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | 2 | O2_02 | TQGXIIPL | GEDA | 3.846% | 565 | Max. windspeed bladeangle | Environment | 0.0048611 | 0.00625 | 0.00625 | 0.033333 | 0 | 0.033333 | Auto reset | Close | 0.0012821 | O2-05 | 40.5639 |  | WTG Unscheduled Maintenance | 29206 | 40.5639
4898 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | 2 | O2_03 | TQGXIIPL | GEDA | 3.846% | 53 | Wind dir.dev. level 1 | Auto reset | 0.0097222 | 0.011806 | 0.011806 | 0.05 | 0 | 0.05 | Auto reset | Close | 0.0019231 | O2-09 | 63.3042 |  | WTG Unscheduled Maintenance | 30386 | 63.3042
4899 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | 2 | O2_03 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down | 0.035417 | 0.042361 | 0.042361 | 0.16667 | 0 | 0.16667 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.0064103 | O2-09 | 211.0139 |  | WTG Breakdown Maintenance | 30386 | 211.0139
4900 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down | 0.036111 | 0.042361 | 0.042361 | 0.15 | 0 | 0.15 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.0057692 | O2-07 | 185.2188 |  | WTG Breakdown Maintenance | 29635 | 185.2188
4901 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.19583 | 0.2 | 0.2 | 0.1 | 0 | 0.1 | Auto reset | Close | 0.0038462 | O2-07 | 123.4792 |  | WTG Unscheduled Maintenance | 29635 | 123.4792
4902 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 53 | Wind dir.dev. level 1 | Auto reset | 0.015972 | 0.017361 | 0.017361 | 0.033333 | 0 | 0.033333 | Auto reset | Close | 0.0012821 | O2-02 | 44.0125 |  | WTG Unscheduled Maintenance | 31689 | 44.0125
4903 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down | 0.035417 | 0.05625 | 0.05625 | 0.5 | 0 | 0.5 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.019231 | O2-02 | 660.1875 |  | WTG Breakdown Maintenance | 31689 | 660.1875
4904 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.065972 | 0.11111 | 0.11111 | 1.0833 | 0 | 1.0833 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.041667 | O2-02 | 1430.4062 |  | WTG Breakdown Maintenance | 31689 | 1430.4062
4905 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 2521 | Gen.sp.analog <<>> gearb.sp. | Break down | 0.59306 | 0.59861 | 0.59861 | 0.13333 | 0 | 0.13333 | Checked related error data log then reset & start WTG. | Close | 0.0051282 | O2-02 | 176.05 |  | WTG Breakdown Maintenance | 31689 | 176.05
4906 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 58 | Wind dir.dev. level 2 | Auto reset | 0.00625 | 0.0083333 | 0.0083333 | 0.05 | 0 | 0.05 | Auto reset | Close | 0.0019231 | O2-26 | 62.4687 |  | WTG Unscheduled Maintenance | 29985 | 62.4687
4907 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 2390 | Brake due to sudden sys.failure | Break down | 0.035417 | 0.045139 | 0.045139 | 0.23333 | 0 | 0.23333 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.0089744 | O2-26 | 291.5208 |  | WTG Breakdown Maintenance | 29985 | 291.5208
4908 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.17778 | 0.21111 | 0.21111 | 0.8 | 0 | 0.8 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.030769 | O2-26 | 999.5 |  | WTG Unscheduled Maintenance | 29985 | 999.5
4909 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.21806 | 0.25694 | 0.25694 | 0.93333 | 0 | 0.93333 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.035897 | O2-26 | 1166.0833 |  | WTG Unscheduled Maintenance | 29985 | 1166.0833
4910 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.99097 | 1899-12-31 | 1899-12-31 | 0.21667 | 0 | 0.21667 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.0083333 | O2-26 | 270.6979 |  | WTG Unscheduled Maintenance | 29985 | 270.6979
4911 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | 2 | O2_09 | TQGXIIPL | GEDA | 3.846% | 58 | Wind dir.dev. level 2 | Auto reset | 0.0083333 | 0.010417 | 0.010417 | 0.05 | 0 | 0.05 | Auto reset | Close | 0.0019231 | O2-03 | 60.2458 |  | WTG Unscheduled Maintenance | 28918 | 60.2458
4912 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | 2 | O2_09 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down | 0.035417 | 0.045833 | 0.045833 | 0.25 | 0 | 0.25 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.0096154 | O2-03 | 301.2292 |  | WTG Breakdown Maintenance | 28918 | 301.2292
4913 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down | 0.035417 | 0.046528 | 0.046528 | 0.26667 | 0 | 0.26667 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.010256 | O2-15 | 298.6444 |  | WTG Breakdown Maintenance | 26878 | 298.6444
4914 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down | 0.035417 | 0.047222 | 0.047222 | 0.28333 | 0 | 0.28333 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.010897 | O2-14 | 331.9014 |  | WTG Breakdown Maintenance | 28114 | 331.9014
4915 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | 2 | O2_14 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.035417 | 0.047917 | 0.047917 | 0.3 | 0 | 0.3 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.011538 | O2-12 | 347.85 |  | WTG Breakdown Maintenance | 27828 | 347.85
4916 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | 2 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down | 0.035417 | 0.048611 | 0.048611 | 0.31667 | 0 | 0.31667 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.012179 | O2-10 | 344.0583 |  | WTG Breakdown Maintenance | 26076 | 344.0583
4917 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | 2 | O2_16 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down | 0.036111 | 0.049306 | 0.049306 | 0.31667 | 0 | 0.31667 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.012179 | O2-21 | 363.6125 |  | WTG Breakdown Maintenance | 27558 | 363.6125
4918 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.036111 | 0.049306 | 0.049306 | 0.31667 | 0 | 0.31667 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.012179 | O2-22 | 413.3951 |  | WTG Breakdown Maintenance | 31331 | 413.3951
4919 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down | 0.036111 | 0.05 | 0.05 | 0.33333 | 0 | 0.33333 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.012821 | O2-06 | 426.1528 |  | WTG Breakdown Maintenance | 30683 | 426.1528
4920 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down | 0.036111 | 0.050694 | 0.050694 | 0.35 | 0 | 0.35 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.013462 | O2-07 | 432.1771 |  | WTG Breakdown Maintenance | 29635 | 432.1771
4921 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | 2 | O2_20 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down | 0.036111 | 0.049306 | 0.049306 | 0.31667 | 0 | 0.31667 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.012179 | O2-24 | 370.9882 |  | WTG Breakdown Maintenance | 28117 | 370.9882
4922 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | 2 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down | 0.049306 | 0.077778 | 0.077778 | 0.68333 | 0 | 0.68333 | Checked related error data log apply shoft reboot then reset & start WTG. | Close | 0.026282 | O2-06 | 873.6132 |  | WTG Breakdown Maintenance | 30683 | 873.6132
4923 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | 2 | O2_21 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.70486 | 0.75764 | 0.75764 | 1.2667 | 0 | 1.2667 | Wtg manual stop for bottom panel inspection work after started wtg | Close | 0.048718 | O2-06 | 1619.3806 |  | WTG Breakdown Maintenance | 30683 | 1619.3806
4924 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | 2 | O2_22 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down | 0.05625 | 0.070139 | 0.070139 | 0.33333 | 0 | 0.33333 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.012821 | O2-06 | 426.1528 |  | WTG Breakdown Maintenance | 30683 | 426.1528
4925 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 58 | Wind dir.dev. level 2 | Auto reset | 0.0083333 | 0.010417 | 0.010417 | 0.05 | 0 | 0.05 | Auto reset | Close | 0.0019231 | O2-11 | 60.6667 |  | WTG Unscheduled Maintenance | 29120 | 60.6667
4926 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down | 0.035417 | 0.052083 | 0.052083 | 0.4 | 0 | 0.4 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.015385 | O2-11 | 485.3333 |  | WTG Breakdown Maintenance | 29120 | 485.3333
4927 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | 2 | O2_24 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down | 0.036111 | 0.052778 | 0.052778 | 0.4 | 0 | 0.4 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.015385 | O2-20 | 447.0833 |  | WTG Breakdown Maintenance | 26825 | 447.0833
4928 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 58 | Wind dir.dev. level 2 | Auto reset | 0.0034722 | 0.0055556 | 0.0055556 | 0.05 | 0 | 0.05 | Auto reset | Close | 0.0019231 | O2-01 | 63.1125 |  | WTG Unscheduled Maintenance | 30294 | 63.1125
4929 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down | 0.035417 | 0.052083 | 0.052083 | 0.4 | 0 | 0.4 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.015385 | O2-01 | 504.9 |  | WTG Breakdown Maintenance | 30294 | 504.9
4930 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.17847 | 0.21181 | 0.21181 | 0.8 | 0 | 0.8 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.030769 | O2-01 | 1009.8 |  | WTG Unscheduled Maintenance | 30294 | 1009.8
4931 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.21806 | 0.26319 | 0.26319 | 1.0833 | 0 | 1.0833 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.041667 | O2-01 | 1367.4375 |  | WTG Unscheduled Maintenance | 30294 | 1367.4375
4932 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | 2 | O2_26 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down | 0.035417 | 0.052778 | 0.052778 | 0.41667 | 0 | 0.41667 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.016026 | O2-01 | 525.9375 |  | WTG Breakdown Maintenance | 30294 | 525.9375
4933 | 2025-05-27 | 2025 | 2025 | 2025-05-01 | 2 | O2_03 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.015972 | 0.26944 | 0.26944 | 6.0833 | 0 | 6.0833 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.23397 | O2-09 | 11059.5 |  | WTG Unscheduled Maintenance | 43632 | 11059.5
4934 | 2025-05-27 | 2025 | 2025 | 2025-05-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.27708 | 0.28472 | 0.28472 | 0.18333 | 0 | 0.18333 | Checked related error data log apply shoft reboot then reset & start WTG. | Close | 0.0070513 | O2-02 | 372.0368 |  | WTG Breakdown Maintenance | 48703 | 372.0368
4935 | 2025-05-27 | 2025 | 2025 | 2025-05-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.88333 | 0.89861 | 0.89861 | 0.36667 | 0 | 0.36667 | Checked related error data log apply shoft reboot then reset & start WTG. | Close | 0.014103 | O2-02 | 744.0736 |  | WTG Breakdown Maintenance | 48703 | 744.0736
4936 | 2025-05-27 | 2025 | 2025 | 2025-05-01 | 2 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.23056 | 0.23819 | 0.23819 | 0.18333 | 0 | 0.18333 | Checked related error data log apply shoft reboot then reset & start WTG. | Close | 0.0070513 | O2-04 | 427.3576 |  | WTG Breakdown Maintenance | 55945 | 427.3576
4937 | 2025-05-27 | 2025 | 2025 | 2025-05-01 | 2 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.26319 | 0.29444 | 0.35278 | 0.75 | 1.4 | 2.15 | Attend and wtg check MPCB Motor and coolant so found QA008 MPCB Tripped after check voltage and fidbac connection tight after fan on temperature normal coolant fill up then reset and started wtg. | Close | 0.082692 | O2-04 | 5011.7396 |  | WTG Breakdown Maintenance | 55945 | 5011.7396
4938 | 2025-05-27 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0 | 0.21111 | 0.21111 | 5.0667 | 0 | 5.0667 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.19487 | O2-26 | 9588.0333 |  | WTG Unscheduled Maintenance | 45417 | 9588.0333
4939 | 2025-05-27 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.575 | 0.92431 | 0.92431 | 8.3833 | 0 | 8.3833 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.32244 | O2-26 | 15864.4104 |  | WTG Unscheduled Maintenance | 45417 | 15864.4104
4940 | 2025-05-27 | 2025 | 2025 | 2025-05-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.21667 | 0.22153 | 0.22153 | 0.11667 | 0 | 0.11667 | Checked related error data log then reset & start WTG. | Close | 0.0044872 | O2-22 | 262.7868 |  | WTG Breakdown Maintenance | 54059 | 262.7868
4941 | 2025-05-27 | 2025 | 2025 | 2025-05-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.23958 | 0.24792 | 0.24792 | 0.2 | 0 | 0.2 | Checked related error data log apply shoft reboot then reset & start WTG. | Close | 0.0076923 | O2-22 | 450.4917 |  | WTG Breakdown Maintenance | 54059 | 450.4917
4942 | 2025-05-27 | 2025 | 2025 | 2025-05-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.575 | 0.90625 | 0.90625 | 7.95 | 0 | 7.95 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.30577 | O2-01 | 15004.9625 |  | WTG Unscheduled Maintenance | 45298 | 15004.9625
4943 | 2025-05-28 | 2025 | 2025 | 2025-05-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.88958 | 0.89097 | 0.89097 | 0.033333 | 0 | 0.033333 | Auto reset | Close | 0.0012821 | O2-07 | 53.5486 |  | WTG Unscheduled Maintenance | 38555 | 53.5486
4944 | 2025-05-28 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.15486 | 0.20556 | 0.20556 | 1.2167 | 0 | 1.2167 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.046795 | O2-26 | 1539.2861 |  | WTG Unscheduled Maintenance | 30364 | 1539.2861
4945 | 2025-05-28 | 2025 | 2025 | 2025-05-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.13889 | 0.14306 | 0.14306 | 0.1 | 0 | 0.1 | Auto reset | Close | 0.0038462 | O2-11 | 156.4625 |  | WTG Unscheduled Maintenance | 37551 | 156.4625
4946 | 2025-05-28 | 2025 | 2025 | 2025-05-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.62639 | 0.63056 | 0.63056 | 0.1 | 0 | 0.1 | Auto reset | Close | 0.0038462 | O2-11 | 156.4625 |  | WTG Unscheduled Maintenance | 37551 | 156.4625
4947 | 2025-05-28 | 2025 | 2025 | 2025-05-01 | 2 | O2_15 | TQGXIIPL | GEDA | 3.846% | 642 | Sim.angle E enc. <> act.angle 2 | Break down | 0.40347 | 0.41319 | 0.41319 | 0.23333 | 0 | 0.23333 | Checked related error data log then reset & started WTG. | Close | 0.0089744 | O2-10 | 396.1319 |  | WTG Breakdown Maintenance | 40745 | 396.1319
4948 | 2025-05-28 | 2025 | 2025 | 2025-05-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.16319 | 0.16597 | 0.16597 | 0.066667 | 0 | 0.066667 | Checked related error data log then reset & started WTG. | Close | 0.0025641 | O2-22 | 109.7056 |  | WTG Breakdown Maintenance | 39494 | 109.7056
4949 | 2025-05-28 | 2025 | 2025 | 2025-05-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.17986 | 0.18403 | 0.18403 | 0.1 | 0 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | O2-22 | 164.5583 |  | WTG Breakdown Maintenance | 39494 | 164.5583
4950 | 2025-05-28 | 2025 | 2025 | 2025-05-01 | 2 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Auto reset | 0.39861 | 0.4 | 0.4 | 0.033333 | 0 | 0.033333 | Auto reset | Close | 0.0012821 | O2-06 | 53.9667 |  | WTG Unscheduled Maintenance | 38856 | 53.9667
4951 | 2025-05-28 | 2025 | 2025 | 2025-05-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding | 0.15694 | 0.20556 | 0.20556 | 1.1667 | 0 | 1.1667 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.044872 | O2-01 | 1757.0486 |  | WTG Unscheduled Maintenance | 36145 | 1757.0486
4952 | 2025-05-28 | 2025 | 2025 | 2025-05-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 172 | SLC MF torque protection | Break down | 0.70069 | 0.80347 | 0.80347 | 2.4667 | 0 | 2.4667 | Attend and wtg check Rotor brake pad Temp Sensor check and all connection check and tight after trail then reset and started wtg. | Close | 0.094872 | O2-01 | 3714.9028 |  | WTG Breakdown Maintenance | 36145 | 3714.9028
4953 | 2025-05-29 | 2025 | 2025 | 2025-05-01 | 2 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Project pending work | 0.42708 | 0.48611 | 0.48611 | 1.4167 | 0 | 1.4167 | Jumper open for Project Pending Work | Close | 0.054487 | O2-05 | 2010.8403 |  | WTG Breakdown Maintenance | 34066 | 2010.8403
4954 | 2025-05-29 | 2025 | 2025 | 2025-05-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Project pending work | 0.42708 | 0.48611 | 0.48611 | 1.4167 | 0 | 1.4167 | Jumper open for Project Pending Work | Close | 0.054487 | O2-02 | 2085.8056 |  | WTG Breakdown Maintenance | 35336 | 2085.8056
4955 | 2025-05-29 | 2025 | 2025 | 2025-05-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Project pending work | 0.42708 | 0.48611 | 0.48611 | 1.4167 | 0 | 1.4167 | Jumper open for Project Pending Work | Close | 0.054487 | O2-01 | 2065.441 |  | WTG Breakdown Maintenance | 34991 | 2065.441
4956 | 2025-05-29 | 2025 | 2025 | 2025-05-01 | 2 | O2_03 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Auto reset | 0.52986 | 0.53264 | 0.53264 | 0.066667 | 0 | 0.066667 | Auto reset | Close | 0.0025641 | O2-09 | 99.3611 |  | WTG Unscheduled Maintenance | 35770 | 99.3611
4957 | 2025-05-29 | 2025 | 2025 | 2025-05-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.61875 | 0.61944 | 0.61944 | 0.016667 | 0 | 0.016667 | Auto reset | Close | 0.00064103 | O2-07 | 25.4333 |  | WTG Unscheduled Maintenance | 36624 | 25.4333
4958 | 2025-05-29 | 2025 | 2025 | 2025-05-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.72222 | 0.72639 | 0.72639 | 0.1 | 0 | 0.1 | Auto reset | Close | 0.0038462 | O2-07 | 152.6 |  | WTG Unscheduled Maintenance | 36624 | 152.6
4959 | 2025-05-29 | 2025 | 2025 | 2025-05-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 5550 | Low hydraulic oil level | Break down | 0.85208 | 0.9125 | 1899-12-31 | 1.45 | 2.1 | 3.55 | Attend wtg check related circuit so check all valve and check oil level so found oil level low after check all yaw calliper and check all pipe check oil leakage WTG WIP | Close | 0.13654 | O2-07 | 5417.3 |  | WTG Breakdown Maintenance | 36624 | 5417.3
4960 | 2025-05-29 | 2025 | 2025 | 2025-05-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Auto reset | 0.61875 | 0.62361 | 0.62361 | 0.11667 | 0 | 0.11667 | Auto reset | Close | 0.0044872 | O2-02 | 171.7722 |  | WTG Unscheduled Maintenance | 35336 | 171.7722
4961 | 2025-05-29 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Auto reset | 0.73403 | 0.73472 | 0.73472 | 0.016667 | 0 | 0.016667 | Auto reset | Close | 0.00064103 | O2-26 | 25.0639 |  | WTG Unscheduled Maintenance | 36092 | 25.0639
4962 | 2025-05-29 | 2025 | 2025 | 2025-05-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.65417 | 0.65833 | 0.65833 | 0.1 | 0 | 0.1 | Auto reset | Close | 0.0038462 | O2-12 | 149.4208 |  | WTG Unscheduled Maintenance | 35861 | 149.4208
4963 | 2025-05-29 | 2025 | 2025 | 2025-05-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down | 0.67847 | 0.68194 | 0.68194 | 0.083333 | 0 | 0.083333 | Checked related error data log then reset & started WTG. | Close | 0.0032051 | O2-14 | 125.1875 |  | WTG Breakdown Maintenance | 36054 | 125.1875
4964 | 2025-05-29 | 2025 | 2025 | 2025-05-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Auto reset | 0.63194 | 0.63264 | 0.63264 | 0.016667 | 0 | 0.016667 | Auto reset | Close | 0.00064103 | O2-07 | 25.4333 |  | WTG Unscheduled Maintenance | 36624 | 25.4333
4965 | 2025-05-29 | 2025 | 2025 | 2025-05-01 | 2 | O2_20 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.60069 | 0.60139 | 0.60139 | 0.016667 | 0 | 0.016667 | Auto reset | Close | 0.00064103 | O2-24 | 25.4889 |  | WTG Unscheduled Maintenance | 36704 | 25.4889
4966 | 2025-05-29 | 2025 | 2025 | 2025-05-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 1731 | Oil temperature gearbox input high | Auto reset | 0.73472 | 0.73611 | 0.73611 | 0.033333 | 0 | 0.033333 | Auto reset | Close | 0.0012821 | O2-11 | 49.7722 |  | WTG Unscheduled Maintenance | 35836 | 49.7722
4967 | 2025-05-29 | 2025 | 2025 | 2025-05-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Auto reset | 0.74097 | 0.74306 | 0.74306 | 0.05 | 0 | 0.05 | Auto reset | Close | 0.0019231 | O2-11 | 74.6583 |  | WTG Unscheduled Maintenance | 35836 | 74.6583
4968 | 2025-05-30 | 2025 | 2025 | 2025-05-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.49444 | 0.5 | 0.5 | 0.13333 | 0 | 0.13333 | Checked related error data log then reset & started WTG. | Close | 0.0051282 | O2-26 | 313.4056 |  | WTG Breakdown Maintenance | 56413 | 313.4056
4969 | 2025-05-30 | 2025 | 2025 | 2025-05-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.64097 | 0.64514 | 0.64514 | 0.1 | 0 | 0.1 | Auto reset | Close | 0.0038462 | O2-26 | 235.0542 |  | WTG Breakdown Maintenance | 56413 | 235.0542
4970 | 2025-05-30 | 2025 | 2025 | 2025-05-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 5550 | Low hydraulic oil level | Break down | 0 | 0.0125 | 0.0125 | 0.3 | 0 | 0.3 | Check All Pipe after fill up oil after trail then reset and started wtg. | Close | 0.011538 | O2-07 | 656.3 |  | WTG Breakdown Maintenance | 52504 | 656.3
4971 | 2025-05-30 | 2025 | 2025 | 2025-05-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.43542 | 0.44097 | 0.44097 | 0.13333 | 0 | 0.13333 | Auto reset | Close | 0.0051282 | O2-07 | 291.6889 |  | WTG Unscheduled Maintenance | 52504 | 291.6889
4972 | 2025-05-30 | 2025 | 2025 | 2025-05-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.79722 | 0.81875 | 0.81875 | 0.51667 | 0 | 0.51667 | WTG Manual stop for PPC Software Updating work Done . | Close | 0.019872 | O2-07 | 1130.2944 |  | WTG Breakdown Maintenance | 52504 | 1130.2944
4973 | 2025-05-30 | 2025 | 2025 | 2025-05-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.092361 | 0.097222 | 0.097222 | 0.11667 | 0 | 0.11667 | Checked related error data log then reset & started WTG. | Close | 0.0044872 | O2-02 | 276.0042 |  | WTG Breakdown Maintenance | 56778 | 276.0042
4974 | 2025-05-30 | 2025 | 2025 | 2025-05-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.61389 | 0.63889 | 0.63889 | 0.6 | 0 | 0.6 | Check Related Error Data log after PPC Software Updating Work Donethen reset and started wtg | Close | 0.023077 | O2-02 | 1419.45 |  | WTG Breakdown Maintenance | 56778 | 1419.45
4975 | 2025-05-30 | 2025 | 2025 | 2025-05-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.70833 | 0.71181 | 0.71181 | 0.083333 | 0 | 0.083333 | Auto reset | Close | 0.0032051 | O2-02 | 197.1458 |  | WTG Unscheduled Maintenance | 56778 | 197.1458
4976 | 2025-05-30 | 2025 | 2025 | 2025-05-01 | 2 | O2_07 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.79722 | 0.81875 | 0.81875 | 0.51667 | 0 | 0.51667 | WTG Manual stop for PPC Software Updating work Done . | Close | 0.019872 | O2-04 | 1116.3229 |  | WTG Breakdown Maintenance | 51855 | 1116.3229
4977 | 2025-05-30 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.32014 | 0.32361 | 0.32361 | 0.083333 | 0 | 0.083333 | Checked related error data log then reset & started WTG. | Close | 0.0032051 | O2-26 | 195.8785 |  | WTG Breakdown Maintenance | 56413 | 195.8785
4978 | 2025-05-30 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Auto reset | 0.35903 | 0.36181 | 0.36181 | 0.066667 | 0 | 0.066667 | Auto reset | Close | 0.0025641 | O2-26 | 156.7028 |  | WTG Breakdown Maintenance | 56413 | 156.7028
4979 | 2025-05-30 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.51319 | 0.51875 | 0.51875 | 0.13333 | 0 | 0.13333 | Checked related error data log then reset & started WTG. | Close | 0.0051282 | O2-26 | 313.4056 |  | WTG Breakdown Maintenance | 56413 | 313.4056
4980 | 2025-05-30 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.88611 | 0.89514 | 0.89514 | 0.21667 | 0 | 0.21667 | check Event And Data log then reset & started wtg. | Close | 0.0083333 | O2-26 | 509.284 |  | WTG Breakdown Maintenance | 56413 | 509.284
4981 | 2025-05-30 | 2025 | 2025 | 2025-05-01 | 2 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.79792 | 0.81667 | 0.81667 | 0.45 | 0 | 0.45 | WTG Manual stop for PPC Software Updating work Done . | Close | 0.017308 | O2-03 | 1037.9437 |  | WTG Breakdown Maintenance | 55357 | 1037.9437
4982 | 2025-05-30 | 2025 | 2025 | 2025-05-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.79792 | 0.81597 | 0.81597 | 0.43333 | 0 | 0.43333 | WTG Manual stop for PPC Software Updating work Done . | Close | 0.016667 | O2-15 | 996.8292 |  | WTG Breakdown Maintenance | 55209 | 996.8292
4983 | 2025-05-30 | 2025 | 2025 | 2025-05-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Auto reset | 0.82569 | 0.82708 | 0.82708 | 0.033333 | 0 | 0.033333 | Auto reset | Close | 0.0012821 | O2-15 | 76.6792 |  | WTG Unscheduled Maintenance | 55209 | 76.6792
4984 | 2025-05-30 | 2025 | 2025 | 2025-05-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Auto reset | 0.67222 | 0.67431 | 0.67431 | 0.05 | 0 | 0.05 | Auto reset | Close | 0.0019231 | O2-14 | 114.7375 |  | WTG Unscheduled Maintenance | 55074 | 114.7375
4985 | 2025-05-30 | 2025 | 2025 | 2025-05-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down | 0.75903 | 0.77014 | 0.77014 | 0.26667 | 0 | 0.26667 | check Event And Data log then reset & started wtg. | Close | 0.010256 | O2-14 | 611.9333 |  | WTG Breakdown Maintenance | 55074 | 611.9333
4986 | 2025-05-30 | 2025 | 2025 | 2025-05-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.79931 | 0.81389 | 0.81389 | 0.35 | 0 | 0.35 | WTG Manual stop for PPC Software Updating work Done . | Close | 0.013462 | O2-14 | 803.1625 |  | WTG Breakdown Maintenance | 55074 | 803.1625
4987 | 2025-05-30 | 2025 | 2025 | 2025-05-01 | 2 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.79931 | 0.81181 | 0.81181 | 0.3 | 0 | 0.3 | WTG Manual stop for PPC Software Updating work Done . | Close | 0.011538 | O2-12 | 681.175 |  | WTG Breakdown Maintenance | 54494 | 681.175
4988 | 2025-05-30 | 2025 | 2025 | 2025-05-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.046528 | 0.11181 | 0.15278 | 1.5667 | 0.98333 | 2.55 | Attend and wtg check converter panel check PT100 Sensor , Replace All filter and clean Radiator after trail then reset and started wtg. | Close | 0.098077 | O2-22 | 6065.8125 |  | WTG Breakdown Maintenance | 57090 | 6065.8125
4989 | 2025-05-30 | 2025 | 2025 | 2025-05-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.49583 | 0.49861 | 0.49861 | 0.066667 | 0 | 0.066667 | check Event And Data log then reset & started wtg. | Close | 0.0025641 | O2-22 | 158.5833 |  | WTG Breakdown Maintenance | 57090 | 158.5833
4990 | 2025-05-30 | 2025 | 2025 | 2025-05-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.72361 | 0.73611 | 0.73611 | 0.3 | 0 | 0.3 | check Event And Data log then reset & started wtg. | Close | 0.011538 | O2-22 | 713.625 |  | WTG Breakdown Maintenance | 57090 | 713.625
4991 | 2025-05-30 | 2025 | 2025 | 2025-05-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down | 0.64236 | 0.65069 | 0.65069 | 0.2 | 0 | 0.2 | check Event And Data log then reset & started wtg. | Close | 0.0076923 | O2-06 | 459.1583 |  | WTG Breakdown Maintenance | 55099 | 459.1583
4992 | 2025-05-30 | 2025 | 2025 | 2025-05-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Auto reset | 0.55208 | 0.55278 | 0.55278 | 0.016667 | 0 | 0.016667 | Auto reset | Close | 0.00064103 | O2-07 | 36.4611 |  | WTG Unscheduled Maintenance | 52504 | 36.4611
4993 | 2025-05-30 | 2025 | 2025 | 2025-05-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Auto reset | 0.65139 | 0.65278 | 0.65278 | 0.033333 | 0 | 0.033333 | Auto reset | Close | 0.0012821 | O2-07 | 72.9222 |  | WTG Unscheduled Maintenance | 52504 | 72.9222
4994 | 2025-05-30 | 2025 | 2025 | 2025-05-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down | 0.75833 | 0.77014 | 0.77014 | 0.28333 | 0 | 0.28333 | check Event And Data log check temp then reset & started wtg. | Close | 0.010897 | O2-07 | 619.8389 |  | WTG Breakdown Maintenance | 52504 | 619.8389
4995 | 2025-05-30 | 2025 | 2025 | 2025-05-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 1731 | Oil temperature gearbox input high | Break down | 0.56806 | 0.575 | 0.575 | 0.16667 | 0 | 0.16667 | check Event And Data log check temp then reset & started wtg. | Close | 0.0064103 | O2-11 | 387.6736 |  | WTG Breakdown Maintenance | 55825 | 387.6736
4996 | 2025-05-30 | 2025 | 2025 | 2025-05-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 1731 | Oil temperature gearbox input high | Break down | 0.60139 | 0.6125 | 0.6125 | 0.26667 | 0 | 0.26667 | check Event And Data log check temp then reset & started wtg. | Close | 0.010256 | O2-11 | 620.2778 |  | WTG Breakdown Maintenance | 55825 | 620.2778
4997 | 2025-05-30 | 2025 | 2025 | 2025-05-01 | 2 | O2_24 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.42292 | 0.42708 | 0.42708 | 0.1 | 0 | 0.1 | Auto reset | Close | 0.0038462 | O2-20 | 224.9083 |  | WTG Unscheduled Maintenance | 53978 | 224.9083
4998 | 2025-05-30 | 2025 | 2025 | 2025-05-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down | 0.72569 | 0.73333 | 0.73333 | 0.18333 | 0 | 0.18333 | check Event And Data log check temp then reset & started wtg. | Close | 0.0070513 | O2-01 | 415.7236 |  | WTG Breakdown Maintenance | 54422 | 415.7236
4999 | 2025-05-30 | 2025 | 2025 | 2025-05-01 | 2 | O2_26 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.51111 | 0.51528 | 0.51528 | 0.1 | 0 | 0.1 | Auto reset | Close | 0.0038462 | O2-01 | 226.7583 |  | WTG Unscheduled Maintenance | 54422 | 226.7583
5000 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.55278 | 0.58819 | 0.58819 | 0.85 | 0 | 0.85 | Check event log and check hydraulic yaw brake pressure After Flushing mode on check pressure , both side Yawing manually and check cable twist after trail then reset and started wtg. | Close | 0.032692 | O2-26 | 1815.7417 |  | WTG Breakdown Maintenance | 51268 | 1815.7417
5001 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.63264 | 0.63681 | 0.63681 | 0.1 | 0 | 0.1 | Auto reset | Close | 0.0038462 | O2-26 | 213.6167 |  | WTG Unscheduled Maintenance | 51268 | 213.6167
5002 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.29583 | 0.29861 | 0.29861 | 0.066667 | 0 | 0.066667 | Auto reset | Close | 0.0025641 | O2-07 | 140.4083 |  | WTG Unscheduled Maintenance | 50547 | 140.4083
5003 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.52292 | 0.54375 | 0.54375 | 0.5 | 0 | 0.5 | Check event log and check hydraulic yaw brake pressure After trail then reset started wtg. | Close | 0.019231 | O2-07 | 1053.0625 |  | WTG Breakdown Maintenance | 50547 | 1053.0625
5004 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.60972 | 0.61389 | 0.61389 | 0.1 | 0 | 0.1 | Auto reset | Close | 0.0038462 | O2-07 | 210.6125 |  | WTG Unscheduled Maintenance | 50547 | 210.6125
5005 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Connectivity issue | 0.66736 | 0.71319 | 0.71319 | 1.1 | 0 | 1.1 | AFTER Feeder shutdown clear than wtg in Disconnected due to O2 07 VCB tripped so After charge than reset and start WTG. | Close | 0.042308 | O2-07 | 2316.7375 |  | WTG Breakdown Maintenance | 50547 | 2316.7375
5006 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 741 | Battery drive trigger by HC | Auto reset | 0.7875 | 0.78889 | 0.78889 | 0.033333 | 0 | 0.033333 | Auto reset | Close | 0.0012821 | O2-26 | 71.2056 |  | WTG Unscheduled Maintenance | 51268 | 71.2056
5007 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | 2 | O2_09 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.53403 | 0.53819 | 0.53819 | 0.1 | 0 | 0.1 | Auto reset | Close | 0.0038462 | O2-03 | 231.4458 |  | WTG Unscheduled Maintenance | 55547 | 231.4458
5008 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Auto reset | 0.70417 | 0.70556 | 0.70556 | 0.033333 | 0 | 0.033333 | Auto reset | Close | 0.0012821 | O2-15 | 73.3056 |  | WTG Unscheduled Maintenance | 52780 | 73.3056
5009 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Auto reset | 0.72569 | 0.72708 | 0.72708 | 0.033333 | 0 | 0.033333 | Auto resert | Close | 0.0012821 | O2-15 | 73.3056 |  | WTG Unscheduled Maintenance | 52780 | 73.3056
5010 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Break down | 0.82569 | 0.82917 | 0.82917 | 0.083333 | 0 | 0.083333 | check Event And Data log check temp then reset & started wtg. | Close | 0.0032051 | O2-15 | 183.2639 |  | WTG Unscheduled Maintenance | 52780 | 183.2639
5011 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.50694 | 0.51111 | 0.51111 | 0.1 | 0 | 0.1 | Auto reset | Close | 0.0038462 | O2-11 | 225.1542 |  | WTG Unscheduled Maintenance | 54037 | 225.1542
5012 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.525 | 0.54375 | 0.54375 | 0.45 | 0 | 0.45 | Check event log and check hydraulic yaw brake pressure and check cable twist removed After trail then reset started wtg. | Close | 0.017308 | O2-11 | 1013.1937 |  | WTG Breakdown Maintenance | 54037 | 1013.1937
5013 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.72917 | 0.73472 | 0.73472 | 0.13333 | 0 | 0.13333 | check Event And Data log check temp then reset & started wtg. | Close | 0.0051282 | O2-11 | 300.2056 |  | WTG Breakdown Maintenance | 54037 | 300.2056
5014 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | 2 | O2_16 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down | 0.72153 | 0.73056 | 0.73056 | 0.21667 | 0 | 0.21667 | check Event And Data log check temp then reset & started wtg. | Close | 0.0083333 | O2-21 | 427.1493 |  | WTG Breakdown Maintenance | 47315 | 427.1493
5015 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.57014 | 0.575 | 0.575 | 0.11667 | 0 | 0.11667 | Auto reset | Close | 0.0044872 | O2-06 | 231.0049 |  | WTG Unscheduled Maintenance | 47521 | 231.0049
5016 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | 2 | O2_20 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.49583 | 0.5 | 0.5 | 0.1 | 0 | 0.1 | Auto reset | Close | 0.0038462 | O2-24 | 196.4875 |  | WTG Unscheduled Maintenance | 47157 | 196.4875
5017 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.51806 | 0.52222 | 0.52222 | 0.1 | 0 | 0.1 | Auto reset | Close | 0.0038462 | O2-11 | 225.1542 |  | WTG Unscheduled Maintenance | 54037 | 225.1542
5018 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | 2 | O2_24 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Auto reset | 0.71736 | 0.71944 | 0.71944 | 0.05 | 0 | 0.05 | Auto reset | Close | 0.0019231 | O2-20 | 99.0979 |  | WTG Unscheduled Maintenance | 47567 | 99.0979
5019 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down | 0.68819 | 0.69861 | 0.69861 | 0.25 | 0 | 0.25 | check Event And Data log check temp then reset & started wtg. | Close | 0.0096154 | O2-01 | 565.9167 |  | WTG Breakdown Maintenance | 54328 | 565.9167
5020 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | 2 | O2_26 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.52222 | 0.52431 | 0.52431 | 0.05 | 0 | 0.05 | Auto reset | Close | 0.0019231 | O2-01 | 113.1833 |  | WTG Unscheduled Maintenance | 54328 | 113.1833
5021 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.57222 | 0.57639 | 0.57639 | 0.1 | 0 | 0.1 | Auto reset | Close | 0.0038462 | O2-15 | 219.9167 |  | WTG Unscheduled Maintenance | 52780 | 219.9167
5022 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.62153 | 0.62222 | 0.62222 | 0.016667 | 0 | 0.016667 | Auto reset | Close | 0.00064103 | O2-15 | 36.6528 |  | WTG Unscheduled Maintenance | 52780 | 36.6528
5023 | 2025-06-01 | 2025 | 2025 | 2025-06-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.74167 | 0.74167 | 0.74583 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-26 | 210.8701 |  | WTG Unscheduled Maintenance | 50608.8333 | 210.8701
5024 | 2025-06-01 | 2025 | 2025 | 2025-06-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.475 | 0.475 | 0.47778 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0025641 | O2-07 | 142.813 |  | WTG Unscheduled Maintenance | 51412.6667 | 142.813
5025 | 2025-06-01 | 2025 | 2025 | 2025-06-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.49514 | 0.49514 | 0.49931 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-07 | 214.2194 |  | WTG Unscheduled Maintenance | 51412.6667 | 214.2194
5026 | 2025-06-01 | 2025 | 2025 | 2025-06-01 | 2 | O2_06 | TQGXIIPL | GEDA | 3.846% | 4540 | Tower oscillation X level 2 | Auto reset | 0.51736 | 0.51736 | 0.52917 | 0 | 0.28333 | 0.28333 | Auto reset | Close | 0.010897 | O2-21 | 623.776 |  | WTG Unscheduled Maintenance | 52837.5 | 623.776
5027 | 2025-06-01 | 2025 | 2025 | 2025-06-01 | 2 | O2_09 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset | 0.69861 | 0.69861 | 0.70903 | 0 | 0.25 | 0.25 | Auto reset | Close | 0.0096154 | O2-03 | 507.3264 |  | WTG Unscheduled Maintenance | 48703.3333 | 507.3264
5028 | 2025-06-01 | 2025 | 2025 | 2025-06-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.51181 | 0.51181 | 0.51597 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-15 | 226.9368 |  | WTG Unscheduled Maintenance | 54464.8333 | 226.9368
5029 | 2025-06-01 | 2025 | 2025 | 2025-06-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.67222 | 0.67222 | 0.67569 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0032051 | O2-12 | 170.3501 |  | WTG Unscheduled Maintenance | 49060.8333 | 170.3501
5030 | 2025-06-01 | 2025 | 2025 | 2025-06-01 | 2 | O2_12 | TQGXIIPL | GEDA | 3.846% | 4540 | Tower oscillation X level 2 | Auto reset | 0.63611 | 0.63611 | 0.64583 | 0 | 0.23333 | 0.23333 | Auto reset | Close | 0.0089744 | O2-14 | 484.6965 |  | WTG Unscheduled Maintenance | 49854.5 | 484.6965
5031 | 2025-06-01 | 2025 | 2025 | 2025-06-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.46389 | 0.46389 | 0.46736 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0032051 | O2-11 | 179.1563 |  | WTG Unscheduled Maintenance | 51597 | 179.1563
5032 | 2025-06-01 | 2025 | 2025 | 2025-06-01 | 2 | O2_14 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.55139 | 0.55139 | 0.55556 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-12 | 204.4201 |  | WTG Unscheduled Maintenance | 49060.8333 | 204.4201
5033 | 2025-06-01 | 2025 | 2025 | 2025-06-01 | 2 | O2_14 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.5625 | 0.5625 | 0.56806 | 0 | 0.13333 | 0.13333 | Auto reset | Close | 0.0051282 | O2-12 | 272.5602 |  | WTG Unscheduled Maintenance | 49060.8333 | 272.5602
5034 | 2025-06-01 | 2025 | 2025 | 2025-06-01 | 2 | O2_14 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset | 0.67917 | 0.67917 | 0.69236 | 0 | 0.31667 | 0.31667 | Auto reset | Close | 0.012179 | O2-12 | 647.3304 |  | WTG Unscheduled Maintenance | 49060.8333 | 647.3304
5035 | 2025-06-01 | 2025 | 2025 | 2025-06-01 | 2 | O2_16 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset | 0.5375 | 0.5375 | 0.54861 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | O2-21 | 587.0833 |  | WTG Unscheduled Maintenance | 52837.5 | 587.0833
5036 | 2025-06-01 | 2025 | 2025 | 2025-06-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.58333 | 0.58333 | 0.625 | 0 | 1 | 1 | check Event and Data log Temp high then temp is normalize then apply shoft reboot then reset & started wtg. | Close | 0.038462 | O2-22 | 2342.875 |  | WTG Unscheduled Maintenance | 56229 | 2342.875
5037 | 2025-06-01 | 2025 | 2025 | 2025-06-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset | 0.53472 | 0.53472 | 0.54514 | 0 | 0.25 | 0.25 | Auto reset | Close | 0.0096154 | O2-07 | 535.5486 |  | WTG Unscheduled Maintenance | 51412.6667 | 535.5486
5038 | 2025-06-01 | 2025 | 2025 | 2025-06-01 | 2 | O2_20 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.51597 | 0.51597 | 0.52153 | 0 | 0.13333 | 0.13333 | Auto reset | Close | 0.0051282 | O2-24 | 296.6157 |  | WTG Unscheduled Maintenance | 53390.8333 | 296.6157
5039 | 2025-06-01 | 2025 | 2025 | 2025-06-01 | 2 | O2_21 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset | 0.56528 | 0.56528 | 0.57639 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | O2-06 | 581.0241 |  | WTG Unscheduled Maintenance | 52292.1667 | 581.0241
5040 | 2025-06-01 | 2025 | 2025 | 2025-06-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.48889 | 0.48889 | 0.49028 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2-11 | 71.6625 |  | WTG Unscheduled Maintenance | 51597 | 71.6625
5041 | 2025-06-01 | 2025 | 2025 | 2025-06-01 | 2 | O2_24 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.52222 | 0.52222 | 0.52639 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-20 | 223.7208 |  | WTG Unscheduled Maintenance | 53693 | 223.7208
5042 | 2025-06-01 | 2025 | 2025 | 2025-06-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.11736 | 0.11736 | 0.12292 | 0 | 0.13333 | 0.13333 | check Event and Data log then reset & started wtg. | Close | 0.0051282 | O2-01 | 281.612 |  | WTG Unscheduled Maintenance | 50690.1667 | 281.612
5043 | 2025-06-01 | 2025 | 2025 | 2025-06-01 | 2 | O2_26 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.63125 | 0.63125 | 0.63542 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-01 | 211.209 |  | WTG Unscheduled Maintenance | 50690.1667 | 211.209
5044 | 2025-06-01 | 2025 | 2025 | 2025-06-01 | 2 | O2_26 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset | 0.70486 | 0.70486 | 0.71181 | 0 | 0.16667 | 0.16667 | Auto reset | Close | 0.0064103 | O2-01 | 352.015 |  | WTG Unscheduled Maintenance | 50690.1667 | 352.015
5045 | 2025-06-02 | 2025 | 2025 | 2025-06-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.51111 | 0.51111 | 0.5125 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2-26 | 62.0137 |  | WTG Unscheduled Maintenance | 44649.8333 | 62.0137
5046 | 2025-06-02 | 2025 | 2025 | 2025-06-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.52361 | 0.52361 | 0.52778 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-07 | 180.6056 |  | WTG Unscheduled Maintenance | 43345.3333 | 180.6056
5047 | 2025-06-02 | 2025 | 2025 | 2025-06-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.67708 | 0.67708 | 0.71736 | 0 | 0.96667 | 0.96667 | check Event and Data log Temp high them temp is normalize then apply shoft reboot then reset & started wtg. | Close | 0.037179 | O2-02 | 1765.3079 |  | WTG Unscheduled Maintenance | 43828.3333 | 1765.3079
5048 | 2025-06-02 | 2025 | 2025 | 2025-06-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Auto reset | 0.75972 | 0.75972 | 0.77083 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | O2-02 | 486.9815 |  | WTG Unscheduled Maintenance | 43828.3333 | 486.9815
5049 | 2025-06-02 | 2025 | 2025 | 2025-06-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.90764 | 0.90764 | 0.91736 | 0 | 0.23333 | 0.23333 | check Event and Data log then apply shoft reboot then reset & started wtg. | Close | 0.0089744 | O2-02 | 426.1088 |  | WTG Unscheduled Maintenance | 43828.3333 | 426.1088
5050 | 2025-06-02 | 2025 | 2025 | 2025-06-01 | 2 | O2_06 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.77778 | 0.77778 | 0.78194 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-21 | 200.0972 |  | WTG Unscheduled Maintenance | 48023.3333 | 200.0972
5051 | 2025-06-02 | 2025 | 2025 | 2025-06-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Auto reset | 0.57153 | 0.57153 | 0.57222 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | O2-26 | 31.0068 |  | WTG Unscheduled Maintenance | 44649.8333 | 31.0068
5052 | 2025-06-02 | 2025 | 2025 | 2025-06-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.64028 | 0.64028 | 0.64444 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-26 | 186.041 |  | WTG Unscheduled Maintenance | 44649.8333 | 186.041
5053 | 2025-06-02 | 2025 | 2025 | 2025-06-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Auto reset | 0.67153 | 0.67153 | 0.67292 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2-26 | 62.0137 |  | WTG Unscheduled Maintenance | 44649.8333 | 62.0137
5054 | 2025-06-02 | 2025 | 2025 | 2025-06-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset | 0.69097 | 0.69097 | 0.70208 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | O2-26 | 496.1093 |  | WTG Unscheduled Maintenance | 44649.8333 | 496.1093
5055 | 2025-06-02 | 2025 | 2025 | 2025-06-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.90417 | 0.90417 | 0.90833 | 0 | 0.1 | 0.1 | check Event and Data log reset & started wtg. | Close | 0.0038462 | O2-26 | 186.041 |  | WTG Unscheduled Maintenance | 44649.8333 | 186.041
5056 | 2025-06-02 | 2025 | 2025 | 2025-06-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.70278 | 0.70278 | 0.70694 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-11 | 183.8806 |  | WTG Unscheduled Maintenance | 44131.3333 | 183.8806
5057 | 2025-06-02 | 2025 | 2025 | 2025-06-01 | 2 | O2_14 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.58819 | 0.58819 | 0.59236 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-12 | 178.5181 |  | WTG Unscheduled Maintenance | 42844.3333 | 178.5181
5058 | 2025-06-02 | 2025 | 2025 | 2025-06-01 | 2 | O2_15 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.73333 | 0.73333 | 0.73542 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | O2-10 | 89.6972 |  | WTG Unscheduled Maintenance | 43054.6667 | 89.6972
5059 | 2025-06-02 | 2025 | 2025 | 2025-06-01 | 2 | O2_16 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Auto reset | 0.41944 | 0.41944 | 0.42361 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-21 | 200.0972 |  | WTG Unscheduled Maintenance | 48023.3333 | 200.0972
5060 | 2025-06-02 | 2025 | 2025 | 2025-06-01 | 2 | O2_16 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.48681 | 0.48681 | 0.49097 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-21 | 200.0972 |  | WTG Unscheduled Maintenance | 48023.3333 | 200.0972
5061 | 2025-06-02 | 2025 | 2025 | 2025-06-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.8125 | 0.8125 | 0.83264 | 0 | 0.48333 | 0.48333 | check Event and Data log Temp high then temp is normalize then apply shoft reboot then reset & started wtg. | Close | 0.01859 | O2-22 | 1027.5465 |  | WTG Unscheduled Maintenance | 51023 | 1027.5465
5062 | 2025-06-02 | 2025 | 2025 | 2025-06-01 | 2 | O2_20 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.57014 | 0.57014 | 0.57431 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-24 | 191.7556 |  | WTG Unscheduled Maintenance | 46021.3333 | 191.7556
5063 | 2025-06-02 | 2025 | 2025 | 2025-06-01 | 2 | O2_21 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.55903 | 0.55903 | 0.5625 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0032051 | O2-06 | 165.7326 |  | WTG Unscheduled Maintenance | 47731 | 165.7326
5064 | 2025-06-02 | 2025 | 2025 | 2025-06-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Auto reset | 0.59931 | 0.59931 | 0.6125 | 0 | 0.31667 | 0.31667 | Auto reset | Close | 0.012179 | O2-11 | 582.2884 |  | WTG Unscheduled Maintenance | 44131.3333 | 582.2884
5065 | 2025-06-03 | 2025 | 2025 | 2025-06-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.57778 | 0.57778 | 0.58194 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-26 | 161.374 |  | WTG Unscheduled Maintenance | 38729.76 | 161.374
5066 | 2025-06-03 | 2025 | 2025 | 2025-06-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.66667 | 0.66667 | 0.66806 | 0 | 0.033333 | 0.033333 | check Event And Data log then reset & started wtg. | Close | 0.0012821 | O2-26 | 53.7913 |  | WTG Unscheduled Maintenance | 38729.76 | 53.7913
5067 | 2025-06-03 | 2025 | 2025 | 2025-06-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.53889 | 0.53889 | 0.54514 | 0 | 0.15 | 0.15 | check Event And Data log then reset & started wtg. | Close | 0.0057692 | O2-07 | 249.4515 |  | WTG Unscheduled Maintenance | 39912.24 | 249.4515
5068 | 2025-06-03 | 2025 | 2025 | 2025-06-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Break down | 0.54653 | 0.54653 | 0.54792 | 0 | 0.033333 | 0.033333 | During Battery test occurred error so check Event And Data log then reset & started wtg. | Close | 0.0012821 | O2-07 | 55.4337 |  | WTG Unscheduled Maintenance | 39912.24 | 55.4337
5069 | 2025-06-03 | 2025 | 2025 | 2025-06-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.625 | 0.625 | 0.62917 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-07 | 166.301 |  | WTG Unscheduled Maintenance | 39912.24 | 166.301
5070 | 2025-06-03 | 2025 | 2025 | 2025-06-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.45833 | 0.45833 | 0.46111 | 0 | 0.066667 | 0.066667 | check Event And Data log then reset & started wtg. | Close | 0.0025641 | O2-02 | 113.388 |  | WTG Unscheduled Maintenance | 40819.68 | 113.388
5071 | 2025-06-03 | 2025 | 2025 | 2025-06-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.64236 | 0.64236 | 0.64375 | 0 | 0.033333 | 0.033333 | check Event And Data log then reset & started wtg. | Close | 0.0012821 | O2-02 | 56.694 |  | WTG Unscheduled Maintenance | 40819.68 | 56.694
5072 | 2025-06-03 | 2025 | 2025 | 2025-06-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.71528 | 0.71875 | 0.77083 | 0.083333 | 1.25 | 1.3333 | Attend and check Convertor in found Ambient control Temp. high so check in convertor panel PT100 value and found loose connection in TB so tightly properly and started Turbine. | Close | 0.051282 | O2-02 | 2267.76 |  | WTG Breakdown Maintenance | 40819.68 | 2267.76
5073 | 2025-06-03 | 2025 | 2025 | 2025-06-01 | 2 | O2_06 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset | 0.59722 | 0.59722 | 0.60833 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | O2-21 | 488.4027 |  | WTG Unscheduled Maintenance | 43956.24 | 488.4027
5074 | 2025-06-03 | 2025 | 2025 | 2025-06-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.44653 | 0.44653 | 0.45069 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-15 | 170.386 |  | WTG Unscheduled Maintenance | 40892.64 | 170.386
5075 | 2025-06-03 | 2025 | 2025 | 2025-06-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset | 0.53194 | 0.53194 | 0.54306 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | O2-12 | 447.92 |  | WTG Unscheduled Maintenance | 40312.8 | 447.92
5076 | 2025-06-03 | 2025 | 2025 | 2025-06-01 | 2 | O2_15 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset | 0.63542 | 0.63542 | 0.64653 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | O2-10 | 445.3707 |  | WTG Unscheduled Maintenance | 40083.36 | 445.3707
5077 | 2025-06-03 | 2025 | 2025 | 2025-06-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.71944 | 0.71944 | 0.74514 | 0 | 0.61667 | 0.61667 | check Event and Data log Temp high then temp is normalize then apply shoft reboot then reset & started wtg. | Close | 0.023718 | O2-22 | 1223.8613 |  | WTG Unscheduled Maintenance | 47631.36 | 1223.8613
5078 | 2025-06-03 | 2025 | 2025 | 2025-06-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down | 0.63056 | 0.63056 | 0.63611 | 0 | 0.13333 | 0.13333 | check Event And Data log then reset & started wtg. | Close | 0.0051282 | O2-07 | 221.7347 |  | WTG Unscheduled Maintenance | 39912.24 | 221.7347
5079 | 2025-06-03 | 2025 | 2025 | 2025-06-01 | 2 | O2_20 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.63542 | 0.63542 | 0.63958 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-24 | 177.946 |  | WTG Unscheduled Maintenance | 42707.04 | 177.946
5080 | 2025-06-03 | 2025 | 2025 | 2025-06-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.39306 | 0.39306 | 0.39722 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-11 | 162.771 |  | WTG Unscheduled Maintenance | 39065.04 | 162.771
5081 | 2025-06-03 | 2025 | 2025 | 2025-06-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.47014 | 0.47014 | 0.47361 | 0 | 0.083333 | 0.083333 | check Event And Data log then reset & started wtg. | Close | 0.0032051 | O2-11 | 135.6425 |  | WTG Unscheduled Maintenance | 39065.04 | 135.6425
5082 | 2025-06-03 | 2025 | 2025 | 2025-06-01 | 2 | O2_24 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset | 0.65069 | 0.65069 | 0.66181 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | O2-20 | 470.9787 |  | WTG Unscheduled Maintenance | 42388.08 | 470.9787
5083 | 2025-06-03 | 2025 | 2025 | 2025-06-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.55208 | 0.55208 | 0.55625 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-01 | 163.752 |  | WTG Unscheduled Maintenance | 39300.48 | 163.752
5084 | 2025-06-03 | 2025 | 2025 | 2025-06-01 | 2 | O2_26 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset | 0.47222 | 0.47222 | 0.48333 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | O2-01 | 436.672 |  | WTG Unscheduled Maintenance | 39300.48 | 436.672
5085 | 2025-06-03 | 2025 | 2025 | 2025-06-01 | 2 | O2_26 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.59028 | 0.59028 | 0.59444 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-01 | 163.752 |  | WTG Unscheduled Maintenance | 39300.48 | 163.752
5086 | 2025-06-04 | 2025 | 2025 | 2025-06-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 177 | SLC MF blade regulation control | Break down | 0.38542 | 0.38542 | 0.3875 | 0 | 0.05 | 0.05 | check Event And Data log then reset & started wtg. | Close | 0.0019231 | O2-07 | 50.5958 |  | WTG Unscheduled Maintenance | 24286 | 50.5958
5087 | 2025-06-04 | 2025 | 2025 | 2025-06-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.60764 | 0.60764 | 0.60833 | 0 | 0.016667 | 0.016667 | check Event And Data log then reset & started wtg. | Close | 0.00064103 | O2-07 | 16.8653 |  | WTG Unscheduled Maintenance | 24286 | 16.8653
5088 | 2025-06-04 | 2025 | 2025 | 2025-06-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.53056 | 0.53056 | 0.53472 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-02 | 107.3292 |  | WTG Unscheduled Maintenance | 25759 | 107.3292
5089 | 2025-06-04 | 2025 | 2025 | 2025-06-01 | 2 | O2_06 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset | 0.60278 | 0.60278 | 0.61389 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | O2-21 | 295.5333 |  | WTG Unscheduled Maintenance | 26598 | 295.5333
5090 | 2025-06-04 | 2025 | 2025 | 2025-06-01 | 2 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.64514 | 0.64514 | 0.65139 | 0 | 0.15 | 0.15 | Bottom Panel Inspection work done than started Turbine. | Close | 0.0057692 | O2-21 | 166.2375 |  | WTG Unscheduled Maintenance | 26598 | 166.2375
5091 | 2025-06-04 | 2025 | 2025 | 2025-06-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.56042 | 0.56042 | 0.56458 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-26 | 112.3333 |  | WTG Unscheduled Maintenance | 26960 | 112.3333
5092 | 2025-06-04 | 2025 | 2025 | 2025-06-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset | 0.46458 | 0.46458 | 0.47569 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | O2-15 | 286.5444 |  | WTG Unscheduled Maintenance | 25789 | 286.5444
5093 | 2025-06-04 | 2025 | 2025 | 2025-06-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6601 | Wind.dir. diff. level 1 | Break down | 0.47569 | 0.47569 | 0.47708 | 0 | 0.033333 | 0.033333 | check Event And Data log then reset & started wtg. | Close | 0.0012821 | O2-15 | 35.8181 |  | WTG Unscheduled Maintenance | 25789 | 35.8181
5094 | 2025-06-04 | 2025 | 2025 | 2025-06-01 | 2 | O2_15 | TQGXIIPL | GEDA | 3.846% | 780 | Error bridging start-up | Break down | 0.50764 | 0.50764 | 0.51042 | 0 | 0.066667 | 0.066667 | During Battery test occurred error so check Event And Data log then reset & started wtg. | Close | 0.0025641 | O2-10 | 69.5639 |  | WTG Unscheduled Maintenance | 25043 | 69.5639
5095 | 2025-06-04 | 2025 | 2025 | 2025-06-01 | 2 | O2_20 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.64583 | 0.64583 | 0.64861 | 0 | 0.066667 | 0.066667 | check Event And Data log then reset & started wtg. | Close | 0.0025641 | O2-24 | 75.5833 |  | WTG Unscheduled Maintenance | 27210 | 75.5833
5096 | 2025-06-05 | 2025 | 2025 | 2025-06-01 | 2 | O2_02 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.46111 | 0.46111 | 0.47083 | 0 | 0.23333 | 0.23333 | check Event And Data log then reset & started wtg. | Close | 0.0089744 | O2-05 | 160.5625 |  | WTG Unscheduled Maintenance | 16515 | 160.5625
5097 | 2025-06-05 | 2025 | 2025 | 2025-06-01 | 2 | O2_02 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.48194 | 0.48194 | 0.48611 | 0 | 0.1 | 0.1 | check Event And Data log then reset & started wtg. | Close | 0.0038462 | O2-05 | 68.8125 |  | WTG Unscheduled Maintenance | 16515 | 68.8125
5098 | 2025-06-05 | 2025 | 2025 | 2025-06-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 177 | SLC MF blade regulation control | Break down | 0.36944 | 0.36944 | 0.38125 | 0 | 0.28333 | 0.28333 | check Event And Data log then reset & started wtg. | Close | 0.010897 | O2-07 | 143.284 |  | WTG Unscheduled Maintenance | 12137 | 143.284
5099 | 2025-06-05 | 2025 | 2025 | 2025-06-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Break down | 0.47569 | 0.47569 | 0.48889 | 0 | 0.31667 | 0.31667 | check Event And Data log then reset & started wtg. | Close | 0.012179 | O2-07 | 160.141 |  | WTG Unscheduled Maintenance | 12137 | 160.141
5100 | 2025-06-05 | 2025 | 2025 | 2025-06-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Break down | 0.51319 | 0.55417 | 0.70139 | 0.98333 | 3.5333 | 4.5167 | Attend and wtg check Axis No 3 so found Pitch Encoder cable connection loose after tight and Repeated error occurred check found Axis no 1 flat resistor failure found after replace then trail so ok after winch load test completed then reset and started wtg. | Close | 0.17372 | O2-07 | 2284.116 |  | WTG Unscheduled Maintenance | 12137 | 2284.116
5101 | 2025-06-05 | 2025 | 2025 | 2025-06-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Auto reset | 0.8375 | 0.8375 | 0.83819 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | O2-15 | 9.6583 |  | WTG Unscheduled Maintenance | 13908 | 9.6583
5102 | 2025-06-05 | 2025 | 2025 | 2025-06-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Auto reset | 0.82847 | 0.82847 | 0.82986 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2-11 | 19.7 |  | WTG Unscheduled Maintenance | 14184 | 19.7
5103 | 2025-06-05 | 2025 | 2025 | 2025-06-01 | 2 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Auto reset | 0.76319 | 0.76319 | 0.76389 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | O2-06 | 11.6465 |  | WTG Unscheduled Maintenance | 16771 | 11.6465
5104 | 2025-06-05 | 2025 | 2025 | 2025-06-01 | 2 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Auto reset | 0.76667 | 0.76667 | 0.77083 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-06 | 69.8792 |  | WTG Unscheduled Maintenance | 16771 | 69.8792
5104 | 2025-06-05 | 2025 | 2025 | 2025-06-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Auto reset | 0.74792 | 0.74792 | 0.74931 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | O2-07 | 16.8569 |  | WTG Unscheduled Maintenance | 12137 | 16.8569
5105 | 2025-06-06 | 2025 | 2025 | 2025-06-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset | 0.80625 | 0.80625 | 0.81736 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | O2-26 | 262.7889 |  | WTG Unscheduled Maintenance | 23651 | 262.7889
5106 | 2025-06-06 | 2025 | 2025 | 2025-06-01 | 2 | O2_03 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Break down | 0.49514 | 0.57639 | 0.7375 | 1.95 | 3.8667 | 5.8167 | Attend and WTG check event log and snap found encoder value deviation Axis No.1 so we have check QA001 contactor manually operate but not pickup after check all connection check rectifier fuse and Diode and QA001 Contactor NO/NC Auxiliry switch check so found NO switch not proper working after all connection check and tight then we have take trail turbine after No any abnormality so started WTG. | Close | 0.22372 | O2-09 | 5555.4014 |  | WTG Breakdown Maintenance | 22922 | 5555.4014
5107 | 2025-06-06 | 2025 | 2025 | 2025-06-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.79444 | 0.79444 | 0.79861 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-07 | 100.5167 |  | WTG Unscheduled Maintenance | 24124 | 100.5167
5108 | 2025-06-06 | 2025 | 2025 | 2025-06-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset | 0.78056 | 0.78056 | 0.79167 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | O2-02 | 311.2333 |  | WTG Unscheduled Maintenance | 28011 | 311.2333
5109 | 2025-06-06 | 2025 | 2025 | 2025-06-01 | 2 | O2_07 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.5625 | 0.5625 | 0.58542 | 0 | 0.55 | 0.55 | check Event and Data log also check error related Perameter then apply shoft reboot then reset & started wtg. | Close | 0.021154 | O2-04 | 595.6271 |  | WTG Unscheduled Maintenance | 25991 | 595.6271
5110 | 2025-06-06 | 2025 | 2025 | 2025-06-01 | 2 | O2_09 | TQGXIIPL | GEDA | 3.846% | 4540 | Tower oscillation X level 2 | Auto reset | 0.80208 | 0.80208 | 0.81319 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | O2-03 | 238.4556 |  | WTG Unscheduled Maintenance | 21461 | 238.4556
5111 | 2025-06-06 | 2025 | 2025 | 2025-06-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 687 | Power failure pitch | Break down | 0.69306 | 0.70833 | 0.8125 | 0.36667 | 2.5 | 2.8667 | Check error related ckt tha found Hub supply 400V MCB tripped so check before and after related ckt nothing found abnormal so charge MCB and reset and started Turbine. | Close | 0.11026 | O2-11 | 2535.925 |  | WTG Breakdown Maintenance | 21231 | 2535.925
5112 | 2025-06-06 | 2025 | 2025 | 2025-06-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset | 0.74792 | 0.74792 | 0.75903 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | O2-22 | 247.4111 |  | WTG Unscheduled Maintenance | 22267 | 247.4111
5113 | 2025-06-06 | 2025 | 2025 | 2025-06-01 | 2 | O2_21 | TQGXIIPL | GEDA | 3.846% | 4540 | Tower oscillation X level 2 | Break down | 0.7625 | 0.7625 | 0.77153 | 0 | 0.21667 | 0.21667 | check Event And Data log then reset & started wtg. | Close | 0.0083333 | O2-06 | 189.6736 |  | WTG Unscheduled Maintenance | 21010 | 189.6736
5114 | 2025-06-06 | 2025 | 2025 | 2025-06-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.51667 | 0.51667 | 0.52431 | 0 | 0.18333 | 0.18333 | check Event And Data log then reset & started wtg. | Close | 0.0070513 | O2-11 | 162.1812 |  | WTG Unscheduled Maintenance | 21231 | 162.1812
5115 | 2025-06-06 | 2025 | 2025 | 2025-06-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.57847 | 0.57847 | 0.58611 | 0 | 0.18333 | 0.18333 | check Event and Data log also check error related Perameter then apply shoft reboot then reset & started wtg. | Close | 0.0070513 | O2-11 | 162.1812 |  | WTG Unscheduled Maintenance | 21231 | 162.1812
5116 | 2025-06-06 | 2025 | 2025 | 2025-06-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.74236 | 0.74236 | 0.75486 | 0 | 0.3 | 0.3 | check Event and Data log also check error related Perameter then apply shoft reboot then reset & started wtg. | Close | 0.011538 | O2-11 | 265.3875 |  | WTG Unscheduled Maintenance | 21231 | 265.3875
5117 | 2025-06-06 | 2025 | 2025 | 2025-06-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 6300 | Yaw error | Break down | 0.78333 | 0.78333 | 0.78472 | 0 | 0.033333 | 0.033333 | check Event And Data log then reset & started wtg. | Close | 0.0012821 | O2-11 | 29.4875 |  | WTG Unscheduled Maintenance | 21231 | 29.4875
5118 | 2025-06-06 | 2025 | 2025 | 2025-06-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0.975 | 0.975 | 1899-12-31 | 0 | 0.6 | 0.6 | Attend and check HPU Unit 9.1 and 9.7 Valve also check yaw System Pressure than wip, | Close | 0.023077 | O2-11 | 530.775 |  | WTG Breakdown Maintenance | 21231 | 530.775
5119 | 2025-06-07 | 2025 | 2025 | 2025-06-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.60625 | 0.60625 | 0.61042 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-26 | 151.4208 |  | WTG Unscheduled Maintenance | 36341 | 151.4208
5120 | 2025-06-07 | 2025 | 2025 | 2025-06-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Customer | 0.43194 | 0.43194 | 0.48194 | 0 | 1.2 | 1.2 | Shutdown taken by GETCO Team for GETCO Tower line Dismentaling Work. | Close | 0.046154 | O2-07 | 1477.6 |  | WTG Breakdown Maintenance | 29552 | 1477.6
5121 | 2025-06-07 | 2025 | 2025 | 2025-06-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Customer | 0.51944 | 0.51944 | 0.53542 | 0 | 0.38333 | 0.38333 | Shutdown taken by GETCO Team for GETCO Tower line Dismentaling Work. | Close | 0.014744 | O2-07 | 472.0111 |  | WTG Breakdown Maintenance | 29552 | 472.0111
5122 | 2025-06-07 | 2025 | 2025 | 2025-06-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Customer | 0.70278 | 0.70278 | 0.71806 | 0 | 0.36667 | 0.36667 | Shutdown taken by GETCO Team for GETCO Tower line Dismentaling Work. | Close | 0.014103 | O2-07 | 451.4889 |  | WTG Breakdown Maintenance | 29552 | 451.4889
5123 | 2025-06-07 | 2025 | 2025 | 2025-06-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.74167 | 0.74167 | 0.74583 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-02 | 163.5375 |  | WTG Unscheduled Maintenance | 39249 | 163.5375
5124 | 2025-06-07 | 2025 | 2025 | 2025-06-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.9125 | 0.9125 | 0.91944 | 0 | 0.16667 | 0.16667 | check Event And Data log then reset & started wtg. | Close | 0.0064103 | O2-02 | 272.5625 |  | WTG Unscheduled Maintenance | 39249 | 272.5625
5125 | 2025-06-07 | 2025 | 2025 | 2025-06-01 | 2 | O2_07 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Customer | 0.43194 | 0.43194 | 0.48194 | 0 | 1.2 | 1.2 | Shutdown taken by GETCO Team for GETCO Tower line Dismentaling Work. | Close | 0.046154 | O2-04 | 1864.05 |  | WTG Breakdown Maintenance | 37281 | 1864.05
5126 | 2025-06-07 | 2025 | 2025 | 2025-06-01 | 2 | O2_07 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Customer | 0.51944 | 0.51944 | 0.71944 | 0 | 4.8 | 4.8 | Shutdown taken by GETCO Team for GETCO Tower line Dismentaling Work. | Close | 0.18462 | O2-04 | 7456.2 |  | WTG Breakdown Maintenance | 37281 | 7456.2
5127 | 2025-06-07 | 2025 | 2025 | 2025-06-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.57153 | 0.57153 | 0.57569 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-26 | 151.4208 |  | WTG Unscheduled Maintenance | 36341 | 151.4208
5128 | 2025-06-07 | 2025 | 2025 | 2025-06-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 53 | Wind dir.dev. level 1 | Break down | 0.6125 | 0.6125 | 0.61319 | 0 | 0.016667 | 0.016667 | check Event And Data log then reset & started wtg. | Close | 0.00064103 | O2-26 | 25.2368 |  | WTG Unscheduled Maintenance | 36341 | 25.2368
5129 | 2025-06-07 | 2025 | 2025 | 2025-06-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.62222 | 0.62222 | 0.62708 | 0 | 0.11667 | 0.11667 | check Event And Data log then reset & started wtg. | Close | 0.0044872 | O2-26 | 176.6576 |  | WTG Unscheduled Maintenance | 36341 | 176.6576
5130 | 2025-06-07 | 2025 | 2025 | 2025-06-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 6056 | High yaw load | Break down | 0.58403 | 0.58403 | 0.58611 | 0 | 0.05 | 0.05 | check Event And Data log then reset & started wtg. | Close | 0.0019231 | O2-12 | 67.9708 |  | WTG Unscheduled Maintenance | 32626 | 67.9708
5131 | 2025-06-07 | 2025 | 2025 | 2025-06-01 | 2 | O2_14 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.60486 | 0.60486 | 0.60903 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-12 | 135.9417 |  | WTG Unscheduled Maintenance | 32626 | 135.9417
5132 | 2025-06-07 | 2025 | 2025 | 2025-06-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Customer | 0.43194 | 0.43194 | 0.48194 | 0 | 1.2 | 1.2 | Shutdown taken by GETCO Team for GETCO Tower line Dismentaling Work. | Close | 0.046154 | O2-07 | 1477.6 |  | WTG Breakdown Maintenance | 29552 | 1477.6
5133 | 2025-06-07 | 2025 | 2025 | 2025-06-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Customer | 0.51944 | 0.51944 | 0.53403 | 0 | 0.35 | 0.35 | Shutdown taken by GETCO Team for GETCO Tower line Dismentaling Work. | Close | 0.013462 | O2-07 | 430.9667 |  | WTG Breakdown Maintenance | 29552 | 430.9667
5134 | 2025-06-07 | 2025 | 2025 | 2025-06-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Customer | 0.70278 | 0.70278 | 0.71806 | 0 | 0.36667 | 0.36667 | Shutdown taken by GETCO Team for GETCO Tower line Dismentaling Work. | Close | 0.014103 | O2-07 | 451.4889 |  | WTG Breakdown Maintenance | 29552 | 451.4889
5135 | 2025-06-07 | 2025 | 2025 | 2025-06-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 4540 | Tower oscillation X level 2 | Break down | 0.77708 | 0.77708 | 0.78333 | 0 | 0.15 | 0.15 | check Event And Data log then reset & started wtg. | Close | 0.0057692 | O2-07 | 184.7 |  | WTG Unscheduled Maintenance | 29552 | 184.7
5136 | 2025-06-07 | 2025 | 2025 | 2025-06-01 | 2 | O2_21 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.61111 | 0.61111 | 0.61528 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-06 | 148.325 |  | WTG Unscheduled Maintenance | 35598 | 148.325
5137 | 2025-06-07 | 2025 | 2025 | 2025-06-01 | 2 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.60139 | 0.60139 | 0.60556 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-06 | 148.325 |  | WTG Unscheduled Maintenance | 35598 | 148.325
5138 | 2025-06-07 | 2025 | 2025 | 2025-06-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down | 0 | 0 | 0.013889 | 0 | 0.33333 | 0.33333 | Attend and check HPU Unit 9.1 and 9.7 Valve also check yaw System Pressure than take trail and started WTG. | Close | 0.012821 | O2-11 | 450.1667 |  | WTG Unscheduled Maintenance | 32412 | 450.1667
5139 | 2025-06-07 | 2025 | 2025 | 2025-06-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 4540 | Tower oscillation X level 2 | Auto reset | 0.77153 | 0.77153 | 0.78194 | 0 | 0.25 | 0.25 | Auto reset | Close | 0.0096154 | O2-01 | 379.625 |  | WTG Unscheduled Maintenance | 36444 | 379.625
5140 | 2025-06-08 | 2025 | 2025 | 2025-06-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.33611 | 0.33611 | 0.34028 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-07 | 114.0833 |  | WTG Unscheduled Maintenance | 27380 | 114.0833
5141 | 2025-06-08 | 2025 | 2025 | 2025-06-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Customer | 0.37222 | 0.37222 | 0.44236 | 0 | 1.6833 | 1.6833 | Shutdown taken by GETCO Team for GETCO Tower line Dismentaling Work. | Close | 0.064744 | O2-07 | 1920.4028 |  | WTG Breakdown Maintenance | 27380 | 1920.4028
5142 | 2025-06-08 | 2025 | 2025 | 2025-06-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Customer | 0.76736 | 0.76736 | 0.78958 | 0 | 0.53333 | 0.53333 | Shutdown taken by GETCO Team for GETCO Tower line Dismentaling Work. | Close | 0.020513 | O2-07 | 608.4444 |  | WTG Breakdown Maintenance | 27380 | 608.4444
5143 | 2025-06-08 | 2025 | 2025 | 2025-06-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.93472 | 0.93472 | 0.97222 | 0 | 0.9 | 0.9 | check Event And Data log then reset & started wtg. | Close | 0.034615 | O2-07 | 1026.75 |  | WTG Unscheduled Maintenance | 27380 | 1026.75
5144 | 2025-06-08 | 2025 | 2025 | 2025-06-01 | 2 | O2_06 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Break down | 0.51528 | 0.51528 | 0.51736 | 0 | 0.05 | 0.05 | check Event And Data log then reset & started wtg. | Close | 0.0019231 | O2-21 | 61.3375 |  | WTG Unscheduled Maintenance | 29442 | 61.3375
5145 | 2025-06-08 | 2025 | 2025 | 2025-06-01 | 2 | O2_07 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Customer | 0.37153 | 0.37153 | 0.78889 | 0 | 10.0167 | 10.0167 | Shutdown taken by GETCO Team for GETCO Tower line Dismentaling Work. | Close | 0.38526 | O2-04 | 13013.7368 |  | WTG Breakdown Maintenance | 31181 | 13013.7368
5146 | 2025-06-08 | 2025 | 2025 | 2025-06-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down | 0.48194 | 0.48194 | 0.49792 | 0 | 0.38333 | 0.38333 | check Event And Data log then reset & started wtg. | Close | 0.014744 | O2-26 | 505.425 |  | WTG Unscheduled Maintenance | 31644 | 505.425
5147 | 2025-06-08 | 2025 | 2025 | 2025-06-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.84306 | 0.84306 | 0.84722 | 0 | 0.1 | 0.1 | check Event And Data log then reset & started wtg. | Close | 0.0038462 | O2-15 | 124.3708 |  | WTG Unscheduled Maintenance | 29849 | 124.3708
5148 | 2025-06-08 | 2025 | 2025 | 2025-06-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.86736 | 0.86736 | 0.89583 | 0 | 0.68333 | 0.68333 | after temp reduse then reset & started wtg. | Close | 0.026282 | O2-15 | 849.8674 |  | WTG Unscheduled Maintenance | 29849 | 849.8674
5149 | 2025-06-08 | 2025 | 2025 | 2025-06-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.90278 | 0.93056 | 0.96736 | 0.66667 | 0.88333 | 1.55 | Attend and wtg check MPCB Motor and coolant so found QA008 MPCB Tripped after check voltage and fidbac connection tight after fan on temperature normal then reset and started wtg. | Close | 0.059615 | O2-15 | 1927.7479 |  | WTG Breakdown Maintenance | 29849 | 1927.7479
5150 | 2025-06-08 | 2025 | 2025 | 2025-06-01 | 2 | O2_16 | TQGXIIPL | GEDA | 3.846% | 558 | Pitch deviation Pitch Back | Major BD | 0.42986 | 0.45833 | 0.71042 | 0.68333 | 6.05 | 6.7333 | WTG attend then check related CKT check Axis no 1 battery box found battery lug broken so replace battery then start wtg also winch load test completed. | Close | 0.25897 | O2-21 | 8260.1167 |  | WTG Breakdown Maintenance | 29442 | 8260.1167
5151 | 2025-06-08 | 2025 | 2025 | 2025-06-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Customer | 0.37153 | 0.37153 | 0.43333 | 0 | 1.4833 | 1.4833 | Shutdown taken by GETCO Team for GETCO Tower line Dismentaling Work. | Close | 0.057051 | O2-07 | 1692.2361 |  | WTG Breakdown Maintenance | 27380 | 1692.2361
5152 | 2025-06-08 | 2025 | 2025 | 2025-06-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Customer | 0.76597 | 0.76597 | 0.78819 | 0 | 0.53333 | 0.53333 | Shutdown taken by GETCO Team for GETCO Tower line Dismentaling Work. | Close | 0.020513 | O2-07 | 608.4444 |  | WTG Breakdown Maintenance | 27380 | 608.4444
5153 | 2025-06-08 | 2025 | 2025 | 2025-06-01 | 2 | O2_24 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Break down | 0.43889 | 0.43889 | 0.44722 | 0 | 0.2 | 0.2 | check Event And Data log then reset & started wtg. | Close | 0.0076923 | O2-20 | 265.9417 |  | WTG Unscheduled Maintenance | 31913 | 265.9417
5154 | 2025-06-09 | 2025 | 2025 | 2025-06-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.60347 | 0.60347 | 0.60764 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-12 | 151.925 |  | WTG Unscheduled Maintenance | 36462 | 151.925
5155 | 2025-06-09 | 2025 | 2025 | 2025-06-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.6 | 0.6 | 0.60417 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-11 | 148.1875 |  | WTG Unscheduled Maintenance | 35565 | 148.1875
5156 | 2025-06-09 | 2025 | 2025 | 2025-06-01 | 2 | O2_14 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset | 0.62778 | 0.62778 | 0.63889 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | O2-12 | 405.1333 |  | WTG Unscheduled Maintenance | 36462 | 405.1333
5157 | 2025-06-09 | 2025 | 2025 | 2025-06-01 | 2 | O2_18 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.49514 | 0.49514 | 0.49931 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-06 | 170.4625 |  | WTG Unscheduled Maintenance | 40911 | 170.4625
5158 | 2025-06-09 | 2025 | 2025 | 2025-06-01 | 2 | O2_26 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down | 0.40556 | 0.40556 | 0.40903 | 0 | 0.083333 | 0.083333 | check Event And Data log then reset & started wtg. | Close | 0.0032051 | O2-01 | 134.2187 |  | WTG Unscheduled Maintenance | 38655 | 134.2187
5159 | 2025-06-10 | 2025 | 2025 | 2025-06-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 643 | Sim.angle E enc. <> act.angle 3 | Break down | 0.33333 | 0.33333 | 0.3375 | 0 | 0.1 | 0.1 | check Event And Data log then reset & started wtg. | Close | 0.0038462 | O2-26 | 168.025 |  | WTG Unscheduled Maintenance | 40326 | 168.025
5160 | 2025-06-10 | 2025 | 2025 | 2025-06-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 643 | Sim.angle E enc. <> act.angle 3 | Break down | 0.84653 | 0.90972 | 1899-12-31 | 1.5167 | 2.1667 | 3.6833 | Turbine Attend for Sim angle E enc.<> act.angle 3 so check error related ckt than check QA001 contactor and it's connection tightness also check all auxillary NO-NC connection than check Motor Encoder connector and connection of Encoder cable than WIP, | Close | 0.14167 | O2-26 | 6188.9208 |  | WTG Breakdown Maintenance | 40326 | 6188.9208
5161 | 2025-06-10 | 2025 | 2025 | 2025-06-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.39444 | 0.39444 | 0.39861 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-07 | 187.2458 |  | WTG Unscheduled Maintenance | 44939 | 187.2458
5162 | 2025-06-10 | 2025 | 2025 | 2025-06-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Customer | 0.43681 | 0.43681 | 0.47778 | 0 | 0.98333 | 0.98333 | WTG Stop for GETCO line work Shutdown. | Close | 0.037821 | O2-07 | 1841.2507 |  | WTG Breakdown Maintenance | 44939 | 1841.2507
5163 | 2025-06-10 | 2025 | 2025 | 2025-06-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Customer | 0.5125 | 0.5125 | 0.52986 | 0 | 0.41667 | 0.41667 | WTG Stop for GETCO line work Shutdown. | Close | 0.016026 | O2-07 | 780.191 |  | WTG Breakdown Maintenance | 44939 | 780.191
5164 | 2025-06-10 | 2025 | 2025 | 2025-06-01 | 2 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.78889 | 0.78889 | 0.79097 | 0 | 0.05 | 0.05 | check Event And Data log then reset & started wtg. | Close | 0.0019231 | O2-07 | 93.6229 |  | WTG Unscheduled Maintenance | 44939 | 93.6229
5165 | 2025-06-10 | 2025 | 2025 | 2025-06-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Break down | 0.50347 | 0.50347 | 0.50556 | 0 | 0.05 | 0.05 | check Event And Data log then reset & started wtg. | Close | 0.0019231 | O2-02 | 100.2771 |  | WTG Unscheduled Maintenance | 48133 | 100.2771
5166 | 2025-06-10 | 2025 | 2025 | 2025-06-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.59792 | 0.59792 | 0.59861 | 0 | 0.016667 | 0.016667 | check Event And Data log then reset & started wtg. | Close | 0.00064103 | O2-02 | 33.4257 |  | WTG Unscheduled Maintenance | 48133 | 33.4257
5167 | 2025-06-10 | 2025 | 2025 | 2025-06-01 | 2 | O2_06 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.49653 | 0.49653 | 0.49722 | 0 | 0.016667 | 0.016667 | check Event And Data log then reset & started wtg. | Close | 0.00064103 | O2-21 | 27.2375 |  | WTG Unscheduled Maintenance | 39222 | 27.2375
5168 | 2025-06-10 | 2025 | 2025 | 2025-06-01 | 2 | O2_07 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Customer | 0.43681 | 0.43681 | 0.53056 | 0 | 2.25 | 2.25 | WTG Stop for GETCO line work Shutdown. | Close | 0.086538 | O2-04 | 4236.6562 |  | WTG Breakdown Maintenance | 45191 | 4236.6562
5169 | 2025-06-10 | 2025 | 2025 | 2025-06-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.11458 | 0.11458 | 0.11875 | 0 | 0.1 | 0.1 | check Event And Data log then reset & started wtg. | Close | 0.0038462 | O2-26 | 168.025 |  | WTG Unscheduled Maintenance | 40326 | 168.025
5170 | 2025-06-10 | 2025 | 2025 | 2025-06-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Break down | 0.31944 | 0.31944 | 0.32639 | 0 | 0.16667 | 0.16667 | check Event And Data log then reset & started wtg. | Close | 0.0064103 | O2-26 | 280.0417 |  | WTG Unscheduled Maintenance | 40326 | 280.0417
5171 | 2025-06-10 | 2025 | 2025 | 2025-06-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down | 0.29306 | 0.29306 | 0.3 | 0 | 0.16667 | 0.16667 | check Event and Data log then apply shoft reboot then reset & started wtg. | Close | 0.0064103 | O2-15 | 277.4028 |  | WTG Unscheduled Maintenance | 39946 | 277.4028
5172 | 2025-06-10 | 2025 | 2025 | 2025-06-01 | 2 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Break down | 0.30278 | 0.35417 | 0.54028 | 1.2333 | 4.4667 | 5.7 | Attend and check error related ckt than found QA008 MPCB was tripped so check connection also check current setting and check voltage but voltage is cut in one phase so check and remove relay and refix then found MPCB one contect was loose inside than tight and take trail and started Turbine. | Close | 0.21923 | O2-15 | 9487.175 |  | WTG Breakdown Maintenance | 39946 | 9487.175
5173 | 2025-06-10 | 2025 | 2025 | 2025-06-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.46389 | 0.46389 | 0.46597 | 0 | 0.05 | 0.05 | check Event And Data log then reset & started wtg. | Close | 0.0019231 | O2-12 | 79.1917 |  | WTG Unscheduled Maintenance | 38012 | 79.1917
5174 | 2025-06-10 | 2025 | 2025 | 2025-06-01 | 2 | O2_14 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.66875 | 0.66875 | 0.66944 | 0 | 0.016667 | 0.016667 | check Event And Data log then reset & started wtg. | Close | 0.00064103 | O2-12 | 26.3972 |  | WTG Unscheduled Maintenance | 38012 | 26.3972
5175 | 2025-06-10 | 2025 | 2025 | 2025-06-01 | 2 | O2_15 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.55625 | 0.55625 | 0.56042 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-10 | 102.7583 |  | WTG Unscheduled Maintenance | 24662 | 102.7583
5176 | 2025-06-10 | 2025 | 2025 | 2025-06-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Auto reset | 0.43819 | 0.43819 | 0.44931 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | O2-22 | 529.1222 |  | WTG Unscheduled Maintenance | 47621 | 529.1222
5177 | 2025-06-10 | 2025 | 2025 | 2025-06-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Customer | 0.43681 | 0.43681 | 0.46042 | 0 | 0.56667 | 0.56667 | WTG Stop for GETCO line work Shutdown. | Close | 0.021795 | O2-07 | 1061.0597 |  | WTG Breakdown Maintenance | 44939 | 1061.0597
5178 | 2025-06-10 | 2025 | 2025 | 2025-06-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Customer | 0.5125 | 0.5125 | 0.52986 | 0 | 0.41667 | 0.41667 | WTG Stop for GETCO line work Shutdown. | Close | 0.016026 | O2-07 | 780.191 |  | WTG Breakdown Maintenance | 44939 | 780.191
5179 | 2025-06-10 | 2025 | 2025 | 2025-06-01 | 2 | O2_24 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.69861 | 0.69861 | 0.70139 | 0 | 0.066667 | 0.066667 | check Event And Data log then reset & started wtg. | Close | 0.0025641 | O2-20 | 116.1639 |  | WTG Unscheduled Maintenance | 41819 | 116.1639
5180 | 2025-06-10 | 2025 | 2025 | 2025-06-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Auto reset | 0.83264 | 0.83264 | 0.84375 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | O2-01 | 354.4667 |  | WTG Unscheduled Maintenance | 31902 | 354.4667
5181 | 2025-06-11 | 2025 | 2025 | 2025-06-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 643 | Sim.angle E enc. <> act.angle 3 | Major BD | 0 | 0 | 0.55069 | 0 | 13.2167 | 13.2167 | Turbine Attend for Sim angle E enc.<> act.angle 3 so check error related ckt than check QA001 contactor and it's connection tightness also check all auxillary NO-NC connection than check Motor Encoder connector and connection of Encoder cable than interchange motor Encoder with onther blade than error shifted so found Motor Encoder faulty so arrenge from other site and replace with new one than done blade -3 calibration done and also winch load capacity testing done than started Turbine. | Close | 0.50833 | O2-26 | 17523.6479 |  | WTG Breakdown Maintenance | 31821 | 17523.6479
5182 | 2025-06-11 | 2025 | 2025 | 2025-06-01 | 2 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.65556 | 0.65556 | 0.65972 | 0 | 0.1 | 0.1 | WTG Stop for PPC parameter Update Work. | Close | 0.0038462 | O2-26 | 132.5875 |  | WTG Breakdown Maintenance | 31821 | 132.5875
5183 | 2025-06-11 | 2025 | 2025 | 2025-06-01 | 2 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.64167 | 0.64167 | 0.65139 | 0 | 0.23333 | 0.23333 | WTG Stop for PPC parameter Update Work. | Close | 0.0089744 | O2-05 | 357.7194 |  | WTG Breakdown Maintenance | 36794 | 357.7194
5184 | 2025-06-11 | 2025 | 2025 | 2025-06-01 | 2 | O2_03 | TQGXIIPL | GEDA | 3.846% | 551 | Pitch motor current too high | Break down | 0.28194 | 0.28194 | 0.28472 | 0 | 0.066667 | 0.066667 | check Event and all axis current in Sam than Data log check reset & started wtg. | Close | 0.0025641 | O2-09 | 87.7333 |  | WTG Unscheduled Maintenance | 31584 | 87.7333
5185 | 2025-06-11 | 2025 | 2025 | 2025-06-01 | 2 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset | 0.63264 | 0.63264 | 0.63681 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | O2-02 | 154.0708 |  | WTG Unscheduled Maintenance | 36977 | 154.0708
5186 | 2025-06-11 | 2025 | 2025 | 2025-06-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Break down | 0.12917 | 0.12917 | 0.13819 | 0 | 0.21667 | 0.21667 | check Event And Data log then reset & started wtg. | Close | 0.0083333 | O2-26 | 287.2729 |  | WTG Unscheduled Maintenance | 31821 | 287.2729
5187 | 2025-06-11 | 2025 | 2025 | 2025-06-01 | 2 | O2_08 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down | 0.17083 | 0.17083 | 0.18125 | 0 | 0.25 | 0.25 | check Event And Data log then reset & started wtg. | Close | 0.0096154 | O2-26 | 331.4687 |  | WTG Unscheduled Maintenance | 31821 | 331.4687
5188 | 2025-06-11 | 2025 | 2025 | 2025-06-01 | 2 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.64028 | 0.64028 | 0.64583 | 0 | 0.13333 | 0.13333 | WTG Stop for PPC parameter Update Work. | Close | 0.0051282 | O2-12 | 164.4111 |  | WTG Breakdown Maintenance | 29594 | 164.4111
5189 | 2025-06-11 | 2025 | 2025 | 2025-06-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.12083 | 0.12083 | 0.12292 | 0 | 0.05 | 0.05 | check Event And Data log then reset & started wtg. | Close | 0.0019231 | O2-11 | 63.3854 |  | WTG Unscheduled Maintenance | 30425 | 63.3854
5190 | 2025-06-11 | 2025 | 2025 | 2025-06-01 | 2 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.6375 | 0.6375 | 0.64375 | 0 | 0.15 | 0.15 | WTG Stop for PPC parameter Update Work. | Close | 0.0057692 | O2-11 | 190.1563 |  | WTG Breakdown Maintenance | 30425 | 190.1563
5191 | 2025-06-11 | 2025 | 2025 | 2025-06-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.65278 | 0.65278 | 0.65694 | 0 | 0.1 | 0.1 | WTG Stop for PPC parameter Update Work. | Close | 0.0038462 | O2-22 | 177.4042 |  | WTG Breakdown Maintenance | 42577 | 177.4042
5192 | 2025-06-11 | 2025 | 2025 | 2025-06-01 | 2 | O2_24 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down | 0.36875 | 0.36875 | 0.37153 | 0 | 0.066667 | 0.066667 | check Event And Data log then reset & started wtg. | Close | 0.0025641 | O2-20 | 100.9111 |  | WTG Unscheduled Maintenance | 36328 | 100.9111
5193 | 2025-06-11 | 2025 | 2025 | 2025-06-01 | 2 | O2_25 | TQGXIIPL | GEDA | 3.846% | 550 | Pitch current asymmetry | Break down | 0.26389 | 0.26389 | 0.27222 | 0 | 0.2 | 0.2 | check Event And Data log then reset & started wtg. | Close | 0.0076923 | O2-01 | 81.1167 |  | WTG Unscheduled Maintenance | 9734 | 81.1167
5194 | 2025-06-11 | 2025 | 2025 | 2025-06-01 | 2 | O2_26 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.42986 | 0.42986 | 0.43611 | 0 | 0.15 | 0.15 | WTG Stop for PPC parameter Update Work. | Close | 0.0057692 | O2-01 | 60.8375 |  | WTG Breakdown Maintenance | 9734 | 60.8375
5194 | 2025-06-12 | 2025 | 2025 | 2025-06-01 | 2 | O2_16 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down | 0.57361 | 0.57361 | 0.61528 | 0 | 1 | 1 | Attend and WTG Check BLS Warning releted ckt found BLS FOS4X module Communication connection loose so retight it start WTG. | Close | 0.038462 | O2-21 | 1534.4167 |  | WTG Breakdown Maintenance | 36826 | 1534.4167
5194 | 2025-06-12 | 2025 | 2025 | 2025-06-01 | 2 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down | 0.09375 | 0.09375 | 0.10347 | 0 | 0.23333 | 0.23333 | After temp reduce then reset & started wtg. | Close | 0.0089744 | O2-22 | 374.5486 |  | WTG Unscheduled Maintenance | 38525 | 374.5486
5194 | 2025-06-12 | 2025 | 2025 | 2025-06-01 | 2 | O2_23 | TQGXIIPL | GEDA | 3.846% | 72 | Outdoor temperature high | Break down | 0.67917 | 0.67917 | 0.6875 | 0 | 0.2 | 0.2 | check Event And Data log then reset & started wtg. | Close | 0.0076923 | O2-11 | 295.5333 |  | WTG Unscheduled Maintenance | 35464 | 295.5333
5194 | 2025-06-12 | 2025 | 2025 | 2025-06-01 | 2 | O2_19 | TQGXIIPL | GEDA | 3.846% | 6601 | Wind.dir. diff. level 1 | Break down | 0.75069 | 0.75069 | 0.75278 | 0 | 0.05 | 0.05 | check Event And Data log then reset & started wtg. | Close | 0.0019231 | O2-06 | 81.1292 |  | WTG Unscheduled Maintenance | 38942 | 81.1292
Formulas:
Month = [Date]-DAY([Date])+1

## IGA_BD
Sr. No. | Date | Finacial Year | Calendor Year | Month | Operating Year | Affected Feeder | SPV | Concumaer | Plant Equivalent Weightage | Breakdown Description | Fault Start TimeStamp | Work Start TimeStamp | Fault Clearance time | Response Time | Resolution Time | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Fault category | Scope | Average wind speed | Loss of KWH | KWH lost during BD/SD | Column1 | Fault Category
1 | 2024-04-21 | 2025 | 2024 | 2024-04-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder_1 Shutdown taken by project Team | 8:32 | 8:32 | 23:23 | 0 | 14.85 | 14.85 | feeder-1 Shutdown taken for Line and USS punch point closing work | Close | 7.425 | IG Unscheduled Maintenance | O2 Project |  | 0 | 0
2 | 2024-04-30 | 2025 | 2024 | 2024-04-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in E/F | 12:10 | 12:10 | 12:29 | 0 | 0.31667 | 0.31667 | Feeder-1 Charged in first trial | Close | 0.15833 | IG Breakdown Maintenance | O2 Project |  | 0 | 0
3 | 2024-04-30 | 2025 | 2024 | 2024-04-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Shutdown taken by project Team | 16:29 | 16:29 | 18:15 | 0:00 | 1.7667 | 1.7667 | Feeder-1 CP136 jumper correction work then charged the feeder | Close | 0.88333 | IG Unscheduled Maintenance | O2 Project |  | 0 | 0
4 | 2024-05-01 | 2025 | 2024 | 2024-05-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Shutdown taken by project Team | 16:14 | 16:14 | 19:04 | 0:00 | 2.8333 | 2.8333 | Feeder-1 WTG-09 tapping work done then charged feeder | Close | 1.4167 | IG Unscheduled Maintenance | O2 Project |  | 0 | 0
5 | 2024-05-03 | 2025 | 2024 | 2024-05-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Shutdown taken by project Team | 15:11 | 15:11 | 17:20 | 0:00 | 2.15 | 2.15 | Feeder-1 WTG-09 tapping work and tree cutting at location O2-20 After work done started feeder | Close | 1.075 | IG Breakdown Maintenance | O2 Project | 5.2935 | 0 | 0
6 | 2024-05-12 | 2025 | 2024 | 2024-05-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown taken by project Team | 9:35 | 9:35 | 10:55 | 0:00 | 1.3333 | 1.3333 | Feeder-1 Charged after feeder seperation work | Close | 0.66667 | IG Breakdown Maintenance | O2 Project | 5.5173 | 0 | 0
| 2024-05-12 | 2025 | 2024 | 2024-05-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-2 shutdown taken by project Team | 17:08 | 17:08 | 18:12 | 0:00 | 1.0667 | 1.0667 | Feeder-2 Charged after feeder seperation work | Close | 0.53333 | IG Breakdown Maintenance | O2 Project | 6.2453 | 0 | 0
7 | 2024-05-13 | 2025 | 2024 | 2024-05-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Shutdown taken by prject Team | 17:35 | 17:35 | 19:06 | 0:00 | 1.5167 | 1.5167 | Feeder-2 Charged after phase sequence change | Close | 0.75833 | IG Breakdown Maintenance | O2 Project | 5.2402 | 0 | 0
8 | 2024-05-15 | 2025 | 2024 | 2024-05-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in O/C fault | 0.70764 | 0.70764 | 0.74236 | 0:00 | 0.83333 | 0.83333 | Feeder-1 tripped due to heavy rain,gusty wind and lightning.After weather normalize trial taken feeder stand ok | Close | 0.41667 | IG Unscheduled Maintenance | O2 Project | 4.2 | 208 | 1560
9 | 2024-05-16 | 2025 | 2024 | 2024-05-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in O/C fault | 9:33 | 9:33 | 18:54 | 0:00 | 9.35 | 9.35 | Feeder-1 tripped due to row issue due to project issue | Close | 4.675 | IG Breakdown Maintenance | O2 Project | 6.1 | 767.6 | 64593.54
10 | 2024-05-17 | 2025 | 2024 | 2024-05-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in O/C fault | 16:02 | 16:02 | 19:38 | 0:00 | 3.6 | 3.6 | Feeder -1 tripped due to 33KV transmission line pole fall-down near (O2-12) WTG during heavy rain and high wind at site so isolate (O2-12) then charged feeder. | Close | 1.8 | IG Breakdown Maintenance | O2 Project | 6 | 723 | 23425.2
11 | 2024-05-18 | 2025 | 2024 | 2024-05-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown taken by project team | 19:35 | 19:35 | 20:04 | 0:00 | 0.48333 | 0.48333 | Feeder -1 shutdown taken for O2-12 restoration and after Pole erection and line stringing near O2-13 then charged feeder | Close | 0.24167 | IG Breakdown Maintenance | O2 Project | 4.7 | 340 | 1479
12 | 2024-05-21 | 2025 | 2024 | 2024-05-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown taken by project team | 15:47 | 15:47 | 16:16 | 0:00 | 0.48333 | 0.48333 | Feeder-1 shutdown for conductor correction work at O2_15 Dog line then after correction charged Feeder | Close | 0.24167 | IG Breakdown Maintenance | O2 Project | 6.5 | 946 | 4115.1
13 | 2024-05-24 | 2025 | 2024 | 2024-05-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown taken by project team | 9:48 | 9:48 | 11:42 | 0:00 | 1.9 | 1.9 | Feeder-1 shutdown taken by project team for O2-02 Tapping work | Close | 0.95 | IG Breakdown Maintenance | O2 Project | 8.5 | 1977.5 | 33815.25
14 | 2024-05-24 | 2025 | 2024 | 2024-05-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1Tripped in O/C fault | 11:50 | 11:50 | 11:59 | 0:00 | 0.15 | 0.15 | Feeder-1 trip in over current. After taking trial so, its hold it & charge it. | Close | 0.075 | IG Unscheduled Maintenance | O2 Project | 8.5 | 1977.5 | 2669.625
| 2024-05-24 | 2025 | 2024 | 2024-05-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown taken by project team | 9:48 | 11:42 | 11:42 | 45:36 | 0 | 1.9 | Feeder-1 shutdown taken by project team for pending work | Close | 0.95 | IG Unscheduled Maintenance | O2 Project | 8.5 | 1977.5 | 33815.25
15 | 2024-05-27 | 2025 | 2024 | 2024-05-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown taken by project Team | 4:00 | 4:00 | 4:29 | 0:00 | 0.48333 | 0.48333 | Feeder-1shutdown taken by project team for project pending work. (66kv SF6 breaker gas refilling work.) | Close | 0.24167 | IG Breakdown Maintenance | O2 Project | 9.8 | 2546.2 | 14767.96
16 | 2024-05-27 | 2025 | 2024 | 2024-05-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Shutdown taken by prject Team | 4:00 | 4:00 | 4:29 | 0:00 | 0.48333 | 0.48333 | Feeder-1shutdown taken by project team for project pending work. (66kv SF6 breaker gas refilling work.) | Close | 0.24167 | IG Breakdown Maintenance | O2 Project | 9.8 | 2546.2 | 14767.96
17 | 2024-05-27 | 2025 | 2024 | 2024-05-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown taken by project team | 13:50 | 13:50 | 18:05 | 0:00 | 4.25 | 4.25 | Feeder-1 Shutdown taken by project team for 66KV OPGW line stringing work | Close | 2.125 | IG Breakdown Maintenance | O2 Project | 9.8 | 2546.2 | 129856.2
18 | 2024-05-27 | 2025 | 2024 | 2024-05-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 shutdown taken by project team | 13:50 | 13:50 | 18:05 | 0:00 | 4.25 | 4.25 | Feeder-1 Shutdown taken by project team for 66KV OPGW line stringing work | Close | 2.125 | IG Breakdown Maintenance | O2 Project | 9.8 | 2546.2 | 129856.2
19 | 2024-05-28 | 2025 | 2024 | 2024-05-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown taken by project team | 10:05 | 10:05 | 17:14 | 0:00 | 7.15 | 7.15 | Feeder-1 shutdown taken by project team for 66kv OPGW line stringing work. | Close | 3.575 | IG Breakdown Maintenance | O2 Project | 10.4 | 2684 | 230287.2
20 | 2024-05-28 | 2025 | 2024 | 2024-05-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 shutdown taken by project team | 10:05 | 10:05 | 17:14 | 0:00 | 7.15 | 7.15 | Feeder-2 shutdown taken by project team for 66kv OPGW line stringing work. | Close | 3.575 | IG Breakdown Maintenance | O2 Project | 10.4 | 2684 | 230287.2
21 | 2024-06-01 | 2025 | 2024 | 2024-06-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown taken by project team | 10:00 | 10:00 | 14:25 | 0:00 | 4.4167 | 4.4167 | 66kv transformer and 33kv incomer pending points closing work. | Close | 2.2083 | IG Breakdown Maintenance | O2 Project | 7.4 | 1383 | 73299
22 | 2024-06-01 | 2025 | 2024 | 2024-06-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 shutdown taken by project team | 9:00 | 9:00 | 18:41 | 0:00 | 9.6833 | 9.6833 | Feeder-02 Location O2_16 & O2_20 USS yard and line punch points closing work. | Close | 4.8417 | IG Breakdown Maintenance | O2 Project | 7.4 | 1383 | 160704.6
23 | 2024-06-02 | 2025 | 2024 | 2024-06-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown taken by project team | 8:56 | 8:56 | 9:32 | 0:00 | 0.6 | 0.6 | Feeder-1 shutdown taken by project team for O2_10 & O2_15 WTGs jumper open and complete pending work. | Close | 0.3 | IG Breakdown Maintenance | O2 Project | 5.4 | 532.8 | 3836.16
24 | 2024-06-02 | 2025 | 2024 | 2024-06-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in Earth fault | 14:25 | 14:25 | 14:28 | 0:00 | 0.05 | 0.05 | Feeder-1 tripped in Earth fault after take a trial then hold it & charge it. | Close | 0.025 | IG Unscheduled Maintenance | O2 Project | 5.4 | 532.8 | 319.68
25 | 2024-06-02 | 2025 | 2024 | 2024-06-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown taken by project team | 17:56 | 17:56 | 18:28 | 0:00 | 0.53333 | 0.53333 | Feeder-1 shutdown taken by project team for O2_10 & O2_15 WTGs jumper Re-connect work. | Close | 0.26667 | IG Breakdown Maintenance | O2 Project | 5.4 | 532.8 | 3409.92
25 | 2024-06-03 | 2025 | 2024 | 2024-06-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 shutdown taken by project team | 8:59 | 8:59 | 16:59 | 0:00 | 8 | 8 | Feeder-02 shutdown taken by project team for project pending work . | Close | 4 | IG Breakdown Maintenance | O2 Project | 6.3 | 946 | 90816
26 | 2024-06-04 | 2025 | 2024 | 2024-06-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown taken by project team | 8:02 | 8:02 | 8:31 | 0:00 | 0.48333 | 0.48333 | Feeder-1 shutdown taken by project team for jumper open and complete pending work after jummper open than start O2-10,O2-13,O2-14,02-15. | Close | 0.24167 | IG Breakdown Maintenance | O2 Project | 7.1 | 1222.5 | 7090.5
27 | 2024-06-04 | 2025 | 2024 | 2024-06-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown taken by project team | 17:00 | 17:00 | 17:22 | 0:00 | 0.36667 | 0.36667 | Feeder-1 shutdown taken by project team for jumper Reconnecting work and complete pending work than charge feeder normaly. | Close | 0.18333 | IG Breakdown Maintenance | O2 Project | 7.1 | 1222.5 | 5379
28 | 2024-06-05 | 2025 | 2024 | 2024-06-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown taken by project team | 8:02 | 8:02 | 8:49 | 0:00 | 0.78333 | 0.78333 | Feeder-1 shutdown taken by project team for jumper open and complete pending work | Close | 0.39167 | IG Breakdown Maintenance | O2 Project | 7.1 | 1222.5 | 11491.5
29 | 2024-06-05 | 2025 | 2024 | 2024-06-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown taken by project team | 14:31 | 14:31 | 16:58 | 0:00 | 2.45 | 2.45 | Feeder-1 shutdown taken by project team for jumper Reconnecting work and complete pending work than charge feeder normaly. | Close | 1.225 | IG Breakdown Maintenance | O2 Project | 7.1 | 1222.5 | 35941.5
30 | 2024-06-08 | 2025 | 2024 | 2024-06-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown taken by project team | 8:08 | 8:08 | 8:54 | 0:00 | 0.76667 | 0.76667 | Feeder-1 shutdown taken for jumper open of O2 05 & O2 02 location for OFC cable laying work | Close | 0.38333 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 4026.84
31 | 2024-06-08 | 2025 | 2024 | 2024-06-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown taken by project team | 17:46 | 17:46 | 19:21 | 0:00 | 1.5833 | 1.5833 | Feeder-1 shutdown taken for jumper Reconnecting work of O2 05 & O2 02 locations. | Close | 0.79167 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 8316.3
32 | 2024-06-09 | 2025 | 2024 | 2024-06-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown taken by project team | 7:01 | 7:01 | 7:42 | 0:00 | 0.68333 | 0.68333 | Feeder-1 shutdown taken for jumper open of O2 05 & O2 02 location for OFC cable laying work& )2-02 pole fell down | Close | 0.34167 | IG Breakdown Maintenance | O2 Project | 6.1 | 767.6 | 6294.32
33 | 2024-06-09 | 2025 | 2024 | 2024-06-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown taken by project team | 17:48 | 17:48 | 19:27 | 0:00 | 1.65 | 1.65 | Feeder-1 shutdown taken for jumper Reconnecting work of O2 05 & O2 02 locations. & O2 02 pole fell down | Close | 0.825 | IG Breakdown Maintenance | O2 Project | 6.1 | 767.6 | 15198.48
34 | 2024-06-09 | 2025 | 2024 | 2024-06-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in Earth fault | 9:13 | 9:13 | 9:17 | 0:00 | 0.066667 | 0.066667 | Feeder-1 tripped in Earth fault after take a trial then hold it & charge it. | Close | 0.033333 | IG Breakdown Maintenance | O2 Project | 6.1 | 767.6 | 614.08
35 | 2024-06-10 | 2025 | 2024 | 2024-06-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown taken by project team | 16:54 | 16:54 | 17:56 | 0:00 | 1.0333 | 1.0333 | Feeder-1 shutdown taken for jumper Reconnecting work(OFC Cable laying work) | Close | 0.51667 | IG Breakdown Maintenance | O2 Project | 6.1 | 767.6 | 9518.24
36 | 2024-06-11 | 2025 | 2024 | 2024-06-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown taken by project team | 8:36 | 8:36 | 9:09 | 0:00 | 0.55 | 0.55 | Feeder-1 shutdown taken for jumper Reconnecting work(OFC Cable laying work) | Close | 0.275 | IG Breakdown Maintenance | O2 Project | 8.1 | 1758.7 | 11607.42
37 | 2024-06-11 | 2025 | 2024 | 2024-06-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown taken by project team | 17:56 | 17:56 | 18:20 | 0:00 | 0.4 | 0.4 | Feeder-1 shutdown taken for jumper Reconnecting work(OFC Cable laying work) | Close | 0.2 | IG Breakdown Maintenance | O2 Project | 8.1 | 1758.7 | 8441.76
38 | 2024-06-12 | 2025 | 2024 | 2024-06-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown taken by project team | 9:32 | 9:32 | 10:14 | 0:00 | 0.7 | 0.7 | Feeder-1 shutdown taken for jumper open of O2 05 & O2 02 location for OFC cable laying work | Close | 0.35 | IG Breakdown Maintenance | O2 Project | 7.6 | 1490 | 12516
39 | 2024-06-12 | 2025 | 2024 | 2024-06-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown taken by project team | 19:00 | 19:00 | 20:04 | 0:00 | 1.0667 | 1.0667 | Feeder-1 shutdown taken for jumper Reconnecting work(OFC Cable laying work) | Close | 0.53333 | IG Breakdown Maintenance | O2 Project | 7.6 | 1490 | 19072
40 | 2024-06-12 | 2025 | 2024 | 2024-06-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in Earth fault | 17:14 | 17:14 | 17:18 | 0:00 | 0.066667 | 0.066667 | Feeder-1 tripped in Earth fault after take a trial then hold it & charge it. | Close | 0.033333 | IG Breakdown Maintenance | O2 Project | 7.6 | 1490 | 1192
41 | 2024-06-13 | 2025 | 2024 | 2024-06-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown taken by project team | 9:00 | 9:00 | 16:33 | 0:00 | 7.55 | 7.55 | Feeder-1 shutdown taken for CP-144 low clerance rectification and OFC joint removing and new OFC laying work. | Close | 3.775 | IG Breakdown Maintenance | O2 Project | 7.5 | 1436.5 | 130146.9
42 | 2024-06-14 | 2025 | 2024 | 2024-06-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown taken by project team | 16:15 | 16:15 | 16:50 | 0:00 | 0.58333 | 0.58333 | Feeder-02 shutdown taken by project team for project pending work . | Close | 0.29167 | IG Breakdown Maintenance | O2 Project | 6.9 | 1124.4 | 7870.8
43 | 2024-06-18 | 2025 | 2024 | 2024-06-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 shutdown taken by project team | 14:05 | 14:05 | 16:29 | 0:00 | 2.4 | 2.4 | Feeder-02 shutdown taken for project team for O2-08 tapping connection work | Close | 1.2 | IG Breakdown Maintenance | O2 Project | 6.6 | 990.6 | 28529.28
44 | 2024-06-19 | 2025 | 2024 | 2024-06-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in Earth fault | 9:17 | 9:17 | 9:20 | 0:00 | 0.05 | 0.05 | Feeder-1 tripped in Earth fault after take a trial then hold it & charge it. During petrolling found conductor moved from pin insulator | Close | 0.025 | IG Breakdown Maintenance | O2 Project | 7.9 | 1650.5 | 990.3
45 | 2024-06-20 | 2025 | 2024 | 2024-06-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 shutdown taken by project team | 19:00 | 19:00 | 20:44 | 0:00 | 1.7333 | 1.7333 | Feeder-02 shutdown taken for project team for O2-06 tapping connection work | Close | 0.86667 | IG Breakdown Maintenance | O2 Project | 7.6 | 1490 | 30992
46 | 2024-06-21 | 2025 | 2024 | 2024-06-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 shutdown taken by project team | 16:52 | 16:52 | 18:16 | 0:00 | 1.4 | 1.4 | Feeder-02 shutdown taken for project team for O2-21 tapping connection work | Close | 0.7 | IG Breakdown Maintenance | O2 Project | 7.8 | 1650.5 | 27728.4
47 | 2024-06-21 | 2025 | 2024 | 2024-06-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Tripped in Earth fault | 21:33 | 21:33 | 21:52 | 0:00 | 0.31667 | 0.31667 | Feeder-1 tripped in Earth fault after take a trial then hold it & charge it. | Close | 0.15833 | IG Unscheduled Maintenance | O2 Project | 7.8 | 1650.5 | 6271.9
48 | 2024-06-22 | 2025 | 2024 | 2024-06-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 shutdown taken by project team | 17:43 | 17:43 | 18:46 | 0:00 | 1.05 | 1.05 | Feeder-02 shutdown taken for project team for location no O2-06 USS yard CTPT charging activity. | Close | 0.525 | IG Breakdown Maintenance | O2 Project | 6.1 | 767.6 | 9671.76
49 | 2024-06-23 | 2025 | 2024 | 2024-06-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown taken by project team | 9:05 | 9:05 | 15:05 | 0:00 | 6 | 6 | Feeder-1 shutdown taken by project team for project pending work | Close | 3 | IG Breakdown Maintenance | O2 Project | 5.9 | 691.3 | 49773.6
50 | 2024-06-23 | 2025 | 2024 | 2024-06-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 shutdown taken by project team | 9:05 | 9:05 | 15:05 | 0:00 | 6 | 6 | Feeder-02 shutdown taken by project team for project pending work | Close | 3 | IG Breakdown Maintenance | O2 Project | 5.9 | 691.3 | 49773.6
51 | 2024-06-24 | 2025 | 2024 | 2024-06-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 shutdown taken by project team | 15:30 | 15:30 | 18:34 | 0:00 | 3.0667 | 3.0667 | Feeder-02 shutdown taken by project team for project pending work | Close | 1.5333 | IG Breakdown Maintenance | O2 Project | 3.4 | 92.4 | 3400.32
52 | 2024-06-25 | 2025 | 2024 | 2024-06-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in Earth fault | 17:18 | 17:18 | 18:52 | 0:00 | 1.5667 | 1.5667 | After 33KV line petrolling found 33kv LA failure in 33KV yard, so bypass the LA then charge freeder-01 | Close | 0.78333 | IG Breakdown Maintenance | O2 Project | 3.9 | 208 | 3910.4
53 | 2024-06-25 | 2025 | 2024 | 2024-06-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Tripped in Earth fault | 17:25 | 17:25 | 17:54 | 0:00 | 0.48333 | 0.48333 | Feeder-1 test trail time 33KV TR.LV VCB TRIP & 66kv SF6 break trip so take all trip related data then all condition are normalise then charge power tranformer then after take a trial then hold it & charge feeder#2 | Close | 0.24167 | IG Breakdown Maintenance | O2 Project | 3.9 | 170.4 | 988.32
54 | 2024-06-26 | 2025 | 2024 | 2024-06-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown 33kv LA (R-phase)removing work. | 9:11 | 9:11 | 9:40 | 0:00 | 0.48333 | 0.48333 | Feeder-1 shutdown 33kv LA (R-phase)removing work. | Close | 0.24167 | IG Breakdown Maintenance | O2 Project | 3.9 | 170.4 | 988.32
55 | 2024-06-28 | 2025 | 2024 | 2024-06-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 shutdown taken by project team | 12:26 | 12:26 | 14:48 | 0:00 | 2.3667 | 2.3667 | Feeder-02 shutdown taken for project team for O2-24 tapping connection work | Close | 1.1833 | IG Breakdown Maintenance | O2 Project | 5.7 | 627.9 | 17832.36
56 | 2024-06-29 | 2025 | 2024 | 2024-06-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown taken by project team | 10:31 | 10:31 | 11:57 | 0:00 | 1.4333 | 1.4333 | Feeder-1 shutdown taken for project team for O2-25 tapping connection work | Close | 0.71667 | IG Breakdown Maintenance | O2 Project | 6.9 | 1124.4 | 19339.68
57 | 2024-07-02 | 2025 | 2024 | 2024-07-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown taken by project team | 14:36 | 14:36 | 15:30 | 0:00 | 0.9 | 0.9 | Feeder-1 shutdown for PGVCL line crossing work. | Close | 0.45 | IG Breakdown Maintenance | O2 Project | 9.7 | 2509.3 | 27100.44
58 | 2024-07-07 | 2025 | 2024 | 2024-07-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder -1 manual trip by local person | 0.90903 | 0.90903 | 0.91319 | 0:00 | 0.1 | 0.1 | Feeder -1 manual trip by local person Vanrajbhai and create ROW, issue is resolved then charged Feeder | Close | 0.05 | IG Breakdown Maintenance | O2 Project | 7.7 | 1543.5 | 1852.2
59 | 2024-07-10 | 2025 | 2024 | 2024-07-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in Earth fault/Over current | 18:43 | 18:43 | 18:55 | 0:00 | 0.2 | 0.2 | Feeder-1 tripped in Earth fault after take a trial then hold it & charge it. | Close | 0.1 | IG Breakdown Maintenance | O2 Project | 10.5297 | 1868.1 | 4483.44
60 | 2024-07-11 | 2025 | 2024 | 2024-07-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in Earth fault &Over current | 19:08 | 19:08 | 19:19 | 0:00 | 0.18333 | 0.18333 | Feeder-1 tripped in Earth fault after take a trial then hold it & charge it. | Close | 0.091667 | IG Breakdown Maintenance | O2 Project | 6.2 | 856.8 | 1884.96
61 | 2024-07-11 | 2025 | 2024 | 2024-07-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in Earth fault &Over current | 19:30 | 19:30 | 24:00 | 0:00 | 4.5 | 4.5 | Feeder-1 again tripped in Earth fault/overcurrent due to ROW issue By local person | Open | 2.25 | IG Breakdown Maintenance | O2 Project | 6.2 | 856.8 | 46267.2
62 | 2024-07-12 | 2025 | 2024 | 2024-07-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in Earth fault &Over current | 0:00 | 0:00 | 2:24 | 0:00 | 2.4 | 2.4 | Feeder-1 tripped in Earth fault after take a trial then hold it & F#1 partially charge it. | Close | 1.2 | IG Breakdown Maintenance | O2 Project | 8.5 | 1977.5 | 56952
63 | 2024-07-12 | 2025 | 2024 | 2024-07-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in Earth fault &Over current | 3:36 | 3:36 | 4:55 | 0:00 | 1.3167 | 1.3167 | Feeder-1 shutdown for jumper connection work. | Close | 0.65833 | IG Breakdown Maintenance | O2 Project | 8.5 | 1977.5 | 31244.5
64 | 2024-07-12 | 2025 | 2024 | 2024-07-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in Earth fault &Over current | 17:03 | 17:03 | 17:36 | 0:00 | 0.55 | 0.55 | Feeder-1 tripped in Earth fault after take a trial then hold it & charge it. | Close | 0.275 | IG Breakdown Maintenance | O2 Project | 8.5 | 1977.5 | 13051.5
65 | 2024-07-13 | 2025 | 2024 | 2024-07-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 shutdown taken by project team | 19:03 | 19:03 | 20:39 | 0:00 | 1.6 | 1.6 | Feeder -2 Shutdown taken by project team for O2_24 tapping work. | Close | 0.8 | IG Breakdown Maintenance | O2 Project | 8.1 | 1758.7 | 33767.04
66 | 2024-07-14 | 2025 | 2024 | 2024-07-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown taken by project team | 16:08 | 16:08 | 17:30 | 0:00 | 1.3667 | 1.3667 | Feeder - 1 shutdown taken by project team for O2_25 tapping work. | Close | 0.68333 | IG Breakdown Maintenance | O2 Project | 7.4 | 1383 | 22681.2
67 | 2024-07-16 | 2025 | 2024 | 2024-07-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in Earth fault | 9:34 | 9:34 | 10:20 | 0:00 | 0.76667 | 0.76667 | Feeder-1 tripped in Earth fault after take a trial then hold it & charge it, during petrolling found the Ayyana Team keep the OFC cable on Feeder-01 line | Close | 0.38333 | IG Breakdown Maintenance | O2 Project | 4.9 | 384 | 3532.8
68 | 2024-07-16 | 2025 | 2024 | 2024-07-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in Earth fault &Over current | 17:02 | 17:02 | 17:08 | 0:00 | 0.1 | 0.1 | Feeder-1 tripped in Earth fault after take a trial then hold it & charge it, during petrolling found the Ayyana Team keep the OFC cable on Feeder-01 line | Close | 0.05 | IG Breakdown Maintenance | O2 Project | 4.9 | 384 | 460.8
69 | 2024-07-19 | 2025 | 2024 | 2024-07-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Shutdown taken by Aayana Team for line crossing stringing work | 7:14 | 7:14 | 10:03 | 0:00 | 2.8167 | 2.8167 | Feeder-1 Shutdown taken by project team for 33kv line crossing work at Feeder-2 CP34 | Close | 1.4083 | IG Breakdown Maintenance | O2 Project | 5.8 | 659.6 | 22294.48
70 | 2024-07-19 | 2025 | 2024 | 2024-07-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Shutdown taken by Aayana Team for line crossing stringing work | 7:14 | 7:14 | 10:03 | 0:00 | 2.8167 | 2.8167 | Feeder-2 Shutdown taken by project team for 33kv line crossing work at Feeder-1 CP36 | Close | 1.4083 | IG Breakdown Maintenance | O2 Project | 5.8 | 659.6 | 22294.48
71 | 2024-07-19 | 2025 | 2024 | 2024-07-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Shutdown taken by project team | 14:15 | 14:15 | 15:32 | 0:00 | 1.2833 | 1.2833 | Feeder-1 Shutdown taken by project team for O2-25 OFC cable laying work. | Close | 0.64167 | IG Breakdown Maintenance | O2 Project | 5.8 | 659.6 | 10157.84
72 | 2024-07-19 | 2025 | 2024 | 2024-07-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in Earth fault /Over current | 23:14 | 23:14 | 23:22 | 0:00 | 0.13333 | 0.13333 | Feeder-1 tripped in Earth fault /Over current due to ROW issue ,Metal chain appliend on conductors after take a trial then hold it & charge it. | Close | 0.066667 | IG Breakdown Maintenance | O2 Project | 5.8 | 659.6 | 1055.36
73 | 2024-07-19 | 2025 | 2024 | 2024-07-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in Earth fault /Over current | 23:32 | 23:32 | 24:00 | 0:00 | 0.46667 | 0.46667 | Feeder-1 tripped in Earth fault/Over current due to ROW issue,Metal chain applied on conductors, Line petrolling work in progress. | Open | 0.23333 | IG Breakdown Maintenance | O2 Project | 5.8 | 659.6 | 3693.76
74 | 2024-07-20 | 2025 | 2024 | 2024-07-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in Earth fault /Over current | 0:00 | 0:00 | 0:39 | 0:00 | 0.65 | 0.65 | Feeder-1 tripped in Earth fault /OC due to Row issue ,Metal chain applied on condoctors after take a trial then hold it & charge it. | Close | 0.325 | IG Breakdown Maintenance | O2 Project | 5.2 | 469.4 | 4881.76
75 | 2024-07-20 | 2025 | 2024 | 2024-07-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in Over current fault | 2:14 | 2:14 | 2:29 | 0:00 | 0.25 | 0.25 | Feeder-1 tripped in Over current fault due to row issue,Metal chain applied on condoctors after take a trial then hold it & charge it. | Close | 0.125 | IG Breakdown Maintenance | O2 Project | 5.2 | 469.4 | 1877.6
76 | 2024-07-20 | 2025 | 2024 | 2024-07-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in Over current fault | 3:51 | 3:51 | 4:24 | 0:00 | 0.55 | 0.55 | Feeder-1 tripped in Over current fault due to row issue,Metal chain applied on condoctors after take a trial then hold it & charge it. | Close | 0.275 | IG Breakdown Maintenance | O2 Project | 5.2 | 469.4 | 4130.72
78 | 2024-07-20 | 2025 | 2024 | 2024-07-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Shutdown taken by project team | 11:25 | 11:25 | 15:16 | 0:00 | 3.85 | 3.85 | Feeder-2 Shutdown taken by project team for O2-24 OFC cable laying work. | Close | 1.925 | IG Breakdown Maintenance | O2 Project | 5.2 | 469.4 | 10843.14
79 | 2024-07-20 | 2025 | 2024 | 2024-07-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 All WTGs Manually stop Due ROW issue | 4:24 | 4:24 | 6:00 | 0:00 | 1.6 | 1.6 | Feeder-1 tripped due to ROW issue ,Metal Chain applied on condoctors and also take more than trial to take feeder-1 charge during identify of fault. | Close | 0.8 | IG Unscheduled Maintenance | O2 Project | 5.2 | 469.4 | 12016.64
80 | 2024-07-20 | 2025 | 2024 | 2024-07-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 All WTGs Manually stop Due ROW issue | 4:59 | 4:59 | 6:00 | 0:00 | 1.0167 | 1.0167 | Feeder-2 Tripped due to Row issue, Metal CHain applied on condoctors and take feeder-2 charge during identify of fault. | Close | 0.50833 | IG Unscheduled Maintenance | O2 Project | 5.2 | 469.4 | 3817.7867
81 | 2024-08-04 | 2025 | 2024 | 2024-08-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Shutdown taken by project team | 10:00 | 10:00 | 11:05 | 0:00 | 1.0833 | 1.0833 | Feeder-1 Shutdown taken for condocutors joint fixing work | Close | 0.54167 | IG Breakdown Maintenance | O2 Project | 8.5 | 1977.5 | 25707.5
82 | 2024-08-04 | 2025 | 2024 | 2024-08-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Shutdown taken by project team | 11:45 | 11:45 | 12:14 | 0:00 | 0.48333 | 0.48333 | Feeder-1 Shutdown taken for condocutors joint fixing work | Close | 0.24167 | IG Breakdown Maintenance | O2 Project | 8.5 | 1977.5 | 11469.5
82 | 2024-08-10 | 2025 | 2024 | 2024-08-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in Earth fault | 11:54 | 11:54 | 12:12 | 0:00 | 0.3 | 0.3 | Feeder-1 tripped in earth fault after test trial feeder hold. | Close | 0.15 | IG Breakdown Maintenance | O2 Project | 8.1 | 1758.7 | 6331.32
82 | 2024-08-12 | 2025 | 2024 | 2024-08-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Shutdown taken by project team | 15:19 | 15:19 | 18:10 | 0:00 | 2.85 | 2.85 | feeder 1 shutdown take by project team. O2-26 location tapping connection work. | Close | 1.425 | IG Breakdown Maintenance | O2 Project | 7.5 | 1436.5 | 49128.3
82 | 2024-08-13 | 2025 | 2024 | 2024-08-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Shutdown taken by project team | 15:07 | 15:07 | 17:36 | 0:00 | 2.4833 | 2.4833 | Feeder-1 shutdown take by project team. O2-26 location CTPT Replacement work. | Close | 1.2417 | IG Breakdown Maintenance | O2 Project | 5.7 | 627.9 | 18711.42
82 | 2024-08-21 | 2025 | 2024 | 2024-08-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Shutdown taken by project team | 18:03 | 18:03 | 19:40 | 0:00 | 1.6167 | 1.6167 | Feeder-2 shutdown take by project team. O2-04 and O2-07 location Tapping connecting work. | Close | 0.80833 | IG Breakdown Maintenance | O2 Project | 3.5 | 108 | 1047.6
83 | 2024-08-24 | 2025 | 2024 | 2024-08-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Shutdown taken by project team | 8:58 | 8:58 | 10:10 | 0:00 | 1.2 | 1.2 | Feeder-2 shutdown take by project team. O2- 04 & O2-07 OFC Laying Work | Close | 0.6 | IG Breakdown Maintenance | O2 Project | 6.8 | 1079.8 | 9070.32
84 | 2024-08-24 | 2025 | 2024 | 2024-08-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Shutdown taken by project team | 13:05 | 13:05 | 13:56 | 0:00 | 0.85 | 0.85 | Feeder-2 shutdown take by project team.O2- 04 & O2-07 line Jumper Closing work | Close | 0.425 | IG Breakdown Maintenance | O2 Project | 6.8 | 1079.8 | 6424.81
85 | 2024-08-24 | 2025 | 2024 | 2024-08-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Shutdown taken by project team | 16:26 | 16:26 | 17:40 | 0:00 | 1.2333 | 1.2333 | Feeder-2 shutdown take by project team.O2-07 line Phase sequence change work. | Close | 0.61667 | IG Breakdown Maintenance | O2 Project | 6.8 | 1079.8 | 9322.2733
86 | 2024-08-28 | 2025 | 2024 | 2024-08-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Tripped in Earth fault | 1:47 | 1:47 | 2:16 | 0:00 | 0.48333 | 0.48333 | Feeder-2 tripped in Earth fault after take a trial then hold it & charge it. | Close | 0.24167 | IG Breakdown Maintenance | O2 Project | 6.8 | 1079.8 | 3653.3233
87 | 2024-08-30 | 2025 | 2024 | 2024-08-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Shutdown taken by project team | 12:28 | 12:28 | 12:57 | 0:00 | 0.48333 | 0.48333 | Feeder-2 shutdown taken by project team for O2_07 & O2_04 line jumper opening work after OFC laying work | Close | 0.24167 | IG Breakdown Maintenance | O2 Project | 7.5 | 1436.5 | 4860.1583
88 | 2024-08-30 | 2025 | 2024 | 2024-08-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in Earth fault over current fault | 22:12 | 22:12 | 22:31 | 0:00 | 0.31667 | 0.31667 | Feeder-1 tripped in over curent due to ROW issue by farmer after take trail then hold it and charge it. | Close | 0.15833 | IG Breakdown Maintenance | O2 Project | 7.5 | 1436.5 | 5913.5917
89 | 2024-08-31 | 2025 | 2024 | 2024-08-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in Earth fault over current fault | 12:17 | 12:17 | 13:11 | 0:00 | 0.9 | 0.9 | Feeder-1 tripped in over curent due to ROW issue by farmer after take trail then hold it and charge it. | Close | 0.45 | IG Breakdown Maintenance | O2 Project | 4.5 | 296 | 3463.2
90 | 2024-09-03 | 2025 | 2024 | 2024-09-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in Earth fault | 22:21 | 22:21 | 22:34 | 0:00 | 0.21667 | 0.21667 | Feeder-1 tripped in over curent due to ROW issue by farmer after take trail then hold it and charge it. | Close | 0.10833 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 1232.855
91 | 2024-09-04 | 2025 | 2024 | 2024-09-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in Earth fault/over current | 6:21 | 6:21 | 6:37 | 0:00 | 0.26667 | 0.26667 | Feeder-1 tripped in over curent due to ROW issue by farmer after take trail then hold it and charge it. | Close | 0.13333 | IG Breakdown Maintenance | O2 Project | 5.8 | 659.6 | 2286.6133
91 | 2024-09-06 | 2025 | 2024 | 2024-09-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in Earth fault/over current | 17:05 | 17:05 | 17:28 | 0:00 | 0.38333 | 0.38333 | Feeder-1 tripped in over curent due to ROW issue by farmer after take trail then hold it and charge it. | Close | 0.19167 | IG Breakdown Maintenance | O2 Project | 6.8 | 1329.5 | 6625.3417
91 | 2024-09-07 | 2025 | 2024 | 2024-09-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Shutdown taken by project team | 9:22 | 9:22 | 16:15 | 0:00 | 6.8833 | 6.8833 | Feeder-2 shutdown taken by Project Pending work & OFC Cable laying Work. | Close | 3.4417 | IG Breakdown Maintenance | O2 Project | 5.8 | 659.6 | 40862.22
92 | 2024-09-08 | 2025 | 2024 | 2024-09-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Shutdown taken by project team | 9:11 | 9:11 | 9:46 | 0:00 | 0.58333 | 0.58333 | Feeder-2 shutdown taken by Project Pending work O2-18 33kv line Jumper opening Work. | Close | 0.29167 | IG Breakdown Maintenance | O2 Project | 4.4 | 274 | 1438.5
93 | 2024-09-08 | 2025 | 2024 | 2024-09-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Shutdown taken by project team | 15:43 | 15:43 | 16:17 | 0:00 | 0.56667 | 0.56667 | Feeder-2 shutdown taken by Project Pending work O2-18 33kv line Jumper closing Work. | Close | 0.28333 | IG Breakdown Maintenance | O2 Project | 4.4 | 274 | 1397.4
94 | 2024-09-09 | 2025 | 2024 | 2024-09-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Shutdown taken by project team | 9:00 | 9:00 | 9:45 | 0:00 | 0.75 | 0.75 | Feeder-1 shutdown taken byProject Pending work O2-25 33kv line Jumper opening Work. | Close | 0.375 | IG Breakdown Maintenance | O2 Project | 5.3 | 501.1 | 4885.725
95 | 2024-09-09 | 2025 | 2024 | 2024-09-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Shutdown taken by project team | 14:30 | 14:30 | 15:10 | 0:00 | 0.66667 | 0.66667 | Feeder-1 shutdown taken by Project Pending work O2-25 33kv line Jumper closing Work. | Close | 0.33333 | IG Breakdown Maintenance | O2 Project | 5.3 | 501.1 | 4342.8667
96 | 2024-09-13 | 2025 | 2024 | 2024-09-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Tripped in Earth fault | 22:55 | 22:55 | 23:09 | 0:00 | 0.23333 | 0.23333 | Feeder-2 tripped in Earth fault after take a trial then hold it & charge it. | Close | 0.11667 | IG Breakdown Maintenance | O2 Project | 6.8 | 1329.5 | 4032.8167
97 | 2024-09-20 | 2025 | 2024 | 2024-09-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Shutdown taken by project team | 17:17 | 17:17 | 19:39 | 0:00 | 2.3667 | 2.3667 | Feeder-1 shutdown taken by Project Pending work O2-08 Line Jumper connection work | Close | 1.1833 | IG Breakdown Maintenance | O2 Project | 5.7 | 696.7 | 21435.1367
98 | 2024-09-20 | 2025 | 2024 | 2024-09-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Tripped in Earth fault | 9:32 | 9:32 | 11:50 | 0:00 | 2.3 | 2.3 | Feeder-2 tripped in Earth fault after take a trial then hold it & charge it. | Close | 1.15 | IG Breakdown Maintenance | O2 Project | 5.7 | 696.7 | 12819.28
99 | 2024-09-20 | 2025 | 2024 | 2024-09-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Tripped in Earth fault | 20:20 | 20:20 | 21:04 | 0:00 | 0.73333 | 0.73333 | Feeder-2 tripped in Earth fault after take a trial then hold it & charge it. | Close | 0.36667 | IG Breakdown Maintenance | O2 Project | 5.7 | 696.7 | 4087.3067
100 | 2024-09-21 | 2025 | 2024 | 2024-09-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Shutdown taken by project team | 9:56 | 9:56 | 10:49 | 0:00 | 0.88333 | 0.88333 | Feeder-1 shutdown taken by O2-08 Line Phase sequence change work | Close | 0.44167 | IG Breakdown Maintenance | O2 Project | 5.5 | 624.5 | 7171.3417
101 | 2024-09-22 | 2025 | 2024 | 2024-09-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Tripped in Earth fault | 8:15 | 8:15 | 8:20 | 0:00 | 0.083333 | 0.083333 | Feeder-2 tripped in Earth fault due to security row due to project payment issue issue after take a trial then hold it & charge it. | Close | 0.041667 | IG Breakdown Maintenance | O2 Project | 5 | 406 | 270.6667
102 | 2024-09-26 | 2025 | 2024 | 2024-09-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Tripped in Earth fault | 0:03 | 0:03 | 3:16 | 0:00 | 3.2167 | 3.2167 | Feeder-2 tripped in Earth fault due to security row due to project payment issue issue after take a trial then hold it & charge it. | Close | 1.6083 | IG Breakdown Maintenance | O2 Project | 5.4 | 532.8 | 13710.72
103 | 2024-09-26 | 2025 | 2024 | 2024-09-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Tripped in Earth fault | 20:03 | 20:03 | 20:20 | 0:00 | 0.28333 | 0.28333 | Feeder-2 tripped in Earth fault due to security row due to project payment issue issue after take a trial then hold it & charge it. | Close | 0.14167 | IG Breakdown Maintenance | O2 Project | 5.4 | 532.8 | 1207.68
104 | 2024-10-01 | 2025 | 2024 | 2024-10-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Shutdown taken by project team | 15:58 | 15:58 | 16:53 | 0:00 | 0.91667 | 0.91667 | Feeder-2 shutdown taken by Project team. Project pending work. | Close | 0.45833 | IG Breakdown Maintenance | O2 Project | 4.1 | 200 | 1466.6667
104 | 2024-10-02 | 2025 | 2024 | 2024-10-01 | Year_1 | O2_04 | TQGXIIPL | GEDA | 3.846% | 02-04 WTG shut down | 8:31 | 8:31 | 11:12 | 0:00 | 2.6833 | 2.6833 | wtg manual stop for HT yard HYPM work | Close | 0.10321 | IG Breakdown Maintenance | O2 Project | 4.1 | 208 | 558.1333
104 | 2024-10-02 | 2025 | 2024 | 2024-10-01 | Year_1 | O2_07 | TQGXIIPL | GEDA | 3.846% | 02-07 WTG shut down | 12:05 | 12:05 | 15:02 | 0:00 | 2.95 | 2.95 | wtg manual stop for HT yard HYPM work | Close | 0.11346 | IG Breakdown Maintenance | O2 Project | 4.1 | 208 | 613.6
105 | 2024-10-03 | 2025 | 2024 | 2024-10-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Tripped in Earth fault | 5:19 | 5:19 | 5:30 | 0:00 | 0.18333 | 0.18333 | Feeder-2 tripped in Earth fault after take a trial then hold it & charge it. | Close | 0.091667 | IG Breakdown Maintenance | O2 Project | 5.4 | 532.8 | 781.44
106 | 2024-10-03 | 2025 | 2024 | 2024-10-01 | Year_1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 02-26 WTG shut down | 8:26 | 8:26 | 11:30 | 0:00 | 3.0667 | 3.0667 | wtg manual stop for HT yard HYPM work | Close | 0.11795 | IG Breakdown Maintenance | O2 Project | 5.4 | 532.8 | 1633.92
107 | 2024-10-03 | 2025 | 2024 | 2024-10-01 | Year_1 | O2_08 | TQGXIIPL | GEDA | 3.846% | 02-08 WTG shut down | 12:00 | 12:00 | 15:08 | 0:00 | 3.1333 | 3.1333 | wtg manual stop for HT yard HYPM work | Close | 0.12051 | IG Breakdown Maintenance | O2 Project | 5.4 | 532.8 | 1669.44
108 | 2024-10-05 | 2025 | 2024 | 2024-10-01 | Year_1 | O2_11 | TQGXIIPL | GEDA | 3.846% | 02-11 WTG shut down | 12:04 | 12:04 | 14:58 | 0:00 | 2.9 | 2.9 | wtg manual stop for HT yard HYPM work | Close | 0.11154 | IG Breakdown Maintenance | O2 Project | 5.47 | 564.5 | 1637.05
109 | 2024-10-05 | 2025 | 2024 | 2024-10-01 | Year_1 | O2_14 | TQGXIIPL | GEDA | 3.846% | 02-14 WTG shut down | 8:25 | 8:25 | 11:52 | 0:00 | 3.45 | 3.45 | wtg manual stop for HT yard HYPM work | Close | 0.13269 | IG Breakdown Maintenance | O2 Project | 5.69 | 627.9 | 2166.255
110 | 2024-10-06 | 2025 | 2024 | 2024-10-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 S/D for Tree trimming work & Jumper tightning Work | 14:15 | 14:15 | 15:29 | 0:00 | 1.2333 | 1.2333 | Feeder-2 S/D for Tree trimming work & Jumper tainting Work by project team | Close | 0.61667 | IG Breakdown Maintenance | O2 Project | 3.7 | 139.2 | 1373.44
111 | 2024-10-06 | 2025 | 2024 | 2024-10-01 | Year_1 | O2_12 | TQGXIIPL | GEDA | 3.846% | 02-12 WTG shut down | 8:37 | 8:37 | 10:45 | 0:00 | 2.1333 | 2.1333 | wtg manual stop for HT yard HYPM work | Close | 0.082051 | IG Breakdown Maintenance | O2 Project | 3.98 | 186 | 396.8
112 | 2024-10-06 | 2025 | 2024 | 2024-10-01 | Year_1 | O2_13 | TQGXIIPL | GEDA | 3.846% | 02-13 WTG shut down | 10:56 | 10:56 | 13:25 | 0:00 | 2.4833 | 2.4833 | wtg manual stop for HT yard HYPM work | Close | 0.095513 | IG Breakdown Maintenance | O2 Project | 3.78 | 154.8 | 384.42
113 | 2024-10-06 | 2025 | 2024 | 2024-10-01 | Year_1 | O2_04 | TQGXIIPL | GEDA | 3.846% | O2-04 VCB Tripped | 16:45 | 16:45 | 18:03 | 0:00 | 1.3 | 1.3 | VCB Tripped so check it than no any abnormality than Charge Vcb. | Close | 0.05 | IG Breakdown Maintenance | O2 Project | 3.53 | 108 | 140.4
114 | 2024-10-07 | 2025 | 2024 | 2024-10-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 S/D taken by Project team | 11:30 | 11:30 | 13:00 | 0:00 | 1.5 | 1.5 | Feeder 2 S/D for O2-19 Jumper connection Work | Close | 0.75 | IG Breakdown Maintenance | O2 Project | 5.2 | 469.4 | 6336.9
115 | 2024-10-07 | 2025 | 2024 | 2024-10-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 S/D taken by Project team | 15:16 | 15:16 | 16:18 | 0:00 | 1.0333 | 1.0333 | Feeder 2 S/D for jumper tightning work | Close | 0.51667 | IG Breakdown Maintenance | O2 Project | 5.2 | 469.4 | 4365.42
116 | 2024-10-08 | 2025 | 2024 | 2024-10-01 | Year_1 | O2_16 | TQGXIIPL | GEDA | 3.846% | 02-16 WTG shut down | 8:52 | 8:52 | 10:19 | 0:00 | 1.45 | 1.45 | wtg manual stop for HT yard HYPM work | Close | 0.055769 | IG Breakdown Maintenance | O2 Project | 4.4 | 274 | 397.3
117 | 2024-10-08 | 2025 | 2024 | 2024-10-01 | Year_1 | O2_20 | TQGXIIPL | GEDA | 3.846% | 02-20 WTG shut down | 11:04 | 11:04 | 14:05 | 0:00 | 3.0167 | 3.0167 | wtg manual stop for HT yard HYPM work | Close | 0.11603 | IG Breakdown Maintenance | O2 Project | 4.4 | 274 | 826.5667
118 | 2024-10-09 | 2025 | 2024 | 2024-10-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Tripped in Earth fault | 17:00 | 17:00 | 17:25 | 0:00 | 0.41667 | 0.41667 | Feeder-2 tripped in Earth fault due to row issue after take a trial then hold it & charge it. | Close | 0.20833 | IG Breakdown Maintenance | O2 Project | 4.1 | 208 | 780
119 | 2024-10-09 | 2025 | 2024 | 2024-10-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Tripped in Earth fault | 18:52 | 18:52 | 22:06 | 0:00 | 3.2333 | 3.2333 | Feeder 2 tripped due to row issue by unknown person so SS team line petroling done than charge Feeder 2 | Close | 1.6167 | IG Breakdown Maintenance | O2 Project | 4.1 | 208 | 6052.8
120 | 2024-10-09 | 2025 | 2024 | 2024-10-01 | Year_1 | O2_06 | TQGXIIPL | GEDA | 3.846% | 02-06 WTG shut down | 8:38 | 8:38 | 11:37 | 0:00 | 2.9833 | 2.9833 | wtg manual stop for HT yard HYPM work | Close | 0.11474 | IG Breakdown Maintenance | O2 Project | 4.1 | 208 | 620.5333
121 | 2024-10-09 | 2025 | 2024 | 2024-10-01 | Year_1 | O2_26 | TQGXIIPL | GEDA | 3.846% | 02-21 WTG shut down | 11:16 | 11:16 | 13:49 | 0:00 | 2.55 | 2.55 | wtg manual stop for HT yard HYPM work | Close | 0.098077 | IG Breakdown Maintenance | O2 Project | 4.1 | 208 | 530.4
122 | 2024-10-09 | 2025 | 2024 | 2024-10-01 | Year_1 | O2_26 | TQGXIIPL | GEDA | 3.846% | O2-26 VCB Tripped | 22:06 | 22:06 | 23:07 | 0:00 | 1.0167 | 1.0167 | VCB Tripped so check it than no any abnormality than Charge Vcb.(After Feeder) | Close | 0.039103 | IG Breakdown Maintenance | O2 Project | 4.1 | 208 | 211.4667
123 | 2024-10-11 | 2025 | 2024 | 2024-10-01 | Year_1 | O2_18 | TQGXIIPL | GEDA | 3.846% | 02-18 WTG shut down | 8:14 | 8:14 | 11:56 | 0:00 | 3.7 | 3.7 | wtg manual stop for HT yard HYPM work | Close | 0.14231 | IG Breakdown Maintenance | O2 Project | 6.35 | 901 | 3333.7
124 | 2024-10-11 | 2025 | 2024 | 2024-10-01 | Year_1 | O2_03 | TQGXIIPL | GEDA | 3.846% | 02-03 WTG shut down | 13:17 | 13:17 | 15:30 | 0:00 | 2.2167 | 2.2167 | wtg manual stop for HT yard HYPM work | Close | 0.085256 | IG Breakdown Maintenance | O2 Project | 6.48 | 946 | 2096.9667
125 | 2024-10-12 | 2025 | 2024 | 2024-10-01 | Year_1 | O2_02 | TQGXIIPL | GEDA | 3.846% | O2-02 WTG Shut down | 9:03 | 9:03 | 11:23 | 0:00 | 2.3333 | 2.3333 | wtg manual stop for HT yard HYPM work | Close | 0.089744 | IG Breakdown Maintenance | O2 Project | 5.08 | 437.7 | 1021.3
126 | 2024-10-12 | 2025 | 2024 | 2024-10-01 | Year_1 | O2_05 | TQGXIIPL | GEDA | 3.846% | O2-05 WTG Shut down | 12:11 | 12:11 | 14:45 | 0:00 | 2.5667 | 2.5667 | wtg manual stop for HT yard HYPM work | Close | 0.098718 | IG Breakdown Maintenance | O2 Project | 5.27 | 501.1 | 1286.1567
127 | 2024-10-13 | 2025 | 2024 | 2024-10-01 | Year_1 | O2_09 | TQGXIIPL | GEDA | 3.846% | O2-09 WTG Shut down | 9:06 | 9:06 | 11:24 | 0:00 | 2.3 | 2.3 | wtg manual stop for HT yard HYPM work | Close | 0.088462 | IG Breakdown Maintenance | O2 Project | 3.9 | 170.4 | 391.92
128 | 2024-10-13 | 2025 | 2024 | 2024-10-01 | Year_1 | O2_05 | TQGXIIPL | GEDA | 3.846% | O2-24 WTG Shut down | 11:47 | 11:47 | 14:41 | 0:00 | 2.9 | 2.9 | wtg manual stop for HT yard HYPM work | Close | 0.11154 | IG Breakdown Maintenance | O2 Project | 3.9 | 170.4 | 494.16
129 | 2024-10-15 | 2025 | 2024 | 2024-10-01 | Year_1 | O2_15 | TQGXIIPL | GEDA | 3.846% | O2-05 VCB Tripped | 19:47 | 19:47 | 21:13 | 0:00 | 1.4333 | 1.4333 | VCB Tripped so check it than no any abnormality than Charge Vcb.(After Feeder) | Close | 0.055128 | IG Breakdown Maintenance | O2 Project | 3.33 | 76.8 | 110.08
130 | 2024-10-15 | 2025 | 2024 | 2024-10-01 | Year_1 | O2_15 | TQGXIIPL | GEDA | 3.846% | O2-15 VCB Tripped | 19:47 | 19:47 | 20:12 | 0:00 | 0.41667 | 0.41667 | VCB Tripped so check it than no any abnormality than Charge Vcb.(After Feeder) | Close | 0.016026 | IG Breakdown Maintenance | O2 Project | 3.21 | 61.2 | 25.5
131 | 2024-10-15 | 2025 | 2024 | 2024-10-01 | Year_1 | O2_19 | TQGXIIPL | GEDA | 3.846% | O2-19 VCB Tripped | 19:47 | 19:47 | 21:42 | 0:00 | 1.9167 | 1.9167 | VCB Tripped so check it than no any abnormality than Charge Vcb.(After Feeder) | Close | 0.073718 | IG Breakdown Maintenance | O2 Project | 3.1 | 45.6 | 87.4
132 | 2024-10-15 | 2025 | 2024 | 2024-10-01 | Year_1 | O2_21 | TQGXIIPL | GEDA | 3.846% | O2-21 VCB Tripped | 19:47 | 19:47 | 21:44 | 0:00 | 1.95 | 1.95 | VCB Tripped so check it than no any abnormality than Charge Vcb.(After Feeder) | Close | 0.075 | IG Breakdown Maintenance | O2 Project | 3 | 30 | 58.5
133 | 2024-10-16 | 2025 | 2024 | 2024-10-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Tripped in Earth fault | 18:21 | 18:21 | 19:18 | 0:00 | 0.95 | 0.95 | Feeder-2 tripped in Earth fault after take a trial then hold it & charge it. | Close | 0.475 | IG Breakdown Maintenance | O2 Project | 4.22 | 230 | 1966.5
134 | 2024-10-16 | 2025 | 2024 | 2024-10-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 HYPM WORK Shut Down | 9:08 | 9:08 | 17:57 | 0:00 | 8.8167 | 8.8167 | Feeder-2 HYPM WORK | Close | 4.4083 | IG Breakdown Maintenance | O2 Project | 4.22 | 230 | 18250.5
135 | 2024-10-16 | 2025 | 2024 | 2024-10-01 | Year_1 | O2_19 | TQGXIIPL | GEDA | 3.846% | O2-19 VCB Tripped | 19:18 | 19:18 | 20:23 | 0:00 | 1.0833 | 1.0833 | VCB Tripped so check it than no any abnormality than Charge Vcb.(After Feeder) | Close | 0.041667 | IG Breakdown Maintenance | O2 Project | 4.43 | 274 | 296.8333
136 | 2024-10-16 | 2025 | 2024 | 2024-10-01 | Year_1 | O2_21 | TQGXIIPL | GEDA | 3.846% | O2-21 VCB Tripped | 19:18 | 19:18 | 22:10 | 0:00 | 2.8667 | 2.8667 | VCB Tripped so check it than no any abnormality than Charge Vcb.(After Feeder) | Close | 0.11026 | IG Breakdown Maintenance | O2 Project | 4.22 | 139.2 | 399.04
137 | 2024-10-17 | 2025 | 2024 | 2024-10-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 HYPM WORK Shut Down | 11:24 | 11:24 | 15:53 | 0:00 | 4.4833 | 4.4833 | Feeder-2 HYPM WORK Shut Down | Close | 2.2417 | IG Breakdown Maintenance | O2 Project | 3.93 | 170.4 | 6875.64
138 | 2024-10-18 | 2025 | 2024 | 2024-10-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 HYPM WORK Shut Down | 9:00 | 9:00 | 18:02 | 0:00 | 9.0333 | 9.0333 | Feeder-1 HYPM WORK Shut Down | Close | 4.5167 | IG Breakdown Maintenance | O2 Project | 3.94 | 170.4 | 21549.92
139 | 2024-10-18 | 2025 | 2024 | 2024-10-01 | Year_1 | O2_08 | TQGXIIPL | GEDA | 3.846% | O2-08 VCB Tripped | 18:02 | 18:02 | 19:49 | 0:00 | 1.7833 | 1.7833 | VCB Tripped so check it than no any abnormality than Charge Vcb.(After Feeder) | Close | 0.06859 | IG Breakdown Maintenance | O2 Project | 3.97 | 186 | 331.7
140 | 2024-10-18 | 2025 | 2024 | 2024-10-01 | Year_1 | O2_22 | TQGXIIPL | GEDA | 3.846% | O2-22 WTG Shutdown | 12:24 | 12:24 | 12:58 | 0:00 | 0.56667 | 0.56667 | WTG Maual stop for HT yard punch point closing work by O2 POWER TEAM | Close | 0.021795 | IG Breakdown Maintenance | O2 Project | 4.31 | 252 | 142.8
141 | 2024-10-19 | 2025 | 2024 | 2024-10-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 HYPM WORK Shut Down | 8:16 | 8:16 | 14:03 | 0:00 | 5.7833 | 5.7833 | Feeder-1 HYPM WORK Shut Down | Close | 2.8917 | IG Breakdown Maintenance | O2 Project | 4.3 | 252 | 20403.6
142 | 2024-10-19 | 2025 | 2024 | 2024-10-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Tripped in Earth fault | 15:44 | 15:44 | 16:14 | 0:00 | 0.5 | 0.5 | Feeder-2 tripped in Earth fault after take a trial then hold it & charge it. | Close | 0.25 | IG Breakdown Maintenance | O2 Project | 3.5 | 108 | 486
143 | 2024-10-19 | 2025 | 2024 | 2024-10-01 | Year_1 | O2_08 | TQGXIIPL | GEDA | 3.846% | O2-08 VCB Tripped | 14:15 | 14:15 | 15:38 | 0:00 | 1.3833 | 1.3833 | VCB Tripped so check it than no any abnormality than Charge Vcb.(After Feeder) | Close | 0.053205 | IG Breakdown Maintenance | O2 Project | 4.5 | 296 | 409.4667
144 | 2024-10-20 | 2025 | 2024 | 2024-10-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in Earth fault | 14:43 | 14:43 | 14:58 | 0:00 | 0.25 | 0.25 | Feeder-1 tripped in Earth fault after take a trial then hold it & charge it. | Close | 0.125 | IG Breakdown Maintenance | O2 Project | 2.7 | 0 | 0
145 | 2024-10-21 | 2025 | 2024 | 2024-10-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | feeder-1 shut Down | 12:14 | 12:14 | 13:33 | 0:00 | 1.3167 | 1.3167 | Feeder-1 take shutdown for pss tr LV power cable inspection work. | Close | 0.65833 | IG Breakdown Maintenance | O2 Project | 3.3 | 104 | 1917.0667
146 | 2024-10-21 | 2025 | 2024 | 2024-10-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | feeder-02 shut Down | 12:14 | 12:14 | 13:33 | 0:00 | 1.3167 | 1.3167 | Feeder-2 take shutdown for pss tr LV power cable inspection work. | Close | 0.65833 | IG Breakdown Maintenance | O2 Project | 3.3 | 104 | 1917.0667
147 | 2024-10-24 | 2025 | 2024 | 2024-10-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Tripped in Earth fault | 12:50 | 12:50 | 13:03 | 0:00 | 0.21667 | 0.21667 | Feeder-2 tripped due to PGVCL stay wire touch with Line due to low clearence issue | Close | 0.10833 | IG Breakdown Maintenance | O2 Project | 4.08 | 208 | 450.6667
148 | 2024-10-24 | 2025 | 2024 | 2024-10-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Tripped in Earth fault | 13:23 | 13:23 | 14:36 | 0:00 | 1.2167 | 1.2167 | Feeder-2 tripped due to PGVCL stay wire touch with Line due to low clearence issue | Close | 0.60833 | IG Breakdown Maintenance | O2 Project | 4.08 | 208 | 2530.6667
149 | 2024-10-24 | 2025 | 2024 | 2024-10-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Tripped in Earth fault | 15:34 | 15:34 | 17:12 | 0:00 | 1.6333 | 1.6333 | Feeder-2 tripped due to PGVCL stay wire touch with Line due to low clearence issue | Close | 0.81667 | IG Breakdown Maintenance | O2 Project | 4.08 | 208 | 3397.3333
150 | 2024-10-24 | 2025 | 2024 | 2024-10-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Tripped in Earth fault | 23:26 | 23:26 | 24:00 | 0:00 | 0.56667 | 0.56667 | Feeder-2 tripped due to PGVCL stay wire touch with Line due to low clearence issue | Open | 0.28333 | IG Breakdown Maintenance | O2 Project | 4.08 | 208 | 1178.6667
151 | 2024-10-25 | 2025 | 2024 | 2024-10-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Tripped in Earth fault | 0:00 | 0:00 | 0:26 | 0:00 | 0.43333 | 0.43333 | Feeder-2 tripped due to PGVCL stay wire touch with Line due to low clearence issue | Close | 0.21667 | IG Breakdown Maintenance | O2 Project | 4.2 | 274 | 1187.3333
152 | 2024-10-25 | 2025 | 2024 | 2024-10-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | feeder-2 shut Down | 1:50 | 1:50 | 2:35 | 0:00 | 0.75 | 0.75 | Feeder-2 shutdowen taken for Jumper correction Work. | Close | 0.375 | IG Breakdown Maintenance | O2 Project | 4.2 | 274 | 2055
153 | 2024-10-25 | 2025 | 2024 | 2024-10-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | feeder-2 shut Down | 13:38 | 13:38 | 13:52 | 0:00 | 0.23333 | 0.23333 | Feeder-2 shutdowen taken for Remove the nylon rope on C0nductor near loc O2-22 | Close | 0.11667 | IG Breakdown Maintenance | O2 Project | 4.2 | 274 | 639.3333
154 | 2024-10-26 | 2025 | 2024 | 2024-10-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | feeder-1 shut Down | 7:12 | 7:12 | 9:29 | 0:00 | 2.2833 | 2.2833 | Feeder-1 shutdowen taken for line tapping work for 02 23. | Close | 1.1417 | IG Breakdown Maintenance | O2 Project | 2.5 | 0 | 0
155 | 2024-10-26 | 2025 | 2024 | 2024-10-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | feeder-1 shut Down | 16:10 | 16:10 | 18:07 | 0:00 | 1.95 | 1.95 | Feeder-1 shutdowen taken for O2-23 OFC laying work | Close | 0.975 | IG Breakdown Maintenance | O2 Project | 2.5 | 0 | 0
156 | 2024-10-26 | 2025 | 2024 | 2024-10-01 | Year_1 | O2_08 | TQGXIIPL | GEDA | 3.846% | O2-08 VCB Tripped | 9:35 | 9:35 | 10:25 | 0:00 | 0.83333 | 0.83333 | after grid resume VCB trip. Wtg was diconnected so charge by BOP team than reset and start WTG. | Close | 0.032051 | IG Breakdown Maintenance | O2 Project | 2.5 | 0 | 0
157 | 2024-10-26 | 2025 | 2024 | 2024-10-01 | Year_1 | O2_08 | TQGXIIPL | GEDA | 3.846% | O2-08 VCB Tripped | 18:20 | 18:20 | 18:42 | 0:00 | 0.36667 | 0.36667 | after grid resume VCB trip.Wtg was diconnected so charge by BOP team than reset and start WTG. | Close | 0.014103 | IG Breakdown Maintenance | O2 Project | 2.5 | 0 | 0
158 | 2024-10-26 | 2025 | 2024 | 2024-10-01 | Year_1 | O2_22 | TQGXIIPL | GEDA | 3.846% | O2-22 VCB Tripped | 22:00 | 22:00 | 24:00 | 0:00 | 1.9997 | 1.9997 | USS yard VCB check by BOP team no found any abnormality then charge vcb (VCB Tripped by Security pament Issue) | Close | 0.076912 | IG Breakdown Maintenance | O2 Project | 2.5 | 0 | 0
159 | 2024-10-27 | 2025 | 2024 | 2024-10-01 | Year_1 | O2_04 | TQGXIIPL | GEDA | 3.846% | VCB Tripped | 12:31 | 12:31 | 13:57 | 0:00 | 1.4333 | 1.4333 | VCB was tripped so charge by BOP team than reset and start WTG. | Close | 0.055128 | IG Breakdown Maintenance | O2 Project | 3.9 | 170.4 | 244.24
160 | 2024-10-27 | 2025 | 2024 | 2024-10-01 | Year_1 | O2_06 | TQGXIIPL | GEDA | 3.846% | VCB Tripped | 4:53 | 4:53 | 5:52 | 0:00 | 0.98333 | 0.98333 | VCB was tripped so charge by BOP team than reset and start WTG. | Close | 0.037821 | IG Breakdown Maintenance | O2 Project | 3.9 | 170.4 | 167.56
161 | 2024-10-27 | 2025 | 2024 | 2024-10-01 | Year_1 | O2_21 | TQGXIIPL | GEDA | 3.846% | VCB Tripped | 5:01 | 5:01 | 6:19 | 0:00 | 1.3 | 1.3 | VCB was tripped so charge by BOP team than reset and start WTG. | Close | 0.05 | IG Breakdown Maintenance | O2 Project | 3.9 | 170.4 | 221.52
162 | 2024-10-27 | 2025 | 2024 | 2024-10-01 | Year_1 | O2_22 | TQGXIIPL | GEDA | 3.846% | VCB Tripped | 0:00 | 0:00 | 2:14 | 0:00 | 2.2333 | 2.2333 | VCB was tripped so charge by BOP team. | Close | 0.085897 | IG Breakdown Maintenance | O2 Project | 3.9 | 170.4 | 380.56
163 | 2024-10-28 | 2025 | 2024 | 2024-10-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | feeder-2 shut Down | 12:50 | 12:50 | 14:27 | 0:00 | 1.6167 | 1.6167 | Feeder-2 shutdowen taken for line tapping work for 02 17. | Close | 0.80833 | IG Breakdown Maintenance | O2 Project | 4.4 | 274 | 4429.6667
164 | 2024-11-07 | 2025 | 2024 | 2024-11-01 | Year_1 | O2_22 | TQGXIIPL | GEDA | 3.846% | O2-22 Grid Loss | 12:43 | 12:43 | 15:15 | 0:00 | 2.5333 | 2.5333 | wtg manual stop for HT yard HYPM work | Close | 0.097436 | IG Breakdown Maintenance | O2 Project | 4.5 | 296 | 749.8667
165 | 2024-11-07 | 2025 | 2024 | 2024-11-01 | Year_1 | O2_23 | TQGXIIPL | GEDA | 3.846% | O2-23 Grid Loss | 8:58 | 8:58 | 11:50 | 0:00 | 2.8667 | 2.8667 | wtg manual stop for HT yard HYPM work | Close | 0.11026 | IG Breakdown Maintenance | O2 Project | 4.5 | 296 | 848.5333
165 | 2024-11-08 | 2025 | 2024 | 2024-11-01 | Year_1 | O2_19 | TQGXIIPL | GEDA | 3.846% | O2-19 Grid Loss | 10:01 | 10:01 | 14:26 | 0:00 | 4.4167 | 4.4167 | wtg manual stop for HT yard HYPM work | Close | 0.16987 | IG Breakdown Maintenance | O2 Project | 3.2 | 61.2 | 270.3
165 | 2024-11-09 | 2025 | 2024 | 2024-11-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | feeder-2 shut Down | 14:42 | 14:42 | 15:25 | 0:00 | 0.71667 | 0.71667 | Feeder-2 shutdowen for material movement project work | Close | 0.35833 | IG Breakdown Maintenance | O2 Project | 4.7 | 340 | 2436.6667
166 | 2024-11-19 | 2025 | 2024 | 2024-11-01 | Year_1 | O2_18 | TQGXIIPL | GEDA | 3.846% | O2-18 Grid LOSS | 13:09 | 13:09 | 15:02 | 0:00 | 1.8833 | 1.8833 | USS yard VCB check by BOP team no found any abnormality then charge vcb (VCB Tripped by Unknown Person Security pament Issue) | Close | 0.072436 | IG Breakdown Maintenance | O2 Project | 4.85 | 384 | 723.2
167 | 2024-11-24 | 2025 | 2024 | 2024-11-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Tripped in Earth fault | 10:35 | 10:35 | 10:59 | 0:00 | 0.4 | 0.4 | Feeder-2 tripped in Earth fault after take a trial then charge it. | Close | 0.2 | IG Breakdown Maintenance | O2 Project | 3.55 | 123.6 | 494.4
167 | 2024-11-24 | 2025 | 2024 | 2024-11-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in Earth fault | 10:35 | 10:35 | 10:55 | 0:00 | 0.33333 | 0.33333 | Feeder-1 tripped in Earth fault after take a trial then charge it. | Close | 0.16667 | IG Breakdown Maintenance | O2 Project | 3.63 | 123.6 | 618
168 | 2024-11-24 | 2025 | 2024 | 2024-11-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in Earth fault | 17:06 | 17:06 | 17:40 | 0:00 | 0.56667 | 0.56667 | Feeder -1 tripped Earth fault/ Master Relay trip Take atrail then charge it | Close | 0.28333 | IG Breakdown Maintenance | O2 Project | 3.6 | 123.6 | 1050.6
169 | 2024-11-24 | 2025 | 2024 | 2024-11-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Tripped in Earth fault | 17:17 | 17:17 | 22:45 | 0:00 | 5.4667 | 5.4667 | Feeder-2 Tripped Earth fault/ Master Relay Trip so check founf O2-04 AND O2-07 Near Conductor Broken by jagdishbhai due to project pending issue | Close | 2.7333 | IG Breakdown Maintenance | O2 Project | 3.6 | 123.6 | 6756.8
170 | 2024-11-24 | 2025 | 2024 | 2024-11-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in Earth fault | 18:06 | 18:06 | 18:37 | 0:00 | 0.51667 | 0.51667 | Feeder -1 tripped Earth fault/ Master Relay trip Take atrail then charge it | Close | 0.25833 | IG Breakdown Maintenance | O2 Project | 3.6 | 123.6 | 957.9
171 | 2024-11-24 | 2025 | 2024 | 2024-11-01 | Year_1 | O2_04 | TQGXIIPL | GEDA | 3.846% | O2-04 VCB Tripped | 22:45 | 22:45 | 24:00 | 0:00 | 1.25 | 1.25 | After grid time VCB OFF condition | Open | 0.048077 | IG Breakdown Maintenance | O2 Project | 3.2 | 61.2 | 76.5
172 | 2024-11-24 | 2025 | 2024 | 2024-11-01 | Year_1 | O2_07 | TQGXIIPL | GEDA | 3.846% | O2-07 VCB Tripped | 22:45 | 22:45 | 24:00 | 0:00 | 1.25 | 1.25 | After grid time VCB OFF condition | Open | 0.048077 | IG Breakdown Maintenance | O2 Project | 3.5 | 108 | 135
173 | 2024-11-24 | 2025 | 2024 | 2024-11-01 | Year_1 | O2_24 | TQGXIIPL | GEDA | 3.846% | O2-24 VCB Tripped | 22:45 | 22:45 | 24:00 | 0:00 | 1.25 | 1.25 | After grid time VCB OFF condition | Close | 0.048077 | IG Breakdown Maintenance | O2 Project | 3.4 | 92.4 | 115.5
174 | 2024-11-24 | 2025 | 2024 | 2024-11-01 | Year_1 | O2_21 | TQGXIIPL | GEDA | 3.846% | O2-21 VCB Tripped | 22:45 | 22:45 | 24:00 | 0:00 | 1.25 | 1.25 | After grid time VCB OFF condition | Close | 0.048077 | IG Breakdown Maintenance | O2 Project | 3.6 | 123.6 | 154.5
175 | 2024-11-24 | 2025 | 2024 | 2024-11-01 | Year_1 | O2_19 | TQGXIIPL | GEDA | 3.846% | O2-19 VCB Tripped | 22:45 | 22:45 | 24:00 | 0:00 | 1.25 | 1.25 | After grid time VCB OFF condition | Close | 0.048077 | IG Breakdown Maintenance | O2 Project | 3.6 | 123.6 | 154.5
176 | 2024-11-25 | 2025 | 2024 | 2024-11-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | feeder-2 shut Down | 19:16 | 19:16 | 19:40 | 0:00 | 0.4 | 0.4 | Feeder 2 shutdown for O2-04 Line Jumper closing work | Close | 0.2 | IG Breakdown Maintenance | O2 Project | 6 | 723 | 2892
177 | 2024-11-25 | 2025 | 2024 | 2024-11-01 | Year_1 | O2_19 | TQGXIIPL | GEDA | 3.846% | O2-19 VCB Tripped | 0:00 | 0:00 | 1:16 | 0:00 | 1.2667 | 1.2667 | After grid time VCB OFF condition | Close | 0.048718 | IG Breakdown Maintenance | O2 Project | 5.64 | 596.2 | 755.1867
178 | 2024-11-25 | 2025 | 2024 | 2024-11-01 | Year_1 | O2_04 | TQGXIIPL | GEDA | 3.846% | O2-04 VCB Tripped | 0:00 | 0:00 | 19:40 | 0:00 | 19.6667 | 19.6667 | After grid time VCB OFF condition | Close | 0.75641 | IG Breakdown Maintenance | O2 Project | 6.45 | 946 | 18604.6667
179 | 2024-11-25 | 2025 | 2024 | 2024-11-01 | Year_1 | O2_07 | TQGXIIPL | GEDA | 3.846% | O2-07 VCB Tripped | 0:00 | 0:00 | 19:40 | 0:00 | 19.6667 | 19.6667 | After grid time VCB OFF condition | Close | 0.75641 | IG Breakdown Maintenance | O2 Project | 7.17 | 1276 | 25094.6667
180 | 2024-11-28 | 2025 | 2024 | 2024-11-01 | Year_1 | O2_13 | TQGXIIPL | GEDA | 3.846% | O2-13 Grid Loss | 15:22 | 15:22 | 17:03 | 0:00 | 1.6833 | 1.6833 | WTG Manual stop For SLDC VCB ON off status checking work | Close | 0.064744 | IG Breakdown Maintenance | O2 Project | 5.23 | 469.4 | 790.1567
181 | 2024-11-29 | 2025 | 2024 | 2024-11-01 | Year_1 | O2_08 | TQGXIIPL | GEDA | 3.846% | O2-08 Grid Loss | 13:00 | 13:00 | 14:12 | 0:00 | 1.2 | 1.2 | USS yard VCB check by BOP team no found any abnormality then charge vcb (VCB Tripped by Security Gurd pament Issue) | Close | 0.046154 | IG Breakdown Maintenance | O2 Project | 6.05 | 767.6 | 921.12
182 | 2024-11-29 | 2025 | 2024 | 2024-11-01 | Year_1 | O2_23 | TQGXIIPL | GEDA | 3.846% | O2-23 Grid Loss | 13:23 | 13:23 | 13:50 | 0:00 | 0.45 | 0.45 | USS yard VCB check by BOP team no found any abnormality then charge vcb (VCB Tripped by Security Gurd pament Issue) | Close | 0.017308 | IG Breakdown Maintenance | O2 Project | 6.18 | 812.2 | 365.49
183 | 2024-11-29 | 2025 | 2024 | 2024-11-01 | Year_1 | O2_26 | TQGXIIPL | GEDA | 3.846% | O2-26 Grid Loss | 13:09 | 13:09 | 15:35 | 0:00 | 2.4333 | 2.4333 | USS yard VCB check by BOP team no found any abnormality then charge vcb (VCB Tripped by Security Gurd pament Issue) | Close | 0.09359 | IG Breakdown Maintenance | O2 Project | 5.91 | 691.3 | 1682.1633
184 | 2024-11-30 | 2025 | 2024 | 2024-11-01 | Year_1 | O2_13 | TQGXIIPL | GEDA | 3.846% | O2-13 Grid Loss | 15:23 | 15:23 | 16:09 | 0:00 | 0.76667 | 0.76667 | WTG Manual stop For SLDC VCB ON off status checking work | Close | 0.029487 | IG Breakdown Maintenance | O2 Project | 7.28 | 1329.5 | 1019.2833
185 | 2024-11-30 | 2025 | 2024 | 2024-11-01 | Year_1 | O2_14 | TQGXIIPL | GEDA | 3.846% | O2-14 Grid Loss | 17:05 | 17:05 | 17:22 | 0:00 | 0.28333 | 0.28333 | WTG Manual stop For SLDC VCB ON off status checking work | Close | 0.010897 | IG Breakdown Maintenance | O2 Project | 7.15 | 1276 | 361.5333
186 | 2024-11-30 | 2025 | 2024 | 2024-11-01 | Year_1 | O2_15 | TQGXIIPL | GEDA | 3.846% | O2-15 Grid Loss | 16:22 | 16:22 | 17:04 | 0:00 | 0.7 | 0.7 | WTG Manual stop For SLDC VCB ON off status checking work | Close | 0.026923 | IG Breakdown Maintenance | O2 Project | 7.42 | 1383 | 968.1
187 | 2024-11-30 | 2025 | 2024 | 2024-11-01 | Year_1 | O2_24 | TQGXIIPL | GEDA | 3.846% | O2-24 Grid Loss | 12:36 | 12:36 | 14:11 | 0:00 | 1.5833 | 1.5833 | WTG Manual stop For SLDC VCB ON off status checking work | Close | 0.060897 | IG Breakdown Maintenance | O2 Project | 7.41 | 1383 | 2189.75
187 | 2024-12-01 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in Earth fault | 16:44 | 16:44 | 17:00 | 0:00 | 0.26667 | 0.26667 | Feeder-1 tripped in Earth fault after take a trial then charge it. ( feeder trip for ROW issue ) | Close | 0.13333 | IG Breakdown Maintenance | O2 Project | 7.11 | 1222.5 | 4890
188 | 2024-12-01 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_05 | TQGXIIPL | GEDA | 3.846% | O2-05 VCB Tripped | 19:03 | 19:03 | 20:39 | 0:00 | 1.6 | 1.6 | After grid time VCB OFF condition | Close | 0.061538 | IG Breakdown Maintenance | O2 Project | 7.39 | 1383 | 2212.8
189 | 2024-12-01 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_25 | TQGXIIPL | GEDA | 3.846% | O2-25 VCB Tripped | 19:03 | 19:03 | 19:49 | 0:00 | 0.76667 | 0.76667 | After grid time VCB OFF condition | Close | 0.029487 | IG Breakdown Maintenance | O2 Project | 7.41 | 1383 | 1060.3
| 2024-12-01 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in Earth fault | 17:40 | 17:40 | 19:03 | 0:00 | 1.3833 | 1.3833 | Feeder-1 tripped in Earth fault after take a trial then charge it. ( feeder trip for ROW issue ) | Close | 0.69167 | IG Breakdown Maintenance | O2 Project | 7.11 |  | 0
190 | 2024-12-02 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in Earth fault | 15:38 | 15:38 | 16:44 | 0:00 | 1.1 | 1.1 | Feeder-1 tripped in Earth fault after take a trial then charge it. ( feeder trip for ROW issue ) | Close | 0.55 | IG Breakdown Maintenance | O2 Project | 7.63 | 1490 | 24585
191 | 2024-12-02 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_10 | TQGXIIPL | GEDA | 3.846% | O2-10 Grid Loss | 12:41 | 12:41 | 13:08 | 0:00 | 0.45 | 0.45 | WTG Manual stop For SLDC VCB ON off status checking work | Close | 0.017308 | IG Breakdown Maintenance | O2 Project | 7.3 | 1329.5 | 598.275
192 | 2024-12-02 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_12 | TQGXIIPL | GEDA | 3.846% | O2-12 Grid Loss | 10:52 | 10:52 | 11:54 | 0:00 | 1.0333 | 1.0333 | WTG Manual stop For SLDC VCB ON off status checking work | Close | 0.039744 | IG Breakdown Maintenance | O2 Project | 7.6 | 1490 | 1539.6667
193 | 2024-12-02 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_11 | TQGXIIPL | GEDA | 3.846% | O2-11 Grid Loss | 12:05 | 12:05 | 12:30 | 0:00 | 0.41667 | 0.41667 | WTG Manual stop For SLDC VCB ON off status checking work | Close | 0.016026 | IG Breakdown Maintenance | O2 Project | 6.5 | 946 | 394.1667
194 | 2024-12-02 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_18 | TQGXIIPL | GEDA | 3.846% | O2-18 Grid Loss | 14:54 | 14:54 | 15:38 | 0:00 | 0.73333 | 0.73333 | WTG Manual stop For SLDC VCB ON off status checking work | Close | 0.028205 | IG Breakdown Maintenance | O2 Project | 7.3 | 1329.5 | 974.9667
195 | 2024-12-02 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_21 | TQGXIIPL | GEDA | 3.846% | O2-21 Grid Loss | 16:32 | 16:32 | 17:06 | 0:00 | 0.56667 | 0.56667 | WTG Manual stop For SLDC VCB ON off status checking work | Close | 0.021795 | IG Breakdown Maintenance | O2 Project | 8.3 | 1868.1 | 1058.59
196 | 2024-12-03 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_06 | TQGXIIPL | GEDA | 3.846% | O2-06 Grid Loss | 10:59 | 10:59 | 11:37 | 0:00 | 0.63333 | 0.63333 | WTG Manual stop For SLDC VCB ON off status checking work | Close | 0.024359 | IG Breakdown Maintenance | O2 Project | 6.87 | 1124.4 | 712.12
197 | 2024-12-03 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_09 | TQGXIIPL | GEDA | 3.846% | O2-09 Grid Loss | 12:32 | 12:32 | 13:29 | 0:00 | 0.95 | 0.95 | WTG Manual stop For SLDC VCB ON off status checking work | Close | 0.036538 | IG Breakdown Maintenance | O2 Project | 6.9 | 1124.4 | 1068.18
198 | 2024-12-03 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_16 | TQGXIIPL | GEDA | 3.846% | O2-16 Grid Loss | 15:06 | 15:06 | 17:14 | 0:00 | 2.1333 | 2.1333 | WTG Manual stop For SLDC VCB ON off status checking work | Close | 0.082051 | IG Breakdown Maintenance | O2 Project | 7.01 | 1169 | 2493.8667
199 | 2024-12-03 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_20 | TQGXIIPL | GEDA | 3.846% | O2-20 Grid Loss | 15:54 | 15:54 | 17:05 | 0:00 | 1.1833 | 1.1833 | WTG Manual stop For SLDC VCB ON off status checking work | Close | 0.045513 | IG Breakdown Maintenance | O2 Project | 6.59 | 990.6 | 1172.21
200 | 2024-12-03 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_26 | TQGXIIPL | GEDA | 3.846% | O2-26 Grid Loss | 17:00 | 17:00 | 17:40 | 0:00 | 0.66667 | 0.66667 | WTG Manual stop For SLDC VCB ON off status checking work | Close | 0.025641 | IG Breakdown Maintenance | O2 Project | 6.76 | 1079.8 | 719.8667
201 | 2024-12-04 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_01 | TQGXIIPL | GEDA | 3.846% | O2-01 Grid Loss | 17:29 | 17:29 | 17:54 | 0:00 | 0.41667 | 0.41667 | WTG Manual stop For SLDC VCB ON off status checking work | Close | 0.016026 | IG Breakdown Maintenance | O2 Project | 8.6 | 2032.2 | 846.75
202 | 2024-12-04 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_04 | TQGXIIPL | GEDA | 3.846% | O2-04 Grid Loss | 10:53 | 10:53 | 11:11 | 0:00 | 0.3 | 0.3 | WTG Manual stop For SLDC VCB ON off status checking work | Close | 0.011538 | IG Breakdown Maintenance | O2 Project | 8.6 | 2032.2 | 609.66
203 | 2024-12-04 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_05 | TQGXIIPL | GEDA | 3.846% | O2-05 Grid Loss | 15:08 | 15:08 | 15:26 | 0:00 | 0.3 | 0.3 | WTG Manual stop For SLDC VCB ON off status checking work | Close | 0.011538 | IG Breakdown Maintenance | O2 Project | 8.6 | 2032.2 | 609.66
204 | 2024-12-04 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_07 | TQGXIIPL | GEDA | 3.846% | O2-07 Grid Loss | 11:37 | 11:37 | 11:55 | 0:00 | 0.3 | 0.3 | WTG Manual stop For SLDC VCB ON off status checking work | Close | 0.011538 | IG Breakdown Maintenance | O2 Project | 8.6 | 2032.2 | 609.66
205 | 2024-12-04 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_25 | TQGXIIPL | GEDA | 3.846% | O2-11 Grid Loss | 16:08 | 16:08 | 16:20 | 0:00 | 0.2 | 0.2 | WTG Manual stop For SLDC VCB ON off status checking work | Close | 0.0076923 | IG Breakdown Maintenance | O2 Project | 8.6 | 2032.2 | 406.44
206 | 2024-12-04 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_05 | TQGXIIPL | GEDA | 3.846% | O2-05 VCB Tripped | 13:37 | 13:37 | 14:34 | 0:00 | 0.95 | 0.95 | After grid time VCB OFF condition | Close | 0.036538 | IG Breakdown Maintenance | O2 Project | 8.6 | 2032.2 | 1930.59
207 | 2024-12-04 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_19 | TQGXIIPL | GEDA | 3.846% | O2-19 VCB Tripped | 16:42 | 16:42 | 17:21 | 0:00 | 0.65 | 0.65 | After grid time VCB OFF condition | Close | 0.025 | IG Breakdown Maintenance | O2 Project | 8.6 | 2032.2 | 1320.93
208 | 2024-12-04 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Trip in over current & Earth fault /Master Relay Trip | 1:08 | 1:08 | 1:18 | 0:00 | 0.16667 | 0.16667 | Feeder-1 Tripped in Over current due to row issue at Near O2-09 related pole shifting issue | Close | 0.083333 | IG Breakdown Maintenance | O2 Project | 8.6 | 2032.2 | 5080.5
209 | 2024-12-04 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 TR LV Power Cable inspection Work | 12:40 | 12:40 | 13:37 | 0:00 | 0.95 | 0.95 | Feeder-1 shutdown taken for TR LV Power Cable inspection Work | Close | 0.475 | IG Breakdown Maintenance | O2 Project | 8.6 | 2032.2 | 28958.85
210 | 2024-12-04 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder 2 Shutdown for PGVCL line crossing work | 12:32 | 12:32 | 16:42 | 0:00 | 4.1667 | 4.1667 | Feeder- 2 Shutdown for PGVCL line crossing work | Close | 2.0833 | IG Breakdown Maintenance | O2 Project | 8.6 | 2032.2 | 84675
211 | 2024-12-05 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_03 | TQGXIIPL | GEDA | 3.846% | O2-03 Grid Loss | 10:53 | 10:53 | 11:19 | 0:00 | 0.43333 | 0.43333 | WTG Manual stop For SLDC VCB ON off status checking work | Close | 0.016667 | IG Breakdown Maintenance | O2 Project | 6.8 | 1079.8 | 4679.1333
212 | 2024-12-07 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_02 | TQGXIIPL | GEDA | 3.846% | O2-02 Grid Loss | 15:13 | 15:13 | 16:14 | 0:00 | 1.0167 | 1.0167 | WTG Manual stop For SLDC VCB ON off status checking work | Close | 0.039103 | IG Breakdown Maintenance | O2 Project | 3.9 | 170.4 | 1732.4
213 | 2024-12-07 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Trip in over current & Earth fault /Master Relay Trip | 19:51 | 19:51 | 24:00 | 0:00 | 4.1497 | 4.1497 | Feeder-1 Tripped in Earth fault/Master Relay Trip F# 1 Shutdown all wtg L2 Phase Voltage Down so line petrolling WIP,(ROW issue ) | Close | 2.0749 | IG Breakdown Maintenance | O2 Project | 3.9 | 170.4 | 10606.69
214 | 2024-12-08 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Trip in over current & Earth fault /Master Relay Trip | 0:00 | 0:00 | 0:06 | 0:00 | 0.1 | 0.1 | Feeder-1 Tripped in Earth fault/Master Relay Trip F# 1 Shutdown all wtg L2 Phase Voltage Down ,During Pertolling One phase deadend Burnout, so replaced with new one and charge the feeder-01(ROW issue) | Close | 0.05 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 656.55
215 | 2024-12-08 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Trip in over current & Earth fault /Master Relay Trip | 13:37 | 13:37 | 13:57 | 0:00 | 0.33333 | 0.33333 | Feeder-1Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on ocnductor ,so remove it and charge the feeder-01(Row issue ) | Close | 0.16667 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 2188.5
216 | 2024-12-08 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Trip in over current & Earth fault /Master Relay Trip | 17:04 | 17:04 | 17:49 | 0:00 | 0.75 | 0.75 | Feeder-1Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on ocnductor ,so remove it and charge the feeder-01(Row issue ) | Close | 0.375 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 4924.125
217 | 2024-12-08 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_05 | TQGXIIPL | GEDA | 3.846% | O2-05 VCB Tripped | 0:07 | 0:07 | 1:42 | 0:00 | 1.5833 | 1.5833 | After feeder charge VCB Charge than reset and start WTG. | Close | 0.060897 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 693.025
218 | 2024-12-08 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_08 | TQGXIIPL | GEDA | 3.846% | O2-08 VCB Tripped | 0:07 | 0:07 | 0:49 | 0:00 | 0.7 | 0.7 | After feeder charge VCB Charge than reset and start WTG. | Close | 0.026923 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 306.39
219 | 2024-12-08 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_08 | TQGXIIPL | GEDA | 3.846% | O2-08 VCB Tripped | 17:50 | 17:50 | 17:56 | 0:00 | 0.1 | 0.1 | After feeder charge VCB Charge than reset and start WTG. | Close | 0.0038462 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 43.77
220 | 2024-12-09 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Trip in over current & Earth fault /Master Relay Trip | 9:51 | 9:51 | 10:38 | 0:00 | 0.78333 | 0.78333 | Feeder-1Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on ocnductor ,so remove it and charge the feeder-01(Row issue ) | Close | 0.39167 | IG Breakdown Maintenance | O2 Project | 8.5 | 1977.5 | 23235.625
221 | 2024-12-09 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Trip in over current & Earth fault /Master Relay Trip | 19:43 | 19:43 | 20:07 | 0:00 | 0.4 | 0.4 | Feeder-1Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on ocnductor ,so remove it and charge the feeder-01(Row issue ) | Close | 0.2 | IG Breakdown Maintenance | O2 Project | 8.5 | 1977.5 | 11865
223 | 2024-12-11 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Trip in over current & Earth fault /Master Relay Trip | 4:10 | 4:10 | 4:45 | 0:00 | 0.58333 | 0.58333 | Feeder-1Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on ocnductor ,so remove it and charge the feeder-01(Row issue ) | Close | 0.29167 | IG Breakdown Maintenance | O2 Project | 7.24 | 1276 | 11165
224 | 2024-12-11 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Trip in over current & Earth fault /Master Relay Trip | 20:18 | 20:18 | 20:39 | 0:00 | 0.35 | 0.35 | Feeder-1Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on ocnductor ,so remove it and charge the feeder-01(Row issue ) | Close | 0.175 | IG Breakdown Maintenance | O2 Project | 7.24 | 1276 | 6699
225 | 2024-12-11 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_09 | TQGXIIPL | GEDA | 3.846% | O2-09 Grid Loss | 20:45 | 20:45 | 21:45 | 0:00 | 1 | 1 | After feeder charge VCB Charge than reset and start WTG. | Close | 0.038462 | IG Breakdown Maintenance | O2 Project | 7.3 | 1329.5 | 1329.5
226 | 2024-12-11 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_13 | TQGXIIPL | GEDA | 3.846% | O2-13 Grid Loss | 20:45 | 20:45 | 21:16 | 0:00 | 0.51667 | 0.51667 | After feeder charge VCB Charge than reset and start WTG. | Close | 0.019872 | IG Breakdown Maintenance | O2 Project | 6.97 | 1169 | 603.9833
227 | 2024-12-11 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_23 | TQGXIIPL | GEDA | 3.846% | O2-23 Grid Loss | 4:45 | 4:45 | 6:30 | 0:00 | 1.75 | 1.75 | After feeder charge VCB Charge than reset and start WTG. | Close | 0.067308 | IG Breakdown Maintenance | O2 Project | 6.9 | 1124.4 | 1967.7
228 | 2024-12-11 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_23 | TQGXIIPL | GEDA | 3.846% | O2-23 Grid Loss | 20:45 | 20:45 | 21:33 | 0:00 | 0.8 | 0.8 | After feeder charge VCB Charge than reset and start WTG. | Close | 0.030769 | IG Breakdown Maintenance | O2 Project | 6.9 | 1124.4 | 899.52
229 | 2024-12-11 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_26 | TQGXIIPL | GEDA | 3.846% | O2-26 Grid Loss | 20:45 | 20:45 | 22:12 | 0:00 | 1.45 | 1.45 | After feeder charge VCB Charge than reset and start WTG. | Close | 0.055769 | IG Breakdown Maintenance | O2 Project | 7.5 | 1276 | 1850.2
230 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Trip in over current & Earth fault /Master Relay Trip | 4:45 | 4:45 | 5:00 | 0:00 | 0.25 | 0.25 | Feeder-1Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on ocnductor ,so remove it and charge the feeder-01 | Close | 0.125 | IG Breakdown Maintenance | O2 Project | 7.5 | 1436 | 5385
231 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-1 Trip in over current & Earth fault /Master Relay Trip+power tranformer inspection work. | 10:35 | 10:35 | 12:41 | 0:00 | 2.1 | 2.1 | Feeder-1Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on ocnductor ,so remove it and charge the feeder-01 | Close | 1.05 | IG Breakdown Maintenance | O2 Project | 7.5 | 1436 | 30156
232 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-2 manual trip for power tranformer inspection work. | 10:50 | 10:50 | 13:00 | 0:00 | 2.1667 | 2.1667 | Feeder-2 manual trip for power tranformer inspection work. | Close | 1.0833 | IG Breakdown Maintenance | O2 Project | 7.5 | 1436 | 46670
233 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Trip in over current & Earth fault /Master Relay Trip | 22:03 | 22:03 | 22:16 | 0:00 | 0.21667 | 0.21667 | Feeder-1Trip in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on ocnductor ,so remove it and charge the feeder-01 | Close | 0.10833 | IG Breakdown Maintenance | O2 Project | 7.5 | 1436 | 4667
234 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_05 | TQGXIIPL | GEDA | 3.846% | Grid Loss | 13:00 | 13:00 | 14:00 | 0:00 | 1 | 1 | After VCB Charge than reset and start WTG. | Close | 0.038462 | IG Breakdown Maintenance | O2 Project | 7.5 | 1436 | 1436
235 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_08 | TQGXIIPL | GEDA | 3.846% | Grid Loss | 13:00 | 13:00 | 13:44 | 0:00 | 0.73333 | 0.73333 | After VCB Charge than reset and start WTG. | Close | 0.028205 | IG Breakdown Maintenance | O2 Project | 7.5 | 1436 | 1053.0667
236 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_13 | TQGXIIPL | GEDA | 3.846% | Grid Loss | 5:10 | 5:10 | 5:18 | 0:00 | 0.13333 | 0.13333 | After VCB Charge than reset and start WTG. | Close | 0.0051282 | IG Breakdown Maintenance | O2 Project | 7.5 | 1436 | 191.4667
237 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_13 | TQGXIIPL | GEDA | 3.846% | Grid Loss | 22:20 | 22:20 | 22:35 | 0:00 | 0.25 | 0.25 | After VCB Charge than reset and start WTG. | Close | 0.0096154 | IG Breakdown Maintenance | O2 Project | 7.5 | 1436 | 359
238 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_23 | TQGXIIPL | GEDA | 3.846% | Grid Loss | 5:10 | 5:10 | 5:41 | 0:00 | 0.51667 | 0.51667 | After grid resume found VCB trip so Charge it. | Close | 0.019872 | IG Breakdown Maintenance | O2 Project | 7.5 | 1436 | 741.9333
239 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_23 | TQGXIIPL | GEDA | 3.846% | Grid Loss | 22:20 | 22:20 | 22:59 | 0:00 | 0.65 | 0.65 | After VCB Charge than reset and start WTG. | Close | 0.025 | IG Breakdown Maintenance | O2 Project | 7.5 | 1436 | 933.4
240 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_26 | TQGXIIPL | GEDA | 3.846% | Grid Loss | 5:10 | 5:10 | 5:59 | 0:00 | 0.81667 | 0.81667 | After VCB Charge than reset and start WTG. | Close | 0.03141 | IG Breakdown Maintenance | O2 Project | 7.5 | 1436 | 1172.7333
241 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_26 | TQGXIIPL | GEDA | 3.846% | Grid Loss | 13:00 | 13:00 | 13:47 | 0:00 | 0.78333 | 0.78333 | After VCB Charge than reset and start WTG. | Close | 0.030128 | IG Breakdown Maintenance | O2 Project | 7.5 | 1436 | 1124.8667
242 | 2024-12-12 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_26 | TQGXIIPL | GEDA | 3.846% | Grid Loss | 22:20 | 22:20 | 23:13 | 0:00 | 0.88333 | 0.88333 | After grid resume found VCB trip so Charge it. | Close | 0.033974 | IG Breakdown Maintenance | O2 Project | 7.5 | 1436 | 1268.4667
243 | 2024-12-13 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Trip in over current & Earth fault /Master Relay Trip | 2:42 | 2:42 | 2:54 | 0:00 | 0.2 | 0.2 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on ocnductor ,so remove it and charge the feeder-01 | Close | 0.1 | IG Breakdown Maintenance | O2 Project | 9.6 | 2472.4 | 7417.2
244 | 2024-12-13 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_11 | TQGXIIPL | GEDA | 3.846% | Grid Loss | 3:10 | 3:10 | 4:35 | 0:00 | 1.4167 | 1.4167 | After VCB Charge than reset and start WTG. | Close | 0.054487 | IG Breakdown Maintenance | O2 Project | 9.6 | 2472.4 | 3502.5667
245 | 2024-12-13 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_13 | TQGXIIPL | GEDA | 3.846% | Grid Loss | 3:10 | 3:10 | 3:37 | 0:00 | 0.45 | 0.45 | After VCB Charge than reset and start WTG. | Close | 0.017308 | IG Breakdown Maintenance | O2 Project | 9.6 | 2472.4 | 1112.58
246 | 2024-12-14 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 S/D taken by Project team | 8:55 | 8:55 | 15:30 | 0:00 | 6.5833 | 6.5833 | Feeder-2 Shutdown for O2-17 line tapping work(project work) | Close | 3.2917 | IG Breakdown Maintenance | O2 Project | 8.4 | 1922.8 | 126584.3333
247 | 2024-12-14 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_06 | TQGXIIPL | GEDA | 3.846% | Grid Loss | 15:30 | 15:30 | 16:06 | 0:00 | 0.6 | 0.6 | After VCB Charge than reset and start WTG. | Close | 0.023077 | IG Breakdown Maintenance | O2 Project | 8.4 | 1922.8 | 1153.68
248 | 2024-12-14 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_19 | TQGXIIPL | GEDA | 3.846% | Grid Loss | 15:30 | 15:30 | 15:53 | 0:00 | 0.38333 | 0.38333 | After VCB Charge than reset and start WTG. | Close | 0.014744 | IG Breakdown Maintenance | O2 Project | 8.4 | 1922.8 | 737.0733
249 | 2024-12-14 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_21 | TQGXIIPL | GEDA | 3.846% | Grid Loss | 15:30 | 15:30 | 16:00 | 0:00 | 0.5 | 0.5 | After grid resume found VCB trip so Charge it. | Close | 0.019231 | IG Breakdown Maintenance | O2 Project | 8.4 | 1922.8 | 961.4
250 | 2024-12-14 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_22 | TQGXIIPL | GEDA | 3.846% | Grid Loss | 15:30 | 15:30 | 15:51 | 0:00 | 0.35 | 0.35 | After grid resume found VCB trip so Charge it. | Close | 0.013462 | IG Breakdown Maintenance | O2 Project | 8.4 | 1922.8 | 672.98
251 | 2024-12-15 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Trip in over current & Earth fault /Master Relay Trip | 13:40 | 13:40 | 14:01 | 0:00 | 0.35 | 0.35 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on ocnductor ,so remove it and charge the feeder-01 | Close | 0.175 | IG Breakdown Maintenance | O2 Project | 5.4163 | 627.9 | 3296.475
252 | 2024-12-16 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Trip in over current & Earth fault /Master Relay Trip | 5:15 | 5:15 | 5:37 | 0:00 | 0.36667 | 0.36667 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on ocnductor ,so remove it and charge the feeder-01 | Close | 0.18333 | IG Breakdown Maintenance | O2 Project | 4.4 | 274 | 1507
253 | 2024-12-16 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Trip in over current & Earth fault /Master Relay Trip | 10:04 | 10:04 | 10:20 | 0:00 | 0.26667 | 0.26667 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on ocnductor ,so remove it and charge the feeder-01 | Close | 0.13333 | IG Breakdown Maintenance | O2 Project | 4.4 | 274 | 1096
254 | 2024-12-16 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Trip in over current & Earth fault /Master Relay Trip | 11:25 | 11:25 | 11:41 | 0:00 | 0.26667 | 0.26667 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on ocnductor ,so remove it and charge the feeder-01 | Close | 0.13333 | IG Breakdown Maintenance | O2 Project | 4.4 | 274 | 1096
255 | 2024-12-17 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Trip in over current & Earth fault /Master Relay Trip | 6:51 | 6:51 | 7:05 | 0:00 | 0.23333 | 0.23333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on ocnductor ,so remove it and charge the feeder-01 | Close | 0.11667 | IG Breakdown Maintenance | O2 Project | 5.3 | 501.1 | 1753.85
256 | 2024-12-17 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 shutdown by Project Team | 9:14 | 9:14 | 10:05 | 0:00 | 0.85 | 0.85 | Feeder-2 shutdown for O2-17 line OFC cable laying work. | Close | 0.425 | IG Breakdown Maintenance | O2 Project | 5.3 | 501.1 | 4259.35
257 | 2024-12-17 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 shutdown by Project Team | 17:45 | 17:45 | 18:45 | 0:00 | 1 | 1 | Feeder-2 shutdown for O2-17 line OFC cable laying work. | Close | 0.5 | IG Breakdown Maintenance | O2 Project | 5.3 | 501.1 | 5011
258 | 2024-12-18 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Trip in over current & Earth fault /Master Relay Trip | 18:00 | 18:00 | 18:14 | 0:00 | 0.23333 | 0.23333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on ocnductor ,so remove it and charge the feeder-01 | Close | 0.11667 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 805
259 | 2024-12-19 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Trip in over current & Earth fault /Master Relay Trip | 22:22 | 22:22 | 22:36 | 0:00 | 0.23333 | 0.23333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on ocnductor ,so remove it and charge the feeder-01 | Close | 0.11667 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 805
260 | 2024-12-20 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Trip in over current & Earth fault /Master Relay Trip | 1:14 | 1:14 | 1:30 | 0:00 | 0.26667 | 0.26667 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on ocnductor ,so remove it and charge the feeder-01 | Close | 0.13333 | IG Breakdown Maintenance | O2 Project | 7.2 | 1276 | 5104
261 | 2024-12-20 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 shutdown for O2-17 line jumper opening work for line sty fixing work (BOB) | 9:05 | 9:05 | 10:11 | 0:00 | 1.1 | 1.1 | Feeder-2 shutdown for O2-17 line jumper opening work for line sty fixing work (BOB) | Close | 0.55 | IG Breakdown Maintenance | O2 Project | 7.2 | 1276 | 14036
262 | 2024-12-20 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 shutdown for O2-17 line jumper closing work | 17:29 | 17:29 | 18:02 | 0:00 | 0.55 | 0.55 | Feeder-2 shutdown for O2-17 line jumper closing work | Close | 0.275 | IG Breakdown Maintenance | O2 Project | 7.2 | 1276 | 7018
263 | 2024-12-20 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Trip in over current & Earth fault /Master Relay Trip | 22:37 | 22:37 | 22:51 | 0:00 | 0.23333 | 0.23333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on ocnductor ,so remove it and charge the feeder-01 | Close | 0.11667 | IG Breakdown Maintenance | O2 Project | 7.2 | 1276 | 4466
264 | 2024-12-20 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_08 | TQGXIIPL | GEDA | 3.846% | After grid resume found VCB trip so Charge it. | 23:10 | 23:10 | 23:58 | 0:00 | 0.8 | 0.8 | After grid resume found VCB trip so Charge it. | Close | 0.030769 | IG Breakdown Maintenance | O2 Project | 7.2 | 1276 | 1020.8
265 | 2024-12-20 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_08 | TQGXIIPL | GEDA | 3.846% | After grid resume found VCB trip so Charge it. | 1:30 | 1:30 | 3:00 | 0:00 | 1.5 | 1.5 | After grid resume found VCB trip so Charge it. | Close | 0.057692 | IG Breakdown Maintenance | O2 Project | 7.2 | 1276 | 1914
266 | 2024-12-20 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_17 | TQGXIIPL | GEDA | 3.846% | VCB manual trip for O2-17 line jumper opening work for line sty fixing work (BOB) | 10:20 | 10:20 | 17:29 | 0:00 | 7.15 | 7.15 | VCB manual trip for O2-17 line jumper opening work for line sty fixing work (BOB) | Close | 0.275 | IG Breakdown Maintenance | O2 Project | 7.2 | 1276 | 9123.4
267 | 2024-12-20 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_26 | TQGXIIPL | GEDA | 3.846% | After grid resume found VCB trip so Charge it. | 1:30 | 1:30 | 3:00 | 0:00 | 1.5 | 1.5 | After grid resume found VCB trip so Charge it. | Close | 0.057692 | IG Breakdown Maintenance | O2 Project | 7.2 | 1276 | 1914
268 | 2024-12-21 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Tripped in over current & Earth fault /Master Relay Trip | 3:00 | 3:00 | 5:28 | 0:00 | 2.4667 | 2.4667 | Feeder-2 Trip in over current & Earth fault /Master Relay Tripped due to CP63 C lamp broken and y phase conductor broken | Close | 1.2333 | IG Breakdown Maintenance | O2 Project | 4.2 | 170.4 | 4623.52
269 | 2024-12-21 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current & Earth fault /Master Relay Trip | 6:40 | 6:40 | 6:55 | 0:00 | 0.25 | 0.25 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on ocnductor ,so remove it and charge the feeder-01 | Close | 0.125 | IG Breakdown Maintenance | O2 Project | 4.2 | 274 | 1027.5
270 | 2024-12-21 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown for O2-25 line jumper OPEN work | 9:25 | 9:25 | 9:57 | 0:00 | 0.53333 | 0.53333 | Feeder-1 shutdown for O2-25 line jumper Open work for project shutdown | Close | 0.26667 | IG Breakdown Maintenance | O2 Project | 4.2 | 274 | 2192
271 | 2024-12-21 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder 2 Line Jumper closing work | 11:29 | 11:29 | 11:53 | 0:00 | 0.4 | 0.4 | Feeder 2 after C clmap replaced charged the feeder-02 | Close | 0.2 | IG Breakdown Maintenance | O2 Project | 4.2 | 170.4 | 749.76
272 | 2024-12-21 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown for O2-25 line jumper CLOSER work | 17:09 | 17:09 | 17:32 | 0:00 | 0.38333 | 0.38333 | Feeder-1 shutdown for O2-25 line jumper closer work for project shutdown | Close | 0.19167 | IG Breakdown Maintenance | O2 Project | 4.2 | 274 | 1575.5
273 | 2024-12-21 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_19 | TQGXIIPL | GEDA | 3.846% | Grid Loss | 5:38 | 5:38 | 5:55 | 0:00 | 0.28333 | 0.28333 | After grid resume found VCB trip so Charge it. | Close | 0.010897 | IG Breakdown Maintenance | O2 Project | 4.2 | 186 | 52.7
274 | 2024-12-21 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_07 | TQGXIIPL | GEDA | 3.846% | Grid Loss | 5:38 | 5:38 | 6:12 | 0:00 | 0.56667 | 0.56667 | After grid resume found VCB trip so Charge it. | Close | 0.021795 | IG Breakdown Maintenance | O2 Project | 4.2 | 208 | 117.8667
275 | 2024-12-21 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_08 | TQGXIIPL | GEDA | 3.846% | Grid Loss | 6:55 | 6:55 | 7:26 | 0:00 | 0.51667 | 0.51667 | After grid resume found VCB trip so Charge it. | Close | 0.019872 | IG Breakdown Maintenance | O2 Project | 4.2 | 186 | 96.1
276 | 2024-12-21 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_08 | TQGXIIPL | GEDA | 3.846% | Grid Loss | 9:57 | 9:57 | 10:37 | 0:00 | 0.66667 | 0.66667 | After grid resume found VCB trip so Charge it. | Close | 0.025641 | IG Breakdown Maintenance | O2 Project | 4.2 | 186 | 124
277 | 2024-12-21 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_24 | TQGXIIPL | GEDA | 3.846% | Grid Loss | 11:53 | 11:53 | 12:03 | 0:00 | 0.16667 | 0.16667 | After grid resume found VCB trip so Charge it. | Close | 0.0064103 | IG Breakdown Maintenance | O2 Project | 4.2 | 208 | 34.6667
278 | 2024-12-21 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_06 | TQGXIIPL | GEDA | 3.846% | Grid Loss | 5:38 | 5:38 | 12:48 | 0:00 | 7.1667 | 7.1667 | Stop Due to line jumper open after VCB Charge then reset and start wtg | Close | 0.27564 | IG Breakdown Maintenance | O2 Project | 4.2 | 139.2 | 997.6
279 | 2024-12-21 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_17 | TQGXIIPL | GEDA | 3.846% | Grid Loss | 5:38 | 5:38 | 12:48 | 0:00 | 7.1667 | 7.1667 | Stop Due to line jumper open after VCB Charge then reset and start wtg | Close | 0.27564 | IG Breakdown Maintenance | O2 Project | 4.2 | 186 | 1333
280 | 2024-12-21 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_18 | TQGXIIPL | GEDA | 3.846% | Grid Loss | 5:38 | 5:38 | 12:48 | 0:00 | 7.1667 | 7.1667 | Stop Due to line jumper open after VCB Charge then reset and start wtg | Close | 0.27564 | IG Breakdown Maintenance | O2 Project | 4.2 | 123.6 | 885.8
281 | 2024-12-21 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_16 | TQGXIIPL | GEDA | 3.846% | Grid Loss | 5:38 | 5:38 | 12:48 | 0:00 | 7.1667 | 7.1667 | Stop Due to line jumper open after VCB Charge then reset and start wtg | Close | 0.27564 | IG Breakdown Maintenance | O2 Project | 4.2 | 186 | 1333
282 | 2024-12-21 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_20 | TQGXIIPL | GEDA | 3.846% | Grid Loss | 5:38 | 5:38 | 12:48 | 0:00 | 7.1667 | 7.1667 | Stop Due to line jumper open after VCB Charge then reset and start wtg | Close | 0.27564 | IG Breakdown Maintenance | O2 Project | 4.2 | 154.8 | 1109.4
283 | 2024-12-21 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_22 | TQGXIIPL | GEDA | 3.846% | Grid Loss | 5:38 | 5:38 | 12:48 | 0:00 | 7.1667 | 7.1667 | Stop Due to line jumper open after VCB Charge then reset and start wtg | Close | 0.27564 | IG Breakdown Maintenance | O2 Project | 4.2 | 208 | 1490.6667
284 | 2024-12-21 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_21 | TQGXIIPL | GEDA | 3.846% | Grid Loss | 5:38 | 5:38 | 12:48 | 0:00 | 7.1667 | 7.1667 | Stop Due to line jumper open after VCB Charge then reset and start wtg | Close | 0.27564 | IG Breakdown Maintenance | O2 Project | 4.2 | 154.8 | 1109.4
285 | 2024-12-21 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_24 | TQGXIIPL | GEDA | 3.846% | Grid Loss | 11:53 | 11:53 | 12:09 | 0:00 | 0.26667 | 0.26667 | After grid resume found VCB trip so Charge it. | Close | 0.010256 | IG Breakdown Maintenance | O2 Project | 4.2 | 208 | 55.4667
286 | 2024-12-21 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_25 | TQGXIIPL | GEDA | 3.846% | Grid Loss | 9:57 | 9:57 | 17:09 | 0:00 | 7.2 | 7.2 | Line Punch point closing | Close | 0.27692 | IG Breakdown Maintenance | O2 Project | 4.2 | 501.1 | 3607.92
287 | 2024-12-21 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_05 | TQGXIIPL | GEDA | 3.846% | Grid Loss | 10:20 | 10:20 | 17:00 | 0:00 | 6.6667 | 6.6667 | Line Punch point closing | Close | 0.25641 | IG Breakdown Maintenance | O2 Project | 4.2 | 469.4 | 3129.3333
288 | 2024-12-22 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Shutdown for O2-05 AND O2-02 Line Jumper Open work | 8:50 | 8:50 | 9:17 | 0:00 | 0.45 | 0.45 | Feeder -1 Shutdown for O2-05 AND O2-02 Line Jumper Open work | Close | 0.225 | IG Breakdown Maintenance | O2 Project | 4.4 | 274 | 1849.5
289 | 2024-12-22 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Shutdown for O2-05 AND O2-02 Line Jumper close work | 13:35 | 13:35 | 14:25 | 0:00 | 0.83333 | 0.83333 | Feeder -1 Shutdown for O2-05 AND O2-02 Line Jumper close work | Close | 0.41667 | IG Breakdown Maintenance | O2 Project | 4.4 | 274 | 3425
290 | 2024-12-22 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Line tripped over current & Earth fault /Master Relay Trip | 12:07 | 12:07 | 12:26 | 0:00 | 0.31667 | 0.31667 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on ocnductor ,so remove it and charge the feeder-01 | Close | 0.15833 | IG Breakdown Maintenance | O2 Project | 4.4 | 274 | 1301.5
291 | 2024-12-22 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Line tripped over current & Earth fault /Master Relay Trip | 22:02 | 22:02 | 22:27 | 0:00 | 0.41667 | 0.41667 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on ocnductor ,so remove it and charge the feeder-01 | Close | 0.20833 | IG Breakdown Maintenance | O2 Project | 4.4 | 274 | 1712.5
292 | 2024-12-22 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_08 | TQGXIIPL | GEDA | 3.846% | O2-08 Grid Loss | 9:27 | 9:27 | 10:23 | 0:00 | 0.93333 | 0.93333 | After grid resume found VCB trip so Charge it. | Close | 0.035897 | IG Breakdown Maintenance | O2 Project | 4.4 | 274 | 255.7333
293 | 2024-12-22 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_02 | TQGXIIPL | GEDA | 3.846% | O2-05 And O2-02 Line Punch Point closing work ( Project ) | 8:50 | 8:50 | 14:25 | 0:00 | 5.5833 | 5.5833 | O2-05 And O2-02 Line Punch Point closing work ( Project ) | Close | 0.21474 | IG Breakdown Maintenance | O2 Project | 4.4 | 274 | 1529.8333
294 | 2024-12-22 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_05 | TQGXIIPL | GEDA | 3.846% | O2-05 And O2-02 Line Punch Point closing work ( Project ) | 8:50 | 8:50 | 14:25 | 0:00 | 5.5833 | 5.5833 | O2-05 And O2-02 Line Punch Point closing work ( Project ) | Close | 0.21474 | IG Breakdown Maintenance | O2 Project | 4.4 | 274 | 1529.8333
295 | 2024-12-22 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_08 | TQGXIIPL | GEDA | 3.846% | O2-08 Grid Loss | 14:25 | 14:25 | 14:48 | 0:00 | 0.38333 | 0.38333 | After grid resume found VCB tripped so Charge it. | Close | 0.014744 | IG Breakdown Maintenance | O2 Project | 4.4 | 274 | 105.0333
296 | 2024-12-22 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_05 | TQGXIIPL | GEDA | 3.846% | O2-05 Grid Loss | 22:37 | 22:37 | 23:48 | 0:00 | 1.1833 | 1.1833 | After grid resume found VCB tripped so Charge it. | Close | 0.045513 | IG Breakdown Maintenance | O2 Project | 4.4 | 274 | 324.2333
297 | 2024-12-22 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_08 | TQGXIIPL | GEDA | 3.846% | O2-08 Grid loss | 22:37 | 22:37 | 22:54 | 0:00 | 0.28333 | 0.28333 | After grid resume found VCB tripped so Charge it. | Close | 0.010897 | IG Breakdown Maintenance | O2 Project | 4.4 | 274 | 77.6333
298 | 2024-12-23 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Line tripped over current & Earth fault /Master Relay Tripped | 1:22 | 1:22 | 1:37 | 0:00 | 0.25 | 0.25 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on ocnductor ,so remove it and charge the feeder-01 | Close | 0.125 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 1641.375
299 | 2024-12-23 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Line tripped over current & Earth fault /Master Relay Tripped | 7:01 | 7:01 | 7:25 | 0:00 | 0.4 | 0.4 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on ocnductor ,so remove it and charge the feeder-01 | Close | 0.2 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 2626.2
300 | 2024-12-23 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Line tripped over current & Earth fault /Master Relay Tripped | 19:17 | 19:17 | 19:39 | 0:00 | 0.36667 | 0.36667 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on ocnductor ,so remove it and charge the feeder-01 | Close | 0.18333 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 2407.35
301 | 2024-12-23 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | O2-01 Line Punch Point closing work (Project) O2-01 Line Jumper Open Work | 9:06 | 9:06 | 9:56 | 0:00 | 0.83333 | 0.83333 | O2-01 Line Punch Point closing work (Project) O2-01 Line Jumper Open Work | Close | 0.41667 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 5471.25
302 | 2024-12-23 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | O2-01 Line Punch Point closing work (Project) O2-01 Line Jumper close Work | 15:50 | 15:50 | 16:22 | 0:00 | 0.53333 | 0.53333 | O2-01 Line Punch Point closing work (Project) O2-01 Line Jumper close Work | Close | 0.26667 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 3501.6
303 | 2024-12-23 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_08 | TQGXIIPL | GEDA | 3.846% | O2-08 Grid Loss | 1:42 | 1:42 | 2:42 | 0:00 | 1 | 1 | After grid resume found VCB tripped so Charge it. | Close | 0.038462 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 437.7
304 | 2024-12-23 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_08 | TQGXIIPL | GEDA | 3.846% | O2-08 Grid Loss | 7:35 | 7:35 | 8:04 | 0:00 | 0.48333 | 0.48333 | After grid resume found VCB tripped so Charge it. | Close | 0.01859 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 211.555
305 | 2024-12-23 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_08 | TQGXIIPL | GEDA | 3.846% | O2-08 Grid Loss | 19:49 | 19:49 | 20:31 | 0:00 | 0.7 | 0.7 | After grid resume found VCB tripped so Charge it. | Close | 0.026923 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 306.39
306 | 2024-12-23 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_05 | TQGXIIPL | GEDA | 3.846% | O2-05 Grid Loss | 19:49 | 19:49 | 21:43 | 0:00 | 1.9 | 1.9 | After grid resume found VCB tripped so Charge it. | Close | 0.073077 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 831.63
307 | 2024-12-23 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_05 | TQGXIIPL | GEDA | 3.846% | O2-05 Grid Loss | 7:35 | 7:35 | 9:14 | 0:00 | 1.65 | 1.65 | After grid resume found VCB tripped so Charge it. | Close | 0.063462 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 722.205
308 | 2024-12-23 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_05 | TQGXIIPL | GEDA | 3.846% | O2-05 Grid Loss | 1:42 | 1:42 | 3:20 | 0:00 | 1.6333 | 1.6333 | After grid resume found VCB tripped so Charge it. | Close | 0.062821 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 714.91
309 | 2024-12-23 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_11 | TQGXIIPL | GEDA | 3.846% | O2-11 Grid Loss | 19:49 | 19:49 | 20:50 | 0:00 | 1.0167 | 1.0167 | After grid resume found VCB tripped so Charge it. | Close | 0.039103 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 444.995
310 | 2024-12-23 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_01 | TQGXIIPL | GEDA | 3.846% | O2-01 Grid Loss | 9:06 | 9:06 | 16:30 | 0:00 | 7.4 | 7.4 | Feeder-1 Shutdown for O2-01 Line Jumper Open Work ( Project Team ) | Close | 0.28462 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 3238.98
311 | 2024-12-23 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_05 | TQGXIIPL | GEDA | 3.846% | O2-05 Grid Loss | 9:06 | 9:06 | 16:30 | 0:00 | 7.4 | 7.4 | Feeder-1 Shutdown for O2-05 Line Jumper Open Work ( Project Team ) | Close | 0.28462 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 3238.98
312 | 2024-12-23 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_25 | TQGXIIPL | GEDA | 3.846% | O2-25 Grid Loss | 9:06 | 9:06 | 16:30 | 0:00 | 7.4 | 7.4 | Feeder-1 Shutdown for O2-25 Line Jumper Open Work ( Project Team ) | Close | 0.28462 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 3238.98
313 | 2024-12-23 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_26 | TQGXIIPL | GEDA | 3.846% | O2-26 Grid Loss | 9:06 | 9:06 | 16:30 | 0:00 | 7.4 | 7.4 | Feeder-1 Shutdown for O2-26 Line Jumper Open Work ( Project Team ) | Close | 0.28462 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 3238.98
314 | 2024-12-23 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_08 | TQGXIIPL | GEDA | 3.846% | O2-08 Grid Loss | 9:06 | 9:06 | 16:30 | 0:00 | 7.4 | 7.4 | Feeder-1 Shutdown for O2-08 Line Jumper Open Work ( Project Team ) | Close | 0.28462 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 3238.98
315 | 2024-12-23 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_02 | TQGXIIPL | GEDA | 3.846% | O2-02 Grid Loss | 9:06 | 9:06 | 16:30 | 0:00 | 7.4 | 7.4 | Feeder-1 Shutdown for O2-02 Line Jumper Open Work ( Project Team ) | Close | 0.28462 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 3238.98
316 | 2024-12-24 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_18 | TQGXIIPL | GEDA | 3.846% | O2-18 Grid Loss | 15:56 | 15:56 | 17:06 | 0:00 | 1.1667 | 1.1667 | VCB Trip After VCB Charge and start wtg | Close | 0.044872 | IG Breakdown Maintenance | O2 Project | 6.5 | 946 | 1103.6667
317 | 2024-12-24 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_23 | TQGXIIPL | GEDA | 3.846% | O2-23 Grid Loss | 15:13 | 15:13 | 15:51 | 0:00 | 0.63333 | 0.63333 | VCB Trip After VCB Charge and start wtg | Close | 0.024359 | IG Breakdown Maintenance | O2 Project | 6.5 | 946 | 599.1333
318 | 2024-12-25 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Line tripped over current & Earth fault /Master Relay Tripped | 5:58 | 5:58 | 6:11 | 0:00 | 0.21667 | 0.21667 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on ocnductor ,so remove it and charge the feeder-01 | Close | 0.10833 | IG Breakdown Maintenance | O2 Project | 6.6 | 990.6 | 3219.45
319 | 2024-12-25 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Line tripped over current & Earth fault /Master Relay Tripped | 18:29 | 18:29 | 18:49 | 0:00 | 0.33333 | 0.33333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on ocnductor ,so remove it and charge the feeder-01 | Close | 0.16667 | IG Breakdown Maintenance | O2 Project | 6.6 | 990.6 | 4953
320 | 2024-12-25 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Line tripped over current & Earth fault /Master Relay Tripped | 9:24 | 9:24 | 10:38 | 0:00 | 1.2333 | 1.2333 | Feeder-2 Tripped in over current & Earth fault ( Full fully tripped by Hytech team ) | Close | 0.61667 | IG Breakdown Maintenance | O2 Project | 6.6 | 990.6 | 13439.14
321 | 2024-12-25 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Sahutdown for O2-04 And 07 Line Jumper open work | 19:45 | 19:45 | 20:20 | 0:00 | 0.58333 | 0.58333 | Feeder-2 Sahutdown for O2-04 And 07 Line Jumper open work | Close | 0.29167 | IG Breakdown Maintenance | O2 Project | 6.6 | 990.6 | 6356.35
322 | 2024-12-25 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Sahutdown for O2-04 And 07 Line Jumper CLOSE work | 21:35 | 21:35 | 22:50 | 0:00 | 1.25 | 1.25 | Feeder-2 Sahutdown for O2-04 And 07 Line Jumper CLOSE work | Close | 0.625 | IG Breakdown Maintenance | O2 Project | 6.6 | 990.6 | 13620.75
323 | 2024-12-25 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_26 | TQGXIIPL | GEDA | 3.846% | O2-26 Grid Loss | 6:26 | 6:26 | 7:01 | 0:00 | 0.58333 | 0.58333 | After grid resume found VCB tripped so Charge it. | Close | 0.022436 | IG Breakdown Maintenance | O2 Project | 6.6 | 990.6 | 6356.35
324 | 2024-12-25 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_13 | TQGXIIPL | GEDA | 3.846% | O2-13 Grid Loss | 6:26 | 6:26 | 6:44 | 0:00 | 0.3 | 0.3 | After grid resume found VCB tripped so Charge it. | Close | 0.011538 | IG Breakdown Maintenance | O2 Project | 6.6 | 990.6 | 297.18
325 | 2024-12-25 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_08 | TQGXIIPL | GEDA | 3.846% | O2-08 Grid Loss | 6:26 | 6:26 | 7:10 | 0:00 | 0.73333 | 0.73333 | After grid resume found VCB tripped so Charge it. | Close | 0.028205 | IG Breakdown Maintenance | O2 Project | 6.6 | 990.6 | 726.44
326 | 2024-12-25 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_24 | TQGXIIPL | GEDA | 3.846% | O2-24 Grid Loss | 10:48 | 10:48 | 11:15 | 0:00 | 0.45 | 0.45 | After grid resume found VCB tripped so Charge it. | Close | 0.017308 | IG Breakdown Maintenance | O2 Project | 6.6 | 990.6 | 445.77
327 | 2024-12-25 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_19 | TQGXIIPL | GEDA | 3.846% | O2-19 Grid Loss | 10:48 | 10:48 | 12:05 | 0:00 | 1.2833 | 1.2833 | After grid resume found VCB tripped so Charge it. | Close | 0.049359 | IG Breakdown Maintenance | O2 Project | 6.6 | 990.6 | 1271.27
328 | 2024-12-25 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_20 | TQGXIIPL | GEDA | 3.846% | O2-20 Grid Loss | 14:59 | 14:59 | 16:19 | 0:00 | 1.3333 | 1.3333 | VCB manually tripped by project team for transformer foundation work | Close | 0.051282 | IG Breakdown Maintenance | O2 Project | 6.6 | 990.6 | 1320.8
329 | 2024-12-25 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_16 | TQGXIIPL | GEDA | 3.846% | O2-16 Grid Loss | 16:45 | 16:45 | 18:00 | 0:00 | 1.25 | 1.25 | VCB manually tripped by project team for transformer foundation work | Close | 0.048077 | IG Breakdown Maintenance | O2 Project | 6.6 | 990.6 | 1238.25
330 | 2024-12-25 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_08 | TQGXIIPL | GEDA | 3.846% | O2-08 Grid Loss | 18:59 | 18:59 | 19:27 | 0:00 | 0.46667 | 0.46667 | After grid resume found VCB tripped so Charge it. | Close | 0.017949 | IG Breakdown Maintenance | O2 Project | 6.6 | 990.6 | 462.28
331 | 2024-12-25 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_05 | TQGXIIPL | GEDA | 3.846% | O2-05 Grid Loss | 18:59 | 18:59 | 20:47 | 0:00 | 1.8 | 1.8 | After grid resume found VCB tripped so Charge it. | Close | 0.069231 | IG Breakdown Maintenance | O2 Project | 6.6 | 990.6 | 1783.08
332 | 2024-12-25 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_07 | TQGXIIPL | GEDA | 3.846% | O2-07 Grid Loss | 22:55 | 22:55 | 23:41 | 0:00 | 0.76667 | 0.76667 | After grid resume found VCB tripped so Charge it. | Close | 0.029487 | IG Breakdown Maintenance | O2 Project | 6.6 | 990.6 | 759.46
333 | 2024-12-25 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_04 | TQGXIIPL | GEDA | 3.846% | O2-04 Grid Loss | 9:24 | 9:24 | 22:50 | 0:00 | 13.4333 | 13.4333 | Feeer-02 O2-04 And O2-07 Line Punch Point closing work (Project Work ) | Close | 0.51667 | IG Breakdown Maintenance | O2 Project | 6.6 | 990.6 | 13307.06
334 | 2024-12-25 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_07 | TQGXIIPL | GEDA | 3.846% | O2-07 Grid Loss | 9:24 | 9:24 | 22:50 | 0:00 | 13.4333 | 13.4333 | Feeer-02 O2-04 And O2-07 Line Punch Point closing work (Project Work ) | Close | 0.51667 | IG Breakdown Maintenance | O2 Project | 6.6 | 990.6 | 13307.06
334 | 2024-12-26 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 shutdown for O2-19 Line Jumper Opening work | 9:09 | 9:09 | 10:05 | 0:00 | 0.93333 | 0.93333 | Feeder-2 shutdown for O2-19 Line Jumper Opening work | Close | 0.46667 | IG Breakdown Maintenance | O2 Project | 5 | 406 | 4168.2667
334 | 2024-12-26 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 shutdown for O2-19 Line Jumper closing work | 16:00 | 16:00 | 17:00 | 0:00 | 1 | 1 | Feeder-2 shutdown for O2-19 Line Jumper closing work | Close | 0.5 | IG Breakdown Maintenance | O2 Project | 5 | 406 | 4466
334 | 2024-12-26 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Line tripped over current & Earth fault /Master Relay Tripped | 18:01 | 18:01 | 18:29 | 0:00 | 0.46667 | 0.46667 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on ocnductor ,so remove it and charge the feeder-01 | Close | 0.23333 | IG Breakdown Maintenance | O2 Project | 5 | 406 | 3031.4667
334 | 2024-12-26 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_17 | TQGXIIPL | GEDA | 3.846% | O2-17 Grid Loss | 10:45 | 10:45 | 12:20 | 0:00 | 1.5833 | 1.5833 | USS yard VCB check by BOP team no found any abnormality then charge vcb (VCB Tripped by Transformer foudation pament Issue) | Close | 0.060897 | IG Breakdown Maintenance | O2 Project | 5 | 406 | 5785.5
334 | 2024-12-26 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_18 | TQGXIIPL | GEDA | 3.846% | O2-18 Grid Loss | 17:00 | 17:00 | 18:15 | 0:00 | 1.25 | 1.25 | USS yard VCB check by BOP team no found any abnormality then charge vcb (VCB Tripped by Transformer foudation pament Issue) | Close | 0.048077 | IG Breakdown Maintenance | O2 Project | 5 | 406 | 507.5
334 | 2024-12-26 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_22 | TQGXIIPL | GEDA | 3.846% | O2-22 Grid Loss | 13:06 | 13:06 | 13:57 | 0:00 | 0.85 | 0.85 | USS yard VCB check by BOP team no found any abnormality then charge vcb (VCB Tripped by Transformer foudation pament Issue) | Close | 0.032692 | IG Breakdown Maintenance | O2 Project | 5 | 406 | 345.1
334 | 2024-12-26 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_21 | TQGXIIPL | GEDA | 3.846% | O2-21 Grid Loss | 14:36 | 14:36 | 17:55 | 0:00 | 3.3167 | 3.3167 | USS yard VCB check by BOP team no found any abnormality then charge vcb (VCB Tripped by Transformer foudation pament Issue) | Close | 0.12756 | IG Breakdown Maintenance | O2 Project | 5 | 406 | 1346.5667
334 | 2024-12-26 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_08 | TQGXIIPL | GEDA | 3.846% | O2-08 Grid Loss | 18:39 | 18:39 | 18:55 | 0:00 | 0.26667 | 0.26667 | After grid resume found VCB tripped so Charge it. | Close | 0.010256 | IG Breakdown Maintenance | O2 Project | 5 | 406 | 108.2667
334 | 2024-12-26 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_19 | TQGXIIPL | GEDA | 3.846% | O2-19 Grid Loss | 9:29 | 9:29 | 17:15 | 0:00 | 7.7667 | 7.7667 | Feeder-2 shutdown for O2-19 Line Jumper closing work | Close | 0.29872 | IG Breakdown Maintenance | O2 Project | 5 | 406 | 3153.2667
335 | 2024-12-27 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on ocnductor ,so remove it and charge the feeder-01 | 17:27 | 17:27 | 17:38 | 0:00 | 0.18333 | 0.18333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on ocnductor ,so remove it and charge the feeder-01 | Close | 0.091667 | IG Breakdown Maintenance | O2 Project | 5.7 | 627.9 | 1726.725
336 | 2024-12-27 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Shutdown for O2-18 Line Jumper opening work | 9:00 | 9:00 | 9:53 | 0:00 | 0.88333 | 0.88333 | Feeder-2 Shutdown for O2-18 Line Jumper opening work | Close | 0.44167 | IG Breakdown Maintenance | O2 Project | 5.7 | 627.9 | 6101.095
337 | 2024-12-27 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Shutdown for O2-18 Line closing work | 17:23 | 17:23 | 18:16 | 0:00 | 0.88333 | 0.88333 | Feeder-2 Shutdown for O2-18 Line closing work | Close | 0.44167 | IG Breakdown Maintenance | O2 Project | 5.7 | 627.9 | 6101.095
338 | 2024-12-27 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_10 | TQGXIIPL | GEDA | 3.846% | O2-10 Grid Loss | 9:31 | 9:31 | 10:24 | 0:00 | 0.88333 | 0.88333 | USS yard VCB check by BOP team no found any abnormality then charge vcb (VCB Tripped by Transformer foudation pament Issue) | Close | 0.033974 | IG Breakdown Maintenance | O2 Project | 5.7 | 627.9 | 554.645
339 | 2024-12-27 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_24 | TQGXIIPL | GEDA | 3.846% | O2-24 Grid Loss | 12:28 | 12:28 | 13:12 | 0:00 | 0.73333 | 0.73333 | USS yard VCB check by BOP team no found any abnormality then charge vcb (VCB Tripped by Transformer foudation pament Issue) | Close | 0.028205 | IG Breakdown Maintenance | O2 Project | 5.7 | 627.9 | 460.46
340 | 2024-12-27 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_15 | TQGXIIPL | GEDA | 3.846% | O2-15 Grid Loss | 13:02 | 13:02 | 13:42 | 0:00 | 0.66667 | 0.66667 | USS yard VCB check by BOP team no found any abnormality then charge vcb (VCB Tripped by Transformer foudation pament Issue) | Close | 0.025641 | IG Breakdown Maintenance | O2 Project | 5.7 | 627.9 | 418.6
341 | 2024-12-27 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_14 | TQGXIIPL | GEDA | 3.846% | O2-14 Grid Loss | 14:02 | 14:02 | 14:52 | 0:00 | 0.83333 | 0.83333 | USS yard VCB check by BOP team no found any abnormality then charge vcb (VCB Tripped by Transformer foudation pament Issue) | Close | 0.032051 | IG Breakdown Maintenance | O2 Project | 5.7 | 627.9 | 523.25
342 | 2024-12-27 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_11 | TQGXIIPL | GEDA | 3.846% | O2-11 Grid Loss | 14:56 | 14:56 | 15:52 | 0:00 | 0.93333 | 0.93333 | USS yard VCB check by BOP team no found any abnormality then charge vcb (VCB Tripped by Transformer foudation pament Issue) | Close | 0.035897 | IG Breakdown Maintenance | O2 Project | 5.7 | 627.9 | 586.04
343 | 2024-12-27 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_12 | TQGXIIPL | GEDA | 3.846% | O2-12 Grid Loss | 16:03 | 16:03 | 16:52 | 0:00 | 0.81667 | 0.81667 | USS yard VCB check by BOP team no found any abnormality then charge vcb (VCB Tripped by Transformer foudation pament Issue) | Close | 0.03141 | IG Breakdown Maintenance | O2 Project | 5.7 | 627.9 | 512.785
344 | 2024-12-27 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_25 | TQGXIIPL | GEDA | 3.846% | O2-25 Grid Loss | 17:52 | 17:52 | 18:25 | 0:00 | 0.55 | 0.55 | After grid resume found VCB tripped so Charge it. | Close | 0.021154 | IG Breakdown Maintenance | O2 Project | 5.7 | 627.9 | 345.345
345 | 2024-12-27 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_13 | TQGXIIPL | GEDA | 3.846% | O2-13 Grid Loss | 18:36 | 18:36 | 19:12 | 0:00 | 0.6 | 0.6 | USS yard VCB check by BOP team no found any abnormality then charge vcb (VCB Tripped by Transformer foudation pament Issue) | Close | 0.023077 | IG Breakdown Maintenance | O2 Project | 5.7 | 627.9 | 376.74
346 | 2024-12-27 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_21 | TQGXIIPL | GEDA | 3.846% | O2-21 Grid Loss | 18:26 | 18:26 | 19:12 | 0:00 | 0.76667 | 0.76667 | After grid resume found VCB tripped so Charge it. | Close | 0.029487 | IG Breakdown Maintenance | O2 Project | 5.7 | 627.9 | 481.39
347 | 2024-12-27 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_06 | TQGXIIPL | GEDA | 3.846% | O2-06 Grid Loss | 9:00 | 9:00 | 18:26 | 0:00 | 9.4333 | 9.4333 | O2-18,06,17,21,22 , O2-18 Line jumper work | Close | 0.36282 | IG Breakdown Maintenance | O2 Project | 5.7 | 627.9 | 5923.19
348 | 2024-12-27 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_17 | TQGXIIPL | GEDA | 3.846% | O2-17 Grid Loss | 9:00 | 9:00 | 18:26 | 0:00 | 9.4333 | 9.4333 | O2-18,06,17,21,22 , O2-18 Line jumper work | Close | 0.36282 | IG Breakdown Maintenance | O2 Project | 5.7 | 627.9 | 5923.19
349 | 2024-12-27 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_21 | TQGXIIPL | GEDA | 3.846% | O2-21 Grid Loss | 9:00 | 9:00 | 18:26 | 0:00 | 9.4333 | 9.4333 | O2-18,06,17,21,22 , O2-18 Line jumper work | Close | 0.36282 | IG Breakdown Maintenance | O2 Project | 5.7 | 627.9 | 5923.19
350 | 2024-12-27 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_22 | TQGXIIPL | GEDA | 3.846% | O2-22 Grid Loss | 9:00 | 9:00 | 18:26 | 0:00 | 9.4333 | 9.4333 | O2-18,06,17,21,22 , O2-18 Line jumper work | Close | 0.36282 | IG Breakdown Maintenance | O2 Project | 5.7 | 627.9 | 5923.19
351 | 2024-12-27 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_18 | TQGXIIPL | GEDA | 3.846% | O2-18 Grid Loss | 9:00 | 9:00 | 18:26 | 0:00 | 9.4333 | 9.4333 | O2-18,06,17,21,22 , O2-18 Line jumper work | Close | 0.36282 | IG Breakdown Maintenance | O2 Project | 5.7 | 627.9 | 5923.19
352 | 2024-12-28 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on ocnductor ,so remove it and charge the feeder-01 | 10:27 | 10:27 | 10:45 | 0:00 | 0.3 | 0.3 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on ocnductor ,so remove it and charge the feeder-01 | Close | 0.15 | IG Breakdown Maintenance | O2 Project | 6.9 | 1124.4 | 5059.8
353 | 2024-12-28 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Shutdown for O2-22 and O2-17 Line Jumper opening work | 9:00 | 9:00 | 9:47 | 0:00 | 0.78333 | 0.78333 | Feeder-2 Shutdown for O2-22 and O2-17 Line Jumper opening work | Close | 0.39167 | IG Breakdown Maintenance | O2 Project | 6.9 | 1124.4 | 9688.58
354 | 2024-12-28 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Shutdown for O2-22 and O2-17 Line Jumper closing work | 17:20 | 17:20 | 17:59 | 0:00 | 0.65 | 0.65 | Feeder-2 Shutdown for O2-22 and O2-17 Line Jumper closing work | Close | 0.325 | IG Breakdown Maintenance | O2 Project | 6.9 | 1124.4 | 8039.46
355 | 2024-12-28 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_03 | TQGXIIPL | GEDA | 3.846% | O2-03 Grid Loss | 11:12 | 11:12 | 12:33 | 0:00 | 1.35 | 1.35 | VCB manually tripped by project team for transformer foundation work | Close | 0.051923 | IG Breakdown Maintenance | O2 Project | 6.9 | 1124.4 | 1517.94
356 | 2024-12-28 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_09 | TQGXIIPL | GEDA | 3.846% | O2-09 Grid Loss | 12:58 | 12:58 | 13:39 | 0:00 | 0.68333 | 0.68333 | VCB manually tripped by project team for transformer foundation work | Close | 0.026282 | IG Breakdown Maintenance | O2 Project | 6.9 | 1124.4 | 768.34
357 | 2024-12-28 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_23 | TQGXIIPL | GEDA | 3.846% | O2-23 Grid Loss | 14:38 | 14:38 | 16:24 | 0:00 | 1.7667 | 1.7667 | VCB manually tripped by project team for transformer foundation work | Close | 0.067949 | IG Breakdown Maintenance | O2 Project | 6.9 | 1124.4 | 1986.44
358 | 2024-12-28 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_26 | TQGXIIPL | GEDA | 3.846% | O2-26 Grid Loss | 16:24 | 16:24 | 17:20 | 0:00 | 0.93333 | 0.93333 | VCB manually tripped by project team for transformer foundation work | Close | 0.035897 | IG Breakdown Maintenance | O2 Project | 6.9 | 1124.4 | 1049.44
359 | 2024-12-28 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_01 | TQGXIIPL | GEDA | 3.846% | O2-01 Grid Loss | 17:17 | 17:17 | 18:12 | 0:00 | 0.91667 | 0.91667 | VCB manually tripped by project team for transformer foundation work | Close | 0.035256 | IG Breakdown Maintenance | O2 Project | 6.9 | 1124.4 | 1030.7
360 | 2024-12-28 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_22 | TQGXIIPL | GEDA | 3.846% | O2-22 Grid Loss | 9:00 | 9:00 | 18:10 | 0:00 | 9.1667 | 9.1667 | O2-22 And O2-17 Line Jumper Work | Close | 0.35256 | IG Breakdown Maintenance | O2 Project | 6.9 | 1124.4 | 10307
361 | 2024-12-28 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_17 | TQGXIIPL | GEDA | 3.846% | O2-17 Grid Loss | 9:00 | 9:00 | 18:10 | 0:00 | 9.1667 | 9.1667 | O2-22 And O2-17 Line Jumper Work | Close | 0.35256 | IG Breakdown Maintenance | O2 Project | 6.9 | 1124.4 | 10307
362 | 2024-12-29 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Shutdown for O2-17 Line Jumper opening work | 9:04 | 9:04 | 9:47 | 0:00 | 0.71667 | 0.71667 | Feeder-2 Shutdown for O2-17 Line Jumper opening work | Close | 0.35833 | IG Breakdown Maintenance | O2 Project | 6.5 | 946 | 7457.6333
363 | 2024-12-29 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Shutdown for O2-17 Line Jumper closing work | 17:09 | 17:09 | 17:47 | 0:00 | 0.63333 | 0.63333 | Feeder-2 Shutdown for O2-17 Line Jumper closing work | Close | 0.31667 | IG Breakdown Maintenance | O2 Project | 6.5 | 946 | 6590.4667
364 | 2024-12-29 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_04 | TQGXIIPL | GEDA | 3.846% | O2-04 Grid Loss | 13:52 | 13:52 | 14:39 | 0:00 | 0.78333 | 0.78333 | VCB manually tripped by project team for transformer foundation work | Close | 0.030128 | IG Breakdown Maintenance | O2 Project | 6.5 | 946 | 741.0333
365 | 2024-12-29 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_07 | TQGXIIPL | GEDA | 3.846% | O2-07 Grid Loss | 12:44 | 12:44 | 14:14 | 0:00 | 1.5 | 1.5 | VCB manually tripped by project team for transformer foundation work | Close | 0.057692 | IG Breakdown Maintenance | O2 Project | 6.5 | 946 | 1419
366 | 2024-12-29 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_19 | TQGXIIPL | GEDA | 3.846% | O2-19 Grid Loss | 11:16 | 11:16 | 11:42 | 0:00 | 0.43333 | 0.43333 | VCB manually tripped by project team for transformer foundation work | Close | 0.016667 | IG Breakdown Maintenance | O2 Project | 6.5 | 946 | 409.9333
367 | 2024-12-29 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_25 | TQGXIIPL | GEDA | 3.846% | O2-25 Grid Loss | 17:20 | 17:20 | 17:57 | 0:00 | 0.61667 | 0.61667 | VCB manually tripped by project team for transformer foundation work | Close | 0.023718 | IG Breakdown Maintenance | O2 Project | 6.5 | 946 | 583.3667
368 | 2024-12-29 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_17 | TQGXIIPL | GEDA | 3.846% | O2-17 Grid Loss | 9:54 | 9:54 | 17:09 | 0:00 | 7.25 | 7.25 | O2-17 Line Jumper Work | Close | 0.27885 | IG Breakdown Maintenance | O2 Project | 6.5 | 946 | 6858.5
369 | 2024-12-30 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on ocnductor ,so remove it and charge the feeder-01 | 12:37 | 12:37 | 12:55 | 0:00 | 0.3 | 0.3 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on ocnductor ,so remove it and charge the feeder-01 | Close | 0.15 | IG Breakdown Maintenance | O2 Project | 5.9 | 691.3 | 3110.85
370 | 2024-12-30 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Shutdown for O2-17 Line Jumper opening work | 8:55 | 8:55 | 9:47 | 0:00 | 0.86667 | 0.86667 | Feeder-2 Shutdown for O2-17 Line Jumper opening work | Close | 0.43333 | IG Breakdown Maintenance | O2 Project | 5.9 | 691.3 | 6590.3933
371 | 2024-12-30 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Shutdown for O2-17 jumper closeing work and O2-24 jumper opening work. | 12:27 | 12:27 | 13:01 | 0:00 | 0.56667 | 0.56667 | Feeder-2 Shutdown for O2-17 jumper closeing work and O2-24 jumper opening work. | Close | 0.28333 | IG Breakdown Maintenance | O2 Project | 5.9 | 691.3 | 4309.1033
372 | 2024-12-30 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Shutdown for O2-24 jumper Closing work. | 14:53 | 14:53 | 15:47 | 0:00 | 0.9 | 0.9 | Feeder-2 Shutdown for O2-24 jumper Closing work. | Close | 0.45 | IG Breakdown Maintenance | O2 Project | 5.9 | 691.3 | 6843.87
373 | 2024-12-30 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_24 | TQGXIIPL | GEDA | 3.846% | O2-24 Grid Loss | 13:10 | 13:10 | 14:53 | 0:00 | 1.7167 | 1.7167 | O2-24 Line Jumper Work | Close | 0.066026 | IG Breakdown Maintenance | O2 Project | 5.9 | 691.3 | 1186.7317
374 | 2024-12-30 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_17 | TQGXIIPL | GEDA | 3.846% | O2-17 Grid Loss | 9:51 | 9:51 | 12:07 | 0:00 | 2.2667 | 2.2667 | O2-17 Line Jumper Work | Close | 0.087179 | IG Breakdown Maintenance | O2 Project | 5.9 | 691.3 | 1566.9467
375 | 2024-12-31 | 2025 | 2024 | 2024-12-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Shutdown for Punch point closing work | 9:12 | 9:12 | 18:08 | 0:00 | 8.9333 | 8.9333 | Feeder-1 Shutdown for Punch point closing work | Close | 4.4667 | IG Breakdown Maintenance | O2 Project | 5.2 | 669.4 | 89699.6
376 | 2024-12-31 | 2025 | 2024 | 2024-12-01 | Year_1 | O2_15 | TQGXIIPL | GEDA | 3.846% | O2-15 Grid Loss | 18:09 | 18:09 | 18:30 | 0:00 | 0.35 | 0.35 | After grid resume found VCB trip so Charge it. | Close | 0.013462 | IG Breakdown Maintenance | O2 Project | 5.2 | 669.4 | 3514.35
377 | 2025-01-01 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Shutdown for Punch point closing work | 9:09 | 9:09 | 17:57 | 0:00 | 8.8 | 8.8 | Feeder-1 Shutdown for Punch point closing work | Close | 4.4 | IG Breakdown Maintenance | O2 Project | 5.3 | 501.1 | 66145.2
378 | 2025-01-01 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Trip in over current & Earth fault/Master relay trip | 13:26 | 13:26 | 15:18 | 0:00 | 1.8667 | 1.8667 | Feeder-2 Tripped in over current & Earth fault /Master Relay Tripped during petroling found the mNylone rope with shorted 3 conductors | Close | 0.93333 | IG Breakdown Maintenance | O2 Project | 5.3 | 501.1 | 10289.2533
379 | 2025-01-01 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_21 | TQGXIIPL | GEDA | 3.846% | After Feeder charge VCB trip so charge it than reset and start WTG. | 15:18 | 15:18 | 15:24 | 0:00 | 0.1 | 0.1 | After grid VCB charged | Close | 0.0038462 | IG Breakdown Maintenance | O2 Project | 5.3 | 501.1 | 50.11
380 | 2025-01-01 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 23:49 | 23:49 | 24:00 | 0:00 | 0.18333 | 0.18333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.091667 | IG Breakdown Maintenance | O2 Project | 5.3 | 501.1 | 1378.025
381 | 2025-01-02 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 0:00 | 0:00 | 0:11 | 0:00 | 0.18333 | 0.18333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.091667 | IG Breakdown Maintenance | O2 Project | 4.1 | 208 | 572
382 | 2025-01-02 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 5:55 | 5:55 | 6:10 | 0:00 | 0.25 | 0.25 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.125 | IG Breakdown Maintenance | O2 Project | 4.1 | 208 | 780
383 | 2025-01-02 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Shutdown for O2-07,04,19 Line jumper opening Work for Section Isolator Fixing Work. | 9:25 | 9:25 | 10:25 | 0:00 | 1 | 1 | Feeder#2 Shutdown for O2-07,04,19 Line jumper opening Work and Section Isolator Fixing Work. | Close | 0.5 | IG Breakdown Maintenance | O2 Project | 4.1 | 208 | 2288
384 | 2025-01-02 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Shutdown for O2-07,04,19 Line jumper opening Work for Section Isolator Fixing Work. | 17:25 | 17:25 | 19:00 | 0:00 | 1.5833 | 1.5833 | Feeder#2 Shutdown for O2-07,04,19 Line jumper closing Work and Section Isolator Fixing Work. | Close | 0.79167 | IG Breakdown Maintenance | O2 Project | 4.1 | 208 | 3622.6667
385 | 2025-01-02 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 23:21 | 23:21 | 23:35 | 0:00 | 0.23333 | 0.23333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.11667 | IG Breakdown Maintenance | O2 Project | 4.1 | 208 | 728
386 | 2025-01-03 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Shutdown for O2-18,22,17,21,06 Line jumper opening Work for Section Isolator Fixing Work. | 9:29 | 9:29 | 10:37 | 0:00 | 1.1333 | 1.1333 | Feeder-2 Shutdown for O2-18,22,17,21,06 Line jumper opening Work for Section Isolator Fixing Work. | Close | 0.56667 | IG Breakdown Maintenance | O2 Project | 2.7 | 0 | 0
387 | 2025-01-03 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Shutdown for O2-18,22,17,21,06 Line jumper Closing Work for Section Isolator Fixing Work. | 17:08 | 17:08 | 17:38 | 0:00 | 0.5 | 0.5 | Feeder-2 Shutdown for O2-18,22,17,21,06 Line jumper Closing Work for Section Isolator Fixing Work. | Close | 0.25 | IG Breakdown Maintenance | O2 Project | 2.7 | 0 | 0
388 | 2025-01-04 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 22:45 | 22:45 | 22:57 | 0:00 | 0.2 | 0.2 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.1 | IG Breakdown Maintenance | O2 Project | 3.1 | 45.6 | 136.8
389 | 2025-01-04 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_06 | TQGXIIPL | GEDA | 3.846% | Partiyally 33kv Feeder-2 shutdown taken by Project team for Section Isolator Installation work near O2-18. | 9:05 | 9:05 | 17:30 | 0:00 | 8.4167 | 8.4167 | Partiyally 33kv Feeder-2 shutdown taken by Project team for Section Isolator Installation work near O2-18. | Close | 0.32372 | IG Breakdown Maintenance | O2 Project | 3.1 | 45.6 | 383.8
390 | 2025-01-04 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_07 | TQGXIIPL | GEDA | 3.846% | Attend and check found vcb tripped after grid then wip | 18:24 | 18:24 | 24:00 | 0:00 | 5.6 | 5.6 | Attend and check found vcb tripped after grid then wip | Close | 0.21538 | IG Breakdown Maintenance | O2 Project | 3.1 | 45.6 | 255.36
391 | 2025-01-04 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_17 | TQGXIIPL | GEDA | 3.846% | Partiyally 33kv Feeder-2 shutdown taken by Project team for Section Isolator Installation work near O2-18. | 9:00 | 9:00 | 17:30 | 0:00 | 8.5 | 8.5 | Partiyally 33kv Feeder-2 shutdown taken by Project team for Section Isolator Installation work near O2-18. | Close | 0.32692 | IG Breakdown Maintenance | O2 Project | 3.1 | 45.6 | 387.6
392 | 2025-01-04 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_18 | TQGXIIPL | GEDA | 3.846% | Partiyally 33kv Feeder-2 shutdown taken by Project team for Section Isolator Installation work near O2-18. | 9:00 | 9:00 | 17:30 | 0:00 | 8.5 | 8.5 | Partiyally 33kv Feeder-2 shutdown taken by Project team for Section Isolator Installation work near O2-18. | Close | 0.32692 | IG Breakdown Maintenance | O2 Project | 3.1 | 45.6 | 387.6
393 | 2025-01-04 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_21 | TQGXIIPL | GEDA | 3.846% | Partiyally 33kv Feeder-2 shutdown taken by Project team for Section Isolator Installation work near O2-18. | 9:00 | 9:00 | 17:30 | 0:00 | 8.5 | 8.5 | Partiyally 33kv Feeder-2 shutdown taken by Project team for Section Isolator Installation work near O2-18. | Close | 0.32692 | IG Breakdown Maintenance | O2 Project | 3.1 | 45.6 | 387.6
394 | 2025-01-04 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_22 | TQGXIIPL | GEDA | 3.846% | Partiyally 33kv Feeder-2 shutdown taken by Project team for Section Isolator Installation work near O2-18. | 9:00 | 9:00 | 17:30 | 0:00 | 8.5 | 8.5 | Partiyally 33kv Feeder-2 shutdown taken by Project team for Section Isolator Installation work near O2-18. | Close | 0.32692 | IG Breakdown Maintenance | O2 Project | 3.1 | 45.6 | 387.6
395 | 2025-01-05 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 12:06 | 12:06 | 12:53 | 0:00 | 0.78333 | 0.78333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.39167 | IG Breakdown Maintenance | O2 Project | 6.3 | 856.8 | 10067.4
396 | 2025-01-05 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 17:01 | 17:01 | 17:17 | 0:00 | 0.26667 | 0.26667 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.13333 | IG Breakdown Maintenance | O2 Project | 6.3 | 856.8 | 3427.2
397 | 2025-01-05 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 19:01 | 19:01 | 19:18 | 0:00 | 0.28333 | 0.28333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.14167 | IG Breakdown Maintenance | O2 Project | 6.3 | 856.8 | 3641.4
398 | 2025-01-05 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 21:58 | 21:58 | 23:07 | 0:00 | 1.15 | 1.15 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.575 | IG Breakdown Maintenance | O2 Project | 6.3 | 856.8 | 14779.8
399 | 2025-01-05 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_06 | TQGXIIPL | GEDA | 3.846% | WTG Manual stop section Isolator open for O2-17,22 Line Section Isolator Fixing Work (Project Work) | 9:11 | 9:11 | 9:58 | 0:00 | 0.78333 | 0.78333 | WTG Manual stop section Isolator open for O2-17,22 Line Section Isolator Fixing Work (Project Work) | Close | 0.030128 | IG Breakdown Maintenance | O2 Project | 6.3 | 856.8 | 671.16
400 | 2025-01-05 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_17 | TQGXIIPL | GEDA | 3.846% | WTG Manual stop section Isolator open for O2-17,22 Line Section Isolator Fixing Work (Project Work) | 9:11 | 9:11 | 16:42 | 0:00 | 7.5167 | 7.5167 | WTG Manual stop section Isolator open for O2-17,22 Line Section Isolator Fixing Work (Project Work) | Close | 0.2891 | IG Breakdown Maintenance | O2 Project | 6.3 | 856.8 | 6440.28
401 | 2025-01-05 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_18 | TQGXIIPL | GEDA | 3.846% | WTG Manual stop section Isolator open for O2-17,22 Line Section Isolator Fixing Work (Project Work) | 9:11 | 9:11 | 9:58 | 0:00 | 0.78333 | 0.78333 | WTG Manual stop section Isolator open for O2-17,22 Line Section Isolator Fixing Work (Project Work) | Close | 0.030128 | IG Breakdown Maintenance | O2 Project | 6.3 | 856.8 | 671.16
402 | 2025-01-05 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_21 | TQGXIIPL | GEDA | 3.846% | WTG Manual stop section Isolator open for O2-17,22 Line Section Isolator Fixing Work (Project Work) | 9:11 | 9:11 | 9:58 | 0:00 | 0.78333 | 0.78333 | WTG Manual stop section Isolator open for O2-17,22 Line Section Isolator Fixing Work (Project Work) | Close | 0.030128 | IG Breakdown Maintenance | O2 Project | 6.3 | 856.8 | 671.16
403 | 2025-01-05 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_22 | TQGXIIPL | GEDA | 3.846% | WTG Manual stop section Isolator open for O2-17,22 Line Section Isolator Fixing Work (Project Work) | 9:11 | 9:11 | 16:42 | 0:00 | 7.5167 | 7.5167 | WTG Manual stop section Isolator open for O2-17,22 Line Section Isolator Fixing Work (Project Work) | Close | 0.2891 | IG Breakdown Maintenance | O2 Project | 6.3 | 856.8 | 6440.28
404 | 2025-01-05 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_06 | TQGXIIPL | GEDA | 3.846% | WTG Manual stop section Isolator open for O2-17,22 Line Section Isolator Fixing Work (Project Work) | 16:21 | 16:21 | 16:42 | 0:00 | 0.35 | 0.35 | WTG Manual stop section Isolator open for O2-17,22 Line Section Isolator Fixing Work (Project Work) | Close | 0.013462 | IG Breakdown Maintenance | O2 Project | 6.3 | 856.8 | 299.88
405 | 2025-01-05 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_18 | TQGXIIPL | GEDA | 3.846% | WTG Manual stop section Isolator open for O2-17,22 Line Section Isolator Fixing Work (Project Work) | 16:21 | 16:21 | 16:42 | 0:00 | 0.35 | 0.35 | WTG Manual stop section Isolator open for O2-17,22 Line Section Isolator Fixing Work (Project Work) | Close | 0.013462 | IG Breakdown Maintenance | O2 Project | 6.3 | 856.8 | 299.88
406 | 2025-01-05 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_21 | TQGXIIPL | GEDA | 3.846% | WTG Manual stop section Isolator open for O2-17,22 Line Section Isolator Fixing Work (Project Work) | 16:21 | 16:21 | 16:42 | 0:00 | 0.35 | 0.35 | WTG Manual stop section Isolator open for O2-17,22 Line Section Isolator Fixing Work (Project Work) | Close | 0.013462 | IG Breakdown Maintenance | O2 Project | 6.3 | 856.8 | 299.88
407 | 2025-01-05 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_06 | TQGXIIPL | GEDA | 3.846% | O2-06 Grid loss | 16:42 | 16:42 | 17:03 | 0:00 | 0.35 | 0.35 | After VCB Charge than reset and start WTG. | Close | 0.013462 | IG Breakdown Maintenance | O2 Project | 6.3 | 856.8 | 299.88
408 | 2025-01-05 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_21 | TQGXIIPL | GEDA | 3.846% | O2-21 Grid loss | 16:42 | 16:42 | 17:21 | 0:00 | 0.65 | 0.65 | After VCB Charge than reset and start WTG. | Close | 0.025 | IG Breakdown Maintenance | O2 Project | 6.3 | 856.8 | 556.92
409 | 2025-01-05 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_22 | TQGXIIPL | GEDA | 3.846% | O2-22 Grid loss | 16:42 | 16:42 | 17:33 | 0:00 | 0.85 | 0.85 | After VCB Charge than reset and start WTG. | Close | 0.032692 | IG Breakdown Maintenance | O2 Project | 6.3 | 856.8 | 728.28
410 | 2025-01-05 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_07 | TQGXIIPL | GEDA | 3.846% | O2-07 Grid loss | 0:00 | 0:00 | 1:37 | 0:00 | 1.6167 | 1.6167 | After VCB Charge than reset and start WTG. | Close | 0.062179 | IG Breakdown Maintenance | O2 Project | 6.3 | 856.8 | 1385.16
411 | 2025-01-05 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_07 | TQGXIIPL | GEDA | 3.846% | O2-07 Grid loss | 0:00 | 0:00 | 0:27 | 0:00 | 0.45 | 0.45 | After VCB Charge than reset and start WTG. | Close | 0.017308 | IG Breakdown Maintenance | O2 Project | 6.3 | 856.8 | 385.56
412 | 2025-01-06 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 10:57 | 10:57 | 11:47 | 0:00 | 0.83333 | 0.83333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.41667 | IG Breakdown Maintenance | O2 Project | 8.4 | 1922.8 | 24035
413 | 2025-01-06 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 15:33 | 15:33 | 16:08 | 0:00 | 0.58333 | 0.58333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.29167 | IG Breakdown Maintenance | O2 Project | 8.3 | 1922.8 | 16824.5
414 | 2025-01-06 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 17:10 | 17:10 | 17:58 | 0:00 | 0.8 | 0.8 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.4 | IG Breakdown Maintenance | O2 Project | 8.3 | 1922.8 | 23073.6
415 | 2025-01-06 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 21:34 | 21:34 | 22:40 | 0:00 | 1.1 | 1.1 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.55 | IG Breakdown Maintenance | O2 Project | 8.3 | 1922.8 | 31726.2
416 | 2025-01-06 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Stop for Senction isolator work & o2-06,16,17,18,20,21,22,24 jumper open work. | 9:41 | 9:41 | 10:18 | 0:00 | 0.61667 | 0.61667 | Feeder-2 Stop for Senction isolator work & o2-06,16,17,18,20,21,22,24 jumper open work. | Close | 0.30833 | IG Breakdown Maintenance | O2 Project | 8.3 | 1922.8 | 13042.9933
417 | 2025-01-06 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Stop for Senction isolator work & o2-06,16,17,18,20,21,22,24 jumper closing work | 15:50 | 15:50 | 17:00 | 0:00 | 1.1667 | 1.1667 | Feeder-2 Stop for Senction isolator work & o2-06,16,17,18,20,21,22,24 jumper closing work | Close | 0.58333 | IG Breakdown Maintenance | O2 Project | 8.3 | 1922.8 | 24675.9333
418 | 2025-01-06 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_06 | TQGXIIPL | GEDA | 3.846% | o2-06,16,17,18,20,21,22,24 jumper closing Open so after jumper closed than reset and start Turbines. | 10:30 | 10:30 | 15:50 | 0:00 | 5.3333 | 5.3333 | o2-06,16,17,18,20,21,22,24 jumper closing Open so after jumper closed than reset and start Turbines. | Close | 0.20513 | IG Breakdown Maintenance | O2 Project | 8.3 | 1922.8 | 10254.9333
419 | 2025-01-06 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_16 | TQGXIIPL | GEDA | 3.846% | o2-06,16,17,18,20,21,22,24 jumper closing Open so after jumper closed than reset and start Turbines. | 10:30 | 10:30 | 15:50 | 0:00 | 5.3333 | 5.3333 | o2-06,16,17,18,20,21,22,24 jumper closing Open so after jumper closed than reset and start Turbines. | Close | 0.20513 | IG Breakdown Maintenance | O2 Project | 8.3 | 1922.8 | 10254.9333
420 | 2025-01-06 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_17 | TQGXIIPL | GEDA | 3.846% | o2-06,16,17,18,20,21,22,24 jumper closing Open so after jumper closed than reset and start Turbines. | 10:30 | 10:30 | 15:50 | 0:00 | 5.3333 | 5.3333 | o2-06,16,17,18,20,21,22,24 jumper closing Open so after jumper closed than reset and start Turbines. | Close | 0.20513 | IG Breakdown Maintenance | O2 Project | 8.3 | 1922.8 | 10254.9333
421 | 2025-01-06 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_18 | TQGXIIPL | GEDA | 3.846% | o2-06,16,17,18,20,21,22,24 jumper closing Open so after jumper closed than reset and start Turbines. | 10:30 | 10:30 | 15:50 | 0:00 | 5.3333 | 5.3333 | o2-06,16,17,18,20,21,22,24 jumper closing Open so after jumper closed than reset and start Turbines. | Close | 0.20513 | IG Breakdown Maintenance | O2 Project | 8.3 | 1922.8 | 10254.9333
422 | 2025-01-06 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_20 | TQGXIIPL | GEDA | 3.846% | o2-06,16,17,18,20,21,22,24 jumper closing Open so after jumper closed than reset and start Turbines. | 10:30 | 10:30 | 15:50 | 0:00 | 5.3333 | 5.3333 | o2-06,16,17,18,20,21,22,24 jumper closing Open so after jumper closed than reset and start Turbines. | Close | 0.20513 | IG Breakdown Maintenance | O2 Project | 8.3 | 1922.8 | 10254.9333
423 | 2025-01-06 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_21 | TQGXIIPL | GEDA | 3.846% | o2-06,16,17,18,20,21,22,24 jumper closing Open so after jumper closed than reset and start Turbines. | 10:30 | 10:30 | 15:50 | 0:00 | 5.3333 | 5.3333 | o2-06,16,17,18,20,21,22,24 jumper closing Open so after jumper closed than reset and start Turbines. | Close | 0.20513 | IG Breakdown Maintenance | O2 Project | 8.3 | 1922.8 | 10254.9333
424 | 2025-01-06 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_22 | TQGXIIPL | GEDA | 3.846% | o2-06,16,17,18,20,21,22,24 jumper closing Open so after jumper closed than reset and start Turbines. | 10:30 | 10:30 | 15:50 | 0:00 | 5.3333 | 5.3333 | o2-06,16,17,18,20,21,22,24 jumper closing Open so after jumper closed than reset and start Turbines. | Close | 0.20513 | IG Breakdown Maintenance | O2 Project | 8.3 | 1922.8 | 10254.9333
425 | 2025-01-06 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_24 | TQGXIIPL | GEDA | 3.846% | o2-06,16,17,18,20,21,22,24 jumper closing Open so after jumper closed than reset and start Turbines. | 10:30 | 10:30 | 15:50 | 0:00 | 5.3333 | 5.3333 | o2-06,16,17,18,20,21,22,24 jumper closing Open so after jumper closed than reset and start Turbines. | Close | 0.20513 | IG Breakdown Maintenance | O2 Project | 8.3 | 1922.8 | 10254.9333
426 | 2025-01-06 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_21 | TQGXIIPL | GEDA | 3.846% | AFTER Feeder shutdown clear than wtg in Disconnected due to O2 21 VCB tripped so charge than reset and start WTG. | 17:00 | 17:00 | 18:04 | 0:00 | 1.0667 | 1.0667 | AFTER Feeder shutdown clear than wtg in Disconnected due to O2 21 VCB tripped so charge than reset and start WTG. | Close | 0.041026 | IG Breakdown Maintenance | O2 Project | 8.3 | 1922.8 | 2050.9867
427 | 2025-01-07 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 0:11 | 0:11 | 1:28 | 0:00 | 1.2833 | 1.2833 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.64167 | IG Breakdown Maintenance | O2 Project | 8.9 | 2196.3 | 42278.775
428 | 2025-01-07 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 17:10 | 17:10 | 17:50 | 0:00 | 0.66667 | 0.66667 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.33333 | IG Breakdown Maintenance | O2 Project | 8.9 | 2196.3 | 21963
429 | 2025-01-07 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 19:17 | 19:17 | 20:10 | 0:00 | 0.88333 | 0.88333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.44167 | IG Breakdown Maintenance | O2 Project | 8.9 | 2196.3 | 29100.975
430 | 2025-01-07 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Manual Tripped ( ROW) Project Payment issue | 21:50 | 21:50 | 23:55 | 0:00 | 2.0833 | 2.0833 | Feeder-01 Manual Tripped ( ROW) Project Payment issue | Close | 1.0417 | IG Breakdown Maintenance | O2 Project | 8.9 | 2196.3 | 68634.375
431 | 2025-01-07 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Manual Tripped ( ROW) Project Payment issue | 21:50 | 21:50 | 24:00 | 0:00 | 2.1667 | 2.1667 | Feeder-02 Manual Tripped ( ROW) Project Payment issue | Close | 1.0833 | IG Breakdown Maintenance | O2 Project | 8.9 | 2196.3 | 52345.15
432 | 2025-01-07 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_11 | TQGXIIPL | GEDA | 3.846% | After VCB Charge than reset and start WTG. | 1:38 | 1:38 | 1:52 | 0:00 | 0.23333 | 0.23333 | After VCB Charge than reset and start WTG. | Close | 0.0089744 | IG Breakdown Maintenance | O2 Project | 8.9 | 2196.3 | 512.47
433 | 2025-01-07 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_14 | TQGXIIPL | GEDA | 3.846% | After VCB Charge than reset and start WTG. | 1:38 | 1:38 | 2:17 | 0:00 | 0.65 | 0.65 | After VCB Charge than reset and start WTG. | Close | 0.025 | IG Breakdown Maintenance | O2 Project | 8.9 | 2196.3 | 1427.595
434 | 2025-01-07 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_08 | TQGXIIPL | GEDA | 3.846% | After VCB Charge than reset and start WTG. | 1:38 | 1:38 | 2:43 | 0:00 | 1.0833 | 1.0833 | After VCB Charge than reset and start WTG. | Close | 0.041667 | IG Breakdown Maintenance | O2 Project | 8.9 | 2196.3 | 2379.325
435 | 2025-01-07 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_26 | TQGXIIPL | GEDA | 3.846% | After VCB Charge than reset and start WTG. | 1:38 | 1:38 | 3:02 | 0:00 | 1.4 | 1.4 | After VCB Charge than reset and start WTG. | Close | 0.053846 | IG Breakdown Maintenance | O2 Project | 8.9 | 2196.3 | 3074.82
436 | 2025-01-08 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Manual Tripped ( ROW) Project Payment issue | 0:00 | 0:00 | 0:20 | 0:00 | 0.33333 | 0.33333 | Feeder-02 Manual Tripped ( ROW) Project Payment issue | Close | 0.16667 | IG Breakdown Maintenance | O2 Project | 7.7 | 1543.5 | 5659.5
437 | 2025-01-08 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 8:14 | 8:14 | 9:14 | 0:00 | 1 | 1 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.5 | IG Breakdown Maintenance | O2 Project | 7.7 | 1543.5 | 23152.5
438 | 2025-01-08 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 16:12 | 16:12 | 16:44 | 0:00 | 0.53333 | 0.53333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.26667 | IG Breakdown Maintenance | O2 Project | 7.7 | 1543.5 | 12348
439 | 2025-01-08 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 17:41 | 17:41 | 18:28 | 0:00 | 0.78333 | 0.78333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.39167 | IG Breakdown Maintenance | O2 Project | 7.7 | 1543.5 | 18136.125
440 | 2025-01-08 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 20:54 | 20:54 | 21:28 | 0:00 | 0.56667 | 0.56667 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.28333 | IG Breakdown Maintenance | O2 Project | 7.7 | 1543.5 | 13119.75
441 | 2025-01-08 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Shutdown for Getco End. | 19:19 | 19:19 | 19:38 | 0:00 | 0.31667 | 0.31667 | Feeder-1 Shutdown for Getco End. | Close | 0.15833 | IG Breakdown Maintenance | O2 Project | 7.7 | 1543.5 | 7331.625
442 | 2025-01-08 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_13 | TQGXIIPL | GEDA | 3.846% | After VCB Charge than reset and start WTG. | 21:28 | 21:28 | 22:07 | 0:00 | 0.65 | 0.65 | After VCB Charge than reset and start WTG. | Close | 0.025 | IG Breakdown Maintenance | O2 Project | 7.7 | 1543.5 | 1003.275
443 | 2025-01-08 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_25 | TQGXIIPL | GEDA | 3.846% | After VCB Charge than reset and start WTG. | 21:28 | 21:28 | 23:30 | 0:00 | 2.0333 | 2.0333 | After VCB Charge than reset and start WTG. | Close | 0.078205 | IG Breakdown Maintenance | O2 Project | 7.7 | 1543.5 | 3138.45
444 | 2025-01-08 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_26 | TQGXIIPL | GEDA | 3.846% | After VCB Charge than reset and start WTG. | 14:16 | 14:16 | 14:48 | 0:00 | 0.53333 | 0.53333 | After VCB Charge than reset and start WTG. | Close | 0.020513 | IG Breakdown Maintenance | O2 Project | 7.7 | 1543.5 | 823.2
445 | 2025-01-08 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_26 | TQGXIIPL | GEDA | 3.846% | After VCB Charge than reset and start WTG. | 21:28 | 21:28 | 22:06 | 0:00 | 0.63333 | 0.63333 | After VCB Charge than reset and start WTG. | Close | 0.024359 | IG Breakdown Maintenance | O2 Project | 7.7 | 1543.5 | 977.55
446 | 2025-01-09 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 11:17 | 11:17 | 11:56 | 0:00 | 0.65 | 0.65 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.325 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 4267.575
447 | 2025-01-09 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 19:52 | 19:52 | 20:41 | 0:00 | 0.81667 | 0.81667 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.40833 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 5361.825
448 | 2025-01-09 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 21:06 | 21:06 | 21:58 | 0:00 | 0.86667 | 0.86667 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.43333 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 5690.1
449 | 2025-01-09 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_23 | TQGXIIPL | GEDA | 3.846% | After VCB Charge than reset and start WTG. | 21:58 | 21:58 | 22:51 | 0:00 | 0.88333 | 0.88333 | After VCB Charge than reset and start WTG. | Close | 0.033974 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 386.635
450 | 2025-01-10 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 4:51 | 4:51 | 5:43 | 0:00 | 0.86667 | 0.86667 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.43333 | IG Breakdown Maintenance | O2 Project | 4.8 | 362 | 4706
451 | 2025-01-10 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 10:25 | 10:25 | 11:43 | 0:00 | 1.3 | 1.3 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.65 | IG Breakdown Maintenance | O2 Project | 4.8 | 362 | 7059
452 | 2025-01-11 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 20:14 | 20:14 | 20:44 | 0:00 | 0.5 | 0.5 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.25 | IG Breakdown Maintenance | O2 Project | 5.3 | 501.1 | 3758.25
453 | 2025-01-11 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 21:24 | 21:24 | 22:30 | 0:00 | 1.1 | 1.1 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.55 | IG Breakdown Maintenance | O2 Project | 5.3 | 501.1 | 8268.15
454 | 2025-01-11 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_13 | TQGXIIPL | GEDA | 3.846% | O2-13 Grid Loss | 20:54 | 21:16 | 21:16 | 8:48 | 0 | 0.36667 | After VCB Charge than reset and start WTG. | Close | 0.014103 | IG Breakdown Maintenance | O2 Project | 5.3 | 501.1 | 183.7367
455 | 2025-01-11 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_11 | TQGXIIPL | GEDA | 3.846% | O2-11 Grid Loss | 22:40 | 23:14 | 23:14 | 13:36 | 0 | 0.56667 | After VCB Charge than reset and start WTG. | Close | 0.021795 | IG Breakdown Maintenance | O2 Project | 5.3 | 501.1 | 283.9567
456 | 2025-01-11 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_13 | TQGXIIPL | GEDA | 3.846% | O2-13 Grid Loss | 22:40 | 23:10 | 23:10 | 12:00 | 0 | 0.5 | After VCB Charge than reset and start WTG. | Close | 0.019231 | IG Breakdown Maintenance | O2 Project | 5.3 | 501.1 | 250.55
457 | 2025-01-12 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 17:36 | 17:36 | 18:10 | 0:00 | 0.56667 | 0.56667 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.28333 | IG Breakdown Maintenance | O2 Project | 7.8 | 1597 | 13574.5
458 | 2025-01-13 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 5:50 | 5:50 | 6:15 | 0:00 | 0.41667 | 0.41667 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.20833 | IG Breakdown Maintenance | O2 Project | 9.7 | 2509.3 | 15683.125
459 | 2025-01-13 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_13 | TQGXIIPL | GEDA | 3.846% | O2-13 Grid Loss | 6:15 | 6:25 | 6:34 | 4:00 | 0.15 | 0.31667 | After VCB Charge than reset and start WTG. | Close | 0.012179 | IG Breakdown Maintenance | O2 Project | 9.7 | 2509.3 | 794.6117
460 | 2025-01-13 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_20 | TQGXIIPL | GEDA | 3.846% | O2-20 Grid Loss | 15:39 | 15:55 | 18:08 | 6:24 | 2.2167 | 2.4833 | After VCB Charge than reset and start WTG. | Close | 0.095513 | IG Breakdown Maintenance | O2 Project | 9.7 | 2509.3 | 6231.4283
461 | 2025-01-13 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_24 | TQGXIIPL | GEDA | 3.846% | O2-24 Grid Loss | 16:03 | 17:30 | 17:58 | 34:48 | 0.46667 | 1.9167 | After VCB Charge than reset and start WTG. | Close | 0.073718 | IG Breakdown Maintenance | O2 Project | 9.7 | 2509.3 | 4809.4917
462 | 2025-01-14 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_20 | TQGXIIPL | GEDA | 3.846% | O2-20 Grid Loss | 18:00 | 18:00 | 18:33 | 0:00 | 0.55 | 0.55 | After VCB Charge than reset and start WTG. | Close | 0.021154 | IG Breakdown Maintenance | O2 Project | 8.3 | 1868.1 | 1027.455
463 | 2025-01-16 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_04 | TQGXIIPL | GEDA | 3.846% | O2_04 Grid Loss | 10:42 | 10:42 | 11:53 | 0:00 | 1.1833 | 1.1833 | wtg manual stop section isolator open for O2-07 Line jumper open for GETCO line crossing work. | Close | 0.045513 | IG Breakdown Maintenance | O2 Project | 9.4 | 2398.6 | 2838.3433
464 | 2025-01-16 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_19 | TQGXIIPL | GEDA | 3.846% | O2_19 Grid Loss | 10:42 | 10:42 | 11:53 | 0:00 | 1.1833 | 1.1833 | wtg manual stop section isolator open for O2-07 Line jumper open for GETCO line crossing work. | Close | 0.045513 | IG Breakdown Maintenance | O2 Project | 9.4 | 2398.6 | 2838.3433
465 | 2025-01-16 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_07 | TQGXIIPL | GEDA | 3.846% | O2_07 Grid Loss | 10:42 | 10:42 | 18:34 | 0:00 | 7.8667 | 7.8667 | wtg manual stop section isolator open for O2-07 Line jumper open for GETCO line crossing work. | Close | 0.30256 | IG Breakdown Maintenance | O2 Project | 9.4 | 2398.6 | 18868.9867
466 | 2025-01-16 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_04 | TQGXIIPL | GEDA | 3.846% | O2_04 Grid Loss | 17:59 | 17:59 | 18:34 | 0:00 | 0.58333 | 0.58333 | wtg manual stop section isolator closing work for O2-07 Line jumper open for GETCO line crossing work. | Close | 0.022436 | IG Breakdown Maintenance | O2 Project | 9.4 | 2398.6 | 1399.1833
467 | 2025-01-16 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_19 | TQGXIIPL | GEDA | 3.846% | O2_19 Grid Loss | 17:59 | 17:59 | 18:34 | 0:00 | 0.58333 | 0.58333 | wtg manual stop section isolator closing work for O2-07 Line jumper open for GETCO line crossing work. | Close | 0.022436 | IG Breakdown Maintenance | O2 Project | 9.4 | 2398.6 | 1399.1833
468 | 2025-01-17 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_04 | TQGXIIPL | GEDA | 3.846% | O2_04 Grid Loss | 9:38 | 9:38 | 10:46 | 0:00 | 1.1333 | 1.1333 | wtg manual stop section isolator open for O2-07 Line jumper open for GETCO line crossing work. | Close | 0.04359 | IG Breakdown Maintenance | O2 Project | 8.6 | 2032.2 | 2303.16
469 | 2025-01-17 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_19 | TQGXIIPL | GEDA | 3.846% | O2_19 Grid Loss | 9:38 | 9:38 | 10:46 | 0:00 | 1.1333 | 1.1333 | wtg manual stop section isolator open for O2-07 Line jumper open for GETCO line crossing work. | Close | 0.04359 | IG Breakdown Maintenance | O2 Project | 8.6 | 2032.2 | 2303.16
470 | 2025-01-17 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_07 | TQGXIIPL | GEDA | 3.846% | O2_07 Grid Loss | 9:38 | 9:38 | 17:43 | 0:00 | 8.0833 | 8.0833 | wtg manual stop section isolator open for O2-07 Line jumper open for GETCO line crossing work. | Close | 0.3109 | IG Breakdown Maintenance | O2 Project | 8.6 | 2032.2 | 16426.95
471 | 2025-01-17 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Shutdown for Getco End. | 17:43 | 17:43 | 18:23 | 0:00 | 0.66667 | 0.66667 | Feeder 2 shutdown for O2-07 Line jumper closing work. | Close | 0.33333 | IG Breakdown Maintenance | O2 Project | 8.6 | 2032.2 | 14902.8
472 | 2025-01-17 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 20:27 | 20:27 | 21:00 | 0:00 | 0.55 | 0.55 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.275 | IG Breakdown Maintenance | O2 Project | 8.6 | 2032.2 | 16765.65
473 | 2025-01-17 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 21:55 | 21:55 | 22:32 | 0:00 | 0.61667 | 0.61667 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.30833 | IG Breakdown Maintenance | O2 Project | 8.6 | 2032.2 | 18797.85
474 | 2025-01-17 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_13 | TQGXIIPL | GEDA | 3.846% | O2_13 Grid Loss | 22:38 | 22:38 | 23:00 | 0:00 | 0.36667 | 0.36667 | After VCB Charge than reset and start WTG. | Close | 0.014103 | IG Breakdown Maintenance | O2 Project | 8.6 | 2032.2 | 745.14
475 | 2025-01-18 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Shutdown for Getco End. | 9:08 | 9:08 | 9:48 | 0:00 | 0.66667 | 0.66667 | Feeder 2 shutdown for section isolator open for O2-07 Line jumper open for GETCO line crossing work. | Close | 0.33333 | IG Breakdown Maintenance | O2 Project | 4.3 | 252 | 1848
476 | 2025-01-18 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Shutdown for Getco End. | 17:55 | 17:55 | 18:19 | 0:00 | 0.4 | 0.4 | Feeder 2 shutdown for section isolator closing for O2-07. | Close | 0.2 | IG Breakdown Maintenance | O2 Project | 4.3 | 252 | 1108.8
477 | 2025-01-18 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_07 | TQGXIIPL | GEDA | 3.846% | O2_07 Grid Loss | 9:08 | 9:08 | 18:25 | 0:00 | 9.2833 | 9.2833 | wtg manual stop section isolator open for O2-07 Line jumper open for GETCO line crossing work. | Close | 0.35705 | IG Breakdown Maintenance | O2 Project | 4.3 | 252 | 2339.4
478 | 2025-01-19 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Shutdown for Getco End. | 8:58 | 8:58 | 9:27 | 0:00 | 0.48333 | 0.48333 | Feeder 2 shutdown for section isolator open for O2-07 Line jumper open for GETCO line crossing work. | Close | 0.24167 | IG Breakdown Maintenance | O2 Project | 3.5 | 108 | 574.2
479 | 2025-01-19 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_07 | TQGXIIPL | GEDA | 3.846% | O2_07 Grid Loss | 8:58 | 8:58 | 19:12 | 0:00 | 10.2333 | 10.2333 | wtg manual stop section isolator open for O2-07 Line jumper open for GETCO line crossing work. | Close | 0.39359 | IG Breakdown Maintenance | O2 Project | 3.5 | 108 | 1105.2
480 | 2025-01-19 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_04 | TQGXIIPL | GEDA | 3.846% | O2_04 Grid Loss | 18:08 | 18:08 | 19:12 | 0:00 | 1.0667 | 1.0667 | wtg manual stop section isolator closing for O2-07 Line jumper closing for GETCO line crossing work. | Close | 0.041026 | IG Breakdown Maintenance | O2 Project | 3.5 | 108 | 115.2
481 | 2025-01-19 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_19 | TQGXIIPL | GEDA | 3.846% | O2_19 Grid Loss | 18:08 | 18:08 | 19:12 | 0:00 | 1.0667 | 1.0667 | wtg manual stop section isolator closing for O2-07 Line jumper closing for GETCO line crossing work. | Close | 0.041026 | IG Breakdown Maintenance | O2 Project | 3.5 | 108 | 115.2
482 | 2025-01-20 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Tripped in over current & Earth fault /Master Relay Tripped | 9:13 | 9:13 | 10:11 | 0:00 | 0.96667 | 0.96667 | Feeder-2 Tripped in over current & Earth fault /Master Relay Tripped due to project pending payment for Mr. mehul , So section isolator open for O2-07,O2-04,O2-19. | Close | 0.48333 | IG Breakdown Maintenance | O2 Project | 3.2 | 61.2 | 650.76
483 | 2025-01-20 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_07 | TQGXIIPL | GEDA | 3.846% | O2-07 Grid Loss | 9:13 | 9:13 | 15:50 | 0:00 | 6.6167 | 6.6167 | wtg manual stop section isolator open O2-O7,O2-04,O2-19 BY BOP team | Close | 0.25449 | IG Breakdown Maintenance | O2 Project | 3.2 | 61.2 | 404.94
484 | 2025-01-20 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_04 | TQGXIIPL | GEDA | 3.846% | O2-04 Grid Loss | 9:13 | 9:13 | 15:50 | 0:00 | 6.6167 | 6.6167 | wtg manual stop section isolator open O2-O7,O2-04,O2-19 BY BOP team | Close | 0.25449 | IG Breakdown Maintenance | O2 Project | 3.2 | 61.2 | 404.94
485 | 2025-01-20 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_19 | TQGXIIPL | GEDA | 3.846% | O2-19 Grid Loss | 9:13 | 9:13 | 15:50 | 0:00 | 6.6167 | 6.6167 | wtg manual stop section isolator open O2-O7,O2-04,O2-19 BY BOP team | Close | 0.25449 | IG Breakdown Maintenance | O2 Project | 3.2 | 61.2 | 404.94
486 | 2025-01-20 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_23 | TQGXIIPL | GEDA | 3.846% | O2-23 Grid Loss | 9:01 | 9:01 | 10:54 | 0:00 | 1.8833 | 1.8833 | After VCB Charge than reset and start WTG. | Close | 0.072436 | IG Breakdown Maintenance | O2 Project | 3.2 | 61.2 | 115.26
487 | 2025-01-23 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Shutdown for transformer oil leakage arresting work. | 11:36 | 11:36 | 13:26 | 0:00 | 1.8333 | 1.8333 | Feeder-1 shutdown for power transformer oil leakage arresting work. | Close | 0.91667 | IG Breakdown Maintenance | O2 Project | 8.5 | 1977.5 | 54381.25
488 | 2025-01-23 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Shutdown for transformer Oil leakage arrensting work | 11:36 | 11:36 | 13:26 | 0:00 | 1.8333 | 1.8333 | Feeder-2 shutdown for power transformer oil leakage arresting work. | Close | 0.91667 | IG Breakdown Maintenance | O2 Project | 8.5 | 1977.5 | 39879.5833
489 | 2025-01-23 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 22:47 | 22:47 | 23:20 | 0:00 | 0.55 | 0.55 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.275 | IG Breakdown Maintenance | O2 Project | 8.5 | 1977.5 | 16314.375
490 | 2025-01-23 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_11 | TQGXIIPL | GEDA | 3.846% | O2-11 Grid Loss | 23:20 | 23:20 | 23:42 | 0:00 | 0.36667 | 0.36667 | After VCB Charge than reset and start WTG. | Close | 0.014103 | IG Breakdown Maintenance | O2 Project | 8.5 | 1977.5 | 725.0833
491 | 2025-01-23 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_10 | TQGXIIPL | GEDA | 3.846% | O2-10 Grid Loss | 4:15 | 4:15 | 6:40 | 0:00 | 2.4167 | 2.4167 | line voltage different each another phase so call BOP team and check line and tranformer and VCB trip by manual and check all canditions is ok so charge VCB start wtg. | Close | 0.092949 | IG Breakdown Maintenance | O2 Project | 8.5 | 1977.5 | 4778.9583
492 | 2025-01-24 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 0:00 | 0:00 | 0:32 | 0:00 | 0.53333 | 0.53333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.26667 | IG Breakdown Maintenance | O2 Project | 9.8 | 2546.2 | 20369.6
493 | 2025-01-24 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 11:53 | 11:53 | 12:27 | 0:00 | 0.56667 | 0.56667 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.28333 | IG Breakdown Maintenance | O2 Project | 9.8 | 2546.2 | 21642.7
494 | 2025-01-24 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 18:10 | 18:10 | 18:32 | 0:00 | 0.36667 | 0.36667 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.18333 | IG Breakdown Maintenance | O2 Project | 9.8 | 2546.2 | 14004.1
495 | 2025-01-24 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 23:52 | 23:52 | 24:00 | 0:00 | 0.13333 | 0.13333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Open | 0.066667 | IG Breakdown Maintenance | O2 Project | 9.8 | 2546.2 | 5092.4
496 | 2025-01-25 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 0:00 | 0:00 | 0:35 | 0:00 | 0.58333 | 0.58333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.29167 | IG Breakdown Maintenance | O2 Project | 7.2 | 1276 | 11165
497 | 2025-01-25 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 shutdown by getco Team | 8:55 | 8:55 | 9:38 | 0:00 | 0.71667 | 0.71667 | Feeder-2 shutdown taking by Getco team for 66kv tower line stringing work and O2-19 jumper open by BOP team. | Close | 0.35833 | IG Breakdown Maintenance | O2 Project | 7.2 | 1276 | 10059.1333
498 | 2025-01-25 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 shutdown by getco Team | 13:58 | 13:58 | 14:34 | 0:00 | 0.6 | 0.6 | Feeder-2 shutdown taking by Getco team for 66kv tower line stringing work and O2-19 jumper closing by BOP team. | Close | 0.3 | IG Breakdown Maintenance | O2 Project | 7.2 | 1276 | 8421.6
499 | 2025-01-25 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 15:40 | 15:40 | 16:19 | 0:00 | 0.65 | 0.65 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.325 | IG Breakdown Maintenance | O2 Project | 7.2 | 1276 | 12441
500 | 2025-01-25 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_13 | TQGXIIPL | GEDA | 3.846% | O2-13 Grid Loss | 0:35 | 0:35 | 0:55 | 0:00 | 0.33333 | 0.33333 | After VCB Charge than reset and start WTG. | Close | 0.012821 | IG Breakdown Maintenance | O2 Project | 7.2 | 1276 | 425.3333
501 | 2025-01-25 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_14 | TQGXIIPL | GEDA | 3.846% | O2-14 Grid Loss | 0:35 | 0:35 | 1:02 | 0:00 | 0.45 | 0.45 | After VCB Charge than reset and start WTG. | Close | 0.017308 | IG Breakdown Maintenance | O2 Project | 7.2 | 1276 | 574.2
502 | 2025-01-25 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_19 | TQGXIIPL | GEDA | 3.846% | O2-19 Grid Loss | 9:38 | 9:38 | 13:58 | 0:00 | 4.3333 | 4.3333 | Getco team for 66kv tower line stringing work and O2-19 jumper open by BOP team.after work completed then reset and start WTG. | Close | 0.16667 | IG Breakdown Maintenance | O2 Project | 7.2 | 1276 | 5529.3333
503 | 2025-01-25 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_17 | TQGXIIPL | GEDA | 3.846% | O2-17 Grid Loss | 18:05 | 18:05 | 18:44 | 0:00 | 0.65 | 0.65 | After VCB Charge than reset and start WTG. | Close | 0.025 | IG Breakdown Maintenance | O2 Project | 7.2 | 1276 | 829.4
504 | 2025-01-25 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_17 | TQGXIIPL | GEDA | 3.846% | O2-17 Grid Loss | 19:15 | 19:15 | 21:57 | 0:00 | 2.7 | 2.7 | After VCB Charge than reset and start WTG. | Close | 0.10385 | IG Breakdown Maintenance | O2 Project | 7.2 | 1276 | 3445.2
505 | 2025-01-25 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_16 | TQGXIIPL | GEDA | 3.846% | O2-16 Grid Loss | 18:18 | 18:18 | 20:36 | 0:00 | 2.3 | 2.3 | After VCB Charge than reset and start WTG. | Close | 0.088462 | IG Breakdown Maintenance | O2 Project | 7.2 | 1276 | 2934.8
506 | 2025-01-27 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 5:15 | 5:15 | 5:53 | 0:00 | 0.63333 | 0.63333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.31667 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 2185
507 | 2025-01-27 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 14:40 | 14:40 | 15:18 | 0:00 | 0.63333 | 0.63333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.31667 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 2185
508 | 2025-01-27 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 16:42 | 16:42 | 17:27 | 0:00 | 0.75 | 0.75 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.375 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 2587.5
509 | 2025-01-27 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 19:49 | 19:49 | 20:23 | 0:00 | 0.56667 | 0.56667 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.28333 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 1955
510 | 2025-01-27 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 22:16 | 22:16 | 22:53 | 0:00 | 0.61667 | 0.61667 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.30833 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 2127.5
511 | 2025-01-27 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_08 | TQGXIIPL | GEDA | 3.846% | O2-08 Grid Loss | 22:53 | 22:53 | 23:40 | 0:00 | 0.78333 | 0.78333 | After VCB Charge than reset and start WTG. | Close | 0.030128 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 180.1667
512 | 2025-01-27 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_25 | TQGXIIPL | GEDA | 3.846% | O2-25 Grid Loss | 22:53 | 22:53 | 24:00 | 0:00 | 1.1167 | 1.1167 | After Feeder Charge Turbine scada down so check by BOP team VCB found tripped so wip, | Close | 0.042949 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 256.8333
513 | 2025-01-28 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Shutdown taking by Ayana team by 33kv Line crossing and Stringing work | 10:57 | 10:57 | 12:34 | 0:00 | 1.6167 | 1.6167 | Feeder-2 Shutdown taking by Ayana team by 33kv Line crossing and Stringing work | Close | 0.80833 | IG Breakdown Maintenance | O2 Project | 3.2 | 61.2 | 1088.34
514 | 2025-01-28 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_10 | TQGXIIPL | GEDA | 3.846% | WTG shut down | 15:42 | 15:42 | 19:34 | 0:00 | 3.8667 | 3.8667 | USS yard Transformer Inspection Work done | Close | 0.14872 | IG Breakdown Maintenance | O2 Project | 3.2 | 61.2 | 236.64
515 | 2025-01-28 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_25 | TQGXIIPL | GEDA | 3.846% | O2-25 Grid Loss | 0:00 | 0:00 | 0:12 | 0:00 | 0.2 | 0.2 | After VCB Charge than reset and start WTG. | Close | 0.0076923 | IG Breakdown Maintenance | O2 Project | 3.2 | 61.2 | 12.24
516 | 2025-01-29 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Shutdown taking by Getco team for 66kv tower line stringing work | 9:00 | 9:00 | 9:47 | 0:00 | 0.78333 | 0.78333 | Feeder-2 Shutdown taking by Getco team for 66kv tower line stringing work | Close | 0.39167 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 1981.8333
517 | 2025-01-29 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 15:57 | 15:57 | 16:37 | 0:00 | 0.66667 | 0.66667 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.33333 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 2300
518 | 2025-01-29 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Shutdown taking by Getco team for 66kv tower line stringing work | 18:04 | 18:04 | 18:38 | 0:00 | 0.56667 | 0.56667 | Feeder-2 Shutdown taking by Getco team for 66kv tower line stringing work | Close | 0.28333 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 1433.6667
519 | 2025-01-29 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 18:39 | 18:39 | 18:59 | 0:00 | 0.33333 | 0.33333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.16667 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 1150
520 | 2025-01-29 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 20:58 | 20:58 | 21:21 | 0:00 | 0.38333 | 0.38333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.19167 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 1322.5
521 | 2025-01-29 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_07 | TQGXIIPL | GEDA | 3.846% | Turbine stop for LC taken by BOP team(Jumper open) | 9:47 | 9:47 | 18:04 | 0:00 | 8.2833 | 8.2833 | Turbine stop for LC taken by BOP team(Jumper open) | Close | 0.31859 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 1905.1667
522 | 2025-01-29 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_10 | TQGXIIPL | GEDA | 3.846% | Voltage asymmetry | 13:50 | 13:50 | 15:57 | 0:00 | 2.1167 | 2.1167 | Attend and check the related ckt check VCB CR panel,check TR LV Box,then measure TR LV Voltage in each tap now It's in under Observation wip, (USS Yard Transformer Checking) | Close | 0.08141 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 486.8333
523 | 2025-01-29 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_10 | TQGXIIPL | GEDA | 3.846% | Voltage asymmetry | 16:37 | 16:37 | 18:39 | 0:00 | 2.0333 | 2.0333 | Attend and check the related ckt check VCB CR panel,check TR LV Box,then measure TR LV Voltage in each tap now It's in under Observation wip, (USS Yard Transformer Checking) | Close | 0.078205 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 467.6667
524 | 2025-01-29 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_10 | TQGXIIPL | GEDA | 3.846% | Voltage asymmetry | 18:59 | 18:59 | 20:38 | 0:00 | 1.65 | 1.65 | Attend and check the related ckt check VCB CR panel,check TR LV Box,then measure TR LV Voltage in each tap than start WTG,now It's in under Observation. (USS Yard Transformer Checking) | Close | 0.063462 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 379.5
525 | 2025-01-30 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Shutdown taking by Getco team for 66kv tower line stringing work | 8:36 | 8:36 | 9:18 | 0:00 | 0.7 | 0.7 | Feeder-2 Shutdown taking by Getco team for 66kv tower line stringing work | Close | 0.35 | IG Breakdown Maintenance | O2 Project | 5.2 | 469.4 | 3614.38
526 | 2025-01-30 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Shutdown taking by Getco team for 66kv tower line stringing work | 18:16 | 18:16 | 18:49 | 0:00 | 0.55 | 0.55 | Feeder-2 Shutdown taking by Getco team for 66kv tower line stringing work | Close | 0.275 | IG Breakdown Maintenance | O2 Project | 5.2 | 469.4 | 2839.87
527 | 2025-01-30 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown for Aayana power materials movement work. | 14:50 | 14:50 | 15:53 | 0:00 | 1.05 | 1.05 | Feeder-1 Shutdown taking by Anaya team for material movment work near O2-12 | Close | 0.525 | IG Breakdown Maintenance | O2 Project | 5.2 | 469.4 | 7393.05
528 | 2025-01-30 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_07 | TQGXIIPL | GEDA | 3.846% | Turbine stop for LC taken by BOP team(Jumper open) | 9:18 | 9:18 | 18:16 | 0:00 | 8.9667 | 8.9667 | Turbine stop for LC taken by BOP team(Jumper open) | Close | 0.34487 | IG Breakdown Maintenance | O2 Project | 5.2 | 469.4 | 4208.9533
529 | 2025-01-31 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Shutdown taking by Getco team for 66kv tower line stringing work | 8:39 | 8:39 | 9:20 | 0:00 | 0.68333 | 0.68333 | Feeder-2 Shutdown taking by Getco team for 66kv tower line stringing work | Close | 0.34167 | IG Breakdown Maintenance | O2 Project | 5.4 | 532.8 | 4004.88
530 | 2025-01-31 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Shutdown taking by Getco team for 66kv tower line stringing work | 18:33 | 18:33 | 19:09 | 0:00 | 0.6 | 0.6 | Feeder-2 Shutdown taking by Getco team for 66kv tower line stringing work | Close | 0.3 | IG Breakdown Maintenance | O2 Project | 5.4 | 532.8 | 3516.48
531 | 2025-01-31 | 2025 | 2024 | 2025-01-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 22:14 | 22:14 | 22:47 | 0:00 | 0.55 | 0.55 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.275 | IG Breakdown Maintenance | O2 Project | 5.4 | 532.8 | 4395.6
532 | 2025-01-31 | 2025 | 2024 | 2025-01-01 | Year_1 | O2_07 | TQGXIIPL | GEDA | 3.846% | Turbine stop for LC taken by BOP team(Jumper open) | 9:20 | 9:20 | 18:33 | 0:00 | 9.2167 | 9.2167 | Turbine stop for LC taken by BOP team(Jumper open) | Close | 0.35449 | IG Breakdown Maintenance | O2 Project | 5.4 | 532.8 | 4910.64
533 | 2025-02-01 | 2025 | 2024 | 2025-02-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 4:50 | 4:50 | 5:17 | 0:00 | 0.45 | 0.45 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.225 | IG Breakdown Maintenance | O2 Project | 6 | 723 | 4880.25
534 | 2025-02-01 | 2025 | 2024 | 2025-02-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 6:25 | 6:25 | 6:50 | 0:00 | 0.41667 | 0.41667 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.20833 | IG Breakdown Maintenance | O2 Project | 6 | 723 | 4518.75
535 | 2025-02-03 | 2025 | 2024 | 2025-02-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 2:42 | 2:42 | 3:12 | 0:00 | 0.5 | 0.5 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.25 | IG Breakdown Maintenance | O2 Project | 2.9 | 0 | 0
536 | 2025-02-04 | 2025 | 2024 | 2025-02-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 0:39 | 0:39 | 1:05 | 0:00 | 0.43333 | 0.43333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.21667 | IG Breakdown Maintenance | O2 Project | 6.1 | 767.6 | 4989.4
537 | 2025-02-04 | 2025 | 2024 | 2025-02-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown for PT Fuse replacement work. | 11:58 | 11:58 | 13:15 | 0:00 | 1.2833 | 1.2833 | Feeder-1PSS power Transformer Shutdown taken for 33kv BUS PT Fuse replacement Work. | Close | 0.64167 | IG Breakdown Maintenance | O2 Project | 6.1 | 767.6 | 14776.3
538 | 2025-02-04 | 2025 | 2024 | 2025-02-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-02 PSS power Transformer Shutdown for PT Fuse replacement work. | 11:58 | 11:58 | 13:15 | 0:00 | 1.2833 | 1.2833 | Feeder-2 shutdown for PT fuse replacement work. | Close | 0.64167 | IG Breakdown Maintenance | O2 Project | 6.1 | 767.6 | 10835.9533
539 | 2025-02-04 | 2025 | 2024 | 2025-02-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 22:17 | 22:17 | 22:43 | 0:00 | 0.43333 | 0.43333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.21667 | IG Breakdown Maintenance | O2 Project | 6.1 | 767.6 | 4989.4
540 | 2025-02-04 | 2025 | 2024 | 2025-02-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 22:58 | 22:58 | 24:00 | 0:00 | 1.0333 | 1.0333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.51667 | IG Breakdown Maintenance | O2 Project | 6.1 | 767.6 | 11897.8
541 | 2025-02-04 | 2025 | 2024 | 2025-02-01 | Year_1 | O2_10 | TQGXIIPL | GEDA | 3.846% | WTG manual stop for Transformer LV side Neutral busbar hardware Replacment work. | 13:15 | 13:15 | 13:51 | 0:00 | 0.6 | 0.6 | WTG manual stop for Transformer LV side Neutral busbar hardware Replacment work. | Close | 0.023077 | IG Breakdown Maintenance | O2 Project | 6.1 | 767.6 | 460.56
542 | 2025-02-08 | 2025 | 2024 | 2025-02-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Shutdown taking by Getco team for 66kv tower line stringing work | 9:09 | 9:09 | 9:46 | 0:00 | 0.61667 | 0.61667 | Feeder-2 shutdown taking by getco team for 66 KV Tower line stringing work | Close | 0.30833 | IG Breakdown Maintenance | O2 Project | 4.8 | 362 | 2455.5667
543 | 2025-02-08 | 2025 | 2024 | 2025-02-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Shutdown taking by Getco team for 66kv tower line stringing work | 15:31 | 15:31 | 15:57 | 0:00 | 0.43333 | 0.43333 | Feeder-2 shutdown taking by getco team for 66 KV Tower line stringing work | Close | 0.21667 | IG Breakdown Maintenance | O2 Project | 4.8 | 362 | 1725.5333
544 | 2025-02-08 | 2025 | 2024 | 2025-02-01 | Year_1 | O2_07 | TQGXIIPL | GEDA | 3.846% | Turbine stop for LC taken by BOP team(Jumper open) | 9:09 | 9:09 | 15:57 | 0:00 | 6.8 | 6.8 | WTG Stop for Jumper open for Getco line stringing | Close | 0.26154 | IG Breakdown Maintenance | O2 Project | 4.8 | 362 | 2461.6
545 | 2025-02-09 | 2025 | 2024 | 2025-02-01 | Year_1 | O2_10 | TQGXIIPL | GEDA | 3.846% | O2_10 Grid loss | 12:22 | 12:22 | 15:22 | 0:00 | 3 | 3 | WTG stop For BOP Team Work in USS Yard for Xmer inspection work done | Close | 0.11538 | IG Breakdown Maintenance | O2 Project | 3.4 | 92.4 | 277.2
546 | 2025-02-10 | 2025 | 2024 | 2025-02-01 | Year_1 | O2_10 | TQGXIIPL | GEDA | 3.846% | O2_10 Grid loss | 10:30 | 10:30 | 15:47 | 0:00 | 5.2833 | 5.2833 | WTG stop For BOP Team Work in USS Yard for Xmer inspection work done | Close | 0.20321 | IG Breakdown Maintenance | O2 Project | 3.2 | 61.2 | 323.34
547 | 2025-02-10 | 2025 | 2024 | 2025-02-01 | Year_1 | O2_19 | TQGXIIPL | GEDA | 3.846% | O2_19 Grid Loss | 11:10 | 11:10 | 15:55 | 0:00 | 4.75 | 4.75 | Attend and chck VCB So found Spring charge Motor Faulty after Check and charge after start wtg | Close | 0.18269 | IG Breakdown Maintenance | O2 Project | 3.2 | 61.2 | 290.7
548 | 2025-02-11 | 2025 | 2024 | 2025-02-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Tripped in over current | 9:45 | 9:45 | 10:45 | 0:00 | 1 | 1 | F#2 Trip in Earth fault over current after Petroling and check line so ok after trail so ok Feeder-2 Normal charge | Close | 0.5 | IG Breakdown Maintenance | O2 Project | 5.5 | 564.5 | 6209.5
549 | 2025-02-12 | 2025 | 2024 | 2025-02-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Tripped in over current | 3:42 | 3:42 | 4:18 | 0:00 | 0.6 | 0.6 | Feeder-2 Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on conductor ,so remove it and charge the feeder-02 | Close | 0.3 | IG Breakdown Maintenance | O2 Project | 5.5 | 564.5 | 3725.7
550 | 2025-02-12 | 2025 | 2024 | 2025-02-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 1:28 | 1:28 | 1:59 | 0:00 | 0.51667 | 0.51667 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.25833 | IG Breakdown Maintenance | O2 Project | 5.5 | 564.5 | 4374.875
551 | 2025-02-12 | 2025 | 2024 | 2025-02-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 3:26 | 3:26 | 3:52 | 0:00 | 0.43333 | 0.43333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.21667 | IG Breakdown Maintenance | O2 Project | 5.5 | 564.5 | 3669.25
552 | 2025-02-12 | 2025 | 2024 | 2025-02-01 | Year_1 | O2_13 | TQGXIIPL | GEDA | 3.846% | O2_13 Grid Loss | 3:52 | 3:52 | 5:12 | 0:00 | 1.3333 | 1.3333 | VCB Off after charge and start wtg | Close | 0.051282 | IG Breakdown Maintenance | O2 Project | 5.5 | 564.5 | 752.6667
552 | 2025-02-13 | 2025 | 2024 | 2025-02-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 shutdown taken for OFC Cable spicing work | 17:06 | 17:06 | 17:32 | 0:00 | 0.43333 | 0.43333 | Feeder-2 shutdown taken for OFC Cable spicing work | Close | 0.21667 | IG Breakdown Maintenance | O2 Project | 5.3 | 501.1 | 2388.5767
553 | 2025-02-14 | 2025 | 2024 | 2025-02-01 | Year_1 | O2_10 | TQGXIIPL | GEDA | 3.846% | Voltage asymmetry | 6:00 | 6:00 | 7:00 | 0:00 | 1 | 1 | After voltage stable reset and start wtg | Close | 0.038462 | IG Breakdown Maintenance | O2 Project | 3.7 | 139.2 | 139.2
554 | 2025-02-14 | 2025 | 2024 | 2025-02-01 | Year_1 | O2_10 | TQGXIIPL | GEDA | 3.846% | Voltage asymmetry | 10:00 | 10:00 | 13:46 | 0:00 | 3.7667 | 3.7667 | USS Yard Transformer Tap Position change from 3 to 2 after reset and start wtg | Close | 0.14487 | IG Breakdown Maintenance | O2 Project | 3.7 | 139.2 | 524.32
555 | 2025-02-14 | 2025 | 2024 | 2025-02-01 | Year_1 | O2_13 | TQGXIIPL | GEDA | 3.846% | O2_13 Grid Loss | 16:17 | 16:17 | 17:06 | 0:00 | 0.81667 | 0.81667 | VCB Off after charge and start wtg | Close | 0.03141 | IG Breakdown Maintenance | O2 Project | 3.7 | 139.2 | 113.68
556 | 2025-02-15 | 2025 | 2024 | 2025-02-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 18:18 | 18:18 | 18:41 | 0:00 | 0.38333 | 0.38333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.19167 | IG Breakdown Maintenance | O2 Project | 7.3 | 1329.5 | 7644.625
557 | 2025-02-15 | 2025 | 2024 | 2025-02-01 | Year_1 | O2_26 | TQGXIIPL | GEDA | 3.846% | O2-26 Grid Loss | 18:41 | 18:41 | 19:26 | 0:00 | 0.75 | 0.75 | After grid time VCB Off after charge and start wtg | Close | 0.028846 | IG Breakdown Maintenance | O2 Project | 7.3 | 1329.5 | 997.125
558 | 2025-02-15 | 2025 | 2024 | 2025-02-01 | Year_1 | O2_08 | TQGXIIPL | GEDA | 3.846% | O2-08 Grid Loss | 18:41 | 18:41 | 19:18 | 0:00 | 0.61667 | 0.61667 | After grid time VCB Off after charge and start wtg | Close | 0.023718 | IG Breakdown Maintenance | O2 Project | 7.3 | 1329.5 | 819.8583
559 | 2025-02-15 | 2025 | 2024 | 2025-02-01 | Year_1 | O2_25 | TQGXIIPL | GEDA | 3.846% | O2-25 Grid Loss | 18:41 | 18:41 | 19:54 | 0:00 | 1.2167 | 1.2167 | After grid time VCB Off after charge and start wtg | Close | 0.046795 | IG Breakdown Maintenance | O2 Project | 7.3 | 1329.5 | 1617.5583
560 | 2025-02-15 | 2025 | 2024 | 2025-02-01 | Year_1 | O2_13 | TQGXIIPL | GEDA | 3.846% | O2-13 Grid Loss | 12:44 | 12:44 | 13:12 | 0:00 | 0.46667 | 0.46667 | After grid time VCB Off after charge and start wtg | Close | 0.017949 | IG Breakdown Maintenance | O2 Project | 7.3 | 1329.5 | 620.4333
561 | 2025-02-16 | 2025 | 2024 | 2025-02-01 | Year_1 | O2_07 | TQGXIIPL | GEDA | 3.846% | O2-07 Grid loss | 20:30 | 20:30 | 21:23 | 0:00 | 0.88333 | 0.88333 | VCB Charge after reset and start wtg | Close | 0.033974 | IG Breakdown Maintenance | O2 Project | 7.1 | 1222.5 | 1079.875
562 | 2025-02-16 | 2025 | 2024 | 2025-02-01 | Year_1 | O2_10 | TQGXIIPL | GEDA | 3.846% | O2-10 Grid Loss | 17:25 | 17:25 | 21:10 | 0:00 | 3.75 | 3.75 | USS Yard transformer voltage rartio & winding resistant testing done then reset and start wtg | Close | 0.14423 | IG Breakdown Maintenance | O2 Project | 7.1 | 1222.5 | 4584.375
563 | 2025-02-17 | 2025 | 2024 | 2025-02-01 | Year_1 | O2_10 | TQGXIIPL | GEDA | 3.846% | Voltage asymmetry | 12:30 | 12:30 | 13:33 | 0:00 | 1.05 | 1.05 | After voltage stable reset and start wtg | Close | 0.040385 | IG Breakdown Maintenance | O2 Project | 6 | 723 | 759.15
564 | 2025-02-17 | 2025 | 2024 | 2025-02-01 | Year_1 | O2_07 | TQGXIIPL | GEDA | 3.846% | O2-07 Grid loss | 9:50 | 9:50 | 10:55 | 0:00 | 1.0833 | 1.0833 | VCB Charge after reset and start wtg | Close | 0.041667 | IG Breakdown Maintenance | O2 Project | 6 | 723 | 783.25
565 | 2025-02-18 | 2025 | 2024 | 2025-02-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown by BOP team | 11:06 | 11:06 | 11:31 | 0:00 | 0.41667 | 0.41667 | Feeder-1 shutdown for O2-10 tapping jumper open | Close | 0.20833 | IG Breakdown Maintenance | O2 Project | 5.9 | 691.3 | 4320.625
566 | 2025-02-18 | 2025 | 2024 | 2025-02-01 | Year_1 | O2_10 | TQGXIIPL | GEDA | 3.846% | O2-10 Grid Loss | 11:31 | 11:31 | 13:29 | 0:00 | 1.9667 | 1.9667 | O2-10 tapping jumper open by BOP team work in USS yard for X'mer inspection work. | Close | 0.075641 | IG Breakdown Maintenance | O2 Project | 5.9 | 691.3 | 1359.5567
567 | 2025-02-18 | 2025 | 2024 | 2025-02-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown by BOP team | 13:29 | 13:29 | 14:06 | 0:00 | 0.61667 | 0.61667 | Feeder-1 shutdown for O2-10 tapping jumper close | Close | 0.30833 | IG Breakdown Maintenance | O2 Project | 5.9 | 691.3 | 6394.525
568 | 2025-02-18 | 2025 | 2024 | 2025-02-01 | Year_1 | O2_10 | TQGXIIPL | GEDA | 3.846% | O2-10 Grid Loss | 15:00 | 15:00 | 16:53 | 0:00 | 1.8833 | 1.8833 | wtg manual stop for BOP team work in USS yard for X'mer inspection work. | Close | 0.072436 | IG Breakdown Maintenance | O2 Project | 5.9 | 691.3 | 1301.9483
569 | 2025-02-19 | 2025 | 2024 | 2025-02-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 7:22 | 7:22 | 7:46 | 0:00 | 0.4 | 0.4 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.2 | IG Breakdown Maintenance | O2 Project | 6.1 | 767 | 4602
570 | 2025-02-20 | 2025 | 2024 | 2025-02-01 | Year_1 | O2_19 | TQGXIIPL | GEDA | 3.846% | O2-19 Grid Loss | 17:54 | 17:54 | 18:50 | 0:00 | 0.93333 | 0.93333 | Uss yard VCB Spring charging motor replacement work | Close | 0.035897 | IG Breakdown Maintenance | O2 Project | 5.7 | 627.9 | 586.04
571 | 2025-02-21 | 2025 | 2024 | 2025-02-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 4:10 | 4:10 | 4:27 | 0:00 | 0.28333 | 0.28333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.14167 | IG Breakdown Maintenance | O2 Project | 5 | 406 | 1725.5
572 | 2025-02-24 | 2025 | 2024 | 2025-02-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 22:51 | 22:51 | 23:17 | 0:00 | 0.43333 | 0.43333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.21667 | IG Breakdown Maintenance | O2 Project | 4.4 | 274 | 1781
573 | 2025-02-24 | 2025 | 2024 | 2025-02-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 23:42 | 23:42 | 23:54 | 0:00 | 0.2 | 0.2 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.1 | IG Breakdown Maintenance | O2 Project | 4.4 | 274 | 822
574 | 2025-02-24 | 2025 | 2024 | 2025-02-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 23:58 | 23:58 | 24:00 | 0:00 | 0.033056 | 0.033056 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Open | 0.016528 | IG Breakdown Maintenance | O2 Project | 4.4 | 274 | 135.8583
575 | 2025-02-24 | 2025 | 2024 | 2025-02-01 | Year_1 | O2_13 | TQGXIIPL | GEDA | 3.846% | O2-13 Grid Loss | 23:17 | 23:17 | 23:36 | 0:00 | 0.31667 | 0.31667 | VCB Charge after reset and start wtg | Close | 0.012179 | IG Breakdown Maintenance | O2 Project | 4.4 | 274 | 86.7667
576 | 2025-02-24 | 2025 | 2024 | 2025-02-01 | Year_1 | O2_08 | TQGXIIPL | GEDA | 3.846% | O2-08 Grid Loss | 23:17 | 23:17 | 23:42 | 0:00 | 0.41667 | 0.41667 | VCB Charge restorartion WIP | Open | 0.016026 | IG Breakdown Maintenance | O2 Project | 4.4 | 274 | 114.1667
577 | 2025-02-24 | 2025 | 2024 | 2025-02-01 | Year_1 | O2_08 | TQGXIIPL | GEDA | 3.846% | O2-08 Grid Loss | 23:54 | 23:54 | 23:58 | 0:00 | 0.066667 | 0.066667 | VCB Charge restorartion WIP | Open | 0.0025641 | IG Breakdown Maintenance | O2 Project | 4.4 | 274 | 18.2667
578 | 2025-02-25 | 2025 | 2024 | 2025-02-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 0:00 | 0:00 | 0:54 | 0:00 | 0.9 | 0.9 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.45 | IG Breakdown Maintenance | O2 Project | 6.4 | 901.4 | 12168.9
579 | 2025-02-25 | 2025 | 2024 | 2025-02-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 10:46 | 10:46 | 11:23 | 0:00 | 0.61667 | 0.61667 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.30833 | IG Breakdown Maintenance | O2 Project | 6.4 | 901.4 | 8337.95
580 | 2025-02-25 | 2025 | 2024 | 2025-02-01 | Year_1 | O2_08 | TQGXIIPL | GEDA | 3.846% | O2-08 Grid Loss | 0:00 | 0:00 | 1:26 | 0:00 | 1.4333 | 1.4333 | VCB Charge after reset and start wtg | Close | 0.055128 | IG Breakdown Maintenance | O2 Project | 6.4 | 901.4 | 1292.0067
581 | 2025-02-26 | 2025 | 2024 | 2025-02-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 0:00 | 0:00 | 0:53 | 0:00 | 0.88333 | 0.88333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.44167 | IG Breakdown Maintenance | O2 Project | 4.7 | 340 | 4505
582 | 2025-02-26 | 2025 | 2024 | 2025-02-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 1:33 | 1:33 | 2:37 | 0:00 | 1.0667 | 1.0667 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.53333 | IG Breakdown Maintenance | O2 Project | 4.7 | 340 | 5440
583 | 2025-02-26 | 2025 | 2024 | 2025-02-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 3:11 | 3:11 | 4:22 | 0:00 | 1.1833 | 1.1833 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.59167 | IG Breakdown Maintenance | O2 Project | 4.7 | 340 | 6035
584 | 2025-02-26 | 2025 | 2024 | 2025-02-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 5:17 | 5:17 | 6:43 | 0:00 | 1.4333 | 1.4333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.71667 | IG Breakdown Maintenance | O2 Project | 4.7 | 340 | 7310
585 | 2025-02-26 | 2025 | 2024 | 2025-02-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 20:25 | 20:25 | 20:58 | 0:00 | 0.55 | 0.55 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.275 | IG Breakdown Maintenance | O2 Project | 4.7 | 340 | 2805
586 | 2025-02-26 | 2025 | 2024 | 2025-02-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 23:01 | 23:01 | 24:00 | 0:00 | 0.98306 | 0.98306 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.49153 | IG Breakdown Maintenance | O2 Project | 4.7 | 340 | 5013.5833
587 | 2025-02-26 | 2025 | 2024 | 2025-02-01 | Year_1 | O2_13 | TQGXIIPL | GEDA | 3.846% | O2-13 Grid Loss | 2:37 | 2:37 | 3:05 | 0:00 | 0.46667 | 0.46667 | VCB Charge after reset and start wtg | Close | 0.017949 | IG Breakdown Maintenance | O2 Project | 4.7 | 340 | 158.6667
588 | 2025-02-26 | 2025 | 2024 | 2025-02-01 | Year_1 | O2_13 | TQGXIIPL | GEDA | 3.846% | O2-13 Grid Loss | 6:43 | 6:43 | 7:15 | 0:00 | 0.53333 | 0.53333 | VCB Charge after reset and start wtg | Close | 0.020513 | IG Breakdown Maintenance | O2 Project | 4.7 | 340 | 181.3333
589 | 2025-02-26 | 2025 | 2024 | 2025-02-01 | Year_1 | O2_25 | TQGXIIPL | GEDA | 3.846% | O2-25 Grid Loss | 4:22 | 4:22 | 4:54 | 0:00 | 0.53333 | 0.53333 | VCB Charge after reset and start wtg | Close | 0.020513 | IG Breakdown Maintenance | O2 Project | 4.7 | 340 | 181.3333
590 | 2025-02-27 | 2025 | 2024 | 2025-02-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 0:00 | 0:00 | 0:30 | 0:00 | 0.5 | 0.5 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.25 | IG Breakdown Maintenance | O2 Project | 4.3 | 252 | 1890
591 | 2025-02-27 | 2025 | 2024 | 2025-02-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 2:54 | 2:54 | 3:35 | 0:00 | 0.68333 | 0.68333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.34167 | IG Breakdown Maintenance | O2 Project | 4.3 | 252 | 2583
592 | 2025-02-27 | 2025 | 2024 | 2025-02-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 14:54 | 14:54 | 15:36 | 0:00 | 0.7 | 0.7 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.35 | IG Breakdown Maintenance | O2 Project | 4.3 | 252 | 2646
593 | 2025-02-27 | 2025 | 2024 | 2025-02-01 | Year_1 | O2_06 | TQGXIIPL | GEDA | 3.846% | O2-06 Grid Loss | 11:26 | 11:26 | 12:12 | 0:00 | 0.76667 | 0.76667 | line shutdown taking by PGVCL Team for 11kv conductor stringing near O2_18, 33kv Line crossing work | Close | 0.029487 | IG Breakdown Maintenance | O2 Project | 4.3 | 252 | 193.2
594 | 2025-02-27 | 2025 | 2024 | 2025-02-01 | Year_1 | O2_17 | TQGXIIPL | GEDA | 3.846% | O2-17 Grid Loss | 11:26 | 11:26 | 12:12 | 0:00 | 0.76667 | 0.76667 | line shutdown taking by PGVCL Team for 11kv conductor stringing near O2_18, 33kv Line crossing work | Close | 0.029487 | IG Breakdown Maintenance | O2 Project | 4.3 | 252 | 193.2
595 | 2025-02-27 | 2025 | 2024 | 2025-02-01 | Year_1 | O2_18 | TQGXIIPL | GEDA | 3.846% | O2-18 Grid Loss | 11:26 | 11:26 | 12:12 | 0:00 | 0.76667 | 0.76667 | line shutdown taking by PGVCL Team for 11kv conductor stringing near O2_18, 33kv Line crossing work | Close | 0.029487 | IG Breakdown Maintenance | O2 Project | 4.3 | 252 | 193.2
596 | 2025-02-27 | 2025 | 2024 | 2025-02-01 | Year_1 | O2_21 | TQGXIIPL | GEDA | 3.846% | O2-21 Grid Loss | 11:26 | 11:26 | 12:12 | 0:00 | 0.76667 | 0.76667 | line shutdown taking by PGVCL Team for 11kv conductor stringing near O2_18, 33kv Line crossing work | Close | 0.029487 | IG Breakdown Maintenance | O2 Project | 4.3 | 252 | 193.2
597 | 2025-02-27 | 2025 | 2024 | 2025-02-01 | Year_1 | O2_22 | TQGXIIPL | GEDA | 3.846% | O2-22 Grid loss | 11:26 | 11:26 | 12:12 | 0:00 | 0.76667 | 0.76667 | line shutdown taking by PGVCL Team for 11kv conductor stringing near O2_18, 33kv Line crossing work | Close | 0.029487 | IG Breakdown Maintenance | O2 Project | 4.3 | 252 | 193.2
598 | 2025-02-28 | 2025 | 2024 | 2025-02-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 0:30 | 0:30 | 1:11 | 0:00 | 0.68333 | 0.68333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.34167 | IG Breakdown Maintenance | O2 Project | 7.1 | 1222.5 | 12530.625
599 | 2025-02-28 | 2025 | 2024 | 2025-02-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 4:00 | 4:00 | 4:37 | 0:00 | 0.61667 | 0.61667 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.30833 | IG Breakdown Maintenance | O2 Project | 7.1 | 1222.5 | 11308.125
600 | 2025-02-28 | 2025 | 2024 | 2025-02-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 6:15 | 6:15 | 6:54 | 0:00 | 0.65 | 0.65 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.325 | IG Breakdown Maintenance | O2 Project | 7.1 | 1222.5 | 11919.375
601 | 2025-02-28 | 2025 | 2024 | 2025-02-01 | Year_1 | O2_13 | TQGXIIPL | GEDA | 3.846% | O2-13 Grid loss | 4:37 | 4:37 | 5:00 | 0:00 | 0.38333 | 0.38333 | VCB Charge after reset and start wtg | Close | 0.014744 | IG Breakdown Maintenance | O2 Project | 7.1 | 1222.5 | 468.625
602 | 2025-02-28 | 2025 | 2024 | 2025-02-01 | Year_1 | O2_13 | TQGXIIPL | GEDA | 3.846% | O2-13 Grid loss | 6:54 | 6:54 | 7:18 | 0:00 | 0.4 | 0.4 | VCB Charge after reset and start wtg | Close | 0.015385 | IG Breakdown Maintenance | O2 Project | 7.1 | 1222.5 | 489
603 | 2025-03-01 | 2025 | 2024 | 2025-03-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 4:38 | 4:38 | 5:18 | 0:00 | 0.66667 | 0.66667 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.33333 | IG Breakdown Maintenance | O2 Project | 6.4 | 901.4 | 9014
604 | 2025-03-01 | 2025 | 2024 | 2025-03-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 6:08 | 6:08 | 6:46 | 0:00 | 0.63333 | 0.63333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.31667 | IG Breakdown Maintenance | O2 Project | 6.4 | 901.4 | 8563.3
605 | 2025-03-01 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_01 | TQGXIIPL | GEDA | 3.846% | Manual Stop for APM Work | 9:00 | 9:00 | 12:07 | 0:00 | 3.1167 | 3.1167 | Manual stop for USS Yard Annual Maintenance work done. | Close | 0.11987 | IG Breakdown Maintenance | O2 Project | 6.4 | 901.4 | 2809.3633
606 | 2025-03-01 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_25 | TQGXIIPL | GEDA | 3.846% | Manual Stop for APM Work | 12:35 | 12:35 | 15:47 | 0:00 | 3.2 | 3.2 | Manual stop for USS Yard Annual Maintenance work done. | Close | 0.12308 | IG Breakdown Maintenance | O2 Project | 6.4 | 901.4 | 2884.48
607 | 2025-03-02 | 2025 | 2024 | 2025-03-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 2:07 | 2:07 | 2:42 | 0:00 | 0.58333 | 0.58333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.29167 | IG Breakdown Maintenance | O2 Project | 5.2 | 469.4 | 4107.25
608 | 2025-03-02 | 2025 | 2024 | 2025-03-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 4:58 | 4:58 | 5:35 | 0:00 | 0.61667 | 0.61667 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.30833 | IG Breakdown Maintenance | O2 Project | 5.2 | 469.4 | 4341.95
609 | 2025-03-02 | 2025 | 2024 | 2025-03-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 6:25 | 6:25 | 7:28 | 0:00 | 1.05 | 1.05 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.525 | IG Breakdown Maintenance | O2 Project | 5.2 | 469.4 | 7393.05
610 | 2025-03-02 | 2025 | 2024 | 2025-03-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 15:15 | 15:15 | 16:01 | 0:00 | 0.76667 | 0.76667 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.38333 | IG Breakdown Maintenance | O2 Project | 5.2 | 469.4 | 5398.1
611 | 2025-03-02 | 2025 | 2024 | 2025-03-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 21:50 | 21:50 | 22:17 | 0:00 | 0.45 | 0.45 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.225 | IG Breakdown Maintenance | O2 Project | 5.2 | 469.4 | 3168.45
612 | 2025-03-02 | 2025 | 2024 | 2025-03-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Tripped in over current | 10:49 | 10:49 | 11:25 | 0:00 | 0.6 | 0.6 | Feeder-2 Tripped in over current & Earth fault /Master Relay due to Bird Fault | Close | 0.3 | IG Breakdown Maintenance | O2 Project | 5.2 | 469.4 | 3098.04
613 | 2025-03-02 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_04 | TQGXIIPL | GEDA | 3.846% | Manual Stop for APM Work | 8:40 | 8:40 | 10:49 | 0:00 | 2.15 | 2.15 | Manual stop for USS Yard Annual Maintenance work wip, | Close | 0.082692 | IG Breakdown Maintenance | O2 Project | 5.2 | 469.4 | 1009.21
614 | 2025-03-02 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_04 | TQGXIIPL | GEDA | 3.846% | Manual Stop for APM Work | 11:25 | 11:25 | 12:00 | 0:00 | 0.58333 | 0.58333 | After grid resume USS Yard Annual Maintenance work done | Close | 0.022436 | IG Breakdown Maintenance | O2 Project | 5.2 | 469.4 | 273.8167
615 | 2025-03-02 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_07 | TQGXIIPL | GEDA | 3.846% | Manual Stop for APM Work | 12:30 | 12:30 | 16:16 | 0:00 | 3.7667 | 3.7667 | Manual stop for USS Yard Annual Maintenance work done. | Close | 0.14487 | IG Breakdown Maintenance | O2 Project | 5.2 | 469.4 | 1768.0733
616 | 2025-03-02 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_10 | TQGXIIPL | GEDA | 3.846% | O2-10 Voltage Assymetry | 14:30 | 14:30 | 14:46 | 0:00 | 0.26667 | 0.26667 | After voltage stable reset and start wtg | Close | 0.010256 | IG Breakdown Maintenance | O2 Project | 5.2 | 469.4 | 125.1733
617 | 2025-03-02 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_13 | TQGXIIPL | GEDA | 3.846% | O2-13 Grid loss | 2:42 | 2:42 | 3:09 | 0:00 | 0.45 | 0.45 | VCB Charge after reset and start wtg | Close | 0.017308 | IG Breakdown Maintenance | O2 Project | 5.2 | 469.4 | 211.23
618 | 2025-03-02 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_13 | TQGXIIPL | GEDA | 3.846% | O2-13 Grid loss | 5:35 | 5:35 | 6:03 | 0:00 | 0.46667 | 0.46667 | VCB Charge after reset and start wtg | Close | 0.017949 | IG Breakdown Maintenance | O2 Project | 5.2 | 469.4 | 219.0533
619 | 2025-03-02 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_25 | TQGXIIPL | GEDA | 3.846% | O2-25 Grid loss | 5:35 | 5:35 | 6:25 | 0:00 | 0.83333 | 0.83333 | After grid resume found VCB trip WIP. | Close | 0.032051 | IG Breakdown Maintenance | O2 Project | 5.2 | 469.4 | 391.1667
620 | 2025-03-02 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_25 | TQGXIIPL | GEDA | 3.846% | O2-25 Grid loss | 7:28 | 7:28 | 7:58 | 0:00 | 0.5 | 0.5 | After grid resume found VCB tripped so VCB Charge after reset and start wtg | Close | 0.019231 | IG Breakdown Maintenance | O2 Project | 5.2 | 469.4 | 234.7
621 | 2025-03-03 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_08 | TQGXIIPL | GEDA | 3.846% | Manual Stop for APM Work | 12:04 | 12:04 | 15:44 | 0:00 | 3.6667 | 3.6667 | USS Yard Annual Maintenance work done. | Close | 0.14103 | IG Breakdown Maintenance | O2 Project | 5.8 | 659.6 | 2418.5333
622 | 2025-03-03 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_10 | TQGXIIPL | GEDA | 3.846% | O2-10 Voltage Assymetry | 9:09 | 9:09 | 9:41 | 0:00 | 0.53333 | 0.53333 | After voltage stable reset and start wtg | Close | 0.020513 | IG Breakdown Maintenance | O2 Project | 5.8 | 659.6 | 351.7867
623 | 2025-03-03 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_10 | TQGXIIPL | GEDA | 3.846% | O2-10 Voltage Assymetry | 11:58 | 11:58 | 14:14 | 0:00 | 2.2667 | 2.2667 | After voltage stable reset and start wtg | Close | 0.087179 | IG Breakdown Maintenance | O2 Project | 5.8 | 659.6 | 1495.0933
624 | 2025-03-03 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_26 | TQGXIIPL | GEDA | 3.846% | Manual Stop for APM Work | 8:35 | 8:35 | 11:56 | 0:00 | 3.35 | 3.35 | USS Yard Annual Maintenance work done. | Close | 0.12885 | IG Breakdown Maintenance | O2 Project | 5.8 | 659.6 | 2209.66
624 | 2025-03-04 | 2025 | 2024 | 2025-03-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 2:22 | 2:22 | 3:06 | 0:00 | 0.73333 | 0.73333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.36667 | IG Breakdown Maintenance | O2 Project | 8.8 | 2141.6 | 23557.6
624 | 2025-03-04 | 2025 | 2024 | 2025-03-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 3:48 | 3:48 | 4:25 | 0:00 | 0.61667 | 0.61667 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.30833 | IG Breakdown Maintenance | O2 Project | 8.8 | 2141.6 | 19809.8
624 | 2025-03-04 | 2025 | 2024 | 2025-03-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 4:55 | 4:55 | 6:06 | 0:00 | 1.1833 | 1.1833 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.59167 | IG Breakdown Maintenance | O2 Project | 8.8 | 2141.6 | 38013.4
624 | 2025-03-04 | 2025 | 2024 | 2025-03-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 9:10 | 9:10 | 9:36 | 0:00 | 0.43333 | 0.43333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.21667 | IG Breakdown Maintenance | O2 Project | 8.8 | 2141.6 | 13920.4
624 | 2025-03-04 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_03 | TQGXIIPL | GEDA | 3.846% | Manual Stop for APM Work | 11:00 | 11:00 | 13:30 | 0:00 | 2.5 | 2.5 | USS Yard Annual Maintenance work done. | Close | 0.096154 | IG Breakdown Maintenance | O2 Project | 8.8 | 2141.6 | 5354
624 | 2025-03-04 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_09 | TQGXIIPL | GEDA | 3.846% | Manual Stop for APM Work | 13:49 | 13:49 | 17:02 | 0:00 | 3.2167 | 3.2167 | USS Yard Annual Maintenance work done. | Close | 0.12372 | IG Breakdown Maintenance | O2 Project | 8.8 | 2141.6 | 6888.8133
624 | 2025-03-04 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_11 | TQGXIIPL | GEDA | 3.846% | O2-11 Grid loss | 6:06 | 6:06 | 6:33 | 0:00 | 0.45 | 0.45 | VCB Charge after reset and start wtg | Close | 0.017308 | IG Breakdown Maintenance | O2 Project | 8.8 | 2141.6 | 963.72
625 | 2025-03-05 | 2025 | 2024 | 2025-03-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 2:34 | 2:34 | 3:07 | 0:00 | 0.55 | 0.55 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.275 | IG Breakdown Maintenance | O2 Project | 8.2 | 1813.4 | 14960.55
626 | 2025-03-05 | 2025 | 2024 | 2025-03-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 5:18 | 5:18 | 5:55 | 0:00 | 0.61667 | 0.61667 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.30833 | IG Breakdown Maintenance | O2 Project | 8.2 | 1813.4 | 16773.95
627 | 2025-03-05 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_08 | TQGXIIPL | GEDA | 3.846% | O2-08 Grid loss | 3:07 | 3:07 | 3:57 | 0:00 | 0.83333 | 0.83333 | VCB Charge after reset and start wtg | Close | 0.032051 | IG Breakdown Maintenance | O2 Project | 8.2 | 1813.4 | 1511.1667
628 | 2025-03-05 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_10 | TQGXIIPL | GEDA | 3.846% | Manual Stop for APM Work | 14:18 | 14:18 | 19:48 | 0:00 | 5.5 | 5.5 | USS Yard Annual Maintenance work done. | Close | 0.21154 | IG Breakdown Maintenance | O2 Project | 8.2 | 1813.4 | 9973.7
629 | 2025-03-05 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_14 | TQGXIIPL | GEDA | 3.846% | Manual Stop for APM Work | 10:14 | 10:14 | 13:50 | 0:00 | 3.6 | 3.6 | USS Yard Annual Maintenance work done. | Close | 0.13846 | IG Breakdown Maintenance | O2 Project | 8.2 | 1813.4 | 6528.24
630 | 2025-03-05 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_17 | TQGXIIPL | GEDA | 3.846% | O2-17 Grid loss | 19:23 | 19:23 | 21:08 | 0:00 | 1.75 | 1.75 | VCB Charge after reset and start wtg | Close | 0.067308 | IG Breakdown Maintenance | O2 Project | 8.2 | 1813.4 | 3173.45
631 | 2025-03-05 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_25 | TQGXIIPL | GEDA | 3.846% | O2-25 Grid loss | 3:07 | 3:07 | 3:42 | 0:00 | 0.58333 | 0.58333 | VCB Charge after reset and start wtg | Close | 0.022436 | IG Breakdown Maintenance | O2 Project | 8.2 | 1813.4 | 1057.8167
632 | 2025-03-06 | 2025 | 2024 | 2025-03-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 23:25 | 23:25 | 24:00 | 0:00 | 0.58333 | 0.58333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.29167 | IG Breakdown Maintenance | O2 Project | 5.5 | 564.5 | 4939.375
633 | 2025-03-06 | 2025 | 2024 | 2025-03-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Tripped in over current | 23:25 | 23:25 | 24:00 | 0:00 | 0.58333 | 0.58333 | Feeder-2 Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on conductor ,so remove it and charge the feeder-02 | Close | 0.29167 | IG Breakdown Maintenance | O2 Project | 5.5 | 564.5 | 3622.2083
634 | 2025-03-06 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_10 | TQGXIIPL | GEDA | 3.846% | O2-10 Grid loss | 9:34 | 9:34 | 19:08 | 0:00 | 9.5667 | 9.5667 | USS Yard LV side cable Inspection Work done than start WTG | Close | 0.36795 | IG Breakdown Maintenance | O2 Project | 5.5 | 564.5 | 5400.3833
635 | 2025-03-07 | 2025 | 2024 | 2025-03-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 0:00 | 0:00 | 0:26 | 0:00 | 0.43333 | 0.43333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.21667 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 1495
636 | 2025-03-07 | 2025 | 2024 | 2025-03-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Tripped in over current | 0:00 | 0:00 | 0:33 | 0:00 | 0.55 | 0.55 | Feeder-2 Tripped in over current & Earth fault /Master Relay Tripped during section isolator open and feeder charge. | Close | 0.275 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 1138.5
637 | 2025-03-07 | 2025 | 2024 | 2025-03-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 1:55 | 1:55 | 2:58 | 0:00 | 1.05 | 1.05 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.525 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 3622.5
638 | 2025-03-07 | 2025 | 2024 | 2025-03-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 5:20 | 5:20 | 6:10 | 0:00 | 0.83333 | 0.83333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.41667 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 2875
639 | 2025-03-07 | 2025 | 2024 | 2025-03-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 6:38 | 6:38 | 7:27 | 0:00 | 0.81667 | 0.81667 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.40833 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 2817.5
640 | 2025-03-07 | 2025 | 2024 | 2025-03-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 8:05 | 8:05 | 8:53 | 0:00 | 0.8 | 0.8 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling no any abnormal, Required pole Shifting-(ROW) | Close | 0.4 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 2760
641 | 2025-03-07 | 2025 | 2024 | 2025-03-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 S/D for O2-10 tapping Jumper open for O2-10 line Inspection Work | 17:17 | 17:17 | 17:35 | 0:00 | 0.3 | 0.3 | Feeder-1 S/D for O2-10 tapping Jumper open for O2-10 line Inspection Work | Close | 0.15 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 1035
642 | 2025-03-07 | 2025 | 2024 | 2025-03-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 S/D for O2-10 tapping Jumper close for O2-10 line Inspection Work done | 19:04 | 19:04 | 19:30 | 0:00 | 0.43333 | 0.43333 | Feeder-1 S/D for O2-10 tapping Jumper close for O2-10 line Inspection Work done | Close | 0.21667 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 1495
643 | 2025-03-07 | 2025 | 2024 | 2025-03-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Tripped in over current | 23:35 | 23:35 | 24:00 | 0:00 | 0.41667 | 0.41667 | Feeder-2 Tripped in over current & Earth fault /Master Relay Tripped during petroling found for pin insulator replace with new reset and start wtg. | Close | 0.20833 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 1054.1667
644 | 2025-03-07 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_06 | TQGXIIPL | GEDA | 3.846% | O2-06 Grid loss | 21:25 | 21:25 | 23:11 | 0:00 | 1.7667 | 1.7667 | USS yard VCB check by BOP team no found any abnormality then charge vcb (VCB Tripped by Unknown Person Security pament Issue) | Close | 0.067949 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 406.3333
645 | 2025-03-07 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_10 | TQGXIIPL | GEDA | 3.846% | O2-10 Voltage asymmetry | 11:05 | 11:05 | 15:31 | 0:00 | 4.4333 | 4.4333 | WTG Manual stop for USS Yard Testing work by BOP Team. | Close | 0.17051 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 1019.6667
646 | 2025-03-07 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_10 | TQGXIIPL | GEDA | 3.846% | O2-10 Grid loss | 17:00 | 17:00 | 19:04 | 0:00 | 2.0667 | 2.0667 | Feeder-1 S/D for O2-10 tapping Jumper close for O2-10 line Inspection Work done | Close | 0.079487 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 475.3333
647 | 2025-03-07 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_13 | TQGXIIPL | GEDA | 3.846% | O2-13 Grid loss | 6:10 | 6:10 | 6:35 | 0:00 | 0.41667 | 0.41667 | VCB Charge after reset and start wtg | Close | 0.016026 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 95.8333
648 | 2025-03-07 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_13 | TQGXIIPL | GEDA | 3.846% | O2-13 Grid loss | 8:53 | 8:53 | 9:19 | 0:00 | 0.43333 | 0.43333 | VCB Charge after reset and start wtg | Close | 0.016667 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 99.6667
649 | 2025-03-07 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_20 | TQGXIIPL | GEDA | 3.846% | O2-20 Grid loss | 13:43 | 13:43 | 15:39 | 0:00 | 1.9333 | 1.9333 | USS yard VCB check by BOP team no found any abnormality then charge vcb (VCB Tripped Security gurd pament Issue) | Close | 0.074359 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 444.6667
650 | 2025-03-07 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_21 | TQGXIIPL | GEDA | 3.846% | O2-21 Grid loss | 21:41 | 21:41 | 23:34 | 0:00 | 1.8833 | 1.8833 | USS yard VCB check by BOP team no found any abnormality then charge vcb (VCB Tripped Security gurd pament Issue) | Close | 0.072436 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 433.1667
651 | 2025-03-07 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_24 | TQGXIIPL | GEDA | 3.846% | O2-24 Grid loss | 13:30 | 13:30 | 14:31 | 0:00 | 1.0167 | 1.0167 | USS yard VCB check by BOP team no found any abnormality then charge vcb (VCB Tripped Security gurd pament Issue) | Close | 0.039103 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 233.8333
652 | 2025-03-07 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_24 | TQGXIIPL | GEDA | 3.846% | O2-24 Grid loss | 14:42 | 14:42 | 15:40 | 0:00 | 0.96667 | 0.96667 | USS yard VCB check by BOP team no found any abnormality then charge vcb (VCB Tripped Security gurd pament Issue) | Close | 0.037179 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 222.3333
653 | 2025-03-08 | 2025 | 2024 | 2025-03-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Tripped in over current | 0:00 | 0:00 | 2:08 | 0:00 | 2.1333 | 2.1333 | Feeder-2 tripped in Over current & Earth fault/Master Relay tripped due to Conductor falling on Pin at F#2 PP165 than after fault find out Feeder-2 Partially Charge (O2-04,07,17,19,22 Section Isolator Open ) Line petroling WIP, | Close | 1.0667 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 10271.36
654 | 2025-03-08 | 2025 | 2024 | 2025-03-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 shutdown by BOP team | 5:05 | 5:05 | 6:10 | 0:00 | 1.0833 | 1.0833 | Feeder-2 Shutdown taking for Section isolator Connect work.(9 WTG Connect and O2-17 & 22 Disconnect)Annual PM work | Close | 0.54167 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 5215.925
655 | 2025-03-08 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_04 | TQGXIIPL | GEDA | 3.846% | O2-04 Grid loss | 2:08 | 2:08 | 2:45 | 0:00 | 0.61667 | 0.61667 | O2-04,07 & 19 Section Isolator Close by BOP team then start WTG. | Close | 0.023718 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 2429.235
656 | 2025-03-08 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_07 | TQGXIIPL | GEDA | 3.846% | O2-07 Grid loss | 2:08 | 2:08 | 2:45 | 0:00 | 0.61667 | 0.61667 | O2-04,07 & 19 Section Isolator Close by BOP team then start WTG. | Close | 0.023718 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 269.915
657 | 2025-03-08 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_10 | TQGXIIPL | GEDA | 3.846% | O2-10 Grid loss | 13:00 | 13:00 | 17:00 | 0:00 | 4 | 4 | WTG Stop For USS Yard VCB Testing work (CRM Test) | Close | 0.15385 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 1750.8
658 | 2025-03-08 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_15 | TQGXIIPL | GEDA | 3.846% | Manual Stop for APM Work | 9:20 | 9:20 | 12:17 | 0:00 | 2.95 | 2.95 | USS Yard Annual Maintenance work done. | Close | 0.11346 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 1291.215
659 | 2025-03-08 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_17 | TQGXIIPL | GEDA | 3.846% | O2-17 Grid loss | 2:08 | 2:08 | 5:05 | 0:00 | 2.95 | 2.95 | Feeder-2 tripped due to Conductor Falling on Pin at F#2 PP165 so line petrolling O2-17 & 22 section isolator open wip | Close | 0.11346 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 1291.215
660 | 2025-03-08 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_17 | TQGXIIPL | GEDA | 3.846% | O2-17 Grid loss | 6:10 | 6:10 | 7:45 | 0:00 | 1.5833 | 1.5833 | Feeder-2 tripped due to Conductor Falling on Pin at F#2 PP165 for line petrolling after fault find out O2-17 & 22 section isolator close and start WTG. | Close | 0.060897 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 693.025
661 | 2025-03-08 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_19 | TQGXIIPL | GEDA | 3.846% | O2-19 Grid loss | 2:08 | 2:08 | 2:45 | 0:00 | 0.61667 | 0.61667 | O2-04,07 & 19 Section Isolator Close by BOP team then start WTG. | Close | 0.023718 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 269.915
662 | 2025-03-08 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_22 | TQGXIIPL | GEDA | 3.846% | O2-22 Grid loss | 2:08 | 2:08 | 5:05 | 0:00 | 2.95 | 2.95 | Feeder-2 tripped due to Conductor Falling on Pin at F#2 PP165 so line petrolling O2-17 & 22 section isolator open wip | Close | 0.11346 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 1291.215
663 | 2025-03-08 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_22 | TQGXIIPL | GEDA | 3.846% | O2-22 Grid loss | 6:10 | 6:10 | 7:45 | 0:00 | 1.5833 | 1.5833 | Feeder-2 tripped due to Conductor Falling on Pin at F#2 PP165 for line petrolling after fault find out O2-17 & 22 section isolator close and start WTG. | Close | 0.060897 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 693.025
664 | 2025-03-10 | 2025 | 2024 | 2025-03-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 22:32 | 22:32 | 23:09 | 0:00 | 0.61667 | 0.61667 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on conductor ,so remove it and charge the feeder-01 | Close | 0.30833 | IG Breakdown Maintenance | O2 Project | 4.3 | 252 | 1398.6
665 | 2025-03-10 | 2025 | 2024 | 2025-03-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 23:56 | 23:56 | 24:00 | 0:00 | 0.066389 | 0.066389 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on conductor ,so remove it and charge the feeder-01 | Close | 0.033194 | IG Breakdown Maintenance | O2 Project | 4.3 | 252 | 150.57
666 | 2025-03-11 | 2025 | 2024 | 2025-03-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 0:00 | 0:00 | 0:49 | 0:00 | 0.81667 | 0.81667 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on conductor ,so remove it and charge the feeder-01 | Close | 0.40833 | IG Breakdown Maintenance | O2 Project | 4.4 | 274 | 3356.5
667 | 2025-03-11 | 2025 | 2024 | 2025-03-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 1:56 | 1:56 | 3:31 | 0:00 | 1.5833 | 1.5833 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on conductor ,so remove it and charge the feeder-01 | Close | 0.79167 | IG Breakdown Maintenance | O2 Project | 4.4 | 274 | 6507.5
668 | 2025-03-11 | 2025 | 2024 | 2025-03-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 3:46 | 3:46 | 4:50 | 0:00 | 1.0667 | 1.0667 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on conductor ,so remove it and charge the feeder-01 | Close | 0.53333 | IG Breakdown Maintenance | O2 Project | 4.4 | 274 | 4384
669 | 2025-03-11 | 2025 | 2024 | 2025-03-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 5:12 | 5:12 | 6:50 | 0:00 | 1.6333 | 1.6333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on conductor ,so remove it and charge the feeder-01 | Close | 0.81667 | IG Breakdown Maintenance | O2 Project | 4.4 | 274 | 6713
670 | 2025-03-11 | 2025 | 2024 | 2025-03-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 7:12 | 7:12 | 8:11 | 0:00 | 0.98333 | 0.98333 | Feeder-1 Tripped in over current & Earth fault /Master Relay Tripped during petroling found the metalic chain on conductor ,so remove it and charge the feeder-01 | Close | 0.49167 | IG Breakdown Maintenance | O2 Project | 4.4 | 274 | 4041.5
671 | 2025-03-11 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_13 | TQGXIIPL | GEDA | 3.846% | O2-13 Grid Loss | 6:50 | 6:50 | 7:12 | 0:00 | 0.36667 | 0.36667 | VCB Charge after reset and start wtg | Close | 0.014103 | IG Breakdown Maintenance | O2 Project | 4.4 | 274 | 100.4667
672 | 2025-03-11 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_13 | TQGXIIPL | GEDA | 3.846% | O2-13 Grid Loss | 8:11 | 8:11 | 8:45 | 0:00 | 0.56667 | 0.56667 | VCB Charge after reset and start wtg | Close | 0.021795 | IG Breakdown Maintenance | O2 Project | 4.4 | 274 | 155.2667
673 | 2025-03-11 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_08 | TQGXIIPL | GEDA | 3.846% | O2-08 Grid loss | 8:11 | 8:11 | 9:06 | 0:00 | 0.91667 | 0.91667 | VCB Charge after reset and start wtg | Close | 0.035256 | IG Breakdown Maintenance | O2 Project | 4.4 | 274 | 251.1667
674 | 2025-03-11 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_25 | TQGXIIPL | GEDA | 3.846% | O2-25 Grid Loss | 8:11 | 8:11 | 9:34 | 0:00 | 1.3833 | 1.3833 | VCB Charge after reset and start wtg | Close | 0.053205 | IG Breakdown Maintenance | O2 Project | 4.4 | 274 | 379.0333
675 | 2025-03-11 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_13 | TQGXIIPL | GEDA | 3.846% | Manual Stop for APM Work | 9:09 | 9:09 | 10:48 | 0:00 | 1.65 | 1.65 | USS Yard Annual Maintenance work done. | Close | 0.063462 | IG Breakdown Maintenance | O2 Project | 4.4 | 274 | 452.1
676 | 2025-03-11 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_11 | TQGXIIPL | GEDA | 3.846% | Manual Stop for APM Work | 11:13 | 11:13 | 14:08 | 0:00 | 2.9167 | 2.9167 | USS Yard Annual Maintenance work done. | Close | 0.11218 | IG Breakdown Maintenance | O2 Project | 4.4 | 274 | 799.1667
677 | 2025-03-11 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_24 | TQGXIIPL | GEDA | 3.846% | Manual Stop for APM Work | 14:43 | 14:43 | 16:55 | 0:00 | 2.2 | 2.2 | USS Yard Annual Maintenance work done. | Close | 0.084615 | IG Breakdown Maintenance | O2 Project | 4.4 | 274 | 602.8
678 | 2025-03-12 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_18 | TQGXIIPL | GEDA | 3.846% | Manual Stop for APM Work | 9:09 | 9:09 | 11:28 | 0:00 | 2.3167 | 2.3167 | USS Yard Annual Maintenance work done. | Close | 0.089103 | IG Breakdown Maintenance | O2 Project | 5.4 | 532.8 | 1234.32
679 | 2025-03-12 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_06 | TQGXIIPL | GEDA | 3.846% | Manual Stop for APM Work | 11:48 | 11:48 | 14:25 | 0:00 | 2.6167 | 2.6167 | USS Yard Annual Maintenance work done. | Close | 0.10064 | IG Breakdown Maintenance | O2 Project | 5.4 | 532.8 | 1394.16
680 | 2025-03-12 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_21 | TQGXIIPL | GEDA | 3.846% | Manual Stop for APM Work | 14:41 | 14:41 | 17:24 | 0:00 | 2.7167 | 2.7167 | USS Yard Annual Maintenance work done. | Close | 0.10449 | IG Breakdown Maintenance | O2 Project | 5.4 | 532.8 | 1447.44
681 | 2025-03-12 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_21 | TQGXIIPL | GEDA | 3.846% | O2_21 Grid Loss | 22:31 | 22:31 | 23:12 | 0:00 | 0.68333 | 0.68333 | USS yard VCB check by BOP team no found any abnormality then charge vcb, VCB tripped due to row issues or security payment issues , | Close | 0.026282 | IG Breakdown Maintenance | O2 Project | 5.4 | 532.8 | 364.08
682 | 2025-03-12 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_06 | TQGXIIPL | GEDA | 3.846% | O2_06 Grid Loss | 22:14 | 22:14 | 22:48 | 0:00 | 0.56667 | 0.56667 | USS yard VCB check by BOP team no found any abnormality then charge vcb, VCB tripped due to row issues or security payment issues , | Close | 0.021795 | IG Breakdown Maintenance | O2 Project | 5.4 | 532.8 | 301.92
683 | 2025-03-12 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_22 | TQGXIIPL | GEDA | 3.846% | O2_22 Grid Loss | 22:26 | 22:26 | 23:26 | 0:00 | 1 | 1 | USS yard VCB check by BOP team no found any abnormality then charge vcb, VCB tripped due to row issues or security payment issues , | Close | 0.038462 | IG Breakdown Maintenance | O2 Project | 5.4 | 532.8 | 532.8
684 | 2025-03-13 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_05 | TQGXIIPL | GEDA | 3.846% | Manual Stop for APM Work | 9:25 | 9:25 | 12:10 | 0:00 | 2.75 | 2.75 | USS Yard Annual Maintenance work done. | Close | 0.10577 | IG Breakdown Maintenance | O2 Project | 7.5 | 1329.5 | 3656.125
685 | 2025-03-13 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_02 | TQGXIIPL | GEDA | 3.846% | Manual Stop for APM Work | 12:23 | 12:23 | 14:51 | 0:00 | 2.4667 | 2.4667 | USS Yard Annual Maintenance work done. | Close | 0.094872 | IG Breakdown Maintenance | O2 Project | 7.5 | 1329.5 | 3279.4333
686 | 2025-03-13 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_26 | TQGXIIPL | GEDA | 3.846% | O2-26 Grid Loss | 9:56 | 9:56 | 12:10 | 0:00 | 2.2333 | 2.2333 | O2-05 VCB trip due to USS Yard Annual Maintenance work done.so wtg discannected from SCADA | Close | 0.085897 | IG Breakdown Maintenance | O2 Project | 7.5 | 1329.5 | 2969.2167
687 | 2025-03-13 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_26 | TQGXIIPL | GEDA | 3.846% | O2-26 Grid Loss | 12:10 | 12:10 | 16:30 | 0:00 | 4.3333 | 4.3333 | USS yard VCB check by BOP team no found any abnormality then charge vcb, VCB tripped due to row issues or security payment issues , | Close | 0.16667 | IG Breakdown Maintenance | O2 Project | 7.5 | 1329.5 | 5761.1667
688 | 2025-03-15 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_12 | TQGXIIPL | GEDA | 3.846% | Manual Stop for APM Work | 8:53 | 8:53 | 11:02 | 0:00 | 2.15 | 2.15 | USS Yard Annual Maintenance work done. | Close | 0.082692 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 941.055
689 | 2025-03-15 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_23 | TQGXIIPL | GEDA | 3.846% | Manual Stop for APM Work | 11:22 | 11:22 | 13:26 | 0:00 | 2.0667 | 2.0667 | USS Yard Annual Maintenance work done. | Close | 0.079487 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 904.58
690 | 2025-03-15 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_20 | TQGXIIPL | GEDA | 3.846% | Manual Stop for APM Work | 14:06 | 14:06 | 15:48 | 0:00 | 1.7 | 1.7 | USS Yard Annual Maintenance work done. | Close | 0.065385 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 744.09
691 | 2025-03-15 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_16 | TQGXIIPL | GEDA | 3.846% | Manual Stop for APM Work | 16:00 | 16:00 | 18:04 | 0:00 | 2.0667 | 2.0667 | USS Yard Annual Maintenance work done. | Close | 0.079487 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 904.58
692 | 2025-03-16 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_17 | TQGXIIPL | GEDA | 3.846% | Manual Stop for APM Work | 9:57 | 9:57 | 11:52 | 0:00 | 1.9167 | 1.9167 | USS Yard Annual Maintenance work done. | Close | 0.073718 | IG Breakdown Maintenance | O2 Project | 6.1 | 767.6 | 1471.2333
693 | 2025-03-16 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_22 | TQGXIIPL | GEDA | 3.846% | Manual Stop for APM Work | 12:08 | 12:08 | 14:00 | 0:00 | 1.8667 | 1.8667 | USS Yard Annual Maintenance work done. | Close | 0.071795 | IG Breakdown Maintenance | O2 Project | 6.2 | 812.12 | 1515.9573
694 | 2025-03-16 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_19 | TQGXIIPL | GEDA | 3.846% | Manual Stop for APM Work | 14:37 | 14:37 | 17:25 | 0:00 | 2.8 | 2.8 | USS Yard Annual Maintenance work done. | Close | 0.10769 | IG Breakdown Maintenance | O2 Project | 5.8 | 659.6 | 1846.88
695 | 2025-03-16 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_10 | TQGXIIPL | GEDA | 3.846% | O2-10 Voltage Assymetry | 12:40 | 12:40 | 17:40 | 0:00 | 5 | 5 | due to grid voltage Unblaced so check Grid voltage and cable so ok after trail so ok then reset and start wtg | Close | 0.19231 | IG Breakdown Maintenance | O2 Project | 6 | 723 | 3615
696 | 2025-03-18 | 2025 | 2024 | 2025-03-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown | 9:00 | 9:00 | 19:04 | 0:00 | 10.0667 | 10.0667 | During PSS Shutdown we have been Done 66KV/33KV PSS Equipment Annual testing & Feeder#1 Annual PM Work | Close | 5.0333 | IG Breakdown Maintenance | O2 Project | 5 | 406 | 61306
697 | 2025-03-18 | 2025 | 2024 | 2025-03-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 shutdown | 9:00 | 9:00 | 19:06 | 0:00 | 10.1 | 10.1 | During PSS Shutdown we have been Done 66KV/33KV PSS Equipment Annual testing work. | Close | 5.05 | IG Breakdown Maintenance | O2 Project | 5 | 406 | 45106.6
697 | 2025-03-22 | 2025 | 2024 | 2025-03-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 shutdown | 9:14 | 9:14 | 19:24 | 0:00 | 10.1667 | 10.1667 | Feeder#2 Shutdown taken for F#2 Line Annual Maintance work | Close | 5.0833 | IG Breakdown Maintenance | O2 Project | 4.7 | 340 | 31110
698 | 2025-03-23 | 2025 | 2024 | 2025-03-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 shutdown | 10:42 | 10:42 | 10:59 | 0:00 | 0.28333 | 0.28333 | O2-17 AND O2-22 Section Isolator Open Feeder-02 Shutdown taken Annual Maintenance Work) | Close | 0.14167 | IG Breakdown Maintenance | O2 Project | 4.5 | 296 | 922.5333
699 | 2025-03-23 | 2025 | 2024 | 2025-03-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 shutdown | 14:24 | 14:24 | 14:43 | 0:00 | 0.31667 | 0.31667 | O2-17 AND O2-22 Section Isolator Close Feeder-02 Shutdown taken Annual Maintenance Work) | Close | 0.15833 | IG Breakdown Maintenance | O2 Project | 4.5 | 296 | 1031.0667
700 | 2025-03-23 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_17 | TQGXIIPL | GEDA | 3.846% | O2-17 Grid loss | 10:42 | 10:42 | 14:43 | 0:00 | 4.0167 | 4.0167 | O2-17 And O2-22 Annual Line Maintenance work | Close | 0.15449 | IG Breakdown Maintenance | O2 Project | 4.5 | 296 | 1188.9333
701 | 2025-03-23 | 2025 | 2024 | 2025-03-01 | Year_1 | O2_22 | TQGXIIPL | GEDA | 3.846% | O2-22 Grid loss | 10:42 | 10:42 | 14:43 | 0:00 | 4.0167 | 4.0167 | O2-17 And O2-22 Annual Line Maintenance work | Close | 0.15449 | IG Breakdown Maintenance | O2 Project | 4.5 | 296 | 1188.9333
700 | 2025-04-03 | 2025 | 2024 | 2025-04-01 | Year_1 | O2_10 | TQGXIIPL | GEDA | 3.846% | O2-10 Manual stop (WTG Manual stop for USS Yard transformer oil leakage arrests work) | 17:48 | 17:48 | 18:09 | 0:00 | 0.35 | 0.35 | WTG Manual stop for USS Yard Transformer Oil Leakage Arrests work | Close | 0.013462 | IG Breakdown Maintenance | O2 Project | 4.8 | 362 | 126.7
701 | 2025-04-05 | 2025 | 2024 | 2025-04-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in Earth fault | 7:45 | 7:45 | 8:20 | 0:00 | 0.58333 | 0.58333 | Feeder-1 tripping Earth fault during line petrolling found for bird fault Pole no CP-103 Near O2-02. Test trail and feeder charge. | Close | 0.29167 | IG Breakdown Maintenance | O2 Project | 4.4 | 274 | 2397.5
702 | 2025-04-07 | 2025 | 2024 | 2025-04-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in Earth fault | 7:25 | 7:25 | 7:48 | 0:00 | 0.38333 | 0.38333 | Feeder-1 tripping Earth fault during line petrolling found for bird fault Pole no CP-34 Near O2-01. Test trail and feeder charge. | Close | 0.19167 | IG Breakdown Maintenance | O2 Project | 7.2 | 1276 | 7337
703 | 2025-04-12 | 2025 | 2024 | 2025-04-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 7:20 | 7:20 | 7:32 | 0:00 | 0.2 | 0.2 | Feeder#1 Trip in Over Current & earth fault/master relay trip | Close | 0.1 | IG Breakdown Maintenance | O2 Project | 5 | 406 | 1218
704 | 2025-04-12 | 2025 | 2024 | 2025-04-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown | 12:26 | 12:26 | 24:00 | 0:00 | 11.5667 | 11.5667 | Manual Shutdown taken for TR LV cable Inspection Work and conductor replacement work. | Open | 5.7833 | IG Breakdown Maintenance | O2 Project | 5 | 406 | 70441
705 | 2025-04-12 | 2025 | 2024 | 2025-04-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 shutdown | 12:26 | 12:26 | 24:00 | 0:00 | 11.5667 | 11.5667 | Manual Shutdown taken for TR LV cable Inspection Work and conductor replacement work. | Open | 5.7833 | IG Breakdown Maintenance | O2 Project | 5 | 406 | 51656.7333
706 | 2025-04-13 | 2025 | 2024 | 2025-04-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown | 0:00 | 0:00 | 7:04 | 0:00 | 7.0667 | 7.0667 | Manual Shutdown taken for TR LV cable Inspection Work and conductor replacement work. | Close | 3.5333 | IG Breakdown Maintenance | O2 Project | 7.6 | 1490 | 157940
707 | 2025-04-13 | 2025 | 2024 | 2025-04-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 shutdown | 0:00 | 0:00 | 7:04 | 0:00 | 7.0667 | 7.0667 | Manual Shutdown taken for TR LV cable Inspection Work and conductor replacement work. | Close | 3.5333 | IG Breakdown Maintenance | O2 Project | 7.6 | 1490 | 115822.6667
708 | 2025-04-16 | 2025 | 2024 | 2025-04-01 | Year_1 | O2_10 | TQGXIIPL | GEDA | 3.846% | Converter torque monitor level 1(grid voltage down) | 9:08 | 9:08 | 9:24 | 0:00 | 0.26667 | 0.26667 | Checked related error data log and found grid voltage down so check by BOP team ,grid volage is normalise then reset & started WTG. | Close | 0.010256 | IG Breakdown Maintenance | O2 Project | 7.9 | 1650.5 | 440.1333
709 | 2025-04-21 | 2025 | 2024 | 2025-04-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown | 8:56 | 8:56 | 9:31 | 0:00 | 0.58333 | 0.58333 | Feeder-1 Shutdown taking by for near O2_09 conductor repairing work & Conductor replacement work Note:- O2_01,26,08,25,02,05 jumper open | Close | 0.29167 | IG Breakdown Maintenance | O2 Project | 5 | 406 | 3552.5
710 | 2025-04-21 | 2025 | 2024 | 2025-04-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown | 18:44 | 18:44 | 19:10 | 0:00 | 0.43333 | 0.43333 | Feeder-1 Shutdown taking by for near O2_09 conductor repairing work & Conductor replacement work Note:- O2_01,26,08,25,02,05 jumper open | Close | 0.21667 | IG Breakdown Maintenance | O2 Project | 5 | 406 | 2639
711 | 2025-04-21 | 2025 | 2024 | 2025-04-01 | Year_1 | O2_01 | TQGXIIPL | GEDA | 3.846% | O2_01 WTG Shutdown | 9:31 | 9:31 | 18:44 | 0:00 | 9.2167 | 9.2167 | Feeder-1 Shutdown taking by for near O2_09 conductor repairing work & Conductor replacement work Note:- O2_01,26,08,25,02,05 jumper open | Close | 0.35449 | IG Breakdown Maintenance | O2 Project | 5 | 406 | 3741.9667
712 | 2025-04-21 | 2025 | 2024 | 2025-04-01 | Year_1 | O2_02 | TQGXIIPL | GEDA | 3.846% | O2_02 WTG Shutdown | 9:31 | 9:31 | 18:44 | 0:00 | 9.2167 | 9.2167 | Feeder-1 Shutdown taking by for near O2_09 conductor repairing work & Conductor replacement work Note:- O2_01,26,08,25,02,05 jumper open | Close | 0.35449 | IG Breakdown Maintenance | O2 Project | 5 | 406 | 3741.9667
713 | 2025-04-21 | 2025 | 2024 | 2025-04-01 | Year_1 | O2_05 | TQGXIIPL | GEDA | 3.846% | O2_05 WTG Shutdown | 9:31 | 9:31 | 18:44 | 0:00 | 9.2167 | 9.2167 | Feeder-1 Shutdown taking by for near O2_09 conductor repairing work & Conductor replacement work Note:- O2_01,26,08,25,02,05 jumper open | Close | 0.35449 | IG Breakdown Maintenance | O2 Project | 5 | 406 | 3741.9667
714 | 2025-04-21 | 2025 | 2024 | 2025-04-01 | Year_1 | O2_08 | TQGXIIPL | GEDA | 3.846% | O2_08 WTG Shutdown | 9:31 | 9:31 | 18:44 | 0:00 | 9.2167 | 9.2167 | Feeder-1 Shutdown taking by for near O2_09 conductor repairing work & Conductor replacement work Note:- O2_01,26,08,25,02,05 jumper open | Close | 0.35449 | IG Breakdown Maintenance | O2 Project | 5 | 406 | 3741.9667
715 | 2025-04-21 | 2025 | 2024 | 2025-04-01 | Year_1 | O2_25 | TQGXIIPL | GEDA | 3.846% | O2_25 WTG Shutdown | 9:31 | 9:31 | 18:44 | 0:00 | 9.2167 | 9.2167 | Feeder-1 Shutdown taking by for near O2_09 conductor repairing work & Conductor replacement work Note:- O2_01,26,08,25,02,05 jumper open | Close | 0.35449 | IG Breakdown Maintenance | O2 Project | 5 | 406 | 3741.9667
716 | 2025-04-21 | 2025 | 2024 | 2025-04-01 | Year_1 | O2_26 | TQGXIIPL | GEDA | 3.846% | O2_26 WTG Shutdown | 9:31 | 9:31 | 18:44 | 0:00 | 9.2167 | 9.2167 | Feeder-1 Shutdown taking by for near O2_09 conductor repairing work & Conductor replacement work Note:- O2_01,26,08,25,02,05 jumper open | Close | 0.35449 | IG Breakdown Maintenance | O2 Project | 5 | 406 | 3741.9667
717 | 2025-04-22 | 2025 | 2024 | 2025-04-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 shutdown | 15:19 | 15:19 | 15:48 | 0:00 | 0.48333 | 0.48333 | Feeder-2 Shutdown taking by for near O2_04 conductor repairing work,& conductor replacement work Note:-O2_04,O2_07,O2_19 isolator closing work | Close | 0.24167 | IG Breakdown Maintenance | O2 Project | 5.2 | 469.4 | 2495.6433
718 | 2025-04-22 | 2025 | 2024 | 2025-04-01 | Year_1 | O2_04 | TQGXIIPL | GEDA | 3.846% | O2_04 WTG Shutdown | 12:36 | 12:36 | 15:19 | 0:00 | 2.7167 | 2.7167 | Feeder-2 Shutdown taking by for near O2_04 conductor repairing work,& conductor replacement work Note:-O2_04,O2_07,O2_19 isolator closing work | Close | 0.10449 | IG Breakdown Maintenance | O2 Project | 5.2 | 469.4 | 1275.2033
719 | 2025-04-22 | 2025 | 2024 | 2025-04-01 | Year_1 | O2_07 | TQGXIIPL | GEDA | 3.846% | O2_07 WTG Shutdown | 12:36 | 12:36 | 15:19 | 0:00 | 2.7167 | 2.7167 | Feeder-2 Shutdown taking by for near O2_04 conductor repairing work,& conductor replacement work Note:-O2_04,O2_07,O2_19 isolator closing work | Close | 0.10449 | IG Breakdown Maintenance | O2 Project | 5.2 | 469.4 | 1275.2033
720 | 2025-04-22 | 2025 | 2024 | 2025-04-01 | Year_1 | O2_19 | TQGXIIPL | GEDA | 3.846% | O2_19 WTG Shutdown | 12:36 | 12:36 | 15:19 | 0:00 | 2.7167 | 2.7167 | Feeder-2 Shutdown taking by for near O2_04 conductor repairing work,& conductor replacement work Note:-O2_04,O2_07,O2_19 isolator closing work | Close | 0.10449 | IG Breakdown Maintenance | O2 Project | 5.2 | 469.4 | 1275.2033
721 | 2025-04-28 | 2025 | 2024 | 2025-04-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 18:12 | 18:12 | 18:23 | 0:00 | 0.18333 | 0.18333 | Feeder#1 Trip in Over Current & earth fault/master relay trip | Close | 0.091667 | IG Breakdown Maintenance | O2 Project | 6.6 | 990.6 | 2724.15
722 | 2025-04-28 | 2025 | 2024 | 2025-04-01 | Year_1 | O2_14 | TQGXIIPL | GEDA | 3.846% | O2-14 WTG Shutdown (Grid loss) | 14:41 | 14:41 | 15:38 | 0:00 | 0.95 | 0.95 | WTG stop for HT Yard Inspection Work. | Close | 0.036538 | IG Breakdown Maintenance | O2 Project | 6.6 | 990.6 | 941.07
723 | 2025-05-06 | 2025 | 2024 | 2025-05-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Tripped in over current. | 0:14 | 0:14 | 0:46 | 0:00 | 0.53333 | 0.53333 | Trip in over current Due to Havy rain and lighting also gusty wind whether normalisation then line inspection test trail and feeder charge | Close | 0.26667 | IG Breakdown Maintenance | O2 Project | 6.9 | 1124.4 | 6596.48
724 | 2025-05-06 | 2025 | 2024 | 2025-05-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Tripped in over current. | 15:32 | 15:32 | 17:50 | 0:00 | 2.3 | 2.3 | Trip in over current Due to Havy rain and lighting also gusty wind whether normalisation then line inspection test trail and feeder charge | Close | 1.15 | IG Breakdown Maintenance | O2 Project | 6.9 | 1124.4 | 28447.32
725 | 2025-05-06 | 2025 | 2024 | 2025-05-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 15:55 | 15:55 | 24:00 | 0:00 | 8.0833 | 8.0833 | Trip in over current Due to Havy rain and lighting also gusty wind whether normalisation then line inspection WIP | Open | 4.0417 | IG Breakdown Maintenance | O2 Project | 6.9 | 1124.4 | 136333.5
726 | 2025-05-06 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_16 | TQGXIIPL | GEDA | 3.846% | O2_16 Grid Loss | 17:50 | 17:50 | 20:48 | 0:00 | 2.9667 | 2.9667 | After grid resume time VCB OFF after PSS Team attend and charge VCB | Close | 0.1141 | IG Breakdown Maintenance | O2 Project | 6.9 | 1124.4 | 3335.72
727 | 2025-05-07 | 2025 | 2024 | 2025-05-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 0:00 | 0:00 | 2:10 | 0:00 | 2.1667 | 2.1667 | Trip in over current Due to Havy rain and lighting also gusty wind whether normalisation then line inspection found for panther line pin isulator damage replace with new reset and test trail and feeder charge | Close | 1.0833 | IG Breakdown Maintenance | O2 Project | 5.8 | 659.6 | 21437
728 | 2025-05-07 | 2025 | 2024 | 2025-05-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown | 16:02 | 16:02 | 16:58 | 0:00 | 0.93333 | 0.93333 | Feeder-1 shutdown take for OFC Splicing work | Close | 0.46667 | IG Breakdown Maintenance | O2 Project | 5.8 | 659.6 | 9234.4
729 | 2025-05-07 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_13 | TQGXIIPL | GEDA | 3.846% | O2_13 Grid Loss | 2:10 | 2:10 | 2:23 | 0:00 | 0.21667 | 0.21667 | After grid resume time VCB OFF after PSS Team attend and charge VCB | Close | 0.0083333 | IG Breakdown Maintenance | O2 Project | 5.8 | 659.6 | 142.9133
730 | 2025-05-07 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_14 | TQGXIIPL | GEDA | 3.846% | O2_14 Grid Loss | 2:10 | 2:10 | 2:32 | 0:00 | 0.36667 | 0.36667 | After grid resume time VCB OFF after PSS Team attend and charge VCB | Close | 0.014103 | IG Breakdown Maintenance | O2 Project | 5.8 | 659.6 | 241.8533
731 | 2025-05-07 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_25 | TQGXIIPL | GEDA | 3.846% | O2_25 Grid Loss | 2:10 | 2:10 | 3:10 | 0:00 | 1 | 1 | After grid resume time VCB OFF after PSS Team attend and charge VCB | Close | 0.038462 | IG Breakdown Maintenance | O2 Project | 5.8 | 659.6 | 659.6
732 | 2025-05-08 | 2025 | 2024 | 2025-05-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 17:54 | 17:54 | 18:54 | 0:00 | 1 | 1 | Feeder#1 Trip in Over Current & earth fault/master relay trip | Close | 0.5 | IG Breakdown Maintenance | O2 Project | 4.1 | 208 | 1872
733 | 2025-05-09 | 2025 | 2024 | 2025-05-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Trip in Earth fault | 17:17 | 17:17 | 19:03 | 0:00 | 1.7667 | 1.7667 | Feeder-2 Trip in Earth fault after take a trial then charge it. | Close | 0.88333 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 4469.6667
734 | 2025-05-09 | 2025 | 2024 | 2025-05-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 shutdown for O2-19 line jumper Open work | 21:47 | 21:47 | 21:57 | 0:00 | 0.16667 | 0.16667 | Feeder-2 shutdown for O2-19 line jumper Open work | Close | 0.083333 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 421.6667
735 | 2025-05-09 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_04 | TQGXIIPL | GEDA | 3.846% | O2_04 Grid Loss | 19:04 | 19:04 | 21:46 | 0:00 | 2.7 | 2.7 | O2-04, O2-19 & O2-07 Internal lines rectification work | Close | 0.10385 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 621
736 | 2025-05-09 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_07 | TQGXIIPL | GEDA | 3.846% | O2_07 Grid Loss | 19:04 | 19:04 | 21:46 | 0:00 | 2.7 | 2.7 | O2-04, O2-19 & O2-07 Internal lines rectification work | Close | 0.10385 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 621
737 | 2025-05-09 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_19 | TQGXIIPL | GEDA | 3.846% | O2_19 Grid Loss | 19:04 | 19:04 | 21:46 | 0:00 | 2.7 | 2.7 | O2-04, O2-19 & O2-07 Internal lines rectification work | Close | 0.10385 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 621
738 | 2025-05-09 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_19 | TQGXIIPL | GEDA | 3.846% | O2_19 Grid Loss | 21:58 | 21:58 | 24:00 | 0:00 | 2.0333 | 2.0333 | O2-19 Internal lines rectification work | Open | 0.078205 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 467.6667
739 | 2025-05-09 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_04 | TQGXIIPL | GEDA | 3.846% | O2_04 Grid Loss | 23:45 | 23:45 | 24:00 | 0:00 | 0.25 | 0.25 | O2-04 & O2-07 Internal lines rectification work | Close | 0.0096154 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 57.5
740 | 2025-05-09 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_07 | TQGXIIPL | GEDA | 3.846% | O2_07 Grid Loss | 23:45 | 23:45 | 24:00 | 0:00 | 0.25 | 0.25 | O2-04 & O2-07 Internal lines rectification work | Close | 0.0096154 | IG Breakdown Maintenance | O2 Project | 4.2 | 230 | 57.5
741 | 2025-05-10 | 2025 | 2024 | 2025-05-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Trip in Earth fault | 13:00 | 13:00 | 14:35 | 0:00 | 1.5833 | 1.5833 | Feeder-2 Trip in Earth fault after take a trial then charge it. | Close | 0.79167 | IG Breakdown Maintenance | O2 Project | 4.9 | 384 | 6688
742 | 2025-05-10 | 2025 | 2024 | 2025-05-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Trip in Earth fault | 18:24 | 18:24 | 18:35 | 0:00 | 0.18333 | 0.18333 | Feeder-2 Trip in Earth fault after take a trial then charge it. | Close | 0.091667 | IG Breakdown Maintenance | O2 Project | 4.9 | 384 | 774.4
743 | 2025-05-10 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_04 | TQGXIIPL | GEDA | 3.846% | O2_04 Grid Loss | 0:00 | 0:00 | 0:54 | 0:00 | 0.9 | 0.9 | O2-04 & O2-07 Internal lines rectification work | Close | 0.034615 | IG Breakdown Maintenance | O2 Project | 4.9 | 384 | 345.6
744 | 2025-05-10 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_07 | TQGXIIPL | GEDA | 3.846% | O2_07 Grid Loss | 0:00 | 0:00 | 0:54 | 0:00 | 0.9 | 0.9 | O2-04 & O2-07 Internal lines rectification work | Close | 0.034615 | IG Breakdown Maintenance | O2 Project | 4.9 | 384 | 345.6
745 | 2025-05-10 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_17 | TQGXIIPL | GEDA | 3.846% | O2_17 Grid Loss | 14:36 | 14:36 | 16:38 | 0:00 | 2.0333 | 2.0333 | O2-17 & O2-22 Internal lines rectification work | Close | 0.078205 | IG Breakdown Maintenance | O2 Project | 4.9 | 384 | 780.8
746 | 2025-05-10 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_22 | TQGXIIPL | GEDA | 3.846% | O2_22 Grid Loss | 14:36 | 14:36 | 16:38 | 0:00 | 2.0333 | 2.0333 | O2-17 & O2-22 Internal lines rectification work | Close | 0.078205 | IG Breakdown Maintenance | O2 Project | 4.9 | 384 | 780.8
747 | 2025-05-10 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_19 | TQGXIIPL | GEDA | 3.846% | O2_19 Grid Loss | 0:00 | 0:00 | 24:00 | 0:00 | 23.9997 | 23.9997 | O2-19 Jumper open work WIP | Open | 0.92307 | IG Breakdown Maintenance | O2 Project | 4.9 | 384 | 9215.8933
747 | 2025-05-11 | 2025 | 2024 | 2025-05-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Trip in Earth fault | 16:21 | 16:21 | 17:25 | 0:00 | 1.0667 | 1.0667 | Feeder-2 Trip in Earth fault after take a trial then charge it. | Close | 0.53333 | IG Breakdown Maintenance | O2 Project | 4.7 | 340 | 3989.3333
747 | 2025-05-11 | 2025 | 2024 | 2025-05-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder#1 Tripped due to Snake fault at Location no O2_13 | 17:38 | 17:38 | 18:10 | 0:00 | 0.53333 | 0.53333 | Feeder#1 Tripped due to snack fault at Location no O2_13 | Close | 0.26667 | IG Breakdown Maintenance | O2 Project | 4.7 | 340 | 2720
748 | 2025-05-11 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_19 | TQGXIIPL | GEDA | 3.846% | O2-19 Grid loss | 17:26 | 17:26 | 19:20 | 0:00 | 1.9 | 1.9 | O2-19 Internal lines rectification work | Close | 0.073077 | IG Breakdown Maintenance | O2 Project | 4.7 | 340 | 646
749 | 2025-05-11 | 2025 | 2024 | 2025-05-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | O2-19 Isolator closing Work | 0:00 | 0:00 | 0:06 | 0:00 | 0.1 | 0.1 | O2-19 Isolator closing Work | Close | 0.05 | IG Breakdown Maintenance | O2 Project | 4.7 | 340 | 34
750 | 2025-05-12 | 2025 | 2024 | 2025-05-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Trip in Earth fault | 15:16 | 15:16 | 16:26 | 0:00 | 1.1667 | 1.1667 | Feeder-2 Trip in Earth fault after take a trial then charge it. | Close | 0.58333 | IG Breakdown Maintenance | O2 Project | 4.9 | 384 | 4928
751 | 2025-05-12 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_19 | TQGXIIPL | GEDA | 3.846% | O2_19 Grid loss | 16:27 | 16:27 | 20:42 | 0:00 | 4.25 | 4.25 | O2-19 Transformer Bushing Replacement work | Close | 0.16346 | IG Breakdown Maintenance | O2 Project | 4.9 | 384 | 1632
752 | 2025-05-13 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_07 | TQGXIIPL | GEDA | 3.846% | O2_07 Grid Loss | 22:29 | 22:29 | 24:00 | 0:00 | 1.5164 | 1.5164 | VCB OFF after BOP Team attend and check VCB wip. | Close | 0.058323 | IG Breakdown Maintenance | O2 Project | 5.2 | 469.4 | 711.7929
753 | 2025-05-14 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_07 | TQGXIIPL | GEDA | 3.846% | O2_07 Grid Loss | 0:00 | 0:00 | 0:06 | 0:00 | 0.1 | 0.1 | VCB OFF after BOP Team attend and check VCB then charge and start WTG | Close | 0.0038462 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 43.77
754 | 2025-05-14 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_07 | TQGXIIPL | GEDA | 3.846% | O2_07 Grid Loss | 8:17 | 8:17 | 9:12 | 0:00 | 0.91667 | 0.91667 | VCB tripped by unknown person after BOP Team attend and check VCB then charge and start WTG | Close | 0.035256 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 401.225
755 | 2025-05-14 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_07 | TQGXIIPL | GEDA | 3.846% | O2_07 Grid Loss | 20:52 | 20:52 | 21:32 | 0:00 | 0.66667 | 0.66667 | VCB tripped by unknown person after BOP Team attend and check VCB then charge and start WTG | Close | 0.025641 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 291.8
756 | 2025-05-15 | 2025 | 2024 | 2025-05-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Trip in Earth fault | 17:49 | 17:49 | 18:24 | 0:00 | 0.58333 | 0.58333 | Feeder#2 Trip in earth Falut/over current (O2_17,O2_22 section isolator open) | Close | 0.29167 | IG Breakdown Maintenance | O2 Project | 4.5 | 296 | 1899.3333
757 | 2025-05-15 | 2025 | 2024 | 2025-05-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 shutdown | 21:26 | 21:26 | 21:33 | 0:00 | 0.11667 | 0.11667 | Feeder-2 shutdown for O2_17 &O2_22 section Isolator closing work | Close | 0.058333 | IG Breakdown Maintenance | O2 Project | 4.5 | 296 | 379.8667
758 | 2025-05-15 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_17 | TQGXIIPL | GEDA | 3.846% | O2_17 Grid Loss | 18:24 | 18:24 | 21:26 | 0:00 | 3.0333 | 3.0333 | O2_17,O2_22 section isolator open BY BOP team | Close | 0.11667 | IG Breakdown Maintenance | O2 Project | 4.5 | 296 | 897.8667
759 | 2025-05-15 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_22 | TQGXIIPL | GEDA | 3.846% | O2_22 Grid Loss | 18:24 | 18:24 | 21:26 | 0:00 | 3.0333 | 3.0333 | O2_17,O2_22 section isolator open BY BOP team | Close | 0.11667 | IG Breakdown Maintenance | O2 Project | 4.5 | 296 | 897.8667
760 | 2025-05-16 | 2025 | 2024 | 2025-05-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Trip in earth Falut/over current | 16:40 | 16:40 | 18:19 | 0:00 | 1.65 | 1.65 | Feeder#2 Trip in earth Falut/over current after take a trial then charge it. | Close | 0.825 | IG Breakdown Maintenance | O2 Project | 5.5 | 564.5 | 10245.675
761 | 2025-05-16 | 2025 | 2024 | 2025-05-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 shutdown | 19:04 | 19:04 | 19:11 | 0:00 | 0.11667 | 0.11667 | Feeder-2 shutdown for O2_07 &O2_04,O2-19 section Isolator closing work | Close | 0.058333 | IG Breakdown Maintenance | O2 Project | 5.5 | 564.5 | 724.4417
762 | 2025-05-16 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_17 | TQGXIIPL | GEDA | 3.846% | O2-17 WTG Shutdown | 15:54 | 15:54 | 16:40 | 0:00 | 0.76667 | 0.76667 | O2_17,O2_22 section isolator open BY BOP team | Close | 0.029487 | IG Breakdown Maintenance | O2 Project | 5.5 | 564.5 | 432.7833
763 | 2025-05-16 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_22 | TQGXIIPL | GEDA | 3.846% | O2-22 WTG Shutdown | 15:54 | 15:54 | 16:40 | 0:00 | 0.76667 | 0.76667 | O2_17,O2_22 section isolator open BY BOP team | Close | 0.029487 | IG Breakdown Maintenance | O2 Project | 5.5 | 564.5 | 432.7833
764 | 2025-05-16 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_07 | TQGXIIPL | GEDA | 3.846% | O2-07 Grid loss | 18:19 | 18:19 | 19:04 | 0:00 | 0.75 | 0.75 | O2_07,O2_04,O2_19 section isolator open BY BOP team | Close | 0.028846 | IG Breakdown Maintenance | O2 Project | 5.5 | 564.5 | 423.375
765 | 2025-05-16 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_04 | TQGXIIPL | GEDA | 3.846% | O2-04 Grid loss | 18:19 | 18:19 | 19:04 | 0:00 | 0.75 | 0.75 | O2_07,O2_04,O2_19 section isolator open BY BOP team | Close | 0.028846 | IG Breakdown Maintenance | O2 Project | 5.5 | 564.5 | 423.375
766 | 2025-05-16 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_19 | TQGXIIPL | GEDA | 3.846% | O2-19 Grid loss | 18:19 | 18:19 | 19:04 | 0:00 | 0.75 | 0.75 | O2_07,O2_04,O2_19 section isolator open BY BOP team | Close | 0.028846 | IG Breakdown Maintenance | O2 Project | 5.5 | 564.5 | 423.375
766 | 2025-05-17 | 2025 | 2024 | 2025-05-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Trip in earth Falut/over current | 6:44 | 6:44 | 6:57 | 0:00 | 0.21667 | 0.21667 | Feeder#2 Trip in earth Falut/over current after take a trial then charge it. | Close | 0.10833 | IG Breakdown Maintenance | O2 Project | 5.2 | 469.4 | 1118.7367
766 | 2025-05-18 | 2025 | 2024 | 2025-05-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown | 11:12 | 11:12 | 12:26 | 0:00 | 1.2333 | 1.2333 | Feeder#1 Shutdown taking by pin insulator fall down repairing work | Close | 0.61667 | IG Breakdown Maintenance | O2 Project | 5.1 | 437.7 | 8097.45
766 | 2025-05-20 | 2025 | 2024 | 2025-05-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Trip in Earth fault | 8:37 | 8:37 | 8:54 | 0:00 | 0.28333 | 0.28333 | Feeder#1Trip in earth Falut/over current /master reley trip after take a trial then charge it. | Close | 0.14167 | IG Breakdown Maintenance | O2 Project | 5.3 | 501.1 | 2129.675
766 | 2025-05-20 | 2025 | 2024 | 2025-05-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Trip in Earth fault | 17:22 | 17:22 | 17:40 | 0:00 | 0.3 | 0.3 | Feeder#2 Trip in earth Falut/over current after take a trial then charge it. | Close | 0.15 | IG Breakdown Maintenance | O2 Project | 5.3 | 501.1 | 1653.63
767 | 2025-05-21 | 2025 | 2024 | 2025-05-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder#1Trip in earth Falut/over current /master reley trip | 10:14 | 10:14 | 13:30 | 0:00 | 3.2667 | 3.2667 | Feeder#1Trip in earth Falut/over current /master reley trip ,Hi teck Project ROW due to payment issue. | Close | 1.6333 | IG Breakdown Maintenance | O2 Project | 4.5 | 296 | 14504
768 | 2025-05-21 | 2025 | 2024 | 2025-05-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown | 13:30 | 13:30 | 19:16 | 0:00 | 5.7667 | 5.7667 | Feeder#1 Shutdown taken by project team 33kv line pending work. | Close | 2.8833 | IG Breakdown Maintenance | O2 Project | 4.5 | 296 | 25604
769 | 2025-05-21 | 2025 | 2024 | 2025-05-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 shutdown | 14:35 | 14:35 | 19:10 | 0:00 | 4.5833 | 4.5833 | Feeder#2 Shutdown taken by project team 33kv line pending work. | Close | 2.2917 | IG Breakdown Maintenance | O2 Project | 4.5 | 296 | 14923.3333
770 | 2025-05-22 | 2025 | 2024 | 2025-05-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Trip in Earth fault | 0:19 | 0:19 | 1:11 | 0:00 | 0.86667 | 0.86667 | Feeder#2 Trip in earth Falut after take a trial then charge it. | Close | 0.43333 | IG Breakdown Maintenance | O2 Project | 3.8 | 154.8 | 1475.76
771 | 2025-05-22 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_04 | TQGXIIPL | GEDA | 3.846% | O2-04 Grid loss | 1:11 | 1:11 | 3:50 | 0:00 | 2.65 | 2.65 | O2-04, O2-07 and O2-19 section Isolator open by BOP team found fault and correct it then close Isotator then start WTG. | Close | 0.10192 | IG Breakdown Maintenance | O2 Project | 3.8 | 154.8 | 410.22
772 | 2025-05-22 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_07 | TQGXIIPL | GEDA | 3.846% | O2-07 Grid loss | 1:11 | 1:11 | 3:50 | 0:00 | 2.65 | 2.65 | O2-04, O2-07 and O2-19 section Isolator open by BOP team found fault and correct it then close Isotator then start WTG. | Close | 0.10192 | IG Breakdown Maintenance | O2 Project | 3.8 | 154.8 | 410.22
773 | 2025-05-22 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_19 | TQGXIIPL | GEDA | 3.846% | O2-19 Grid loss | 1:11 | 1:11 | 3:50 | 0:00 | 2.65 | 2.65 | O2-04, O2-07 and O2-19 section Isolator open by BOP team found fault and correct it then close Isotator then start WTG. | Close | 0.10192 | IG Breakdown Maintenance | O2 Project | 3.8 | 154.8 | 410.22
774 | 2025-05-22 | 2025 | 2024 | 2025-05-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown | 9:11 | 9:11 | 11:23 | 0:00 | 2.2 | 2.2 | Feeder#1 Shutdown taken by project team for section Isolator installation work | Close | 1.1 | IG Breakdown Maintenance | O2 Project | 3.8 | 154.8 | 5108.4
775 | 2025-05-22 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_01 | TQGXIIPL | GEDA | 3.846% | O2-01 WTG Shutdown (Grid loss) | 11:23 | 11:23 | 17:55 | 0:00 | 6.5333 | 6.5333 | jumper open by project team at O2 14 for section Isolator installation work. | Close | 0.25128 | IG Breakdown Maintenance | O2 Project | 3.8 | 154.8 | 1011.36
776 | 2025-05-22 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_02 | TQGXIIPL | GEDA | 3.846% | O2-02 WTG Shutdown (Grid loss) | 11:23 | 11:23 | 17:55 | 0:00 | 6.5333 | 6.5333 | jumper open by project team at O2 14 for section Isolator installation work. | Close | 0.25128 | IG Breakdown Maintenance | O2 Project | 3.8 | 154.8 | 1011.36
777 | 2025-05-22 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_03 | TQGXIIPL | GEDA | 3.846% | O2-03 WTG Shutdown (Grid loss) | 11:23 | 11:23 | 17:55 | 0:00 | 6.5333 | 6.5333 | jumper open by project team at O2 14 for section Isolator installation work. | Close | 0.25128 | IG Breakdown Maintenance | O2 Project | 3.8 | 154.8 | 1011.36
778 | 2025-05-22 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_05 | TQGXIIPL | GEDA | 3.846% | O2-05 WTG Shutdown (Grid loss) | 11:23 | 11:23 | 17:55 | 0:00 | 6.5333 | 6.5333 | jumper open by project team at O2 14 for section Isolator installation work. | Close | 0.25128 | IG Breakdown Maintenance | O2 Project | 3.8 | 154.8 | 1011.36
779 | 2025-05-22 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_08 | TQGXIIPL | GEDA | 3.846% | O2-08 WTG Shutdown (Grid loss) | 11:23 | 11:23 | 17:55 | 0:00 | 6.5333 | 6.5333 | jumper open by project team at O2 14 for section Isolator installation work. | Close | 0.25128 | IG Breakdown Maintenance | O2 Project | 3.8 | 154.8 | 1011.36
780 | 2025-05-22 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_09 | TQGXIIPL | GEDA | 3.846% | O2-09 WTG Shutdown (Grid loss) | 11:23 | 11:23 | 17:55 | 0:00 | 6.5333 | 6.5333 | jumper open by project team at O2 14 for section Isolator installation work. | Close | 0.25128 | IG Breakdown Maintenance | O2 Project | 3.8 | 154.8 | 1011.36
781 | 2025-05-22 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_11 | TQGXIIPL | GEDA | 3.846% | O2-11 WTG Shutdown (Grid loss) | 11:23 | 11:23 | 17:55 | 0:00 | 6.5333 | 6.5333 | jumper open by project team at O2 14 for section Isolator installation work. | Close | 0.25128 | IG Breakdown Maintenance | O2 Project | 3.8 | 154.8 | 1011.36
782 | 2025-05-22 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_12 | TQGXIIPL | GEDA | 3.846% | O2-12 WTG Shutdown (Grid loss) | 11:23 | 11:23 | 17:55 | 0:00 | 6.5333 | 6.5333 | jumper open by project team at O2 14 for section Isolator installation work. | Close | 0.25128 | IG Breakdown Maintenance | O2 Project | 3.8 | 154.8 | 1011.36
783 | 2025-05-22 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_14 | TQGXIIPL | GEDA | 3.846% | O2-14 WTG Shutdown (Grid loss) | 11:23 | 11:23 | 17:55 | 0:00 | 6.5333 | 6.5333 | jumper open by project team at O2 14 for section Isolator installation work. | Close | 0.25128 | IG Breakdown Maintenance | O2 Project | 3.8 | 154.8 | 1011.36
784 | 2025-05-22 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_23 | TQGXIIPL | GEDA | 3.846% | O2-23 WTG Shutdown (Grid loss) | 11:23 | 11:23 | 17:55 | 0:00 | 6.5333 | 6.5333 | jumper open by project team at O2 14 for section Isolator installation work. | Close | 0.25128 | IG Breakdown Maintenance | O2 Project | 3.8 | 154.8 | 1011.36
785 | 2025-05-22 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_25 | TQGXIIPL | GEDA | 3.846% | O2-25 WTG Shutdown (Grid loss) | 11:23 | 11:23 | 17:55 | 0:00 | 6.5333 | 6.5333 | jumper open by project team at O2 14 for section Isolator installation work. | Close | 0.25128 | IG Breakdown Maintenance | O2 Project | 3.8 | 154.8 | 1011.36
786 | 2025-05-22 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_26 | TQGXIIPL | GEDA | 3.846% | O2-26 WTG Shutdown (Grid loss) | 11:23 | 11:23 | 17:55 | 0:00 | 6.5333 | 6.5333 | jumper open by project team at O2 14 for section Isolator installation work. | Close | 0.25128 | IG Breakdown Maintenance | O2 Project | 3.8 | 154.8 | 1011.36
787 | 2025-05-22 | 2025 | 2024 | 2025-05-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown | 17:55 | 17:55 | 19:01 | 0:00 | 1.1 | 1.1 | Feeder#1 Shutdown taken by project team for section Isolator installation work and jumper closing work at O2-14. | Close | 0.55 | IG Breakdown Maintenance | O2 Project | 3.8 | 154.8 | 2554.2
788 | 2025-05-23 | 2025 | 2024 | 2025-05-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Trip in Earth fault | 0.85833 | 0.85833 | 0.87222 | 0:00 | 0.33333 | 0.33333 | Feeder-2 tripped in Earth fault after take a trial then charge it. | Close | 0.16667 | IG Breakdown Maintenance | O2 Project | 4.9 | 384 | 1408
789 | 2025-05-24 | 2025 | 2024 | 2025-05-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown | 9:22 | 9:22 | 10:35 | 0:00 | 1.2167 | 1.2167 | Feeder#1 Shutdown taken by project team for section Isolator installation work | Close | 0.60833 | IG Breakdown Maintenance | O2 Project | 7.6 | 1490 | 27192.5
790 | 2025-05-24 | 2025 | 2024 | 2025-05-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown | 17:07 | 17:07 | 18:28 | 0:00 | 1.35 | 1.35 | Feeder#1 Shutdown taken by project team for section Isolator installation work | Close | 0.675 | IG Breakdown Maintenance | O2 Project | 7.6 | 1490 | 30172.5
791 | 2025-05-24 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_01 | TQGXIIPL | GEDA | 3.846% | O2-01 WTG Shutdown (Grid loss) | 10:35 | 10:35 | 17:07 | 0:00 | 6.5333 | 6.5333 | jumper open by project team for section Isolator installation work. | Close | 0.25128 | IG Breakdown Maintenance | O2 Project | 7.6 | 1490 | 9734.6667
792 | 2025-05-24 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_02 | TQGXIIPL | GEDA | 3.846% | O2-02 WTG Shutdown (Grid loss) | 10:35 | 10:35 | 17:07 | 0:00 | 6.5333 | 6.5333 | jumper open by project team for section Isolator installation work. | Close | 0.25128 | IG Breakdown Maintenance | O2 Project | 7.6 | 1490 | 9734.6667
793 | 2025-05-24 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_05 | TQGXIIPL | GEDA | 3.846% | O2-05 WTG Shutdown (Grid loss) | 10:35 | 10:35 | 17:07 | 0:00 | 6.5333 | 6.5333 | jumper open by project team for section Isolator installation work. After grid rusume start WTG | Close | 0.25128 | IG Breakdown Maintenance | O2 Project | 7.6 | 1490 | 9734.6667
794 | 2025-05-24 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_08 | TQGXIIPL | GEDA | 3.846% | O2-08 WTG Shutdown (Grid loss) | 10:35 | 10:35 | 17:07 | 0:00 | 6.5333 | 6.5333 | jumper open by project team for section Isolator installation work. After grid rusume start WTG | Close | 0.25128 | IG Breakdown Maintenance | O2 Project | 7.6 | 1490 | 9734.6667
795 | 2025-05-24 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_09 | TQGXIIPL | GEDA | 3.846% | O2-09 WTG Shutdown (Grid loss) | 10:35 | 10:35 | 17:07 | 0:00 | 6.5333 | 6.5333 | jumper open by project team for section Isolator installation work. | Close | 0.25128 | IG Breakdown Maintenance | O2 Project | 7.6 | 1490 | 9734.6667
796 | 2025-05-24 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_25 | TQGXIIPL | GEDA | 3.846% | O2-25 WTG Shutdown (Grid loss) | 10:35 | 10:35 | 17:07 | 0:00 | 6.5333 | 6.5333 | jumper open by project team for section Isolator installation work. | Close | 0.25128 | IG Breakdown Maintenance | O2 Project | 7.6 | 1490 | 9734.6667
797 | 2025-05-24 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_26 | TQGXIIPL | GEDA | 3.846% | O2-26 WTG Shutdown (Grid loss) | 10:35 | 10:35 | 17:07 | 0:00 | 6.5333 | 6.5333 | jumper open by project team for section Isolator installation work. | Close | 0.25128 | IG Breakdown Maintenance | O2 Project | 7.6 | 1490 | 9734.6667
798 | 2025-05-25 | 2025 | 2024 | 2025-05-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feefer-1 shutdown | 9:30 | 9:30 | 10:20 | 0:00 | 0.83333 | 0.83333 | Feeder#1 Shutdown taken by project team for section Isolator installation work | Close | 0.41667 | IG Breakdown Maintenance | O2 Project | 7.7 | 1543.5 | 19293.75
799 | 2025-05-25 | 2025 | 2024 | 2025-05-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder#1 Trip in Over Current | 15:42 | 15:42 | 16:56 | 0:00 | 1.2333 | 1.2333 | Feeder#1 Trip in Over Current after take a trial then charge it. | Close | 0.61667 | IG Breakdown Maintenance | O2 Project | 7.7 | 1543.5 | 28554.75
800 | 2025-05-25 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_05 | TQGXIIPL | GEDA | 3.846% | O2-05 WTG Shutdown (Grid loss) | 10:20 | 10:20 | 15:42 | 0:00 | 5.3667 | 5.3667 | jumper open by project team for section Isolator installation work. | Close | 0.20641 | IG Breakdown Maintenance | O2 Project | 7.7 | 1543.5 | 8283.45
801 | 2025-05-25 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_25 | TQGXIIPL | GEDA | 3.846% | O2-25 WTG Shutdown (Grid loss) | 10:20 | 10:20 | 15:42 | 0:00 | 5.3667 | 5.3667 | jumper open by project team for section Isolator installation work. | Close | 0.20641 | IG Breakdown Maintenance | O2 Project | 7.7 | 1543.5 | 8283.45
802 | 2025-05-25 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_02 | TQGXIIPL | GEDA | 3.846% | O2-02 WTG Shutdown (Grid loss) | 10:20 | 10:20 | 15:42 | 0:00 | 5.3667 | 5.3667 | jumper open by project team for section Isolator installation work. | Close | 0.20641 | IG Breakdown Maintenance | O2 Project | 7.7 | 1543.5 | 8283.45
803 | 2025-05-26 | 2025 | 2024 | 2025-05-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder#1 Trip in Over Current | 0:37 | 0:37 | 0:51 | 0:00 | 0.23333 | 0.23333 | Feeder#1 Trip in Over Current after take a trial then charge it. | Close | 0.11667 | IG Breakdown Maintenance | O2 Project | 7.1 | 1222.5 | 4278.75
804 | 2025-05-26 | 2025 | 2024 | 2025-05-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Trip in Earth fault | 0:02 | 0:02 | 0:52 | 0:00 | 0.83333 | 0.83333 | Feeder-2 tripped in Earth fault after take a trial then charge it. | Close | 0.41667 | IG Breakdown Maintenance | O2 Project | 7.1 | 1222.5 | 11206.25
805 | 2025-05-27 | 2025 | 2024 | 2025-05-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder#1 Trip in Earth fault | 10:36 | 10:36 | 13:33 | 0:00 | 2.95 | 2.95 | Feeder#1 Trip in Over Current after take a trial then charge it. | Close | 1.475 | IG Breakdown Maintenance | O2 Project | 9.5 | 2435.5 | 107770.875
806 | 2025-05-28 | 2025 | 2024 | 2025-05-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feefer-1 shutdown | 9:12 | 9:12 | 9:41 | 0:00 | 0.48333 | 0.48333 | Feeder#1 Shutdown taken by project team for section Isolator installation work | Close | 0.24167 | IG Breakdown Maintenance | O2 Project | 8.4 | 1922.8 | 13940.3
807 | 2025-05-28 | 2025 | 2024 | 2025-05-01 | Year_1 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feefer-1 shutdown | 11:35 | 11:35 | 12:39 | 0:00 | 1.0667 | 1.0667 | Feeder#1 Shutdown taken by project team for section Isolator installation work | Close | 0.53333 | IG Breakdown Maintenance | O2 Project | 8.4 | 1922.8 | 30764.8
808 | 2025-05-28 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_01 | TQGXIIPL | GEDA | 3.846% | O2-01 WTG Shutdown (Grid loss) | 9:41 | 9:41 | 11:35 | 0:00 | 1.9 | 1.9 | jumper open by project team for section Isolator installation work. | Close | 0.073077 | IG Breakdown Maintenance | O2 Project | 8.4 | 1922.8 | 3653.32
809 | 2025-05-28 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_09 | TQGXIIPL | GEDA | 3.846% | O2-09 WTG Shutdown (Grid loss) | 9:41 | 9:41 | 11:35 | 0:00 | 1.9 | 1.9 | jumper open by project team for section Isolator installation work. | Close | 0.073077 | IG Breakdown Maintenance | O2 Project | 8.4 | 1922.8 | 3653.32
810 | 2025-05-28 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_25 | TQGXIIPL | GEDA | 3.846% | O2-25 WTG Shutdown (Grid loss) | 9:41 | 9:41 | 11:35 | 0:00 | 1.9 | 1.9 | jumper open by project team for section Isolator installation work. | Close | 0.073077 | IG Breakdown Maintenance | O2 Project | 8.4 | 1922.8 | 3653.32
811 | 2025-05-28 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_26 | TQGXIIPL | GEDA | 3.846% | O2-26 WTG Shutdown (Grid loss) | 9:41 | 9:41 | 11:35 | 0:00 | 1.9 | 1.9 | jumper open by project team for section Isolator installation work. | Close | 0.073077 | IG Breakdown Maintenance | O2 Project | 8.4 | 1922.8 | 3653.32
812 | 2025-05-28 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_08 | TQGXIIPL | GEDA | 3.846% | O2-08 WTG Shutdown (Grid loss) | 9:41 | 9:41 | 11:35 | 0:00 | 1.9 | 1.9 | jumper open by project team for section Isolator installation work. | Close | 0.073077 | IG Breakdown Maintenance | O2 Project | 8.4 | 1922.8 | 3653.32
813 | 2025-05-28 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_05 | TQGXIIPL | GEDA | 3.846% | O2-05 WTG Shutdown (Grid loss) | 9:41 | 9:41 | 11:35 | 0:00 | 1.9 | 1.9 | jumper open by project team for section Isolator installation work. | Close | 0.073077 | IG Breakdown Maintenance | O2 Project | 8.4 | 1922.8 | 3653.32
814 | 2025-05-28 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_02 | TQGXIIPL | GEDA | 3.846% | O2-02 WTG Shutdown (Grid loss) | 9:41 | 9:41 | 11:35 | 0:00 | 1.9 | 1.9 | jumper open by project team for section Isolator installation work. | Close | 0.073077 | IG Breakdown Maintenance | O2 Project | 8.4 | 1922.8 | 3653.32
815 | 2025-05-28 | 2025 | 2024 | 2025-05-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feefer-2 shutdown | 12:52 | 12:52 | 17:08 | 0:00 | 4.2667 | 4.2667 | Feeder#2 Shutdown taken by project team for section Isolator installation work | Close | 2.1333 | IG Breakdown Maintenance | O2 Project | 8.4 | 1922.8 | 90243.4133
816 | 2025-05-28 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_08 | TQGXIIPL | GEDA | 3.846% | O2-08 WTG Shutdown (Grid loss) | 12:39 | 12:39 | 17:08 | 0:00 | 4.4833 | 4.4833 | jumper open by project team for section Isolator installation work. | Close | 0.17244 | IG Breakdown Maintenance | O2 Project | 8.4 | 1922.8 | 8620.5533
817 | 2025-05-28 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_26 | TQGXIIPL | GEDA | 3.846% | O2-26 WTG Shutdown (Grid loss) | 12:39 | 12:39 | 17:08 | 0:00 | 4.4833 | 4.4833 | jumper open by project team for section Isolator installation work. | Close | 0.17244 | IG Breakdown Maintenance | O2 Project | 8.4 | 1922.8 | 8620.5533
818 | 2025-05-31 | 2025 | 2024 | 2025-05-01 | Year_1 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Trip in Earth fault | 15:15 | 15:15 | 16:01 | 0:00 | 0.76667 | 0.76667 | Feeder-2 Trip in Earth fault after take a trial then charge it. | Close | 0.38333 | IG Breakdown Maintenance | O2 Project | 9.6 | 2472.4 | 24641.5867
819 | 2025-05-31 | 2025 | 2024 | 2025-05-01 | Year_1 | O2_07 | TQGXIIPL | GEDA | 3.846% | O2-07 Grid loss | 16:01 | 16:01 | 17:09 | 0:00 | 1.1333 | 1.1333 | After grid resume found VCB tripped so VCB Charge after reset and start wtg | Close | 0.04359 | IG Breakdown Maintenance | O2 Project | 9.6 | 2472.4 | 2802.0533
820 | 2025-06-03 | 2025 | 2024 | 2025-06-01 | Year_1 | O2_03 | TQGXIIPL | GEDA | 3.846% | O2-03 WTG Shutdown (Grid loss) | 18:43 | 18:43 | 19:01 | 0:00 | 0.3 | 0.3 | USS work for BOP. | Close | 0.011538 | IG Breakdown Maintenance | O2 Project | 8.2 | 1813.4 | 544.02
Formulas:
Month = [Date]-DAY([Date])+1

## Grid_BD
Sr. No. | Date | Finacial Year | Calendor Year | Month | Operating Year | Affected System | SPV | Concumaer | Plant Equivalent Weightage | Fault Code | Breakdown Description | Fault Start TimeStamp | Work Start TimeStamp | Fault Clearance time | Response Time | Resolution Time | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Fault Category | Average wind speed | Loss of KWH | KWH lost during BD/SD
1 | 2024-05-11 | 2025 | 2024 | 2024-05-01 | Year_1 | Line1 | TQGXIIPL | GEDA | 100% | Manual shutdown | 66KV shutdown taken by getco | 10:43 | 10:43 | 12:12 | 0 | 1.4833 | 1.4833 | Shutdown taken by getco for meter correction work | Close | 1.4833 |  | 5 | 437.7 | 3246.275
2 | 2024-07-13 | 2025 | 2024 | 2024-07-01 | Year_1 | Line1 | TQGXIIPL | GEDA | 100% | Bay-66Kv line trip | Bay-66Kv trip at 220Kv GETCO End | 17:22 | 17:22 | 19:03 | 0 | 1.6833 | 1.6833 | Bay-66kv line trip from GETCO End 220Kv charkha. (Two nos. Transformer with bus coupler trip in GETCO 220Kv Charkha GSS) | Close | 1.6833 |  | 8.14 | 1758.7 | 35525.74
3 | 2024-07-28 | 2025 | 2024 | 2024-07-01 | Year_1 | Line1 | TQGXIIPL | GEDA | 100% | Bay-66Kv line trip | Bay-66Kv trip at 220Kv GETCO End | 16:12 | 16:12 | 18:05 | 0 | 1.8833 | 1.8833 | Bay-66kv line trip from GETCO End 220Kv charkha After petrolling we coulnt find anything ,so we have charged the line | Close | 1.8833 |  | 6.5 | 946 | 28506.1333
5 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | Year_1 | Line1 | TQGXIIPL | GEDA | 100% | Bay-66Kv line trip | Bay-66Kv tripped due to OPGW touch with R phase | 10:05 | 10:05 | 11:15 | 0 | 1.1667 | 1.1667 | 66KV line found OPGW Cable to R phase clearance low at Tower no 26 to 27 due to High wind | Close | 1.1667 |  | 12.8 | 2835 | 59535
6 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | Year_1 | Line1 | TQGXIIPL | GEDA | 100% | Bay-66Kv line trip | Bay-66Kv tripped due to OPGW touch with R phase | 12:29 | 12:29 | 13:45 | 0 | 1.2667 | 1.2667 | 66KV line found OPGW Cable to R phase clearance low at Tower no 26 to 27 due to High wind | Close | 1.2667 |  | 12.8 | 2835 | 64638
7 | 2024-08-26 | 2025 | 2024 | 2024-08-01 | Year_1 | Line1 | TQGXIIPL | GEDA | 100% | Bay-66Kv line trip | Bay-66Kv tripped due to OPGW touch with R phase | 15:43 | 15:43 | 21:10 | 0 | 5.45 | 5.45 | 66KV line found OPGW Cable to R phase clearance low at Tower no 26 to 27 due to High wind | Close | 5.45 |  | 12.8 | 2835 | 278113.5
8 | 2024-09-02 | 2025 | 2024 | 2024-09-01 | Year_1 | Line1 | TQGXIIPL | GEDA | 100% | Manual shutdown | 66KV line shutdown taken by getco | 10:50 | 10:50 | 17:06 | 0 | 6.2667 | 6.2667 | 66Kv line shutdown for OPGW conductor sag rectification work | Close | 6.2667 |  | 5 | 444 | 52865.6
9 | 2024-09-06 | 2025 | 2024 | 2024-09-01 | Year_1 | Line1 | TQGXIIPL | GEDA | 100% | Manual shutdown | 66KV line shutdown taken by getco | 9:58 | 9:58 | 11:35 | 0 | 1.6167 | 1.6167 | 66KV line shutdown for CT oil leakage arresting work at 220KV Genco end | Close | 1.6167 |  | 6.8 | 1329.5 | 40837.8083
10 | 2024-09-17 | 2025 | 2024 | 2024-09-01 | Year_1 | Line1 | TQGXIIPL | GEDA | 100% | Bay-66Kv line trip | Bay-66KV trip at 220Kv GETCO End | 0:32 | 0:32 | 4:04 | 0 | 3.5333 | 3.5333 | 66 KV Line Trip Over Voltage and Under Voltage Protection Operator | Close | 3.5333 |  | 4.5 | 326 | 24189.2
11 | 2024-09-29 | 2025 | 2024 | 2024-09-01 | Year_1 | Line1 | TQGXIIPL | GEDA | 100% | Bay-66Kv line trip | 66KV Line trip earth fault/ over current | 16:37 | 16:37 | 17:45 | 0 | 1.1333 | 1.1333 | 66 kv line trip Getco end so after grid voltage normal after charge | Close | 1.1333 |  | 3.7 | 139.2 | 3312.96
12 | 2024-10-15 | 2025 | 2024 | 2024-10-01 | Year_1 | Line1 | TQGXIIPL | GEDA | 100% | Manual shutdown | 66 KV Line & PSS shutdown | 8:26 | 8:26 | 19:46 | 0 | 11.3333 | 11.3333 | 66 KV #1 Line & PSS HYPM WORK | Close | 11.3333 |  | 3.2 | 61.2 | 15952.8
13 | 2025-02-28 | 2025 | 2025 | 2025-02-01 | Year_1 | Line1 | TQGXIIPL | GEDA | 100% | Manual shutdown | 66Kv Line shutdown taking By GETCO team from Getco end 66KV line Strengthening work. | 8:20 | 8:20 | 18:34 | 0 | 10.2333 | 10.2333 | 66Kv Line shutdown taking By GETCO team from Getco end 66KV line Strengthening work. | Close | 10.2333 |  | 7.1 | 1222.5 | 325266.5
0
Formulas:
Month = [Date]-DAY([Date])+1

## WTG-PM
Sr no | Site | Location | Turbine ID | DOC | Date of Operation | 2024 |  |  |  |  | 2025
[6 empty] | WTG 1st Month PM |  |  |  |  | WTG YPM
[6 empty] | Plan Date | Actual Date | Diff. Days | Adherence | Remark | Plan Date | 1st Day | 2nd Day | Diff. Days | Adherence | Remarks
1 | Babra | O2-11 | 5333 | 2024-03-31 | 2024-05-20 | 2024-07-08 | 2024-08-02 | 25 | 100 |  | 2025-02-27 | 2025-03-07 | 2025-03-08 | 8
2 | Babra | O2-12 | 5334 | 2024-03-31 | 2024-05-06 | 2024-06-24 | 2024-07-31 | 37 | 92.2222 | Deleyed due to other turbines restoration work | 2025-03-03 | 2025-03-11 | 2025-03-12 | 8
3 | Babra | O2-13 | 5335 | 2024-03-31 | 2024-05-02 | 2024-06-20 | 2024-07-06 | 16 | 100 |  | 2025-03-05 | 2025-03-17 | 2025-03-19 | 12
4 | Babra | O2-14 | 5336 | 2024-03-31 | 2024-05-05 | 2024-06-23 | 2024-07-16 | 23 | 100 |  | 2025-03-07 | 2025-03-20 | 2025-03-21 | 13
5 | Babra | O2-10 | 5332 | 2024-04-02 | 2024-05-05 | 2024-06-23 | 2024-07-11 | 18 | 100 |  | 2025-03-11 | 2025-04-01 | 2025-04-02 | 21
6 | Babra | O2-03 | 5341 | 2024-04-02 | 2024-05-06 | 2024-06-24 | 2024-07-19 | 25 | 100 |  | 2025-03-17 | 2025-04-05 | 2025-04-06 | 19
7 | Babra | O2-15 | 5342 | 2024-04-19 | 2024-05-02 | 2024-06-20 | 2024-07-09 | 19 | 100 |  | 2025-03-19 | 2025-04-13 | 2025-04-14 | 25
8 | Babra | O2-16 | 5337 | 2024-04-19 | 2024-05-15 | 2024-07-03 | 2024-08-19 | 47 | 81.1111 | Delayed due to turbine lift not working and lift operation delay from project team | 2025-03-21 | 2025-04-15 | 2025-04-21 | 25
9 | Babra | O2-20 | 5343 | 2024-04-19 | 2024-05-02 | 2024-06-20 | 2024-07-03 | 13 | 100 |  | 2025-03-25 | 2025-04-25 | 2025-04-26 | 31
10 | Babra | O2-09 | 5331 | 2024-05-25 | 2024-05-21 | 2024-07-09 | 2024-08-16 | 38 | 91.1111 | Delayed due to turbine access road issue | 2025-03-27 | 2025-04-07 | 2025-04-08 | 11
11 | Babra | O2-05 | 5329 | 2024-04-19 | 2024-05-21 | 2024-07-09 | 2024-08-12 | 34 | 95.5556 | Delayed due to turbine access road issue | 2025-04-01 | 2025-03-22 | 2025-03-25 | -10
12 | Babra | O2-02 | 5340 | 2024-05-25 | 2024-05-24 | 2024-07-12 | 2024-10-27 | 107 | 14.4444 | Deleyed due to turbine access road access issue | 2025-04-03 | 2025-04-17 | 2025-04-18 | 14
13 | Babra | O2-01 | 5346 | 2024-06-26 | 2024-06-14 | 2024-08-02 | 2024-08-13 | 11 | 100 |  | 2025-04-07 | 2025-04-03 | 2025-04-04 | -4
14 | Babra | O2-06 | 5347 | 2024-06-26 | 2024-06-24 | 2024-08-12 | 2024-09-04 | 23 | 100 |  | 2025-04-09 | 2025-04-28 | 2025-04-29 | 19
15 | Babra | O2-18 | 5349 | 2024-06-26 | 2024-06-25 | 2024-08-13 | 2024-08-21 | 8 | 100 |  | 2025-04-11 | 2025-04-19 | 2025-04-20 | 8
16 | Babra | O2-21 | 5344 | 2024-06-26 | 2024-06-22 | 2024-08-10 | 2024-08-23 | 13 | 100 |  | 2025-04-15 | 2025-05-02 |  | 17 |  | PM Completed -01 day
17 | Babra | O2-24 | 5352 | 2024-07-25 | 2024-07-25 | 2024-09-12 | 2024-09-09 | -3 | 100 |  | 2025-04-17 | 2025-05-03 |  | 16 |  | PM Completed -01 day
18 | Babra | O2-25 | 5353 | 2024-06-26 | 2024-07-19 | 2024-09-06 | 2024-09-06 | 0 | 100 |  | 2025-04-21 | 2025-05-04 |  | 13 |  | PM Completed -01 day
19 | Babra | O2-26 | 5345 | 2024-08-18 | 2024-08-20 | 2024-09-10 | 2024-09-13 | 3 | 100 |  | 2025-10-01
20 | Babra | O2-04 | 5328 | 2024-08-22 | 2024-08-29 | 2024-10-17 | 2024-10-18 | 1 | 100 |  | 2025-10-03
21 | Babra | O2-07 | 5330 | 2024-08-24 | 2024-09-03 | 2024-10-22 | 2024-10-21 | -1 | 100 |  | 2025-10-05
22 | Babra | O2-08 | 5348 | 2024-09-21 | 2024-09-21 | 2024-11-09 | 2024-10-25 | -15 | 100 |  | 2025-10-08
23 | Babra | O2-19 | 5339 | 2024-10-13 | 2024-10-13 | 2024-12-14 | 2024-12-15 | 1 | 100 |  | 2025-10-10
24 | Babra | O2-22 | 5351 | 2024-10-17 | 2024-10-17 | 2024-12-15 | 2024-12-16 | 1 | 100 |  | 2025-10-12
25 | Babra | O2-23 | 5350 | 2024-10-28 | 2024-10-26 | 2024-12-16 | 2024-12-17 | 1 | 100 |  | 2025-10-15
26 | Babra | O2-17 | 5338 | 4564600% | 4564600% | 4567700% | 4567700% | 0 | 100 |  | 2025-10-17
Note : New WTGs maintenacne will add based on commissioning date
Formulas:
Plan Date = [Date of Operation]+49

## Modelling New (hidden)
Sr. No. | Month Name | Month Number | Month | CY | FY | No. of Days in Month | GHI | POA | WS | Tamb | Tmod | Egrid (MWh) | Bugt_Capacity | PR | Daily POA | Days Operated | MTD POA | YTD POA | Daily Energy (MWh) | MTD Energy (MWh) | YTD Energy (MWh) | Bugt CUF (%) | Bugt CUF (%) MTD | Bugt CUF (%)YTD | Ave. Cap MTD | Ave. Cap YTD | CC Energy MTD | WS MTD | WS YTD | Bugt PA | Bugt EGA | Bugt TA | Bugt MA | Bugt IGA | Corelation | Bugt Line loss | Bugt Reactive Power | Bugt Capacity | CC*Bugt | Total Capacity | 70.4
1 | April | 4 | 2024-04-01 | 2024 | FY25 | 30 |  |  | 6.65 |  |  | 0 | 0 |  |  | 30 |  |  | 0 | 0 | 0 |  |  |  | 24.3 | 24.3 |  | 6.65 | 6.65 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5% |  |  | Hourly reactive power bugt | 3.52
2 | May | 5 | 2024-05-01 | 2024 | FY25 | 31 |  |  | 7.19 |  |  | 8711.265 | 27 |  |  | 31 |  |  | 281.0085 | 8711.265 | 8711.265 | 43.37% | 43.37% | 22.04% | 26.7387 | 25.5194 |  | 7.19 | 6.92 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5% |  |  | Day | 84.48
3 | June | 6 | 2024-06-01 | 2024 | FY25 | 30 |  |  | 7.15 |  |  | 7436.691 | 27 |  |  | 30 |  |  | 247.8897 | 7436.691 | 16147.956 | 38.25% | 38.25% | 27.38% | 34.9967 | 28.6785 |  | 7.15 | 6.9967 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
4 | July | 7 | 2024-07-01 | 2024 | FY25 | 31 |  |  | 8.18 |  |  | 24024.425 | 70.2 |  |  | 31 |  |  | 774.9815 | 24024.425 | 40172.381 | 46% | 46% | 19.54% | 44.5516 | 32.6467 |  | 8.18 | 7.2925 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
5 | August | 8 | 2024-08-01 | 2024 | FY25 | 31 |  |  | 9.01 |  |  | 22325.728 | 70.2 |  |  | 31 |  |  | 720.1848 | 22325.728 | 62498.109 | 42.75% | 42.75% | 24.25% | 49.471 | 36.0116 |  | 9.01 | 7.636 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
6 | September | 9 | 2024-09-01 | 2024 | FY25 | 30 |  |  | 8.16 |  |  | 15949.744 | 70.2 |  |  | 30 |  |  | 531.6581 | 15949.744 | 78447.853 | 31.56% | 31.56% | 25.44% | 56.43 | 39.4147 |  | 8.16 | 7.7233 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
7 | October | 10 | 2024-10-01 | 2024 | FY25 | 31 |  |  | 9.21 |  |  | 11324.645 | 70.2 |  |  | 31 |  |  | 365.3111 | 11324.645 | 89772.498 | 21.68% | 21.68% | 24.9% | 62.0129 | 42.643 |  | 9.21 | 7.9357 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
8 | November | 11 | 2024-11-01 | 2024 | FY25 | 30 |  |  | 8.33 |  |  | 12231.399 | 70.2 |  |  | 30 |  |  | 407.7133 | 12231.399 | 102003.897 | 24.2% | 24.2% | 24.81% | 67.5 | 45.7501 |  | 8.33 | 7.985 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
9 | December | 12 | 2024-12-01 | 2024 | FY25 | 31 |  |  | 6.95 |  |  | 17896.983 | 70.2 |  |  | 31 |  |  | 577.322 | 17896.983 | 119900.88 | 34.27% | 34.27% | 25.88% | 68.7194 | 48.3022 |  | 6.95 | 7.87 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
10 | January | 1 | 2025-01-01 | 2025 | FY25 | 31 |  |  | 5.57 |  |  | 19110.338 | 70.2 |  |  | 31 |  |  | 616.4625 | 19110.338 | 139011.218 | 36.59% | 36.59% | 26.96% | 70.2 | 50.492 |  | 5.57 | 7.64 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
11 | February | 2 | 2025-02-01 | 2025 | FY25 | 28 |  |  | 5.52 |  |  | 14703.772 | 70.2 |  |  | 28 |  |  | 525.1347 | 14703.772 | 153714.99 | 31.17% | 31.17% | 27.32% | 70.2 | 52.2837 |  | 5.52 | 7.4473 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
12 | March | 4 | 2025-03-01 | 2025 | FY25 | 31 |  |  | 6.89 |  |  | 19615.902 | 70.2 |  |  | 31 |  |  | 632.771 | 19615.902 | 173330.892 | 37.56% | 37.56% | 28.19% | 70.2 | 53.7767 |  | 6.89 | 7.4008 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
13 | April | 5 | 2025-04-01 | 2025 | FY26 | 30 |  |  | 6.65 |  |  | 20932.8163 | 70.2 |  |  | 30 |  |  | 697.7605 | 20932.8163 | 20932.8163 | 41.42% | 41.42% | 41.42% | 70.2 | 70.2 |  | 6.65 | 6.65 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
14 | May | 6 | 2025-05-01 | 2025 | FY26 | 31 |  |  | 7.19 |  |  | 28170.0535 | 70.2 |  |  | 31 |  |  | 908.7114 | 28170.0535 | 49102.8698 | 53.94% | 53.94% | 47.78% | 70.2 | 70.2 |  | 7.19 | 6.92 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
15 | June | 7 | 2025-06-01 | 2025 | FY26 | 30 |  |  | 7.15 |  |  | 24048.3982 | 70.2 |  |  | 12 |  |  | 801.6133 | 9619.3593 | 58722.2291 | 47.58% | 47.58% | 47.75% | 70.2 | 70.2 |  | 7.15 | 6.9967 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
16 | July | 8 | 2025-07-01 | 2025 | FY26 | 31 |  |  | 8.18 |  |  | 29880.3782 | 70.2 |  |  | 0 |  |  | 963.8832 | 0 | 58722.2291 | 57.21% |  | 47.75% |  | 70.2 |  | 8.18 | 7.2925 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
17 | August | 9 | 2025-08-01 | 2025 | FY26 | 31 |  |  | 9.01 |  |  | 27767.6242 | 70.2 |  |  | 0 |  |  | 895.7298 | 0 | 58722.2291 | 53.17% |  | 47.75% |  | 70.2 |  | 9.01 | 7.636 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
18 | September | 10 | 2025-09-01 | 2025 | FY26 | 30 |  |  | 8.16 |  |  | 15869.9956 | 70.2 |  |  | 0 |  |  | 528.9999 | 0 | 58722.2291 | 31.4% |  | 47.75% |  | 70.2 |  | 8.16 | 7.7233 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
19 | October | 11 | 2025-10-01 | 2025 | FY26 | 31 |  |  | 9.21 |  |  | 11268.0214 | 70.2 |  |  | 0 |  |  | 363.4846 | 0 | 58722.2291 | 21.57% |  | 47.75% |  | 70.2 |  | 9.21 | 7.9357 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
20 | November | 12 | 2025-11-01 | 2025 | FY26 | 30 |  |  | 8.33 |  |  | 12170.242 | 70.2 |  |  | 0 |  |  | 405.6747 | 0 | 58722.2291 | 24.08% |  | 47.75% |  | 70.2 |  | 8.33 | 7.985 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
21 | December | 1 | 2025-12-01 | 2025 | FY26 | 31 |  |  | 6.95 |  |  | 17807.4981 | 70.2 |  |  | 0 |  |  | 574.4354 | 0 | 58722.2291 | 34.1% |  | 47.75% |  | 70.2 |  | 6.95 | 7.87 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
22 | January | 2 | 2026-01-01 | 2026 | FY26 | 31 |  |  | 5.57 |  |  | 19014.7861 | 70.2 |  |  | 0 |  |  | 613.3802 | 0 | 58722.2291 | 36.41% |  | 47.75% |  | 70.2 |  | 5.57 | 7.64 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
23 | February | 4 | 2026-02-01 | 2026 | FY26 | 28 |  |  | 5.52 |  |  | 14630.2536 | 70.2 |  |  | 0 |  |  | 522.5091 | 0 | 58722.2291 | 31.01% |  | 47.75% |  | 70.2 |  | 5.52 | 7.4473 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
24 | March | 5 | 2026-03-01 | 2026 | FY26 | 31 |  |  | 6.89 |  |  | 19517.8228 | 70.2 |  |  | 0 |  |  | 629.6072 | 0 | 58722.2291 | 37.37% |  | 47.75% |  | 70.2 |  | 6.89 | 7.4008 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
Formulas:
No. of Days in Month = DAY(EOMONTH([Month],0))

## Modelling (hidden)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
Date | FY | Year | Month | Days | E_Grid daily MWh | E_Grid MTD MWh | E_Grid YTD MWh | WS Daily | WS MTD | WS YTD | CUF Daily | CUF MTD | CUF YTD | Day Capacity | MTD Capacity | YTD Capacity |  |  | Month | Days | Wind Speed (m/s) | Egrid Energy (KWh) | Capacity
4538300% | 2025 | 2024 | 2024-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0! | [5 empty] | 4 | 30 | 8.29 | 0 | 0
4538400% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0! | [5 empty] | 5 | 31 | 9.1 | 8711265 | 27
4538500% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0! | [5 empty] | 6 | 30 | 8.23 | 7436691 | 27
4538600% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0! | [5 empty] | 7 | 31 | 9.35 | 24024425 | 70.2
4538700% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0! | [5 empty] | 8 | 31 | 8.47 | 22325728 | 70.2
4538800% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0! | [5 empty] | 9 | 30 | 7.08 | 15949744 | 70.2
4538900% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0! | [5 empty] | 10 | 31 | 5.65 | 11324645 | 70.2
4539000% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0! | [5 empty] | 11 | 30 | 5.59 | 12231399 | 70.2
4539100% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0! | [5 empty] | 12 | 31 | 6.99 | 17896983 | 70.2
4539200% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0! | [5 empty] | 1 | 31 | 6.74 | 19110338 | 70.2
4539300% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0! | [5 empty] | 2 | 28 | 7.3 | 14703772 | 70.2
4539400% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0! | [5 empty] | 3 | 31 | 7.28 | 19615902 | 70.2
4539500% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0! | [7 empty] | 7.5058 | 22937709.6
4539600% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0!
4539700% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0!
4539800% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0!
4539900% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0!
4540000% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0!
4540100% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0!
4540200% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0!
4540300% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0!
4540400% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0!
4540500% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0!
4540600% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0!
4540700% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0!
4540800% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0!
4540900% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0!
4541000% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0!
4541100% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0!
4541200% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0!
4541300% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 281.0085 | 281.0085 | 9.1 | 9.1 | 8.3161 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 1 | 1
4541400% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 562.0171 | 562.0171 | 9.1 | 9.1 | 8.3406 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 2 | 2
4541500% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 843.0256 | 843.0256 | 9.1 | 9.1 | 8.3636 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 3 | 3
4541600% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 1124.0342 | 1124.0342 | 9.1 | 9.1 | 8.3853 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 4 | 4
4541700% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 1405.0427 | 1405.0427 | 9.1 | 9.1 | 8.4057 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 5 | 5
4541800% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 1686.0513 | 1686.0513 | 9.1 | 9.1 | 8.425 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 6 | 6
4541900% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 1967.0598 | 1967.0598 | 9.1 | 9.1 | 8.4432 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 7 | 7
4542000% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 2248.0684 | 2248.0684 | 9.1 | 9.1 | 8.4605 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 8 | 8
4542100% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 2529.0769 | 2529.0769 | 9.1 | 9.1 | 8.4769 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 9 | 9
4542200% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 2810.0855 | 2810.0855 | 9.1 | 9.1 | 8.4925 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 10 | 10
4542300% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 3091.094 | 3091.094 | 9.1 | 9.1 | 8.5073 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 11 | 11
4542400% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 3372.1026 | 3372.1026 | 9.1 | 9.1 | 8.5214 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 12 | 12
4542500% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 3653.1111 | 3653.1111 | 9.1 | 9.1 | 8.5349 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 13 | 13
4542600% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 3934.1197 | 3934.1197 | 9.1 | 9.1 | 8.5477 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 14 | 14
4542700% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 4215.1282 | 4215.1282 | 9.1 | 9.1 | 8.56 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 15 | 15
4542800% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 4496.1368 | 4496.1368 | 9.1 | 9.1 | 8.5717 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 16 | 16
4542900% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 4777.1453 | 4777.1453 | 9.1 | 9.1 | 8.583 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 17 | 17
4543000% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 5058.1539 | 5058.1539 | 9.1 | 9.1 | 8.5938 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 18 | 18
4543100% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 5339.1624 | 5339.1624 | 9.1 | 9.1 | 8.6041 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 19 | 19
4543200% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 5620.171 | 5620.171 | 9.1 | 9.1 | 8.614 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 20 | 20
4543300% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 5901.1795 | 5901.1795 | 9.1 | 9.1 | 8.6235 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 21 | 21
4543400% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 6182.1881 | 6182.1881 | 9.1 | 9.1 | 8.6327 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 22 | 22
4543500% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 6463.1966 | 6463.1966 | 9.1 | 9.1 | 8.6415 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 23 | 23
4543600% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 6744.2052 | 6744.2052 | 9.1 | 9.1 | 8.65 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 24 | 24
4543700% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 7025.2137 | 7025.2137 | 9.1 | 9.1 | 8.6582 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 25 | 25
4543800% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 7306.2223 | 7306.2223 | 9.1 | 9.1 | 8.6661 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 26 | 26
4543900% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 7587.2308 | 7587.2308 | 9.1 | 9.1 | 8.6737 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 27 | 27
4544000% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 7868.2394 | 7868.2394 | 9.1 | 9.1 | 8.681 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 28 | 28
4544100% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 8149.2479 | 8149.2479 | 9.1 | 9.1 | 8.6881 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 29 | 29
4544200% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 8430.2565 | 8430.2565 | 9.1 | 9.1 | 8.695 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 30 | 30
4544300% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 8711.265 | 8711.265 | 9.1 | 9.1 | 8.7016 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 31 | 31
4544400% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 247.8897 | 8959.1547 | 8.23 | 8.23 | 8.694 | 38.25% | 38.25% | 43.21% | 27 | 27 | 27 | 1 | 32
4544500% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 495.7794 | 9207.0444 | 8.23 | 8.23 | 8.6867 | 38.25% | 38.25% | 43.06% | 27 | 27 | 27 | 2 | 33
4544600% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 743.6691 | 9454.9341 | 8.23 | 8.23 | 8.6795 | 38.25% | 38.25% | 42.91% | 27 | 27 | 27 | 3 | 34
4544700% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 991.5588 | 9702.8238 | 8.23 | 8.23 | 8.6726 | 38.25% | 38.25% | 42.78% | 27 | 27 | 27 | 4 | 35
4544800% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 1239.4485 | 9950.7135 | 8.23 | 8.23 | 8.6659 | 38.25% | 38.25% | 42.66% | 27 | 27 | 27 | 5 | 36
4544900% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 1487.3382 | 10198.6032 | 8.23 | 8.23 | 8.6594 | 38.25% | 38.25% | 42.54% | 27 | 27 | 27 | 6 | 37
4545000% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 1735.2279 | 10446.4929 | 8.23 | 8.23 | 8.6531 | 38.25% | 38.25% | 42.42% | 27 | 27 | 27 | 7 | 38
4545100% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 1983.1176 | 10694.3826 | 8.23 | 8.23 | 8.647 | 38.25% | 38.25% | 42.32% | 27 | 27 | 27 | 8 | 39
4545200% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 2231.0073 | 10942.2723 | 8.23 | 8.23 | 8.641 | 38.25% | 38.25% | 42.22% | 27 | 27 | 27 | 9 | 40
4545300% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 2478.897 | 11190.162 | 8.23 | 8.23 | 8.6352 | 38.25% | 38.25% | 42.12% | 27 | 27 | 27 | 10 | 41
4545400% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 2726.7867 | 11438.0517 | 8.23 | 8.23 | 8.6296 | 38.25% | 38.25% | 42.03% | 27 | 27 | 27 | 11 | 42
4545500% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 2974.6764 | 11685.9414 | 8.23 | 8.23 | 8.6241 | 38.25% | 38.25% | 41.94% | 27 | 27 | 27 | 12 | 43
4545600% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 3222.5661 | 11933.8311 | 8.23 | 8.23 | 8.6188 | 38.25% | 38.25% | 41.86% | 27 | 27 | 27 | 13 | 44
4545700% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 3470.4558 | 12181.7208 | 8.23 | 8.23 | 8.6136 | 38.25% | 38.25% | 41.78% | 27 | 27 | 27 | 14 | 45
4545800% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 3718.3455 | 12429.6105 | 8.23 | 8.23 | 8.6086 | 38.25% | 38.25% | 41.7% | 27 | 27 | 27 | 15 | 46
4545900% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 3966.2352 | 12677.5002 | 8.23 | 8.23 | 8.6036 | 38.25% | 38.25% | 41.63% | 27 | 27 | 27 | 16 | 47
4546000% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 4214.1249 | 12925.3899 | 8.23 | 8.23 | 8.5988 | 38.25% | 38.25% | 41.56% | 27 | 27 | 27 | 17 | 48
4546100% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 4462.0146 | 13173.2796 | 8.23 | 8.23 | 8.5942 | 38.25% | 38.25% | 41.49% | 27 | 27 | 27 | 18 | 49
4546200% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 4709.9043 | 13421.1693 | 8.23 | 8.23 | 8.5896 | 38.25% | 38.25% | 41.42% | 27 | 27 | 27 | 19 | 50
4546300% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 4957.794 | 13669.059 | 8.23 | 8.23 | 8.5852 | 38.25% | 38.25% | 41.36% | 27 | 27 | 27 | 20 | 51
4546400% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 5205.6837 | 13916.9487 | 8.23 | 8.23 | 8.5809 | 38.25% | 38.25% | 41.3% | 27 | 27 | 27 | 21 | 52
4546500% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 5453.5734 | 14164.8384 | 8.23 | 8.23 | 8.5766 | 38.25% | 38.25% | 41.24% | 27 | 27 | 27 | 22 | 53
4546600% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 5701.4631 | 14412.7281 | 8.23 | 8.23 | 8.5725 | 38.25% | 38.25% | 41.19% | 27 | 27 | 27 | 23 | 54
4546700% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 5949.3528 | 14660.6178 | 8.23 | 8.23 | 8.5685 | 38.25% | 38.25% | 41.14% | 27 | 27 | 27 | 24 | 55
4546800% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 6197.2425 | 14908.5075 | 8.23 | 8.23 | 8.5645 | 38.25% | 38.25% | 41.08% | 27 | 27 | 27 | 25 | 56
4546900% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 6445.1322 | 15156.3972 | 8.23 | 8.23 | 8.5607 | 38.25% | 38.25% | 41.03% | 27 | 27 | 27 | 26 | 57
4547000% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 6693.0219 | 15404.2869 | 8.23 | 8.23 | 8.5569 | 38.25% | 38.25% | 40.99% | 27 | 27 | 27 | 27 | 58
4547100% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 6940.9116 | 15652.1766 | 8.23 | 8.23 | 8.5533 | 38.25% | 38.25% | 40.94% | 27 | 27 | 27 | 28 | 59
4547200% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 7188.8013 | 15900.0663 | 8.23 | 8.23 | 8.5497 | 38.25% | 38.25% | 40.9% | 27 | 27 | 27 | 29 | 60
4547300% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 7436.691 | 16147.956 | 8.23 | 8.23 | 8.5462 | 38.25% | 38.25% | 40.85% | 27 | 27 | 27 | 30 | 61
4547400% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 774.9815 | 16922.9375 | 9.35 | 9.35 | 8.5549 | 46% | 46% | 41.06% | 70.2 | 70.2 | 27.6968 | 1 | 62
4547500% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 1549.9629 | 17697.9189 | 9.35 | 9.35 | 8.5634 | 46% | 46% | 41.26% | 70.2 | 70.2 | 28.3714 | 2 | 63
4547600% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 2324.9444 | 18472.9004 | 9.35 | 9.35 | 8.5718 | 46% | 46% | 41.44% | 70.2 | 70.2 | 29.025 | 3 | 64
4547700% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 3099.9258 | 19247.8818 | 9.35 | 9.35 | 8.58 | 46% | 46% | 41.6% | 70.2 | 70.2 | 29.6585 | 4 | 65
4547800% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 3874.9073 | 20022.8633 | 9.35 | 9.35 | 8.588 | 46% | 46% | 41.76% | 70.2 | 70.2 | 30.2727 | 5 | 66
4547900% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 4649.8887 | 20797.8447 | 9.35 | 9.35 | 8.5959 | 46% | 46% | 41.9% | 70.2 | 70.2 | 30.8687 | 6 | 67
4548000% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 5424.8702 | 21572.8262 | 9.35 | 9.35 | 8.6036 | 46% | 46% | 42.03% | 70.2 | 70.2 | 31.4471 | 7 | 68
4548100% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 6199.8516 | 22347.8076 | 9.35 | 9.35 | 8.6111 | 46% | 46% | 42.16% | 70.2 | 70.2 | 32.0087 | 8 | 69
4548200% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 6974.8331 | 23122.7891 | 9.35 | 9.35 | 8.6185 | 46% | 46% | 42.28% | 70.2 | 70.2 | 32.5543 | 9 | 70
4548300% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 7749.8145 | 23897.7705 | 9.35 | 9.35 | 8.6257 | 46% | 46% | 42.39% | 70.2 | 70.2 | 33.0845 | 10 | 71
4548400% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 8524.796 | 24672.752 | 9.35 | 9.35 | 8.6328 | 46% | 46% | 42.49% | 70.2 | 70.2 | 33.6 | 11 | 72
4548500% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 9299.7774 | 25447.7334 | 9.35 | 9.35 | 8.6398 | 46% | 46% | 42.59% | 70.2 | 70.2 | 34.1014 | 12 | 73
4548600% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 10074.7589 | 26222.7149 | 9.35 | 9.35 | 8.6466 | 46% | 46% | 42.69% | 70.2 | 70.2 | 34.5892 | 13 | 74
4548700% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 10849.7403 | 26997.6963 | 9.35 | 9.35 | 8.6533 | 46% | 46% | 42.78% | 70.2 | 70.2 | 35.064 | 14 | 75
4548800% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 11624.7218 | 27772.6778 | 9.35 | 9.35 | 8.6599 | 46% | 46% | 42.86% | 70.2 | 70.2 | 35.5263 | 15 | 76
4548900% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 12399.7032 | 28547.6592 | 9.35 | 9.35 | 8.6664 | 46% | 46% | 42.94% | 70.2 | 70.2 | 35.9766 | 16 | 77
4549000% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 13174.6847 | 29322.6407 | 9.35 | 9.35 | 8.6727 | 46% | 46% | 43.01% | 70.2 | 70.2 | 36.4154 | 17 | 78
4549100% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 13949.6661 | 30097.6221 | 9.35 | 9.35 | 8.6789 | 46% | 46% | 43.09% | 70.2 | 70.2 | 36.843 | 18 | 79
4549200% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 14724.6476 | 30872.6036 | 9.35 | 9.35 | 8.685 | 46% | 46% | 43.15% | 70.2 | 70.2 | 37.26 | 19 | 80
4549300% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 15499.629 | 31647.585 | 9.35 | 9.35 | 8.691 | 46% | 46% | 43.22% | 70.2 | 70.2 | 37.6667 | 20 | 81
4549400% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 16274.6105 | 32422.5665 | 9.35 | 9.35 | 8.6969 | 46% | 46% | 43.28% | 70.2 | 70.2 | 38.0634 | 21 | 82
4549500% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 17049.5919 | 33197.5479 | 9.35 | 9.35 | 8.7027 | 46% | 46% | 43.34% | 70.2 | 70.2 | 38.4506 | 22 | 83
4549600% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 17824.5734 | 33972.5294 | 9.35 | 9.35 | 8.7083 | 46% | 46% | 43.4% | 70.2 | 70.2 | 38.8286 | 23 | 84
4549700% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 18599.5548 | 34747.5108 | 9.35 | 9.35 | 8.7139 | 46% | 46% | 43.45% | 70.2 | 70.2 | 39.1976 | 24 | 85
4549800% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 19374.5363 | 35522.4923 | 9.35 | 9.35 | 8.7194 | 46% | 46% | 43.51% | 70.2 | 70.2 | 39.5581 | 25 | 86
4549900% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 20149.5177 | 36297.4737 | 9.35 | 9.35 | 8.7248 | 46% | 46% | 43.56% | 70.2 | 70.2 | 39.9103 | 26 | 87
4550000% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 20924.4992 | 37072.4552 | 9.35 | 9.35 | 8.7301 | 46% | 46% | 43.61% | 70.2 | 70.2 | 40.2545 | 27 | 88
4550100% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 21699.4806 | 37847.4366 | 9.35 | 9.35 | 8.7353 | 46% | 46% | 43.65% | 70.2 | 70.2 | 40.591 | 28 | 89
4550200% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 22474.4621 | 38622.4181 | 9.35 | 9.35 | 8.7404 | 46% | 46% | 43.7% | 70.2 | 70.2 | 40.92 | 29 | 90
4550300% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 23249.4435 | 39397.3995 | 9.35 | 9.35 | 8.7455 | 46% | 46% | 43.74% | 70.2 | 70.2 | 41.2418 | 30 | 91
4550400% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 24024.425 | 40172.381 | 9.35 | 9.35 | 8.7504 | 46% | 46% | 43.78% | 70.2 | 70.2 | 41.5565 | 31 | 92
4550500% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 720.1848 | 40892.5658 | 8.47 | 8.47 | 8.7481 | 42.75% | 42.75% | 43.76% | 70.2 | 70.2 | 41.8645 | 1 | 93
4550600% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 1440.3695 | 41612.7505 | 8.47 | 8.47 | 8.7459 | 42.75% | 42.75% | 43.74% | 70.2 | 70.2 | 42.166 | 2 | 94
4550700% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 2160.5543 | 42332.9353 | 8.47 | 8.47 | 8.7437 | 42.75% | 42.75% | 43.73% | 70.2 | 70.2 | 42.4611 | 3 | 95
4550800% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 2880.7391 | 43053.1201 | 8.47 | 8.47 | 8.7415 | 42.75% | 42.75% | 43.71% | 70.2 | 70.2 | 42.75 | 4 | 96
4550900% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 3600.9239 | 43773.3049 | 8.47 | 8.47 | 8.7394 | 42.75% | 42.75% | 43.69% | 70.2 | 70.2 | 43.033 | 5 | 97
4551000% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 4321.1086 | 44493.4896 | 8.47 | 8.47 | 8.7373 | 42.75% | 42.75% | 43.68% | 70.2 | 70.2 | 43.3102 | 6 | 98
4551100% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 5041.2934 | 45213.6744 | 8.47 | 8.47 | 8.7352 | 42.75% | 42.75% | 43.66% | 70.2 | 70.2 | 43.5818 | 7 | 99
4551200% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 5761.4782 | 45933.8592 | 8.47 | 8.47 | 8.7332 | 42.75% | 42.75% | 43.65% | 70.2 | 70.2 | 43.848 | 8 | 100
4551300% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 6481.663 | 46654.044 | 8.47 | 8.47 | 8.7311 | 42.75% | 42.75% | 43.63% | 70.2 | 70.2 | 44.1089 | 9 | 101
4551400% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 7201.8477 | 47374.2287 | 8.47 | 8.47 | 8.7292 | 42.75% | 42.75% | 43.62% | 70.2 | 70.2 | 44.3647 | 10 | 102
4551500% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 7922.0325 | 48094.4135 | 8.47 | 8.47 | 8.7272 | 42.75% | 42.75% | 43.61% | 70.2 | 70.2 | 44.6155 | 11 | 103
4551600% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 8642.2173 | 48814.5983 | 8.47 | 8.47 | 8.7253 | 42.75% | 42.75% | 43.59% | 70.2 | 70.2 | 44.8615 | 12 | 104
4551700% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 9362.4021 | 49534.7831 | 8.47 | 8.47 | 8.7234 | 42.75% | 42.75% | 43.58% | 70.2 | 70.2 | 45.1029 | 13 | 105
4551800% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 10082.5868 | 50254.9678 | 8.47 | 8.47 | 8.7215 | 42.75% | 42.75% | 43.57% | 70.2 | 70.2 | 45.3396 | 14 | 106
4551900% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 10802.7716 | 50975.1526 | 8.47 | 8.47 | 8.7197 | 42.75% | 42.75% | 43.56% | 70.2 | 70.2 | 45.572 | 15 | 107
4552000% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 11522.9564 | 51695.3374 | 8.47 | 8.47 | 8.7179 | 42.75% | 42.75% | 43.55% | 70.2 | 70.2 | 45.8 | 16 | 108
4552100% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 12243.1412 | 52415.5222 | 8.47 | 8.47 | 8.7161 | 42.75% | 42.75% | 43.54% | 70.2 | 70.2 | 46.0239 | 17 | 109
4552200% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 12963.3259 | 53135.7069 | 8.47 | 8.47 | 8.7144 | 42.75% | 42.75% | 43.52% | 70.2 | 70.2 | 46.2436 | 18 | 110
4552300% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 13683.5107 | 53855.8917 | 8.47 | 8.47 | 8.7126 | 42.75% | 42.75% | 43.51% | 70.2 | 70.2 | 46.4595 | 19 | 111
4552400% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 14403.6955 | 54576.0765 | 8.47 | 8.47 | 8.7109 | 42.75% | 42.75% | 43.5% | 70.2 | 70.2 | 46.6714 | 20 | 112
4552500% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 15123.8803 | 55296.2613 | 8.47 | 8.47 | 8.7092 | 42.75% | 42.75% | 43.49% | 70.2 | 70.2 | 46.8796 | 21 | 113
4552600% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 15844.065 | 56016.446 | 8.47 | 8.47 | 8.7076 | 42.75% | 42.75% | 43.48% | 70.2 | 70.2 | 47.0842 | 22 | 114
4552700% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 16564.2498 | 56736.6308 | 8.47 | 8.47 | 8.7059 | 42.75% | 42.75% | 43.47% | 70.2 | 70.2 | 47.2852 | 23 | 115
4552800% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 17284.4346 | 57456.8156 | 8.47 | 8.47 | 8.7043 | 42.75% | 42.75% | 43.46% | 70.2 | 70.2 | 47.4828 | 24 | 116
4552900% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 18004.6194 | 58177.0004 | 8.47 | 8.47 | 8.7027 | 42.75% | 42.75% | 43.46% | 70.2 | 70.2 | 47.6769 | 25 | 117
4553000% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 18724.8041 | 58897.1851 | 8.47 | 8.47 | 8.7011 | 42.75% | 42.75% | 43.45% | 70.2 | 70.2 | 47.8678 | 26 | 118
4553100% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 19444.9889 | 59617.3699 | 8.47 | 8.47 | 8.6996 | 42.75% | 42.75% | 43.44% | 70.2 | 70.2 | 48.0555 | 27 | 119
4553200% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 20165.1737 | 60337.5547 | 8.47 | 8.47 | 8.6981 | 42.75% | 42.75% | 43.43% | 70.2 | 70.2 | 48.24 | 28 | 120
4553300% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 20885.3585 | 61057.7395 | 8.47 | 8.47 | 8.6966 | 42.75% | 42.75% | 43.42% | 70.2 | 70.2 | 48.4215 | 29 | 121
4553400% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 21605.5432 | 61777.9242 | 8.47 | 8.47 | 8.6951 | 42.75% | 42.75% | 43.41% | 70.2 | 70.2 | 48.6 | 30 | 122
4553500% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 22325.728 | 62498.109 | 8.47 | 8.47 | 8.6936 | 42.75% | 42.75% | 43.41% | 70.2 | 70.2 | 48.7756 | 31 | 123
4553600% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 531.6581 | 63029.7671 | 7.08 | 7.08 | 8.6831 | 31.56% | 31.56% | 43.27% | 70.2 | 70.2 | 48.9484 | 1 | 124
4553700% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 1063.3163 | 63561.4253 | 7.08 | 7.08 | 8.6728 | 31.56% | 31.56% | 43.13% | 70.2 | 70.2 | 49.1184 | 2 | 125
4553800% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 1594.9744 | 64093.0834 | 7.08 | 7.08 | 8.6626 | 31.56% | 31.56% | 43% | 70.2 | 70.2 | 49.2857 | 3 | 126
4553900% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 2126.6325 | 64624.7415 | 7.08 | 7.08 | 8.6525 | 31.56% | 31.56% | 42.88% | 70.2 | 70.2 | 49.4504 | 4 | 127
4554000% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 2658.2907 | 65156.3997 | 7.08 | 7.08 | 8.6425 | 31.56% | 31.56% | 42.75% | 70.2 | 70.2 | 49.6125 | 5 | 128
4554100% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 3189.9488 | 65688.0578 | 7.08 | 7.08 | 8.6327 | 31.56% | 31.56% | 42.63% | 70.2 | 70.2 | 49.7721 | 6 | 129
4554200% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 3721.6069 | 66219.7159 | 7.08 | 7.08 | 8.623 | 31.56% | 31.56% | 42.51% | 70.2 | 70.2 | 49.9292 | 7 | 130
4554300% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 4253.2651 | 66751.3741 | 7.08 | 7.08 | 8.6134 | 31.56% | 31.56% | 42.39% | 70.2 | 70.2 | 50.084 | 8 | 131
4554400% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 4784.9232 | 67283.0322 | 7.08 | 7.08 | 8.604 | 31.56% | 31.56% | 42.28% | 70.2 | 70.2 | 50.2364 | 9 | 132
4554500% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 5316.5813 | 67814.6903 | 7.08 | 7.08 | 8.5946 | 31.56% | 31.56% | 42.16% | 70.2 | 70.2 | 50.3865 | 10 | 133
4554600% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 5848.2395 | 68346.3485 | 7.08 | 7.08 | 8.5854 | 31.56% | 31.56% | 42.05% | 70.2 | 70.2 | 50.5343 | 11 | 134
4554700% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 6379.8976 | 68878.0066 | 7.08 | 7.08 | 8.5762 | 31.56% | 31.56% | 41.95% | 70.2 | 70.2 | 50.68 | 12 | 135
4554800% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 6911.5557 | 69409.6647 | 7.08 | 7.08 | 8.5672 | 31.56% | 31.56% | 41.84% | 70.2 | 70.2 | 50.8235 | 13 | 136
4554900% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 7443.2139 | 69941.3229 | 7.08 | 7.08 | 8.5583 | 31.56% | 31.56% | 41.74% | 70.2 | 70.2 | 50.965 | 14 | 137
4555000% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 7974.872 | 70472.981 | 7.08 | 7.08 | 8.5495 | 31.56% | 31.56% | 41.64% | 70.2 | 70.2 | 51.1043 | 15 | 138
4555100% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 8506.5301 | 71004.6391 | 7.08 | 7.08 | 8.5408 | 31.56% | 31.56% | 41.54% | 70.2 | 70.2 | 51.2417 | 16 | 139
4555200% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 9038.1883 | 71536.2973 | 7.08 | 7.08 | 8.5322 | 31.56% | 31.56% | 41.44% | 70.2 | 70.2 | 51.3771 | 17 | 140
4555300% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 9569.8464 | 72067.9554 | 7.08 | 7.08 | 8.5237 | 31.56% | 31.56% | 41.34% | 70.2 | 70.2 | 51.5106 | 18 | 141
4555400% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 10101.5045 | 72599.6135 | 7.08 | 7.08 | 8.5153 | 31.56% | 31.56% | 41.25% | 70.2 | 70.2 | 51.6423 | 19 | 142
4555500% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 10633.1627 | 73131.2717 | 7.08 | 7.08 | 8.5071 | 31.56% | 31.56% | 41.16% | 70.2 | 70.2 | 51.772 | 20 | 143
4555600% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 11164.8208 | 73662.9298 | 7.08 | 7.08 | 8.4989 | 31.56% | 31.56% | 41.07% | 70.2 | 70.2 | 51.9 | 21 | 144
4555700% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 11696.4789 | 74194.5879 | 7.08 | 7.08 | 8.4907 | 31.56% | 31.56% | 40.98% | 70.2 | 70.2 | 52.0262 | 22 | 145
4555800% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 12228.1371 | 74726.2461 | 7.08 | 7.08 | 8.4827 | 31.56% | 31.56% | 40.89% | 70.2 | 70.2 | 52.1507 | 23 | 146
4555900% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 12759.7952 | 75257.9042 | 7.08 | 7.08 | 8.4748 | 31.56% | 31.56% | 40.81% | 70.2 | 70.2 | 52.2735 | 24 | 147
4556000% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 13291.4533 | 75789.5623 | 7.08 | 7.08 | 8.467 | 31.56% | 31.56% | 40.72% | 70.2 | 70.2 | 52.3946 | 25 | 148
4556100% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 13823.1115 | 76321.2205 | 7.08 | 7.08 | 8.4592 | 31.56% | 31.56% | 40.64% | 70.2 | 70.2 | 52.5141 | 26 | 149
4556200% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 14354.7696 | 76852.8786 | 7.08 | 7.08 | 8.4516 | 31.56% | 31.56% | 40.56% | 70.2 | 70.2 | 52.632 | 27 | 150
4556300% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 14886.4277 | 77384.5367 | 7.08 | 7.08 | 8.444 | 31.56% | 31.56% | 40.48% | 70.2 | 70.2 | 52.7483 | 28 | 151
4556400% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 15418.0859 | 77916.1949 | 7.08 | 7.08 | 8.4365 | 31.56% | 31.56% | 40.4% | 70.2 | 70.2 | 52.8632 | 29 | 152
4556500% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 15949.744 | 78447.853 | 7.08 | 7.08 | 8.4291 | 31.56% | 31.56% | 40.33% | 70.2 | 70.2 | 52.9765 | 30 | 153
4556600% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 365.3111 | 78813.1641 | 5.65 | 5.65 | 8.414 | 21.68% | 21.68% | 40.17% | 70.2 | 70.2 | 53.0883 | 1 | 154
4556700% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 730.6223 | 79178.4753 | 5.65 | 5.65 | 8.399 | 21.68% | 21.68% | 40.01% | 70.2 | 70.2 | 53.1987 | 2 | 155
4556800% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 1095.9334 | 79543.7864 | 5.65 | 5.65 | 8.3842 | 21.68% | 21.68% | 39.85% | 70.2 | 70.2 | 53.3077 | 3 | 156
4556900% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 1461.2445 | 79909.0975 | 5.65 | 5.65 | 8.3696 | 21.68% | 21.68% | 39.7% | 70.2 | 70.2 | 53.4153 | 4 | 157
4557000% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 1826.5556 | 80274.4086 | 5.65 | 5.65 | 8.3552 | 21.68% | 21.68% | 39.55% | 70.2 | 70.2 | 53.5215 | 5 | 158
4557100% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 2191.8668 | 80639.7198 | 5.65 | 5.65 | 8.3408 | 21.68% | 21.68% | 39.41% | 70.2 | 70.2 | 53.6264 | 6 | 159
4557200% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 2557.1779 | 81005.0309 | 5.65 | 5.65 | 8.3267 | 21.68% | 21.68% | 39.26% | 70.2 | 70.2 | 53.73 | 7 | 160
4557300% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 2922.489 | 81370.342 | 5.65 | 5.65 | 8.3127 | 21.68% | 21.68% | 39.12% | 70.2 | 70.2 | 53.8323 | 8 | 161
4557400% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 3287.8002 | 81735.6532 | 5.65 | 5.65 | 8.2988 | 21.68% | 21.68% | 38.98% | 70.2 | 70.2 | 53.9333 | 9 | 162
4557500% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 3653.1113 | 82100.9643 | 5.65 | 5.65 | 8.2851 | 21.68% | 21.68% | 38.84% | 70.2 | 70.2 | 54.0331 | 10 | 163
4557600% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 4018.4224 | 82466.2754 | 5.65 | 5.65 | 8.2715 | 21.68% | 21.68% | 38.71% | 70.2 | 70.2 | 54.1317 | 11 | 164
4557700% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 4383.7335 | 82831.5865 | 5.65 | 5.65 | 8.2581 | 21.68% | 21.68% | 38.57% | 70.2 | 70.2 | 54.2291 | 12 | 165
4557800% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 4749.0447 | 83196.8977 | 5.65 | 5.65 | 8.2447 | 21.68% | 21.68% | 38.44% | 70.2 | 70.2 | 54.3253 | 13 | 166
4557900% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 5114.3558 | 83562.2088 | 5.65 | 5.65 | 8.2316 | 21.68% | 21.68% | 38.31% | 70.2 | 70.2 | 54.4204 | 14 | 167
4558000% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 5479.6669 | 83927.5199 | 5.65 | 5.65 | 8.2185 | 21.68% | 21.68% | 38.18% | 70.2 | 70.2 | 54.5143 | 15 | 168
4558100% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 5844.9781 | 84292.8311 | 5.65 | 5.65 | 8.2056 | 21.68% | 21.68% | 38.06% | 70.2 | 70.2 | 54.6071 | 16 | 169
4558200% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 6210.2892 | 84658.1422 | 5.65 | 5.65 | 8.1929 | 21.68% | 21.68% | 37.93% | 70.2 | 70.2 | 54.6988 | 17 | 170
4558300% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 6575.6003 | 85023.4533 | 5.65 | 5.65 | 8.1802 | 21.68% | 21.68% | 37.81% | 70.2 | 70.2 | 54.7895 | 18 | 171
4558400% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 6940.9115 | 85388.7645 | 5.65 | 5.65 | 8.1677 | 21.68% | 21.68% | 37.69% | 70.2 | 70.2 | 54.8791 | 19 | 172
4558500% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 7306.2226 | 85754.0756 | 5.65 | 5.65 | 8.1553 | 21.68% | 21.68% | 37.57% | 70.2 | 70.2 | 54.9676 | 20 | 173
4558600% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 7671.5337 | 86119.3867 | 5.65 | 5.65 | 8.143 | 21.68% | 21.68% | 37.46% | 70.2 | 70.2 | 55.0552 | 21 | 174
4558700% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 8036.8448 | 86484.6978 | 5.65 | 5.65 | 8.1308 | 21.68% | 21.68% | 37.34% | 70.2 | 70.2 | 55.1417 | 22 | 175
4558800% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 8402.156 | 86850.009 | 5.65 | 5.65 | 8.1188 | 21.68% | 21.68% | 37.23% | 70.2 | 70.2 | 55.2273 | 23 | 176
4558900% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 8767.4671 | 87215.3201 | 5.65 | 5.65 | 8.1069 | 21.68% | 21.68% | 37.12% | 70.2 | 70.2 | 55.3119 | 24 | 177
4559000% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 9132.7782 | 87580.6312 | 5.65 | 5.65 | 8.095 | 21.68% | 21.68% | 37.01% | 70.2 | 70.2 | 55.3955 | 25 | 178
4559100% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 9498.0894 | 87945.9424 | 5.65 | 5.65 | 8.0833 | 21.68% | 21.68% | 36.9% | 70.2 | 70.2 | 55.4782 | 26 | 179
4559200% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 9863.4005 | 88311.2535 | 5.65 | 5.65 | 8.0718 | 21.68% | 21.68% | 36.79% | 70.2 | 70.2 | 55.56 | 27 | 180
4559300% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 10228.7116 | 88676.5646 | 5.65 | 5.65 | 8.0603 | 21.68% | 21.68% | 36.69% | 70.2 | 70.2 | 55.6409 | 28 | 181
4559400% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 10594.0227 | 89041.8757 | 5.65 | 5.65 | 8.0489 | 21.68% | 21.68% | 36.58% | 70.2 | 70.2 | 55.7209 | 29 | 182
4559500% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 10959.3339 | 89407.1869 | 5.65 | 5.65 | 8.0377 | 21.68% | 21.68% | 36.48% | 70.2 | 70.2 | 55.8 | 30 | 183
4559600% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 11324.645 | 89772.498 | 5.65 | 5.65 | 8.0265 | 21.68% | 21.68% | 36.38% | 70.2 | 70.2 | 55.8783 | 31 | 184
4559700% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 407.7133 | 90180.2113 | 5.59 | 5.59 | 8.0152 | 24.2% | 24.2% | 36.3% | 70.2 | 70.2 | 55.9557 | 1 | 185
4559800% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 815.4266 | 90587.9246 | 5.59 | 5.59 | 8.0039 | 24.2% | 24.2% | 36.22% | 70.2 | 70.2 | 56.0323 | 2 | 186
4559900% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 1223.1399 | 90995.6379 | 5.59 | 5.59 | 7.9928 | 24.2% | 24.2% | 36.14% | 70.2 | 70.2 | 56.108 | 3 | 187
4560000% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 1630.8532 | 91403.3512 | 5.59 | 5.59 | 7.9818 | 24.2% | 24.2% | 36.06% | 70.2 | 70.2 | 56.183 | 4 | 188
4560100% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 2038.5665 | 91811.0645 | 5.59 | 5.59 | 7.9709 | 24.2% | 24.2% | 35.98% | 70.2 | 70.2 | 56.2571 | 5 | 189
4560200% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 2446.2798 | 92218.7778 | 5.59 | 5.59 | 7.96 | 24.2% | 24.2% | 35.9% | 70.2 | 70.2 | 56.3305 | 6 | 190
4560300% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 2853.9931 | 92626.4911 | 5.59 | 5.59 | 7.9493 | 24.2% | 24.2% | 35.83% | 70.2 | 70.2 | 56.4031 | 7 | 191
4560400% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 3261.7064 | 93034.2044 | 5.59 | 5.59 | 7.9387 | 24.2% | 24.2% | 35.75% | 70.2 | 70.2 | 56.475 | 8 | 192
4560500% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 3669.4197 | 93441.9177 | 5.59 | 5.59 | 7.9282 | 24.2% | 24.2% | 35.68% | 70.2 | 70.2 | 56.5461 | 9 | 193
4560600% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 4077.133 | 93849.631 | 5.59 | 5.59 | 7.9177 | 24.2% | 24.2% | 35.6% | 70.2 | 70.2 | 56.6165 | 10 | 194
4560700% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 4484.8463 | 94257.3443 | 5.59 | 5.59 | 7.9074 | 24.2% | 24.2% | 35.53% | 70.2 | 70.2 | 56.6862 | 11 | 195
4560800% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 4892.5596 | 94665.0576 | 5.59 | 5.59 | 7.8971 | 24.2% | 24.2% | 35.46% | 70.2 | 70.2 | 56.7551 | 12 | 196
4560900% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 5300.2729 | 95072.7709 | 5.59 | 5.59 | 7.887 | 24.2% | 24.2% | 35.39% | 70.2 | 70.2 | 56.8234 | 13 | 197
4561000% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 5707.9862 | 95480.4842 | 5.59 | 5.59 | 7.8769 | 24.2% | 24.2% | 35.32% | 70.2 | 70.2 | 56.8909 | 14 | 198
4561100% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 6115.6995 | 95888.1975 | 5.59 | 5.59 | 7.8669 | 24.2% | 24.2% | 35.25% | 70.2 | 70.2 | 56.9578 | 15 | 199
4561200% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 6523.4128 | 96295.9108 | 5.59 | 5.59 | 7.857 | 24.2% | 24.2% | 35.18% | 70.2 | 70.2 | 57.024 | 16 | 200
4561300% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 6931.1261 | 96703.6241 | 5.59 | 5.59 | 7.8472 | 24.2% | 24.2% | 35.11% | 70.2 | 70.2 | 57.0896 | 17 | 201
4561400% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 7338.8394 | 97111.3374 | 5.59 | 5.59 | 7.8375 | 24.2% | 24.2% | 35.05% | 70.2 | 70.2 | 57.1545 | 18 | 202
4561500% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 7746.5527 | 97519.0507 | 5.59 | 5.59 | 7.8278 | 24.2% | 24.2% | 34.98% | 70.2 | 70.2 | 57.2187 | 19 | 203
4561600% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 8154.266 | 97926.764 | 5.59 | 5.59 | 7.8182 | 24.2% | 24.2% | 34.92% | 70.2 | 70.2 | 57.2824 | 20 | 204
4561700% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 8561.9793 | 98334.4773 | 5.59 | 5.59 | 7.8088 | 24.2% | 24.2% | 34.85% | 70.2 | 70.2 | 57.3454 | 21 | 205
4561800% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 8969.6926 | 98742.1906 | 5.59 | 5.59 | 7.7994 | 24.2% | 24.2% | 34.79% | 70.2 | 70.2 | 57.4078 | 22 | 206
4561900% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 9377.4059 | 99149.9039 | 5.59 | 5.59 | 7.79 | 24.2% | 24.2% | 34.73% | 70.2 | 70.2 | 57.4696 | 23 | 207
4562000% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 9785.1192 | 99557.6172 | 5.59 | 5.59 | 7.7808 | 24.2% | 24.2% | 34.67% | 70.2 | 70.2 | 57.5308 | 24 | 208
4562100% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 10192.8325 | 99965.3305 | 5.59 | 5.59 | 7.7716 | 24.2% | 24.2% | 34.6% | 70.2 | 70.2 | 57.5914 | 25 | 209
4562200% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 10600.5458 | 100373.0438 | 5.59 | 5.59 | 7.7625 | 24.2% | 24.2% | 34.54% | 70.2 | 70.2 | 57.6514 | 26 | 210
4562300% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 11008.2591 | 100780.7571 | 5.59 | 5.59 | 7.7535 | 24.2% | 24.2% | 34.48% | 70.2 | 70.2 | 57.7109 | 27 | 211
4562400% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 11415.9724 | 101188.4704 | 5.59 | 5.59 | 7.7446 | 24.2% | 24.2% | 34.43% | 70.2 | 70.2 | 57.7698 | 28 | 212
4562500% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 11823.6857 | 101596.1837 | 5.59 | 5.59 | 7.7357 | 24.2% | 24.2% | 34.37% | 70.2 | 70.2 | 57.8282 | 29 | 213
4562600% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 12231.399 | 102003.897 | 5.59 | 5.59 | 7.7269 | 24.2% | 24.2% | 34.31% | 70.2 | 70.2 | 57.886 | 30 | 214
4562700% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 577.322 | 102581.219 | 6.99 | 6.99 | 7.7239 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 57.9433 | 1 | 215
4562800% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 1154.6441 | 103158.5411 | 6.99 | 6.99 | 7.7209 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 58 | 2 | 216
4562900% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 1731.9661 | 103735.8631 | 6.99 | 6.99 | 7.718 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 58.0562 | 3 | 217
4563000% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 2309.2881 | 104313.1851 | 6.99 | 6.99 | 7.715 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 58.1119 | 4 | 218
4563100% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 2886.6102 | 104890.5072 | 6.99 | 6.99 | 7.7121 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 58.1671 | 5 | 219
4563200% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 3463.9322 | 105467.8292 | 6.99 | 6.99 | 7.7092 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 58.2218 | 6 | 220
4563300% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 4041.2542 | 106045.1512 | 6.99 | 6.99 | 7.7064 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 58.276 | 7 | 221
4563400% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 4618.5763 | 106622.4733 | 6.99 | 6.99 | 7.7035 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 58.3297 | 8 | 222
4563500% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 5195.8983 | 107199.7953 | 6.99 | 6.99 | 7.7007 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 58.383 | 9 | 223
4563600% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 5773.2203 | 107777.1173 | 6.99 | 6.99 | 7.6979 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 58.4357 | 10 | 224
4563700% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 6350.5424 | 108354.4394 | 6.99 | 6.99 | 7.6951 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 58.488 | 11 | 225
4563800% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 6927.8644 | 108931.7614 | 6.99 | 6.99 | 7.6924 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 58.5398 | 12 | 226
4563900% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 7505.1864 | 109509.0834 | 6.99 | 6.99 | 7.6896 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 58.5912 | 13 | 227
4564000% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 8082.5085 | 110086.4055 | 6.99 | 6.99 | 7.6869 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 58.6421 | 14 | 228
4564100% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 8659.8305 | 110663.7275 | 6.99 | 6.99 | 7.6842 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 58.6926 | 15 | 229
4564200% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 9237.1525 | 111241.0495 | 6.99 | 6.99 | 7.6816 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 58.7426 | 16 | 230
4564300% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 9814.4745 | 111818.3715 | 6.99 | 6.99 | 7.6789 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 58.7922 | 17 | 231
4564400% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 10391.7966 | 112395.6936 | 6.99 | 6.99 | 7.6763 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 58.8414 | 18 | 232
4564500% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 10969.1186 | 112973.0156 | 6.99 | 6.99 | 7.6737 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 58.8901 | 19 | 233
4564600% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 11546.4406 | 113550.3376 | 6.99 | 6.99 | 7.6711 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 58.9385 | 20 | 234
4564700% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 12123.7627 | 114127.6597 | 6.99 | 6.99 | 7.6685 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 58.9864 | 21 | 235
4564800% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 12701.0847 | 114704.9817 | 6.99 | 6.99 | 7.666 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 59.0339 | 22 | 236
4564900% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 13278.4067 | 115282.3037 | 6.99 | 6.99 | 7.6634 | 34.27% | 34.27% | 34.3% | 70.2 | 70.2 | 59.081 | 23 | 237
4565000% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 13855.7288 | 115859.6258 | 6.99 | 6.99 | 7.6609 | 34.27% | 34.27% | 34.3% | 70.2 | 70.2 | 59.1277 | 24 | 238
4565100% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 14433.0508 | 116436.9478 | 6.99 | 6.99 | 7.6584 | 34.27% | 34.27% | 34.3% | 70.2 | 70.2 | 59.1741 | 25 | 239
4565200% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 15010.3728 | 117014.2698 | 6.99 | 6.99 | 7.656 | 34.27% | 34.27% | 34.3% | 70.2 | 70.2 | 59.22 | 26 | 240
4565300% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 15587.6949 | 117591.5919 | 6.99 | 6.99 | 7.6535 | 34.27% | 34.27% | 34.3% | 70.2 | 70.2 | 59.2656 | 27 | 241
4565400% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 16165.0169 | 118168.9139 | 6.99 | 6.99 | 7.6511 | 34.27% | 34.27% | 34.3% | 70.2 | 70.2 | 59.3107 | 28 | 242
4565500% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 16742.3389 | 118746.2359 | 6.99 | 6.99 | 7.6486 | 34.27% | 34.27% | 34.3% | 70.2 | 70.2 | 59.3556 | 29 | 243
4565600% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 17319.661 | 119323.558 | 6.99 | 6.99 | 7.6462 | 34.27% | 34.27% | 34.3% | 70.2 | 70.2 | 59.4 | 30 | 244
4565700% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 17896.983 | 119900.88 | 6.99 | 6.99 | 7.6439 | 34.27% | 34.27% | 34.3% | 70.2 | 70.2 | 59.4441 | 31 | 245
4565800% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 616.4625 | 120517.3425 | 6.74 | 6.74 | 7.6406 | 36.59% | 36.59% | 34.31% | 70.2 | 70.2 | 59.4878 | 1 | 246
4565900% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 1232.925 | 121133.805 | 6.74 | 6.74 | 7.6373 | 36.59% | 36.59% | 34.33% | 70.2 | 70.2 | 59.5312 | 2 | 247
4566000% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 1849.3875 | 121750.2675 | 6.74 | 6.74 | 7.6341 | 36.59% | 36.59% | 34.34% | 70.2 | 70.2 | 59.5742 | 3 | 248
4566100% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 2465.8501 | 122366.7301 | 6.74 | 6.74 | 7.6309 | 36.59% | 36.59% | 34.35% | 70.2 | 70.2 | 59.6169 | 4 | 249
4566200% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 3082.3126 | 122983.1926 | 6.74 | 6.74 | 7.6277 | 36.59% | 36.59% | 34.36% | 70.2 | 70.2 | 59.6592 | 5 | 250
4566300% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 3698.7751 | 123599.6551 | 6.74 | 6.74 | 7.6246 | 36.59% | 36.59% | 34.37% | 70.2 | 70.2 | 59.7012 | 6 | 251
4566400% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 4315.2376 | 124216.1176 | 6.74 | 6.74 | 7.6214 | 36.59% | 36.59% | 34.38% | 70.2 | 70.2 | 59.7429 | 7 | 252
4566500% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 4931.7001 | 124832.5801 | 6.74 | 6.74 | 7.6183 | 36.59% | 36.59% | 34.39% | 70.2 | 70.2 | 59.7842 | 8 | 253
4566600% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 5548.1626 | 125449.0426 | 6.74 | 6.74 | 7.6152 | 36.59% | 36.59% | 34.4% | 70.2 | 70.2 | 59.8252 | 9 | 254
4566700% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 6164.6252 | 126065.5052 | 6.74 | 6.74 | 7.6121 | 36.59% | 36.59% | 34.41% | 70.2 | 70.2 | 59.8659 | 10 | 255
4566800% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 6781.0877 | 126681.9677 | 6.74 | 6.74 | 7.6091 | 36.59% | 36.59% | 34.42% | 70.2 | 70.2 | 59.9063 | 11 | 256
4566900% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 7397.5502 | 127298.4302 | 6.74 | 6.74 | 7.6061 | 36.59% | 36.59% | 34.43% | 70.2 | 70.2 | 59.9463 | 12 | 257
4567000% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 8014.0127 | 127914.8927 | 6.74 | 6.74 | 7.6031 | 36.59% | 36.59% | 34.44% | 70.2 | 70.2 | 59.986 | 13 | 258
4567100% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 8630.4752 | 128531.3552 | 6.74 | 6.74 | 7.6001 | 36.59% | 36.59% | 34.45% | 70.2 | 70.2 | 60.0255 | 14 | 259
4567200% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 9246.9377 | 129147.8177 | 6.74 | 6.74 | 7.5971 | 36.59% | 36.59% | 34.46% | 70.2 | 70.2 | 60.0646 | 15 | 260
4567300% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 9863.4003 | 129764.2803 | 6.74 | 6.74 | 7.5942 | 36.59% | 36.59% | 34.47% | 70.2 | 70.2 | 60.1034 | 16 | 261
4567400% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 10479.8628 | 130380.7428 | 6.74 | 6.74 | 7.5912 | 36.59% | 36.59% | 34.48% | 70.2 | 70.2 | 60.142 | 17 | 262
4567500% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 11096.3253 | 130997.2053 | 6.74 | 6.74 | 7.5883 | 36.59% | 36.59% | 34.49% | 70.2 | 70.2 | 60.1802 | 18 | 263
4567600% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 11712.7878 | 131613.6678 | 6.74 | 6.74 | 7.5854 | 36.59% | 36.59% | 34.5% | 70.2 | 70.2 | 60.2182 | 19 | 264
4567700% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 12329.2503 | 132230.1303 | 6.74 | 6.74 | 7.5826 | 36.59% | 36.59% | 34.5% | 70.2 | 70.2 | 60.2558 | 20 | 265
4567800% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 12945.7128 | 132846.5928 | 6.74 | 6.74 | 7.5797 | 36.59% | 36.59% | 34.51% | 70.2 | 70.2 | 60.2932 | 21 | 266
4567900% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 13562.1754 | 133463.0554 | 6.74 | 6.74 | 7.5769 | 36.59% | 36.59% | 34.52% | 70.2 | 70.2 | 60.3303 | 22 | 267
4568000% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 14178.6379 | 134079.5179 | 6.74 | 6.74 | 7.5741 | 36.59% | 36.59% | 34.53% | 70.2 | 70.2 | 60.3672 | 23 | 268
4568100% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 14795.1004 | 134695.9804 | 6.74 | 6.74 | 7.5713 | 36.59% | 36.59% | 34.54% | 70.2 | 70.2 | 60.4037 | 24 | 269
4568200% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 15411.5629 | 135312.4429 | 6.74 | 6.74 | 7.5685 | 36.59% | 36.59% | 34.55% | 70.2 | 70.2 | 60.44 | 25 | 270
4568300% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 16028.0254 | 135928.9054 | 6.74 | 6.74 | 7.5658 | 36.59% | 36.59% | 34.56% | 70.2 | 70.2 | 60.476 | 26 | 271
4568400% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 16644.4879 | 136545.3679 | 6.74 | 6.74 | 7.563 | 36.59% | 36.59% | 34.57% | 70.2 | 70.2 | 60.5118 | 27 | 272
4568500% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 17260.9505 | 137161.8305 | 6.74 | 6.74 | 7.5603 | 36.59% | 36.59% | 34.58% | 70.2 | 70.2 | 60.5473 | 28 | 273
4568600% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 17877.413 | 137778.293 | 6.74 | 6.74 | 7.5576 | 36.59% | 36.59% | 34.58% | 70.2 | 70.2 | 60.5825 | 29 | 274
4568700% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 18493.8755 | 138394.7555 | 6.74 | 6.74 | 7.555 | 36.59% | 36.59% | 34.59% | 70.2 | 70.2 | 60.6175 | 30 | 275
4568800% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 19110.338 | 139011.218 | 6.74 | 6.74 | 7.5523 | 36.59% | 36.59% | 34.6% | 70.2 | 70.2 | 60.6522 | 31 | 276
4568900% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 525.1347 | 139536.3527 | 7.3 | 7.3 | 7.5515 | 31.17% | 31.17% | 34.59% | 70.2 | 70.2 | 60.6866 | 1 | 277
4569000% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 1050.2694 | 140061.4874 | 7.3 | 7.3 | 7.5506 | 31.17% | 31.17% | 34.57% | 70.2 | 70.2 | 60.7209 | 2 | 278
4569100% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 1575.4041 | 140586.6221 | 7.3 | 7.3 | 7.5498 | 31.17% | 31.17% | 34.56% | 70.2 | 70.2 | 60.7548 | 3 | 279
4569200% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 2100.5389 | 141111.7569 | 7.3 | 7.3 | 7.549 | 31.17% | 31.17% | 34.54% | 70.2 | 70.2 | 60.7886 | 4 | 280
4569300% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 2625.6736 | 141636.8916 | 7.3 | 7.3 | 7.5482 | 31.17% | 31.17% | 34.53% | 70.2 | 70.2 | 60.8221 | 5 | 281
4569400% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 3150.8083 | 142162.0263 | 7.3 | 7.3 | 7.5474 | 31.17% | 31.17% | 34.52% | 70.2 | 70.2 | 60.8553 | 6 | 282
4569500% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 3675.943 | 142687.161 | 7.3 | 7.3 | 7.5466 | 31.17% | 31.17% | 34.5% | 70.2 | 70.2 | 60.8883 | 7 | 283
4569600% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 4201.0777 | 143212.2957 | 7.3 | 7.3 | 7.5459 | 31.17% | 31.17% | 34.49% | 70.2 | 70.2 | 60.9211 | 8 | 284
4569700% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 4726.2124 | 143737.4304 | 7.3 | 7.3 | 7.5451 | 31.17% | 31.17% | 34.48% | 70.2 | 70.2 | 60.9537 | 9 | 285
4569800% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 5251.3471 | 144262.5651 | 7.3 | 7.3 | 7.5443 | 31.17% | 31.17% | 34.46% | 70.2 | 70.2 | 60.986 | 10 | 286
4569900% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 5776.4819 | 144787.6999 | 7.3 | 7.3 | 7.5435 | 31.17% | 31.17% | 34.45% | 70.2 | 70.2 | 61.0181 | 11 | 287
4570000% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 6301.6166 | 145312.8346 | 7.3 | 7.3 | 7.5428 | 31.17% | 31.17% | 34.44% | 70.2 | 70.2 | 61.05 | 12 | 288
4570100% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 6826.7513 | 145837.9693 | 7.3 | 7.3 | 7.542 | 31.17% | 31.17% | 34.42% | 70.2 | 70.2 | 61.0817 | 13 | 289
4570200% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 7351.886 | 146363.104 | 7.3 | 7.3 | 7.5412 | 31.17% | 31.17% | 34.41% | 70.2 | 70.2 | 61.1131 | 14 | 290
4570300% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 7877.0207 | 146888.2387 | 7.3 | 7.3 | 7.5405 | 31.17% | 31.17% | 34.4% | 70.2 | 70.2 | 61.1443 | 15 | 291
4570400% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 8402.1554 | 147413.3734 | 7.3 | 7.3 | 7.5398 | 31.17% | 31.17% | 34.38% | 70.2 | 70.2 | 61.1753 | 16 | 292
4570500% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 8927.2901 | 147938.5081 | 7.3 | 7.3 | 7.539 | 31.17% | 31.17% | 34.37% | 70.2 | 70.2 | 61.2061 | 17 | 293
4570600% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 9452.4249 | 148463.6429 | 7.3 | 7.3 | 7.5383 | 31.17% | 31.17% | 34.36% | 70.2 | 70.2 | 61.2367 | 18 | 294
4570700% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 9977.5596 | 148988.7776 | 7.3 | 7.3 | 7.5375 | 31.17% | 31.17% | 34.35% | 70.2 | 70.2 | 61.2671 | 19 | 295
4570800% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 10502.6943 | 149513.9123 | 7.3 | 7.3 | 7.5368 | 31.17% | 31.17% | 34.34% | 70.2 | 70.2 | 61.2973 | 20 | 296
4570900% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 11027.829 | 150039.047 | 7.3 | 7.3 | 7.5361 | 31.17% | 31.17% | 34.32% | 70.2 | 70.2 | 61.3273 | 21 | 297
4571000% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 11552.9637 | 150564.1817 | 7.3 | 7.3 | 7.5354 | 31.17% | 31.17% | 34.31% | 70.2 | 70.2 | 61.357 | 22 | 298
4571100% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 12078.0984 | 151089.3164 | 7.3 | 7.3 | 7.5347 | 31.17% | 31.17% | 34.3% | 70.2 | 70.2 | 61.3866 | 23 | 299
4571200% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 12603.2331 | 151614.4511 | 7.3 | 7.3 | 7.5339 | 31.17% | 31.17% | 34.29% | 70.2 | 70.2 | 61.416 | 24 | 300
4571300% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 13128.3679 | 152139.5859 | 7.3 | 7.3 | 7.5332 | 31.17% | 31.17% | 34.27% | 70.2 | 70.2 | 61.4452 | 25 | 301
4571400% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 13653.5026 | 152664.7206 | 7.3 | 7.3 | 7.5325 | 31.17% | 31.17% | 34.26% | 70.2 | 70.2 | 61.4742 | 26 | 302
4571500% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 14178.6373 | 153189.8553 | 7.3 | 7.3 | 7.5318 | 31.17% | 31.17% | 34.25% | 70.2 | 70.2 | 61.503 | 27 | 303
4571600% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 14703.772 | 153714.99 | 7.3 | 7.3 | 7.5311 | 31.17% | 31.17% | 34.24% | 70.2 | 70.2 | 61.5316 | 28 | 304
4571700% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 632.771 | 154347.761 | 7.28 | 7.28 | 7.5304 | 37.56% | 37.56% | 34.25% | 70.2 | 70.2 | 61.56 | 1 | 305
4571800% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 1265.5421 | 154980.5321 | 7.28 | 7.28 | 7.5296 | 37.56% | 37.56% | 34.26% | 70.2 | 70.2 | 61.5882 | 2 | 306
4571900% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 1898.3131 | 155613.3031 | 7.28 | 7.28 | 7.5289 | 37.56% | 37.56% | 34.28% | 70.2 | 70.2 | 61.6163 | 3 | 307
4572000% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 2531.0841 | 156246.0741 | 7.28 | 7.28 | 7.5282 | 37.56% | 37.56% | 34.29% | 70.2 | 70.2 | 61.6442 | 4 | 308
4572100% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 3163.8552 | 156878.8452 | 7.28 | 7.28 | 7.5274 | 37.56% | 37.56% | 34.3% | 70.2 | 70.2 | 61.6718 | 5 | 309
4572200% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 3796.6262 | 157511.6162 | 7.28 | 7.28 | 7.5267 | 37.56% | 37.56% | 34.31% | 70.2 | 70.2 | 61.6994 | 6 | 310
4572300% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 4429.3972 | 158144.3872 | 7.28 | 7.28 | 7.526 | 37.56% | 37.56% | 34.32% | 70.2 | 70.2 | 61.7267 | 7 | 311
4572400% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 5062.1683 | 158777.1583 | 7.28 | 7.28 | 7.5253 | 37.56% | 37.56% | 34.34% | 70.2 | 70.2 | 61.7538 | 8 | 312
4572500% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 5694.9393 | 159409.9293 | 7.28 | 7.28 | 7.5245 | 37.56% | 37.56% | 34.35% | 70.2 | 70.2 | 61.7808 | 9 | 313
4572600% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 6327.7103 | 160042.7003 | 7.28 | 7.28 | 7.5238 | 37.56% | 37.56% | 34.36% | 70.2 | 70.2 | 61.8076 | 10 | 314
4572700% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 6960.4814 | 160675.4714 | 7.28 | 7.28 | 7.5231 | 37.56% | 37.56% | 34.37% | 70.2 | 70.2 | 61.8343 | 11 | 315
4572800% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 7593.2524 | 161308.2424 | 7.28 | 7.28 | 7.5224 | 37.56% | 37.56% | 34.38% | 70.2 | 70.2 | 61.8608 | 12 | 316
4572900% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 8226.0234 | 161941.0134 | 7.28 | 7.28 | 7.5217 | 37.56% | 37.56% | 34.39% | 70.2 | 70.2 | 61.8871 | 13 | 317
4573000% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 8858.7945 | 162573.7845 | 7.28 | 7.28 | 7.521 | 37.56% | 37.56% | 34.41% | 70.2 | 70.2 | 61.9132 | 14 | 318
4573100% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 9491.5655 | 163206.5555 | 7.28 | 7.28 | 7.5203 | 37.56% | 37.56% | 34.42% | 70.2 | 70.2 | 61.9392 | 15 | 319
4573200% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 10124.3365 | 163839.3265 | 7.28 | 7.28 | 7.5197 | 37.56% | 37.56% | 34.43% | 70.2 | 70.2 | 61.965 | 16 | 320
4573300% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 10757.1075 | 164472.0975 | 7.28 | 7.28 | 7.519 | 37.56% | 37.56% | 34.44% | 70.2 | 70.2 | 61.9907 | 17 | 321
4573400% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 11389.8786 | 165104.8686 | 7.28 | 7.28 | 7.5183 | 37.56% | 37.56% | 34.45% | 70.2 | 70.2 | 62.0161 | 18 | 322
4573500% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 12022.6496 | 165737.6396 | 7.28 | 7.28 | 7.5176 | 37.56% | 37.56% | 34.46% | 70.2 | 70.2 | 62.0415 | 19 | 323
4573600% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 12655.4206 | 166370.4106 | 7.28 | 7.28 | 7.5169 | 37.56% | 37.56% | 34.47% | 70.2 | 70.2 | 62.0667 | 20 | 324
4573700% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 13288.1917 | 167003.1817 | 7.28 | 7.28 | 7.5163 | 37.56% | 37.56% | 34.48% | 70.2 | 70.2 | 62.0917 | 21 | 325
4573800% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 13920.9627 | 167635.9527 | 7.28 | 7.28 | 7.5156 | 37.56% | 37.56% | 34.49% | 70.2 | 70.2 | 62.1166 | 22 | 326
4573900% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 14553.7337 | 168268.7237 | 7.28 | 7.28 | 7.515 | 37.56% | 37.56% | 34.5% | 70.2 | 70.2 | 62.1413 | 23 | 327
4574000% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 15186.5048 | 168901.4948 | 7.28 | 7.28 | 7.5143 | 37.56% | 37.56% | 34.51% | 70.2 | 70.2 | 62.1659 | 24 | 328
4574100% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 15819.2758 | 169534.2658 | 7.28 | 7.28 | 7.5136 | 37.56% | 37.56% | 34.52% | 70.2 | 70.2 | 62.1903 | 25 | 329
4574200% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 16452.0468 | 170167.0368 | 7.28 | 7.28 | 7.513 | 37.56% | 37.56% | 34.53% | 70.2 | 70.2 | 62.2145 | 26 | 330
4574300% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 17084.8179 | 170799.8079 | 7.28 | 7.28 | 7.5124 | 37.56% | 37.56% | 34.55% | 70.2 | 70.2 | 62.2387 | 27 | 331
4574400% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 17717.5889 | 171432.5789 | 7.28 | 7.28 | 7.5117 | 37.56% | 37.56% | 34.56% | 70.2 | 70.2 | 62.2627 | 28 | 332
4574500% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 18350.3599 | 172065.3499 | 7.28 | 7.28 | 7.5111 | 37.56% | 37.56% | 34.57% | 70.2 | 70.2 | 62.2865 | 29 | 333
4574600% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 18983.131 | 172698.121 | 7.28 | 7.28 | 7.5104 | 37.56% | 37.56% | 34.58% | 70.2 | 70.2 | 62.3102 | 30 | 334
4574700% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 19615.902 | 173330.892 | 7.28 | 7.28 | 7.5098 | 37.56% | 37.56% | 34.59% | 70.2 | 70.2 | 62.3337 | 31 | 335
Formulas:
Month = [Date]-DAY([Date])+1
Days = DAY(EOMONTH(Modelling[[#This Row],[Date]],0))

## Basic Data (hidden)
[15 empty] | No. | Senvion Control | No._1 | Senvion Control M | Type | Brakg. Prg. | Alarm | Auto Reset | Avail. grp. | System
| Generator | Consumer | Capacity | % Plant Equiva. Weightage | Feeder | TX | USS | MY |  |  |  | Fault Category |  |  | 0 | System OK | 0 | System OK | Info | 0 |  | 20 | 32
O2_01 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F1 | TX1 | O2_01 |  | Total Capacity | 70.2 | Open | WTG | IG | EG | 10 | Negative power, too little wind | 240 | Awaiting wind | Info | 50 |  | 10 | 5
O2_02 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F1 | TX1 | O2_02 |  |  | 43 | Close | WTG Unscheduled Maintenance | IG Unscheduled Maintenance | EG Unscheduled Maintenance | 11 | Negative power, too little wind with icing | -- | -- | Info | 50 |  | 10 | 6
O2_03 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F1 | TX1 | O2_03 |  |  |  |  | WTG Breakdown Maintenance | IG Breakdown Maintenance | EG Breakdown Maintenance | 16 | Timeout start for icing | -- | -- | Info | 50 |  | 20 | 6
O2_04 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F2 | TX1 | O2_04 |  |  |  |  | WTG Scheduled Maintenance | IG Scheduled Maintenance | EG Scheduled Maintenance | 20 | Manual stop - on site | 13 | Manual stop | Info | 60 |  | 30 | 9
O2_05 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F1 | TX1 | O2_05 |  |  |  |  | WTG Environmental | IG Force Majeure | EG Force Majeure | 21 | Manual stop - remote | 11 | Stop via communica. | Info | 60 |  | 0 | 30
O2_06 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F2 | TX1 | O2_06 |  |  |  |  | WTG Force Majeure |  |  | 25 | Manual stop without login | -- | -- | Info | 60 | X | 30 | 9
O2_07 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F2 | TX1 | O2_07 | [7 empty] | 28 | WTG stop | -- | -- | Info | 52 |  | 20 | 9
O2_08 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F2 | TX1 | O2_08 | [7 empty] | 30 | Wind sector stop | -- | -- | Info | 52 |  | 20 | 5
O2_09 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F1 | TX1 | O2_09 | [7 empty] | 45 | Limiting wind speed exceeded | -- | -- | Info | 0 |  | 20 | 27
O2_10 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F1 | TX1 | O2_10 | [7 empty] | 46 | Max. wind dir. deviation high wind sp. | -- | -- | Error | 52 |  | 20 | 5 | Nacelle
O2_11 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F1 | TX1 | O2_11 | [7 empty] | 47 | Max. windspeed BP50 | -- | -- | Info | 52 |  | 20 | 5
O2_12 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F1 | TX1 | O2_12 | [7 empty] | 50 | Night operation | 1541 | Night operation | Info | 52 |  | 20 | 2
O2_13 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F1 | TX1 | O2_13 | [7 empty] | 53 | Wind dir.dev. level 1 | -- | -- | Error | 52 |  | 20 | 5 | Nacelle
O2_14 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F1 | TX1 | O2_14 | [7 empty] | 54 | WTG shutdown - pitch angle & stormp. Ignored | -- | -- | Info | 180 | X | 20 | 1
O2_15 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F1 | TX1 | O2_15 | [7 empty] | 55 | WTG shut down | 1754 | WTG shutdown | Info | 52 |  | 20 | 1
O2_16 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F1 | TX1 | O2_16 | [7 empty] | 57 | Reduced power active | -- | -- | Info | 0 |  | 20 | 32
O2_17 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F2 | TX1 | O2_17 | [7 empty] | 58 | Wind dir.dev. level 2 | -- | -- | Error | 52 |  | 20 | 5 | Nacelle
O2_18 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F2 | TX1 | O2_18 | [7 empty] | 59 | Max. acceleration | -- | -- | Warning | 0 | X | 20 | 28
O2_19 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F2 | TX1 | O2_19 | [7 empty] | 60 | Wind > power | 203 | Wind > power | Error | 52 | X | 0 | 15 | Wind Sensor
O2_20 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F1 | TX1 | O2_20 | [7 empty] | 61 | Wind < power | 202 | Wind < power | Error | 52 | X | 0 | 15 | Wind Sensor
O2_21 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F2 | TX1 | O2_21 | [7 empty] | 62 | Extreme gust | 213 | Extreme gust | Info | 20 |  | 30 | 28
O2_22 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F2 | TX1 | O2_22 | [7 empty] | 64 | Max. wind speed | 250 | Wind > max. | Info | 52 |  | 20 | 5
O2_23 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F2 | TX1 | O2_23 | [7 empty] | 65 | Absence of wind during run-up | 204 | Free wheel->cut in G | Info | 50 |  | 20 | 28
O2_24 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F2 | TX1 | O2_24 | [7 empty] | 70 | Icing (nacelle ice sensor) | 206 | Ice warning | Info | 0 |  | 30 | 28
O2_25 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F2 | TX1 | O2_25 | [7 empty] | 71 | Outdoor temperature low | 200 | Outdoor temp. low | Info | 52 |  | 30 | 6
O2_26 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F2 | TX1 | O2_26 | [7 empty] | 72 | Outdoor temperature high | 201 | Outdoor temp. high | Info | 52 |  | 30 | 6
[15 empty] | 75 | Reduced power gearbox | 27 | Reduced power | Warning | 0 |  | 20 | 27
[15 empty] | 76 | Reduced power generator | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 77 | Reduced power transformer | 2024 | [P] reduced trafo | Warning | 0 | X | 20 | 27
[15 empty] | 81 | Outdoor temp. extremely low | -- | -- | Warning | 0 |  | 30 | 27
[15 empty] | 85 | Outdoor temp.>working range | 246 | -- | Info | 0 |  | 20 | 27
[15 empty] | 86 | 4-20mA outside temp. nacelle 1 | -- | -- | Error | 52 | X | 20 | 21 | Nacelle
[15 empty] | 87 | 4-20mA outside temp. nacelle 2 | -- | -- | Error | 52 | X | 20 | 21 | Nacelle
[15 empty] | 88 | Outs.temp. nacelle implaus. | -- | -- | Error | 52 | X | 20 | 21 | Nacelle
[15 empty] | 89 | Nacelle outs/inside temp. comp implausible | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 110 | Emergency stop top box | 16 | Emer.stop cont.panel | Info | 190 | X | 0 | 11
[15 empty] | 111 | Emergency stop nacelle | 92 | Emer. stop nacelle | Info | 190 | X | 0 | 11
[15 empty] | 115 | Emergency stop converter | 1404 | Freq.conv. emer.stop | Info | 190 | X | 0 | 12
[15 empty] | 117 | Emergency stop base box | 2150 | Emer. stop bottombox | Info | 190 | X | 0 | 12
[15 empty] | 120 | Conv. emergency stop 2 | -- | -- | Info | 190 | X | 0 | 12
Wind_F1 | TQGXIIPL | GEDA | 35.1 | 50% | [10 empty] | 121 | Emer.stop tower base | -- | -- | Info | 190 | X | 0 | 12
Wind_F2 | TQGXIIPL | GEDA | 35.1 | 50% | [10 empty] | 151 | SLC app. not running | -- | -- | Info | 52 |  | 20 | 15
O2_01 | TQGXIIPL | GEDA | 2.7 | 3.846% | [10 empty] | 152 | SLC app. not in SAFE mode | -- | -- | Error | 52 | X | 20 | 15 | Safety System
O2_02 | TQGXIIPL | GEDA | 2.7 | 3.846% | [10 empty] | 153 | SLC SF max. cable winding | -- | -- | Error | 75 | X | 0 | 15 | Safety System
O2_03 | TQGXIIPL | GEDA | 2.7 | 3.846% | [10 empty] | 154 | SLC SF generator temperature | -- | -- | Error | 75 | X | 0 | 15 | Safety System
O2_04 | TQGXIIPL | GEDA | 2.7 | 3.846% | [10 empty] | 156 | SLC SF overspeed | -- | -- | Error | 190 | X | 0 | 15 | Safety System
O2_05 | TQGXIIPL | GEDA | 2.7 | 3.846% | [10 empty] | 157 | SLC SF max. tower oscillation | -- | -- | Error | 180 | X | 0 | 15 | Safety System
O2_06 | TQGXIIPL | GEDA | 2.7 | 3.846% | [10 empty] | 158 | SLC SF max. rotor brake pad temp. | -- | -- | Error | 75 | X | 0 | 15 | Safety System
O2_07 | TQGXIIPL | GEDA | 2.7 | 3.846% | [10 empty] | 159 | SLC SF emergency stop | -- | -- | Error | 190 | X | 0 | 15 | Safety System
O2_08 | TQGXIIPL | GEDA | 2.7 | 3.846% | [10 empty] | 170 | SLC MF brake request HC | -- | -- | Error | 170 | X | 20 | 15 | Safety System
O2_09 | TQGXIIPL | GEDA | 2.7 | 3.846% | [10 empty] | 171 | SLC MF converter grid disconnection | -- | -- | Error | 75 | X | 20 | 15 | Converter system
O2_10 | TQGXIIPL | GEDA | 2.7 | 3.846% | [10 empty] | 172 | SLC MF torque protection | -- | -- | Error | 75 | X | 20 | 15 | Safety System
O2_11 | TQGXIIPL | GEDA | 2.7 | 3.846% | [10 empty] | 173 | SLC MF max. tower oscillation analog | -- | -- | Error | 75 | X | 20 | 15 | Safety System
O2_12 | TQGXIIPL | GEDA | 2.7 | 3.846% | [10 empty] | 175 | SLC error | -- | -- | Error | 60 | X | 0 | 15 | Safety System
O2_13 | TQGXIIPL | GEDA | 2.7 | 3.846% | [10 empty] | 176 | SLC warning | -- | -- | Warning | 0 | X | 0 | 27
O2_14 | TQGXIIPL | GEDA | 2.7 | 3.846% | [10 empty] | 177 | SLC MF blade regulation control | -- | -- | Error | 180 | X | 0 | 15 | Safety System
O2_15 | TQGXIIPL | GEDA | 2.7 | 3.846% | [10 empty] | 178 | SLC MF safe operation speed limit | -- | -- | Error | 75 | X | 20 | 15 | Safety System
O2_16 | TQGXIIPL | GEDA | 2.7 | 3.846% | [10 empty] | 181 | SLC implaus. speed | -- | -- | Error | 52 | X | 0 | 15 | Safety System
O2_17 | TQGXIIPL | GEDA | 2.7 | 3.846% | [10 empty] | 182 | SLC interface error | -- | -- | Error | 52 | X | 0 | 15 | Safety System
O2_18 | TQGXIIPL | GEDA | 2.7 | 3.846% | [10 empty] | 183 | SLC run-time limit active | -- | -- | Info | 0 | X | 20 | 28
O2_19 | TQGXIIPL | GEDA | 2.7 | 3.846% | [10 empty] | 200 | Release manual pitch | 7 | Turbine is serviced | Info | 60 |  | 20 | 9
O2_20 | TQGXIIPL | GEDA | 2.7 | 3.846% | [10 empty] | 201 | Manual pitch active | -- | -- | Info | 180 |  | 20 | 9
O2_21 | TQGXIIPL | GEDA | 2.7 | 3.846% | [10 empty] | 205 | Pitch service mode | -- | -- | Info | 60 |  | 20 | 9
O2_22 | TQGXIIPL | GEDA | 2.7 | 3.846% | [10 empty] | 210 | Manual brake | 451 | Manual brake | Info | 60 |  | 20 | 9
O2_23 | TQGXIIPL | GEDA | 2.7 | 3.846% | [10 empty] | 220 | Sound characteristic A active | 2174 | Noise reduct.1 start | Info | 0 |  | 20 | 28
O2_24 | TQGXIIPL | GEDA | 2.7 | 3.846% | [10 empty] | 221 | Sound characteristic C active | -- | -- | Info | 0 |  | 20 | 28
O2_25 | TQGXIIPL | GEDA | 2.7 | 3.846% | [10 empty] | 225 | Sound characteristic B active | 2176 | Noise reduct.2 start | Info | 0 |  | 20 | 28
O2_26 | TQGXIIPL | GEDA | 2.7 | 3.846% | [10 empty] | 226 | Sound characteristic D active | -- | -- | Info | 0 |  | 20 | 28
[15 empty] | 228 | Noise reduction stop | -- | -- | Info | 52 |  | 20 | 2
[15 empty] | 229 | Bat protection active | -- | -- | Info | 52 |  | 20 | 28
[15 empty] | 245 | Parameterized P red. | -- | -- | Info | 0 |  | 20 | 28
[15 empty] | 246 | Parameterized speed red. | -- | -- | Info | 0 |  | 20 | 28
[15 empty] | 248 | Red. op. soft cut out | -- | -- | Info | 0 |  | 20 | 28
[15 empty] | 249 | Soft cut out par. implausible | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 250 | Update active | -- | -- | Info | 0 |  | 20 | 28
[15 empty] | 251 | Stop for man./aut. reboot | -- | -- | Info | 60 |  | 20 | 28
[15 empty] | 252 | Update failed | -- | -- | Warning | 0 |  | 20 | 28
[15 empty] | 253 | Manual reboot | -- | -- | Info | 60 |  | 20 | 28
[15 empty] | 254 | Man. shutdown error | -- | -- | Error | 60 |  | 0 | 28
TX1 | TQGXIIPL | GEDA | 70 | 100% | [10 empty] | 305 | Brake control | 424 | Brake control | Error | 52 | X | 0 | 23
Line1 | TQGXIIPL | GEDA | 70 | 100% | [10 empty] | 308 | Max. braking time BP20 | -- | -- | Error | 75 | X | 0 | 18
[15 empty] | 310 | Max. braking time BP50 | 431 | B50 brake time > max | Error | 180 | X | 0 | 18
[15 empty] | 320 | Max. braking time BP52 | 495 | B52 brake time>max. | Error | 180 | X | 0 | 18
[15 empty] | 325 | Max. braking time BP60 | 494 | B60 brake time>max. | Error | 180 | X | 0 | 18
[15 empty] | 330 | Max. braking time BP75 | 448 | B75 brake time > max | Error | 180 | X | 0 | 18
[15 empty] | 331 | Parameter setting BP75 implausible | -- | -- | Error | 52 | X | 20 | 15
[15 empty] | 332 | Max. braking time BP170 | 1824 | B170 brake time >max. | Error | 190 | X | 0 | 18
[15 empty] | 335 | Max. braking time BP180 | 490 | B180 brake time>max. | Error | 190 | X | 0 | 18
[15 empty] | 340 | Max. braking time BP190 | 491 | B190 brake time>max. | Error | 190 | X | 0 | 18
[15 empty] | 360 | Timeout systemtest 1 | 1540 | T.out selftest no. 1 | Error | 52 | X | 0 | 21
[15 empty] | 365 | Timeout systemtest 2 | -- | -- | Error | 52 | X | 0 | 21
[15 empty] | 370 | Timeout systemtest 3 | -- | -- | Error | 52 | X | 0 | 21
[15 empty] | 400 | Manual operation | 26 | Manual operation | Info | 0 |  | 0 | 27
[15 empty] | 402 | Semi-automatic operation | -- | -- | Info | 0 |  | 20 | 27
[15 empty] | 403 | PMU active power semi-aut. op. | -- | -- | Info | 0 |  | 20 | 32
[15 empty] | 404 | PMU react. power semi-aut. op. | -- | -- | Info | 0 |  | 20 | 32
[15 empty] | 405 | Stop manual operation | -- | -- | Info | 52 |  | 20 | 9
[15 empty] | 412 | Test brake program 190 | -- | -- | Info | 190 |  | 0 | 9
[15 empty] | 414 | Test brake program 180 | -- | -- | Info | 180 |  | 0 | 9
[15 empty] | 415 | Test brake program 170 | -- | -- | Info | 170 |  | 0 | 9
[15 empty] | 416 | Test brake program 75 | -- | -- | Info | 75 |  | 0 | 9
[15 empty] | 418 | Test brake program 60 | -- | -- | Info | 60 |  | 0 | 9
[15 empty] | 420 | Test brake program 52 | -- | -- | Info | 52 |  | 0 | 9
[15 empty] | 422 | Test brake program 50 | -- | -- | Info | 50 |  | 0 | 9
[15 empty] | 424 | Test brake program 20 | -- | -- | Info | 20 |  | 30 | 27
[15 empty] | 430 | No-load rotation active | -- | -- | Info | 75 |  | 20 | 28
[15 empty] | 435 | No speed development | -- | -- | Error | 180 | X | 0 | 15
[15 empty] | 440 | Repeating error BP 0 | -- | -- | Warning | 0 | X | 0 | 27
[15 empty] | 455 | Repeating error BP52 | -- | -- | Error | 52 | X | 0 | 25
[15 empty] | 460 | Repeating error BP60 | -- | -- | Error | 60 | X | 0 | 25
[15 empty] | 465 | Repeating error BP75 | -- | -- | Error | 75 | X | 0 | 25
[15 empty] | 468 | Repeating error BP170 | -- | -- | Error | 170 | X | 0 | 25
[15 empty] | 470 | Repeating error BP180 | -- | -- | Error | 180 | X | 0 | 25
[15 empty] | 475 | Repeating error BP190 | -- | -- | Error | 190 | X | 0 | 25
[15 empty] | 513 | Timeout bridging limit switches | -- | -- | Error | 52 | X | 0 | 18
[15 empty] | 515 | Pitch limit switches | 1130 | Pitch endstop switch | Error | 52 | X | 0 | 18 | Pitch system
[15 empty] | 516 | Pitch limit switch 1 | 1906 | Pitch endstop 1 | Error | 52 | X | 0 | 18 | Pitch system
[15 empty] | 517 | Pitch limit switch 2 | 1908 | Pitch endstop 2 | Error | 52 | X | 0 | 18 | Pitch system
[15 empty] | 518 | Pitch limit switch 3 | 1909 | Pitch endstop 3 | Error | 52 | X | 0 | 18 | Pitch system
[15 empty] | 520 | Overload axis 1 | 1150 | Pitch 1 current>max | Error | 52 | X | 0 | 18
[15 empty] | 525 | Overload axis 2 | 1151 | Pitch 2 current>max | Error | 52 | X | 0 | 18
[15 empty] | 530 | Overload axis 3 | 1152 | Pitch 3 current>max | Error | 52 | X | 0 | 18
[15 empty] | 550 | Pitch current asymmetry | 1156 | Pitch(M)current asym | Error | 52 | X | 0 | 18 | Pitch system
[15 empty] | 551 | Pitch motor current too high | -- | -- | Error | 52 | X | 0 | 18 | Pitch system
[15 empty] | 553 | Blade pitch deviation test | -- | -- | Error | 52 |  | 10 | 18 | Pitch system
[15 empty] | 555 | Pitch angle deviation | 1113 | Pitch angle diff. | Error | 52 |  | 10 | 18 | Pitch system
[15 empty] | 556 | Pitch deviation BP170 | -- | -- | Error | 52 | X | 0 | 18 | Pitch system
[15 empty] | 558 | Pitch deviation Pitch Back | -- | -- | Error | 52 | X | 0 | 18 | Pitch system
[15 empty] | 563 | Pitch too fast during fast pitch back | -- | -- | Error | 52 | X | 0 | 18 | Pitch system
[15 empty] | 564 | Bladeangle implausible | -- | -- | Error | 180 | X | 0 | 18 | Pitch system
[15 empty] | 565 | Max. windspeed bladeangle | 258 | Pitch angle>max.wind | Error | 52 |  | 30 | 5 | Pitch system
[15 empty] | 566 | Pitch too slow BP50 | -- | -- | Error | 180 | X | 0 | 18 | Pitch system
[15 empty] | 567 | Pitch too slow BP52 | -- | -- | Error | 180 | X | 0 | 18 | Pitch system
[15 empty] | 568 | Pitch too slow BP60 | -- | -- | Error | 180 | X | 0 | 18 | Pitch system
[15 empty] | 569 | Pitch too slow BP75 | -- | -- | Error | 170 | X | 0 | 18 | Pitch system
[15 empty] | 570 | Pitch too slow BP180 | -- | -- | Error | 190 | X | 0 | 18 | Pitch system
[15 empty] | 574 | Pitch too slow BP190 | -- | -- | Error | 190 | X | 0 | 18 | Pitch system
[15 empty] | 576 | Pitch too slow BP170 | -- | -- | Error | 190 | X | 0 | 18 | Pitch system
[15 empty] | 577 | Pitch too fast BP170 | -- | -- | Error | 52 | X | 0 | 18 | Pitch system
[15 empty] | 578 | Pitch set point slow hold time BP75 | -- | -- | Error | 75 | X | 0 | 16 | Pitch system
[15 empty] | 579 | Pitch too fast BP75 | -- | -- | Error | 75 | X | 0 | 18 | Pitch system
[15 empty] | 581 | Set point><actual value axis 1 | 1922 | Pitch setp.<>meas. 1 | Error | 180 | X | 0 | 18 | Pitch system
[15 empty] | 582 | Set point><actual value axis 2 | 1923 | Pitch setp.<>meas. 2 | Error | 180 | X | 0 | 18 | Pitch system
[15 empty] | 583 | Set point><actual value axis 3 | 1924 | Pitch setp.<>meas. 3 | Error | 180 | X | 0 | 18 | Pitch system
[15 empty] | 586 | Dev. single pitch angle targ. | -- | -- | Error | 170 |  | 20 | 16 | Pitch system
[15 empty] | 588 | Target >< act. coll. pitch angle | -- | -- | Error | 180 | X | 0 | 18 | Pitch system
[15 empty] | 589 | Targ. pitch angle coll. dev. | -- | -- | Error | 52 |  | 20 | 16 | Pitch system
[15 empty] | 592 | Great deviation blade pitches | -- | -- | Error | 180 | X | 0 | 18 | Pitch system
[15 empty] | 594 | Blade pitch check running | -- | -- | Info | 0 |  | 20 | 28
[15 empty] | 600 | Max. temp. motor axis 1 | 1147 | Pitch motor temp. 1 | Error | 52 |  | 30 | 18 | Pitch system
[15 empty] | 605 | Max. temp. motor axis 2 | 1148 | Pitch motor temp. 2 | Error | 52 |  | 30 | 18 | Pitch system
[15 empty] | 610 | Max. temp. motor axis 3 | 1149 | Pitch motor temp. 3 | Error | 52 |  | 30 | 18 | Pitch system
[15 empty] | 628 | Max. temp. pitch motor PTC | 1199 | Pitch(M) sub2 temp. | Error | 52 |  | 20 | 18 | Pitch system
[15 empty] | 630 | Overload fan pitch motor | 1173 | Th.rel.pitch(M) fan | Error | 52 | X | 20 | 18 | Pitch system
[15 empty] | 641 | Sim.angle E enc. <> act.angle 1 | -- | -- | Error | 180 | X | 0 | 18 | Pitch system
[15 empty] | 642 | Sim.angle E enc. <> act.angle 2 | -- | -- | Error | 180 | X | 0 | 18 | Pitch system
[15 empty] | 643 | Sim.angle E enc. <> act.angle 3 | -- | -- | Error | 180 | X | 0 | 18 | Pitch system
[15 empty] | 644 | Sim.angle D <> E enc. | -- | -- | Info | 0 |  | 0 | 27
[15 empty] | 650 | Pitch controller communication error | 1157 | Pitch ctrl.communic. | Error | 180 |  | 10 | 18 | Pitch Control system
[15 empty] | 652 | Pitch controller initialisation error | -- | -- | Error | 180 |  | 10 | 18 | Pitch Control system
[15 empty] | 653 | Blade load sensors comm.failure | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 654 | Blade load sensors firmware error | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 656 | Error pitch converter 1 | 1910 | Pitch ctrl. error 1 | Error | 180 | X | 20 | 18 | Pitch Control system
[15 empty] | 657 | Error pitch converter 2 | 1911 | Pitch ctrl. error 2 | Error | 180 | X | 20 | 18 | Pitch Control system
[15 empty] | 658 | Error pitch converter 3 | 1912 | Pitch ctrl. error 3 | Error | 180 | X | 20 | 18 | Pitch Control system
[15 empty] | 660 | Limit switches error 91° | 1159 | Pitch <> endstop | Error | 190 | X | 0 | 18 | Pitch Control system
[15 empty] | 664 | Pitch system temperature low | -- | -- | Info | 52 |  | 20 | 6
[15 empty] | 665 | Pitch error | 1161 | Pitch error | Error | 52 | X | 20 | 18 | Pitch Control system
[15 empty] | 666 | Pitch box temp. too low | -- | -- | Error | 52 | X | 20 | 18 | Pitch Control system
[15 empty] | 667 | Pitch box temp. implaus. | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 668 | Battery boxes overtemp. | -- | -- | Error | 52 | X | 0 | 18 | Pitch Battery system
[15 empty] | 669 | Battery boxes heating sys. fault | -- | -- | Error | 52 | X | 20 | 18 | Pitch Battery system
[15 empty] | 670 | Max. pitch speed encoder A | 1163 | Pitch motor rpm high | Error | 180 | X | 0 | 18 | Pitch Control system
[15 empty] | 672 | Max. pitch speed encoder B | -- | -- | Error | 180 | X | 0 | 18 | Pitch Control system
[15 empty] | 675 | Pitch measuring system 1><2 | 1166 | Pitchmeas.sys. 1<>2 | Error | 180 | X | 0 | 21 | Pitch Control system
[15 empty] | 679 | Pitch system temperature high | -- | -- | Error | 52 | X | 20 | 18 | Pitch Control system
[15 empty] | 681 | Limit switch error 95° axis 1 | -- | -- | Warning | 0 | X | 0 | 27
[15 empty] | 682 | Limit switch error 95° axis 2 | -- | -- | Warning | 0 | X | 0 | 27
[15 empty] | 683 | Limit switch error 95° axis 3 | -- | -- | Warning | 0 | X | 0 | 27
[15 empty] | 687 | Power failure pitch | 1931 | No grid in hub | Error | 75 | X | 20 | 24 | Pitch Battery system
[15 empty] | 691 | Targ. pitch angle implaus. | -- | -- | Error | 170 | X | 0 | 16 | Pitch Control system
[15 empty] | 693 | Coll. pitch targ.rate exceed. | -- | -- | Error | 170 | X | 0 | 16 | Pitch Control system
[15 empty] | 694 | Sel. pitch targ.rate exceed. | -- | -- | Error | 170 | X | 0 | 16 | Pitch Control system
[15 empty] | 695 | Hub temperature high | 1198 | Hub is too hot | Error | 52 |  | 30 | 22 | Pitch system
[15 empty] | 696 | Indiv. setp.pitch ang. offset incorr. | -- | -- | Error | 52 | X | 0 | 16 | Pitch system
[15 empty] | 697 | Timeout B sensor active | -- | -- | Info | 0 |  | 0 | 27
[15 empty] | 700 | Batt. undervoltage/overvoltage | 57 | Batt. voltage stop | Error | 52 | X | 0 | 18 | Pitch Battery system
[15 empty] | 707 | Stop battery test | 2408 | Battery Check | Info | 52 |  | 10 | 28
[15 empty] | 710 | Battery test | 95 | Battery test | Info | 180 |  | 10 | 28
[15 empty] | 711 | Battery monitoring axis 1 | -- | -- | Warning | 0 | X | 0 | 27
[15 empty] | 712 | Battery monitoring axis 2 | -- | -- | Warning | 0 | X | 0 | 27
[15 empty] | 713 | Battery monitoring axis 3 | -- | -- | Warning | 0 | X | 0 | 27
[15 empty] | 714 | Battery monitoring test interval | -- | -- | Warning | 0 | X | 0 | 27
[15 empty] | 715 | Charging circuit pitch | 1175 | Pitch bat. charger | Error | 52 | X | 0 | 18 | Pitch Battery system
[15 empty] | 716 | Battery charge cycle axis 1 error | -- | -- | Warning | 0 | X | 0 | 27
[15 empty] | 717 | Battery charge cycle axis 2 error | -- | -- | Warning | 0 | X | 0 | 27
[15 empty] | 718 | Battery charge cycle axis 3 error | -- | -- | Warning | 0 | X | 0 | 27
[15 empty] | 740 | Pitch back trigger by HC | -- | -- | Error | 170 |  | 20 | 18 | Pitch Battery system
[15 empty] | 741 | Battery drive trigger by HC | -- | -- | Error | 180 |  | 20 | 18 | Pitch Battery system
[15 empty] | 775 | Pitch heating mode | -- | -- | Info | 60 |  | 20 | 6
[15 empty] | 776 | Timeout pitch heating mode | -- | -- | Warning | 0 | X | 0 | 27
[15 empty] | 780 | Error bridging start-up | -- | -- | Error | 52 | X | 0 | 18 | Pitch Battery system
[15 empty] | 785 | Error brake resistor CHP | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 786 | Signal bridging start-up + CHP | -- | -- | Warning | 0 |  | 0 | 27
[15 empty] | 806 | High rotor speed hub | -- | -- | Error | 75 | X | 30 | 14
[15 empty] | 811 | Maximum rotor speed hub | -- | -- | Error | 190 | X | 0 | 14
[15 empty] | 821 | Rotor rotation direction hub | -- | -- | Info | 52 |  | 20 | 15
[15 empty] | 825 | Rotor speed hub<>gear.sp. | -- | -- | Error | 52 |  | 20 | 21
[15 empty] | 826 | Rotor speed hub<<>>gear.sp. | -- | -- | Error | 52 |  | 20 | 21
[15 empty] | 829 | Rotor speed SLC<>gear.sp. | -- | -- | Error | 52 |  | 20 | 21
[15 empty] | 830 | Calc. rotor position implausible | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 831 | Rotor position diff. | -- | -- | Error | 52 | X | 0 | 21
[15 empty] | 835 | Check determ. of rotor position | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 836 | Rotor pos. change not plausible | -- | -- | Error | 52 | X | 0 | 21
[15 empty] | 850 | Error lubrication pump pitch | 1932 | Hub lubrication | Warning | 0 |  | 20 | 27
[15 empty] | 855 | Stop after blade bear.lubr.dr. BP50 | -- | -- | Info | 50 |  | 20 | 28
[15 empty] | 856 | Stop after blade bear.lubr.dr. 90° | -- | -- | Info | 52 |  | 20 | 28
[15 empty] | 857 | Blade bear.lubr.dr. timeout | -- | -- | Warning | 0 | X | 0 | 27
[15 empty] | 858 | Blade bear.lubr. failure | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 871 | Light icing (rotor bl. ice sensor) | -- | -- | Info | 0 |  | 30 | 28
[15 empty] | 872 | Icing (Rotor bl. ice sensor) | -- | -- | Info | 0 |  | 30 | 28
[15 empty] | 873 | Icing (rotor bl. ice sens. no eval.) | -- | -- | Info | 0 |  | 30 | 28
[15 empty] | 874 | Rotor blade ice sensor error | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 875 | Rot.bl. ice sens. com. err. | -- | -- | Info | 0 |  | 20 | 27
[15 empty] | 876 | Rot.bl. ice s. eval. not pos. | -- | -- | Info | 0 |  | 30 | 27
[15 empty] | 877 | Rot.bl. ice sens. not ready | -- | -- | Info | 0 |  | 20 | 27
[15 empty] | 878 | Rotor blade ice sensor bypass active | -- | -- | Info | 0 |  | 20 | 27
[15 empty] | 960 | Blade load sensors not RFO | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 961 | Blade load sensors zero offset indiv. Error | -- | -- | Warning | 0 | X | 0 | 27
[15 empty] | 962 | Blade load sensors gain error | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 963 | Blade load sensors homog. error | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 964 | Blade load sensors strain diff. high | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 965 | Blade load sensors implaus.meas.val. | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 967 | Blade load sensors signal check | -- | -- | Warning | 0 |  | 20 | 28
[15 empty] | 968 | Blade load sensors signal check error | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 969 | Rotor blade load sensor back-up mode | -- | -- | Warning | 0 |  | 20 | 28
[15 empty] | 970 | Alarm - cont. blade load sensors back-up mode | -- | -- | Warning | 0 | X | 0 | 27
[15 empty] | 971 | Stop - blade load sensors back-up mode | -- | -- | Info | 52 |  | 20 | 15
[15 empty] | 972 | Blade load sensors no signal activity | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 973 | Check blade bend.mom. | -- | -- | Info | 75 | X | 20 | 15
[15 empty] | 974 | Blade load sensors zero offset error | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 1001 | Drive train oscillation Z level 0 | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 1005 | Drive train oscillation Z level 1 | 1558 | WP4084#2 CH1 level 1 | Error | 52 | X | 20 | 15
[15 empty] | 1015 | Drive train oscillation Z level 2 | 1564 | WP4084#2 CH1 level 2 | Error | 52 | X | 0 | 15
[15 empty] | 1050 | Drivetrain oscillations | -- | -- | Warning | 0 |  | 10 | 27
[15 empty] | 1055 | Max. drivetrain oscillations | -- | -- | Error | 52 | X | 0 | 25
[15 empty] | 1065 | Drive train monitor level 1 | -- | -- | Info | 52 |  | 20 | 15
[15 empty] | 1070 | Drive train monitor level 2 | -- | -- | Info | 52 |  | 20 | 15
[15 empty] | 1125 | 4-20mA drive train acceleration Z | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 1130 | Acceleration detector drivetrain | -- | -- | Error | 52 | X | 0 | 21
[15 empty] | 1150 | CMS drive train system error | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 1151 | CMS drive train meas. val. ev. | -- | -- | Info | 0 |  | 20 | 27
[15 empty] | 1160 | Comm.err. IEC client -> CMS drive tr. | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 1161 | Comm.err. IEC server <- CMS drive tr. | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 1200 | High temp. rotorbearing | 1713 | (R) bearing temp. | Warning | 0 |  | 30 | 27
[15 empty] | 1210 | Max. temp. rotorbearing | 1714 | (R) bear. temp. stop | Error | 52 | X | 0 | 22
[15 empty] | 1215 | 4-20mA rotor bear. temp. | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 1216 | 4-20mA rotor bear. temp. timeout | -- | -- | Error | 52 | X | 0 | 21
[15 empty] | 1311 | Rotor bearing lubrication pump 1 overload | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 1312 | Rotor bearing lubrication pump 2 overload | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 1313 | Rotor bear. lubr.cont. 1 empty | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 1314 | Rotor bear. lubr.cont. 2 empty | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 1316 | Timeout fault rotor bear. lubr. | -- | -- | Error | 52 | X | 20 | 23
[15 empty] | 1319 | Rotor bearing lubrication failure | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 1320 | Rotor bearing lubric. man.op. | -- | -- | Info | 0 |  | 20 | 27
[15 empty] | 1321 | Max. time rotor bear.lubr. 1 | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 1322 | Max. time rotor bear.lubr. 2 | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 1405 | Rotor locked: Stop | 1585 | Rotor locked | Info | 60 | X | 0 | 9
[15 empty] | 1407 | Rotor lock - wind too strong | -- | -- | Info | 60 | X | 0 | 9
[15 empty] | 1408 | Rotor lock 1 on | -- | -- | Info | 0 |  | 20 | 28
[15 empty] | 1409 | Rotor lock 2 on | -- | -- | Info | 0 |  | 20 | 28
[15 empty] | 1410 | Rotor lock - no storm position | -- | -- | Info | 190 | X | 0 | 9
[15 empty] | 1500 | High gearbox oil pressure | 1337 | Gear oil press. high | Error | 52 | X | 0 | 23
[15 empty] | 1510 | Low gearbox oil pressure | 1306 | Gear oil press. low | Error | 52 | X | 0 | 23
[15 empty] | 1520 | 4-20mA press. gearbox pump | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 1525 | 4-20mA press. gearbox inlet | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 1530 | Error measuring pressure inlet gear | -- | -- | Warning | 0 |  | 10 | 27
[15 empty] | 1548 | Missing gear oil (low rpm) | -- | -- | Error | 52 | X | 20 | 23
[15 empty] | 1550 | Missing gear oil (high rpm) | 1355 | Missing gear oil | Error | 52 | X | 20 | 23
[15 empty] | 1552 | Gearbox warm-up stage | 2315 | -- | Info | 0 |  | 20 | 28
[15 empty] | 1555 | Gear heating enabled | -- | -- | Info | 0 |  | 20 | 28
[15 empty] | 1557 | Gearbox warmed up idling | -- | -- | Info | 0 |  | 20 | 28
[15 empty] | 1558 | Timeout gearoil heating routine Active | -- | -- | Warning | 0 | X | 0 | 27
[15 empty] | 1560 | Manual operation fan gear | -- | -- | Info | 0 |  | 20 | 28
[15 empty] | 1565 | Manual operation gear heating | -- | -- | Info | 0 |  | 20 | 28
[15 empty] | 1570 | Manual operation gear oil pump | -- | -- | Info | 0 |  | 20 | 28
[15 empty] | 1600 | High gear speed | 310 | Gear overspeed | Error | 75 | X | 30 | 14
[15 empty] | 1610 | Maximum gear speed | 328 | Gear overspeed max. | Error | 190 | X | 0 | 14
[15 empty] | 1625 | Implausible gear speed leap | -- | -- | Error | 52 |  | 20 | 21
[15 empty] | 1630 | Disc filter adaption implausible | -- | -- | Error | 52 | X | 0 | 21
[15 empty] | 1680 | Gearb.sp. SLC <> gearb.sp. | -- | -- | Error | 52 |  | 20 | 21
[15 empty] | 1685 | Gear ratio param. implaus. | -- | -- | Error | 52 | X | 20 | 15
[15 empty] | 1700 | High temp. gear bearing 1 | 1323 | Gear bearing temp. 1 | Warning | 0 |  | 20 | 27
[15 empty] | 1705 | Max. temp. gear bearing 1 | 1324 | Gear bear.temp.1stop | Error | 52 | X | 0 | 22
[15 empty] | 1707 | PT100 gear bearing 1 defect | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 1708 | Error measuring temp. gear bearing 1 | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 1710 | High temp. gear bearing 2 | 1325 | Gear bearing temp. 2 | Warning | 0 |  | 20 | 27
[15 empty] | 1715 | Max. temp. gear bearing 2 | 1326 | Gear bear.temp.2stop | Error | 52 | X | 0 | 22
[15 empty] | 1717 | PT100 gear bearing 2 defect | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 1718 | Error measuring temp. gear bearing 2 | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 1720 | Max. oilsump temperature | 1327 | Gear oil temp. high | Error | 52 | X | 20 | 22
[15 empty] | 1723 | Oilsump temperature high | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 1725 | Low gear oil temperature | 1328 | Gear oil temp. low | Info | 52 | X | 30 | 6
[15 empty] | 1727 | PT100 gear oil sump defect | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 1728 | Error measuring temp. gear oil sump | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 1729 | PT100 inlet gear defect | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 1731 | Oil temperature gearbox input high | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 1732 | Max. oil temperature gearbox input | -- | -- | Error | 52 | X | 0 | 22
[15 empty] | 1738 | Error measuring temp. inlet gear | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 1740 | High temp. gear bearing 3 | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 1745 | Max. temp. gear bearing 3 | -- | -- | Error | 52 | X | 0 | 22
[15 empty] | 1747 | PT100 gear bearing 3 defect | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 1748 | Error measuring temp. gear bearing 3 | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 1750 | High temp. gear bearing 4 | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 1755 | Max. temp. gear bearing 4 | -- | -- | Error | 52 | X | 0 | 22
[15 empty] | 1757 | PT100 gear bearing 4 defect | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 1758 | Error measuring temp. gear bearing 4 | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 1800 | Overload gear oil pump | 1332 | Gear oil(P)therm. | Error | 52 | X | 20 | 24
[15 empty] | 1810 | Overload gear heating | 920 | Gearheat.therm.relay | Warning | 0 | X | 20 | 27
[15 empty] | 1816 | Fault fan gear oil cooler 1 | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 1818 | Overload fan 1 gear oil cooler | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 1819 | Overload fan 2 gear oil cooler | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 1822 | Fault fan gear oil cooler 2 | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 1824 | Fault fan gear oil cooler 1+2 | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 1860 | Oil filter gear choked | 1339 | Gear oil fil.1 chok. | Warning | 0 | X | 0 | 27
[15 empty] | 1870 | 4-20mA pressure diff. gear oil filter | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 1880 | Error meas. press. diff. oil filter | -- | -- | Warning | 0 | X | 10 | 27
[15 empty] | 1920 | Particle sensor defect | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 1922 | Particle Gear Alarm 10min | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 1924 | Particle Gear Alarm 24h | -- | -- | Error | 52 | X | 0 | 23
[15 empty] | 1926 | Particle Gear Alarm Total | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 2005 | Check brake | -- | -- | Error | 52 | X | 0 | 23
[15 empty] | 2007 | Brake pads warning | -- | -- | Warning | 0 | X | 30 | 27
[15 empty] | 2050 | Brake closed in operation | 1833 | Brake closed | Error | 170 | X | 0 | 23
[15 empty] | 2125 | Timeout brake closed | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 2150 | Impulse braking | -- | -- | Info | 52 | X | 20 | 28
[15 empty] | 2160 | Permanent braking | -- | -- | Info | 0 | X | 20 | 28
[15 empty] | 2170 | Additional braking | -- | -- | Info | 75 | X | 20 | 28
[15 empty] | 2200 | Max. braking energy exceeded | -- | -- | Error | 52 | X | 0 | 15
[15 empty] | 2340 | Temp. rot.br.pad implaus. | -- | -- | Error | 52 | X | 0 | 23
[15 empty] | 2350 | Disc brake cooling down | -- | -- | Info | 52 |  | 20 | 28
[15 empty] | 2355 | Temp. rot.br.pad high | -- | -- | Info | 0 |  | 20 | 28
[15 empty] | 2356 | Max rot.br.pad temp. exceed. | -- | -- | Info | 75 |  | 0 | 15
[15 empty] | 2357 | Dragging brake monitoring | -- | -- | Info | 75 |  | 20 | 15
[15 empty] | 2358 | Temp. rot.br.pad high timeout | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 2360 | Error measuring temp. rot.br.pad 1 | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 2361 | PT100 rot.br.pad 1 defect | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 2370 | Error measuring temp. rot.br.pad 2 | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 2371 | PT100 rot.br.pad 2 defect | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 2380 | 0-10V error volt.buffer rot.br. | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 2390 | Brake due to sudden sys.failure | -- | -- | Error | 52 | X | 0 | 24
[15 empty] | 2515 | Implausible gen. speed leap | -- | -- | Error | 52 | X | 0 | 21
[15 empty] | 2520 | Gen.speed analog<>gear.speed | -- | -- | Error | 52 |  | 20 | 20
[15 empty] | 2521 | Gen.sp.analog <<>> gearb.sp. | -- | -- | Error | 52 |  | 20 | 21
[15 empty] | 2530 | Gen. power derating act. | -- | -- | Info | 0 |  | 20 | 32
[15 empty] | 2540 | Gen.speed pulse error | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 2541 | Gen.speed voltage error | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 2550 | Overload generator fan 1 | 918 | Fan(G)ext.term.relay | Warning | 0 | X | 20 | 27
[15 empty] | 2600 | High temp. gen. bearing 1 | 526 | (G) bearing 1 temp. | Warning | 0 |  | 30 | 27
[15 empty] | 2605 | Max. temp. gen. bearing 1 | 527 | (G)bear.1 temp. stop | Error | 52 | X | 0 | 22
[15 empty] | 2607 | PT100 gen. bearing 1 defect | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 2608 | Error measuring temp. gen.bearing 1 | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 2610 | High temp. gen. bearing 2 | 528 | (G) bearing 2 temp. | Warning | 0 |  | 30 | 27
[15 empty] | 2615 | Max. temp. gen. bearing 2 | 529 | (G)bear.2 temp. stop | Error | 52 | X | 0 | 22
[15 empty] | 2617 | PT100 gen. bearing 2 defect | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 2618 | Error measuring temp. gen. bearing 2 | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 2650 | Overload generator fan 2 | 936 | (G)fan 2.term. relay | Warning | 0 | X | 20 | 27
[15 empty] | 2655 | Overload generator fan 3 | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 2660 | Thermistor generator | 510 | Thermistor G1 stator | Error | 52 | X | 0 | 22
[15 empty] | 2662 | PT100 stator temp. 2 defect | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 2663 | Error measuring temp. 2 stator | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 2665 | High stator temperature | 513 | G1 stator temp. | Warning | 0 |  | 30 | 27
[15 empty] | 2666 | High stator temperature 2 | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 2670 | Max. temp. stator | 514 | G1 stator temp. stop | Error | 52 | X | 30 | 22
[15 empty] | 2671 | Max. temp. stator 2 | -- | -- | Error | 52 | X | 20 | 22
[15 empty] | 2672 | PT100 stator temp. defect | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 2673 | Error measuring temp. stator | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 2674 | Overload generator heating | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 2675 | Overload gen. heating: stop | -- | -- | Error | 52 | X | 20 | 24
[15 empty] | 2685 | Slipring cell temp. high | 2025 | (G) slipr.air temp | Warning | 0 |  | 20 | 27
[15 empty] | 2687 | Max. slip ring cell temp. | 2026 | (G) slipr.air stop | Error | 52 |  | 30 | 22
[15 empty] | 2689 | PT100 slipring temp. defect | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 2691 | Error meas. slip ring temp. | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 2695 | P red. incr. gen. coolant temp. | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 2696 | Gen. max. coolant temp. | -- | -- | Error | 52 | X | 20 | 22
[15 empty] | 2710 | Generator power too high | 530 | (G) power too high | Error | 52 | X | 20 | 20
[15 empty] | 2800 | Max. power peak | 550 | (G) peak power max. | Error | 52 | X | 0 | 24
[15 empty] | 2810 | Service generator brushes | 554 | (G)Brushes worn | Warning | 0 | X | 0 | 27
[15 empty] | 2811 | Fault generator brushes | -- | -- | Error | 52 | X | 0 | 20
[15 empty] | 2822 | Overload lubrication generator | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 2823 | Fault gen. bearing lubrication | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 2826 | Man. oper. gen. lubrication | -- | -- | Info | 0 |  | 20 | 28
[15 empty] | 2828 | Timeout fault gen. lubrication | -- | -- | Error | 52 | X | 20 | 23
[15 empty] | 2829 | Gen.lubr. self-protect. active | -- | -- | Info | 0 |  | 20 | 32
[15 empty] | 2831 | Max. time generator bear.lubr. | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 2832 | Generator bearing lubr. Container empty | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 2900 | Manual operation generator heating | -- | -- | Info | 0 |  | 20 | 27
[15 empty] | 2910 | Manual operation generator fan 1 | -- | -- | Info | 0 |  | 20 | 27
[15 empty] | 2920 | Manual operation generator fan 2 | -- | -- | Info | 0 |  | 20 | 27
[15 empty] | 2930 | Manual operation generator fan 3 | -- | -- | Info | 0 |  | 20 | 27
[15 empty] | 2950 | Lightning protection defect | 602 | Lightning prot. def. | Warning | 0 |  | 0 | 27
[15 empty] | 3000 | Frequency converter not ready | 1401 | Freq.conv. not ready | Error | 75 |  | 10 | 20
[15 empty] | 3005 | Conv. fuse tripped | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 3010 | Conv. comm.error | -- | -- | Error | 52 | X | 20 | 15
[15 empty] | 3011 | Conv. SDO transm.error | -- | -- | Warning | 0 | X | 0 | 27
[15 empty] | 3020 | Chopper util. incr. | -- | -- | Warning | 0 |  | 20 | 28
[15 empty] | 3021 | Max. chopper util. | -- | -- | Error | 75 |  | 20 | 20
[15 empty] | 3030 | Conv. warning | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 3040 | Conv reset after grid restoration | -- | -- | Info | 52 |  | 30 | 28
[15 empty] | 3050 | Freq. conv. speed window | 330 | Rpm <> window | Error | 52 |  | 10 | 20
[15 empty] | 3060 | Conv. emerg.off type A | -- | -- | Error | 75 | X | 20 | 20
[15 empty] | 3061 | Conv. emerg.off type B | -- | -- | Error | 75 | X | 20 | 20
[15 empty] | 3062 | Conv. emerg.off type C | -- | -- | Error | 75 | X | 20 | 20
[15 empty] | 3063 | Conv. emerg.off type D | -- | -- | Error | 75 | X | 20 | 20
[15 empty] | 3064 | Conv. emerg.off type E | -- | -- | Error | 75 | X | 20 | 20
[15 empty] | 3065 | Conv. emerg.off type F | -- | -- | Error | 75 | X | 20 | 20
[15 empty] | 3090 | Frequency converter spare protection | -- | -- | Error | 75 | X | 0 | 20
[15 empty] | 3095 | Error converter disconnection | -- | -- | Error | 75 | X | 0 | 20
[15 empty] | 3096 | Converter disconnection implausible | -- | -- | Error | 52 | X | 0 | 20
[15 empty] | 3097 | Max. negative active power | -- | -- | Error | 75 | X | 0 | 20
[15 empty] | 3110 | Frequency converter error | 1409 | Freq. conv. error | Error | 75 | X | 20 | 20
[15 empty] | 3120 | Frequency converter overspeed | 1411 | Freq.conv.overspeed | Error | 75 |  | 10 | 14
[15 empty] | 3121 | Conv. underspeed | -- | -- | Error | 75 |  | 10 | 14
[15 empty] | 3125 | Timeout ready for connection | 651 | Cut in 0_>G1 | Error | 52 |  | 10 | 24
[15 empty] | 3130 | Timeout grid synchronisation | 1415 | Freq.conv. <> sync. | Error | 52 |  | 10 | 20
[15 empty] | 3140 | Frequency converter operation range | 1416 | Freq.conv.<>workinga | Error | 52 |  | 10 | 20
[15 empty] | 3155 | Limit conv. output act.power | -- | -- | Info | 0 |  | 20 | 27
[15 empty] | 3160 | Cable overload | 1693 | Cable overload | Warning | 0 |  | 20 | 27
[15 empty] | 3161 | P reduction power cord overl. | -- | -- | Info | 0 |  | 20 | 27
[15 empty] | 3162 | Cable overload stop | 1694 | Cable overload stop | Error | 52 |  | 20 | 24
[15 empty] | 3164 | P reduction stator cable overl. | -- | -- | Info | 0 |  | 20 | 27
[15 empty] | 3200 | Frequency converter temp. low | 1602 | Freq.conv.temp.low | Info | 52 |  | 20 | 6
[15 empty] | 3201 | Bypass conv. heating mode | -- | -- | Info | 0 |  | 20 | 28
[15 empty] | 3202 | Timeout converter temp. low | -- | -- | Error | 52 | X | 0 | 6
[15 empty] | 3210 | Frequency converter load rejection | 1644 | Freq.conv.<>parallel | Error | 75 |  | 10 | 20
[15 empty] | 3211 | Conv. load shedding (CAN) | -- | -- | Error | 75 |  | 10 | 20
[15 empty] | 3220 | Reduced power converter | 1792 | [P] reduced conv. | Warning | 0 |  | 20 | 27
[15 empty] | 3222 | Timeout reduced power conv. | -- | -- | Error | 52 | X | 20 | 20
[15 empty] | 3225 | Limit reactive power converter | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 3227 | Timeout Q limit converter | -- | -- | Warning | 0 | X | 0 | 27
[15 empty] | 3250 | No power | 1688 | No power | Error | 52 |  | 20 | 20
[15 empty] | 3255 | Converter power too high | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 3260 | Converter power too low | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 3265 | Converter torque <> setpoint | 1686 | Converter<>setpoint | Warning | 0 |  | 20 | 27
[15 empty] | 3267 | Calculated torque implausible | -- | -- | Error | 52 | X | 0 | 16
[15 empty] | 3270 | Converter torque monitor level 0 | -- | -- | Info | 0 |  | 20 | 27
[15 empty] | 3271 | Converter torque monitor level 1 | -- | -- | Error | 75 |  | 20 | 15
[15 empty] | 3280 | Conv. COM mode active | -- | -- | Info | 0 |  | 20 | 28
[15 empty] | 3281 | Conv. COM mode stop | -- | -- | Info | 60 |  | 0 | 9
[15 empty] | 3350 | No pressure increase following pump start-up | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 3351 | Timeout no pressure increase following pump start-up | -- | -- | Warning | 52 | X | 0 | 23
[15 empty] | 3355 | No temp. rise after heat.coolant on | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 3356 | Pump cooling sys. (tower base) diff.press. Low | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 3357 | Pump cooling sys. (tower base) diff.press. too low | -- | -- | Error | 52 | X | 0 | 23
[15 empty] | 3358 | Pump cooling sys. (tower base) diff.press. High | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 3359 | Pump cooling sys. (tower base) diff.press. too high | -- | -- | Error | 52 | X | 0 | 23
[15 empty] | 3360 | Implaus. act. in conv.cooling system | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 3365 | Fan 1 cool.sys. error | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 3366 | Fan 2 cool.sys. error | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 3367 | Fan 3 cool.sys. error | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 3368 | Fan 4 cool.sys. error | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 3370 | Coolant press. low | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 3371 | Coolant press. too low | -- | -- | Warning | 0 | X | 0 | 27
[15 empty] | 3372 | Cool sys. press. switch tripped | -- | -- | Warning | 0 | X | 0 | 27
[15 empty] | 3373 | Coolant press. high (with pump on) | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 3374 | Coolant press. too high (with pump on) | -- | -- | Warning | 0 | X | 0 | 27
[15 empty] | 3375 | Coolant press. high (with pump off) | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 3376 | Coolant press. too high (with pump on) | -- | -- | Warning | 0 | X | 0 | 27
[15 empty] | 3377 | 4-20mA coolant press. | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 3378 | Pump coolant inlet press. 4-20mA | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 3380 | Coolant temp. high | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 3381 | P red. incr. conv. coolant temp. | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 3385 | Coolant temp. too high | -- | -- | Warning | 0 |  | 0 | 27
[15 empty] | 3386 | Conv. max. coolant temp. | -- | -- | Error | 52 | X | 20 | 22
[15 empty] | 3387 | 4-20mA coolant temp. | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 3390 | Cool.sys. pump man.oper. | -- | -- | Info | 0 |  | 20 | 28
[15 empty] | 3391 | Heating coolant 1&2 man.oper. | -- | -- | Info | 0 |  | 20 | 28
[15 empty] | 3392 | Fans group 1&2 cool.sys.man.oper. | -- | -- | Info | 0 |  | 20 | 28
[15 empty] | 3393 | Heating fans 1-4 cool.sys.man.oper. | -- | -- | Info | 0 |  | 20 | 28
[15 empty] | 3395 | Pump cooling sys. overload | -- | -- | Error | 52 | X | 20 | 24
[15 empty] | 3396 | Coolant heating 1&2 overload | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 3397 | Heating overload fans 1- 4 cooling sys. | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 3400 | UPS warning | 1762 | UPS Warning | Warning | 0 |  | 0 | 27
[15 empty] | 3410 | UPS error | -- | -- | Error | 52 | X | 0 | 24
[15 empty] | 3420 | UPS buffer time too short | -- | -- | Error | 52 | X | 0 | 24
[15 empty] | 3430 | UPS error | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 3440 | UPS air conditioning faulty | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 3455 | Grid loss auxiliary power | -- | -- | Info | 75 | X | 20 | 4
[15 empty] | 3460 | Grid loss auxiliary power without grid loss net | -- | -- | Error | 52 | X | 20 | 24
[15 empty] | 3461 | Grid loss without grid loss auxiliary power | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 3500 | Grid loss | 102 | Phase drop | Info | 75 |  | 20 | 4
[15 empty] | 3501 | Grid disconnection for self-protection | -- | -- | Info | 75 |  | 20 | 4
[15 empty] | 3502 | Timeout grid error | -- | -- | Error | 75 | X | 0 | 4
[15 empty] | 3503 | Zero-seq. syst. volt. high | -- | -- | Info | 52 |  | 20 | 4
[15 empty] | 3530 | High voltage - level 1 | 110 | Voltage high | Info | 75 |  | 20 | 4
[15 empty] | 3531 | High voltage - level 2 | -- | -- | Info | 75 |  | 20 | 4
[15 empty] | 3532 | Min. voltage cut in | -- | -- | Info | 52 |  | 20 | 4
[15 empty] | 3533 | Max. voltage cut in | -- | -- | Info | 52 |  | 20 | 4
[15 empty] | 3534 | Repeat voltage dip | -- | -- | Info | 52 |  | 20 | 4
[15 empty] | 3535 | Low voltage - level 1 | 111 | Voltage low | Info | 75 |  | 20 | 4
[15 empty] | 3536 | Low voltage - level 2 | -- | -- | Info | 75 |  | 20 | 4
[15 empty] | 3537 | Transient fault | 128 | Transient grid error | Info | 0 |  | 20 | 27
[15 empty] | 3540 | High frequency - level 1 | 120 | Frequency high | Info | 75 |  | 20 | 4
[15 empty] | 3541 | High frequency - level 2 | -- | -- | Info | 75 |  | 20 | 4
[15 empty] | 3542 | Max. frequency cut in | -- | -- | Info | 52 |  | 20 | 4
[15 empty] | 3543 | High frequency - P reduction | -- | -- | Info | 0 |  | 20 | 27
[15 empty] | 3544 | Time limit high freq. - P red. | -- | -- | Info | 0 | X | 0 | 27
[15 empty] | 3545 | Low frequency - Level 1 | 121 | Frequency low | Info | 75 |  | 20 | 4
[15 empty] | 3546 | Low frequency - level 2 | -- | -- | Info | 75 |  | 20 | 4
[15 empty] | 3547 | Overfrequency | 134 | Critical frequency | Info | 0 |  | 20 | 27
[15 empty] | 3550 | Phase angle | 130 | L1-L2-L3 12 | Info | 75 |  | 20 | 4
[15 empty] | 3551 | Phase angle | -- | -- | Info | 75 |  | 20 | 4
[15 empty] | 3555 | Current asymmetry | 601 | Current asymmetry | Error | 52 | X | 10 | 20
[15 empty] | 3560 | Voltage asymmetry | -- | -- | Error | 52 | X | 10 | 4
[15 empty] | 3562 | Timeout max. freq. cut in | -- | -- | Info | 52 |  | 20 | 4
[15 empty] | 3570 | Grid error | 156 | Grid error | Info | 75 |  | 20 | 4
[15 empty] | 3571 | Low frequency - level 3 | -- | -- | Info | 75 |  | 20 | 4
[15 empty] | 3572 | Low frequency - level 4 | -- | -- | Info | 75 |  | 20 | 4
[15 empty] | 3573 | Low frequency - level 5 | -- | -- | Info | 75 |  | 20 | 4
[15 empty] | 3574 | Low frequency - level 6 | -- | -- | Info | 75 |  | 20 | 4
[15 empty] | 3575 | Minimum grid frequency | -- | -- | Info | 75 |  | 20 | 4
[15 empty] | 3576 | Min. frequency cut in | -- | -- | Info | 52 |  | 20 | 4
[15 empty] | 3577 | Underfrequency | -- | -- | Info | 0 |  | 20 | 27
[15 empty] | 3581 | High frequency - level 3 | -- | -- | Info | 75 |  | 20 | 4
[15 empty] | 3582 | High frequency - level 4 | -- | -- | Info | 75 |  | 20 | 4
[15 empty] | 3583 | High frequency - level 5 | -- | -- | Info | 75 |  | 20 | 4
[15 empty] | 3584 | High frequency - level 6 | -- | -- | Info | 75 |  | 20 | 4
[15 empty] | 3585 | Maximum grid frequency | -- | -- | Info | 75 |  | 20 | 4
[15 empty] | 3586 | P reduction frequency prot. | -- | -- | Info | 0 |  | 20 | 27
[15 empty] | 3590 | Overvoltage | -- | -- | Info | 75 |  | 10 | 4
[15 empty] | 3591 | Transient voltage peak | -- | -- | Info | 0 |  | 20 | 27
[15 empty] | 3592 | Repeat transient voltage peak | -- | -- | Info | 52 |  | 20 | 4
[15 empty] | 3593 | Grid recovery | -- | -- | Info | 52 |  | 20 | 4
[15 empty] | 3594 | No Connection permission | -- | -- | Info | 52 |  | 20 | 4
[15 empty] | 3595 | Grid parameters implausible | -- | -- | Error | 52 |  | 20 | 16
[15 empty] | 3630 | VQ protection | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 3632 | VQ protection stop | -- | -- | Error | 52 |  | 20 | 4
[15 empty] | 3640 | Dynamic frequency control | -- | -- | Info | 0 |  | 30 | 28
[15 empty] | 3642 | End additional power | -- | -- | Info | 0 |  | 20 | 28
[15 empty] | 3750 | Grid measurement error | -- | -- | Error | 52 |  | 30 | 24
[15 empty] | 3751 | Initialization grid meas. | -- | -- | Info | 52 |  | 20 | 28
[15 empty] | 3800 | Circuit breaker | 600 | Main switch off | Error | 75 | X | 30 | 20
[15 empty] | 3802 | MVS Trafo CB off | -- | -- | Info | 75 | X | 20 | 9
[15 empty] | 3803 | P reduction current limitation | -- | -- | Info | 0 |  | 20 | 28
[15 empty] | 3804 | MVS Trafo CB tripped | -- | -- | Error | 75 | X | 0 | 24
[15 empty] | 3805 | Max. transformer temp. | 2022 | Trafo temp.stop | Error | 52 | X | 20 | 22
[15 empty] | 3807 | MVS Trafo CB remote off | -- | -- | Info | 75 | X | 0 | 9
[15 empty] | 3809 | P reduction apparent power limitation | -- | -- | Info | 0 |  | 20 | 28
[15 empty] | 3810 | Medium voltage off | 2023 | Medium Voltage off | Error | 75 | X | 0 | 15
[15 empty] | 3812 | MVS Transf. Disc. off | -- | -- | Info | 75 | X | 0 | 9
[15 empty] | 3814 | MVS Transf. ES on | -- | -- | Info | 75 | X | 0 | 9
[15 empty] | 3836 | MSS Protection system error | -- | -- | Error | 52 | X | 0 | 24
[15 empty] | 3840 | SF6 boiler pressure too low | 1695 | SF6-Pressure low | Error | 52 | X | 0 | 24
[15 empty] | 3849 | Spare potection inactive | -- | -- | Error | 52 | X | 0 | 24
[15 empty] | 3866 | LV HRC fuses triggered | -- | -- | Error | 52 | X | 0 | 24
[15 empty] | 3869 | Lightning protect. transf. Defect | -- | -- | Warning | 0 | X | 0 | 27
[15 empty] | 3892 | PT100 transf. int. defect. | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 3894 | Error meas. temp. transf.int. | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 3898 | Max. transformer temp. PT100 | -- | -- | Error | 52 |  | 20 | 22
[15 empty] | 3901 | Timeout max. transf. temp. | -- | -- | Error | 75 | X | 0 | 22
[15 empty] | 3904 | Max. temp. supply transformer | -- | -- | Error | 52 |  | 20 | 22
[15 empty] | 3907 | Max. temp. supply transf. grid disconn. | -- | -- | Error | 52 | X | 0 | 22
[15 empty] | 3912 | Transf. oil pressure too high | -- | -- | Error | 75 | X | 0 | 24
[15 empty] | 3914 | Transf. fill level too low | -- | -- | Error | 52 | X | 20 | 24
[15 empty] | 3942 | PT100 supply transformer def. | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 3943 | Error measuring PT100 supply transf. | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 3950 | Aux. power operation error | -- | -- | Error | 52 | X | 20 | 24
[15 empty] | 3954 | Max. overv. aux. power ctrl. | -- | -- | Error | 52 | X | 0 | 24
[15 empty] | 3960 | Max. temp. aux. transf. nacelle | -- | -- | Error | 52 |  | 20 | 22
[15 empty] | 3962 | PT100 aux. transformer nacelle def. | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 3963 | Error meas. nacelle aux. transf. | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 3970 | Transformer pump overload | -- | -- | Warning | 0 | X | 0 | 27
[15 empty] | 3972 | Transf. pump thermist. tripped | -- | -- | Warning | 0 | X | 0 | 27
[15 empty] | 3974 | Transf. pump man.oper. | -- | -- | Info | 0 |  | 20 | 27
[15 empty] | 4000 | High temperature nacelle | 30 | Nacelle temp. | Warning | 0 |  | 20 | 27
[15 empty] | 4020 | Max. temperature nacelle | 31 | Nacelle temp. stop | Error | 52 |  | 20 | 6
[15 empty] | 4024 | 4-20mA inside temp. nacelle | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 4061 | Rel. air hum. nacelle inside high (in operation) | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 4062 | Rel. air hum. nacelle inside too high (in operation) | -- | -- | Error | 52 | X | 20 | 6
[15 empty] | 4072 | Rel. air hum. nacelle inside too high | -- | -- | Info | 52 |  | 20 | 6
[15 empty] | 4075 | 4-20mA rel. air humidity nacelle int. | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 4086 | 4-20mA rel. air humidity tower base int. | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 4091 | Rel. air hum. tower base inside high (in operation) | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 4092 | Rel. air hum. tower base inside too high | -- | -- | Info | 52 |  | 20 | 6
[15 empty] | 4093 | Rel. air hum. tower base inside too high (in operation) | -- | -- | Error | 52 | X | 20 | 6
[15 empty] | 4100 | Vibration | 5 | Vibration | Error | 180 | X | 0 | 23
[15 empty] | 4150 | Vibration sensor error | -- | -- | Info | 52 |  | 0 | 13
[15 empty] | 4200 | Fault fire alarm system | -- | -- | Error | 52 | X | 20 | 15
[15 empty] | 4201 | Fire warning | 2231 | Smoke warning | Error | 52 | X | 0 | 15
[15 empty] | 4202 | Fire alarm | -- | -- | Error | 52 | X | 0 | 15
[15 empty] | 4203 | Fire shut down | 2232 | Smole stop | Error | 52 | X | 0 | 15
[15 empty] | 4204 | Service fire alarm system | -- | -- | Info | 0 | X | 20 | 28
[15 empty] | 4205 | Fire alarm system inactive | -- | -- | Error | 52 | X | 0 | 9
[15 empty] | 4210 | Smoke warning nacelle | -- | -- | Warning | 0 | X | 0 | 27
[15 empty] | 4215 | Smoke warning nacelle stop | -- | -- | Error | 52 | X | 0 | 15
[15 empty] | 4220 | Smoke warning tower base | -- | -- | Warning | 0 | X | 0 | 27
[15 empty] | 4225 | Smoke warning tow. base stop | -- | -- | Error | 52 | X | 0 | 15
[15 empty] | 4230 | Grid disc. smoke warning | -- | -- | Error | 75 | X | 0 | 15
[15 empty] | 4250 | Manual operation nacelle fan | -- | -- | Info | 0 |  | 20 | 27
[15 empty] | 4252 | Failure nacelle fan | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 4253 | Overload nacelle fan | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 4255 | Dry mode nacelle | -- | -- | Info | 0 |  | 20 | 28
[15 empty] | 4260 | Manual operation rotor hub fan | -- | -- | Info | 0 |  | 20 | 27
[15 empty] | 4262 | Failure rotor hub fan | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 4263 | Overload rotor hub fan | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 4270 | Manual operation cooling pump | -- | -- | Info | 0 |  | 20 | 27
[15 empty] | 4272 | Failure cooling pump | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 4273 | Overload cooling pump | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 4275 | Pressure coolant nacelle high | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 4276 | Pressure difference cooling pump (nacelle) low | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 4277 | Coolant pump diff.press. (nacelle) too low | -- | -- | Warning | 0 | X | 0 | 27
[15 empty] | 4278 | Coolant pump diff.press. (nacelle) high | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 4279 | Coolant pump diff.press. (nacelle) too high | -- | -- | Warning | 0 | X | 0 | 27
[15 empty] | 4280 | Error meas. pressure coolant nacelle | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 4281 | Signal Pressure coolant nacelle disturbed | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 4285 | Error meas. coolant press nacelle pump inlet | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 4286 | Signal Pressure coolant nacelle pump inlet disturbed | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 4290 | Error meas. temperature coolant nacelle cooler | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 4291 | Signal Temperature coolant nacelle cooler disturbed | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 4293 | Error meas. temperature coolant generator | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 4294 | Signal Temperature coolant generator disturbed | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 4296 | Error meas. temperature coolant gearbox | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 4297 | Signal Temperature coolant gearbox disturbed | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 4500 | Tower resonance | 205 | Tower resonance time | Info | 50 |  | 20 | 28
[15 empty] | 4502 | Nat. tower freq. implausible | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 4503 | Nat. tower freq. calc. imp. | -- | -- | Info | 0 |  | 20 | 27
[15 empty] | 4510 | Tower oscillation Y level 1 | 1539 | WP4084#1 CH1 level 1 | Info | 52 |  | 20 | 15
[15 empty] | 4511 | Tower oscillation Y level 1 standst. | -- | -- | Info | 52 | X | 0 | 15
[15 empty] | 4520 | Tower oscillation X level 1 | 1555 | WP4084#1 CH2 level 1 | Info | 52 |  | 20 | 15
[15 empty] | 4521 | Tower oscillation X level 1 standst. | -- | -- | Info | 52 | X | 0 | 15
[15 empty] | 4530 | Tower oscillation Y level 2 | 1556 | WP4084#1 CH1 level 2 | Info | 52 |  | 20 | 15
[15 empty] | 4531 | Tower oscillation Y level 2 standst. | -- | -- | Info | 52 | X | 0 | 15
[15 empty] | 4535 | Tower oscillation Y level 3 | -- | -- | Error | 52 | X | 0 | 15
[15 empty] | 4540 | Tower oscillation X level 2 | 1557 | WP4084#1 CH2 level 2 | Info | 52 |  | 20 | 15
[15 empty] | 4541 | Tower oscillation X level 2 standst. | -- | -- | Info | 52 | X | 0 | 15
[15 empty] | 4545 | Tower oscillation X level 3 | -- | -- | Error | 52 | X | 0 | 15
[15 empty] | 4555 | Tower accel. difference | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 4565 | System fault accel. sensor 1 | -- | -- | Error | 52 | X | 0 | 21
[15 empty] | 4582 | Oscil.sensor 1: check firmware | -- | -- | Error | 52 |  | 0 | 21
[15 empty] | 4583 | Oscil.sensor 2: check firmware | -- | -- | Error | 52 |  | 0 | 21
[15 empty] | 4584 | Oscill. encoder tower (BP act.) | -- | -- | Error | 52 | X | 0 | 21
[15 empty] | 4585 | 4-20mA tower acceleration Y | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 4587 | 4-20mA tower acceleration X | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 4588 | Oscillation encoder tower | -- | -- | Error | 52 |  | 20 | 21
[15 empty] | 4589 | Oscillation encoder TwC | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 4600 | PT100 base box temp. defect | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 4603 | Base box temperature high | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 4604 | Base box temperature low | -- | -- | Warning | 0 |  | 30 | 27
[15 empty] | 4605 | Error measuring temp. tower base box | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 4607 | Heating/fan base box faulty | -- | -- | Warning | 0 |  | 0 | 27
[15 empty] | 4608 | Tower distrib. cabinet def. | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 4609 | Max. base box temp. | -- | -- | Error | 52 | X | 20 | 22
[15 empty] | 4611 | PT100 temp. tower base defective | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 4620 | Tower base temp. impermissible | -- | -- | Info | 0 |  | 20 | 27
[15 empty] | 4645 | 4-20mA tower accel. Y2 (TwC) | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 4647 | 4-20mA tower accel. X2 (TwC) | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 4700 | Failure tower fan | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 4710 | Manual operation tower fan | -- | -- | Info | 0 |  | 20 | 27
[15 empty] | 4720 | Tower fan overload | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 4730 | Drying mode tower base | -- | -- | Info | 0 |  | 20 | 28
[15 empty] | 4800 | Persons in the tower base | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 4810 | Tower door opened | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 4951 | Accel.sensor XF/YF comm.error | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 4956 | Accel.sensor XF/YF system error | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 4960 | Tower oscillation YF | -- | -- | Info | 52 | X | 20 | 15
[15 empty] | 4970 | Tower oscillation XF | -- | -- | Info | 52 | X | 20 | 15
[15 empty] | 5000 | Breakdown obstacle light | 1561 | Flight warn.ligh.out | Warning | 0 | X | 20 | 27
[15 empty] | 5001 | Breakdown low intensity obstacle light | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 5020 | Failure visibility measuring | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 5025 | Error no. visibility meas. devices | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 5100 | Service obstacle light | 1569 | Flight warn.ligh.def | Warning | 0 | X | 0 | 27
[15 empty] | 5500 | High hydraulic pressure | 1223 | (H)sys. press. high | Error | 52 | X | 10 | 23 | Hydraulic system
[15 empty] | 5505 | High hydr. press. flush. mode | -- | -- | Warning | 0 |  | 0 | 27
[15 empty] | 5506 | Rot.br. press. high | -- | -- | Error | 52 | X | 20 | 23 | Hydraulic system
[15 empty] | 5507 | Max. rot.br. press. | -- | -- | Error | 52 | X | 20 | 23 | Hydraulic system
[15 empty] | 5510 | Low hydraulic pressure | 1224 | (H)sys. press. low | Error | 52 | X | 20 | 23 | Hydraulic system
[15 empty] | 5516 | Rot.br. press. low | -- | -- | Error | 52 | X | 20 | 23 | Hydraulic system
[15 empty] | 5517 | Drain valve (MVB) test fail | -- | -- | Error | 52 | X | 0 | 23 | Hydraulic system
[15 empty] | 5520 | 4-20mA hydraulic pressure | -- | -- | Error | 52 | X | 20 | 21 | Hydraulic system
[15 empty] | 5525 | 4-20mA rot.br. press. | -- | -- | Error | 52 | X | 20 | 21 | Hydraulic system
[15 empty] | 5550 | Low hydraulic oil level | 1201 | (H) oil level low | Error | 52 | X | 0 | 23 | Hydraulic system
[15 empty] | 5600 | Overload hydraulic pump | 1207 | (H)motor therm.relay | Error | 52 | X | 20 | 24 | Hydraulic system
[15 empty] | 5700 | Max. operation time hydraulic | 1213 | (H) oper.time > max. | Error | 52 | X | 0 | 23 | Hydraulic system
[15 empty] | 5710 | Min. operation time hydraulic | 1214 | (H) oper.time < min. | Error | 52 | X | 10 | 23 | Hydraulic system
[15 empty] | 5730 | Pressure drop hydraulic sys. | -- | -- | Warning | 0 | X | 0 | 27
[15 empty] | 5750 | Manual operation hydraulic pump | -- | -- | Info | 0 |  | 20 | 27
[15 empty] | 5760 | Hydraulic oil flushing operation | -- | -- | Info | 52 |  | 20 | 28
[15 empty] | 5770 | Manual op. hydr. oil flushing | -- | -- | Info | 52 |  | 20 | 28
[15 empty] | 6000 | Overload electr. yaw brake | 747 | Yaw(B) therm. relay | Error | 52 | X | 20 | 24 | Yaw system
[15 empty] | 6007 | Overload yaw motors group 1 | -- | -- | Error | 52 | X | 20 | 24 | Yaw system
[15 empty] | 6012 | Overload yaw motors group 2 | -- | -- | Error | 52 | X | 20 | 24 | Yaw system
[15 empty] | 6039 | Max. time yaw bear.lubr. | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 6040 | Overload yaw lubr. pump | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 6041 | Yaw bearing lubric. man.op. | -- | -- | Info | 0 |  | 20 | 27
[15 empty] | 6043 | Timeout fault yaw lubrication | -- | -- | Error | 52 | X | 20 | 23 | Yaw system
[15 empty] | 6046 | Error yaw lubr. pump (no ext. press. build-up) | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 6047 | Error yaw lubr. pump (no ext. press. red.) | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 6048 | Yaw lubr. container empty | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 6052 | High yaw motor current | -- | -- | Info | 0 |  | 20 | 28
[15 empty] | 6054 | Easy yaw | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 6056 | High yaw load | -- | -- | Error | 52 |  | 20 | 6 | Yaw system
[15 empty] | 6100 | Rotating direction yaw | 742 | Yaw sensor A/B | Error | 52 |  | 10 | 21 | Yaw system
[15 empty] | 6111 | Yaw velocity too low | -- | -- | Error | 52 | X | 10 | 21 | Yaw system
[15 empty] | 6115 | Yaw sensor A defect | -- | -- | Error | 52 | X | 0 | 21 | Yaw system
[15 empty] | 6116 | Yaw sensor B defect | -- | -- | Error | 52 | X | 0 | 21 | Yaw system
[15 empty] | 6120 | Uncontrolled yaw movement | -- | -- | Error | 52 | X | 20 | 23 | Yaw system
[15 empty] | 6130 | Yaw speed high | -- | -- | Error | 52 | X | 20 | 23 | Yaw system
[15 empty] | 6200 | Cable autounwind | 715 | Cable autounwind | Info | 52 |  | 20 | 28
[15 empty] | 6210 | Max. cable twistangle | 722 | Cable twisted | Error | 52 | X | 0 | 21 | Yaw system
[15 empty] | 6300 | Yaw error | 700 | Error by yawing | Error | 52 | X | 0 | 21 | Yaw system
[15 empty] | 6350 | Check nacelle position! | 777 | Check nacelle pos. | Warning | 0 |  | 0 | 27
[15 empty] | 6355 | Error nacelle pos. Load Man. | -- | -- | Warning | 0 | X | 0 | 27
[15 empty] | 6356 | Untwisting sensor test | -- | -- | Info | 52 |  | 20 | 28
[15 empty] | 6357 | Nacelle position sensor fault | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 6400 | Manual yaw brake | -- | -- | Info | 52 |  | 20 | 9
[15 empty] | 6410 | Manual yaw | -- | -- | Info | 0 |  | 20 | 28
[15 empty] | 6411 | Manual yaw via pushbutton | -- | -- | Info | 0 |  | 20 | 28
[15 empty] | 6412 | Tower referencing act. | -- | -- | Info | 52 |  | 20 | 28
[15 empty] | 6430 | Yaw current par. implausible | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 6432 | 4-20mA yaw current sensor | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 6460 | Yaw park pos. in case of icing | -- | -- | Info | 52 | X | 20 | 6
[15 empty] | 6501 | Wind.sp. diff. level 1 | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 6505 | Wind.sp. diff. level 2 | -- | -- | Error | 52 | X | 0 | 21 | Wind Sensor
[15 empty] | 6506 | Dev. wind meas./est. | -- | -- | Warning | 0 |  | 0 | 27
[15 empty] | 6510 | Anemometer 1 defect | 224 | Wind gauge R out | Warning | 0 | X | 20 | 27
[15 empty] | 6512 | Reboot anemometer 1 | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 6721 | Comm.err. IEC server -> Shadow Mgmt. Unit | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 6750 | Man. oper. meteorology heating | -- | -- | Info | 0 |  | 20 | 28
[15 empty] | 7001 | Task runtime failure 1ms | -- | -- | Error | 180 | X | 0 | 16 | PLC system
[15 empty] | 7002 | Task runtime failure 5ms | -- | -- | Error | 180 | X | 0 | 16 | PLC system
[15 empty] | 7003 | Task runtime failure 10 ms | -- | -- | Error | 180 | X | 0 | 16 | PLC system
[15 empty] | 7004 | Task runtime failure grid measuring | -- | -- | Error | 180 | X | 0 | 16 | PLC system
[15 empty] | 7005 | Division by zero | 39 | Division by zero | Error | 180 | X | 0 | 16 | PLC system
[15 empty] | 7008 | Reboot necessary after update | -- | -- | Info | 0 |  | 20 | 28
[15 empty] | 7009 | Unexpected reboot | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 7010 | Parameter unreadable | 40 | Parameter crash | Error | 170 | X | 20 | 16 | PLC system
[15 empty] | 7011 | Loading parameters | -- | -- | Info | 60 |  | 20 | 9
[15 empty] | 7012 | Manual snapshot | -- | -- | Info | 0 |  | 20 | 32
[15 empty] | 7013 | Alarm call test | 38 | Alarm call test | Info | 0 | X | 20 | 32
[15 empty] | 7014 | Cond. snapshot | -- | -- | Info | 0 |  | 20 | 32
[15 empty] | 7016 | Parameter outside limits | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 7017 | Parameter outside limits stop | -- | -- | Error | 52 | X | 20 | 15 | PLC system
[15 empty] | 7018 | Parameter update active | -- | -- | Info | 0 | X | 20 | 28
[15 empty] | 7019 | Unsafe parametrization | -- | -- | Error | 52 | X | 0 | 15 | PLC system
[15 empty] | 7025 | Configuration error | -- | -- | Error | 52 | X | 0 | 15 | PLC system
[15 empty] | 7026 | License error | -- | -- | Info | 0 |  | 0 | 27
[15 empty] | 7027 | Runtime error | -- | -- | Info | 0 |  | 20 | 28
[15 empty] | 7028 | Software exception error | -- | -- | Info | 0 |  | 0 | 28
[15 empty] | 7029 | File transfer error | -- | -- | Info | 0 |  | 20 | 28
[15 empty] | 7030 | Controller flags implausible | -- | -- | Error | 170 | X | 0 | 16 | PLC system
[15 empty] | 7031 | Controller parameter setting implausible | -- | -- | Error | 75 |  | 0 | 16 | PLC system
[15 empty] | 7035 | Controller feed forward function reduced 50% | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 7036 | Controller feed forward function deactivated | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 7040 | Set point above rated speed | -- | -- | Error | 170 | X | 0 | 15
[15 empty] | 7050 | PT100 top box defect | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 7052 | P red. incr. top box temp. | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 7053 | Top box temperature high | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 7054 | Top box temperature low | -- | -- | Warning | 0 |  | 30 | 27
[15 empty] | 7055 | Error meas. top box temp. | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 7057 | Heating/fan top box faulty | -- | -- | Warning | 0 |  | 0 | 27
[15 empty] | 7058 | Fuses overload | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 7059 | Max. top box temp | -- | -- | Error | 52 | X | 20 | 22
[15 empty] | 7085 | Comm. error switch top box | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 7090 | Comm. error base box switch | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 7092 | IEC interface read requests | -- | -- | Info | 0 |  | 20 | 27
[15 empty] | 7160 | Manual stop on site - maint. Required | -- | -- | Error | 52 | X | 0 | 15
[15 empty] | 7250 | HC/WTC comm. version conflict | -- | -- | Error | 52 | X | 0 | 16
[15 empty] | 7324 | Check time synchronization | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 7325 | Time sync. failed (SNTP error) | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 7335 | mconfig.ini check failed | -- | -- | Error | 60 | X | 20 | 16 | PLC system
[15 empty] | 7340 | TwC algorithm implausible | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 7350 | New initialization rotor pos. | -- | -- | Info | 52 |  | 10 | 28
[15 empty] | 7400 | High CPU temperature | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 7401 | Max. temperature CPU | 43 | Internal temp. high | Error | 52 | X | 20 | 16 | PLC system
[15 empty] | 7402 | CPU Failure RTC | 2122 | Time adjust. error | Warning | 0 | X | 0 | 27
[15 empty] | 7403 | CPU NVRAM battery | 42 | Internal battery low | Warning | 0 | X | 0 | 27
[15 empty] | 7404 | CPU memory error | 1725 | WP3100 Watchdog | Error | 180 | X | 0 | 16 | PLC system
[15 empty] | 7415 | PLC hardware error | -- | -- | Error | 52 | X | 20 | 16
[15 empty] | 7421 | CAN bus module firmware | -- | -- | Error | 52 | X | 20 | 16
[15 empty] | 7425 | Profinet communication (nacelle cool.sys.) disrupted | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 7610 | Firmware update required | -- | -- | Info | 0 |  | 0 | 28
[15 empty] | 7611 | Firmware update failed | -- | -- | Warning | 0 |  | 0 | 27
[15 empty] | 8000 | Park master stop | 99 | Parkmasterstop | Info | 52 |  | 20 | 30
[15 empty] | 8001 | Slave tripping | -- | -- | Info | 75 |  | 20 | 4
[15 empty] | 8002 | Emer. power op. active | -- | -- | Info | 52 |  | 20 | 4
[15 empty] | 8100 | Comm. failure FDM all clients | 1007 | No park communica. | Warning | 0 |  | 20 | 27
[15 empty] | 8105 | Parkmaster operation failed | -- | -- | Info | 0 |  | 0 | 27
[15 empty] | 8200 | PMU snapshot | -- | -- | Info | 0 |  | 20 | 32
[15 empty] | 8300 | Icing (farm) | -- | -- | Info | 0 | X | 20 | 28
[15 empty] | 8400 | Comm. failure FPM | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 8401 | Comm. failure FPM: stop | -- | -- | Error | 52 |  | 20 | 16
[15 empty] | 8402 | No assignment to a PMU | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 8405 | Fallback setpoints active | -- | -- | Info | 0 |  | 20 | 28
[15 empty] | 8410 | IP duplicate in WF network | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 8420 | BCP master with same seg.no. | -- | -- | Warning | 0 | X | 20 | 27
[15 empty] | 9000 | P output externally reduced | 1793 | [P] reduced EU | Info | 0 |  | 20 | 27
[15 empty] | 9001 | P limit. extern. IEC | -- | -- | Info | 0 |  | 20 | 27
[15 empty] | 9006 | dU limit. extern. IEC | -- | -- | Info | 0 |  | 20 | 27
[15 empty] | 9022 | Stop ext. prot.dev. | -- | -- | Info | 52 |  | 20 | 2
[15 empty] | 9085 | Fallback P limit. failure IEC | -- | -- | Info | 0 |  | 20 | 28
[15 empty] | 9086 | IEC failure: stop | -- | -- | Error | 52 | X | 20 | 16
[15 empty] | 9087 | Fallback dU limit. failure IEC | -- | -- | Info | 0 |  | 20 | 28
[15 empty] | 9090 | Client failure | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 9210 | Externally stopped | 135 | EU-stop | Info | 52 |  | 20 | 4
[15 empty] | 9211 | External stop IEC | -- | -- | Info | 52 |  | 20 | 4
[15 empty] | 9801 | MVS grid disconn. off | -- | -- | Info | 75 | X | 0 | 9
[15 empty] | 9802 | MVS grid ES on | -- | -- | Info | 75 | X | 0 | 9
[15 empty] | 9811 | MVS cable outlet 1 disconn. off | -- | -- | Info | 0 | X | 0 | 27
[15 empty] | 9812 | MVS cable outlet 1 ES on | -- | -- | Info | 0 | X | 0 | 27
[15 empty] | 9821 | MVS cable outlet 2 disconn. off | -- | -- | Info | 0 | X | 0 | 27
[15 empty] | 9822 | MVS cable outlet 2 ES on | -- | -- | Info | 0 | X | 0 | 27
[15 empty] | 15000 | Hot air de-icing positioning | -- | -- | Info | 52 |  | 20 | 6
[15 empty] | 15001 | Ending hot air de-icing | -- | -- | Info | 52 |  | 20 | 6
[15 empty] | 15003 | HAD man. ice prevention | -- | -- | Info | 0 |  | 20 | 32
[15 empty] | 15004 | HAD ice prevention | -- | -- | Info | 0 |  | 20 | 32
[15 empty] | 15005 | Hot air de-icing active | -- | -- | Info | 60 |  | 20 | 6
[15 empty] | 15010 | HAD semi-aut. op. | -- | -- | Info | 60 |  | 20 | 9
[15 empty] | 15015 | HAD motor prot. fan OFF | -- | -- | Warning | 0 |  | 0 | 27
[15 empty] | 15016 | HAD motor prot. heat.reg. OFF | -- | -- | Warning | 0 |  | 0 | 27
[15 empty] | 15021 | HAD motor prot. heat.reg. A1 | -- | -- | Warning | 0 |  | 0 | 27
[15 empty] | 15022 | HAD motor prot. heat.reg. A2 | -- | -- | Warning | 0 |  | 0 | 27
[15 empty] | 15023 | HAD motor prot. heat.reg. A3 | -- | -- | Warning | 0 |  | 0 | 27
[15 empty] | 15040 | HAD outside temp. de-icing too High | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 15041 | HAD outside temp. de-icing too Low | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 15042 | HAD outside temp. ice prev. too High | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 15043 | HAD outside temp. ice prev. too low | -- | --
[15 empty] | 15050 | HAD overtemp. relay | -- | -- | Warning | 0 |  | 0 | 27
[15 empty] | 15055 | HAD overtemp. flow | -- -- |  | Warning | 0 |  | 0 | 27
[15 empty] | 15056 | HAD overtemp. control box | -- -- |  | Warning | 0 |  | 0 | 27
[15 empty] | 15060 | HAD overtemp. heating | -- -- |  | Warning | 0 |  | 0 | 27
[15 empty] | 15062 | HAD temp. sensor drift A1 | -- -- |  | Warning | 0 |  | 0 | 27
[15 empty] | 15065 | temp. sensor error | -- |  | Warning | 0 |  | 0 | 27
[15 empty] | 15068 | rotor pos. sensor error | -- |  | Warning | 0 |  | 0 | 27
[15 empty] | 15071 | error HFU contact. A1 | -- |  | Warning | 0 |  | 0 | 27
[15 empty] | 15072 | error HFU contact. A2 | -- |  | Warning | 0 |  | 0 | 27
[15 empty] | 15073 | error HFU contact. A3 | -- |  | Warning | 0 |  | 0 | 27
[15 empty] | 15078 | error overtemp. Relay | -- |  | Warning | 0 |  | 0 | 27
[15 empty] | 15081 | motor prot. fan A1 | -- |  | Warning | 0 |  | 0 | 27
[15 empty] | 15082 | motor prot. fan A2 | -- |  | Warning | 0 |  | 0 | 27
[15 empty] | 15083 | motor prot. fan A3 | -- |  | Warning | 0 |  | 0 | 27
[15 empty] | 15085 | de-icing implausible | -- |  | Warning | 0 |  | 0 | 27
[15 empty] | 15090 | communication error | -- |  | Warning | 0 |  | 10 | 27
[15 empty] | 15091 | comm.version error | -- |  | Warning | 0 |  | 20 | 27
[15 empty] | 15094 | rotor pos. implausible | -- |  | Warning | 0 |  | 0 | 27
[15 empty] | 15095 | timeout positioning | -- |  | Warning | 0 |  | 0 | 27
[15 empty] | 15096 | timeout de-icing A1 | -- |  | Warning | 0 |  | 0 | 27
[15 empty] | 15097 | timeout de-icing A2 | -- |  | Warning | 0 |  | 0 | 27
[15 empty] | 15098 | timeout de-icing A3 | -- |  | Warning | 0 |  | 0 | 27
[15 empty] | 15101 | max. CPU temp. | -- |  | Warning | 0 | X | 20 | 27
[15 empty] | 15102 | CPU error RTC | -- |  | Warning | 0 | X | 0 | 27
[15 empty] | 15103 | CPU NVRAM battery | -- |  | Warning | 0 | X | 0 | 27
[15 empty] | 15104 | CPU memory error | -- |  | Warning | 0 | X | 0 | 27
[15 empty] | 15105 | division by zero | -- |  | Warning | 0 | X | 0 | 27
[15 empty] | 15106 | prog.runtime error 10ms | -- |  | Warning | 0 | X | 0 | 27
[15 empty] | 15107 | mconfig.ini check failed | -- |  | Warning | 0 | X | 20 | 27
[15 empty] | 15115 | PLC hardware error | -- |  | Warning | 0 | X | 20 | 27
[15 empty] | CE100001 | Manual Stop | [7 empty] | Control Panel
[15 empty] | CE100002 | Major BD - Blade | [7 empty] | Blade
[15 empty] | CE100003 | Major BD - Transformer | [7 empty] | Transformer
[15 empty] | CE100004 | Major BD - Generator | [7 empty] | Generator
[15 empty] | CE100005 | Major BD - Gearbox | [7 empty] | Gearbox
[15 empty] | CE100006 | Major BD - Main Bearing | [7 empty] | Main Bearing
[15 empty] | CE100007 | Transmission Line Related work | [7 empty] | Transmission System
[15 empty] | CE100008 | General Work Stoppage | [7 empty] | General Work
[15 empty] | CE100009 | Major BD - Power Cable | [7 empty] | Power Cable
[15 empty] | CE100011 | Major BD - DFIG | [7 empty] | DFIG
[15 empty] | CE100012 | Major BD - Foundation | [7 empty] | Foundation
[15 empty] | CE100013 | Theft | [7 empty] | Theft
[15 empty] | CE100010 | Manual Stop - Preventive Maintenance Activity | [7 empty] | Preventive Maintenance
[15 empty] | CE100014 | Manual Stop - Audit | [7 empty] | Audit
[15 empty] | CE100015 | Manual Stop - Safety Related | [7 empty] | Safety
[15 empty] | CE100016 | Manual Stop - Blade Cleaning | [7 empty] | Blade
[15 empty] | CE100017 | UPS breakdown | [7 empty] | Control Panel
[15 empty] | 3355 | No temp. rise after heat.coolant on | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 3356 | Pump cooling sys. (tower base) diff.press low | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 6515 | 4-20mA anemometer 1 | -- | -- | Warning | 0 | X | 20 | 27 | Wind Sensor
[15 empty] | 6520 | Anemometer 2 defect | -- | -- | Warning | 0 | X | 20 | 27 | Wind Sensor
[15 empty] | 6522 | Reboot anemometer 2 | -- | -- | Warning | 0 |  | 20 | 27 | Wind Sensor
[15 empty] | 6525 | 4-20mA anemometer 2 | -- | -- | Warning | 0 | X | 20 | 27 | Wind Sensor
[15 empty] | 6526 | Anemometer 3 defect | -- | -- | Warning | 0 | X | 20 | 27 | Wind Sensor
[15 empty] | 6527 | 4-20mA anemometer 3 | -- | -- | Warning | 0 | X | 20 | 27 | Wind Sensor
[15 empty] | 6530 | Anemometer defect | -- | -- | Error | 52 | X | 20 | 21 | Wind Sensor
[15 empty] | 6540 | Icing (anemometer) | -- | -- | Information | 0 |  | 30 | 28 | Wind Sensor
[15 empty] | 6541 | No ice detection available | -- | -- | Error | 52 | X | 20 | 21 | Wind Sensor
[15 empty] | 6542 | Reset of icing st. cd. possible | -- | -- | Information | 0 | X | 20 | 32 | Wind Sensor
[15 empty] | 6571 | Ice anemometer de-icing | -- | -- | Information | 0 |  | 30 | 28 | Wind Sensor
[15 empty] | 6601 | Wind.dir. diff. level 1 | -- | -- | Warning | 0 |  | 20 | 27 | Wind Sensor
[15 empty] | 6605 | Wind.dir. diff. level 2 | -- | -- | Error | 52 | X | 0 | 21 | Wind Sensor
[15 empty] | 6620 | Vane defect | -- | -- | Error | 52 | X | 20 | 21 | Wind Sensor
[15 empty] | 6621 | Vane 1 defect | -- | -- | Warning | 0 |  | 20 | 27 | Wind Sensor
[15 empty] | 6622 | Vane 2 defect | -- | -- | Warning | 0 | X | 20 | 27 | Wind Sensor
[15 empty] | 6625 | Check vane! | -- | -- | Error | 52 | X | 0 | 21 | Wind Sensor
[15 empty] | 6630 | 4-20 mA vane 1 | -- | -- | Warning | 0 | X | 20 | 27 | Wind Sensor
[15 empty] | 6635 | 4-20 mA vane 2 | -- | -- | Warning | 0 | X | 20 | 27 | Wind Sensor
[15 empty] | 6670 | Light icing (red. operation) | -- | -- | Information | 0 | X | 20 | 28 | Wind Sensor
[15 empty] | 6680 | Icing (red. operation) | -- | -- | Information | 0 | X | 20 | 28 | Wind Sensor
[15 empty] | 6681 | Light icing (dev. electr. power) | -- | -- | Information | 0 |  | 30 | 28 | Wind Sensor
[15 empty] | 6682 | Icing (dev. electr. power) | -- | -- | Information | 0 |  | 30 | 28 | Wind Sensor
[15 empty] | 6686 | Extreme icing (wind > power) | -- | -- | Information | 0 | X | 30 | 27 | Wind Sensor
[15 empty] | 6690 | Icing (stop) | -- | -- | Information | 52 | X | 20 | 6 | Wind Sensor
[15 empty] | 6694 | Timed red. icing operation act. | -- | -- | Information | 0 |  | 20 | 28 | Wind Sensor
[15 empty] | 6695 | Stop in case of ice det. act. | -- | -- | Information | 0 | X | 20 | 28 | Wind Sensor
[15 empty] | 6696 | Test start during potential icing | -- | -- | Information | 0 |  | 30 | 28 | Wind Sensor
[15 empty] | 6697 | Max. starts during icing | -- | -- | Information | 52 | X | 30 | 6 | Wind Sensor
[15 empty] | 6700 | Shadow casting | -- | -- | Information | 52 |  | 20 | 2
[15 empty] | 6710 | Shadow Management Unit defect | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 6711 | Shadow Management Unit out of service | -- | -- | Error | 52 | X | 20 | 21
[15 empty] | 6712 | Shadow Management Unit warning | -- | -- | Warning | 0 |  | 20 | 27
[15 empty] | 6720 | Comm.err. IEC client -> Shadow Mgmt. Unit | -- | -- | Warning | 0 |  | 20 | 27