## Daily Dashboard
Performance Summary DRES 8MW
Month | 2025-06-01
Date | 2025-06-11
Operation Year | 2026
Year Start Date | 2025-04-01
Year End Date | 2026-03-31
Sr. No. | Particular | Target | Measured | Deviation | Remarks
1 | E_Grid Daily (MWh) | 25.9197 | 24.9 | -3.934%
| E_Grid MTD(MWh) | 311.037 | 327.3 | 5.229%
| E_Grid YTD (MWh) | 2390.2539 | 2243.75 | -6.129%
2 | CUF Daily(%) | 13.46% | 12.93% | -3.934%
| CUF MTD(%) | 14.69% | 15.46% | 5.229%
| CUF YTD(%) | 17.25% | 16.19% | -6.129%
3 | PR_Daily (%) | 67.89% | 86.47% | 27.37%
| PR_MTD (%) | 67.89% | 80.53% | 18.62%
| PR_YTD (%) | 68.47% | 73.97% | 8.026%
4 | POA Daily (KWh/m2) | 4.76 | 3.59 | -24.58%
| POA MTD(KWh/m2) | 57.12 | 50.67 | -11.29%
| POA YTD(KWh/m2) | 435.22 | 378.19 | -13.1%
5 | PA Daily (KWh/m2) | 98.04% | 100% | 1.999%
| PA MTD(KWh/m2) | 98.04% | 100% | 1.999%
| PA YTD(KWh/m2) | 98.04% | 96.88% | -1.185%
6 | GA Daily (KWh/m2) | 98% | 100% | 2.041%
| GA MTD(KWh/m2) | 98% | 95.52% | -2.533%
| GA YTD(KWh/m2) | 98% | 95.94% | -2.105%

## CMS_Data
Daily
Tagname | Date | Target | Actual | Difference
E Grid Target | 4581900% | 25.9197 | 24.9 | 1.0197
Shadding | 4581900% | 0 | 0 | 0
Soiling | 4581900% | 0 | 0 | 0
IAM | 4581900% | 0 | 0 | 0
Bifacial Gain | 4581900% | 0 | 0 | 0
Temperature | 4581900% | 0 | 0 | 0
Mismatch | 4581900% | 0 | 0 | 0
DC Ohmic | 4581900% | 0 | 0 | 0
AC Ohmic | 4581900% | 0 | 0 | 0
Inverter Conversion | 4581900% | 0 | 0 | 0
MPPT Mismatch | 4581900% | 0 | 0 | 0
Clipping Loss | 4581900% | 0 | 0 | 0
Curtailment Order | 4581900% | 0 | 0 | 0
Reactive Power | 4581900% | 0 | 0 | 0
Plant Uptime | 4581900% | 98.04 | 100 | 1.96 | 0.50803
Grid Uptime | 4581900% | 98 | 100 | 2 | 0.51839
Tracker Uptime | 4581900% | 0 | 0 | 0 | 0
Tracker Gain | 4581900% | 0 | 0 | 0
Dc Unbalanced Load | 4581900% | 0 | 0 | 0
Measured | 4581900% | 24.9 | 24.9 | 24.9
Repowering Delay | 4581900% | 0 | 0 | 0
Capacity Shortfall | 4581900% | 0 | 0 | 0
PR | 4581900% | 0 | 6.3777 | 6.3777
POA | 4581900% | 4.76 | 3.59 | -1.17 | -6.371

## Annual KPI
Till Date | 2025-06-11 | 2025-06-01
7.5 MW Dres Energy Private Limited Performance Summary-YTD
Year | Days | Estimated POA(KWh/m2) | Measured POA (KWh/m2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Targt PR (%) | Measured PR(%) | Target DC CUF (%) | Measured DC CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%)
2026 | 72 | 435.22 | 378.19 | 2390.2539 | 2243.75 | 68.47% | 73.97% | 17.25% | 16.19% | 98% | 95.94% | 98.04% | 96.88%
7.5 MW Dres Energy Private Limited Performance Summary-Monthwise
Year | Days | Estimated POA(KWh/m2) | Measured POA (KWh/m2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Targt PR (%) | Measured PR(%) | Target DC CUF (%) | Measured DC CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%)
2025-04-01 | 30 | 191.7 | 174.2 | 1038.3069 | 1001 | 67.53% | 71.64% | 17.98% | 17.33% | 98% | 97.44% | 98.04% | 93.09%
2025-05-01 | 31 | 186.4 | 157.12 | 1040.9101 | 941.05 | 69.62% | 74.67% | 17.44% | 15.77% | 98% | 94.78% | 98.04% | 99.43%
2025-06-01 | 12 | 57.12 | 50.67 | 311.037 | 327.3 | 67.89% | 80.53% | 13.46% | 14.17% | 98% | 95.52% | 98.04% | 100%
2025-07-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 98% |  | 98.04%
2025-08-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 98% |  | 98.04%
2025-09-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 98% |  | 98.04%
2025-10-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 98% |  | 98.04%
2025-11-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 98% |  | 98.04%
2025-12-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 98% |  | 98.04%
2026-01-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 98% |  | 98.04%
2026-02-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 98% |  | 98.04%
2026-03-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 98% |  | 98.04%

## Monthly KPI
Till Date | 2025-06-11
7.5 MW Dres Energy Private Limited Performance Summary
Year | Days | Estimated POA(KWh/m2) | Measured POA (KWh/m2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Targt PR (%) | Measured PR(%) | Target DC CUF (%) | Measured DC CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%)
2025-06-01 | 11 | 57.12 | 50.67 | 311.037 | 327.3 | 67.89% | 80.53% | 14.69% | 15.46% | 98% | 95.52% | 98.04% | 100%
Start Date | 2025-06-05
End Date | 2025-06-11
DRES Energy Private Limited 7.5 MW Performance Summary
Month | Days | Estimated POA(KWh/m2) | Measured POA (KWh/m2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Targt PR (%) | Measured PR(%) | Target DC CUF (%) | Measured DC CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%)
2025-06-01 | 7 | 33.32 | 24.12 | 181.4382 | 154.15 | 67.89% | 79.68% | 13.46% | 11.44% | 98% | 92.32% | 98.04% | 100%
Formulas:
Days = [Days, row below]-6

## Daily KPI
Date | Financial Year | Calendar Year | Month Year | Days | Operating Hours | GHI-UP (KWh/m2) | GHI-Down(KWh/m2) | POA-UP(KWh/m2) | POA-Down(KWh/m2) | Amb_Temp(°C) | Mod_Temp(°C) | WS_Avg(m/s) | WS_Max(m/s) | PA(%) | MA (%) | IGA (%) | EGA(%) | EMA (%) | TA (%) | PR(%) | WPR(%) | CUF(%) | Gen_Exp (kWh) | Mtr_Export (kWh) | Mtr_Import (kWh) | Mtr_Net_Exp (KWh) | Operational Capacity (MW) | Bugt_Resource | Bugt_Energy | Bugt PR | Bugt CUF | Bugt_PA | Bugt_EGA | Expected Energy | Actual Energy WPR | RA (%) | Mod Clean Dry (Num) | Mod Clean Wet (Num) | Line Loss(%) | Reactive Power (%) | Bugt Line loss (%) (Wind) | Bugt Reactive Power (%) (Wind) | Bugt Capacity | CC*Bugt
2025-03-29 | 2025 | 2025 | 2025-03-01 | 31 | 12.0833 | 0 |  | 5.53 |  | 0 | 45.37 | 0 | 0 | [9 empty] | 25201 |  |  |  | 8.0209 | 6.7871 | 38844.7742 | 71.36% | 20.18% | 98.04% | 98% | [9 empty] | 8.0209
2025-03-30 | 2025 | 2025 | 2025-03-01 | 31 | 12.1 | 0 |  | 5.95 |  | 0 | 45.2 | 0 | 0 | 77.12% |  |  | 100% |  |  | 56.78% |  | 14.08% | 27454 | 27200 | 100 | 27100 | 8.0209 | 6.7871 | 38844.7742 | 71.36% | 20.18% | 98.04% | 98% | [9 empty] | 8.0209
2025-03-31 | 2025 | 2025 | 2025-03-01 | 31 | 12.15 | 0 |  | 5.99 |  | 0 | 44.04 | 0 | 0 | 77.42% |  |  | 100% |  |  | 56.82% |  | 14.18% | 27676.2 | 27400 | 100 | 27300 | 8.0209 | 6.7871 | 38844.7742 | 71.36% | 20.18% | 98.04% | 98% | [9 empty] | 8.0209
2025-04-01 | 2026 | 2025 | 2025-04-01 | 30 | 12.05 | 0 |  | 6.04 |  | 0 | 45.06 | 0 | 0 | 78.52% |  |  | 100% |  |  | 56.87% |  | 14.31% | 27882.6 | 27650 | 100 | 27550 | 8.0209 | 6.39 | 34610.2284 | 67.53% | 17.98% | 98.04% | 98% | [9 empty] | 8.0209
2025-04-02 | 2026 | 2025 | 2025-04-01 | 30 | 12.2333 | 0 |  | 6.71 |  | 0 | 44.65 | 0 | 0 | 73.59% |  |  | 96.76% |  |  | 53.33% |  | 14.91% | 29060.9 | 28800 | 100 | 28700 | 8.0209 | 6.39 | 34610.2284 | 67.53% | 17.98% | 98.04% | 98% | [9 empty] | 8.0209
2025-04-03 | 2026 | 2025 | 2025-04-01 | 30 | 11.45 | 0 |  | 3.79 |  | 0 | 36.42 | 0 | 0 | 79.57% |  |  | 73.87% |  |  | 48.85% |  | 7.714% | 15103.3 | 14950 | 100 | 14850 | 8.0209 | 6.39 | 34610.2284 | 67.53% | 17.98% | 98.04% | 98% | [9 empty] | 8.0209
2025-04-04 | 2026 | 2025 | 2025-04-01 | 30 | 12.35 | 0 |  | 6.83 |  | 0 | 44.06 | 0 | 0 | 75.01% |  |  | 100% |  |  | 58.32% |  | 16.6% | 32349.9 | 32050 | 100 | 31950 | 8.0209 | 6.39 | 34610.2284 | 67.53% | 17.98% | 98.04% | 98% | [9 empty] | 8.0209
2025-04-05 | 2026 | 2025 | 2025-04-01 | 30 | 12.25 | 0 |  | 6.96 |  | 0 | 46.18 | 0 | 0 | 71.5% |  |  | 100% |  |  | 56.43% |  | 16.36% | 31819 | 31600 | 100 | 31500 | 8.0209 | 6.39 | 34610.2284 | 67.53% | 17.98% | 98.04% | 98% | [9 empty] | 8.0209
2025-04-06 | 2026 | 2025 | 2025-04-01 | 30 | 12.2 | 0 |  | 6.77 |  | 0 | 45.22 | 0 | 0 | 77.51% |  |  | 100% |  |  | 62.43% |  | 17.61% | 34264.9 | 34000 | 100 | 33900 | 8.0209 | 6.39 | 34610.2284 | 67.53% | 17.98% | 98.04% | 98% | [9 empty] | 8.0209
2025-04-07 | 2026 | 2025 | 2025-04-01 | 30 | 12.25 | 0 |  | 5.97 |  | 0 | 45.66 | 0 | 0 | 81.72% |  |  | 100% |  |  | 73.51% |  | 18.29% | 35585 | 35300 | 100 | 35200 | 8.0209 | 6.39 | 34610.2284 | 67.53% | 17.98% | 98.04% | 98% | [9 empty] | 8.0209
2025-04-08 | 2026 | 2025 | 2025-04-01 | 30 | 12.2 | 0 |  | 5.83 |  | 0 | 43.19 | 0 | 0 | 87.02% |  |  | 100% |  |  | 74.95% |  | 18.21% | 35437.8 | 35150 | 100 | 35050 | 8.0209 | 6.39 | 34610.2284 | 67.53% | 17.98% | 98.04% | 98% | [9 empty] | 8.0209
2025-04-09 | 2026 | 2025 | 2025-04-01 | 30 | 12.2333 | 0 |  | 6.34 |  | 0 | 44.41 | 0 | 0 | 84.3% |  |  | 100% |  |  | 71.97% |  | 19.01% | 36980 | 36700 | 100 | 36600 | 8.0209 | 6.39 | 34610.2284 | 67.53% | 17.98% | 98.04% | 98% | [9 empty] | 8.0209
2025-04-10 | 2026 | 2025 | 2025-04-01 | 30 | 11.8 | 0 |  | 4.85 |  | 0 | 40.22 | 0 | 0 | 100% |  |  | 97.37% |  |  | 83.93% |  | 16.96% | 33025 | 32750 | 100 | 32650 | 8.0209 | 6.39 | 34610.2284 | 67.53% | 17.98% | 98.04% | 98% | [9 empty] | 8.0209
2025-04-11 | 2026 | 2025 | 2025-04-01 | 30 | 12.4667 | 0 |  | 6.33 |  | 0 | 41.85 | 0 | 0 | 96.69% |  |  | 100% |  |  | 77.4% |  | 20.42% | 39702.3 | 39400 | 100 | 39300 | 8.0209 | 6.39 | 34610.2284 | 67.53% | 17.98% | 98.04% | 98% | [9 empty] | 8.0209
2025-04-12 | 2026 | 2025 | 2025-04-01 | 30 | 12.3333 | 0 |  | 6.54 |  | 0 | 43.84 | 0 | 0 | 96.52% |  |  | 100% |  |  | 73.97% |  | 20.16% | 39165 | 38900 | 100 | 38800 | 8.0209 | 6.39 | 34610.2284 | 67.53% | 17.98% | 98.04% | 98% | [9 empty] | 8.0209
2025-04-13 | 2026 | 2025 | 2025-04-01 | 30 | 12.4167 | 0 |  | 6.35 |  | 0 | 45.16 | 0 | 0 | 97.87% |  |  | 95.17% |  |  | 71.37% |  | 18.88% | 36720.4 | 36450 | 100 | 36350 | 8.0209 | 6.39 | 34610.2284 | 67.53% | 17.98% | 98.04% | 98% | [9 empty] | 8.0209
2025-04-14 | 2026 | 2025 | 2025-04-01 | 30 | 12.4667 | 0 |  | 6.09 |  | 0 | 43.95 | 0 | 0 | 96.04% |  |  | 100% |  |  | 79.12% |  | 20.08% | 39032 | 38750 | 100 | 38650 | 8.0209 | 6.39 | 34610.2284 | 67.53% | 17.98% | 98.04% | 98% | [9 empty] | 8.0209
2025-04-15 | 2026 | 2025 | 2025-04-01 | 30 | 12.6 | 0 |  | 5.28 |  | 0 | 42.86 | 0 | 0 | 98.81% |  |  | 99.3% |  |  | 80.05% |  | 17.61% | 34340 | 34000 | 100 | 33900 | 8.0209 | 6.39 | 34610.2284 | 67.53% | 17.98% | 98.04% | 98% | [9 empty] | 8.0209
2025-04-16 | 2026 | 2025 | 2025-04-01 | 30 | 12.5 | 0 |  | 5.92 |  | 0 | 42.54 | 0 | 0 | 98.36% |  |  | 93.16% |  |  | 62.13% |  | 15.32% | 29859.4 | 29600 | 100 | 29500 | 8.0209 | 6.39 | 34610.2284 | 67.53% | 17.98% | 98.04% | 98% | [9 empty] | 8.0209
2025-04-17 | 2026 | 2025 | 2025-04-01 | 30 | 12.5 | 0 |  | 5.66 |  | 0 | 43.35 | 0 | 0 | 100% |  |  | 100% |  |  | 78.75% |  | 18.57% | 36154.4 | 35850 | 100 | 35750 | 8.0209 | 6.39 | 34610.2284 | 67.53% | 17.98% | 98.04% | 98% | [9 empty] | 8.0209
2025-04-18 | 2026 | 2025 | 2025-04-01 | 30 | 12.5167 | 0 |  | 5.38 |  | 0 | 43.02 | 0 | 0 | 100% |  |  | 100% |  |  | 62.34% |  | 13.97% | 27239.5 | 27000 | 100 | 26900 | 8.0209 | 6.39 | 34610.2284 | 67.53% | 17.98% | 98.04% | 98% | [9 empty] | 8.0209
2025-04-19 | 2026 | 2025 | 2025-04-01 | 30 | 12.4167 | 0 |  | 5.54 |  | 0 | 43.31 | 0 | 0 | 100% |  |  | 95.91% |  |  | 74.94% |  | 17.3% | 33721.5 | 33400 | 100 | 33300 | 8.0209 | 6.39 | 34610.2284 | 67.53% | 17.98% | 98.04% | 98% | [9 empty] | 8.0209
2025-04-20 | 2026 | 2025 | 2025-04-01 | 30 | 12.5 | 0 |  | 5.12 |  | 0 | 45.39 | 0 | 0 | 100% |  |  | 100% |  |  | 97.77% |  | 20.86% | 40625.9 | 40250 | 100 | 40150 | 8.0209 | 6.39 | 34610.2284 | 67.53% | 17.98% | 98.04% | 98% | [9 empty] | 8.0209
2025-04-21 | 2026 | 2025 | 2025-04-01 | 30 | 12.45 | 0 |  | 5.26 |  | 0 | 43.8 | 0 | 0 | 100% |  |  | 80.25% |  |  | 68.74% |  | 15.06% | 29341.9 | 29100 | 100 | 29000 | 8.0209 | 6.39 | 34610.2284 | 67.53% | 17.98% | 98.04% | 98% | [9 empty] | 8.0209
2025-04-22 | 2026 | 2025 | 2025-04-01 | 30 | 12.5 | 0 |  | 5.79 |  | 0 | 46.12 | 0 | 0 | 100% |  |  | 100% |  |  | 73% |  | 17.61% | 34331.3 | 34000 | 100 | 33900 | 8.0209 | 6.39 | 34610.2284 | 67.53% | 17.98% | 98.04% | 98% | [9 empty] | 8.0209
2025-04-23 | 2026 | 2025 | 2025-04-01 | 30 | 12.3833 | 0 |  | 5.92 |  | 0 | 47.02 | 0 | 0 | 100% |  |  | 100% |  |  | 68.66% |  | 16.93% | 33061.4 | 32700 | 100 | 32600 | 8.0209 | 6.39 | 34610.2284 | 67.53% | 17.98% | 98.04% | 98% | [9 empty] | 8.0209
2025-04-24 | 2026 | 2025 | 2025-04-01 | 30 | 12.2333 | 0 |  | 5.6 |  | 0 | 46.38 | 0 | 0 | 100% |  |  | 97.77% |  |  | 78.37% |  | 18.29% | 35600.4 | 35300 | 100 | 35200 | 8.0209 | 6.39 | 34610.2284 | 67.53% | 17.98% | 98.04% | 98% | [9 empty] | 8.0209
2025-04-25 | 2026 | 2025 | 2025-04-01 | 30 | 12.0833 | 0 |  | 5.72 |  | 0 | 46.34 | 0 | 0 | 100% |  |  | 94.5% |  |  | 69.09% |  | 16.47% | 32081 | 31800 | 100 | 31700 | 8.0209 | 6.39 | 34610.2284 | 67.53% | 17.98% | 98.04% | 98% | [9 empty] | 8.0209
2025-04-26 | 2026 | 2025 | 2025-04-01 | 30 | 12.4167 | 0 |  | 5.2 |  | 0 | 45.56 | 0 | 0 | 100% |  |  | 99.14% |  |  | 88.35% |  | 19.14% | 37233.2 | 36900 | 50 | 36850 | 8.0209 | 6.39 | 34610.2284 | 67.53% | 17.98% | 98.04% | 98% | [9 empty] | 8.0209
2025-04-27 | 2026 | 2025 | 2025-04-01 | 30 | 12.55 | 0 |  | 4.69 |  | 0 | 41.92 | 0 | 0 | 100% |  |  | 100% |  |  | 72.57% |  | 14.18% | 27668.3 | 27400 | 100 | 27300 | 8.0209 | 6.39 | 34610.2284 | 67.53% | 17.98% | 98.04% | 98% | [9 empty] | 8.0209
2025-04-28 | 2026 | 2025 | 2025-04-01 | 30 | 12.6333 | 0 |  | 6.33 |  | 0 | 44.84 | 0 | 0 | 100% |  |  | 100% |  |  | 79.37% |  | 20.93% | 40735.3 | 40400 | 100 | 40300 | 8.0209 | 6.39 | 34610.2284 | 67.53% | 17.98% | 98.04% | 98% | [9 empty] | 8.0209
2025-04-29 | 2026 | 2025 | 2025-04-01 | 30 | 12.6 | 0 |  | 5.62 |  | 0 | 44.35 | 0 | 0 | 99.79% |  |  | 100% |  |  | 75.31% |  | 17.64% | 34322.4 | 34050 | 100 | 33950 | 8.0209 | 6.39 | 34610.2284 | 67.53% | 17.98% | 98.04% | 98% | [9 empty] | 8.0209
2025-04-30 | 2026 | 2025 | 2025-04-01 | 30 | 12.6 | 0 |  | 5.77 |  | 0 | 46.33 | 0 | 0 | 100% |  |  | 100% |  |  | 85.67% |  | 20.6% | 40093.5 | 39750 | 100 | 39650 | 8.0209 | 6.39 | 34610.2284 | 67.53% | 17.98% | 98.04% | 98% | [9 empty] | 8.0209
2025-05-01 | 2026 | 2025 | 2025-05-01 | 31 | 12.6333 | 0 |  | 5.52 |  | 0 | 45.19 | 0 | 0 | 100% |  |  | 95.49% |  |  | 84.36% |  | 19.4% | 37802.4 | 37450 | 100 | 37350 | 8.0209 | 6.0129 | 33577.7446 | 69.62% | 17.44% | 98.04% | 98% | [9 empty] | 8.0209
2025-05-02 | 2026 | 2025 | 2025-05-01 | 31 | 12.6 | 0 |  | 6.17 |  | 0 | 45.19 | 0 | 0 | 100% |  |  | 89.56% |  |  | 62.54% |  | 16.08% | 31347.7 | 31050 | 100 | 30950 | 8.0209 | 6.0129 | 33577.7446 | 69.62% | 17.44% | 98.04% | 98% | [9 empty] | 8.0209
2025-05-03 | 2026 | 2025 | 2025-05-01 | 31 | 12.5833 | 0 |  | 5.93 |  | 0 | 45.51 | 0 | 0 | 100% |  |  | 100% |  |  | 80.42% |  | 19.87% | 38672.9 | 38350 | 100 | 38250 | 8.0209 | 6.0129 | 33577.7446 | 69.62% | 17.44% | 98.04% | 98% | [9 empty] | 8.0209
2025-05-04 | 2026 | 2025 | 2025-05-01 | 31 | 12.7167 | 0 |  | 5.27 |  | 0 | 42.88 | 0 | 0 | 100% |  |  | 49% |  |  | 48.5% |  | 10.65% | 20778 | 20600 | 100 | 20500 | 8.0209 | 6.0129 | 33577.7446 | 69.62% | 17.44% | 98.04% | 98% | [9 empty] | 8.0209
2025-05-05 | 2026 | 2025 | 2025-05-01 | 31 | 12.3167 | 0 |  | 6.52 |  | 0 | 45.43 | 0 | 0 | 100% |  |  | 100% |  |  | 77.25% |  | 20.99% | 40864.5 | 40500 | 100 | 40400 | 8.0209 | 6.0129 | 33577.7446 | 69.62% | 17.44% | 98.04% | 98% | [9 empty] | 8.0209
2025-05-06 | 2026 | 2025 | 2025-05-01 | 31 | 12.5 | 0 |  | 6.2 |  | 0 | 44.26 | 0 | 0 | 100% |  |  | 100% |  |  | 77.52% |  | 20.03% | 38984.7 | 38650 | 100 | 38550 | 8.0209 | 6.0129 | 33577.7446 | 69.62% | 17.44% | 98.04% | 98% | [9 empty] | 8.0209
2025-05-07 | 2026 | 2025 | 2025-05-01 | 31 | 12.7667 | 0 |  | 6.58 |  | 0 | 43.99 | 0 | 0 | 100% |  |  | 100% |  |  | 73.9% |  | 20.26% | 39449.4 | 39100 | 100 | 39000 | 8.0209 | 6.0129 | 33577.7446 | 69.62% | 17.44% | 98.04% | 98% | [9 empty] | 8.0209
2025-05-08 | 2026 | 2025 | 2025-05-01 | 31 | 12.45 | 0 |  | 6.72 |  | 0 | 44.03 | 0 | 0 | 100% |  |  | 97.43% |  |  | 72.26% |  | 20.23% | 39372.2 | 39050 | 100 | 38950 | 8.0209 | 6.0129 | 33577.7446 | 69.62% | 17.44% | 98.04% | 98% | [9 empty] | 8.0209
2025-05-09 | 2026 | 2025 | 2025-05-01 | 31 | 12.65 | 0 |  | 6.54 |  | 0 | 44.38 | 0 | 0 | 100% |  |  | 100% |  |  | 73.58% |  | 20.05% | 39049.7 | 38700 | 100 | 38600 | 8.0209 | 6.0129 | 33577.7446 | 69.62% | 17.44% | 98.04% | 98% | [9 empty] | 8.0209
2025-05-10 | 2026 | 2025 | 2025-05-01 | 31 | 12.5 | 0 |  | 4.98 |  | 0 | 42.32 | 0 | 0 | 100% |  |  | 100% |  |  | 81.86% |  | 16.99% | 33104.3 | 32800 | 100 | 32700 | 8.0209 | 6.0129 | 33577.7446 | 69.62% | 17.44% | 98.04% | 98% | [9 empty] | 8.0209
2025-05-11 | 2026 | 2025 | 2025-05-01 | 31 | 12.75 | 0 |  | 5.82 |  | 0 | 43.47 | 0 | 0 | 100% |  |  | 100% |  |  | 72.41% |  | 17.56% | 34153.3 | 33900 | 100 | 33800 | 8.0209 | 6.0129 | 33577.7446 | 69.62% | 17.44% | 98.04% | 98% | [9 empty] | 8.0209
2025-05-12 | 2026 | 2025 | 2025-05-01 | 31 | 11.8667 | 0 |  | 6.33 |  | 0 | 44.17 | 0 | 0 | 100% |  |  | 100% |  |  | 78% |  | 20.57% | 39985.7 | 39700 | 100 | 39600 | 8.0209 | 6.0129 | 33577.7446 | 69.62% | 17.44% | 98.04% | 98% | [9 empty] | 8.0209
2025-05-13 | 2026 | 2025 | 2025-05-01 | 31 | 12.6 | 0 |  | 5.18 |  | 0 | 42.05 | 0 | 0 | 100% |  |  | 100% |  |  | 83.04% |  | 17.92% | 34932.2 | 34600 | 100 | 34500 | 8.0209 | 6.0129 | 33577.7446 | 69.62% | 17.44% | 98.04% | 98% | [9 empty] | 8.0209
2025-05-14 | 2026 | 2025 | 2025-05-01 | 31 | 12.3 | 0 |  | 5.23 |  | 0 | 41.35 | 0 | 0 | 100% |  |  | 99.99% |  |  | 80.57% |  | 17.56% | 34215.9 | 33900 | 100 | 33800 | 8.0209 | 6.0129 | 33577.7446 | 69.62% | 17.44% | 98.04% | 98% | [9 empty] | 8.0209
2025-05-15 | 2026 | 2025 | 2025-05-01 | 31 | 12.2 | 0 |  | 3.03 |  | 0 | 33.73 | 0 | 0 | 94.64% |  |  | 98.06% |  |  | 76.74% |  | 9.688% | 19019.4 | 18800 | 150 | 18650 | 8.0209 | 6.0129 | 33577.7446 | 69.62% | 17.44% | 98.04% | 98% | [9 empty] | 8.0209
2025-05-16 | 2026 | 2025 | 2025-05-01 | 31 | 12.85 | 0 |  | 5.42 |  | 0 | 41.83 | 0 | 0 | 90.58% |  |  | 95.02% |  |  | 67.63% |  | 15.27% | 29638 | 29500 | 100 | 29400 | 8.0209 | 6.0129 | 33577.7446 | 69.62% | 17.44% | 98.04% | 98% | [9 empty] | 8.0209
2025-05-17 | 2026 | 2025 | 2025-05-01 | 31 | 12.8 | 0 |  | 5.27 |  | 0 | 40.74 | 0 | 0 | 100% |  |  | 96.59% |  |  | 75.23% |  | 16.52% | 32209.8 | 31900 | 100 | 31800 | 8.0209 | 6.0129 | 33577.7446 | 69.62% | 17.44% | 98.04% | 98% | [9 empty] | 8.0209
2025-05-18 | 2026 | 2025 | 2025-05-01 | 31 | 12.65 | 0 |  | 5.23 |  | 0 | 41.05 | 0 | 0 | 100% |  |  | 59.41% |  |  | 51.49% |  | 11.22% | 21889.2 | 21700 | 100 | 21600 | 8.0209 | 6.0129 | 33577.7446 | 69.62% | 17.44% | 98.04% | 98% | [9 empty] | 8.0209
2025-05-19 | 2026 | 2025 | 2025-05-01 | 31 | 12.8 | 0 |  | 4.91 |  | 0 | 40.53 | 0 | 0 | 100% |  |  | 90.29% |  |  | 71.61% |  | 14.65% | 28476.9 | 28300 | 100 | 28200 | 8.0209 | 6.0129 | 33577.7446 | 69.62% | 17.44% | 98.04% | 98% | [9 empty] | 8.0209
2025-05-20 | 2026 | 2025 | 2025-05-01 | 31 | 12.7167 | 0 |  | 4.84 |  | 0 | 40.06 | 0 | 0 | 98.04% |  |  | 100% |  |  | 77.28% |  | 15.58% | 30308.4 | 30100 | 100 | 30000 | 8.0209 | 6.0129 | 33577.7446 | 69.62% | 17.44% | 98.04% | 98% | [9 empty] | 8.0209
2025-05-21 | 2026 | 2025 | 2025-05-01 | 31 | 12.8333 | 0 |  | 3.26 |  | 0 | 33.83 | 0 | 0 | 100% |  |  | 97.85% |  |  | 76.87% |  | 10.44% | 20402.3 | 20200 | 100 | 20100 | 8.0209 | 6.0129 | 33577.7446 | 69.62% | 17.44% | 98.04% | 98% | [9 empty] | 8.0209
2025-05-22 | 2026 | 2025 | 2025-05-01 | 31 | 12.5333 | 0 |  | 5.56 |  | 0 | 48.87 | 0 | 0 | 99.74% |  |  | 76.19% |  |  | 60.99% |  | 14.13% | 27545.8 | 27300 | 100 | 27200 | 8.0209 | 6.0129 | 33577.7446 | 69.62% | 17.44% | 98.04% | 98% | [9 empty] | 8.0209
2025-05-23 | 2026 | 2025 | 2025-05-01 | 31 | 12.8333 | 0 |  | 5.31 |  | 0 | 36.07 | 0 | 0 | 100% |  |  | 100% |  |  | 76.66% |  | 16.96% | 33052.5 | 32750 | 100 | 32650 | 8.0209 | 6.0129 | 33577.7446 | 69.62% | 17.44% | 98.04% | 98% | [9 empty] | 8.0209
2025-05-24 | 2026 | 2025 | 2025-05-01 | 31 | 12.5833 | 0 |  | 4.32 |  | 0 | 34.13 | 0 | 0 | 100% |  |  | 98.25% |  |  | 77.78% |  | 14% | 27302.8 | 27050 | 100 | 26950 | 8.0209 | 6.0129 | 33577.7446 | 69.62% | 17.44% | 98.04% | 98% | [9 empty] | 8.0209
2025-05-25 | 2026 | 2025 | 2025-05-01 | 31 | 12.8667 | 0 |  | 3.74 |  | 0 | 33.6 | 0 | 0 | 99.44% |  |  | 99.73% |  |  | 78% |  | 12.16% | 23674.3 | 23500 | 100 | 23400 | 8.0209 | 6.0129 | 33577.7446 | 69.62% | 17.44% | 98.04% | 98% | [9 empty] | 8.0209
2025-05-26 | 2026 | 2025 | 2025-05-01 | 31 | 12.8 | 0 |  | 2.88 |  | 0 | 33.68 | 0 | 0 | 100% |  |  | 99.15% |  |  | 81.38% |  | 9.766% | 19067.3 | 18900 | 100 | 18800 | 8.0209 | 6.0129 | 33577.7446 | 69.62% | 17.44% | 98.04% | 98% | [9 empty] | 8.0209
2025-05-27 | 2026 | 2025 | 2025-05-01 | 31 | 12.5833 | 0 |  | 3.04 |  | 0 | 32.93 | 0 | 0 | 100% |  |  | 96.08% |  |  | 80.59% |  | 10.21% | 19930.6 | 19750 | 100 | 19650 | 8.0209 | 6.0129 | 33577.7446 | 69.62% | 17.44% | 98.04% | 98% | [9 empty] | 8.0209
2025-05-28 | 2026 | 2025 | 2025-05-01 | 31 | 12.8333 | 0 |  | 3.25 |  | 0 | 32.46 | 0 | 0 | 100% |  |  | 100% |  |  | 84.2% |  | 11.4% | 22243 | 22050 | 100 | 21950 | 8.0209 | 6.0129 | 33577.7446 | 69.62% | 17.44% | 98.04% | 98% | [9 empty] | 8.0209
2025-05-29 | 2026 | 2025 | 2025-05-01 | 31 | 12.7333 | 0 |  | 2.67 |  | 0 | 32.15 | 0 | 0 | 100% |  |  | 100% |  |  | 87.55% |  | 9.74% | 19012.1 | 18900 | 150 | 18750 | 8.0209 | 6.0129 | 33577.7446 | 69.62% | 17.44% | 98.04% | 98% | [9 empty] | 8.0209
2025-05-30 | 2026 | 2025 | 2025-05-01 | 31 | 12.9167 | 0 |  | 5.3 |  | 0 | 37.7 | 0 | 0 | 100% |  |  | 100% |  |  | 83.04% |  | 18.34% | 35750.8 | 35400 | 100 | 35300 | 8.0209 | 6.0129 | 33577.7446 | 69.62% | 17.44% | 98.04% | 98% | [9 empty] | 8.0209
2025-05-31 | 2026 | 2025 | 2025-05-01 | 31 | 12.9833 | 0 |  | 6.1 |  | 0 | 39.9 | 0 | 0 | 100% |  |  | 100% |  |  | 81.14% |  | 20.62% | 40077.7 | 39800 | 100 | 39700 | 8.0209 | 6.0129 | 33577.7446 | 69.62% | 17.44% | 98.04% | 98% | [9 empty] | 8.0209
2025-06-01 | 2026 | 2025 | 2025-06-01 | 30 | 12.9167 | 0 |  | 5.88 |  | 0 | 39.09 | 0 | 0 | 100% |  |  | 100% |  |  | 81.63% |  | 20% | 38871.4 | 38600 | 100 | 38500 | 8.0209 | 4.76 | 25919.7483 | 67.89% | 13.46% | 98.04% | 98% | [9 empty] | 8.0209
2025-06-02 | 2026 | 2025 | 2025-06-01 | 30 | 12.8833 | 0 |  | 4.76 |  | 0 | 36.1 | 0 | 0 | 100% |  |  | 100% |  |  | 84.6% |  | 16.78% | 32605.4 | 32400 | 100 | 32300 | 8.0209 | 4.76 | 25919.7483 | 67.89% | 13.46% | 98.04% | 98% | [9 empty] | 8.0209
2025-06-03 | 2026 | 2025 | 2025-06-01 | 30 | 12.6 | 0 |  | 5.86 |  | 0 | 39.56 | 0 | 0 | 100% |  |  | 100% |  |  | 76.59% |  | 18.7% | 36404 | 36100 | 100 | 36000 | 8.0209 | 4.76 | 25919.7483 | 67.89% | 13.46% | 98.04% | 98% | [9 empty] | 8.0209
2025-06-04 | 2026 | 2025 | 2025-06-01 | 30 | 12.7333 | 0 |  | 6.25 |  | 0 | 41.45 | 0 | 0 | 100% |  |  | 100% |  |  | 81.29% |  | 21.17% | 41212.7 | 40850 | 100 | 40750 | 8.0209 | 4.76 | 25919.7483 | 67.89% | 13.46% | 98.04% | 98% | [9 empty] | 8.0209
2025-06-05 | 2026 | 2025 | 2025-06-01 | 30 | 12.6167 | 0 |  | 4.03 |  | 0 | 37.67 | 0 | 0 | 100% |  |  | 97.16% |  |  | 84.77% |  | 14.23% | 27722.7 | 27500 | 100 | 27400 | 8.0209 | 4.76 | 25919.7483 | 67.89% | 13.46% | 98.04% | 98% | [9 empty] | 8.0209
2025-06-06 | 2026 | 2025 | 2025-06-01 | 30 | 12.4833 | 0 |  | 4.75 |  | 0 | 41.22 | 0 | 0 | 100% |  |  | 100% |  |  | 78.35% |  | 15.51% | 30212.8 | 29950 | 100 | 29850 | 8.0209 | 4.76 | 25919.7483 | 67.89% | 13.46% | 98.04% | 98% | [9 empty] | 8.0209
2025-06-07 | 2026 | 2025 | 2025-06-01 | 30 | 12.9333 | 0 |  | 4.29 |  | 0 | 37.89 | 0 | 0 | 100% |  |  | 89.63% |  |  | 72.51% |  | 12.96% | 25280.1 | 25050 | 100 | 24950 | 8.0209 | 4.76 | 25919.7483 | 67.89% | 13.46% | 98.04% | 98% | [9 empty] | 8.0209
2025-06-08 | 2026 | 2025 | 2025-06-01 | 30 | 12.5333 | 0 |  | 4.79 |  | 0 | 38.24 | 0 | 0 | 100% |  |  | 100% |  |  | 82.12% |  | 16.39% | 31919.2 | 31650 | 100 | 31550 | 8.0209 | 4.76 | 25919.7483 | 67.89% | 13.46% | 98.04% | 98% | [9 empty] | 8.0209
2025-06-09 | 2026 | 2025 | 2025-06-01 | 30 | 12.1 | 0 |  | 1.05 |  | 0 | 26.95 | 0 | 0 | 100% |  |  | 59.43% |  |  | 53.43% |  | 2.338% | 4681 | 4600 | 100 | 4500 | 8.0209 | 4.76 | 25919.7483 | 67.89% | 13.46% | 98.04% | 98% | [9 empty] | 8.0209
2025-06-10 | 2026 | 2025 | 2025-06-01 | 30 | 12.6167 | 0 |  | 1.62 |  | 0 | 28.69 | 0 | 0 | 100% |  |  | 100% |  |  | 84.66% |  | 5.714% | 11204.9 | 11100 | 100 | 11000 | 8.0209 | 4.76 | 25919.7483 | 67.89% | 13.46% | 98.04% | 98% | [9 empty] | 8.0209
2025-06-11 | 2026 | 2025 | 2025-06-01 | 30 | 12.5667 | 0 |  | 3.59 |  | 0 | 32.62 | 0 | 0 | 100% |  |  | 100% |  |  | 86.47% |  | 12.93% | 25245 | 25000 | 100 | 24900 | 8.0209 | 4.76 | 25919.7483 | 67.89% | 13.46% | 98.04% | 98% | [9 empty] | 8.0209
2025-06-12 | 2026 | 2025 | 2025-06-01 | 30 | 12.6333 | 0 |  | 3.8 |  | 0 | 36.04 | 0 | 0 | 100% |  |  | 100% |  |  | 83.99% |  | 13.3% | 25924.2 | 25700 | 100 | 25600 | 8.0209 | 4.76 | 25919.7483 | 67.89% | 13.46% | 98.04% | 98% | [9 empty] | 8.0209
2025-06-13 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 4.76 | 25919.7483 | 67.89% | 13.46% | 98.04% | 98% | [9 empty] | 8.0209
2025-06-14 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 4.76 | 25919.7483 | 67.89% | 13.46% | 98.04% | 98% | [9 empty] | 8.0209
2025-06-15 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 4.76 | 25919.7483 | 67.89% | 13.46% | 98.04% | 98% | [9 empty] | 8.0209
2025-06-16 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 4.76 | 25919.7483 | 67.89% | 13.46% | 98.04% | 98% | [9 empty] | 8.0209
2025-06-17 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 4.76 | 25919.7483 | 67.89% | 13.46% | 98.04% | 98% | [9 empty] | 8.0209
2025-06-18 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 4.76 | 25919.7483 | 67.89% | 13.46% | 98.04% | 98% | [9 empty] | 8.0209
2025-06-19 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 4.76 | 25919.7483 | 67.89% | 13.46% | 98.04% | 98% | [9 empty] | 8.0209
2025-06-20 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 4.76 | 25919.7483 | 67.89% | 13.46% | 98.04% | 98% | [9 empty] | 8.0209
2025-06-21 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 4.76 | 25919.7483 | 67.89% | 13.46% | 98.04% | 98% | [9 empty] | 8.0209
2025-06-22 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 4.76 | 25919.7483 | 67.89% | 13.46% | 98.04% | 98% | [9 empty] | 8.0209
2025-06-23 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 4.76 | 25919.7483 | 67.89% | 13.46% | 98.04% | 98% | [9 empty] | 8.0209
2025-06-24 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 4.76 | 25919.7483 | 67.89% | 13.46% | 98.04% | 98% | [9 empty] | 8.0209
2025-06-25 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 4.76 | 25919.7483 | 67.89% | 13.46% | 98.04% | 98% | [9 empty] | 8.0209
2025-06-26 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 4.76 | 25919.7483 | 67.89% | 13.46% | 98.04% | 98% | [9 empty] | 8.0209
2025-06-27 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 4.76 | 25919.7483 | 67.89% | 13.46% | 98.04% | 98% | [9 empty] | 8.0209
2025-06-28 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 4.76 | 25919.7483 | 67.89% | 13.46% | 98.04% | 98% | [9 empty] | 8.0209
2025-06-29 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 4.76 | 25919.7483 | 67.89% | 13.46% | 98.04% | 98% | [9 empty] | 8.0209
2025-06-30 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 4.76 | 25919.7483 | 67.89% | 13.46% | 98.04% | 98% | [9 empty] | 8.0209
2025-07-01 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.0452 | 22929.9491 | 70.67% | 11.91% | 98.04% | 98% | [9 empty] | 8.0209
2025-07-02 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.0452 | 22929.9491 | 70.67% | 11.91% | 98.04% | 98% | [9 empty] | 8.0209
2025-07-03 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.0452 | 22929.9491 | 70.67% | 11.91% | 98.04% | 98% | [9 empty] | 8.0209
2025-07-04 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.0452 | 22929.9491 | 70.67% | 11.91% | 98.04% | 98% | [9 empty] | 8.0209
2025-07-05 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.0452 | 22929.9491 | 70.67% | 11.91% | 98.04% | 98% | [9 empty] | 8.0209
2025-07-06 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.0452 | 22929.9491 | 70.67% | 11.91% | 98.04% | 98% | [9 empty] | 8.0209
2025-07-07 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.0452 | 22929.9491 | 70.67% | 11.91% | 98.04% | 98% | [9 empty] | 8.0209
2025-07-08 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.0452 | 22929.9491 | 70.67% | 11.91% | 98.04% | 98% | [9 empty] | 8.0209
2025-07-09 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.0452 | 22929.9491 | 70.67% | 11.91% | 98.04% | 98% | [9 empty] | 8.0209
2025-07-10 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.0452 | 22929.9491 | 70.67% | 11.91% | 98.04% | 98% | [9 empty] | 8.0209
2025-07-11 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.0452 | 22929.9491 | 70.67% | 11.91% | 98.04% | 98% | [9 empty] | 8.0209
2025-07-12 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.0452 | 22929.9491 | 70.67% | 11.91% | 98.04% | 98% | [9 empty] | 8.0209
2025-07-13 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.0452 | 22929.9491 | 70.67% | 11.91% | 98.04% | 98% | [9 empty] | 8.0209
2025-07-14 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.0452 | 22929.9491 | 70.67% | 11.91% | 98.04% | 98% | [9 empty] | 8.0209
2025-07-15 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.0452 | 22929.9491 | 70.67% | 11.91% | 98.04% | 98% | [9 empty] | 8.0209
2025-07-16 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.0452 | 22929.9491 | 70.67% | 11.91% | 98.04% | 98% | [9 empty] | 8.0209
2025-07-17 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.0452 | 22929.9491 | 70.67% | 11.91% | 98.04% | 98% | [9 empty] | 8.0209
2025-07-18 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.0452 | 22929.9491 | 70.67% | 11.91% | 98.04% | 98% | [9 empty] | 8.0209
2025-07-19 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.0452 | 22929.9491 | 70.67% | 11.91% | 98.04% | 98% | [9 empty] | 8.0209
2025-07-20 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.0452 | 22929.9491 | 70.67% | 11.91% | 98.04% | 98% | [9 empty] | 8.0209
2025-07-21 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.0452 | 22929.9491 | 70.67% | 11.91% | 98.04% | 98% | [9 empty] | 8.0209
2025-07-22 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.0452 | 22929.9491 | 70.67% | 11.91% | 98.04% | 98% | [9 empty] | 8.0209
2025-07-23 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.0452 | 22929.9491 | 70.67% | 11.91% | 98.04% | 98% | [9 empty] | 8.0209
2025-07-24 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.0452 | 22929.9491 | 70.67% | 11.91% | 98.04% | 98% | [9 empty] | 8.0209
2025-07-25 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.0452 | 22929.9491 | 70.67% | 11.91% | 98.04% | 98% | [9 empty] | 8.0209
2025-07-26 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.0452 | 22929.9491 | 70.67% | 11.91% | 98.04% | 98% | [9 empty] | 8.0209
2025-07-27 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.0452 | 22929.9491 | 70.67% | 11.91% | 98.04% | 98% | [9 empty] | 8.0209
2025-07-28 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.0452 | 22929.9491 | 70.67% | 11.91% | 98.04% | 98% | [9 empty] | 8.0209
2025-07-29 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.0452 | 22929.9491 | 70.67% | 11.91% | 98.04% | 98% | [9 empty] | 8.0209
2025-07-30 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.0452 | 22929.9491 | 70.67% | 11.91% | 98.04% | 98% | [9 empty] | 8.0209
2025-07-31 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.0452 | 22929.9491 | 70.67% | 11.91% | 98.04% | 98% | [9 empty] | 8.0209
2025-08-01 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.2161 | 24273.1568 | 71.78% | 12.61% | 98.04% | 98% | [9 empty] | 8.0209
2025-08-02 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.2161 | 24273.1568 | 71.78% | 12.61% | 98.04% | 98% | [9 empty] | 8.0209
2025-08-03 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.2161 | 24273.1568 | 71.78% | 12.61% | 98.04% | 98% | [9 empty] | 8.0209
2025-08-04 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.2161 | 24273.1568 | 71.78% | 12.61% | 98.04% | 98% | [9 empty] | 8.0209
2025-08-05 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.2161 | 24273.1568 | 71.78% | 12.61% | 98.04% | 98% | [9 empty] | 8.0209
2025-08-06 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.2161 | 24273.1568 | 71.78% | 12.61% | 98.04% | 98% | [9 empty] | 8.0209
2025-08-07 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.2161 | 24273.1568 | 71.78% | 12.61% | 98.04% | 98% | [9 empty] | 8.0209
2025-08-08 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.2161 | 24273.1568 | 71.78% | 12.61% | 98.04% | 98% | [9 empty] | 8.0209
2025-08-09 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.2161 | 24273.1568 | 71.78% | 12.61% | 98.04% | 98% | [9 empty] | 8.0209
2025-08-10 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.2161 | 24273.1568 | 71.78% | 12.61% | 98.04% | 98% | [9 empty] | 8.0209
2025-08-11 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.2161 | 24273.1568 | 71.78% | 12.61% | 98.04% | 98% | [9 empty] | 8.0209
2025-08-12 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.2161 | 24273.1568 | 71.78% | 12.61% | 98.04% | 98% | [9 empty] | 8.0209
2025-08-13 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.2161 | 24273.1568 | 71.78% | 12.61% | 98.04% | 98% | [9 empty] | 8.0209
2025-08-14 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.2161 | 24273.1568 | 71.78% | 12.61% | 98.04% | 98% | [9 empty] | 8.0209
2025-08-15 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.2161 | 24273.1568 | 71.78% | 12.61% | 98.04% | 98% | [9 empty] | 8.0209
2025-08-16 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.2161 | 24273.1568 | 71.78% | 12.61% | 98.04% | 98% | [9 empty] | 8.0209
2025-08-17 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.2161 | 24273.1568 | 71.78% | 12.61% | 98.04% | 98% | [9 empty] | 8.0209
2025-08-18 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.2161 | 24273.1568 | 71.78% | 12.61% | 98.04% | 98% | [9 empty] | 8.0209
2025-08-19 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.2161 | 24273.1568 | 71.78% | 12.61% | 98.04% | 98% | [9 empty] | 8.0209
2025-08-20 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.2161 | 24273.1568 | 71.78% | 12.61% | 98.04% | 98% | [9 empty] | 8.0209
2025-08-21 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.2161 | 24273.1568 | 71.78% | 12.61% | 98.04% | 98% | [9 empty] | 8.0209
2025-08-22 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.2161 | 24273.1568 | 71.78% | 12.61% | 98.04% | 98% | [9 empty] | 8.0209
2025-08-23 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.2161 | 24273.1568 | 71.78% | 12.61% | 98.04% | 98% | [9 empty] | 8.0209
2025-08-24 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.2161 | 24273.1568 | 71.78% | 12.61% | 98.04% | 98% | [9 empty] | 8.0209
2025-08-25 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.2161 | 24273.1568 | 71.78% | 12.61% | 98.04% | 98% | [9 empty] | 8.0209
2025-08-26 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.2161 | 24273.1568 | 71.78% | 12.61% | 98.04% | 98% | [9 empty] | 8.0209
2025-08-27 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.2161 | 24273.1568 | 71.78% | 12.61% | 98.04% | 98% | [9 empty] | 8.0209
2025-08-28 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.2161 | 24273.1568 | 71.78% | 12.61% | 98.04% | 98% | [9 empty] | 8.0209
2025-08-29 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.2161 | 24273.1568 | 71.78% | 12.61% | 98.04% | 98% | [9 empty] | 8.0209
2025-08-30 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.2161 | 24273.1568 | 71.78% | 12.61% | 98.04% | 98% | [9 empty] | 8.0209
2025-08-31 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.2161 | 24273.1568 | 71.78% | 12.61% | 98.04% | 98% | [9 empty] | 8.0209
2025-09-01 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.8467 | 27099.0308 | 69.71% | 14.08% | 98.04% | 98% | [9 empty] | 8.0209
2025-09-02 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.8467 | 27099.0308 | 69.71% | 14.08% | 98.04% | 98% | [9 empty] | 8.0209
2025-09-03 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.8467 | 27099.0308 | 69.71% | 14.08% | 98.04% | 98% | [9 empty] | 8.0209
2025-09-04 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.8467 | 27099.0308 | 69.71% | 14.08% | 98.04% | 98% | [9 empty] | 8.0209
2025-09-05 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.8467 | 27099.0308 | 69.71% | 14.08% | 98.04% | 98% | [9 empty] | 8.0209
2025-09-06 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.8467 | 27099.0308 | 69.71% | 14.08% | 98.04% | 98% | [9 empty] | 8.0209
2025-09-07 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.8467 | 27099.0308 | 69.71% | 14.08% | 98.04% | 98% | [9 empty] | 8.0209
2025-09-08 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.8467 | 27099.0308 | 69.71% | 14.08% | 98.04% | 98% | [9 empty] | 8.0209
2025-09-09 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.8467 | 27099.0308 | 69.71% | 14.08% | 98.04% | 98% | [9 empty] | 8.0209
2025-09-10 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.8467 | 27099.0308 | 69.71% | 14.08% | 98.04% | 98% | [9 empty] | 8.0209
2025-09-11 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.8467 | 27099.0308 | 69.71% | 14.08% | 98.04% | 98% | [9 empty] | 8.0209
2025-09-12 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.8467 | 27099.0308 | 69.71% | 14.08% | 98.04% | 98% | [9 empty] | 8.0209
2025-09-13 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.8467 | 27099.0308 | 69.71% | 14.08% | 98.04% | 98% | [9 empty] | 8.0209
2025-09-14 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.8467 | 27099.0308 | 69.71% | 14.08% | 98.04% | 98% | [9 empty] | 8.0209
2025-09-15 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.8467 | 27099.0308 | 69.71% | 14.08% | 98.04% | 98% | [9 empty] | 8.0209
2025-09-16 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.8467 | 27099.0308 | 69.71% | 14.08% | 98.04% | 98% | [9 empty] | 8.0209
2025-09-17 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.8467 | 27099.0308 | 69.71% | 14.08% | 98.04% | 98% | [9 empty] | 8.0209
2025-09-18 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.8467 | 27099.0308 | 69.71% | 14.08% | 98.04% | 98% | [9 empty] | 8.0209
2025-09-19 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.8467 | 27099.0308 | 69.71% | 14.08% | 98.04% | 98% | [9 empty] | 8.0209
2025-09-20 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.8467 | 27099.0308 | 69.71% | 14.08% | 98.04% | 98% | [9 empty] | 8.0209
2025-09-21 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.8467 | 27099.0308 | 69.71% | 14.08% | 98.04% | 98% | [9 empty] | 8.0209
2025-09-22 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.8467 | 27099.0308 | 69.71% | 14.08% | 98.04% | 98% | [9 empty] | 8.0209
2025-09-23 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.8467 | 27099.0308 | 69.71% | 14.08% | 98.04% | 98% | [9 empty] | 8.0209
2025-09-24 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.8467 | 27099.0308 | 69.71% | 14.08% | 98.04% | 98% | [9 empty] | 8.0209
2025-09-25 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.8467 | 27099.0308 | 69.71% | 14.08% | 98.04% | 98% | [9 empty] | 8.0209
2025-09-26 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.8467 | 27099.0308 | 69.71% | 14.08% | 98.04% | 98% | [9 empty] | 8.0209
2025-09-27 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.8467 | 27099.0308 | 69.71% | 14.08% | 98.04% | 98% | [9 empty] | 8.0209
2025-09-28 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.8467 | 27099.0308 | 69.71% | 14.08% | 98.04% | 98% | [9 empty] | 8.0209
2025-09-29 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.8467 | 27099.0308 | 69.71% | 14.08% | 98.04% | 98% | [9 empty] | 8.0209
2025-09-30 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.8467 | 27099.0308 | 69.71% | 14.08% | 98.04% | 98% | [9 empty] | 8.0209
2025-10-01 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.1226 | 29797.6793 | 72.52% | 15.48% | 98.04% | 98% | [9 empty] | 8.0209
2025-10-02 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.1226 | 29797.6793 | 72.52% | 15.48% | 98.04% | 98% | [9 empty] | 8.0209
2025-10-03 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.1226 | 29797.6793 | 72.52% | 15.48% | 98.04% | 98% | [9 empty] | 8.0209
2025-10-04 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.1226 | 29797.6793 | 72.52% | 15.48% | 98.04% | 98% | [9 empty] | 8.0209
2025-10-05 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.1226 | 29797.6793 | 72.52% | 15.48% | 98.04% | 98% | [9 empty] | 8.0209
2025-10-06 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.1226 | 29797.6793 | 72.52% | 15.48% | 98.04% | 98% | [9 empty] | 8.0209
2025-10-07 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.1226 | 29797.6793 | 72.52% | 15.48% | 98.04% | 98% | [9 empty] | 8.0209
2025-10-08 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.1226 | 29797.6793 | 72.52% | 15.48% | 98.04% | 98% | [9 empty] | 8.0209
2025-10-09 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.1226 | 29797.6793 | 72.52% | 15.48% | 98.04% | 98% | [9 empty] | 8.0209
2025-10-10 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.1226 | 29797.6793 | 72.52% | 15.48% | 98.04% | 98% | [9 empty] | 8.0209
2025-10-11 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.1226 | 29797.6793 | 72.52% | 15.48% | 98.04% | 98% | [9 empty] | 8.0209
2025-10-12 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.1226 | 29797.6793 | 72.52% | 15.48% | 98.04% | 98% | [9 empty] | 8.0209
2025-10-13 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.1226 | 29797.6793 | 72.52% | 15.48% | 98.04% | 98% | [9 empty] | 8.0209
2025-10-14 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.1226 | 29797.6793 | 72.52% | 15.48% | 98.04% | 98% | [9 empty] | 8.0209
2025-10-15 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.1226 | 29797.6793 | 72.52% | 15.48% | 98.04% | 98% | [9 empty] | 8.0209
2025-10-16 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.1226 | 29797.6793 | 72.52% | 15.48% | 98.04% | 98% | [9 empty] | 8.0209
2025-10-17 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.1226 | 29797.6793 | 72.52% | 15.48% | 98.04% | 98% | [9 empty] | 8.0209
2025-10-18 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.1226 | 29797.6793 | 72.52% | 15.48% | 98.04% | 98% | [9 empty] | 8.0209
2025-10-19 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.1226 | 29797.6793 | 72.52% | 15.48% | 98.04% | 98% | [9 empty] | 8.0209
2025-10-20 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.1226 | 29797.6793 | 72.52% | 15.48% | 98.04% | 98% | [9 empty] | 8.0209
2025-10-21 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.1226 | 29797.6793 | 72.52% | 15.48% | 98.04% | 98% | [9 empty] | 8.0209
2025-10-22 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.1226 | 29797.6793 | 72.52% | 15.48% | 98.04% | 98% | [9 empty] | 8.0209
2025-10-23 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.1226 | 29797.6793 | 72.52% | 15.48% | 98.04% | 98% | [9 empty] | 8.0209
2025-10-24 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.1226 | 29797.6793 | 72.52% | 15.48% | 98.04% | 98% | [9 empty] | 8.0209
2025-10-25 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.1226 | 29797.6793 | 72.52% | 15.48% | 98.04% | 98% | [9 empty] | 8.0209
2025-10-26 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.1226 | 29797.6793 | 72.52% | 15.48% | 98.04% | 98% | [9 empty] | 8.0209
2025-10-27 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.1226 | 29797.6793 | 72.52% | 15.48% | 98.04% | 98% | [9 empty] | 8.0209
2025-10-28 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.1226 | 29797.6793 | 72.52% | 15.48% | 98.04% | 98% | [9 empty] | 8.0209
2025-10-29 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.1226 | 29797.6793 | 72.52% | 15.48% | 98.04% | 98% | [9 empty] | 8.0209
2025-10-30 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.1226 | 29797.6793 | 72.52% | 15.48% | 98.04% | 98% | [9 empty] | 8.0209
2025-10-31 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.1226 | 29797.6793 | 72.52% | 15.48% | 98.04% | 98% | [9 empty] | 8.0209
2025-11-01 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.4333 | 30935.3689 | 70.98% | 16.07% | 98.04% | 98% | [9 empty] | 8.0209
2025-11-02 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.4333 | 30935.3689 | 70.98% | 16.07% | 98.04% | 98% | [9 empty] | 8.0209
2025-11-03 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.4333 | 30935.3689 | 70.98% | 16.07% | 98.04% | 98% | [9 empty] | 8.0209
2025-11-04 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.4333 | 30935.3689 | 70.98% | 16.07% | 98.04% | 98% | [9 empty] | 8.0209
2025-11-05 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.4333 | 30935.3689 | 70.98% | 16.07% | 98.04% | 98% | [9 empty] | 8.0209
2025-11-06 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.4333 | 30935.3689 | 70.98% | 16.07% | 98.04% | 98% | [9 empty] | 8.0209
2025-11-07 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.4333 | 30935.3689 | 70.98% | 16.07% | 98.04% | 98% | [9 empty] | 8.0209
2025-11-08 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.4333 | 30935.3689 | 70.98% | 16.07% | 98.04% | 98% | [9 empty] | 8.0209
2025-11-09 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.4333 | 30935.3689 | 70.98% | 16.07% | 98.04% | 98% | [9 empty] | 8.0209
2025-11-10 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.4333 | 30935.3689 | 70.98% | 16.07% | 98.04% | 98% | [9 empty] | 8.0209
2025-11-11 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.4333 | 30935.3689 | 70.98% | 16.07% | 98.04% | 98% | [9 empty] | 8.0209
2025-11-12 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.4333 | 30935.3689 | 70.98% | 16.07% | 98.04% | 98% | [9 empty] | 8.0209
2025-11-13 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.4333 | 30935.3689 | 70.98% | 16.07% | 98.04% | 98% | [9 empty] | 8.0209
2025-11-14 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.4333 | 30935.3689 | 70.98% | 16.07% | 98.04% | 98% | [9 empty] | 8.0209
2025-11-15 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.4333 | 30935.3689 | 70.98% | 16.07% | 98.04% | 98% | [9 empty] | 8.0209
2025-11-16 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.4333 | 30935.3689 | 70.98% | 16.07% | 98.04% | 98% | [9 empty] | 8.0209
2025-11-17 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.4333 | 30935.3689 | 70.98% | 16.07% | 98.04% | 98% | [9 empty] | 8.0209
2025-11-18 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.4333 | 30935.3689 | 70.98% | 16.07% | 98.04% | 98% | [9 empty] | 8.0209
2025-11-19 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.4333 | 30935.3689 | 70.98% | 16.07% | 98.04% | 98% | [9 empty] | 8.0209
2025-11-20 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.4333 | 30935.3689 | 70.98% | 16.07% | 98.04% | 98% | [9 empty] | 8.0209
2025-11-21 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.4333 | 30935.3689 | 70.98% | 16.07% | 98.04% | 98% | [9 empty] | 8.0209
2025-11-22 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.4333 | 30935.3689 | 70.98% | 16.07% | 98.04% | 98% | [9 empty] | 8.0209
2025-11-23 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.4333 | 30935.3689 | 70.98% | 16.07% | 98.04% | 98% | [9 empty] | 8.0209
2025-11-24 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.4333 | 30935.3689 | 70.98% | 16.07% | 98.04% | 98% | [9 empty] | 8.0209
2025-11-25 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.4333 | 30935.3689 | 70.98% | 16.07% | 98.04% | 98% | [9 empty] | 8.0209
2025-11-26 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.4333 | 30935.3689 | 70.98% | 16.07% | 98.04% | 98% | [9 empty] | 8.0209
2025-11-27 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.4333 | 30935.3689 | 70.98% | 16.07% | 98.04% | 98% | [9 empty] | 8.0209
2025-11-28 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.4333 | 30935.3689 | 70.98% | 16.07% | 98.04% | 98% | [9 empty] | 8.0209
2025-11-29 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.4333 | 30935.3689 | 70.98% | 16.07% | 98.04% | 98% | [9 empty] | 8.0209
2025-11-30 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.4333 | 30935.3689 | 70.98% | 16.07% | 98.04% | 98% | [9 empty] | 8.0209
2025-12-01 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.2806 | 31172.6933 | 73.6% | 16.19% | 98.04% | 98% | [9 empty] | 8.0209
2025-12-02 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.2806 | 31172.6933 | 73.6% | 16.19% | 98.04% | 98% | [9 empty] | 8.0209
2025-12-03 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.2806 | 31172.6933 | 73.6% | 16.19% | 98.04% | 98% | [9 empty] | 8.0209
2025-12-04 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.2806 | 31172.6933 | 73.6% | 16.19% | 98.04% | 98% | [9 empty] | 8.0209
2025-12-05 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.2806 | 31172.6933 | 73.6% | 16.19% | 98.04% | 98% | [9 empty] | 8.0209
2025-12-06 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.2806 | 31172.6933 | 73.6% | 16.19% | 98.04% | 98% | [9 empty] | 8.0209
2025-12-07 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.2806 | 31172.6933 | 73.6% | 16.19% | 98.04% | 98% | [9 empty] | 8.0209
2025-12-08 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.2806 | 31172.6933 | 73.6% | 16.19% | 98.04% | 98% | [9 empty] | 8.0209
2025-12-09 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.2806 | 31172.6933 | 73.6% | 16.19% | 98.04% | 98% | [9 empty] | 8.0209
2025-12-10 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.2806 | 31172.6933 | 73.6% | 16.19% | 98.04% | 98% | [9 empty] | 8.0209
2025-12-11 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.2806 | 31172.6933 | 73.6% | 16.19% | 98.04% | 98% | [9 empty] | 8.0209
2025-12-12 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.2806 | 31172.6933 | 73.6% | 16.19% | 98.04% | 98% | [9 empty] | 8.0209
2025-12-13 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.2806 | 31172.6933 | 73.6% | 16.19% | 98.04% | 98% | [9 empty] | 8.0209
2025-12-14 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.2806 | 31172.6933 | 73.6% | 16.19% | 98.04% | 98% | [9 empty] | 8.0209
2025-12-15 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.2806 | 31172.6933 | 73.6% | 16.19% | 98.04% | 98% | [9 empty] | 8.0209
2025-12-16 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.2806 | 31172.6933 | 73.6% | 16.19% | 98.04% | 98% | [9 empty] | 8.0209
2025-12-17 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.2806 | 31172.6933 | 73.6% | 16.19% | 98.04% | 98% | [9 empty] | 8.0209
2025-12-18 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.2806 | 31172.6933 | 73.6% | 16.19% | 98.04% | 98% | [9 empty] | 8.0209
2025-12-19 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.2806 | 31172.6933 | 73.6% | 16.19% | 98.04% | 98% | [9 empty] | 8.0209
2025-12-20 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.2806 | 31172.6933 | 73.6% | 16.19% | 98.04% | 98% | [9 empty] | 8.0209
2025-12-21 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.2806 | 31172.6933 | 73.6% | 16.19% | 98.04% | 98% | [9 empty] | 8.0209
2025-12-22 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.2806 | 31172.6933 | 73.6% | 16.19% | 98.04% | 98% | [9 empty] | 8.0209
2025-12-23 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.2806 | 31172.6933 | 73.6% | 16.19% | 98.04% | 98% | [9 empty] | 8.0209
2025-12-24 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.2806 | 31172.6933 | 73.6% | 16.19% | 98.04% | 98% | [9 empty] | 8.0209
2025-12-25 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.2806 | 31172.6933 | 73.6% | 16.19% | 98.04% | 98% | [9 empty] | 8.0209
2025-12-26 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.2806 | 31172.6933 | 73.6% | 16.19% | 98.04% | 98% | [9 empty] | 8.0209
2025-12-27 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.2806 | 31172.6933 | 73.6% | 16.19% | 98.04% | 98% | [9 empty] | 8.0209
2025-12-28 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.2806 | 31172.6933 | 73.6% | 16.19% | 98.04% | 98% | [9 empty] | 8.0209
2025-12-29 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.2806 | 31172.6933 | 73.6% | 16.19% | 98.04% | 98% | [9 empty] | 8.0209
2025-12-30 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.2806 | 31172.6933 | 73.6% | 16.19% | 98.04% | 98% | [9 empty] | 8.0209
2025-12-31 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.2806 | 31172.6933 | 73.6% | 16.19% | 98.04% | 98% | [9 empty] | 8.0209
2026-01-01 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.9323 | 34475.663 | 72.46% | 17.91% | 98.04% | 98% | [9 empty] | 8.0209
2026-01-02 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.9323 | 34475.663 | 72.46% | 17.91% | 98.04% | 98% | [9 empty] | 8.0209
2026-01-03 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.9323 | 34475.663 | 72.46% | 17.91% | 98.04% | 98% | [9 empty] | 8.0209
2026-01-04 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.9323 | 34475.663 | 72.46% | 17.91% | 98.04% | 98% | [9 empty] | 8.0209
2026-01-05 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.9323 | 34475.663 | 72.46% | 17.91% | 98.04% | 98% | [9 empty] | 8.0209
2026-01-06 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.9323 | 34475.663 | 72.46% | 17.91% | 98.04% | 98% | [9 empty] | 8.0209
2026-01-07 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.9323 | 34475.663 | 72.46% | 17.91% | 98.04% | 98% | [9 empty] | 8.0209
2026-01-08 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.9323 | 34475.663 | 72.46% | 17.91% | 98.04% | 98% | [9 empty] | 8.0209
2026-01-09 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.9323 | 34475.663 | 72.46% | 17.91% | 98.04% | 98% | [9 empty] | 8.0209
2026-01-10 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.9323 | 34475.663 | 72.46% | 17.91% | 98.04% | 98% | [9 empty] | 8.0209
2026-01-11 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.9323 | 34475.663 | 72.46% | 17.91% | 98.04% | 98% | [9 empty] | 8.0209
2026-01-12 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.9323 | 34475.663 | 72.46% | 17.91% | 98.04% | 98% | [9 empty] | 8.0209
2026-01-13 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.9323 | 34475.663 | 72.46% | 17.91% | 98.04% | 98% | [9 empty] | 8.0209
2026-01-14 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.9323 | 34475.663 | 72.46% | 17.91% | 98.04% | 98% | [9 empty] | 8.0209
2026-01-15 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.9323 | 34475.663 | 72.46% | 17.91% | 98.04% | 98% | [9 empty] | 8.0209
2026-01-16 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.9323 | 34475.663 | 72.46% | 17.91% | 98.04% | 98% | [9 empty] | 8.0209
2026-01-17 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.9323 | 34475.663 | 72.46% | 17.91% | 98.04% | 98% | [9 empty] | 8.0209
2026-01-18 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.9323 | 34475.663 | 72.46% | 17.91% | 98.04% | 98% | [9 empty] | 8.0209
2026-01-19 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.9323 | 34475.663 | 72.46% | 17.91% | 98.04% | 98% | [9 empty] | 8.0209
2026-01-20 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.9323 | 34475.663 | 72.46% | 17.91% | 98.04% | 98% | [9 empty] | 8.0209
2026-01-21 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.9323 | 34475.663 | 72.46% | 17.91% | 98.04% | 98% | [9 empty] | 8.0209
2026-01-22 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.9323 | 34475.663 | 72.46% | 17.91% | 98.04% | 98% | [9 empty] | 8.0209
2026-01-23 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.9323 | 34475.663 | 72.46% | 17.91% | 98.04% | 98% | [9 empty] | 8.0209
2026-01-24 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.9323 | 34475.663 | 72.46% | 17.91% | 98.04% | 98% | [9 empty] | 8.0209
2026-01-25 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.9323 | 34475.663 | 72.46% | 17.91% | 98.04% | 98% | [9 empty] | 8.0209
2026-01-26 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.9323 | 34475.663 | 72.46% | 17.91% | 98.04% | 98% | [9 empty] | 8.0209
2026-01-27 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.9323 | 34475.663 | 72.46% | 17.91% | 98.04% | 98% | [9 empty] | 8.0209
2026-01-28 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.9323 | 34475.663 | 72.46% | 17.91% | 98.04% | 98% | [9 empty] | 8.0209
2026-01-29 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.9323 | 34475.663 | 72.46% | 17.91% | 98.04% | 98% | [9 empty] | 8.0209
2026-01-30 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.9323 | 34475.663 | 72.46% | 17.91% | 98.04% | 98% | [9 empty] | 8.0209
2026-01-31 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.9323 | 34475.663 | 72.46% | 17.91% | 98.04% | 98% | [9 empty] | 8.0209
2026-02-01 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.5714 | 33989.3402 | 64.49% | 17.66% | 98.04% | 98% | [9 empty] | 8.0209
2026-02-02 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.5714 | 33989.3402 | 64.49% | 17.66% | 98.04% | 98% | [9 empty] | 8.0209
2026-02-03 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.5714 | 33989.3402 | 64.49% | 17.66% | 98.04% | 98% | [9 empty] | 8.0209
2026-02-04 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.5714 | 33989.3402 | 64.49% | 17.66% | 98.04% | 98% | [9 empty] | 8.0209
2026-02-05 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.5714 | 33989.3402 | 64.49% | 17.66% | 98.04% | 98% | [9 empty] | 8.0209
2026-02-06 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.5714 | 33989.3402 | 64.49% | 17.66% | 98.04% | 98% | [9 empty] | 8.0209
2026-02-07 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.5714 | 33989.3402 | 64.49% | 17.66% | 98.04% | 98% | [9 empty] | 8.0209
2026-02-08 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.5714 | 33989.3402 | 64.49% | 17.66% | 98.04% | 98% | [9 empty] | 8.0209
2026-02-09 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.5714 | 33989.3402 | 64.49% | 17.66% | 98.04% | 98% | [9 empty] | 8.0209
2026-02-10 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.5714 | 33989.3402 | 64.49% | 17.66% | 98.04% | 98% | [9 empty] | 8.0209
2026-02-11 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.5714 | 33989.3402 | 64.49% | 17.66% | 98.04% | 98% | [9 empty] | 8.0209
2026-02-12 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.5714 | 33989.3402 | 64.49% | 17.66% | 98.04% | 98% | [9 empty] | 8.0209
2026-02-13 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.5714 | 33989.3402 | 64.49% | 17.66% | 98.04% | 98% | [9 empty] | 8.0209
2026-02-14 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.5714 | 33989.3402 | 64.49% | 17.66% | 98.04% | 98% | [9 empty] | 8.0209
2026-02-15 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.5714 | 33989.3402 | 64.49% | 17.66% | 98.04% | 98% | [9 empty] | 8.0209
2026-02-16 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.5714 | 33989.3402 | 64.49% | 17.66% | 98.04% | 98% | [9 empty] | 8.0209
2026-02-17 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.5714 | 33989.3402 | 64.49% | 17.66% | 98.04% | 98% | [9 empty] | 8.0209
2026-02-18 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.5714 | 33989.3402 | 64.49% | 17.66% | 98.04% | 98% | [9 empty] | 8.0209
2026-02-19 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.5714 | 33989.3402 | 64.49% | 17.66% | 98.04% | 98% | [9 empty] | 8.0209
2026-02-20 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.5714 | 33989.3402 | 64.49% | 17.66% | 98.04% | 98% | [9 empty] | 8.0209
2026-02-21 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.5714 | 33989.3402 | 64.49% | 17.66% | 98.04% | 98% | [9 empty] | 8.0209
2026-02-22 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.5714 | 33989.3402 | 64.49% | 17.66% | 98.04% | 98% | [9 empty] | 8.0209
2026-02-23 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.5714 | 33989.3402 | 64.49% | 17.66% | 98.04% | 98% | [9 empty] | 8.0209
2026-02-24 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.5714 | 33989.3402 | 64.49% | 17.66% | 98.04% | 98% | [9 empty] | 8.0209
2026-02-25 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.5714 | 33989.3402 | 64.49% | 17.66% | 98.04% | 98% | [9 empty] | 8.0209
2026-02-26 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.5714 | 33989.3402 | 64.49% | 17.66% | 98.04% | 98% | [9 empty] | 8.0209
2026-02-27 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.5714 | 33989.3402 | 64.49% | 17.66% | 98.04% | 98% | [9 empty] | 8.0209
2026-02-28 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.5714 | 33989.3402 | 64.49% | 17.66% | 98.04% | 98% | [9 empty] | 8.0209
2026-03-01 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.7871 | 38219.0285 | 70.21% | 19.85% | 98.04% | 98% | [9 empty] | 8.0209
2026-03-02 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.7871 | 38219.0285 | 70.21% | 19.85% | 98.04% | 98% | [9 empty] | 8.0209
2026-03-03 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.7871 | 38219.0285 | 70.21% | 19.85% | 98.04% | 98% | [9 empty] | 8.0209
2026-03-04 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.7871 | 38219.0285 | 70.21% | 19.85% | 98.04% | 98% | [9 empty] | 8.0209
2026-03-05 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.7871 | 38219.0285 | 70.21% | 19.85% | 98.04% | 98% | [9 empty] | 8.0209
2026-03-06 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.7871 | 38219.0285 | 70.21% | 19.85% | 98.04% | 98% | [9 empty] | 8.0209
2026-03-07 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.7871 | 38219.0285 | 70.21% | 19.85% | 98.04% | 98% | [9 empty] | 8.0209
2026-03-08 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.7871 | 38219.0285 | 70.21% | 19.85% | 98.04% | 98% | [9 empty] | 8.0209
2026-03-09 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.7871 | 38219.0285 | 70.21% | 19.85% | 98.04% | 98% | [9 empty] | 8.0209
2026-03-10 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.7871 | 38219.0285 | 70.21% | 19.85% | 98.04% | 98% | [9 empty] | 8.0209
2026-03-11 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.7871 | 38219.0285 | 70.21% | 19.85% | 98.04% | 98% | [9 empty] | 8.0209
2026-03-12 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.7871 | 38219.0285 | 70.21% | 19.85% | 98.04% | 98% | [9 empty] | 8.0209
2026-03-13 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.7871 | 38219.0285 | 70.21% | 19.85% | 98.04% | 98% | [9 empty] | 8.0209
2026-03-14 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.7871 | 38219.0285 | 70.21% | 19.85% | 98.04% | 98% | [9 empty] | 8.0209
2026-03-15 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.7871 | 38219.0285 | 70.21% | 19.85% | 98.04% | 98% | [9 empty] | 8.0209
2026-03-16 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.7871 | 38219.0285 | 70.21% | 19.85% | 98.04% | 98% | [9 empty] | 8.0209
2026-03-17 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.7871 | 38219.0285 | 70.21% | 19.85% | 98.04% | 98% | [9 empty] | 8.0209
2026-03-18 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.7871 | 38219.0285 | 70.21% | 19.85% | 98.04% | 98% | [9 empty] | 8.0209
2026-03-19 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.7871 | 38219.0285 | 70.21% | 19.85% | 98.04% | 98% | [9 empty] | 8.0209
2026-03-20 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.7871 | 38219.0285 | 70.21% | 19.85% | 98.04% | 98% | [9 empty] | 8.0209
2026-03-21 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.7871 | 38219.0285 | 70.21% | 19.85% | 98.04% | 98% | [9 empty] | 8.0209
2026-03-22 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.7871 | 38219.0285 | 70.21% | 19.85% | 98.04% | 98% | [9 empty] | 8.0209
2026-03-23 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.7871 | 38219.0285 | 70.21% | 19.85% | 98.04% | 98% | [9 empty] | 8.0209
2026-03-24 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.7871 | 38219.0285 | 70.21% | 19.85% | 98.04% | 98% | [9 empty] | 8.0209
2026-03-25 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.7871 | 38219.0285 | 70.21% | 19.85% | 98.04% | 98% | [9 empty] | 8.0209
2026-03-26 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.7871 | 38219.0285 | 70.21% | 19.85% | 98.04% | 98% | [9 empty] | 8.0209
2026-03-27 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.7871 | 38219.0285 | 70.21% | 19.85% | 98.04% | 98% | [9 empty] | 8.0209
2026-03-28 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.7871 | 38219.0285 | 70.21% | 19.85% | 98.04% | 98% | [9 empty] | 8.0209
2026-03-29 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.7871 | 38219.0285 | 70.21% | 19.85% | 98.04% | 98% | [9 empty] | 8.0209
2026-03-30 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.7871 | 38219.0285 | 70.21% | 19.85% | 98.04% | 98% | [9 empty] | 8.0209
2026-03-31 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.7871 | 38219.0285 | 70.21% | 19.85% | 98.04% | 98% | [9 empty] | 8.0209
Formulas:
Month Year = Table13[[#This Row],[Date]]-DAY(Table13[[#This Row],[Date]])+1
Days = DAY(EOMONTH([Date],0))
Date = [Date, row above]+1

## Raw Data
[7 empty] | 2 | 3 | 4 | [12 empty] | 5 | 6 | 7 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Finacial Year | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Date | Plant DC Capcity (MW) | Sunrise Time (POA>20 W/m2) | Sunset Time (POA<20 W/m2) | Inv1_U1 | Inv1_U2 | Inv1_U3 | Inv1_U4 | Inv2_U1 | Inv2_U2 | Inv2_U3 | Inv2_U4 | Inv3_U1 | Inv3_U2 | Inv3_U3 | Inv3_U4 | Inv1 | Inv2 | Inv3 | 33 kV Outgoinng Export Reading | 33 kV Outgoinng Import Reading | GHI(Wh/m2) | POA(kWh/m2) | Avg. Ambient Temp (POA>20W/m2) | Avg. Module Temp (POA>20W/m2) | Avg. Wind Speed (m/s) | Max. Wind Speed (m/s) | Rain Fall (mm) | Inverters Generation ( kWh) | Export (kWh) | Import (kWh) | Net Export (kWh) | Operating hours | Remarks
2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | 2025-03-29 | 8.0209 | 0.26389 | 0.76736 | 1933.8 | 2016.7 | 0 | 1936 | 2747.8 | 2648.6 | 2650.9 | 0 | 2806.3 | 2812.7 | 2801.6 | 2846.6 | 5886.5 | 8047.3 | 11267.2 | 87507.7 | 396.05 |  | 5.53 | 0 | 45.37 | 0 | 0 |  | 25201 | #REF! | #REF! | #REF! | 12.0833
2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | 2025-03-30 | 8.0209 | 0.26389 | 0.76806 | 2170.2 | 2173 | 0 | 2259.9 | 2967.5 | 2865.8 | 2866.5 | 0 | 3098.3 | 3030.7 | 3023.5 | 2998.6 | 6603.1 | 8699.8 | 12151.1 | 87534.9 | 396.15 |  | 5.95 | 0 | 45.2 | 0 | 0 |  | 27454 | 27200 | 100 | 27100 | 12.1
2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | 2025-03-31 | 8.0209 | 0.26389 | 0.77014 | 2297 | 2214 | 0 | 2215 | 2897 | 2877.3 | 2966.3 | 0 | 3044.5 | 3047.9 | 3105.3 | 3011.9 | 6726 | 8740.6 | 12209.6 | 87562.3 | 396.25 |  | 5.99 | 0 | 44.04 | 0 | 0 |  | 27676.2 | 27400 | 100 | 27300 | 12.15
2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-01 | 8.0209 | 0.26389 | 0.76597 | 2241.5 | 2332.1 | 0 | 2244.3 | 3001.1 | 2891.7 | 2895.1 | 0 | 3062.7 | 3066.2 | 3053.9 | 3094 | 6817.9 | 8787.9 | 12276.8 | 87589.95 | 396.35 |  | 6.04 | 0 | 45.06 | 0 | 0 |  | 27882.6 | 27650 | 100 | 27550 | 12.05
2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-02 | 8.0209 | 0.26319 | 0.77292 | 1871.4 | 1873.4 | 0 | 1962.2 | 3313.2 | 3198.2 | 3202.5 | 0 | 3474.5 | 3406.2 | 3392.8 | 3366.5 | 5707 | 9713.9 | 13640 | 87618.75 | 396.45 |  | 6.71 | 0 | 44.65 | 0 | 0 |  | 29060.9 | 28800 | 100 | 28700 | 12.2333
2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-03 | 8.0209 | 0.26319 | 0.74028 | 1305.6 | 1299.4 | 0 | 1230.1 | 1525.9 | 1646.2 | 1517.1 | 0 | 1600 | 1793 | 1598.9 | 1587.1 | 3835.1 | 4689.2 | 6579 | 87633.7 | 396.55 |  | 3.79 | 0 | 36.42 | 0 | 0 |  | 15103.3 | 14950 | 100 | 14850 | 11.45
2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-04 | 8.0209 | 0.25625 | 0.77083 | 1897 | 1939.6 | 0 | 1919 | 4131 | 4185.2 | 4108 | 0 | 3620.8 | 3534.5 | 3520.7 | 3494.1 | 5755.6 | 12424.2 | 14170.1 | 87665.75 | 396.65 |  | 6.83 | 0 | 44.06 | 0 | 0 |  | 32349.9 | 32050 | 100 | 31950 | 12.35
2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-05 | 8.0209 | 0.25833 | 0.76875 | 1634.8 | 1638.1 | 0 | 1708.3 | 4161 | 4130.8 | 4204.3 | 0 | 3583.4 | 3647.3 | 3569.8 | 3541.2 | 4981.2 | 12496.1 | 14341.7 | 87697.35 | 396.75 |  | 6.96 | 0 | 46.18 | 0 | 0 |  | 31819 | 31600 | 100 | 31500 | 12.25
2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-06 | 8.0209 | 0.26111 | 0.76944 | 2178.2 | 2181.8 | 0 | 2243 | 4543.8 | 4462.9 | 4472 | 0 | 3545 | 3550 | 3581.7 | 3506.5 | 6603 | 13478.7 | 14183.2 | 87731.35 | 396.85 |  | 6.77 | 0 | 45.22 | 0 | 0 |  | 34264.9 | 34000 | 100 | 33900 | 12.2
2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-07 | 8.0209 | 0.25833 | 0.76875 | 3305 | 3239.4 | 0 | 3239.2 | 4057.7 | 3964.9 | 3971 | 0 | 3450.2 | 3452.7 | 3437.5 | 3467.4 | 9783.6 | 11993.6 | 13807.8 | 87766.65 | 396.95 |  | 5.97 | 0 | 45.66 | 0 | 0 |  | 35585 | 35300 | 100 | 35200 | 12.25
2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-08 | 8.0209 | 0.25764 | 0.76597 | 3922.9 | 3922.4 | 0 | 4007.1 | 3889.5 | 3789.1 | 3795.7 | 0 | 3096.5 | 3020.9 | 3009.4 | 2984.3 | 11852.4 | 11474.3 | 12111.1 | 87801.8 | 397.05 |  | 5.83 | 0 | 43.19 | 0 | 0 |  | 35437.8 | 35150 | 100 | 35050 | 12.2
2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-09 | 8.0209 | 0.25694 | 0.76667 | 4071.2 | 4162.8 | 0 | 4079.7 | 3828.1 | 3895.3 | 3811.2 | 0 | 3274.5 | 3354.9 | 3264.9 | 3237.4 | 12313.7 | 11534.6 | 13131.7 | 87838.5 | 397.15 |  | 6.34 | 0 | 44.41 | 0 | 0 |  | 36980 | 36700 | 100 | 36600 | 12.2333
2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-10 | 8.0209 | 0.25833 | 0.75 | 3679.6 | 3680 | 0 | 3757 | 3539.7 | 3519 | 3602.9 | 0 | 2800.5 | 2805.8 | 2868.5 | 2772 | 11116.6 | 10661.6 | 11246.8 | 87871.25 | 397.25 |  | 4.85 | 0 | 40.22 | 0 | 0 |  | 33025 | 32750 | 100 | 32650 | 11.8 | Pyranometer sent for Calibration.Poa Values are Taken From 7 MW DRES Medchal Site.
2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-11 | 8.0209 | 0.24861 | 0.76806 | 4387.2 | 4389.2 | 0 | 4454.9 | 4209.5 | 4119.8 | 4126.1 | 0 | 3499.3 | 3504.2 | 3490.8 | 3521.3 | 13231.3 | 12455.4 | 14015.6 | 87910.65 | 397.35 |  | 6.33 | 0 | 41.85 | 0 | 0 |  | 39702.3 | 39400 | 100 | 39300 | 12.4667 | Pyranometer sent for Calibration.Poa Values are Taken From 7 MW DRES Medchal Site.
2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-12 | 8.0209 | 0.25347 | 0.76736 | 4404.2 | 4455.3 | 0 | 4412.2 | 3896.2 | 3921.6 | 3876.4 | 0 | 3548.7 | 3597.4 | 3540.1 | 3512.9 | 13271.7 | 11694.2 | 14199.1 | 87949.55 | 397.45 |  | 6.54 | 0 | 43.84 | 0 | 0 |  | 39165 | 38900 | 100 | 38800 | 12.3333 | Pyranometer sent for Calibration.Poa Values are Taken From 7 MW DRES Medchal Site.
2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-13 | 8.0209 | 0.25139 | 0.76875 | 4147.2 | 4149.4 | 0 | 4214.5 | 3709 | 3625.1 | 3630.6 | 0 | 3303.9 | 3311 | 3297.7 | 3332 | 12511.1 | 10964.7 | 13244.6 | 87986 | 397.55 |  | 6.35 | 0 | 45.16 | 0 | 0 |  | 36720.4 | 36450 | 100 | 36350 | 12.4167 | Pyranometer sent for Calibration.Poa Values are Taken From 7 MW DRES Medchal Site.
2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-14 | 8.0209 | 0.25069 | 0.77014 | 4387.7 | 4311.6 | 0 | 4309.5 | 4036.7 | 4090.1 | 4017 | 0 | 3543.1 | 3464.9 | 3449.9 | 3421.5 | 13008.8 | 12143.8 | 13879.4 | 88024.75 | 397.65 |  | 6.09 | 0 | 43.95 | 0 | 0 |  | 39032 | 38750 | 100 | 38650 | 12.4667 | Pyranometer sent for Calibration.Poa Values are Taken From 7 MW DRES Medchal Site.
2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-15 | 8.0209 | 0.25069 | 0.77569 | 3868.8 | 3934 | 0 | 3869.6 | 3670.1 | 3581 | 3585 | 0 | 2948.9 | 3019.8 | 2943.8 | 2919 | 11672.4 | 10836.1 | 11831.5 | 88058.75 | 397.75 |  | 5.28 | 0 | 42.86 | 0 | 0 |  | 34340 | 34000 | 100 | 33900 | 12.6 | Pyranometer sent for Calibration.Poa Values are Taken From 7 MW DRES Medchal Site.
2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-16 | 8.0209 | 0.25 | 0.77083 | 3292.4 | 3290.2 | 0 | 3424.3 | 3186.3 | 3250.3 | 3172.5 | 0 | 2549.3 | 2554 | 2615.2 | 2524.9 | 10006.9 | 9609.1 | 10243.4 | 88088.35 | 397.85 |  | 5.92 | 0 | 42.54 | 0 | 0 |  | 29859.4 | 29600 | 100 | 29500 | 12.5 | Pyranometer sent for Calibration.Poa Values are Taken From 7 MW DRES Medchal Site.
2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-17 | 8.0209 | 0.25 | 0.77083 | 4005.4 | 4005.6 | 0 | 4075.2 | 3898.3 | 3875.5 | 3953.3 | 0 | 3075.7 | 3082.8 | 3071.7 | 3110.9 | 12086.2 | 11727.1 | 12341.1 | 88124.2 | 397.95 |  | 5.66 | 0 | 43.35 | 0 | 0 |  | 36154.4 | 35850 | 100 | 35750 | 12.5 | Pyranometer sent for Calibration.Poa Values are Taken From 7 MW DRES Medchal Site.
2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-18 | 8.0209 | 0.25417 | 0.77569 | 3006.8 | 3069.8 | 0 | 3036.6 | 3017.2 | 2920.6 | 2926 | 0 | 2360.1 | 2304.9 | 2314.5 | 2283 | 9113.2 | 8863.8 | 9262.5 | 88151.2 | 398.05 |  | 5.38 | 0 | 43.02 | 0 | 0 |  | 27239.5 | 27000 | 100 | 26900 | 12.5167 | Pyranometer sent for Calibration.Poa Values are Taken From 7 MW DRES Medchal Site.
2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-19 | 8.0209 | 0.25625 | 0.77361 | 3762.1 | 3761 | 0 | 3834.3 | 3622 | 3718.5 | 3605.2 | 0 | 2839.8 | 2918.6 | 2842.7 | 2817.3 | 11357.4 | 10945.7 | 11418.4 | 88184.6 | 398.15 |  | 5.54 | 0 | 43.31 | 0 | 0 |  | 33721.5 | 33400 | 100 | 33300 | 12.4167 | Pyranometer sent for Calibration.Poa Values are Taken From 7 MW DRES Medchal Site.
2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-20 | 8.0209 | 0.25347 | 0.77431 | 4569.8 | 4570 | 0 | 4636.9 | 4310.2 | 4279.6 | 4358.8 | 0 | 3469.6 | 3471.7 | 3527.1 | 3432.2 | 13776.7 | 12948.6 | 13900.6 | 88224.85 | 398.25 |  | 5.12 | 0 | 45.39 | 0 | 0 |  | 40625.9 | 40250 | 100 | 40150 | 12.5 | Pyranometer sent for Calibration.Poa Values are Taken From 7 MW DRES Medchal Site.
2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-21 | 8.0209 | 0.25069 | 0.76944 | 3283.1 | 3253.7 | 0 | 3284.3 | 3215 | 3123.7 | 3126.7 | 0 | 2572.2 | 2507.7 | 2498.1 | 2477.4 | 9821.1 | 9465.4 | 10055.4 | 88253.95 | 398.35 |  | 5.26 | 0 | 43.8 | 0 | 0 |  | 29341.9 | 29100 | 100 | 29000 | 12.45 | Pyranometer sent for Calibration.Poa Values are Taken From 7 MW DRES Medchal Site.
2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-22 | 8.0209 | 0.25 | 0.77083 | 3821.5 | 3819.7 | 0 | 3868.1 | 3776.1 | 3684 | 3690.2 | 0 | 2906.3 | 2929.4 | 2959.1 | 2876.9 | 11509.3 | 11150.3 | 11671.7 | 88287.95 | 398.45 |  | 5.79 | 0 | 46.12 | 0 | 0 |  | 34331.3 | 34000 | 100 | 33900 | 12.5 | Pyranometer sent for Calibration.Poa Values are Taken From 7 MW DRES Medchal Site.
2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-23 | 8.0209 | 0.25069 | 0.76667 | 3684 | 3682.6 | 0 | 3753.7 | 3556.6 | 3608.5 | 3542.9 | 0 | 2798.7 | 2803.6 | 2862.4 | 2768.4 | 11120.3 | 10708 | 11233.1 | 88320.65 | 398.55 |  | 5.92 | 0 | 47.02 | 0 | 0 |  | 33061.4 | 32700 | 100 | 32600 | 12.3833 | Pyranometer sent for Calibration.Poa Values are Taken From 7 MW DRES Medchal Site.
2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-24 | 8.0209 | 0.25278 | 0.7625 | 4045.7 | 3970.5 | 0 | 3968.8 | 3826.9 | 3805 | 3888.8 | 0 | 3016.6 | 3019.6 | 3008.8 | 3049.7 | 11985 | 11520.7 | 12094.7 | 88355.95 | 398.65 |  | 5.6 | 0 | 46.38 | 0 | 0 |  | 35600.4 | 35300 | 100 | 35200 | 12.2333 | Pyranometer sent for Calibration.Poa Values are Taken From 7 MW DRES Medchal Site.
2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-25 | 8.0209 | 0.25347 | 0.75694 | 3589 | 3572 | 0 | 3643 | 3524 | 3433 | 3444 | 0 | 2778 | 2706 | 2715 | 2677 | 10804 | 10401 | 10876 | 88387.75 | 398.75 |  | 5.72 | 0 | 46.34 | 0 | 0 |  | 32081 | 31800 | 100 | 31700 | 12.0833 | Pyranometer sent for Calibration.Poa Values are Taken From 7 MW DRES Medchal Site.
2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-26 | 8.0209 | 0.25 | 0.76736 | 4210 | 4153.7 | 0 | 4150.4 | 4020.1 | 3995.5 | 4060.2 | 0 | 3154 | 3160.6 | 3205.2 | 3123.5 | 12514.1 | 12075.8 | 12643.3 | 88424.65 | 398.8 |  | 5.2 | 0 | 45.56 | 0 | 0 |  | 37233.2 | 36900 | 50 | 36850 | 12.4167 | Pyranometer sent for Calibration.Poa Values are Taken From 7 MW DRES Medchal Site.
2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-27 | 8.0209 | 0.25 | 0.77292 | 3066.2 | 3152.6 | 0 | 3092.5 | 3046.7 | 2965.5 | 2942 | 0 | 2351.4 | 2326.7 | 2326.5 | 2398.2 | 9311.3 | 8954.2 | 9402.8 | 88452.05 | 398.9 |  | 4.69 | 0 | 41.92 | 0 | 0 |  | 27668.3 | 27400 | 100 | 27300 | 12.55 | Pyranometer sent for Calibration.Poa Values are Taken From 7 MW DRES Medchal Site.
2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-28 | 8.0209 | 0.25 | 0.77639 | 4545.8 | 4544.1 | 0 | 4607.9 | 4449 | 4357 | 4361.6 | 0 | 3460.5 | 3527.9 | 3455.5 | 3426 | 13697.8 | 13167.6 | 13869.9 | 88492.45 | 399 |  | 6.33 | 0 | 44.84 | 0 | 0 |  | 40735.3 | 40400 | 100 | 40300 | 12.6333 | Pyranometer sent for Calibration.Poa Values are Taken From 7 MW DRES Medchal Site.
2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-29 | 8.0209 | 0.25208 | 0.77708 | 3928 | 3859.3 | 0 | 3860.2 | 3633 | 3611.9 | 3681.9 | 0 | 2929.8 | 2927.6 | 2989.4 | 2901.3 | 11647.5 | 10926.8 | 11748.1 | 88526.5 | 399.1 |  | 5.62 | 0 | 44.35 | 0 | 0 |  | 34322.4 | 34050 | 100 | 33950 | 12.6 | Pyranometer sent for Calibration.Poa Values are Taken From 7 MW DRES Medchal Site.
2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-30 | 8.0209 | 0.25 | 0.775 | 4484.5 | 4555.4 | 0 | 4481.6 | 4397.9 | 4290.8 | 4299.4 | 0 | 3388.4 | 3394.8 | 3379.8 | 3420.9 | 13521.5 | 12988.1 | 13583.9 | 88566.25 | 399.2 |  | 5.77 | 0 | 46.33 | 0 | 0 |  | 40093.5 | 39750 | 100 | 39650 | 12.6 | Pyranometer sent for Calibration.Poa Values are Taken From 7 MW DRES Medchal Site.
2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-01 | 8.0209 | 0.25069 | 0.77708 | 4221.6 | 4219.5 | 0 | 4291.2 | 4074.6 | 4129.1 | 4058.6 | 0 | 3258.8 | 3197.3 | 3188.6 | 3163.1 | 12732.3 | 12262.3 | 12807.8 | 88603.7 | 399.3 |  | 5.52 | 0 | 45.19 | 0 | 0 |  | 37802.4 | 37450 | 100 | 37350 | 12.6333 | Pyranometer sent for Calibration.Poa Values are Taken From 7 MW DRES Medchal Site.
2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-02 | 8.0209 | 0.25069 | 0.77569 | 3549.1 | 3509.5 | 0 | 3509.7 | 3429.8 | 3371.7 | 3376.2 | 0 | 2647.7 | 2652 | 2681.3 | 2620.7 | 10568.3 | 10177.7 | 10601.7 | 88634.75 | 399.4 |  | 6.17 | 0 | 45.19 | 0 | 0 |  | 31347.7 | 31050 | 100 | 30950 | 12.6 | Pyranometer sent for Calibration.Poa Values are Taken From 7 MW DRES Medchal Site.
2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-03 | 8.0209 | 0.25486 | 0.77917 | 4313.5 | 4385.3 | 0 | 4311.3 | 4250.5 | 4146.5 | 4153.8 | 0 | 3268.8 | 3274.5 | 3263 | 3305.7 | 13010.1 | 12550.8 | 13112 | 88673.1 | 399.5 |  | 5.93 | 0 | 45.51 | 0 | 0 |  | 38672.9 | 38350 | 100 | 38250 | 12.5833 | Pyranometer sent for Calibration.Poa Values are Taken From 7 MW DRES Medchal Site.
2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-04 | 8.0209 | 0.24931 | 0.77917 | 2298.8 | 2298.7 | 0 | 2402.6 | 2203.1 | 2284.1 | 2194 | 0 | 1854.1 | 1755.2 | 1750 | 1737.4 | 7000.1 | 6681.2 | 7096.7 | 88693.7 | 399.6 |  | 5.27 | 0 | 42.88 | 0 | 0 |  | 20778 | 20600 | 100 | 20500 | 12.7167 | Pyranometer sent for Calibration.Poa Values are Taken From 7 MW DRES Medchal Site.
2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-05 | 8.0209 | 0.25347 | 0.76667 | 4560.9 | 4560.8 | 0 | 4633.8 | 4392.7 | 4367.1 | 4452.3 | 0 | 3467.1 | 3543.1 | 3458.8 | 3427.9 | 13755.5 | 13212.1 | 13896.9 | 88734.2 | 399.7 |  | 6.52 | 0 | 45.43 | 0 | 0 |  | 40864.5 | 40500 | 100 | 40400 | 12.3167 | Pyranometer sent for Calibration.Poa Values are Taken From 7 MW DRES Medchal Site.
2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-06 | 8.0209 | 0.25 | 0.77083 | 4418.6 | 4338.2 | 0 | 4337.5 | 4278.3 | 4175.2 | 4181.9 | 0 | 3304 | 3310.5 | 3368.7 | 3271.8 | 13094.3 | 12635.4 | 13255 | 88772.85 | 399.8 |  | 6.2 | 0 | 44.26 | 0 | 0 |  | 38984.7 | 38650 | 100 | 38550 | 12.5 | Pyranometer sent for Calibration.Poa Values are Taken From 7 MW DRES Medchal Site.
2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-07 | 8.0209 | 0.24444 | 0.77639 | 4366.4 | 4440.9 | 0 | 4368.3 | 4351.3 | 4244 | 4252.6 | 0 | 3345.9 | 3354 | 3341 | 3385 | 13175.6 | 12847.9 | 13425.9 | 88811.95 | 399.9 |  | 6.58 | 0 | 43.99 | 0 | 0 |  | 39449.4 | 39100 | 100 | 39000 | 12.7667
2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-08 | 8.0209 | 0.25139 | 0.77014 | 4360.7 | 4360.7 | 0 | 4477.2 | 4222.4 | 4311.3 | 4204.6 | 0 | 3451.8 | 3345.1 | 3332 | 3306.4 | 13198.6 | 12738.3 | 13435.3 | 88851 | 400 |  | 6.72 | 0 | 44.03 | 0 | 0 |  | 39372.2 | 39050 | 100 | 38950 | 12.45
2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-09 | 8.0209 | 0.25069 | 0.77778 | 4365.2 | 4364.3 | 0 | 4442 | 4197.7 | 4170.9 | 4257.4 | 0 | 3299.8 | 3386.1 | 3296.2 | 3270.1 | 13171.5 | 12626 | 13252.2 | 88889.7 | 400.1 |  | 6.54 | 0 | 44.38 | 0 | 0 |  | 39049.7 | 38700 | 100 | 38600 | 12.65
2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-10 | 8.0209 | 0.25069 | 0.77153 | 3754.8 | 3671.2 | 0 | 3671 | 3671.9 | 3564.6 | 3569.4 | 0 | 2783.2 | 2793.5 | 2863.2 | 2761.5 | 11097 | 10805.9 | 11201.4 | 88922.5 | 400.2 |  | 4.98 | 0 | 42.32 | 0 | 0 |  | 33104.3 | 32800 | 100 | 32700 | 12.5
2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-11 | 8.0209 | 0.25 | 0.78125 | 3877.4 | 3938 | 0 | 3876.6 | 3679.5 | 3592.4 | 3597.9 | 0 | 2887.7 | 2897.3 | 2884.9 | 2921.6 | 11692 | 10869.8 | 11591.5 | 88956.4 | 400.3 |  | 5.82 | 0 | 43.47 | 0 | 0 |  | 34153.3 | 33900 | 100 | 33800 | 12.75
2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-12 | 8.0209 | 0.24653 | 0.74097 | 4479 | 4481.5 | 0 | 4548.8 | 4305.4 | 4276.2 | 4354 | 0 | 3376.8 | 3451.6 | 3368.6 | 3343.8 | 13509.3 | 12935.6 | 13540.8 | 88996.1 | 400.4 |  | 6.33 | 0 | 44.17 | 0 | 0 |  | 39985.7 | 39700 | 100 | 39600 | 11.8667
2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-13 | 8.0209 | 0.24375 | 0.76875 | 3959.7 | 3895.5 | 0 | 3895.5 | 3842.2 | 3749.1 | 3754.9 | 0 | 2948.3 | 2956.1 | 3007.8 | 2923.1 | 11750.7 | 11346.2 | 11835.3 | 89030.7 | 400.5 |  | 5.18 | 0 | 42.05 | 0 | 0 |  | 34932.2 | 34600 | 100 | 34500 | 12.6
2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-14 | 8.0209 | 0.24514 | 0.75764 | 3808.9 | 3877.1 | 0 | 3809.7 | 3739.1 | 3639 | 3645.6 | 0 | 2910.8 | 2918.8 | 2910.9 | 2956 | 11495.7 | 11023.7 | 11696.5 | 89064.6 | 400.6 |  | 5.23 | 0 | 41.35 | 0 | 0 |  | 34215.9 | 33900 | 100 | 33800 | 12.3
2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-15 | 8.0209 | 0.26875 | 0.77708 | 2266.6 | 2266.3 | 0 | 2371.2 | 2028.5 | 2015.4 | 2017.6 | 0 | 1488.2 | 1494.7 | 1591.7 | 1479.2 | 6904.1 | 6061.5 | 6053.8 | 89083.4 | 400.75 |  | 3.03 | 0 | 33.73 | 0 | 0 |  | 19019.4 | 18800 | 150 | 18650 | 12.2
2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-16 | 8.0209 | 0.24375 | 0.77917 | 2608.8 | 2520.7 | 0 | 2521.3 | 3674 | 3563 | 3568.8 | 0 | 2776.6 | 2788.2 | 2776.2 | 2840.4 | 7650.8 | 10805.8 | 11181.4 | 89112.9 | 400.85 |  | 5.42 | 0 | 41.83 | 0 | 0 |  | 29638 | 29500 | 100 | 29400 | 12.85
2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-17 | 8.0209 | 0.24306 | 0.77639 | 3579.8 | 3581.2 | 0 | 3583.4 | 3531.6 | 3508.6 | 3514.2 | 0 | 2731.5 | 2739.2 | 2729.9 | 2710.4 | 10744.4 | 10554.4 | 10911 | 89144.8 | 400.95 |  | 5.27 | 0 | 40.74 | 0 | 0 |  | 32209.8 | 31900 | 100 | 31800 | 12.8
2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-18 | 8.0209 | 0.25069 | 0.77778 | 2412.7 | 2412.3 | 0 | 2580 | 2467 | 2287.6 | 2284.2 | 0 | 1821.8 | 1827.8 | 1987.2 | 1808.6 | 7405 | 7038.8 | 7445.4 | 89166.5 | 401.05 |  | 5.23 | 0 | 41.05 | 0 | 0 |  | 21889.2 | 21700 | 100 | 21600 | 12.65
2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-19 | 8.0209 | 0.25 | 0.78333 | 3259.8 | 3175 | 0 | 3178.2 | 3141.3 | 3019.8 | 3021.3 | 0 | 2403.8 | 2411.8 | 2403.7 | 2462.2 | 9613 | 9182.4 | 9681.5 | 89194.8 | 401.15 |  | 4.91 | 0 | 40.53 | 0 | 0 |  | 28476.9 | 28300 | 100 | 28200 | 12.8
2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-20 | 8.0209 | 0.24792 | 0.77778 | 3442.4 | 3441.4 | 0 | 3518.4 | 3333.2 | 3312.8 | 3398.2 | 0 | 2450 | 2474.9 | 2503.5 | 2433.6 | 10402.2 | 10044.2 | 9862 | 89224.9 | 401.25 |  | 4.84 | 0 | 40.06 | 0 | 0 |  | 30308.4 | 30100 | 100 | 30000 | 12.7167
2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-21 | 8.0209 | 0.24306 | 0.77778 | 2267.3 | 2257.6 | 0 | 2347.6 | 2283.5 | 2172.8 | 2175.2 | 0 | 1704 | 1709.7 | 1704.2 | 1780.4 | 6872.5 | 6631.5 | 6898.3 | 89245.1 | 401.35 |  | 3.26 | 0 | 33.83 | 0 | 0 |  | 20402.3 | 20200 | 100 | 20100 | 12.8333
2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-22 | 8.0209 | 0.24375 | 0.76597 | 3018.2 | 3126.6 | 0 | 3018.1 | 2937.2 | 3021.7 | 2919.3 | 0 | 2351.4 | 2366.7 | 2451.3 | 2335.3 | 9162.9 | 8878.2 | 9504.7 | 89272.4 | 401.45 |  | 5.56 | 0 | 48.87 | 0 | 0 |  | 27545.8 | 27300 | 100 | 27200 | 12.5333
2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-23 | 8.0209 | 0.24653 | 0.78125 | 3603.1 | 3601 | 0 | 3674.8 | 3522.5 | 3500.6 | 3569.5 | 0 | 2882.1 | 2892.1 | 2881.2 | 2925.6 | 10878.9 | 10592.6 | 11581 | 89305.15 | 401.55 |  | 5.31 | 0 | 36.07 | 0 | 0 |  | 33052.5 | 32750 | 100 | 32650 | 12.8333
2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-24 | 8.0209 | 0.25069 | 0.775 | 3019.4 | 2987.5 | 0 | 3031.1 | 2996 | 2898.8 | 2900.2 | 0 | 2350.9 | 2511.7 | 2311.9 | 2295.3 | 9038 | 8795 | 9469.8 | 89332.2 | 401.65 |  | 4.32 | 0 | 34.13 | 0 | 0 |  | 27302.8 | 27050 | 100 | 26950 | 12.5833
2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-25 | 8.0209 | 0.24375 | 0.77986 | 2667.1 | 2750.9 | 0 | 2668.6 | 2563.8 | 2629.4 | 2547.5 | 0 | 1941.6 | 1999.5 | 1941.9 | 1964 | 8086.6 | 7740.7 | 7847 | 89355.7 | 401.75 |  | 3.74 | 0 | 33.6 | 0 | 0 |  | 23674.3 | 23500 | 100 | 23400 | 12.8667
2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-26 | 8.0209 | 0.25139 | 0.78472 | 2109 | 2109.8 | 0 | 2231.7 | 2027.2 | 2016.2 | 2117.7 | 0 | 1582.5 | 1588.5 | 1590.6 | 1694.1 | 6450.5 | 6161.1 | 6455.7 | 89374.6 | 401.85 |  | 2.88 | 0 | 33.68 | 0 | 0 |  | 19067.3 | 18900 | 100 | 18800 | 12.8
2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-27 | 8.0209 | 0.24375 | 0.76806 | 2252.6 | 2198.6 | 0 | 2201.3 | 2194.7 | 2131.4 | 2127.2 | 0 | 1692.3 | 1722.9 | 1724.7 | 1684.9 | 6652.5 | 6453.3 | 6824.8 | 89394.35 | 401.95 |  | 3.04 | 0 | 32.93 | 0 | 0 |  | 19930.6 | 19750 | 100 | 19650 | 12.5833
2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-28 | 8.0209 | 0.24306 | 0.77778 | 2468.7 | 2484.3 | 0 | 2559.5 | 2371.7 | 2427.8 | 2343 | 0 | 1880.8 | 1858 | 1880.5 | 1968.7 | 7512.5 | 7142.5 | 7588 | 89416.4 | 402.05 |  | 3.25 | 0 | 32.46 | 0 | 0 |  | 22243 | 22050 | 100 | 21950 | 12.8333
2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-29 | 8.0209 | 0.24653 | 0.77708 | 2110 | 2109.2 | 0 | 2201.5 | 2029.2 | 2018.2 | 2104.5 | 0 | 1680 | 1589.5 | 1589.5 | 1580.5 | 6420.7 | 6151.9 | 6439.5 | 89435.3 | 402.2 |  | 2.67 | 0 | 32.15 | 0 | 0 |  | 19012.1 | 18900 | 150 | 18750 | 12.7333
2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-30 | 8.0209 | 0.24306 | 0.78125 | 4068.3 | 4002.9 | 0 | 4006 | 3908.4 | 3815.9 | 3821.3 | 0 | 3017.6 | 3095.9 | 3017.3 | 2997.2 | 12077.2 | 11545.6 | 12128 | 89470.7 | 402.3 |  | 5.3 | 0 | 37.7 | 0 | 0 |  | 35750.8 | 35400 | 100 | 35300 | 12.9167
2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-31 | 8.0209 | 0.24306 | 0.78403 | 4454.9 | 4539.5 | 0 | 4459.1 | 4400.3 | 4285.8 | 4293.8 | 0 | 3393.7 | 3406.3 | 3476.4 | 3367.9 | 13453.5 | 12979.9 | 13644.3 | 89510.5 | 402.4 |  | 6.1 | 0 | 39.9 | 0 | 0 |  | 40077.7 | 39800 | 100 | 39700 | 12.9833
2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-01 | 8.0209 | 0.24583 | 0.78403 | 4306 | 4305.8 | 0 | 4390.2 | 4164.1 | 4221.1 | 4143.8 | 0 | 3319.4 | 3331.1 | 3317.7 | 3372.2 | 13002 | 12529 | 13340.4 | 89549.1 | 402.5 |  | 5.88 | 0 | 39.09 | 0 | 0 |  | 38871.4 | 38600 | 100 | 38500 | 12.9167
2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-02 | 8.0209 | 0.24653 | 0.78333 | 3571.5 | 3570.3 | 0 | 3655.5 | 3455 | 3433.3 | 3521.2 | 0 | 2914.4 | 2841.7 | 2831.1 | 2811.4 | 10797.3 | 10409.5 | 11398.6 | 89581.5 | 402.6 |  | 4.76 | 0 | 36.1 | 0 | 0 |  | 32605.4 | 32400 | 100 | 32300 | 12.8833
2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-03 | 8.0209 | 0.25 | 0.775 | 4089.7 | 4021.7 | 0 | 4023.3 | 3975.6 | 3872.2 | 3877 | 0 | 3127 | 3143.2 | 3177.4 | 3096.9 | 12134.7 | 11724.8 | 12544.5 | 89617.6 | 402.7 |  | 5.86 | 0 | 39.56 | 0 | 0 |  | 36404 | 36100 | 100 | 36000 | 12.6
2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-04 | 8.0209 | 0.24722 | 0.77778 | 4579.9 | 4658.6 | 0 | 4581.3 | 4510.2 | 4397.2 | 4405.3 | 0 | 3512 | 3515.8 | 3578.6 | 3473.8 | 13819.8 | 13312.7 | 14080.2 | 89658.45 | 402.8 |  | 6.25 | 0 | 41.45 | 0 | 0 |  | 41212.7 | 40850 | 100 | 40750 | 12.7333
2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-05 | 8.0209 | 0.25 | 0.77569 | 3101.4 | 3099.4 | 0 | 3151.2 | 2980.1 | 3012.1 | 2962.5 | 0 | 2343.3 | 2353 | 2343.3 | 2376.4 | 9352 | 8954.7 | 9416 | 89685.95 | 402.9 |  | 4.03 | 0 | 37.67 | 0 | 0 |  | 27722.7 | 27500 | 100 | 27400 | 12.6167
2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-06 | 8.0209 | 0.24931 | 0.76944 | 3353.2 | 3352.7 | 0 | 3425.2 | 3212.7 | 3192.9 | 3268.3 | 0 | 2656.9 | 2596.4 | 2586.6 | 2567.9 | 10131.1 | 9673.9 | 10407.8 | 89715.9 | 403 |  | 4.75 | 0 | 41.22 | 0 | 0 |  | 30212.8 | 29950 | 100 | 29850 | 12.4833
2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-07 | 8.0209 | 0.24444 | 0.78333 | 2885.2 | 2794.6 | 0 | 2796.5 | 2783 | 2678.4 | 2680.4 | 0 | 2145.4 | 2156.4 | 2231.6 | 2128.6 | 8476.3 | 8141.8 | 8662 | 89740.95 | 403.1 |  | 4.29 | 0 | 37.89 | 0 | 0 |  | 25280.1 | 25050 | 100 | 24950 | 12.9333
2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-08 | 8.0209 | 0.24444 | 0.76667 | 3543.9 | 3654.5 | 0 | 3544.6 | 3522 | 3381.5 | 3385.3 | 0 | 2696.2 | 2707.4 | 2805.3 | 2678.5 | 10743 | 10288.8 | 10887.4 | 89772.6 | 403.2 |  | 4.79 | 0 | 38.24 | 0 | 0 |  | 31919.2 | 31650 | 100 | 31550 | 12.5333
2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-09 | 8.0209 | 0.27917 | 0.78333 | 460.1 | 461.5 | 0 | 669.4 | 433.2 | 649.9 | 428.4 | 0 | 343.1 | 345.8 | 343.4 | 546.2 | 1591 | 1511.5 | 1578.5 | 89777.2 | 403.3 |  | 1.05 | 0 | 26.95 | 0 | 0 |  | 4681 | 4600 | 100 | 4500 | 12.1
2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-10 | 8.0209 | 0.24931 | 0.775 | 1229.4 | 1341.9 | 0 | 1234.6 | 1284.5 | 1170.6 | 1164 | 0 | 916.8 | 921.6 | 1029.2 | 912.3 | 3805.9 | 3619.1 | 3779.9 | 89788.3 | 403.4 |  | 1.62 | 0 | 28.69 | 0 | 0 |  | 11204.9 | 11100 | 100 | 11000 | 12.6167
2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-11 | 8.0209 | 0.25486 | 0.77847 | 2811.3 | 2809.9 | 0 | 2878.5 | 2696.1 | 2676.7 | 2797.2 | 0 | 2195.3 | 2134.9 | 2128.2 | 2116.9 | 8499.7 | 8170 | 8575.3 | 89813.3 | 403.5 |  | 3.59 | 0 | 32.62 | 0 | 0 |  | 25245 | 25000 | 100 | 24900 | 12.5667
2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-12 | 8.0209 | 0.24722 | 0.77361 | 2962.3 | 2893.2 | 0 | 2896.8 | 2841.2 | 2751.9 | 2751.5 | 0 | 2188.8 | 2269.3 | 2191.1 | 2178.1 | 8752.3 | 8344.6 | 8827.3 | 89839 | 403.6 |  | 3.8 | 0 | 36.04 | 0 | 0 |  | 25924.2 | 25700 | 100 | 25600 | 12.6333
Formulas:
Days = DAY(EOMONTH(Table3[[#This Row],[Month Year]],0))
Date = [Date, row above]+1

## Basic Data (hidden)
Equipment | Affected DC Capacity | Plant Equivalent Weightage | Fault Category Plant BD sheet | Fault Category Tracker BD sheet | Tracker Equipment | Weightage of BD | Plant Equivalent Weightage | Status
Inv1 | 2694.6 | 33.59% | Module | MSAT100_PCB | MSAT_Type1 (5*63) | 315 | 0.8621% | Open
Inv2 | 2630.8 | 32.8% | String Cable | MSAT200_PCB | MSAT_Type2(4*63) | 252 | 0.6897% | Close
Inv3 | 2695.5 | 33.61% | String Fuse | Tilt Sensor | MSAT_Type3(3*63) | 189 | 0.5172%
Inv 1 (630kw) unit 1 | 669.6 | 8.348% | SCB | Actuator | MSAT_Type4(5*42) | 210 | 0.5747%
Inv 1 (630kw) unit 2 | 669.6 | 8.348% | SCB Cable | Battery | MSAT_Type5(4*42) | 168 | 0.4598%
Inv 1 (630kw) unit 3 | 675 | 8.416% | SCB Fuse | Charge Controller | MSAT_Type6(3*42) | 126 | 0.3448%
Inv 1 (630kw) unit 4 | 680.4 | 8.483% | Inverter | RTC | Tilt Sensor_Type1(1*63) | 63 | 0.1724%
Inv 2 (630kw) unit 1 | 658.8 | 8.214% | Inv 1 (630kw) unit 1 | Gateway | Tilt Sensor_Type2(1*42) | 42 | 0.1149%
Inv 2 (630kw) unit 2 | 658.8 | 8.214% | Inv 1 (630kw) unit 2 | MMS | Baatery_Type1(5*63) | 315 | 0.8621%
Inv 2 (630kw) unit 3 | 658.8 | 8.214% | Inv 1 (630kw) unit 3 |  | Baatery_Type2(4*63) | 252 | 0.6897%
Inv 2 (630kw) unit 4 | 658.8 | 8.214% | Inv 1 (630kw) unit 4 |  | Baatery_Type3(3*63) | 189 | 0.5172%
Inv 3 (630kw) unit 1 | 671.76 | 8.375% | Inv 2 (630kw) unit 1 |  | Baatery_Type4(5*42) | 210 | 0.5747%
Inv 3 (630kw) unit 2 | 661.32 | 8.245% | Inv 2 (630kw) unit 2 |  | Baatery_Type5(4*42) | 168 | 0.4598%
Inv 3 (630kw) unit 3 | 680.04 | 8.478% | Inv 2 (630kw) unit 3 |  | Baatery_Type6(3*42) | 126 | 0.3448%
Inv 3 (630kw) unit 4 | 680.04 | 8.478% | Inv 2 (630kw) unit 4 |  | CCU_Type1(5*63) | 315 | 0.8621%
Inv1_CB1 | 111.6 | 1.391% | Inv 3 (630kw) unit 1 |  | CCU_Type2(4*63) | 252 | 0.6897%
Inv1_CB2 | 111.6 | 1.391% | Inv 3 (630kw) unit 2 |  | CCU_Type3(3*63) | 189 | 0.5172%
Inv1_CB3 | 111.6 | 1.391% | Inv 3 (630kw) unit 3 |  | CCU_Type4(5*42) | 210 | 0.5747%
Inv1_CB4 | 111.6 | 1.391% | Inv 3 (630kw) unit 4 |  | CCU_Type5(4*42) | 168 | 0.4598%
Inv1_CB5 | 111.6 | 1.391% | InverterAC Cable |  | CCU_Type6(3*42) | 126 | 0.3448%
Inv1_CB6 | 111.6 | 1.391% | IDT |  | Actuator Type1(1*63) | 63 | 0.1724%
Inv1_CB7 | 111.6 | 1.391% | IDT MV Cable |  | Actuator Type2(1*42) | 42 | 0.1149%
Inv1_CB8 | 111.6 | 1.391% | IC MV Panel |  | RTC
Inv1_CB9 | 111.6 | 1.391% | Incomer MV Cable |  | Gateway
Inv1_CB10 | 111.6 | 1.391% | Incomer MV Panel |  | Repeater
Inv1_CB11 | 111.6 | 1.391% | Metering System Plant |  | Switch
Inv1_CB12 | 111.6 | 1.391% | Grid System
Inv1_CB13 | 111.6 | 1.391% | Metering System Grid
Inv1_CB14 | 111.6 | 1.391% | WMS
Inv1_CB15 | 111.6 | 1.391% | MMS
Inv1_CB16 | 113.4 | 1.414% | Battery Charger_MCR
Inv1_CB17 | 113.4 | 1.414% | IC_UPS
Inv1_CB18 | 113.4 | 1.414% | IC_Auxiliary Tranformer
Inv1_CB19 | 113.4 | 1.414% | IC_Auxiliary DB
Inv1_CB20 | 113.4 | 1.414% | IC_SCADA Panel
Inv1_CB21 | 113.4 | 1.414% | MC4 Connector
Inv1_CB22 | 113.4 | 1.414% | Y-Connector
Inv1_CB23 | 113.4 | 1.414%
Inv1_CB24 | 113.4 | 1.414%
Inv2_CB1 | 113.4 | 1.414%
Inv2_CB2 | 108 | 1.346%
Inv2_CB3 | 108 | 1.346%
Inv2_CB4 | 109.8 | 1.369%
Inv2_CB5 | 109.8 | 1.369%
Inv2_CB6 | 109.8 | 1.369%
Inv2_CB7 | 109.8 | 1.369%
Inv2_CB8 | 109.8 | 1.369%
Inv2_CB9 | 109.8 | 1.369%
Inv2_CB10 | 109.8 | 1.369%
Inv2_CB11 | 109.8 | 1.369%
Inv2_CB12 | 109.8 | 1.369%
Inv2_CB13 | 109.8 | 1.369%
Inv2_CB14 | 109.8 | 1.369%
Inv2_CB15 | 109.8 | 1.369%
Inv2_CB16 | 109.8 | 1.369%
Inv2_CB17 | 109.8 | 1.369%
Inv2_CB18 | 109.8 | 1.369%
Inv2_CB19 | 109.8 | 1.369%
Inv2_CB20 | 109.8 | 1.369%
Inv2_CB21 | 109.8 | 1.369%
Inv2_CB22 | 109.8 | 1.369%
Inv2_CB23 | 109.8 | 1.369%
Inv2_CB24 | 109.8 | 1.369%
Inv3_CB1 | 111.6 | 1.391%
Inv3_CB2 | 111.6 | 1.391%
Inv3_CB3 | 111.6 | 1.391%
Inv3_CB4 | 112.32 | 1.4%
Inv3_CB5 | 112.32 | 1.4%
Inv3_CB6 | 112.32 | 1.4%
Inv3_CB7 | 112.32 | 1.4%
Inv3_CB8 | 109.8 | 1.369%
Inv3_CB9 | 109.8 | 1.369%
Inv3_CB10 | 109.8 | 1.369%
Inv3_CB11 | 109.8 | 1.369%
Inv3_CB12 | 109.8 | 1.369%
Inv3_CB13 | 113.34 | 1.413%
Inv3_CB14 | 113.34 | 1.413%
Inv3_CB15 | 113.34 | 1.413%
Inv3_CB16 | 113.34 | 1.413%
Inv3_CB17 | 113.34 | 1.413%
Inv3_CB18 | 113.34 | 1.413%
Inv3_CB19 | 113.34 | 1.413%
Inv3_CB20 | 113.34 | 1.413%
Inv3_CB21 | 113.34 | 1.413%
Inv3_CB22 | 113.34 | 1.413%
Inv3_CB23 | 113.34 | 1.413%
Inv3_CB24 | 113.34 | 1.413%
IC1_IDT | 2694.6 | 33.59%
IC2_IDT | 2630.8 | 32.8%
IC3_IDT | 2695.5 | 33.61%
ICOG1_IC1 | 2694.6 | 33.59%
ICOG2_IC2 | 2630.8 | 32.8%
ICOG3_IC3 | 2695.5 | 33.61%
Isolator1 | 2694.6 | 33.59%
Isolator2 | 2630.8 | 32.8%
Isolator3 | 2695.5 | 33.61%
Outgoing | 8020.9 | 100%
Inv1_cb1_S 1 | 11.16 | 0.1391%
Inv1_cb1_S 2 | 11.16 | 0.1391%
Inv1_cb1_S 3 | 11.16 | 0.1391%
Inv1_cb1_S 4 | 11.16 | 0.1391%
Inv1_cb1_S 5 | 11.16 | 0.1391%
Inv1_cb1_S 6 | 11.16 | 0.1391%
Inv1_cb1_S 7 | 11.16 | 0.1391%
Inv1_cb1_S 8 | 11.16 | 0.1391%
Inv1_cb1_S 9 | 11.16 | 0.1391%
Inv1_cb1_S 10 | 11.16 | 0.1391%
Inv1_cb2_S 1 | 11.16 | 0.1391%
Inv1_cb2_S 2 | 11.16 | 0.1391%
Inv1_cb2_S 3 | 11.16 | 0.1391%
Inv1_cb2_S 4 | 11.16 | 0.1391%
Inv1_cb2_S 5 | 11.16 | 0.1391%
Inv1_cb2_S 6 | 11.16 | 0.1391%
Inv1_cb2_S 7 | 11.16 | 0.1391%
Inv1_cb2_S 8 | 11.16 | 0.1391%
Inv1_cb2_S 9 | 11.16 | 0.1391%
Inv1_cb2_S 10 | 11.16 | 0.1391%
Inv1_cb3_S 1 | 11.16 | 0.1391%
Inv1_cb3_S 2 | 11.16 | 0.1391%
Inv1_cb3_S 3 | 11.16 | 0.1391%
Inv1_cb3_S 4 | 11.16 | 0.1391%
Inv1_cb3_S 5 | 11.16 | 0.1391%
Inv1_cb3_S 6 | 11.16 | 0.1391%
Inv1_cb3_S 7 | 11.16 | 0.1391%
Inv1_cb3_S 8 | 11.16 | 0.1391%
Inv1_cb3_S 9 | 11.16 | 0.1391%
Inv1_cb3_S 10 | 11.16 | 0.1391%
Inv1_cb4_S 1 | 11.16 | 0.1391%
Inv1_cb4_S 2 | 11.16 | 0.1391%
Inv1_cb4_S 3 | 11.16 | 0.1391%
Inv1_cb4_S 4 | 11.16 | 0.1391%
Inv1_cb4_S 5 | 11.16 | 0.1391%
Inv1_cb4_S 6 | 11.16 | 0.1391%
Inv1_cb4_S 7 | 11.16 | 0.1391%
Inv1_cb4_S 8 | 11.16 | 0.1391%
Inv1_cb4_S 9 | 11.16 | 0.1391%
Inv1_cb4_S 10 | 11.16 | 0.1391%
Inv1_cb5_S 1 | 11.16 | 0.1391%
Inv1_cb5_S 2 | 11.16 | 0.1391%
Inv1_cb5_S 3 | 11.16 | 0.1391%
Inv1_cb5_S 4 | 11.16 | 0.1391%
Inv1_cb5_S 5 | 11.16 | 0.1391%
Inv1_cb5_S 6 | 11.16 | 0.1391%
Inv1_cb5_S 7 | 11.16 | 0.1391%
Inv1_cb5_S 8 | 11.16 | 0.1391%
Inv1_cb5_S 9 | 11.16 | 0.1391%
Inv1_cb5_S 10 | 11.16 | 0.1391%
Inv1_cb6_S 1 | 11.16 | 0.1391%
Inv1_cb6_S 2 | 11.16 | 0.1391%
Inv1_cb6_S 3 | 11.16 | 0.1391%
Inv1_cb6_S 4 | 11.16 | 0.1391%
Inv1_cb6_S 5 | 11.16 | 0.1391%
Inv1_cb6_S 6 | 11.16 | 0.1391%
Inv1_cb6_S 7 | 11.16 | 0.1391%
Inv1_cb6_S 8 | 11.16 | 0.1391%
Inv1_cb6_S 9 | 11.16 | 0.1391%
Inv1_cb6_S 10 | 11.16 | 0.1391%
Inv1_cb7_S 1 | 11.16 | 0.1391%
Inv1_cb7_S 2 | 11.16 | 0.1391%
Inv1_cb7_S 3 | 11.16 | 0.1391%
Inv1_cb7_S 4 | 11.16 | 0.1391%
Inv1_cb7_S 5 | 11.16 | 0.1391%
Inv1_cb7_S 6 | 11.16 | 0.1391%
Inv1_cb7_S 7 | 11.16 | 0.1391%
Inv1_cb7_S 8 | 11.16 | 0.1391%
Inv1_cb7_S 9 | 11.16 | 0.1391%
Inv1_cb7_S 10 | 11.16 | 0.1391%
Inv1_cb8_S 1 | 11.16 | 0.1391%
Inv1_cb8_S 2 | 11.16 | 0.1391%
Inv1_cb8_S 3 | 11.16 | 0.1391%
Inv1_cb8_S 4 | 11.16 | 0.1391%
Inv1_cb8_S 5 | 11.16 | 0.1391%
Inv1_cb8_S 6 | 11.16 | 0.1391%
Inv1_cb8_S 7 | 11.16 | 0.1391%
Inv1_cb8_S 8 | 11.16 | 0.1391%
Inv1_cb8_S 9 | 11.16 | 0.1391%
Inv1_cb8_S 10 | 11.16 | 0.1391%
Inv1_cb9_S 1 | 11.16 | 0.1391%
Inv1_cb9_S 2 | 11.16 | 0.1391%
Inv1_cb9_S 3 | 11.16 | 0.1391%
Inv1_cb9_S 4 | 11.16 | 0.1391%
Inv1_cb9_S 5 | 11.16 | 0.1391%
Inv1_cb9_S 6 | 11.16 | 0.1391%
Inv1_cb9_S 7 | 11.16 | 0.1391%
Inv1_cb9_S 8 | 11.16 | 0.1391%
Inv1_cb9_S 9 | 11.16 | 0.1391%
Inv1_cb9_S 10 | 11.16 | 0.1391%
Inv1_cb10_S 1 | 11.16 | 0.1391%
Inv1_cb10_S 2 | 11.16 | 0.1391%
Inv1_cb10_S 3 | 11.16 | 0.1391%
Inv1_cb10_S 4 | 11.16 | 0.1391%
Inv1_cb10_S 5 | 11.16 | 0.1391%
Inv1_cb10_S 6 | 11.16 | 0.1391%
Inv1_cb10_S 7 | 11.16 | 0.1391%
Inv1_cb10_S 8 | 11.16 | 0.1391%
Inv1_cb10_S 9 | 11.16 | 0.1391%
Inv1_cb10_S 10 | 11.16 | 0.1391%
Inv1_cb11_S 1 | 11.16 | 0.1391%
Inv1_cb11_S 2 | 11.16 | 0.1391%
Inv1_cb11_S 3 | 11.16 | 0.1391%
Inv1_cb11_S 4 | 11.16 | 0.1391%
Inv1_cb11_S 5 | 11.16 | 0.1391%
Inv1_cb11_S 6 | 11.16 | 0.1391%
Inv1_cb11_S 7 | 11.16 | 0.1391%
Inv1_cb11_S 8 | 11.16 | 0.1391%
Inv1_cb11_S 9 | 11.16 | 0.1391%
Inv1_cb11_S 10 | 11.16 | 0.1391%
Inv1_cb12_S 1 | 11.16 | 0.1391%
Inv1_cb12_S 2 | 11.16 | 0.1391%
Inv1_cb12_S 3 | 11.16 | 0.1391%
Inv1_cb12_S 4 | 11.16 | 0.1391%
Inv1_cb12_S 5 | 11.16 | 0.1391%
Inv1_cb12_S 6 | 11.16 | 0.1391%
Inv1_cb12_S 7 | 11.16 | 0.1391%
Inv1_cb12_S 8 | 11.16 | 0.1391%
Inv1_cb12_S 9 | 11.16 | 0.1391%
Inv1_cb12_S 10 | 11.16 | 0.1391%
Inv1_cb13_S 1 | 11.16 | 0.1391%
Inv1_cb13_S 2 | 11.16 | 0.1391%
Inv1_cb13_S 3 | 11.16 | 0.1391%
Inv1_cb13_S 4 | 11.16 | 0.1391%
Inv1_cb13_S 5 | 11.16 | 0.1391%
Inv1_cb13_S 6 | 11.16 | 0.1391%
Inv1_cb13_S 7 | 11.16 | 0.1391%
Inv1_cb13_S 8 | 11.16 | 0.1391%
Inv1_cb13_S 9 | 11.16 | 0.1391%
Inv1_cb13_S 10 | 11.16 | 0.1391%
Inv1_cb14_S 1 | 11.16 | 0.1391%
Inv1_cb14_S 2 | 11.16 | 0.1391%
Inv1_cb14_S 3 | 11.16 | 0.1391%
Inv1_cb14_S 4 | 11.16 | 0.1391%
Inv1_cb14_S 5 | 11.16 | 0.1391%
Inv1_cb14_S 6 | 11.16 | 0.1391%
Inv1_cb14_S 7 | 11.16 | 0.1391%
Inv1_cb14_S 8 | 11.16 | 0.1391%
Inv1_cb14_S 9 | 11.16 | 0.1391%
Inv1_cb14_S 10 | 11.16 | 0.1391%
Inv1_cb15_S 1 | 11.16 | 0.1391%
Inv1_cb15_S 2 | 11.16 | 0.1391%
Inv1_cb15_S 3 | 11.16 | 0.1391%
Inv1_cb15_S 4 | 11.16 | 0.1391%
Inv1_cb15_S 5 | 11.16 | 0.1391%
Inv1_cb15_S 6 | 11.16 | 0.1391%
Inv1_cb15_S 7 | 11.16 | 0.1391%
Inv1_cb15_S 8 | 11.16 | 0.1391%
Inv1_cb15_S 9 | 11.16 | 0.1391%
Inv1_cb15_S 10 | 11.16 | 0.1391%
Inv1_cb16_S 1 | 11.34 | 0.1414%
Inv1_cb16_S 2 | 11.34 | 0.1414%
Inv1_cb16_S 3 | 11.34 | 0.1414%
Inv1_cb16_S 4 | 11.34 | 0.1414%
Inv1_cb16_S 5 | 11.34 | 0.1414%
Inv1_cb16_S 6 | 11.34 | 0.1414%
Inv1_cb16_S 7 | 11.34 | 0.1414%
Inv1_cb16_S 8 | 11.34 | 0.1414%
Inv1_cb16_S 9 | 11.34 | 0.1414%
Inv1_cb16_S 10 | 11.34 | 0.1414%
Inv1_cb17_S 1 | 11.34 | 0.1414%
Inv1_cb17_S 2 | 11.34 | 0.1414%
Inv1_cb17_S 3 | 11.34 | 0.1414%
Inv1_cb17_S 4 | 11.34 | 0.1414%
Inv1_cb17_S 5 | 11.34 | 0.1414%
Inv1_cb17_S 6 | 11.34 | 0.1414%
Inv1_cb17_S 7 | 11.34 | 0.1414%
Inv1_cb17_S 8 | 11.34 | 0.1414%
Inv1_cb17_S 9 | 11.34 | 0.1414%
Inv1_cb17_S 10 | 11.34 | 0.1414%
Inv1_cb18_S 1 | 11.34 | 0.1414%
Inv1_cb18_S 2 | 11.34 | 0.1414%
Inv1_cb18_S 3 | 11.34 | 0.1414%
Inv1_cb18_S 4 | 11.34 | 0.1414%
Inv1_cb18_S 5 | 11.34 | 0.1414%
Inv1_cb18_S 6 | 11.34 | 0.1414%
Inv1_cb18_S 7 | 11.34 | 0.1414%
Inv1_cb18_S 8 | 11.34 | 0.1414%
Inv1_cb18_S 9 | 11.34 | 0.1414%
Inv1_cb18_S 10 | 11.34 | 0.1414%
Inv1_cb19_S 1 | 11.34 | 0.1414%
Inv1_cb19_S 2 | 11.34 | 0.1414%
Inv1_cb19_S 3 | 11.34 | 0.1414%
Inv1_cb19_S 4 | 11.34 | 0.1414%
Inv1_cb19_S 5 | 11.34 | 0.1414%
Inv1_cb19_S 6 | 11.34 | 0.1414%
Inv1_cb19_S 7 | 11.34 | 0.1414%
Inv1_cb19_S 8 | 11.34 | 0.1414%
Inv1_cb19_S 9 | 11.34 | 0.1414%
Inv1_cb19_S 10 | 11.34 | 0.1414%
Inv1_cb20_S 1 | 11.34 | 0.1414%
Inv1_cb20_S 2 | 11.34 | 0.1414%
Inv1_cb20_S 3 | 11.34 | 0.1414%
Inv1_cb20_S 4 | 11.34 | 0.1414%
Inv1_cb20_S 5 | 11.34 | 0.1414%
Inv1_cb20_S 6 | 11.34 | 0.1414%
Inv1_cb20_S 7 | 11.34 | 0.1414%
Inv1_cb20_S 8 | 11.34 | 0.1414%
Inv1_cb20_S 9 | 11.34 | 0.1414%
Inv1_cb20_S 10 | 11.34 | 0.1414%
Inv1_cb21_S 1 | 11.34 | 0.1414%
Inv1_cb21_S 2 | 11.34 | 0.1414%
Inv1_cb21_S 3 | 11.34 | 0.1414%
Inv1_cb21_S 4 | 11.34 | 0.1414%
Inv1_cb21_S 5 | 11.34 | 0.1414%
Inv1_cb21_S 6 | 11.34 | 0.1414%
Inv1_cb21_S 7 | 11.34 | 0.1414%
Inv1_cb21_S 8 | 11.34 | 0.1414%
Inv1_cb21_S 9 | 11.34 | 0.1414%
Inv1_cb21_S 10 | 11.34 | 0.1414%
Inv1_cb22_S 1 | 11.34 | 0.1414%
Inv1_cb22_S 2 | 11.34 | 0.1414%
Inv1_cb22_S 3 | 11.34 | 0.1414%
Inv1_cb22_S 4 | 11.34 | 0.1414%
Inv1_cb22_S 5 | 11.34 | 0.1414%
Inv1_cb22_S 6 | 11.34 | 0.1414%
Inv1_cb22_S 7 | 11.34 | 0.1414%
Inv1_cb22_S 8 | 11.34 | 0.1414%
Inv1_cb22_S 9 | 11.34 | 0.1414%
Inv1_cb22_S 10 | 11.34 | 0.1414%
Inv1_cb23_S 1 | 11.34 | 0.1414%
Inv1_cb23_S 2 | 11.34 | 0.1414%
Inv1_cb23_S 3 | 11.34 | 0.1414%
Inv1_cb23_S 4 | 11.34 | 0.1414%
Inv1_cb23_S 5 | 11.34 | 0.1414%
Inv1_cb23_S 6 | 11.34 | 0.1414%
Inv1_cb23_S 7 | 11.34 | 0.1414%
Inv1_cb23_S 8 | 11.34 | 0.1414%
Inv1_cb23_S 9 | 11.34 | 0.1414%
Inv1_cb23_S 10 | 11.34 | 0.1414%
Inv1_cb24_S 1 | 11.34 | 0.1414%
Inv1_cb24_S 2 | 11.34 | 0.1414%
Inv1_cb24_S 3 | 11.34 | 0.1414%
Inv1_cb24_S 4 | 11.34 | 0.1414%
Inv1_cb24_S 5 | 11.34 | 0.1414%
Inv1_cb24_S 6 | 11.34 | 0.1414%
Inv1_cb24_S 7 | 11.34 | 0.1414%
Inv1_cb24_S 8 | 11.34 | 0.1414%
Inv1_cb24_S 9 | 11.34 | 0.1414%
Inv1_cb24_S 10 | 11.34 | 0.1414%
Inv2_cb1_S 1 | 11.34 | 0.1414%
Inv2_cb1_S 2 | 11.34 | 0.1414%
Inv2_cb1_S 3 | 11.34 | 0.1414%
Inv2_cb1_S 4 | 11.34 | 0.1414%
Inv2_cb1_S 5 | 11.34 | 0.1414%
Inv2_cb1_S 6 | 11.34 | 0.1414%
Inv2_cb1_S 7 | 11.34 | 0.1414%
Inv2_cb1_S 8 | 11.34 | 0.1414%
Inv2_cb1_S 9 | 11.34 | 0.1414%
Inv2_cb1_S 10 | 11.34 | 0.1414%
Inv2_cb2_S 1 | 10.8 | 0.1346%
Inv2_cb2_S 2 | 10.8 | 0.1346%
Inv2_cb2_S 3 | 10.8 | 0.1346%
Inv2_cb2_S 4 | 10.8 | 0.1346%
Inv2_cb2_S 5 | 10.8 | 0.1346%
Inv2_cb2_S 6 | 10.8 | 0.1346%
Inv2_cb2_S 7 | 10.8 | 0.1346%
Inv2_cb2_S 8 | 10.8 | 0.1346%
Inv2_cb2_S 9 | 10.8 | 0.1346%
Inv2_cb2_S 10 | 10.8 | 0.1346%
Inv2_cb3_S 1 | 10.8 | 0.1346%
Inv2_cb3_S 2 | 10.8 | 0.1346%
Inv2_cb3_S 3 | 10.8 | 0.1346%
Inv2_cb3_S 4 | 10.8 | 0.1346%
Inv2_cb3_S 5 | 10.8 | 0.1346%
Inv2_cb3_S 6 | 10.8 | 0.1346%
Inv2_cb3_S 7 | 10.8 | 0.1346%
Inv2_cb3_S 8 | 10.8 | 0.1346%
Inv2_cb3_S 9 | 10.8 | 0.1346%
Inv2_cb3_S 10 | 10.8 | 0.1346%
Inv2_cb4_S 1 | 10.98 | 0.1369%
Inv2_cb4_S 2 | 10.98 | 0.1369%
Inv2_cb4_S 3 | 10.98 | 0.1369%
Inv2_cb4_S 4 | 10.98 | 0.1369%
Inv2_cb4_S 5 | 10.98 | 0.1369%
Inv2_cb4_S 6 | 10.98 | 0.1369%
Inv2_cb4_S 7 | 10.98 | 0.1369%
Inv2_cb4_S 8 | 10.98 | 0.1369%
Inv2_cb4_S 9 | 10.98 | 0.1369%
Inv2_cb4_S 10 | 10.98 | 0.1369%
Inv2_cb5_S 1 | 10.98 | 0.1369%
Inv2_cb5_S 2 | 10.98 | 0.1369%
Inv2_cb5_S 3 | 10.98 | 0.1369%
Inv2_cb5_S 4 | 10.98 | 0.1369%
Inv2_cb5_S 5 | 10.98 | 0.1369%
Inv2_cb5_S 6 | 10.98 | 0.1369%
Inv2_cb5_S 7 | 10.98 | 0.1369%
Inv2_cb5_S 8 | 10.98 | 0.1369%
Inv2_cb5_S 9 | 10.98 | 0.1369%
Inv2_cb5_S 10 | 10.98 | 0.1369%
Inv2_cb6_S 1 | 10.98 | 0.1369%
Inv2_cb6_S 2 | 10.98 | 0.1369%
Inv2_cb6_S 3 | 10.98 | 0.1369%
Inv2_cb6_S 4 | 10.98 | 0.1369%
Inv2_cb6_S 5 | 10.98 | 0.1369%
Inv2_cb6_S 6 | 10.98 | 0.1369%
Inv2_cb6_S 7 | 10.98 | 0.1369%
Inv2_cb6_S 8 | 10.98 | 0.1369%
Inv2_cb6_S 9 | 10.98 | 0.1369%
Inv2_cb6_S 10 | 10.98 | 0.1369%
Inv2_cb7_S 1 | 10.98 | 0.1369%
Inv2_cb7_S 2 | 10.98 | 0.1369%
Inv2_cb7_S 3 | 10.98 | 0.1369%
Inv2_cb7_S 4 | 10.98 | 0.1369%
Inv2_cb7_S 5 | 10.98 | 0.1369%
Inv2_cb7_S 6 | 10.98 | 0.1369%
Inv2_cb7_S 7 | 10.98 | 0.1369%
Inv2_cb7_S 8 | 10.98 | 0.1369%
Inv2_cb7_S 9 | 10.98 | 0.1369%
Inv2_cb7_S 10 | 10.98 | 0.1369%
Inv2_cb8_S 1 | 10.98 | 0.1369%
Inv2_cb8_S 2 | 10.98 | 0.1369%
Inv2_cb8_S 3 | 10.98 | 0.1369%
Inv2_cb8_S 4 | 10.98 | 0.1369%
Inv2_cb8_S 5 | 10.98 | 0.1369%
Inv2_cb8_S 6 | 10.98 | 0.1369%
Inv2_cb8_S 7 | 10.98 | 0.1369%
Inv2_cb8_S 8 | 10.98 | 0.1369%
Inv2_cb8_S 9 | 10.98 | 0.1369%
Inv2_cb8_S 10 | 10.98 | 0.1369%
Inv2_cb9_S 1 | 10.98 | 0.1369%
Inv2_cb9_S 2 | 10.98 | 0.1369%
Inv2_cb9_S 3 | 10.98 | 0.1369%
Inv2_cb9_S 4 | 10.98 | 0.1369%
Inv2_cb9_S 5 | 10.98 | 0.1369%
Inv2_cb9_S 6 | 10.98 | 0.1369%
Inv2_cb9_S 7 | 10.98 | 0.1369%
Inv2_cb9_S 8 | 10.98 | 0.1369%
Inv2_cb9_S 9 | 10.98 | 0.1369%
Inv2_cb9_S 10 | 10.98 | 0.1369%
Inv2_cb10_S 1 | 10.98 | 0.1369%
Inv2_cb10_S 2 | 10.98 | 0.1369%
Inv2_cb10_S 3 | 10.98 | 0.1369%
Inv2_cb10_S 4 | 10.98 | 0.1369%
Inv2_cb10_S 5 | 10.98 | 0.1369%
Inv2_cb10_S 6 | 10.98 | 0.1369%
Inv2_cb10_S 7 | 10.98 | 0.1369%
Inv2_cb10_S 8 | 10.98 | 0.1369%
Inv2_cb10_S 9 | 10.98 | 0.1369%
Inv2_cb10_S 10 | 10.98 | 0.1369%
Inv2_cb11_S 1 | 10.98 | 0.1369%
Inv2_cb11_S 2 | 10.98 | 0.1369%
Inv2_cb11_S 3 | 10.98 | 0.1369%
Inv2_cb11_S 4 | 10.98 | 0.1369%
Inv2_cb11_S 5 | 10.98 | 0.1369%
Inv2_cb11_S 6 | 10.98 | 0.1369%
Inv2_cb11_S 7 | 10.98 | 0.1369%
Inv2_cb11_S 8 | 10.98 | 0.1369%
Inv2_cb11_S 9 | 10.98 | 0.1369%
Inv2_cb11_S 10 | 10.98 | 0.1369%
Inv2_cb12_S 1 | 10.98 | 0.1369%
Inv2_cb12_S 2 | 10.98 | 0.1369%
Inv2_cb12_S 3 | 10.98 | 0.1369%
Inv2_cb12_S 4 | 10.98 | 0.1369%
Inv2_cb12_S 5 | 10.98 | 0.1369%
Inv2_cb12_S 6 | 10.98 | 0.1369%
Inv2_cb12_S 7 | 10.98 | 0.1369%
Inv2_cb12_S 8 | 10.98 | 0.1369%
Inv2_cb12_S 9 | 10.98 | 0.1369%
Inv2_cb12_S 10 | 10.98 | 0.1369%
Inv2_cb13_S 1 | 10.98 | 0.1369%
Inv2_cb13_S 2 | 10.98 | 0.1369%
Inv2_cb13_S 3 | 10.98 | 0.1369%
Inv2_cb13_S 4 | 10.98 | 0.1369%
Inv2_cb13_S 5 | 10.98 | 0.1369%
Inv2_cb13_S 6 | 10.98 | 0.1369%
Inv2_cb13_S 7 | 10.98 | 0.1369%
Inv2_cb13_S 8 | 10.98 | 0.1369%
Inv2_cb13_S 9 | 10.98 | 0.1369%
Inv2_cb13_S 10 | 10.98 | 0.1369%
Inv2_cb14_S 1 | 10.98 | 0.1369%
Inv2_cb14_S 2 | 10.98 | 0.1369%
Inv2_cb14_S 3 | 10.98 | 0.1369%
Inv2_cb14_S 4 | 10.98 | 0.1369%
Inv2_cb14_S 5 | 10.98 | 0.1369%
Inv2_cb14_S 6 | 10.98 | 0.1369%
Inv2_cb14_S 7 | 10.98 | 0.1369%
Inv2_cb14_S 8 | 10.98 | 0.1369%
Inv2_cb14_S 9 | 10.98 | 0.1369%
Inv2_cb14_S 10 | 10.98 | 0.1369%
Inv2_cb15_S 1 | 10.98 | 0.1369%
Inv2_cb15_S 2 | 10.98 | 0.1369%
Inv2_cb15_S 3 | 10.98 | 0.1369%
Inv2_cb15_S 4 | 10.98 | 0.1369%
Inv2_cb15_S 5 | 10.98 | 0.1369%
Inv2_cb15_S 6 | 10.98 | 0.1369%
Inv2_cb15_S 7 | 10.98 | 0.1369%
Inv2_cb15_S 8 | 10.98 | 0.1369%
Inv2_cb15_S 9 | 10.98 | 0.1369%
Inv2_cb15_S 10 | 10.98 | 0.1369%
Inv2_cb16_S 1 | 10.98 | 0.1369%
Inv2_cb16_S 2 | 10.98 | 0.1369%
Inv2_cb16_S 3 | 10.98 | 0.1369%
Inv2_cb16_S 4 | 10.98 | 0.1369%
Inv2_cb16_S 5 | 10.98 | 0.1369%
Inv2_cb16_S 6 | 10.98 | 0.1369%
Inv2_cb16_S 7 | 10.98 | 0.1369%
Inv2_cb16_S 8 | 10.98 | 0.1369%
Inv2_cb16_S 9 | 10.98 | 0.1369%
Inv2_cb16_S 10 | 10.98 | 0.1369%
Inv2_cb17_S 1 | 10.98 | 0.1369%
Inv2_cb17_S 2 | 10.98 | 0.1369%
Inv2_cb17_S 3 | 10.98 | 0.1369%
Inv2_cb17_S 4 | 10.98 | 0.1369%
Inv2_cb17_S 5 | 10.98 | 0.1369%
Inv2_cb17_S 6 | 10.98 | 0.1369%
Inv2_cb17_S 7 | 10.98 | 0.1369%
Inv2_cb17_S 8 | 10.98 | 0.1369%
Inv2_cb17_S 9 | 10.98 | 0.1369%
Inv2_cb17_S 10 | 10.98 | 0.1369%
Inv2_cb18_S 1 | 10.98 | 0.1369%
Inv2_cb18_S 2 | 10.98 | 0.1369%
Inv2_cb18_S 3 | 10.98 | 0.1369%
Inv2_cb18_S 4 | 10.98 | 0.1369%
Inv2_cb18_S 5 | 10.98 | 0.1369%
Inv2_cb18_S 6 | 10.98 | 0.1369%
Inv2_cb18_S 7 | 10.98 | 0.1369%
Inv2_cb18_S 8 | 10.98 | 0.1369%
Inv2_cb18_S 9 | 10.98 | 0.1369%
Inv2_cb18_S 10 | 10.98 | 0.1369%
Inv2_cb19_S 1 | 10.98 | 0.1369%
Inv2_cb19_S 2 | 10.98 | 0.1369%
Inv2_cb19_S 3 | 10.98 | 0.1369%
Inv2_cb19_S 4 | 10.98 | 0.1369%
Inv2_cb19_S 5 | 10.98 | 0.1369%
Inv2_cb19_S 6 | 10.98 | 0.1369%
Inv2_cb19_S 7 | 10.98 | 0.1369%
Inv2_cb19_S 8 | 10.98 | 0.1369%
Inv2_cb19_S 9 | 10.98 | 0.1369%
Inv2_cb19_S 10 | 10.98 | 0.1369%
Inv2_cb20_S 1 | 10.98 | 0.1369%
Inv2_cb20_S 2 | 10.98 | 0.1369%
Inv2_cb20_S 3 | 10.98 | 0.1369%
Inv2_cb20_S 4 | 10.98 | 0.1369%
Inv2_cb20_S 5 | 10.98 | 0.1369%
Inv2_cb20_S 6 | 10.98 | 0.1369%
Inv2_cb20_S 7 | 10.98 | 0.1369%
Inv2_cb20_S 8 | 10.98 | 0.1369%
Inv2_cb20_S 9 | 10.98 | 0.1369%
Inv2_cb20_S 10 | 10.98 | 0.1369%
Inv2_cb21_S 1 | 10.98 | 0.1369%
Inv2_cb21_S 2 | 10.98 | 0.1369%
Inv2_cb21_S 3 | 10.98 | 0.1369%
Inv2_cb21_S 4 | 10.98 | 0.1369%
Inv2_cb21_S 5 | 10.98 | 0.1369%
Inv2_cb21_S 6 | 10.98 | 0.1369%
Inv2_cb21_S 7 | 10.98 | 0.1369%
Inv2_cb21_S 8 | 10.98 | 0.1369%
Inv2_cb21_S 9 | 10.98 | 0.1369%
Inv2_cb21_S 10 | 10.98 | 0.1369%
Inv2_cb22_S 1 | 10.98 | 0.1369%
Inv2_cb22_S 2 | 10.98 | 0.1369%
Inv2_cb22_S 3 | 10.98 | 0.1369%
Inv2_cb22_S 4 | 10.98 | 0.1369%
Inv2_cb22_S 5 | 10.98 | 0.1369%
Inv2_cb22_S 6 | 10.98 | 0.1369%
Inv2_cb22_S 7 | 10.98 | 0.1369%
Inv2_cb22_S 8 | 10.98 | 0.1369%
Inv2_cb22_S 9 | 10.98 | 0.1369%
Inv2_cb22_S 10 | 10.98 | 0.1369%
Inv2_cb23_S 1 | 10.98 | 0.1369%
Inv2_cb23_S 2 | 10.98 | 0.1369%
Inv2_cb23_S 3 | 10.98 | 0.1369%
Inv2_cb23_S 4 | 10.98 | 0.1369%
Inv2_cb23_S 5 | 10.98 | 0.1369%
Inv2_cb23_S 6 | 10.98 | 0.1369%
Inv2_cb23_S 7 | 10.98 | 0.1369%
Inv2_cb23_S 8 | 10.98 | 0.1369%
Inv2_cb23_S 9 | 10.98 | 0.1369%
Inv2_cb23_S 10 | 10.98 | 0.1369%
Inv2_cb24_S 1 | 10.98 | 0.1369%
Inv2_cb24_S 2 | 10.98 | 0.1369%
Inv2_cb24_S 3 | 10.98 | 0.1369%
Inv2_cb24_S 4 | 10.98 | 0.1369%
Inv2_cb24_S 5 | 10.98 | 0.1369%
Inv2_cb24_S 6 | 10.98 | 0.1369%
Inv2_cb24_S 7 | 10.98 | 0.1369%
Inv2_cb24_S 8 | 10.98 | 0.1369%
Inv2_cb24_S 9 | 10.98 | 0.1369%
Inv2_cb24_S 10 | 10.98 | 0.1369%
Inv3_cb1_S 1 | 11.16 | 0.1391%
Inv3_cb1_S 2 | 11.16 | 0.1391%
Inv3_cb1_S 3 | 11.16 | 0.1391%
Inv3_cb1_S 4 | 11.16 | 0.1391%
Inv3_cb1_S 5 | 11.16 | 0.1391%
Inv3_cb1_S 6 | 11.16 | 0.1391%
Inv3_cb1_S 7 | 11.16 | 0.1391%
Inv3_cb1_S 8 | 11.16 | 0.1391%
Inv3_cb1_S 9 | 11.16 | 0.1391%
Inv3_cb1_S 10 | 11.16 | 0.1391%
Inv3_cb2_S 1 | 11.16 | 0.1391%
Inv3_cb2_S 2 | 11.16 | 0.1391%
Inv3_cb2_S 3 | 11.16 | 0.1391%
Inv3_cb2_S 4 | 11.16 | 0.1391%
Inv3_cb2_S 5 | 11.16 | 0.1391%
Inv3_cb2_S 6 | 11.16 | 0.1391%
Inv3_cb2_S 7 | 11.16 | 0.1391%
Inv3_cb2_S 8 | 11.16 | 0.1391%
Inv3_cb2_S 9 | 11.16 | 0.1391%
Inv3_cb2_S 10 | 11.16 | 0.1391%
Inv3_cb3_S 1 | 11.16 | 0.1391%
Inv3_cb3_S 2 | 11.16 | 0.1391%
Inv3_cb3_S 3 | 11.16 | 0.1391%
Inv3_cb3_S 4 | 11.16 | 0.1391%
Inv3_cb3_S 5 | 11.16 | 0.1391%
Inv3_cb3_S 6 | 11.16 | 0.1391%
Inv3_cb3_S 7 | 11.16 | 0.1391%
Inv3_cb3_S 8 | 11.16 | 0.1391%
Inv3_cb3_S 9 | 11.16 | 0.1391%
Inv3_cb3_S 10 | 11.16 | 0.1391%
Inv3_cb4_S 1 | 11.232 | 0.14%
Inv3_cb4_S 2 | 11.232 | 0.14%
Inv3_cb4_S 3 | 11.232 | 0.14%
Inv3_cb4_S 4 | 11.232 | 0.14%
Inv3_cb4_S 5 | 11.232 | 0.14%
Inv3_cb4_S 6 | 11.232 | 0.14%
Inv3_cb4_S 7 | 11.232 | 0.14%
Inv3_cb4_S 8 | 11.232 | 0.14%
Inv3_cb4_S 9 | 11.232 | 0.14%
Inv3_cb4_S 10 | 11.232 | 0.14%
Inv3_cb5_S 1 | 11.232 | 0.14%
Inv3_cb5_S 2 | 11.232 | 0.14%
Inv3_cb5_S 3 | 11.232 | 0.14%
Inv3_cb5_S 4 | 11.232 | 0.14%
Inv3_cb5_S 5 | 11.232 | 0.14%
Inv3_cb5_S 6 | 11.232 | 0.14%
Inv3_cb5_S 7 | 11.232 | 0.14%
Inv3_cb5_S 8 | 11.232 | 0.14%
Inv3_cb5_S 9 | 11.232 | 0.14%
Inv3_cb5_S 10 | 11.232 | 0.14%
Inv3_cb6_S 1 | 11.232 | 0.14%
Inv3_cb6_S 2 | 11.232 | 0.14%
Inv3_cb6_S 3 | 11.232 | 0.14%
Inv3_cb6_S 4 | 11.232 | 0.14%
Inv3_cb6_S 5 | 11.232 | 0.14%
Inv3_cb6_S 6 | 11.232 | 0.14%
Inv3_cb6_S 7 | 11.232 | 0.14%
Inv3_cb6_S 8 | 11.232 | 0.14%
Inv3_cb6_S 9 | 11.232 | 0.14%
Inv3_cb6_S 10 | 11.232 | 0.14%
Inv3_cb7_S 1 | 11.232 | 0.14%
Inv3_cb7_S 2 | 11.232 | 0.14%
Inv3_cb7_S 3 | 11.232 | 0.14%
Inv3_cb7_S 4 | 11.232 | 0.14%
Inv3_cb7_S 5 | 11.232 | 0.14%
Inv3_cb7_S 6 | 11.232 | 0.14%
Inv3_cb7_S 7 | 11.232 | 0.14%
Inv3_cb7_S 8 | 11.232 | 0.14%
Inv3_cb7_S 9 | 11.232 | 0.14%
Inv3_cb7_S 10 | 11.232 | 0.14%
Inv3_cb8_S 1 | 10.98 | 0.1369%
Inv3_cb8_S 2 | 10.98 | 0.1369%
Inv3_cb8_S 3 | 10.98 | 0.1369%
Inv3_cb8_S 4 | 10.98 | 0.1369%
Inv3_cb8_S 5 | 10.98 | 0.1369%
Inv3_cb8_S 6 | 10.98 | 0.1369%
Inv3_cb8_S 7 | 10.98 | 0.1369%
Inv3_cb8_S 8 | 10.98 | 0.1369%
Inv3_cb8_S 9 | 10.98 | 0.1369%
Inv3_cb8_S 10 | 10.98 | 0.1369%
Inv3_cb9_S 1 | 10.98 | 0.1369%
Inv3_cb9_S 2 | 10.98 | 0.1369%
Inv3_cb9_S 3 | 10.98 | 0.1369%
Inv3_cb9_S 4 | 10.98 | 0.1369%
Inv3_cb9_S 5 | 10.98 | 0.1369%
Inv3_cb9_S 6 | 10.98 | 0.1369%
Inv3_cb9_S 7 | 10.98 | 0.1369%
Inv3_cb9_S 8 | 10.98 | 0.1369%
Inv3_cb9_S 9 | 10.98 | 0.1369%
Inv3_cb9_S 10 | 10.98 | 0.1369%
Inv3_cb10_S 1 | 10.98 | 0.1369%
Inv3_cb10_S 2 | 10.98 | 0.1369%
Inv3_cb10_S 3 | 10.98 | 0.1369%
Inv3_cb10_S 4 | 10.98 | 0.1369%
Inv3_cb10_S 5 | 10.98 | 0.1369%
Inv3_cb10_S 6 | 10.98 | 0.1369%
Inv3_cb10_S 7 | 10.98 | 0.1369%
Inv3_cb10_S 8 | 10.98 | 0.1369%
Inv3_cb10_S 9 | 10.98 | 0.1369%
Inv3_cb10_S 10 | 10.98 | 0.1369%
Inv3_cb11_S 1 | 10.98 | 0.1369%
Inv3_cb11_S 2 | 10.98 | 0.1369%
Inv3_cb11_S 3 | 10.98 | 0.1369%
Inv3_cb11_S 4 | 10.98 | 0.1369%
Inv3_cb11_S 5 | 10.98 | 0.1369%
Inv3_cb11_S 6 | 10.98 | 0.1369%
Inv3_cb11_S 7 | 10.98 | 0.1369%
Inv3_cb11_S 8 | 10.98 | 0.1369%
Inv3_cb11_S 9 | 10.98 | 0.1369%
Inv3_cb11_S 10 | 10.98 | 0.1369%
Inv3_cb12_S 1 | 10.98 | 0.1369%
Inv3_cb12_S 2 | 10.98 | 0.1369%
Inv3_cb12_S 3 | 10.98 | 0.1369%
Inv3_cb12_S 4 | 10.98 | 0.1369%
Inv3_cb12_S 5 | 10.98 | 0.1369%
Inv3_cb12_S 6 | 10.98 | 0.1369%
Inv3_cb12_S 7 | 10.98 | 0.1369%
Inv3_cb12_S 8 | 10.98 | 0.1369%
Inv3_cb12_S 9 | 10.98 | 0.1369%
Inv3_cb12_S 10 | 10.98 | 0.1369%
Inv3_cb13_S 1 | 11.34 | 0.1414%
Inv3_cb13_S 2 | 11.34 | 0.1414%
Inv3_cb13_S 3 | 11.34 | 0.1414%
Inv3_cb13_S 4 | 11.34 | 0.1414%
Inv3_cb13_S 5 | 11.34 | 0.1414%
Inv3_cb13_S 6 | 11.34 | 0.1414%
Inv3_cb13_S 7 | 11.34 | 0.1414%
Inv3_cb13_S 8 | 11.34 | 0.1414%
Inv3_cb13_S 9 | 11.34 | 0.1414%
Inv3_cb13_S 10 | 11.34 | 0.1414%
Inv3_cb14_S 1 | 11.34 | 0.1414%
Inv3_cb14_S 2 | 11.34 | 0.1414%
Inv3_cb14_S 3 | 11.34 | 0.1414%
Inv3_cb14_S 4 | 11.34 | 0.1414%
Inv3_cb14_S 5 | 11.34 | 0.1414%
Inv3_cb14_S 6 | 11.34 | 0.1414%
Inv3_cb14_S 7 | 11.34 | 0.1414%
Inv3_cb14_S 8 | 11.34 | 0.1414%
Inv3_cb14_S 9 | 11.34 | 0.1414%
Inv3_cb14_S 10 | 11.34 | 0.1414%
Inv3_cb15_S 1 | 11.34 | 0.1414%
Inv3_cb15_S 2 | 11.34 | 0.1414%
Inv3_cb15_S 3 | 11.34 | 0.1414%
Inv3_cb15_S 4 | 11.34 | 0.1414%
Inv3_cb15_S 5 | 11.34 | 0.1414%
Inv3_cb15_S 6 | 11.34 | 0.1414%
Inv3_cb15_S 7 | 11.34 | 0.1414%
Inv3_cb15_S 8 | 11.34 | 0.1414%
Inv3_cb15_S 9 | 11.34 | 0.1414%
Inv3_cb15_S 10 | 11.34 | 0.1414%
Inv3_cb16_S 1 | 11.34 | 0.1414%
Inv3_cb16_S 2 | 11.34 | 0.1414%
Inv3_cb16_S 3 | 11.34 | 0.1414%
Inv3_cb16_S 4 | 11.34 | 0.1414%
Inv3_cb16_S 5 | 11.34 | 0.1414%
Inv3_cb16_S 6 | 11.34 | 0.1414%
Inv3_cb16_S 7 | 11.34 | 0.1414%
Inv3_cb16_S 8 | 11.34 | 0.1414%
Inv3_cb16_S 9 | 11.34 | 0.1414%
Inv3_cb16_S 10 | 11.34 | 0.1414%
Inv3_cb17_S 1 | 11.34 | 0.1414%
Inv3_cb17_S 2 | 11.34 | 0.1414%
Inv3_cb17_S 3 | 11.34 | 0.1414%
Inv3_cb17_S 4 | 11.34 | 0.1414%
Inv3_cb17_S 5 | 11.34 | 0.1414%
Inv3_cb17_S 6 | 11.34 | 0.1414%
Inv3_cb17_S 7 | 11.34 | 0.1414%
Inv3_cb17_S 8 | 11.34 | 0.1414%
Inv3_cb17_S 9 | 11.34 | 0.1414%
Inv3_cb17_S 10 | 11.34 | 0.1414%
Inv3_cb18_S 1 | 11.34 | 0.1414%
Inv3_cb18_S 2 | 11.34 | 0.1414%
Inv3_cb18_S 3 | 11.34 | 0.1414%
Inv3_cb18_S 4 | 11.34 | 0.1414%
Inv3_cb18_S 5 | 11.34 | 0.1414%
Inv3_cb18_S 6 | 11.34 | 0.1414%
Inv3_cb18_S 7 | 11.34 | 0.1414%
Inv3_cb18_S 8 | 11.34 | 0.1414%
Inv3_cb18_S 9 | 11.34 | 0.1414%
Inv3_cb18_S 10 | 11.34 | 0.1414%
Inv3_cb19_S 1 | 11.34 | 0.1414%
Inv3_cb19_S 2 | 11.34 | 0.1414%
Inv3_cb19_S 3 | 11.34 | 0.1414%
Inv3_cb19_S 4 | 11.34 | 0.1414%
Inv3_cb19_S 5 | 11.34 | 0.1414%
Inv3_cb19_S 6 | 11.34 | 0.1414%
Inv3_cb19_S 7 | 11.34 | 0.1414%
Inv3_cb19_S 8 | 11.34 | 0.1414%
Inv3_cb19_S 9 | 11.34 | 0.1414%
Inv3_cb19_S 10 | 11.34 | 0.1414%
Inv3_cb20_S 1 | 11.34 | 0.1414%
Inv3_cb20_S 2 | 11.34 | 0.1414%
Inv3_cb20_S 3 | 11.34 | 0.1414%
Inv3_cb20_S 4 | 11.34 | 0.1414%
Inv3_cb20_S 5 | 11.34 | 0.1414%
Inv3_cb20_S 6 | 11.34 | 0.1414%
Inv3_cb20_S 7 | 11.34 | 0.1414%
Inv3_cb20_S 8 | 11.34 | 0.1414%
Inv3_cb20_S 9 | 11.34 | 0.1414%
Inv3_cb20_S 10 | 11.34 | 0.1414%
Inv3_cb21_S 1 | 11.34 | 0.1414%
Inv3_cb21_S 2 | 11.34 | 0.1414%
Inv3_cb21_S 3 | 11.34 | 0.1414%
Inv3_cb21_S 4 | 11.34 | 0.1414%
Inv3_cb21_S 5 | 11.34 | 0.1414%
Inv3_cb21_S 6 | 11.34 | 0.1414%
Inv3_cb21_S 7 | 11.34 | 0.1414%
Inv3_cb21_S 8 | 11.34 | 0.1414%
Inv3_cb21_S 9 | 11.34 | 0.1414%
Inv3_cb21_S 10 | 11.34 | 0.1414%
Inv3_cb22_S 1 | 11.34 | 0.1414%
Inv3_cb22_S 2 | 11.34 | 0.1414%
Inv3_cb22_S 3 | 11.34 | 0.1414%
Inv3_cb22_S 4 | 11.34 | 0.1414%
Inv3_cb22_S 5 | 11.34 | 0.1414%
Inv3_cb22_S 6 | 11.34 | 0.1414%
Inv3_cb22_S 7 | 11.34 | 0.1414%
Inv3_cb22_S 8 | 11.34 | 0.1414%
Inv3_cb22_S 9 | 11.34 | 0.1414%
Inv3_cb22_S 10 | 11.34 | 0.1414%
Inv3_cb23_S 1 | 11.34 | 0.1414%
Inv3_cb23_S 2 | 11.34 | 0.1414%
Inv3_cb23_S 3 | 11.34 | 0.1414%
Inv3_cb23_S 4 | 11.34 | 0.1414%
Inv3_cb23_S 5 | 11.34 | 0.1414%
Inv3_cb23_S 6 | 11.34 | 0.1414%
Inv3_cb23_S 7 | 11.34 | 0.1414%
Inv3_cb23_S 8 | 11.34 | 0.1414%
Inv3_cb23_S 9 | 11.34 | 0.1414%
Inv3_cb23_S 10 | 11.34 | 0.1414%
Inv3_cb24_S 1 | 11.34 | 0.1414%
Inv3_cb24_S 2 | 11.34 | 0.1414%
Inv3_cb24_S 3 | 11.34 | 0.1414%
Inv3_cb24_S 4 | 11.34 | 0.1414%
Inv3_cb24_S 5 | 11.34 | 0.1414%
Inv3_cb24_S 6 | 11.34 | 0.1414%
Inv3_cb24_S 7 | 11.34 | 0.1414%
Inv3_cb24_S 8 | 11.34 | 0.1414%
Inv3_cb24_S 9 | 11.34 | 0.1414%
Inv3_cb24_S 10 | 11.34 | 0.1414%

## Inv_SY
[21 empty] | 2694.6 | 2630.8 | 2695.5
[8 empty] | DC Capacity | 669.6 | 669.6 | 675 | 680.4 | 658.8 | 658.8 | 658.8 | 658.8 | 671.76 | 661.32 | 680.04 | 680.04 | 2694.6 | 2630.8 | 2695.5
Finacial Year | Start Month | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Date | Plant DC Capcity (MW) | Inv 1 (630kw) unit 1 | Inv 1 (630kw) unit 2 | Inv 1 (630kw) unit 3 | Inv 1 (630kw) unit 4 | Inv 2 (630kw) unit 1 | Inv 2 (630kw) unit 2 | Inv 2 (630kw) unit 3 | Inv 2 (630kw) unit 4 | Inv 3 (630kw) unit 1 | Inv 3 (630kw) unit 2 | Inv 3 (630kw) unit 3 | Inv 3 (630kw) unit 4 | Inv1 | Inv2 | Inv3 | Avg. SY | Max. SY
FY2025-26 | 4 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | 2025-03-29 | 8.0209 | 2.888 | 3.0118 | 0 | 2.8454 | 4.1709 | 4.0203 | 4.0238 | 0 | 4.1775 | 4.2532 | 4.1198 | 4.1859 | 2.1846 | 3.0589 | 4.18 | 3.1411 | 4.18
FY2025-26 | 4 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | 2025-03-30 | 8.0209 | 3.241 | 3.2452 | 0 | 3.3214 | 4.5044 | 4.35 | 4.3511 | 0 | 4.6122 | 4.5828 | 4.4461 | 4.4094 | 2.4505 | 3.3069 | 4.5079 | 3.4218 | 4.5079
FY2025-26 | 4 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | 2025-03-31 | 8.0209 | 3.4304 | 3.3065 | 0 | 3.2554 | 4.3974 | 4.3675 | 4.5026 | 0 | 4.5321 | 4.6088 | 4.5663 | 4.429 | 2.4961 | 3.3224 | 4.5296 | 3.4494 | 4.5296
FY2025-26 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-01 | 8.0209 | 3.3475 | 3.4828 | 0 | 3.2985 | 4.5554 | 4.3893 | 4.3945 | 0 | 4.5592 | 4.6365 | 4.4908 | 4.5497 | 2.5302 | 3.3404 | 4.5546 | 3.4751 | 4.5546
FY2025-26 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-02 | 8.0209 | 2.7948 | 2.7978 | 0 | 2.8839 | 5.0291 | 4.8546 | 4.8611 | 0 | 5.1722 | 5.1506 | 4.9891 | 4.9504 | 2.1179 | 3.6924 | 5.0603 | 3.6235 | 5.0603
FY2025-26 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-03 | 8.0209 | 1.9498 | 1.9406 | 0 | 1.8079 | 2.3162 | 2.4988 | 2.3028 | 0 | 2.3818 | 2.7112 | 2.3512 | 2.3338 | 1.4233 | 1.7824 | 2.4407 | 1.8821 | 2.4407
FY2025-26 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-04 | 8.0209 | 2.833 | 2.8967 | 0 | 2.8204 | 6.2705 | 6.3528 | 6.2356 | 0 | 5.39 | 5.3446 | 5.1772 | 5.1381 | 2.136 | 4.7226 | 5.2569 | 4.0385 | 5.2569
FY2025-26 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-05 | 8.0209 | 2.4415 | 2.4464 | 0 | 2.5107 | 6.316 | 6.2702 | 6.3818 | 0 | 5.3343 | 5.5152 | 5.2494 | 5.2073 | 1.8486 | 4.7499 | 5.3206 | 3.973 | 5.3206
FY2025-26 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-06 | 8.0209 | 3.253 | 3.2584 | 0 | 3.2966 | 6.8971 | 6.7743 | 6.7881 | 0 | 5.2772 | 5.3681 | 5.2669 | 5.1563 | 2.4505 | 5.1234 | 5.2618 | 4.2786 | 5.2618
FY2025-26 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-07 | 8.0209 | 4.9358 | 4.8378 | 0 | 4.7607 | 6.1592 | 6.0184 | 6.0276 | 0 | 5.1361 | 5.2209 | 5.0548 | 5.0988 | 3.6308 | 4.5589 | 5.1225 | 4.4374 | 5.1225
FY2025-26 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-08 | 8.0209 | 5.8586 | 5.8578 | 0 | 5.8893 | 5.9039 | 5.7515 | 5.7615 | 0 | 4.6095 | 4.568 | 4.4253 | 4.3884 | 4.3986 | 4.3615 | 4.4931 | 4.4177 | 4.4931
FY2025-26 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-09 | 8.0209 | 6.08 | 6.2168 | 0 | 5.996 | 5.8107 | 5.9127 | 5.7851 | 0 | 4.8745 | 5.073 | 4.801 | 4.7606 | 4.5698 | 4.3844 | 4.8717 | 4.6086 | 4.8717
FY2025-26 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-10 | 8.0209 | 5.4952 | 5.4958 | 0 | 5.5218 | 5.373 | 5.3415 | 5.4689 | 0 | 4.1689 | 4.2427 | 4.2181 | 4.0762 | 4.1255 | 4.0526 | 4.1724 | 4.1169 | 4.1724
FY2025-26 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-11 | 8.0209 | 6.552 | 6.555 | 0 | 6.5475 | 6.3896 | 6.2535 | 6.2631 | 0 | 5.2092 | 5.2988 | 5.1332 | 5.1781 | 4.9103 | 4.7345 | 5.1996 | 4.9481 | 5.1996
FY2025-26 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-12 | 8.0209 | 6.5774 | 6.6537 | 0 | 6.4847 | 5.9141 | 5.9526 | 5.884 | 0 | 5.2827 | 5.4397 | 5.2057 | 5.1657 | 4.9253 | 4.4451 | 5.2677 | 4.8794 | 5.2677
FY2025-26 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-13 | 8.0209 | 6.1935 | 6.1968 | 0 | 6.1942 | 5.6299 | 5.5026 | 5.5109 | 0 | 4.9183 | 5.0067 | 4.8493 | 4.8997 | 4.643 | 4.1678 | 4.9136 | 4.5748 | 4.9136
FY2025-26 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-14 | 8.0209 | 6.5527 | 6.4391 | 0 | 6.3338 | 6.1274 | 6.2084 | 6.0974 | 0 | 5.2744 | 5.2394 | 5.0731 | 5.0313 | 4.8277 | 4.616 | 5.1491 | 4.8643 | 5.1491
FY2025-26 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-15 | 8.0209 | 5.7778 | 5.8751 | 0 | 5.6872 | 5.5709 | 5.4356 | 5.4417 | 0 | 4.3898 | 4.5663 | 4.3289 | 4.2924 | 4.3318 | 4.1189 | 4.3894 | 4.28 | 4.3894
FY2025-26 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-16 | 8.0209 | 4.917 | 4.9137 | 0 | 5.0328 | 4.8365 | 4.9337 | 4.8156 | 0 | 3.795 | 3.862 | 3.8457 | 3.7129 | 3.7137 | 3.6525 | 3.8002 | 3.7221 | 3.8002
FY2025-26 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-17 | 8.0209 | 5.9818 | 5.9821 | 0 | 5.9894 | 5.9173 | 5.8827 | 6.0008 | 0 | 4.5786 | 4.6616 | 4.5169 | 4.5746 | 4.4853 | 4.4576 | 4.5784 | 4.5071 | 4.5784
FY2025-26 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-18 | 8.0209 | 4.4904 | 4.5845 | 0 | 4.463 | 4.5798 | 4.4332 | 4.4414 | 0 | 3.5133 | 3.4853 | 3.4035 | 3.3572 | 3.382 | 3.3692 | 3.4363 | 3.3958 | 3.4363
FY2025-26 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-19 | 8.0209 | 5.6184 | 5.6168 | 0 | 5.6354 | 5.4979 | 5.6444 | 5.4724 | 0 | 4.2274 | 4.4133 | 4.1802 | 4.1428 | 4.2149 | 4.1606 | 4.2361 | 4.2039 | 4.2361
FY2025-26 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-20 | 8.0209 | 6.8247 | 6.825 | 0 | 6.815 | 6.5425 | 6.4961 | 6.6163 | 0 | 5.1649 | 5.2497 | 5.1866 | 5.0471 | 5.1127 | 4.9219 | 5.157 | 5.0639 | 5.157
FY2025-26 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-21 | 8.0209 | 4.9031 | 4.8592 | 0 | 4.827 | 4.8801 | 4.7415 | 4.7461 | 0 | 3.829 | 3.792 | 3.6735 | 3.643 | 3.6447 | 3.5979 | 3.7304 | 3.6577 | 3.7304
FY2025-26 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-22 | 8.0209 | 5.7071 | 5.7045 | 0 | 5.685 | 5.7318 | 5.592 | 5.6014 | 0 | 4.3264 | 4.4296 | 4.3514 | 4.2305 | 4.2712 | 4.2384 | 4.3301 | 4.2799 | 4.3301
FY2025-26 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-23 | 8.0209 | 5.5018 | 5.4997 | 0 | 5.5169 | 5.3986 | 5.4774 | 5.3778 | 0 | 4.1662 | 4.2394 | 4.2092 | 4.0709 | 4.1269 | 4.0702 | 4.1674 | 4.1215 | 4.1674
FY2025-26 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-24 | 8.0209 | 6.042 | 5.9297 | 0 | 5.833 | 5.8089 | 5.7757 | 5.9029 | 0 | 4.4906 | 4.566 | 4.4244 | 4.4846 | 4.4478 | 4.3792 | 4.487 | 4.438 | 4.487
FY2025-26 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-25 | 8.0209 | 5.3599 | 5.3345 | 0 | 5.3542 | 5.3491 | 5.211 | 5.2277 | 0 | 4.1354 | 4.0918 | 3.9924 | 3.9365 | 4.0095 | 3.9536 | 4.0349 | 3.9993 | 4.0349
FY2025-26 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-26 | 8.0209 | 6.2873 | 6.2033 | 0 | 6.0999 | 6.1022 | 6.0648 | 6.163 | 0 | 4.6951 | 4.7792 | 4.7133 | 4.5931 | 4.6441 | 4.5902 | 4.6905 | 4.6416 | 4.6905
FY2025-26 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-27 | 8.0209 | 4.5792 | 4.7082 | 0 | 4.5451 | 4.6246 | 4.5014 | 4.4657 | 0 | 3.5004 | 3.5183 | 3.4211 | 3.5266 | 3.4555 | 3.4036 | 3.4883 | 3.4492 | 3.4883
FY2025-26 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-28 | 8.0209 | 6.7888 | 6.7863 | 0 | 6.7723 | 6.7532 | 6.6135 | 6.6205 | 0 | 5.1514 | 5.3346 | 5.0813 | 5.0379 | 5.0834 | 5.0052 | 5.1456 | 5.0781 | 5.1456
FY2025-26 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-29 | 8.0209 | 5.8662 | 5.7636 | 0 | 5.6734 | 5.5146 | 5.4825 | 5.5888 | 0 | 4.3614 | 4.4269 | 4.3959 | 4.2664 | 4.3225 | 4.1534 | 4.3584 | 4.2781 | 4.3584
Formulas:
Days = DAY(EOMONTH([Month Year],0))
Date = [Date, row above]+1

## Inv_SY_Dev
Finacial Year | Start Month | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Date | Plant DC Capcity (MW) | Inv 1 (630kw) unit 1 wrt avg | Inv 1 (630kw) unit 2 wrt avg | Inv 1 (630kw) unit 3 wrt avg | Inv 1 (630kw) unit 4 wrt avg | Inv 2 (630kw) unit 1 wrt avg | Inv 2 (630kw) unit 2 wrt avg | Inv 2 (630kw) unit 3 wrt avg | Inv 2 (630kw) unit 4 wrt avg | Inv 3 (630kw) unit 1 wrt avg | Inv 3 (630kw) unit 2 wrt avg | Inv 3 (630kw) unit 3 wrt avg | Inv 3 (630kw) unit 4 wrt avg | Inv 1 (630kw) unit 1 wrt max | Inv 1 (630kw) unit 2 wrt max | Inv 1 (630kw) unit 3 wrt max | Inv 1 (630kw) unit 4 wrt max | Inv 2 (630kw) unit 1 wrt max | Inv 2 (630kw) unit 2 wrt max | Inv 2 (630kw) unit 3 wrt max | Inv 2 (630kw) unit 4 wrt max | Inv 3 (630kw) unit 1 wrt max | Inv 3 (630kw) unit 2 wrt max | Inv 3 (630kw) unit 3 wrt max | Inv 3 (630kw) unit 4 wrt max | Inv1 wrt avg | Inv2 wrt avg | Inv3 wrt avg | Inv1 wrt avg2 | Inv2 wrt avg3 | Inv3 wrt avg4
2025 | 4 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | 2025-03-29 | 8.02 | -8.059% | -4.118% | -100% | -9.416% | 32.78% | 27.99% | 28.1% | -100% | 32.99% | 35.4% | 31.15% | 33.26% | -30.91% | -27.95% | -100% | -31.93% | -0.2174% | -3.82% | -3.736% | -100% | -0.05909% | 1.75% | -1.441% | 0.1418% | -30.45% | -2.619% | 33.07% | -47.74% | -26.82% | 0%
2025 | 4 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | 2025-03-30 | 8.02 | -5.282% | -5.16% | -100% | -2.933% | 31.64% | 27.13% | 27.16% | -100% | 34.79% | 33.93% | 29.93% | 28.86% | -28.1% | -28.01% | -100% | -26.32% | -0.07806% | -3.503% | -3.479% | -100% | 2.314% | 1.661% | -1.372% | -2.184% | -28.39% | -3.357% | 31.74% | -45.64% | -26.64% | 0%
2025 | 4 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | 2025-03-31 | 8.02 | -0.55% | -4.144% | -100% | -5.623% | 27.48% | 26.62% | 30.53% | -100% | 31.39% | 33.61% | 32.38% | 28.4% | -24.27% | -27% | -100% | -28.13% | -2.919% | -3.579% | -0.597% | -100% | 0.05522% | 1.748% | 0.8108% | -2.221% | -27.64% | -3.681% | 31.32% | -44.89% | -26.65% | 0%
2026 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-01 | 8.02 | -3.67% | 0.2237% | -100% | -5.081% | 31.09% | 26.31% | 26.46% | -100% | 31.2% | 33.42% | 29.23% | 30.93% | -26.5% | -23.53% | -100% | -27.58% | 0.01866% | -3.627% | -3.514% | -100% | 0.1024% | 1.799% | -1.401% | -0.1059% | -27.19% | -3.875% | 31.06% | -44.45% | -26.66% | 0%
2026 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-02 | 8.02 | -22.87% | -22.79% | -100% | -20.41% | 38.79% | 33.97% | 34.15% | -100% | 42.74% | 42.14% | 37.69% | 36.62% | -44.77% | -44.71% | -100% | -43.01% | -0.6154% | -4.065% | -3.936% | -100% | 2.212% | 1.785% | -1.406% | -2.171% | -41.55% | 1.9% | 39.65% | -58.15% | -27.03% | 0%
2026 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-03 | 8.02 | 3.596% | 3.104% | -100% | -3.944% | 23.06% | 32.76% | 22.35% | -100% | 26.55% | 44.05% | 24.92% | 24% | -20.11% | -20.49% | -100% | -25.93% | -5.103% | 2.378% | -5.65% | -100% | -2.414% | 11.08% | -3.669% | -4.38% | -24.38% | -5.298% | 29.68% | -41.69% | -26.97% | 0%
2026 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-04 | 8.02 | -29.85% | -28.27% | -100% | -30.16% | 55.27% | 57.3% | 54.4% | -100% | 33.47% | 32.34% | 28.2% | 27.23% | -46.11% | -44.9% | -100% | -46.35% | 19.28% | 20.85% | 18.62% | -100% | 2.531% | 1.668% | -1.517% | -2.261% | -47.11% | 16.94% | 30.17% | -59.37% | -10.16% | 0%
2026 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-05 | 8.02 | -38.55% | -38.43% | -100% | -36.81% | 58.97% | 57.82% | 60.63% | -100% | 34.26% | 38.82% | 32.13% | 31.07% | -54.11% | -54.02% | -100% | -52.81% | 18.71% | 17.85% | 19.94% | -100% | 0.2582% | 3.657% | -1.338% | -2.129% | -53.47% | 19.55% | 33.92% | -65.26% | -10.73% | 0%
2026 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-06 | 8.02 | -23.97% | -23.84% | -100% | -22.95% | 61.2% | 58.33% | 58.65% | -100% | 23.34% | 25.46% | 23.1% | 20.52% | -38.18% | -38.08% | -100% | -37.35% | 31.08% | 28.74% | 29.01% | -100% | 0.2922% | 2.019% | 0.09672% | -2.005% | -42.73% | 19.75% | 22.98% | -53.43% | -2.63% | 0%
2026 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-07 | 8.02 | 11.23% | 9.023% | -100% | 7.286% | 38.8% | 35.63% | 35.84% | -100% | 15.74% | 17.66% | 13.91% | 14.9% | -3.646% | -5.558% | -100% | -7.063% | 20.24% | 17.49% | 17.67% | -100% | 0.264% | 1.921% | -1.321% | -0.463% | -18.18% | 2.738% | 15.44% | -29.12% | -11% | 0%
2026 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-08 | 8.02 | 32.62% | 32.6% | -100% | 33.31% | 33.64% | 30.19% | 30.42% | -100% | 4.342% | 3.401% | 0.1721% | -0.6634% | 30.39% | 30.37% | -100% | 31.08% | 31.4% | 28.01% | 28.23% | -100% | 2.592% | 1.667% | -1.508% | -2.329% | -0.4335% | -1.272% | 1.706% | -2.103% | -2.928% | 0%
2026 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-09 | 8.02 | 31.93% | 34.9% | -100% | 30.1% | 26.08% | 28.3% | 25.53% | -100% | 5.769% | 10.08% | 4.175% | 3.297% | 24.8% | 27.61% | -100% | 23.08% | 19.27% | 21.37% | 18.75% | -100% | 0.05741% | 4.133% | -1.451% | -2.281% | -0.8435% | -4.865% | 5.708% | -6.198% | -10% | 0%
2026 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-10 | 8.02 | 33.48% | 33.5% | -100% | 34.13% | 30.51% | 29.75% | 32.84% | -100% | 1.264% | 3.058% | 2.46% | -0.9867% | 31.7% | 31.72% | -100% | 32.34% | 28.77% | 28.02% | 31.07% | -100% | -0.08475% | 1.685% | 1.095% | -2.306% | 0.2103% | -1.561% | 1.35% | -1.125% | -2.872% | 0%
2026 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-11 | 8.02 | 32.41% | 32.47% | -100% | 32.32% | 29.13% | 26.38% | 26.57% | -100% | 5.275% | 7.087% | 3.741% | 4.647% | 26.01% | 26.07% | -100% | 25.92% | 22.89% | 20.27% | 20.45% | -100% | 0.1831% | 1.907% | -1.277% | -0.4145% | -0.7645% | -4.318% | 5.083% | -5.564% | -8.946% | 0%
2026 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-12 | 8.02 | 34.8% | 36.36% | -100% | 32.9% | 21.21% | 22% | 20.59% | -100% | 8.266% | 11.48% | 6.688% | 5.869% | 24.86% | 26.31% | -100% | 23.1% | 12.27% | 13% | 11.7% | -100% | 0.2845% | 3.266% | -1.177% | -1.936% | 0.9412% | -8.9% | 7.959% | -6.5% | -15.62% | 0%
2026 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-13 | 8.02 | 35.38% | 35.46% | -100% | 35.4% | 23.06% | 20.28% | 20.46% | -100% | 7.508% | 9.439% | 5.999% | 7.102% | 26.05% | 26.12% | -100% | 26.06% | 14.58% | 11.99% | 12.16% | -100% | 0.0952% | 1.894% | -1.309% | -0.2826% | 1.491% | -8.896% | 7.405% | -5.507% | -15.18% | 0%
2026 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-14 | 8.02 | 34.71% | 32.37% | -100% | 30.21% | 25.97% | 27.63% | 25.35% | -100% | 8.43% | 7.711% | 4.293% | 3.434% | 27.26% | 25.05% | -100% | 23.01% | 19% | 20.57% | 18.42% | -100% | 2.433% | 1.753% | -1.476% | -2.287% | -0.7514% | -5.104% | 5.855% | -6.241% | -10.35% | 0%
2026 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-15 | 8.02 | 34.99% | 37.27% | -100% | 32.88% | 30.16% | 27% | 27.14% | -100% | 2.565% | 6.689% | 1.141% | 0.2891% | 31.63% | 33.85% | -100% | 29.57% | 26.92% | 23.84% | 23.98% | -100% | 0.01046% | 4.032% | -1.378% | -2.209% | 1.209% | -3.764% | 2.554% | -1.312% | -6.161% | 0%
2026 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-16 | 8.02 | 32.1% | 32.01% | -100% | 35.21% | 29.94% | 32.55% | 29.38% | -100% | 1.956% | 3.757% | 3.318% | -0.249% | 29.39% | 29.3% | -100% | 32.43% | 27.27% | 29.83% | 26.72% | -100% | -0.1376% | 1.626% | 1.197% | -2.298% | -0.227% | -1.87% | 2.097% | -2.276% | -3.885% | 0%
2026 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-17 | 8.02 | 32.72% | 32.73% | -100% | 32.89% | 31.29% | 30.52% | 33.14% | -100% | 1.585% | 3.427% | 0.2178% | 1.497% | 30.65% | 30.66% | -100% | 30.82% | 29.24% | 28.49% | 31.07% | -100% | 0.003522% | 1.817% | -1.343% | -0.08354% | -0.4833% | -1.098% | 1.582% | -2.033% | -2.638% | 0%
2026 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-18 | 8.02 | 32.23% | 35% | -100% | 31.42% | 34.87% | 30.55% | 30.79% | -100% | 3.459% | 2.634% | 0.2246% | -1.139% | 30.68% | 33.42% | -100% | 29.88% | 33.28% | 29.01% | 29.25% | -100% | 2.242% | 1.427% | -0.9547% | -2.303% | -0.4071% | -0.7835% | 1.191% | -1.579% | -1.951% | 0%
2026 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-19 | 8.02 | 33.65% | 33.61% | -100% | 34.05% | 30.78% | 34.27% | 30.18% | -100% | 0.5601% | 4.982% | -0.5628% | -1.451% | 32.63% | 32.59% | -100% | 33.03% | 29.79% | 33.24% | 29.18% | -100% | -0.2052% | 4.183% | -1.32% | -2.201% | 0.2621% | -1.029% | 0.7669% | -0.501% | -1.782% | 0%
2026 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-20 | 8.02 | 34.77% | 34.78% | -100% | 34.58% | 29.2% | 28.28% | 30.66% | -100% | 1.996% | 3.669% | 2.424% | -0.332% | 32.34% | 32.34% | -100% | 32.15% | 26.87% | 25.97% | 28.3% | -100% | 0.1546% | 1.797% | 0.5748% | -2.131% | 0.9645% | -2.803% | 1.839% | -0.8582% | -4.558% | 0%
2026 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-21 | 8.02 | 34.05% | 32.85% | -100% | 31.97% | 33.42% | 29.63% | 29.76% | -100% | 4.685% | 3.671% | 0.431% | -0.4012% | 31.43% | 30.26% | -100% | 29.4% | 30.82% | 27.1% | 27.23% | -100% | 2.643% | 1.649% | -1.527% | -2.343% | -0.3544% | -1.634% | 1.989% | -2.297% | -3.552% | 0%
2026 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-22 | 8.02 | 33.35% | 33.28% | -100% | 32.83% | 33.92% | 30.66% | 30.88% | -100% | 1.087% | 3.498% | 1.67% | -1.154% | 31.8% | 31.74% | -100% | 31.29% | 32.37% | 29.14% | 29.36% | -100% | -0.08481% | 2.299% | 0.4917% | -2.3% | -0.2021% | -0.9703% | 1.172% | -1.358% | -2.118% | 0%
2026 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-23 | 8.02 | 33.49% | 33.44% | -100% | 33.86% | 30.99% | 32.9% | 30.48% | -100% | 1.085% | 2.861% | 2.127% | -1.227% | 32.02% | 31.97% | -100% | 32.38% | 29.55% | 31.44% | 29.05% | -100% | -0.02719% | 1.729% | 1.003% | -2.314% | 0.1308% | -1.243% | 1.113% | -0.9711% | -2.33% | 0%
2026 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-24 | 8.02 | 36.14% | 33.61% | -100% | 31.43% | 30.89% | 30.14% | 33.01% | -100% | 1.185% | 2.885% | -0.305% | 1.05% | 34.65% | 32.15% | -100% | 30% | 29.46% | 28.72% | 31.55% | -100% | 0.08012% | 1.761% | -1.394% | -0.05366% | 0.2209% | -1.325% | 1.104% | -0.8739% | -2.403% | 0%
2026 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-25 | 8.02 | 34.02% | 33.39% | -100% | 33.88% | 33.75% | 30.3% | 30.71% | -100% | 3.403% | 2.313% | -0.1724% | -1.57% | 32.84% | 32.21% | -100% | 32.7% | 32.57% | 29.15% | 29.56% | -100% | 2.492% | 1.411% | -1.052% | -2.437% | 0.2549% | -1.144% | 0.8893% | -0.6288% | -2.015% | 0%
2026 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-26 | 8.02 | 35.46% | 33.64% | -100% | 31.42% | 31.47% | 30.66% | 32.78% | -100% | 1.153% | 2.965% | 1.544% | -1.045% | 34.04% | 32.25% | -100% | 30.05% | 30.1% | 29.3% | 31.39% | -100% | 0.09824% | 1.891% | 0.4846% | -2.077% | 0.05455% | -1.108% | 1.054% | -0.9888% | -2.14% | 0%
2026 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-27 | 8.02 | 32.76% | 36.5% | -100% | 31.77% | 34.08% | 30.51% | 29.47% | -100% | 1.484% | 2.004% | -0.8129% | 2.244% | 31.27% | 34.97% | -100% | 30.29% | 32.57% | 29.04% | 28.02% | -100% | 0.3447% | 0.8581% | -1.927% | 1.096% | 0.185% | -1.321% | 1.136% | -0.94% | -2.429% | 0%
2026 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-28 | 8.02 | 33.69% | 33.64% | -100% | 33.36% | 32.99% | 30.24% | 30.38% | -100% | 1.444% | 5.053% | 0.06423% | -0.79% | 31.94% | 31.89% | -100% | 31.61% | 31.24% | 28.53% | 28.66% | -100% | 0.1131% | 3.674% | -1.249% | -2.092% | 0.1057% | -1.435% | 1.33% | -1.208% | -2.729% | 0%
2026 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-29 | 8.02 | 37.12% | 34.72% | -100% | 32.61% | 28.9% | 28.15% | 30.64% | -100% | 1.946% | 3.478% | 2.754% | -0.2747% | 34.59% | 32.24% | -100% | 30.17% | 26.53% | 25.79% | 28.23% | -100% | 0.06807% | 1.571% | 0.8605% | -2.112% | 1.038% | -2.915% | 1.877% | -0.8232% | -4.704% | 0%
2026 | 4 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | 2025-04-30 | 8.02
2026 | 4 | 2025 | Year_2 | Year_2 | May-25 | 31 | 2025-05-01 | 8.02
2026 | 4 | 2025 | Year_2 | Year_2 | May-25 | 31 | 2025-05-02 | 8.02
2026 | 4 | 2025 | Year_2 | Year_2 | May-25 | 31 | 2025-05-03 | 8.02
2026 | 4 | 2025 | Year_2 | Year_2 | May-25 | 31 | 2025-05-04 | 8.02
2026 | 4 | 2025 | Year_2 | Year_2 | May-25 | 31 | 2025-05-05 | 8.02
2026 | 4 | 2025 | Year_2 | Year_2 | May-25 | 31 | 2025-05-06 | 8.02
2026 | 4 | 2025 | Year_2 | Year_2 | May-25 | 31 | 2025-05-07 | 8.02
2026 | 4 | 2025 | Year_2 | Year_2 | May-25 | 31 | 2025-05-08 | 8.02
2026 | 4 | 2025 | Year_2 | Year_2 | May-25 | 31 | 2025-05-09 | 8.02
2026 | 4 | 2025 | Year_2 | Year_2 | May-25 | 31 | 2025-05-10 | 8.02
Formulas:
Days = DAY(EOMONTH([Month Year],0))
Date = [Date, row above]+1

## Plant BD
Sr. No. | Finacial Year | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Date | Sunrise Time (POA>20 W/m2) | Sunset Time (POA<20 W/m2) | Total Generation Time | Affceted Equipment | DC Capacity Affceted (kW) | Plant Equivalent Weightage | Affected Equipmenet Location | Fault Catrgory | Fault Code (As per HMI) | Breakdown Description | Fault Time | Acknowledgemnet Time | Work Start time on Fault | Work Completiuon time on fualt | Acknowdlegemnet time | Response Time | Resolution Time | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Lost PoA(Wh/m2) | Approxuimate Energy Loss (KWh) | PTW No. | Job Card No.
1 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 2025-03-29 | 6:20 | 18:25 | 12.0833 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.26389 |  |  | 0.4125 | -6.3333 | -6.3333 | 3.5667 | 3.5667 | Waiting for inverter spares | open | 0.29775 | 0.94 | 449.1266
2 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 2025-03-29 | 6:20 | 18:25 | 12.0833 | Inv 2 (630kw) unit 4 | 658.8 | 8.214% | Inverter_2 | Kept off Due to unit-4 IGBT's to Block-1 . |  | Kept off Due to unit-4 IGBT's to Block-1 . | 0.26389 |  |  | 0.76736 | -6.3333 | -6.3333 | 12.0833 | 12.0833 | Waiting for inverter spares | open | 0.99247 | 5.53 | 2599.5859
3 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 2025-03-29 | 6:20 | 18:25 | 12.0833 | Inv1 | 2694.6 | 33.59% | Inverter_1 | PM High Fault |  | Inverter trip due to Pm high fault | 0.4125 |  |  | 0.41736 | -9.9 | -9.9 | 0.11667 | 0.11667 | Inverter restarted | close | 0.039194 | 0.08 | 153.8189
4 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 2025-03-29 | 6:20 | 18:25 | 12.0833 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.41736 |  |  | 0.42708 | -10.0167 | -10.0167 | 0.23333 | 0.23333 | Waiting for inverter spares | open | 0.019479 | 0.16 | 76.4471
5 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 2025-03-29 | 6:20 | 18:25 | 12.0833 | Inv1 | 2694.6 | 33.59% | Inverter_1 | PM High Fault |  | Inverter trip due to Pm high fault | 0.42708 |  |  | 0.43125 | -10.25 | -10.25 | 0.1 | 0.1 | Inverter restarted | close | 0.033595 | 0.08 | 153.8189
6 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 2025-03-29 | 6:20 | 18:25 | 12.0833 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.43125 |  |  | 0.52986 | -10.35 | -10.35 | 2.3667 | 2.3667 | Waiting for inverter spares | open | 0.19757 | 1.99 | 950.8105
7 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 2025-03-29 | 6:20 | 18:25 | 12.0833 | Inv 1 (630kw) unit 2 | 669.6 | 8.348% | Inverter_1 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | Unit-2 Kept off Due to Inverter Continous PM High Fault | 0.43125 |  |  | 0.52986 | -10.35 | -10.35 | 2.3667 | 2.3667 | Unit-2 Kept off Due to Inverter Continous PM High Fault | open | 0.19757 | 1.99 | 950.8105
8 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 2025-03-29 | 6:20 | 18:25 | 12.0833 | Inv1 | 2694.6 | 33.59% | Inverter_1 | PM High Fault |  | Inverter trip due to Pm high fault | 0.52986 |  |  | 0.53611 | -12.7167 | -12.7167 | 0.15 | 0.15 | Inverter restarted | close | 0.050392 | 0.14 | 269.1831
9 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 2025-03-29 | 6:20 | 18:25 | 12.0833 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.53611 |  |  | 0.5625 | -12.8667 | -12.8667 | 0.63333 | 0.63333 | Waiting for inverter spares | open | 0.052872 | 0.58 | 277.1207
10 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 2025-03-29 | 6:20 | 18:25 | 12.0833 | Inv 1 (630kw) unit 2 | 669.6 | 8.348% | Inverter_1 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | Unit-2 Kept off Due to Inverter Continous PM High Fault | 0.53611 |  |  | 0.5625 | -12.8667 | -12.8667 | 0.63333 | 0.63333 | Unit-2 Kept off Due to Inverter Continous PM High Fault | open | 0.052872 | 0.58 | 277.1207
11 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 2025-03-29 | 6:20 | 18:25 | 12.0833 | Inv1 | 2694.6 | 33.59% | Inverter_1 | PM High Fault |  | Inverter trip due to Pm high fault | 0.5625 |  |  | 0.56875 | -13.5 | -13.5 | 0.15 | 0.15 | Inverter restarted | close | 0.050392 | 0.14 | 269.1831
12 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 2025-03-29 | 6:20 | 18:25 | 12.0833 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.56875 |  |  | 0.63681 | -13.65 | -13.65 | 1.6333 | 1.6333 | Waiting for inverter spares | open | 0.13635 | 1.02 | 487.3501
13 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 2025-03-29 | 6:20 | 18:25 | 12.0833 | Inv 1 (630kw) unit 2 | 669.6 | 8.348% | Inverter_1 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | Unit-2 Kept off Due to Inverter Continous PM High Fault | 0.56875 |  |  | 0.63681 | -13.65 | -13.65 | 1.6333 | 1.6333 | Unit-2 Kept off Due to Inverter Continous PM High Fault | open | 0.13635 | 1.02 | 487.3501
14 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 2025-03-29 | 6:20 | 18:25 | 12.0833 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter Manually key stop to start the Unit-2 |  | Inverter Manually key stop to start the Unit-2 | 0.63681 |  |  | 0.6375 | -15.2833 | -15.2833 | 0.016667 | 0.016667 | Inverter restarted | close | 0.0055991 | 0.01 | 19.2274
15 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 2025-03-29 | 6:20 | 18:25 | 12.0833 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.6375 |  |  | 0.76736 | -15.3 | -15.3 | 3.1167 | 3.1167 | Waiting for inverter spares | open | 0.26019 | 0.45 | 215.0074
16 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 2025-03-30 | 6:20 | 18:26 | 12.1 | Inv 2 (630kw) unit 4 | 658.8 | 8.214% | Inverter_1 | Kept off Due to unit-4 IGBT's to Block-1 . |  | Kept off Due to unit-4 IGBT's to Block-1 . | 0.26389 |  |  | 0.76806 | -6.3333 | -6.3333 | 12.1 | 12.1 | Waiting for inverter spares | open | 0.99384 | 5.95 | 2797.0229
17 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 2025-03-30 | 6:20 | 18:26 | 12.1 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.26389 |  |  | 0.42986 | -6.3333 | -6.3333 | 3.9833 | 3.9833 | Waiting for inverter spares | open | 0.33254 | 1.2 | 573.3531
18 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 2025-03-30 | 6:20 | 18:26 | 12.1 | Inv1 | 2694.6 | 33.59% | Inverter_1 | PM High Fault |  | Inverter trip due to Pm high fault | 0.42986 |  |  | 0.43472 | -10.3167 | -10.3167 | 0.11667 | 0.11667 | Inverter restarted | close | 0.039194 | 0.09 | 173.0463
19 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 2025-03-30 | 6:20 | 18:26 | 12.1 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.43472 |  |  | 0.44167 | -10.4333 | -10.4333 | 0.16667 | 0.16667 | Waiting for inverter spares | open | 0.013914 | 0.12 | 57.3353
20 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 2025-03-30 | 6:20 | 18:26 | 12.1 | Inv 1 (630kw) unit 2 | 669.6 | 8.348% | Inverter_1 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | Unit-2 Kept off Due to Inverter Continous PM High Fault | 0.43472 |  |  | 0.44167 | -10.4333 | -10.4333 | 0.16667 | 0.16667 | Unit-2 Kept off Due to Inverter Continous PM High Fault | open | 0.013914 | 0.12 | 57.3353
21 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 2025-03-30 | 6:20 | 18:26 | 12.1 | Inv1 | 2694.6 | 33.59% | Inverter_1 | PM High Fault |  | Inverter trip due to Pm high fault | 0.44167 |  |  | 0.44722 | -10.6 | -10.6 | 0.13333 | 0.13333 | Inverter restarted | close | 0.044793 | 0.11 | 211.501
22 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 2025-03-30 | 6:20 | 18:26 | 12.1 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.44722 |  |  | 0.6875 | -10.7333 | -10.7333 | 5.7667 | 5.7667 | Waiting for inverter spares | open | 0.48141 | 4.24 | 2025.8475
23 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 2025-03-30 | 6:20 | 18:26 | 12.1 | Inv 1 (630kw) unit 2 | 669.6 | 8.348% | Inverter_1 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | Unit-2 Kept off Due to Inverter Continous PM High Fault | 0.44722 |  |  | 0.6875 | -10.7333 | -10.7333 | 5.7667 | 5.7667 | Unit-2 Kept off Due to Inverter Continous PM High Fault | open | 0.48141 | 4.24 | 2025.8475
24 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 2025-03-30 | 6:20 | 18:26 | 12.1 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter Manually key stop to start the Unit-2 |  | Inverter Manually key stop to start the Unit-2 | 0.6875 |  |  | 0.69028 | -16.5 | -16.5 | 0.066667 | 0.066667 | Inverter restarted | close | 0.022396 | 0.01 | 19.2274
25 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 2025-03-30 | 6:20 | 18:26 | 12.1 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.69028 |  |  | 0.76806 | -16.5667 | -16.5667 | 1.8667 | 1.8667 | Waiting for inverter spares | open | 0.15583 | 0.21 | 100.3368
26 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 2025-03-31 | 6:20 | 18:29 | 12.15 | Inv 2 (630kw) unit 4 | 658.8 | 8.214% | Inverter_1 | Kept off Due to unit-4 IGBT's to Block-1 . |  | Kept off Due to unit-4 IGBT's to Block-1 . | 0.26389 |  |  | 0.77014 | -6.3333 | -6.3333 | 12.15 | 12.15 | Waiting for inverter spares | open | 0.99795 | 5.99 | 2815.8264
27 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 2025-03-31 | 6:20 | 18:29 | 12.15 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.26389 |  |  | 0.43542 | -6.3333 | -6.3333 | 4.1167 | 4.1167 | Waiting for inverter spares | open | 0.34367 | 1.28 | 611.5766
28 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 2025-03-31 | 6:20 | 18:29 | 12.15 | Inv1 | 2694.6 | 33.59% | Inverter_1 | PM High Fault |  | Inverter trip due to Pm high fault | 0.43542 |  |  | 0.43889 | -10.45 | -10.45 | 0.083333 | 0.083333 | Inverter restarted | close | 0.027996 | 0.06 | 115.3642
29 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 2025-03-31 | 6:20 | 18:29 | 12.15 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.43889 |  |  | 0.44653 | -10.5333 | -10.5333 | 0.18333 | 0.18333 | Waiting for inverter spares | open | 0.015305 | 0.14 | 66.8912
30 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 2025-03-31 | 6:20 | 18:29 | 12.15 | Inv 1 (630kw) unit 2 | 669.6 | 8.348% | Inverter_1 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | Unit-2 Kept off Due to Inverter Continous PM High Fault | 0.43889 |  |  | 0.44653 | -10.5333 | -10.5333 | 0.18333 | 0.18333 | Unit-2 Kept off Due to Inverter Continous PM High Fault | open | 0.015305 | 0.14 | 66.8912
31 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 2025-03-31 | 6:20 | 18:29 | 12.15 | Inv1 | 2694.6 | 33.59% | Inverter_1 | PM High Fault |  | Inverter trip due to Pm high fault | 0.44653 |  |  | 0.45 | -10.7167 | -10.7167 | 0.083333 | 0.083333 | Inverter restarted | close | 0.027996 | 0.07 | 134.5916
32 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 2025-03-31 | 6:20 | 18:29 | 12.15 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.45 |  |  | 0.68403 | -10.8 | -10.8 | 5.6167 | 5.6167 | Waiting for inverter spares | open | 0.46889 | 4.16 | 1987.624
33 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 2025-03-31 | 6:20 | 18:29 | 12.15 | Inv 1 (630kw) unit 2 | 669.6 | 8.348% | Inverter_1 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | Unit-2 Kept off Due to Inverter Continous PM High Fault | 0.45 |  |  | 0.68403 | -10.8 | -10.8 | 5.6167 | 5.6167 | Unit-2 Kept off Due to Inverter Continous PM High Fault | open | 0.46889 | 4.16 | 1987.624
34 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 2025-03-31 | 6:20 | 18:29 | 12.15 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter Manually key stop to start the Unit-2 |  | Inverter Manually key stop to start the Unit-2 | 0.68403 |  |  | 0.68611 | -16.4167 | -16.4167 | 0.05 | 0.05 | Inverter restarted | close | 0.016797 | 0.02 | 38.4547
35 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 2025-03-31 | 6:20 | 18:29 | 12.15 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.68611 |  |  | 0.76389 | -16.4667 | -16.4667 | 1.8667 | 1.8667 | Waiting for inverter spares | open | 0.15583 | 0.29 | 138.5603
36 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-01 | 6:20 | 18:23 | 12.05 | Inv 2 (630kw) unit 4 | 658.8 | 8.214% | Inverter_1 | Kept off Due to unit-4 IGBT's to Block-1 . |  | Kept off Due to unit-4 IGBT's to Block-1 . | 0.26389 |  |  | 0.76597 | -6.3333 | -6.3333 | 12.05 | 12.05 | Waiting for inverter spares | open | 0.98973 | 6.04 | 2687.0208
37 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-01 | 6:20 | 18:23 | 12.05 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.26389 |  |  | 0.44028 | -6.3333 | -6.3333 | 4.2333 | 4.2333 | Waiting for inverter spares | open | 0.35341 | 1.41 | 637.5512
38 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-01 | 6:20 | 18:23 | 12.05 | Inv1 | 2694.6 | 33.59% | Inverter_1 | PM High Fault |  | Inverter trip due to Pm high fault | 0.44028 |  |  | 0.44583 | -10.5667 | -10.5667 | 0.13333 | 0.13333 | Inverter restarted | close | 0.044793 | 0.1 | 181.9595
39 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-01 | 6:20 | 18:23 | 12.05 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.44583 |  |  | 0.69306 | -10.7 | -10.7 | 5.9333 | 5.9333 | Waiting for inverter spares | open | 0.49533 | 4.33 | 1957.87
40 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-01 | 6:20 | 18:23 | 12.05 | Inv 1 (630kw) unit 2 | 669.6 | 8.348% | Inverter_1 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | Unit-2 Kept off Due to Inverter Continous PM High Fault | 0.44583 |  |  | 0.69306 | -10.7 | -10.7 | 5.9333 | 5.9333 | Unit-2 Kept off Due to Inverter Continous PM High Fault | open | 0.49533 | 4.33 | 1957.87
41 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-01 | 6:20 | 18:23 | 12.05 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter Manually key stop to start the Unit-2 |  | Inverter Manually key stop to start the Unit-2 | 0.69306 |  |  | 0.69444 | -16.6333 | -16.6333 | 0.033333 | 0.033333 | Inverter restarted | close | 0.011198 | 0.01 | 18.196
42 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-01 | 6:20 | 18:23 | 12.05 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.69444 |  |  | 0.76597 | -16.6667 | -16.6667 | 1.7167 | 1.7167 | Waiting for inverter spares | open | 0.14331 | 0.21 | 94.9544
43 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-02 | 6:19 | 18:33 | 12.2333 | Inv 2 (630kw) unit 4 | 658.8 | 8.214% | Inverter_2 | Kept off Due to unit-4 IGBT's to Block-1 . |  | Kept off Due to unit-4 IGBT's to Block-1 . | 0.26319 |  |  | 0.77292 | -6.3167 | -6.3167 | 12.2333 | 12.2333 | Waiting for inverter spares | open | 1.0048 | 6.71 | 2985.0844
44 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-02 | 6:19 | 18:33 | 12.2333 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.26319 |  |  | 0.40764 | -6.3167 | -6.3167 | 3.4667 | 3.4667 | Waiting for inverter spares | open | 0.2894 | 1.01 | 456.6856
45 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-02 | 6:19 | 18:33 | 12.2333 | Inv1 | 2694.6 | 33.59% | Inverter_1 | PM High Fault |  | Inverter trip due to Pm high fault | 0.40764 |  |  | 0.41389 | -9.7833 | -9.7833 | 0.15 | 0.15 | Inverter restarted | close | 0.050392 | 0.12 | 218.3514
46 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-02 | 6:19 | 18:33 | 12.2333 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.41389 |  |  | 0.42153 | -9.9333 | -9.9333 | 0.18333 | 0.18333 | Waiting for inverter spares | open | 0.015305 | 0.15 | 67.8246
47 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-02 | 6:19 | 18:33 | 12.2333 | Inv 1 (630kw) unit 2 | 669.6 | 8.348% | Inverter_1 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | Unit-2 Kept off Due to Inverter Continous PM High Fault | 0.41389 |  |  | 0.42153 | -9.9333 | -9.9333 | 0.18333 | 0.18333 | Waiting for inverter spares | open | 0.015305 | 0.15 | 67.8246
48 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-02 | 6:19 | 18:33 | 12.2333 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.42153 |  |  | 0.4875 | -10.1167 | -10.1167 | 1.5833 | 1.5833 | Waiting for inverter spares | open | 0.13218 | 1.45 | 655.6378
49 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-02 | 6:19 | 18:33 | 12.2333 | Inv 1 (630kw) unit 2 | 669.6 | 8.348% | Inverter_1 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | Unit-2 Kept off Due to Inverter Continous PM High Fault | 0.42153 |  |  | 0.4875 | -10.1167 | -10.1167 | 1.5833 | 1.5833 | Waiting for inverter spares | open | 0.13218 | 1.45 | 655.6378
50 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-02 | 6:19 | 18:33 | 12.2333 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Pm high fault |  | Inverter trip due to Pm high fault | 0.4875 |  |  | 0.49306 | -11.7 | -11.7 | 0.13333 | 0.13333 | Inverter restarted | close | 0.044793 | 0.18 | 327.5272
51 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-02 | 6:19 | 18:33 | 12.2333 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.49306 |  |  | 0.50833 | -11.8333 | -11.8333 | 0.36667 | 0.36667 | Waiting for inverter spares | open | 0.03061 | 0.39 | 176.3439
52 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-02 | 6:19 | 18:33 | 12.2333 | Inv 1 (630kw) unit 2 | 669.6 | 8.348% | Inverter_1 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | Unit-2 Kept off Due to Inverter Continous PM High Fault | 0.49306 |  |  | 0.50833 | -11.8333 | -11.8333 | 0.36667 | 0.36667 | Waiting for inverter spares | open | 0.03061 | 0.39 | 176.3439
53 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-02 | 6:19 | 18:33 | 12.2333 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Pm high fault |  | Inverter trip due to Pm high fault | 0.50833 |  |  | 0.51319 | -12.2 | -12.2 | 0.11667 | 0.11667 | Inverter restarted | close | 0.039194 | 0.13 | 236.5474
54 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-02 | 6:19 | 18:33 | 12.2333 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.51319 |  |  | 0.53056 | -12.3167 | -12.3167 | 0.41667 | 0.41667 | Waiting for inverter spares | open | 0.034784 | 0.42 | 189.9089
55 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-02 | 6:19 | 18:33 | 12.2333 | Inv 1 (630kw) unit 2 | 669.6 | 8.348% | Inverter_1 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | Unit-2 Kept off Due to Inverter Continous PM High Fault | 0.51319 |  |  | 0.53056 | -12.3167 | -12.3167 | 0.41667 | 0.41667 | Waiting for inverter spares | open | 0.034784 | 0.42 | 189.9089
56 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-02 | 6:19 | 18:33 | 12.2333 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Pm high fault |  | Inverter trip due to Pm high fault | 0.53056 |  |  | 0.53611 | -12.7333 | -12.7333 | 0.13333 | 0.13333 | Inverter restarted | close | 0.044793 | 0.14 | 254.7433
57 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-02 | 6:19 | 18:33 | 12.2333 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.53611 |  |  | 0.54583 | -12.8667 | -12.8667 | 0.23333 | 0.23333 | Waiting for inverter spares | open | 0.019479 | 0.29 | 131.1276
58 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-02 | 6:19 | 18:33 | 12.2333 | Inv 1 (630kw) unit 2 | 669.6 | 8.348% | Inverter_1 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | Unit-2 Kept off Due to Inverter Continous PM High Fault | 0.53611 |  |  | 0.54583 | -12.8667 | -12.8667 | 0.23333 | 0.23333 | Waiting for inverter spares | open | 0.019479 | 0.29 | 131.1276
59 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-02 | 6:19 | 18:33 | 12.2333 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Pm high fault |  | Inverter trip due to Pm high fault | 0.54583 |  |  | 0.60347 | -13.1 | -13.1 | 1.3833 | 1.3833 | Inverter restarted | close | 0.46473 | 1.18 | 2147.1225
60 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-02 | 6:19 | 18:33 | 12.2333 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.60347 |  |  | 0.69444 | -14.4833 | -14.4833 | 2.1833 | 2.1833 | Waiting for inverter spares | open | 0.18227 | 1.24 | 560.6833
61 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-02 | 6:19 | 18:33 | 12.2333 | Inv 1 (630kw) unit 2 | 669.6 | 8.348% | Inverter_1 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | Unit-2 Kept off Due to Inverter Continous PM High Fault | 0.60347 |  |  | 0.69444 | -14.4833 | -14.4833 | 2.1833 | 2.1833 | Waiting for inverter spares | open | 0.18227 | 1.24 | 560.6833
62 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-02 | 6:19 | 18:33 | 12.2333 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter Manually key stop to start the Unit-2 |  | Inverter Manually key stop to start the Unit-2 | 0.69444 |  |  | 0.69653 | -16.6667 | -16.6667 | 0.05 | 0.05 | Inverter restarted | close | 0.016797 | 0.02 | 36.3919
63 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-02 | 6:19 | 18:33 | 12.2333 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.69653 |  |  | 0.77292 | -16.7167 | -16.7167 | 1.8333 | 1.8333 | Waiting for inverter spares | open | 0.15305 | 0.17 | 76.8679
64 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-03 | 6:19 | 17:46 | 11.45 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.26319 |  |  | 0.44792 | -6.3167 | -6.3167 | 4.4333 | 4.4333 | Waiting for inverter spares | open | 0.3701 | 1.29 | 583.2915
65 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-03 | 6:19 | 17:46 | 11.45 | Inv 2 (630kw) unit 4 | 658.8 | 8.214% | Inverter_2 | Kept off Due to unit-4 IGBT's to Block-1 . |  | Kept off Due to unit-4 IGBT's to Block-1 . | 0.26319 |  |  | 0.57153 | -6.3167 | -6.3167 | 7.4 | 7.4 | Waiting for inverter spares | open | 0.6078 | 3.1 | 1379.1001
66 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-03 | 6:19 | 17:46 | 11.45 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Pm high fault |  | Inverter trip due to Pm high fault | 0.44792 |  |  | 0.45278 | -10.75 | -10.75 | 0.11667 | 0.11667 | Inverter restarted | close | 0.039194 | 0.14 | 254.7433
67 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-03 | 6:19 | 17:46 | 11.45 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.45278 |  |  | 0.57153 | -10.8667 | -10.8667 | 2.85 | 2.85 | Waiting for inverter spares | open | 0.23792 | 1.72 | 777.722
68 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-03 | 6:19 | 17:46 | 11.45 | Inv 1 (630kw) unit 2 | 669.6 | 8.348% | Inverter_1 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | Unit-2 Kept off Due to Inverter Continous PM High Fault | 0.45278 |  |  | 0.57153 | -10.8667 | -10.8667 | 2.85 | 2.85 | Unit-2 Kept off Due to Inverter Continous PM High Fault | open | 0.23792 | 1.72 | 777.722
69 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-03 | 6:19 | 17:46 | 11.45 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.69653 |  |  | 0.74028 | -16.7167 | -16.7167 | 1.05 | 1.05 | Waiting for inverter spares | open | 0.087656 | 0.03 | 13.5649
70 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-03 | 6:19 | 17:46 | 11.45 | Inv 1 (630kw) unit 2 | 669.6 | 8.348% | Inverter_1 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | Unit-2 Kept off Due to Inverter Continous PM High Fault | 0.69653 |  |  | 0.74028 | -16.7167 | -16.7167 | 1.05 | 1.05 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | 0.087656 | 0.03 | 13.5649
71 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-03 | 6:19 | 17:46 | 11.45 | Inv 2 (630kw) unit 4 | 658.8 | 8.214% | Inverter_2 | Kept off Due to unit-4 IGBT's to Block-1 . |  | Kept off Due to unit-4 IGBT's to Block-1 . | 0.69653 |  |  | 0.74028 | -16.7167 | -16.7167 | 1.05 | 1.05 | Waiting for inverter spares | open | 0.086242 | 0.03 | 13.3461
72 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-04 | 6:09 | 18:30 | 12.35 | Inv 2 (630kw) unit 4 | 658.8 | 8.214% | Inverter_2 | Kept off Due to unit-4 IGBT's to Block-1 . |  | Kept off Due to unit-4 IGBT's to Block-1 . | 0.25625 |  |  | 0.77083 | -6.15 | -6.15 | 12.35 | 12.35 | Waiting for inverter spares | open | 1.0144 | 6.83 | 3038.4689
73 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-04 | 6:09 | 18:30 | 12.35 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Pm high fault |  | Inverter trip due to Pm high fault | 0.38125 |  |  | 0.38403 | -9.15 | -9.15 | 0.066667 | 0.066667 | Inverter restarted | close | 0.022396 | 0.04 | 72.7838
74 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-04 | 6:09 | 18:30 | 12.35 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.38403 |  |  | 0.41667 | -9.2167 | -9.2167 | 0.78333 | 0.78333 | Waiting for inverter spares | open | 0.065394 | 0.55 | 248.6902
75 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-04 | 6:09 | 18:30 | 12.35 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Pm high fault |  | Inverter trip due to Pm high fault | 0.41667 |  |  | 0.42361 | -10 | -10 | 0.16667 | 0.16667 | Waiting for inverter spares | open | 0.055991 | 0.14 | 254.7433
76 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-04 | 6:09 | 18:30 | 12.35 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.42361 |  |  | 0.43403 | -10.1667 | -10.1667 | 0.25 | 0.25 | Waiting for inverter spares | open | 0.02087 | 0.22 | 99.4761
77 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-04 | 6:09 | 18:30 | 12.35 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Pm high fault |  | Inverter trip due to Pm high fault | 0.43403 |  |  | 0.4375 | -10.4167 | -10.4167 | 0.083333 | 0.083333 | Inverter restarted | close | 0.027996 | 0.08 | 145.5676
78 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-04 | 6:09 | 18:30 | 12.35 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.4375 |  |  | 0.44444 | -10.5 | -10.5 | 0.16667 | 0.16667 | Waiting for inverter spares | open | 0.013914 | 0.14 | 63.303
79 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-04 | 6:09 | 18:30 | 12.35 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Pm high fault |  | Inverter trip due to Pm high fault | 0.44444 |  |  | 0.44653 | -10.6667 | -10.6667 | 0.05 | 0.05 | Inverter restarted | close | 0.016797 | 0.05 | 90.9798
80 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-04 | 6:09 | 18:30 | 12.35 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Pm high fault |  | Inverter trip due to Pm high fault | 0.44722 |  |  | 0.46528 | -10.7333 | -10.7333 | 0.43333 | 0.43333 | Inverter restarted | close | 0.14558 | 0.43 | 782.426
81 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-04 | 6:09 | 18:30 | 12.35 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.46528 |  |  | 0.46875 | -11.1667 | -11.1667 | 0.083333 | 0.083333 | Waiting for inverter spares | open | 0.0069568 | 0.09 | 40.6948
82 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-04 | 6:09 | 18:30 | 12.35 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Pm high fault |  | Inverter trip due to Pm high fault | 0.46875 |  |  | 0.5 | -11.25 | -11.25 | 0.75 | 0.75 | Inverter restarted | close | 0.25196 | 0.73 | 1328.3046
83 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-04 | 6:09 | 18:30 | 12.35 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.5 |  |  | 0.50278 | -12 | -12 | 0.066667 | 0.066667 | Waiting for inverter spares | open | 0.0055655 | 0.08 | 36.1731
84 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-04 | 6:09 | 18:30 | 12.35 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Pm high fault |  | Inverter trip due to Pm high fault | 0.50278 |  |  | 0.55139 | -12.0667 | -12.0667 | 1.1667 | 1.1667 | Inverter restarted | close | 0.39194 | 1.11 | 2019.7508
85 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-04 | 6:09 | 18:30 | 12.35 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.55139 |  |  | 0.57292 | -13.2333 | -13.2333 | 0.51667 | 0.51667 | Waiting for inverter spares | open | 0.043132 | 0.44 | 198.9521
86 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-04 | 6:09 | 18:30 | 12.35 | Inv 1 (630kw) unit 2 | 669.6 | 8.348% | Inverter_1 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | Unit-2 Kept off Due to Inverter Continous PM High Fault | 0.55139 |  |  | 0.57292 | -13.2333 | -13.2333 | 0.51667 | 0.51667 | Waiting for inverter spares | open | 0.043132 | 0.44 | 198.9521
87 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-04 | 6:09 | 18:30 | 12.35 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Pm high fault |  | Inverter trip due to Pm high fault | 0.57292 |  |  | 0.57708 | -13.75 | -13.75 | 0.1 | 0.1 | Inverter restarted | close | 0.033595 | 0.12 | 218.3514
88 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-04 | 6:09 | 18:30 | 12.35 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.57708 |  |  | 0.60278 | -13.85 | -13.85 | 0.61667 | 0.61667 | Waiting for inverter spares | open | 0.051481 | 0.53 | 239.6469
89 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-04 | 6:09 | 18:30 | 12.35 | Inv 1 (630kw) unit 2 | 669.6 | 8.348% | Inverter_1 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | Unit-2 Kept off Due to Inverter Continous PM High Fault | 0.57708 |  |  | 0.60278 | -13.85 | -13.85 | 0.61667 | 0.61667 | Waiting for inverter spares | open | 0.051481 | 0.53 | 239.6469
90 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-04 | 6:09 | 18:30 | 12.35 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Pm high fault |  | Inverter trip due to Pm high fault | 0.60278 |  |  | 0.60625 | -14.4667 | -14.4667 | 0.083333 | 0.083333 | Inverter restarted | close | 0.027996 | 0.09 | 163.7636
91 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-04 | 6:09 | 18:30 | 12.35 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.60625 |  |  | 0.68125 | -14.55 | -14.55 | 1.8 | 1.8 | Waiting for inverter spares | open | 0.15027 | 1.02 | 461.2072
92 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-04 | 6:09 | 18:30 | 12.35 | Inv 1 (630kw) unit 2 | 669.6 | 8.348% | Inverter_1 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | Unit-2 Kept off Due to Inverter Continous PM High Fault | 0.60625 |  |  | 0.68125 | -14.55 | -14.55 | 1.8 | 1.8 | Waiting for inverter spares | open | 0.15027 | 1.02 | 461.2072
93 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-04 | 6:09 | 18:30 | 12.35 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter Manually key stop to start the Unit-2 |  | Inverter Manually key stop to start the Unit-2 | 0.68125 |  |  | 0.68264 | -16.35 | -16.35 | 0.033333 | 0.033333 | Inverter restarted | close | 0.011198 | 0.02 | 36.3919
94 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-04 | 6:09 | 18:30 | 12.35 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.68264 |  |  | 0.77083 | -16.3833 | -16.3833 | 2.1167 | 2.1167 | Waiting for inverter spares | open | 0.1767 | 0.45 | 203.4738
95 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.25833 |  |  | 0.40208 | -6.2 | -6.2 | 3.45 | 3.45 | Waiting for inverter spares | open | 0.28801 | 0.97 | 438.599
96 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv 2 (630kw) unit 4 | 658.8 | 8.214% | Inverter_2 | Kept off Due to unit-4 IGBT's to Block-1 . |  | Kept off Due to unit-4 IGBT's to Block-1 . | 0.25833 |  |  | 0.55069 | -6.2 | -6.2 | 7.0167 | 7.0167 | Waiting for inverter spares | open | 0.57632 | 4.13 | 1837.3172
97 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Pm high fault |  | Inverter trip due to Pm high fault | 0.40208 |  |  | 0.40764 | -9.65 | -9.65 | 0.13333 | 0.13333 | Inverter restarted | close | 0.044793 | 0.1 | 181.9595
98 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.40764 |  |  | 0.4125 | -9.7833 | -9.7833 | 0.11667 | 0.11667 | Waiting for inverter spares | open | 0.0097396 | 0.09 | 40.6948
99 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Pm high fault |  | Inverter trip due to Pm high fault | 0.4125 |  |  | 0.41806 | -9.9 | -9.9 | 0.13333 | 0.13333 | Inverter restarted | close | 0.044793 | 0.1 | 181.9595
100 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.41806 |  |  | 0.42292 | -10.0333 | -10.0333 | 0.11667 | 0.11667 | Waiting for inverter spares | open | 0.0097396 | 0.09 | 40.6948
101 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Pm high fault |  | Inverter trip due to Pm high fault | 0.42292 |  |  | 0.42917 | -10.15 | -10.15 | 0.15 | 0.15 | Inverter restarted | close | 0.050392 | 0.12 | 218.3514
102 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.42917 |  |  | 0.4625 | -10.3 | -10.3 | 0.8 | 0.8 | Waiting for inverter spares | open | 0.066786 | 0.68 | 307.4715
103 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv 1 (630kw) unit 2 | 669.6 | 8.348% | Inverter_1 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | Unit-2 Kept off Due to Inverter Continous PM High Fault | 0.42917 |  |  | 0.4625 | -10.3 | -10.3 | 0.8 | 0.8 | Waiting for inverter spares | open | 0.066786 | 0.68 | 307.4715
104 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Pm high fault |  | Inverter trip due to Pm high fault | 0.4625 |  |  | 0.46875 | -11.1 | -11.1 | 0.15 | 0.15 | Inverter restarted | close | 0.050392 | 0.13 | 236.5474
105 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.46875 |  |  | 0.48819 | -11.25 | -11.25 | 0.46667 | 0.46667 | Waiting for inverter spares | open | 0.038958 | 0.44 | 198.9521
106 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv 1 (630kw) unit 2 | 669.6 | 8.348% | Inverter_1 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | Unit-2 Kept off Due to Inverter Continous PM High Fault | 0.46875 |  |  | 0.48819 | -11.25 | -11.25 | 0.46667 | 0.46667 | Waiting for inverter spares | open | 0.038958 | 0.44 | 198.9521
107 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Pm high fault |  | Inverter trip due to Pm high fault | 0.48819 |  |  | 0.50903 | -11.7167 | -11.7167 | 0.5 | 0.5 | Inverter restarted | close | 0.16797 | 0.49 | 891.6017
108 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.50903 |  |  | 0.51597 | -12.2167 | -12.2167 | 0.16667 | 0.16667 | Waiting for inverter spares | open | 0.013914 | 0.17 | 76.8679
109 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv 1 (630kw) unit 2 | 669.6 | 8.348% | Inverter_1 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | Unit-2 Kept off Due to Inverter Continous PM High Fault | 0.50903 |  |  | 0.51597 | -12.2167 | -12.2167 | 0.16667 | 0.16667 | Waiting for inverter spares | open | 0.013914 | 0.17 | 76.8679
110 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Pm high fault |  | Inverter trip due to Pm high fault | 0.51597 |  |  | 0.52431 | -12.3833 | -12.3833 | 0.2 | 0.2 | Inverter restarted | close | 0.067189 | 0.21 | 382.115
111 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.52431 |  |  | 0.52917 | -12.5833 | -12.5833 | 0.11667 | 0.11667 | Waiting for inverter spares | open | 0.0097396 | 0.13 | 58.7813
112 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv 1 (630kw) unit 2 | 669.6 | 8.348% | Inverter_1 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | Unit-2 Kept off Due to Inverter Continous PM High Fault | 0.52431 |  |  | 0.52917 | -12.5833 | -12.5833 | 0.11667 | 0.11667 | Waiting for inverter spares | open | 0.0097396 | 0.13 | 58.7813
113 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Pm high fault |  | Inverter trip due to Pm high fault | 0.52917 |  |  | 0.53472 | -12.7 | -12.7 | 0.13333 | 0.13333 | Inverter restarted | close | 0.044793 | 0.14 | 254.7433
114 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.53472 |  |  | 0.53819 | -12.8333 | -12.8333 | 0.083333 | 0.083333 | Waiting for inverter spares | open | 0.0069568 | 0.09 | 40.6948
115 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv 1 (630kw) unit 2 | 669.6 | 8.348% | Inverter_1 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | Unit-2 Kept off Due to Inverter Continous PM High Fault | 0.53472 |  |  | 0.53819 | -12.8333 | -12.8333 | 0.083333 | 0.083333 | Waiting for inverter spares | open | 0.0069568 | 0.09 | 40.6948
116 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Pm high fault |  | Inverter trip due to Pm high fault | 0.53819 |  |  | 0.54583 | -12.9167 | -12.9167 | 0.18333 | 0.18333 | Inverter restarted | close | 0.06159 | 0.19 | 345.7231
117 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.54583 |  |  | 0.55139 | -13.1 | -13.1 | 0.13333 | 0.13333 | Waiting for inverter spares | open | 0.011131 | 0.14 | 63.303
118 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv 1 (630kw) unit 2 | 669.6 | 8.348% | Inverter_1 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | Unit-2 Kept off Due to Inverter Continous PM High Fault | 0.54583 |  |  | 0.55139 | -13.1 | -13.1 | 0.13333 | 0.13333 | Waiting for inverter spares | open | 0.011131 | 0.14 | 63.303
119 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Pm high fault |  | Inverter trip due to Pm high fault | 0.55139 |  |  | 0.55694 | -13.2333 | -13.2333 | 0.13333 | 0.13333 | Inverter restarted | close | 0.044793 | 0.14 | 254.7433
120 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv2 | 2630.8 | 32.8% | Inverter_2 | Inverter trip due to Over temperature |  | Inverter trip due to Over temperature | 0.55208 |  |  | 0.57708 | -13.25 | -13.25 | 0.6 | 0.6 | Inverter restarted | close | 0.1968 | 0.59 | 1048.1425
121 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv 2 (630kw) unit 4 | 658.8 | 8.214% | Inverter_2 | Kept off Due to unit-4 IGBT's to Block-1 . |  | Kept off Due to unit-4 IGBT's to Block-1 . | 0.57708 |  |  | 0.76875 | -13.85 | -13.85 | 4.6 | 4.6 | Waiting for inverter spares | open | 0.37782 | 2.23 | 992.0623
122 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.55694 |  |  | 0.56042 | -13.3667 | -13.3667 | 0.083333 | 0.083333 | Waiting for inverter spares | open | 0.0069568 | 0.09 | 40.6948
123 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv 1 (630kw) unit 2 | 669.6 | 8.348% | Inverter_1 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | Unit-2 Kept off Due to Inverter Continous PM High Fault | 0.55694 |  |  | 0.56042 | -13.3667 | -13.3667 | 0.083333 | 0.083333 | Waiting for inverter spares | open | 0.0069568 | 0.09 | 40.6948
124 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Pm high fault |  | Inverter trip due to Pm high fault | 0.56042 |  |  | 0.58264 | -13.45 | -13.45 | 0.53333 | 0.53333 | Inverter restarted | close | 0.17917 | 0.51 | 927.9936
125 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.58264 |  |  | 0.59097 | -13.9833 | -13.9833 | 0.2 | 0.2 | Waiting for inverter spares | open | 0.016696 | 0.19 | 85.9112
126 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv 1 (630kw) unit 2 | 669.6 | 8.348% | Inverter_1 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | Unit-2 Kept off Due to Inverter Continous PM High Fault | 0.58264 |  |  | 0.59097 | -13.9833 | -13.9833 | 0.2 | 0.2 | Waiting for inverter spares | open | 0.016696 | 0.19 | 85.9112
127 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Pm high fault |  | Inverter trip due to Pm high fault | 0.59097 |  |  | 0.59861 | -14.1833 | -14.1833 | 0.18333 | 0.18333 | Inverter restarted | close | 0.06159 | 0.17 | 309.3312
128 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.59861 |  |  | 0.60278 | -14.3667 | -14.3667 | 0.1 | 0.1 | Waiting for inverter spares | open | 0.0083482 | 0.1 | 45.2164
129 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv 1 (630kw) unit 2 | 669.6 | 8.348% | Inverter_1 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | Unit-2 Kept off Due to Inverter Continous PM High Fault | 0.59861 |  |  | 0.60278 | -14.3667 | -14.3667 | 0.1 | 0.1 | Waiting for inverter spares | open | 0.0083482 | 0.1 | 45.2164
130 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Pm high fault |  | Inverter trip due to Pm high fault | 0.60278 |  |  | 0.60833 | -14.4667 | -14.4667 | 0.13333 | 0.13333 | Inverter restarted | close | 0.044793 | 0.12 | 218.3514
131 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.60833 |  |  | 0.61458 | -14.6 | -14.6 | 0.15 | 0.15 | Waiting for inverter spares | open | 0.012522 | 0.13 | 58.7813
132 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv 1 (630kw) unit 2 | 669.6 | 8.348% | Inverter_1 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | Unit-2 Kept off Due to Inverter Continous PM High Fault | 0.60833 |  |  | 0.61458 | -14.6 | -14.6 | 0.15 | 0.15 | Waiting for inverter spares | open | 0.012522 | 0.13 | 58.7813
133 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Pm high fault |  | Inverter trip due to Pm high fault | 0.61458 |  |  | 0.62222 | -14.75 | -14.75 | 0.18333 | 0.18333 | Inverter restarted | close | 0.06159 | 0.16 | 291.1353
134 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.62222 |  |  | 0.62986 | -14.9333 | -14.9333 | 0.18333 | 0.18333 | Waiting for inverter spares | open | 0.015305 | 0.15 | 67.8246
135 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv 1 (630kw) unit 2 | 669.6 | 8.348% | Inverter_1 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | Unit-2 Kept off Due to Inverter Continous PM High Fault | 0.62222 |  |  | 0.62986 | -14.9333 | -14.9333 | 0.18333 | 0.18333 | Waiting for inverter spares | open | 0.015305 | 0.15 | 67.8246
136 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Pm high fault |  | Inverter trip due to Pm high fault | 0.62986 |  |  | 0.63542 | -15.1167 | -15.1167 | 0.13333 | 0.13333 | Inverter restarted | close | 0.044793 | 0.11 | 200.1555
137 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.63542 |  |  | 0.64444 | -15.25 | -15.25 | 0.21667 | 0.21667 | Waiting for inverter spares | open | 0.018088 | 0.16 | 72.3462
138 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv 1 (630kw) unit 2 | 669.6 | 8.348% | Inverter_1 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | Unit-2 Kept off Due to Inverter Continous PM High Fault | 0.63542 |  |  | 0.64444 | -15.25 | -15.25 | 0.21667 | 0.21667 | Waiting for inverter spares | open | 0.018088 | 0.16 | 72.3462
139 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Pm high fault |  | Inverter trip due to Pm high fault | 0.64444 |  |  | 0.66042 | -15.4667 | -15.4667 | 0.38333 | 0.38333 | Inverter restarted | close | 0.12878 | 0.244 | 443.9813
140 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.66042 |  |  | 0.70278 | -15.85 | -15.85 | 1.0167 | 1.0167 | Waiting for inverter spares | open | 0.084873 | 0.46 | 207.9954
141 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv 1 (630kw) unit 2 | 669.6 | 8.348% | Inverter_1 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | Unit-2 Kept off Due to Inverter Continous PM High Fault | 0.66042 |  |  | 0.70278 | -15.85 | -15.85 | 1.0167 | 1.0167 | Waiting for inverter spares | open | 0.084873 | 0.46 | 207.9954
142 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter Manually key stop to start the Unit-2 |  | Inverter Manually key stop to start the Unit-2 | 0.70278 |  |  | 0.70417 | -16.8667 | -16.8667 | 0.033333 | 0.033333 | Inverter restarted | close | 0.011198 | 0.01 | 18.196
143 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.70417 |  |  | 0.72917 | -16.9 | -16.9 | 0.6 | 0.6 | Waiting for inverter spares | open | 0.050089 | 0.14 | 63.303
144 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 6:12 | 18:27 | 12.25 | Inv1 | 2694.6 | 33.59% | Inverter_1 | shutdown taken for IGBT Interchange purpose |  | shutdown taken for IGBT Interchange purpose | 0.72917 |  |  | 0.76875 | -17.5 | -17.5 | 0.95 | 0.95 | Inverter restarted | close | 0.31915 | 0.05 | 90.9798
145 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-06 | 6:16 | 18:28 | 12.2 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.26111 |  |  | 0.42361 | -6.2667 | -6.2667 | 3.9 | 3.9 | Waiting for inverter spares | open | 0.32558 | 1.34 | 605.8997
146 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-06 | 6:16 | 18:28 | 12.2 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Pm high fault |  | Inverter trip due to Pm high fault | 0.42361 |  |  | 0.42917 | -10.1667 | -10.1667 | 0.13333 | 0.13333 | Inverter restarted | close | 0.044793 | 0.11 | 200.1555
147 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-06 | 6:16 | 18:28 | 12.2 | Inv 2 (630kw) unit 4 | 658.8 | 8.214% | Inverter_2 | Kept off Due to unit-4 IGBT's to Block-1 . |  | Kept off Due to unit-4 IGBT's to Block-1 . | 0.26111 |  |  | 0.76944 | -6.2667 | -6.2667 | 12.2 | 12.2 | Waiting for inverter spares | open | 1.0021 | 6.77 | 3011.7767
148 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-06 | 6:16 | 18:28 | 12.2 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.42917 |  |  | 0.43333 | -10.3 | -10.3 | 0.1 | 0.1 | Waiting for inverter spares | open | 0.0083482 | 0.09 | 40.6948
149 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-06 | 6:16 | 18:28 | 12.2 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Pm high fault |  | Inverter trip due to Pm high fault | 0.43333 |  |  | 0.4375 | -10.4 | -10.4 | 0.1 | 0.1 | Inverter restarted | close | 0.033595 | 0.09 | 163.7636
150 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-06 | 6:16 | 18:28 | 12.2 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.4375 |  |  | 0.46736 | -10.5 | -10.5 | 0.71667 | 0.71667 | Waiting for inverter spares | open | 0.059829 | 0.63 | 284.8633
151 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-06 | 6:16 | 18:28 | 12.2 | Inv 1 (630kw) unit 2 | 669.6 | 8.348% | Inverter_1 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | Unit-2 Kept off Due to Inverter Continous PM High Fault | 0.4375 |  |  | 0.46736 | -10.5 | -10.5 | 0.71667 | 0.71667 | Waiting for inverter spares | open | 0.059829 | 0.63 | 284.8633
152 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-06 | 6:16 | 18:28 | 12.2 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Pm high fault |  | Inverter trip due to Pm high fault | 0.46736 |  |  | 0.47222 | -11.2167 | -11.2167 | 0.11667 | 0.11667 | Inverter restarted | close | 0.039194 | 0.12 | 218.3514
153 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-06 | 6:16 | 18:28 | 12.2 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.47222 |  |  | 0.48611 | -11.3333 | -11.3333 | 0.33333 | 0.33333 | Waiting for inverter spares | open | 0.027827 | 0.33 | 149.2141
154 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-06 | 6:16 | 18:28 | 12.2 | Inv 1 (630kw) unit 2 | 669.6 | 8.348% | Inverter_1 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | Unit-2 Kept off Due to Inverter Continous PM High Fault | 0.47222 |  |  | 0.48611 | -11.3333 | -11.3333 | 0.33333 | 0.33333 | Waiting for inverter spares | open | 0.027827 | 0.33 | 149.2141
155 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-06 | 6:16 | 18:28 | 12.2 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Pm high fault |  | Inverter trip due to Pm high fault | 0.48611 |  |  | 0.49167 | -11.6667 | -11.6667 | 0.13333 | 0.13333 | Inverter restarted | close | 0.044793 | 0.14 | 254.7433
156 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-06 | 6:16 | 18:28 | 12.2 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.49167 |  |  | 0.50069 | -11.8 | -11.8 | 0.21667 | 0.21667 | Waiting for inverter spares | open | 0.018088 | 0.23 | 103.9977
157 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-06 | 6:16 | 18:28 | 12.2 | Inv 1 (630kw) unit 2 | 669.6 | 8.348% | Inverter_1 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | Unit-2 Kept off Due to Inverter Continous PM High Fault | 0.49167 |  |  | 0.50069 | -11.8 | -11.8 | 0.21667 | 0.21667 | Waiting for inverter spares | open | 0.018088 | 0.23 | 103.9977
158 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-06 | 6:16 | 18:28 | 12.2 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Pm high fault |  | Inverter trip due to Pm high fault | 0.50069 |  |  | 0.51944 | -12.0167 | -12.0167 | 0.45 | 0.45 | Inverter restarted | close | 0.15118 | 0.41 | 746.0341
159 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-06 | 6:16 | 18:28 | 12.2 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.51944 |  |  | 0.53403 | -12.4667 | -12.4667 | 0.35 | 0.35 | Waiting for inverter spares | open | 0.029219 | 0.3 | 135.6492
160 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-06 | 6:16 | 18:28 | 12.2 | Inv 1 (630kw) unit 2 | 669.6 | 8.348% | Inverter_1 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | Unit-2 Kept off Due to Inverter Continous PM High Fault | 0.51944 |  |  | 0.53403 | -12.4667 | -12.4667 | 0.35 | 0.35 | Waiting for inverter spares | open | 0.029219 | 0.3 | 135.6492
161 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-06 | 6:16 | 18:28 | 12.2 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Pm high fault |  | Inverter trip due to Pm high fault | 0.53403 |  |  | 0.54028 | -12.8167 | -12.8167 | 0.15 | 0.15 | Inverter restarted | close | 0.050392 | 0.05 | 90.9798
162 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-06 | 6:16 | 18:28 | 12.2 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.54028 |  |  | 0.55 | -12.9667 | -12.9667 | 0.23333 | 0.23333 | Waiting for inverter spares | open | 0.019479 | 0.23 | 103.9977
163 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-06 | 6:16 | 18:28 | 12.2 | Inv 1 (630kw) unit 2 | 669.6 | 8.348% | Inverter_1 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | Unit-2 Kept off Due to Inverter Continous PM High Fault | 0.54028 |  |  | 0.55 | -12.9667 | -12.9667 | 0.23333 | 0.23333 | Waiting for inverter spares | open | 0.019479 | 0.23 | 103.9977
164 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-06 | 6:16 | 18:28 | 12.2 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Pm high fault |  | Inverter trip due to Pm high fault | 0.55 |  |  | 0.56111 | -13.2 | -13.2 | 0.26667 | 0.26667 | Inverter restarted | close | 0.089586 | 0.18 | 327.5272
165 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-06 | 6:16 | 18:28 | 12.2 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.56111 |  |  | 0.57014 | -13.4667 | -13.4667 | 0.21667 | 0.21667 | Waiting for inverter spares | open | 0.018088 | 0.21 | 94.9544
166 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-06 | 6:16 | 18:28 | 12.2 | Inv 1 (630kw) unit 2 | 669.6 | 8.348% | Inverter_1 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | Unit-2 Kept off Due to Inverter Continous PM High Fault | 0.56111 |  |  | 0.57014 | -13.4667 | -13.4667 | 0.21667 | 0.21667 | Waiting for inverter spares | open | 0.018088 | 0.21 | 94.9544
167 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-06 | 6:16 | 18:28 | 12.2 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Pm high fault |  | Inverter trip due to Pm high fault | 0.57014 |  |  | 0.57708 | -13.6833 | -13.6833 | 0.16667 | 0.16667 | Inverter restarted | close | 0.055991 | 0.17 | 309.3312
168 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-06 | 6:16 | 18:28 | 12.2 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.57708 |  |  | 0.59236 | -13.85 | -13.85 | 0.36667 | 0.36667 | Waiting for inverter spares | open | 0.03061 | 0.35 | 158.2574
169 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-06 | 6:16 | 18:28 | 12.2 | Inv 1 (630kw) unit 2 | 669.6 | 8.348% | Inverter_1 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | Unit-2 Kept off Due to Inverter Continous PM High Fault | 0.57708 |  |  | 0.59236 | -13.85 | -13.85 | 0.36667 | 0.36667 | Waiting for inverter spares | open | 0.03061 | 0.35 | 158.2574
170 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-06 | 6:16 | 18:28 | 12.2 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Pm high fault |  | Inverter trip due to Pm high fault | 0.59236 |  |  | 0.59861 | -14.2167 | -14.2167 | 0.15 | 0.15 | Inverter restarted | close | 0.050392 | 0.15 | 272.9393
171 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-06 | 6:16 | 18:28 | 12.2 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.59861 |  |  | 0.68889 | -14.3667 | -14.3667 | 2.1667 | 2.1667 | Waiting for inverter spares | open | 0.18088 | 1.48 | 669.2027
172 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-06 | 6:16 | 18:28 | 12.2 | Inv 1 (630kw) unit 2 | 669.6 | 8.348% | Inverter_1 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | Unit-2 Kept off Due to Inverter Continous PM High Fault | 0.59861 |  |  | 0.68889 | -14.3667 | -14.3667 | 2.1667 | 2.1667 | Waiting for inverter spares | open | 0.18088 | 1.48 | 669.2027
173 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-06 | 6:16 | 18:28 | 12.2 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter Manually key stop to start the Unit-2 |  | Inverter Manually key stop to start the Unit-2 | 0.68889 |  |  | 0.69028 | -16.5333 | -16.5333 | 0.033333 | 0.033333 | Inverter restarted | close | 0.011198 | 0.02 | 36.3919
174 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-06 | 6:16 | 18:28 | 12.2 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.69028 |  |  | 0.76944 | -16.5667 | -16.5667 | 1.9 | 1.9 | Waiting for inverter spares | open | 0.15862 | 0.35 | 158.2574
175 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-07 | 6:12 | 18:27 | 12.25 | Inv 2 (630kw) unit 4 | 658.8 | 8.214% | Inverter_2 | Kept off Due to unit-4 IGBT's to Block-1 . |  | Kept off Due to unit-4 IGBT's to Block-1 . | 0.25833 |  |  | 0.525 | -6.2 | -6.2 | 6.4 | 6.4 | Waiting for inverter spares | open | 0.52567 | 2.93 | 1303.472
176 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-07 | 6:12 | 18:27 | 12.25 | Inv2 | 2630.8 | 32.8% | Inverter_2 | Inverter trip due to Over temperature |  | Inverter trip due to Over temperature | 0.525 |  |  | 0.54861 | -12.6 | -12.6 | 0.56667 | 0.56667 | Inverter restarted | close | 0.18586 | 0.45 | 799.4308
177 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-07 | 6:12 | 18:27 | 12.25 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.25833 |  |  | 0.41944 | -6.2 | -6.2 | 3.8667 | 3.8667 | Waiting for inverter spares | open | 0.3228 | 0.67 | 302.9499
178 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-07 | 6:12 | 18:27 | 12.25 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Pm high fault |  | Inverter trip due to Pm high fault | 0.41944 |  |  | 0.42569 | -10.0667 | -10.0667 | 0.15 | 0.15 | Inverter restarted | close | 0.050392 | 0.12 | 218.3514
179 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-07 | 6:12 | 18:27 | 12.25 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.42569 |  |  | 0.44514 | -10.2167 | -10.2167 | 0.46667 | 0.46667 | Waiting for inverter spares | open | 0.038958 | 0.37 | 167.3007
180 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-07 | 6:12 | 18:27 | 12.25 | Inv 1 (630kw) unit 2 | 669.6 | 8.348% | Inverter_1 | Unit-2 Kept off Due to Inverter Continous PM High Fault |  | Unit-2 Kept off Due to Inverter Continous PM High Fault | 0.42569 |  |  | 0.44514 | -10.2167 | -10.2167 | 0.46667 | 0.46667 | Waiting for inverter spares | open | 0.038958 | 0.37 | 167.3007
181 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-07 | 6:12 | 18:27 | 12.25 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Manually stopped Service engineer visited site Inverter inspection continous pm high fault | Manually stopped Service engineer visited site. Inverter inspection work in progress due to continous pm high fault | Manually stopped Service engineer visited site. Inverter inspection work in progress due to continous pm high fault | 0.44514 |  |  | 0.49792 | -10.6833 | -10.6833 | 1.2667 | 1.2667 | Inverter restarted | close | 0.42553 | 1.14 | 2074.3387
182 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-07 | 6:12 | 18:27 | 12.25 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.49792 |  |  | 0.76875 | -11.95 | -11.95 | 6.5 | 6.5 | Waiting for inverter spares | open | 0.54263 | 3.7 | 1673.0067
183 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-07 | 6:12 | 18:27 | 12.25 | Inv 2 (630kw) unit 4 | 658.8 | 8.214% | Inverter_2 | Kept off Due to unit-4 IGBT's to Block-1 . |  | Kept off Due to unit-4 IGBT's to Block-1 . | 0.54861 |  |  | 0.76875 | -13.1667 | -13.1667 | 5.2833 | 5.2833 | Waiting for inverter spares | open | 0.43395 | 2.62 | 1165.562
184 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-08 | 6:11 | 18:23 | 12.2 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.25764 |  |  | 0.76597 | -6.1833 | -6.1833 | 12.2 | 12.2 | Waiting for inverter spares | open | 1.0185 | 5.83 | 2636.1159
185 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-08 | 6:11 | 18:23 | 12.2 | Inv 2 (630kw) unit 4 | 658.8 | 8.214% | Inverter_2 | Kept off Due to unit-4 IGBT's to Block-1 . |  | Kept off Due to unit-4 IGBT's to Block-1 . | 0.25764 |  |  | 0.76597 | -6.1833 | -6.1833 | 12.2 | 12.2 | Waiting for inverter spares | open | 1.0021 | 5.83 | 2593.5979
186 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-09 | 6:10 | 18:24 | 12.2333 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.25694 |  |  | 0.57847 | -6.1667 | -6.1667 | 7.7167 | 7.7167 | Waiting for inverter spares | open | 0.6442 | 4.64 | 2098.0408
187 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-09 | 6:10 | 18:24 | 12.2333 | Inv 2 (630kw) unit 4 | 658.8 | 8.214% | Inverter_2 | Kept off Due to unit-4 IGBT's to Block-1 . |  | Kept off Due to unit-4 IGBT's to Block-1 . | 0.25694 |  |  | 0.55694 | -6.1667 | -6.1667 | 7.2 | 7.2 | Waiting for inverter spares | open | 0.59138 | 4.15 | 1846.2146
188 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-09 | 6:10 | 18:24 | 12.2333 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Over temperature |  | Inverter trip due to Over temperature | 0.57847 |  |  | 0.59444 | -13.8833 | -13.8833 | 0.38333 | 0.38333 | Inverter restarted | close | 0.12878 | 0.36 | 655.0543
189 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-09 | 6:10 | 18:24 | 12.2333 | Inv2 | 2630.8 | 32.8% | Inverter_2 | Inverter trip due to Over temperature |  | Inverter trip due to Over temperature | 0.55694 |  |  | 0.58125 | -13.3667 | -13.3667 | 0.58333 | 0.58333 | Inverter restarted | close | 0.19133 | 0.56 | 994.8472
190 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-09 | 6:10 | 18:24 | 12.2333 | Inv 1 (630kw) unit 1 | 669.6 | 8.348% | Inverter_1 | Kept off Due to unit-1 Flash Over |  | Kept off Due to unit-1 Flash Over | 0.59444 |  |  | 0.76667 | -14.2667 | -14.2667 | 4.1333 | 4.1333 | Waiting for inverter spares | open | 0.34506 | 1.36 | 614.943
191 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-09 | 6:10 | 18:24 | 12.2333 | Inv 2 (630kw) unit 4 | 658.8 | 8.214% | Inverter_2 | Kept off Due to unit-4 IGBT's to Block-1 . |  | Kept off Due to unit-4 IGBT's to Block-1 . | 0.58125 |  |  | 0.76667 | -13.95 | -13.95 | 4.45 | 4.45 | Waiting for inverter spares | open | 0.3655 | 1.36 | 605.0246
192 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-11 | 5:58 | 18:26 | 12.4667 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Over temperature |  | Inverter trip due to Over temperature | 0.55625 |  |  | 0.57083 | -13.35 | -13.35 | 0.35 | 0.35 | Inverter restarted | close | 0.11758 | 0.3 | 545.8786
193 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-11 | 5:58 | 18:26 | 12.4667 | Inv2 | 2630.8 | 32.8% | Inverter_2 | Inverter trip due to Over temperature |  | Inverter trip due to Over temperature | 0.55972 |  |  | 0.58194 | -13.4333 | -13.4333 | 0.53333 | 0.53333 | Inverter restarted | close | 0.17493 | 0.45 | 799.4308
194 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-12 | 6:05 | 18:25 | 12.3333 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Over temperature |  | Inverter trip due to Over temperature | 0.54583 |  |  | 0.56111 | -13.1 | -13.1 | 0.36667 | 0.36667 | Inverter restarted | close | 0.12318 | 0.33 | 600.4665
195 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-12 | 6:05 | 18:25 | 12.3333 | Inv2 | 2630.8 | 32.8% | Inverter_2 | Inverter trip due to Over temperature |  | Inverter trip due to Over temperature | 0.54167 |  |  | 0.5625 | -13 | -13 | 0.5 | 0.5 | Inverter restarted | close | 0.164 | 0.45 | 799.4308
196 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-13 | 6:02 | 18:27 | 12.4167 | Inv2 | 2630.8 | 32.8% | Inverter_2 | Inverter trip due to Over temperature |  | Inverter trip due to Over temperature | 0.53889 |  |  | 0.54792 | -12.9333 | -12.9333 | 0.21667 | 0.21667 | Inverter restarted | close | 0.071065 | 0.21 | 373.0677
197 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-13 | 6:02 | 18:27 | 12.4167 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Over temperature |  | Inverter trip due to Over temperature | 0.55 |  |  | 0.55486 | -13.2 | -13.2 | 0.11667 | 0.11667 | Inverter restarted | close | 0.039194 | 0.12 | 218.3514
198 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-13 | 6:02 | 18:27 | 12.4167 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Over temperature |  | Inverter trip due to Over temperature | 0.56458 |  |  | 0.56875 | -13.55 | -13.55 | 0.1 | 0.1 | Inverter restarted | close | 0.033595 | 0.11 | 200.1555
199 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-14 | 6:01 | 18:29 | 12.4667 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Inverter trip due to Over temperature |  | Inverter trip due to Over temperature | 0.52708 |  |  | 0.54097 | -12.65 | -12.65 | 0.33333 | 0.33333 | Inverter restarted | close | 0.11198 | 0.33 | 600.4665
200 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-14 | 6:01 | 18:29 | 12.4667 | Inv2 | 2630.8 | 32.8% | Inverter_2 | Inverter trip due to Over temperature |  | Inverter trip due to Over temperature | 0.52639 |  |  | 0.55069 | -12.6333 | -12.6333 | 0.58333 | 0.58333 | Inverter restarted | close | 0.19133 | 0.56 | 994.8472
201 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-15 | 6:01 | 18:37 | 12.6 | Inv2 | 2630.8 | 32.8% | Inverter_2 | Inverter trip due to Over temperature |  | Inverter trip due to Over temperature | 0.52431 |  |  | 0.53472 | -12.5833 | -12.5833 | 0.25 | 0.25 | Inverter restarted | close | 0.081998 | 0.23 | 408.5979
202 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-16 | 6:00 | 18:30 | 12.5 | Inv1 | 2694.6 | 33.59% | Inverter_1 | Ground Fault |  | Ground Fault | 0.63611 |  |  | 0.65972 | -15.2667 | -15.2667 | 0.56667 | 0.56667 | Inverter restarted | close | 0.19037 | 0.27 | 491.2907
203 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-29 | 6:03 | 18:39 | 12.6 | Inv2 | 2630.8 | 32.8% | Inverter_2 | Ground Fault |  | Ground Fault | 0.65972 |  |  | 0.675 | -15.8333 | -15.8333 | 0.36667 | 0.36667 | Inverter restarted | close | 0.12026 | 0.04 | 71.0605
204 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-15 | 6:27 | 18:39 | 12.2 | Inv2 | 2630.8 | 32.8% | Inverter_2 | Ground Fault |  | Ground Fault | 0.31736 |  |  | 0.42986 | -7.6167 | -7.6167 | 2.7 | 2.7 | Inverter restarted | close | 0.88558 | 0.21 | 384.6372
205 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-15 | 6:27 | 18:39 | 12.2 | Inv3 | 2695.5 | 33.61% | Inverter_3 | Ground Fault |  | Ground Fault | 0.39306 |  |  | 0.44792 | -9.4333 | -9.4333 | 1.3167 | 1.3167 | Inverter restarted | close | 0.44248 | 0.22 | 412.8632
206 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-15 | 6:27 | 18:39 | 12.2 | Inv2_CB1 | 113.4 | 1.414% | Inverter_2 | Ground Fault |  | Ground Fault | 0.42986 |  |  | 0.53403 | -10.3167 | -10.3167 | 2.5 | 2.5 | Isolated Faulty string from Scb | close | 0.035345 | 0.88 | 69.4768
207 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-15 | 6:27 | 18:39 | 12.2 | Inv2_CB12 | 109.8 | 1.369% | Inverter_2 | Ground Fault |  | Ground Fault | 0.42986 |  |  | 0.53403 | -10.3167 | -10.3167 | 2.5 | 2.5 | Isolated Faulty string from Scb | close | 0.034223 | 0.88 | 67.2712
208 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-15 | 6:27 | 18:39 | 12.2 | Inv3_CB20 | 113.34 | 1.413% | Inverter_3 | Ground Fault |  | Ground Fault | 0.44792 |  |  | 0.50764 | -10.75 | -10.75 | 1.4333 | 1.4333 | Isolated Faulty string from Scb | close | 0.020254 | 0.39 | 30.7746
209 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-15 | 6:27 | 18:39 | 12.2 | Inv3_CB22 | 113.34 | 1.413% | Inverter_3 | Ground Fault |  | Ground Fault | 0.44792 |  |  | 0.50764 | -10.75 | -10.75 | 1.4333 | 1.4333 | Isolated Faulty string from Scb | close | 0.020254 | 0.39 | 30.7746
210 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-15 | 6:27 | 18:39 | 12.2 | Inv3_CB23 | 113.34 | 1.413% | Inverter_3 | Ground Fault |  | Ground Fault | 0.44792 |  |  | 0.50764 | -10.75 | -10.75 | 1.4333 | 1.4333 | Isolated Faulty string from Scb | close | 0.020254 | 0.39 | 30.7746
211 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-15 | 6:27 | 18:39 | 12.2 | Inv3_CB12 | 109.8 | 1.369% | Inverter_3 | Ground Fault |  | Ground Fault | 0.44792 |  |  | 0.50764 | -10.75 | -10.75 | 1.4333 | 1.4333 | Isolated Faulty string from Scb | close | 0.019621 | 0.39 | 29.8134
212 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-16 | 5:51 | 18:42 | 12.85 | Inv1 | 2694.6 | 33.59% | Inverter_1 | HT panel Tripped Over cureent and Earth Fault |  | HT panel Tripped Over cureent and Earth Fault | 0.41667 |  |  | 0.52361 | -10 | -10 | 2.5667 | 2.5667 | Visual inspection done found Healthy.We have Checked the IR Values got Fine Charged the Panel | close | 0.86226 | 1.63 | 3057.92
213 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-20 | 5:57 | 18:40 | 12.7167 | Inv3 | 2695.5 | 33.61% | Inverter_3 | Ground Fault |  | Ground Fault | 0.56319 |  |  | 0.57708 | -13.5167 | -13.5167 | 0.33333 | 0.33333 | Inverter restarted | close | 0.11202 | 0.32 | 600.5284
214 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-22 | 5:51 | 18:23 | 12.5333 | Inv3_CB16 | 113.34 | 1.413% | Inverter_3 | Ground Fault |  | Ground Fault | 0.25625 |  |  | 0.34167 | -6.15 | -6.15 | 2.05 | 2.05 | Isolated Faulty string from Scb | close | 0.028968 | 0.14 | 11.0473
215 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-22 | 5:51 | 18:23 | 12.5333 | Inv3_CB16 | 113.34 | 1.413% | Inverter_3 | Ground Fault |  | Ground Fault | 0.39167 |  |  | 0.44097 | -9.4 | -9.4 | 1.1833 | 1.1833 | Isolated Faulty string from Scb | close | 0.016721 | 0.77 | 60.7601
216 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-25 | 5:51 | 18:43 | 12.8667 | Inv3 | 2695.5 | 33.61% | Inverter_3 | Ground Fault |  | Ground Fault | 0.63819 |  |  | 0.64861 | -15.3167 | -15.3167 | 0.25 | 0.25 | Inverter restarted | close | 0.084015 | 0.07 | 131.3656
Formulas:
Month Year = Table1[[#This Row],[Date]]-DAY(Table1[[#This Row],[Date]])+1
Days = DAY(EOMONTH(Table1[[#This Row],[Month Year]],0))

## Grid BD
Sr. No. | Finacial Year | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Date | Sunrise Time (POA>20 W/m2) | Sunset Time (POA<20 W/m2) | Total Generation Time | Affceted Equipment | DC Capacity Affceted (kW) | Affected Equipmenet Location | Fault Catergory | Plant Equivalent Weightage | Fault Code (As per HMI) | Breakdown Description | Fault Time | Acknowledgemnet Time | Work Start time on Fault | Work Completiuon time on fualt | Acknowdlegemnet time | Response Time | Resolution Time | Action taken | Status | Plant Equivalent breakdown | Lost POA (Wh/m2) | Approxuimate Energy Loss (KWh)
1 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-02 | 6:19 | 18:33 | 12.2333 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Due to 33kv Incoming supply failure | 10:07 |  |  | 10:15 |  |  | 0.13333 | NA | Close | 0.13333 | 0.12 | 962.508
2 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-03 | 6:19 | 17:46 | 11.45 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Due to Heavy wind & Rain TGSPDCL 33kv Line Breakdown | 13:43 |  |  | 16:43 |  |  | 3 | NA | Close | 3 | 0.655 | 5253.6895
3 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-10 | 6:12 | 18:00 | 11.8 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Due to Heavy wind & Rain TGSPDCL 33kv Line Breakdown | 15:04 |  |  | 18:30 |  |  | 3.4333 | NA | Close | 3.4333 | 0.11 | 882.299
4 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-13 | 6:02 | 18:27 | 12.4167 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Due to 33kv Incoming supply failure | 13:19 |  |  | 13:33 |  |  | 0.23333 | NA | Close | 0.23333 | 0.23 | 1844.807
5 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-15 | 6:01 | 18:37 | 12.6 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Due to 33kv Incoming supply failure | 7:49 |  |  | 7:58 |  |  | 0.15 | NA | Close | 0.15 | 0.03 | 240.627
6 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-16 | 6:00 | 18:30 | 12.5 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Due to Heavy wind & Rain TGSPDCL 33kv Incomimg Failure | 14:21 |  |  | 14:41 |  |  | 0.33333 | NA | Close | 0.33333 | 0.25 | 2005.225
7 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-16 | 6:00 | 18:30 | 12.5 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Due to Heavy wind & Rain TGSPDCL 33kv Incomimg Failure | 16:45 |  |  | 18:10 |  |  | 1.4167 | NA | Close | 1.4167 | 0.02 | 160.418
8 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-19 | 6:09 | 18:34 | 12.4167 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Breakdown At TGSPDCL Substation | 16:22 |  |  | 17:47 |  |  | 1.4167 | NA | Close | 1.4167 | 0.17 | 1363.553
9 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-19 | 6:09 | 18:34 | 12.4167 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Due to 33kv Incoming supply failure | 18:09 |  |  | 18:36 |  |  | 0.45 | NA | Close | 0.45 | 0.007 | 56.1463
10 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-21 | 6:01 | 18:28 | 12.45 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Breakdown At TGSPDCL Substation | 11:28 |  |  | 12:28 |  |  | 1 | NA | Close | 1 | 0.89 | 7138.601
11 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-24 | 6:04 | 18:18 | 12.2333 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Due to Heavy wind & Rain TGSPDCL 33kv Incomimg Failure | 16:36 |  |  | 19:25 |  |  | 2.8167 | NA | Close | 2.8167 | 0.1 | 802.09
12 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-25 | 6:05 | 18:10 | 12.0833 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Due to Heavy wind & Rain TGSPDCL 33kv Incomimg Failure | 16:06 |  |  | 18:10 |  |  | 2.0667 | NA | Close | 2.0667 | 0.23 | 1844.807
13 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-26 | 6:00 | 18:25 | 12.4167 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Due to 33kv Incoming supply failure | 15:47 |  |  | 16:07 |  |  | 0.33333 | NA | Close | 0.33333 | 0.04 | 320.836
14 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-01 | 6:01 | 18:39 | 12.6333 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Due to 33kv Incoming supply failure | 10:32 |  |  | 10:48 |  |  | 0.26667 | NA | Close | 0.26667 | 0.22 | 1764.598
15 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-02 | 6:01 | 18:37 | 12.6 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Breakdown At 132 kv TGSPDCL Substation | 9:20 |  |  | 10:00 |  |  | 0.66667 | NA | Close | 0.66667 | 0.45 | 3609.405
16 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-04 | 5:59 | 18:42 | 12.7167 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | PTR Breakdown at 33 kv TGSPDCL Substation | 12:22 |  |  | 18:28 |  |  | 6.1 | NA | Close | 6.1 | 2.66 | 21335.594
17 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-08 | 6:02 | 18:29 | 12.45 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Due to 33kv Incoming supply failure | 10:20 |  |  | 10:28 |  |  | 0.13333 | NA | Close | 0.13333 | 0.12 | 962.508
18 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-08 | 6:02 | 18:29 | 12.45 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Due to 33kv Incoming supply failure | 17:53 |  |  | 17:59 |  |  | 0.1 | NA | Close | 0.1 | 0.008 | 64.1672
19 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-14 | 5:53 | 18:11 | 12.3 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Due to 33kv Incoming supply failure | 17:54 |  |  | 18:25 |  |  | 0.51667 | NA | Close | 0.51667 | 0.0006 | 4.8125
20 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-15 | 6:27 | 18:39 | 12.2 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Due to 33kv Incoming supply failure | 14:18 |  |  | 14:27 |  |  | 0.15 | NA | Close | 0.15 | 0.046 | 368.9614
21 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-16 | 5:51 | 18:42 | 12.85 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Due to 33kv Incoming supply failure | 9:44 |  |  | 10:00 |  |  | 0.26667 | NA | Close | 0.26667 | 0.122 | 978.5498
22 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-16 | 5:51 | 18:42 | 12.85 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Due to 33kv Incoming supply failure | 15:14 |  |  | 15:21 |  |  | 0.11667 | NA | Close | 0.11667 | 0.07 | 561.463
23 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-17 | 5:50 | 18:38 | 12.8 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Due to 33kv Incoming supply failure | 5:55 |  |  | 7:31 |  |  | 1.6 | NA | Close | 1.6 | 0.12 | 962.508
24 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-17 | 5:50 | 18:38 | 12.8 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Due to 33kv Incoming supply failure | 8:10 |  |  | 8:15 |  |  | 0.083333 | NA | Close | 0.083333 | 0.02 | 160.418
25 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-18 | 6:01 | 18:40 | 12.65 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Due to 33kv Incoming supply failure | 9:02 |  |  | 10:35 |  |  | 1.55 | NA | Close | 1.55 | 1.02 | 8181.318
26 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-18 | 6:01 | 18:40 | 12.65 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Due to 33kv Incoming supply failure | 13:33 |  |  | 14:10 |  |  | 0.61667 | NA | Close | 0.61667 | 0.48 | 3850.032
27 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-18 | 6:01 | 18:40 | 12.65 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Due to 33kv Incoming supply failure | 14:52 |  |  | 15:28 |  |  | 0.6 | NA | Close | 0.6 | 0.34 | 2727.106
28 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-19 | 6:00 | 18:48 | 12.8 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Due to 33kv Incoming supply failure | 12:34 |  |  | 13:14 |  |  | 0.66667 | NA | Close | 0.66667 | 0.378 | 3031.9002
29 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-21 | 5:50 | 18:40 | 12.8333 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Due to 33kv Incoming supply failure | 14:44 |  |  | 17:48 |  |  | 3.0667 | NA | Close | 3.0667 | 0.055 | 441.1495
30 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-22 | 5:51 | 18:23 | 12.5333 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Due to 33kv Incoming supply failure | 8:12 |  |  | 9:24 |  |  | 1.2 | NA | Close | 1.2 | 0.49 | 3930.241
31 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-22 | 5:51 | 18:23 | 12.5333 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Due to 33kv Incoming supply failure | 11:04 |  |  | 11:30 |  |  | 0.43333 | NA | Close | 0.43333 | 0.38 | 3047.942
32 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-22 | 5:51 | 18:23 | 12.5333 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Due to 33kv Incoming supply failure | 15:48 |  |  | 16:11 |  |  | 0.38333 | NA | Close | 0.38333 | 0.19 | 1523.971
33 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-24 | 6:01 | 18:36 | 12.5833 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Due to 33kv Incoming supply failure | 15:44 |  |  | 15:54 |  |  | 0.16667 | NA | Close | 0.16667 | 0.05 | 401.045
34 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-24 | 6:01 | 18:36 | 12.5833 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Due to 33kv Incoming supply failure | 16:32 |  |  | 16:58 |  |  | 0.43333 | NA | Close | 0.43333 | 0.01 | 80.209
35 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-25 | 5:51 | 18:43 | 12.8667 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Due to 33kv Incoming supply failure | 17:46 |  |  | 18:01 |  |  | 0.25 | NA | Close | 0.25 | 0.008 | 64.1672
36 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-26 | 6:02 | 18:50 | 12.8 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Due to 33kv Incoming supply failure | 13:22 |  |  | 13:29 |  |  | 0.11667 | NA | Close | 0.11667 | 0.02 | 160.418
37 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-27 | 5:51 | 18:26 | 12.5833 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Due to 33kv Incoming supply failure | 7:52 |  |  | 8:21 |  |  | 0.48333 | NA | Close | 0.48333 | 0.1 | 802.09
38 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-05 | 6:00 | 18:37 | 12.6167 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Due to 33kv Incoming supply failure | 9:54 |  |  | 10:08 |  |  | 0.23333 | NA | Close | 0.23333 | 0.1 | 802.09
39 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-07 | 5:52 | 18:48 | 12.9333 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Due to 33kv Incoming supply failure | 7:40 |  |  | 7:48 |  |  | 0.13333 | NA | Close | 0.13333 | 0.02 | 160.418
40 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-07 | 5:52 | 18:48 | 12.9333 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Due to 33kv Incoming supply failure | 9:21 |  |  | 9:27 |  |  | 0.1 | NA | Close | 0.1 | 0.07 | 561.463
41 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-07 | 5:52 | 18:48 | 12.9333 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Due to 33kv Incoming supply failure | 13:52 |  |  | 15:38 |  |  | 1.7667 | NA | Close | 1.7667 | 0.27 | 2165.643
42 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-09 | 6:42 | 18:48 | 12.1 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Due to TGSPDCL 33kv line Breakdown | 9:35 |  |  | 12:29 |  |  | 2.9 | NA | Close | 2.9 | 0.36 | 2887.524
43 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-09 | 6:42 | 18:48 | 12.1 | Outgoing | 8020.9 | PLANT | Grid System | 100% |  | Due to 33kv Incoming supply failure | 15:58 |  |  | 16:13 |  |  | 0.25 | NA | Close | 0.25 | 0.023 | 184.4807
Formulas:
Days = DAY(EOMONTH(Table19[[#This Row],[Month Year]],0))

## Modelling New (hidden)
Sr. No. | Month Name | Month Number | Month | CY | FY | No. of Days in Month | GHI | POA | WS | Tamb | Tmod | Egrid (MWh) | Bugt_Capacity | PR | Daily POA | Days Operated | MTD POA | YTD POA | Daily Energy (MWh) | MTD Energy (MWh) | YTD Energy (MWh) | Bugt CUF (%) | Bugt CUF (%) MTD | Bugt CUF (%)YTD | Ave. Cap MTD | Ave. Cap YTD | CC Energy MTD | WS MTD | WS YTD | Bugt PA | Bugt EGA | Bugt TA | Bugt MA | Bugt IGA | Corelation | Bugt Line loss | Bugt Reactive Power | Bugt Capacity | CC*Bugt | DC Capacity | 8.0209
1 | April | 4 | 2018-04-01 | 2018 | FY19 | 30 | 193.6 | 191.7 |  |  |  | 1055.6538 | 8.0209 | 68.66% | 6.39 | 0 | 0 | 0 | 35.1885 | 0 | 0 | 18.28% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
2 | May | 5 | 2018-05-01 | 2018 | FY19 | 31 | 198.6 | 186.4 |  |  |  | 1060.9586 | 8.0209 | 70.96% | 6.0129 | 0 | 0 | 0 | 34.2245 | 0 | 0 | 17.78% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
3 | June | 6 | 2018-06-01 | 2018 | FY19 | 30 | 154.8 | 142.8 |  |  |  | 790.4142 | 8.0209 | 69.01% | 4.76 | 0 | 0 | 0 | 26.3471 | 0 | 0 | 13.69% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
4 | July | 7 | 2018-07-01 | 2018 | FY19 | 31 | 134.4 | 125.4 |  |  |  | 721.4518 | 8.0209 | 71.73% | 4.0452 | 0 | 0 | 0 | 23.2726 | 0 | 0 | 12.09% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
5 | August | 8 | 2018-08-01 | 2018 | FY19 | 31 | 134.6 | 130.7 |  |  |  | 763.8902 | 8.0209 | 72.87% | 4.2161 | 0 | 0 | 0 | 24.6416 | 0 | 0 | 12.8% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
6 | September | 9 | 2018-09-01 | 2018 | FY19 | 30 | 142.5 | 145.4 |  |  |  | 827.5477 | 8.0209 | 70.96% | 4.8467 | 0 | 0 | 0 | 27.5849 | 0 | 0 | 14.33% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
7 | October | 10 | 2018-10-01 | 2018 | FY19 | 31 | 145.7 | 158.8 |  |  |  | 938.9484 | 8.0209 | 73.72% | 5.1226 | 0 | 0 | 0 | 30.2887 | 0 | 0 | 15.73% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
8 | November | 11 | 2018-11-01 | 2018 | FY19 | 30 | 138.9 | 163 |  |  |  | 944.2531 | 8.0209 | 72.22% | 5.4333 | 0 | 0 | 0 | 31.4751 | 0 | 0 | 16.35% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
9 | December | 12 | 2018-12-01 | 2018 | FY19 | 31 | 134.7 | 163.7 |  |  |  | 981.3867 | 8.0209 | 74.74% | 5.2806 | 0 | 0 | 0 | 31.6576 | 0 | 0 | 16.45% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
10 | January | 1 | 2019-01-01 | 2019 | FY19 | 31 | 151.6 | 183.9 |  |  |  | 1087.4826 | 8.0209 | 73.73% | 5.9323 | 0 | 0 | 0 | 35.0801 | 0 | 0 | 18.22% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
11 | February | 2 | 2019-02-01 | 2019 | FY19 | 28 | 159.9 | 184 |  |  |  | 1038.6059 | 8.0209 | 70.37% | 6.5714 | 0 | 0 | 0 | 37.0931 | 0 | 0 | 19.27% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
12 | March | 3 | 2019-03-01 | 2019 | FY19 | 31 | 197.2 | 210.4 |  |  |  | 1204.188 | 8.0209 | 71.36% | 6.7871 | 0 | 0 | 0 | 38.8448 | 0 | 0 | 20.18% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
13 | April | 4 | 2019-04-01 | 2019 | FY20 | 30 | 193.6 | 191.7 |  |  |  | 1055.6538 | 8.0209 | 68.66% | 6.39 | 0 | 0 | 0 | 35.1885 | 0 | 0 | 18.28% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
14 | May | 5 | 2019-05-01 | 2019 | FY20 | 31 | 198.6 | 186.4 |  |  |  | 1060.9586 | 8.0209 | 70.96% | 6.0129 | 0 | 0 | 0 | 34.2245 | 0 | 0 | 17.78% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
15 | June | 6 | 2019-06-01 | 2019 | FY20 | 30 | 154.8 | 142.8 |  |  |  | 790.4142 | 8.0209 | 69.01% | 4.76 | 0 | 0 | 0 | 26.3471 | 0 | 0 | 13.69% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
16 | July | 7 | 2019-07-01 | 2019 | FY20 | 31 | 134.4 | 125.4 |  |  |  | 721.4518 | 8.0209 | 71.73% | 4.0452 | 0 | 0 | 0 | 23.2726 | 0 | 0 | 12.09% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
17 | August | 8 | 2019-08-01 | 2025 | FY20 | 31 | 134.6 | 130.7 |  |  |  | 763.8902 | 8.0209 | 72.87% | 4.2161 | 0 | 0 | 0 | 24.6416 | 0 | 0 | 12.8% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
18 | September | 9 | 2019-09-01 | 2025 | FY20 | 30 | 142.5 | 145.4 |  |  |  | 827.5477 | 8.0209 | 70.96% | 4.8467 | 0 | 0 | 0 | 27.5849 | 0 | 0 | 14.33% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
19 | October | 10 | 2019-10-01 | 2025 | FY20 | 31 | 145.7 | 158.8 |  |  |  | 938.9484 | 8.0209 | 73.72% | 5.1226 | 0 | 0 | 0 | 30.2887 | 0 | 0 | 15.73% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
20 | November | 11 | 2019-11-01 | 2025 | FY20 | 30 | 138.9 | 163 |  |  |  | 944.2531 | 8.0209 | 72.22% | 5.4333 | 0 | 0 | 0 | 31.4751 | 0 | 0 | 16.35% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
21 | December | 12 | 2019-12-01 | 2025 | FY20 | 31 | 134.7 | 163.7 |  |  |  | 981.3867 | 8.0209 | 74.74% | 5.2806 | 0 | 0 | 0 | 31.6576 | 0 | 0 | 16.45% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
22 | January | 1 | 2020-01-01 | 2025 | FY20 | 31 | 151.6 | 183.9 |  |  |  | 1087.4826 | 8.0209 | 73.73% | 5.9323 | 0 | 0 | 0 | 35.0801 | 0 | 0 | 18.22% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
23 | February | 2 | 2020-02-01 | 2025 | FY20 | 29 | 159.9 | 184 |  |  |  | 1038.6059 | 8.0209 | 70.37% | 6.3448 | 0 | 0 | 0 | 35.814 | 0 | 0 | 18.6% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
24 | March | 3 | 2020-03-01 | 2025 | FY20 | 31 | 197.2 | 210.4 |  |  |  | 1204.188 | 8.0209 | 71.36% | 6.7871 | 0 | 0 | 0 | 38.8448 | 0 | 0 | 20.18% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
25 | April | 4 | 2020-04-01 | 2025 | FY21 | 30 | 193.6 | 191.7 |  |  |  | 1055.6538 | 8.0209 | 68.66% | 6.39 | 0 | 0 | 0 | 35.1885 | 0 | 0 | 18.28% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
26 | May | 5 | 2020-05-01 | 2026 | FY21 | 31 | 198.6 | 186.4 |  |  |  | 1060.9586 | 8.0209 | 70.96% | 6.0129 | 0 | 0 | 0 | 34.2245 | 0 | 0 | 17.78% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
27 | June | 6 | 2020-06-01 | 2026 | FY21 | 30 | 154.8 | 142.8 |  |  |  | 790.4142 | 8.0209 | 69.01% | 4.76 | 0 | 0 | 0 | 26.3471 | 0 | 0 | 13.69% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
28 | July | 7 | 2020-07-01 | 2026 | FY21 | 31 | 134.4 | 125.4 |  |  |  | 721.4518 | 8.0209 | 71.73% | 4.0452 | 0 | 0 | 0 | 23.2726 | 0 | 0 | 12.09% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
29 | August | 8 | 2020-08-01 | 2020 | FY21 | 31 | 134.6 | 130.7 |  |  |  | 763.8902 | 8.0209 | 72.87% | 4.2161 | 0 | 0 | 0 | 24.6416 | 0 | 0 | 12.8% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
30 | September | 9 | 2020-09-01 | 2020 | FY21 | 30 | 142.5 | 145.4 |  |  |  | 827.5477 | 8.0209 | 70.96% | 4.8467 | 0 | 0 | 0 | 27.5849 | 0 | 0 | 14.33% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
31 | October | 10 | 2020-10-01 | 2020 | FY21 | 31 | 145.7 | 158.8 |  |  |  | 938.9484 | 8.0209 | 73.72% | 5.1226 | 0 | 0 | 0 | 30.2887 | 0 | 0 | 15.73% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
32 | November | 11 | 2020-11-01 | 2020 | FY21 | 30 | 138.9 | 163 |  |  |  | 944.2531 | 8.0209 | 72.22% | 5.4333 | 0 | 0 | 0 | 31.4751 | 0 | 0 | 16.35% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
33 | December | 12 | 2020-12-01 | 2020 | FY21 | 31 | 134.7 | 163.7 |  |  |  | 981.3867 | 8.0209 | 74.74% | 5.2806 | 0 | 0 | 0 | 31.6576 | 0 | 0 | 16.45% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
34 | January | 1 | 2021-01-01 | 2021 | FY21 | 31 | 151.6 | 183.9 |  |  |  | 1087.4826 | 8.0209 | 73.73% | 5.9323 | 0 | 0 | 0 | 35.0801 | 0 | 0 | 18.22% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
35 | February | 2 | 2021-02-01 | 2021 | FY21 | 28 | 159.9 | 184 |  |  |  | 1038.6059 | 8.0209 | 70.37% | 6.5714 | 0 | 0 | 0 | 37.0931 | 0 | 0 | 19.27% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
36 | March | 3 | 2021-03-01 | 2021 | FY21 | 31 | 197.2 | 210.4 |  |  |  | 1204.188 | 8.0209 | 71.36% | 6.7871 | 0 | 0 | 0 | 38.8448 | 0 | 0 | 20.18% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
37 | April | 4 | 2021-04-01 | 2021 | FY22 | 30 | 193.6 | 191.7 |  |  |  | 1055.6538 | 8.0209 | 68.66% | 6.39 | 0 | 0 | 0 | 35.1885 | 0 | 0 | 18.28% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
38 | May | 5 | 2021-05-01 | 2021 | FY22 | 31 | 198.6 | 186.4 |  |  |  | 1060.9586 | 8.0209 | 70.96% | 6.0129 | 0 | 0 | 0 | 34.2245 | 0 | 0 | 17.78% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
39 | June | 6 | 2021-06-01 | 2021 | FY22 | 30 | 154.8 | 142.8 |  |  |  | 790.4142 | 8.0209 | 69.01% | 4.76 | 0 | 0 | 0 | 26.3471 | 0 | 0 | 13.69% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
40 | July | 7 | 2021-07-01 | 2021 | FY22 | 31 | 134.4 | 125.4 |  |  |  | 721.4518 | 8.0209 | 71.73% | 4.0452 | 0 | 0 | 0 | 23.2726 | 0 | 0 | 12.09% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
41 | August | 8 | 2021-08-01 | 2021 | FY22 | 31 | 134.6 | 130.7 |  |  |  | 763.8902 | 8.0209 | 72.87% | 4.2161 | 0 | 0 | 0 | 24.6416 | 0 | 0 | 12.8% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
42 | September | 9 | 2021-09-01 | 2021 | FY22 | 30 | 142.5 | 145.4 |  |  |  | 827.5477 | 8.0209 | 70.96% | 4.8467 | 0 | 0 | 0 | 27.5849 | 0 | 0 | 14.33% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
43 | October | 10 | 2021-10-01 | 2021 | FY22 | 31 | 145.7 | 158.8 |  |  |  | 938.9484 | 8.0209 | 73.72% | 5.1226 | 0 | 0 | 0 | 30.2887 | 0 | 0 | 15.73% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
44 | November | 11 | 2021-11-01 | 2021 | FY22 | 30 | 138.9 | 163 |  |  |  | 944.2531 | 8.0209 | 72.22% | 5.4333 | 0 | 0 | 0 | 31.4751 | 0 | 0 | 16.35% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
45 | December | 12 | 2021-12-01 | 2021 | FY22 | 31 | 134.7 | 163.7 |  |  |  | 981.3867 | 8.0209 | 74.74% | 5.2806 | 0 | 0 | 0 | 31.6576 | 0 | 0 | 16.45% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
46 | January | 1 | 2022-01-01 | 2022 | FY22 | 31 | 151.6 | 183.9 |  |  |  | 1087.4826 | 8.0209 | 73.73% | 5.9323 | 0 | 0 | 0 | 35.0801 | 0 | 0 | 18.22% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
47 | February | 2 | 2022-02-01 | 2022 | FY22 | 28 | 159.9 | 184 |  |  |  | 1038.6059 | 8.0209 | 70.37% | 6.5714 | 0 | 0 | 0 | 37.0931 | 0 | 0 | 19.27% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
48 | March | 3 | 2022-03-01 | 2022 | FY22 | 31 | 197.2 | 210.4 |  |  |  | 1204.188 | 8.0209 | 71.36% | 6.7871 | 0 | 0 | 0 | 38.8448 | 0 | 0 | 20.18% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
49 | April | 4 | 2022-04-01 | 2022 | FY23 | 30 | 193.6 | 191.7 |  |  |  | 1055.6538 | 8.0209 | 68.66% | 6.39 | 0 | 0 | 0 | 35.1885 | 0 | 0 | 18.28% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
50 | May | 5 | 2022-05-01 | 2022 | FY23 | 31 | 198.6 | 186.4 |  |  |  | 1060.9586 | 8.0209 | 70.96% | 6.0129 | 0 | 0 | 0 | 34.2245 | 0 | 0 | 17.78% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
51 | June | 6 | 2022-06-01 | 2022 | FY23 | 30 | 154.8 | 142.8 |  |  |  | 790.4142 | 8.0209 | 69.01% | 4.76 | 0 | 0 | 0 | 26.3471 | 0 | 0 | 13.69% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
52 | July | 7 | 2022-07-01 | 2022 | FY23 | 31 | 134.4 | 125.4 |  |  |  | 721.4518 | 8.0209 | 71.73% | 4.0452 | 0 | 0 | 0 | 23.2726 | 0 | 0 | 12.09% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
53 | August | 8 | 2022-08-01 | 2022 | FY23 | 31 | 134.6 | 130.7 |  |  |  | 763.8902 | 8.0209 | 72.87% | 4.2161 | 0 | 0 | 0 | 24.6416 | 0 | 0 | 12.8% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
54 | September | 9 | 2022-09-01 | 2022 | FY23 | 30 | 142.5 | 145.4 |  |  |  | 827.5477 | 8.0209 | 70.96% | 4.8467 | 0 | 0 | 0 | 27.5849 | 0 | 0 | 14.33% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
55 | October | 10 | 2022-10-01 | 2022 | FY23 | 31 | 145.7 | 158.8 |  |  |  | 938.9484 | 8.0209 | 73.72% | 5.1226 | 0 | 0 | 0 | 30.2887 | 0 | 0 | 15.73% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
56 | November | 11 | 2022-11-01 | 2022 | FY23 | 30 | 138.9 | 163 |  |  |  | 944.2531 | 8.0209 | 72.22% | 5.4333 | 0 | 0 | 0 | 31.4751 | 0 | 0 | 16.35% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
57 | December | 12 | 2022-12-01 | 2022 | FY23 | 31 | 134.7 | 163.7 |  |  |  | 981.3867 | 8.0209 | 74.74% | 5.2806 | 0 | 0 | 0 | 31.6576 | 0 | 0 | 16.45% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
58 | January | 1 | 2023-01-01 | 2023 | FY23 | 31 | 151.6 | 183.9 |  |  |  | 1087.4826 | 8.0209 | 73.73% | 5.9323 | 0 | 0 | 0 | 35.0801 | 0 | 0 | 18.22% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
59 | February | 2 | 2023-02-01 | 2023 | FY23 | 28 | 159.9 | 184 |  |  |  | 1038.6059 | 8.0209 | 70.37% | 6.5714 | 0 | 0 | 0 | 37.0931 | 0 | 0 | 19.27% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
60 | March | 3 | 2023-03-01 | 2023 | FY23 | 31 | 197.2 | 210.4 |  |  |  | 1204.188 | 8.0209 | 71.36% | 6.7871 | 0 | 0 | 0 | 38.8448 | 0 | 0 | 20.18% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
61 | April | 4 | 2023-04-01 | 2023 | FY24 | 30 | 193.6 | 191.7 |  |  |  | 1055.6538 | 8.0209 | 68.66% | 6.39 | 0 | 0 | 0 | 35.1885 | 0 | 0 | 18.28% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
62 | May | 5 | 2023-05-01 | 2023 | FY24 | 31 | 198.6 | 186.4 |  |  |  | 1060.9586 | 8.0209 | 70.96% | 6.0129 | 0 | 0 | 0 | 34.2245 | 0 | 0 | 17.78% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
63 | June | 6 | 2023-06-01 | 2023 | FY24 | 30 | 154.8 | 142.8 |  |  |  | 790.4142 | 8.0209 | 69.01% | 4.76 | 0 | 0 | 0 | 26.3471 | 0 | 0 | 13.69% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
64 | July | 7 | 2023-07-01 | 2023 | FY24 | 31 | 134.4 | 125.4 |  |  |  | 721.4518 | 8.0209 | 71.73% | 4.0452 | 0 | 0 | 0 | 23.2726 | 0 | 0 | 12.09% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
65 | August | 8 | 2023-08-01 | 2023 | FY24 | 31 | 134.6 | 130.7 |  |  |  | 763.8902 | 8.0209 | 72.87% | 4.2161 | 0 | 0 | 0 | 24.6416 | 0 | 0 | 12.8% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
66 | September | 9 | 2023-09-01 | 2023 | FY24 | 30 | 142.5 | 145.4 |  |  |  | 827.5477 | 8.0209 | 70.96% | 4.8467 | 0 | 0 | 0 | 27.5849 | 0 | 0 | 14.33% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
67 | October | 10 | 2023-10-01 | 2023 | FY24 | 31 | 145.7 | 158.8 |  |  |  | 938.9484 | 8.0209 | 73.72% | 5.1226 | 0 | 0 | 0 | 30.2887 | 0 | 0 | 15.73% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
68 | November | 11 | 2023-11-01 | 2023 | FY24 | 30 | 138.9 | 163 |  |  |  | 944.2531 | 8.0209 | 72.22% | 5.4333 | 0 | 0 | 0 | 31.4751 | 0 | 0 | 16.35% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
69 | December | 12 | 2023-12-01 | 2023 | FY24 | 31 | 134.7 | 163.7 |  |  |  | 981.3867 | 8.0209 | 74.74% | 5.2806 | 0 | 0 | 0 | 31.6576 | 0 | 0 | 16.45% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
70 | January | 1 | 2024-01-01 | 2024 | FY24 | 31 | 151.6 | 183.9 |  |  |  | 1087.4826 | 8.0209 | 73.73% | 5.9323 | 0 | 0 | 0 | 35.0801 | 0 | 0 | 18.22% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
71 | February | 2 | 2024-02-01 | 2024 | FY24 | 29 | 159.9 | 184 |  |  |  | 1038.6059 | 8.0209 | 70.37% | 6.3448 | 0 | 0 | 0 | 35.814 | 0 | 0 | 18.6% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
72 | March | 3 | 2024-03-01 | 2024 | FY24 | 31 | 197.2 | 210.4 |  |  |  | 1204.188 | 8.0209 | 71.36% | 6.7871 | 0 | 0 | 0 | 38.8448 | 0 | 0 | 20.18% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
73 | April | 4 | 2024-04-01 | 2024 | FY25 | 30 | 193.6 | 191.7 |  |  |  | 1055.6538 | 8.0209 | 68.66% | 6.39 | 0 | 0 | 0 | 35.1885 | 0 | 0 | 18.28% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
74 | May | 5 | 2024-05-01 | 2024 | FY25 | 31 | 198.6 | 186.4 |  |  |  | 1060.9586 | 8.0209 | 70.96% | 6.0129 | 0 | 0 | 0 | 34.2245 | 0 | 0 | 17.78% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
75 | June | 6 | 2024-06-01 | 2024 | FY25 | 30 | 154.8 | 142.8 |  |  |  | 790.4142 | 8.0209 | 69.01% | 4.76 | 0 | 0 | 0 | 26.3471 | 0 | 0 | 13.69% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
76 | July | 7 | 2024-07-01 | 2024 | FY25 | 31 | 134.4 | 125.4 |  |  |  | 721.4518 | 8.0209 | 71.73% | 4.0452 | 0 | 0 | 0 | 23.2726 | 0 | 0 | 12.09% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
77 | August | 8 | 2024-08-01 | 2024 | FY25 | 31 | 134.6 | 130.7 |  |  |  | 763.8902 | 8.0209 | 72.87% | 4.2161 | 0 | 0 | 0 | 24.6416 | 0 | 0 | 12.8% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
78 | September | 9 | 2024-09-01 | 2024 | FY25 | 30 | 142.5 | 145.4 |  |  |  | 827.5477 | 8.0209 | 70.96% | 4.8467 | 0 | 0 | 0 | 27.5849 | 0 | 0 | 14.33% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
79 | October | 10 | 2024-10-01 | 2024 | FY25 | 31 | 145.7 | 158.8 |  |  |  | 938.9484 | 8.0209 | 73.72% | 5.1226 | 0 | 0 | 0 | 30.2887 | 0 | 0 | 15.73% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
80 | November | 11 | 2024-11-01 | 2024 | FY25 | 30 | 138.9 | 163 |  |  |  | 944.2531 | 8.0209 | 72.22% | 5.4333 | 0 | 0 | 0 | 31.4751 | 0 | 0 | 16.35% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
81 | December | 12 | 2024-12-01 | 2024 | FY25 | 31 | 134.7 | 163.7 |  |  |  | 981.3867 | 8.0209 | 74.74% | 5.2806 | 0 | 0 | 0 | 31.6576 | 0 | 0 | 16.45% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
82 | January | 1 | 2025-01-01 | 2025 | FY25 | 31 | 151.6 | 183.9 |  |  |  | 1087.4826 | 8.0209 | 73.73% | 5.9323 | 0 | 0 | 0 | 35.0801 | 0 | 0 | 18.22% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
83 | February | 2 | 2025-02-01 | 2025 | FY25 | 28 | 159.9 | 184 |  |  |  | 1038.6059 | 8.0209 | 70.37% | 6.5714 | 0 | 0 | 0 | 37.0931 | 0 | 0 | 19.27% |  |  |  | 8.0209 |  |  |  | 98.04% | 98%
84 | March | 3 | 2025-03-01 | 2025 | FY25 | 31 | 197.2 | 210.4 |  |  |  | 1204.188 | 8.0209 | 71.36% | 6.7871 | 2 | 13.5742 | 13.5742 | 38.8448 | 77.6895 | 77.6895 | 20.18% | 20.18% | 20.18% | 8.0209 | 8.0209 |  |  |  | 98.04% | 98%
85 | April | 4 | 2025-04-01 | 2025 | FY26 | 30 | 193.6 | 191.7 |  |  |  | 1038.3069 | 8.0209 | 67.53% | 6.39 | 30 | 191.7 | 191.7 | 34.6102 | 1038.3069 | 1038.3069 | 17.98% | 17.98% | 17.98% | 8.0209 | 8.0209 |  |  |  | 98.04% | 98%
86 | May | 5 | 2025-05-01 | 2025 | FY26 | 31 | 198.6 | 186.4 |  |  |  | 1040.9101 | 8.0209 | 69.62% | 6.0129 | 31 | 186.4 | 378.1 | 33.5777 | 1040.9101 | 2079.2169 | 17.44% | 17.44% | 17.71% | 8.0209 | 8.0209 |  |  |  | 98.04% | 98%
87 | June | 6 | 2025-06-01 | 2025 | FY26 | 30 | 154.8 | 142.8 |  |  |  | 777.5924 | 8.0209 | 67.89% | 4.76 | 12 | 57.12 | 435.22 | 25.9197 | 311.037 | 2390.2539 | 13.46% | 13.46% | 17.01% | 8.0209 | 8.0209 |  |  |  | 98.04% | 98%
88 | July | 7 | 2025-07-01 | 2025 | FY26 | 31 | 134.4 | 125.4 |  |  |  | 710.8284 | 8.0209 | 70.67% | 4.0452 | 0 | 0 | 435.22 | 22.9299 | 0 | 2390.2539 | 11.91% |  | 17.01% |  | 8.0209 |  |  |  | 98.04% | 98%
89 | August | 8 | 2025-08-01 | 2025 | FY26 | 31 | 134.6 | 130.7 |  |  |  | 752.4679 | 8.0209 | 71.78% | 4.2161 | 0 | 0 | 435.22 | 24.2732 | 0 | 2390.2539 | 12.61% |  | 17.01% |  | 8.0209 |  |  |  | 98.04% | 98%
90 | September | 9 | 2025-09-01 | 2025 | FY26 | 30 | 142.5 | 145.4 |  |  |  | 812.9709 | 8.0209 | 69.71% | 4.8467 | 0 | 0 | 435.22 | 27.099 | 0 | 2390.2539 | 14.08% |  | 17.01% |  | 8.0209 |  |  |  | 98.04% | 98%
91 | October | 10 | 2025-10-01 | 2025 | FY26 | 31 | 145.7 | 158.8 |  |  |  | 923.7281 | 8.0209 | 72.52% | 5.1226 | 0 | 0 | 435.22 | 29.7977 | 0 | 2390.2539 | 15.48% |  | 17.01% |  | 8.0209 |  |  |  | 98.04% | 98%
92 | November | 11 | 2025-11-01 | 2025 | FY26 | 30 | 138.9 | 163 |  |  |  | 928.0611 | 8.0209 | 70.98% | 5.4333 | 0 | 0 | 435.22 | 30.9354 | 0 | 2390.2539 | 16.07% |  | 17.01% |  | 8.0209 |  |  |  | 98.04% | 98%
93 | December | 12 | 2025-12-01 | 2025 | FY26 | 31 | 134.7 | 163.7 |  |  |  | 966.3535 | 8.0209 | 73.6% | 5.2806 | 0 | 0 | 435.22 | 31.1727 | 0 | 2390.2539 | 16.19% |  | 17.01% |  | 8.0209 |  |  |  | 98.04% | 98%
94 | January | 1 | 2026-01-01 | 2026 | FY26 | 31 | 151.6 | 183.9 |  |  |  | 1068.7456 | 8.0209 | 72.46% | 5.9323 | 0 | 0 | 435.22 | 34.4757 | 0 | 2390.2539 | 17.91% |  | 17.01% |  | 8.0209 |  |  |  | 98.04% | 98%
95 | February | 2 | 2026-02-01 | 2026 | FY26 | 28 | 159.9 | 184 |  |  |  | 951.7015 | 8.0209 | 64.49% | 6.5714 | 0 | 0 | 435.22 | 33.9893 | 0 | 2390.2539 | 17.66% |  | 17.01% |  | 8.0209 |  |  |  | 98.04% | 98%
96 | March | 3 | 2026-03-01 | 2026 | FY26 | 31 | 197.2 | 210.4 |  |  |  | 1184.7899 | 8.0209 | 70.21% | 6.7871 | 0 | 0 | 435.22 | 38.219 | 0 | 2390.2539 | 19.85% |  | 17.01% |  | 8.0209 |  |  |  | 98.04% | 98%
Formulas:
No. of Days in Month = DAY(EOMONTH([Month],0))

## Mod_CL
Sr. No. | Finacial Year | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Date | Cycle Number | Resources | Inv 1 (630kw) unit 1 | Inv 1 (630kw) unit 2 | Inv 1 (630kw) unit 3 | Inv 1 (630kw) unit 4 | Inv 2 (630kw) unit 1 | Inv 2 (630kw) unit 2 | Inv 2 (630kw) unit 3 | Inv 2 (630kw) unit 4 | Inv 3 (630kw) unit 1 | Inv 3 (630kw) unit 2 | Inv 3 (630kw) unit 3 | Inv 3 (630kw) unit 4 | Total NO. Module cleaned | Morning Start Time | Morning End Time | Evening Start Time | Evening End time | Brush/MOP Replcemnet | Water Test Report | Remarks for the day
1 | 2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | 2025-03-29 | [14 empty] | 0 | [6 empty] | Due to Rain module cleaning not done
2 | 2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | 2025-03-30 | [14 empty] | 0 | [6 empty] | Due to Rain module cleaning not done
3 | 2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | 2025-03-31 | [14 empty] | 0 | [6 empty] | Due to Rain module cleaning not done
4 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-01 | 1 | 2 | 2160 | 2160 | 2160 | 2160 | [8 empty] | 8640
5 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-02 | 1 | 2 |  |  |  |  | 2160 | 2160 | 2160 | 2160 |  |  |  |  | 8640
6 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-03 | 1 | 2 | [8 empty] | 2160 | 2160 | 2160 | 2160 | 8640
7 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-04 | 2 | 2 | 2160 | 2160 | 2160 | 2160 | [8 empty] | 8640
8 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-05 | 2 | 2 |  |  |  |  | 2160 | 2160 | 2160 | 2160 |  |  |  |  | 8640
9 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-06 | [14 empty] | 0 | [6 empty] | Helpers Taken Weekly OFF
10 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-07 | 2 | 2 | [8 empty] | 2160 | 2160 | 2160 | 2160 | 8640
11 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-08 | 3 | 2 | 2160 | 2160 | 2160 | 2160 | [8 empty] | 8640
12 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-09 | 3 | 2 |  |  |  |  | 2160 | 2160 | 2160 | 2160 |  |  |  |  | 8640
13 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-10 | 3 | 2 | [8 empty] | 2160 | 2160 | 2160 | 2160 | 8640
14 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-11 | 4 | 2 | 2160 | 2160 | 2160 | 2160 | [8 empty] | 8640
15 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-12 | 4 | 2 |  |  |  |  | 2160 | 2160 | 2160 | 2160 |  |  |  |  | 8640
16 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-13 | 4 | 2 | [12 empty] | 0 | [6 empty] | Helpers Taken Weekly OFF
17 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-14 | 4 | 2 | [8 empty] | 2160 | 2160 | 2160 | 2160 | 8640
18 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-15 | 5 | 2 | 2160 | 2160 | 2160 | 2160 | [8 empty] | 8640
19 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-16 | 5 | 2 |  |  |  |  | 2160 | 2160 | 2160 | 2160 |  |  |  |  | 8640
20 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-17 | 5 | 2 | [12 empty] | 0 | [6 empty] | Not Done Due to Rain
21 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-18 | 5 | 2 | [8 empty] | 2160 | 2160 | 2160 | 2160 | 8640
22 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-19 | 6 | 2 | [12 empty] | 0 | [6 empty] | Not Done Due to Rain
23 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-20 | 6 | 2 | [12 empty] | 0
24 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-21 | 6 | 2 | 2160 | 2160 | 2160 | 2160 | [8 empty] | 8640
25 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-22 | 6 | 2 | [12 empty] | 0 | [6 empty] | Not Done Due to Rain
26 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-23 | 6 | 2 |  |  |  |  | 2160 | 2160 | 2160 | 2160 |  |  |  |  | 8640
27 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-24 | 6 | 2 | [8 empty] | 2160 | 2160 | 2160 | 2160 | 8640
28 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-25 | 7 | 2 | 2160 | 2160 | 2160 | 2160 | [8 empty] | 8640
29 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-26 | 7 | 2 |  |  |  |  | 2160 | 2160 | 2160 | 2160 |  |  |  |  | 8640
30 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-27 | 7 | 2 | [12 empty] | 0 | [6 empty] | Helpers Taken Weekly OFF
31 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-28 | 7 | 2 | [8 empty] | 2160 | 2160 | 2160 | 2160 | 8640
32 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-29 | 8 | 2 | 2160 | 2160 | 2160 | 2160 | [8 empty] | 8640
33 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-30 | 8 | 2 |  |  |  |  | 2160 | 2160 | 2160 | 2160 |  |  |  |  | 8640
34 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-01 | 1 | 2 | 2160 | 2160 | 2160 | 2160 | [8 empty] | 8640
35 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-02 | 1 | 2 |  |  |  |  | 2160 | 2160 | 2160 | 2160 |  |  |  |  | 8640
36 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-03 | 1 | 2 | [8 empty] | 2160 | 2160 | 2160 | 2160 | 8640
37 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-04 | 2 | 2 | [12 empty] | 0 | [6 empty] | Helpers Taken Weekly OFF
38 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-05 | 2 | 2 | 2160 | 2160 | 2160 | 2160 | [8 empty] | 8640
39 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-06 | 2 | 2 |  |  |  |  | 2160 | 2160 | 2160 | 2160 |  |  |  |  | 8640
40 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-07 | 2 | 2 | [8 empty] | 2160 | 2160 | 2160 | 2160 | 8640
41 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-08 | 3 | 2 | 2160 | 2160 | 2160 | 2160 | [8 empty] | 8640
42 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-09 | 3 | 2 |  |  |  |  | 2160 | 2160 | 2160 | 2160 |  |  |  |  | 8640
43 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-10 | 3 | 2 | [8 empty] | 2160 | 2160 | 2160 | 2160 | 8640
44 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-11 | 4 | 2 | 2160 | 2160 | 2160 | 2160 | [8 empty] | 8640
45 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-12 | 4 | 2 |  |  |  |  | 2160 | 2160 | 2160 | 2160 |  |  |  |  | 8640
46 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-13 | 4 | 2 | [8 empty] | 2160 | 2160 | 2160 | 2160 | 8640
47 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-14 | 5 | 2 | 2160 | 2160 | 2160 | 2160 | [8 empty] | 8640
48 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-15 | 5 | 2 |  |  |  |  | 2160 | 2160 | 2160 | 2160 |  |  |  |  | 8640
49 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-16 | 5 | 2 | [8 empty] | 2160 | 2160 | 2160 | 2160 | 8640
50 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-17 | 6 | 2 | 2160 | 2160 | 2160 | 2160 | [8 empty] | 8640
51 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-18 | 6 | 2 | [12 empty] | 0 | [6 empty] | Helpers Taken Weekly OFF
52 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-19 | 6 | 2 |  |  |  |  | 2160 | 2160 | 2160 | 2160 |  |  |  |  | 8640
53 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-20 | 6 | 2 | [8 empty] | 2160 | 2160 | 2160 | 2160 | 8640
54 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-21 | 7 | 2 | 2160 | 2160 | 2160 | 2160 | [8 empty] | 8640
55 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-22 | 7 | 2 |  |  |  |  | 2160 | 2160 | 2160 | 2160 |  |  |  |  | 8640
56 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-23 | 7 | 2 | [8 empty] | 2160 | 2160 | 2160 | 2160 | 8640
57 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-24 | 8 | 2 | 2160 | 2160 | 2160 | 2160 | [8 empty] | 8640
58 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-25 | 8 | 2 | [12 empty] | 0 | [6 empty] | Helpers Taken Weekly OFF
59 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-26 | 8 | 2 |  |  |  |  | 2160 | 2160 | 2160 | 2160 |  |  |  |  | 8640
60 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-27 | 8 | 2 | [8 empty] | 2160 | 2160 | 2160 | 2160 | 8640
61 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-28 | 9 | 2 | 2160 | 2160 | 2160 | 2160 | [8 empty] | 8640
62 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-29 | 9 | 2 |  |  |  |  | 2160 | 2160 | 2160 | 2160 |  |  |  |  | 8640
63 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-30 | 9 | 2 | [8 empty] | 2160 | 2160 | 2160 | 2160 | 8640
64 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-31 | 10 | 2 | 2160 | 2160 | 2160 | 2160 | [8 empty] | 8640
65 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-01 | 1 | 2 | [12 empty] | 0 | [6 empty] | Helpers Taken Weekly OFF
66 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-02 | 1 | 2 | 2160 | 2160 | 2160 | 2160 | [8 empty] | 8640
67 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-03 | 1 | 2 |  |  |  |  | 2160 | 2160 | 2160 | 2160 |  |  |  |  | 8640
68 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-04 | 2 | 2 | 2160 | 2160 | 2160 | 2160 | [8 empty] | 8640
69 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-05 | 2 | 2 |  |  |  |  | 2160 | 2160 | 2160 | 2160 |  |  |  |  | 8640
70 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-06 | 2 | 2 | [8 empty] | 2160 | 2160 | 2160 | 2160 | 8640
71 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-07 | 3 | 2 | 2160 | 2160 | 2160 | 2160 | [8 empty] | 8640
72 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-08 | 3 | 2 | [12 empty] | 0 | [6 empty] | Helpers Taken Weekly OFF
73 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-09 | 3 | 2 | [12 empty] | 0 | [6 empty] | Not Done Due to Rain
74 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-10 | 3 | 2 |  |  |  |  | 2160 | 2160 | 2160 | 2160 |  |  |  |  | 8640
75 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-11 | [14 empty] | 0
Formulas:
Days = DAY(EOMONTH(Mod_CL[[#This Row],[Month Year]],0))
Date = [Date, row above]+1

## Grass_Cutting
Sr. No. | Finacial Year | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Date | Cycle Number | Resources | Inv1 | Inv2 | Inv3 | Total Number of Table cut | Remarks for the day
1 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-01 | [5 empty] | 0
2 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-02 | [5 empty] | 0
3 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-03 | [5 empty] | 0
4 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-04 | [5 empty] | 0
5 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-05 | [5 empty] | 0
6 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-06 | [5 empty] | 0
7 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-07 | [5 empty] | 0
8 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-08 | [5 empty] | 0
9 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-09 | [5 empty] | 0
10 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-10 | [5 empty] | 0
11 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-11 | [5 empty] | 0
12 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-12 | [5 empty] | 0
13 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-13 | [5 empty] | 0
14 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-14 | [5 empty] | 0
15 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-15 | [5 empty] | 0
16 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-16 | [5 empty] | 0
17 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-17 | [5 empty] | 0
18 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-18 | [5 empty] | 0
19 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-19 | [5 empty] | 0
20 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-20 | [5 empty] | 0
21 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-21 | [5 empty] | 0
Formulas:
Days = DAY(EOMONTH([Month Year],0))
Date = [Date, row above]+1

## Spare_Consumable
Sr. No. | Finacial Year | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Date | Item Consumed | Qty Consumed | Place of Consumption | Ownership of Spare/Consumable | Remarks for the day
1 | 2026 | 2025 | 2024-2025 | 2025 | 2025-01-26 |  | 2025-04-01
2 | 2026 | 2025 | 2024-2025 | 2025 | 2025-01-26 |  | 2025-04-02
3 | 2026 | 2025 | 2024-2025 | 2025 | 2025-01-26 |  | 2025-04-03
4 | 2026 | 2025 | 2024-2025 | 2025 | 2025-01-26 |  | 2025-04-04
5 | 2026 | 2025 | 2024-2025 | 2025 | 2025-01-26 |  | 2025-04-05
6 | 2026 | 2025 | 2024-2025 | 2025 | 2025-01-26 |  | 2025-04-06
7 | 2026 | 2025 | 2024-2025 | 2025 | 2025-01-26 |  | 2025-04-07