## O2Summary
Performance Summary PWEGPL
Month | 2025-06-01
Date | 2025-06-12
Financial Year | Year-3
Year Start Date | 2025-04-01
Year End Date | 2026-03-31
Sr. No. | Particular | Target | Measured | Deviation | Remarks
1 | E_Grid Daily (MWh) | 501.2753 | 420 | -16.21%
| E_Grid MTD(MWh) | 6015.3041 | 6106.8 | 1.521%
| E_Grid YTD (MWh) | 33551.9985 | 25573.2 | -23.78%
2 | Wind Speed Daily | 5.6311 | 4.6823 | -16.85%
| Wind Speed MTD | 5.6311 | 5.2195 | -7.31%
| Wind Speed YTD | 6.0011 | 4.6888 | -21.87%
3 | PA Daily | 96.03% | 94.32% | -1.782%
| PA MTD | 96.03% | 92.93% | -3.23%
| PA YTD | 96.03% | 92.16% | -4.033%
4 | MA Daily | 97% | 94.32% | -2.764%
| MA MTD | 97% | 94.17% | -2.914%
| MA YTD | 97% | 92.85% | -4.274%
5 | EGA Daily | 99.5% | 100% | 0.5025%
| EGA MTD | 99.5% | 100% | 0.5025%
| EGA YTD | 99.5% | 100% | 0.5025%
6 | IGA Daily | 99% | 100% | 1.01%
| IGA MTD | 99% | 98.68% | -0.3256%
| IGA YTD | 99% | 99.25% | 0.251%
7 | CUF Daily | 26.78% | 22.44% | -16.21%
| CUF MTD | 26.78% | 27.18% | 1.521%
| CUF YTD | 24.55% | 18.71% | -23.78%
8 | Line Loss Daily | 5% | 1.442% | 71.17%
| Line Loss MTD | 5% | 1.015% | 79.7%
| Line Loss YTD | 5% | 1.806% | 63.89%
9 | Reactive Power Daily | 5% | 0.001407% | 99.97%
| Reactive Power MTD | 5% | 0.0005422% | 99.99%
| Reactive Power YTD | 5% | 0.00593% | 99.88%
10 | Expected Energy Daily | 428.57 | 428.579 | 0.0021%
| Expected Energy MTD | 6163.32 | 6163.384 | 0.001038%
| Expected Energy YTD | 26036.988 | 26059.81 | 0.08765%

## AnnualKPI
Till Date | 2025-06-12 | 2025-06-01
PWEGPL Performance Summary-YTD
Year | Days | Estimated WS(m/s) | Measured WS (m/s) | Budgeted Energy (MWh) | Measured Energy (MWh) | Target CUF (%) | Measured CUF (%) | Target GA (%) | Measured GA (%) | Target MA (%) | Measured MA (%) | Target IGA(%) | Measured IGA (%) | Target PA(%) | Measured PA (%) | Expected Energy | Loss (%) | Reactive Power (%)
2026 | 73 | 6.0011 | 4.6888 | 33551.9985 | 25573.2 | 24.55% | 18.71% | 99.5% | 100% | 97% | 92.85% | 99% | 99.25% | 96.03% | 92.16% | 26036.988 | 1.806% | 0.00593%

## MonthlyKPI
Till Date | 2025-06-12 | 0 | 0 | 0 | 0
PWEGPL Performance Summary (MTD)
Year | Days | Estimated WS(m/s) | Measured WS (m/s) | Budgeted Energy (MWh) | Measured Energy (MWh) | Target CUF (%) | Measured CUF (%) | Target GA (%) | Measured GA (%) | Target MA (%) | Measured MA (%) | Target IGA (%) | Measured IGA (%) | Target PA(%) | Measured PA (%) | WTG Total (MWh) | Line Losses(%) | E_WS_Corrected | Expected Energy | Loss (%) | Reactive Power (%)
2025-06-01 | 12 | 5.6311 | 5.2195 | 6015.3041 | 6106.8 | 26.78% | 27.18% | 99.5% | 100% | 97% | 94.17% | 99% | 98.68% | 96.03% | 92.93% | 6163.384 | 0.9266% | 6.1633 | 6163.32 | 1.015% | 0.0005422%
Start Date | 2025-06-06
End Date | 2025-06-12
PWEGPL Performance Summary (WTD)
Year | Days | Estimated WS(m/s) | Measured WS (m/s) | Budgeted Energy (MWh) | Measured Energy (MWh) | Target CUF (%) | Measured CUF (%) | Target GA (%) | Measured GA (%) | Target MA (%) | Measured MA (%) | Target IGA (%) | Measured IGA (%) | Target PA(%) | Measured PA (%) | E_WS_Corrected
2025-06-01 | 7 | 5.6311 | 5.3328 | 3508.9274 | 3790.8 | 26.78% | 28.93% | 99.5% | 100% | 97% | 93.99% | 99% | 99.71% | 96.03% | 93.71% | 3.8288
Start Date | 2025-05-14
End Date | 2025-06-12
PWEGPL Performance Summary (LTD)
Year | Days | Estimated WS(m/s) | Measured WS (m/s) | Budgeted Energy (MWh) | Measured Energy (MWh) | Target CUF (%) | Measured CUF (%) | Target GA (%) | Measured GA (%) | Target MA (%) | Measured MA (%) | Target IGA (%) | Measured IGA (%) | Target PA(%) | Measured PA (%)
2025-06-01 | 30 | 5.6311 | 4.6345 | 16066.2952 | 11270.4 | 28.61% | 20.07% | 99.5% | 100% | 97% | 93.29% | 99% | 98.5% | 96.03% | 91.9%
Formulas:
Days = [Days, row below]-6

## Daily KPI
Date | Financial Year | Calendar Year | Month Year | Days | Operating Hours | GHI-UP (KWh/m2) | GHI-Down(KWh/m2) | POA-UP(KWh/m2) | POA-Down(KWh/m2) | Amb_Temp(°C) | Mod_Temp(°C) | WS_Avg(m/s) | WS_Max(m/s) | PA(%) | MA (%) | IGA (%) | EGA(%) | EMA (%) | TA (%) | PR(%) | WPR(%) | CUF(%) | Gen_Exp (kWh) | Mtr_Export (kWh) | Mtr_Import (kWh) | Mtr_Net_Exp (KWh) | Operational Capacity (MW) | Bugt_Resource | Bugt_Energy | Bugt PR | Bugt CUF | Bugt_PA | Bugt_EGA | Expected Energy | Actual Energy WPR | RA (%) | Mod Clean Dry (Num) | Mod Clean Wet (Num) | Line Loss(%) | Reactive Power (%) | Bugt Line loss (%) (Wind) | Bugt Reactive Power (%) (Wind) | Bugt Capacity | CC*Bugt
2025-03-29 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 3.5474 | 0 | [9 empty] | 125761 |  |  |  | 80 | 4.6 | 257758.0645 |  | 13.42% | 96.03% | 99.5% | 0 |  |  |  |  | 0% | 0% | 5% | 5% | 80
2025-03-30 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 3.5682 | 0 | 92.81% | 92.81% | 100% | 100% |  |  |  |  | 4.938% | 111431 | 99600 | 4800 | 94800 | 80 | 4.6 | 257758.0645 |  | 13.42% | 96.03% | 99.5% | 0 |  |  |  |  | 10.62% | 0% | 5% | 5% | 80
2025-03-31 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 4.391 | 0 | 88.58% | 88.79% | 99.77% | 100% |  |  |  |  | 12.94% | 258117 | 250800 | 2400 | 248400 | 80 | 4.6 | 257758.0645 |  | 13.42% | 96.03% | 99.5% | 0 |  |  |  |  | 2.835% | 0.01852% | 5% | 5% | 80
2025-04-01 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.0569 | 0 | 83.81% | 85.33% | 98.22% | 100% |  |  |  |  | 10.64% | 216864 | 202800 | 3600 | 199200 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 217.953 |  |  |  |  | 6.485% | 0.02213% | 5% | 5% | 78
2025-04-02 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.5428 | 0 | 87.37% | 88.82% | 98.36% | 100% |  |  |  |  | 22.37% | 428910 | 418800 | 0 | 418800 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 422.859 |  |  |  |  | 2.357% | 0.01541% | 5% | 5% | 78
2025-04-03 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.391 | 0 | 90% | 90.31% | 99.65% | 100% |  |  |  |  | 13.21% | 257492 | 250800 | 3600 | 247200 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 255.178 |  |  |  |  | 2.599% | 0.02012% | 5% | 5% | 78
2025-04-04 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.0579 | 0 | 85.6% | 85.6% | 100% | 100% |  |  |  |  | 7.5% | 161561 | 144000 | 3600 | 140400 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 165.1 |  |  |  |  | 10.87% | 0.02802% | 5% | 5% | 78
2025-04-05 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 2.9132 | 0 | 92.5% | 92.5% | 100% | 100% |  |  |  |  | 3.782% | 81163 | 75600 | 4800 | 70800 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 77.212 |  |  |  |  | 6.854% | 0.09428% | 5% | 5% | 78
2025-04-06 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 3.3879 | 0 | 91.34% | 91.34% | 100% | 100% |  |  |  |  | 5.385% | 111449 | 104400 | 3600 | 100800 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 106.019 |  |  |  |  | 6.325% | 0.0396% | 5% | 5% | 78
2025-04-07 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.1233 | 0 | 87.01% | 90.47% | 96.18% | 100% |  |  |  |  | 11.73% | 236100 | 222000 | 2400 | 219600 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 238.176 |  |  |  |  | 5.972% | 0.01324% | 5% | 5% | 78
2025-04-08 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 3.4951 | 0 | 92.26% | 92.26% | 100% | 100% |  |  |  |  | 7.756% | 151284 | 150000 | 4800 | 145200 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 149.33 |  |  |  |  | 0.8487% | 0.02619% | 5% | 5% | 78
2025-04-09 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.8151 | 0 | 89.35% | 89.35% | 100% | 100% |  |  |  |  | 16.35% | 327786 | 308400 | 2400 | 306000 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 327.512 |  |  |  |  | 5.914% | 0.01299% | 5% | 5% | 78
2025-04-10 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.5674 | 0 | 94.53% | 94.53% | 100% | 100% |  |  |  |  | 27.31% | 519730 | 513600 | 2400 | 511200 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 511 |  |  |  |  | 1.179% | 0.0008926% | 5% | 5% | 78
2025-04-11 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.5762 | 0 | 94.23% | 94.23% | 100% | 100% |  |  |  |  | 27.31% | 514588 | 511200 | 0 | 511200 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 514 |  |  |  |  | 0.6584% | 0% | 5% | 5% | 78
2025-04-12 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.4377 | 0 | 94.03% | 94.03% | 100% | 100% |  |  |  |  | 24.81% | 469515 | 465600 | 1200 | 464400 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 469.51 |  |  |  |  | 0.8338% | 0.0007802% | 5% | 5% | 78
2025-04-13 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.8151 | 0 | 94.73% | 94.73% | 100% | 100% |  |  |  |  | 17.63% | 333663 | 331200 | 1200 | 330000 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 333.66 |  |  |  |  | 0.7382% | 0.00143% | 5% | 5% | 78
2025-04-14 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 6.7597 | 0 | 94.68% | 94.68% | 100% | 100% |  |  |  |  | 31.92% | 601869 | 598800 | 1200 | 597600 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 601.869 |  |  |  |  | 0.5099% | 0.000793% | 5% | 5% | 78
2025-04-15 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.9428 | 0 | 93.75% | 93.75% | 100% | 100% |  |  |  |  | 27.95% | 530337 | 526800 | 3600 | 523200 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 530.337 |  |  |  |  | 0.6669% | 0.0009% | 5% | 5% | 78
2025-04-16 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.5674 | 0 | 94.3% | 94.3% | 100% | 100% |  |  |  |  | 29.42% | 552581 | 550800 | 0 | 550800 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 552.581 |  |  |  |  | 0.3223% | 0.0006495% | 5% | 5% | 78
2025-04-17 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.5762 | 0 | 94.45% | 94.45% | 100% | 100% |  |  |  |  | 27.88% | 522462 | 522000 | 0 | 522000 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 522.462 |  |  |  |  | 0.08843% | 0.0006869% | 5% | 5% | 78
2025-04-18 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.8151 | 0 | 93.84% | 93.84% | 100% | 100% |  |  |  |  | 16.86% | 320599 | 316800 | 1200 | 315600 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 320.59 |  |  |  |  | 1.185% | 0.002246% | 5% | 5% | 78
2025-04-19 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.5097 | 0 | 94.17% | 94.17% | 100% | 100% |  |  |  |  | 21.54% | 407326 | 405600 | 2400 | 403200 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 407.32 |  |  |  |  | 0.4237% | 0% | 5% | 5% | 78
2025-04-20 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 6.721 | 0 | 94.18% | 94.18% | 100% | 100% |  |  |  |  | 40.13% | 752099 | 751200 | 0 | 751200 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 752.09 |  |  |  |  | 0.1195% | 0% | 5% | 5% | 78
2025-04-21 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.2598 | 0 | 94.29% | 94.29% | 100% | 100% |  |  |  |  | 15.45% | 299034 | 291600 | 2400 | 289200 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 299.03 |  |  |  |  | 2.486% | 0.002809% | 5% | 5% | 78
2025-04-22 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.0569 | 0 | 93.43% | 93.43% | 100% | 100% |  |  |  |  | 11.35% | 215096 | 213600 | 1200 | 212400 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 215.09 |  |  |  |  | 0.6955% | 0.003905% | 5% | 5% | 78
2025-04-23 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 3.4903 | 0 | 94.25% | 94.25% | 100% | 100% |  |  |  |  | 6.474% | 128167 | 126000 | 4800 | 121200 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 128.16 |  |  |  |  | 1.691% | 0.005618% | 5% | 5% | 78
2025-04-24 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.2944 | 0 | 93.05% | 93.05% | 100% | 100% |  |  |  |  | 10.51% | 203962 | 198000 | 1200 | 196800 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 203.96 |  |  |  |  | 2.923% | 0.004698% | 5% | 5% | 78
2025-04-25 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.2262 | 0 | 93.13% | 93.13% | 100% | 100% |  |  |  |  | 12.76% | 243861 | 242400 | 3600 | 238800 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 243.86 |  |  |  |  | 0.5991% | 0.0009862% | 5% | 5% | 78
2025-04-26 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.8151 | 0 | 94.18% | 94.18% | 100% | 100% |  |  |  |  | 20.13% | 379529 | 376800 | 0 | 376800 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 379.52 |  |  |  |  | 0.719% | 0.0006337% | 5% | 5% | 78
2025-04-27 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.2369 | 0 | 93.4% | 93.4% | 100% | 100% |  |  |  |  | 9.744% | 190112 | 187200 | 4800 | 182400 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 190.11 |  |  |  |  | 1.532% | 0.004418% | 5% | 5% | 78
2025-04-28 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.0569 | 0 | 93.92% | 93.92% | 100% | 100% |  |  |  |  | 14.36% | 271844 | 268800 | 0 | 268800 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 271.84 |  |  |  |  | 1.12% | 0.002205% | 5% | 5% | 78
2025-04-29 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.0569 | 0 | 94.44% | 94.44% | 100% | 100% |  |  |  |  | 14.1% | 271570 | 268800 | 4800 | 264000 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 271.54 |  |  |  |  | 1.02% | 0.002657% | 5% | 5% | 78
2025-04-30 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.9428 | 0 | 93% | 93% | 100% | 100% |  |  |  |  | 31.47% | 590942 | 589200 | 0 | 589200 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 590.94 |  |  |  |  | 0.2948% | 0.000407% | 5% | 5% | 78
2025-05-01 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 5.8867 | 0 | 90.99% | 92.87% | 97.98% | 100% |  |  |  |  | 31.22% | 588285 | 584400 | 0 | 584400 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 588.28 |  |  |  |  | 0.6604% | 0% | 5% | 5% | 78
2025-05-02 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.5097 | 0 | 92.46% | 92.46% | 100% | 100% |  |  |  |  | 25.06% | 491493 | 469200 | 0 | 469200 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 491.49 |  |  |  |  | 4.536% | 0.00122% | 5% | 5% | 78
2025-05-03 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 6.9187 | 0 | 93.55% | 93.55% | 100% | 100% |  |  |  |  | 32.76% | 616130 | 614400 | 1200 | 613200 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 616.13 |  |  |  |  | 0.2808% | 0.0001922% | 5% | 5% | 78
2025-05-04 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.8151 | 0 | 92.91% | 92.91% | 100% | 100% |  |  |  |  | 21.03% | 404176 | 397200 | 3600 | 393600 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 404.17 |  |  |  |  | 1.726% | 0.000595% | 5% | 5% | 78
2025-05-05 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.0569 | 0 | 91.08% | 91.08% | 100% | 100% |  |  |  |  | 14.04% | 266316 | 262800 | 0 | 262800 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 266.31 |  |  |  |  | 1.32% | 0.00219% | 5% | 5% | 78
2025-05-06 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.391 | 0 | 92.29% | 92.37% | 99.91% | 100% |  |  |  |  | 16.03% | 306808 | 304800 | 4800 | 300000 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 306.8 |  |  |  |  | 0.6545% | 0.001173% | 5% | 5% | 78
2025-05-07 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.8151 | 0 | 92.2% | 92.2% | 100% | 100% |  |  |  |  | 17.95% | 351123 | 336000 | 0 | 336000 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 351.12 |  |  |  |  | 4.307% | 0.00137% | 5% | 5% | 78
2025-05-08 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.0569 | 0 | 93.78% | 93.78% | 100% | 100% |  |  |  |  | 16.6% | 315253 | 310800 | 0 | 310800 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 315.25 |  |  |  |  | 1.413% | 0.001138% | 5% | 5% | 78
2025-05-09 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 3.8852 | 0 | 93.01% | 93.01% | 100% | 100% |  |  |  |  | 7.308% | 144826 | 141600 | 4800 | 136800 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 144.82 |  |  |  |  | 2.228% | 0.01078% | 5% | 5% | 78
2025-05-10 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.2369 | 0 | 93.81% | 93.81% | 100% | 100% |  |  |  |  | 10.06% | 194224 | 192000 | 3600 | 188400 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 194.22 |  |  |  |  | 1.145% | 0.005544% | 5% | 5% | 78
2025-05-11 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.8151 | 0 | 90.74% | 90.74% | 100% | 100% |  |  |  |  | 17.82% | 338208 | 334800 | 1200 | 333600 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 338.2 |  |  |  |  | 1.008% | 0.001772% | 5% | 5% | 78
2025-05-12 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 3.5474 | 0 | 88.04% | 88.31% | 99.69% | 100% |  |  |  |  | 5.833% | 112662 | 111600 | 2400 | 109200 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 112.66 |  |  |  |  | 0.9426% | 0.005177% | 5% | 5% | 78
2025-05-13 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.8055 | 0 | 92.61% | 92.61% | 100% | 100% |  |  |  |  | 10.51% | 205550 | 201600 | 4800 | 196800 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 205.55 |  |  |  |  | 1.922% | 0.004086% | 5% | 5% | 78
2025-05-14 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 3.4951 | 0 | 89.49% | 89.49% | 100% | 100% |  |  |  |  | 6.987% | 139230 | 135600 | 4800 | 130800 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 139.23 |  |  |  |  | 2.607% | 0.008378% | 5% | 5% | 78
2025-05-15 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 3.5474 | 0 | 91.09% | 91.09% | 100% | 100% |  |  |  |  | 10.19% | 194666 | 192000 | 1200 | 190800 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 194.66 |  |  |  |  | 1.37% | 0.003079% | 5% | 5% | 78
2025-05-16 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.0569 | 0 | 91.41% | 92.21% | 99.13% | 100% |  |  |  |  | 16.99% | 321526 | 318000 | 0 | 318000 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 321.52 |  |  |  |  | 1.097% | 0.001496% | 5% | 5% | 78
2025-05-17 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 3.8852 | 0 | 89.14% | 91.2% | 97.74% | 100% |  |  |  |  | 9.167% | 176988 | 174000 | 2400 | 171600 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 176.98 |  |  |  |  | 1.688% | 0.002049% | 5% | 5% | 78
2025-05-18 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 3.5474 | 0 | 93.91% | 93.91% | 100% | 100% |  |  |  |  | 6.667% | 131285 | 127200 | 2400 | 124800 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 131.28 |  |  |  |  | 3.112% | 0.006398% | 5% | 5% | 78
2025-05-19 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 3.4951 | 0 | 88.89% | 93.33% | 95.24% | 100% |  |  |  |  | 7.179% | 141695 | 138000 | 3600 | 134400 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 141.69 |  |  |  |  | 2.608% | 0.01355% | 5% | 5% | 78
2025-05-20 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 3.8852 | 0 | 89.47% | 92.58% | 96.64% | 100% |  |  |  |  | 9.231% | 178470 | 176400 | 3600 | 172800 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 178.47 |  |  |  |  | 1.16% | 0.004043% | 5% | 5% | 78
2025-05-21 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 3.5474 | 0 | 91.58% | 92.78% | 98.7% | 100% |  |  |  |  | 9.744% | 191723 | 187200 | 4800 | 182400 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 191.73 |  |  |  |  | 2.359% | 0.002509% | 5% | 5% | 78
2025-05-22 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.8055 | 0 | 92.91% | 92.91% | 100% | 100% |  |  |  |  | 15% | 286041 | 285600 | 4800 | 280800 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 286.08 |  |  |  |  | 0.1542% | 0.00714% | 5% | 5% | 78
2025-05-23 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 2.9906 | 0 | 87.14% | 93.58% | 93.11% | 100% |  |  |  |  | 4.231% | 87964 | 84000 | 4800 | 79200 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 87.96 |  |  |  |  | 4.506% | 0.02048% | 5% | 5% | 78
2025-05-24 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.6823 | 0 | 92.52% | 93.17% | 99.31% | 100% |  |  |  |  | 13.59% | 261720 | 258000 | 3600 | 254400 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 261.72 |  |  |  |  | 1.421% | 0.002304% | 5% | 5% | 78
2025-05-25 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 3.8852 | 0 | 94.28% | 94.28% | 100% | 100% |  |  |  |  | 12.31% | 236447 | 231600 | 1200 | 230400 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 236.44 |  |  |  |  | 2.05% | 0.002551% | 5% | 5% | 78
2025-05-26 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 3.4951 | 0 | 92.83% | 92.83% | 100% | 100% |  |  |  |  | 7.179% | 140266 | 138000 | 3600 | 134400 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 140.26 |  |  |  |  | 1.616% | 0.006858% | 5% | 5% | 78
2025-05-27 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.8151 | 0 | 88.22% | 92.92% | 94.95% | 100% |  |  |  |  | 23.21% | 436047 | 434400 | 0 | 434400 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 436.04 |  |  |  |  | 0.3777% | 0% | 5% | 5% | 78
2025-05-28 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.5097 | 0 | 91.79% | 91.84% | 99.95% | 100% |  |  |  |  | 22.24% | 424522 | 420000 | 3600 | 416400 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 424.52 |  |  |  |  | 1.065% | 0.001133% | 5% | 5% | 78
2025-05-29 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 5.739 | 0 | 93.02% | 93.18% | 99.83% | 100% |  |  |  |  | 28.4% | 539046 | 531600 | 0 | 531600 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 539.04 |  |  |  |  | 1.381% | 0.0002265% | 5% | 5% | 78
2025-05-30 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 5.2598 | 0 | 94.21% | 94.21% | 100% | 100% |  |  |  |  | 29.36% | 552531 | 549600 | 0 | 549600 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 552.53 |  |  |  |  | 0.5305% | 0.000221% | 5% | 5% | 78
2025-05-31 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 6.7597 | 0 | 89.79% | 93.13% | 96.41% | 100% |  |  |  |  | 44.17% | 829710 | 826800 | 0 | 826800 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 829.71 |  |  |  |  | 0.3507% | 0% | 5% | 5% | 78
2025-06-01 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 6.6618 | 0 | 94.31% | 94.38% | 99.93% | 100% |  |  |  |  | 41.79% | 785959 | 782400 | 0 | 782400 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 785.95 |  |  |  |  | 0.4528% | 0% | 5% | 5% | 78
2025-06-02 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 4.8151 | 0 | 92.56% | 93.46% | 99.03% | 100% |  |  |  |  | 20.26% | 381731 | 379200 | 0 | 379200 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 381.73 |  |  |  |  | 0.663% | 0% | 5% | 5% | 78
2025-06-03 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 5.2598 | 0 | 93.6% | 93.81% | 99.77% | 100% |  |  |  |  | 38.85% | 730526 | 727200 | 0 | 727200 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 730.52 |  |  |  |  | 0.4553% | 0% | 5% | 5% | 78
2025-06-04 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 3.8852 | 0 | 84.61% | 96.74% | 87.46% | 100% |  |  |  |  | 8.397% | 161209 | 157200 | 0 | 157200 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 161.2 |  |  |  |  | 2.487% | 0.001492% | 5% | 5% | 78
2025-06-05 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 4.6823 | 0 | 93.77% | 93.77% | 100% | 100% |  |  |  |  | 14.42% | 275124 | 272400 | 2400 | 270000 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 275.12 |  |  |  |  | 0.9901% | 0.002192% | 5% | 5% | 78
2025-06-06 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 4.8151 | 0 | 94.19% | 94.19% | 100% | 100% |  |  |  |  | 21.22% | 409156 | 397200 | 0 | 397200 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 409.15 |  |  |  |  | 2.922% | 0.0002984% | 5% | 5% | 78
2025-06-07 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 5.2598 | 0 | 94.31% | 94.31% | 100% | 100% |  |  |  |  | 29.36% | 551667 | 549600 | 0 | 549600 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 551.66 |  |  |  |  | 0.3747% | 0% | 5% | 5% | 78
2025-06-08 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 5.4377 | 0 | 93.82% | 95.68% | 98.06% | 100% |  |  |  |  | 30.19% | 567412 | 565200 | 0 | 565200 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 567.41 |  |  |  |  | 0.3898% | 0.0002152% | 5% | 5% | 78
2025-06-09 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 6.9444 | 0 | 93.6% | 93.6% | 100% | 100% |  |  |  |  | 44.04% | 826022 | 824400 | 0 | 824400 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 826.02 |  |  |  |  | 0.1964% | 0% | 5% | 5% | 78
2025-06-10 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 5.3749 | 0 | 93.11% | 93.11% | 100% | 100% |  |  |  |  | 29.36% | 554892 | 552000 | 2400 | 549600 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 554.89 |  |  |  |  | 0.5212% | 0.0006535% | 5% | 5% | 78
2025-06-11 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 4.8151 | 0 | 92.61% | 92.71% | 99.89% | 100% |  |  |  |  | 25.9% | 491107 | 484800 | 0 | 484800 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 491.1 |  |  |  |  | 1.284% | 0.0002486% | 5% | 5% | 78
2025-06-12 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 4.6823 | 0 | 94.32% | 94.32% | 100% | 100% |  |  |  |  | 22.44% | 428579 | 422400 | 2400 | 420000 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 428.57 |  |  |  |  | 1.442% | 0.001407% | 5% | 5% | 78
2025-06-13 | 2026 | 2025 | 2025-06-01 | 30 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 0 |  |  |  |  | 0% |  | 5% | 5% | 78
2025-06-14 | 2026 | 2025 | 2025-06-01 | 30 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 0 |  |  |  |  | 0% |  | 5% | 5% | 78
2025-06-15 | 2026 | 2025 | 2025-06-01 | 30 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 0 |  |  |  |  | 0% |  | 5% | 5% | 78
2025-06-16 | 2026 | 2025 | 2025-06-01 | 30 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-06-17 | 2026 | 2025 | 2025-06-01 | 30 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-06-18 | 2026 | 2025 | 2025-06-01 | 30 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-06-19 | 2026 | 2025 | 2025-06-01 | 30 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-06-20 | 2026 | 2025 | 2025-06-01 | 30 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-06-21 | 2026 | 2025 | 2025-06-01 | 30 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-06-22 | 2026 | 2025 | 2025-06-01 | 30 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-06-23 | 2026 | 2025 | 2025-06-01 | 30 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-06-24 | 2026 | 2025 | 2025-06-01 | 30 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-06-25 | 2026 | 2025 | 2025-06-01 | 30 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-06-26 | 2026 | 2025 | 2025-06-01 | 30 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-06-27 | 2026 | 2025 | 2025-06-01 | 30 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-06-28 | 2026 | 2025 | 2025-06-01 | 30 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-06-29 | 2026 | 2025 | 2025-06-01 | 30 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-06-30 | 2026 | 2025 | 2025-06-01 | 30 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-07-01 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-07-02 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-07-03 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-07-04 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-07-05 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-07-06 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-07-07 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-07-08 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-07-09 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-07-10 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-07-11 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-07-12 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-07-13 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-07-14 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-07-15 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-07-16 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-07-17 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-07-18 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-07-19 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-07-20 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-07-21 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-07-22 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-07-23 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-07-24 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-07-25 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-07-26 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-07-27 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-07-28 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-07-29 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-07-30 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-07-31 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-08-01 | 2026 | 2025 | 2025-08-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-08-02 | 2026 | 2025 | 2025-08-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-08-03 | 2026 | 2025 | 2025-08-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-08-04 | 2026 | 2025 | 2025-08-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-08-05 | 2026 | 2025 | 2025-08-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-08-06 | 2026 | 2025 | 2025-08-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-08-07 | 2026 | 2025 | 2025-08-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-08-08 | 2026 | 2025 | 2025-08-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-08-09 | 2026 | 2025 | 2025-08-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-08-10 | 2026 | 2025 | 2025-08-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-08-11 | 2026 | 2025 | 2025-08-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-08-12 | 2026 | 2025 | 2025-08-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-08-13 | 2026 | 2025 | 2025-08-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-08-14 | 2026 | 2025 | 2025-08-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-08-15 | 2026 | 2025 | 2025-08-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | 0 | [6 empty] | 5% | 5% | 78
2025-08-16 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-08-17 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-08-18 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-08-19 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-08-20 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-08-21 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-08-22 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-08-23 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-08-24 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-08-25 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-08-26 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-08-27 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-08-28 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-08-29 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-08-30 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-08-31 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-01 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-02 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-03 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-04 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-05 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-06 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-07 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-08 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-09 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-10 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-11 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-12 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-13 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-14 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-15 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-16 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-17 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-18 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-19 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-20 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-21 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-22 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-23 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-24 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-25 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-26 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-27 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-28 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-29 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-30 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-01 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-02 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-03 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-04 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-05 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-06 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-07 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-08 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-09 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-10 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-11 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-12 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-13 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-14 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-15 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-16 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-17 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-18 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-19 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-20 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-21 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-22 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-23 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-24 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-25 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-26 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-27 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-28 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-29 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-30 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-31 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-01 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-02 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-03 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-04 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-05 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-06 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-07 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-08 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-09 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-10 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-11 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-12 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-13 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-14 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-15 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-16 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-17 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-18 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-19 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-20 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-21 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-22 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-23 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-24 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-25 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-26 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-27 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-28 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-29 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-30 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-01 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-02 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-03 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-04 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-05 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-06 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-07 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-08 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-09 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-10 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-11 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-12 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-13 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-14 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-15 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-16 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-17 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-18 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-19 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-20 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-21 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-22 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-23 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-24 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-25 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-26 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-27 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-28 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-29 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-30 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-31 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-01 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-02 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-03 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-04 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-05 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-06 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-07 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-08 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-09 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-10 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-11 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-12 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-13 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-14 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-15 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-16 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-17 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-18 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-19 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-20 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-21 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-22 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-23 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-24 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-25 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-26 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-27 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-28 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-29 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-30 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-31 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-01 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-02 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-03 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-04 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-05 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-06 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-07 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-08 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-09 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-10 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-11 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-12 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-13 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-14 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-15 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-16 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-17 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-18 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-19 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-20 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-21 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-22 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-23 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-24 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-25 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-26 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-27 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-28 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-01 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-02 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-03 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-04 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-05 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-06 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-07 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-08 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-09 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-10 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-11 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-12 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-13 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-14 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-15 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-16 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-17 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-18 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-19 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-20 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-21 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-22 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-23 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-24 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-25 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-26 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-27 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-28 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-29 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-30 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-31 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
Formulas:
Month Year = Table13[[#This Row],[Date]]-DAY(Table13[[#This Row],[Date]])+1
Days = DAY(EOMONTH([Date],0))
Date = [Date, row above]+1

## Analytices
Start Date | 2025-06-12
End Date | 2025-06-12 | 24 | 5
WTG No. | G01 | G02 | G03 | G04 | G05 | G06 | G07 | G08 | G09 | G10 | G11 | G12 | G13 | G14 | G15 | G16 | G17 | G18 | G19 | G20 | G21 | G22 | G23 | G25 | G26 | G27 | G28 | G29 | G30 | G31 | G32 | G33 | G34 | G35 | G36 | G37 | G38 | G39 | G40
MA | 69.38% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 94.44% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0.001157% | 100% | 0.001157% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 96.74%
WTG BD Hours | 7.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.9997 | 0 | 23.9997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.78333
IGA | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
METERING YARD
FEEDER | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OG
TRANSFER | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
USS
EGA | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
External Grid | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Generation | 12983 | 14968 | 14951 | 14966 | 9811 | 14959 | 14931 | 14967 | 12731 | 14972 | 14981 | 12735 | 12738 | 12741 | 12762 | 12758 | 12764 | 12760 | 12772 | 12775 | 9837 | 9831 | 9828 | 9855 | 8970 | 9850 | 9862 | 0 | 9868 | 0 | 8985 | 8957 | 8958 | 8951 | 8962 | 8959 | 8948 | 8964 | 8969
PA | 69.38% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 94.44% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0.001157% | 100% | 0.001157% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 96.74%
Sum of BD | 7.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.9997 | 0 | 23.9997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.78333
Count of BD | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
MTTR WTG | 7.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.9997 | 0 | 23.9997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.78333
MTBF WTG | 16.65 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 22.6667 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 0.00027778 | 24 | 0.00027778 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 23.2167
WS (M/S) | 4.9 | 5.3 | 4.7 | 5.1 | 5 | 5.1 | 4.8 | 4.5 | 5.1 | 4.8 | 5.3 | 5 | 5.2 | 5.2 | 5 | 5.4 | 5 | 5.5 | 5.4 | 5.7 | 0 | 5.3 | 4.8 | 5 | 5.3 | 5 | 5 | 0 | 4.8 | 0 | 5 | 5 | 5 | 5.2 | 5.2 | 4.9 | 5.2 | 4.9 | 5.2
Fault Analysis
2023-04-01
|  |  | Put hour Here |  | Default hour for full Data
|  |  | 19272 |  | 19272
Finacial Year | (Multiple Items)
Row Labels | Sum of Breakdown Time | Count of Error Text | MTTR | MTBF
Active Crowbar Failure | 0.21667 | 1 | 0.21667 | 19272
Active Crowbar IGBT Errors | 9.3333 | 2 | 4.6667 | 9636
Analogue Card Failure | 6.0667 | 2 | 3.0333 | 9636
Automatic Secondaries Not OK Too Long | 33.9333 | 20 | 1.6967 | 963.6
Automatic Unwinding | 14.6167 | 7 | 2.0881 | 2753.1429
Blade Position Meas. Error | 22.4167 | 6 | 3.7361 | 3212
Bus Error - Interbus Failure | 325.7333 | 93 | 3.5025 | 207.2258
Bus Preload Protection Thermal Relay Failure | 31.2833 | 12 | 2.6069 | 1606
CAN Communication Failure | 30.95 | 19 | 1.6289 | 1014.3158
CCW Feedback Failure | 72.8167 | 10 | 7.2817 | 1927.2
Change Pause-Remote Control Reset | 5.1667 | 1 | 5.1667 | 19272
Controlled Emergency Series Battery Failure | 13.3167 | 5 | 2.6633 | 3854.4
Converter High Ambient Temperature Alarm | 0.41667 | 1 | 0.41667 | 19272
Coolant Of The Coolant Circuit Failure | 0.33333 | 2 | 0.16667 | 9636
CW Feedback Failure | 40.2667 | 13 | 3.0974 | 1482.4615
DTD Filter Alarm 1 | 9.9667 | 7 | 1.4238 | 2753.1429
Emergency Series HUB Trigger | 45.1333 | 18 | 2.5074 | 1070.6667
Emergency Series Not OK | 1.9 | 2 | 0.95 | 9636
Error In Phase R Of The Inverter | 9.9833 | 4 | 2.4958 | 4818
Error In Phase S Of The Inverter | 13.5 | 2 | 6.75 | 9636
Error In Phase T Of The Inverter | 3.25 | 2 | 1.625 | 9636
Error In Phase T Of The Rectifier | 14.8667 | 4 | 3.7167 | 4818
Excess Current Phase R Of Stator | 1.5167 | 1 | 1.5167 | 19272
Excessive Temperature Of Coolant At The Input Of The Cooling Circuit | 0.36667 | 1 | 0.36667 | 19272
Excessive Temperature Of The Control Module | 7.0833 | 3 | 2.3611 | 6424
Failure Of The Contactor's Rotor Power | 13.0667 | 19 | 0.68772 | 1014.3158
Frequency Failure | 2.35 | 2 | 1.175 | 9636
Gearbox Fan Thermal Relays | 50.6833 | 11 | 4.6076 | 1752
Gearbox Pump Thermal Relay Triggered and High Gearbox Oil Temperature | 6.6667 | 2 | 3.3333 | 9636
Generator Fans Thermal Relay Triggered Too Long | 8 | 7 | 1.1429 | 2753.1429
Generator NDE Bearing High Temperature Alarm | 7.0833 | 8 | 0.88542 | 2409
Generator Slipping Ring High Temperature | 45.05 | 18 | 2.5028 | 1070.6667
Grid Voltage Failure | 169 | 71 | 2.3803 | 271.4366
Heating Protection Triggered | 3.6333 | 2 | 1.8167 | 9636
Heating/Coolant Thermal Magnetic Failure | 107.5833 | 18 | 5.9769 | 1070.6667
High Gearbox Oil Temperature | 3.8833 | 2 | 1.9417 | 9636
High Generator Speed | 0.46667 | 1 | 0.46667 | 19272
High Generator Winding Temperature | 21.8833 | 11 | 1.9894 | 1752
High Grid Harmonic Distortion | 3.55 | 3 | 1.1833 | 6424
High Temperature Of Coolant In The Input Of The Cooling Circuit | 10.4333 | 5 | 2.0867 | 3854.4
High Yaw Brake Pressure | 120.0833 | 23 | 5.221 | 837.913
HU Pump Drive Failure | 48.4333 | 12 | 4.0361 | 1606
Hydraulic Oil High Temperature | 40.05 | 13 | 3.0808 | 1482.4615
Low Level Hydraulic Group Refrigeration Oil | 917.15 | 200 | 4.5858 | 96.36
Low Pitch Value In Stop Mode (1 Cylinder) | 147.4167 | 7 | 21.0595 | 2753.1429
Low Pressure Of Emergency Accumulators | 35.8 | 10 | 3.58 | 1927.2
Low Pressure On Hydraulic Group | 152.7167 | 47 | 3.2493 | 410.0426
Magnetothermic Of The Stator Protection Failure Or Door Open | 15.9167 | 4 | 3.9792 | 4818
Magnetothermic Trigger Of The Stator Protection | 74.6333 | 34 | 2.1951 | 566.8235
Manual Stop | 241.3161 | 69 | 3.4973 | 279.3043
Max. Pump time | 12.2333 | 4 | 3.0583 | 4818
OGS | 25.3333 | 6 | 4.2222 | 3212
Orienting and High Yaw Brake Pressure | 20.6833 | 5 | 4.1367 | 3854.4
Orienting and Low Yaw Brake Pressure | 4.9833 | 1 | 4.9833 | 19272
Overheating In The Grid's Inductance | 3.5167 | 3 | 1.1722 | 6424
Pitch Drive Error | 287.5333 | 50 | 5.7507 | 385.44
PLC Module Failure | 29.3833 | 12 | 2.4486 | 1606
PLC-Converter Communication Error | 420.55 | 64 | 6.5711 | 301.125
Preload Failure | 24.2833 | 8 | 3.0354 | 2409
Rotor Or Generator High Speed in STOP Or EMERGENCY | 9.15 | 3 | 3.05 | 6424
Rotor Protection Thermal Magnetic Failure | 3.6 | 1 | 3.6 | 19272
Rotor Speed Reading Failure | 7.2333 | 4 | 1.8083 | 4818
Speed Read Incorrectly | 92.7833 | 15 | 6.1856 | 1284.8
Temp. Measurement Module Failure | 4.2333 | 3 | 1.4111 | 6424
Top Emergency Button | 2.6833 | 4 | 0.67083 | 4818
Trafo Fan Thermal Relay Triggered Too Long | 8.5333 | 10 | 0.85333 | 1927.2
Very High Disalignment | 5.6667 | 1 | 5.6667 | 19272
Very Low Pressure On Hydraulic Unit | 33.9167 | 11 | 3.0833 | 1752
Vibration Sensor | 22.5833 | 4 | 5.6458 | 4818
Wear Brushes Generator Triggered Too Long | 6.65 | 5 | 1.33 | 3854.4
Wind Vane Failure Alarm | 3.1667 | 1 | 3.1667 | 19272
Yaw Contactor Active | 12.0333 | 4 | 3.0083 | 4818
Yaw Motors Error | 74.65 | 24 | 3.1104 | 803
Yaw Motors Over Current Protection | 11.0833 | 5 | 2.2167 | 3854.4
Yaw Sensor Wiring Error | 79.4833 | 40 | 1.9871 | 481.8
Yawing Motor Thermal Relays | 9.8333 | 3 | 3.2778 | 6424
Yawing Sensor Failure | 9.2167 | 2 | 4.6083 | 9636
(blank) | 0 |  | #DIV/0! | #DIV/0!
Stator Contactor Failure | 4.9 | 1 | 4.9 | 19272
Hydraulic Filter Dirty | 1.5833 | 1
Slipping Rings Fan Or Heating Resistor Failure | 9.1667 | 3
Gearbox Oil High Temperature Warning | 46.4167 | 15
Difference Between 2 Blades Too High | 69.3167 | 12
Low Bus Voltage | 12.0833 | 1
Change Emergency-Local Reset | 7.5167 | 1
Trigger Of Overvoltage Protection | 8.05 | 1
Initialization Failure | 20.9167 | 3
Gearbox Oil Level Low | 97.3833 | 27
SF6 Breaker Fault | 751.8167 | 49
Low Pressure On Brake Circuit | 6.5 | 2
Transmission Line Related work | 141.1333 | 74
Manual Stop - Preventive Maintenance Activity | 1141.2667 | 151
Manual Stop - Audit | 626.25 | 174
Minimum Hydraulic Unit Temperature | 27.3831 | 8
Generator DE Bearing High Temperature Alarm | 19.45 | 2
Generator's Fans Failure Confirmation | 37.8667 | 19
Low Pressure In Gearbox | 7.55 | 4
Fault In 24v Power Supply | 0.61667 | 1
Out Of Range In Slippage | 6.6667 | 1
High Gearbox Bearing Temperature | 28.1167 | 8
Gearbox Pump Thermal Relay | 8.7167 | 5
Major BD - Transformer | 1528.415 | 65
Major BD - Blade | 3511.6667 | 148
Failure In The Gearbox Oil Particle Sensor | 61.5667 | 6
Rectifier Phase S Overcurrent | 86.9667 | 5
UPS breakdown | 3.3167 | 13
Maximum Synchronization Time | 2.4 | 1
Encoder Suynchronism Error | 16.7667 | 6
Transformer Fan Control Failure | 2.9 | 1
Encoder Not OK | 37.05 | 5
Maximum Time For Stator Disconnection | 2.9333 | 2
High Rotor Speed | 326.2167 | 16
Magnetothermic Trigger Of The Line Protection | 4.5667 | 1
Hydraulic Pump Protection | 25.15 | 4
Gearbox Bearing High Temperature Warning | 28.6 | 3
Max Orientation Time | 7.9667 | 2
General Work Stoppage | 85.9167 | 34
Gearbox Fan Feedback Failure | 3.4833 | 2
Automatics Not Ok | 0.45 | 1
Gearbox Fan Thermal Relays Triggered and High Gearbox Oil Temperature | 9.05 | 3
Wear Brushes Generator | 6.5 | 3
Hydraulic Unit Cooling Failure | 4.7667 | 1
SF6 and HV side | 230.8333 | 50
Fault In Analog Electronic Power Supply | 4.7 | 1
Very High Temperature Of Hydraulic Unit Oil | 2.3833 | 2
High Temperature Of The Control Module | 4.0667 | 1
Grand Total | 13265.5808 | 2069
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.

## Input_Raw
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106
[5 empty] | Energy Generated by individual Turbine | [38 empty] | Wind Speed (M/s) | [42 empty] | Meter Readings | [7 empty] | Calculated Energy Numbers
Date | Finacial Year | Calendor Year | Month Year | Days | G01 | G02 | G03 | G04 | G05 | G06 | G07 | G08 | G09 | G10 | G11 | G12 | G13 | G14 | G15 | G16 | G17 | G18 | G19 | G20 | G21 | G22 | G23 | G25 | G26 | G27 | G28 | G29 | G30 | G31 | G32 | G33 | G34 | G35 | G36 | G37 | G38 | G39 | G40 | WS_G01 | WS_G02 | WS_G03 | WS_G04 | WS_G05 | WS_G06 | WS_G07 | WS_G08 | WS_G09 | WS_G10 | WS_G11 | WS_G12 | WS_G13 | WS_G14 | WS_G15 | WS_G16 | WS_G17 | WS_G18 | WS_G19 | WS_G20 | WS_G21 | WS_G22 | WS_G23 | WS_G25 | WS_G26 | WS_G27 | WS_G28 | WS_G29 | WS_G30 | WS_G31 | WS_G32 | WS_G33 | WS_G34 | WS_G35 | WS_G36 | WS_G37 | WS_G38 | WS_G39 | WS_G40 | WTG Total Gneration (KWh) | Wind Speed Average cumulative (m/S)2 | Wind Speed Max (m/S) | Rain (mm) | 33 kV_Wind_F1_Export reading | 33 kV_Wind_F1_Import reading | 33 kV_Wind_F2_Export_reading | 33 kV_Wind_F2_Import_reading | 33 kV_Wind_F3_Export_Reading | 33 kV_Wind_F3_Import_Reading | 33 kV_Wind_F4_Export Reading | 33 kV_Wind_F4_Import Reading | 33 kV_F1_Total_Export (KWh) | 33 kV_Wind_F1_Import (KWh) | 33 kV_F2_Total_Export (KWh)2 | 33 kV_Wind_F2_Import (KWh) | 33 kV_Wind_F3_Export (KWh) | 33 kV_Wind_F3_Import (KWh)2 | 33 kV_Wind_F4_Export (KWh) | 33 kV_Wind_F4_Import (KWh)2 | 33 kV_Wind_Total_Export (KWh) | 33 kV_Wind_Total_Import (KWh) | 33 kV Line Loss (%) | Forecasting Data count received on Forecasting Portal | Forecasting Penalties (INR) | Expected Energy As Per Power Curve (MWh) | Reactive Energy (MVArH) | Operational Capacity | Column1
2025-03-29 | 2025 | 2025 | 2025-03-01 | 31 | 3576 | 5244 | 3376 | 3992 | 2114 | 3446 | 4316 | 4376 | 3336 | 2784 | 3724 | 4284 | 4556 | 5446 | 4725 | 3332 | 3446 | 3780 | 4017 | 5100 | 4216 | 2780 | 1846 | 2882 | 2546 | 3164 | 2420 | 0 | 2614 | 0 | 2684 | 2107 | 2688 | 2976 | 2792 | 2818 | 2858 | 2612 | 2788 | 3.93 | 3.99 | 3.9 | 3.78 | 3.4 | 4.13 | 3.8 | 4.05 | 3.76 | 3.86 | 4.06 | 3.98 | 4.04 | 4.03 | 3.88 | 4.18 | 3.41 | 4.09 | 4.29 | 4.06 | 4.5 | 3.75 | 3.14 | 3.53 | 3.02 | 3.42 | 3.48 | 0 | 3.31 | 0 | 3.29 | 3.51 | 3.38 | 3.42 | 3.69 | 3.98 | 3.43 | 3.41 | 3.47 | 125761 | 3.5474 |  |  | 237611 | 2156 | 278009 | 2188 | 253479 | 1795 | 289037 | 1839 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0% | 0 | 0 |  |  | 80
2025-03-30 | 2025 | 2025 | 2025-03-01 | 31 | 2552 | 3752 | 2170 | 3336 | 2196 | 2804 | 3645 | 3288 | 3376 | 3000 | 2864 | 3892 | 3398 | 3550 | 3998 | 3892 | 3980 | 3348 | 3505 | 3775 | 3630 | 2556 | 1802 | 2822 | 2672 | 2662 | 1552 | 0 | 2712 | 0 | 2760 | 2289 | 2512 | 2838 | 3150 | 2882 | 2772 | 2708 | 2791 | 3.21 | 3.42 | 3.52 | 3.63 | 3.23 | 3.53 | 3.4 | 3.17 | 3.02 | 3.2 | 3.52 | 3.17 | 4.36 | 4.09 | 4.46 | 4.36 | 4.67 | 4.28 | 4.44 | 4.5 | 4.11 | 3.93 | 4.13 | 4.08 | 3.47 | 3.92 | 3.89 | 0 | 3.8 | 0 | 3.61 | 3.69 | 3.51 | 3.72 | 3.87 | 3.73 | 3.54 | 3.45 | 3.53 | 111431 | 3.5682 |  |  | 237629 | 2157 | 278030 | 2189 | 253501 | 1796 | 289059 | 1840 | 21600 | 1200 | 25200 | 1200 | 26400 | 1200 | 26400 | 1200 | 99600 | 4800 | 10.62% | 96 | 2931 |  |  | 80
2025-03-31 | 2025 | 2025 | 2025-03-01 | 31 | 9436 | 10444 | 8994 | 7992 | 5532 | 8810 | 6040 | 8864 | 8552 | 7384 | 9876 | 5883 | 7698 | 7408 | 6173 | 7064 | 8016 | 6908 | 8564 | 10477 | 6850 | 3920 | 4886 | 7082 | 5480 | 6348 | 6006 | 0 | 4162 | 0 | 5080 | 6703 | 7996 | 4764 | 4792 | 5596 | 6680 | 7552 | 4105 | 4.76 | 4.88 | 4.8 | 4.65 | 4.27 | 5.04 | 5.09 | 4.76 | 4.82 | 4.8 | 4.93 | 4.74 | 4.55 | 4.63 | 4.57 | 4.63 | 4.82 | 4.84 | 4.83 | 5.1 | 4.76 | 4.34 | 4.24 | 4.48 | 4.55 | 4.34 | 4.26 | 0 | 3.79 | 0 | 4.37 | 4.3 | 4.48 | 4.78 | 4.74 | 4.25 | 4.44 | 4.59 | 5.03 | 258117 | 4.391 |  |  | 237670 | 2158 | 278051 | 2189 | 253571 | 1796 | 289136 | 1841 | 49200 | 1200 | 25200 | 0 | 84000 | 0 | 92400 | 1200 | 250800 | 2400 | 2.835% | 96 | 17068 |  |  | 80
2025-04-01 | 2026 | 2025 | 2025-04-01 | 30 | 3664 | 7960 | 5356 | 5976 | 4726 | 7228 | 6951 | 6252 | 5836 | 6356 | 6456 | 6719 | 5686 | 4942 | 4039 | 5316 | 6766 | 6572 | 6788 | 7386 | 5148 | 4276 | 5832 | 7202 | 5834 | 6752 | 6260 | 0 | 3918 | 0 | 5518 | 6091 | 7280 | 5474 | 3390 | 7150 | 5240 | 6772 | 3752 | 4.58 | 4.46 | 3.97 | 4.15 | 3.78 | 4.38 | 4.4 | 4.13 | 4.08 | 3.95 | 4.01 | 4.04 | 3.98 | 3.84 | 3.92 | 3.95 | 4.15 | 4.01 | 3.99 | 4.01 | 3.76 | 3.87 | 3.95 | 4.26 | 4.2 | 4.22 | 4.21 | 0 | 5.44 | 0 | 4.17 | 4.15 | 4.32 | 4.55 | 6.32 | 4.45 | 4.87 | 4.31 | 5.39 | 216864 | 4.0569 |  |  | 237715 | 2159 | 278085 | 2190 | 253615 | 1797 | 289182 | 1841 | 54000 | 1200 | 40800 | 1200 | 52800 | 1200 | 55200 | 0 | 202800 | 3600 | 6.485% | 96 | 12280 | 217.953 |  | 78
2025-04-02 | 2026 | 2025 | 2025-04-01 | 30 | 12200 | 10784 | 10570 | 5956 | 11540 | 12082 | 12510 | 12108 | 14236 | 10960 | 14128 | 14485 | 11088 | 12636 | 14796 | 7036 | 15820 | 16424 | 17394 | 17007 | 14520 | 1916 | 11964 | 11672 | 12938 | 10732 | 10142 | 0 | 10722 | 0 | 2722 | 10250 | 11038 | 10894 | 13146 | 11114 | 11404 | 11460 | 8516 | 5.59 | 6.18 | 5.43 | 5.42 | 5.97 | 6.06 | 5.51 | 5.15 | 5.98 | 5.33 | 6.31 | 5.92 | 5.96 | 5.77 | 5.83 | 5.9 | 6.05 | 5.8 | 5.74 | 6.66 | 5.05 | 6.2 | 6.1 | 5.88 | 6 | 5.88 | 5.94 | 0 | 5.74 | 0 | 5.52 | 5.76 | 6.04 | 6.02 | 5.85 | 6.03 | 5.99 | 5.42 | 6.19 | 428910 | 5.5428 |  |  | 237798 | 2159 | 278152 | 2190 | 253699 | 1797 | 289297 | 1841 | 99600 | 0 | 80400 | 0 | 100800 | 0 | 138000 | 0 | 418800 | 0 | 2.357% | 96 | 47311 | 422.859 |  | 78
2025-04-03 | 2026 | 2025 | 2025-04-01 | 30 | 7048 | 9292 | 6462 | 6772 | 7822 | 2735 | 3420 | 6800 | 8864 | 6280 | 7464 | 8930 | 8852 | 8384 | 8346 | 6660 | 10152 | 6368 | 10280 | 9239 | 7800 | 6952 | 7522 | 6640 | 7248 | 6588 | 6354 | 0 | 6816 | 0 | 4938 | 5908 | 3472 | 6490 | 7198 | 6498 | 4518 | 6232 | 6148 | 4.76 | 4.88 | 4.8 | 4.65 | 4.27 | 5.04 | 5.09 | 4.76 | 4.82 | 4.8 | 4.93 | 4.74 | 4.55 | 4.63 | 4.57 | 4.63 | 4.82 | 4.84 | 4.83 | 5.1 | 4.76 | 4.34 | 4.24 | 4.48 | 4.55 | 4.34 | 4.26 | 0 | 3.79 | 0 | 4.37 | 4.3 | 4.48 | 4.78 | 4.74 | 4.25 | 4.44 | 4.59 | 5.03 | 257492 | 4.391 |  |  | 237846 | 2160 | 278199 | 2190 | 253740 | 1798 | 289370 | 1842 | 57600 | 1200 | 56400 | 0 | 49200 | 1200 | 87600 | 1200 | 250800 | 3600 | 2.599% | 96 | 16092 | 255.178 |  | 78
2025-04-04 | 2026 | 2025 | 2025-04-01 | 30 | 5220 | 3700 | 4436 | 884 | 4908 | 879 | 3033 | 4092 | 4356 | 5040 | 5292 | 4980 | 4190 | 5796 | 4270 | 4 | 5176 | 5752 | 5103 | 6702 | 5566 | 5420 | 4696 | 5078 | 4574 | 4378 | 4658 | 0 | 5344 | 0 | 4332 | 4113 | 972 | 5000 | 5438 | 5268 | 4266 | 4168 | 4477 | 4.2 | 4.48 | 4.15 | 4.23 | 4.09 | 4.41 | 4.2 | 4.38 | 4.25 | 4.12 | 4.51 | 4.56 | 4.66 | 4.58 | 4.72 | 4.72 | 4.38 | 4.61 | 4.79 | 4.5 | 4.21 | 4.3 | 4 | 4.35 | 3.93 | 4.2 | 4.18 | 0 | 4.02 | 0 | 4 | 4.03 | 4.05 | 4.25 | 4.25 | 3.98 | 4.05 | 4.03 | 3.89 | 161561 | 4.0579 |  |  | 237878 | 2161 | 278228 | 2191 | 253768 | 1798 | 289401 | 1843 | 38400 | 1200 | 34800 | 1200 | 33600 | 0 | 37200 | 1200 | 144000 | 3600 | 10.87% | 96 | 38147 | 165.1 |  | 78
2025-04-05 | 2026 | 2025 | 2025-04-01 | 30 | 1960 | 2540 | 1912 | 2284 | 1866 | 1710 | 1956 | 2084 | 1724 | 1448 | 1816 | 1786 | 1928 | 1700 | 1532 | 0 | 2102 | 2172 | 2177 | 2192 | 2750 | 2576 | 2268 | 1934 | 2976 | 1682 | 2572 | 0 | 2976 | 0 | 2664 | 2373 | 2528 | 3056 | 2968 | 3038 | 2406 | 2536 | 2971 | 3.1605 | 3.5608 | 3.1151 | 3.3498 | 3.3269 | 3.1994 | 3.1127 | 3.3075 | 3.3208 | 2.8659 | 3.1959 | 3.2102 | 3.4381 | 3.1364 | 3.1875 | 0 | 3.2244 | 3.1802 | 3.1785 | 3.0892 | 3.3397 | 3.33 | 3.1537 | 2.9716 | 3.1007 | 2.7795 | 3.1705 | 0 | 3.0811 | 0 | 3.1179 | 2.8482 | 2.909 | 3.1531 | 3.0024 | 3.149 | 3.0592 | 3.2 | 3.0888 | 81163 | 2.9132 |  |  | 237901 | 2162 | 278244 | 2192 | 253780 | 1799 | 289413 | 1844 | 27600 | 1200 | 19200 | 1200 | 14400 | 1200 | 14400 | 1200 | 75600 | 4800 | 6.854% | 96 | 5488 | 77.212 |  | 78
2025-04-06 | 2026 | 2025 | 2025-04-01 | 30 | 3220 | 3560 | 2644 | 3256 | 3041 | 3480 | 3428 | 3332 | 2736 | 3352 | 3412 | 2747 | 3356 | 3212 | 2079 | 0 | 3500 | 3472 | 3023 | 4229 | 3275 | 3188 | 2686 | 3736 | 2808 | 2780 | 2824 | 0 | 3354 | 0 | 2450 | 2918 | 3590 | 3136 | 3438 | 2096 | 2330 | 2992 | 2769 | 3.93 | 3.99 | 3.9 | 3.78 | 3.4 | 4.13 | 3.8 | 3.5 | 3.76 | 3.86 | 4.06 | 3.98 | 4.04 | 4.03 | 3.88 | 0 | 3.41 | 4.09 | 4.29 | 4.06 | 3.02 | 3.75 | 3.14 | 3.53 | 3.01 | 3.42 | 3.48 | 0 | 3.31 | 0 | 3.29 | 3.51 | 3.38 | 3.42 | 3.69 | 3.98 | 3.43 | 3.41 | 3.47 | 111449 | 3.3879 |  |  | 237924 | 2163 | 278263 | 2193 | 253803 | 1800 | 289435 | 1844 | 27600 | 1200 | 22800 | 1200 | 27600 | 1200 | 26400 | 0 | 104400 | 3600 | 6.325% | 96 | 233 | 106.019 |  | 78
2025-04-07 | 2026 | 2025 | 2025-04-01 | 30 | 5128 | 6280 | 5516 | 5776 | 5745 | 5410 | 4061 | 6316 | 4348 | 6676 | 7840 | 5758 | 6856 | 6352 | 5989 | 0 | 5120 | 7232 | 6608 | 9324 | 7629 | 7949 | 7329 | 7206 | 7220 | 7025 | 7807 | 0 | 7195 | 0 | 7223 | 5906 | 6153 | 7858 | 6181 | 6848 | 6891 | 6523 | 6822 | 4.61 | 4.84 | 4.6 | 4.69 | 3.8 | 4.82 | 4.78 | 4.8 | 4.38 | 4.71 | 5.09 | 4.76 | 4.95 | 4.85 | 4.66 | 0 | 4.6 | 5.05 | 4.8 | 5.43 | 4.22 | 4.18 | 4.05 | 4.57 | 3.71 | 4.35 | 4.49 | 0 | 4.12 | 0 | 3.89 | 4.17 | 4.26 | 4.16 | 4.38 | 4.16 | 3.8 | 4.04 | 4.04 | 236100 | 4.1233 |  |  | 237977 | 2163 | 278309 | 2193 | 253844 | 1801 | 289480 | 1845 | 63600 | 0 | 55200 | 0 | 49200 | 1200 | 54000 | 1200 | 222000 | 2400 | 5.972% | 96 | 5005 | 238.176 |  | 78
2025-04-08 | 2026 | 2025 | 2025-04-01 | 30 | 4316 | 3696 | 3986 | 2420 | 4046 | 5079 | 4140 | 4684 | 1744 | 4112 | 4460 | 4310 | 4204 | 4472 | 1155 | 0 | 5408 | 5168 | 5578 | 6118 | 4592 | 4328 | 4704 | 4450 | 3958 | 4076 | 3910 | 0 | 5106 | 0 | 3788 | 3435 | 3696 | 4568 | 5094 | 4896 | 3666 | 3596 | 4325 | 3.74 | 3.74 | 3.75 | 3.66 | 3.58 | 4.01 | 3.68 | 3.94 | 3.7 | 3.66 | 3.85 | 3.83 | 3.84 | 3.92 | 3.11 | 0 | 4.02 | 3.98 | 4.12 | 4.16 | 3.79 | 3.68 | 3.68 | 3.85 | 3.49 | 3.7 | 3.67 | 0 | 3.9 | 0 | 3.66 | 3.57 | 3.7 | 3.91 | 4.05 | 3.93 | 3.61 | 4.13 | 3.7 | 151284 | 3.4951 |  |  | 238011 | 2164 | 278337 | 2194 | 253876 | 1802 | 289511 | 1846 | 40800 | 1200 | 33600 | 1200 | 38400 | 1200 | 37200 | 1200 | 150000 | 4800 | 0.8487% | 96 | 4615 | 149.33 |  | 78
2025-04-09 | 2026 | 2025 | 2025-04-01 | 30 | 11140 | 7480 | 9628 | 2232 | 9056 | 7947 | 9460 | 9688 | 6482 | 3688 | 12444 | 9350 | 8102 | 10392 | 9464 | 1112 | 12968 | 12416 | 11728 | 12297 | 8994 | 8152 | 10714 | 10910 | 8828 | 9116 | 8908 | 0 | 9794 | 0 | 7086 | 7543 | 8482 | 8556 | 9864 | 10140 | 7702 | 7590 | 8333 | 4.85 | 5.37 | 4.76 | 4.77 | 5.09 | 5.19 | 4.8 | 4.87 | 5.25 | 4.98 | 5.45 | 5.28 | 5.32 | 5.14 | 5.09 | 5.27 | 5.07 | 5.36 | 6.59 | 5.63 | 5.4 | 5.44 | 4.66 | 4.98 | 4.95 | 4.71 | 4.88 | 0 | 4.86 | 0 | 4.59 | 4.73 | 4.88 | 4.88 | 5.07 | 5.05 | 4.83 | 4.74 | 5.01 | 327786 | 4.8151 |  |  | 238080 | 2165 | 278399 | 2195 | 253934 | 1802 | 289579 | 1846 | 82800 | 1200 | 74400 | 1200 | 69600 | 0 | 81600 | 0 | 308400 | 2400 | 5.914% | 96 | 91469 | 327.512 |  | 78
2025-04-10 | 2026 | 2025 | 2025-04-01 | 30 | 14750 | 13334 | 13120 | 12895 | 13940 | 14632 | 15060 | 14658 | 14103 | 13510 | 16678 | 14261 | 11088 | 10532 | 14296 | 8036 | 15320 | 16124 | 16394 | 16007 | 16920 | 16264 | 14364 | 14072 | 15618 | 13132 | 12542 | 0 | 13122 | 0 | 12891 | 12930 | 13718 | 13574 | 15826 | 13794 | 14084 | 14140 | 14001 | 5.59 | 6.18 | 5.43 | 5.42 | 5.97 | 6.06 | 5.51 | 5.15 | 5.98 | 5.33 | 6.31 | 5.92 | 5.96 | 5.77 | 5.83 | 5.9 | 6.05 | 5.8 | 5.74 | 6.66 | 6.01 | 6.2 | 6.1 | 5.88 | 6 | 5.88 | 5.94 | 0 | 5.74 | 0 | 5.52 | 5.76 | 6.04 | 6.02 | 5.85 | 6.03 | 5.99 | 5.42 | 6.19 | 519730 | 5.5674 |  |  | 238197 | 2165 | 278494 | 2195 | 254041 | 1803 | 289688 | 1847 | 140400 | 0 | 114000 | 0 | 128400 | 1200 | 130800 | 1200 | 513600 | 2400 | 1.179% | 96 | 97193 | 511 |  | 78 | No scada available server OS failed
2025-04-11 | 2026 | 2025 | 2025-04-01 | 30 | 14293 | 14793 | 14285 | 14379 | 13985 | 14594 | 14284 | 14594 | 14159 | 14743 | 14852 | 14273 | 14184 | 14221 | 14457 | 9475 | 14263 | 14282 | 14291 | 14296 | 14704 | 14790 | 14721 | 14894 | 12720 | 14974 | 14802 | 0 | 14964 | 0 | 12790 | 12748 | 12742 | 12973 | 12785 | 12790 | 12863 | 12830 | 12795 | 5.83 | 5.9 | 6.05 | 5.8 | 5.74 | 6.21 | 6.01 | 6.2 | 6.1 | 6.1 | 5.88 | 6 | 5.88 | 5.94 | 6.2 | 5.74 | 6.23 | 5.52 | 5.76 | 6.04 | 6.02 | 5.85 | 6.03 | 5.42 | 6.19 | 5.59 | 6.01 | 0 | 5.42 | 0 | 6 | 5.51 | 5.15 | 5.98 | 5.33 | 6.1 | 5.92 | 5.92 | 5.9 | 514588 | 5.5762 |  |  | 238303 | 2165 | 278592 | 2195 | 254150 | 1803 | 289801 | 1847 | 127200 | 0 | 117600 | 0 | 130800 | 0 | 135600 | 0 | 511200 | 0 | 0.6584% | 96 | 79804 | 514 |  | 78 | No scada available server OS failed
2025-04-12 | 2026 | 2025 | 2025-04-01 | 30 | 14925 | 15604 | 15395 | 15942 | 10932 | 15953 | 15693 | 15831 | 12593 | 15603 | 15493 | 12862 | 12749 | 12852 | 12784 | 8839 | 12860 | 10527 | 12949 | 12973 | 12692 | 12639 | 11302 | 12842 | 10937 | 12706 | 12852 | 0 | 12793 | 0 | 11295 | 10183 | 10962 | 10981 | 10939 | 10926 | 10969 | 10210 | 10928 | 5.63 | 6.04 | 5.55 | 5.6 | 6.19 | 6.25 | 5.75 | 5.53 | 5.55 | 5.54 | 5.96 | 5.74 | 5.9 | 5.75 | 5.91 | 5.82 | 5.86 | 6.15 | 6.47 | 6.22 | 5.08 | 6.26 | 5.87 | 5.93 | 5.43 | 5.57 | 5.63 | 0 | 5.51 | 0 | 5.16 | 5.45 | 5.48 | 5.59 | 5.63 | 5.54 | 5.55 | 5.62 | 5.36 | 469515 | 5.4377 |  |  | 238392 | 2166 | 278675 | 2195 | 254265 | 1803 | 289902 | 1847 | 106800 | 1200 | 99600 | 0 | 138000 | 0 | 121200 | 0 | 465600 | 1200 | 0.8338% | 96 | 83785 | 469.51 |  | 78 | No scada available server OS failed
2025-04-13 | 2026 | 2025 | 2025-04-01 | 30 | 9219 | 9742 | 9769 | 9731 | 7948 | 9727 | 9768 | 9759 | 8864 | 9742 | 9749 | 8846 | 8790 | 8732 | 8759 | 6190 | 8742 | 8756 | 8796 | 8789 | 7939 | 8268 | 8179 | 8264 | 9214 | 8280 | 8264 | 0 | 8295 | 0 | 9627 | 9637 | 9695 | 9635 | 9637 | 9678 | 9629 | 9317 | 9687 | 4.85 | 5.37 | 4.76 | 4.77 | 5.09 | 5.19 | 4.8 | 4.87 | 5.25 | 4.98 | 5.45 | 5.28 | 5.32 | 5.14 | 5.09 | 5.27 | 5.07 | 5.36 | 6.59 | 5.63 | 5.4 | 5.44 | 4.66 | 4.98 | 4.95 | 4.71 | 4.88 | 0 | 4.86 | 0 | 4.59 | 4.73 | 4.88 | 4.88 | 5.07 | 5.05 | 4.83 | 4.74 | 5.01 | 333663 | 4.8151 |  |  | 238471 | 2166 | 278729 | 2196 | 254337 | 1803 | 289973 | 1847 | 94800 | 0 | 64800 | 1200 | 86400 | 0 | 85200 | 0 | 331200 | 1200 | 0.7382% | 96 | 38289 | 333.66 |  | 78 | No scada available server OS failed
2025-04-14 | 2026 | 2025 | 2025-04-01 | 30 | 17456 | 18268 | 18198 | 18467 | 14740 | 18104 | 18132 | 18105 | 17283 | 16001 | 16100 | 17426 | 17421 | 17056 | 17528 | 8943 | 17354 | 17965 | 17954 | 17695 | 14846 | 14749 | 14769 | 14754 | 15738 | 14803 | 14824 | 0 | 14795 | 0 | 15796 | 15740 | 15791 | 15846 | 15846 | 15825 | 15742 | 15962 | 15847 | 7.28 | 7.74 | 7.38 | 7.5 | 6.95 | 6.64 | 0 | 7.59 | 7.79 | 7.37 | 7.73 | 7.52 | 7.72 | 7.67 | 7.75 | 7.66 | 8.38 | 7.44 | 8.44 | 7.02 | 6.9 | 7.2 | 7.24 | 7.4 | 7.39 | 7.05 | 6.74 | 0 | 7.37 | 0 | 6.79 | 6.65 | 6.54 | 7.02 | 7.65 | 7.66 | 6.74 | 6.53 | 7.19 | 601869 | 6.7597 |  |  | 238602 | 2166 | 278827 | 2196 | 254472 | 1803 | 290108 | 1848 | 157200 | 0 | 117600 | 0 | 162000 | 0 | 162000 | 1200 | 598800 | 1200 | 0.5099% | 96 | 33860 | 601.869 |  | 78 | No scada available server OS failed
2025-04-15 | 2026 | 2025 | 2025-04-01 | 30 | 14297 | 14921 | 14963 | 14367 | 15592 | 14874 | 14853 | 14869 | 15102 | 14848 | 14863 | 15107 | 15111 | 15123 | 15143 | 9457 | 15132 | 15164 | 15179 | 15189 | 15853 | 15895 | 15867 | 15874 | 12759 | 15842 | 15896 | 0 | 15862 | 0 | 12796 | 12706 | 12759 | 12749 | 12796 | 12793 | 12795 | 10236 | 12705 | 6.04 | 6.55 | 6.01 | 5.72 | 6.71 | 6.27 | 6 | 5.79 | 6 | 6.65 | 6.61 | 6.36 | 6.31 | 6.18 | 6.29 | 6.5 | 6.63 | 6.48 | 6.75 | 6.78 | 6.72 | 6.39 | 5.76 | 5.9 | 6.3 | 5.66 | 5.5 | 5.76 | 5.28 | 0 | 5.85 | 5.65 | 5.63 | 5.65 | 5.94 | 5.56 | 5.81 | 5.84 | 5.94 | 530337 | 5.9428 |  |  | 238704 | 2167 | 278932 | 2197 | 254583 | 1804 | 290229 | 1848 | 122400 | 1200 | 126000 | 1200 | 133200 | 1200 | 145200 | 0 | 526800 | 3600 | 0.6669% | 96 | 145066 | 530.337 |  | 78 | No scada available server OS failed
2025-04-16 | 2026 | 2025 | 2025-04-01 | 30 | 16756 | 16731 | 16721 | 16734 | 12150 | 16742 | 16732 | 16749 | 16196 | 16742 | 16782 | 16187 | 16186 | 16164 | 16184 | 9321 | 16189 | 16147 | 16197 | 16169 | 12169 | 12189 | 12190 | 12185 | 14915 | 12169 | 12185 | 0 | 12168 | 0 | 14925 | 14952 | 14958 | 14952 | 14984 | 14984 | 14952 | 14963 | 14962 | 5.59 | 6.18 | 5.43 | 5.42 | 5.97 | 6.06 | 5.51 | 5.15 | 5.98 | 5.33 | 6.31 | 5.92 | 5.96 | 5.77 | 5.83 | 5.9 | 6.05 | 5.8 | 5.74 | 6.66 | 6.01 | 6.2 | 6.1 | 5.88 | 6 | 5.88 | 5.94 | 0 | 5.74 | 0 | 5.52 | 5.76 | 6.04 | 6.02 | 5.85 | 6.03 | 5.99 | 5.42 | 6.19 | 552581 | 5.5674 |  |  | 238828 | 2167 | 279013 | 2197 | 254708 | 1804 | 290358 | 1848 | 148800 | 0 | 97200 | 0 | 150000 | 0 | 154800 | 0 | 550800 | 0 | 0.3223% | 96 | 160779 | 552.581 |  | 78 | No scada available server OS failed
2025-04-17 | 2026 | 2025 | 2025-04-01 | 30 | 15153 | 15183 | 16583 | 16584 | 13650 | 16573 | 15190 | 16587 | 13458 | 16784 | 16596 | 14923 | 14937 | 14976 | 14979 | 9674 | 14979 | 14943 | 14943 | 14964 | 13687 | 13696 | 13674 | 13653 | 12556 | 13687 | 13659 | 0 | 13653 | 0 | 12562 | 12547 | 12589 | 12538 | 12565 | 12567 | 12564 | 12032 | 12574 | 5.83 | 5.9 | 6.05 | 5.8 | 5.74 | 6.21 | 6.01 | 6.2 | 6.1 | 6.1 | 5.88 | 6 | 5.88 | 5.94 | 6.2 | 5.74 | 6.23 | 5.52 | 5.76 | 6.04 | 6.02 | 5.85 | 6.03 | 5.42 | 6.19 | 5.59 | 6.01 | 0 | 5.42 | 0 | 6 | 5.51 | 5.15 | 5.98 | 5.33 | 6.1 | 5.92 | 5.92 | 5.9 | 522462 | 5.5762 |  |  | 238932 | 2167 | 279104 | 2197 | 254829 | 1804 | 290477 | 1848 | 124800 | 0 | 109200 | 0 | 145200 | 0 | 142800 | 0 | 522000 | 0 | 0.08843% | 96 | 182469 | 522.462 |  | 78 | No scada available server OS failed
2025-04-18 | 2026 | 2025 | 2025-04-01 | 30 | 9986 | 9964 | 9942 | 9960 | 8859 | 9936 | 9962 | 9967 | 8168 | 9997 | 9989 | 8164 | 8196 | 8164 | 8153 | 5639 | 8169 | 8176 | 8148 | 8243 | 8895 | 8858 | 8853 | 8857 | 8106 | 8895 | 8824 | 0 | 8852 | 0 | 8165 | 8169 | 8158 | 7963 | 7584 | 8139 | 8147 | 8163 | 8189 | 4.85 | 5.37 | 4.76 | 4.77 | 5.09 | 5.19 | 4.8 | 4.87 | 5.25 | 4.98 | 5.45 | 5.28 | 5.32 | 5.14 | 5.09 | 5.27 | 5.07 | 5.36 | 6.59 | 5.63 | 5.4 | 5.44 | 4.66 | 4.98 | 4.95 | 4.71 | 4.88 | 0 | 4.86 | 0 | 4.59 | 4.73 | 4.88 | 4.88 | 5.07 | 5.05 | 4.83 | 4.74 | 5.01 | 320599 | 4.8151 |  |  | 238998 | 2167 | 279163 | 2197 | 254903 | 1804 | 290542 | 1849 | 79200 | 0 | 70800 | 0 | 88800 | 0 | 78000 | 1200 | 316800 | 1200 | 1.185% | 96 | 88227 | 320.59 |  | 78 | No scada available server OS failed
2025-04-19 | 2026 | 2025 | 2025-04-01 | 30 | 12321 | 12334 | 12353 | 12327 | 10590 | 12358 | 12364 | 12387 | 11389 | 12389 | 12393 | 11358 | 10948 | 11378 | 11385 | 8429 | 11364 | 11398 | 11428 | 11463 | 10569 | 10595 | 8792 | 10563 | 10352 | 10585 | 10567 | 0 | 10589 | 0 | 10274 | 9590 | 10290 | 10363 | 10368 | 10374 | 10387 | 10338 | 10374 | 4.73 | 5.25 | 4.97 | 4.56 | 4.53 | 5.13 | 4.74 | 4.54 | 5.04 | 4.65 | 5.08 | 5.09 | 5.15 | 6.01 | 4.79 | 4.63 | 4.4 | 4.69 | 5.17 | 5.05 | 4.8 | 4.95 | 4.57 | 4.87 | 4.67 | 4.45 | 4.48 | 0 | 4.42 | 0 | 4.25 | 4.37 | 4.48 | 4.63 | 4.57 | 4.44 | 4.53 | 4.53 | 4.67 | 407326 | 4.5097 |  |  | 239083 | 2168 | 279232 | 2197 | 254995 | 1805 | 290634 | 1849 | 102000 | 1200 | 82800 | 0 | 110400 | 1200 | 110400 | 0 | 405600 | 2400 | 0.4237% | 96 | 87932 | 407.32 |  | 78 | No scada available server OS failed
2025-04-20 | 2026 | 2025 | 2025-04-01 | 30 | 20358 | 20376 | 20321 | 19585 | 20876 | 20387 | 20341 | 20365 | 21187 | 20369 | 20385 | 21179 | 19457 | 21178 | 21190 | 21179 | 21187 | 21185 | 21189 | 21254 | 20854 | 20862 | 20832 | 20858 | 19245 | 20835 | 20863 | 0 | 20851 | 0 | 19254 | 19276 | 19267 | 19259 | 19274 | 19248 | 19256 | 19289 | 19228 | 7.13 | 7.22 | 7.2 | 7.2 | 6.86 | 6.84 | 7.63 | 7.38 | 7.33 | 7.21 | 7.65 | 7.19 | 7.34 | 7.41 | 7.49 | 7.4 | 7.65 | 7.28 | 8.03 | 7.54 | 6.5 | 7.13 | 7.11 | 7.2 | 6.69 | 6.89 | 6.85 | 0 | 7.3 | 0 | 6.26 | 6.56 | 6.37 | 6.77 | 7.26 | 7.17 | 6.41 | 6.12 | 6.55 | 752099 | 6.721 |  |  | 239243 | 2168 | 279371 | 2197 | 255147 | 1805 | 290809 | 1849 | 192000 | 0 | 166800 | 0 | 182400 | 0 | 210000 | 0 | 751200 | 0 | 0.1195% | 96 | 191708 | 752.09 |  | 78 | No scada available server OS failed
2025-04-21 | 2026 | 2025 | 2025-04-01 | 30 | 8279 | 8290 | 8289 | 8278 | 8013 | 8268 | 8242 | 8281 | 7742 | 8284 | 8295 | 7748 | 7732 | 7753 | 7759 | 6349 | 7749 | 7736 | 7782 | 7793 | 8051 | 8057 | 8003 | 8042 | 8284 | 8073 | 8034 | 0 | 8055 | 0 | 8241 | 8417 | 8486 | 8494 | 8496 | 8452 | 8467 | 8463 | 8257 | 5.8621 | 6.3056 | 5.2877 | 5.3705 | 5.0465 | 5.8957 | 5.8957 | 5.8117 | 6.2648 | 4.8664 | 5.6272 | 5.7042 | 5.5212 | 5.7344 | 6.0185 | 5.5628 | 6.2912 | 5.9452 | 6.1094 | 6.4611 | 5.9728 | 4.9143 | 5.1145 | 5.336 | 5.0755 | 5.3435 | 5.0553 | 0 | 5 | 0 | 4.943 | 4.9765 | 5.2576 | 5.6703 | 5.5863 | 5.4673 | 5.2684 | 5.2848 | 5.2838 | 299034 | 5.2598 |  |  | 239312 | 2169 | 279424 | 2198 | 255208 | 1805 | 290869 | 1849 | 82800 | 1200 | 63600 | 1200 | 73200 | 0 | 72000 | 0 | 291600 | 2400 | 2.486% | 95 | 78346 | 299.03 |  | 78 | No scada available server OS failed
2025-04-22 | 2026 | 2025 | 2025-04-01 | 30 | 4363 | 4335 | 4367 | 4342 | 6344 | 4051 | 4375 | 4365 | 6342 | 4379 | 4395 | 6356 | 5538 | 6342 | 6367 | 6321 | 6376 | 6372 | 6398 | 6392 | 6356 | 5989 | 6347 | 6375 | 6450 | 6358 | 6332 | 0 | 6349 | 0 | 5579 | 5595 | 6487 | 6431 | 6458 | 6435 | 6479 | 6482 | 6474 | 4.58 | 4.46 | 3.97 | 4.15 | 3.78 | 4.38 | 4.4 | 4.13 | 4.08 | 3.95 | 4.01 | 4.04 | 3.98 | 3.84 | 3.92 | 3.95 | 4.15 | 4.01 | 3.99 | 4.01 | 3.76 | 3.87 | 3.95 | 4.26 | 4.2 | 4.22 | 4.21 | 0 | 5.44 | 0 | 4.17 | 4.15 | 4.32 | 4.55 | 6.32 | 4.45 | 4.87 | 4.31 | 5.39 | 215096 | 4.0569 |  |  | 239364 | 2169 | 279466 | 2198 | 255240 | 1805 | 290921 | 1850 | 62400 | 0 | 50400 | 0 | 38400 | 0 | 62400 | 1200 | 213600 | 1200 | 0.6955% | 96 | 29652 | 215.09 |  | 78 | No scada available server OS failed
2025-04-23 | 2026 | 2025 | 2025-04-01 | 30 | 3742 | 3758 | 3745 | 3742 | 3153 | 3164 | 3746 | 3789 | 3923 | 3754 | 3784 | 3942 | 3956 | 3932 | 3951 | 3956 | 3973 | 3957 | 3521 | 3989 | 3158 | 3021 | 3153 | 2680 | 3102 | 3157 | 3178 | 0 | 3167 | 0 | 2859 | 3123 | 3124 | 3154 | 3157 | 3185 | 3136 | 3174 | 3162 | 3.93 | 3.99 | 3.9 | 3.78 | 3.4 | 4.13 | 3.8 | 3.5 | 3.76 | 3.86 | 4.06 | 3.98 | 4.04 | 4.03 | 3.88 | 3.99 | 3.41 | 4.09 | 4.29 | 4.06 | 3.02 | 3.75 | 3.14 | 3.53 | 3.01 | 3.42 | 3.48 | 0 | 3.31 | 0 | 3.29 | 3.51 | 3.38 | 3.42 | 3.69 | 3.98 | 3.43 | 3.41 | 3.47 | 128167 | 3.4903 |  |  | 239389 | 2170 | 279486 | 2199 | 255268 | 1806 | 290953 | 1851 | 30000 | 1200 | 24000 | 1200 | 33600 | 1200 | 38400 | 1200 | 126000 | 4800 | 1.691% | 90 | 5922 | 128.16 |  | 78 | No scada available server OS failed
2025-04-24 | 2026 | 2025 | 2025-04-01 | 30 | 5021 | 5279 | 5297 | 5278 | 5423 | 5289 | 5267 | 5243 | 4434 | 5276 | 5292 | 4432 | 4452 | 4457 | 4432 | 4475 | 4478 | 4472 | 4489 | 4498 | 5490 | 5289 | 5489 | 5467 | 6041 | 5472 | 5484 | 0 | 5479 | 0 | 7158 | 7169 | 7184 | 7167 | 7172 | 7182 | 7156 | 6258 | 6021 | 4.33 | 4.54 | 4.49 | 4.18 | 4.27 | 4.89 | 4.38 | 4.32 | 4.44 | 4.47 | 4.89 | 4.48 | 4.5 | 4.5 | 4.37 | 4.5 | 4.41 | 4.67 | 5.98 | 5.16 | 4.2 | 4.72 | 4.05 | 4.62 | 4.45 | 4.26 | 4.37 | 0 | 4.93 | 0 | 4.07 | 4.82 | 4.43 | 4.27 | 4.59 | 4.5 | 4.33 | 4.5 | 4.6 | 203962 | 4.2944 |  |  | 239445 | 2170 | 279521 | 2200 | 255306 | 1806 | 290989 | 1851 | 67200 | 0 | 42000 | 1200 | 45600 | 0 | 43200 | 0 | 198000 | 1200 | 2.923% | 96 | 7484 | 203.96 |  | 78 | No scada available server OS failed
2025-04-25 | 2026 | 2025 | 2025-04-01 | 30 | 7021 | 7056 | 7041 | 6563 | 6587 | 7053 | 7069 | 6690 | 6032 | 7059 | 7089 | 6063 | 6321 | 6345 | 6356 | 6332 | 6341 | 6345 | 6347 | 6389 | 6583 | 6021 | 6545 | 6564 | 6832 | 6527 | 6544 | 0 | 6575 | 0 | 6853 | 6842 | 6021 | 6829 | 6839 | 6869 | 6882 | 5587 | 6849 | 4.61 | 4.84 | 4.6 | 4.69 | 3.8 | 4.82 | 4.78 | 4.8 | 4.38 | 4.71 | 5.09 | 4.76 | 4.95 | 4.85 | 4.66 | 4.01 | 4.6 | 5.05 | 4.8 | 5.43 | 4.22 | 4.18 | 4.05 | 4.57 | 3.71 | 4.35 | 4.49 | 0 | 4.12 | 0 | 3.89 | 4.17 | 4.26 | 4.16 | 4.38 | 4.16 | 3.8 | 4.04 | 4.04 | 243861 | 4.2262 |  |  | 239500 | 2171 | 279564 | 2200 | 255358 | 1807 | 291041 | 1852 | 66000 | 1200 | 51600 | 0 | 62400 | 1200 | 62400 | 1200 | 242400 | 3600 | 0.5991% | 96 | 6052 | 243.86 |  | 78 | No scada available server OS failed
2025-04-26 | 2026 | 2025 | 2025-04-01 | 30 | 10931 | 10952 | 10932 | 10921 | 8845 | 10210 | 10953 | 10959 | 11852 | 10944 | 10965 | 11856 | 11862 | 11832 | 11842 | 11857 | 11843 | 11853 | 11869 | 11897 | 8363 | 8563 | 8856 | 8842 | 9321 | 8858 | 8839 | 0 | 8849 | 0 | 9323 | 9342 | 9354 | 9344 | 9063 | 9340 | 9356 | 9376 | 9365 | 4.85 | 5.37 | 4.76 | 4.77 | 5.09 | 5.19 | 4.8 | 4.87 | 5.25 | 4.98 | 5.45 | 5.28 | 5.32 | 5.14 | 5.09 | 5.27 | 5.07 | 5.36 | 6.59 | 5.63 | 5.4 | 5.44 | 4.66 | 4.98 | 4.95 | 4.71 | 4.88 | 0 | 4.86 | 0 | 4.59 | 4.73 | 4.88 | 4.88 | 5.07 | 5.05 | 4.83 | 4.74 | 5.01 | 379529 | 4.8151 |  |  | 239577 | 2171 | 279622 | 2200 | 255439 | 1807 | 291139 | 1852 | 92400 | 0 | 69600 | 0 | 97200 | 0 | 117600 | 0 | 376800 | 0 | 0.719% | 96 | 53692 | 379.52 |  | 78 | No scada available server OS failed
2025-04-27 | 2026 | 2025 | 2025-04-01 | 30 | 5801 | 5823 | 5812 | 5824 | 4832 | 5849 | 5365 | 5859 | 5634 | 5864 | 5879 | 5641 | 5623 | 5321 | 5642 | 5648 | 5645 | 5649 | 5672 | 5679 | 4845 | 4265 | 4823 | 4854 | 4532 | 4210 | 4867 | 0 | 4879 | 0 | 4565 | 4521 | 4526 | 4556 | 4021 | 4537 | 4539 | 4567 | 3943 | 4.23 | 4.33 | 4.21 | 4.28 | 4.21 | 4.48 | 4.23 | 4.35 | 4.35 | 4.18 | 4.62 | 4.31 | 4.42 | 4.46 | 4.3 | 4.5 | 5.8 | 4.68 | 4.85 | 4.97 | 4.72 | 4.43 | 4.49 | 4.62 | 4.33 | 4.36 | 4.24 | 0 | 4.44 | 0 | 4.26 | 4.44 | 4.44 | 4.44 | 4.48 | 4.54 | 4.25 | 4.41 | 4.59 | 190112 | 4.2369 |  |  | 239613 | 2172 | 279653 | 2201 | 255482 | 1808 | 291185 | 1853 | 43200 | 1200 | 37200 | 1200 | 51600 | 1200 | 55200 | 1200 | 187200 | 4800 | 1.532% | 96 | 17621 | 190.11 |  | 78 | No scada available server OS failed
2025-04-28 | 2026 | 2025 | 2025-04-01 | 30 | 8035 | 8042 | 8051 | 7521 | 6672 | 8044 | 8020 | 8047 | 7821 | 8053 | 8059 | 7844 | 7856 | 7842 | 7823 | 7834 | 7818 | 7820 | 7853 | 7280 | 6632 | 6640 | 6621 | 6644 | 7021 | 6635 | 6654 | 0 | 5521 | 0 | 7034 | 7056 | 7045 | 7062 | 6760 | 7052 | 7044 | 7041 | 7047 | 4.58 | 4.46 | 3.97 | 4.15 | 3.78 | 4.38 | 4.4 | 4.13 | 4.08 | 3.95 | 4.01 | 4.04 | 3.98 | 3.84 | 3.92 | 3.95 | 4.15 | 4.01 | 3.99 | 4.01 | 3.76 | 3.87 | 3.95 | 4.26 | 4.2 | 4.22 | 4.21 | 0 | 5.44 | 0 | 4.17 | 4.15 | 4.32 | 4.55 | 6.32 | 4.45 | 4.87 | 4.31 | 5.39 | 271844 | 4.0569 |  |  | 239671 | 2172 | 279696 | 2201 | 255541 | 1808 | 291249 | 1853 | 69600 | 0 | 51600 | 0 | 70800 | 0 | 76800 | 0 | 268800 | 0 | 1.12% | 96 | 49821 | 271.84 |  | 78 | No scada available server OS failed
2025-04-29 | 2026 | 2025 | 2025-04-01 | 30 | 6459 | 6487 | 6443 | 6473 | 6742 | 6452 | 6401 | 6459 | 8098 | 6453 | 6467 | 8073 | 8068 | 8079 | 8082 | 8061 | 8013 | 8047 | 8056 | 8067 | 6755 | 5210 | 6776 | 6785 | 8124 | 6778 | 5567 | 0 | 6792 | 0 | 8135 | 8122 | 8132 | 8184 | 8157 | 8162 | 8151 | 8121 | 8139 | 4.58 | 4.46 | 3.97 | 4.15 | 3.78 | 4.38 | 4.4 | 4.13 | 4.08 | 3.95 | 4.01 | 4.04 | 3.98 | 3.84 | 3.92 | 3.95 | 4.15 | 4.01 | 3.99 | 4.01 | 3.76 | 3.87 | 3.95 | 4.26 | 4.2 | 4.22 | 4.21 | 0 | 5.44 | 0 | 4.17 | 4.15 | 4.32 | 4.55 | 6.32 | 4.45 | 4.87 | 4.31 | 5.39 | 271570 | 4.0569 |  |  | 239738 | 2173 | 279738 | 2202 | 255589 | 1809 | 291316 | 1854 | 80400 | 1200 | 50400 | 1200 | 57600 | 1200 | 80400 | 1200 | 268800 | 4800 | 1.02% | 96 | 39915 | 271.54 |  | 78 | No scada available server OS failed
2025-04-30 | 2026 | 2025 | 2025-04-01 | 30 | 16089 | 16078 | 16042 | 14467 | 15425 | 16059 | 16042 | 16072 | 17489 | 16079 | 14989 | 17467 | 17482 | 17421 | 17429 | 17435 | 17445 | 17466 | 17487 | 17501 | 15456 | 12641 | 13935 | 15467 | 15921 | 15432 | 12782 | 0 | 15469 | 0 | 15934 | 15954 | 14263 | 15967 | 15945 | 15932 | 15957 | 15955 | 15968 | 6.04 | 6.55 | 6.01 | 5.72 | 6.71 | 6.27 | 6 | 5.79 | 6 | 6.65 | 6.61 | 6.36 | 6.31 | 6.18 | 6.29 | 6.5 | 6.63 | 6.48 | 6.75 | 6.78 | 6.72 | 6.39 | 5.76 | 5.9 | 6.3 | 5.66 | 5.5 | 5.76 | 5.28 | 0 | 5.85 | 5.65 | 5.63 | 5.65 | 5.94 | 5.56 | 5.81 | 5.84 | 5.94 | 590942 | 5.9428 |  |  | 239869 | 2173 | 279835 | 2202 | 255707 | 1809 | 291461 | 1854 | 157200 | 0 | 116400 | 0 | 141600 | 0 | 174000 | 0 | 589200 | 0 | 0.2948% | 96 | 129769 | 590.94 |  | 78 | No scada available server OS failed
2025-05-01 | 2026 | 2025 | 2025-05-01 | 31 | 16821 | 16852 | 16832 | 16825 | 15121 | 16832 | 16844 | 16842 | 16583 | 16845 | 16858 | 16574 | 16587 | 16537 | 16573 | 16001 | 16529 | 16542 | 16584 | 16578 | 15124 | 13052 | 15142 | 15152 | 15528 | 15562 | 15526 | 0 | 13531 | 0 | 15532 | 13574 | 15535 | 15534 | 15565 | 15546 | 15537 | 15542 | 15543 | 5.58 | 6.55 | 5.67 | 5.72 | 6.71 | 6.27 | 6 | 5.79 | 6 | 6.65 | 5.98 | 6.36 | 6.31 | 5.42 | 6.29 | 6.5 | 6.63 | 6.48 | 6.75 | 6.78 | 6.72 | 6.39 | 5.76 | 5.9 | 6.3 | 5.66 | 5.5 | 5.76 | 5.28 | 0 | 5.85 | 5.65 | 5.63 | 5.65 | 5.94 | 5.56 | 5.81 | 5.84 | 5.94 | 588285 | 5.8867 |  |  | 239996 | 2173 | 279932 | 2202 | 255833 | 1809 | 291598 | 1854 | 152400 | 0 | 116400 | 0 | 151200 | 0 | 164400 | 0 | 584400 | 0 | 0.6604% | 96 | 139458 | 588.28 |  | 78 | No scada available server OS failed
2025-05-02 | 2026 | 2025 | 2025-05-01 | 31 | 14538 | 14554 | 14576 | 14574 | 12967 | 14573 | 11052 | 14576 | 13721 | 14621 | 14678 | 13753 | 14749 | 14756 | 14732 | 14765 | 14768 | 12952 | 14789 | 14799 | 12888 | 12863 | 12877 | 12889 | 11834 | 11750 | 12844 | 0 | 12856 | 0 | 11453 | 11842 | 11849 | 11832 | 11854 | 11844 | 11824 | 11856 | 11845 | 4.73 | 5.25 | 4.97 | 4.56 | 4.53 | 5.13 | 4.74 | 4.54 | 5.04 | 4.65 | 5.08 | 5.09 | 5.15 | 6.01 | 4.79 | 4.63 | 4.4 | 4.69 | 5.17 | 5.05 | 4.8 | 4.95 | 4.57 | 4.87 | 4.67 | 4.45 | 4.48 | 0 | 4.42 | 0 | 4.25 | 4.37 | 4.48 | 4.63 | 4.57 | 4.44 | 4.53 | 4.53 | 4.67 | 491493 | 4.5097 |  |  | 240094 | 2173 | 280017 | 2202 | 255927 | 1809 | 291712 | 1854 | 117600 | 0 | 102000 | 0 | 112800 | 0 | 136800 | 0 | 469200 | 0 | 4.536% | 96 | 152479 | 491.49 |  | 78 | No scada available server OS failed
2025-05-03 | 2026 | 2025 | 2025-05-01 | 31 | 17432 | 17421 | 17434 | 17442 | 16349 | 17435 | 17425 | 17443 | 17731 | 17456 | 17489 | 17727 | 18239 | 18211 | 18234 | 18242 | 18222 | 18234 | 17248 | 18221 | 16595 | 16548 | 16531 | 16523 | 14845 | 16543 | 16562 | 0 | 16569 | 0 | 14321 | 14856 | 14842 | 13521 | 14847 | 14834 | 14841 | 14865 | 14852 | 7.28 | 7.74 | 7.38 | 7.5 | 6.95 | 6.64 | 6.2 | 7.59 | 7.79 | 7.37 | 7.73 | 7.52 | 7.72 | 7.67 | 7.75 | 7.66 | 8.38 | 7.44 | 8.44 | 7.02 | 6.9 | 7.2 | 7.24 | 7.4 | 7.39 | 7.05 | 6.74 | 0 | 7.37 | 0 | 6.79 | 6.65 | 6.54 | 7.02 | 7.65 | 7.66 | 6.74 | 6.53 | 7.19 | 616130 | 6.9187 |  |  | 240216 | 2173 | 280127 | 2203 | 256057 | 1809 | 291862 | 1854 | 146400 | 0 | 132000 | 1200 | 156000 | 0 | 180000 | 0 | 614400 | 1200 | 0.2808% | 96 | 208104 | 616.13 |  | 78 | No scada available server OS failed
2025-05-04 | 2026 | 2025 | 2025-05-01 | 31 | 10932 | 10952 | 10976 | 10967 | 11167 | 10974 | 10953 | 10963 | 13230 | 10963 | 10977 | 13571 | 13578 | 13064 | 13853 | 13852 | 13674 | 13569 | 13863 | 13761 | 11153 | 11012 | 11145 | 11147 | 5192 | 11151 | 11152 | 0 | 11164 | 0 | 8752 | 8732 | 8758 | 8787 | 5147 | 8759 | 8742 | 8795 | 8749 | 4.85 | 5.37 | 4.76 | 4.77 | 5.09 | 5.19 | 4.8 | 4.87 | 5.25 | 4.98 | 5.45 | 5.28 | 5.32 | 5.14 | 5.09 | 5.27 | 5.07 | 5.36 | 6.59 | 5.63 | 5.4 | 5.44 | 4.66 | 4.98 | 4.95 | 4.71 | 4.88 | 0 | 4.86 | 0 | 4.59 | 4.73 | 4.88 | 4.88 | 5.07 | 5.05 | 4.83 | 4.74 | 5.01 | 404176 | 4.8151 |  |  | 240282 | 2174 | 280201 | 2203 | 256139 | 1810 | 291971 | 1855 | 79200 | 1200 | 88800 | 0 | 98400 | 1200 | 130800 | 1200 | 397200 | 3600 | 1.726% | 96 | 7564 | 404.17 |  | 78 | No scada available server OS failed
2025-05-05 | 2026 | 2025 | 2025-05-01 | 31 | 6172 | 8301 | 8352 | 8341 | 6500 | 8346 | 8346 | 8323 | 8289 | 8356 | 8367 | 8021 | 8240 | 8026 | 8256 | 8254 | 8562 | 8267 | 8287 | 8299 | 6521 | 6524 | 7721 | 7752 | 0 | 7767 | 7756 | 0 | 7741 | 0 | 5832 | 5847 | 5831 | 5867 | 5844 | 5821 | 5853 | 5849 | 5885 | 4.58 | 4.46 | 3.97 | 4.15 | 3.78 | 4.38 | 4.4 | 4.13 | 4.08 | 3.95 | 4.01 | 4.04 | 3.98 | 3.84 | 3.92 | 3.95 | 4.15 | 4.01 | 3.99 | 4.01 | 3.76 | 3.87 | 3.95 | 4.26 | 4.2 | 4.22 | 4.21 | 0 | 5.44 | 0 | 4.17 | 4.15 | 4.32 | 4.55 | 6.32 | 4.45 | 4.87 | 4.31 | 5.39 | 266316 | 4.0569 |  |  | 240325 | 2174 | 280249 | 2203 | 256199 | 1810 | 292039 | 1855 | 51600 | 0 | 57600 | 0 | 72000 | 0 | 81600 | 0 | 262800 | 0 | 1.32% | 96 | 53090 | 266.31 |  | 78 | No scada available server OS failed
2025-05-06 | 2026 | 2025 | 2025-05-01 | 31 | 9263 | 9255 | 9241 | 9245 | 8301 | 9247 | 9251 | 9053 | 9673 | 9249 | 9287 | 9681 | 9657 | 9652 | 9645 | 8562 | 9644 | 9640 | 8361 | 9688 | 8321 | 7531 | 7542 | 8367 | 3521 | 8356 | 8376 | 0 | 8364 | 0 | 6972 | 6964 | 6977 | 6952 | 6953 | 5128 | 6945 | 6983 | 6961 | 4.76 | 4.88 | 4.8 | 4.65 | 4.27 | 5.04 | 5.09 | 4.76 | 4.82 | 4.8 | 4.93 | 4.74 | 4.55 | 4.63 | 4.57 | 4.63 | 4.82 | 4.84 | 4.83 | 5.1 | 4.76 | 4.34 | 4.24 | 4.48 | 4.55 | 4.34 | 4.26 | 0 | 3.79 | 0 | 4.37 | 4.3 | 4.48 | 4.78 | 4.74 | 4.25 | 4.44 | 4.59 | 5.03 | 306808 | 4.391 |  |  | 240378 | 2175 | 280303 | 2204 | 256268 | 1811 | 292117 | 1856 | 63600 | 1200 | 64800 | 1200 | 82800 | 1200 | 93600 | 1200 | 304800 | 4800 | 0.6545% | 96 | 42452 | 306.8 |  | 78 | No scada available server OS failed
2025-05-07 | 2026 | 2025 | 2025-05-01 | 31 | 10973 | 12685 | 12694 | 11052 | 8461 | 11205 | 10989 | 12648 | 14478 | 12686 | 12734 | 14484 | 14476 | 14467 | 14489 | 13963 | 14472 | 13735 | 14535 | 14599 | 4731 | 4538 | 4634 | 4587 | 4742 | 9472 | 9453 | 0 | 4967 | 0 | 4739 | 4790 | 4021 | 4783 | 4762 | 3904 | 3632 | 6794 | 6749 | 4.85 | 5.37 | 4.76 | 4.77 | 5.09 | 5.19 | 4.8 | 4.87 | 5.25 | 4.98 | 5.45 | 5.28 | 5.32 | 5.14 | 5.09 | 5.27 | 5.07 | 5.36 | 6.59 | 5.63 | 5.4 | 5.44 | 4.66 | 4.98 | 4.95 | 4.71 | 4.88 | 0 | 4.86 | 0 | 4.59 | 4.73 | 4.88 | 4.88 | 5.07 | 5.05 | 4.83 | 4.74 | 5.01 | 351123 | 4.8151 |  |  | 240415 | 2175 | 280338 | 2204 | 256357 | 1811 | 292236 | 1856 | 44400 | 0 | 42000 | 0 | 106800 | 0 | 142800 | 0 | 336000 | 0 | 4.307% | 96 | 45221 | 351.12 |  | 78 | No scada available server OS failed
2025-05-08 | 2026 | 2025 | 2025-05-01 | 31 | 8876 | 8856 | 8467 | 8849 | 7901 | 8860 | 8872 | 8893 | 10832 | 8401 | 8890 | 10821 | 10846 | 10849 | 10850 | 10842 | 10856 | 10847 | 10879 | 10876 | 7949 | 7251 | 7934 | 7373 | 6841 | 7921 | 7369 | 0 | 7942 | 0 | 6837 | 6845 | 6867 | 6287 | 6856 | 5639 | 6859 | 6263 | 6857 | 4.58 | 4.46 | 3.97 | 4.15 | 3.78 | 4.38 | 4.4 | 4.13 | 4.08 | 3.95 | 4.01 | 4.04 | 3.98 | 3.84 | 3.92 | 3.95 | 4.15 | 4.01 | 3.99 | 4.01 | 3.76 | 3.87 | 3.95 | 4.26 | 4.2 | 4.22 | 4.21 | 0 | 5.44 | 0 | 4.17 | 4.15 | 4.32 | 4.55 | 6.32 | 4.45 | 4.87 | 4.31 | 5.39 | 315253 | 4.0569 |  |  | 240469 | 2175 | 280388 | 2204 | 256422 | 1811 | 292326 | 1856 | 64800 | 0 | 60000 | 0 | 78000 | 0 | 108000 | 0 | 310800 | 0 | 1.413% | 96 | 53455 | 315.25 |  | 78 | No scada available server OS failed
2025-05-09 | 2026 | 2025 | 2025-05-01 | 31 | 4021 | 4032 | 3562 | 3583 | 4562 | 3521 | 4024 | 3536 | 3832 | 3543 | 4026 | 4056 | 4059 | 4062 | 4053 | 4059 | 4055 | 4062 | 4067 | 4072 | 4531 | 4564 | 4521 | 4562 | 3587 | 4537 | 4526 | 0 | 4555 | 0 | 3579 | 3593 | 3061 | 3582 | 3578 | 3072 | 3569 | 3056 | 3566 | 4.0641 | 4.0593 | 4.0183 | 3.9908 | 3.9708 | 4.1533 | 4.1533 | 4.3953 | 4.0946 | 4.1891 | 4.5516 | 4.0448 | 4.0977 | 4.1514 | 4.115 | 4.1475 | 4.3757 | 4.3612 | 4.2471 | 4.3102 | 4.1 | 4.0657 | 3.9718 | 4.168 | 3.8945 | 3.9962 | 4.0166 | 0 | 4.1 | 0 | 3.8082 | 3.9238 | 4.0072 | 4.0677 | 4.0488 | 4.1113 | 3.861 | 3.9457 | 3.9454 | 144826 | 3.8852 |  |  | 240497 | 2176 | 280418 | 2205 | 256450 | 1812 | 292358 | 1857 | 33600 | 1200 | 36000 | 1200 | 33600 | 1200 | 38400 | 1200 | 141600 | 4800 | 2.228% | 44 | 3437 | 144.82 |  | 78 | No scada available server OS failed
2025-05-10 | 2026 | 2025 | 2025-05-01 | 31 | 6650 | 6658 | 6673 | 3206 | 4055 | 6692 | 6703 | 6698 | 6300 | 6712 | 6693 | 7043 | 6965 | 6923 | 7206 | 7190 | 7205 | 6965 | 6942 | 7164 | 4052 | 4048 | 4060 | 4048 | 3590 | 4083 | 4032 | 0 | 4116 | 0 | 3476 | 3598 | 3056 | 3587 | 3573 | 3577 | 3563 | 3561 | 3561 | 4.23 | 4.33 | 4.21 | 4.28 | 4.21 | 4.48 | 4.23 | 4.35 | 4.35 | 4.18 | 4.62 | 4.31 | 4.42 | 4.46 | 4.3 | 4.5 | 5.8 | 4.68 | 4.85 | 4.97 | 4.72 | 4.43 | 4.49 | 4.62 | 4.33 | 4.36 | 4.24 | 0 | 4.44 | 0 | 4.26 | 4.44 | 4.44 | 4.44 | 4.48 | 4.54 | 4.25 | 4.41 | 4.59 | 194224 | 4.2369 |  |  | 240525 | 2177 | 280445 | 2205 | 256497 | 1813 | 292416 | 1858 | 33600 | 1200 | 32400 | 0 | 56400 | 1200 | 69600 | 1200 | 192000 | 3600 | 1.145% | 0 | 0 | 194.22 |  | 78 | No scada available server OS failed
2025-05-11 | 2026 | 2025 | 2025-05-01 | 31 | 12206 | 12243 | 12116 | 5892 | 8608 | 12178 | 12998 | 12208 | 11345 | 12064 | 12092 | 11236 | 11299 | 11376 | 11407 | 11348 | 11369 | 11272 | 11454 | 11344 | 3206 | 8658 | 3569 | 8533 | 6275 | 8712 | 8517 | 0 | 8653 | 0 | 6087 | 6225 | 6105 | 6275 | 6260 | 6235 | 6273 | 6308 | 6262 | 4.85 | 5.37 | 4.76 | 4.77 | 5.09 | 5.19 | 4.8 | 4.87 | 5.25 | 4.98 | 5.45 | 5.28 | 5.32 | 5.14 | 5.09 | 5.27 | 5.07 | 5.36 | 6.59 | 5.63 | 5.4 | 5.44 | 4.66 | 4.98 | 4.95 | 4.71 | 4.88 | 0 | 4.86 | 0 | 4.59 | 4.73 | 4.88 | 4.88 | 5.07 | 5.05 | 4.83 | 4.74 | 5.01 | 338208 | 4.8151 |  |  | 240577 | 2177 | 280494 | 2206 | 256583 | 1813 | 292508 | 1858 | 62400 | 0 | 58800 | 1200 | 103200 | 0 | 110400 | 0 | 334800 | 1200 | 1.008% | 0 | 0 | 338.2 |  | 78 | No scada available server OS failed
2025-05-12 | 2026 | 2025 | 2025-05-01 | 31 | 3065 | 3066 | 2784 | 2259 | 4032 | 3086 | 3109 | 3046 | 3381 | 3125 | 3110 | 3357 | 3392 | 3347 | 3362 | 3317 | 3327 | 3465 | 3456 | 3408 | 758 | 2856 | 1102 | 4157 | 2670 | 4213 | 4215 | 0 | 4167 | 0 | 2699 | 2567 | 2607 | 2743 | 2736 | 2687 | 2673 | 2676 | 2642 | 3.93 | 3.99 | 3.9 | 3.78 | 3.4 | 4.13 | 3.8 | 4.05 | 3.76 | 3.86 | 4.06 | 3.98 | 4.04 | 4.03 | 3.88 | 4.18 | 3.41 | 4.09 | 4.29 | 4.06 | 4.5 | 3.75 | 3.14 | 3.53 | 3.02 | 3.42 | 3.48 | 0 | 3.31 | 0 | 3.29 | 3.51 | 3.38 | 3.42 | 3.69 | 3.98 | 3.43 | 3.41 | 3.47 | 112662 | 3.5474 |  |  | 240599 | 2178 | 280515 | 2206 | 256605 | 1813 | 292536 | 1859 | 26400 | 1200 | 25200 | 0 | 26400 | 0 | 33600 | 1200 | 111600 | 2400 | 0.9426% | 0 | 0 | 112.66 |  | 78 | No scada available server OS failed
2025-05-13 | 2026 | 2025 | 2025-05-01 | 31 | 6782 | 6734 | 6789 | 5976 | 4621 | 6821 | 6345 | 6599 | 7324 | 6759 | 6775 | 7344 | 7354 | 6898 | 7344 | 7256 | 7299 | 7378 | 7359 | 7387 | 4108 | 4516 | 4598 | 4588 | 3825 | 4576 | 4414 | 0 | 4579 | 0 | 3978 | 3996 | 3987 | 4116 | 4112 | 4022 | 4056 | 4008 | 927 | 4.85 | 5.26 | 4.68 | 5.05 | 5 | 5.11 | 4.84 | 4.48 | 5.09 | 4.83 | 5.29 | 5.04 | 5.15 | 5.24 | 4.99 | 5.44 | 4.96 | 5.48 | 5.43 | 5.67 | 0 | 5.29 | 4.82 | 5.04 | 5.32 | 5.01 | 5.03 | 0,0 | 4.81 | 0 | 4.95 | 5.01 | 4.99 | 5.16 | 5.21 | 4.87 | 5.18 | 4.85 | 5.19 | 205550 | 4.8055 |  |  | 240629 | 2179 | 280544 | 2207 | 256654 | 1814 | 292596 | 1860 | 36000 | 1200 | 34800 | 1200 | 58800 | 1200 | 72000 | 1200 | 201600 | 4800 | 1.922% | 0 | 0 | 205.55 |  | 78 | No scada available server OS failed
2025-05-14 | 2026 | 2025 | 2025-05-01 | 31 | 4822 | 4843 | 4845 | 4423 | 3239 | 4812 | 4878 | 4780 | 5060 | 4796 | 4821 | 5012 | 4749 | 1056 | 5076 | 5064 | 5096 | 5013 | 5043 | 5024 | 1998 | 3256 | 3212 | 3197 | 2911 | 3243 | 2368 | 0 | 3268 | 0 | 2943 | 2879 | 2867 | 2976 | 2913 | 2945 | 2901 | 2901 | 0 | 3.74 | 3.74 | 3.75 | 3.66 | 3.58 | 4.01 | 3.68 | 3.94 | 3.7 | 3.66 | 3.85 | 3.83 | 3.84 | 3.92 | 3.11 | 0 | 4.02 | 3.98 | 4.12 | 4.16 | 3.79 | 3.68 | 3.68 | 3.85 | 3.49 | 3.7 | 3.67 | 0 | 3.9 | 0 | 3.66 | 3.57 | 3.7 | 3.91 | 4.05 | 3.93 | 3.61 | 4.13 | 3.7 | 139230 | 3.4951 |  |  | 240650 | 2180 | 280563 | 2208 | 256689 | 1815 | 292634 | 1861 | 25200 | 1200 | 22800 | 1200 | 42000 | 1200 | 45600 | 1200 | 135600 | 4800 | 2.607% | 96 | 34850 | 139.23 |  | 78 | No scada available server OS failed
2025-05-15 | 2026 | 2025 | 2025-05-01 | 31 | 6421 | 6453 | 6423 | 6431 | 5032 | 6021 | 6023 | 6452 | 5890 | 6464 | 6479 | 5859 | 5867 | 5858 | 5842 | 5854 | 5875 | 5879 | 5870 | 5848 | 5067 | 5058 | 5022 | 4596 | 4572 | 5056 | 5042 | 0 | 5074 | 0 | 4529 | 3021 | 4572 | 4556 | 4581 | 4549 | 4588 | 2677 | 1265 | 3.93 | 3.99 | 3.9 | 3.78 | 3.4 | 4.13 | 3.8 | 4.05 | 3.76 | 3.86 | 4.06 | 3.98 | 4.04 | 4.03 | 3.88 | 4.18 | 3.41 | 4.09 | 4.29 | 4.06 | 4.5 | 3.75 | 3.14 | 3.53 | 3.02 | 3.42 | 3.48 | 0 | 3.31 | 0 | 3.29 | 3.51 | 3.38 | 3.42 | 3.69 | 3.98 | 3.43 | 3.41 | 3.47 | 194666 | 3.5474 |  |  | 240682 | 2180 | 280596 | 2208 | 256736 | 1816 | 292682 | 1861 | 38400 | 0 | 39600 | 0 | 56400 | 1200 | 57600 | 0 | 192000 | 1200 | 1.37% | 96 | 708 | 194.66 |  | 78 | No scada available server OS failed
2025-05-16 | 2026 | 2025 | 2025-05-01 | 31 | 9898 | 9872 | 10542 | 9888 | 8169 | 9874 | 10576 | 10587 | 8749 | 10556 | 10578 | 8787 | 8764 | 8769 | 8760 | 9946 | 9984 | 9966 | 7253 | 9989 | 8166 | 8152 | 8121 | 8176 | 7376 | 8162 | 8165 | 0 | 8175 | 0 | 7365 | 7370 | 7342 | 7359 | 7383 | 7376 | 7369 | 7388 | 6574 | 4.58 | 4.46 | 3.97 | 4.15 | 3.78 | 4.38 | 4.4 | 4.13 | 4.08 | 3.95 | 4.01 | 4.04 | 3.98 | 3.84 | 3.92 | 3.95 | 4.15 | 4.01 | 3.99 | 4.01 | 3.76 | 3.87 | 3.95 | 4.26 | 4.2 | 4.22 | 4.21 | 0 | 5.44 | 0 | 4.17 | 4.15 | 4.32 | 4.55 | 6.32 | 4.45 | 4.87 | 4.31 | 5.39 | 321526 | 4.0569 |  |  | 240740 | 2180 | 280655 | 2208 | 256811 | 1816 | 292755 | 1861 | 69600 | 0 | 70800 | 0 | 90000 | 0 | 87600 | 0 | 318000 | 0 | 1.097% | 96 | 1873 | 321.52 |  | 78 | No scada available server OS failed
2025-05-17 | 2026 | 2025 | 2025-05-01 | 31 | 5673 | 5132 | 5684 | 5681 | 4123 | 5424 | 5163 | 5642 | 6458 | 5635 | 5673 | 6475 | 6438 | 6473 | 6451 | 6423 | 6446 | 6475 | 1297 | 6452 | 4135 | 4154 | 4111 | 4156 | 2867 | 4127 | 4123 | 0 | 4145 | 0 | 3521 | 3536 | 3573 | 3557 | 3564 | 3535 | 3547 | 3550 | 3569 | 4.0641 | 4.0593 | 4.0183 | 3.9908 | 3.9708 | 4.1533 | 4.1533 | 4.3953 | 4.0946 | 4.1891 | 4.5516 | 4.0448 | 4.0977 | 4.1514 | 4.115 | 4.1475 | 4.3757 | 4.3612 | 4.2471 | 4.3102 | 4.1 | 4.0657 | 3.9718 | 4.168 | 3.8945 | 3.9962 | 4.0166 | 0 | 4.1 | 0 | 3.8082 | 3.9238 | 4.0072 | 4.0677 | 4.0488 | 4.1113 | 3.861 | 3.9457 | 3.9454 | 176988 | 3.8852 |  |  | 240768 | 2181 | 280682 | 2208 | 256852 | 1816 | 292804 | 1862 | 33600 | 1200 | 32400 | 0 | 49200 | 0 | 58800 | 1200 | 174000 | 2400 | 1.688% | 96 | 15134 | 176.98 |  | 78 | No scada available server OS failed
2025-05-18 | 2026 | 2025 | 2025-05-01 | 31 | 3466 | 3564 | 3552 | 3546 | 3521 | 3576 | 3537 | 3551 | 4056 | 3532 | 3543 | 4052 | 4033 | 4042 | 4034 | 4011 | 4047 | 4052 | 4040 | 4057 | 3523 | 3511 | 3525 | 3514 | 3162 | 3515 | 3543 | 0 | 3548 | 0 | 2487 | 3145 | 3121 | 3154 | 3132 | 3136 | 3156 | 3149 | 3152 | 3.93 | 3.99 | 3.9 | 3.78 | 3.4 | 4.13 | 3.8 | 4.05 | 3.76 | 3.86 | 4.06 | 3.98 | 4.04 | 4.03 | 3.88 | 4.18 | 3.41 | 4.09 | 4.29 | 4.06 | 4.5 | 3.75 | 3.14 | 3.53 | 3.02 | 3.42 | 3.48 | 0 | 3.31 | 0 | 3.29 | 3.51 | 3.38 | 3.42 | 3.69 | 3.98 | 3.43 | 3.41 | 3.47 | 131285 | 3.5474 |  |  | 240792 | 2181 | 280705 | 2209 | 256878 | 1817 | 292837 | 1862 | 28800 | 0 | 27600 | 1200 | 31200 | 1200 | 39600 | 0 | 127200 | 2400 | 3.112% | 96 | 55 | 131.28 |  | 78 | No scada available server OS failed
2025-05-19 | 2026 | 2025 | 2025-05-01 | 31 | 3821 | 3824 | 3809 | 3815 | 3190 | 3821 | 3829 | 3825 | 3550 | 3839 | 3852 | 3523 | 3522 | 3556 | 3528 | 3542 | 3541 | 3540 | 3559 | 3567 | 4102 | 2789 | 4115 | 4136 | 4021 | 4140 | 4109 | 0 | 4121 | 0 | 4101 | 4111 | 4116 | 4121 | 4119 | 4153 | 4132 | 4127 | 4129 | 3.74 | 3.74 | 3.75 | 3.66 | 3.58 | 4.01 | 3.68 | 3.94 | 3.7 | 3.66 | 3.85 | 3.83 | 3.84 | 3.92 | 3.11 | 0 | 4.02 | 3.98 | 4.12 | 4.16 | 3.79 | 3.68 | 3.68 | 3.85 | 3.49 | 3.7 | 3.67 | 0 | 3.9 | 0 | 3.66 | 3.57 | 3.7 | 3.91 | 4.05 | 3.93 | 3.61 | 4.13 | 3.7 | 141695 | 3.4951 |  |  | 240825 | 2182 | 280730 | 2210 | 256906 | 1817 | 292866 | 1863 | 39600 | 1200 | 30000 | 1200 | 33600 | 0 | 34800 | 1200 | 138000 | 3600 | 2.608% | 96 | 5662 | 141.69 |  | 78 | No scada available server OS failed
2025-05-20 | 2026 | 2025 | 2025-05-01 | 31 | 5587 | 5267 | 5278 | 5575 | 5201 | 5562 | 5579 | 5565 | 5321 | 5032 | 5543 | 5342 | 5347 | 5352 | 5353 | 5021 | 5042 | 5034 | 5045 | 5067 | 4693 | 5205 | 5200 | 5215 | 3501 | 5210 | 5242 | 0 | 5245 | 0 | 3515 | 3690 | 3692 | 3679 | 3698 | 3678 | 3682 | 3516 | 3696 | 4.0641 | 4.0593 | 4.0183 | 3.9908 | 3.9708 | 4.1533 | 4.1533 | 4.3953 | 4.0946 | 4.1891 | 4.5516 | 4.0448 | 4.0977 | 4.1514 | 4.115 | 4.1475 | 4.3757 | 4.3612 | 4.2471 | 4.3102 | 4.1 | 4.0657 | 3.9718 | 4.168 | 3.8945 | 3.9962 | 4.0166 | 0 | 4.1 | 0 | 3.8082 | 3.9238 | 4.0072 | 4.0677 | 4.0488 | 4.1113 | 3.861 | 3.9457 | 3.9454 | 178470 | 3.8852 |  |  | 240855 | 2183 | 280764 | 2210 | 256946 | 1818 | 292909 | 1864 | 36000 | 1200 | 40800 | 0 | 48000 | 1200 | 51600 | 1200 | 176400 | 3600 | 1.16% | 96 | 2876 | 178.47 |  | 78 | No scada available server OS failed
2025-05-21 | 2026 | 2025 | 2025-05-01 | 31 | 5618 | 5628 | 5632 | 5640 | 5601 | 5079 | 5633 | 5622 | 5173 | 5656 | 5674 | 5174 | 5164 | 5156 | 5177 | 5148 | 5142 | 5156 | 5176 | 5178 | 5632 | 5621 | 4621 | 5637 | 4021 | 5636 | 5644 | 0 | 5654 | 0 | 4631 | 4637 | 4645 | 4642 | 4666 | 4665 | 4633 | 4647 | 4664 | 3.93 | 3.99 | 3.9 | 3.78 | 3.4 | 4.13 | 3.8 | 4.05 | 3.76 | 3.86 | 4.06 | 3.98 | 4.04 | 4.03 | 3.88 | 4.18 | 3.41 | 4.09 | 4.29 | 4.06 | 4.5 | 3.75 | 3.14 | 3.53 | 3.02 | 3.42 | 3.48 | 0 | 3.31 | 0 | 3.29 | 3.51 | 3.38 | 3.42 | 3.69 | 3.98 | 3.43 | 3.41 | 3.47 | 191723 | 3.5474 |  |  | 240892 | 2184 | 280800 | 2211 | 256987 | 1819 | 292951 | 1865 | 44400 | 1200 | 43200 | 1200 | 49200 | 1200 | 50400 | 1200 | 187200 | 4800 | 2.359% | 96 | 9688 | 191.73 |  | 78 | No scada available server OS failed
2025-05-22 | 2026 | 2025 | 2025-05-01 | 31 | 6537 | 6585 | 6279 | 6263 | 8296 | 6578 | 6542 | 6545 | 9753 | 6567 | 6582 | 9745 | 9746 | 9723 | 9748 | 9752 | 9758 | 9742 | 9772 | 9784 | 8833 | 8842 | 8829 | 8835 | 6041 | 8846 | 8852 | 0 | 8853 | 0 | 5885 | 6046 | 6042 | 6055 | 6057 | 6048 | 5564 | 6049 | 6067 | 4.85 | 5.26 | 4.68 | 5.05 | 5 | 5.11 | 4.84 | 4.48 | 5.09 | 4.83 | 5.29 | 5.04 | 5.15 | 5.24 | 4.99 | 5.44 | 4.96 | 5.48 | 5.43 | 5.67 | 0 | 5.29 | 4.82 | 5.04 | 5.32 | 5.01 | 5.03 | 0,0 | 4.81 | 0 | 4.95 | 5.01 | 4.99 | 5.16 | 5.21 | 4.87 | 5.18 | 4.85 | 5.19 | 286041 | 4.8055 |  |  | 240941 | 2185 | 280858 | 2212 | 257037 | 1820 | 293032 | 1866 | 58800 | 1200 | 69600 | 1200 | 60000 | 1200 | 97200 | 1200 | 285600 | 4800 | 0.1542% | 96 | 3218 | 286.08 |  | 78 | No scada available server OS failed
2025-05-23 | 2026 | 2025 | 2025-05-01 | 31 | 2801 | 2812 | 2817 | 2814 | 2032 | 2801 | 2809 | 2816 | 3103 | 2832 | 2840 | 3108 | 3107 | 3118 | 3001 | 3109 | 3111 | 3104 | 3128 | 3135 | 2045 | 2042 | 2007 | 2021 | 1521 | 2014 | 2038 | 0 | 2042 | 0 | 1532 | 1542 | 1526 | 1535 | 1542 | 1540 | 1538 | 1539 | 1542 | 3.1605 | 3.5608 | 3.1151 | 3.3498 | 3.3269 | 3.1994 | 3.1127 | 3.3075 | 3.3208 | 2.8659 | 3.1959 | 3.2102 | 3.4381 | 3.1364 | 3.1875 | 3.02 | 3.2244 | 3.1802 | 3.1785 | 3.0892 | 3.3397 | 3.33 | 3.1537 | 2.9716 | 3.1007 | 2.7795 | 3.1705 | 0 | 3.0811 | 0 | 3.1179 | 2.8482 | 2.909 | 3.1531 | 3.0024 | 3.149 | 3.0592 | 3.2 | 3.0888 | 87964 | 2.9906 |  |  | 240953 | 2186 | 280871 | 2213 | 257057 | 1821 | 293057 | 1867 | 14400 | 1200 | 15600 | 1200 | 24000 | 1200 | 30000 | 1200 | 84000 | 4800 | 4.506% | 96 | 45073 | 87.96 |  | 78 | No scada available server OS failed
2025-05-24 | 2026 | 2025 | 2025-05-01 | 31 | 7042 | 7032 | 7021 | 7022 | 7732 | 7053 | 7043 | 7033 | 7342 | 7057 | 7069 | 7352 | 7347 | 7349 | 7354 | 6521 | 7365 | 7359 | 7387 | 7395 | 7768 | 7758 | 7743 | 7728 | 5831 | 7721 | 7772 | 0 | 7787 | 0 | 6467 | 6457 | 6043 | 6452 | 6456 | 6451 | 6458 | 6487 | 6466 | 4.85 | 5.26 | 4.68 | 5.05 | 5 | 5.11 | 4.84 | 4.48 | 5.09 | 4.83 | 5.29 | 5.04 | 5.15 | 5.24 | 4.99 | 5.44 | 4.96 | 5.48 | 5.43 | 5.67 | 0 | 5.29 | 4.82 | 5.04 | 5.32 | 5.01 | 5.03 | 0 | 4.81 | 0 | 4.95 | 5.01 | 4.99 | 5.16 | 5.21 | 4.87 | 5.18 | 4.85 | 5.19 | 261720 | 4.6823 |  |  | 241005 | 2187 | 280922 | 2214 | 257109 | 1822 | 293117 | 1867 | 62400 | 1200 | 61200 | 1200 | 62400 | 1200 | 72000 | 0 | 258000 | 3600 | 1.421% | 96 | 54003 | 261.72 |  | 78 | No scada available server OS failed
2025-05-25 | 2026 | 2025 | 2025-05-01 | 31 | 7125 | 7129 | 7132 | 7136 | 5501 | 7142 | 7122 | 7126 | 7109 | 6749 | 7164 | 7110 | 7118 | 7126 | 7129 | 6898 | 6473 | 7108 | 7142 | 7149 | 5521 | 5518 | 5509 | 5524 | 5842 | 5516 | 5528 | 0 | 5532 | 0 | 5589 | 5822 | 5821 | 5842 | 5846 | 5844 | 5824 | 5839 | 5842 | 4.0641 | 4.0593 | 4.0183 | 3.9908 | 3.9708 | 4.1533 | 4.1533 | 4.3953 | 4.0946 | 4.1891 | 4.5516 | 4.0448 | 4.0977 | 4.1514 | 4.115 | 4.1475 | 4.3757 | 4.3612 | 4.2471 | 4.3102 | 4.1 | 4.0657 | 3.9718 | 4.168 | 3.8945 | 3.9962 | 4.0166 | 0 | 4.1 | 0 | 3.8082 | 3.9238 | 4.0072 | 4.0677 | 4.0488 | 4.1113 | 3.861 | 3.9457 | 3.9454 | 236447 | 3.8852 |  |  | 241053 | 2187 | 280958 | 2214 | 257161 | 1822 | 293174 | 1868 | 57600 | 0 | 43200 | 0 | 62400 | 0 | 68400 | 1200 | 231600 | 1200 | 2.05% | 96 | 64981 | 236.44 |  | 78 | No scada available server OS failed
2025-05-26 | 2026 | 2025 | 2025-05-01 | 31 | 4453 | 4458 | 4421 | 4290 | 3602 | 4456 | 4434 | 4426 | 3729 | 4456 | 4467 | 3742 | 3745 | 3749 | 3752 | 3750 | 3753 | 3321 | 3356 | 3758 | 3656 | 3643 | 3622 | 3234 | 3552 | 3652 | 3649 | 0 | 3424 | 0 | 3553 | 3572 | 3522 | 3562 | 3565 | 3560 | 3532 | 3529 | 3321 | 3.74 | 3.74 | 3.75 | 3.66 | 3.58 | 4.01 | 3.68 | 3.94 | 3.7 | 3.66 | 3.85 | 3.83 | 3.84 | 3.92 | 3.11 | 0 | 4.02 | 3.98 | 4.12 | 4.16 | 3.79 | 3.68 | 3.68 | 3.85 | 3.49 | 3.7 | 3.67 | 0 | 3.9 | 0 | 3.66 | 3.57 | 3.7 | 3.91 | 4.05 | 3.93 | 3.61 | 4.13 | 3.7 | 140266 | 3.4951 |  |  | 241082 | 2188 | 280981 | 2215 | 257194 | 1823 | 293204 | 1868 | 34800 | 1200 | 27600 | 1200 | 39600 | 1200 | 36000 | 0 | 138000 | 3600 | 1.616% | 94 | 14022 | 140.26 |  | 78 | No scada available server OS failed
2025-05-27 | 2026 | 2025 | 2025-05-01 | 31 | 8741 | 10621 | 10623 | 10219 | 11850 | 10227 | 10615 | 10632 | 14750 | 10645 | 10658 | 14755 | 14752 | 14749 | 14754 | 14758 | 14762 | 14742 | 14782 | 12689 | 11856 | 11852 | 11811 | 11861 | 10450 | 11852 | 11859 | 0 | 10981 | 0 | 10452 | 9572 | 10421 | 10465 | 10459 | 10456 | 10448 | 10463 | 10465 | 4.85 | 5.37 | 4.76 | 4.77 | 5.09 | 5.19 | 4.8 | 4.87 | 5.25 | 4.98 | 5.45 | 5.28 | 5.32 | 5.14 | 5.09 | 5.27 | 5.07 | 5.36 | 6.59 | 5.63 | 5.4 | 5.44 | 4.66 | 4.98 | 4.95 | 4.71 | 4.88 | 0 | 4.86 | 0 | 4.59 | 4.73 | 4.88 | 4.88 | 5.07 | 5.05 | 4.83 | 4.74 | 5.01 | 436047 | 4.8151 |  |  | 241168 | 2188 | 281059 | 2215 | 257271 | 1823 | 293325 | 1868 | 103200 | 0 | 93600 | 0 | 92400 | 0 | 145200 | 0 | 434400 | 0 | 0.3777% | 96 | 86461 | 436.04 |  | 78 | No scada available server OS failed
2025-05-28 | 2026 | 2025 | 2025-05-01 | 31 | 5219 | 16389 | 16385 | 16380 | 9901 | 16374 | 15953 | 16387 | 13721 | 16382 | 16389 | 13750 | 13752 | 12032 | 13759 | 13021 | 13752 | 13744 | 13759 | 13782 | 9957 | 9952 | 9932 | 9967 | 7450 | 9962 | 9969 | 0 | 9974 | 0 | 7432 | 7021 | 7422 | 7437 | 7442 | 7445 | 7431 | 7447 | 7451 | 4.73 | 5.25 | 4.97 | 4.56 | 4.53 | 5.13 | 4.74 | 4.54 | 5.04 | 4.65 | 5.08 | 5.09 | 5.15 | 6.01 | 4.79 | 4.63 | 4.4 | 4.69 | 5.17 | 5.05 | 4.8 | 4.95 | 4.57 | 4.87 | 4.67 | 4.45 | 4.48 | 0 | 4.42 | 0 | 4.25 | 4.37 | 4.48 | 4.63 | 4.57 | 4.44 | 4.53 | 4.53 | 4.67 | 424522 | 4.5097 |  |  | 241229 | 2189 | 281125 | 2216 | 257382 | 1823 | 293437 | 1869 | 73200 | 1200 | 79200 | 1200 | 133200 | 0 | 134400 | 1200 | 420000 | 3600 | 1.065% | 96 | 167998 | 424.52 |  | 78 | No scada available server OS failed
2025-05-29 | 2026 | 2025 | 2025-05-01 | 31 | 16456 | 16445 | 16454 | 16001 | 16466 | 16423 | 16427 | 16421 | 16001 | 16456 | 16467 | 16467 | 12578 | 14842 | 16061 | 16032 | 16034 | 16027 | 16072 | 16085 | 12252 | 12256 | 12235 | 11021 | 13852 | 12264 | 12268 | 0 | 12276 | 0 | 13863 | 10521 | 13853 | 13845 | 12853 | 13857 | 13839 | 13879 | 13897 | 5.58 | 6.55 | 5.67 | 5.72 | 6.71 | 6.27 | 6 | 5.79 | 6 | 6.65 | 5.98 | 6.36 | 6.31 | 5.42 | 6.29 | 6.5 | 6.63 | 6.48 | 6.75 | 6.78 | 6.72 | 6.39 | 5.76 | 5.9 | 6.3 | 5.66 | 5.5 | 0 | 5.28 | 0 | 5.85 | 5.65 | 5.63 | 5.65 | 5.94 | 5.56 | 5.81 | 5.84 | 5.94 | 539046 | 5.739 |  |  | 241340 | 2189 | 281205 | 2216 | 257505 | 1823 | 293566 | 1869 | 133200 | 0 | 96000 | 0 | 147600 | 0 | 154800 | 0 | 531600 | 0 | 1.381% | 96 | 52674 | 539.04 |  | 78 | No scada available server OS failed
2025-05-30 | 2026 | 2025 | 2025-05-01 | 31 | 15835 | 14321 | 15869 | 14797 | 11790 | 15894 | 15864 | 15892 | 18652 | 15889 | 15896 | 18632 | 18643 | 18645 | 18665 | 17521 | 18675 | 18653 | 18678 | 18692 | 11789 | 11797 | 11735 | 8749 | 13604 | 11795 | 10990 | 0 | 11786 | 0 | 13631 | 13656 | 13621 | 13645 | 13652 | 13642 | 13625 | 13647 | 13664 | 5.8621 | 6.3056 | 5.2877 | 5.3705 | 5.0465 | 5.8957 | 5.8957 | 5.8117 | 6.2648 | 4.8664 | 5.6272 | 5.7042 | 5.5212 | 5.7344 | 6.0185 | 5.5628 | 6.2912 | 5.9452 | 6.1094 | 6.4611 | 5.9728 | 4.9143 | 5.1145 | 5.336 | 5.0755 | 5.3435 | 5.0553 | 0 | 5 | 0 | 4.943 | 4.9765 | 5.2576 | 5.6703 | 5.5863 | 5.4673 | 5.2684 | 5.2848 | 5.2838 | 552531 | 5.2598 |  |  | 241453 | 2189 | 281280 | 2216 | 257621 | 1823 | 293720 | 1869 | 135600 | 0 | 90000 | 0 | 139200 | 0 | 184800 | 0 | 549600 | 0 | 0.5305% | 96 | 111665 | 552.53 |  | 78 | No scada available server OS failed
2025-05-31 | 2026 | 2025 | 2025-05-01 | 31 | 27801 | 27807 | 27806 | 27819 | 17106 | 27841 | 27854 | 27867 | 26901 | 27878 | 27897 | 24649 | 26906 | 26909 | 26945 | 26942 | 26963 | 26942 | 26983 | 26997 | 17115 | 17167 | 17109 | 15902 | 15980 | 17190 | 17189 | 0 | 17192 | 0 | 17851 | 17832 | 17842 | 17821 | 17300 | 17839 | 17847 | 17852 | 17869 | 7.28 | 7.74 | 7.38 | 7.5 | 6.95 | 6.64 | 0 | 7.59 | 7.79 | 7.37 | 7.73 | 7.52 | 7.72 | 7.67 | 7.75 | 7.66 | 8.38 | 7.44 | 8.44 | 7.02 | 6.9 | 7.2 | 7.24 | 7.4 | 7.39 | 7.05 | 6.74 | 0 | 7.37 | 0 | 6.79 | 6.65 | 6.54 | 7.02 | 7.65 | 7.66 | 6.74 | 6.53 | 7.19 | 829710 | 6.7597 |  |  | 241599 | 2189 | 281393 | 2216 | 257829 | 1823 | 293942 | 1869 | 175200 | 0 | 135600 | 0 | 249600 | 0 | 266400 | 0 | 826800 | 0 | 0.3507% | 96 | 291053 | 829.71 |  | 78 | No scada available server OS failed
2025-06-01 | 2026 | 2025 | 2025-06-01 | 30 | 25119 | 25121 | 25115 | 25122 | 19223 | 25134 | 25123 | 25131 | 20263 | 25165 | 25172 | 23119 | 23112 | 23132 | 23145 | 23144 | 23151 | 23134 | 23167 | 23178 | 19243 | 18521 | 18501 | 18509 | 17921 | 19245 | 19252 | 0 | 19267 | 0 | 17945 | 17924 | 17952 | 17946 | 17956 | 17949 | 17932 | 17967 | 17959 | 7.13 | 7.22 | 7.2 | 7.2 | 6.86 | 6.84 | 7.52 | 7.38 | 7.33 | 7.21 | 7.51 | 7.19 | 7.34 | 7.41 | 7.21 | 7.4 | 7.01 | 7.28 | 7.58 | 7.54 | 6.5 | 7.13 | 7.11 | 7.2 | 6.69 | 6.89 | 6.85 | 0 | 7.02 | 0 | 6.26 | 6.56 | 6.37 | 6.77 | 7.01 | 7.01 | 6.41 | 6.12 | 6.55 | 785959 | 6.6618 |  |  | 241748 | 2189 | 281518 | 2216 | 258017 | 1823 | 294132 | 1869 | 178800 | 0 | 150000 | 0 | 225600 | 0 | 228000 | 0 | 782400 | 0 | 0.4528% | 96 | 247411 | 785.95 |  | 78 | No scada available server OS failed
2025-06-02 | 2026 | 2025 | 2025-06-01 | 30 | 10401 | 10407 | 10402 | 9518 | 9544 | 10409 | 10399 | 8107 | 12223 | 10456 | 10467 | 12232 | 12234 | 12245 | 12256 | 12252 | 12254 | 12233 | 12267 | 11499 | 9556 | 9552 | 9545 | 10260 | 9102 | 10256 | 10267 | 0 | 10278 | 0 | 9105 | 8664 | 9109 | 8678 | 9111 | 9110 | 9103 | 9114 | 9116 | 4.85 | 5.37 | 4.76 | 4.77 | 5.09 | 5.19 | 4.8 | 4.87 | 5.25 | 4.98 | 5.45 | 5.28 | 5.32 | 5.14 | 5.09 | 5.27 | 5.07 | 5.36 | 6.59 | 5.63 | 5.4 | 5.44 | 4.66 | 4.98 | 4.95 | 4.71 | 4.88 | 0 | 4.86 | 0 | 4.59 | 4.73 | 4.88 | 4.88 | 5.07 | 5.05 | 4.83 | 4.74 | 5.01 | 381731 | 4.8151 |  |  | 241822 | 2189 | 281584 | 2216 | 258092 | 1823 | 294233 | 1869 | 88800 | 0 | 79200 | 0 | 90000 | 0 | 121200 | 0 | 379200 | 0 | 0.663% | 96 | 14431 | 381.73 |  | 78 | No scada available server OS failed
2025-06-03 | 2026 | 2025 | 2025-06-01 | 30 | 21256 | 21262 | 21242 | 21234 | 18241 | 21265 | 21254 | 21262 | 21621 | 21268 | 19969 | 21632 | 21634 | 21638 | 21642 | 21640 | 21652 | 21657 | 21647 | 20782 | 18242 | 18236 | 18230 | 18256 | 18022 | 18251 | 18276 | 0 | 18280 | 0 | 18067 | 18065 | 18046 | 17021 | 18037 | 18069 | 18065 | 17489 | 18076 | 5.8621 | 6.3056 | 5.2877 | 5.3705 | 5.0465 | 5.8957 | 5.8957 | 5.8117 | 6.2648 | 4.8664 | 5.6272 | 5.7042 | 5.5212 | 5.7344 | 6.0185 | 5.5628 | 6.2912 | 5.9452 | 6.1094 | 6.4611 | 5.9728 | 4.9143 | 5.1145 | 5.336 | 5.0755 | 5.3435 | 5.0553 | 0 | 5 | 0 | 4.943 | 4.9765 | 5.2576 | 5.6703 | 5.5863 | 5.4673 | 5.2684 | 5.2848 | 5.2838 | 730526 | 5.2598 |  |  | 241970 | 2189 | 281705 | 2216 | 258250 | 1823 | 294412 | 1869 | 177600 | 0 | 145200 | 0 | 189600 | 0 | 214800 | 0 | 727200 | 0 | 0.4553% | 96 | 118681 | 730.52 |  | 78 | No scada available server OS failed
2025-06-04 | 2026 | 2025 | 2025-06-01 | 30 | 5742 | 5721 | 5723 | 5734 | 2321 | 5728 | 5722 | 5719 | 6001 | 5732 | 5747 | 6021 | 6025 | 6030 | 6045 | 6023 | 6033 | 6021 | 6038 | 6039 | 2345 | 2356 | 2342 | 2365 | 3050 | 2362 | 2356 | 0 | 2372 | 0 | 3059 | 3069 | 3054 | 3059 | 3051 | 3055 | 3034 | 3059 | 3056 | 4.0641 | 4.0593 | 4.0183 | 3.9908 | 3.9708 | 4.1533 | 4.1533 | 4.3953 | 4.0946 | 4.1891 | 4.5516 | 4.0448 | 4.0977 | 4.1514 | 4.115 | 4.1475 | 4.3757 | 4.3612 | 4.2471 | 4.3102 | 4.1 | 4.0657 | 3.9718 | 4.168 | 3.8945 | 3.9962 | 4.0166 | 0 | 4.1 | 0 | 3.8082 | 3.9238 | 4.0072 | 4.0677 | 4.0488 | 4.1113 | 3.861 | 3.9457 | 3.9454 | 161209 | 3.8852 |  |  | 241995 | 2189 | 281720 | 2216 | 258292 | 1823 | 294461 | 1869 | 30000 | 0 | 18000 | 0 | 50400 | 0 | 58800 | 0 | 157200 | 0 | 2.487% | 96 | 19160 | 161.2 |  | 78 | No scada available server OS failed
2025-06-05 | 2026 | 2025 | 2025-06-01 | 30 | 9011 | 9018 | 9015 | 8627 | 6821 | 7959 | 9009 | 9012 | 8001 | 9019 | 8644 | 8012 | 8015 | 8012 | 8021 | 8016 | 8025 | 8019 | 7778 | 8078 | 6832 | 6828 | 6809 | 6845 | 6215 | 6840 | 6856 | 0 | 6862 | 0 | 6218 | 6221 | 6224 | 6232 | 5589 | 5753 | 6211 | 6232 | 6245 | 4.85 | 5.26 | 4.68 | 5.05 | 5 | 5.11 | 4.84 | 4.48 | 5.09 | 4.83 | 5.29 | 5.04 | 5.15 | 5.24 | 4.99 | 5.44 | 4.96 | 5.48 | 5.43 | 5.67 | 0 | 5.29 | 4.82 | 5.04 | 5.32 | 5.01 | 5.03 | 0 | 4.81 | 0 | 4.95 | 5.01 | 4.99 | 5.16 | 5.21 | 4.87 | 5.18 | 4.85 | 5.19 | 275124 | 4.6823 |  |  | 242045 | 2190 | 281765 | 2216 | 258358 | 1824 | 294527 | 1869 | 60000 | 1200 | 54000 | 0 | 79200 | 1200 | 79200 | 0 | 272400 | 2400 | 0.9901% | 96 | 8433 | 275.12 |  | 78 | No scada available server OS failed
2025-06-06 | 2026 | 2025 | 2025-06-01 | 30 | 14601 | 14605 | 12264 | 14606 | 9321 | 14611 | 14608 | 14615 | 12801 | 14632 | 14640 | 12857 | 12846 | 12852 | 12845 | 12843 | 12842 | 12847 | 12867 | 12876 | 9354 | 9352 | 9345 | 9359 | 7790 | 9355 | 9362 | 0 | 9365 | 0 | 7756 | 7759 | 7784 | 7787 | 7780 | 6689 | 7769 | 7782 | 7789 | 4.85 | 5.37 | 4.76 | 4.77 | 5.09 | 5.19 | 4.8 | 4.87 | 5.25 | 4.98 | 5.45 | 5.28 | 5.32 | 5.14 | 5.09 | 5.27 | 5.07 | 5.36 | 6.59 | 5.63 | 5.4 | 5.44 | 4.66 | 4.98 | 4.95 | 4.71 | 4.88 | 0 | 4.86 | 0 | 4.59 | 4.73 | 4.88 | 4.88 | 5.07 | 5.05 | 4.83 | 4.74 | 5.01 | 409156 | 4.8151 |  |  | 242109 | 2190 | 281828 | 2216 | 258466 | 1824 | 294623 | 1869 | 76800 | 0 | 75600 | 0 | 129600 | 0 | 115200 | 0 | 397200 | 0 | 2.922% | 96 | 35674 | 409.15 |  | 78 | No scada available server OS failed
2025-06-07 | 2026 | 2025 | 2025-06-01 | 30 | 19801 | 19807 | 19809 | 18098 | 13021 | 19815 | 19801 | 19811 | 16321 | 19819 | 19821 | 16342 | 16345 | 16347 | 16344 | 16332 | 16322 | 16329 | 16345 | 16352 | 13051 | 13042 | 13038 | 13045 | 10821 | 13042 | 12590 | 0 | 12542 | 0 | 10829 | 10824 | 10832 | 10835 | 10838 | 10840 | 10831 | 10841 | 10844 | 5.8621 | 6.3056 | 5.2877 | 5.3705 | 5.0465 | 5.8957 | 5.8957 | 5.8117 | 6.2648 | 4.8664 | 5.6272 | 5.7042 | 5.5212 | 5.7344 | 6.0185 | 5.5628 | 6.2912 | 5.9452 | 6.1094 | 6.4611 | 5.9728 | 4.9143 | 5.1145 | 5.336 | 5.0755 | 5.3435 | 5.0553 | 0 | 5 | 0 | 4.943 | 4.9765 | 5.2576 | 5.6703 | 5.5863 | 5.4673 | 5.2684 | 5.2848 | 5.2838 | 551667 | 5.2598 |  |  | 242199 | 2190 | 281913 | 2216 | 258613 | 1824 | 294759 | 1869 | 108000 | 0 | 102000 | 0 | 176400 | 0 | 163200 | 0 | 549600 | 0 | 0.3747% | 96 | 70776 | 551.66 |  | 78 | No scada available server OS failed
2025-06-08 | 2026 | 2025 | 2025-06-01 | 30 | 20601 | 20609 | 20611 | 20615 | 12000 | 20619 | 20605 | 20621 | 18150 | 20626 | 20632 | 18154 | 18159 | 18162 | 18167 | 18165 | 18169 | 18159 | 18176 | 18184 | 12012 | 12015 | 12001 | 12145 | 10350 | 12121 | 12125 | 0 | 12132 | 0 | 10379 | 10372 | 10376 | 10374 | 10362 | 10368 | 10359 | 10367 | 10370 | 5.63 | 6.04 | 5.55 | 5.6 | 6.19 | 6.25 | 5.75 | 5.53 | 5.55 | 5.54 | 5.96 | 5.74 | 5.9 | 5.75 | 5.91 | 5.82 | 5.86 | 6.15 | 6.47 | 6.22 | 5.08 | 6.26 | 5.87 | 5.93 | 5.43 | 5.57 | 5.63 | 0 | 5.51 | 0 | 5.16 | 5.45 | 5.48 | 5.59 | 5.63 | 5.54 | 5.55 | 5.62 | 5.36 | 567412 | 5.4377 |  |  | 242285 | 2190 | 281993 | 2216 | 258767 | 1824 | 294910 | 1869 | 103200 | 0 | 96000 | 0 | 184800 | 0 | 181200 | 0 | 565200 | 0 | 0.3898% | 96 | 100593 | 567.41 |  | 78 | No scada available server OS failed
2025-06-09 | 2026 | 2025 | 2025-06-01 | 30 | 24750 | 24757 | 24743 | 24298 | 23401 | 24756 | 24732 | 24745 | 21821 | 24775 | 24789 | 21850 | 21856 | 21520 | 21860 | 21845 | 21861 | 21848 | 21878 | 21250 | 23422 | 23419 | 23411 | 23421 | 20121 | 21998 | 23434 | 0 | 22789 | 0 | 20114 | 20124 | 20128 | 20135 | 20138 | 20140 | 20119 | 19629 | 20145 | 7.28 | 7.74 | 7.38 | 7.5 | 6.95 | 6.64 | 7.2 | 7.59 | 7.79 | 7.37 | 7.73 | 7.52 | 7.72 | 7.67 | 7.75 | 7.66 | 8.38 | 7.44 | 8.44 | 7.02 | 6.9 | 7.2 | 7.24 | 7.4 | 7.39 | 7.05 | 6.74 | 0 | 7.37 | 0 | 6.79 | 6.65 | 6.54 | 7.02 | 7.65 | 7.66 | 6.74 | 6.53 | 7.19 | 826022 | 6.9444 |  |  | 242452 | 2190 | 282147 | 2216 | 258952 | 1824 | 295091 | 1869 | 200400 | 0 | 184800 | 0 | 222000 | 0 | 217200 | 0 | 824400 | 0 | 0.1964% | 96 | 186028 | 826.02 |  | 78 | No scada available server OS failed
2025-06-10 | 2026 | 2025 | 2025-06-01 | 30 | 13301 | 11520 | 13323 | 13335 | 12629 | 13346 | 13337 | 13364 | 22332 | 13372 | 13378 | 22326 | 22342 | 20987 | 21535 | 21522 | 22321 | 22316 | 22345 | 21452 | 12672 | 12662 | 11201 | 12678 | 11701 | 12672 | 12689 | 0 | 12692 | 0 | 11711 | 11723 | 11721 | 11723 | 11732 | 11734 | 11721 | 11735 | 11742 | 5.63 | 6.04 | 5.55 | 5.6 | 6.19 | 6.25 | 5.75 | 5.53 | 5.55 | 5.54 | 5.96 | 5.74 | 5.4 | 5.5 | 5.41 | 5.42 | 5.86 | 6.15 | 6.47 | 6.22 | 5.08 | 6.26 | 5.87 | 5.93 | 5.43 | 5.57 | 5.63 | 0 | 5.51 | 0 | 5.16 | 5.35 | 5.38 | 5.49 | 5.43 | 5.44 | 5.45 | 5.52 | 5.36 | 554892 | 5.3749 |  |  | 242550 | 2190 | 282231 | 2217 | 259051 | 1824 | 295270 | 1870 | 117600 | 0 | 100800 | 1200 | 118800 | 0 | 214800 | 1200 | 552000 | 2400 | 0.5212% | 96 | 137294 | 554.89 |  | 78 | No scada available server OS failed
2025-06-11 | 2026 | 2025 | 2025-06-01 | 30 | 17911 | 17915 | 17919 | 17913 | 14410 | 17917 | 15631 | 17921 | 9561 | 17934 | 17938 | 9565 | 9566 | 9568 | 9572 | 9522 | 9539 | 9542 | 9578 | 9582 | 14472 | 14474 | 14458 | 14462 | 12111 | 14457 | 14454 | 0 | 14468 | 0 | 11598 | 12132 | 12135 | 12142 | 12148 | 12145 | 12139 | 12152 | 12156 | 4.85 | 5.37 | 4.76 | 4.77 | 5.09 | 5.19 | 4.8 | 4.87 | 5.25 | 4.98 | 5.45 | 5.28 | 5.32 | 5.14 | 5.09 | 5.27 | 5.07 | 5.36 | 6.59 | 5.63 | 5.4 | 5.44 | 4.66 | 4.98 | 4.95 | 4.71 | 4.88 | 0 | 4.86 | 0 | 4.59 | 4.73 | 4.88 | 4.88 | 5.07 | 5.05 | 4.83 | 4.74 | 5.01 | 491107 | 4.8151 |  |  | 242649 | 2190 | 282326 | 2217 | 259182 | 1824 | 295349 | 1870 | 118800 | 0 | 114000 | 0 | 157200 | 0 | 94800 | 0 | 484800 | 0 | 1.284% | 96 | 100851 | 491.1 |  | 78 | No scada available server OS failed
2025-06-12 | 2026 | 2025 | 2025-06-01 | 30 | 12983 | 14968 | 14951 | 14966 | 9811 | 14959 | 14931 | 14967 | 12731 | 14972 | 14981 | 12735 | 12738 | 12741 | 12762 | 12758 | 12764 | 12760 | 12772 | 12775 | 9837 | 9831 | 9828 | 9855 | 8970 | 9850 | 9862 | 0 | 9868 | 0 | 8985 | 8957 | 8958 | 8951 | 8962 | 8959 | 8948 | 8964 | 8969 | 4.85 | 5.26 | 4.68 | 5.05 | 5 | 5.11 | 4.84 | 4.48 | 5.09 | 4.83 | 5.29 | 5.04 | 5.15 | 5.24 | 4.99 | 5.44 | 4.96 | 5.48 | 5.43 | 5.67 | 0 | 5.29 | 4.82 | 5.04 | 5.32 | 5.01 | 5.03 | 0 | 4.81 | 0 | 4.95 | 5.01 | 4.99 | 5.16 | 5.21 | 4.87 | 5.18 | 4.85 | 5.19 | 428579 | 4.6823 |  |  | 242722 | 2191 | 282390 | 2217 | 259292 | 1825 | 295454 | 1870 | 87600 | 1200 | 76800 | 0 | 132000 | 1200 | 126000 | 0 | 422400 | 2400 | 1.442% | 70 | 115200 | 428.57 |  | 78 | No scada available server OS failed
2025-06-13 | 2026 | 2025 | 2025-06-01 | 30 | [78 empty] | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
2025-06-14 | 2026 | 2025 | 2025-06-01 | 30 | [78 empty] | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
2025-06-15 | 2026 | 2025 | 2025-06-01 | 30 | [78 empty] | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
2025-06-16 | 2026 | 2025 | 2025-06-01 | 30 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-06-17 | 2026 | 2025 | 2025-06-01 | 30 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-06-18 | 2026 | 2025 | 2025-06-01 | 30 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-06-19 | 2026 | 2025 | 2025-06-01 | 30 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-06-20 | 2026 | 2025 | 2025-06-01 | 30 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-06-21 | 2026 | 2025 | 2025-06-01 | 30 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-06-22 | 2026 | 2025 | 2025-06-01 | 30 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-06-23 | 2026 | 2025 | 2025-06-01 | 30 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-06-24 | 2026 | 2025 | 2025-06-01 | 30 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-06-25 | 2026 | 2025 | 2025-06-01 | 30 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-06-26 | 2026 | 2025 | 2025-06-01 | 30 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-06-27 | 2026 | 2025 | 2025-06-01 | 30 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-06-28 | 2026 | 2025 | 2025-06-01 | 30 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-06-29 | 2026 | 2025 | 2025-06-01 | 30 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-06-30 | 2026 | 2025 | 2025-06-01 | 30 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-07-01 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-07-02 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-07-03 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-07-04 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-07-05 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-07-06 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-07-07 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-07-08 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-07-09 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-07-10 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-07-11 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-07-12 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-07-13 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-07-14 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-07-15 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-07-16 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-07-17 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-07-18 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-07-19 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-07-20 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-07-21 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-07-22 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-07-23 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-07-24 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-07-25 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-07-26 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-07-27 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-07-28 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-07-29 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-07-30 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-07-31 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-08-01 | 2026 | 2025 | 2025-08-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-08-02 | 2026 | 2025 | 2025-08-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-08-03 | 2026 | 2025 | 2025-08-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-08-04 | 2026 | 2025 | 2025-08-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-08-05 | 2026 | 2025 | 2025-08-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-08-06 | 2026 | 2025 | 2025-08-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-08-07 | 2026 | 2025 | 2025-08-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-08-08 | 2026 | 2025 | 2025-08-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-08-09 | 2026 | 2025 | 2025-08-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-08-10 | 2026 | 2025 | 2025-08-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-08-11 | 2026 | 2025 | 2025-08-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-08-12 | 2026 | 2025 | 2025-08-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-08-13 | 2026 | 2025 | 2025-08-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-08-14 | 2026 | 2025 | 2025-08-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
2025-08-15 | 2026 | 2025 | 2025-08-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | [7 empty] | 0 | 0
Formulas:
Month Year = [Date]-DAY([Date])+1
Days = DAY(EOMONTH(Input_Raw[[#This Row],[Date]],0))
Date = [Date, row above]+1

## Modelling New (hidden)
Sr. No. | Month Name | Month Number | Month | CY | FY | No. of Days in Month | GHI | POA | WS | Tamb | Tmod | Egrid (MWh) | Bugt_Capacity | PR | Daily POA | Days Operated | MTD POA | YTD POA | Daily Energy (MWh) | MTD Energy (MWh) | YTD Energy (MWh) | Bugt CUF (%) | Bugt CUF (%) MTD | Bugt CUF (%)YTD | Ave. Cap MTD | Ave. Cap YTD | CC Energy MTD | WS MTD | WS YTD | Bugt PA | Bugt EGA | Bugt TA | Bugt MA | Bugt IGA | Corelation | Bugt Line loss | Bugt Reactive Power | Bugt Capacity | CC*Bugt | Capacity | 78
1 | April | 4 | 2021-04-01 | 2021 | FY22 | 30 |  |  | 5.6333 |  |  | 11863.8432 | 80 |  |  | 0 |  |  | 395.4614 | 0 | 0 | 20.6% | [5 empty] | 6.4041 | 6.4041 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5% |  |  | Hourly reactive power bugt | 3.9
2 | May | 5 | 2021-05-01 | 2021 | FY22 | 31 |  |  | 6.5667 |  |  | 20092.2163 | 80 |  |  | 0 |  |  | 648.136 | 0 | 0 | 33.76% | [5 empty] | 5.9682 | 6.1861 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5% |  |  | Day | 93.6
3 | June | 6 | 2021-06-01 | 2021 | FY22 | 30 |  |  | 6.5667 |  |  | 17455.8067 | 80 |  |  | 0 |  |  | 581.8602 | 0 | 0 | 30.31% | [5 empty] | 5.6311 | 6.0011 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
4 | July | 7 | 2021-07-01 | 2021 | FY22 | 31 |  |  | 7.6 |  |  | 21077.401 | 80 |  |  | 0 |  |  | 679.9162 | 0 | 0 | 35.41% | [5 empty] | 7.1311 | 6.2836 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
5 | August | 8 | 2021-08-01 | 2021 | FY22 | 31 |  |  | 6.8667 |  |  | 22159.7165 | 80 |  |  | 0 |  |  | 714.8296 | 0 | 0 | 37.23% | [5 empty] | 9.453 | 6.9175 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
6 | September | 9 | 2021-09-01 | 2021 | FY22 | 30 |  |  | 5.0333 |  |  | 9726.9638 | 80 |  |  | 0 |  |  | 324.2321 | 0 | 0 | 16.89% | [5 empty] | 10.3038 | 7.4819 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
7 | October | 10 | 2021-10-01 | 2021 | FY22 | 31 |  |  | 3.9667 |  |  | 5924.9837 | 80 |  |  | 0 |  |  | 191.1285 | 0 | 0 | 9.955% | [5 empty] | 8.5195 | 7.6301 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
8 | November | 11 | 2021-11-01 | 2021 | FY22 | 30 |  |  | 4.0333 |  |  | 5661.3427 | 80 |  |  | 0 |  |  | 188.7114 | 0 | 0 | 9.829% | [5 empty] | 7.2367 | 7.5809 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
9 | December | 12 | 2021-12-01 | 2021 | FY22 | 31 |  |  | 4.4333 |  |  | 6618.7757 | 80 |  |  | 0 |  |  | 213.5089 | 0 | 0 | 11.12% | [5 empty] | 6.0016 | 7.4054 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
10 | January | 1 | 2022-01-01 | 2022 | FY22 | 31 |  |  | 3.8 |  |  | 4606.7789 | 80 |  |  | 0 |  |  | 148.6058 | 0 | 0 | 7.74% | [5 empty] | 6.7074 | 7.3356 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
11 | February | 2 | 2022-02-01 | 2022 | FY22 | 28 |  |  | 4.3 |  |  | 5619.7152 | 80 |  |  | 0 |  |  | 200.7041 | 0 | 0 | 10.45% | [5 empty] | 7.0533 | 7.31 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
12 | March | 3 | 2022-03-01 | 2022 | FY22 | 31 |  |  | 4.6 |  |  | 7950.8563 | 80 |  |  | 0 |  |  | 256.4792 | 0 | 0 | 13.36% | [5 empty] | 7.4111 | 7.3184 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
13 | April | 4 | 2022-04-01 | 2022 | FY23 | 30 |  |  | 5.6333 |  |  | 11863.8432 | 80 |  |  | 0 |  |  | 395.4614 | 0 | 0 | 20.6% | [5 empty] | 6.4041 | 6.4041 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
14 | May | 5 | 2022-05-01 | 2022 | FY23 | 31 |  |  | 6.5667 |  |  | 20092.2163 | 80 |  |  | 0 |  |  | 648.136 | 0 | 0 | 33.76% | [5 empty] | 5.9682 | 6.1861 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
15 | June | 6 | 2022-06-01 | 2022 | FY23 | 30 |  |  | 6.5667 |  |  | 17455.8067 | 80 |  |  | 0 |  |  | 581.8602 | 0 | 0 | 30.31% | [5 empty] | 5.6311 | 6.0011 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
16 | July | 7 | 2022-07-01 | 2022 | FY23 | 31 |  |  | 7.6 |  |  | 21077.401 | 80 |  |  | 0 |  |  | 679.9162 | 0 | 0 | 35.41% | [5 empty] | 7.1311 | 6.2836 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
17 | August | 8 | 2022-08-01 | 2022 | FY23 | 31 |  |  | 6.8667 |  |  | 22159.7165 | 80 |  |  | 0 |  |  | 714.8296 | 0 | 0 | 37.23% | [5 empty] | 9.453 | 6.9175 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
18 | September | 9 | 2022-09-01 | 2022 | FY23 | 30 |  |  | 5.0333 |  |  | 9726.9638 | 80 |  |  | 0 |  |  | 324.2321 | 0 | 0 | 16.89% | [5 empty] | 10.3038 | 7.4819 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
19 | October | 10 | 2022-10-01 | 2022 | FY23 | 31 |  |  | 3.9667 |  |  | 5924.9837 | 80 |  |  | 0 |  |  | 191.1285 | 0 | 0 | 9.955% | [5 empty] | 8.5195 | 7.6301 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
20 | November | 11 | 2022-11-01 | 2022 | FY23 | 30 |  |  | 4.0333 |  |  | 5661.3427 | 80 |  |  | 0 |  |  | 188.7114 | 0 | 0 | 9.829% | [5 empty] | 7.2367 | 7.5809 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
21 | December | 12 | 2022-12-01 | 2022 | FY23 | 31 |  |  | 4.4333 |  |  | 6618.7757 | 80 |  |  | 0 |  |  | 213.5089 | 0 | 0 | 11.12% | [5 empty] | 6.0016 | 7.4054 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
22 | January | 1 | 2023-01-01 | 2023 | FY23 | 31 |  |  | 3.8 |  |  | 4606.7789 | 80 |  |  | 0 |  |  | 148.6058 | 0 | 0 | 7.74% | [5 empty] | 6.7074 | 7.3356 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
23 | February | 2 | 2023-02-01 | 2023 | FY23 | 28 |  |  | 4.3 |  |  | 5619.7152 | 80 |  |  | 0 |  |  | 200.7041 | 0 | 0 | 10.45% | [5 empty] | 7.0533 | 7.31 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
24 | March | 3 | 2023-03-01 | 2023 | FY23 | 31 |  |  | 4.6 |  |  | 7950.8563 | 80 |  |  | 0 |  |  | 256.4792 | 0 | 0 | 13.36% | [5 empty] | 7.4111 | 7.3184 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
25 | April | 4 | 2023-04-01 | 2023 | FY24 | 30 |  |  | 5.6333 |  |  | 11000 | 80 |  |  | 0 |  |  | 366.6667 | 0 | 0 | 19.1% | [5 empty] | 6.4041 | 6.4041 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
26 | May | 5 | 2023-05-01 | 2023 | FY24 | 31 |  |  | 6.5667 |  |  | 19240 | 80 |  |  | 0 |  |  | 620.6452 | 0 | 0 | 32.33% | [5 empty] | 5.9682 | 7.3184 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
27 | June | 6 | 2023-06-01 | 2023 | FY24 | 30 |  |  | 6.5667 |  |  | 16180 | 80 |  |  | 0 |  |  | 539.3333 | 0 | 0 | 28.09% | [5 empty] | 5.6311 | 6.0011 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
28 | July | 7 | 2023-07-01 | 2023 | FY24 | 31 |  |  | 7.6 |  |  | 20190 | 80 |  |  | 0 |  |  | 651.2903 | 0 | 0 | 33.92% | [5 empty] | 7.1311 | 6.2836 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
29 | August | 8 | 2023-08-01 | 2023 | FY24 | 31 |  |  | 6.8667 |  |  | 21230 | 80 |  |  | 0 |  |  | 684.8387 | 0 | 0 | 35.67% | [5 empty] | 9.453 | 6.9175 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
30 | September | 9 | 2023-09-01 | 2023 | FY24 | 30 |  |  | 5.0333 |  |  | 9020 | 80 |  |  | 0 |  |  | 300.6667 | 0 | 0 | 15.66% | [5 empty] | 10.3038 | 7.4819 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
31 | October | 10 | 2023-10-01 | 2023 | FY24 | 31 |  |  | 3.9667 |  |  | 6030 | 80 |  |  | 0 |  |  | 194.5161 | 0 | 0 | 10.13% | [5 empty] | 8.5195 | 7.6301 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
32 | November | 11 | 2023-11-01 | 2023 | FY24 | 30 |  |  | 4.0333 |  |  | 5580 | 80 |  |  | 0 |  |  | 186 | 0 | 0 | 9.688% | [5 empty] | 7.2367 | 7.5809 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
33 | December | 12 | 2023-12-01 | 2023 | FY24 | 31 |  |  | 4.4333 |  |  | 6740 | 80 |  |  | 0 |  |  | 217.4194 | 0 | 0 | 11.32% | [5 empty] | 6.0016 | 7.4054 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
34 | January | 1 | 2024-01-01 | 2024 | FY24 | 31 |  |  | 3.8 |  |  | 4700 | 80 |  |  | 0 |  |  | 151.6129 | 0 | 0 | 7.897% | [5 empty] | 6.7074 | 7.3356 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
35 | February | 2 | 2024-02-01 | 2024 | FY24 | 29 |  |  | 4.3 |  |  | 5360 | 80 |  |  | 0 |  |  | 184.8276 | 0 | 0 | 9.626% | [5 empty] | 7.0533 | 7.31 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
36 | March | 3 | 2024-03-01 | 2024 | FY24 | 31 |  |  | 4.6 |  |  | 8110 | 80 |  |  | 0 |  |  | 261.6129 | 0 | 0 | 13.63% | [5 empty] | 7.4111 | 7.3184 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
37 | April | 4 | 2024-04-01 | 2024 | FY25 | 30 |  |  | 5.6333 |  |  | 11919.2 | 80 |  |  | 0 |  |  | 397.3067 | 0 | 0 | 20.69% | [5 empty] | 6.4041 | 6.4041 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
38 | May | 5 | 2024-05-01 | 2024 | FY25 | 31 |  |  | 6.5667 |  |  | 20174.9 | 80 |  |  | 0 |  |  | 650.8032 | 0 | 773.2742 | 33.9% | [5 empty] | 5.9682 | 7.3184 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
39 | June | 6 | 2024-06-01 | 2024 | FY25 | 30 |  |  | 6.5667 |  |  | 17527.1 | 80 |  |  | 0 |  |  | 584.2367 | 0 | 0 | 30.43% | [5 empty] | 5.6311 | 6.0011 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
40 | July | 7 | 2024-07-01 | 2024 | FY25 | 31 |  |  | 7.6 |  |  | 21165.2 | 80 |  |  | 0 |  |  | 682.7484 | 0 | 0 | 35.56% | [5 empty] | 7.1311 | 6.2836 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
41 | August | 8 | 2024-08-01 | 2024 | FY25 | 31 |  |  | 6.8667 |  |  | 22256.9 | 80 |  |  | 0 |  |  | 717.9645 | 0 | 0 | 37.39% | [5 empty] | 9.453 | 6.9175 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
42 | September | 9 | 2024-09-01 | 2024 | FY25 | 30 |  |  | 5.0333 |  |  | 9773.8 | 80 |  |  | 0 |  |  | 325.7933 | 0 | 0 | 16.97% | [5 empty] | 10.3038 | 7.4819 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
43 | October | 10 | 2024-10-01 | 2024 | FY25 | 31 |  |  | 3.9667 |  |  | 5947 | 80 |  |  | 0 |  |  | 191.8387 | 0 | 0 | 9.992% | [5 empty] | 8.5195 | 7.6301 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
44 | November | 11 | 2024-11-01 | 2024 | FY25 | 30 |  |  | 4.0333 |  |  | 5683.6 | 80 |  |  | 0 |  |  | 189.4533 | 0 | 0 | 9.867% | [5 empty] | 7.2367 | 7.5809 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
45 | December | 12 | 2024-12-01 | 2024 | FY25 | 31 |  |  | 4.4333 |  |  | 6645.2 | 80 |  |  | 0 |  |  | 214.3613 | 0 | 0 | 11.16% | [5 empty] | 6.0016 | 7.4054 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
46 | January | 1 | 2025-01-01 | 2025 | FY25 | 31 |  |  | 3.8 |  |  | 4628.1 | 80 |  |  | 0 |  |  | 149.2935 | 0 | 0 | 7.776% | [5 empty] | 6.7074 | 7.3356 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
47 | February | 2 | 2025-02-01 | 2025 | FY25 | 28 |  |  | 4.3 |  |  | 5610.2 | 80 |  |  | 0 |  |  | 200.3643 | 0 | 0 | 10.44% | [5 empty] | 7.0533 | 7.31 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
48 | March | 3 | 2025-03-01 | 2025 | FY25 | 31 |  |  | 4.6 |  |  | 7990.5 | 80 |  |  | 3 |  |  | 257.7581 | 773.2742 | 773.2742 | 13.42% | 13.42% | 13.42% | 80 | 80 |  | 7.4111 | 7.3184 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
49 | April | 4 | 2025-04-01 | 2025 | FY26 | 30 |  |  | 5.6333 |  |  | 10226.6542 | 78 |  |  | 30 |  |  | 340.8885 | 10226.6542 | 10226.6542 | 18.21% | 18.21% | 18.21% | 78 | 78 |  | 6.4041 | 6.4041 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
50 | May | 5 | 2025-05-01 | 2025 | FY26 | 31 |  |  | 6.5667 |  |  | 17310.0402 | 78 |  |  | 31 |  |  | 558.3884 | 17310.0402 | 27536.6944 | 29.83% | 29.83% | 24.11% | 78 | 78 |  | 5.9682 | 6.1861 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
51 | June | 6 | 2025-06-01 | 2025 | FY26 | 30 |  |  | 6.5667 |  |  | 15038.2603 | 78 |  |  | 12 |  |  | 501.2753 | 6015.3041 | 33551.9985 | 26.78% | 26.78% | 24.55% | 31.2 | 62.4 |  | 5.6311 | 6.0011 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
52 | July | 7 | 2025-07-01 | 2025 | FY26 | 31 |  |  | 7.6 |  |  | 18159.7324 | 78 |  |  | 0 |  |  | 585.7978 | 0 | 33551.9985 | 31.29% |  | 24.55% | 0 | 46.8 |  | 7.1311 | 6.2836 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
53 | August | 8 | 2025-08-01 | 2025 | FY26 | 31 |  |  | 6.8667 |  |  | 19096.4226 | 78 |  |  | 0 |  |  | 616.0136 | 0 | 33551.9985 | 32.91% |  | 24.55% | 0 | 37.44 |  | 9.453 | 6.9175 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
54 | September | 9 | 2025-09-01 | 2025 | FY26 | 30 |  |  | 5.0333 |  |  | 8385.892 | 78 |  |  | 0 |  |  | 279.5297 | 0 | 33551.9985 | 14.93% |  | 24.55% |  | 37.44 |  | 10.3038 | 7.4819 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
55 | October | 10 | 2025-10-01 | 2025 | FY26 | 31 |  |  | 3.9667 |  |  | 5102.5337 | 78 |  |  | 0 |  |  | 164.5979 | 0 | 33551.9985 | 8.793% |  | 24.55% |  | 37.44 |  | 8.5195 | 7.6301 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
56 | November | 11 | 2025-11-01 | 2025 | FY26 | 30 |  |  | 4.0333 |  |  | 4876.5139 | 78 |  |  | 0 |  |  | 162.5505 | 0 | 33551.9985 | 8.683% |  | 24.55% |  | 37.44 |  | 7.2367 | 7.5809 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
57 | December | 12 | 2025-12-01 | 2025 | FY26 | 31 |  |  | 4.4333 |  |  | 5701.5948 | 78 |  |  | 0 |  |  | 183.9224 | 0 | 33551.9985 | 9.825% |  | 24.55% |  | 37.44 |  | 6.0016 | 7.4054 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
58 | January | 1 | 2026-01-01 | 2026 | FY26 | 31 |  |  | 3.8 |  |  | 3970.8953 | 78 |  |  | 0 |  |  | 128.0934 | 0 | 33551.9985 | 6.843% |  | 24.55% |  | 37.44 |  | 6.7074 | 7.3356 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
59 | February | 2 | 2026-02-01 | 2026 | FY26 | 28 |  |  | 4.3 |  |  | 4813.5808 | 78 |  |  | 0 |  |  | 171.9136 | 0 | 33551.9985 | 9.183% |  | 24.55% |  | 37.44 |  | 7.0533 | 7.31 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
60 | March | 3 | 2026-03-01 | 2026 | FY26 | 31 |  |  | 4.6 |  |  | 6855.8432 | 78 |  |  | 0 |  |  | 221.1562 | 0 | 33551.9985 | 11.81% |  | 24.55% |  | 37.44 |  | 7.4111 | 7.3184 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
Formulas:
No. of Days in Month = DAY(EOMONTH([Month],0))

## WTG_BD
Sr. No. | Date | Finacial Year | Calendor Year | Month | Operating Year | Affected WTG | SPV | Concumaer | Plant Equivalent Weightage | Error Code | Error Text | Breakdown Description | Fault Start TimeStamp | Work Start TimeStamp | Fault Clearance time | Response Time | Resolution Time | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Paired WTG for Enegy based MA | Energy Production during breakdwon of paired WTG | Special remarks | Fault Category | Paired WTG Generation for loss calculation. | loss | PTW No. | Job Card No. | Fault Category
1 | 2025-03-29 | 2025 | 2025 | 2025-03-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 2418.3194 | None | WTG Force Majeaure | 2420 | 2418.3194
2 | 2025-03-29 | 2025 | 2025 | 2025-03-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 2418.3194 | None | WTG Force Majeaure | 2420 | 2418.3194
3 | 2025-03-29 | 2025 | 2025 | 2025-03-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | 5200 | Magnetothermic Trigger Of The Line Protection | BD | 16:05 | 16:05 | 16:19 | 0 | 0.23333 | 0.23333 | Reset then restore wtg. | Close | 0.0059829 | G03 | 32.8222 | None | WTG Breakdown Maintenance | 3376 | 32.8222
4 | 2025-03-29 | 2025 | 2025 | 2025-03-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | 5200 | Magnetothermic Trigger Of The Line Protection | BD | 20:21 | 20:21 | 20:26 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G03 | 11.7222 | None | WTG Breakdown Maintenance | 3376 | 11.7222
5 | 2025-03-29 | 2025 | 2025 | 2025-03-01 | Year_3 | G05 | PWEGPL | MSEDCL | 2.564% | 5204 | Emergency Series Not OK | BD | 20:16 | 20:16 | 20:21 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G22 | 9.6528 | None | WTG Breakdown Maintenance | 2780 | 9.6528
6 | 2025-03-29 | 2025 | 2025 | 2025-03-01 | Year_3 | G06 | PWEGPL | MSEDCL | 2.564% | 700 | PLC-Converter Communication Error | BD | 10:50 | 11:40 | 12:29 | 0.83333 | 0.81667 | 1.65 | CCU reset then restore wtg. | Close | 0.042308 | G03 | 232.1 | None | WTG Breakdown Maintenance | 3376 | 232.1
7 | 2025-03-29 | 2025 | 2025 | 2025-03-01 | Year_3 | G21 | PWEGPL | MSEDCL | 2.564% | 202 | Low Pressure On Brake Circuit | BD | 20:17 | 20:17 | 20:22 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G22 | 9.6528 | None | WTG Breakdown Maintenance | 2780 | 9.6528
8 | 2025-03-29 | 2025 | 2025 | 2025-03-01 | Year_3 | G22 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD | 20:18 | 20:18 | 20:23 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G21 | 14.6389 | None | WTG Breakdown Maintenance | 4216 | 14.6389
9 | 2025-03-29 | 2025 | 2025 | 2025-03-01 | Year_3 | G33 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD | 8:34 | 14:14 | 17:06 | 5.6667 | 2.8667 | 8.5333 | Checked related circuit found ok the restore wtg. | Close | 0.2188 | G34 | 955.7333 | None | WTG Breakdown Maintenance | 2688 | 955.7333
10 | 2025-03-29 | 2025 | 2025 | 2025-03-01 | Year_3 | G34 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD | 9:03 | 9:03 | 9:08 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G35 | 10.3333 | None | WTG Breakdown Maintenance | 2976 | 10.3333
11 | 2025-03-29 | 2025 | 2025 | 2025-03-01 | Year_3 | G34 | PWEGPL | MSEDCL | 2.564% | 5200 | Magnetothermic Trigger Of The Line Protection | BD | 17:26 | 17:26 | 17:35 | 0 | 0.15 | 0.15 | Reset then restore wtg. | Close | 0.0038462 | G35 | 18.6 | None | WTG Breakdown Maintenance | 2976 | 18.6
12 | 2025-03-29 | 2025 | 2025 | 2025-03-01 | Year_3 | G36 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD | 9:15 | 9:15 | 9:20 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G37 | 9.7847 | None | WTG Breakdown Maintenance | 2818 | 9.7847
13 | 2025-03-29 | 2025 | 2025 | 2025-03-01 | Year_3 | G36 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD | 10:16 | 10:16 | 10:21 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G37 | 9.7847 | None | WTG Breakdown Maintenance | 2818 | 9.7847
14 | 2025-03-29 | 2025 | 2025 | 2025-03-01 | Year_3 | G36 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD | 10:54 | 10:54 | 10:59 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G37 | 9.7847 | None | WTG Breakdown Maintenance | 2818 | 9.7847
15 | 2025-03-29 | 2025 | 2025 | 2025-03-01 | Year_3 | G36 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD | 11:44 | 11:44 | 13:29 | 0 | 1.75 | 1.75 | Reset then restore wtg. | Close | 0.044872 | G37 | 205.4792 | None | WTG Breakdown Maintenance | 2818 | 205.4792
16 | 2025-03-29 | 2025 | 2025 | 2025-03-01 | Year_3 | G36 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD | 15:04 | 15:28 | 17:43 | 0.4 | 2.25 | 2.65 | Checked related circuit found ok then restore wtg. | Close | 0.067949 | G37 | 311.1542 | None | WTG Breakdown Maintenance | 2818 | 311.1542
17 | 2025-03-30 | 2025 | 2025 | 2025-03-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 1550.9222 | None | WTG Force Majeaure | 1552 | 1550.9222
18 | 2025-03-30 | 2025 | 2025 | 2025-03-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 1550.9222 | None | WTG Force Majeaure | 1552 | 1550.9222
19 | 2025-03-30 | 2025 | 2025 | 2025-03-01 | Year_3 | G01 | PWEGPL | MSEDCL | 2.564% | 125 | Yaw Motors Over Current Protection | BD | 11:46 | 14:08 | 18:42 | 2.3667 | 4.5667 | 6.9333 | Checked related circuit found yaw motor failure so replaced yaw motor with new one then restore wtg. | Close | 0.17778 | G07 | 1053 | None | WTG Breakdown Maintenance | 3645 | 1053
20 | 2025-03-30 | 2025 | 2025 | 2025-03-01 | Year_3 | G02 | PWEGPL | MSEDCL | 2.564% | 5203 | Heating/Coolant Thermal Magnetic Failure | BD | 2:18 | 3:03 | 7:49 | 0.75 | 4.7667 | 5.5167 | Checked related circuit found CCU coolant cooling motor failure so replaced then start wtg. | Close | 0.14145 | G04 | 766.8167 | None | WTG Breakdown Maintenance | 3336 | 766.8167
21 | 2025-03-30 | 2025 | 2025 | 2025-03-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | 5200 | Magnetothermic Trigger Of The Line Protection | BD | 14:49 | 14:49 | 15:00 | 0 | 0.18333 | 0.18333 | Auto reset | Close | 0.0047009 | G03 | 16.5764 | None | WTG Breakdown Maintenance | 2170 | 16.5764
22 | 2025-03-30 | 2025 | 2025 | 2025-03-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | 5200 | Magnetothermic Trigger Of The Line Protection | BD | 16:22 | 18:56 | 18:59 | 2.5667 | 0.05 | 2.6167 | Reboot then restore wtg. | Close | 0.067094 | G03 | 236.5903 | None | WTG Breakdown Maintenance | 2170 | 236.5903
23 | 2025-03-30 | 2025 | 2025 | 2025-03-01 | Year_3 | G27 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 12:21 | 12:21 | 17:04 | 0 | 4.7167 | 4.7167 | Manual stop for blade bush gap inspection work. | Close | 0.12094 | G25 | 554.6014 | None | WTG Force Majeaure | 2822 | 554.6014
24 | 2025-03-30 | 2025 | 2025 | 2025-03-01 | Year_3 | G28 | PWEGPL | MSEDCL | 2.564% | 524 | High Temperature Of The Control Module | BD | 0:45 | 1:50 | 1:58 | 1.0833 | 0.13333 | 1.2167 | Reboot then restore wtg. | Close | 0.031197 | G30 | 137.4833 | None | WTG Breakdown Maintenance | 2712 | 137.4833
25 | 2025-03-30 | 2025 | 2025 | 2025-03-01 | Year_3 | G28 | PWEGPL | MSEDCL | 2.564% | 524 | High Temperature Of The Control Module | BD | 11:28 | 17:24 | 17:42 | 5.9333 | 0.3 | 6.2333 | Check related circuit found ok then restore wtg. | Close | 0.15983 | G30 | 704.3667 | None | WTG Breakdown Maintenance | 2712 | 704.3667
26 | 2025-03-30 | 2025 | 2025 | 2025-03-01 | Year_3 | G35 | PWEGPL | MSEDCL | 2.564% | 103 | CCW Feedback Failure | BD | 10:06 | 10:06 | 10:16 | 0 | 0.16667 | 0.16667 | Auto reset | Close | 0.0042735 | G36 | 21.875 | None | WTG Breakdown Maintenance | 3150 | 21.875
27 | 2025-03-30 | 2025 | 2025 | 2025-03-01 | Year_3 | G35 | PWEGPL | MSEDCL | 2.564% | 103 | CCW Feedback Failure | BD | 10:22 | 12:31 | 16:00 | 2.15 | 3.4833 | 5.6333 | Check related circuit found yaw motor failure so replace with new one then restore wtg. | Close | 0.14444 | G36 | 739.375 | None | WTG Breakdown Maintenance | 3150 | 739.375
28 | 2025-03-30 | 2025 | 2025 | 2025-03-01 | Year_3 | G40 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD | 12:21 | 12:21 | 12:26 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G39 | 9.4028 | None | WTG Breakdown Maintenance | 2708 | 9.4028
29 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 6001.8292 | None | WTG Force Majeaure | 6006 | 6001.8292
30 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 6001.8292 | None | WTG Force Majeaure | 6006 | 6001.8292
31 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G01 | PWEGPL | MSEDCL | 2.564% | 5205 | Magnetothermic Of The Stator Protection Failure Or Door Open | BD | 13:13 | 13:13 | 13:17 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0017094 | G07 | 16.7778 | None | WTG Breakdown Maintenance | 6040 | 16.7778
32 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G01 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD | 13:31 | 13:31 | 13:41 | 0 | 0.16667 | 0.16667 | Auto reset | Close | 0.0042735 | G07 | 41.9444 | None | WTG Breakdown Maintenance | 6040 | 41.9444
33 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G03 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 11:10 | 11:10 | 13:10 | 0 | 2 | 2 | Manual stop for blade bush gap inspection work. | Close | 0.051282 | G04 | 666 | None | WTG Force Majeaure | 7992 | 666
34 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | 523 | High Temperature Of Coolant In The Input Of The Cooling Circuit | BD | 15:46 | 15:46 | 15:51 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G03 | 31.2292 | None | WTG Breakdown Maintenance | 8994 | 31.2292
35 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | 5200 | Magnetothermic Trigger Of The Line Protection | BD | 16:13 | 16:13 | 16:35 | 0 | 0.36667 | 0.36667 | Auto reset | Close | 0.0094017 | G03 | 137.4083 | None | WTG Breakdown Maintenance | 8994 | 137.4083
36 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G06 | PWEGPL | MSEDCL | 2.564% | 116 | Orienting and High Yaw Brake Pressure | BD | 16:32 | 16:32 | 16:37 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G03 | 31.2292 | None | WTG Breakdown Maintenance | 8994 | 31.2292
37 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G07 | PWEGPL | MSEDCL | 2.564% | 2102 | PLC Module Failure | BD | 16:31 | 19:28 | 19:31 | 2.95 | 0.05 | 3 | Reboot then restore wtg. | Close | 0.076923 | G01 | 1179.5 | None | WTG Breakdown Maintenance | 9436 | 1179.5
38 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G07 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD | 20:18 | 20:18 | 20:23 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G01 | 32.7639 | None | WTG Breakdown Maintenance | 9436 | 32.7639
39 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G09 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD | 19:20 | 19:46 | 19:46 | 0.43333 | 0 | 0.43333 | Reset then restore wtg. | Close | 0.011111 | G12 | 106.2208 | None | WTG Breakdown Maintenance | 5883 | 106.2208
40 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G10 | PWEGPL | MSEDCL | 2.564% | 527 | High Temperature Of Upper Radiator | BD | 16:34 | 16:34 | 16:39 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G11 | 34.2917 | None | WTG Breakdown Maintenance | 9876 | 34.2917
41 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G10 | PWEGPL | MSEDCL | 2.564% | 527 | High Temperature Of Upper Radiator | BD | 17:13 | 17:13 | 17:18 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G11 | 34.2917 | None | WTG Breakdown Maintenance | 9876 | 34.2917
42 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G10 | PWEGPL | MSEDCL | 2.564% | 527 | High Temperature Of Upper Radiator | BD | 17:30 | 17:30 | 17:35 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G11 | 34.2917 | None | WTG Breakdown Maintenance | 9876 | 34.2917
43 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G10 | PWEGPL | MSEDCL | 2.564% | 527 | High Temperature Of Upper Radiator | BD | 18:54 | 19:45 | 19:45 | 0.85 | 0 | 0.85 | Reset then restore wtg. | Close | 0.021795 | G11 | 349.775 | None | WTG Breakdown Maintenance | 9876 | 349.775
44 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G11 | PWEGPL | MSEDCL | 2.564% | 116 | Orienting and High Yaw Brake Pressure | BD | 16:38 | 16:38 | 16:43 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G10 | 25.6389 | None | WTG Breakdown Maintenance | 7384 | 25.6389
45 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G12 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD | 16:25 | 16:25 | 16:29 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0017094 | G13 | 21.3833 | None | WTG Breakdown Maintenance | 7698 | 21.3833
46 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G12 | PWEGPL | MSEDCL | 2.564% | 5210 | Failure Of The Contactor's Rotor Power | BD | 16:31 | 16:31 | 16:50 | 0 | 0.31667 | 0.31667 | Reset then restore wtg. | Close | 0.0081197 | G13 | 101.5708 | None | WTG Breakdown Maintenance | 7698 | 101.5708
47 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G12 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD | 16:52 | 16:52 | 18:05 | 0 | 1.2167 | 1.2167 | Reset then restore wtg. | Close | 0.031197 | G13 | 390.2458 | None | WTG Breakdown Maintenance | 7698 | 390.2458
48 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G12 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD | 18:20 | 18:20 | 18:30 | 0 | 0.16667 | 0.16667 | Auto reset | Close | 0.0042735 | G13 | 53.4583 | None | WTG Breakdown Maintenance | 7698 | 53.4583
49 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G12 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD | 20:17 | 21:57 | 22:16 | 1.6667 | 0.31667 | 1.9833 | Reboot then restore wtg. | Close | 0.050855 | G13 | 636.1542 | None | WTG Breakdown Maintenance | 7698 | 636.1542
50 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G13 | PWEGPL | MSEDCL | 2.564% | 550 | Generator Fans Thermal Relay Triggered Too Long | BD | 15:10 | 15:50 | 16:02 | 0.66667 | 0.2 | 0.86667 | Reset then restore wtg. | Close | 0.022222 | G14 | 267.5111 | None | WTG Breakdown Maintenance | 7408 | 267.5111
51 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G13 | PWEGPL | MSEDCL | 2.564% | 426 | Rotor Speed Reading Failure | BD | 20:34 | 20:34 | 20:45 | 0 | 0.18333 | 0.18333 | Auto reset | Close | 0.0047009 | G14 | 56.5889 | None | WTG Breakdown Maintenance | 7408 | 56.5889
52 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G14 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD | 8:30 | 11:11 | 13:00 | 2.6833 | 1.8167 | 4.5 | Check related circuit found ok then restore wtg. | Close | 0.11538 | G15 | 1157.4375 | None | WTG Breakdown Maintenance | 6173 | 1157.4375
53 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G14 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD | 16:27 | 16:27 | 16:37 | 0 | 0.16667 | 0.16667 | Auto reset | Close | 0.0042735 | G15 | 42.8681 | None | WTG Breakdown Maintenance | 6173 | 42.8681
54 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G15 | PWEGPL | MSEDCL | 2.564% | 722 | Wind Vane Failure Alarm | BD | 16:24 | 17:56 | 17:56 | 1.5333 | 0 | 1.5333 | Reset then restore wtg. | Close | 0.039316 | G14 | 473.2889 | None | WTG Breakdown Maintenance | 7408 | 473.2889
55 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G16 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD | 16:31 | 16:31 | 16:36 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G17 | 27.8333 | None | WTG Breakdown Maintenance | 8016 | 27.8333
56 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G16 | PWEGPL | MSEDCL | 2.564% | 804 | Difference Between 2 Blades Too High | BD | 17:55 | 17:55 | 18:00 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G17 | 27.8333 | None | WTG Breakdown Maintenance | 8016 | 27.8333
57 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G16 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 18:12 | 18:27 | 18:45 | 0.25 | 0.3 | 0.55 | Auto reset | Close | 0.014103 | G17 | 183.7 | None | WTG Breakdown Maintenance | 8016 | 183.7
58 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G16 | PWEGPL | MSEDCL | 2.564% | 804 | Difference Between 2 Blades Too High | BD | 20:41 | 20:41 | 20:46 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G17 | 27.8333 | None | WTG Breakdown Maintenance | 8016 | 27.8333
59 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G16 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD | 21:21 | 21:28 | 21:33 | 0.11667 | 0.083333 | 0.2 | Auto reset | Close | 0.0051282 | G17 | 66.8 | None | WTG Breakdown Maintenance | 8016 | 66.8
60 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G17 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD | 18:22 | 18:22 | 18:39 | 0 | 0.28333 | 0.28333 | Reboot then restore wtg. | Close | 0.007265 | G16 | 83.3944 | None | WTG Breakdown Maintenance | 7064 | 83.3944
61 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G18 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD | 16:31 | 16:31 | 16:47 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.0068376 | G19 | 95.1556 | None | WTG Breakdown Maintenance | 8564 | 95.1556
62 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G18 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD | 18:12 | 18:12 | 18:35 | 0 | 0.38333 | 0.38333 | Auto reset | Close | 0.0098291 | G19 | 136.7861 | None | WTG Breakdown Maintenance | 8564 | 136.7861
63 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G18 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD | 20:38 | 21:29 | 21:30 | 0.85 | 0.016667 | 0.86667 | Auto reset | Close | 0.022222 | G19 | 309.2556 | None | WTG Breakdown Maintenance | 8564 | 309.2556
64 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G21 | PWEGPL | MSEDCL | 2.564% | 5228 | Preload Failure | BD | 19:38 | 23:50 | 23:54 | 4.2 | 0.066667 | 4.2667 | Reboot then restore wtg. | Close | 0.1094 | G22 | 696.8889 | None | WTG Breakdown Maintenance | 3920 | 696.8889
65 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G22 | PWEGPL | MSEDCL | 2.564% | 402 | Gearbox Oil Level Low | BD | 19:37 | 23:36 | 23:59 | 3.9833 | 0.38333 | 4.3667 | work in progress | Open | 0.11197 | G21 | 1246.3194 | None | WTG Breakdown Maintenance | 6850 | 1246.3194
66 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G23 | PWEGPL | MSEDCL | 2.564% | 2102 | PLC Module Failure | BD | 14:11 | 14:45 | 17:26 | 0.56667 | 2.6833 | 3.25 | Check related circuit found RTD module failure so repalced with new one then restore wtg. | Close | 0.083333 | G22 | 530.8333 | None | WTG Breakdown Maintenance | 3920 | 530.8333
67 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G23 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD | 21:07 | 21:28 | 21:29 | 0.35 | 0.016667 | 0.36667 | Reset then restore wtg. | Close | 0.0094017 | G22 | 59.8889 | None | WTG Breakdown Maintenance | 3920 | 59.8889
68 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G26 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD | 3:27 | 3:27 | 4:21 | 0 | 0.9 | 0.9 | Reset then restore wtg. | Close | 0.023077 | G32 | 190.5 | None | WTG Breakdown Maintenance | 5080 | 190.5
69 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G26 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD | 9:10 | 11:32 | 16:53 | 2.3667 | 5.35 | 7.7167 | Checked related circuit found no leakage then top-up 5 liter HU oil then restore wtg. | Close | 0.19786 | G32 | 1633.3611 | None | WTG Breakdown Maintenance | 5080 | 1633.3611
70 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G26 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD | 19:20 | 19:20 | 19:50 | 0 | 0.5 | 0.5 | Reset then restore wtg. | Close | 0.012821 | G32 | 105.8333 | None | WTG Breakdown Maintenance | 5080 | 105.8333
71 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G27 | PWEGPL | MSEDCL | 2.564% | 426 | Rotor Speed Reading Failure | BD | 21:02 | 21:02 | 21:07 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G25 | 24.5903 | None | WTG Breakdown Maintenance | 7082 | 24.5903
72 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G30 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD | 19:37 | 19:37 | 23:59 | 0 | 4.3667 | 4.3667 | work in progress | Open | 0.11197 | G28 | 1092.7583 | None | WTG Breakdown Maintenance | 6006 | 1092.7583
73 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G32 | PWEGPL | MSEDCL | 2.564% | 2102 | PLC Module Failure | BD | 17:55 | 19:35 | 19:39 | 1.6667 | 0.066667 | 1.7333 | Reboot then restore wtg. | Close | 0.044444 | G26 | 395.7778 | None | WTG Breakdown Maintenance | 5480 | 395.7778
74 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G33 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD | 20:18 | 20:18 | 20:23 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G34 | 27.7639 | None | WTG Breakdown Maintenance | 7996 | 27.7639
75 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G34 | PWEGPL | MSEDCL | 2.564% | 5200 | Magnetothermic Trigger Of The Line Protection | BD | 17:54 | 17:54 | 17:59 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G33 | 23.2743 | None | WTG Breakdown Maintenance | 6703 | 23.2743
76 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G35 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD | 19:20 | 19:20 | 23:59 | 0 | 4.65 | 4.65 | work in progress | Open | 0.11923 | G36 | 928.45 | None | WTG Breakdown Maintenance | 4792 | 928.45
77 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G36 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD | 8:34 | 8:34 | 8:39 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G35 | 16.5417 | None | WTG Breakdown Maintenance | 4764 | 16.5417
78 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G36 | PWEGPL | MSEDCL | 2.564% | 426 | Rotor Speed Reading Failure | BD | 9:21 | 9:21 | 9:26 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G35 | 16.5417 | None | WTG Breakdown Maintenance | 4764 | 16.5417
79 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G36 | PWEGPL | MSEDCL | 2.564% | 804 | Difference Between 2 Blades Too High | BD | 10:43 | 10:48 | 10:48 | 0.083333 | 0 | 0.083333 | Auto reset | Close | 0.0021368 | G35 | 16.5417 | None | WTG Breakdown Maintenance | 4764 | 16.5417
80 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G36 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD | 11:32 | 11:32 | 11:37 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G35 | 16.5417 | None | WTG Breakdown Maintenance | 4764 | 16.5417
81 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G36 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD | 12:15 | 12:15 | 13:08 | 0 | 0.88333 | 0.88333 | Reset then restore wtg. | Close | 0.02265 | G35 | 175.3417 | None | WTG Breakdown Maintenance | 4764 | 175.3417
82 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G36 | PWEGPL | MSEDCL | 2.564% | 804 | Difference Between 2 Blades Too High | BD | 13:42 | 13:42 | 14:11 | 0 | 0.48333 | 0.48333 | Reset then restore wtg. | Close | 0.012393 | G35 | 95.9417 | None | WTG Breakdown Maintenance | 4764 | 95.9417
83 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G36 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD | 19:20 | 19:20 | 23:59 | 0 | 4.65 | 4.65 | work in progress | Open | 0.11923 | G35 | 923.025 | None | WTG Breakdown Maintenance | 4764 | 923.025
84 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G37 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD | 8:35 | 14:10 | 19:07 | 5.5833 | 4.95 | 10.5333 | Checked related circuit found leakage form yaw caliper so replaced yaw caliper seal then top-up 30 liter oil then restore wtg. | Close | 0.27009 | G36 | 2103.1556 | None | WTG Breakdown Maintenance | 4792 | 2103.1556
85 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G38 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD | 19:20 | 19:20 | 19:52 | 0 | 0.53333 | 0.53333 | Reset then restore wtg. | Close | 0.013675 | G39 | 167.8222 | None | WTG Breakdown Maintenance | 7552 | 167.8222
86 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G39 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD | 19:20 | 19:20 | 19:52 | 0 | 0.53333 | 0.53333 | Reset then restore wtg. | Close | 0.013675 | G38 | 148.4444 | None | WTG Breakdown Maintenance | 6680 | 148.4444
87 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G40 | PWEGPL | MSEDCL | 2.564% | 804 | Difference Between 2 Blades Too High | BD | 7:06 | 7:06 | 7:11 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G39 | 26.2222 | None | WTG Breakdown Maintenance | 7552 | 26.2222
88 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G40 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD | 14:45 | 14:45 | 14:50 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G39 | 26.2222 | None | WTG Breakdown Maintenance | 7552 | 26.2222
89 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G40 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD | 15:40 | 15:40 | 15:45 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G39 | 26.2222 | None | WTG Breakdown Maintenance | 7552 | 26.2222
90 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G40 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD | 17:53 | 17:53 | 17:58 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G39 | 26.2222 | None | WTG Breakdown Maintenance | 7552 | 26.2222
91 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G40 | PWEGPL | MSEDCL | 2.564% | 804 | Difference Between 2 Blades Too High | BD | 18:24 | 19:19 | 19:35 | 0.91667 | 0.26667 | 1.1833 | Reboot then restore wtg. | Close | 0.030342 | G39 | 372.3556 | None | WTG Breakdown Maintenance | 7552 | 372.3556
92 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_3 | G40 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD | 19:39 | 19:39 | 23:59 | 0 | 4.3333 | 4.3333 | work in progress | Open | 0.11111 | G39 | 1363.5556 | None | WTG Breakdown Maintenance | 7552 | 1363.5556
93 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 6255.6528 | None | WTG Force Majeaure | 6260 | 6255.6528
94 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 6255.6528 | None | WTG Force Majeaure | 6260 | 6255.6528
95 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | Year_3 | G01 | PWEGPL | MSEDCL | 2.564% | 107 | Yawing Motor Thermal Relays | BD | 9:27 | 9:27 | 9:49 | 0 | 0.36667 | 0.36667 | Auto reset | Close | 0.0094017 | G07 | 106.1958 | None | WTG Breakdown Maintenance | 6951 | 106.1958
96 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | Year_3 | G01 | PWEGPL | MSEDCL | 2.564% | 125 | Yaw Motors Over Current Protection | BD | 11:22 | 15:30 | 17:17 | 4.1333 | 1.7833 | 5.9167 | Checked and found MPCB tripped so recorrect it then restore wtg. | Close | 0.15171 | G07 | 1713.6146 | None | WTG Breakdown Maintenance | 6951 | 1713.6146
97 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | Year_3 | G01 | PWEGPL | MSEDCL | 2.564% | 804 | Difference Between 2 Blades Too High | BD | 17:18 | 17:18 | 20:22 | 0 | 3.0667 | 3.0667 | Checked and found Balde A proportional valve failure so replaced with new one then restore wtg | Close | 0.078632 | G07 | 888.1833 | None | WTG Breakdown Maintenance | 6951 | 888.1833
98 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | 5202 | Stator Contactor Failure | BD | 22:09 | 22:09 | 22:14 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G03 | 18.5972 | None | WTG Breakdown Maintenance | 5356 | 18.5972
99 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | Year_3 | G08 | PWEGPL | MSEDCL | 2.564% | 110 | Yaw Sensor Wiring Error | BD | 4:44 | 7:12 | 7:28 | 2.4667 | 0.26667 | 2.7333 | Untwist then restore wtg. | Close | 0.070085 | G08 | 712.0333 | None | WTG Breakdown Maintenance | 6252 | 712.0333
100 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | Year_3 | G12 | PWEGPL | MSEDCL | 2.564% | 5210 | Failure Of The Contactor's Rotor Power | BD | 2:44 | 2:44 | 2:49 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G13 | 19.7431 | None | WTG Breakdown Maintenance | 5686 | 19.7431
101 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | Year_3 | G12 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD | 12:50 | 12:50 | 12:55 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G13 | 19.7431 | None | WTG Breakdown Maintenance | 5686 | 19.7431
102 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | Year_3 | G13 | PWEGPL | MSEDCL | 2.564% | 5210 | Failure Of The Contactor's Rotor Power | BD | 22:35 | 22:35 | 23:59 | 0 | 1.4 | 1.4 | work in progress | Open | 0.035897 | G14 | 288.2833 | None | WTG Breakdown Maintenance | 4942 | 288.2833
103 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | Year_3 | G14 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD | 22:19 | 22:19 | 22:24 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G15 | 14.0243 | None | WTG Breakdown Maintenance | 4039 | 14.0243
104 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | Year_3 | G14 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD | 23:03 | 23:59 | 23:59 | 0.93333 | 0 | 0.93333 | work in progress | Open | 0.023932 | G15 | 157.0722 | None | WTG Breakdown Maintenance | 4039 | 157.0722
105 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | Year_3 | G15 | PWEGPL | MSEDCL | 2.564% | 5210 | Failure Of The Contactor's Rotor Power | BD | 22:35 | 22:35 | 23:18 | 0 | 0.71667 | 0.71667 | Auto reset | Close | 0.018376 | G16 | 158.7417 | None | WTG Breakdown Maintenance | 5316 | 158.7417
106 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | Year_3 | G16 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD | 4:58 | 4:58 | 5:03 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G17 | 23.4931 | None | WTG Breakdown Maintenance | 6766 | 23.4931
107 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | Year_3 | G16 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 22:56 | 23:52 | 23:59 | 0.93333 | 0.11667 | 1.05 | Reboot then restore wtg. | Close | 0.026923 | G17 | 296.0125 | None | WTG Breakdown Maintenance | 6766 | 296.0125
108 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | Year_3 | G17 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD | 23:13 | 23:13 | 23:59 | 0 | 0.76667 | 0.76667 | work in progress | Open | 0.019658 | G16 | 169.8167 | None | WTG Breakdown Maintenance | 5316 | 169.8167
109 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | Year_3 | G18 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD | 22:23 | 22:23 | 23:59 | 0 | 1.6 | 1.6 | Auto reset | Close | 0.041026 | G19 | 452.5333 | None | WTG Breakdown Maintenance | 6788 | 452.5333
110 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | Year_3 | G19 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD | 23:11 | 23:11 | 23:59 | 0 | 0.8 | 0.8 | work in progress | Open | 0.020513 | G18 | 219.0667 | None | WTG Breakdown Maintenance | 6572 | 219.0667
111 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | Year_3 | G20 | PWEGPL | MSEDCL | 2.564% | 5200 | Magnetothermic Trigger Of The Line Protection | BD | 23:03 | 23:15 | 23:59 | 0.2 | 0.73333 | 0.93333 | work in progress | Open | 0.023932 | G19 | 263.9778 | None | WTG Breakdown Maintenance | 6788 | 263.9778
112 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | Year_3 | G22 | PWEGPL | MSEDCL | 2.564% | 5210 | Failure Of The Contactor's Rotor Power | BD | 22:35 | 23:11 | 23:59 | 0.6 | 0.8 | 1.4 | work in progress | Close | 0.035897 | G05 | 275.6833 | None | WTG Breakdown Maintenance | 4726 | 275.6833
113 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | Year_3 | G30 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD | 0:00 | 2:29 | 13:56 | 2.4833 | 11.45 | 13.9333 | Checked and found Netural relay failure so rplaced with new one then restore wtg. | Close | 0.35726 | G28 | 3634.2778 | None | WTG Breakdown Maintenance | 6260 | 3634.2778
114 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | Year_3 | G32 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 4:37 | 4:37 | 5:10 | 0 | 0.55 | 0.55 | Reboot then restore wtg. | Close | 0.014103 | G26 | 133.6958 | None | WTG Breakdown Maintenance | 5834 | 133.6958
115 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | Year_3 | G32 | PWEGPL | MSEDCL | 2.564% | 700 | PLC-Converter Communication Error | BD | 13:25 | 15:37 | 15:44 | 2.2 | 0.11667 | 2.3167 | Reboot then restore wtg. | Close | 0.059402 | G26 | 563.1431 | None | WTG Breakdown Maintenance | 5834 | 563.1431
116 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | Year_3 | G32 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD | 23:04 | 23:04 | 23:59 | 0 | 0.91667 | 0.91667 | work in progress | Close | 0.023504 | G26 | 222.8264 | None | WTG Breakdown Maintenance | 5834 | 222.8264
117 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | Year_3 | G33 | PWEGPL | MSEDCL | 2.564% | 907 | Emergency Series HUB Trigger | BD | 23:21 | 23:21 | 23:26 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G34 | 25.2778 | None | WTG Breakdown Maintenance | 7280 | 25.2778
118 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | Year_3 | G35 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD | 0:00 | 1:26 | 3:11 | 1.4333 | 1.75 | 3.1833 | Reboot then restore wtg. | Close | 0.081624 | G36 | 449.6458 | None | WTG Breakdown Maintenance | 3390 | 449.6458
119 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | Year_3 | G36 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD | 0:00 | 3:59 | 15:59 | 3.9833 | 12 | 15.9833 | Checked and found balluf sensor cable failure so replaced with new one then restore then restore | Close | 0.40983 | G37 | 4761.7014 | None | WTG Breakdown Maintenance | 7150 | 4761.7014
120 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | Year_3 | G38 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD | 4:44 | 5:23 | 5:23 | 0.65 | 0 | 0.65 | Reset then restore wtg. | Close | 0.016667 | G39 | 183.4083 | None | WTG Breakdown Maintenance | 6772 | 183.4083
121 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | Year_3 | G38 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD | 6:18 | 6:18 | 11:49 | 0 | 5.5167 | 5.5167 | Checked and found no leakage then tou-up 5 litre oil then restore wtg. | Close | 0.14145 | G39 | 1556.6194 | None | WTG Breakdown Maintenance | 6772 | 1556.6194
122 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | Year_3 | G38 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | Manual stop | 11:49 | 11:49 | 15:32 | 0 | 3.7167 | 3.7167 | Manual stop for blade bush gap inspection work | Close | 0.095299 | G39 | 1048.7194 | None | WTG Unscheduled Maintenance | 6772 | 1048.7194
123 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | Year_3 | G39 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD | 23:26 | 23:36 | 23:36 | 0.16667 | 0 | 0.16667 | Auto reset | Close | 0.0042735 | G40 | 26.0556 | None | WTG Breakdown Maintenance | 3752 | 26.0556
124 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | Year_3 | G40 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD | 0:00 | 4:42 | 5:19 | 4.7 | 0.61667 | 5.3167 | Auto reset | Close | 0.13632 | G39 | 1500.1861 | None | WTG Breakdown Maintenance | 6772 | 1500.1861
125 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | Year_3 | G40 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD | 6:00 | 11:13 | 11:24 | 5.2167 | 0.18333 | 5.4 | Reboot then restore wtg. | Close | 0.13846 | G39 | 1523.7 | None | WTG Breakdown Maintenance | 6772 | 1523.7
126 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | Year_3 | G40 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD | 15:49 | 16:13 | 16:15 | 0.4 | 0.033333 | 0.43333 | Reboot then restore wtg. | Close | 0.011111 | G39 | 122.2722 | None | WTG Breakdown Maintenance | 6772 | 122.2722
127 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | Year_3 | G40 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD | 22:23 | 22:39 | 23:04 | 0.26667 | 0.41667 | 0.68333 | Reboot then restore wtg. | Close | 0.017521 | G39 | 192.8139 | None | WTG Breakdown Maintenance | 6772 | 192.8139
128 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 10134.9569 | None | WTG Force Majeaure | 10142 | 10134.9569
129 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 10134.9569 | None | WTG Force Majeaure | 10142 | 10134.9569
130 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | Year_3 | G02 | PWEGPL | MSEDCL | 2.564% | 5225 | Fault In Analog Electronic Power Supply | BD | 1:21 | 3:58 | 4:36 | 2.6167 | 0.63333 | 3.25 | Reset CCU tchen restore wtg. | Close | 0.083333 | G04 | 806.5417 | None | WTG Breakdown Maintenance | 5956 | 806.5417
131 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | 5203 | Heating/Coolant Thermal Magnetic Failure | BD | 4:13 | 5:25 | 8:30 | 1.2 | 3.0833 | 4.2833 | Checked related circuit found MPCB failure so replaced with new one then restore wtg. | Close | 0.10983 | G03 | 1886.4514 | None | WTG Breakdown Maintenance | 10570 | 1886.4514
132 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD | 8:30 | 11:59 | 11:59 | 3.4833 | 0 | 3.4833 | Reset then restore wtg. | Close | 0.089316 | G03 | 1534.1181 | None | WTG Breakdown Maintenance | 10570 | 1534.1181
133 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | Year_3 | G12 | PWEGPL | MSEDCL | 2.564% | 5210 | Failure Of The Contactor's Rotor Power | BD | 3:18 | 3:18 | 3:38 | 0 | 0.33333 | 0.33333 | Auto reset | Close | 0.008547 | G13 | 154 | None | WTG Breakdown Maintenance | 11088 | 154
134 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | Year_3 | G12 | PWEGPL | MSEDCL | 2.564% | 5210 | Failure Of The Contactor's Rotor Power | BD | 13:16 | 13:26 | 13:27 | 0.16667 | 0.016667 | 0.18333 | Reset then restore wtg. | Close | 0.0047009 | G13 | 84.7 | None | WTG Breakdown Maintenance | 11088 | 84.7
135 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | Year_3 | G13 | PWEGPL | MSEDCL | 2.564% | 5228 | Preload Failure | BD | 1:57 | 2:30 | 3:26 | 0.55 | 0.93333 | 1.4833 | Found addon block loose so tight it then restore wtg. | Close | 0.038034 | G14 | 780.975 | None | WTG Breakdown Maintenance | 12636 | 780.975
136 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | Year_3 | G13 | PWEGPL | MSEDCL | 2.564% | 500 | High Generator Winding Temperature | BD | 7:04 | 7:04 | 7:09 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G14 | 43.875 | None | WTG Breakdown Maintenance | 12636 | 43.875
137 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | Year_3 | G13 | PWEGPL | MSEDCL | 2.564% | 500 | High Generator Winding Temperature | BD | 7:20 | 7:20 | 7:25 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G14 | 43.875 | None | WTG Breakdown Maintenance | 12636 | 43.875
138 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | Year_3 | G13 | PWEGPL | MSEDCL | 2.564% | 500 | High Generator Winding Temperature | BD | 7:47 | 7:47 | 7:52 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G14 | 43.875 | None | WTG Breakdown Maintenance | 12636 | 43.875
139 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | Year_3 | G13 | PWEGPL | MSEDCL | 2.564% | 500 | High Generator Winding Temperature | BD | 8:21 | 8:21 | 8:46 | 0 | 0.41667 | 0.41667 | Reset then restore wtg. | Close | 0.010684 | G14 | 219.375 | None | WTG Breakdown Maintenance | 12636 | 219.375
140 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | Year_3 | G13 | PWEGPL | MSEDCL | 2.564% | 500 | High Generator Winding Temperature | BD | 10:17 | 10:17 | 10:22 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G14 | 43.875 | None | WTG Breakdown Maintenance | 12636 | 43.875
141 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | Year_3 | G13 | PWEGPL | MSEDCL | 2.564% | 500 | High Generator Winding Temperature | BD | 10:40 | 10:40 | 10:45 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G14 | 43.875 | None | WTG Breakdown Maintenance | 12636 | 43.875
142 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | Year_3 | G14 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD | 0:00 | 2:07 | 2:19 | 2.1167 | 0.2 | 2.3167 | Reset then restore wtg. | Close | 0.059402 | G15 | 1428.225 | None | WTG Breakdown Maintenance | 14796 | 1428.225
143 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | Year_3 | G16 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 0:00 | 0:18 | 0:28 | 0.3 | 0.16667 | 0.46667 | Reboot then restore wtg. | Close | 0.011966 | G17 | 307.6111 | None | WTG Breakdown Maintenance | 15820 | 307.6111
144 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | Year_3 | G16 | PWEGPL | MSEDCL | 2.564% | 444 | Gearbox Pump Thermal Relay Triggered and High Gearbox Oil Temperature | BD | 3:24 | 3:24 | 9:08 | 0 | 5.7333 | 5.7333 | Reset then restore wtg. | Close | 0.14701 | G17 | 3779.2222 | None | WTG Breakdown Maintenance | 15820 | 3779.2222
145 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | Year_3 | G16 | PWEGPL | MSEDCL | 2.564% | 412 | Gearbox Fan Thermal Relays | BD | 9:13 | 9:13 | 12:01 | 0 | 2.8 | 2.8 | Reset then restore wtg. | Close | 0.071795 | G17 | 1845.6667 | None | WTG Breakdown Maintenance | 15820 | 1845.6667
146 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | Year_3 | G17 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD | 0:00 | 0:39 | 1:01 | 0.65 | 0.36667 | 1.0167 | Reboot then restore wtg. | Close | 0.026068 | G16 | 298.0528 | None | WTG Breakdown Maintenance | 7036 | 298.0528
147 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | Year_3 | G17 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD | 8:04 | 8:04 | 8:09 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G16 | 24.4306 | None | WTG Breakdown Maintenance | 7036 | 24.4306
148 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | Year_3 | G18 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD | 8:09 | 8:09 | 8:14 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G19 | 60.3958 | None | WTG Breakdown Maintenance | 17394 | 60.3958
149 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | Year_3 | G22 | PWEGPL | MSEDCL | 2.564% | 5228 | Preload Failure | BD | 0:00 | 10:26 | 10:54 | 10.4333 | 0.46667 | 10.9 | Found addon block malfunction so replaced it then restore wtg. | Close | 0.27949 | G05 | 5241.0833 | None | WTG Breakdown Maintenance | 11540 | 5241.0833
150 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | Year_3 | G22 | PWEGPL | MSEDCL | 2.564% | 800 | Pitch Drive Error | BD | 12:14 | 12:14 | 12:24 | 0 | 0.16667 | 0.16667 | Auto reset | Close | 0.0042735 | G05 | 80.1389 | None | WTG Breakdown Maintenance | 11540 | 80.1389
151 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | Year_3 | G22 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD | 13:39 | 13:39 | 14:49 | 0 | 1.1667 | 1.1667 | Reset then restore wtg. | Close | 0.029915 | G05 | 560.9722 | None | WTG Breakdown Maintenance | 11540 | 560.9722
152 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | Year_3 | G22 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 14:49 | 14:49 | 17:52 | 0 | 3.05 | 3.05 | Manual stop for Blade bush gap inspection work | Close | 0.078205 | G05 | 1466.5417 | None | WTG Force Majeaure | 11540 | 1466.5417
153 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | Year_3 | G22 | PWEGPL | MSEDCL | 2.564% | 2106 | Temp. Measurement Module Failure | BD | 18:53 | 22:29 | 22:35 | 3.6 | 0.1 | 3.7 | Reboot then restore wtg. | Close | 0.094872 | G05 | 1779.0833 | None | WTG Breakdown Maintenance | 11540 | 1779.0833
154 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | Year_3 | G26 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD | 5:33 | 5:33 | 5:38 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G32 | 9.4514 | None | WTG Breakdown Maintenance | 2722 | 9.4514
155 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | Year_3 | G26 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD | 10:48 | 10:48 | 10:53 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G32 | 9.4514 | None | WTG Breakdown Maintenance | 2722 | 9.4514
156 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | Year_3 | G26 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD | 12:49 | 12:49 | 12:54 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G32 | 9.4514 | None | WTG Breakdown Maintenance | 2722 | 9.4514
157 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | Year_3 | G32 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD | 0:00 | 10:45 | 10:50 | 10.75 | 0.083333 | 10.8333 | Reboot then restore wtg. | Close | 0.27778 | G26 | 5840.0694 | None | WTG Breakdown Maintenance | 12938 | 5840.0694
158 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | Year_3 | G32 | PWEGPL | MSEDCL | 2.564% | 700 | PLC-Converter Communication Error | BD | 19:39 | 23:10 | 23:11 | 3.5167 | 0.016667 | 3.5333 | Reset then restore wtg. | Close | 0.090598 | G26 | 1904.7611 | None | WTG Breakdown Maintenance | 12938 | 1904.7611
159 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | Year_3 | G32 | PWEGPL | MSEDCL | 2.564% | 700 | PLC-Converter Communication Error | BD | 23:20 | 23:23 | 23:59 | 0.05 | 0.6 | 0.65 | work in progress | Close | 0.016667 | G26 | 350.4042 | None | WTG Breakdown Maintenance | 12938 | 350.4042
160 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | Year_3 | G39 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD | 8:11 | 8:11 | 8:16 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G38 | 39.5972 | None | WTG Breakdown Maintenance | 11404 | 39.5972
161 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | Year_3 | G39 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD | 11:51 | 11:51 | 11:56 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G38 | 39.5972 | None | WTG Breakdown Maintenance | 11404 | 39.5972
162 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | Year_3 | G39 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD | 19:46 | 19:46 | 19:57 | 0 | 0.18333 | 0.18333 | Auto reset | Close | 0.0047009 | G38 | 87.1139 | None | WTG Breakdown Maintenance | 11404 | 87.1139
163 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | Year_3 | G40 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD | 7:40 | 10:58 | 10:58 | 3.3 | 0 | 3.3 | Reset then restore wtg. | Close | 0.084615 | G39 | 1575.75 | None | WTG Breakdown Maintenance | 11460 | 1575.75
164 | 2025-04-03 | 2025 | 2025 | 2025-04-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 6349.5875 | None | WTG Force Majeaure | 6354 | 6349.5875
165 | 2025-04-03 | 2025 | 2025 | 2025-04-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 6349.5875 | None | WTG Force Majeaure | 6354 | 6349.5875
166 | 2025-04-03 | 2025 | 2025 | 2025-04-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | 1825 | Automatics Not Ok | BD | 6:16 | 6:16 | 6:21 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G03 | 22.4375 | None | WTG Breakdown Maintenance | 6462 | 22.4375
167 | 2025-04-03 | 2025 | 2025 | 2025-04-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | 1825 | Automatics Not Ok | BD | 7:58 | 7:58 | 8:03 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G03 | 22.4375 | None | WTG Breakdown Maintenance | 6462 | 22.4375
168 | 2025-04-03 | 2025 | 2025 | 2025-04-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | 1825 | Automatics Not Ok | BD | 16:14 | 16:14 | 16:19 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G03 | 22.4375 | None | WTG Breakdown Maintenance | 6462 | 22.4375
169 | 2025-04-03 | 2025 | 2025 | 2025-04-01 | Year_3 | G06 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD | 18:10 | 19:00 | 19:32 | 0.83333 | 0.53333 | 1.3667 | Checked and found SF-6 breaker tripped so charge SF-6 breaker then chen all motor found ok then restore wtg. | Close | 0.035043 | G03 | 367.975 | None | WTG Breakdown Maintenance | 6462 | 367.975
170 | 2025-04-03 | 2025 | 2025 | 2025-04-01 | Year_3 | G06 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD | 20:01 | 21:47 | 23:59 | 1.7667 | 2.2 | 3.9667 | work in progress | Open | 0.10171 | G03 | 1068.025 | None | WTG Breakdown Maintenance | 6462 | 1068.025
171 | 2025-04-03 | 2025 | 2025 | 2025-04-01 | Year_3 | G07 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD | 3:43 | 3:43 | 6:53 | 0 | 3.1667 | 3.1667 | Reset then restore wtg. | Close | 0.081197 | G01 | 929.9444 | None | WTG Breakdown Maintenance | 7048 | 929.9444
172 | 2025-04-03 | 2025 | 2025 | 2025-04-01 | Year_3 | G07 | PWEGPL | MSEDCL | 2.564% | 813 | Low Pressure Of Emergency Accumulators | BD | 18:42 | 19:50 | 19:50 | 1.1333 | 0 | 1.1333 | Reset then restore wtg. | Close | 0.02906 | G01 | 332.8222 | None | WTG Breakdown Maintenance | 7048 | 332.8222
173 | 2025-04-03 | 2025 | 2025 | 2025-04-01 | Year_3 | G07 | PWEGPL | MSEDCL | 2.564% | 2102 | PLC Module Failure | BD | 20:38 | 20:38 | 23:59 | 0 | 3.35 | 3.35 | work in progress | Close | 0.085897 | G01 | 983.7833 | None | WTG Breakdown Maintenance | 7048 | 983.7833
174 | 2025-04-03 | 2025 | 2025 | 2025-04-01 | Year_3 | G13 | PWEGPL | MSEDCL | 2.564% | 500 | High Generator Winding Temperature | BD | 11:31 | 11:31 | 11:36 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G12 | 31.0069 | None | WTG Breakdown Maintenance | 8930 | 31.0069
175 | 2025-04-03 | 2025 | 2025 | 2025-04-01 | Year_3 | G16 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 19:40 | 22:08 | 22:40 | 2.4667 | 0.53333 | 3 | Reboot then restore wtg. | Close | 0.076923 | G17 | 1269 | None | WTG Breakdown Maintenance | 10152 | 1269
176 | 2025-04-03 | 2025 | 2025 | 2025-04-01 | Year_3 | G16 | PWEGPL | MSEDCL | 2.564% | 5248 | Active Crowbar IGBT Errors | BD | 23:51 | 23:51 | 23:59 | 0 | 0.13333 | 0.13333 | work in progress | Close | 0.0034188 | G17 | 56.4 | None | WTG Breakdown Maintenance | 10152 | 56.4
177 | 2025-04-03 | 2025 | 2025 | 2025-04-01 | Year_3 | G18 | PWEGPL | MSEDCL | 2.564% | 813 | Low Pressure Of Emergency Accumulators | BD | 19:46 | 19:46 | 19:51 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G19 | 35.6944 | None | WTG Breakdown Maintenance | 10280 | 35.6944
178 | 2025-04-03 | 2025 | 2025 | 2025-04-01 | Year_3 | G18 | PWEGPL | MSEDCL | 2.564% | 813 | Low Pressure Of Emergency Accumulators | BD | 20:11 | 22:52 | 22:54 | 2.6833 | 0.033333 | 2.7167 | Reset then restore wtg. | Close | 0.069658 | G19 | 1163.6389 | None | WTG Breakdown Maintenance | 10280 | 1163.6389
179 | 2025-04-03 | 2025 | 2025 | 2025-04-01 | Year_3 | G25 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD | 12:01 | 14:11 | 15:25 | 2.1667 | 1.2333 | 3.4 | Checked related circuit found no leakage then restore wtg. | Close | 0.087179 | G27 | 933.3 | None | WTG Breakdown Maintenance | 6588 | 933.3
180 | 2025-04-03 | 2025 | 2025 | 2025-04-01 | Year_3 | G32 | PWEGPL | MSEDCL | 2.564% | 700 | PLC-Converter Communication Error | BD | 0:07 | 1:35 | 1:45 | 1.4667 | 0.16667 | 1.6333 | Reset then restore wtg. | Close | 0.04188 | G26 | 493.2667 | None | WTG Breakdown Maintenance | 7248 | 493.2667
181 | 2025-04-03 | 2025 | 2025 | 2025-04-01 | Year_3 | G32 | PWEGPL | MSEDCL | 2.564% | 700 | PLC-Converter Communication Error | BD | 6:12 | 7:21 | 12:06 | 1.15 | 4.75 | 5.9 | Checked related circuit found module failure so replace module then found nacelle to hub cable one core failure so used spare cable core then restore wtg. | Close | 0.15128 | G26 | 1781.8 | None | WTG Breakdown Maintenance | 7248 | 1781.8
182 | 2025-04-03 | 2025 | 2025 | 2025-04-01 | Year_3 | G33 | PWEGPL | MSEDCL | 2.564% | 813 | Low Pressure Of Emergency Accumulators | BD | 11:59 | 13:04 | 13:11 | 1.0833 | 0.11667 | 1.2 | Reboot then restore wtg. | Close | 0.030769 | G34 | 173.6 | None | WTG Breakdown Maintenance | 3472 | 173.6
183 | 2025-04-03 | 2025 | 2025 | 2025-04-01 | Year_3 | G33 | PWEGPL | MSEDCL | 2.564% | 813 | Low Pressure Of Emergency Accumulators | BD | 13:13 | 13:49 | 15:17 | 0.6 | 1.4667 | 2.0667 | Checked related circuit found pressure switch and solenid valve cable failure so replaced with new one the restore wtg. | Close | 0.052991 | G34 | 583.1444 | None | WTG Breakdown Maintenance | 6772 | 583.1444
184 | 2025-04-03 | 2025 | 2025 | 2025-04-01 | Year_3 | G34 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD | 20:31 | 23:59 | 23:59 | 3.4667 | 0 | 3.4667 | work in progress | Close | 0.088889 | G33 | 853.3778 | None | WTG Breakdown Maintenance | 5908 | 853.3778
185 | 2025-04-03 | 2025 | 2025 | 2025-04-01 | Year_3 | G36 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | BD | 15:39 | 15:39 | 17:07 | 0 | 1.4667 | 1.4667 | Manual stop for blade bush gap inspection work | Close | 0.037607 | G37 | 397.1 | None | WTG Breakdown Maintenance | 6498 | 397.1
186 | 2025-04-03 | 2025 | 2025 | 2025-04-01 | Year_3 | G38 | PWEGPL | MSEDCL | 2.564% | 5203 | Heating/Coolant Thermal Magnetic Failure | BD | 1:36 | 11:09 | 12:23 | 9.55 | 1.2333 | 10.7833 | checked related circuit found MPCB tripped so correct it then restore wtg. | Close | 0.2765 | G39 | 2029.9625 | None | WTG Breakdown Maintenance | 4518 | 2029.9625
187 | 2025-04-03 | 2025 | 2025 | 2025-04-01 | Year_3 | G39 | PWEGPL | MSEDCL | 2.564% | 804 | Difference Between 2 Blades Too High | BD | 20:31 | 20:31 | 20:48 | 0 | 0.28333 | 0.28333 | Auto reset | Close | 0.007265 | G38 | 73.5722 | None | WTG Breakdown Maintenance | 6232 | 73.5722
188 | 2025-04-03 | 2025 | 2025 | 2025-04-01 | Year_3 | G40 | PWEGPL | MSEDCL | 2.564% | 804 | Difference Between 2 Blades Too High | BD | 14:32 | 14:32 | 14:37 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G40 | 21.3472 | None | WTG Breakdown Maintenance | 6148 | 21.3472
189 | 2025-04-03 | 2025 | 2025 | 2025-04-01 | Year_3 | G40 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 20:07 | 20:07 | 20:42 | 0 | 0.58333 | 0.58333 | Auto reset | Close | 0.014957 | G40 | 149.4306 | None | WTG Breakdown Maintenance | 6148 | 149.4306
190 | 2025-04-03 | 2025 | 2025 | 2025-04-01 | Year_3 | G40 | PWEGPL | MSEDCL | 2.564% | 813 | Low Pressure Of Emergency Accumulators | BD | 21:53 | 21:53 | 21:58 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G40 | 21.3472 | None | WTG Breakdown Maintenance | 6148 | 21.3472
191 | 2025-04-04 | 2025 | 2025 | 2025-04-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 4654.7653 | None | WTG Force Majeaure | 4658 | 4654.7653
192 | 2025-04-04 | 2025 | 2025 | 2025-04-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 4654.7653 | None | WTG Force Majeaure | 4658 | 4654.7653
193 | 2025-04-04 | 2025 | 2025 | 2025-04-01 | Year_3 | G03 | PWEGPL | MSEDCL | 2.564% | 110 | Yaw Sensor Wiring Error | BD | 12:18 | 14:00 | 14:24 | 1.7 | 0.4 | 2.1 | Untwist then restore wtg. | Close | 0.053846 | G04 | 77.35 | None | WTG Breakdown Maintenance | 884 | 77.35
194 | 2025-04-04 | 2025 | 2025 | 2025-04-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | 1825 | Automatics Not Ok | BD | 0:43 | 1:46 | 11:06 | 1.05 | 9.3333 | 10.3833 | Check related circuit found loose connection so tight it then update software then restore wtg. | Close | 0.26624 | G03 | 1919.1861 | None | WTG Breakdown Maintenance | 4436 | 1919.1861
195 | 2025-04-04 | 2025 | 2025 | 2025-04-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | 5200 | Magnetothermic Trigger Of The Line Protection | BD | 19:30 | 22:17 | 22:17 | 2.7833 | 0 | 2.7833 | Reset then restore wtg. | Close | 0.071368 | G03 | 514.4528 | None | WTG Breakdown Maintenance | 4436 | 514.4528
196 | 2025-04-04 | 2025 | 2025 | 2025-04-01 | Year_3 | G06 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD | 0:00 | 0:00 | 13:47 | 0 | 13.7833 | 13.7833 | Checked related circuit found SF-6 breaker tripped so we checked T connector found ok then checked power cable then checked transformer then restore wtg. | Close | 0.35342 | G03 | 2547.6194 | None | WTG Breakdown Maintenance | 4436 | 2547.6194
197 | 2025-04-04 | 2025 | 2025 | 2025-04-01 | Year_3 | G07 | PWEGPL | MSEDCL | 2.564% | 2102 | PLC Module Failure | BD | 0:00 | 4:03 | 4:30 | 4.05 | 0.45 | 4.5 | Reboot then restore wtg. | Close | 0.11538 | G01 | 978.75 | None | WTG Breakdown Maintenance | 5220 | 978.75
198 | 2025-04-04 | 2025 | 2025 | 2025-04-01 | Year_3 | G08 | PWEGPL | MSEDCL | 2.564% | 125 | Yaw Motors Over Current Protection | BD | 14:40 | 15:47 | 24:00 | 1.1167 | 8.2167 | 9.3333 | Check related circuit found yaw motor failure so replace with new one then restore wtg. | Close | 0.23932 | G03 | 1725.1111 | None | WTG Breakdown Maintenance | 4436 | 1725.1111
199 | 2025-04-04 | 2025 | 2025 | 2025-04-01 | Year_3 | G11 | PWEGPL | MSEDCL | 2.564% | 116 | Orienting and High Yaw Brake Pressure | BD | 12:06 | 12:06 | 12:11 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G10 | 17.5 | None | WTG Breakdown Maintenance | 5040 | 17.5
200 | 2025-04-04 | 2025 | 2025 | 2025-04-01 | Year_3 | G11 | PWEGPL | MSEDCL | 2.564% | 116 | Orienting and High Yaw Brake Pressure | BD | 12:47 | 12:47 | 12:52 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G10 | 17.5 | None | WTG Breakdown Maintenance | 5040 | 17.5
201 | 2025-04-04 | 2025 | 2025 | 2025-04-01 | Year_3 | G12 | PWEGPL | MSEDCL | 2.564% | 5210 | Failure Of The Contactor's Rotor Power | BD | 13:32 | 13:42 | 13:42 | 0.16667 | 0 | 0.16667 | Reset then restore wtg. | Close | 0.0042735 | G09 | 30.25 | None | WTG Breakdown Maintenance | 4356 | 30.25
202 | 2025-04-04 | 2025 | 2025 | 2025-04-01 | Year_3 | G13 | PWEGPL | MSEDCL | 2.564% | 500 | High Generator Winding Temperature | BD | 0:09 | 0:09 | 0:14 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G12 | 17.2917 | None | WTG Breakdown Maintenance | 4980 | 17.2917
203 | 2025-04-04 | 2025 | 2025 | 2025-04-01 | Year_3 | G14 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD | 15:42 | 15:42 | 15:56 | 0 | 0.23333 | 0.23333 | Reset then restore wtg. | Close | 0.0059829 | G13 | 40.7361 | None | WTG Breakdown Maintenance | 4190 | 40.7361
204 | 2025-04-04 | 2025 | 2025 | 2025-04-01 | Year_3 | G16 | PWEGPL | MSEDCL | 2.564% | 5248 | Active Crowbar IGBT Errors | BD | 0:00 | 0:00 | 9:50 | 0 | 9.8333 | 9.8333 | work in progress | Open | 0.25214 | G17 | 2120.7222 | None | WTG Breakdown Maintenance | 5176 | 2120.7222
205 | 2025-04-04 | 2025 | 2025 | 2025-04-01 | Year_3 | G16 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 9:50 | 9:50 | 14:10 | 0 | 4.3333 | 4.3333 | manual stop for blade bush gap inspection work | Close | 0.11111 | G17 | 934.5556 | None | WTG Force Majeaure | 5176 | 934.5556
206 | 2025-04-04 | 2025 | 2025 | 2025-04-01 | Year_3 | G16 | PWEGPL | MSEDCL | 2.564% | 5248 | Active Crowbar IGBT Errors | BD | 14:10 | 14:10 | 23:59 | 0 | 9.8167 | 9.8167 | work in progress | Open | 0.25171 | G17 | 2117.1278 | None | WTG Breakdown Maintenance | 5176 | 2117.1278
207 | 2025-04-04 | 2025 | 2025 | 2025-04-01 | Year_3 | G23 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 0:43 | 0:43 | 1:05 | 0 | 0.36667 | 0.36667 | Reset then restore wtg. | Close | 0.0094017 | G05 | 74.9833 | None | WTG Breakdown Maintenance | 4908 | 74.9833
208 | 2025-04-04 | 2025 | 2025 | 2025-04-01 | Year_3 | G25 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD | 10:03 | 10:03 | 10:50 | 0 | 0.78333 | 0.78333 | Reset then restore wtg. | Close | 0.020085 | G27 | 142.8931 | None | WTG Breakdown Maintenance | 4378 | 142.8931
209 | 2025-04-04 | 2025 | 2025 | 2025-04-01 | Year_3 | G34 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD | 0:00 | 6:04 | 6:04 | 6.0667 | 0 | 6.0667 | Reset then restore wtg. | Close | 0.15556 | G33 | 1039.675 | None | WTG Breakdown Maintenance | 4113 | 1039.675
210 | 2025-04-05 | 2025 | 2025 | 2025-04-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 2570.2139 | None | WTG Force Majeaure | 2572 | 2570.2139
211 | 2025-04-05 | 2025 | 2025 | 2025-04-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 2570.2139 | None | WTG Force Majeaure | 2572 | 2570.2139
212 | 2025-04-05 | 2025 | 2025 | 2025-04-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | 5200 | Magnetothermic Trigger Of The Line Protection | BD | 11:22 | 11:22 | 11:38 | 0 | 0.26667 | 0.26667 | Reset then restore wtg. | Close | 0.0068376 | G03 | 21.2444 | None | WTG Breakdown Maintenance | 1912 | 21.2444
213 | 2025-04-05 | 2025 | 2025 | 2025-04-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | 5200 | Magnetothermic Trigger Of The Line Protection | BD | 23:53 | 23:53 | 23:57 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0017094 | G03 | 5.3111 | None | WTG Breakdown Maintenance | 1912 | 5.3111
214 | 2025-04-05 | 2025 | 2025 | 2025-04-01 | Year_3 | G11 | PWEGPL | MSEDCL | 2.564% | 116 | Orienting and High Yaw Brake Pressure | BD | 3:46 | 3:46 | 3:51 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G10 | 5.0278 | None | WTG Breakdown Maintenance | 1448 | 5.0278
215 | 2025-04-05 | 2025 | 2025 | 2025-04-01 | Year_3 | G11 | PWEGPL | MSEDCL | 2.564% | 116 | Orienting and High Yaw Brake Pressure | BD | 12:37 | 12:37 | 12:42 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G10 | 5.0278 | None | WTG Breakdown Maintenance | 1448 | 5.0278
216 | 2025-04-05 | 2025 | 2025 | 2025-04-01 | Year_3 | G13 | PWEGPL | MSEDCL | 2.564% | 550 | Generator Fans Thermal Relay Triggered Too Long | BD | 17:47 | 18:11 | 18:16 | 0.4 | 0.083333 | 0.48333 | Reboot then restore wtg. | Close | 0.012393 | G14 | 34.2361 | None | WTG Breakdown Maintenance | 1700 | 34.2361
217 | 2025-04-05 | 2025 | 2025 | 2025-04-01 | Year_3 | G22 | PWEGPL | MSEDCL | 2.564% | 800 | Pitch Drive Error | BD | 16:23 | 16:23 | 16:28 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G21 | 9.5486 | None | WTG Breakdown Maintenance | 2750 | 9.5486
218 | 2025-04-05 | 2025 | 2025 | 2025-04-01 | Year_3 | G33 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 11:40 | 11:40 | 16:38 | 0 | 4.9667 | 4.9667 | manual stop for blade bush gap inspection work | Close | 0.12735 | G34 | 523.1556 | None | WTG Breakdown Maintenance | 2528 | 523.1556
219 | 2025-04-06 | 2025 | 2025 | 2025-04-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 2822.0389 | None | WTG Force Majeaure | 2824 | 2822.0389
220 | 2025-04-06 | 2025 | 2025 | 2025-04-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 2822.0389 | None | WTG Force Majeaure | 2824 | 2822.0389
221 | 2025-04-06 | 2025 | 2025 | 2025-04-01 | Year_3 | G01 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD | 14:35 | 14:35 | 14:40 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G07 | 11.9028 | None | WTG Breakdown Maintenance | 3428 | 11.9028
222 | 2025-04-06 | 2025 | 2025 | 2025-04-01 | Year_3 | G15 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 10:45 | 10:45 | 13:44 | 0 | 2.9833 | 2.9833 | Manual stop for blade bush gap inspection work. | Close | 0.076496 | G14 | 399.2694 | None | WTG Force Majeaure | 3212 | 399.2694
223 | 2025-04-06 | 2025 | 2025 | 2025-04-01 | Year_3 | G16 | PWEGPL | MSEDCL | 2.564% | 5248 | Active Crowbar IGBT Errors | BD | 0:00 | 0:00 | 23:59 | 0 | 23.9833 | 23.9833 | work in progress | Open | 0.61496 | G17 | 3497.5694 | None | WTG Breakdown Maintenance | 3500 | 3497.5694
224 | 2025-04-07 | 2025 | 2025 | 2025-04-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 7801.5785 | None | WTG Force Majeaure | 7807 | 7801.5785
225 | 2025-04-07 | 2025 | 2025 | 2025-04-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 7801.5785 | None | WTG Force Majeaure | 7807 | 7801.5785
226 | 2025-04-07 | 2025 | 2025 | 2025-04-01 | Year_3 | G01 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD | 2:25 | 2:25 | 2:30 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G07 | 14.1007 | None | WTG Breakdown Maintenance | 4061 | 14.1007
227 | 2025-04-07 | 2025 | 2025 | 2025-04-01 | Year_3 | G01 | PWEGPL | MSEDCL | 2.564% | 800 | Pitch Drive Error | BD | 17:43 | 17:43 | 17:48 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G07 | 14.1007 | None | WTG Breakdown Maintenance | 4061 | 14.1007
228 | 2025-04-07 | 2025 | 2025 | 2025-04-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | 5200 | Magnetothermic Trigger Of The Line Protection | BD | 16:29 | 16:29 | 16:31 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0008547 | G03 | 7.6611 | None | WTG Breakdown Maintenance | 5516 | 7.6611
229 | 2025-04-07 | 2025 | 2025 | 2025-04-01 | Year_3 | G06 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD | 1:24 | 1:29 | 2:35 | 0.083333 | 1.1 | 1.1833 | check and found SF-6 breaker tripped so charge it then checked all motors then restore wtg. | Close | 0.030342 | G03 | 271.9694 | None | WTG Breakdown Maintenance | 5516 | 271.9694
230 | 2025-04-07 | 2025 | 2025 | 2025-04-01 | Year_3 | G07 | PWEGPL | MSEDCL | 2.564% | 227 | Hydraulic HUB Filter Dirty Too Long | BD | 4:37 | 7:27 | 7:27 | 2.8333 | 0 | 2.8333 | Reset then restore wtg. | Close | 0.07265 | G01 | 605.3889 | None | WTG Breakdown Maintenance | 5128 | 605.3889
231 | 2025-04-07 | 2025 | 2025 | 2025-04-01 | Year_3 | G16 | PWEGPL | MSEDCL | 2.564% | 5248 | Active Crowbar IGBT Errors | BD | 0:00 | 0:00 | 23:59 | 0 | 23.9833 | 23.9833 | work in progress | Close | 0.61496 | G17 | 5116.4444 | None | WTG Breakdown Maintenance | 5120 | 5116.4444
232 | 2025-04-07 | 2025 | 2025 | 2025-04-01 | Year_3 | G28 | PWEGPL | MSEDCL | 2.564% | 523 | High Temperature Of Coolant In The Input Of The Cooling Circuit | BD | 14:18 | 14:18 | 14:23 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G30 | 24.9826 | None | WTG Breakdown Maintenance | 7195 | 24.9826
233 | 2025-04-07 | 2025 | 2025 | 2025-04-01 | Year_3 | G28 | PWEGPL | MSEDCL | 2.564% | 523 | High Temperature Of Coolant In The Input Of The Cooling Circuit | BD | 16:06 | 16:06 | 16:17 | 0 | 0.18333 | 0.18333 | Auto reset | Close | 0.0047009 | G30 | 54.9618 | None | WTG Breakdown Maintenance | 7195 | 54.9618
234 | 2025-04-07 | 2025 | 2025 | 2025-04-01 | Year_3 | G28 | PWEGPL | MSEDCL | 2.564% | 523 | High Temperature Of Coolant In The Input Of The Cooling Circuit | BD | 16:38 | 16:38 | 16:48 | 0 | 0.16667 | 0.16667 | Auto reset | Close | 0.0042735 | G30 | 49.9653 | None | WTG Breakdown Maintenance | 7195 | 49.9653
235 | 2025-04-07 | 2025 | 2025 | 2025-04-01 | Year_3 | G28 | PWEGPL | MSEDCL | 2.564% | 523 | High Temperature Of Coolant In The Input Of The Cooling Circuit | BD | 19:44 | 19:44 | 19:49 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G30 | 24.9826 | None | WTG Breakdown Maintenance | 7195 | 24.9826
236 | 2025-04-07 | 2025 | 2025 | 2025-04-01 | Year_3 | G28 | PWEGPL | MSEDCL | 2.564% | 523 | High Temperature Of Coolant In The Input Of The Cooling Circuit | BD | 20:07 | 20:07 | 20:12 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G30 | 24.9826 | None | WTG Breakdown Maintenance | 7195 | 24.9826
237 | 2025-04-07 | 2025 | 2025 | 2025-04-01 | Year_3 | G33 | PWEGPL | MSEDCL | 2.564% | CE100008 | General Work Stoppage | BD | 12:10 | 12:10 | 17:16 | 0 | 5.1 | 5.1 | Manual stop for Blade A pitch seal replacement work | Close | 0.13077 | G34 | 1307.5125 | None | WTG Unscheduled Maintenance | 6153 | 1307.5125
238 | 2025-04-07 | 2025 | 2025 | 2025-04-01 | Year_3 | G38 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD | 14:24 | 14:24 | 14:29 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G40 | 23.6875 | None | WTG Breakdown Maintenance | 6822 | 23.6875
239 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 3907.2847 | None | WTG Force Majeaure | 3910 | 3907.2847
240 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 3907.2847 | None | WTG Force Majeaure | 3910 | 3907.2847
241 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | Year_3 | G01 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD | 12:59 | 12:59 | 13:04 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G07 | 14.375 | None | WTG Breakdown Maintenance | 4140 | 14.375
242 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | Year_3 | G03 | PWEGPL | MSEDCL | 2.564% | 426 | Rotor Speed Reading Failure | BD | 4:33 | 4:33 | 4:38 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G04 | 8.4028 | None | WTG Breakdown Maintenance | 2420 | 8.4028
243 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | 5200 | Magnetothermic Trigger Of The Line Protection | BD | 13:42 | 13:42 | 13:47 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G03 | 13.8403 | None | WTG Breakdown Maintenance | 3986 | 13.8403
244 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | 523 | High Temperature Of Coolant In The Input Of The Cooling Circuit | BD | 13:59 | 13:59 | 14:04 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G03 | 13.8403 | None | WTG Breakdown Maintenance | 3986 | 13.8403
245 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | 5200 | Magnetothermic Trigger Of The Line Protection | BD | 22:49 | 23:59 | 23:59 | 1.1667 | 0 | 1.1667 | work in progress | Open | 0.029915 | G03 | 193.7639 | None | WTG Breakdown Maintenance | 3986 | 193.7639
246 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | Year_3 | G09 | PWEGPL | MSEDCL | 2.564% | 5203 | Heating/Coolant Thermal Magnetic Failure | BD | 19:19 | 23:09 | 23:59 | 3.8333 | 0.83333 | 4.6667 | work in progress | Open | 0.11966 | G12 | 838.0556 | None | WTG Breakdown Maintenance | 4310 | 838.0556
247 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | Year_3 | G10 | PWEGPL | MSEDCL | 2.564% | 527 | High Temperature Of Upper Radiator | BD | 23:45 | 23:45 | 23:50 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G11 | 15.4861 | None | WTG Breakdown Maintenance | 4460 | 15.4861
248 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | Year_3 | G11 | PWEGPL | MSEDCL | 2.564% | 577 | Slipping Rings Fan Or Heating Resistor Failure | BD | 9:14 | 11:24 | 13:26 | 2.1667 | 2.0333 | 4.2 | Checked related circuit found relay failure so replaced reley then restore wtg. | Close | 0.10769 | G10 | 719.6 | None | WTG Breakdown Maintenance | 4112 | 719.6
249 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | Year_3 | G13 | PWEGPL | MSEDCL | 2.564% | 500 | High Generator Winding Temperature | BD | 23:53 | 23:53 | 23:58 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G12 | 14.9653 | None | WTG Breakdown Maintenance | 4310 | 14.9653
250 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | Year_3 | G14 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD | 13:08 | 13:08 | 13:19 | 0 | 0.18333 | 0.18333 | Auto reset | Close | 0.0047009 | G15 | 8.8229 | None | WTG Breakdown Maintenance | 1155 | 8.8229
251 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | Year_3 | G16 | PWEGPL | MSEDCL | 2.564% | 5248 | Active Crowbar IGBT Errors | BD | 0:00 | 0:00 | 23:59 | 0 | 23.9833 | 23.9833 | work in progress | Open | 0.61496 | G15 | 1154.1979 | None | WTG Breakdown Maintenance | 1155 | 1154.1979
252 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | Year_3 | G23 | PWEGPL | MSEDCL | 2.564% | 2106 | Temp. Measurement Module Failure | BD | 4:19 | 4:19 | 4:24 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G05 | 14.0486 | None | WTG Breakdown Maintenance | 4046 | 14.0486
253 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | Year_3 | G23 | PWEGPL | MSEDCL | 2.564% | 501 | Generator DE Bearing High Temperature Alarm | BD | 4:30 | 4:30 | 4:35 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G05 | 14.0486 | None | WTG Breakdown Maintenance | 4046 | 14.0486
254 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | Year_3 | G23 | PWEGPL | MSEDCL | 2.564% | 2106 | Temp. Measurement Module Failure | BD | 6:14 | 6:14 | 6:34 | 0 | 0.33333 | 0.33333 | Auto reset | Close | 0.008547 | G05 | 56.1944 | None | WTG Breakdown Maintenance | 4046 | 56.1944
255 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | Year_3 | G23 | PWEGPL | MSEDCL | 2.564% | 2106 | Temp. Measurement Module Failure | BD | 9:10 | 9:10 | 9:18 | 0 | 0.13333 | 0.13333 | Auto reset | Close | 0.0034188 | G05 | 22.4778 | None | WTG Breakdown Maintenance | 4046 | 22.4778
256 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | Year_3 | G26 | PWEGPL | MSEDCL | 2.564% | 527 | High Temperature Of Upper Radiator | BD | 23:57 | 23:57 | 23:59 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0008547 | G32 | 5.2611 | None | WTG Breakdown Maintenance | 3788 | 5.2611
257 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | Year_3 | G28 | PWEGPL | MSEDCL | 2.564% | 523 | High Temperature Of Coolant In The Input Of The Cooling Circuit | Manual stop | 11:18 | 11:18 | 12:26 | 0 | 1.1333 | 1.1333 | Coolant cooling rediator clean then restore wtg. | Close | 0.02906 | G30 | 241.1167 | None | WTG Unscheduled Maintenance | 5106 | 241.1167
258 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | Year_3 | G30 | PWEGPL | MSEDCL | 2.564% | 426 | Rotor Speed Reading Failure | BD | 8:07 | 8:07 | 8:12 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G28 | 13.5764 | None | WTG Breakdown Maintenance | 3910 | 13.5764
259 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | Year_3 | G30 | PWEGPL | MSEDCL | 2.564% | 426 | Rotor Speed Reading Failure | BD | 9:02 | 9:02 | 9:07 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G28 | 13.5764 | None | WTG Breakdown Maintenance | 3910 | 13.5764
260 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | Year_3 | G30 | PWEGPL | MSEDCL | 2.564% | 426 | Rotor Speed Reading Failure | BD | 9:24 | 9:24 | 9:29 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G28 | 13.5764 | None | WTG Breakdown Maintenance | 3910 | 13.5764
261 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | Year_3 | G33 | PWEGPL | MSEDCL | 2.564% | CE100008 | General Work Stoppage | Manual stop | 15:34 | 15:34 | 16:49 | 0 | 1.25 | 1.25 | Gear box oil leakage arrest then top-up 15 liter gear oil then start wtg. | Close | 0.032051 | G34 | 192.5 | None | WTG Unscheduled Maintenance | 3696 | 192.5
262 | 2025-04-08 | 2025 | 2025 | 2025-04-01 | Year_3 | G37 | PWEGPL | MSEDCL | 2.564% | 402 | Gearbox Oil Level Low | BD | 5:40 | 5:40 | 9:20 | 0 | 3.6667 | 3.6667 | Reset then restore wtg. | Close | 0.094017 | G36 | 778.25 | None | WTG Breakdown Maintenance | 5094 | 778.25
263 | 2025-04-09 | 2025 | 2025 | 2025-04-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 8901.8139 | None | WTG Force Majeaure | 8908 | 8901.8139
264 | 2025-04-09 | 2025 | 2025 | 2025-04-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 8901.8139 | None | WTG Force Majeaure | 8908 | 8901.8139
265 | 2025-04-09 | 2025 | 2025 | 2025-04-01 | Year_3 | G01 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD | 10:25 | 10:25 | 10:30 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G07 | 32.8472 | None | WTG Breakdown Maintenance | 9460 | 32.8472
266 | 2025-04-09 | 2025 | 2025 | 2025-04-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | 5200 | Magnetothermic Trigger Of The Line Protection | BD | 0:00 | 0:00 | 0:42 | 0 | 0.7 | 0.7 | Reset then restore wtg. | Close | 0.017949 | G03 | 280.8167 | None | WTG Breakdown Maintenance | 9628 | 280.8167
267 | 2025-04-09 | 2025 | 2025 | 2025-04-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | 208 | HU Pump Drive Failure | BD | 7:40 | 11:19 | 11:35 | 3.65 | 0.26667 | 3.9167 | Checked related circuit found contactor straked so replaced with new one then restore wtg. | Close | 0.10043 | G03 | 1571.2361 | None | WTG Breakdown Maintenance | 9628 | 1571.2361
268 | 2025-04-09 | 2025 | 2025 | 2025-04-01 | Year_3 | G09 | PWEGPL | MSEDCL | 2.564% | 5203 | Heating/Coolant Thermal Magnetic Failure | BD | 0:00 | 0:00 | 2:14 | 0 | 2.2333 | 2.2333 | Checked related circuit found ccU coolant cooling motor & MPCB failure so replaced with new one then restore wtg. then start wtg. | Close | 0.057265 | G12 | 870.0694 | None | WTG Breakdown Maintenance | 9350 | 870.0694
269 | 2025-04-09 | 2025 | 2025 | 2025-04-01 | Year_3 | G10 | PWEGPL | MSEDCL | 2.564% | 527 | High Temperature Of Upper Radiator | BD | 0:38 | 0:38 | 0:43 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G11 | 43.2083 | None | WTG Breakdown Maintenance | 12444 | 43.2083
270 | 2025-04-09 | 2025 | 2025 | 2025-04-01 | Year_3 | G10 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD | 7:40 | 11:19 | 11:22 | 3.65 | 0.05 | 3.7 | Reset then restore wtg. | Close | 0.094872 | G11 | 1918.45 | None | WTG Breakdown Maintenance | 12444 | 1918.45
271 | 2025-04-09 | 2025 | 2025 | 2025-04-01 | Year_3 | G12 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD | 13:53 | 13:53 | 14:03 | 0 | 0.16667 | 0.16667 | Auto reset | Close | 0.0042735 | G13 | 56.2639 | None | WTG Breakdown Maintenance | 8102 | 56.2639
272 | 2025-04-09 | 2025 | 2025 | 2025-04-01 | Year_3 | G15 | PWEGPL | MSEDCL | 2.564% | 502 | Generator NDE Bearing High Temperature Alarm | BD | 5:02 | 5:02 | 5:07 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G14 | 36.0833 | None | WTG Breakdown Maintenance | 10392 | 36.0833
273 | 2025-04-09 | 2025 | 2025 | 2025-04-01 | Year_3 | G16 | PWEGPL | MSEDCL | 2.564% | 5248 | Active Crowbar IGBT Errors | BD | 0:00 | 0:00 | 18:54 | 0 | 18.9 | 18.9 | Replaced Carbon brush and holder then restore wtg and power set to 500 kw | Close | 0.48462 | G17 | 10226.475 | Due to material shortage power set on 500 kw | WTG Breakdown Maintenance | 12986 | 10226.475
274 | 2025-04-09 | 2025 | 2025 | 2025-04-01 | Year_3 | G18 | PWEGPL | MSEDCL | 2.564% | 502 | Generator NDE Bearing High Temperature Alarm | BD | 1:40 | 1:40 | 1:45 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G19 | 40.7222 | None | WTG Breakdown Maintenance | 11728 | 40.7222
275 | 2025-04-09 | 2025 | 2025 | 2025-04-01 | Year_3 | G18 | PWEGPL | MSEDCL | 2.564% | 502 | Generator NDE Bearing High Temperature Alarm | BD | 5:20 | 5:20 | 5:25 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G19 | 40.7222 | None | WTG Breakdown Maintenance | 11728 | 40.7222
276 | 2025-04-09 | 2025 | 2025 | 2025-04-01 | Year_3 | G19 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD | 9:31 | 13:52 | 13:52 | 4.35 | 0 | 4.35 | Reset then restore wtg. | Close | 0.11154 | G20 | 2228.8312 | None | WTG Breakdown Maintenance | 12297 | 2228.8312
277 | 2025-04-09 | 2025 | 2025 | 2025-04-01 | Year_3 | G22 | PWEGPL | MSEDCL | 2.564% | 402 | Gearbox Oil Level Low | BD | 5:40 | 5:40 | 8:30 | 0 | 2.8333 | 2.8333 | Reset then restore wtg. | Close | 0.07265 | G21 | 1061.7917 | None | WTG Breakdown Maintenance | 8994 | 1061.7917
278 | 2025-04-09 | 2025 | 2025 | 2025-04-01 | Year_3 | G26 | PWEGPL | MSEDCL | 2.564% | 527 | High Temperature Of Upper Radiator | BD | 3:02 | 3:02 | 3:07 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G32 | 24.6042 | None | WTG Breakdown Maintenance | 7086 | 24.6042
279 | 2025-04-09 | 2025 | 2025 | 2025-04-01 | Year_3 | G26 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD | 13:17 | 13:17 | 13:22 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G32 | 24.6042 | None | WTG Breakdown Maintenance | 7086 | 24.6042
280 | 2025-04-09 | 2025 | 2025 | 2025-04-01 | Year_3 | G37 | PWEGPL | MSEDCL | 2.564% | 5219 | Coolant Of The Coolant Circuit Failure | BD | 14:24 | 14:52 | 14:54 | 0.46667 | 0.033333 | 0.5 | Reset then restore wtg. | Close | 0.012821 | G36 | 205.5 | None | WTG Breakdown Maintenance | 9864 | 205.5
281 | 2025-04-10 | 2025 | 2025 | 2025-04-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 12533.2903 | None | WTG Force Majeaure | 12542 | 12533.2903
282 | 2025-04-10 | 2025 | 2025 | 2025-04-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 12533.2903 | None | WTG Force Majeaure | 12542 | 12533.2903
283 | 2025-04-10 | 2025 | 2025 | 2025-04-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | 5200 | Magnetothermic Trigger Of The Line Protection | BD | 14:35 | 15:32 | 15:36 | 0.95 | 0.066667 | 1.0167 | Reboot then restore wtg. | Close | 0.026068 | G03 | 555.7778 | None | WTG Breakdown Maintenance | 13120 | 555.7778
284 | 2025-04-10 | 2025 | 2025 | 2025-04-01 | Year_3 | G07 | PWEGPL | MSEDCL | 2.564% | 211 | Hydraulic HUB Filter Dirty | BD | 14:45 | 16:03 | 16:05 | 1.3 | 0.033333 | 1.3333 | Reset then restore wtg. | Close | 0.034188 | G01 | 819.4444 | None | WTG Breakdown Maintenance | 14750 | 819.4444
285 | 2025-04-10 | 2025 | 2025 | 2025-04-01 | Year_3 | G12 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD | 14:02 | 14:35 | 14:45 | 0.55 | 0.16667 | 0.71667 | Reboot then restore wtg. | Close | 0.018376 | G13 | 331.1 | None | WTG Breakdown Maintenance | 11088 | 331.1
286 | 2025-04-10 | 2025 | 2025 | 2025-04-01 | Year_3 | G14 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop | 12:22 | 12:22 | 17:05 | 0 | 4.7167 | 4.7167 | Manual stop for Blade A pitch seal replacement work | Close | 0.12094 | G15 | 2809.5611 | None | WTG Unscheduled Maintenance | 14296 | 2809.5611
287 | 2025-04-11 | 2025 | 2025 | 2025-04-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 14791.7208 | None | WTG Force Majeaure | 14802 | 14791.7208
288 | 2025-04-11 | 2025 | 2025 | 2025-04-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 14791.7208 | None | WTG Force Majeaure | 14802 | 14791.7208
289 | 2025-04-11 | 2025 | 2025 | 2025-04-01 | Year_3 | G03 | PWEGPL | MSEDCL | 2.564% | CE100008 | General Work Stoppage | Manual stop | 11:50 | 11:50 | 13:15 | 0 | 1.4167 | 1.4167 | Manual stop for gear box hose replacement work | Close | 0.036325 | G04 | 848.7604 | None | WTG Unscheduled Maintenance | 14379 | 848.7604
290 | 2025-04-11 | 2025 | 2025 | 2025-04-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | CE100008 | General Work Stoppage | Manual stop | 13:30 | 13:30 | 14:15 | 0 | 0.75 | 0.75 | Manual stop for CCU raditor cleaning work | Close | 0.019231 | G03 | 446.4062 | None | WTG Unscheduled Maintenance | 14285 | 446.4062
291 | 2025-04-11 | 2025 | 2025 | 2025-04-01 | Year_3 | G07 | PWEGPL | MSEDCL | 2.564% | CE100008 | General Work Stoppage | Manual stop | 15:18 | 15:18 | 16:02 | 0 | 0.73333 | 0.73333 | Manual stop for CCU raditor cleaning work | Close | 0.018803 | G01 | 436.7306 | None | WTG Unscheduled Maintenance | 14293 | 436.7306
292 | 2025-04-12 | 2025 | 2025 | 2025-04-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 12843.075 | None | WTG Force Majeaure | 12852 | 12843.075
293 | 2025-04-12 | 2025 | 2025 | 2025-04-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 12843.075 | None | WTG Force Majeaure | 12852 | 12843.075
294 | 2025-04-12 | 2025 | 2025 | 2025-04-01 | Year_3 | G01 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD | 11:11 | 12:19 | 12:20 | 1.1333 | 0.016667 | 1.15 | Reset then restore wtg. | Close | 0.029487 | G07 | 751.9562 | None | WTG Breakdown Maintenance | 15693 | 751.9562
295 | 2025-04-12 | 2025 | 2025 | 2025-04-01 | Year_3 | G18 | PWEGPL | MSEDCL | 2.564% | 5205 | Magnetothermic Of The Stator Protection Failure Or Door Open | BD | 10:10 | 10:35 | 12:26 | 0.41667 | 1.85 | 2.2667 | check related circuit found ACB relay malfuction so replace with new one then restore wtg. | Close | 0.05812 | G19 | 1222.9611 | None | WTG Breakdown Maintenance | 12949 | 1222.9611
296 | 2025-04-12 | 2025 | 2025 | 2025-04-01 | Year_3 | G23 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD | 9:20 | 10:02 | 11:15 | 0.7 | 1.2167 | 1.9167 | Check related circuit found no leakage then restore wtg. | Close | 0.049145 | G22 | 1009.3646 | None | WTG Breakdown Maintenance | 12639 | 1009.3646
297 | 2025-04-12 | 2025 | 2025 | 2025-04-01 | Year_3 | G33 | PWEGPL | MSEDCL | 2.564% | 907 | Emergency Series HUB Trigger | BD | 14:10 | 15:02 | 15:05 | 0.86667 | 0.05 | 0.91667 | Reset then restore wtg. | Close | 0.023504 | G34 | 418.6875 | None | WTG Breakdown Maintenance | 10962 | 418.6875
298 | 2025-04-12 | 2025 | 2025 | 2025-04-01 | Year_3 | G39 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD | 14:45 | 15:38 | 15:40 | 0.88333 | 0.033333 | 0.91667 | Reboot then restore wtg. | Close | 0.023504 | G40 | 417.3889 | None | WTG Breakdown Maintenance | 10928 | 417.3889
299 | 2025-04-13 | 2025 | 2025 | 2025-04-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 8258.2611 | None | WTG Force Majeaure | 8264 | 8258.2611
300 | 2025-04-13 | 2025 | 2025 | 2025-04-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 8258.2611 | None | WTG Force Majeaure | 8264 | 8258.2611
301 | 2025-04-13 | 2025 | 2025 | 2025-04-01 | Year_3 | G01 | PWEGPL | MSEDCL | 2.564% | 5210 | Failure Of The Contactor's Rotor Power | BD | 13:01 | 14:05 | 14:07 | 1.0667 | 0.033333 | 1.1 | Reboot then restore wtg. | Close | 0.028205 | G07 | 447.7 | None | WTG Breakdown Maintenance | 9768 | 447.7
302 | 2025-04-13 | 2025 | 2025 | 2025-04-01 | Year_3 | G05 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD | 15:05 | 15:30 | 15:32 | 0.41667 | 0.033333 | 0.45 | Reboot then restore wtg. | Close | 0.011538 | G22 | 155.025 | None | WTG Breakdown Maintenance | 8268 | 155.025
303 | 2025-04-13 | 2025 | 2025 | 2025-04-01 | Year_3 | G21 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD | 15:05 | 15:45 | 15:47 | 0.66667 | 0.033333 | 0.7 | Reboot then restore wtg. | Close | 0.017949 | G22 | 241.15 | None | WTG Breakdown Maintenance | 8268 | 241.15
304 | 2025-04-13 | 2025 | 2025 | 2025-04-01 | Year_3 | G26 | PWEGPL | MSEDCL | 2.564% | CE100008 | General Work Stoppage | Manual stop | 11:56 | 11:56 | 13:37 | 0 | 1.6833 | 1.6833 | Manual stop for gear box hose replacement work | Close | 0.043162 | G32 | 675.2271 | None | WTG Unscheduled Maintenance | 9627 | 675.2271
305 | 2025-04-13 | 2025 | 2025 | 2025-04-01 | Year_3 | G39 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD | 10:42 | 11:30 | 11:32 | 0.8 | 0.033333 | 0.83333 | Reboot then restore wtg. | Close | 0.021368 | G40 | 336.3542 | None | WTG Breakdown Maintenance | 9687 | 336.3542
306 | 2025-04-14 | 2025 | 2025 | 2025-04-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 14813.7056 | None | WTG Force Majeaure | 14824 | 14813.7056
307 | 2025-04-14 | 2025 | 2025 | 2025-04-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 14813.7056 | None | WTG Force Majeaure | 14824 | 14813.7056
308 | 2025-04-14 | 2025 | 2025 | 2025-04-01 | Year_3 | G10 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop | 12:10 | 12:10 | 15:30 | 0 | 3.3333 | 3.3333 | Manual stop for Lift supporting & plateform guide clamp replaced then clean CCU radiator then restore wyg. | Close | 0.08547 | G11 | 2236.1111 | None | WTG Breakdown Maintenance | 16100 | 2236.1111
309 | 2025-04-14 | 2025 | 2025 | 2025-04-01 | Year_3 | G11 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop | 16:15 | 16:15 | 17:20 | 0 | 1.0833 | 1.0833 | Manual stop for CCU raditor cleaning work | Close | 0.027778 | G10 | 722.2674 | None | WTG Breakdown Maintenance | 16001 | 722.2674
310 | 2025-04-14 | 2025 | 2025 | 2025-04-01 | Year_3 | G01 | PWEGPL | MSEDCL | 2.564% | 5210 | Failure Of The Contactor's Rotor Power | BD | 14:09 | 14:39 | 15:30 | 0.5 | 0.85 | 1.35 | Checked related circuit found ok then interchange addon then restore wtg. | Close | 0.034615 | G07 | 1019.925 | None | WTG Breakdown Maintenance | 18132 | 1019.925
311 | 2025-04-15 | 2025 | 2025 | 2025-04-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 15884.9611 | None | WTG Force Majeaure | 15896 | 15884.9611
312 | 2025-04-15 | 2025 | 2025 | 2025-04-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 15884.9611 | None | WTG Force Majeaure | 15896 | 15884.9611
313 | 2025-04-15 | 2025 | 2025 | 2025-04-01 | Year_3 | G01 | PWEGPL | MSEDCL | 2.564% | 5210 | Failure Of The Contactor's Rotor Power | BD | 10:47 | 11:32 | 11:34 | 0.75 | 0.033333 | 0.78333 | Reset then restore wtg. | Close | 0.020085 | G07 | 484.7854 | None | WTG Breakdown Maintenance | 14853 | 484.7854
314 | 2025-04-15 | 2025 | 2025 | 2025-04-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 15:35 | 16:10 | 16:12 | 0.58333 | 0.033333 | 0.61667 | Reboot then restore wtg. | Close | 0.015812 | G03 | 384.466 | None | WTG Breakdown Maintenance | 14963 | 384.466
315 | 2025-04-15 | 2025 | 2025 | 2025-04-01 | Year_3 | G39 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop | 11:30 | 11:30 | 15:45 | 0 | 4.25 | 4.25 | Blade C Pitch seal replaced then start wtg. | Close | 0.10897 | G40 | 2249.8438 | None | WTG Unscheduled Maintenance | 12705 | 2249.8438
316 | 2025-04-16 | 2025 | 2025 | 2025-04-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 15873.9299 | None | WTG Force Majeaure | 15884.9611 | 15873.9299
317 | 2025-04-16 | 2025 | 2025 | 2025-04-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 15873.9299 | None | WTG Force Majeaure | 15884.9611 | 15873.9299
318 | 2025-04-16 | 2025 | 2025 | 2025-04-01 | Year_3 | G21 | PWEGPL | MSEDCL | 2.564% | 5228 | Preload Failure | BD | 15:12 | 15:41 | 15:58 | 0.48333 | 0.28333 | 0.76667 | Checked related circuit found addon loose so tight it then restore wtg. | Close | 0.019658 | G22 | 388.7319 | None | WTG Breakdown Maintenance | 12169 | 388.7319
319 | 2025-04-16 | 2025 | 2025 | 2025-04-01 | Year_3 | G25 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD | 15:12 | 16:05 | 16:07 | 0.88333 | 0.033333 | 0.91667 | Reset then restore wtg. | Close | 0.023504 | G27 | 465.3993 | None | WTG Breakdown Maintenance | 12185 | 465.3993
320 | 2025-04-16 | 2025 | 2025 | 2025-04-01 | Year_3 | G38 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD | 15:12 | 16:15 | 16:18 | 1.05 | 0.05 | 1.1 | Reset then restore wtg. | Close | 0.028205 | G40 | 685.3 | None | WTG Breakdown Maintenance | 14952 | 685.3
321 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 12168.0823 | None | WTG Force Majeaure | 12176.5382 | 12168.0823
322 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 12168.0823 | None | WTG Force Majeaure | 12176.5382 | 12168.0823
323 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | Year_3 | G01 | PWEGPL | MSEDCL | 2.564% | 207 | Hydraulic Oil High Temperature | BD | 4:02 | 4:50 | 4:52 | 0.8 | 0.033333 | 0.83333 | Reboot then restore wtg. | Close | 0.021368 | G07 | 527.4306 | None | WTG Breakdown Maintenance | 15190 | 527.4306
324 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | Year_3 | G01 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop | 11:20 | 11:20 | 13:10 | 0 | 1.8333 | 1.8333 | Check related circuit found internal leakage from proportional valve so replaced with new one then restore wtg. | Close | 0.047009 | G07 | 1160.3472 | None | WTG Unscheduled Maintenance | 15190 | 1160.3472
325 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | Year_3 | G02 | PWEGPL | MSEDCL | 2.564% | 502 | Generator NDE Bearing High Temperature Alarm | BD | 4:16 | 5:10 | 5:12 | 0.9 | 0.033333 | 0.93333 | Reboot then restore wtg. | Close | 0.023932 | G04 | 644.9333 | None | WTG Breakdown Maintenance | 16584 | 644.9333
326 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | Year_3 | G02 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop | 13:22 | 13:22 | 14:35 | 0 | 1.2167 | 1.2167 | check related circuit found generator earthing brush wear out then replace it then restore wtg. | Close | 0.031197 | G04 | 840.7167 | None | WTG Unscheduled Maintenance | 16584 | 840.7167
327 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | Year_3 | G07 | PWEGPL | MSEDCL | 2.564% | 403 | High Gearbox Oil Temperature | BD | 3:25 | 4:02 | 4:05 | 0.61667 | 0.05 | 0.66667 | Reboot then restore wtg. | Close | 0.017094 | G01 | 420.9167 | None | WTG Breakdown Maintenance | 15153 | 420.9167
328 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | Year_3 | G07 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop | 11:19 | 11:19 | 13:06 | 0 | 1.7833 | 1.7833 | Check related circuit found MPCB tripped so correct it then check motor found ok then check connection then restore wtg. | Close | 0.045726 | G01 | 1125.9521 | None | WTG Unscheduled Maintenance | 15153 | 1125.9521
329 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | Year_3 | G09 | PWEGPL | MSEDCL | 2.564% | 416 | Vibration Sensor | BD | 7:45 | 9:25 | 9:26 | 1.6667 | 0.016667 | 1.6833 | Reset then restore wtg. | Close | 0.043162 | G12 | 1046.6826 | None | WTG Breakdown Maintenance | 14923 | 1046.6826
330 | 2025-04-17 | 2025 | 2025 | 2025-04-01 | Year_3 | G39 | PWEGPL | MSEDCL | 2.564% | 5200 | Magnetothermic Trigger Of The Line Protection | BD | 8:45 | 9:48 | 9:50 | 1.05 | 0.033333 | 1.0833 | Reboot then restore wtg. | Close | 0.027778 | G40 | 567.5764 | None | WTG Breakdown Maintenance | 12574 | 567.5764
331 | 2025-04-18 | 2025 | 2025 | 2025-04-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 8817.8722 | None | WTG Force Majeaure | 8824 | 8817.8722
332 | 2025-04-18 | 2025 | 2025 | 2025-04-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 8817.8722 | None | WTG Force Majeaure | 8824 | 8817.8722
333 | 2025-04-18 | 2025 | 2025 | 2025-04-01 | Year_3 | G23 | PWEGPL | MSEDCL | 2.564% | 2106 | Temp. Measurement Module Failure | BD | 9:35 | 9:35 | 9:40 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G22 | 30.7569 | None | WTG Breakdown Maintenance | 8858 | 30.7569
334 | 2025-04-18 | 2025 | 2025 | 2025-04-01 | Year_3 | G23 | PWEGPL | MSEDCL | 2.564% | 2106 | Temp. Measurement Module Failure | BD | 10:12 | 10:12 | 10:17 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G22 | 30.7569 | None | WTG Breakdown Maintenance | 8858 | 30.7569
335 | 2025-04-18 | 2025 | 2025 | 2025-04-01 | Year_3 | G23 | PWEGPL | MSEDCL | 2.564% | 2106 | Temp. Measurement Module Failure | BD | 12:15 | 12:32 | 12:35 | 0.28333 | 0.05 | 0.33333 | Reboot then restore wtg. | Close | 0.008547 | G22 | 123.0278 | None | WTG Breakdown Maintenance | 8858 | 123.0278
336 | 2025-04-18 | 2025 | 2025 | 2025-04-01 | Year_3 | G30 | PWEGPL | MSEDCL | 2.564% | 426 | Rotor Speed Reading Failure | BD | 11:05 | 11:05 | 11:54 | 0 | 0.81667 | 0.81667 | check related circuit found rotor sensor connection loose so tight it | Close | 0.02094 | G28 | 300.2611 | None | WTG Breakdown Maintenance | 8824 | 300.2611
337 | 2025-04-18 | 2025 | 2025 | 2025-04-01 | Year_3 | G36 | PWEGPL | MSEDCL | 2.564% | 800 | Pitch Drive Error | BD | 9:45 | 11:55 | 15:05 | 2.1667 | 3.1667 | 5.3333 | Check related circuit found proportion valve cable connector loose so tight it then restore wtg. | Close | 0.13675 | G35 | 1769.5556 | None | WTG Breakdown Maintenance | 7963 | 1769.5556
338 | 2025-04-18 | 2025 | 2025 | 2025-04-01 | Year_3 | G35 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD | 16:48 | 17:35 | 17:38 | 0.78333 | 0.05 | 0.83333 | Reset then restore wtg. | Close | 0.021368 | G33 | 283.6458 | None | WTG Breakdown Maintenance | 8169 | 283.6458
339 | 2025-04-18 | 2025 | 2025 | 2025-04-01 | Year_3 | G23 | PWEGPL | MSEDCL | 2.564% | 2106 | Temp. Measurement Module Failure | BD | 16:20 | 16:45 | 17:47 | 0.41667 | 1.0333 | 1.45 | Checked related circuit found Sensor ok then replaced module | Close | 0.037179 | G22 | 533.1167 | None | WTG Breakdown Maintenance | 8824 | 533.1167
340 | 2025-04-19 | 2025 | 2025 | 2025-04-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 10559.6618 | None | WTG Force Majeaure | 10567 | 10559.6618
341 | 2025-04-19 | 2025 | 2025 | 2025-04-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 10559.6618 | None | WTG Force Majeaure | 10567 | 10559.6618
342 | 2025-04-19 | 2025 | 2025 | 2025-04-01 | Year_3 | G13 | PWEGPL | MSEDCL | 2.564% | 5210 | Failure Of The Contactor's Rotor Power | BD | 14:58 | 15:15 | 15:18 | 0.28333 | 0.05 | 0.33333 | Reboot then restore wtg. | Close | 0.008547 | G14 | 158.0278 | None | WTG Breakdown Maintenance | 11378 | 158.0278
343 | 2025-04-19 | 2025 | 2025 | 2025-04-01 | Year_3 | G23 | PWEGPL | MSEDCL | 2.564% | CE100008 | General Work Stoppage | Manual stop | 11:15 | 11:15 | 18:03 | 0 | 6.8 | 6.8 | Manual stop for Blade A pitch seal replacement work | Close | 0.17436 | G05 | 3000.5 | None | WTG Unscheduled Maintenance | 10590 | 3000.5
344 | 2025-04-19 | 2025 | 2025 | 2025-04-01 | Year_3 | G33 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 14:37 | 15:13 | 16:10 | 0.6 | 0.95 | 1.55 | Check related circuit found loose connection so tight it then restore wtg. | Close | 0.039744 | G34 | 664.5625 | None | WTG Breakdown Maintenance | 10290 | 664.5625
345 | 2025-04-20 | 2025 | 2025 | 2025-04-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 20848.5118 | None | WTG Force Majeaure | 20863 | 20848.5118
346 | 2025-04-20 | 2025 | 2025 | 2025-04-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 20848.5118 | None | WTG Force Majeaure | 20863 | 20848.5118
347 | 2025-04-20 | 2025 | 2025 | 2025-04-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | 719 | Cup Anemometer Failure Warning | BD | 11:30 | 12:12 | 12:13 | 0.7 | 0.016667 | 0.71667 | Reset then restore wtg. | Close | 0.018376 | G03 | 606.8076 | None | WTG Breakdown Maintenance | 20321 | 606.8076
348 | 2025-04-20 | 2025 | 2025 | 2025-04-01 | Year_3 | G13 | PWEGPL | MSEDCL | 2.564% | 500 | High Generator Winding Temperature | BD | 4:05 | 4:05 | 4:10 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G14 | 73.5347 | None | WTG Breakdown Maintenance | 21178 | 73.5347
349 | 2025-04-20 | 2025 | 2025 | 2025-04-01 | Year_3 | G13 | PWEGPL | MSEDCL | 2.564% | 500 | High Generator Winding Temperature | BD | 5:34 | 5:34 | 5:39 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G14 | 73.5347 | None | WTG Breakdown Maintenance | 21178 | 73.5347
350 | 2025-04-20 | 2025 | 2025 | 2025-04-01 | Year_3 | G13 | PWEGPL | MSEDCL | 2.564% | 500 | High Generator Winding Temperature | BD | 6:45 | 6:45 | 6:50 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G14 | 73.5347 | None | WTG Breakdown Maintenance | 21178 | 73.5347
351 | 2025-04-20 | 2025 | 2025 | 2025-04-01 | Year_3 | G13 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop | 11:25 | 11:25 | 15:23 | 0 | 3.9667 | 3.9667 | Manual stop for generator cooling motor inspection and rectification work | Close | 0.10171 | G14 | 3500.2528 | None | WTG Unscheduled Maintenance | 21178 | 3500.2528
352 | 2025-04-20 | 2025 | 2025 | 2025-04-01 | Year_3 | G22 | PWEGPL | MSEDCL | 2.564% | 813 | Low Pressure Of Emergency Accumulators | BD | 16:24 | 16:52 | 16:54 | 0.46667 | 0.033333 | 0.5 | Reset then restore wtg. | Close | 0.012821 | G05 | 434.9167 | None | WTG Breakdown Maintenance | 20876 | 434.9167
353 | 2025-04-21 | 2025 | 2025 | 2025-04-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 8028.4208 | None | WTG Force Majeaure | 8034 | 8028.4208
354 | 2025-04-21 | 2025 | 2025 | 2025-04-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 8028.4208 | None | WTG Force Majeaure | 8034 | 8028.4208
355 | 2025-04-21 | 2025 | 2025 | 2025-04-01 | Year_3 | G16 | PWEGPL | MSEDCL | 2.564% | CE100008 | General Work Stoppage | Manual stop | 15:52 | 15:52 | 17:30 | 0 | 1.6333 | 1.6333 | Manual stop for Slipring carbon brush & spring replacement and power set to 2000kw max. | Close | 0.04188 | G17 | 527.3625 | None | WTG Unscheduled Maintenance | 7749 | 527.3625
356 | 2025-04-21 | 2025 | 2025 | 2025-04-01 | Year_3 | G32 | PWEGPL | MSEDCL | 2.564% | 1824 | Trafo Fan Thermal Relay | BD | 13:53 | 14:35 | 14:36 | 0.7 | 0.016667 | 0.71667 | Reset then restore wtg. | Close | 0.018376 | G26 | 247.3694 | None | WTG Breakdown Maintenance | 8284 | 247.3694
357 | 2025-04-21 | 2025 | 2025 | 2025-04-01 | Year_3 | G26 | PWEGPL | MSEDCL | 2.564% | 1824 | Trafo Fan Thermal Relay | BD | 13:32 | 14:42 | 14:43 | 1.1667 | 0.016667 | 1.1833 | Reset then restore wtg. | Close | 0.030342 | G40 | 407.116 | None | WTG Breakdown Maintenance | 8257 | 407.116
358 | 2025-04-21 | 2025 | 2025 | 2025-04-01 | Year_3 | G40 | PWEGPL | MSEDCL | 2.564% | 1824 | Trafo Fan Thermal Relay | BD | 14:05 | 14:51 | 14:52 | 0.76667 | 0.016667 | 0.78333 | Reset then restore wtg. | Close | 0.020085 | G39 | 276.2229 | None | WTG Breakdown Maintenance | 8463 | 276.2229
359 | 2025-04-22 | 2025 | 2025 | 2025-04-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 6327.6028 | None | WTG Force Majeaure | 6332 | 6327.6028
360 | 2025-04-22 | 2025 | 2025 | 2025-04-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 6327.6028 | None | WTG Force Majeaure | 6332 | 6327.6028
361 | 2025-04-22 | 2025 | 2025 | 2025-04-01 | Year_3 | G06 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 7:14 | 8:01 | 8:03 | 0.78333 | 0.033333 | 0.81667 | Reboot then restore wtg. | Close | 0.02094 | G03 | 148.5993 | None | WTG Breakdown Maintenance | 4367 | 148.5993
362 | 2025-04-22 | 2025 | 2025 | 2025-04-01 | Year_3 | G06 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 14:10 | 14:43 | 14:45 | 0.55 | 0.033333 | 0.58333 | Reboot then restore wtg. | Close | 0.014957 | G03 | 106.1424 | None | WTG Breakdown Maintenance | 4367 | 106.1424
363 | 2025-04-22 | 2025 | 2025 | 2025-04-01 | Year_3 | G13 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop | 10:38 | 10:38 | 12:22 | 0 | 1.7333 | 1.7333 | Manual stop for CCU motor replaced then restore wtg. | Close | 0.044444 | G14 | 458.0333 | None | WTG Unscheduled Maintenance | 6342 | 458.0333
364 | 2025-04-22 | 2025 | 2025 | 2025-04-01 | Year_3 | G32 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop | 11:06 | 11:06 | 16:14 | 0 | 5.1333 | 5.1333 | Manual stop for transformer fan replacement work | Close | 0.13162 | G26 | 1379.5833 | None | WTG Unscheduled Maintenance | 6450 | 1379.5833
365 | 2025-04-22 | 2025 | 2025 | 2025-04-01 | Year_3 | G33 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 17:10 | 17:45 | 17:50 | 0.58333 | 0.083333 | 0.66667 | Reboot then restore wtg. | Close | 0.017094 | G34 | 180.1944 | None | WTG Breakdown Maintenance | 6487 | 180.1944
366 | 2025-04-23 | 2025 | 2025 | 2025-04-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 3175.7931 | None | WTG Force Majeaure | 3178 | 3175.7931
367 | 2025-04-23 | 2025 | 2025 | 2025-04-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 3175.7931 | None | WTG Force Majeaure | 3178 | 3175.7931
368 | 2025-04-23 | 2025 | 2025 | 2025-04-01 | Year_3 | G19 | PWEGPL | MSEDCL | 2.564% | 118 | Yaw Motors Error | BD | 18:15 | 18:49 | 18:50 | 0.56667 | 0.016667 | 0.58333 | Reset then restore wtg. | Close | 0.014957 | G18 | 96.1771 | None | WTG Breakdown Maintenance | 3957 | 96.1771
369 | 2025-04-23 | 2025 | 2025 | 2025-04-01 | Year_3 | G22 | PWEGPL | MSEDCL | 2.564% | 813 | Low Pressure Of Emergency Accumulators | BD | 18:02 | 18:55 | 18:56 | 0.88333 | 0.016667 | 0.9 | Reset then restore wtg. | Close | 0.023077 | G05 | 118.2375 | None | WTG Breakdown Maintenance | 3153 | 118.2375
370 | 2025-04-23 | 2025 | 2025 | 2025-04-01 | Year_3 | G25 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop | 10:55 | 10:55 | 16:30 | 0 | 5.5833 | 5.5833 | Manual stop for transformer fan replacement work | Close | 0.14316 | G27 | 734.441 | None | WTG Unscheduled Maintenance | 3157 | 734.441
371 | 2025-04-23 | 2025 | 2025 | 2025-04-01 | Year_3 | G32 | PWEGPL | MSEDCL | 2.564% | 525 | High Ambient Temperature In The Converter | BD | 16:18 | 17:01 | 17:03 | 0.71667 | 0.033333 | 0.75 | Reboot then restore wtg. | Close | 0.019231 | G26 | 96.9375 | None | WTG Breakdown Maintenance | 3102 | 96.9375
372 | 2025-04-24 | 2025 | 2025 | 2025-04-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 5480.1917 | None | WTG Force Majeaure | 5484 | 5480.1917
373 | 2025-04-24 | 2025 | 2025 | 2025-04-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 5480.1917 | None | WTG Force Majeaure | 5484 | 5480.1917
374 | 2025-04-24 | 2025 | 2025 | 2025-04-01 | Year_3 | G01 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 17:23 | 18:25 | 18:27 | 1.0333 | 0.033333 | 1.0667 | Reboot then restore wtg. | Close | 0.02735 | G07 | 234.0889 | None | WTG Breakdown Maintenance | 5267 | 234.0889
375 | 2025-04-24 | 2025 | 2025 | 2025-04-01 | Year_3 | G22 | PWEGPL | MSEDCL | 2.564% | 813 | Low Pressure Of Emergency Accumulators | BD | 17:48 | 18:23 | 18:25 | 0.58333 | 0.033333 | 0.61667 | Reset then restore wtg. | Close | 0.015812 | G05 | 139.341 | None | WTG Breakdown Maintenance | 5423 | 139.341
376 | 2025-04-24 | 2025 | 2025 | 2025-04-01 | Year_3 | G26 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop | 11:50 | 11:50 | 16:18 | 0 | 4.4667 | 4.4667 | Manual stop for transformer fan replacement work | Close | 0.11453 | G32 | 1332.1833 | None | WTG Unscheduled Maintenance | 7158 | 1332.1833
377 | 2025-04-24 | 2025 | 2025 | 2025-04-01 | Year_3 | G39 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 15:00 | 15:00 | 17:07 | 0 | 2.1167 | 2.1167 | Manual stop for Blade bush gap inspection work | Close | 0.054274 | G38 | 631.1194 | None | IG Force Majeaure | 7156 | 631.1194
378 | 2025-04-24 | 2025 | 2025 | 2025-04-01 | Year_3 | G40 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop | 11:40 | 11:40 | 16:20 | 0 | 4.6667 | 4.6667 | Manual stop for transformer fan replacement work | Close | 0.11966 | G38 | 1391.4444 | None | WTG Unscheduled Maintenance | 7156 | 1391.4444
379 | 2025-04-25 | 2025 | 2025 | 2025-04-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 6539.4556 | None | WTG Force Majeaure | 6544 | 6539.4556
380 | 2025-04-25 | 2025 | 2025 | 2025-04-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 6539.4556 | None | WTG Force Majeaure | 6544 | 6539.4556
381 | 2025-04-25 | 2025 | 2025 | 2025-04-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 14:28 | 15:10 | 15:12 | 0.7 | 0.033333 | 0.73333 | Reset then restore wtg. | Close | 0.018803 | G03 | 215.1417 | None | WTG Breakdown Maintenance | 7041 | 215.1417
382 | 2025-04-25 | 2025 | 2025 | 2025-04-01 | Year_3 | G08 | PWEGPL | MSEDCL | 2.564% | CE100008 | General Work Stoppage | Manual stop | 18:40 | 18:40 | 19:30 | 0 | 0.83333 | 0.83333 | Manual stop for generator temp. Apply grease and connections checking | Close | 0.021368 | G03 | 244.4792 | None | WTG Unscheduled Maintenance | 7041 | 244.4792
383 | 2025-04-25 | 2025 | 2025 | 2025-04-01 | Year_3 | G09 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD | 9:40 | 10:32 | 10:33 | 0.86667 | 0.016667 | 0.88333 | Reset then restore wtg. | Close | 0.02265 | G12 | 223.1521 | None | WTG Breakdown Maintenance | 6063 | 223.1521
384 | 2025-04-25 | 2025 | 2025 | 2025-04-01 | Year_3 | G12 | PWEGPL | MSEDCL | 2.564% | 2119 | CTRL Error - Processor Stopped | BD | 9:25 | 10:32 | 11:45 | 1.1167 | 1.2167 | 2.3333 | Check and found PLC card failure so replaced card then update softwear then restore wtg. | Close | 0.059829 | G09 | 586.4444 | None | WTG Breakdown Maintenance | 6032 | 586.4444
385 | 2025-04-25 | 2025 | 2025 | 2025-04-01 | Year_3 | G22 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop | 13:38 | 13:38 | 15:02 | 0 | 1.4 | 1.4 | Manual stop for repeted error found pressure switch loose connection so tight it then restore wtg. | Close | 0.035897 | G05 | 384.2417 | None | WTG Unscheduled Maintenance | 6587 | 384.2417
386 | 2025-04-25 | 2025 | 2025 | 2025-04-01 | Year_3 | G34 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 14:50 | 14:50 | 16:45 | 0 | 1.9167 | 1.9167 | Manual stop for Blade bush gap inspection work | Close | 0.049145 | G33 | 546.4097 | None | IG Force Majeaure | 6842 | 546.4097
387 | 2025-04-25 | 2025 | 2025 | 2025-04-01 | Year_3 | G39 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop | 11:33 | 11:33 | 18:35 | 0 | 7.0333 | 7.0333 | Manual stop for Blade B pitch seal replacement work | Close | 0.18034 | G40 | 2007.1375 | None | WTG Unscheduled Maintenance | 6849 | 2007.1375
388 | 2025-04-25 | 2025 | 2025 | 2025-04-01 | Year_3 | G19 | PWEGPL | MSEDCL | 2.564% | 110 | Yaw Sensor Wiring Error | BD | 6:20 | 6:54 | 7:35 | 0.56667 | 0.68333 | 1.25 | Check and found yaw encoder failure so replaced with new one then restore wtg. | Close | 0.032051 | G18 | 330.4687 | None | WTG Breakdown Maintenance | 6345 | 330.4687
389 | 2025-04-26 | 2025 | 2025 | 2025-04-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 8832.8618 | None | WTG Force Majeaure | 8839 | 8832.8618
390 | 2025-04-26 | 2025 | 2025 | 2025-04-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 8832.8618 | None | WTG Force Majeaure | 8839 | 8832.8618
391 | 2025-04-26 | 2025 | 2025 | 2025-04-01 | Year_3 | G06 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop | 11:05 | 11:05 | 14:25 | 0 | 3.3333 | 3.3333 | Manual stop for transformer fan replacement work | Close | 0.08547 | G03 | 1518.3333 | None | WTG Unscheduled Maintenance | 10932 | 1518.3333
392 | 2025-04-26 | 2025 | 2025 | 2025-04-01 | Year_3 | G21 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 11:15 | 11:15 | 14:10 | 0 | 2.9167 | 2.9167 | Manual stop for Blade bush gap inspection work | Close | 0.074786 | G22 | 1040.6424 | None | WTG Force Majeaure | 8563 | 1040.6424
393 | 2025-04-26 | 2025 | 2025 | 2025-04-01 | Year_3 | G22 | PWEGPL | MSEDCL | 2.564% | 500 | High Generator Winding Temperature | BD | 13:05 | 13:05 | 13:10 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G21 | 29.0382 | None | WTG Breakdown Maintenance | 8363 | 29.0382
394 | 2025-04-26 | 2025 | 2025 | 2025-04-01 | Year_3 | G22 | PWEGPL | MSEDCL | 2.564% | 500 | High Generator Winding Temperature | BD | 16:10 | 16:10 | 16:15 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G21 | 29.0382 | None | WTG Breakdown Maintenance | 8363 | 29.0382
395 | 2025-04-26 | 2025 | 2025 | 2025-04-01 | Year_3 | G25 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM | 11:55 | 11:55 | 19:20 | 0 | 7.4167 | 7.4167 | Manual stop for HYPM work | Close | 0.19017 | G27 | 2737.3681 | None | WTG Scheduled Maintenance | 8858 | 2737.3681
396 | 2025-04-26 | 2025 | 2025 | 2025-04-01 | Year_3 | G36 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 16:10 | 16:47 | 16:49 | 0.61667 | 0.033333 | 0.65 | Reboot then restore wtg. | Close | 0.016667 | G35 | 253.0667 | None | WTG Breakdown Maintenance | 9344 | 253.0667
397 | 2025-04-27 | 2025 | 2025 | 2025-04-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 4863.6201 | None | WTG Force Majeaure | 4867 | 4863.6201
398 | 2025-04-27 | 2025 | 2025 | 2025-04-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 4863.6201 | None | WTG Force Majeaure | 4867 | 4863.6201
399 | 2025-04-27 | 2025 | 2025 | 2025-04-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD | 12:58 | 13:30 | 13:32 | 0.53333 | 0.033333 | 0.56667 | Reset then restore wtg. | Close | 0.01453 | G03 | 137.2278 | None | WTG Breakdown Maintenance | 5812 | 137.2278
400 | 2025-04-27 | 2025 | 2025 | 2025-04-01 | Year_3 | G07 | PWEGPL | MSEDCL | 2.564% | 410 | OGS | BD | 16:50 | 17:36 | 17:38 | 0.76667 | 0.033333 | 0.8 | OGS reset then restore wg. | Close | 0.020513 | G01 | 193.3667 | None | WTG Breakdown Maintenance | 5801 | 193.3667
401 | 2025-04-27 | 2025 | 2025 | 2025-04-01 | Year_3 | G14 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 15:32 | 16:10 | 17:02 | 0.63333 | 0.86667 | 1.5 | Slip ring clean then restore wtg. | Close | 0.038462 | G15 | 352.625 | None | WTG Breakdown Maintenance | 5642 | 352.625
402 | 2025-04-27 | 2025 | 2025 | 2025-04-01 | Year_3 | G27 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM | 11:16 | 11:16 | 17:50 | 0 | 6.5667 | 6.5667 | HYPM done then restore wtg. | Close | 0.16838 | G25 | 1328.1083 | None | WTG Scheduled Maintenance | 4854 | 1328.1083
403 | 2025-04-27 | 2025 | 2025 | 2025-04-01 | Year_3 | G36 | PWEGPL | MSEDCL | 2.564% | 5210 | Failure Of The Contactor's Rotor Power | BD | 7:10 | 8:06 | 8:08 | 0.93333 | 0.033333 | 0.96667 | Reset then restore wtg. | Close | 0.024786 | G35 | 183.5056 | None | WTG Breakdown Maintenance | 4556 | 183.5056
404 | 2025-04-27 | 2025 | 2025 | 2025-04-01 | Year_3 | G40 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 11:02 | 11:02 | 14:20 | 0 | 3.3 | 3.3 | Manual stop for Blade bush gap inspection work | Close | 0.084615 | G39 | 627.9625 | None | WTG Force Majeaure | 4567 | 627.9625
405 | 2025-04-27 | 2025 | 2025 | 2025-04-01 | Year_3 | G22 | PWEGPL | MSEDCL | 2.564% | 800 | Pitch Drive Error | BD | 17:05 | 18:45 | 18:48 | 1.6667 | 0.05 | 1.7167 | Reboot then restore wtg. | Close | 0.044017 | G21 | 346.5521 | None | WTG Breakdown Maintenance | 4845 | 346.5521
406 | 2025-04-28 | 2025 | 2025 | 2025-04-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 6649.3792 | None | WTG Force Majeaure | 6654 | 6649.3792
407 | 2025-04-28 | 2025 | 2025 | 2025-04-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 6649.3792 | None | WTG Force Majeaure | 6654 | 6649.3792
408 | 2025-04-28 | 2025 | 2025 | 2025-04-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 11:02 | 11:02 | 14:25 | 0 | 3.3833 | 3.3833 | Manual stop for Blade bush gap inspection work | Close | 0.086752 | G03 | 1134.9674 | None | WTG Force Majeaure | 8051 | 1134.9674
409 | 2025-04-28 | 2025 | 2025 | 2025-04-01 | Year_3 | G20 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD | 12:04 | 12:38 | 15:39 | 0.56667 | 3.0167 | 3.5833 | Check related circuit found Hub main accumulator failure so replaced with new one then restore wtg. | Close | 0.09188 | G19 | 1172.4965 | None | WTG Breakdown Maintenance | 7853 | 1172.4965
410 | 2025-04-28 | 2025 | 2025 | 2025-04-01 | Year_3 | G30 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | PM | 11:15 | 11:15 | 17:05 | 0 | 5.8333 | 5.8333 | HYPM done then restore wtg. | Close | 0.14957 | G28 | 1617.2917 | None | WTG Scheduled Maintenance | 6654 | 1617.2917
411 | 2025-04-28 | 2025 | 2025 | 2025-04-01 | Year_3 | G36 | PWEGPL | MSEDCL | 2.564% | 110 | Yaw Sensor Wiring Error | BD | 15:05 | 15:42 | 15:43 | 0.61667 | 0.016667 | 0.63333 | Reset then restore wtg. | Close | 0.016239 | G35 | 186.3583 | None | WTG Breakdown Maintenance | 7062 | 186.3583
412 | 2025-04-29 | 2025 | 2025 | 2025-04-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 5563.134 | None | WTG Force Majeaure | 5567 | 5563.134
413 | 2025-04-29 | 2025 | 2025 | 2025-04-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 5563.134 | None | WTG Force Majeaure | 5567 | 5563.134
414 | 2025-04-29 | 2025 | 2025 | 2025-04-01 | Year_3 | G07 | PWEGPL | MSEDCL | 2.564% | 410 | OGS | BD | 15:20 | 16:07 | 16:30 | 0.78333 | 0.38333 | 1.1667 | Check OGS sensor Replaced OGS guard then restore wtg. | Close | 0.029915 | G01 | 313.9792 | None | WTG Breakdown Maintenance | 6459 | 313.9792
415 | 2025-04-29 | 2025 | 2025 | 2025-04-01 | Year_3 | G22 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD | 9:10 | 10:12 | 17:09 | 1.0333 | 6.95 | 7.9833 | Check related circuit found hub main accumulator failure so replaced accumulator then found gear box oil leakage from hose so replaced GB hose then restore wtg. | Close | 0.2047 | G05 | 2242.6514 | None | WTG Breakdown Maintenance | 6742 | 2242.6514
416 | 2025-04-29 | 2025 | 2025 | 2025-04-01 | Year_3 | G28 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | PM | 8:12 | 8:12 | 14:45 | 0 | 6.55 | 6.55 | HYPM done then restore wtg. | Close | 0.16795 | G30 | 1853.65 | None | WTG Scheduled Maintenance | 6792 | 1853.65
417 | 2025-04-30 | 2025 | 2025 | 2025-04-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 12773.1236 | None | WTG Force Majeaure | 12782 | 12773.1236
418 | 2025-04-30 | 2025 | 2025 | 2025-04-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 12773.1236 | None | WTG Force Majeaure | 12782 | 12773.1236
419 | 2025-04-30 | 2025 | 2025 | 2025-04-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD | 6:21 | 8:01 | 15:32 | 1.6667 | 7.5167 | 9.1833 | Check related circuit found HU pressure drop continuous so check HU pump then check NRV valve then replaced RV 8-10 & Break Valve restore wtg. | Close | 0.23547 | G03 | 6138.2931 | None | WTG Breakdown Maintenance | 16042 | 6138.2931
420 | 2025-04-30 | 2025 | 2025 | 2025-04-01 | Year_3 | G11 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 7:09 | 8:10 | 8:12 | 1.0167 | 0.033333 | 1.05 | Reboot then restore wtg. | Close | 0.026923 | G10 | 703.4563 | None | WTG Breakdown Maintenance | 16079 | 703.4563
421 | 2025-04-30 | 2025 | 2025 | 2025-04-01 | Year_3 | G22 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 8:20 | 12:07 | 12:10 | 3.7833 | 0.05 | 3.8333 | Reboot then restore wtg. | Close | 0.098291 | G05 | 2463.7153 | None | WTG Breakdown Maintenance | 15425 | 2463.7153
422 | 2025-04-30 | 2025 | 2025 | 2025-04-01 | Year_3 | G22 | PWEGPL | MSEDCL | 2.564% | 500 | High Generator Winding Temperature | BD | 14:10 | 14:35 | 15:21 | 0.41667 | 0.76667 | 1.1833 | Check related circuit found single winding temp. high so check sensor then used spare sensor then restore wtg. | Close | 0.030342 | G05 | 760.5382 | None | WTG Breakdown Maintenance | 15425 | 760.5382
423 | 2025-04-30 | 2025 | 2025 | 2025-04-01 | Year_3 | G23 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 14:07 | 15:45 | 15:47 | 1.6333 | 0.033333 | 1.6667 | Reboot then restore wtg. | Close | 0.042735 | G05 | 1071.1806 | None | WTG Breakdown Maintenance | 15425 | 1071.1806
424 | 2025-04-30 | 2025 | 2025 | 2025-04-01 | Year_3 | G28 | PWEGPL | MSEDCL | 2.564% | 5212 | Bus Preload Protection Thermal Relay Failure | BD | 6:40 | 10:12 | 12:32 | 3.5333 | 2.3333 | 5.8667 | Check related circuit found MPCB tripped so correct it then restore wtg. | Close | 0.15043 | G30 | 3781.3111 | None | WTG Breakdown Maintenance | 15469 | 3781.3111
425 | 2025-04-30 | 2025 | 2025 | 2025-04-01 | Year_3 | G34 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | PM | 12:40 | 12:40 | 18:30 | 0 | 5.8333 | 5.8333 | HYPM done then restore wtg. | Close | 0.14957 | G33 | 3877.7083 | None | WTG Scheduled Maintenance | 15954 | 3877.7083
426 | 2025-05-01 | 2025 | 2025 | 2025-05-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 15515.2181 | None | WTG Force Majeaure | 15526 | 15515.2181
427 | 2025-05-01 | 2025 | 2025 | 2025-05-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 15515.2181 | None | WTG Force Majeaure | 15526 | 15515.2181
428 | 2025-05-01 | 2025 | 2025 | 2025-05-01 | Year_3 | G16 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD | 8:20 | 9:15 | 9:16 | 0.91667 | 0.016667 | 0.93333 | Reset then restore wtg. | Close | 0.023932 | G17 | 642.7944 | None | WTG Breakdown Maintenance | 16529 | 642.7944
429 | 2025-05-01 | 2025 | 2025 | 2025-05-01 | Year_3 | G22 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 8:32 | 9:45 | 12:40 | 1.2167 | 2.9167 | 4.1333 | Check related circuit found loose connection so tigh it then restore wtg. | Close | 0.10598 | G05 | 2604.1722 | None | WTG Breakdown Maintenance | 15121 | 2604.1722
430 | 2025-05-01 | 2025 | 2025 | 2025-05-01 | Year_3 | G22 | PWEGPL | MSEDCL | 2.564% | 208 | HU Pump Drive Failure | BD | 13:10 | 13:11 | 14:20 | 0.016667 | 1.15 | 1.1667 | Checked related circuit found HU contactor failure so replaced with new one then restore wtg. | Close | 0.029915 | G05 | 735.0486 | None | WTG Breakdown Maintenance | 15121 | 735.0486
431 | 2025-05-01 | 2025 | 2025 | 2025-05-01 | Year_3 | G22 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD | 15:12 | 15:13 | 16:05 | 0.016667 | 0.86667 | 0.88333 | Checked related circuit found relay malfuction so interchage reley then restore wtg. | Close | 0.02265 | G05 | 556.5368 | None | WTG Breakdown Maintenance | 15121 | 556.5368
432 | 2025-05-01 | 2025 | 2025 | 2025-05-01 | Year_3 | G30 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 14:25 | 14:25 | 17:07 | 0 | 2.7 | 2.7 | Manual stop for Blade bush gap inspection work | Close | 0.069231 | G28 | 1746.675 | None | WTG Force Majeaure | 15526 | 1746.675
433 | 2025-05-01 | 2025 | 2025 | 2025-05-01 | Year_3 | G33 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM | 11:21 | 11:21 | 17:25 | 0 | 6.0667 | 6.0667 | HYPM done then restore wtg. | Close | 0.15556 | G34 | 3926.9028 | None | WTG Scheduled Maintenance | 15535 | 3926.9028
434 | 2025-05-01 | 2025 | 2025 | 2025-05-01 | Year_3 | G07 | PWEGPL | MSEDCL | 2.564% | CE100008 | General Work Stoppage | Manual stop | 8:21 | 8:21 | 13:32 | 0 | 5.1833 | 5.1833 | Manual stop for oil leakage inspection work. Found oil leakage from Blade C so replaced pitch seal then restore wtg. | Close | 0.13291 | G01 | 3632.8688 | None | WTG Unscheduled Maintenance | 16821 | 3632.8688
435 | 2025-05-02 | 2025 | 2025 | 2025-05-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 12835.0806 | None | WTG Force Majeaure | 12844 | 12835.0806
436 | 2025-05-02 | 2025 | 2025 | 2025-05-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 12835.0806 | None | WTG Force Majeaure | 12844 | 12835.0806
437 | 2025-05-02 | 2025 | 2025 | 2025-05-01 | Year_3 | G07 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD | 4:30 | 8:25 | 15:02 | 3.9167 | 6.6167 | 10.5333 | Check related circuit found oil leakage from Blade B. So replaced pitch seal then top-up 15 liter oil then restore wtg. | Close | 0.27009 | G01 | 5956.6806 | None | WTG Unscheduled Maintenance | 14789 | 6490.7278
438 | 2025-05-02 | 2025 | 2025 | 2025-05-01 | Year_3 | G18 | PWEGPL | MSEDCL | 2.564% | 5236 | Error In Phase R Of The Inverter | BD | 9:10 | 9:32 | 15:21 | 0.36667 | 5.8167 | 6.1833 | Checked related circuit found carbon brush spring and holder failure so replaced with new one then restore wtg. | Close | 0.15855 | G19 | 3810.2215 | None | WTG Breakdown Maintenance | 14789 | 3810.2215
439 | 2025-05-02 | 2025 | 2025 | 2025-05-01 | Year_3 | G22 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD | 16:05 | 16:05 | 16:10 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | G05 | 50.4792 | None | WTG Breakdown Maintenance | 14538 | 50.4792
440 | 2025-05-02 | 2025 | 2025 | 2025-05-01 | Year_3 | G27 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 11:54 | 11:54 | 15:24 | 0 | 3.5 | 3.5 | Manual stop for Blade bush gap inspection work | Close | 0.089744 | G25 | 1879.6458 | None | WTG Breakdown Maintenance | 12889 | 1879.6458
441 | 2025-05-02 | 2025 | 2025 | 2025-05-01 | Year_3 | G32 | PWEGPL | MSEDCL | 2.564% | 119 | Yaw Contactor Active | BD | 15:56 | 16:35 | 16:37 | 0.65 | 0.033333 | 0.68333 | Reboot then restore wtg. | Close | 0.017521 | G26 | 336.9403 | None | WTG Breakdown Maintenance | 11834 | 336.9403
442 | 2025-05-03 | 2025 | 2025 | 2025-05-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 16550.4986 | None | WTG Force Majeaure | 16562 | 16550.4986
443 | 2025-05-03 | 2025 | 2025 | 2025-05-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 16550.4986 | None | WTG Force Majeaure | 16562 | 16550.4986
444 | 2025-05-03 | 2025 | 2025 | 2025-05-01 | Year_3 | G09 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD | 15:10 | 15:35 | 15:36 | 0.41667 | 0.016667 | 0.43333 | Reset then restore wtg. | Close | 0.011111 | G12 | 320.0708 | None | WTG Breakdown Maintenance | 17727 | 320.0708
445 | 2025-05-03 | 2025 | 2025 | 2025-05-01 | Year_3 | G12 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD | 14:42 | 15:02 | 15:03 | 0.33333 | 0.016667 | 0.35 | Reset then restore wtg. | Close | 0.0089744 | G13 | 265.9854 | None | WTG Breakdown Maintenance | 18239 | 265.9854
446 | 2025-05-03 | 2025 | 2025 | 2025-05-01 | Year_3 | G19 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop | 8:30 | 8:30 | 13:21 | 0 | 4.85 | 4.85 | Manual stop for oil leakage inspection & rectification found oil leak for Blade B pitch seal so replaced pith seal then restore wtg. | Close | 0.12436 | G18 | 3684.7875 | None | WTG Unscheduled Maintenance | 18234 | 3684.7875
447 | 2025-05-03 | 2025 | 2025 | 2025-05-01 | Year_3 | G32 | PWEGPL | MSEDCL | 2.564% | 102 | CW Feedback Failure | BD | 9:45 | 10:20 | 10:21 | 0.58333 | 0.016667 | 0.6 | Reset then restore wtg. | Close | 0.015385 | G26 | 371.125 | None | WTG Breakdown Maintenance | 14845 | 371.125
448 | 2025-05-03 | 2025 | 2025 | 2025-05-01 | Year_3 | G35 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM | 11:21 | 11:21 | 17:25 | 0 | 6.0667 | 6.0667 | HYPM done then checked blade bush gap inspection then restore wtg. | Close | 0.15556 | G36 | 3752.9917 | None | WTG Scheduled Maintenance | 14847 | 3752.9917
449 | 2025-05-03 | 2025 | 2025 | 2025-05-01 | Year_3 | G37 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 13:21 | 14:32 | 14:35 | 1.1833 | 0.05 | 1.2333 | Reboot then restore wtg. | Close | 0.031624 | G36 | 762.9708 | None | WTG Breakdown Maintenance | 14847 | 762.9708
450 | 2025-05-04 | 2025 | 2025 | 2025-05-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 11144.2556 | None | WTG Force Majeaure | 11152 | 11144.2556
451 | 2025-05-04 | 2025 | 2025 | 2025-05-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 11144.2556 | None | WTG Force Majeaure | 11152 | 11144.2556
452 | 2025-05-04 | 2025 | 2025 | 2025-05-01 | Year_3 | G12 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD | 13:56 | 14:20 | 14:21 | 0.4 | 0.016667 | 0.41667 | Reset then restore wtg. | Close | 0.010684 | G13 | 235.7292 | None | WTG Breakdown Maintenance | 13578 | 235.7292
453 | 2025-05-04 | 2025 | 2025 | 2025-05-01 | Year_3 | G22 | PWEGPL | MSEDCL | 2.564% | 813 | Low Pressure Of Emergency Accumulators | BD | 18:05 | 18:42 | 18:43 | 0.61667 | 0.016667 | 0.63333 | Reset then restore wtg. | Close | 0.016239 | G05 | 294.6847 | None | WTG Breakdown Maintenance | 11167 | 294.6847
454 | 2025-05-04 | 2025 | 2025 | 2025-05-01 | Year_3 | G26 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop | 10:45 | 10:45 | 23:59 | 0 | 13.2333 | 13.2333 | Manual stop for pitch seal replacement work (work in progress) | Open | 0.33932 | G32 | 4825.7556 | None | WTG Unscheduled Maintenance | 8752 | 4825.7556
455 | 2025-05-04 | 2025 | 2025 | 2025-05-01 | Year_3 | G36 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM | 10:35 | 10:35 | 17:10 | 0 | 6.5833 | 6.5833 | HYPM done then then restore wtg. | Close | 0.1688 | G37 | 2402.6424 | None | WTG Scheduled Maintenance | 8759 | 2402.6424
456 | 2025-05-05 | 2025 | 2025 | 2025-05-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 7750.6139 | None | WTG Force Majeaure | 7756 | 7750.6139
457 | 2025-05-05 | 2025 | 2025 | 2025-05-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 7750.6139 | None | WTG Force Majeaure | 7756 | 7750.6139
458 | 2025-05-05 | 2025 | 2025 | 2025-05-01 | Year_3 | G01 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop | 9:42 | 9:42 | 17:09 | 0 | 7.45 | 7.45 | Manual stop for Yaw caliper seal replacement work. | Close | 0.19103 | G07 | 2590.7375 | None | WTG Unscheduled Maintenance | 8346 | 2590.7375
459 | 2025-05-05 | 2025 | 2025 | 2025-05-01 | Year_3 | G05 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer | 17:01 | 17:01 | 18:05 | 0 | 1.0667 | 1.0667 | SEM meter Pole CT & PT installation work | Close | 0.02735 | G22 | 289.9556 | None | WTG Unscheduled Maintenance | 6524 | 289.9556
460 | 2025-05-05 | 2025 | 2025 | 2025-05-01 | Year_3 | G12 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD | 17:08 | 17:40 | 17:41 | 0.53333 | 0.016667 | 0.55 | Reset then restore wtg. | Close | 0.014103 | G09 | 189.9563 | None | WTG Breakdown Maintenance | 8289 | 189.9563
461 | 2025-05-05 | 2025 | 2025 | 2025-05-01 | Year_3 | G14 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 17:05 | 17:30 | 17:31 | 0.41667 | 0.016667 | 0.43333 | Reset then restore wtg. | Close | 0.011111 | G15 | 149.0667 | None | WTG Breakdown Maintenance | 8256 | 149.0667
462 | 2025-05-05 | 2025 | 2025 | 2025-05-01 | Year_3 | G21 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer | 12:00 | 12:00 | 12:24 | 0 | 0.4 | 0.4 | SEM meter Pole CT & PT installation work | Close | 0.010256 | G22 | 108.7333 | None | WTG Unscheduled Maintenance | 6524 | 108.7333
463 | 2025-05-05 | 2025 | 2025 | 2025-05-01 | Year_3 | G22 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer | 12:37 | 12:37 | 13:20 | 0 | 0.71667 | 0.71667 | SEM meter Pole CT & PT installation work | Close | 0.018376 | G05 | 194.0972 | None | WTG Unscheduled Maintenance | 6500 | 194.0972
464 | 2025-05-05 | 2025 | 2025 | 2025-05-01 | Year_3 | G26 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop | 0:00 | 0:00 | 23:59 | 0 | 23.9833 | 23.9833 | Manual stop for pitch seal replacement work (work in progress) | Open | 0.61496 | G32 | 5827.95 | None | WTG Breakdown Maintenance | 5832 | 5827.95
465 | 2025-05-05 | 2025 | 2025 | 2025-05-01 | Year_3 | G28 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 13:58 | 13:58 | 16:45 | 0 | 2.7833 | 2.7833 | Manual stop for Blade bush gap inspection work | Close | 0.071368 | G30 | 897.741 | None | WTG Force Majeaure | 7741 | 897.741
466 | 2025-05-06 | 2025 | 2025 | 2025-05-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 8370.1833 | None | WTG Force Majeaure | 8376 | 8370.1833
467 | 2025-05-06 | 2025 | 2025 | 2025-05-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 8370.1833 | None | WTG Force Majeaure | 8376 | 8370.1833
468 | 2025-05-06 | 2025 | 2025 | 2025-05-01 | Year_3 | G16 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD | 14:02 | 14:37 | 14:38 | 0.58333 | 0.016667 | 0.6 | Reset then restore wtg. | Close | 0.015385 | G17 | 241.1 | None | WTG Breakdown Maintenance | 9644 | 241.1
469 | 2025-05-06 | 2025 | 2025 | 2025-05-01 | Year_3 | G19 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD | 12:32 | 13:10 | 14:12 | 0.63333 | 1.0333 | 1.6667 | Check related circuit check all motor found ok then restore wtg. | Close | 0.042735 | G18 | 669.4444 | None | WTG Breakdown Maintenance | 9640 | 669.4444
470 | 2025-05-06 | 2025 | 2025 | 2025-05-01 | Year_3 | G22 | PWEGPL | MSEDCL | 2.564% | 813 | Low Pressure Of Emergency Accumulators | BD | 13:05 | 13:52 | 13:53 | 0.78333 | 0.016667 | 0.8 | Reset then restore wtg. | Close | 0.020513 | G05 | 276.7 | None | WTG Breakdown Maintenance | 8301 | 276.7
471 | 2025-05-06 | 2025 | 2025 | 2025-05-01 | Year_3 | G23 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 15:20 | 16:02 | 16:04 | 0.7 | 0.033333 | 0.73333 | Reboot then restore wtg. | Close | 0.018803 | G05 | 253.6417 | None | WTG Breakdown Maintenance | 8301 | 253.6417
472 | 2025-05-06 | 2025 | 2025 | 2025-05-01 | Year_3 | G26 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop | 0:00 | 0:00 | 15:43 | 0 | 15.7167 | 15.7167 | Replaced Blade B pitch cylinder then top up 22 liter HU oil then restore wtg. | Close | 0.40299 | G32 | 4565.6917 | None | WTG Unscheduled Maintenance | 6972 | 4565.6917
473 | 2025-05-06 | 2025 | 2025 | 2025-05-01 | Year_3 | G37 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM | 11:22 | 11:22 | 18:21 | 0 | 6.9833 | 6.9833 | HYPM done then checked blade bush gap inspection then restore wtg. | Close | 0.17906 | G36 | 2023.1299 | None | WTG Scheduled Maintenance | 6953 | 2023.1299
474 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 9446.4354 | None | WTG Force Majeaure | 9453 | 9446.4354
475 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 9446.4354 | None | WTG Force Majeaure | 9453 | 9446.4354
476 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | Year_3 | G01 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 15:53 | 16:35 | 16:37 | 0.7 | 0.033333 | 0.73333 | Reboot then restore wtg. | Close | 0.018803 | G07 | 335.775 | None | WTG Breakdown Maintenance | 10989 | 335.775
477 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | Year_3 | G06 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 15:53 | 16:30 | 16:32 | 0.61667 | 0.033333 | 0.65 | Reboot then restore wtg. | Close | 0.016667 | G03 | 343.7958 | None | WTG Breakdown Maintenance | 12694 | 343.7958
478 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | Year_3 | G07 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 15:54 | 16:45 | 16:47 | 0.85 | 0.033333 | 0.88333 | Reboot then restore wtg. | Close | 0.02265 | G01 | 403.8674 | None | WTG Breakdown Maintenance | 10973 | 403.8674
479 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | Year_3 | G16 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 15:59 | 16:20 | 16:22 | 0.35 | 0.033333 | 0.38333 | Reboot then restore wtg. | Close | 0.0098291 | G17 | 231.15 | None | WTG Breakdown Maintenance | 14472 | 231.15
480 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | Year_3 | G18 | PWEGPL | MSEDCL | 2.564% | 5205 | Magnetothermic Of The Stator Protection Failure Or Door Open | BD | 15:55 | 16:35 | 16:44 | 0.66667 | 0.15 | 0.81667 | Reboot then restore wtg. | Close | 0.02094 | G19 | 494.5937 | None | WTG Breakdown Maintenance | 14535 | 494.5937
481 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | Year_3 | G21 | PWEGPL | MSEDCL | 2.564% | 5219 | Coolant Of The Coolant Circuit Failure | BD | 16:34 | 18:50 | 18:52 | 2.2667 | 0.033333 | 2.3 | Reboot then restore wtg. | Close | 0.058974 | G22 | 434.8917 | None | WTG Breakdown Maintenance | 4538 | 434.8917
482 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | Year_3 | G22 | PWEGPL | MSEDCL | 2.564% | 5203 | Heating/Coolant Thermal Magnetic Failure | BD | 15:30 | 16:42 | 19:12 | 1.2 | 2.5 | 3.7 | Checked related circuit found MPCB tripped so checked motor resistance then restore wtg. | Close | 0.094872 | G05 | 1304.4042 | None | WTG Breakdown Maintenance | 8461 | 1304.4042
483 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | Year_3 | G23 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 15:50 | 18:59 | 19:01 | 3.15 | 0.033333 | 3.1833 | Reboot then restore wtg. | Close | 0.081624 | G05 | 1122.2576 | None | WTG Breakdown Maintenance | 8461 | 1122.2576
484 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | Year_3 | G25 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 11:30 | 11:30 | 14:47 | 0 | 3.2833 | 3.2833 | Manual stop for Blade bush gap inspection work | Close | 0.084188 | G27 | 1295.8222 | None | WTG Force Majeaure | 9472 | 1295.8222
485 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | Year_3 | G30 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 16:50 | 18:45 | 18:47 | 1.9167 | 0.033333 | 1.95 | Reboot then restore wtg. | Close | 0.05 | G28 | 768.0563 | None | WTG Breakdown Maintenance | 9453 | 768.0563
486 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | Year_3 | G34 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 16:58 | 19:00 | 19:02 | 2.0333 | 0.033333 | 2.0667 | Reboot then restore wtg. | Close | 0.052991 | G33 | 412.4722 | None | WTG Breakdown Maintenance | 4790 | 412.4722
487 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | Year_3 | G37 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD | 16:18 | 19:15 | 19:17 | 2.95 | 0.033333 | 2.9833 | Reset then restore wtg. | Close | 0.076496 | G36 | 591.9431 | None | WTG Breakdown Maintenance | 4762 | 591.9431
488 | 2025-05-07 | 2025 | 2025 | 2025-05-01 | Year_3 | G38 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM | 11:30 | 11:30 | 17:48 | 0 | 6.3 | 6.3 | HYPM done then restore wtg. | Close | 0.16154 | G39 | 1783.425 | None | WTG Scheduled Maintenance | 6794 | 1783.425
489 | 2025-05-08 | 2025 | 2025 | 2025-05-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 7363.8826 | None | WTG Force Majeaure | 7369 | 7363.8826
490 | 2025-05-08 | 2025 | 2025 | 2025-05-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 7363.8826 | None | WTG Force Majeaure | 7369 | 7363.8826
491 | 2025-05-08 | 2025 | 2025 | 2025-05-01 | Year_3 | G03 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 13:02 | 15:30 | 15:32 | 2.4667 | 0.033333 | 2.5 | Reboot then restore wtg. | Close | 0.064103 | G04 | 921.7708 | None | WTG Breakdown Maintenance | 8849 | 921.7708
492 | 2025-05-08 | 2025 | 2025 | 2025-05-01 | Year_3 | G10 | PWEGPL | MSEDCL | 2.564% | 1899 | Automatic Secondaries Not OK | BD | 13:15 | 15:02 | 15:03 | 1.7833 | 0.016667 | 1.8 | Reset then restore wtg. | Close | 0.046154 | G11 | 666.75 | None | WTG Breakdown Maintenance | 8890 | 666.75
493 | 2025-05-08 | 2025 | 2025 | 2025-05-01 | Year_3 | G22 | PWEGPL | MSEDCL | 2.564% | 5203 | Heating/Coolant Thermal Magnetic Failure | BD | 9:10 | 9:42 | 13:30 | 0.53333 | 3.8 | 4.3333 | Check related circuit found MPCB & Contactor failure so replaced with new one then restore wtg. | Close | 0.11111 | G05 | 1426.5694 | None | WTG Breakdown Maintenance | 7901 | 1426.5694
494 | 2025-05-08 | 2025 | 2025 | 2025-05-01 | Year_3 | G25 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer | 12:18 | 12:18 | 12:34 | 0 | 0.26667 | 0.26667 | SEM meter Pole CT & PT installation work | Close | 0.0068376 | G27 | 88.0111 | None | WTG Unscheduled Maintenance | 7921 | 88.0111
495 | 2025-05-08 | 2025 | 2025 | 2025-05-01 | Year_3 | G28 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer | 11:42 | 11:42 | 12:01 | 0 | 0.31667 | 0.31667 | SEM meter Pole CT & PT installation work | Close | 0.0081197 | G30 | 104.7903 | None | WTG Unscheduled Maintenance | 7942 | 104.7903
496 | 2025-05-08 | 2025 | 2025 | 2025-05-01 | Year_3 | G35 | PWEGPL | MSEDCL | 2.564% | 5220 | Encoder Not OK | BD | 9:48 | 10:07 | 10:08 | 0.31667 | 0.016667 | 0.33333 | Reset then restore wtg. | Close | 0.008547 | G36 | 95.2222 | None | WTG Breakdown Maintenance | 6856 | 95.2222
497 | 2025-05-08 | 2025 | 2025 | 2025-05-01 | Year_3 | G35 | PWEGPL | MSEDCL | 2.564% | 5220 | Encoder Not OK | BD | 13:10 | 14:08 | 14:10 | 0.96667 | 0.033333 | 1 | Reboot then restore wtg. | Close | 0.025641 | G36 | 285.6667 | None | WTG Breakdown Maintenance | 6856 | 285.6667
498 | 2025-05-08 | 2025 | 2025 | 2025-05-01 | Year_3 | G37 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD | 9:51 | 10:15 | 16:37 | 0.4 | 6.3667 | 6.7667 | Checked related circuit found oil leakage from Blade A. so replaced pitch seal then restore wtg. | Close | 0.1735 | G36 | 1933.0111 | None | WTG Breakdown Maintenance | 6856 | 1933.0111
499 | 2025-05-08 | 2025 | 2025 | 2025-05-01 | Year_3 | G39 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD | 10:12 | 10:34 | 10:36 | 0.36667 | 0.033333 | 0.4 | Reset then restore wtg. | Close | 0.010256 | G40 | 114.2833 | None | WTG Breakdown Maintenance | 6857 | 114.2833
500 | 2025-05-08 | 2025 | 2025 | 2025-05-01 | Year_3 | G39 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD | 13:02 | 13:55 | 13:57 | 0.88333 | 0.033333 | 0.91667 | Reboot then restore wtg. | Close | 0.023504 | G40 | 261.8993 | None | WTG Breakdown Maintenance | 6857 | 261.8993
501 | 2025-05-09 | 2025 | 2025 | 2025-05-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 4522.8569 | None | WTG Force Majeaure | 4526 | 4522.8569
502 | 2025-05-09 | 2025 | 2025 | 2025-05-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 4522.8569 | None | WTG Force Majeaure | 4526 | 4522.8569
503 | 2025-05-09 | 2025 | 2025 | 2025-05-01 | Year_3 | G03 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer | 12:07 | 12:07 | 12:30 | 0 | 0.38333 | 0.38333 | SEM meter Pole CT & PT installation work | Close | 0.0098291 | G04 | 57.2285 | None | WTG Unscheduled Maintenance | 3583 | 57.2285
504 | 2025-05-09 | 2025 | 2025 | 2025-05-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer | 12:57 | 12:57 | 13:20 | 0 | 0.38333 | 0.38333 | SEM meter Pole CT & PT installation work | Close | 0.0098291 | G03 | 56.8931 | None | WTG Unscheduled Maintenance | 3562 | 56.8931
505 | 2025-05-09 | 2025 | 2025 | 2025-05-01 | Year_3 | G06 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer | 16:57 | 16:57 | 17:16 | 0 | 0.31667 | 0.31667 | SEM meter Pole CT & PT installation work | Close | 0.0081197 | G03 | 46.9986 | None | WTG Unscheduled Maintenance | 3562 | 46.9986
506 | 2025-05-09 | 2025 | 2025 | 2025-05-01 | Year_3 | G08 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer | 11:18 | 11:18 | 11:53 | 0 | 0.58333 | 0.58333 | SEM meter Pole CT & PT installation work | Close | 0.014957 | G03 | 86.5764 | None | WTG Unscheduled Maintenance | 3562 | 86.5764
507 | 2025-05-09 | 2025 | 2025 | 2025-05-01 | Year_3 | G09 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer | 15:32 | 15:32 | 15:55 | 0 | 0.38333 | 0.38333 | SEM meter Pole CT & PT installation work | Close | 0.0098291 | G12 | 64.7833 | None | WTG Unscheduled Maintenance | 4056 | 64.7833
508 | 2025-05-09 | 2025 | 2025 | 2025-05-01 | Year_3 | G10 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer | 16:16 | 16:16 | 16:36 | 0 | 0.33333 | 0.33333 | SEM meter Pole CT & PT installation work | Close | 0.008547 | G11 | 55.9167 | None | WTG Unscheduled Maintenance | 4026 | 55.9167
509 | 2025-05-09 | 2025 | 2025 | 2025-05-01 | Year_3 | G34 | PWEGPL | MSEDCL | 2.564% | CE100008 | General Work Stoppage | Manual stop | 11:10 | 11:10 | 12:30 | 0 | 1.3333 | 1.3333 | Manual stop for oil leakage inspection work | Close | 0.034188 | G33 | 199.6111 | None | WTG Unscheduled Maintenance | 3593 | 199.6111
510 | 2025-05-09 | 2025 | 2025 | 2025-05-01 | Year_3 | G37 | PWEGPL | MSEDCL | 2.564% | 1819 | RC Filter Failure | BD | 14:27 | 15:01 | 17:30 | 0.56667 | 2.4833 | 3.05 | Check related circuit found 33k resistor and RC filter card failure so replaced both with new one then restore wtg. | Close | 0.078205 | G36 | 454.7042 | None | WTG Breakdown Maintenance | 3578 | 454.7042
511 | 2025-05-09 | 2025 | 2025 | 2025-05-01 | Year_3 | G39 | PWEGPL | MSEDCL | 2.564% | CE100008 | General Work Stoppage | Manual stop | 11:20 | 11:20 | 12:45 | 0 | 1.4167 | 1.4167 | Manual stop for oil leakage inspection work | Close | 0.036325 | G40 | 210.4931 | None | WTG Unscheduled Maintenance | 3566 | 210.4931
512 | 2025-05-10 | 2025 | 2025 | 2025-05-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 4029.2 | None | WTG Force Majeaure | 4032 | 4029.2
513 | 2025-05-10 | 2025 | 2025 | 2025-05-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 4029.2 | None | WTG Force Majeaure | 4032 | 4029.2
514 | 2025-05-10 | 2025 | 2025 | 2025-05-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD | 10:58 | 11:50 | 23:59 | 0.86667 | 12.15 | 13.0167 | work in progress | Open | 0.33376 | G03 | 3619.1757 | None | WTG Breakdown Maintenance | 6673 | 3619.1757
515 | 2025-05-10 | 2025 | 2025 | 2025-05-01 | Year_3 | G09 | PWEGPL | MSEDCL | 2.564% | 800 | Pitch Drive Error | BD | 16:26 | 16:55 | 18:58 | 0.48333 | 2.05 | 2.5333 | Checked related circuit found propotional valve failure then replaced . | Close | 0.064957 | G12 | 743.4278 | None | WTG Breakdown Maintenance | 7043 | 743.4278
516 | 2025-05-11 | 2025 | 2025 | 2025-05-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 8511.0854 | None | WTG Force Majeaure | 8517 | 8511.0854
517 | 2025-05-11 | 2025 | 2025 | 2025-05-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 8511.0854 | None | WTG Force Majeaure | 8517 | 8511.0854
518 | 2025-05-11 | 2025 | 2025 | 2025-05-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD | 0:00 | 12:18 | 13:42 | 12.3 | 1.4 | 13.7 | Change PRV-10 & RV 8-10 Valve than start the WTG | Close | 0.35128 | G03 | 6916.2167 | None | WTG Breakdown Maintenance | 12116 | 6916.2167
519 | 2025-05-11 | 2025 | 2025 | 2025-05-01 | Year_3 | G21 | PWEGPL | MSEDCL | 2.564% | 5228 | Preload Failure | BD | 8:30 | 10:10 | 23:59 | 1.6667 | 13.8167 | 15.4833 | Checked related circuit found KC004 Contactor replace | Open | 0.39701 | G22 | 5585.6125 | None | WTG Breakdown Maintenance | 8658 | 5585.6125
520 | 2025-05-11 | 2025 | 2025 | 2025-05-01 | Year_3 | G23 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 10:30 | 11:15 | 23:04 | 0.75 | 11.8167 | 12.5667 | Checked related circuit & replace slipring and CAP module than start WTG | Close | 0.32222 | G22 | 4533.425 | None | WTG Breakdown Maintenance | 8658 | 4533.425
521 | 2025-05-12 | 2025 | 2025 | 2025-05-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 4212.0729 | None | WTG Force Majeaure | 4215 | 4212.0729
522 | 2025-05-12 | 2025 | 2025 | 2025-05-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 4212.0729 | None | WTG Force Majeaure | 4215 | 4212.0729
523 | 2025-05-12 | 2025 | 2025 | 2025-05-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD | 9:16 | 11:57 | 13:42 | 2.6833 | 1.75 | 4.4333 | Checked related circuit found niddel valve failure than replace . | Close | 0.11368 | G07 | 574.3014 | None | WTG Breakdown Maintenance | 3109 | 574.3014
524 | 2025-05-12 | 2025 | 2025 | 2025-05-01 | Year_3 | G03 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 11:20 | 11:20 | 13:35 | 0 | 2.25 | 2.25 | Manual stop for Blade bush gap inspection work | Close | 0.057692 | G06 | 289.3125 | None | WTG Force Majeaure | 3086 | 289.3125
525 | 2025-05-12 | 2025 | 2025 | 2025-05-01 | Year_3 | G23 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 9:15 | 11:21 | 17:21 | 2.1 | 6 | 8.1 | Checked related circuit found Cab module failure then replace. | Close | 0.20769 | G05 | 1360.8 | None | WTG Force Majeaure | 4032 | 1360.8
526 | 2025-05-12 | 2025 | 2025 | 2025-05-01 | Year_3 | G22 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer | 11:32 | 11:32 | 13:35 | 0 | 2.05 | 2.05 | SEM Yard Earthing work done then restore wtg. | Close | 0.052564 | G05 | 344.4 | None | WTG Unscheduled Maintenance | 4032 | 344.4
527 | 2025-05-12 | 2025 | 2025 | 2025-05-01 | Year_3 | G21 | PWEGPL | MSEDCL | 2.564% | 5228 | Preload Failure | BD | 0:00 | 0:00 | 20:36 | 0 | 20.6 | 20.6 | Checked related circuit found KC004 Contactor addon replace | Close | 0.52821 | G05 | 3460.8 | None | WTG Breakdown Maintenance | 4032 | 3460.8
528 | 2025-05-13 | 2025 | 2025 | 2025-05-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G30 | 4575.8201 | None | WTG Force Majeaure | 4579 | 4575.8201
529 | 2025-05-13 | 2025 | 2025 | 2025-05-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G30 | 4575.8201 | None | WTG Force Majeaure | 4579 | 4575.8201
530 | 2025-05-13 | 2025 | 2025 | 2025-05-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD | 12:04 | 12:38 | 15:19 | 0.56667 | 2.6833 | 3.25 | No leakage fond than start WTG | Close | 0.083333 | G02 | 911.8958 | None | WTG Breakdown Maintenance | 6734 | 911.8958
531 | 2025-05-13 | 2025 | 2025 | 2025-05-01 | Year_3 | G07 | PWEGPL | MSEDCL | 2.564% | 5236 | Error In Phase R Of The Inverter | BD | 20:14 | 20:43 | 21:32 | 0.48333 | 0.81667 | 1.3 | Checked related circuit no any obsarvation than start WTG | Close | 0.033333 | G01 | 367.3583 | None | WTG Breakdown Maintenance | 6782 | 367.3583
532 | 2025-05-13 | 2025 | 2025 | 2025-05-01 | Year_3 | G14 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 17:30 | 17:30 | 21:48 | 0 | 4.3 | 4.3 | Manual stop for Blade bush gap inspection work | Close | 0.11026 | G15 | 1315.8 | None | WTG Force Majeaure | 7344 | 1315.8
533 | 2025-05-13 | 2025 | 2025 | 2025-05-01 | Year_3 | G40 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD | 5:45 | 12:45 | 23:59 | 7 | 11.2333 | 18.2333 | checked T connector failure (work in progress) | Open | 0.46752 | G39 | 3044.9667 | Material shotage Tee connector. | WTG Breakdown Maintenance | 4008 | 3044.9667
534 | 2025-05-13 | 2025 | 2025 | 2025-05-01 | Year_3 | G28 | PWEGPL | MSEDCL | 2.564% | 2114 | Analogue Card Failure | BD | 12:17 | 12:38 | 13:01 | 0.35 | 0.38333 | 0.73333 | Reset then restore wtg. | Close | 0.018803 | G30 | 139.9139 | None | WTG Breakdown Maintenance | 4579 | 139.9139
535 | 2025-05-13 | 2025 | 2025 | 2025-05-01 | Year_3 | G21 | PWEGPL | MSEDCL | 2.564% | 5228 | Preload Failure | BD | 6:14 | 10:12 | 10:18 | 3.9667 | 0.1 | 4.0667 | Reset then restore wtg. | Close | 0.10427 | G22 | 765.2111 | None | WTG Breakdown Maintenance | 4516 | 765.2111
536 | 2025-05-14 | 2025 | 2025 | 2025-05-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G30 | 3265.7306 | None | WTG Force Majeaure | 3268 | 3265.7306
537 | 2025-05-14 | 2025 | 2025 | 2025-05-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G30 | 3265.7306 | None | WTG Force Majeaure | 3268 | 3265.7306
538 | 2025-05-14 | 2025 | 2025 | 2025-05-01 | Year_3 | G28 | PWEGPL | MSEDCL | 2.564% | 803 | Low Pitch Value In Stop Mode (1 Cylinder) | BD | 11:10 | 11:55 | 14:24 | 0.75 | 2.4833 | 3.2333 | Check related ckt found bulluf sensor failure then replaced & restore WTG. | Close | 0.082906 | G30 | 440.2722 | None | WTG Breakdown Maintenance | 3268 | 440.2722
539 | 2025-05-14 | 2025 | 2025 | 2025-05-01 | Year_3 | G40 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | checked T connector failure (work in progress) | Open | 0.61496 | G39 | 2898.9854 | Material shotage Tee connector. | WTG Breakdown Maintenance | 2901 | 2898.9854
540 | 2025-05-14 | 2025 | 2025 | 2025-05-01 | Year_3 | G14 | PWEGPL | MSEDCL | 2.564% | 5232 | Error In Phase R Of The Rectifier | BD | 6:30 | 8:11 | 22:10 | 1.6833 | 13.9833 | 15.6667 | Check related ckt found Component failure then replace Rectifire Side 3 IGBT,Fuse ,KC002 Contactor ,800 HC resistor and check capacitor bank then restore WTG. | Close | 0.40171 | G15 | 3313.5 | None | WTG Breakdown Maintenance | 5076 | 3313.5
541 | 2025-05-14 | 2025 | 2025 | 2025-05-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD | 17:55 | 19:02 | 20:29 | 1.1167 | 1.45 | 2.5667 | Check related ckt found hose damaged then replaced and restore WTG. | Close | 0.065812 | G02 | 517.9319 | None | WTG Breakdown Maintenance | 4843 | 517.9319
542 | 2025-05-14 | 2025 | 2025 | 2025-05-01 | Year_3 | G13 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 15:15 | 15:15 | 18:30 | 0 | 3.25 | 3.25 | Manual stop for Blade bush gap inspection work | Close | 0.083333 | G12 | 678.7083 | None | WTG Force Majeaure | 5012 | 678.7083
543 | 2025-05-14 | 2025 | 2025 | 2025-05-01 | Year_3 | G21 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 7:34 | 11:34 | 13:30 | 4 | 1.9333 | 5.9333 | Manual stop for Blade bush gap inspection work | Close | 0.15214 | G22 | 804.9556 | None | WTG Force Majeaure | 3256 | 804.9556
544 | 2025-05-14 | 2025 | 2025 | 2025-05-01 | Year_3 | G21 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | FM | 2:02 | 2:02 | 3:18 | 0 | 1.2667 | 1.2667 | Transformer inspection work. | Close | 0.032479 | G22 | 171.8444 | None | WTG Unscheduled Maintenance | 3256 | 171.8444
545 | 2025-05-15 | 2025 | 2025 | 2025-05-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 5038.4986 | None | WTG Force Majeaure | 5042 | 5038.4986
546 | 2025-05-15 | 2025 | 2025 | 2025-05-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 5038.4986 | None | WTG Force Majeaure | 5042 | 5038.4986
547 | 2025-05-15 | 2025 | 2025 | 2025-05-01 | Year_3 | G06 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer | 11:28 | 11:28 | 14:26 | 0 | 2.9667 | 2.9667 | SEM meter Pole CT & PT installation work | Close | 0.076068 | G03 | 793.9542 | None | WTG Unscheduled Maintenance | 6423 | 793.9542
548 | 2025-05-15 | 2025 | 2025 | 2025-05-01 | Year_3 | G07 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer | 14:15 | 14:15 | 16:00 | 0 | 1.75 | 1.75 | SEM meter Pole CT & PT installation work | Close | 0.044872 | G01 | 468.1979 | None | WTG Unscheduled Maintenance | 6421 | 468.1979
549 | 2025-05-15 | 2025 | 2025 | 2025-05-01 | Year_3 | G12 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 11:15 | 11:15 | 14:40 | 0 | 3.4167 | 3.4167 | Manual stop for Blade bush gap inspection work | Close | 0.087607 | G13 | 835.2326 | None | WTG Force Majeaure | 5867 | 835.2326
550 | 2025-05-15 | 2025 | 2025 | 2025-05-01 | Year_3 | G25 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD | 13:20 | 14:02 | 15:46 | 0.7 | 1.7333 | 2.4333 | Check related circuit found no leakage then restore wtg. | Close | 0.062393 | G27 | 512.6222 | None | WTG Breakdown Maintenance | 5056 | 512.6222
551 | 2025-05-15 | 2025 | 2025 | 2025-05-01 | Year_3 | G33 | PWEGPL | MSEDCL | 2.564% | CE100008 | General Work Stoppage | Manual stop | 12:28 | 12:28 | 16:27 | 0 | 3.9833 | 3.9833 | Manual stop for Gearbox fan motor replaced then restore wtg. | Close | 0.10214 | G34 | 758.825 | None | WTG Unscheduled Maintenance | 4572 | 758.825
552 | 2025-05-15 | 2025 | 2025 | 2025-05-01 | Year_3 | G39 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM | 12:07 | 12:07 | 18:58 | 0 | 6.85 | 6.85 | HYPM done then then restore wtg. | Close | 0.17564 | G38 | 1309.4917 | None | WTG Scheduled Maintenance | 4588 | 1309.4917
553 | 2025-05-15 | 2025 | 2025 | 2025-05-01 | Year_3 | G40 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD | 0:00 | 19:40 | 20:33 | 19.6667 | 0.88333 | 20.55 | Check related circuit found B Phase Tee connector failure so replaced with new one then restore wtg. | Close | 0.52692 | G26 | 3914.775 | Material shotage Tee connector. | WTG Breakdown Maintenance | 4572 | 3914.775
554 | 2025-05-16 | 2025 | 2025 | 2025-05-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 8159.3299 | None | WTG Force Majeaure | 8165 | 8159.3299
555 | 2025-05-16 | 2025 | 2025 | 2025-05-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 8159.3299 | None | WTG Force Majeaure | 8165 | 8159.3299
556 | 2025-05-16 | 2025 | 2025 | 2025-05-01 | Year_3 | G01 | PWEGPL | MSEDCL | 2.564% | 800 | Pitch Drive Error | BD | 12:01 | 12:35 | 15:14 | 0.56667 | 2.65 | 3.2167 | Checked related circuit found loose connection so tight it then restore wtg. | Close | 0.082479 | G07 | 1417.4778 | None | WTG Unscheduled Maintenance | 10576 | 1417.4778
557 | 2025-05-16 | 2025 | 2025 | 2025-05-01 | Year_3 | G02 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer | 12:30 | 12:30 | 14:10 | 0 | 1.6667 | 1.6667 | Manual stop for SEM meter CT/PT istallation work | Close | 0.042735 | G04 | 686.6667 | None | WTG Unscheduled Maintenance | 9888 | 686.6667
558 | 2025-05-16 | 2025 | 2025 | 2025-05-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD | 16:21 | 16:41 | 18:35 | 0.33333 | 1.9 | 2.2333 | Check related circuit found ok then set PRV 8-10 Valve then replaced Gearbox cooling fan motor replaced then restore wtg. | Close | 0.057265 | G03 | 980.9917 | None | WTG Unscheduled Maintenance | 10542 | 980.9917
559 | 2025-05-16 | 2025 | 2025 | 2025-05-01 | Year_3 | G06 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 16:30 | 17:45 | 17:50 | 1.25 | 0.083333 | 1.3333 | Reset then restore wtg. | Close | 0.034188 | G03 | 585.6667 | None | WTG Breakdown Maintenance | 10542 | 585.6667
560 | 2025-05-16 | 2025 | 2025 | 2025-05-01 | Year_3 | G19 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop | 11:40 | 11:40 | 23:59 | 0 | 12.3167 | 12.3167 | Manual stop for pitch seal replacement work (Pitch cylinder head sturcked work in progress) | Open | 0.31581 | G18 | 5114.4958 | None | WTG Breakdown Maintenance | 9966 | 5114.4958
561 | 2025-05-16 | 2025 | 2025 | 2025-05-01 | Year_3 | G40 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM | 11:46 | 11:46 | 17:28 | 0 | 5.7 | 5.7 | HYPM done then then restore wtg. | Close | 0.14615 | G39 | 1754.65 | None | WTG Scheduled Maintenance | 7388 | 1754.65
562 | 2025-05-17 | 2025 | 2025 | 2025-05-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 4120.1368 | None | WTG Force Majeaure | 4123 | 4120.1368
563 | 2025-05-17 | 2025 | 2025 | 2025-05-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 4120.1368 | None | WTG Force Majeaure | 4123 | 4120.1368
564 | 2025-05-17 | 2025 | 2025 | 2025-05-01 | Year_3 | G06 | PWEGPL | MSEDCL | 2.564% | CE100008 | General Work Stoppage | Manual stop | 11:33 | 11:33 | 14:40 | 0 | 3.1167 | 3.1167 | Checked related circuit found ok then replaced smoke sensor then restore wtg. | Close | 0.079915 | G03 | 738.1306 | None | WTG Unscheduled Maintenance | 5684 | 738.1306
565 | 2025-05-17 | 2025 | 2025 | 2025-05-01 | Year_3 | G19 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop | 0:00 | 0:00 | 22:45 | 0 | 22.75 | 22.75 | Manual stop for Blade B pitch cylinder replaced then restore wtg. | Close | 0.58333 | G18 | 6137.7604 | None | WTG Unscheduled Maintenance | 6475 | 6137.7604
566 | 2025-05-17 | 2025 | 2025 | 2025-05-01 | Year_3 | G26 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM | 12:16 | 12:16 | 19:46 | 0 | 7.5 | 7.5 | HYPM done then then restore wtg. | Close | 0.19231 | G32 | 1100.3125 | None | WTG Scheduled Maintenance | 3521 | 1100.3125
567 | 2025-05-17 | 2025 | 2025 | 2025-05-01 | Year_3 | G02 | PWEGPL | MSEDCL | 2.564% | 5225 | Fault In Analog Electronic Power Supply | BD | 14:48 | 15:20 | 15:22 | 0.53333 | 0.033333 | 0.56667 | Reset then restore wtg. | Close | 0.01453 | G04 | 134.1347 | None | WTG Breakdown Maintenance | 5681 | 134.1347
568 | 2025-05-17 | 2025 | 2025 | 2025-05-01 | Year_3 | G07 | PWEGPL | MSEDCL | 2.564% | 5225 | Fault In Analog Electronic Power Supply | BD | 14:48 | 15:37 | 15:39 | 0.81667 | 0.033333 | 0.85 | Reset then restore wtg. | Close | 0.021795 | G01 | 200.9187 | None | WTG Breakdown Maintenance | 5673 | 200.9187
569 | 2025-05-18 | 2025 | 2025 | 2025-05-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 3540.5396 | None | WTG Force Majeaure | 3543 | 3540.5396
570 | 2025-05-18 | 2025 | 2025 | 2025-05-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 3569.5194 | None | WTG Force Majeaure | 3572 | 3569.5194
571 | 2025-05-18 | 2025 | 2025 | 2025-05-01 | Year_3 | G01 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 12:55 | 13:17 | 14:05 | 0.36667 | 0.8 | 1.1667 | Slipring clean then restore wtg | Close | 0.029915 | G07 | 171.9375 | None | WTG Breakdown Maintenance | 3537 | 171.9375
572 | 2025-05-18 | 2025 | 2025 | 2025-05-01 | Year_3 | G32 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM | 12:26 | 12:26 | 18:03 | 0 | 5.6167 | 5.6167 | HYPM done then then restore wtg. | Close | 0.14402 | G26 | 739.9958 | None | WTG Scheduled Maintenance | 3162 | 739.9958
573 | 2025-05-18 | 2025 | 2025 | 2025-05-01 | Year_3 | G33 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 16:10 | 16:42 | 16:45 | 0.53333 | 0.05 | 0.58333 | Reboot then restore wtg. | Close | 0.014957 | G34 | 75.8576 | None | WTG Breakdown Maintenance | 3121 | 75.8576
574 | 2025-05-19 | 2025 | 2025 | 2025-05-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 4106.1465 | None | WTG Force Majeaure | 4109 | 4106.1465
575 | 2025-05-19 | 2025 | 2025 | 2025-05-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 4106.1465 | None | WTG Force Majeaure | 4109 | 4106.1465
576 | 2025-05-19 | 2025 | 2025 | 2025-05-01 | Year_3 | G05 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer | 11:16 | 11:16 | 12:20 | 0 | 1.0667 | 1.0667 | Manual stop for SEM meter CT/PT istallation work | Close | 0.02735 | G23 | 868.7222 | None | WTG Unscheduled Maintenance | 4115 | 182.8889
577 | 2025-05-19 | 2025 | 2025 | 2025-05-01 | Year_3 | G22 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM | 11:04 | 11:04 | 17:30 | 0 | 6.4333 | 6.4333 | HYPM done then then restore wtg. | Close | 0.16496 | G21 | 1099.5639 | None | WTG Scheduled Maintenance | 4102 | 1099.5639
578 | 2025-05-19 | 2025 | 2025 | 2025-05-01 | Year_3 | G28 | PWEGPL | MSEDCL | 2.564% | 2102 | PLC Module Failure | BD | 16:22 | 16:58 | 17:01 | 0.6 | 0.05 | 0.65 | Reboot then restore wtg. | Close | 0.016667 | G30 | 111.6104 | None | WTG Breakdown Maintenance | 4121 | 111.6104
579 | 2025-05-20 | 2025 | 2025 | 2025-05-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 5238.3597 | None | WTG Force Majeaure | 5242 | 5238.3597
580 | 2025-05-20 | 2025 | 2025 | 2025-05-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 5238.3597 | None | WTG Force Majeaure | 5242 | 5238.3597
581 | 2025-05-20 | 2025 | 2025 | 2025-05-01 | Year_3 | G02 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD | 16:02 | 16:35 | 16:37 | 0.55 | 0.033333 | 0.58333 | Reset then restore wtg. | Close | 0.014957 | G04 | 135.5035 | None | WTG Breakdown Maintenance | 5575 | 135.5035
582 | 2025-05-20 | 2025 | 2025 | 2025-05-01 | Year_3 | G03 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD | 16:15 | 16:52 | 16:54 | 0.61667 | 0.033333 | 0.65 | Reset then restore wtg. | Close | 0.016667 | G04 | 150.9896 | None | WTG Breakdown Maintenance | 5575 | 150.9896
583 | 2025-05-20 | 2025 | 2025 | 2025-05-01 | Year_3 | G09 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD | 16:15 | 17:02 | 17:04 | 0.78333 | 0.033333 | 0.81667 | Reset then restore wtg. | Close | 0.02094 | G12 | 181.7764 | None | WTG Breakdown Maintenance | 5342 | 181.7764
584 | 2025-05-20 | 2025 | 2025 | 2025-05-01 | Year_3 | G10 | PWEGPL | MSEDCL | 2.564% | CE100008 | General Work Stoppage | Manual stop | 11:20 | 11:20 | 16:10 | 0 | 4.8333 | 4.8333 | Manual stop for lift clamp replacement work | Close | 0.12393 | G11 | 1116.2986 | None | WTG Unscheduled Maintenance | 5543 | 1116.2986
585 | 2025-05-20 | 2025 | 2025 | 2025-05-01 | Year_3 | G21 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM | 11:40 | 11:40 | 17:41 | 0 | 6.0167 | 6.0167 | HYPM done then then restore wtg. | Close | 0.15427 | G22 | 1303.6111 | None | WTG Scheduled Maintenance | 5200 | 1303.6111
586 | 2025-05-20 | 2025 | 2025 | 2025-05-01 | Year_3 | G32 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD | 14:25 | 15:10 | 15:12 | 0.75 | 0.033333 | 0.78333 | Reset then restore wtg. | Close | 0.020085 | G26 | 114.2687 | None | WTG Breakdown Maintenance | 3501 | 114.2687
587 | 2025-05-20 | 2025 | 2025 | 2025-05-01 | Year_3 | G26 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD | 14:25 | 15:25 | 15:27 | 1 | 0.033333 | 1.0333 | Reset then restore wtg. | Close | 0.026496 | G40 | 159.1333 | None | WTG Breakdown Maintenance | 3696 | 159.1333
588 | 2025-05-20 | 2025 | 2025 | 2025-05-01 | Year_3 | G39 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD | 14:25 | 15:44 | 15:46 | 1.3167 | 0.033333 | 1.35 | Reset then restore wtg. | Close | 0.034615 | G40 | 207.9 | None | WTG Breakdown Maintenance | 3696 | 207.9
589 | 2025-05-21 | 2025 | 2025 | 2025-05-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 5640.0806 | None | WTG Force Majeaure | 5644 | 5640.0806
590 | 2025-05-21 | 2025 | 2025 | 2025-05-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 5640.0806 | None | WTG Force Majeaure | 5644 | 5640.0806
591 | 2025-05-21 | 2025 | 2025 | 2025-05-01 | Year_3 | G01 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer | 11:53 | 11:53 | 12:45 | 0 | 0.86667 | 0.86667 | Manual stop for SEM meter CT/PT istallation work | Close | 0.022222 | G07 | 203.4139 | None | WTG Unscheduled Maintenance | 5633 | 203.4139
592 | 2025-05-21 | 2025 | 2025 | 2025-05-01 | Year_3 | G06 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD | 14:07 | 14:51 | 15:55 | 0.73333 | 1.0667 | 1.8 | Checked related circuit found ok then restore wtg. | Close | 0.046154 | G03 | 422.4 | None | WTG Breakdown Maintenance | 5632 | 422.4
593 | 2025-05-21 | 2025 | 2025 | 2025-05-01 | Year_3 | G23 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM | 12:10 | 12:10 | 19:00 | 0 | 6.8333 | 6.8333 | HYPM done then then restore wtg. | Close | 0.17521 | G05 | 1594.7292 | None | WTG Scheduled Maintenance | 5601 | 1594.7292
594 | 2025-05-21 | 2025 | 2025 | 2025-05-01 | Year_3 | G33 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD | 18:07 | 18:42 | 21:39 | 0.58333 | 2.95 | 3.5333 | checked related circuit found no leakage then top-up 10 liter HU oil then restore wtg. | Close | 0.090598 | G34 | 683.8472 | None | WTG Breakdown Maintenance | 4645 | 683.8472
595 | 2025-05-22 | 2025 | 2025 | 2025-05-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 8845.8528 | None | WTG Force Majeaure | 8852 | 8845.8528
596 | 2025-05-22 | 2025 | 2025 | 2025-05-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 8845.8528 | None | WTG Force Majeaure | 8852 | 8845.8528
597 | 2025-05-22 | 2025 | 2025 | 2025-05-01 | Year_3 | G03 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer | 15:37 | 15:37 | 17:05 | 0 | 1.4667 | 1.4667 | Manual stop for SEM meter CT/PT istallation work | Close | 0.037607 | G04 | 382.7389 | None | WTG Unscheduled Maintenance | 6263 | 382.7389
598 | 2025-05-22 | 2025 | 2025 | 2025-05-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer | 14:35 | 14:35 | 15:25 | 0 | 0.83333 | 0.83333 | Manual stop for SEM meter CT/PT istallation work | Close | 0.021368 | G03 | 218.0208 | None | WTG Unscheduled Maintenance | 6279 | 218.0208
599 | 2025-05-22 | 2025 | 2025 | 2025-05-01 | Year_3 | G05 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM | 11:51 | 11:51 | 18:11 | 0 | 6.3333 | 6.3333 | HYPM done then then restore wtg. | Close | 0.16239 | G22 | 2333.3056 | None | WTG Scheduled Maintenance | 8842 | 2333.3056
600 | 2025-05-22 | 2025 | 2025 | 2025-05-01 | Year_3 | G32 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 12:30 | 13:30 | 13:32 | 1 | 0.033333 | 1.0333 | Reset then restore wtg. | Close | 0.026496 | G26 | 260.0986 | None | WTG Breakdown Maintenance | 6041 | 260.0986
601 | 2025-05-22 | 2025 | 2025 | 2025-05-01 | Year_3 | G38 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop | 11:04 | 11:04 | 13:14 | 0 | 2.1667 | 2.1667 | Manual stop for Carbon brush replacement work. | Close | 0.055556 | G39 | 546.0903 | None | WTG Unscheduled Maintenance | 6049 | 546.0903
602 | 2025-05-23 | 2025 | 2025 | 2025-05-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 2036.5847 | None | WTG Force Majeaure | 2038 | 2036.5847
603 | 2025-05-23 | 2025 | 2025 | 2025-05-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 2036.5847 | None | WTG Force Majeaure | 2038 | 2036.5847
604 | 2025-05-23 | 2025 | 2025 | 2025-05-01 | Year_3 | G11 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 14:57 | 15:42 | 15:45 | 0.75 | 0.05 | 0.8 | Reset then restore wtg. | Close | 0.020513 | G10 | 94.3333 | None | WTG Breakdown Maintenance | 2830 | 94.3333
605 | 2025-05-23 | 2025 | 2025 | 2025-05-01 | Year_3 | G12 | PWEGPL | MSEDCL | 2.564% | 5210 | Failure Of The Contactor's Rotor Power | Manual stop | 11:20 | 11:20 | 13:30 | 0 | 2.1667 | 2.1667 | Manual stop for repeted error (low pressure on hydraulic group and failure of the rotor power supply failure) found losse connection and set RV8-10 valve then restore wtg. | Close | 0.055556 | G13 | 280.4931 | None | WTG Unscheduled Maintenance | 3107 | 280.4931
606 | 2025-05-23 | 2025 | 2025 | 2025-05-01 | Year_3 | G15 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM | 11:17 | 11:17 | 17:57 | 0 | 6.6667 | 6.6667 | HYPM done then then restore wtg. | Close | 0.17094 | G16 | 863.6111 | None | WTG Scheduled Maintenance | 3109 | 863.6111
607 | 2025-05-23 | 2025 | 2025 | 2025-05-01 | Year_3 | G16 | PWEGPL | MSEDCL | 2.564% | 5225 | Fault In Analog Electronic Power Supply | BD | 16:01 | 16:25 | 16:27 | 0.4 | 0.033333 | 0.43333 | Reset then restore wtg. | Close | 0.011111 | G17 | 56.1708 | None | WTG Breakdown Maintenance | 3111 | 56.1708
608 | 2025-05-23 | 2025 | 2025 | 2025-05-01 | Year_3 | G25 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer | 14:15 | 14:15 | 15:00 | 0 | 0.75 | 0.75 | Manual stop for SEM meter CT/PT earthing istallation work | Close | 0.019231 | G27 | 62.9375 | None | WTG Unscheduled Maintenance | 2014 | 62.9375
609 | 2025-05-24 | 2025 | 2025 | 2025-05-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 7766.6028 | None | WTG Force Majeaure | 7772 | 7766.6028
610 | 2025-05-24 | 2025 | 2025 | 2025-05-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 7766.6028 | None | WTG Force Majeaure | 7772 | 7766.6028
611 | 2025-05-24 | 2025 | 2025 | 2025-05-01 | Year_3 | G16 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM | 12:10 | 12:10 | 19:55 | 0 | 7.75 | 7.75 | HYPM done then then restore wtg. | Close | 0.19872 | G17 | 2378.2813 | None | WTG Scheduled Maintenance | 7365 | 2378.2813
612 | 2025-05-24 | 2025 | 2025 | 2025-05-01 | Year_3 | G26 | PWEGPL | MSEDCL | 2.564% | CE100008 | General Work Stoppage | PM | 13:55 | 13:55 | 16:01 | 0 | 2.1 | 2.1 | Manual stop for HU main accumulator replacement work | Close | 0.053846 | G32 | 565.8625 | None | WTG Unscheduled Maintenance | 6467 | 565.8625
613 | 2025-05-24 | 2025 | 2025 | 2025-05-01 | Year_3 | G34 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD | 12:20 | 12:58 | 13:00 | 0.63333 | 0.033333 | 0.66667 | Reset then restore wtg. | Close | 0.017094 | G33 | 179.3611 | None | WTG Breakdown Maintenance | 6457 | 179.3611
614 | 2025-05-25 | 2025 | 2025 | 2025-05-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 5524.1611 | None | WTG Force Majeaure | 5528 | 5524.1611
615 | 2025-05-25 | 2025 | 2025 | 2025-05-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 5524.1611 | None | WTG Force Majeaure | 5528 | 5524.1611
616 | 2025-05-25 | 2025 | 2025 | 2025-05-01 | Year_3 | G10 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD | 11:00 | 11:30 | 11:31 | 0.5 | 0.016667 | 0.51667 | Reset then restore wtg. | Close | 0.013248 | G11 | 154.225 | None | WTG Breakdown Maintenance | 7164 | 154.225
617 | 2025-05-25 | 2025 | 2025 | 2025-05-01 | Year_3 | G16 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 5:23 | 6:43 | 6:45 | 1.3333 | 0.033333 | 1.3667 | Reboot then restore wtg. | Close | 0.035043 | G15 | 405.9569 | None | WTG Breakdown Maintenance | 7129 | 405.9569
618 | 2025-05-25 | 2025 | 2025 | 2025-05-01 | Year_3 | G17 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM | 10:58 | 10:58 | 17:59 | 0 | 7.0167 | 7.0167 | HYPM done then then restore wtg. | Close | 0.17991 | G16 | 2016.7069 | None | WTG Scheduled Maintenance | 6898 | 2016.7069
619 | 2025-05-25 | 2025 | 2025 | 2025-05-01 | Year_3 | G32 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 12:36 | 12:36 | 14:05 | 0 | 1.4833 | 1.4833 | Manual stop for Blade bush gap inspection work | Close | 0.038034 | G26 | 361.0681 | None | WTG Force Majeaure | 5842 | 361.0681
620 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 3646.466 | None | WTG Force Majeaure | 3649 | 3646.466
621 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 3646.466 | None | WTG Force Majeaure | 3649 | 3646.466
622 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 20:00 | 20:58 | 21:00 | 0.96667 | 0.033333 | 1 | Reset then restore wtg. | Close | 0.025641 | G03 | 184.2083 | None | WTG Breakdown Maintenance | 4421 | 184.2083
623 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | Year_3 | G18 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM | 13:05 | 13:05 | 19:51 | 0 | 6.7667 | 6.7667 | HYPM done then then restore wtg. | Close | 0.1735 | G17 | 1058.1375 | None | WTG Scheduled Maintenance | 3753 | 1058.1375
624 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | Year_3 | G19 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM | 11:21 | 11:21 | 18:15 | 0 | 6.9 | 6.9 | HYPM done then then restore wtg. | Close | 0.17692 | G20 | 1080.425 | None | WTG Scheduled Maintenance | 3758 | 1080.425
625 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | Year_3 | G25 | PWEGPL | MSEDCL | 2.564% | 5203 | Heating/Coolant Thermal Magnetic Failure | BD | 13:02 | 13:35 | 15:10 | 0.55 | 1.5833 | 2.1333 | Checked and found FG780 MPCB tripped so correct it then checked motor and connections then restore wtg. | Close | 0.054701 | G27 | 324.6222 | None | WTG Breakdown Maintenance | 3652 | 324.6222
626 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | Year_3 | G25 | PWEGPL | MSEDCL | 2.564% | 5203 | Heating/Coolant Thermal Magnetic Failure | BD | 23:16 | 23:40 | 23:59 | 0.4 | 0.31667 | 0.71667 | work in progress | Open | 0.018376 | G27 | 109.0528 | None | WTG Breakdown Maintenance | 3652 | 109.0528
627 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | Year_3 | G30 | PWEGPL | MSEDCL | 2.564% | 208 | HU Pump Drive Failure | BD | 16:15 | 16:53 | 17:30 | 0.63333 | 0.61667 | 1.25 | Checked related circuit found HU contactor failure so replaced with new one then restore wtg. | Close | 0.032051 | G28 | 190.0521 | None | WTG Breakdown Maintenance | 3649 | 190.0521
628 | 2025-05-26 | 2025 | 2025 | 2025-05-01 | Year_3 | G40 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 17:00 | 17:58 | 18:00 | 0.96667 | 0.033333 | 1 | Reset then restore wtg. | Close | 0.025641 | G39 | 147.0417 | None | WTG Breakdown Maintenance | 3529 | 147.0417
629 | 2025-05-27 | 2025 | 2025 | 2025-05-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 11850.7646 | None | WTG Force Majeaure | 11859 | 11850.7646
630 | 2025-05-27 | 2025 | 2025 | 2025-05-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 11850.7646 | None | WTG Force Majeaure | 11859 | 11850.7646
631 | 2025-05-27 | 2025 | 2025 | 2025-05-01 | Year_3 | G01 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD | 19:50 | 19:50 | 23:59 | 0 | 4.15 | 4.15 | (work in progress) Tee-connector failure wtg side. | Close | 0.10641 | G07 | 1835.5104 | None | WTG Breakdown Maintenance | 10615 | 1835.5104
632 | 2025-05-27 | 2025 | 2025 | 2025-05-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | CE100014 | Manual Stop - Audit | Manual stop/Customer | 13:30 | 13:30 | 15:00 | 0 | 1.5 | 1.5 | Manual stop for Customer audit work | Close | 0.038462 | G03 | 663.9375 | None | WTG Unscheduled Maintenance | 10623 | 663.9375
633 | 2025-05-27 | 2025 | 2025 | 2025-05-01 | Year_3 | G06 | PWEGPL | MSEDCL | 2.564% | CE100014 | Manual Stop - Audit | Manual stop/Customer | 11:10 | 11:10 | 13:00 | 0 | 1.8333 | 1.8333 | Manual stop for Customer audit work | Close | 0.047009 | G03 | 811.4792 | None | WTG Unscheduled Maintenance | 10623 | 811.4792
634 | 2025-05-27 | 2025 | 2025 | 2025-05-01 | Year_3 | G20 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM | 11:39 | 11:39 | 18:36 | 0 | 6.95 | 6.95 | HYPM done then then restore wtg. | Close | 0.17821 | G19 | 4280.6208 | None | WTG Scheduled Maintenance | 14782 | 4280.6208
635 | 2025-05-27 | 2025 | 2025 | 2025-05-01 | Year_3 | G25 | PWEGPL | MSEDCL | 2.564% | 5203 | Heating/Coolant Thermal Magnetic Failure | BD | 0:00 | 0:00 | 1:18 | 0 | 1.3 | 1.3 | Checked related circuit found MPCB failure so replaced with new one then restore wtg. | Close | 0.033333 | G27 | 641.9833 | None | WTG Breakdown Maintenance | 11852 | 641.9833
636 | 2025-05-27 | 2025 | 2025 | 2025-05-01 | Year_3 | G30 | PWEGPL | MSEDCL | 2.564% | CE100014 | Manual Stop - Audit | Manual stop/Customer | 11:20 | 11:20 | 12:40 | 0 | 1.3333 | 1.3333 | Manual stop for Customer audit work | Close | 0.034188 | G28 | 658.8333 | None | WTG Unscheduled Maintenance | 11859 | 658.8333
637 | 2025-05-27 | 2025 | 2025 | 2025-05-01 | Year_3 | G33 | PWEGPL | MSEDCL | 2.564% | CE100014 | Manual Stop - Audit | Manual stop/Customer | 13:10 | 13:10 | 14:20 | 0 | 1.1667 | 1.1667 | Manual stop for Customer audit work | Close | 0.029915 | G34 | 506.5764 | None | WTG Unscheduled Maintenance | 10421 | 506.5764
638 | 2025-05-28 | 2025 | 2025 | 2025-05-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 9962.0771 | None | WTG Force Majeaure | 9969 | 9962.0771
639 | 2025-05-28 | 2025 | 2025 | 2025-05-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 9962.0771 | None | WTG Force Majeaure | 9969 | 9962.0771
640 | 2025-05-28 | 2025 | 2025 | 2025-05-01 | Year_3 | G01 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD | 0:00 | 0:00 | 16:10 | 0 | 16.1667 | 16.1667 | Checked related circuit found Tee connector failure so replaced Tee connector with new one then restore wtg. | Close | 0.41453 | G07 | 10746.1181 | None | WTG Breakdown Maintenance | 15953 | 10746.1181
641 | 2025-05-28 | 2025 | 2025 | 2025-05-01 | Year_3 | G07 | PWEGPL | MSEDCL | 2.564% | 5225 | Fault In Analog Electronic Power Supply | BD | 1:18 | 1:48 | 1:50 | 0.5 | 0.033333 | 0.53333 | Reset then restore wtg. | Close | 0.013675 | G03 | 364.1111 | None | WTG Breakdown Maintenance | 16385 | 364.1111
642 | 2025-05-28 | 2025 | 2025 | 2025-05-01 | Year_3 | G14 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM | 10:15 | 10:15 | 17:36 | 0 | 7.35 | 7.35 | HYPM done then then restore wtg. | Close | 0.18846 | G15 | 4213.6937 | None | WTG Scheduled Maintenance | 13759 | 4213.6937
643 | 2025-05-28 | 2025 | 2025 | 2025-05-01 | Year_3 | G16 | PWEGPL | MSEDCL | 2.564% | 5225 | Fault In Analog Electronic Power Supply | BD | 11:04 | 11:35 | 11:45 | 0.51667 | 0.16667 | 0.68333 | CCU reset then restore wtg. | Close | 0.017521 | G17 | 391.55 | None | WTG Breakdown Maintenance | 13752 | 391.55
644 | 2025-05-28 | 2025 | 2025 | 2025-05-01 | Year_3 | G33 | PWEGPL | MSEDCL | 2.564% | 800 | Pitch Drive Error | BD | 15:12 | 15:52 | 19:38 | 0.66667 | 3.7667 | 4.4333 | Checked related circuit found TA033 power supply failure so replaced with new one then restore wtg. | Close | 0.11368 | G34 | 1371.0083 | None | WTG Breakdown Maintenance | 7422 | 1371.0083
645 | 2025-05-29 | 2025 | 2025 | 2025-05-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 12259.4806 | None | WTG Force Majeaure | 12268 | 12259.4806
646 | 2025-05-29 | 2025 | 2025 | 2025-05-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 12259.4806 | None | WTG Force Majeaure | 12268 | 12259.4806
647 | 2025-05-29 | 2025 | 2025 | 2025-05-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD | 17:35 | 18:20 | 18:22 | 0.75 | 0.033333 | 0.78333 | Reset then restore wtg. | Close | 0.020085 | G03 | 537.0403 | None | WTG Breakdown Maintenance | 16454 | 537.0403
648 | 2025-05-29 | 2025 | 2025 | 2025-05-01 | Year_3 | G13 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM | 11:30 | 11:30 | 18:45 | 0 | 7.25 | 7.25 | HYPM done then then restore wtg. | Close | 0.1859 | G12 | 4974.4062 | None | WTG Scheduled Maintenance | 16467 | 4974.4062
649 | 2025-05-29 | 2025 | 2025 | 2025-05-01 | Year_3 | G14 | PWEGPL | MSEDCL | 2.564% | 5238 | Error In Phase T Of The Inverter | BD | 11:00 | 11:35 | 14:20 | 0.58333 | 2.75 | 3.3333 | Checked related circuit found Diode failure so replaced with new one then restore wtg. | Close | 0.08547 | G15 | 2230.6944 | None | WTG Breakdown Maintenance | 16061 | 2230.6944
650 | 2025-05-29 | 2025 | 2025 | 2025-05-01 | Year_3 | G25 | PWEGPL | MSEDCL | 2.564% | 5203 | Heating/Coolant Thermal Magnetic Failure | BD | 15:15 | 18:32 | 18:35 | 3.2833 | 0.05 | 3.3333 | Reset then restore wtg. | Close | 0.08547 | G27 | 1703.3333 | None | WTG Breakdown Maintenance | 12264 | 1703.3333
651 | 2025-05-29 | 2025 | 2025 | 2025-05-01 | Year_3 | G33 | PWEGPL | MSEDCL | 2.564% | CE100008 | General Work Stoppage | Manual stop | 12:55 | 12:55 | 20:10 | 0 | 7.25 | 7.25 | Manual stop for Customer audit point rectification and Gear box damper replacement work. | Close | 0.1859 | G34 | 4184.7604 | None | WTG Unscheduled Maintenance | 13853 | 4184.7604
652 | 2025-05-29 | 2025 | 2025 | 2025-05-01 | Year_3 | G36 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 17:01 | 18:15 | 18:18 | 1.2333 | 0.05 | 1.2833 | Reboot then restore wtg. | Close | 0.032906 | G37 | 740.9646 | None | WTG Breakdown Maintenance | 13857 | 740.9646
653 | 2025-05-30 | 2025 | 2025 | 2025-05-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 10982.3681 | None | WTG Force Majeaure | 10990 | 10982.3681
654 | 2025-05-30 | 2025 | 2025 | 2025-05-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 10982.3681 | None | WTG Force Majeaure | 10990 | 10982.3681
655 | 2025-05-30 | 2025 | 2025 | 2025-05-01 | Year_3 | G02 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer | 16:22 | 16:22 | 19:30 | 0 | 3.1333 | 3.1333 | Manual stop for SEM meter CT/PT connection work | Close | 0.080342 | G04 | 1931.8306 | None | WTG Unscheduled Maintenance | 14797 | 1931.8306
656 | 2025-05-30 | 2025 | 2025 | 2025-05-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD | 13:47 | 14:15 | 14:55 | 0.46667 | 0.66667 | 1.1333 | Checked reslsted circuit found PRV valve failure so replaced with new one then restore wtg. | Close | 0.02906 | G03 | 749.3694 | None | WTG Breakdown Maintenance | 15869 | 749.3694
657 | 2025-05-30 | 2025 | 2025 | 2025-05-01 | Year_3 | G16 | PWEGPL | MSEDCL | 2.564% | 5202 | Stator Contactor Failure | BD | 9:45 | 11:31 | 14:01 | 1.7667 | 2.5 | 4.2667 | Check related circuit found Addon and CCU malfunction so replaced addon and reset CCU then restore wtg. | Close | 0.1094 | G17 | 3320 | None | WTG Breakdown Maintenance | 18675 | 3320
658 | 2025-05-30 | 2025 | 2025 | 2025-05-01 | Year_3 | G25 | PWEGPL | MSEDCL | 2.564% | 800 | Pitch Drive Error | BD | 10:50 | 12:24 | 20:50 | 1.5667 | 8.4333 | 10 | Check related circuit found Proportion valve cable damage form connecter side so replaced it then take tail after that error occurred heating /coolant thermal relay failure so checked and found Coolant pump and motor failure so replaced with new one then restore wtg. | Close | 0.25641 | G27 | 4914.5833 | None | WTG Breakdown Maintenance | 11795 | 4914.5833
659 | 2025-05-30 | 2025 | 2025 | 2025-05-01 | Year_3 | G28 | PWEGPL | MSEDCL | 2.564% | 800 | Pitch Drive Error | BD | 10:15 | 10:56 | 12:05 | 0.68333 | 1.15 | 1.8333 | Checked releated circuit found proportional valve failure so replaced with new one then restore wtg. | Close | 0.047009 | G30 | 900.3194 | None | WTG Breakdown Maintenance | 11786 | 900.3194
660 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 17177.0632 | None | WTG Force Majeaure | 17189 | 17177.0632
661 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 17177.0632 | None | WTG Force Majeaure | 17189 | 17177.0632
662 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | Year_3 | G12 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM | 11:10 | 11:10 | 18:16 | 0 | 7.1 | 7.1 | HYPM done then then restore wtg. | Close | 0.18205 | G13 | 7959.6917 | None | WTG Scheduled Maintenance | 26906 | 7959.6917
663 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | Year_3 | G05 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD | 12:45 | 13:40 | 13:42 | 0.91667 | 0.033333 | 0.95 | Reset then restore wtg. | Close | 0.024359 | G22 | 679.5271 | None | WTG Breakdown Maintenance | 17167 | 679.5271
664 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | Year_3 | G21 | PWEGPL | MSEDCL | 2.564% | 5219 | Coolant Of The Coolant Circuit Failure | BD | 12:45 | 13:00 | 14:20 | 0.25 | 1.3333 | 1.5833 | Checked related circuit found ok then restore wtg. | Close | 0.040598 | G22 | 1132.5451 | None | WTG Breakdown Maintenance | 17167 | 1132.5451
665 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | Year_3 | G22 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD | 12:45 | 13:10 | 13:12 | 0.41667 | 0.033333 | 0.45 | Reset then restore wtg. | Close | 0.011538 | G21 | 320.9063 | None | WTG Breakdown Maintenance | 17115 | 320.9063
666 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | Year_3 | G23 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD | 12:45 | 13:30 | 13:32 | 0.75 | 0.033333 | 0.78333 | Reset then restore wtg. | Close | 0.020085 | G05 | 558.3208 | None | WTG Breakdown Maintenance | 17106 | 558.3208
667 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | Year_3 | G25 | PWEGPL | MSEDCL | 2.564% | 5203 | Heating/Coolant Thermal Magnetic Failure | BD | 4:30 | 5:20 | 5:22 | 0.83333 | 0.033333 | 0.86667 | Reset then restore wtg. | Close | 0.022222 | G27 | 620.75 | None | WTG Breakdown Maintenance | 17190 | 620.75
668 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | Year_3 | G25 | PWEGPL | MSEDCL | 2.564% | 5203 | Heating/Coolant Thermal Magnetic Failure | BD | 9:47 | 11:44 | 14:40 | 1.95 | 2.9333 | 4.8833 | Checked related circuit found Coolant motor failure so replaced with new one then restore wtg. | Close | 0.12521 | G27 | 3497.6875 | None | WTG Breakdown Maintenance | 17190 | 3497.6875
669 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | Year_3 | G26 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 8:40 | 9:22 | 13:35 | 0.7 | 4.2167 | 4.9167 | Slip ring clean then restore wtg. | Close | 0.12607 | G32 | 3656.9757 | None | WTG Breakdown Maintenance | 17851 | 3656.9757
670 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | Year_3 | G26 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 14:25 | 14:35 | 16:20 | 0.16667 | 1.75 | 1.9167 | Checked related circuit found cab module malfunction so interchange then restore wtg. | Close | 0.049145 | G32 | 1425.6007 | None | WTG Breakdown Maintenance | 17851 | 1425.6007
671 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | Year_3 | G26 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 17:01 | 17:01 | 19:30 | 0 | 2.4833 | 2.4833 | Checked related circuit found slip ring TB damage so replaced TB then reconnection done then restore wtg. | Close | 0.063675 | G32 | 1847.0826 | None | WTG Breakdown Maintenance | 17851 | 1847.0826
672 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | Year_3 | G27 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD | 11:38 | 12:05 | 12:06 | 0.45 | 0.016667 | 0.46667 | Reset then restore wtg. | Close | 0.011966 | G25 | 309.1861 | None | WTG Breakdown Maintenance | 15901 | 309.1861
673 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | Year_3 | G28 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD | 11:38 | 12:30 | 12:31 | 0.86667 | 0.016667 | 0.88333 | Reset then restore wtg. | Close | 0.02265 | G30 | 632.7611 | None | WTG Breakdown Maintenance | 17192 | 632.7611
674 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | Year_3 | G35 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD | 11:38 | 12:45 | 12:46 | 1.1167 | 0.016667 | 1.1333 | Reset then restore wtg. | Close | 0.02906 | G36 | 816.9444 | None | WTG Breakdown Maintenance | 17300 | 816.9444
675 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | Year_3 | G35 | PWEGPL | MSEDCL | 2.564% | 5210 | Failure Of The Contactor's Rotor Power | BD | 15:10 | 16:01 | 16:02 | 0.85 | 0.016667 | 0.86667 | Reset then restore wtg. | Close | 0.022222 | G36 | 624.7222 | None | WTG Breakdown Maintenance | 17300 | 624.7222
676 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | Year_3 | G36 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD | 11:38 | 13:10 | 13:11 | 1.5333 | 0.016667 | 1.55 | Reboot then restore wtg. | Close | 0.039744 | G37 | 1152.1021 | None | WTG Breakdown Maintenance | 17839 | 1152.1021
677 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | Year_3 | G38 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD | 11:38 | 13:30 | 13:31 | 1.8667 | 0.016667 | 1.8833 | Reset then restore wtg. | Close | 0.048291 | G39 | 1400.8861 | None | WTG Breakdown Maintenance | 17852 | 1400.8861
678 | 2025-06-01 | 2025 | 2025 | 2025-06-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 19238.6306 | None | WTG Force Majeaure | 19252 | 19238.6306
679 | 2025-06-01 | 2025 | 2025 | 2025-06-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 19238.6306 | None | WTG Force Majeaure | 19252 | 19238.6306
680 | 2025-06-01 | 2025 | 2025 | 2025-06-01 | Year_3 | G09 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM | 11:15 | 11:15 | 18:10 | 0 | 6.9167 | 6.9167 | HYPM done then then restore wtg. | Close | 0.17735 | G12 | 6662.7674 | None | WTG Scheduled Maintenance | 23119 | 6662.7674
681 | 2025-06-01 | 2025 | 2025 | 2025-06-01 | Year_3 | G22 | PWEGPL | MSEDCL | 2.564% | 5210 | Failure Of The Contactor's Rotor Power | BD | 12:33 | 13:01 | 13:02 | 0.46667 | 0.016667 | 0.48333 | Reset then restore wtg. | Close | 0.012393 | G21 | 387.5326 | None | WTG Breakdown Maintenance | 19243 | 387.5326
682 | 2025-06-01 | 2025 | 2025 | 2025-06-01 | Year_3 | G23 | PWEGPL | MSEDCL | 2.564% | 5210 | Failure Of The Contactor's Rotor Power | BD | 12:33 | 13:15 | 13:16 | 0.7 | 0.016667 | 0.71667 | Reset then restore wtg. | Close | 0.018376 | G05 | 574.0201 | None | WTG Breakdown Maintenance | 19223 | 574.0201
683 | 2025-06-01 | 2025 | 2025 | 2025-06-01 | Year_3 | G25 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD | 12:33 | 13:10 | 13:11 | 0.61667 | 0.016667 | 0.63333 | Reset then restore wtg. | Close | 0.016239 | G27 | 507.8542 | None | WTG Breakdown Maintenance | 19245 | 507.8542
684 | 2025-06-02 | 2025 | 2025 | 2025-06-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 10259.8701 | None | WTG Force Majeaure | 10267 | 10259.8701
685 | 2025-06-02 | 2025 | 2025 | 2025-06-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 10259.8701 | None | WTG Force Majeaure | 10267 | 10259.8701
686 | 2025-06-02 | 2025 | 2025 | 2025-06-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD | 10:30 | 11:04 | 13:20 | 0.56667 | 2.2667 | 2.8333 | Checked related circuit found HU hose failure so replaced with new one then restore wtg. | Close | 0.07265 | G03 | 1228.0139 | None | WTG Breakdown Maintenance | 10402 | 1228.0139
687 | 2025-06-02 | 2025 | 2025 | 2025-06-01 | Year_3 | G08 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM | 11:20 | 11:20 | 17:45 | 0 | 6.4167 | 6.4167 | HYPM done then then restore wtg. | Close | 0.16453 | G03 | 2781.0903 | None | WTG Scheduled Maintenance | 10402 | 2781.0903
688 | 2025-06-02 | 2025 | 2025 | 2025-06-01 | Year_3 | G20 | PWEGPL | MSEDCL | 2.564% | 5203 | Heating/Coolant Thermal Magnetic Failure | BD | 18:55 | 19:38 | 21:01 | 0.71667 | 1.3833 | 2.1 | Checked related circuit found ccU coolant cooling motor failure so replaced with new one then restore wtg. then start wtg. | Close | 0.053846 | G19 | 1073.3625 | None | WTG Breakdown Maintenance | 12267 | 1073.3625
689 | 2025-06-02 | 2025 | 2025 | 2025-06-01 | Year_3 | G33 | PWEGPL | MSEDCL | 2.564% | CE100008 | General Work Stoppage | Manual stop | 11:27 | 11:27 | 12:30 | 0 | 1.05 | 1.05 | Manual stop for HYPM pending point rectification and radaitor clening work | Close | 0.026923 | G34 | 398.5188 | None | WTG Unscheduled Maintenance | 9109 | 398.5188
690 | 2025-06-02 | 2025 | 2025 | 2025-06-01 | Year_3 | G35 | PWEGPL | MSEDCL | 2.564% | CE100008 | General Work Stoppage | Manual stop | 13:05 | 13:05 | 14:02 | 0 | 0.95 | 0.95 | Manual stop for HYPM pending piont rectification work | Close | 0.024359 | G36 | 360.6438 | None | WTG Unscheduled Maintenance | 9111 | 360.6438
691 | 2025-06-02 | 2025 | 2025 | 2025-06-01 | Year_3 | G33 | PWEGPL | MSEDCL | 2.564% | 509 | Generator Slipping Ring High Temperature | BD | 17:45 | 18:12 | 18:13 | 0.45 | 0.016667 | 0.46667 | Reset then restore wtg. | Close | 0.011966 | G34 | 177.1194 | None | WTG Breakdown Maintenance | 9109 | 177.1194
692 | 2025-06-03 | 2025 | 2025 | 2025-06-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 18263.3083 | None | WTG Force Majeaure | 18276 | 18263.3083
693 | 2025-06-03 | 2025 | 2025 | 2025-06-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | G28 | 18263.3083 | None | WTG Force Majeaure | 18276 | 18263.3083
694 | 2025-06-03 | 2025 | 2025 | 2025-06-01 | Year_3 | G11 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD | 10:21 | 12:11 | 12:12 | 1.8333 | 0.016667 | 1.85 | Reset then restore wtg. | Close | 0.047436 | G10 | 1639.4083 | None | WTG Breakdown Maintenance | 21268 | 1639.4083
695 | 2025-06-03 | 2025 | 2025 | 2025-06-01 | Year_3 | G11 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | Manual stop | 12:12 | 12:12 | 18:30 | 0 | 6.3 | 6.3 | HYPM done then then restore wtg. | Close | 0.16154 | G10 | 5582.85 | None | WTG Scheduled Maintenance | 21268 | 5582.85
696 | 2025-06-03 | 2025 | 2025 | 2025-06-01 | Year_3 | G19 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 11:20 | 11:37 | 11:39 | 0.28333 | 0.033333 | 0.31667 | Reboot then restore wtg. | Close | 0.0081197 | G18 | 285.7521 | None | WTG Breakdown Maintenance | 21657 | 285.7521
697 | 2025-06-03 | 2025 | 2025 | 2025-06-01 | Year_3 | G20 | PWEGPL | MSEDCL | 2.564% | 5203 | Heating/Coolant Thermal Magnetic Failure | BD | 9:45 | 11:01 | 12:12 | 1.2667 | 1.1833 | 2.45 | Checked releated circuit found MPCB failure so replaced with new one then restore wtg. | Close | 0.062821 | G18 | 2210.8187 | None | WTG Breakdown Maintenance | 21657 | 2210.8187
698 | 2025-06-03 | 2025 | 2025 | 2025-06-01 | Year_3 | G35 | PWEGPL | MSEDCL | 2.564% | 118 | Yaw Motors Error | BD | 14:45 | 15:30 | 16:15 | 0.75 | 0.75 | 1.5 | Checked related circuit found losse connection in yaw sensor so tight it then restore wtg. | Close | 0.038462 | G36 | 1127.3125 | None | WTG Breakdown Maintenance | 18037 | 1127.3125
699 | 2025-06-03 | 2025 | 2025 | 2025-06-01 | Year_3 | G39 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD | 15:45 | 16:30 | 16:31 | 0.75 | 0.016667 | 0.76667 | Reset then restore wtg. | Close | 0.019658 | G40 | 577.4278 | None | WTG Breakdown Maintenance | 18076 | 577.4278
700 | 2025-06-04 | 2025 | 2025 | 2025-06-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | G28 | 2355.9727 | None | WTG Force Majeaure | 2356 | 2355.9727
701 | 2025-06-04 | 2025 | 2025 | 2025-06-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | G28 | 2355.9727 | None | WTG Force Majeaure | 2356 | 2355.9727
702 | 2025-06-04 | 2025 | 2025 | 2025-06-01 | Year_3 | G27 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop | 11:15 | 11:15 | 12:10 | 0 | 0.91667 | 0.91667 | Manual stop for HYPM pending piont rectification work | Close | 0.023504 | G25 | 90.3299 | None | WTG Unscheduled Maintenance | 2365 | 90.3299
703 | 2025-06-04 | 2025 | 2025 | 2025-06-01 | Year_3 | G34 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop | 11:18 | 11:18 | 12:10 | 0 | 0.86667 | 0.86667 | Manual stop for HYPM pending piont rectification work | Close | 0.022222 | G34 | 110.2833 | None | WTG Unscheduled Maintenance | 3054 | 110.2833
704 | 2025-06-04 | 2025 | 2025 | 2025-06-01 | Year_3 | G21 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD | 20:55 | 21:15 | 21:16 | 0.33333 | 0.016667 | 0.35 | Reset then restore wtg. | Close | 0.0089744 | G22 | 34.3583 | None | WTG Breakdown Maintenance | 2356 | 34.3583
705 | 2025-06-04 | 2025 | 2025 | 2025-06-01 | Year_3 | G23 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD | 20:55 | 21:30 | 21:31 | 0.58333 | 0.016667 | 0.6 | Reset then restore wtg. | Close | 0.015385 | G22 | 58.9 | None | WTG Breakdown Maintenance | 2356 | 58.9
706 | 2025-06-04 | 2025 | 2025 | 2025-06-01 | Year_3 | G27 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD | 20:55 | 21:45 | 21:46 | 0.83333 | 0.016667 | 0.85 | Reset then restore wtg. | Close | 0.021795 | G25 | 83.7604 | None | WTG Breakdown Maintenance | 2365 | 83.7604
707 | 2025-06-04 | 2025 | 2025 | 2025-06-01 | Year_3 | G25 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD | 20:55 | 21:50 | 21:51 | 0.91667 | 0.016667 | 0.93333 | Reset then restore wtg. | Close | 0.023932 | G27 | 91.8556 | None | WTG Breakdown Maintenance | 2362 | 91.8556
708 | 2025-06-04 | 2025 | 2025 | 2025-06-01 | Year_3 | G28 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD | 20:55 | 22:00 | 22:01 | 1.0833 | 0.016667 | 1.1 | Reset then restore wtg. | Close | 0.028205 | G30 | 108.7167 | None | WTG Breakdown Maintenance | 2372 | 108.7167
709 | 2025-06-05 | 2025 | 2025 | 2025-06-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | G28 | 6855.9206 | None | WTG Force Majeaure | 6856 | 6855.9206
710 | 2025-06-05 | 2025 | 2025 | 2025-06-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | G28 | 6855.9206 | None | WTG Force Majeaure | 6856 | 6855.9206
711 | 2025-06-05 | 2025 | 2025 | 2025-06-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 11:01 | 11:38 | 12:07 | 0.61667 | 0.48333 | 1.1 | Slip ring clean then restore wtg. | Close | 0.028205 | G03 | 413.1875 | None | WTG Breakdown Maintenance | 9015 | 413.1875
712 | 2025-06-05 | 2025 | 2025 | 2025-06-01 | Year_3 | G06 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM | 11:27 | 11:27 | 18:20 | 0 | 6.8833 | 6.8833 | HYPM done then then restore wtg. | Close | 0.1765 | G03 | 2585.5521 | None | WTG Scheduled Maintenance | 9015 | 2585.5521
713 | 2025-06-05 | 2025 | 2025 | 2025-06-01 | Year_3 | G11 | PWEGPL | MSEDCL | 2.564% | 116 | Orienting and High Yaw Brake Pressure | BD | 16:58 | 17:29 | 17:30 | 0.51667 | 0.016667 | 0.53333 | Reset then restore wtg. | Close | 0.013675 | G10 | 200.4222 | None | WTG Breakdown Maintenance | 9019 | 200.4222
714 | 2025-06-05 | 2025 | 2025 | 2025-06-01 | Year_3 | G14 | PWEGPL | MSEDCL | 2.564% | 116 | Orienting and High Yaw Brake Pressure | BD | 11:15 | 11:32 | 11:33 | 0.28333 | 0.016667 | 0.3 | Reset then restore wtg. | Close | 0.0076923 | G15 | 100.2625 | None | WTG Breakdown Maintenance | 8021 | 100.2625
715 | 2025-06-05 | 2025 | 2025 | 2025-06-01 | Year_3 | G19 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 15:30 | 15:50 | 16:20 | 0.33333 | 0.5 | 0.83333 | Slip ring clean then restore wtg. | Close | 0.021368 | G18 | 278.4375 | None | WTG Breakdown Maintenance | 8019 | 278.4375
716 | 2025-06-05 | 2025 | 2025 | 2025-06-01 | Year_3 | G36 | PWEGPL | MSEDCL | 2.564% | CE100008 | General Work Stoppage | Manual stop | 12:15 | 12:15 | 13:45 | 0 | 1.5 | 1.5 | Manual stop for HYPM pending piont rectification work | Close | 0.038462 | G35 | 389.5 | None | WTG Unscheduled Maintenance | 6232 | 389.5
717 | 2025-06-05 | 2025 | 2025 | 2025-06-01 | Year_3 | G37 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 11:00 | 11:27 | 12:05 | 0.45 | 0.63333 | 1.0833 | Slip ring clean then restore wtg. | Close | 0.027778 | G36 | 252.2813 | None | WTG Breakdown Maintenance | 5589 | 252.2813
718 | 2025-06-06 | 2025 | 2025 | 2025-06-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | G28 | 9361.8916 | None | WTG Force Majeaure | 9362 | 9361.8916
719 | 2025-06-06 | 2025 | 2025 | 2025-06-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | G28 | 9361.8916 | None | WTG Force Majeaure | 9362 | 9361.8916
720 | 2025-06-06 | 2025 | 2025 | 2025-06-01 | Year_3 | G03 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM | 11:36 | 11:36 | 18:12 | 0 | 6.6 | 6.6 | HYPM done then then restore wtg. | Close | 0.16923 | G04 | 4016.65 | None | WTG Scheduled Maintenance | 14606 | 4016.65
721 | 2025-06-06 | 2025 | 2025 | 2025-06-01 | Year_3 | G14 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop | 10:50 | 10:50 | 11:45 | 0 | 0.91667 | 0.91667 | Manual stop for repeated error found valve malfunction so replaced with new one then restore wtg. | Close | 0.023504 | G15 | 490.6076 | None | WTG Breakdown Maintenance | 12845 | 490.6076
722 | 2025-06-06 | 2025 | 2025 | 2025-06-01 | Year_3 | G37 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD | 17:30 | 18:01 | 21:29 | 0.51667 | 3.4667 | 3.9833 | Checked related circuit found oil leakage from Blade C Accumulator so replaced with new one then N2 refilling done then restore wtg. | Close | 0.10214 | G36 | 1291.2639 | None | WTG Unscheduled Maintenance | 7780 | 1291.2639
723 | 2025-06-07 | 2025 | 2025 | 2025-06-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | G28 | 12589.8543 | None | WTG Force Majeaure | 12590 | 12589.8543
724 | 2025-06-07 | 2025 | 2025 | 2025-06-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | G28 | 12589.8543 | None | WTG Force Majeaure | 12590 | 12589.8543
725 | 2025-06-07 | 2025 | 2025 | 2025-06-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM | 11:10 | 11:10 | 18:05 | 0 | 6.9167 | 6.9167 | HYPM done then then restore wtg. | Close | 0.17735 | G03 | 5708.8437 | None | WTG Scheduled Maintenance | 19809 | 5708.8437
726 | 2025-06-07 | 2025 | 2025 | 2025-06-01 | Year_3 | G28 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop | 11:09 | 11:09 | 13:35 | 0 | 2.4333 | 2.4333 | Manual stop for HYPM pending piont rectification work | Close | 0.062393 | G30 | 1271.6194 | None | WTG Unscheduled Maintenance | 12542 | 1271.6194
727 | 2025-06-07 | 2025 | 2025 | 2025-06-01 | Year_3 | G30 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop | 14:24 | 14:24 | 16:20 | 0 | 1.9333 | 1.9333 | Manual stop for HYPM pending piont rectification work | Close | 0.049573 | G28 | 1014.1944 | None | WTG Unscheduled Maintenance | 12590 | 1014.1944
728 | 2025-06-08 | 2025 | 2025 | 2025-06-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | G28 | 12124.8597 | None | WTG Force Majeaure | 12125 | 12124.8597
729 | 2025-06-08 | 2025 | 2025 | 2025-06-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | G28 | 12124.8597 | None | WTG Force Majeaure | 12125 | 12124.8597
730 | 2025-06-08 | 2025 | 2025 | 2025-06-01 | Year_3 | G21 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD | 21:05 | 21:18 | 21:19 | 0.21667 | 0.016667 | 0.23333 | Reset then restore wtg. | Close | 0.0059829 | G22 | 116.8125 | None | WTG Breakdown Maintenance | 12015 | 116.8125
731 | 2025-06-08 | 2025 | 2025 | 2025-06-01 | Year_3 | G22 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD | 21:05 | 21:15 | 21:16 | 0.16667 | 0.016667 | 0.18333 | Reset then restore wtg. | Close | 0.0047009 | G23 | 91.6743 | None | WTG Breakdown Maintenance | 12001 | 91.6743
732 | 2025-06-08 | 2025 | 2025 | 2025-06-01 | Year_3 | G25 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD | 21:05 | 21:35 | 21:36 | 0.5 | 0.016667 | 0.51667 | Reset then restore wtg. | Close | 0.013248 | G27 | 260.9382 | None | WTG Breakdown Maintenance | 12121 | 260.9382
733 | 2025-06-08 | 2025 | 2025 | 2025-06-01 | Year_3 | G28 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD | 21:05 | 21:48 | 21:49 | 0.71667 | 0.016667 | 0.73333 | Reset then restore wtg. | Close | 0.018803 | G30 | 370.7 | None | WTG Breakdown Maintenance | 12132 | 370.7
734 | 2025-06-08 | 2025 | 2025 | 2025-06-01 | Year_3 | G30 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD | 21:05 | 21:55 | 21:56 | 0.83333 | 0.016667 | 0.85 | Reset then restore wtg. | Close | 0.021795 | G28 | 429.4271 | None | WTG Breakdown Maintenance | 12125 | 429.4271
735 | 2025-06-09 | 2025 | 2025 | 2025-06-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | G28 | 23433.7288 | None | WTG Force Majeaure | 23434 | 23433.7288
736 | 2025-06-09 | 2025 | 2025 | 2025-06-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | G28 | 23433.7288 | None | WTG Force Majeaure | 23434 | 23433.7288
737 | 2025-06-09 | 2025 | 2025 | 2025-06-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 17:45 | 18:10 | 18:12 | 0.41667 | 0.033333 | 0.45 | Reboot then restore wtg. | Close | 0.011538 | G03 | 463.9312 | None | WTG Breakdown Maintenance | 24743 | 463.9312
738 | 2025-06-09 | 2025 | 2025 | 2025-06-01 | Year_3 | G12 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD | 11:30 | 11:55 | 13:10 | 0.41667 | 1.25 | 1.6667 | Checked related coircuit found HU main accumulator pressure low so refilled N2 then restore wtg. | Close | 0.042735 | G13 | 1517.7778 | None | WTG Breakdown Maintenance | 21856 | 1517.7778
739 | 2025-06-09 | 2025 | 2025 | 2025-06-01 | Year_3 | G14 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 16:05 | 16:30 | 16:32 | 0.41667 | 0.033333 | 0.45 | Reboot then restore wtg. | Close | 0.011538 | G13 | 409.8 | None | WTG Breakdown Maintenance | 21856 | 409.8
740 | 2025-06-09 | 2025 | 2025 | 2025-06-01 | Year_3 | G20 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 10:45 | 11:11 | 12:05 | 0.43333 | 0.9 | 1.3333 | Slip ring clean then restore wtg. | Close | 0.034188 | G19 | 1215.4444 | None | WTG Breakdown Maintenance | 21878 | 1215.4444
741 | 2025-06-09 | 2025 | 2025 | 2025-06-01 | Year_3 | G30 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD | 17:00 | 17:25 | 18:20 | 0.41667 | 0.91667 | 1.3333 | Inspection done then restore wtg. | Close | 0.034188 | G28 | 1301.8889 | None | WTG Breakdown Maintenance | 23434 | 1301.8889
742 | 2025-06-09 | 2025 | 2025 | 2025-06-01 | Year_3 | G39 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD | 10:42 | 11:24 | 12:30 | 0.7 | 1.1 | 1.8 | Checked related circuit found KR003 relay in loose condition so tight it then restore wtg | Close | 0.046154 | G40 | 1510.875 | None | WTG Breakdown Maintenance | 20145 | 1510.875
743 | 2025-06-09 | 2025 | 2025 | 2025-06-01 | Year_3 | G27 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 14:05 | 14:05 | 17:15 | 0 | 3.1667 | 3.1667 | Manual stop for Blade bush gap inspection work | Close | 0.081197 | G25 | 3090.2708 | None | WTG Force Majeaure | 23421 | 3090.2708
744 | 2025-06-10 | 2025 | 2025 | 2025-06-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | G28 | 12688.8531 | None | WTG Force Majeaure | 12689 | 12688.8531
745 | 2025-06-10 | 2025 | 2025 | 2025-06-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | G28 | 12688.8531 | None | WTG Force Majeaure | 12689 | 12688.8531
746 | 2025-06-10 | 2025 | 2025 | 2025-06-01 | Year_3 | G02 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM | 11:55 | 11:55 | 18:44 | 0 | 6.8167 | 6.8167 | HYPM done then then restore wtg. | Close | 0.17479 | G04 | 3787.5104 | None | WTG Scheduled Maintenance | 13335 | 3787.5104
747 | 2025-06-10 | 2025 | 2025 | 2025-06-01 | Year_3 | G14 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD | 15:30 | 16:05 | 19:50 | 0.58333 | 3.75 | 4.3333 | Checked related circuit found PRV -8 Valve failure so replaced with new one then restore wtg. | Close | 0.11111 | G13 | 4033.9722 | None | WTG Breakdown Maintenance | 22342 | 4033.9722
748 | 2025-06-10 | 2025 | 2025 | 2025-06-01 | Year_3 | G15 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop | 16:15 | 16:15 | 17:50 | 0 | 1.5833 | 1.5833 | Manual stop for yaw abnormal sound rectification work | Close | 0.040598 | G16 | 1419.8542 | None | WTG Unscheduled Maintenance | 21522 | 1419.8542
749 | 2025-06-10 | 2025 | 2025 | 2025-06-01 | Year_3 | G16 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop | 11:28 | 11:28 | 12:50 | 0 | 1.3667 | 1.3667 | Manual stop for yaw abnormal sound rectification work | Close | 0.035043 | G17 | 1271.0569 | None | WTG Unscheduled Maintenance | 22321 | 1271.0569
750 | 2025-06-10 | 2025 | 2025 | 2025-06-01 | Year_3 | G20 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 11:50 | 12:20 | 14:23 | 0.5 | 2.05 | 2.55 | checked related circuit found loose connection so tight it then apply sealant then restore wtg. | Close | 0.065385 | G19 | 2374.1562 | None | WTG Breakdown Maintenance | 22345 | 2374.1562
751 | 2025-06-10 | 2025 | 2025 | 2025-06-01 | Year_3 | G23 | PWEGPL | MSEDCL | 2.564% | 502 | Generator NDE Bearing High Temperature Alarm | BD | 9:35 | 11:48 | 14:10 | 2.2167 | 2.3667 | 4.5833 | Replaced lift guide clamp then checked related circuit found generator carbon brush wear out and spring damage so replaced with new one then restore wtg. | Close | 0.11752 | G05 | 2411.7882 | None | WTG Breakdown Maintenance | 12629 | 2411.7882
752 | 2025-06-11 | 2025 | 2025 | 2025-06-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | G28 | 14453.8327 | None | WTG Force Majeaure | 14454 | 14453.8327
753 | 2025-06-11 | 2025 | 2025 | 2025-06-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | G28 | 14453.8327 | None | WTG Force Majeaure | 14454 | 14453.8327
754 | 2025-06-11 | 2025 | 2025 | 2025-06-01 | Year_3 | G02 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD | 16:45 | 17:27 | 17:28 | 0.7 | 0.016667 | 0.71667 | Reset then restore wtg. | Close | 0.018376 | G03 | 535.0813 | None | WTG Breakdown Maintenance | 17919 | 535.0813
755 | 2025-06-11 | 2025 | 2025 | 2025-06-01 | Year_3 | G03 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD | 16:45 | 17:07 | 17:08 | 0.36667 | 0.016667 | 0.38333 | Reset then restore wtg. | Close | 0.0098291 | G04 | 286.1104 | None | WTG Breakdown Maintenance | 17913 | 286.1104
756 | 2025-06-11 | 2025 | 2025 | 2025-06-01 | Year_3 | G04 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD | 16:45 | 17:14 | 17:15 | 0.48333 | 0.016667 | 0.5 | Reset then restore wtg. | Close | 0.012821 | G03 | 373.3125 | None | WTG Breakdown Maintenance | 17919 | 373.3125
757 | 2025-06-11 | 2025 | 2025 | 2025-06-01 | Year_3 | G06 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD | 16:45 | 17:01 | 17:02 | 0.26667 | 0.016667 | 0.28333 | Reset then restore wtg. | Close | 0.007265 | G03 | 211.5438 | None | WTG Breakdown Maintenance | 17919 | 211.5438
758 | 2025-06-11 | 2025 | 2025 | 2025-06-01 | Year_3 | G07 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM | 10:44 | 10:44 | 18:45 | 0 | 8.0167 | 8.0167 | HYPM done then then restore wtg. | Close | 0.20556 | G01 | 5982.7715 | None | WTG Scheduled Maintenance | 17911 | 5982.7715
759 | 2025-06-11 | 2025 | 2025 | 2025-06-01 | Year_3 | G10 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD | 16:45 | 18:10 | 18:11 | 1.4167 | 0.016667 | 1.4333 | Reset then restore wtg. | Close | 0.036752 | G11 | 1071.2972 | None | WTG Breakdown Maintenance | 17938 | 1071.2972
760 | 2025-06-11 | 2025 | 2025 | 2025-06-01 | Year_3 | G16 | PWEGPL | MSEDCL | 2.564% | 116 | Orienting and High Yaw Brake Pressure | BD | 16:30 | 17:15 | 17:16 | 0.75 | 0.016667 | 0.76667 | Reset then restore wtg. | Close | 0.019658 | G17 | 304.7181 | None | WTG Breakdown Maintenance | 9539 | 304.7181
761 | 2025-06-11 | 2025 | 2025 | 2025-06-01 | Year_3 | G32 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD | 17:10 | 17:59 | 18:02 | 0.81667 | 0.05 | 0.86667 | Reboot then restore wtg. | Close | 0.022222 | G26 | 437.3417 | None | WTG Breakdown Maintenance | 12111 | 437.3417
762 | 2025-06-12 | 2025 | 2025 | 2025-06-01 | Year_3 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | G28 | 9861.8859 | None | WTG Force Majeaure | 9862 | 9861.8859
763 | 2025-06-12 | 2025 | 2025 | 2025-06-01 | Year_3 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | G28 | 9861.8859 | None | WTG Force Majeaure | 9862 | 9861.8859
764 | 2025-06-12 | 2025 | 2025 | 2025-06-01 | Year_3 | G01 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM | 10:59 | 10:59 | 18:20 | 0 | 7.35 | 7.35 | HYPM done then then restore wtg. | Close | 0.18846 | G07 | 4572.6187 | None | WTG Scheduled Maintenance | 14931 | 4572.6187
765 | 2025-06-12 | 2025 | 2025 | 2025-06-01 | Year_3 | G40 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop | 11:45 | 11:45 | 12:32 | 0 | 0.78333 | 0.78333 | Manual stop for HYPM pending point rectification work | Close | 0.020085 | G39 | 292.575 | None | WTG Unscheduled Maintenance | 8964 | 292.575
766 | 2025-06-12 | 2025 | 2025 | 2025-06-01 | Year_3 | G12 | PWEGPL | MSEDCL | 2.564% | 550 | Generator Fans Thermal Relay Triggered Too Long | BD | 22:35 | 23:22 | 23:55 | 0.78333 | 0.55 | 1.3333 | Checked related circuit found cable connection loose so tight it then restore wtg | Close | 0.034188 | G13 | 707.6667 | None | WTG Breakdown Maintenance | 12738 | 707.6667
767 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
768 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
769 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
770 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
771 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
772 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
773 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
774 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
775 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
776 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
777 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
778 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
779 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
780 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
781 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
782 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
783 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
784 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
785 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
786 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
787 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
788 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
789 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
790 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
791 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
792 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
793 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
794 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
795 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
796 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
797 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
798 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
799 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
800 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
801 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
802 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
803 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
804 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
805 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
806 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
807 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
808 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
809 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
810 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
811 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
812 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
813 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
814 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
815 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
816 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
817 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
818 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
819 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
820 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
821 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
822 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
823 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
824 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
825 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
826 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
827 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
828 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
829 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
830 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
831 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
832 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
833 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
834 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
835 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
836 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
837 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
838 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
839 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
840 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
841 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
842 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
843 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
844 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
845 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
846 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
847 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
848 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
849 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
850 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
851 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
852 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
853 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
854 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
855 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
856 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
857 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
858 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
859 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
860 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
861 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
862 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
863 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
864 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
865 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
866 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
867 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
868 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
869 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
870 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
871 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
872 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
873 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
874 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
875 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
876 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
877 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
878 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
879 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
880 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
881 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
882 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
883 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
884 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
885 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
886 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
887 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
888 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
889 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
890 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
891 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
892 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
893 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
894 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
895 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
896 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
897 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
898 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
899 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
900 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
901 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
902 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
903 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
904 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
905 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
906 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
907 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
908 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
909 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
910 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
911 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
912 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
913 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
914 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
915 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
916 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
917 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
918 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
919 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
920 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
921 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
922 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
923 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
924 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
925 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
926 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
927 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
928 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
929 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
930 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
931 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
932 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
933 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
934 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
935 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
936 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
937 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
938 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
939 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
940 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
941 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
942 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
943 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
944 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
945 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
946 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
947 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
948 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
949 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
950 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
951 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
952 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
953 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
954 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
955 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
956 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
957 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
958 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
959 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
960 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
961 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
962 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
963 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
964 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
965 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
966 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
967 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
968 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
969 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
970 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
971 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
972 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
973 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
974 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
975 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
976 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
977 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
978 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
979 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
980 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
981 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
982 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
983 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
984 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
985 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
986 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
987 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
988 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
989 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
990 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
991 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
992 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
993 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
994 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
995 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
996 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
997 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
998 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
999 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1000 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1001 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1002 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1003 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1004 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1005 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1006 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1007 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1008 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1009 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1010 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1011 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1012 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1013 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1014 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1015 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1016 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1017 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1018 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1019 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1020 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1021 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1022 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1023 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1024 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1025 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1026 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1027 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1028 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1029 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1030 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1031 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1032 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1033 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1034 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1035 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1036 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1037 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1038 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1039 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1040 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1041 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1042 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1043 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1044 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1045 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1046 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1047 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1048 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1049 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1050 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1051 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1052 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1053 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1054 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1055 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1056 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1057 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
1058 |  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
|  |  |  | 1899-12-31 | [6 empty] | #N/A | [5 empty] | 0 | 0 |  |  | 0 | [5 empty] | 0
Formulas:
Month = [Date]-DAY([Date])+1

## WTG Reactive Power
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44
Date | Financial Year | Calendar Year | Month Year | G01 | G02 | G03 | G04 | G05 | G06 | G07 | G08 | G09 | G10 | G11 | G12 | G13 | G14 | G15 | G16 | G17 | G18 | G19 | G20 | G21 | G22 | G23 | G25 | G26 | G27 | G28 | G29 | G30 | G31 | G32 | G33 | G34 | G35 | G36 | G37 | G38 | G39 | G40 | Total Reactive Power (kVArh) | Column1
2025-03-29 | 2025 | 2025 | 2025-03-01 | [39 empty] | 0
2025-03-30 | 2025 | 2025 | 2025-03-01 | [39 empty] | 0
2025-03-31 | 2025 | 2025 | 2025-03-01 | 2411.487 | 891.6197 | 1879.9699 | 874.2626 | 880.4713 | 636.2265 | 372.8833 | 641.519 | 906.0887 | 2260.394 | 383.091 | 377.6865 | 2175.7978 | 1993.9216 | 1758.4657 | 2234.1107 | 1964.6707 | 2190.6098 | 441.9792 | 670.5095 | 1570.8376 | 1180.1707 | 1761.4244 | 999.7058 | 1757.046 | 677.2118 | 333.82 | 0 | 1635.0767 | 0 | 1909.0221 | 573.7749 | 742.5826 | 1713.1288 | 1709.3145 | -8.1559 | 2496.8774 | 783.4712 | 2020.958 | 47802.0313
2025-04-01 | 2026 | 2025 | 2025-04-01 | 2322.1235 | 880.1081 | 2078.5867 | 914.5695 | 945.8455 | 637.9924 | 748.219 | 777.1361 | 722.7967 | 2126.2865 | 729.4575 | 657.0716 | 2115.474 | 1806.1052 | 1979.2855 | 2123.0251 | 2192.0195 | 2109.1038 | 708.9222 | 620.7477 | 1738.0668 | 1166.9419 | 1782.3727 | 1210.9576 | 1935.1739 | 703.6288 | 551.5907 | 0 | 1232.2376 | 0 | 1843.691 | 697.056 | 823.1135 | 1362.145 | 1053.6383 | -3.8062 | 2338.3736 | 824.4841 | 1543.8372 | 47998.3787
2025-04-02 | 2026 | 2025 | 2025-04-01 | 2637.2192 | 1097.0692 | 2227.8404 | 923.7416 | 938.2683 | 1297.9406 | 808.4993 | 1289.6567 | 1427.063 | 2544.821 | 855.7841 | 904.2495 | 2402.8842 | 2695.9843 | 2431.9187 | 2122.2456 | 2309.7017 | 3275.5917 | 852.7877 | 1820.6796 | 2426.154 | 491.6329 | 2794.5914 | 1860.9447 | 2885.9037 | 1148.8614 | 1083.9293 | 0 | 2614.3132 | 0 | 823.2844 | 1097.612 | 1182.3387 | 2677.0025 | 2930.4442 | -5.806 | 3280.2777 | 1180.1252 | 2777.1324 | 66112.6877
2025-04-03 | 2026 | 2025 | 2025-04-01 | 2246.2058 | 999.8763 | 2226.0732 | 964.8013 | 886.5267 | 310.4275 | 434.6387 | 696.4918 | 942.5248 | 2164.418 | 725.648 | 756.4623 | 2369.339 | 2369.0812 | 2227.3578 | 2284.8013 | 2242.396 | 2133.4678 | 722.128 | 931.433 | 2229.9002 | 1362.7018 | 2262.5322 | 1064.164 | 2218.1311 | 670.9676 | 487.7805 | 0 | 1891.0717 | 0 | 1266.729 | 571.0981 | 344.8436 | 2159.9289 | 2167.4363 | -0.62418 | 1525.8424 | 613.2425 | 2334.2306 | 51804.0749
2025-04-04 | 2026 | 2025 | 2025-04-01 | 2041.9638 | 388.9551 | 2124.023 | 127.742 | 918.1217 | 83.6738 | 539.6643 | 499.3578 | 465.2299 | 2022.4022 | 707.9753 | 724.6901 | 1884.747 | 2115.7314 | 2050.154 | 111.5131 | 2221.5963 | 2113.498 | 747.0538 | 736.9155 | 2084.2164 | 1478.5472 | 1975.4358 | 888.9653 | 2010.7748 | 476.8457 | 507.5768 | 0 | 2028.1925 | 0 | 1944.1858 | 451.6692 | 93.7413 | 1857.9228 | 2067.6373 | -2.4657 | 2138.7909 | 441.671 | 2200.4018 | 45269.1172
2025-04-05 | 2026 | 2025 | 2025-04-01 | 1876.6226 | 2453.1843 | 1792.9483 | 2211.351 | 1764.4128 | 1666.3205 | 1910.9348 | 2018.7832 | 1635.8613 | 1357.6993 | 1716.0805 | 1716.427 | 1822.3371 | 1593.3717 | 1444.4012 | 0 | 2021.6525 | 2078.9627 | 2082.5695 | 2121.1535 | 2701.0488 | 2515.4811 | 2220.8267 | 1930.8067 | 2949.735 | 1640.4508 | 2557.8496 | 0 | 2950.7668 | 0 | 2629.0589 | 2369.3689 | 2486.7691 | 3025.3162 | 2939.6089 | 3016.1374 | 2372.7201 | 0 | 2927.9752 | 76518.994
2025-04-06 | 2026 | 2025 | 2025-04-01 | 1810.3475 | 373.706 | 2124.0686 | 120.3521 | 0 | 372.111 | 634.795 | 349.298 | 288.821 | 1822.0809 | 624.6403 | 638.458 | 1762.0523 | 1807.978 | 1542.3584 | 0 | 2143.8435 | 1837.3247 | 647.149 | 444.1512 | 2084.2164 | 1478.5472 | 1975.4358 | 888.9653 | 2010.7748 | 476.8457 | 507.5768 | 0 | 2028.1925 | 0 | 1944.1858 | 451.6692 | 93.7413 | 1857.9228 | 2067.6373 | 2145 | 2138.7909 | 441.671 | 2200.4018 | 44135.1102
2025-04-07 | 2026 | 2025 | 2025-04-01 | 1891.7158 | 673.008 | 2044.8962 | 479.9239 | 258.3903 | 586.396 | 540.2957 | 662.5477 | 457.5581 | 2060.9708 | 700.0054 | 762.4624 | 2042.7492 | 2029.6797 | 1694.1446 | 0 | 2094.7339 | 2125.3133 | 720.4764 | 1004.4539 | 944.4695 | 597.1967 | 720.9387 | 16.8658 | 702.9906 | 165.7304 | -68.1872 | 0 | 725.9068 | 0 | 702.3264 | 85.5696 | 155.8761 | 729.0436 | 764.1744 | -1.6386 | 720.3451 | 710 | 759.7323 | 31261.0615
2025-04-08 | 2026 | 2025 | 2025-04-01 | 1910.5437 | 389.2763 | 2048.9178 | -47.8144 | 623.8795 | 358.6271 | 561.9942 | 296.7837 | 178.8487 | 1892.529 | 266.9529 | 603.1785 | 1810.7305 | 1934.8088 | 1567.0379 | 0 | 2093.95 | 2007.1697 | 428.6528 | 384.5257 | 2064.975 | 1452.7388 | 1940.4757 | 51.5167 | 1888.164 | 376.72 | 142.9288 | 0 | 1956.1253 | 0 | 1867.137 | 107.2599 | 385.3045 | 1937.8512 | 2011.0095 | -9.7052 | 2026.7745 | 15.593 | 2099.0948 | 39624.5559
2025-04-09 | 2026 | 2025 | 2025-04-01 | 616.5324 | 137.0467 | 567.342 | 36.0524 | 752.842 | 203.4382 | 198.4896 | 242.9161 | 0 | 437.3383 | 202.867 | 495.0081 | 941.903 | 2566.5919 | 1891.3042 | 427.4053 | 2182.9024 | 2428.2554 | 393.7 | 582.7216 | 2179.2963 | 1444.5757 | 2370.1045 | 687.6252 | 2398.027 | 874.1103 | 818.9967 | 0 | 2465.8407 | 0 | 2208.1021 | 636.8648 | 906.724 | 2368.0593 | 2513.1359 | -4.2376 | 2640.5093 | 0 | 2760.133 | 42572.5238
2025-04-10 | 2026 | 2025 | 2025-04-01 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 0 | 129 | 0 | 129 | 129 | 129 | 129 | 129 | -5 | 129 | 129 | 129 | 4639 | No scada available server OS failed-reading as per billing meter
2025-04-11 | 2026 | 2025 | 2025-04-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-04-12 | 2026 | 2025 | 2025-04-01 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 0 | 99 | 0 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 3663 | No scada available server OS failed-reading as per billing meter
2025-04-13 | 2026 | 2025 | 2025-04-01 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 0 | 129 | 0 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 4773 | No scada available server OS failed-reading as per billing meter
2025-04-14 | 2026 | 2025 | 2025-04-01 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 0 | 129 | 0 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 4773 | No scada available server OS failed-reading as per billing meter
2025-04-15 | 2026 | 2025 | 2025-04-01 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 0 | 129 | 0 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 4773 | No scada available server OS failed-reading as per billing meter
2025-04-16 | 2026 | 2025 | 2025-04-01 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 0 | 97 | 0 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 3589 | No scada available server OS failed-reading as per billing meter
2025-04-17 | 2026 | 2025 | 2025-04-01 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 0 | 97 | 0 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 3589 | No scada available server OS failed-reading as per billing meter
2025-04-18 | 2026 | 2025 | 2025-04-01 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 0 | 194.5946 | 0 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 7200 | No scada available server OS failed-reading as per billing meter
2025-04-19 | 2026 | 2025 | 2025-04-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-04-20 | 2026 | 2025 | 2025-04-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-04-21 | 2026 | 2025 | 2025-04-01 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 0 | 227 | 0 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 8399 | No scada available server OS failed-reading as per billing meter
2025-04-22 | 2026 | 2025 | 2025-04-01 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 0 | 227 | 0 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 8399 | No scada available server OS failed-reading as per billing meter
2025-04-23 | 2026 | 2025 | 2025-04-01 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 194 | 195 | 195 | 193 | 195 | 185 | 195 | 195 | 195 | 0 | 195 | 0 | 193 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 7200 | No scada available server OS failed-reading as per billing meter
2025-04-24 | 2026 | 2025 | 2025-04-01 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 0 | 259 | 0 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 9583 | No scada available server OS failed-reading as per billing meter
2025-04-25 | 2026 | 2025 | 2025-04-01 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 0 | 65 | 0 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 2405 | No scada available server OS failed-reading as per billing meter
2025-04-26 | 2026 | 2025 | 2025-04-01 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 0 | 65 | 0 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 2405 | No scada available server OS failed-reading as per billing meter
2025-04-27 | 2026 | 2025 | 2025-04-01 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 0 | 227 | 0 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 8399 | No scada available server OS failed-reading as per billing meter
2025-04-28 | 2026 | 2025 | 2025-04-01 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 0 | 162 | 0 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 5994 | No scada available server OS failed-reading as per billing meter
2025-04-29 | 2026 | 2025 | 2025-04-01 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 0 | 195 | 0 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 7215 | No scada available server OS failed-reading as per billing meter
2025-04-30 | 2026 | 2025 | 2025-04-01 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 0 | 65 | 0 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 2405 | No scada available server OS failed-reading as per billing meter
2025-05-01 | 2026 | 2025 | 2025-05-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-05-02 | 2026 | 2025 | 2025-05-01 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 0 | 162 | 0 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 5994 | No scada available server OS failed-reading as per billing meter
2025-05-03 | 2026 | 2025 | 2025-05-01 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 0 | 32 | 0 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 1184 | No scada available server OS failed-reading as per billing meter
2025-05-04 | 2026 | 2025 | 2025-05-01 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 0 | 65 | 0 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 2405 | No scada available server OS failed-reading as per billing meter
2025-05-05 | 2026 | 2025 | 2025-05-01 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 0 | 162 | 162 | 0 | 162 | 0 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 5832 | No scada available server OS failed-reading as per billing meter
2025-05-06 | 2026 | 2025 | 2025-05-01 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 72 | 98 | 98 | 0 | 98 | 0 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 3600 | No scada available server OS failed-reading as per billing meter
2025-05-07 | 2026 | 2025 | 2025-05-01 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 0 | 130 | 0 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 4810 | No scada available server OS failed-reading as per billing meter
2025-05-08 | 2026 | 2025 | 2025-05-01 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 0 | 97 | 0 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 3589 | No scada available server OS failed-reading as per billing meter
2025-05-09 | 2026 | 2025 | 2025-05-01 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 0 | 422 | 0 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 15614 | No scada available server OS failed-reading as per billing meter
2025-05-10 | 2026 | 2025 | 2025-05-01 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 0 | 291 | 0 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 10767 | No scada available server OS failed-reading as per billing meter
2025-05-11 | 2026 | 2025 | 2025-05-01 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 0 | 162 | 0 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 5994 | No scada available server OS failed-reading as per billing meter
2025-05-12 | 2026 | 2025 | 2025-05-01 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 0 | 162 | 162 | 0 | 162 | 0 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 5832 | No scada available server OS failed-reading as per billing meter
2025-05-13 | 2026 | 2025 | 2025-05-01 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 0 | 227 | 0 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 8399 | No scada available server OS failed-reading as per billing meter
2025-05-14 | 2026 | 2025 | 2025-05-01 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 0 | 324 | 0 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 0 | 11664 | No scada available server OS failed-reading as per billing meter
2025-05-15 | 2026 | 2025 | 2025-05-01 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 0 | 162 | 0 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 5994 | No scada available server OS failed-reading as per billing meter
2025-05-16 | 2026 | 2025 | 2025-05-01 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 0 | 130 | 0 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 4810 | No scada available server OS failed-reading as per billing meter
2025-05-17 | 2026 | 2025 | 2025-05-01 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 0 | 98 | 0 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 3626 | No scada available server OS failed-reading as per billing meter
2025-05-18 | 2026 | 2025 | 2025-05-01 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 0 | 227 | 0 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 8399 | No scada available server OS failed-reading as per billing meter
2025-05-19 | 2026 | 2025 | 2025-05-01 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 0 | 519 | 0 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 19203 | No scada available server OS failed-reading as per billing meter
2025-05-20 | 2026 | 2025 | 2025-05-01 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 0 | 195 | 0 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 7215 | No scada available server OS failed-reading as per billing meter
2025-05-21 | 2026 | 2025 | 2025-05-01 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 0 | 130 | 0 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 4810 | No scada available server OS failed-reading as per billing meter
2025-05-22 | 2026 | 2025 | 2025-05-01 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 0 | 552 | 0 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 20424 | No scada available server OS failed-reading as per billing meter
2025-05-23 | 2026 | 2025 | 2025-05-01 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 0 | 487 | 0 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 18019 | No scada available server OS failed-reading as per billing meter
2025-05-24 | 2026 | 2025 | 2025-05-01 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 0 | 163 | 0 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 6031 | No scada available server OS failed-reading as per billing meter
2025-05-25 | 2026 | 2025 | 2025-05-01 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 0 | 163 | 0 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 6031 | No scada available server OS failed-reading as per billing meter
2025-05-26 | 2026 | 2025 | 2025-05-01 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 0 | 260 | 0 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 9620 | No scada available server OS failed-reading as per billing meter
2025-05-27 | 2026 | 2025 | 2025-05-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-05-28 | 2026 | 2025 | 2025-05-01 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 0 | 130 | 0 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 4810 | No scada available server OS failed-reading as per billing meter
2025-05-29 | 2026 | 2025 | 2025-05-01 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 33 | 0 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 1221 | No scada available server OS failed-reading as per billing meter
2025-05-30 | 2026 | 2025 | 2025-05-01 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 33 | 0 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 1221 | No scada available server OS failed-reading as per billing meter
2025-05-31 | 2026 | 2025 | 2025-05-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-06-01 | 2026 | 2025 | 2025-06-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-06-02 | 2026 | 2025 | 2025-06-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-06-03 | 2026 | 2025 | 2025-06-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-06-04 | 2026 | 2025 | 2025-06-01 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 0 | 65 | 0 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 2405 | No scada available server OS failed-reading as per billing meter
2025-06-05 | 2026 | 2025 | 2025-06-01 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 0 | 163 | 0 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 6031 | No scada available server OS failed-reading as per billing meter
2025-06-06 | 2026 | 2025 | 2025-06-01 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 33 | 0 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 1221 | No scada available server OS failed-reading as per billing meter
2025-06-07 | 2026 | 2025 | 2025-06-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-06-08 | 2026 | 2025 | 2025-06-01 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 33 | 0 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 1221 | No scada available server OS failed-reading as per billing meter
2025-06-09 | 2026 | 2025 | 2025-06-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-06-10 | 2026 | 2025 | 2025-06-01 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 0 | 98 | 0 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 3626 | No scada available server OS failed-reading as per billing meter
2025-06-11 | 2026 | 2025 | 2025-06-01 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 33 | 0 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 1221 | No scada available server OS failed-reading as per billing meter
2025-06-12 | 2026 | 2025 | 2025-06-01 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 0 | 163 | 0 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 6031 | No scada available server OS failed-reading as per billing meter
2025-06-13 | 2026 | 2025 | 2025-06-01 | [39 empty] | 0
2025-06-14 | 2026 | 2025 | 2025-06-01 | [39 empty] | 0
2025-06-15 | 2026 | 2025 | 2025-06-01 | [39 empty] | 0
2025-06-16 | 2026 | 2025 | 2025-06-01 | [39 empty] | 0
2025-06-17 | 2026 | 2025 | 2025-06-01 | [39 empty] | 0
2025-06-18 | 2026 | 2025 | 2025-06-01 | [39 empty] | 0
2025-06-19 | 2026 | 2025 | 2025-06-01 | [39 empty] | 0
2025-06-20 | 2026 | 2025 | 2025-06-01 | [39 empty] | 0
2025-06-21 | 2026 | 2025 | 2025-06-01 | [39 empty] | 0
2025-06-22 | 2026 | 2025 | 2025-06-01 | [39 empty] | 0
2025-06-23 | 2026 | 2025 | 2025-06-01 | [39 empty] | 0
2025-06-24 | 2026 | 2025 | 2025-06-01 | [39 empty] | 0
2025-06-25 | 2026 | 2025 | 2025-06-01 | [39 empty] | 0
2025-06-26 | 2026 | 2025 | 2025-06-01 | [39 empty] | 0
2025-06-27 | 2026 | 2025 | 2025-06-01 | [39 empty] | 0
2025-06-28 | 2026 | 2025 | 2025-06-01 | [39 empty] | 0
2025-06-29 | 2026 | 2025 | 2025-06-01 | [39 empty] | 0
2025-06-30 | 2026 | 2025 | 2025-06-01 | [39 empty] | 0
2025-07-01 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-02 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-03 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-04 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-05 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-06 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-07 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-08 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-09 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-10 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-11 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-12 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-13 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-14 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-15 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-16 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-17 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-18 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-19 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-20 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-21 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-22 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-23 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-24 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-25 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-26 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-27 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-28 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-29 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-30 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-31 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-08-01 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-02 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-03 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-04 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-05 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-06 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-07 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-08 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-09 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-10 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-11 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-12 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-13 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-14 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-15 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-16 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-17 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-18 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-19 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-20 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-21 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-22 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-23 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-24 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-25 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-26 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-27 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-28 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-29 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-30 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-31 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-09-01 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-02 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-03 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-04 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-05 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-06 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-07 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-08 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-09 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-10 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-11 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-12 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-13 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-14 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-15 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-16 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-17 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-18 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-19 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-20 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-21 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-22 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-23 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-24 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-25 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-26 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-27 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-28 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-29 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-30 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-10-01 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-02 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-03 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-04 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-05 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-06 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-07 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-08 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-09 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-10 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-11 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-12 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-13 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-14 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-15 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-16 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-17 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-18 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-19 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-20 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-21 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-22 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-23 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-24 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-25 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-26 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-27 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-28 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-29 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-30 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-31 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-11-01 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-02 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-03 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-04 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-05 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-06 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-07 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-08 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-09 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-10 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-11 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-12 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-13 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-14 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-15 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-16 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-17 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-18 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-19 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-20 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-21 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-22 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-23 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-24 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-25 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-26 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-27 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-28 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-29 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-30 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-12-01 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-02 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-03 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-04 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-05 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-06 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-07 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-08 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-09 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-10 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-11 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-12 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-13 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-14 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-15 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-16 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-17 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-18 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-19 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-20 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-21 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-22 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-23 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-24 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-25 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-26 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-27 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-28 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-29 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-30 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-31 | 2026 | 2025 | 2025-12-01 | 2411.487 | 891.6197 | 1879.9699 | 874.2626 | 880.4713 | 636.2265 | 372.8833 | 641.519 | 906.0887 | 2260.394 | 383.091 | 377.6865 | 2175.7978 | 1993.9216 | 1758.4657 | 2234.1107 | 1964.6707 | 2190.6098 | 441.9792 | 670.5095 | 1570.8376 | 1180.1707 | 1761.4244 | 999.7058 | 1757.046 | 677.2118 | 333.82 | 0 | 1635.0767 | 0 | 1909.0221 | 573.7749 | 742.5826 | 1713.1288 | 1709.3145 | -8.1559 | 2496.8774 | 783.4712 | 2020.958 | 47802.0313
Formulas:
Month Year = [Date]-DAY([Date])+1
Date = [Date, row above]+1

## IGA_BD
Sr. No. | Date | Finacial Year | Calendor Year | Month | Operating Year | Affected Feeder | SPV | Concumaer | Plant Equivalent Weightage | Breakdown Description | Fault Start TimeStamp | Work Start TimeStamp | Fault Clearance time | Response Time | Resolution Time | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Column1 | Fault category | Scope | KWH lost during BD/SD | Fault Category
1 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_1 | Wind_F2 | PWEGPL | MSEDCL | 25.64% | F-2 tripped due to Earth fault | 19:20 | 19:20 | 19:37 | 0 | 0.28333 | 0.28333 | Test charged & stood ok | Close | 0.07265 | Test charged & stood ok | IG Breakdown Maintenance | SGSL | 580
2 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | Year_1 | Wind_F3 | PWEGPL | MSEDCL | 23.08% | F-3 tripped due to Earth fault / Over current | 22:35 | 22:35 | 23:59 | 0 | 1.4 | 1.4 | Test charged & stood ok | Open | 0.32308 | Test charged & stood ok | IG Breakdown Maintenance | SGSL | 2898
3 | 2025-04-01 | 2025 | 2025 | 2025-04-01 | Year_1 | Wind_F1 | PWEGPL | MSEDCL | 25.64% | F-1 tripped due to Earth fault / Over current | 22:38 | 22:38 | 23:03 | 0 | 0.41667 | 0.41667 | Test charged & stood ok | Close | 0.10684 | Test charged & stood ok | IG Breakdown Maintenance | SGSL | 708.3333
4 | 2025-04-02 | 2025 | 2025 | 2025-04-01 | Year_1 | Wind_F3 | PWEGPL | MSEDCL | 23.08% | F-3 tripped due to Earth fault / Over current | 0:00 | 0:00 | 1:21 | 0 | 1.35 | 1.35 | Circuit open then close one by one | Close | 0.31154 | Circuit open then close one by one | IG Breakdown Maintenance | SGSL | 6986.25
5 | 2025-04-03 | 2025 | 2025 | 2025-04-01 | Year_1 | Wind_F2 | PWEGPL | MSEDCL | 25.64% | F-2 tripped due to Earth fault | 21:24 | 21:24 | 21:45 | 0 | 0.35 | 0.35 | Test charged & stood ok | Close | 0.089744 | Test charged & stood ok | IG Breakdown Maintenance | SGSL | 857.5
6 | 2025-04-07 | 2025 | 2025 | 2025-04-01 | Year_1 | Wind_F3 | PWEGPL | MSEDCL | 23.08% | F-3 Shutdown taken for scada cable rectification work | 12:37 | 12:37 | 14:38 | 0 | 2.0167 | 2.0167 | Scada cable rejoint then restore feeder | Close | 0.46538 | Scada cable rejoint then restore feeder | IG Unscheduled Maintenance | SGSL | 4083.75
7 | 2025-04-07 | 2025 | 2025 | 2025-04-01 | Year_1 | Wind_F4 | PWEGPL | MSEDCL | 25.64% | F-4 Shutdown taken for scada cable rectification work | 12:37 | 12:37 | 14:39 | 0 | 2.0333 | 2.0333 | Scada cable rejoint then restore feeder | Close | 0.52137 | Scada cable rejoint then restore feeder | IG Unscheduled Maintenance | SGSL | 4631.4815
8 | 2025-05-01 | 2025 | 2025 | 2025-05-01 | Year_1 | Wind_F3 | PWEGPL | MSEDCL | 23.08% | F-3 Shutdown taken for 11Kv line restoration work. | 17:05 | 17:05 | 18:00 | 0 | 0.91667 | 0.91667 | 11 Kv line restore then restore feeder | Close | 0.21154 | 11 Kv line restore then restore feeder | IG Unscheduled Maintenance | SGSL | 5651.25
9 | 2025-05-01 | 2025 | 2025 | 2025-05-01 | Year_1 | Wind_F4 | PWEGPL | MSEDCL | 25.64% | F-4 Shutdown taken for 11Kv line restoration work. | 17:05 | 17:05 | 18:00 | 0 | 0.91667 | 0.91667 | 11 Kv line restore then restore feeder | Close | 0.23504 | 11 Kv line restore then restore feeder | IG Unscheduled Maintenance | SGSL | 6416.6667
10 | 2025-05-06 | 2025 | 2025 | 2025-05-01 | Year_1 | Wind_F2 | PWEGPL | MSEDCL | 25.64% | F-2 tripped due to Earth fault | 16:26 | 16:26 | 16:32 | 0 | 0.1 | 0.1 | Test charged & stood ok | Close | 0.025641 | Test charged & stood ok | IG Breakdown Maintenance | SGSL | 265
11 | 2025-05-12 | 2025 | 2025 | 2025-05-01 | Year_1 | Wind_F3 | PWEGPL | MSEDCL | 23.08% | F-3 tripped due to Earth fault | 15:02 | 15:02 | 15:12 | 0 | 0.16667 | 0.16667 | Test charged & stood ok | Close | 0.038462 | Test charged & stood ok | IG Breakdown Maintenance | SGSL | 214
12 | 2025-05-12 | 2025 | 2025 | 2025-05-01 | Year_1 | Wind_F1 | PWEGPL | MSEDCL | 25.64% | F-1 tripped due to Earth fault | 15:21 | 15:21 | 15:28 | 0 | 0.11667 | 0.11667 | Test charged & stood ok | Close | 0.029915 | Test charged & stood ok | IG Breakdown Maintenance | SGSL | 126
13 | 2025-05-16 | 2025 | 2025 | 2025-05-01 | Year_1 | Wind_F4_Ckt2 | PWEGPL | MSEDCL | 12.82% | F-4 Shutdown taken for line & HT yard preventive maintenance work | 14:00 | 14:00 | 15:20 | 0 | 1.3333 | 1.3333 | Line & HT yard maintenance work done then restore circuit | Close | 0.17094 | Line & HT yard maintenance work done then restore circuit | IG Scheduled Maintenance | SGSL | 2777.7778
14 | 2025-05-17 | 2025 | 2025 | 2025-05-01 | Year_1 | Wind_F3 | PWEGPL | MSEDCL | 23.08% | F-3 Shutdown taken for line & HT yard preventive maintenance work | 13:00 | 13:00 | 14:48 | 0 | 1.8 | 1.8 | Line & HT yard maintenance work done then restore feeder | Close | 0.41538 | Line & HT yard maintenance work done then restore feeder | IG Scheduled Maintenance | SGSL | 3969
15 | 2025-05-19 | 2025 | 2025 | 2025-05-01 | Year_1 | Wind_F1 | PWEGPL | MSEDCL | 25.64% | F-1 tripped due to Earth fault | 20:44 | 20:44 | 21:00 | 0 | 0.26667 | 0.26667 | Test charged & stood ok | Close | 0.068376 | Test charged & stood ok | IG Breakdown Maintenance | SGSL | 333.3333
16 | 2025-05-19 | 2025 | 2025 | 2025-05-01 | Year_1 | Wind_F4_Ckt1 | PWEGPL | MSEDCL | 12.82% | F-4 tripped due to Earth fault | 21:12 | 21:12 | 22:07 | 0 | 0.91667 | 0.91667 | Circuit 2 isolator open then closed | Close | 0.11752 | Circuit 2 isolator open then closed | IG Breakdown Maintenance | SGSL | 1283.3333
17 | 2025-05-19 | 2025 | 2025 | 2025-05-01 | Year_1 | Wind_F4_Ckt2 | PWEGPL | MSEDCL | 12.82% | F-4 tripped due to Earth fault | 21:12 | 21:12 | 23:59 | 0 | 2.7833 | 2.7833 | work in progress | Open | 0.35684 | work in progress | IG Breakdown Maintenance | SGSL | 4035.8333
18 | 2025-05-19 | 2025 | 2025 | 2025-05-01 | Year_1 | Wind_F4_Ckt2 | PWEGPL | MSEDCL | 12.82% | F-4 tripped due to Earth fault | 0:00 | 0:00 | 0:44 | 0 | 0.73333 | 0.73333 | LA failure in G12 HT yard so replaced it then restore feeder | Close | 0.094017 | LA failure in G12 HT yard so replaced it then restore feeder | IG Breakdown Maintenance | SGSL | 1063.3333
19 | 2025-05-20 | 2025 | 2025 | 2025-05-01 | Year_1 | Wind_F4_Ckt1 | PWEGPL | MSEDCL | 12.82% | F-4 Ckt-1 Shutdown taken for line & HT yard preventive maintenance work | 10:35 | 10:35 | 11:47 | 0 | 1.2 | 1.2 | Line & HT yard maintenance work done then restore feeder | Close | 0.15385 | Line & HT yard maintenance work done then restore feeder | IG Scheduled Maintenance | SGSL | 2580
20 | 2025-05-20 | 2025 | 2025 | 2025-05-01 | Year_1 | Wind_F1 | PWEGPL | MSEDCL | 25.64% | F-1 Shutdown taken for line & HT yard preventive maintenance work | 12:30 | 12:30 | 14:00 | 0 | 1.5 | 1.5 | Line & HT yard maintenance work done then restore feeder | Close | 0.38462 | Line & HT yard maintenance work done then restore feeder | IG Scheduled Maintenance | SGSL | 2550
21 | 2025-05-20 | 2025 | 2025 | 2025-05-01 | Year_1 | Wind_F1 | PWEGPL | MSEDCL | 25.64% | F-1 tripped due to Earth fault | 18:17 | 18:17 | 18:48 | 0 | 0.51667 | 0.51667 | Test charged & stood ok | Close | 0.13248 | Test charged & stood ok | IG Breakdown Maintenance | SGSL | 878.3333
22 | 2025-05-21 | 2025 | 2025 | 2025-05-01 | Year_1 | Wind_F2_Ckt2 | PWEGPL | MSEDCL | 15.38% | F-2 Shutdown taken for line & HT yard preventive maintenance work | 11:20 | 11:20 | 12:40 | 0 | 1.3333 | 1.3333 | Line & HT yard maintenance work done then restore feeder | Close | 0.20513 | Line & HT yard maintenance work done then restore feeder | IG Breakdown Maintenance | SGSL | 2400
23 | 2025-05-23 | 2025 | 2025 | 2025-05-01 | Year_1 | Wind_F1 | PWEGPL | MSEDCL | 25.64% | F-1 Shutdown taken for line & VCB yard preventive maintenance work | 10:52 | 10:52 | 14:18 | 0 | 3.4333 | 3.4333 | Line & VCB yard maintenance work done then restore feeder | Close | 0.88034 | Line & VCB yard maintenance work done then restore feeder | IG Scheduled Maintenance | SGSL | 2231.6667
24 | 2025-05-23 | 2025 | 2025 | 2025-05-01 | Year_1 | Wind_F2 | PWEGPL | MSEDCL | 25.64% | F-2 Shutdown taken for line & VCB yard preventive maintenance work | 10:52 | 10:52 | 14:18 | 0 | 3.4333 | 3.4333 | Line & VCB yard maintenance work done then restore feeder | Close | 0.88034 | Line & VCB yard maintenance work done then restore feeder | IG Scheduled Maintenance | SGSL | 2060
25 | 2025-05-23 | 2025 | 2025 | 2025-05-01 | Year_1 | Wind_F4_Ckt2 | PWEGPL | MSEDCL | 12.82% | F-4 Shutdown taken for container movement work | 14:48 | 14:48 | 16:01 | 0 | 1.2167 | 1.2167 | Container movement then restore feeder | Close | 0.15598 | Container movement then restore feeder | IG Unscheduled Maintenance | O2 power | 1216.6667
26 | 2025-05-23 | 2025 | 2025 | 2025-05-01 | Year_1 | Wind_F4_Ckt1 | PWEGPL | MSEDCL | 12.82% | F-4 Shutdown taken for PT replacement work . | 15:40 | 15:40 | 16:01 | 0 | 0.35 | 0.35 | PT replaced then restore feeder | Close | 0.044872 | PT replaced then restore feeder | IG Unscheduled Maintenance | SGSL | 350
27 | 2025-05-24 | 2025 | 2025 | 2025-05-01 | Year_1 | Wind_F4 | PWEGPL | MSEDCL | 25.64% | F-4 shutdown taken for Protection PT replaced | 14:24 | 14:24 | 15:05 | 0 | 0.68333 | 0.68333 | PT replaced then restore feeder | Close | 0.17521 | PT replaced then restore feeder | IG Unscheduled Maintenance | SGSL | 1777
28 | 2025-05-27 | 2025 | 2025 | 2025-05-01 | Year_1 | Wind_F2 | PWEGPL | MSEDCL | 25.64% | F-2 tripped due to Earth fault | 11:30 | 11:30 | 11:36 | 0 | 0.1 | 0.1 | Test charged & stood ok | Close | 0.025641 | Test charged & stood ok | IG Unscheduled Maintenance | SGSL | 430
29 | 2025-05-27 | 2025 | 2025 | 2025-05-01 | Year_1 | Wind_F3 | PWEGPL | MSEDCL | 23.08% | F-3 tripped due to Earth fault | 15:40 | 15:40 | 19:50 | 0 | 4.1667 | 4.1667 | G01 Isolator open then restore feeder | Close | 0.96154 | Wtg G01 Isolator open then restore feeder | IG Unscheduled Maintenance | SGSL | 22687.5
30 | 2025-05-28 | 2025 | 2025 | 2025-05-01 | Year_1 | Wind_F2 | PWEGPL | MSEDCL | 25.64% | F-2 tripped due to Earth fault | 14:21 | 14:21 | 14:25 | 0 | 0.066667 | 0.066667 | Test charged & stood ok | Close | 0.017094 | Test charged & stood ok | IG Unscheduled Maintenance | SGSL | 203
31 | 2025-05-29 | 2025 | 2025 | 2025-05-01 | Year_1 | Wind_F2 | PWEGPL | MSEDCL | 25.64% | F-2 tripped due to Earth fault | 8:26 | 8:26 | 8:32 | 0 | 0.1 | 0.1 | Test charged & stood ok | Close | 0.025641 | Test charged & stood ok | IG Unscheduled Maintenance | SGSL | 555
32 | 2025-05-29 | 2025 | 2025 | 2025-05-01 | Year_1 | Wind_F2 | PWEGPL | MSEDCL | 25.64% | F-2 tripped due to Earth fault | 9:26 | 9:26 | 9:30 | 0 | 0.066667 | 0.066667 | Test charged & stood ok | Close | 0.017094 | Test charged & stood ok | IG Breakdown Maintenance | SGSL | 370
33 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | Year_1 | Wind_F2_Ckt1 | PWEGPL | MSEDCL | 10.26% | F-2 tripped due to Earth fault | 10:05 | 10:05 | 11:38 | 0 | 1.55 | 1.55 | Circuit 2 isolator open then charge feeder circuit 1 | Close | 0.15897 | Circuit 2 isolator open then charge feeder circuit 1 | IG Unscheduled Maintenance | SGSL | 11315
34 | 2025-05-31 | 2025 | 2025 | 2025-05-01 | Year_1 | Wind_F2_Ckt2 | PWEGPL | MSEDCL | 15.38% | F-2 tripped due to Earth fault | 10:05 | 10:05 | 12:45 | 0 | 2.6667 | 2.6667 | Circuit 2 petorling done then charge circuit 2 | Close | 0.41026 | Circuit 2 petorling done then charge circuit 2 | IG Unscheduled Maintenance | SGSL | 19466.6667
35 | 2025-06-01 | 2025 | 2025 | 2025-06-01 | Year_1 | Wind_F2 | PWEGPL | MSEDCL | 25.64% | F-2 tripped due to Earth fault | 12:31 | 12:31 | 12:33 | 0 | 0.033333 | 0.033333 | Test charged & stood ok | Close | 0.008547 | Test charged & stood ok | IG Breakdown Maintenance | SGSL | 248.3333
36 | 2025-06-01 | 2025 | 2025 | 2025-06-01 | Year_1 | Wind_F1 | PWEGPL | MSEDCL | 25.64% | F-1 tripped due to Earth fault | 16:45 | 16:45 | 16:48 | 0 | 0.05 | 0.05 | Test charged & stood ok | Close | 0.012821 | Test charged & stood ok | IG Breakdown Maintenance | SGSL | 312.5
37 | 2025-06-02 | 2025 | 2025 | 2025-06-01 | Year_1 | Wind_F2_Ckt1 | PWEGPL | MSEDCL | 10.26% | F-2 Shutdown taken for line & HT yard preventive maintenance work | 14:55 | 14:55 | 15:55 | 0 | 1 | 1 | Line & HT yard maintenance work done then restore circuit | Close | 0.10256 | Line & HT yard maintenance work done then restore circuit | IG Scheduled Maintenance | SGSL | 3700
38 | 2025-06-03 | 2025 | 2025 | 2025-06-01 | Year_1 | Wind_F2 | PWEGPL | MSEDCL | 25.64% | F-2 tripped due to Earth fault | 4:40 | 4:40 | 4:54 | 0 | 0.23333 | 0.23333 | Test charged & stood ok | Close | 0.059829 | Test charged & stood ok | IG Breakdown Maintenance | SGSL | 1702
39 | 2025-06-04 | 2025 | 2025 | 2025-06-01 | Year_1 | Wind_F3 | PWEGPL | MSEDCL | 23.08% | F-3 Shutdown taken for line & VCB yard preventive maintenance work | 10:30 | 10:30 | 14:11 | 0 | 3.6833 | 3.6833 | Line & VCB yard maintenance work done then restore feeder | Close | 0.85 | Line & VCB yard maintenance work done then restore feeder | IG Scheduled Maintenance | SGSL | 8121.75
40 | 2025-06-04 | 2025 | 2025 | 2025-06-01 | Year_1 | Wind_F4 | PWEGPL | MSEDCL | 25.64% | F-4 Shutdown taken for line & VCB yard preventive maintenance work | 10:30 | 10:30 | 14:11 | 0 | 3.6833 | 3.6833 | Line & VCB yard maintenance work done then restore feeder | Close | 0.94444 | Line & VCB yard maintenance work done then restore feeder | IG Scheduled Maintenance | SGSL | 8594.4444
41 | 2025-06-04 | 2025 | 2025 | 2025-06-01 | Year_1 | Wind_F2 | PWEGPL | MSEDCL | 25.64% | F-2 tripped due to Earth fault | 14:35 | 14:35 | 14:50 | 0 | 0.25 | 0.25 | Test charged & stood ok | Close | 0.064103 | Test charged & stood ok | IG Unscheduled Maintenance | SGSL | 312.5
42 | 2025-06-04 | 2025 | 2025 | 2025-06-01 | Year_1 | Wind_F2 | PWEGPL | MSEDCL | 25.64% | F-2 Shutdown taken for Protection CT replacement work | 16:30 | 16:30 | 20:55 | 0 | 4.4167 | 4.4167 | Portection CT replaced then restore feeder | Close | 1.1325 | Portection CT replaced then restore feeder | IG Unscheduled Maintenance | SGSL | 5520.8333
43 | 2025-06-08 | 2025 | 2025 | 2025-06-01 | Year_1 | Wind_F2 | PWEGPL | MSEDCL | 25.64% | F-2 tripped due to Earth fault | 6:49 | 6:49 | 6:51 | 0 | 0.033333 | 0.033333 | Test charged & stood ok | Close | 0.008547 | Test charged & stood ok | IG Breakdown Maintenance | SGSL | 179.1667
44 | 2025-06-08 | 2025 | 2025 | 2025-06-01 | Year_1 | Wind_F2 | PWEGPL | MSEDCL | 25.64% | F-2 tripped due to Over current | 19:02 | 19:02 | 21:05 | 0 | 2.05 | 2.05 | Line petroling done then charged feeder | Close | 0.52564 | Line petroling done then charged feeder | IG Breakdown Maintenance | SGSL | 11018.75
45 | 2025-06-11 | 2025 | 2025 | 2025-06-01 | Year_1 | Wind_F3 | PWEGPL | MSEDCL | 23.08% | F-3 tripped due to Over current | 16:37 | 16:37 | 16:45 | 0 | 0.13333 | 0.13333 | Test charged & stood ok | Close | 0.030769 | Test charged & stood ok | IG Breakdown Maintenance | SGSL | 527
46 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
47 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
48 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
49 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
50 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
51 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
52 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
53 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
54 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
55 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
56 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
57 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
58 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
59 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
60 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
61 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
62 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
63 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
64 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
65 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
66 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
67 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
68 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
69 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
70 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
71 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
72 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
73 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
74 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
75 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
76 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
77 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
78 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
79 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
80 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
81 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
82 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
83 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
84 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
85 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
86 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
87 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
88 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
89 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
90 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
91 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
92 |  | 2025 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
93 |  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
94 |  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
95 |  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
96 |  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
97 |  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
98 |  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
99 |  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
100 |  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
101 |  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 2026 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | 1900 | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
|  | #VALUE! | 1900 | 1899-12-31 | [9 empty] | 0 |  | 0
Formulas:
Month = [Date]-DAY([Date])+1

## Grid_BD
Sr. No. | Date | Finacial Year | Calendor Year | Month | Operating Year | Affected System | SPV | Concumaer | Plant Equivalent Weightage | Breakdown Description | Fault Start TimeStamp | Work Start TimeStamp | Fault Clearance time | Response Time | Resolution Time | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Fault Category | Approx. Energy loss (kWh)
1 | 2023-02-01 | 2023 | 2023 | 2023-02-01 | Year_1 | Line1 | PWEGPL | MSEDCL | 100% | Grid Failure | 17:33 | 17:38 | 18:22 | 0.083333 | 0.73333 | 0.81667 | Charged feeders post Grid resume | Close | 0.81667
2 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
3 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
4 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
5 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
6 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
7 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
8 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
9 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
10 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
11 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
12 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
13 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
14 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
15 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
16 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
17 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
18 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
19 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
20 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
21 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
22 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
23 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
24 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
25 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
26 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
27 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
28 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
29 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
30 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
31 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
32 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
33 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
34 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
35 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
36 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
37 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
38 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
39 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
40 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
41 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
42 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
43 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
44 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
45 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
46 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
47 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
48 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
49 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
50 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
51 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
52 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
53 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
54 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
55 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
56 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
57 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
58 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
59 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
60 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
61 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
62 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
63 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
64 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
65 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
66 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
67 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
68 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
69 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
70 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
71 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
72 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
73 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
74 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
75 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
76 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
77 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
78 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
79 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
80 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
81 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
82 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
83 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
84 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
85 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
86 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
87 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
88 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
89 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
90 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
91 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
92 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
93 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
94 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
95 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
96 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
97 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
98 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
99 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
100 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
101 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
102 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
103 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
104 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
105 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
106 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
107 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
108 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
109 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
110 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
111 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
112 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
113 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
114 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
115 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
116 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
117 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
118 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
119 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
120 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
121 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
122 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
123 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
124 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
125 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
126 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
127 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
128 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
129 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
130 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
131 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
132 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
133 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
134 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
135 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
136 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
137 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
138 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
139 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
140 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
141 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
142 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
143 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
144 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
145 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
146 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
147 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
148 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
149 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
150 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
151 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
152 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
153 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
154 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
155 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
156 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
157 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
158 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
159 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
160 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
161 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
162 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
163 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
164 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
165 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
166 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
167 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
168 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
169 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
170 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
171 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
172 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
173 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
174 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
175 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
176 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
177 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
178 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
179 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
180 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
181 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
182 |  | 1900 | 1900 | 1899-12-31 | Year_1 | [8 empty] | 0 |  | 0
Formulas:
Month = [Date]-DAY([Date])+1

## PM record
Suzlon Mirkala Yearly maintenance schedule Plan Vs Actual Year 2023-24
Sr No | Turbine No | Generator Make | Turbine ID | 6 Months Schedule Date | Completed Date | 12 Months Schedule Date | Completed Date | 18 Months Schedule Date | Completed Date | 24 Months Schedule Date | Completed Date | 30 Months Schedule Date | Completed Date | 36 Months Schedule Date | Completed Date | 42 Months Schedule Date | Completed Date | 48 Months Schedule Date | Completed Date | 54 Month PM Schedule Date | Completed Date | 60Month PM Schedule Date | Completed Date | 66 Month PM Schedule Date | Completed Date | 72 Month PM Schedule Date | Completed Date | 78 Month PM Schedule Date | Completed Date | 84 Month PM Schedule Date | Completed Date | 90 Month PM Schedule Date | Completed Date | 96 Month PM Schedule Date | Completed Date | Delay in Days | 102 Month PM Schedule Date | Completed Date | Delay in Days | 108 Month PM Schedule Date(Suzlon) Day-1 | 108 Month PM Schedule Date(Suzlon) Day-2 | Completed Date Day1 | Completed Date Day2 | Delay in Days | PM delay resons | 114 Month Half year PM Schedule Date | Completed Date | Delay in Days | 120 Month YPM Schedule Date (Day-01) | 120 Month YPM Schedule Date (Day-02) | 120 Month YPM Completed Date (Day-01) | 120 Month YPM Completed Date (Day-02) | Delay in Days | PM delay resons | WTG | 126 Month Plan Date HYPM | 126 Month Actual Date HYPM | Diff. Days | Adherence | Remarks
1 | G 24 | ABB | 100261368 | 2014-12-19 | 2014-12-19 | 2015-06-19 | 2015-06-22 | 2015-12-19 | 2015-12-19 | 2016-06-19 | 2016-07-14 | 2016-12-19 | 2016-12-26 | 2017-06-19 | 2017-06-23 | 2017-12-19 | 2018-01-11 | 2018-06-19 | 2018-08-06 | 2018-12-14 | 2019-01-28 | 2019-09-07 | 2019-09-04 | 2020-03-05 | 2020-04-25 | 2020-09-01 | 2020-12-22 | 2021-03-01 | 2021-03-26 | 2021-09-01 | 2022-05-19 | 2022-03-01 | 2022-05-19 | 2022-09-01 | 2022-09-24 | 23 | 2023-02-28 | 2023-03-14 | 14 | 2023-10-10 | 2023-10-11 | 2023-12-16 | 2023-12-18 | 68 |  | 2024-03-01 | 2024-03-04 | 3
2 | G 25 | ABB | 100261366 | 2014-12-21 | 2014-12-21 | 2015-06-21 | 2015-08-01 | 2015-12-21 | 2015-12-21 | 2016-06-21 | 2016-07-21 | 2016-12-21 | 2016-12-28 | 2017-06-21 | 2017-06-24 | 2017-12-21 | 2018-01-08 | 2018-06-21 | 2018-08-08 | 2018-12-16 | 2019-01-29 | 2019-09-08 | 2019-09-07 | 2020-03-06 | 2020-04-30 | 2020-09-02 | 2020-12-18 | 2021-03-02 | 2021-03-27 | 2021-09-01 | 2022-05-20 | 2022-03-02 | 2022-05-20 | 2022-09-01 | 2022-09-25 | 24 | 2023-02-28 | 2023-03-17 | 17 | 2023-10-12 | 2023-10-13 | 2023-10-10 | 2023-10-31 | 18 |  | 2024-03-02 | 2024-03-05 | 3 | 2024-11-05 | 2024-11-06 | 2024-11-06 | 2024-11-07 | 1 |  | PWEGPL25 | 2025-04-26 | 2025-04-26 | 0 | 100 | Delay due to payment issue
3 | G 27 | ABB | 100261367 | 2014-12-23 | 2014-12-23 | 2015-06-23 | 2015-06-17 | 2015-12-23 | 2015-12-22 | 2016-06-23 | 2016-07-22 | 2016-12-23 | 2016-12-27 | 2017-06-23 | 2017-07-07 | 2017-12-23 | 2018-01-09 | 2018-06-23 | 2018-08-14 | 2018-12-18 | 2019-01-30 | 2019-09-09 | 2019-09-16 | 2020-03-07 | 2020-05-01 | 2020-09-03 | 2020-12-17 | 2021-03-03 | 2021-03-28 | 2021-09-03 | 2022-05-19 | 2022-03-03 | 2022-05-19 | 2022-09-03 | 2022-09-26 | 23 | 2023-03-02 | 2023-03-21 | 19 | 2023-10-14 | 2023-10-15 | 2023-12-18 | 2023-12-16 | 62 |  | 2024-03-04 | 2024-03-06 | 2 | 2024-11-07 | 2024-11-08 | 2024-11-08 | 2024-11-09 | 1 |  | PWEGPL27 | 2025-04-27 | 2025-04-27 | 0 | 100
4 | G 31 | CANTERY | 100261341 | 2014-12-25 | 2014-12-25 | 2015-06-25 | 2015-06-21 | 2015-12-25 | 2015-12-26 | 2016-06-25 | 2016-07-23 | 2016-12-25 | 2017-01-02 | 2017-06-25 | 2017-07-19 | 2017-12-25 | 2018-01-12 | 2018-06-25 | 2018-08-24 | 2018-12-20 | 2019-02-02 | 2019-09-10 | 2019-09-17 | 2020-03-08 | 2020-05-02 | 2020-09-04 | 2020-12-25 | 2021-03-04 | 2021-03-29 | 2021-09-03 | 2022-05-21 | 2022-03-04 | 2022-05-21 | 2022-09-03 | 2022-09-27 | 24 | 2023-03-02 | 2023-03-24 | 22 | 2023-10-16 | 2023-10-17 | 2023-10-19 | 2023-11-18 | 32 | ROW at site office (11-10-23 to 16-10-23) for crane movement to G20 & Multiple activities at site BD & G20 restoration work.(20-10-23 to 27-10-2023) /limited manpower at site | 2024-03-05 | 2024-03-08 | 3 | 2024-11-09 | 2024-11-11 | 2024-11-18 | 2024-11-19 | 8 | Manual stop for blade bush gap issue retrofitting work on 14-Dec-24 @15:02 | PWEGPL31 | 2025-06-07 |  | -45815 | -50788.8889 | Major B.D Blade root bush gap issue in blade no 596
5 | G 30 | CANTERY | 100261340 | 2014-12-27 | 2014-12-27 | 2015-06-27 | 2015-06-27 | 2015-12-27 | 2015-12-28 | 2016-06-27 | 2016-07-25 | 2016-12-27 | 2017-01-03 | 2017-06-27 | 2017-07-08 | 2017-12-27 | 2018-01-13 | 2018-06-27 | 2018-08-17 | 2018-12-22 | 2019-02-01 | 2019-09-11 | 2019-09-18 | 2020-03-09 | 2020-05-03 | 2020-09-05 | 2020-12-24 | 2021-03-05 | 2021-03-30 | 2021-09-06 | 2022-05-23 | 2022-03-05 | 2022-05-23 | 2022-09-06 | 2022-09-28 | 22 | 2023-03-05 | 2023-03-27 | 22 | 2023-10-18 | 2023-10-19 | 2023-10-18 | 2023-11-07 | 19 | ROW at site office (11-10-23 to 16-10-23) for crane movement to G20 & Multiple activities at site BD & G20 restoration work.(20-10-23 to 27-10-2023) /limited manpower at site | 2024-03-06 | 2024-03-09 | 3 | 2024-11-12 | 2024-11-13 | 2024-11-23 | 2024-11-24 | 11 |  | PWEGPL30 | 2025-04-28 | 2025-04-28 | 0 | 100
6 | G 29 | CANTERY | 100261337 | 2015-01-01 | 2015-01-01 | 2015-07-01 | 2015-07-10 | 2016-01-01 | 2015-12-29 | 2016-07-01 | 2016-07-26 | 2017-01-01 | 2017-01-19 | 2017-07-01 | 2017-07-10 | 2018-01-01 | 2018-01-15 | 2018-07-01 | 2018-08-16 | 2018-12-27 | 2019-01-31 | 2019-09-12 | 2019-09-21 | 2020-03-10 | 2020-05-04 | 2020-09-06 | 2020-12-23 | 2021-03-08 | 2021-03-31 | 2021-09-06 | 2022-05-24 | 2022-03-07 | 2022-05-24 | 2022-09-06 | 2022-09-29 | 23 | 2023-03-05 | 2023-03-28 | 23 | 2023-10-20 | 2023-10-21 | 2023-10-17 | 2023-11-06 | 16 | ROW at site office (11-10-23 to 16-10-23) for crane movement to G20 & Multiple activities at site BD & G20 restoration work.(20-10-23 to 27-10-2023) /limited manpower at site | 2024-03-07 | 2024-03-11 | 4 | 2024-11-14 | 2024-11-15 | 2024-11-21 | 2024-11-22 | 7 |  | PWEGPL29 | 2025-06-08 |  | -45816 | -50790 | Major B.D Blade root bush gap issue blade 636 de erected
7 | G 34 | ABB | 100261333 | 2015-01-04 | 2015-01-04 | 2015-07-04 | 2015-08-01 | 2016-01-04 | 2016-01-04 | 2016-07-04 | 2016-07-30 | 2017-01-04 | 2017-01-23 | 2017-07-04 | 2017-08-02 | 2018-01-04 | 2018-01-16 | 2018-07-04 | 2018-08-18 | 2018-12-30 | 2019-02-04 | 2019-09-13 | 2019-09-23 | 2020-03-11 | 2020-05-13 | 2020-09-07 | 2020-12-26 | 2021-03-09 | 2021-04-01 | 2021-09-08 | 2022-06-02 | 2022-03-08 | 2022-06-02 | 2022-09-08 | 2022-10-01 | 23 | 2023-03-07 | 2023-03-30 | 23 | 2023-10-22 | 2023-10-23 | 2023-11-16 | 2023-11-17 | 25 |  | 2024-03-08 | 2024-03-12 | 4 | 2024-11-16 | 2024-11-18 | 2024-11-10 | 2024-11-11 | -7 |  | PWEGPL28 | 2025-04-29 | 2025-04-29 | 0 | 100
8 | G 33 | ABB | 100261334 | 2015-01-07 | 2015-01-07 | 2015-07-07 | 2015-07-20 | 2016-01-07 | 2016-01-06 | 2016-07-07 | 2016-08-01 | 2017-01-07 | 2017-01-24 | 2017-07-07 | 2017-08-04 | 2018-01-07 | 2018-01-17 | 2018-07-07 | 2018-08-20 | 2019-01-02 | 2019-02-06 | 2019-09-14 | 2019-09-25 | 2020-03-12 | 2020-05-14 | 2020-09-08 | 2020-12-27 | 2021-03-10 | 2021-04-02 | 2021-09-08 | 2022-06-03 | 2022-03-09 | 2022-06-03 | 2022-09-08 | 2022-10-02 | 24 | 2023-03-07 | 2023-03-31 | 24 | 2023-10-24 | 2023-10-25 | 2023-10-27 | 2023-11-08 | 14 | ROW at site office (11-10-23 to 16-10-23) for crane movement to G20 & Multiple activities at site BD & G20 restoration work.(20-10-23 to 27-10-2023) /limited manpower at site | 2024-03-09 | 2024-03-15 | 6 | 2024-11-19 | 2024-11-20 | 2024-11-12 | 2024-11-14 | -6 |  | PWEGPL34 | 2025-04-30 | 2025-04-30 | 0 | 100
9 | G 35 | ABB | 100261372 | 2015-01-08 | 2015-01-08 | 2015-07-08 | 2015-08-04 | 2016-01-08 | 2016-01-08 | 2016-07-08 | 2016-08-03 | 2017-01-08 | 2017-01-21 | 2017-07-08 | 2017-08-06 | 2018-01-08 | 2018-01-18 | 2018-07-08 | 2018-08-21 | 2019-01-03 | 2019-02-07 | 2019-09-15 | 2019-09-26 | 2020-03-13 | 2020-05-06 | 2020-09-09 | 2020-12-28 | 2021-03-11 | 2021-04-03 | 2021-09-10 | 2022-06-06 | 2022-03-10 | 2022-06-06 | 2022-09-10 | 2022-10-03 | 23 | 2023-03-09 | 2023-04-04 | 26 | 2023-10-26 | 2023-10-27 | 2023-11-20 | 2023-11-21 | 25 |  | 2024-03-11 | 2024-03-19 | 8 | 2024-11-21 | 2024-11-22 | 2024-11-25 | 2024-11-26 | 4 |  | PWEGPL33 | 2025-05-01 | 2025-05-01 | 0 | 100
10 | G 36 | ABB | 100261371 | 2015-01-10 | 2015-01-10 | 2015-07-10 | 2015-08-02 | 2016-01-10 | 2016-01-10 | 2016-07-10 | 2016-08-05 | 2017-01-10 | 2017-01-30 | 2017-07-10 | 2017-08-07 | 2018-01-10 | 2018-01-19 | 2018-07-10 | 2018-08-27 | 2019-01-05 | 2019-02-08 | 2019-09-16 | 2019-09-27 | 2020-03-14 | 2020-05-14 | 2020-09-10 | 2021-01-01 | 2021-03-12 | 2021-04-04 | 2021-09-10 | 2022-06-05 | 2022-03-11 | 2022-06-05 | 2022-09-10 | 2022-10-05 | 25 | 2023-03-09 | 2023-04-03 | 25 | 2023-10-28 | 2023-10-29 | 2023-11-22 | 2023-11-23 | 25 |  | 2024-03-12 | 2024-03-20 | 8 | 2024-11-23 | 2024-11-25 | 2024-11-28 | 2024-11-29 | 4 |  | PWEGPL35 | 2025-05-02 | 2025-05-03 | 1 | 100 | delay due to Pitch seal replaced in G-07
11 | G 37 | CANTERY | 100261338 | 2015-01-13 | 2015-01-13 | 2015-07-13 | 2015-08-05 | 2016-01-13 | 2016-01-13 | 2016-07-13 | 2016-08-12 | 2017-01-13 | 2017-01-25 | 2017-07-13 | 2017-08-08 | 2018-01-13 | 2018-01-20 | 2018-07-13 | 2018-08-22 | 2019-01-08 | 2019-02-09 | 2019-09-17 | 2019-09-28 | 2020-03-15 | 2020-05-15 | 2020-09-11 | 2020-12-29 | 2021-03-15 | 2021-04-06 | 2021-09-13 | 2022-06-09 | 2022-03-12 | 2022-06-09 | 2022-09-13 | 2022-10-06 | 23 | 2023-03-12 | 2023-04-05 | 24 | 2023-10-30 | 2023-10-31 | 2023-11-24 | 2023-11-25 | 25 |  | 2024-03-13 | 2024-03-21 | 8 | 2024-11-26 | 2024-11-27 | 2024-11-30 | 2024-12-01 | 4 |  | PWEGPL36 | 2025-05-03 | 2025-05-04 | 1 | 100
12 | G 38 | ABB | 100261403 | 2015-01-20 | 2015-01-20 | 2015-07-20 | 2015-07-20 | 2016-01-20 | 2016-01-17 | 2016-07-20 | 2016-08-13 | 2017-01-20 | 2017-02-02 | 2017-07-20 | 2017-08-09 | 2018-01-20 | 2018-01-25 | 2018-07-20 | 2018-09-01 | 2019-01-15 | 2019-02-11 | 2019-09-18 | 2019-09-29 | 2020-03-16 | 2020-05-15 | 2020-09-12 | 2020-12-30 | 2021-03-16 | 2021-04-08 | 2021-09-13 | 2022-06-10 | 2022-03-14 | 2022-06-10 | 2022-09-13 | 2022-10-08 | 25 | 2023-03-12 | 2023-04-06 | 25 | 2023-11-01 | 2023-11-02 | 2023-11-25 | 2023-11-24 | 22 |  | 2024-03-14 | 2024-03-23 | 9 | 2024-11-28 | 2024-11-29 | 2024-12-02 | 2024-12-03 | 4 |  | PWEGPL37 | 2025-05-04 | 2025-05-06 | 2 | 100 | Delay due to Pitch cylinder replacement work in G-26
13 | G 39 | ABB | 100261374 | 2015-01-22 | 2015-01-22 | 2015-07-22 | 2015-07-18 | 2016-01-22 | 2016-01-21 | 2016-07-22 | 2016-08-14 | 2017-01-22 | 2017-02-03 | 2017-07-22 | 2017-08-10 | 2018-01-22 | 2018-01-27 | 2018-07-22 | 2018-09-03 | 2019-01-17 | 2019-02-12 | 2019-09-19 | 2019-09-30 | 2020-03-17 | 2020-05-16 | 2020-09-13 | 2020-10-13 | 2021-03-17 | 2021-04-21 | 2021-09-15 | 2022-06-11 | 2022-03-15 | 2022-06-11 | 2022-09-15 | 2022-10-09 | 24 | 2023-03-14 | 2023-04-07 | 24 | 2023-11-03 | 2023-11-04 | 2023-11-27 | 2023-11-28 | 24 |  | 2024-03-15 | 2024-03-22 | 7 | 2024-11-30 | 2024-12-02 | 2024-12-06 | 2024-12-07 | 5 | 02 days Maint activity stopped for G-25 PM pending completion work. | PWEGPL38 | 2025-05-05 | 2025-05-07 | 2 | 100
14 | G 40 | CANTERY | 100261336 | 2015-01-28 | 2015-01-28 | 2015-07-28 | 2015-08-17 | 2016-01-28 | 2016-01-29 | 2016-07-28 | 2016-08-16 | 2017-01-28 | 2017-01-28 | 2017-07-28 | 2017-08-24 | 2018-01-28 | 2018-01-29 | 2018-07-28 | 2018-11-05 | 2019-01-23 | 2019-02-13 | 2019-09-20 | 2019-10-02 | 2020-03-18 | 2020-05-05 | 2020-09-14 | 2020-10-14 | 2021-03-18 | 2021-04-09 | 2021-09-15 | 2022-06-12 | 2022-03-16 | 2022-06-12 | 2022-09-15 | 2022-10-10 | 25 | 2023-03-14 | 2023-04-12 | 29 | 2023-11-05 | 2023-11-06 | 2023-11-29 | 2023-11-27 | 21 | PM team has taken weekly off and they continue to PM work on Sunday | 2024-03-16 | 2024-03-25 | 9 | 2024-12-03 | 2024-12-04 | 2024-12-08 | 2024-12-10 | 6 | PM postpone to 10-12-24 due to N2 Not avail. | PWEGPL39 | 2025-05-06 | 2025-05-15 | 9 | 100 | Delayed due to 8 employess GWO training(for 4days)
15 | G 26 | ABB | 100261404 | 2015-01-30 | 2015-01-30 | 2015-07-30 | 2015-08-19 | 2016-01-30 | 2016-01-30 | 2016-07-30 | 2016-08-18 | 2017-01-30 | 2017-02-04 | 2017-07-30 | 2017-08-11 | 2018-01-30 | 2018-01-30 | 2018-07-30 | 2018-11-06 | 2019-01-25 | 2019-02-20 | 2019-09-21 | 2019-10-03 | 2020-03-19 | 2020-05-16 | 2020-09-15 | 2020-10-20 | 2021-03-19 | 2021-04-19 | 2021-09-17 | 2022-06-13 | 2022-03-17 | 2022-06-13 | 2022-09-17 | 2022-10-11 | 24 | 2023-03-16 | 2023-04-14 | 29 | 2023-11-07 | 2023-11-08 | 2023-11-30 | 2023-12-01 | 23 | PM team-02 employees on leave. Date- 28-11-23 | 2024-03-18 | 2024-03-26 | 8 | 2024-12-05 | 2024-12-06 | 2024-12-12 | 2024-12-15 | 9 | PM Postpone 2day to 15-12-24 ,due to G-33 Pitch seal replacement work & team busy in 14-12-24 &G-26 B.D | PWEGPL40 | 2025-05-08 | 2025-05-16 | 8 | 100
16 | G 32 | ABB | 100261369 | 2015-02-03 | 2015-02-03 | 2015-08-03 | 2015-08-22 | 2016-02-03 | 2016-02-03 | 2016-08-03 | 2016-08-19 | 2017-02-03 | 2017-02-10 | 2017-08-03 | 2017-08-28 | 2018-02-03 | 2018-02-12 | 2018-08-03 | 2018-11-07 | 2019-01-29 | 2019-02-21 | 2019-09-22 | 2019-10-06 | 2020-03-20 | 2020-05-17 | 2020-09-16 | 2020-10-21 | 2021-03-22 | 2021-04-20 | 2021-09-17 | 2022-06-14 | 2022-03-18 | 2022-06-14 | 2022-09-17 | 2022-10-14 | 27 | 2023-03-16 | 2023-04-17 | 32 | 2023-11-09 | 2023-11-10 | 2023-12-01 | 2023-12-02 | 22 | PM team-02 employees on leave. Date- 29-11-23 | 2024-03-19 | 2024-03-16 | 3 | 2024-12-07 | 2024-12-09 | 2024-12-16 | 2024-12-17 | 8 | Delay due to G-26 ,pin ball hardware damaged from 12-dec-24 to 18-dec-24 | PWEGPL26 | 2025-05-09 | 2025-05-17 | 8 | 100
17 | G 28 | CANTERY | 100261339 | 2015-02-04 | 2015-02-04 | 2015-08-04 | 2015-08-28 | 2016-02-04 | 2016-02-04 | 2016-08-04 | 2016-08-23 | 2017-02-04 | 2017-02-09 | 2017-08-04 | 2017-09-01 | 2018-02-04 | 2018-03-07 | 2018-08-04 | 2018-11-08 | 2019-01-30 | 2019-02-26 | 2019-09-23 | 2019-10-07 | 2020-03-21 | 2020-05-12 | 2020-09-17 | 2020-12-20 | 2021-03-23 | 2021-04-10 | 2021-09-20 | 2022-05-28 | 2022-03-19 | 2022-05-28 | 2022-09-20 | 2022-09-30 | 10 | 2023-03-19 | 2023-03-29 | 10 | 2023-11-11 | 2023-11-12 | 2023-10-11 | 2023-11-04 | -8 | ROW at site office (11-10-23 to 16-10-23) for crane movement to G20 | 2024-03-20 | 2024-03-27 | 7 | 2024-12-10 | 2024-12-11 | 2024-12-20 | 2024-12-21 | 10 |  | PWEGPL32 | 2025-05-10 | 2025-05-18 | 8 | 100
18 | G 21 | CANTERY | 100261410 | 2015-03-30 | 2015-03-30 | 2015-09-30 | 2015-06-19 | 2016-03-30 | 2016-03-22 | 2016-09-30 | 2016-10-17 | 2017-03-30 | 2017-04-01 | 2017-09-29 | 2017-09-25 | 2018-03-30 | 2018-06-19 | 2018-09-29 | 2018-11-09 | 2019-03-25 | 2019-03-06 | 2019-09-24 | 2019-10-09 | 2020-03-22 | 2020-05-17 | 2020-09-18 | 2020-10-18 | 2021-03-24 | 2021-04-11 | 2021-09-20 | 2022-06-27 | 2022-03-21 | 2022-06-27 | 2022-09-20 | 2022-10-15 | 25 | 2023-03-19 | 2023-04-18 | 30 | 2023-11-13 | 2023-11-14 | 2023-12-05 | 2023-12-06 | 22 |  | 2024-03-22 | 2024-03-29 | 7 | 2024-12-12 | 2024-12-13 | 2025-03-11 | 2025-03-15 | 92 | Major B.D(Stopped due to Blade Root gap) on 15-July-24@12:51 ,Repair work completed on 15-Feb-25 | PWEGPL21 | 2025-05-11 | 2025-05-20 | 9 | 100
19 | G 22 | ABB | 100261399 | 2015-03-31 | 2015-03-31 | 2015-09-30 | 2015-09-03 | 2016-03-31 | 2016-03-29 | 2016-10-01 | 2016-10-04 | 2017-03-31 | 2017-04-04 | 2017-09-30 | 2017-09-26 | 2018-03-31 | 2018-06-21 | 2018-09-30 | 2018-11-10 | 2019-03-26 | 2019-03-07 | 2019-09-25 | 2019-10-12 | 2020-03-23 | 2020-05-19 | 2020-09-19 | 2020-12-15 | 2021-03-25 | 2021-04-22 | 2021-09-22 | 2022-07-05 | 2022-03-22 | 2022-07-05 | 2022-09-22 | 2022-10-16 | 24 | 2023-03-21 | 2023-04-19 | 29 | 2023-11-15 | 2023-11-16 | 2023-12-04 | 2023-12-05 | 19 |  | 2024-03-23 | 2024-03-30 | 7 | 2024-12-14 | 2024-12-16 | 2024-12-27 | 2024-12-28 | 12 |  | PWEGPL22 | 2025-05-12 | 2025-05-19 | 7 | 100
20 | G 23 | ABB | 100261392 | 2015-04-01 | 2015-04-01 | 2015-10-01 | 2015-06-22 | 2016-04-01 | 2016-03-31 | 2016-10-02 | 2016-10-18 | 2017-04-01 | 2017-04-07 | 2017-10-01 | 2017-11-14 | 2018-04-01 | 2018-06-22 | 2018-10-01 | 2018-11-12 | 2019-03-27 | 2019-02-15 | 2019-09-26 | 2019-10-13 | 2020-03-24 | 2020-05-18 | 2020-09-20 | 2020-12-16 | 2021-03-26 | 2021-04-24 | 2021-09-22 | 2022-06-28 | 2022-03-23 | 2022-06-28 | 2022-09-22 | 2022-12-20 | 89 | 2023-03-21 | 2023-05-06 | 46 | 2023-11-17 | 2023-11-18 | 2024-03-13 | 2024-03-14 | 117 | WTG under major BM blade crack | 2024-03-25 | 2024-03-14 | 11 | 2024-12-17 | 2024-12-18 | 2024-12-24 | 2024-12-26 | 8 |  | PWEGPL23 | 2025-05-13 | 2025-05-21 | 8 | 100
21 | G 05 | ABB | 100261396 | 2015-04-03 | 2015-04-03 | 2015-10-03 | 2015-10-03 | 2016-04-03 | 2016-04-25 | 2016-10-03 | 2016-10-03 | 2017-04-03 | 2017-04-08 | 2017-10-03 | 2017-11-15 | 2018-04-03 | 2018-06-27 | 2018-10-03 | 2018-11-14 | 2019-03-29 | 2019-03-08 | 2019-09-27 | 2019-10-14 | 2020-03-25 | 2020-04-25 | 2020-09-21 | 2020-12-11 | 2021-03-29 | 2021-04-25 | 2021-09-24 | 2022-06-24 | 2022-03-24 | 2022-06-24 | 2022-09-24 | 2022-12-21 | 88 | 2023-03-23 | 2023-05-07 | 45 | 2023-11-19 | 2023-11-20 | 2023-12-02 | 2023-12-04 | 14 |  | 2024-03-26 | 2024-04-01 | 6 | 2024-12-19 | 2024-12-20 | 2024-12-22 | 2024-12-23 | 3 | Little early taken due to HG temp error & resolved | PWEGPL05 | 2025-05-15 | 2025-05-22 | 7 | 100
22 | G 15 | ABB | 100261393 | 2015-04-05 | 2015-04-05 | 2015-10-05 | 2015-10-05 | 2016-04-05 | 2016-04-04 | 2016-10-05 | 2016-10-05 | 2017-04-05 | 2017-04-10 | 2017-10-05 | 2017-11-16 | 2018-04-05 | 2018-07-01 | 2018-10-05 | 2018-11-16 | 2019-03-31 | 2019-03-09 | 2019-09-28 | 2019-10-15 | 2020-03-26 | 2020-04-26 | 2020-09-22 | 2020-10-22 | 2021-03-30 | 2021-04-26 | 2021-09-24 | 2022-06-20 | 2022-03-25 | 2022-06-20 | 2022-09-24 | 2022-12-22 | 89 | 2023-03-23 | 2023-05-08 | 46 | 2023-11-21 | 2023-11-22 | 2023-12-12 | 2023-12-13 | 21 |  | 2024-03-27 | 2024-04-02 | 6 | 2024-12-21 | 2024-12-23 | 2024-12-29 | 2024-12-30 | 7 |  | PWEGPL15 | 2025-05-16 | 2025-05-23 | 7 | 100
23 | G 16 | ABB | 100261402 | 2015-04-06 | 2015-04-06 | 2015-10-06 | 2015-10-07 | 2016-04-06 | 2016-04-01 | 2016-10-06 | 2016-10-06 | 2017-04-06 | 2017-04-11 | 2017-10-06 | 2017-11-17 | 2018-04-06 | 2018-07-02 | 2018-10-06 | 2018-11-17 | 2019-04-01 | 2019-03-11 | 2019-09-29 | 2019-10-16 | 2020-03-27 | 2020-04-26 | 2020-09-23 | 2020-10-23 | 2021-03-31 | 2021-04-27 | 2021-09-27 | 2022-05-26 | 2022-03-26 | 2022-05-26 | 2022-09-27 | 2022-12-23 | 87 | 2023-03-26 | 2023-05-09 | 44 | 2023-11-23 | 2023-11-24 | 2023-12-13 | 2023-12-12 | 18 |  | 2024-03-29 | 2024-04-03 | 5 | 2024-12-24 | 2024-12-25 | 2025-01-02 | 2025-01-03 | 9 | PM team have taken off on 31/12/24 | PWEGPL16 | 2025-05-17 | 2025-05-24 | 7 | 100
24 | G 17 | ABB | 100261394 | 2015-04-07 | 2015-04-07 | 2015-10-07 | 2015-10-08 | 2016-04-07 | 2016-04-09 | 2016-10-07 | 2016-10-07 | 2017-04-07 | 2017-04-12 | 2017-10-07 | 2017-11-18 | 2018-04-07 | 2018-07-20 | 2018-10-07 | 2018-11-18 | 2019-04-02 | 2019-03-12 | 2019-09-30 | 2019-10-17 | 2020-03-28 | 2020-04-27 | 2020-09-24 | 2020-10-24 | 2021-04-01 | 2021-04-29 | 2021-09-27 | 2022-05-18 | 2022-03-28 | 2022-05-18 | 2022-09-27 | 2022-12-24 | 88 | 2023-03-26 | 2023-05-28 | 63 | 2023-11-25 | 2023-11-26 | 2023-12-10 | 2023-12-11 | 15 |  | 2024-03-30 | 2024-03-18 | 12 | 2024-12-26 | 2024-12-27 | 2025-01-04 | 2025-01-06 | 10 | PM team have taken off on 01/01/25 & on dated 05/01/25 PM cancelled due to vehicle issue | PWEGPL17 | 2025-05-18 | 2025-05-25 | 7 | 100
25 | G 18 | ABB | 100261254 | 2015-04-08 | 2015-04-08 | 2015-10-08 | 2015-10-09 | 2016-04-08 | 2016-04-15 | 2016-10-08 | 2016-10-08 | 2017-04-08 | 2017-04-13 | 2017-10-08 | 2017-11-20 | 2018-04-08 | 2018-07-16 | 2018-10-08 | 2018-11-19 | 2019-04-03 | 2019-03-13 | 2019-10-01 | 2019-10-18 | 2020-03-29 | 2020-04-27 | 2020-09-25 | 2020-12-07 | 2021-04-02 | 2021-04-30 | 2021-09-29 | 2022-07-01 | 2022-03-29 | 2022-07-01 | 2022-09-29 | 2022-12-25 | 87 | 2023-03-28 | 2023-05-29 | 62 | 2023-11-27 | 2023-11-28 | 2023-12-09 | 2023-12-11 | 13 | Team-01 assigned Yaw drive replacement work at G-15 | 2024-04-01 | 2024-04-04 | 3 | 2024-12-28 | 2024-12-30 | 2025-01-07 | 2025-01-08 | 9 |  | PWEGPL18 | 2025-05-19 | 2025-05-26 | 7 | 100
26 | G 19 | ABB | 100261400 | 2015-04-10 | 2015-04-10 | 2015-10-10 | 2015-10-10 | 2016-04-10 | 2016-04-16 | 2016-10-10 | 2016-10-09 | 2017-04-10 | 2017-04-17 | 2017-10-10 | 2017-11-21 | 2018-04-10 | 2018-07-19 | 2018-10-10 | 2018-11-20 | 2019-04-05 | 2019-03-14 | 2019-10-02 | 2019-10-20 | 2020-03-30 | 2020-04-28 | 2020-09-26 | 2020-12-04 | 2021-04-05 | 2021-05-04 | 2021-09-29 | 2022-06-17 | 2022-03-30 | 2022-06-17 | 2022-09-29 | 2022-12-26 | 88 | 2023-03-28 | 2023-05-29 | 62 | 2023-11-29 | 2023-11-30 | 2023-12-07 | 2023-12-08 | 8 |  | 2024-04-02 | 2024-04-05 | 3 | 2024-12-31 | 2025-01-01 | 2025-01-10 | 2025-01-11 | 10 | on dated 09-Jan-25 ,PM cancelled due to G-18 PM Pending point Closing work | PWEGPL19 | 2025-05-20 | 2025-05-26 | 6 | 100
27 | G 20 | ABB | 100261395 | 2015-04-27 | 2015-04-27 | 2015-10-27 | 2015-10-27 | 2016-04-27 | 2016-04-07 | 2016-10-27 | 2016-10-10 | 2017-04-27 | 2017-04-27 | 2017-10-27 | 2017-11-22 | 2018-04-27 | 2018-07-17 | 2018-10-27 | 2018-11-25 | 2019-04-22 | 2019-03-16 | 2019-10-03 | 2019-10-21 | 2020-03-31 | 2020-04-28 | 2020-09-27 | 2020-12-09 | 2021-04-06 | 2021-05-05 | 2021-10-01 | 2022-06-30 | 2022-03-31 | 2022-06-30 | 2022-10-01 | 2022-12-27 | 87 | 2023-03-30 | 2023-05-30 | 61 | 2023-12-01 | 2023-12-02 | 2023-12-06 | 2023-12-07 | 5 |  | 2024-04-03 | 2024-04-06 | 3 | 2025-01-02 | 2025-01-03 | 2025-01-12 | 2025-01-13 | 10 |  | PWEGPL20 | 2025-05-22 | 2025-05-27 | 5 | 100
28 | G 14 | CANTERY | 100261409 | 2015-04-29 | 2015-04-29 | 2015-10-29 | 2015-10-28 | 2016-04-29 | 2016-04-07 | 2016-10-29 | 2016-10-12 | 2017-04-29 | 2017-04-29 | 2017-10-29 | 2017-11-27 | 2018-04-29 | 2018-07-23 | 2018-10-29 | 2018-11-26 | 2019-04-24 | 2019-04-03 | 2019-10-04 | 2019-10-22 | 2020-04-01 | 2020-04-29 | 2020-09-28 | 2020-10-28 | 2021-04-07 | 2021-04-15 | 2021-10-01 | 2022-07-04 | 2022-04-01 | 2022-07-04 | 2022-10-01 | 2022-12-28 | 88 | 2023-03-30 | 2023-05-30 | 61 | 2023-12-03 | 2023-12-04 | 2023-12-15 | 2023-12-14 | 10 |  | 2024-04-04 | 2024-04-08 | 4 | 2025-01-04 | 2025-01-06 | 2025-01-14 | 2025-01-20 | 14 | on the date 15-01-25 PM Team Taken w-off | PWEGPL14 | 2025-05-23 | 2025-05-28 | 5 | 100
29 | G 13 | CANTERY | 100261219 | 2015-04-30 | 2015-04-30 | 2015-10-30 | 2015-10-29 | 2016-04-30 | 2016-04-11 | 2016-10-30 | 2016-11-25 | 2017-04-30 | 2017-04-30 | 2017-10-30 | 2017-11-28 | 2018-04-30 | 2018-07-24 | 2018-10-30 | 2018-11-27 | 2019-04-25 | 2019-04-04 | 2019-10-05 | 2019-10-23 | 2020-04-02 | 2020-04-29 | 2020-09-29 | 2020-12-02 | 2021-04-08 | 2021-05-06 | 2021-10-04 | 2022-07-03 | 2022-04-02 | 2022-07-03 | 2022-10-04 | 2022-12-29 | 86 | 2023-04-02 | 2023-05-31 | 59 | 2023-12-05 | 2023-12-06 | 2023-12-14 | 2023-12-15 | 9 |  | 2024-04-05 | 2024-04-09 | 4 | 2025-01-07 | 2025-01-08 | 2025-01-21 | 2025-01-22 | 14 | PM Postpone to 20-01-24,due to recreational(Sports) event as per sidhu's mail communication | PWEGPL13 | 2025-05-24 | 2025-05-29 | 5 | 100
30 | G 12 | ABB | 100261370 | 2015-05-04 | 2015-05-04 | 2015-11-04 | 2015-10-30 | 2016-05-04 | 2016-05-02 | 2016-11-04 | 2016-10-13 | 2017-05-04 | 2017-05-22 | 2017-11-04 | 2017-11-23 | 2018-05-04 | 2018-07-31 | 2018-11-04 | 2018-11-28 | 2019-04-29 | 2019-04-07 | 2019-10-06 | 2019-10-24 | 2020-04-03 | 2020-04-30 | 2020-09-30 | 2020-11-30 | 2021-04-09 | 2021-05-07 | 2021-10-04 | 2022-07-02 | 2022-04-04 | 2022-07-02 | 2022-10-04 | 2022-12-30 | 87 | 2023-04-02 | 2023-05-31 | 59 | 2023-12-07 | 2023-12-08 | 2023-12-20 | 2023-12-19 | 11 |  | 2024-04-06 | 2024-04-10 | 4 | 2025-01-09 | 2025-01-10 | 2025-01-23 | 2025-01-24 | 14 |  | PWEGPL12 | 2025-05-25 | 2025-05-31 | 6 | 100
31 | G 09 | ABB | 100261253 | 2015-05-05 | 2015-05-05 | 2015-11-05 | 2015-11-04 | 2016-05-05 | 2016-05-21 | 2016-11-05 | 2016-10-15 | 2017-05-05 | 2017-05-23 | 2017-11-05 | 2017-11-24 | 2018-05-05 | 2018-07-25 | 2018-11-05 | 2018-11-30 | 2019-04-30 | 2019-04-06 | 2019-10-07 | 2019-10-25 | 2020-04-04 | 2020-05-01 | 2020-10-01 | 2020-10-31 | 2021-04-12 | 2021-05-08 | 2021-10-06 | 2022-06-07 | 2022-04-05 | 2022-06-07 | 2022-10-06 | 2022-12-30 | 85 | 2023-04-04 | 2023-06-01 | 58 | 2023-12-09 | 2023-12-10 | 2023-12-19 | 2023-12-20 | 10 |  | 2024-04-08 | 2024-04-11 | 3 | 2025-01-11 | 2025-01-13 | 2025-01-25 | 2025-01-27 | 14 | PM Cancelled in 26th jan ,Republic day | PWEGPL09 | 2025-05-26 | 2025-06-01 | 6 | 100
32 | G 08 | ABB | 100261398 | 2015-05-07 | 2015-05-07 | 2015-11-07 | 2015-11-05 | 2016-05-07 | 2016-04-23 | 2016-11-07 | 2016-10-19 | 2017-05-07 | 2017-05-24 | 2017-11-07 | 2017-11-25 | 2018-05-07 | 2018-07-26 | 2018-11-07 | 2018-12-01 | 2019-05-02 | 2019-04-09 | 2019-10-08 | 2019-10-26 | 2020-04-05 | 2020-05-02 | 2020-10-02 | 2020-11-22 | 2021-04-13 | 2021-05-09 | 2021-10-06 | 2022-06-29 | 2022-04-06 | 2022-06-29 | 2022-10-06 | 2022-12-31 | 86 | 2023-04-04 | 2023-06-01 | 58 | 2023-12-11 | 2023-12-12 | 2023-12-22 | 2023-12-21 | 9 |  | 2024-04-09 | 2024-04-12 | 3 | 2025-01-14 | 2025-01-15 | 2025-01-28 | 2025-01-29 | 14 |  | PWEGPL08 | 2025-05-27 | 2025-06-02 | 6 | 100
33 | G 06 | CANTERY | 100261216 | 2015-05-08 | 2015-05-08 | 2015-11-08 | 2015-11-06 | 2016-05-08 | 2016-05-08 | 2016-11-08 | 2016-10-20 | 2017-05-08 | 2017-05-25 | 2017-11-08 | 2017-11-29 | 2018-05-08 | 2018-07-27 | 2018-11-08 | 2018-12-02 | 2019-05-03 | 2019-05-21 | 2019-10-09 | 2019-10-28 | 2020-04-06 | 2020-05-03 | 2020-10-03 | 2020-12-21 | 2021-04-14 | 2021-05-10 | 2021-10-08 | 2022-06-26 | 2022-04-07 | 2022-06-26 | 2022-10-08 | 2023-01-02 | 86 | 2023-04-06 | 2023-06-03 | 58 | 2023-12-13 | 2023-12-14 | 2023-12-21 | 2023-12-22 | 8 |  | 2024-04-10 | 2024-04-13 | 3 | 2025-01-16 | 2025-01-17 | 2025-01-30 | 2025-01-31 | 14 |  | PWEGPL06 | 2025-05-29 | 2025-06-05 | 7 | 100
34 | G 03 | ABB | 100261397 | 2015-05-09 | 2015-05-09 | 2015-11-09 | 2015-11-07 | 2016-05-09 | 2016-05-10 | 2016-11-09 | 2016-10-22 | 2017-05-09 | 2017-05-26 | 2017-11-09 | 2017-12-03 | 2018-05-09 | 2018-07-28 | 2018-11-09 | 2018-12-03 | 2019-05-04 | 2019-05-22 | 2019-10-10 | 2019-10-30 | 2020-04-07 | 2020-05-04 | 2020-10-04 | 2020-11-04 | 2021-04-15 | 2021-05-11 | 2021-10-08 | 2022-06-25 | 2022-04-08 | 2022-06-25 | 2022-10-08 | 2023-01-03 | 87 | 2023-04-06 | 2023-06-03 | 58 | 2023-12-15 | 2023-12-16 | 2023-12-25 | 2023-12-23 | 7 |  | 2024-04-11 | 2024-04-15 | 4 | 2025-01-18 | 2025-01-20 | 2025-02-01 | 2025-02-05 | 16 | Day-02 Activity not taken due to N2 Not avail.(& day-2 taken after G-04) | PWEGPL03 | 2025-05-30 | 2025-06-06 | 7 | 100
35 | G 04 | CANTERY | 100261342 | 2015-05-10 | 2015-05-10 | 2015-11-10 | 2015-11-25 | 2016-05-10 | 2016-05-12 | 2016-11-10 | 2016-10-23 | 2017-05-10 | 2017-05-29 | 2017-11-10 | 2017-12-10 | 2018-05-10 | 2018-08-02 | 2018-11-10 | 2018-12-04 | 2019-05-05 | 2019-05-26 | 2019-10-11 | 2019-10-31 | 2020-04-08 | 2020-05-05 | 2020-10-05 | 2020-11-20 | 2021-04-16 | 2021-05-25 | 2021-10-11 | 2022-06-22 | 2022-04-09 | 2022-06-22 | 2022-10-11 | 2023-01-04 | 85 | 2023-04-09 | 2023-06-04 | 56 | 2023-12-17 | 2023-12-18 | 2023-12-23 | 2023-12-25 | 7 |  | 2024-04-12 | 2024-04-16 | 4 | 2025-01-21 | 2025-01-22 | 2025-02-02 | 2025-02-04 | 13 | Day-02 not taken due to Annual Blood donation drive | PWEGPL04 | 2025-05-31 | 2025-06-07 | 7 | 100
36 | G 02 | ABB | 100261373 | 2015-05-11 | 2015-05-11 | 2015-11-11 | 2015-11-08 | 2016-05-11 | 2016-05-13 | 2016-11-11 | 2016-10-24 | 2017-05-11 | 2017-05-30 | 2017-11-11 | 2017-12-09 | 2018-05-11 | 2018-08-01 | 2018-11-11 | 2018-12-05 | 2019-05-06 | 2019-05-27 | 2019-10-12 | 2019-11-04 | 2020-04-09 | 2020-05-06 | 2020-10-06 | 2020-11-18 | 2021-04-19 | 2021-05-26 | 2021-10-11 | 2022-06-21 | 2022-04-11 | 2022-06-21 | 2022-10-11 | 2023-01-05 | 86 | 2023-04-09 | 2023-06-05 | 57 | 2023-12-19 | 2023-12-20 | 2023-12-28 | 2023-12-29 | 9 |  | 2024-04-13 | 2024-04-18 | 5 | 2025-01-23 | 2025-01-24 | 2025-02-06 | 2025-02-07 | 14 |  | PWEGPL02 | 2025-06-01 | 2025-06-10 | 9 | 100
37 | G 07 | CANTERY | 100261361 | 2015-05-16 | 2015-05-16 | 2015-11-16 | 2015-11-09 | 2016-05-16 | 2016-05-20 | 2016-11-16 | 2016-11-28 | 2017-05-16 | 2017-05-31 | 2017-11-16 | 2017-12-13 | 2018-05-16 | 2018-07-30 | 2018-11-16 | 2018-12-06 | 2019-05-11 | 2019-05-28 | 2019-10-13 | 2019-11-02 | 2020-04-10 | 2020-05-07 | 2020-10-07 | 2020-11-11 | 2021-04-20 | 2021-04-13 | 2021-10-13 | 2022-06-19 | 2022-04-12 | 2022-06-19 | 2022-10-13 | 2023-01-06 | 85 | 2023-04-11 | 2023-06-05 | 55 | 2023-12-21 | 2023-12-22 | 2023-12-27 | 2023-12-26 | 4 |  | 2024-04-15 | 2024-04-19 | 4 | 2025-01-25 | 2025-01-27 | 2025-02-08 | 2025-02-10 | 14 |  | PWEGPL07 | 2025-06-02 | 2025-06-11 | 9 | 100
38 | G 01 | CANTERY | 100261335 | 2015-05-17 | 2015-05-17 | 2015-11-17 | 2015-11-10 | 2016-05-17 | 2016-05-16 | 2016-11-17 | 2016-11-29 | 2017-05-17 | 2017-06-01 | 2017-11-17 | 2017-12-14 | 2018-05-17 | 2018-08-03 | 2018-11-17 | 2018-12-07 | 2019-05-12 | 2019-05-30 | 2019-10-14 | 2019-11-03 | 2020-04-11 | 2020-05-09 | 2020-10-08 | 2020-11-08 | 2021-04-21 | 2021-04-14 | 2021-10-13 | 2022-06-18 | 2022-04-13 | 2022-06-18 | 2022-10-13 | 2023-01-07 | 86 | 2023-04-11 | 2023-06-04 | 54 | 2023-12-23 | 2023-12-24 | 2023-12-26 | 2023-12-27 | 3 |  | 2024-04-16 | 2024-04-21 | 5 | 2025-01-28 | 2025-01-29 | 2025-02-11 | 2025-02-12 | 14 |  | PWEGPL01 | 2025-06-03 | 2025-06-12 | 9 | 100
39 | G 10 | ABB | 100261401 | 2015-05-20 | 2015-05-20 | 2015-11-20 | 2015-11-26 | 2016-05-20 | 2016-05-11 | 2016-11-20 | 2016-11-30 | 2017-05-20 | 2017-06-02 | 2017-11-20 | 2017-12-15 | 2018-05-20 | 2018-06-29 | 2018-11-20 | 2018-12-08 | 2019-05-15 | 2019-05-29 | 2019-10-15 | 2019-11-05 | 2020-04-12 | 2020-05-10 | 2020-10-09 | 2020-11-26 | 2021-04-22 | 2021-05-27 | 2021-10-15 | 2022-06-16 | 2022-04-14 | 2022-06-16 | 2022-10-15 | 2023-01-09 | 86 | 2023-04-13 | 2023-06-02 | 50 | 2023-12-25 | 2023-12-26 | 2024-01-02 | 2023-12-31 | 5 |  | 2024-04-17 | 2024-04-22 | 5 | 2025-01-30 | 2025-01-31 | 2025-02-13 | 2025-02-14 | 14 |  | PWEGPL10 | 2025-06-05 |  | -45813 | -50786.6667
40 | G 11 | ABB | 100261173 | 2015-05-21 | 2015-05-21 | 2015-11-21 | 2015-10-16 | 2016-05-21 | 2016-05-17 | 2016-11-21 | 2016-12-01 | 2017-05-21 | 2017-06-03 | 2017-11-21 | 2017-12-16 | 2018-05-21 | 2018-06-18 | 2018-11-21 | 2018-12-09 | 2019-05-16 | 2019-04-19 | 2019-10-16 | 2019-11-06 | 2020-04-13 | 2020-05-11 | 2020-10-10 | 2020-11-28 | 2021-04-23 | 2021-05-28 | 2021-10-15 | 2022-06-15 | 2022-04-15 | 2022-06-15 | 2022-10-15 | 2023-01-08 | 85 | 2023-04-13 | 2023-06-02 | 50 | 2023-12-27 | 2023-12-28 | 2023-12-29 | 2023-12-28 | 0 |  | 2024-04-18 | 2024-04-23 | 5 | 2025-02-01 | 2025-02-02 | 2025-02-15 | 2025-02-17 | 15 | PM 1day postpone due to G-37 B.D(HU oil level)so replaced 3nos accumulator | PWEGPL11 | 2025-06-06 | 2025-06-03 | -3 | 100

## Spar Parts Consumption
Sr. No. | Date | Location | Material Name | Quantity | UoM | Remark
1 | 2025-03-29 | G36 | shim (1mm) | 4 | pc
2 | 2025-03-29 | G36 | AI module | 2 | pc
3 | 2025-03-30 | G35 | Yaw motor (Bonifigoli) | 1 | pc
4 | 2025-03-30 | G35 | Yaw contactor (26-30-10) | 1 | pc
5 | 2025-03-30 | G35 | Addon (NC) | 1 | pc
6 | 2025-03-30 | G01 | Yaw motor (Bonifigoli) | 1 | pc
7 | 2025-04-01 | G01 | proportional valve | 1 | pc
8 | 2025-04-01 | G38 | Hydraulic Oil | 5 | liter
9 | 2025-04-01 | G36 | WS251 cable | 1 | pc
10 | 2025-04-01 | G30 | netural relay | 1 | pc
11 | 2025-04-03 | G32 | cab module 9 pin | 1 | pc
12 | 2025-04-03 | G33 | WS240 cable | 1 | pc
13 | 2025-04-04 | G08 | Yaw motor | 1 | pc
14 | 2025-04-07 | G33 | Pitch seal kit | 1 | set
15 | 2025-04-07 | G33 | Gear box oil | 15 | liter
16 | 2025-04-09 | G09 | CCU coolant motor | 1 | pc
17 | 2025-04-09 | G09 | MPCB | 1 | pc
18 | 2025-04-09 | G04 | HU contactor | 1 | pc
19 | 2025-04-10 | G14 | Pitch seal kit | 1 | set
20 | 2025-04-10 | G03 | Gear box hose | 1 | pc
21 | 2025-04-11 | G18 | ACB reley (F5103057) | 1 | set
22 | 2025-04-13 | G26 | Gear box hose | 1 | pc
23 | 2025-04-15 | G39 | Pitch seal kit | 1 | set
24 | 2025-04-15 | G39 | HU contactor (52-30-10) | 1 | pc
25 | 2025-04-15 | G39 | NO addon | 1 | pc
26 | 2025-04-17 | G15 | Proportional valve | 1 | pc
27 | 2025-04-19 | G23 | HU contactor (52-30-10) | 1 | pc
28 | 2025-04-19 | G23 | Pitch seal kit | 1 | pc
29 | 2025-04-19 | G23 | HU oil | 10 | liter
30 | 2025-04-21 | G16 | Brush holder | 3 | pc
31 | 2025-04-21 | G16 | Brush holder spring | 7 | pc
32 | 2025-04-22 | G32 | Transformer fan | 3 | pc
33 | 2025-04-22 | G13 | CCU coolant motor | 1 | pc
34 | 2025-04-23 | G25 | Transformer fan | 3 | pc
35 | 2025-04-24 | G26 | Transformer fan | 3 | pc
36 | 2025-04-24 | G40 | Transformer fan | 5 | pc
37 | 2025-04-25 | G19 | Yaw encoder | 1 | pc
38 | 2025-04-25 | G12 | Plc Flash card | 1 | pc
39 | 2025-04-25 | G39 | Pitch seal kit | 1 | pc
40 | 2025-04-26 | G06 | Transformer fan | 3 | pc
41 | 2025-04-28 | G20 | Accumulator (24 liter) 143 bar | 1 | pc
42 | 2025-04-29 | G07 | OGS garud | 1 | pc
43 | 2025-04-29 | G22 | Hub Main accumulator (143 bar) 24 liter | 1 | pc
44 | 2025-04-29 | G22 | Gear box hose | 1 | pc
45 | 2025-04-29 | G04 | RV 8-10 | 2 | pc
46 | 2025-04-29 | G04 | Electro operate valve | 2 | pc
47 | 2025-04-30 | G07 | Pitch seal kit | 1 | set
48 | 2025-04-30 | G22 | HU Contactor | 1 | pc
49 | 2025-04-30 | G22 | Addon (NO) | 1 | pc
50 | 2025-05-02 | G07 | Pitch seal kit | 1 | set
51 | 2025-05-02 | G07 | HU oil | 15 | liter
52 | 2025-05-02 | G18 | Brush holder | 3 | pc
53 | 2025-05-02 | G18 | Brush holder spring | 8 | pc
54 | 2025-05-03 | G19 | Pitch seal kit | 1 | set
55 | 2025-05-05 | G01 | Yaw Caliper Seal | 2 | set
56 | 2025-05-06 | G26 | Pitch cylinder | 1 | pc
57 | 2025-05-06 | G26 | HU oil | 22 | liter
58 | 2025-05-08 | G22 | MPCB (1.6 to 2.4) | 1 | pc
59 | 2025-05-08 | G22 | Contactor (12-30-10) | 1 | pc
60 | 2025-05-08 | G37 | Pitch seal kit | 1 | pc
61 | 2025-05-09 | G37 | 33k Resistor | 1 | pc
62 | 2025-05-09 | G37 | RC bus filter card | 1 | pc
63 | 2025-05-10 | G04 | PRV-10 valve | 1 | pc
64 | 2025-05-10 | G04 | RV 8-10 valve | 1 | pc
65 | 2025-05-10 | G09 | Propotional Valve | 1 | pc
66 | 2025-05-11 | G23 | Slipring unit | 1 | pc
67 | 2025-05-11 | G23 | CAB Module | 1 | pc
68 | 2025-05-11 | G21 | KC004 contactor | 1 | pc
69 | 2025-05-12 | G23 | CAB Module | 1 | pc
70 | 2025-05-12 | G04 | Needle Valve | 1 | pc
71 | 2025-05-14 | G14 | Single Drive card | 3 | pc
72 | 2025-05-14 | G14 | IGBT | 3 | pc
73 | 2025-05-14 | G14 | 125A Fuse | 2 | pc
74 | 2025-05-14 | G14 | KC002 Contactor | 1 | pc
75 | 2025-05-14 | G14 | 800 HC Resistor | 6 | pc
76 | 2025-05-14 | G04 | Hydraulic pump hose | 1 | pc
77 | 2025-05-15 | G33 | Power supply (10 Amp) | 1 | pc
78 | 2025-05-15 | G33 | Gearbox fan cooling motor | 1 | pc
79 | 2025-05-15 | G40 | Tee - Connector | 1 | set
80 | 2025-05-16 | G04 | Gear box fan cooling motor | 1 | pc
81 | 2025-05-17 | G19 | Pitch cylinder | 1 | pc
82 | 2025-05-17 | G06 | Sealant | 1 | pc
83 | 2025-05-20 | G10 | Lift guide clamp | 4 | pc
84 | 2025-05-21 | G33 | HU oil | 10 | liter
85 | 2025-05-22 | G38 | Carbon brush ABB | 26 | pc
86 | 2025-05-22 | G38 | Carbon brush Spring ABB | 4 | pc
87 | 2025-05-24 | G26 | HU main accumulator (32 liter) | 1 | pc
88 | 2025-05-26 | G25 | MPCB (1.6 to 2.4) | 1 | pc
89 | 2025-05-26 | G30 | HU contactor (52-30-10) | 1 | pc
90 | 2025-05-28 | G33 | Power supply (20 Amp) | 1 | pc
91 | 2025-05-29 | G33 | Gear box damper | 2 | pc
92 | 2025-05-30 | G28 | Proportional valve | 1 | pc
93 | 2025-05-30 | G25 | Coolant pump with motor | 1 | set
94 | 2025-05-30 | G16 | Addon | 1 | pc
95 | 2025-05-30 | G04 | PRV-10 valve | 1 | pc
96 | 2025-05-31 | G25 | Coolant motor | 1 | pc
97 | 2025-06-02 | G04 | HU hose (GP037088 | 1 | pc
98 | 2025-06-02 | G20 | CCU cooling motor | 1 | pc
99 | 2025-06-02 | G33 | Carbon brush | 8 | pc
100 | 2025-06-02 | G35 | carbon brush | 10 | pc
101 | 2025-06-03 | G20 | MPCB (1.6 to 2.4) | 1 | pc
102 | 2025-06-05 | G36 | Carbon brush | 18 | pc
103 | 2025-06-05 | G36 | Carbon brush Spring ABB | 4 | pc
104 | 2025-06-06 | G14 | PRV8-10 valve | 1 | pc
105 | 2025-06-06 | G37 | Accumulator (24 liter) 143 bar | 1 | pc
106 | 2025-06-10 | G23 | Lift guide clamp | 1 | pc
107 | 2025-06-10 | G23 | Carbon brush | 2 | pc
108 | 2025-06-10 | G23 | Carbon brush Spring ABB | 1 | pc
109 | 2025-06-10 | G15 | gadus | 1 | pc
110 | 2025-06-10 | G16 | gadus | 1 | pc
111 | 2025-06-10 | G14 | PRV1-10 valve | 2 | pc
112 | 2025-06-10 | G14 | RV8-10 valve | 2 | pc
113
114
115
116
117
118
119
120
121
122
123
124
125
126
127
128
129
130
131
132
133
134
135
136
137
138
139
140
141
142
143
144
145

## Basic Data (hidden)
[12 empty] | 100 | Yawing Sensor Failure | Fault Category
| Generator | Consumer | Capacity | % Plant Equiva. Weightage | Feeder | TX | USS | MY |  |  |  | 101 | Maximum Winding Error | WTG Unscheduled Maintenance | IG Unscheduled Maintenance | EG Unscheduled Maintenance
G01 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F3 | TX2 | G01 |  | Total Capacity | 78 | Open | 102 | CW Feedback Failure | WTG Breakdown Maintenance | IG Breakdown Maintenance | EG Breakdown Maintenance
G02 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F3 | TX2 | G02 |  |  |  | Close | 103 | CCW Feedback Failure | WTG Scheduled Maintenance | IG Scheduled Maintenance | EG Scheduled Maintenance
G03 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F3 | TX2 | G03 |  |  |  |  | 104 | Max Orientation Time | WTG Environmental | IG Force Majeure | EG Force Majeure
G04 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F3 | TX2 | G04 |  |  |  |  | 105 | Maximum Unwinding Time | WTG Force Majeure
G05 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F2 | TX1 | G05 |  |  |  |  | 106 | Unwinding Error
G06 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F3 | TX2 | G06 |  |  |  |  | 107 | Yawing Motor Thermal Relays
G07 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F3 | TX2 | G07 |  |  |  |  | 108 | Automatic Unwinding
G08 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F3 | TX2 | G08 |  |  |  |  | 110 | Yaw Sensor Wiring Error
G09 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F4 | TX2 | G09 |  |  |  |  | 112 | Yaw Beak Wear
G10 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F3 | TX2 | G10 |  |  |  |  | 114 | Low Yaw Brake Pressure
G11 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F3 | TX2 | G11 |  |  |  |  | 115 | High Yaw Brake Pressure
G12 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F4 | TX2 | G12 |  |  |  |  | 116 | Orienting and High Yaw Brake Pressure
G13 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F4 | TX2 | G13 |  |  |  |  | 117 | Orienting and Low Yaw Brake Pressure
G14 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F4 | TX2 | G14 |  |  |  |  | 118 | Yaw Motors Error
G15 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F4 | TX2 | G15 |  |  |  |  | 119 | Yaw Contactor Active
G16 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F4 | TX2 | G16 |  |  |  |  | 121 | Low Grease Level for Yaw Plates
G17 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F4 | TX2 | G17 |  |  |  |  | 122 | Yaw Plate Lubrication Failure
G18 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F4 | TX2 | G18 |  |  |  |  | 123 | Low Grease Level For Yaw Pinion
G19 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F4 | TX2 | G19 |  |  |  |  | 124 | Yaw Pinion Lubrication Failure
G20 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F4 | TX2 | G20 |  |  |  |  | 125 | Yaw Motors Over Current Protection
G21 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F2 | TX1 | G21 |  |  |  |  | 126 | Excessive Yaw Drag
G22 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F2 | TX1 | G22 |  |  |  |  | 127 | Possible Yaw Circuit Leakages
G23 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F2 | TX1 | G23 |  |  |  |  | 128 | Auto Yaw Not Possible
G25 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F2 | TX1 | G25 |  |  |  |  | 130 | Yaw Pinion Lubrication Failure Too Long
G26 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F1 | TX1 | G26 |  |  |  |  | 200 | Minimum Hydraulic Unit Temperature
G27 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F2 | TX1 | G27 |  |  |  |  | 201 | Max. Pump time
G28 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F2 | TX1 | G28 |  |  |  |  | 202 | Low Pressure On Brake Circuit
G29 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F2 | TX1 | G29 |  |  |  |  | 203 | Low Pressure On Hydraulic Group
G30 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F2 | TX1 | G30 |  |  |  |  | 204 | Hydraulic Filter Dirty
G31 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F2 | TX1 | G31 |  |  |  |  | 205 | Low Level Hydraulic Group Refrigeration Oil
G32 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F1 | TX1 | G32 |  |  |  |  | 207 | Hydraulic Oil High Temperature
G33 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F1 | TX1 | G33 |  |  |  |  | 208 | HU Pump Drive Failure
G34 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F1 | TX1 | G34 |  |  |  |  | 211 | Hydraulic HUB Filter Dirty
G35 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F1 | TX1 | G35 |  |  |  |  | 212 | Leakage In The HUB
G36 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F1 | TX1 | G36 |  |  |  |  | 213 | Hydraulic Pump Protection
G37 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F1 | TX1 | G37 |  |  |  |  | 214 | Maximum HU Preheating Time
G38 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F1 | TX1 | G38 |  |  |  |  | 217 | Warning Load Control valve Malfunction
G39 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F1 | TX1 | G39 |  |  |  |  | 218 | Low Oil Temperature : Heating Procedure Request
G40 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F1 | TX1 | G40 |  |  |  |  | 219 | Hydraulic Unit Alarm Temperature
Wind_F1 | PWEGPL | MSEDCL | 20 | 25.64% | [7 empty] | 221 | Hydraulic Unit Cooling Failure
Wind_F1_Ckt1 | PWEGPL | MSEDCL | 10 | 12.82%
Wind_F1_Ckt2 | PWEGPL | MSEDCL | 10 | 12.82%
Wind_F2 | PWEGPL | MSEDCL | 20 | 25.64% | [7 empty] | 222 | Very Low Pressure On Hydraulic Unit
Wind_F2_Ckt1 | PWEGPL | MSEDCL | 8 | 10.26%
Wind_F2_Ckt2 | PWEGPL | MSEDCL | 12 | 15.38%
Wind_F3 | PWEGPL | MSEDCL | 18 | 23.08% | [7 empty] | 223 | Very High Temperature Of Hydraulic Unit Oil
Wind_F3_Ckt1 | PWEGPL | MSEDCL | 10 | 12.82%
Wind_F3_Ckt2 | PWEGPL | MSEDCL | 8 | 10.26%
Wind_F4 | PWEGPL | MSEDCL | 20 | 25.64% | [7 empty] | 226 | Hydraulic Filter Dirty Too Long
Wind_F4_Ckt1 | PWEGPL | MSEDCL | 10 | 12.82%
Wind_F4_Ckt2 | PWEGPL | MSEDCL | 10 | 12.82%
TX1 | PWEGPL | MSEDCL | 40 | 51.28% | [7 empty] | 227 | Hydraulic HUB Filter Dirty Too Long
TX2 | PWEGPL | MSEDCL | 38 | 48.72% | [7 empty] | 228 | Time Out For Oil Heating In Operation
Line1 | PWEGPL | MSEDCL | 78 | 100% | [7 empty] | 300 | Anemo Failure
[12 empty] | 302 | High Wind Speed
[12 empty] | 303 | TOP Zero Degrees
[12 empty] | 304 | Ambient Temperature Low
[12 empty] | 305 | Ambient Temperature High
[12 empty] | 306 | High Temperature On Trafo Winding
[12 empty] | 307 | Overheating On Trafo Winding
[12 empty] | 309 | Smoke Sensor
[12 empty] | 310 | Machine On Preheating
[12 empty] | 312 | Zero Degrees HUB
[12 empty] | 313 | Very High Disalignment
[12 empty] | 314 | High Misalignment and Orienting Badly
[12 empty] | 315 | Beacon Failure
[12 empty] | 317 | Low Nacelle Temperature
[12 empty] | 318 | High Nacelle Temperature
[12 empty] | 319 | Ice On Nacelle
[12 empty] | 320 | Ice Sensor Error
[12 empty] | 321 | Low Ground Cabinet Temperature
[12 empty] | 324 | High Temperature Kit System Failure
[12 empty] | 325 | High Temperature Kit Feedback Failure
[12 empty] | 326 | Low Temperature Kit System Failure
[12 empty] | 327 | Low Temperature Kit Feedback Error
[12 empty] | 341 | Ice Shake
[12 empty] | 343 | Turbine Under Ice Operation
[12 empty] | 344 | High Temperature In Auxiliary Transformer
[12 empty] | 345 | Very High Temperature In Auxiliary Transformer
[12 empty] | 347 | GUYS Functionality Active
[12 empty] | 349 | Transformer Winding High Temperature Warning
[12 empty] | 352 | Converter Water Pressure High
[12 empty] | 354 | Converter Water Pressure Low
[12 empty] | 356 | Auxiliary Transformer Windings High Temperature Warning
[12 empty] | 357 | SADEI System Failure
[12 empty] | 360 | High Wind Turbulence Intensity Alarm
[12 empty] | 361 | VHT - Top Cabinet Maximum Temperature
[12 empty] | 362 | VHT - Ground Cabinet Maximum Temperature
[12 empty] | 363 | VHT - HUB Cabinet Maximum Temperature
[12 empty] | 364 | VHT - Air Conditioning Top Cabinet Feedback
[12 empty] | 365 | VHT - Air Conditioning Ground Cabinet Feedback
[12 empty] | 366 | VHT - Air Conditioning HUB Cabinet Feedback
[12 empty] | 400 | Maximum Generator - Rotor Discrepancy
[12 empty] | 401 | Low Pressure In Gearbox
[12 empty] | 402 | Gearbox Oil Level Low
[12 empty] | 403 | High Gearbox Oil Temperature
[12 empty] | 404 | High Gearbox Bearing Temperature
[12 empty] | 405 | Rotor Or Generator High Speed in STOP Or EMERGENCY
[12 empty] | 406 | High Generator Speed
[12 empty] | 407 | High Rotor Speed
[12 empty] | 408 | Rotor Or Generator High Speed In Pause
[12 empty] | 409 | Generator - Rotor Discrepancy
[12 empty] | 410 | OGS
[12 empty] | 411 | High Brake Temperature
[12 empty] | 412 | Gearbox Fan Thermal Relays
[12 empty] | 413 | Gearbox Fan Feedback Failure
[12 empty] | 414 | Gearbox Fans Active
[12 empty] | 415 | Low Gearbox Oil Temperature
[12 empty] | 416 | Vibration Sensor
[12 empty] | 417 | Gearbox Main Filter Dirty
[12 empty] | 418 | Auxiliary Gearbox Filter Dirty
[12 empty] | 419 | Gearbox Pump Feedback Failure
[12 empty] | 421 | Gearbox Pump Thermal Relay
[12 empty] | 422 | Gearbox Pump Auxiliary Filter Thermal Relay
[12 empty] | 423 | Gearbox Main Filter Dirty Warning
[12 empty] | 424 | Gearbox Oil Heating Thermal Circuit Breaker
[12 empty] | 425 | Gearbox Heating Resistors Feedback Failure
[12 empty] | 426 | Rotor Speed Reading Failure
[12 empty] | 427 | Gearbox Auxiliary Filter Dirty Warning
[12 empty] | 429 | Gearbox Oil High Temperature Warning
[12 empty] | 430 | Gearbox Bearing High Temperature Warning
[12 empty] | 431 | Vibration Sensor After Switching To STOP Or EMERGENCY Mode
[12 empty] | 432 | Metal Particles In Gearbox Oil
[12 empty] | 433 | Failure In The Gearbox Oil Particle Sensor
[12 empty] | 434 | Low Grease Level for Main Shaft Bearing
[12 empty] | 435 | Main Shaft Bearing Lubrication Failure
[12 empty] | 441 | Gearbox Fan Thermal Relays Triggered and High Gearbox Oil Temperature
[12 empty] | 442 | Gearbox Pump Contactor Feedback Failure and High Gearbox Oil Temperature
[12 empty] | 444 | Gearbox Pump Thermal Relay Triggered and High Gearbox Oil Temperature
[12 empty] | 445 | Gearbox Pump Auxiliary Filter Thermal Relay Triggered Too Long
[12 empty] | 446 | Gearbox Fan Feedback Failure and High Gearbox Oil Temperature
[12 empty] | 447 | Gearbox Heating Resistor Feedback Failure and High Gearbox Oil Temperature
[12 empty] | 448 | Main Shaft Bearing Lubrication Failure Too Long
[12 empty] | 500 | High Generator Winding Temperature
[12 empty] | 501 | Generator DE Bearing High Temperature Alarm
[12 empty] | 502 | Generator NDE Bearing High Temperature Alarm
[12 empty] | 506 | Generator Thermal Relay Fans
[12 empty] | 507 | Generator's Fans Failure Confirmation
[12 empty] | 509 | Generator Slipping Ring High Temperature
[12 empty] | 514 | Grid Voltage Dip Warning
[12 empty] | 515 | Active Crowbar On Warning
[12 empty] | 516 | Generator Winding High Temperature Warning
[12 empty] | 517 | Generator DE Bearing High Temperature Warning
[12 empty] | 518 | Generator NDE Bearing High Temperature Warning
[12 empty] | 519 | Nacelle Temperature
[12 empty] | 523 | High Temperature Of Coolant In The Input Of The Cooling Circuit
[12 empty] | 524 | High Temperature Of The Control Module
[12 empty] | 525 | High Ambient Temperature In The Converter
[12 empty] | 526 | High Ambient Temperature In The Stator Thermo-Magnet
[12 empty] | 527 | High Temperature Of Upper Radiator
[12 empty] | 528 | High Temperature Of Lower Radiator
[12 empty] | 530 | High Temperature Of Inver Inductance
[12 empty] | 532 | Low Grease Level For Generator Bearings
[12 empty] | 533 | Generator Bearing Lubrication Failure
[12 empty] | 534 | Maximum Slip Rings Heating Time
[12 empty] | 537 | Wear Brushes Generator
[12 empty] | 538 | Converter High Ambient Temperature Alarm
[12 empty] | 539 | Converter Inlet Ambient Temperature Sensor Failure
[12 empty] | 550 | Generator Fans Thermal Relay Triggered Too Long
[12 empty] | 551 | Generator Bearing Lubrication Failure Too Long
[12 empty] | 552 | Wear Brushes Generator Triggered Too Long
[12 empty] | 565 | Main Shaft Front Bearing Extreme Temperature
[12 empty] | 566 | Main Shaft Front Bearing High Temperature Warning
[12 empty] | 567 | Main Shaft Rear Bearing Extreme Temperature
[12 empty] | 568 | Main Shaft Rear Bearing High Temperature Warning
[12 empty] | 571 | Generator Slip Rings High Temperature Warning
[12 empty] | 572 | Converter Coolant In The Input Of The Cooling Circuit High Temperature Warning
[12 empty] | 573 | Converter Control Module High Temperature Warning
[12 empty] | 574 | Converter Upper Radiator High Temperature Warning
[12 empty] | 575 | Converter Lower Radiator High Temperature Warning
[12 empty] | 576 | Generator Fans Failure Too Long
[12 empty] | 577 | Slipping Rings Fan Or Heating Resistor Failure
[12 empty] | 600 | ATD Filters Out Of Range
[12 empty] | 601 | ATD Saturation Alarm
[12 empty] | 602 | Maximum Time For Stator Connection
[12 empty] | 603 | Maximum Time For Stator Disconnection
[12 empty] | 609 | Speed Reference Not Allowed
[12 empty] | 610 | Permission Denied For Star and Delta Connection
[12 empty] | 611 | Maximum Time To Make A Connection Change In The Stator
[12 empty] | 612 | Maximum Time For Connection In Star
[12 empty] | 613 | Maximum Time For Connection In Delta
[12 empty] | 615 | Accelerometer Vibration Alarm
[12 empty] | 616 | Rotor Block
[12 empty] | 619 | Calibration Test Not Executed Or NO OK
[12 empty] | 621 | Maximum Synchronization Time
[12 empty] | 622 | Non-Consecutive Accelerometer Reading Error
[12 empty] | 623 | Accelerometer Measurement Error
[12 empty] | 624 | LTD Saturation Alarm
[12 empty] | 625 | LTD Filters Out Of Range
[12 empty] | 626 | Azimuth Inductive Sensor Failure
[12 empty] | 627 | Grid Frequency Disturbance - Inertia Emulation Activation
[12 empty] | 628 | Pitch LTD Saturation Alarm
[12 empty] | 629 | Pitch LTD Filters Out Of Range
[12 empty] | 700 | PLC-Converter Communication Error
[12 empty] | 702 | Sonic Communication Failure
[12 empty] | 703 | Remote Control Com Failure
[12 empty] | 707 | SMP Communication Failure
[12 empty] | 708 | Pause Due To Remote Control Communications Failure
[12 empty] | 711 | Sonic Error.NRG Operates
[12 empty] | 715 | Wattmeter Failure
[12 empty] | 716 | NRG.Error Sonic Operates
[12 empty] | 717 | NRG Failure
[12 empty] | 718 | 24 Hours With NRG Or Too Many Sonic-NRG Changes
[12 empty] | 719 | Cup Anemometer Failure Warning
[12 empty] | 720 | Sonic Failure, Cup Anemometer Operates Warning
[12 empty] | 721 | Wind Vane Failure Warning
[12 empty] | 722 | Wind Vane Failure Alarm
[12 empty] | 728 | WTG PLC-GENSET Communication Failure
[12 empty] | 800 | Pitch Drive Error
[12 empty] | 802 | Low Pitch Value In Stop Mode (2 Cylinders)
[12 empty] | 803 | Low Pitch Value In Stop Mode (1 Cylinder)
[12 empty] | 804 | Difference Between 2 Blades Too High
[12 empty] | 806 | Possible Ice On Blades
[12 empty] | 811 | Non-Consecutive Pitch Reading Errors
[12 empty] | 812 | Blade Position Meas. Error
[12 empty] | 813 | Low Pressure Of Emergency Accumulators
[12 empty] | 814 | ACP Alarm
[12 empty] | 816 | Blade Bearing Lubrication System Problem
[12 empty] | 817 | Blade Bearing Lubrication System Error
[12 empty] | 819 | Low Grease Level For Blade Bearings
[12 empty] | 820 | Blade Bearing Lubrication Failure
[12 empty] | 823 | Incorrect Emergency Speed
[12 empty] | 825 | Blade Bearing Lubrication Failure Too Long
[12 empty] | 828 | Pitch Rate Error During TPR Shutdown
[12 empty] | 829 | Pitch Electrovalves Power Supply Failure
[12 empty] | 900 | Top Emergency Button
[12 empty] | 901 | Emergency Series Feedback Error
[12 empty] | 902 | Opening Series For Test
[12 empty] | 903 | Authoriz Person In Turbine
[12 empty] | 904 | Presence Of Unauth. Person In Turbine
[12 empty] | 905 | Controlled Emergency Series Battery Failure
[12 empty] | 906 | Trigger Of FG230 Or FM230
[12 empty] | 907 | Emergency Series HUB Trigger
[12 empty] | 908 | Ground Emergency Button
[12 empty] | 911 | Change Emergency-Local Reset
[12 empty] | 912 | Change Emergency-Remote Control Reset
[12 empty] | 913 | Change Stop Local Reset
[12 empty] | 914 | Change Stop-Remote Control Reset
[12 empty] | 915 | Change Pause-Local Reset
[12 empty] | 916 | Change Pause-Remote Control Reset
[12 empty] | 917 | Basic Data Incorrectly Entered
[12 empty] | 932 | WTG Shutdown Requested By Flight Manager
[12 empty] | 1800 | Not Performing Pole Trial
[12 empty] | 1801 | Pole Test Missing
[12 empty] | 1812 | Lock And Send To Run: Frequency Out Of Range
[12 empty] | 1813 | DTD Filter Alarm 1
[12 empty] | 1814 | DTD Filter Alarm 2
[12 empty] | 1816 | Speed Filters Alarm Torque Loop
[12 empty] | 1817 | Speed Filters Alarm Speed Loop
[12 empty] | 1818 | Switchgear Contactor Trigger
[12 empty] | 1819 | RC Filter Failure
[12 empty] | 1820 | RC Filter
[12 empty] | 1821 | Heating Protection Triggered
[12 empty] | 1822 | Discussion Due To Low Temperature
[12 empty] | 1823 | Coolant Confirmation Failure
[12 empty] | 1824 | Trafo Fan Thermal Relay
[12 empty] | 1825 | Automatics Not Ok
[12 empty] | 1828 | Trigger Of Overvoltage Protection
[12 empty] | 1832 | Reactive Power Production By The Converter Is Limited
[12 empty] | 1833 | Transformer Fan Control Failure
[12 empty] | 1834 | MV Switch Trip From Arc Detector
[12 empty] | 1835 | MV Switch Trip From Neutral Detector
[12 empty] | 1836 | MV Switch Trip From Transformer Fuses
[12 empty] | 1835 | MV Switch Trip From CCU
[12 empty] | 1838 | Lock And Send To Run: Voltage Out Of Range
[12 empty] | 1840 | Transformer Over Voltage Operation Time Exceeded
[12 empty] | 1874 | Latched Control Relay Fault Alarm
[12 empty] | 1875 | MV Switch Trip From TOP Cabinet Button Or Latched Control Relay Handle
[12 empty] | 1876 | The MV Switch Gear Has Not Tripped
[12 empty] | 1878 | Smoke Sensor In Ground
[12 empty] | 1879 | Warning Auxiliary Leakage Current
[12 empty] | 1880 | Alarm Auxiliary Leakage Current
[12 empty] | 1882 | Transformer Auxiliary Services Fuses
[12 empty] | 1885 | External Temperature Multiplexer Failure
[12 empty] | 1893 | Trafo Fan Thermal Relay Triggered Too Long
[12 empty] | 1894 | Automatic Secondaries Not OK Too Long
[12 empty] | 1895 | Auxiliary Leakage Current Too Long
[12 empty] | 1896 | Low Grid Voltage
[12 empty] | 1899 | Automatic Secondaries Not OK
[12 empty] | 1909 | WT UY Ground Power Supply Circuit Breaker Tripped
[12 empty] | 1910 | WT UY Top Power Supply Circuit Breaker Tripped
[12 empty] | 1911 | WT UY Ground KMGS1 Contactor Failure
[12 empty] | 1912 | WT UY Top KMGS2 Contactor Failure
[12 empty] | 1913 | WT UY Ground Switch Selector Active
[12 empty] | 1914 | WT UY Impulse Relay activation (TL) Failure
[12 empty] | 1915 | WT UY System Is Initializing
[12 empty] | 1917 | Discrepancy Between Emergency Indicators
[12 empty] | 2100 | PLC Voltage Recovery
[12 empty] | 2101 | Counter Card Failure
[12 empty] | 2102 | PLC Module Failure
[12 empty] | 2106 | Temp. Measurement Module Failure
[12 empty] | 2107 | Initialization Failure
[12 empty] | 2113 | Cycle Time Exceeded
[12 empty] | 2114 | Analogue Card Failure
[12 empty] | 2115 | Change Auto Reset->Remote
[12 empty] | 2116 | Change Remote Reset->Local
[12 empty] | 2117 | PLC Internal Error Warning
[12 empty] | 2118 | Bus Error - Interbus Failure
[12 empty] | 2119 | CTRL Error - Processor Stopped
[12 empty] | 2120 | Optical Fiber Low Quality
[12 empty] | 2124 | Flash Writing Error
[12 empty] | 2125 | Flash Writing Limit Exveeded
[12 empty] | 2129 | PLC Data Incorrect
[12 empty] | 2130 | GATEWAY Configuration Error
[12 empty] | 2131 | UPS Fail
[12 empty] | 2198 | Temperature Measurement Module Failure
[12 empty] | 5200 | Magnetothermic Trigger Of The Line Protection
[12 empty] | 5201 | Magnetothermic Trigger Of The Stator Protection
[12 empty] | 5202 | Stator Contactor Failure
[12 empty] | 5203 | Heating/Coolant Thermal Magnetic Failure
[12 empty] | 5204 | Emergency Series Not OK
[12 empty] | 5205 | Magnetothermic Of The Stator Protection Failure Or Door Open
[12 empty] | 5206 | Brake Chopper Failure
[12 empty] | 5207 | Excessive Temperature Of Coolant At The Input Of The Cooling Circuit
[12 empty] | 5208 | Brake Chopper IGBT 2 Failure
[12 empty] | 5209 | Brake Chopper Driver 2 Failure
[12 empty] | 5210 | Failure Of The Contactor's Rotor Power
[12 empty] | 5212 | Bus Preload Protection Thermal Relay Failure
[12 empty] | 5213 | Crowbar Overvoltage
[12 empty] | 5213 | Crowbar Not OK
[12 empty] | 5215 | Rotor Protection Thermal Magnetic Failure
[12 empty] | 5216 | Grid Voltage Failure
[12 empty] | 5217 | Frequency Failure
[12 empty] | 5218 | Phase Rotation Failure
[12 empty] | 5219 | Coolant Of The Coolant Circuit Failure
[12 empty] | 5220 | Encoder Not OK
[12 empty] | 5221 | Encoder Suynchronism Error
[12 empty] | 5222 | Speed Read Incorrectly
[12 empty] | 5223 | Brake Chopper Driver 1 Failure
[12 empty] | 5224 | Out Of Range In Slippage
[12 empty] | 5225 | Fault In Analog Electronic Power Supply
[12 empty] | 5227 | Fault In 24v Power Supply
[12 empty] | 5228 | Preload Failure
[12 empty] | 5229 | Data Capture Failure In Test
[12 empty] | 5230 | Test Rotor Movement
[12 empty] | 5231 | Discrepancy In power Regulation
[12 empty] | 5232 | Error In Phase R Of The Rectifier
[12 empty] | 5233 | Error In Phase S Of The Rectifier
[12 empty] | 5234 | Error In Phase T Of The Rectifier
[12 empty] | 5235 | Rectifier Driver Error (Edriver) Or Of The Inverter (Edriver I)
[12 empty] | 5236 | Error In Phase R Of The Inverter
[12 empty] | 5237 | Error In Phase S Of The Inverter
[12 empty] | 5238 | Error In Phase T Of The Inverter
[12 empty] | 5239 | Rectifier Phase R Overcurrent
[12 empty] | 5240 | Rectifier Phase S Overcurrent
[12 empty] | 5241 | Excess Current Phase R Of Rotor
[12 empty] | 5242 | Excess Current Phasse S Of Rotor
[12 empty] | 5243 | Excess Current Phase R Of Stator
[12 empty] | 5244 | Excess Current Phase S Of Stator
[12 empty] | 5245 | Bus Over Voltage Detected By Hardware
[12 empty] | 5246 | Bus Over Voltage Detected By Software
[12 empty] | 5247 | Low Bus Voltage
[12 empty] | 5248 | Active Crowbar IGBT Errors
[12 empty] | 5249 | Earth Leakage In The Stator
[12 empty] | 5250 | Brake Chopper IGBT 1 Failure
[12 empty] | 5251 | Active Crowbar Failure
[12 empty] | 5252 | Actuator Of The Coolant Circuit Failure
[12 empty] | 5253 | Excess Temperature In The Radiator's Hardware
[12 empty] | 5254 | Excessive Temperature Of The Control Module
[12 empty] | 5255 | Overtemperature Thermostats Of The Cabinet Cubicle
[12 empty] | 5256 | Excessive Ambient Temperature Of The Converter
[12 empty] | 5257 | Excess Ambient Temperature In The Stator Thermo-Magnet
[12 empty] | 5258 | Excessive Temperature Of The Upper Radiator
[12 empty] | 5259 | Excessive Temperature Of The Lower Radiator
[12 empty] | 5260 | Overheating In The Grid's Inductance
[12 empty] | 5261 | Overheating In The Rectifiers Inductance
[12 empty] | 5262 | Overheating In The Inverter's Inductance
[12 empty] | 5263 | CAN Communication Failure
[12 empty] | 5264 | High Transient Grid Harmonic Distortion
[12 empty] | 5265 | High Grid Harmonic Voltage Distortion
[12 empty] | 5266 | Power Transformer Internal Failure
[12 empty] | 5267 | 690V Circuits Ground Faults
[12 empty] | 5268 | High Grid Harmonic Distortion
[12 empty] | 5269 | High Grid Harmonic Distortion Warning
[12 empty] | 5270 | Earth Leakage In The Rotor
[12 empty] | 2509 | SF6 Breaker Fault
[12 empty] | CE100001 | Manual Stop
[12 empty] | CE100002 | Major BD - Blade
[12 empty] | CE100003 | Major BD - Transformer
[12 empty] | CE100004 | Major BD - Generator
[12 empty] | CE100005 | Major BD - Gearbox
[12 empty] | CE100006 | Major BD - Main Bearing
[12 empty] | CE100007 | Transmission Line Related work
[12 empty] | CE100008 | General Work Stoppage
[12 empty] | CE100009 | Major BD - Power Cable
[12 empty] | CE100011 | Major BD - DFIG
[12 empty] | CE100012 | Major BD - Foundation
[12 empty] | CE100013 | Theft
[12 empty] | CE100010 | Manual Stop - Preventive Maintenance Activity
[12 empty] | CE100014 | Manual Stop - Audit
[12 empty] | CE100015 | Manual Stop - Safety Related
[12 empty] | CE100016 | Manual Stop - Blade Cleaning
[12 empty] | CE100017 | UPS breakdown
[12 empty] | CE100018 | SF6 and HV side