## O2Summary
Performance Summary PWEPL
Month | 2025-06-01
Date | 2025-06-12
Financial Year | Year-3
Year Start Date | 2025-04-01
Year End Date | 2026-03-31
Sr. No. | Particular | Target | Measured | Deviation | Remarks
1 | E_Grid Daily (MWh) | 519.7696 | 645.773 | 24.24%
| E_Grid MTD(MWh) | 6237.2352 | 6313.588 | 1.224%
| E_Grid YTD (MWh) | 23929.0996 | 23481.238 | -1.872%
2 | Wind Speed Daily | 6.81 | 7.3545 | 7.996%
| Wind Speed MTD | 6.81 | 6.8026 | -0.109%
| Wind Speed YTD | 6.0011 | 5.4548 | -9.104%
3 | PA Daily | 96.03% | 100% | 4.134%
| PA MTD | 96.03% | 99.35% | 3.455%
| PA YTD | 96.03% | 97.16% | 1.173%
4 | EGA Daily | 99.5% | 100% | 0.5025%
| EGA MTD | 99.5% | 99.53% | 0.02869%
| EGA YTD | 99.5% | 99.09% | -0.4076%
5 | IGA Daily | 99% | 100% | 1.01%
| IGA MTD | 99% | 99.83% | 0.8429%
| IGA YTD | 99% | 98.14% | -0.8713%
6 | MA Daily | 97% | 100% | 3.093%
| MA MTD | 97% | 99.83% | 2.922%
| MA YTD | 97% | 98.14% | 1.173%
7 | CUF Daily | 30.76% | 38.22% | 24.24%
| CUF MTD | 30.76% | 31.14% | 1.224%
| CUF YTD | 19.4% | 19.04% | -1.872%
8 | Line Loss Daily | 5% | -2.22e-14% | 100%
| Line Loss MTD | 5% | 9.252e-16% | 100%
| Line Loss YTD | 5% | 3.042e-16% | 100%
9 | Reactive Power Daily | 5% | 0.02017% | 99.6%
| Reactive Power MTD | 5% | 0.01471% | 99.71%
| Reactive Power YTD | 5% | 0.01481% | 99.7%
10 | Expected Energy Daily | 611.16 | 645.773 | 5.663%
| Expected Energy MTD | 4317.99 | 6313.588 | 46.22%
| Expected Energy YTD | 20299.91 | 23481.238 | 15.67%
Feeder4

## AnnualKPI
Till Date | 2025-06-12 | 2025-06-01
PWEPL Performance Summary-YTD
Year | Days | Estimated WS(m/s) | Measured WS (m/s) | Budgeted Energy (MWh) | Measured Energy (MWh) | Target CUF (%) | Measured CUF (%) | Target GA (%) | Measured GA (%) | Target MA (%) | Measured MA (%) | Target IGA(%) | Measured IGA (%) | Target PA(%) | Measured PA (%) | Expected Energy | Loss (%) | Reactive Power (%)
2026 | 73 | 6.0011 | 5.4548 | 23929.0996 | 23481.238 | 19.4% | 19.04% | 99.5% | 99.09% | 97% | 99% | 99% | 98.14% | 96.03% | 97.16% | 20299.91 | 3.042e-16% | 0.01481%

## MonthlyKPI
Till Date | 2025-06-12 | 0 | 0 | 0 | 0
PWEPL Performance Summary (MTD)
Year | Days | Estimated WS(m/s) | Measured WS (m/s) | Budgeted Energy (MWh) | Measured Energy (MWh) | Target CUF (%) | Measured CUF (%) | Target GA (%) | Measured GA (%) | Target MA (%) | Measured MA (%) | Target IGA (%) | Measured IGA (%) | Target PA(%) | Measured PA (%) | WTG Total (MWh) | Line Losses(%) | E_WS_Corrected | Expected Energy | Loss (%) | Reactive Power (%)
2025-06-01 | 12 | 6.81 | 6.8026 | 6237.2352 | 6313.588 | 30.76% | 31.14% | 99.5% | 99.53% | 97% | 99.51% | 99% | 99.83% | 96.03% | 99.35% | 6313.588 | 0% | 4317.99 | 4317.99 | 9.252e-16% | 0.01471%
Start Date | 2025-06-06
End Date | 2025-06-12
PWEPL Performance Summary (WTD)
Year | Days | Estimated WS(m/s) | Measured WS (m/s) | Budgeted Energy (MWh) | Measured Energy (MWh) | Target CUF (%) | Measured CUF (%) | Target GA (%) | Measured GA (%) | Target MA (%) | Measured MA (%) | Target IGA (%) | Measured IGA (%) | Target PA(%) | Measured PA (%) | E_WS_Corrected
2025-06-01 | 7 | 6.81 | 6.9956 | 3638.3872 | 3932.271 | 30.76% | 33.25% | 99.5% | 99.19% | 97% | 99.67% | 99% | 100% | 96.03% | 99.67% | 2715.01
Start Date | 2025-05-14
End Date | 2025-06-12
PWEGPL Performance Summary (LTD)
Year | Days | Estimated WS(m/s) | Measured WS (m/s) | Budgeted Energy (MWh) | Measured Energy (MWh) | Target CUF (%) | Measured CUF (%) | Target GA (%) | Measured GA (%) | Target MA (%) | Measured MA (%) | Target IGA (%) | Measured IGA (%) | Target PA(%) | Measured PA (%)
2025-06-01 | 30 | 5.6311 | 6.0938 | 12536.3444 | 12809.094 | 24.73% | 25.27% | 99.7% | 99.5% | 98.6% | 99.39% | 99.5% | 98.26% | 98.11% | 97.66%
Formulas:
Days = [Days, row below]-6

## Analytics
Start Date | 2025-05-16
End Date | 2025-06-12 | 648 | 5.8936
WTG No. | P-01 | P-02 | P-03 | P-04 | P-05 | P-06 | P-07 | P-08 | P-09 | P-10 | P-11 | P-12 | P-13 | P-14 | P-15 | P-16 | P-17 | P-18 | P-19 | P-20 | P-22 | P-23 | P-25 | P-26 | P-27 | P-28 | P-31 | P-32 | P-34 | P-37 | P-38 | P-40 | P-41 | P-42 | P-43 | P-45 | P-46 | P-47 | P-48 | P-50 | P-51 | P-52 | P-55 | P-56
MA | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.82% | 100% | 100% | 99.99% | 96.73% | 99.45% | 97.99% | 100% | 99.8% | 100% | 99.69% | 99.98% | 100% | 100% | 100% | 99.53% | 99.14% | 96.74% | 98.96% | 100% | 98.91% | 100% | 99.2% | 99.96% | 100% | 99.24% | 100% | 100% | 100% | 100% | 99.33% | 100% | 100% | 99.67% | 100% | 99.9% | 99.64%
WTG BD Hours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.15 | 0 | 0 | 0.083333 | 21.2 | 3.5667 | 13.0167 | 0 | 1.2833 | 0 | 2 | 0.15 | 0 | 0 | 0 | 3.0167 | 5.5833 | 21.1167 | 6.7167 | 0 | 7.0833 | 0 | 5.1833 | 0.23333 | 0 | 4.9333 | 0 | 0 | 0 | 0 | 4.3167 | 0 | 0 | 2.1333 | 0 | 0.63333 | 235%
IGA | 98.04% | 98.04% | 98.04% | 96.9% | 98.17% | 98.17% | 98.04% | 96.91% | 96.91% | 96.91% | 96.91% | 96.91% | 96.91% | 96.9% | 96.9% | 96.9% | 96.9% | 98.04% | 96.9% | 96.9% | 96.9% | 96.9% | 96.91% | 96.91% | 96.91% | 96.91% | 98.04% | 98.04% | 96.9% | 98.04% | 96.9% | 98.17% | 98.17% | 98.17% | 96.9% | 98.17% | 98.17% | 98.17% | 98.17% | 98.04% | 98.04% | 98.04% | 98.04% | 98.04% | 97.5%
METERING YARD | [44 empty] | #DIV/0!
FEEDER | 12.6833 | 12.6833 | 12.6833 | 20.0833 | 11.8667 | 11.8667 | 12.6833 | 20.0333 | 20.0333 | 20.0333 | 20.0333 | 20.0333 | 20.0333 | 20.0833 | 20.0833 | 20.0833 | 20.0833 | 12.6833 | 20.0833 | 20.0833 | 20.0833 | 20.0833 | 20.0333 | 20.0333 | 20.0333 | 20.0333 | 12.6833 | 12.6833 | 20.0833 | 12.6833 | 20.0833 | 11.8667 | 11.8667 | 11.8667 | 20.0833 | 11.8667 | 11.8667 | 11.8667 | 11.8667 | 12.6833 | 12.6833 | 12.6833 | 12.6833 | 12.6833 | 1620%
OG | [44 empty] | #DIV/0!
TRANSFER | [44 empty] | #DIV/0!
USS | [44 empty] | #DIV/0!
EGA | 100% | 100% | 100% | 99.62% | 99.86% | 99.86% | 100% | 99.58% | 99.58% | 99.58% | 99.58% | 99.58% | 99.58% | 99.62% | 99.62% | 99.62% | 99.62% | 100% | 99.62% | 99.62% | 99.62% | 99.62% | 99.58% | 99.58% | 99.58% | 99.58% | 100% | 100% | 99.62% | 100% | 99.62% | 99.86% | 99.86% | 99.86% | 99.62% | 99.86% | 99.86% | 99.86% | 99.86% | 100% | 100% | 100% | 100% | 100% | 99.77%
External Grid | 0 | 0 | 0 | 2.45 | 0.88333 | 0.88333 | 0 | 2.7167 | 2.7167 | 2.7167 | 2.7167 | 2.7167 | 2.7167 | 2.45 | 2.45 | 2.45 | 2.45 | 0 | 2.45 | 2.45 | 2.45 | 2.45 | 2.7167 | 2.7167 | 2.7167 | 2.7167 | 0 | 0 | 2.45 | 0 | 2.45 | 0.88333 | 0.88333 | 0.88333 | 2.45 | 0.88333 | 0.88333 | 0.88333 | 0.88333 | 0 | 0 | 0 | 0 | 0 | 146.6%
Generation | 389535 | 390350 | 367852 | 309224 | 360401 | 351379 | 304450 | 201642 | 172752 | 194514 | 213999 | 232630 | 211036 | 215558 | 188849 | 211291 | 215851 | 356738 | 221901 | 186082 | 299354 | 294543 | 251493 | 255888 | 268780 | 238344 | 353006 | 215273 | 302204 | 279279 | 224400 | 246526 | 359932 | 370832 | 239318 | 425240 | 401880 | 347215 | 384488 | 203542 | 292790 | 313310 | 392402 | 357120 | 12613193
PA | 98.04% | 98.04% | 98.04% | 96.52% | 98.03% | 98.03% | 98.04% | 96.49% | 96.31% | 96.49% | 96.49% | 96.48% | 93.22% | 95.97% | 94.51% | 96.52% | 96.32% | 98.04% | 96.21% | 96.5% | 96.52% | 96.52% | 96.49% | 96.02% | 95.63% | 93.23% | 97.01% | 98.04% | 95.43% | 98.04% | 95.72% | 98% | 98.03% | 97.27% | 96.52% | 98.03% | 98.03% | 98.03% | 97.37% | 98.04% | 98.04% | 97.71% | 98.04% | 97.94% | 96.91%
Sum of BD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.15 | 0 | 0 | 0.083333 | 21.2 | 3.5667 | 13.0167 | 0 | 1.2833 | 0 | 2 | 0.15 | 0 | 0 | 0 | 3.0167 | 5.5833 | 21.1167 | 6.7167 | 0 | 7.0833 | 0 | 5.1833 | 0.23333 | 0 | 4.9333 | 0 | 0 | 0 | 0 | 4.3167 | 0 | 0 | 2.1333 | 0 | 0.63333 | 235%
Count of BD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 6 | 2 | 3 | 0 | 2 | 0 | 2 | 1 | 0 | 0 | 0 | 3 | 2 | 4 | 2 | 0 | 4 | 0 | 4 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 1 | 0 | 2 | 102.3%
MTTR WTG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.15 | 0 | 0 | 0.083333 | 3.5333 | 1.7833 | 4.3389 | 0 | 0.64167 | 0 | 1 | 0.15 | 0 | 0 | 0 | 1.0056 | 2.7917 | 5.2792 | 3.3583 | 0 | 1.7708 | 0 | 1.2958 | 0.23333 | 0 | 4.9333 | 0 | 0 | 0 | 0 | 1.4389 | 0 | 0 | 2.1333 | 0 | 0.31667 | 0.84631
MTBF WTG | 648 | 648 | 648 | 648 | 648 | 648 | 648 | 648 | 646.85 | 648 | 648 | 647.9167 | 104.4667 | 322.2167 | 211.6611 | 648 | 323.3583 | 648 | 323 | 647.85 | 648 | 648 | 648 | 214.9944 | 321.2083 | 156.7208 | 320.6417 | 648 | 160.2292 | 648 | 160.7042 | 647.7667 | 648 | 643.0667 | 648 | 648 | 648 | 648 | 214.5611 | 648 | 648 | 645.8667 | 648 | 323.6833 | 528.1082
WS (M/S) | 6.7971 | 6.9782 | 6.805 | 6.4811 | 6.6604 | 6.9189 | 6.3782 | 5.5657 | 5.5271 | 5.6786 | 5.7718 | 5.8936 | 5.8436 | 5.5636 | 5.7489 | 5.7843 | 5.6839 | 6.4539 | 6.0382 | 5.4204 | 6.0886 | 6.3132 | 5.835 | 6.0504 | 6.3236 | 6.1975 | 6.3375 | 5.9414 | 6.1011 | 6.2286 | 5.7114 | 6.0268 | 6.7404 | 6.9186 | 6.0971 | 7.0314 | 7.6257 | 6.7468 | 6.9407 | 5.7407 | 5.8964 | 6.2411 | 6.9193 | 7.0861 | 6.253
Line loss (%)
Corelation (%)
Reactive Power
Fault Analysis
|  |  | Put hour Here |  | Default hour for full Data
|  |  | #REF! |  | #REF!
Row Labels | Sum of Breakdown Time | Count of Error Text | MTTR | MTBF
Gearbox oil overtemperature | 289.1 | 73 | 3.9603 | #REF!
Line CCU collective faults | 207.0167 | 26 | 7.9622 | #REF!
PLC fault 24V Supply | 84.2253 | 12 | 7.0188 | #REF!
Anemometer defec | 65.85 | 8 | 8.2313 | #REF!
Line CCU fault current | 65.0833 | 7 | 9.2976 | #REF!
Pitch thyristor 3 fault | 58.0833 | 9 | 6.4537 | #REF!
Yaw tooth sensor 1 timeout | 40.3 | 20 | 2.015 | #REF!
Rotor speeds not plausible | 39.8 | 7 | 5.6857 | #REF!
Communication fault wind measurement device | 34.2167 | 5 | 6.8433 | #REF!
No communication Cu | 28.95 | 2 | 14.475 | #REF!
Pitch thyristor 1 fault | 26.9833 | 3 | 8.9944 | #REF!
Brake not released secondary brake | 20.25 | 2 | 10.125 | #REF!
CCU fault at abnormal grid condition | 18.5167 | 2 | 9.2583 | #REF!
Grid voltage drop CU | 18.0167 | 20 | 0.90083 | #REF!
Pitch thyristor 2 fault | 17.8833 | 4 | 4.4708 | #REF!
Communication fault pitch controller Axis 2 | 15.5833 | 4 | 3.8958 | #REF!
Gearbox oil level too low | 14.3833 | 9 | 1.5981 | #REF!
Line CCU fault voltage | 13.3667 | 3 | 4.4556 | #REF!
Timeout yaw counter | 6.5667 | 3 | 2.1889 | #REF!
Yaw tooth sensor 2 timeout | 6.5333 | 4 | 1.6333 | #REF!
axis 3 fault pitch controlle | 6.4667 | 5 | 1.2933 | #REF!
Yaw Brake Voltage 230Volt not OK | 6.0333 | 4 | 1.5083 | #REF!
Temp. sensor error (shut down) | 5.9 | 3 | 1.9667 | #REF!
System re-initialization after grid outage | 5.4167 | 13 | 0.41667 | #REF!
DTA DIN03 control breaker status | 5.3333 | 1 | 5.3333 | #REF!
Battery voltage not OK axis 1 | 4.6167 | 1 | 4.6167 | #REF!
axis 2 fault pitch controller | 4.3 | 2 | 2.15 | #REF!
Pitch control deviation Axis 3 | 4.25 | 2 | 2.125 | #REF!
Yaw Mapping | 3.8333 | 1 | 3.8333 | #REF!
Communication fault Pitch controller | 3.1833 | 1 | 3.1833 | #REF!
Internal Line VCB tripped in over current | 3.1167 | 2 | 1.5583 | #REF!
axis 1 fault pitch controller | 2.85 | 4 | 0.7125 | #REF!
TopBox DIN21 motor protection aux contact string | 2.8 | 4 | 0.7 | #REF!
Ratio generator-/rotor speed | 2.6833 | 1 | 2.6833 | #REF!
Line fault voltage | 2.25 | 1 | 2.25 | #REF!
Feedback error circuit breaker | 1.9333 | 1 | 1.9333 | #REF!
Shaft bearing overtemperature | 1.9 | 1 | 1.9 | #REF!
No speed reduction with secondary braking | 1.25 | 4 | 0.3125 | #REF!
Brake does not close | 1.0167 | 1 | 1.0167 | #REF!
Pitch control deviation axis 1 | 1 | 1 | 1 | #REF!
Limit switch 90deg-rotorblade defective | 0.66667 | 1 | 0.66667 | #REF!
Safety chain | 0.6 | 2 | 0.3 | #REF!
Pitch malfunction 2 or 3 blades | 0.58333 | 1 | 0.58333 | #REF!
Yaw runaway | 0.48333 | 1 | 0.48333 | #REF!
Yaw sensor error | 0.41667 | 1 | 0.41667 | #REF!
Secondary braking time too high | 0.38333 | 2 | 0.19167 | #REF!
Secondary brake test | 0.13333 | 1 | 0.13333 | #REF!
Incorrect Error Code | 0 | 12 | 0 | #REF!
Grand Total | 1144.1086 | 297 | 3.8522 | #REF!
|  |  | #DIV/0! | #REF!

## Daily KPI
Date | Financial Year | Calendar Year | Month Year | Days | Operating Hours | GHI-UP (KWh/m2) | GHI-Down(KWh/m2) | POA-UP(KWh/m2) | POA-Down(KWh/m2) | Amb_Temp(°C) | Mod_Temp(°C) | WS_Avg(m/s) | WS_Max(m/s) | PA(%) | MA (%) | IGA (%) | EGA(%) | EMA (%) | TA (%) | PR(%) | WPR(%) | CUF(%) | Gen_Exp (kWh) | Mtr_Export (kWh) | Mtr_Import (kWh) | Mtr_Net_Exp (KWh) | Operational Capacity (MW) | Bugt_Resource | Bugt_Energy | Bugt PR | Bugt CUF | Bugt_PA | Bugt_EGA | Expected Energy | Actual Energy WPR | RA (%) | Mod Clean Dry (Num) | Mod Clean Wet (Num) | Line Loss(%) | Reactive Power (%) | Bugt Line loss (%) (Wind) | Bugt Reactive Power (%) (Wind) | Bugt Capacity | CC*Bugt
2025-03-29 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 4.6409 | 5.68 | 96.85% | 99.33% | 97.5% | 100% |  |  |  |  | 9.999% | 168935 | 168935 | 0 | 168935 | 70.4 | 4.565 | 177354.8387 |  | 10.5% | 96.03% | 99.5% | 156.79 |  |  |  |  | 0% | 0% | 5% | 5% | 70.4
2025-03-30 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 4.9325 | 6.15 | 99.5% | 100% | 99.5% | 100% |  |  |  |  | 11.24% | 189877 | 189877 | 0 | 189877 | 70.4 | 4.565 | 177354.8387 |  | 10.5% | 96.03% | 99.5% | 162.74 |  |  |  |  | 0% | 0% | 5% | 5% | 70.4
2025-03-31 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 3.7164 | 4.75 | 95.4% | 99.59% | 95.79% | 100% |  |  |  |  | 5.196% | 87784 | 87784 | 0 | 87784 | 70.4 | 4.565 | 177354.8387 |  | 10.5% | 96.03% | 99.5% | 66.47 |  |  |  |  | -1.11e-14% | 0% | 5% | 5% | 70.4
2025-04-01 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.0677 | 6.47 | 85.43% | 98.56% | 86.68% | 100% |  |  |  |  | 14.47% | 244495 | 244495 | 0 | 244495 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 188.67 |  |  |  |  | -1.11e-14% | 0.01526% | 5% | 5% | 70.4
2025-04-02 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.4718 | 6.87 | 96.84% | 99.12% | 97.71% | 100% |  |  |  |  | 18.69% | 315710 | 315710 | 0 | 315710 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 309.39 |  |  |  |  | 2.22e-14% | 0.02014% | 5% | 5% | 70.4
2025-04-03 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 3.5082 | 4.18 | 94.45% | 98.41% | 95.98% | 100% |  |  |  |  | 4.559% | 77037 | 77037 | 0 | 77037 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 72.87 |  |  |  |  | 0% | 0.01943% | 5% | 5% | 70.4
2025-04-04 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.1436 | 5.01 | 93.44% | 99.98% | 93.46% | 100% |  |  |  |  | 6.937% | 117205 | 117205 | 0 | 117205 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 115.95 |  |  |  |  | 0% | 0.01764% | 5% | 5% | 70.4
2025-04-05 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.4491 | 5.5 | 93.03% | 94.99% | 97.94% | 100% |  |  |  |  | 7.543% | 127441 | 127441 | 0 | 127441 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 123.65 |  |  |  |  | 0% | 0.002704% | 5% | 5% | 70.4
2025-04-06 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 3.8152 | 4.7 | 96.94% | 99.87% | 97.07% | 100% |  |  |  |  | 5.749% | 97130 | 97130 | 0 | 97130 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 129.36 |  |  |  |  | 0% | 0.0005914% | 5% | 5% | 70.4
2025-04-07 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.3709 | 5.5 | 97.31% | 98.98% | 98.32% | 100% |  |  |  |  | 7.909% | 133637 | 133637 | 0 | 133637 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 94.92 |  |  |  |  | 0% | 0.01422% | 5% | 5% | 70.4
2025-04-08 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.1109 | 4.86 | 96.65% | 97.86% | 98.76% | 83.44% |  |  |  |  | 5.49% | 92765 | 92765 | 0 | 92765 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 38.78 |  |  |  |  | 2.22e-14% | 0.008602% | 5% | 5% | 70.4
2025-04-09 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.2959 | 5.39 | 96.56% | 98.81% | 97.72% | 100% |  |  |  |  | 8.27% | 139732 | 139732 | 0 | 139732 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 101.75 |  |  |  |  | 0% | 0.01468% | 5% | 5% | 70.4
2025-04-10 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.3873 | 6.9 | 96.5% | 99.49% | 96.99% | 100% |  |  |  |  | 15.47% | 261367 | 261367 | 0 | 261367 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 248.27 |  |  |  |  | -2.22e-14% | 0.01973% | 5% | 5% | 70.4
2025-04-11 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.1159 | 6.04 | 96.05% | 98.75% | 97.26% | 100% |  |  |  |  | 13.85% | 234033 | 234033 | 0 | 234033 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 233.77 |  |  |  |  | 0% | 0.02008% | 5% | 5% | 70.4
2025-04-12 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.4291 | 6.85 | 98.98% | 99.13% | 99.85% | 100% |  |  |  |  | 15.97% | 269769 | 269769 | 0 | 269769 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 265.35 |  |  |  |  | 0% | 0.02021% | 5% | 5% | 70.4
2025-04-13 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.9427 | 6.62 | 100% | 100% | 100% | 100% |  |  |  |  | 13.47% | 227580 | 227580 | 0 | 227580 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 222.36 |  |  |  |  | -1.11e-14% | 0.02016% | 5% | 5% | 70.4
2025-04-14 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.9261 | 6.46 | 99.89% | 99.89% | 100% | 100% |  |  |  |  | 13.69% | 231240 | 231240 | 0 | 231240 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 220.87 |  |  |  |  | 0% | 0.02007% | 5% | 5% | 70.4
2025-04-15 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.0939 | 6.81 | 99.15% | 99.15% | 100% | 83.04% |  |  |  |  | 15.08% | 254860 | 254860 | 0 | 254860 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 107.5 |  |  |  |  | -1.11e-14% | 0.008959% | 5% | 5% | 70.4
2025-04-16 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.2598 | 6.18 | 99.17% | 99.17% | 100% | 100% |  |  |  |  | 17.85% | 301619 | 301619 | 0 | 301619 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 142.22 |  |  |  |  | 0% | 0.004154% | 5% | 5% | 70.4
2025-04-17 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 6.2409 | 8.07 | 98.68% | 99.08% | 99.6% | 100% |  |  |  |  | 24.06% | 406593 | 406593 | 0 | 406593 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 392.95 |  |  |  |  | -1.11e-14% | 0.01305% | 5% | 5% | 70.4
2025-04-18 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.7127 | 7.18 | 99.06% | 99.06% | 100% | 100% |  |  |  |  | 21.53% | 363733 | 363733 | 0 | 363733 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 354.48 |  |  |  |  | 0% | 0.01384% | 5% | 5% | 70.4
2025-04-19 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.7152 | 7.01 | 99.08% | 99.08% | 100% | 100% |  |  |  |  | 18.73% | 316438 | 316438 | 0 | 316438 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 301.5 |  |  |  |  | 0% | 0.02% | 5% | 5% | 70.4
2025-04-20 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.1234 | 6.58 | 100% | 100% | 100% | 100% |  |  |  |  | 18.02% | 304485 | 304485 | 0 | 304485 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 293.29 |  |  |  |  | 0% | 0.01992% | 5% | 5% | 70.4
2025-04-21 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.4977 | 5.55 | 98.21% | 100% | 98.21% | 100% |  |  |  |  | 11.29% | 190695 | 190695 | 0 | 190695 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 187.51 |  |  |  |  | 0% | 0.02027% | 5% | 5% | 70.4
2025-04-22 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.2566 | 5.27 | 97.95% | 99.56% | 98.39% | 85.19% |  |  |  |  | 7.189% | 121460 | 121460 | 0 | 121460 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 80.64 |  |  |  |  | 2.22e-14% | 0.01991% | 5% | 5% | 70.4
2025-04-23 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.6352 | 5.79 | 93.98% | 98.42% | 95.5% | 100% |  |  |  |  | 10.98% | 185519 | 185519 | 0 | 185519 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 170 |  |  |  |  | 0% | 0.01848% | 5% | 5% | 70.4
2025-04-24 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.6136 | 5.65 | 94.43% | 99.18% | 95.21% | 100% |  |  |  |  | 8.925% | 150802 | 150802 | 0 | 150802 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 135 |  |  |  |  | 2.22e-14% | 0.02274% | 5% | 5% | 70.4
2025-04-25 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.542 | 5.76 | 97.24% | 98.56% | 98.66% | 100% |  |  |  |  | 10.07% | 170185 | 170185 | 0 | 170185 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 176.57 |  |  |  |  | 0% | 0.02027% | 5% | 5% | 70.4
2025-04-26 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.3225 | 5.12 | 90.95% | 97.98% | 92.83% | 100% |  |  |  |  | 8.564% | 144697 | 144697 | 0 | 144697 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 147.15 |  |  |  |  | 0% | 0.02008% | 5% | 5% | 70.4
2025-04-27 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 3.9584 | 4.59 | 98.98% | 98.98% | 100% | 100% |  |  |  |  | 6.724% | 113604 | 113604 | 0 | 113604 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 112.74 |  |  |  |  | -1.11e-14% | 0.02017% | 5% | 5% | 70.4
2025-04-28 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.1516 | 5.13 | 98.36% | 98.36% | 100% | 100% |  |  |  |  | 7.795% | 131712 | 131712 | 0 | 131712 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 131.18 |  |  |  |  | 0% | 0.0174% | 5% | 5% | 70.4
2025-04-29 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.8641 | 5.78 | 99.2% | 99.2% | 100% | 100% |  |  |  |  | 12.13% | 204908 | 204908 | 0 | 204908 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 203.66 |  |  |  |  | 0% | 0.02022% | 5% | 5% | 70.4
2025-04-30 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.6725 | 7.02 | 99.32% | 99.32% | 100% | 100% |  |  |  |  | 17.99% | 304033 | 304033 | 0 | 304033 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 298.91 |  |  |  |  | 0% | 0.02023% | 5% | 5% | 70.4
2025-05-01 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 5.5466 | 7.19 | 99.87% | 99.87% | 100% | 100% |  |  |  |  | 19.94% | 336843 | 336843 | 0 | 336843 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 326.23 |  |  |  |  | -2.22e-14% | 0.01989% | 5% | 5% | 70.4
2025-05-02 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 6.2659 | 8.36 | 99.21% | 99.21% | 100% | 100% |  |  |  |  | 29.17% | 492802 | 492802 | 0 | 492802 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 475.46 |  |  |  |  | 0% | 0.02024% | 5% | 5% | 70.4
2025-05-03 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 6.4045 | 8.31 | 95.88% | 99.86% | 96.02% | 100% |  |  |  |  | 28.25% | 477257 | 477257 | 0 | 477257 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 347.9 |  |  |  |  | 2.22e-14% | 0.02028% | 5% | 5% | 70.4
2025-05-04 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 6.7609 | 9.13 | 100% | 100% | 100% | 100% |  |  |  |  | 29.44% | 497495 | 497495 | 0 | 497495 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 493.44 |  |  |  |  | 0% | 0.02027% | 5% | 5% | 70.4
2025-05-05 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 6.318 | 7.96 | 99.47% | 99.47% | 100% | 100% |  |  |  |  | 27.24% | 460318 | 460318 | 0 | 460318 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 464.18 |  |  |  |  | 0% | 0.02025% | 5% | 5% | 70.4
2025-05-06 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 5.9805 | 7.49 | 100% | 100% | 100% | 100% |  |  |  |  | 22.59% | 381718 | 381718 | 0 | 381718 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 380.97 |  |  |  |  | 0% | 0.0202% | 5% | 5% | 70.4
2025-05-07 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 6.8957 | 8.71 | 100% | 100% | 100% | 100% |  |  |  |  | 31.09% | 525250 | 525250 | 0 | 525250 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 522.37 |  |  |  |  | 0% | 0.02028% | 5% | 5% | 70.4
2025-05-08 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 7.2266 | 9.55 | 98.51% | 98.7% | 99.81% | 100% |  |  |  |  | 36.51% | 616955 | 616955 | 0 | 616955 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 592.7 |  |  |  |  | 0% | 0.0203% | 5% | 5% | 70.4
2025-05-09 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 5.0366 | 6.73 | 93% | 95.48% | 97.4% | 100% |  |  |  |  | 12.42% | 209885 | 209885 | 0 | 209885 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 202.61 |  |  |  |  | 0% | 0.02018% | 5% | 5% | 70.4
2025-05-10 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.4364 | 6.13 | 90.97% | 94.87% | 95.89% | 100% |  |  |  |  | 9.242% | 156148 | 156148 | 0 | 156148 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 141.12 |  |  |  |  | 2.22e-14% | 0.01931% | 5% | 5% | 70.4
2025-05-11 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 3.907 | 4.99 | 96.57% | 96.57% | 100% | 100% |  |  |  |  | 6.398% | 108095 | 108095 | 0 | 108095 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 105.19 |  |  |  |  | 0% | 0.02001% | 5% | 5% | 70.4
2025-05-12 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 3.5143 | 4.8 | 87.33% | 95.84% | 91.12% | 100% |  |  |  |  | 5.433% | 91789 | 91789 | 0 | 91789 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 124.03 |  |  |  |  | 0% | 0.02434% | 5% | 5% | 70.4
2025-05-13 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 3.398 | 4.01 | 96.44% | 96.44% | 100% | 87.88% |  |  |  |  | 4.919% | 83105 | 83105 | 0 | 83105 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 35.5 |  |  |  |  | -2.22e-14% | 0.01851% | 5% | 5% | 70.4
2025-05-14 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 3.7082 | 4.69 | 85.41% | 95.99% | 88.98% | 100% |  |  |  |  | 5.791% | 97848 | 97848 | 0 | 97848 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 107.19 |  |  |  |  | 0% | 0.01972% | 5% | 5% | 70.4
2025-05-15 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.022 | 5.43 | 94.1% | 97.69% | 96.32% | 100% |  |  |  |  | 5.803% | 98053 | 98053 | 0 | 98053 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 91.28 |  |  |  |  | 0% | 0.02019% | 5% | 5% | 70.4
2025-05-16 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 3.5484 | 4.28 | 99.22% | 99.96% | 99.27% | 100% |  |  |  |  | 4.409% | 74497 | 74497 | 0 | 74497 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 5.64 |  |  |  |  | 0% | 0.0009501% | 5% | 5% | 70.4
2025-05-17 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.8418 | 6.14 | 99.25% | 99.46% | 99.79% | 100% |  |  |  |  | 10.39% | 175607 | 175607 | 0 | 175607 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 38.29 |  |  |  |  | 0% | 0.008761% | 5% | 5% | 70.4
2025-05-18 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 5.5184 | 6.98 | 96.91% | 100% | 96.91% | 100% |  |  |  |  | 8.093% | 136747 | 136747 | 0 | 136747 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 65.28 |  |  |  |  | 0% | 0.001875% | 5% | 5% | 70.4
2025-05-19 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.9407 | 5.89 | 98.13% | 99.78% | 98.34% | 100% |  |  |  |  | 7.331% | 123872 | 123872 | 0 | 123872 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 77.28 |  |  |  |  | -1.11e-14% | 0.001307% | 5% | 5% | 70.4
2025-05-20 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.4509 | 5.38 | 91.04% | 97.97% | 92.93% | 100% |  |  |  |  | 6.745% | 113971 | 113971 | 0 | 113971 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 79.88 |  |  |  |  | -1.11e-14% | 0.0003105% | 5% | 5% | 70.4
2025-05-21 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.4891 | 6.25 | 100% | 100% | 100% | 100% |  |  |  |  | 9.291% | 156981 | 156981 | 0 | 156981 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 155.18 |  |  |  |  | 0% | 0% | 5% | 5% | 70.4
2025-05-22 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.5873 | 6.51 | 98.39% | 100% | 98.39% | 100% |  |  |  |  | 9.733% | 164448 | 164448 | 0 | 164448 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 170.89 |  |  |  |  | 0% | 0.01091% | 5% | 5% | 70.4
2025-05-23 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.4518 | 6.17 | 86.22% | 99.6% | 86.56% | 100% |  |  |  |  | 8.679% | 146641 | 146641 | 0 | 146641 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 170.25 |  |  |  |  | 0% | 0.01511% | 5% | 5% | 70.4
2025-05-24 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 2.885 | 3.79 | 99.64% | 99.64% | 100% | 100% |  |  |  |  | 2.919% | 49311 | 49311 | 0 | 49311 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 48.3 |  |  |  |  | 0% | 0.04492% | 5% | 5% | 70.4
2025-05-25 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 6.3202 | 8.55 | 99.01% | 99.25% | 99.77% | 100% |  |  |  |  | 29.4% | 496668 | 496668 | 0 | 496668 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 500.2 |  |  |  |  | 0% | 0.00446% | 5% | 5% | 70.4
2025-05-26 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 7.1618 | 9.75 | 94.94% | 99.18% | 95.72% | 100% |  |  |  |  | 34.73% | 586779 | 586779 | 0 | 586779 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 588 |  |  |  |  | 0% | 0.003775% | 5% | 5% | 70.4
2025-05-27 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 6.3984 | 8.17 | 100% | 100% | 100% | 100% |  |  |  |  | 29.87% | 504609 | 504609 | 0 | 504609 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 503 |  |  |  |  | 2.22e-14% | 0.00439% | 5% | 5% | 70.4
2025-05-28 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 7.1457 | 8.91 | 96.68% | 99.74% | 96.93% | 100% |  |  |  |  | 34.25% | 578733 | 578733 | 0 | 578733 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 579 |  |  |  |  | 0% | 0.003828% | 5% | 5% | 70.4
2025-05-29 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 7.6143 | 9.62 | 99.73% | 99.73% | 100% | 100% |  |  |  |  | 42.11% | 711533 | 711533 | 0 | 711533 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 715.1 |  |  |  |  | 0% | 0.003113% | 5% | 5% | 70.4
2025-05-30 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 10.2359 | 12.39 | 99.55% | 99.66% | 99.88% | 100% |  |  |  |  | 75.98% | 1283785 | 1283785 | 0 | 1283785 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 1280.2 |  |  |  |  | 0% | 0.001726% | 5% | 5% | 70.4
2025-05-31 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 8.8632 | 11.18 | 99.86% | 100% | 99.86% | 100% |  |  |  |  | 58.91% | 995423 | 995423 | 0 | 995423 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 994 |  |  |  |  | 0% | 0.002225% | 5% | 5% | 70.4
2025-06-01 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 6.5211 | 8.93 | 100% | 100% | 100% | 100% |  |  |  |  | 28.24% | 477059 | 477059 | 0 | 477059 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 372 |  |  |  |  | -1.11e-14% | 0.004643% | 5% | 5% | 70.4
2025-06-02 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 6.645 | 8.89 | 98.01% | 98.77% | 99.23% | 100% |  |  |  |  | 29.03% | 490432 | 490432 | 0 | 490432 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 148.3 |  |  |  |  | 0% | 0.006864% | 5% | 5% | 70.4
2025-06-03 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 6.7316 | 8.99 | 99.22% | 99.52% | 99.69% | 100% |  |  |  |  | 31.06% | 524861 | 524861 | 0 | 524861 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 321.96 |  |  |  |  | 0% | 0.01811% | 5% | 5% | 70.4
2025-06-04 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 6.6355 | 9.1 | 98.76% | 98.8% | 99.96% | 100% |  |  |  |  | 30.21% | 510411 | 510411 | 0 | 510411 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 439.93 |  |  |  |  | 2.22e-14% | 0.01893% | 5% | 5% | 70.4
2025-06-05 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 6.1284 | 7.6 | 98.5% | 99.37% | 99.13% | 100% |  |  |  |  | 22.4% | 378554 | 378554 | 0 | 378554 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 320.79 |  |  |  |  | 0% | 0.01788% | 5% | 5% | 70.4
2025-06-06 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 5.317 | 6.84 | 98.67% | 98.67% | 100% | 100% |  |  |  |  | 14.4% | 243339 | 243339 | 0 | 243339 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 208.73 |  |  |  |  | 0% | 0.01778% | 5% | 5% | 70.4
2025-06-07 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 5.6864 | 7.26 | 99.72% | 99.72% | 100% | 100% |  |  |  |  | 17.61% | 297459 | 297459 | 0 | 297459 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 255.38 |  |  |  |  | 0% | 0.01797% | 5% | 5% | 70.4
2025-06-08 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 6.8177 | 8.57 | 99.88% | 99.88% | 100% | 100% |  |  |  |  | 29.71% | 501923 | 501923 | 0 | 501923 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 448.22 |  |  |  |  | 0% | 0.0188% | 5% | 5% | 70.4
2025-06-09 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 7.3814 | 9.48 | 99.97% | 99.97% | 100% | 100% |  |  |  |  | 37.35% | 631093 | 631093 | 0 | 631093 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 553.03 |  |  |  |  | 2.22e-14% | 0.01868% | 5% | 5% | 70.4
2025-06-10 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 7.9764 | 10.03 | 99.8% | 99.8% | 100% | 94.34% |  |  |  |  | 43.98% | 743030 | 743030 | 0 | 743030 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 333 |  |  |  |  | 0% | 0.009079% | 5% | 5% | 70.4
2025-06-11 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 8.4359 | 10.56 | 99.65% | 99.65% | 100% | 100% |  |  |  |  | 51.47% | 869654 | 869654 | 0 | 869654 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 305.49 |  |  |  |  | 0% | 0.00756% | 5% | 5% | 70.4
2025-06-12 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 7.3545 | 9.94 | 100% | 100% | 100% | 100% |  |  |  |  | 38.22% | 645773 | 645773 | 0 | 645773 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 611.16 |  |  |  |  | -2.22e-14% | 0.02017% | 5% | 5% | 70.4
2025-06-13 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-06-14 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-06-15 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-06-16 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-06-17 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-06-18 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-06-19 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-06-20 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-06-21 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-06-22 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-06-23 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-06-24 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-06-25 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-06-26 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-06-27 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-06-28 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-06-29 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-06-30 | 2026 | 2025 | 2025-06-01 | 30 | [23 empty] | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-01 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-02 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-03 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-04 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-05 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-06 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-07 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-08 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-09 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-10 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-11 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-12 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-13 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-14 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-15 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-16 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-17 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-18 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-19 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-20 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-21 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-22 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-23 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-24 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-25 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-26 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-27 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-28 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-29 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-30 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-31 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-01 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-02 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-03 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-04 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-05 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-06 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-07 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-08 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-09 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-10 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-11 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-12 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-13 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-14 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-15 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-16 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-17 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-18 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-19 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-20 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-21 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-22 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-23 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-24 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-25 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-26 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-27 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-28 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-29 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-30 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-31 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-01 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-02 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-03 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-04 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-05 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-06 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-07 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-08 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-09 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-10 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-11 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-12 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-13 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-14 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-15 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-16 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-17 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-18 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-19 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-20 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-21 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-22 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-23 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-24 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-25 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-26 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-27 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-28 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-29 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-30 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-01 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-02 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-03 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-04 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-05 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-06 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-07 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-08 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-09 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-10 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-11 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-12 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-13 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-14 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-15 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-16 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-17 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-18 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-19 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-20 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-21 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-22 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-23 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-24 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-25 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-26 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-27 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-28 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-29 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-30 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-31 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-01 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-02 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-03 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-04 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-05 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-06 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-07 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-08 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-09 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-10 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-11 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-12 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-13 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-14 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-15 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-16 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-17 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-18 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-19 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-20 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-21 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-22 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-23 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-24 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-25 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-26 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-27 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-28 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-29 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-30 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-01 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-02 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-03 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-04 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-05 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-06 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-07 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-08 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-09 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-10 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-11 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-12 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-13 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-14 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-15 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-16 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-17 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-18 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-19 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-20 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-21 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-22 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-23 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-24 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-25 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-26 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-27 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-28 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-29 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-30 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-31 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-01 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-02 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-03 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-04 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-05 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-06 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-07 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-08 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-09 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-10 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-11 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-12 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-13 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-14 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-15 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-16 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-17 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-18 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-19 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-20 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-21 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-22 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-23 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-24 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-25 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-26 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-27 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-28 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-29 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-30 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-31 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-01 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-02 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-03 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-04 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-05 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-06 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-07 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-08 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-09 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-10 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-11 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-12 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-13 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-14 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-15 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-16 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-17 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-18 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-19 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-20 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-21 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-22 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-23 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-24 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-25 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-26 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-27 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-28 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-01 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-02 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-03 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-04 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-05 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-06 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-07 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-08 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-09 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-10 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-11 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-12 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-13 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-14 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-15 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-16 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-17 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-18 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-19 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-20 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-21 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-22 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-23 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-24 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-25 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-26 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-27 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-28 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-29 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-30 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-31 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
Formulas:
Month Year = Daily_KPI[[#This Row],[Date]]-DAY(Daily_KPI[[#This Row],[Date]])+1
Days = DAY(EOMONTH([Date],0))
Date = [Date, row above]+1

## Input_Raw
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117
[5 empty] | Energy Generated by individual Turbine | [43 empty] | Wind Speed (M/s) | [47 empty] | Meter Readings | [7 empty] | Calculated Energy Numbers
Date | Finacial Year | Calendor Year | Month Year | Days | P-01 | P-02 | P-03 | P-04 | P-05 | P-06 | P-07 | P-08 | P-09 | P-10 | P-11 | P-12 | P-13 | P-14 | P-15 | P-16 | P-17 | P-18 | P-19 | P-20 | P-22 | P-23 | P-25 | P-26 | P-27 | P-28 | P-31 | P-32 | P-34 | P-37 | P-38 | P-40 | P-41 | P-42 | P-43 | P-45 | P-46 | P-47 | P-48 | P-50 | P-51 | P-52 | P-55 | P-56 | WS_P-01 | WS_P-02 | WS_P-03 | WS_P-04 | WS_P-05 | WS_P-06 | WS_P-07 | WS_P-08 | WS_P-09 | WS_P-10 | WS_P-11 | WS_P-12 | WS_P-13 | WS_P-14 | WS_P-15 | WS_P-16 | WS_P-17 | WS_P-18 | WS_P-19 | WS_P-20 | WS_P-22 | WS_P-23 | WS_P-25 | WS_P-26 | WS_P-27 | WS_P-28 | WS_P-31 | WS_P-32 | WS_P-34 | WS_P-37 | WS_P-38 | WS_P-40 | WS_P-41 | WS_P-42 | WS_P-43 | WS_P-45 | WS_P-46 | WS_P-47 | WS_P-48 | WS_P-50 | WS_P-51 | WS_P-52 | WS_P-55 | WS_P-56 | WTG Total Gneration (MWh) | Wind Speed Average cumulative (m/S)2 | Wind Speed Max (m/S) | Rain (mm) | 33 kV_Wind_F1_Export reading | 33 kV_Wind_F1_Import reading | 33 kV_Wind_F2_Export_reading | 33 kV_Wind_F2_Import_reading | 33 kV_Wind_F3_Export_Reading | 33 kV_Wind_F3_Import_Reading | 33 kV_Wind_F4_Export Reading | 33 kV_Wind_F4_Import Reading | 33 kV_F1_Total_Export (MWh) | 33 kV_Wind_F1_Import (MWh) | 33 kV_F2_Total_Export (MWh)2 | 33 kV_Wind_F2_Import (MWh) | 33 kV_Wind_F3_Export (MWh) | 33 kV_Wind_F3_Import (MWh)2 | 33 kV_Wind_F4_Export (MWh) | 33 kV_Wind_F4_Import (MWh)2 | 33 kV_Wind_Total_Export (MWh) | 33 kV_Wind_Total_Import (MWh) | 33 kV Line Loss (%) | EbMA(%) | Forecasting Data count received on Forecasting Portal | Forecasting Penalties (INR) | Expected Energy As Per Power Curve (MWh) | Reactive Energy (MVArH) | Operational Capacity
2025-03-29 | 2025 | 2025 | 2025-03-01 | 31 | 6588 | 6752 | 7308 | 4560 | 4436 | 3156 | 4936 | 2472 | 1594 | 1536 | 1938 | 2062 | 2156 | 2066 | 1992 | 2430 | 2670 | 6332 | 2648 | 2525 | 4952 | 5652 | 3308 | 2956 | 3544 | 3264 | 7016 | 2540 | 4808 | 3862 | 3224 | 2220 | 3612 | 4604 | 3274 | 6072 | 4800 | 4032 | 4272 | 2936 | 2990 | 4564 | 5896 | 4380 | 5.01 | 5.26 | 5.33 | 5.18 | 4.52 | 4.41 | 4.94 | 4.26 | 3.85 | 4.11 | 3.96 | 4.15 | 4.18 | 4.34 | 4.37 | 4.53 | 4.61 | 5.17 | 4.65 | 4.3 | 5.46 | 5.6 | 4.2 | 4.48 | 4.73 | 4.71 | 4.99 | 3.82 | 5.2 | 4.61 | 4.51 | 4.11 | 4.72 | 4.53 | 4.69 | 5.68 | 4.91 | 4.35 | 4.67 | 4.05 | 4.09 | 4.75 | 5.16 | 5.05 | 168.935 | 4.6409 | 5.68 |  | 24830 |  | 40801 |  | 37204 |  | 66100 |  | 24.83 |  | 40.801 |  | 37.204 |  | 66.1 |  | 168.935 | 0 | 0% |  | 89 | 251.75 | 156.79 |  | 70.4
2025-03-30 | 2025 | 2025 | 2025-03-01 | 31 | 8936 | 7288 | 6868 | 6172 | 4268 | 3588 | 5354 | 2160 | 1444 | 1408 | 1792 | 2198 | 2320 | 2460 | 2208 | 2244 | 2764 | 6940 | 2756 | 2719 | 6344 | 6796 | 3068 | 3092 | 3684 | 3152 | 5592 | 2868 | 5300 | 4688 | 3244 | 1882 | 3968 | 5704 | 3516 | 6320 | 5152 | 4908 | 5504 | 3816 | 4472 | 5472 | 8544 | 6904 | 5.8 | 5.57 | 5.5 | 5.61 | 4.83 | 4.92 | 5.25 | 4.52 | 4.04 | 4.33 | 4 | 4.32 | 4.41 | 4.46 | 4.45 | 4.38 | 4.54 | 5.58 | 4.58 | 4.35 | 5.63 | 5.61 | 4.6 | 4.98 | 5.38 | 5.24 | 4.91 | 4.21 | 5.24 | 4.96 | 4.46 | 4.16 | 5.02 | 5.15 | 4.49 | 5.9 | 5.21 | 4.86 | 5.34 | 4.38 | 4.66 | 5.17 | 6.15 | 5.88 | 189.877 | 4.9325 | 6.15 |  | 24318 |  | 46523 |  | 41294 |  | 77742 |  | 24.318 |  | 46.523 |  | 41.294 |  | 77.742 |  | 189.877 | 0 | 0% |  | 90 | 884 | 162.74 |  | 70.4
2025-03-31 | 2025 | 2025 | 2025-03-01 | 31 | 3784 | 2960 | 2816 | 970 | 2856 | 1928 | 2996 | 1136 | 688 | 828 | 994 | 1212 | 1248 | 1368 | 1206 | 1338 | 1552 | 3472 | 1504 | 1374 | 1404 | 1652 | 1660 | 1740 | 2112 | 1848 | 2168 | 864 | 1232 | 1868 | 1724 | 1038 | 2564 | 3656 | 1132 | 3596 | 2932 | 2932 | 3200 | 1018 | 1536 | 1926 | 4148 | 3604 | 4.11 | 4.13 | 3.94 | 3.15 | 3.98 | 3.88 | 4.19 | 3.27 | 3.02 | 3.39 | 3.26 | 3.49 | 3.45 | 3.43 | 3.48 | 3.39 | 3.77 | 4.25 | 3.59 | 3.31 | 3.85 | 3.86 | 3.38 | 3.97 | 4.04 | 3.91 | 3.29 | 2.89 | 3.34 | 3.59 | 3.27 | 3.19 | 4.29 | 4.33 | 3.52 | 4.75 | 4.32 | 3.98 | 4.36 | 2.74 | 3.19 | 3.7 | 4.68 | 4.6 | 87.784 | 3.7164 | 4.75 |  | 13466 |  | 16456 |  | 24702 |  | 33160 |  | 13.466 |  | 16.456 |  | 24.702 |  | 33.16 |  | 87.784 | 0 | -1.11e-14% |  | 88 | 2257.38 | 66.47 |  | 70.4
2025-04-01 | 2026 | 2025 | 2025-04-01 | 30 | 4268 | 4068 | 3800 | 7152 | 6388 | 6152 | 2860 | 5052 | 4148 | 6102 | 7662 | 7860 | 7466 | 7150 | 5670 | 5514 | 5412 | 3300 | 6996 | 5745 | 7184 | 8632 | 7020 | 6844 | 4100 | 6952 | 3420 | 3056 | 5872 | 3422 | 6164 | 4716 | 6208 | 5104 | 8556 | 8624 | 6180 | 4920 | 5324 | 4338 | 3536 | 3794 | 4236 | 3528 | 4.52 | 4.61 | 4.6 | 5.2 | 5.11 | 5.17 | 4.42 | 5.73 | 4.86 | 5.41 | 5.49 | 5.61 | 5.42 | 5.37 | 5.08 | 4.85 | 4.87 | 4.29 | 5.26 | 4.81 | 5.4 | 5.55 | 5.94 | 6.34 | 5.5 | 6.47 | 4.09 | 4.37 | 4.82 | 4.79 | 4.75 | 4.52 | 5.61 | 4.8 | 5.37 | 5.88 | 5.2 | 4.57 | 4.92 | 4.29 | 4.61 | 4.8 | 4.98 | 4.73 | 244.495 | 5.0677 | 6.47 |  | 63206 |  | 80047 |  | 53616 |  | 47626 |  | 63.206 |  | 80.047 |  | 53.616 |  | 47.626 |  | 244.495 | 0 | -1.11e-14% |  | 89 | 25300 | 188.67 |  | 70.4
2025-04-02 | 2026 | 2025 | 2025-04-01 | 30 | 6296 | 4972 | 4080 | 5304 | 10732 | 9008 | 5052 | 4672 | 3214 | 4976 | 5884 | 7356 | 8586 | 8718 | 6402 | 7596 | 8356 | 5740 | 10008 | 8600 | 5096 | 5336 | 6688 | 8336 | 8316 | 8028 | 4244 | 5576 | 4028 | 7408 | 9640 | 5766 | 10360 | 7964 | 7744 | 11976 | 7700 | 8872 | 8504 | 6352 | 7568 | 7352 | 9220 | 8084 | 5.1 | 4.96 | 4.74 | 5 | 6.19 | 6.02 | 5.03 | 5.12 | 4.64 | 5.25 | 5.11 | 5.52 | 5.84 | 5.87 | 5.48 | 5.7 | 5.68 | 5.27 | 5.98 | 5.65 | 5.05 | 4.95 | 5.37 | 6.07 | 6.26 | 6.2 | 4.63 | 4.68 | 4.76 | 5.15 | 5.85 | 5.01 | 6.55 | 5.63 | 5.26 | 6.87 | 4.8 | 5.68 | 5.94 | 5.09 | 5.35 | 5.44 | 6.04 | 5.98 | 315.71 | 5.4718 | 6.87 |  | 66056 |  | 86828 |  | 80882 |  | 81944 |  | 66.056 |  | 86.828 |  | 80.882 |  | 81.944 |  | 315.71 | 0 | 2.22e-14% |  | 95 | 25676 | 309.39 |  | 70.4
2025-04-03 | 2026 | 2025 | 2025-04-01 | 30 | 2864 | 2514 | 2568 | 2582 | 2348 | 1772 | 2086 | 1076 | 770 | 922 | 942 | 1016 | 1002 | 546 | 562 | 706 | 894 | 2588 | 948 | 819 | 2296 | 2480 | 1360 | 1556 | 1696 | 1508 | 1344 | 1312 | 2600 | 1758 | 1100 | 1526 | 2160 | 2624 | 1444 | 2944 | 2740 | 2456 | 2628 | 1136 | 1716 | 1784 | 2800 | 2544 | 3.75 | 3.9 | 3.77 | 3.82 | 3.63 | 3.71 | 3.81 | 3.04 | 2.96 | 3.25 | 3.06 | 3.27 | 3.08 | 2.93 | 3.05 | 3.1 | 3.42 | 3.91 | 3.15 | 3.08 | 3.88 | 3.78 | 3.07 | 3.8 | 3.58 | 3.47 | 3.43 | 3.06 | 4 | 3.38 | 3 | 3.29 | 4.05 | 3.83 | 3.1 | 4.1 | 4.17 | 3.59 | 4.09 | 2.9 | 3.31 | 3.58 | 4.03 | 4.18 | 77.037 | 3.5082 | 4.18 |  | 11848 |  | 16977 |  | 21198 |  | 27014 |  | 11.848 |  | 16.977 |  | 21.198 |  | 27.014 |  | 77.037 | 0 | 0% |  | 94 | 7538.5 | 72.87 |  | 70.4
2025-04-04 | 2026 | 2025 | 2025-04-01 | 30 | 2716 | 2818 | 3052 | 3092 | 3528 | 2796 | 2618 | 2496 | 1856 | 2022 | 2102 | 2154 | 2434 | 1572 | 798 | 1024 | 1380 | 3196 | 1406 | 1083 | 3124 | 3560 | 3108 | 2848 | 3372 | 3032 | 3404 | 2240 | 2868 | 3262 | 1412 | 1696 | 3168 | 2904 | 3116 | 4976 | 4096 | 3300 | 3096 | 1672 | 2784 | 3192 | 3516 | 3316 | 3.96 | 4.34 | 4.27 | 3.99 | 4.15 | 4.29 | 4.33 | 3.96 | 3.8 | 4.17 | 3.88 | 4.03 | 4.02 | 4.03 | 3.52 | 3.7 | 4.02 | 4.42 | 3.89 | 3.63 | 4.3 | 4.34 | 3.96 | 4.35 | 4.3 | 4.22 | 3.98 | 3.89 | 4.03 | 4.39 | 3.61 | 3.66 | 4.53 | 4.07 | 4.04 | 5.01 | 4.83 | 4.02 | 4.4 | 3.65 | 4.19 | 4.59 | 4.67 | 4.89 | 117.205 | 4.1436 | 5.01 |  | 25424 |  | 24435 |  | 29560 |  | 37786 |  | 25.424 |  | 24.435 |  | 29.56 |  | 37.786 |  | 117.205 | 0 | 0% |  | 80 | 1459.87 | 115.95 |  | 70.4
2025-04-05 | 2026 | 2025 | 2025-04-01 | 30 | 2060 | 3368 | 3088 | 5440 | 2920 | 2352 | 2928 | 2116 | 2560 | 2424 | 2928 | 2598 | 2442 | 2302 | 1794 | 2010 | 1980 | 2884 | 2430 | 2109 | 5192 | 6060 | 4888 | 4600 | 3876 | 3448 | 932 | 1628 | 4012 | 3004 | 2596 | 1232 | 2628 | 2704 | 4318 | 4076 | 2524 | 2308 | 2484 | 1624 | 1794 | 2880 | 4144 | 1756 | 4.42 | 4.77 | 4.64 | 5.33 | 4.37 | 4.39 | 4.61 | 3.98 | 4.5 | 4.7 | 4.5 | 4.44 | 4.39 | 4.29 | 4.17 | 4.18 | 4.13 | 4.47 | 4.35 | 4.07 | 5.38 | 5.5 | 4.9 | 5.23 | 4.86 | 4.79 | 4.02 | 3.47 | 4.77 | 4.29 | 4.09 | 3.79 | 4.63 | 4.21 | 4.78 | 5.01 | 4.37 | 3.73 | 4.3 | 3.58 | 3.47 | 4.34 | 4.92 | 4.63 | 127.441 | 4.4491 | 5.5 |  | 31880 |  | 40243 |  | 23228 |  | 32090 |  | 31.88 |  | 40.243 |  | 23.228 |  | 32.09 |  | 127.441 | 0 | 0% |  | 93 | 0 | 123.65 |  | 70.4
2025-04-06 | 2026 | 2025 | 2025-04-01 | 30 | 3244 | 3292 | 3884 | 3042 | 2524 | 2080 | 2482 | 1488 | 976 | 926 | 1140 | 1108 | 1112 | 1008 | 936 | 1118 | 1250 | 2768 | 1508 | 1524 | 3800 | 4304 | 2012 | 1844 | 2212 | 1920 | 2236 | 1880 | 2572 | 2672 | 1566 | 1008 | 2348 | 2512 | 1958 | 3400 | 2372 | 1964 | 2248 | 2640 | 2660 | 3484 | 3868 | 2240 | 4.23 | 4.51 | 4.56 | 4.14 | 3.63 | 3.82 | 4.23 | 3.61 | 3.24 | 3.51 | 3.25 | 3.43 | 3.26 | 3.08 | 3.13 | 3.02 | 3.43 | 4.12 | 3.39 | 3.18 | 4.67 | 4.7 | 3.63 | 4.14 | 4 | 3.78 | 3.84 | 3.49 | 3.96 | 3.96 | 3.03 | 3.09 | 4.17 | 3.84 | 3.59 | 4.66 | 4.34 | 3.64 | 3.99 | 3.64 | 3.73 | 4.3 | 4.67 | 4.24 | 97.13 | 3.8152 | 4.7 |  | 14738 |  | 24586 |  | 20456 |  | 37350 |  | 14.738 |  | 24.586 |  | 20.456 |  | 37.35 |  | 97.13 | 0 | 0% |  | 42 | 0 | 129.36 |  | 70.4
2025-04-07 | 2026 | 2025 | 2025-04-01 | 30 | 4816 | 6158 | 6360 | 4018 | 2620 | 2224 | 3702 | 1354 | 864 | 940 | 1064 | 1380 | 1418 | 1652 | 1514 | 1754 | 1870 | 4848 | 2142 | 1905 | 3932 | 4732 | 2128 | 2264 | 2656 | 2448 | 6486 | 2492 | 3980 | 3524 | 1970 | 604 | 2424 | 3584 | 2560 | 4672 | 3496 | 3156 | 3300 | 2890 | 4412 | 4524 | 4924 | 3876 | 4.79 | 5.37 | 5.5 | 4.86 | 4.04 | 4.26 | 4.86 | 3.65 | 3.57 | 3.76 | 3.51 | 3.8 | 3.77 | 3.82 | 3.92 | 3.88 | 4 | 5.07 | 4.1 | 3.75 | 4.99 | 5.12 | 3.84 | 4.43 | 4.38 | 4.32 | 5.13 | 4.03 | 4.83 | 4.52 | 3.62 | 3.43 | 4.5 | 4.43 | 4.07 | 5.13 | 4.88 | 4.17 | 4.58 | 3.96 | 4.6 | 4.9 | 5.19 | 4.99 | 133.637 | 4.3709 | 5.5 |  | 16516 |  | 32029 |  | 26080 |  | 59012 |  | 16.516 |  | 32.029 |  | 26.08 |  | 59.012 |  | 133.637 | 0 | 0% |  | 88 | 753.5 | 94.92 |  | 70.4
2025-04-08 | 2026 | 2025 | 2025-04-01 | 30 | 3588 | 1666 | 2912 | 2518 | 2796 | 2304 | 3262 | 1310 | 772 | 796 | 884 | 1082 | 1258 | 1118 | 1130 | 1160 | 1552 | 3528 | 1812 | 1467 | 2608 | 2816 | 1656 | 1684 | 2024 | 1904 | 2276 | 1236 | 2236 | 2142 | 1766 | 1798 | 2904 | 3448 | 1660 | 3304 | 3252 | 1624 | 3272 | 1198 | 1706 | 2192 | 3764 | 3380 | 4.41 | 4.43 | 4.37 | 4.17 | 4.12 | 4.38 | 4.57 | 3.88 | 3.53 | 3.84 | 3.64 | 3.84 | 3.87 | 3.71 | 3.73 | 3.64 | 4 | 4.45 | 4.14 | 3.7 | 4.47 | 4.4 | 3.93 | 4.41 | 4.5 | 4.48 | 3.79 | 3.21 | 4.16 | 3.87 | 3.66 | 3.86 | 4.64 | 4.52 | 3.76 | 4.86 | 4.86 | 4.33 | 4.69 | 3.08 | 3.49 | 4.05 | 4.75 | 4.69 | 92.765 | 4.1109 | 4.86 |  | 13370 |  | 21843 |  | 24702 |  | 32850 |  | 13.37 |  | 21.843 |  | 24.702 |  | 32.85 |  | 92.765 | 0 | 2.22e-14% |  | 57 | 0 | 38.78 |  | 70.4
2025-04-09 | 2026 | 2025 | 2025-04-01 | 30 | 5684 | 5040 | 3864 | 4080 | 3472 | 3760 | 5310 | 2120 | 1412 | 1598 | 1914 | 2114 | 2158 | 2354 | 2188 | 2644 | 2842 | 3504 | 2940 | 2546 | 3968 | 3264 | 2184 | 2680 | 2864 | 2632 | 3202 | 1676 | 4084 | 2292 | 2702 | 2586 | 3384 | 3928 | 2786 | 4772 | 4544 | 3144 | 3176 | 2280 | 2364 | 2540 | 5452 | 5684 | 4.83 | 4.93 | 4.44 | 4.78 | 4.13 | 4.67 | 5.02 | 3.85 | 3.49 | 3.89 | 3.75 | 3.96 | 3.95 | 3.9 | 3.96 | 4.05 | 4.19 | 4.51 | 4.25 | 3.91 | 4.9 | 4.36 | 3.73 | 4.49 | 4.42 | 4.31 | 3.9 | 3.33 | 4.81 | 3.77 | 3.73 | 3.98 | 4.65 | 4.52 | 4.08 | 5.16 | 5.21 | 4.22 | 5.39 | 3.6 | 3.69 | 3.96 | 5.09 | 5.26 | 139.732 | 4.2959 | 5.39 |  | 21676 |  | 36398 |  | 32766 |  | 48892 |  | 21.676 |  | 36.398 |  | 32.766 |  | 48.892 |  | 139.732 | 0 | 0% |  | 57 | 786.88 | 101.75 |  | 70.4
2025-04-10 | 2026 | 2025 | 2025-04-01 | 30 | 10424 | 12190 | 6296 | 7670 | 7064 | 7756 | 11548 | 3632 | 2030 | 2106 | 2814 | 3628 | 4604 | 4408 | 4292 | 4496 | 4924 | 9236 | 5034 | 4201 | 6720 | 5204 | 3724 | 4296 | 4368 | 4048 | 4240 | 3476 | 7492 | 4094 | 4744 | 4258 | 6916 | 8448 | 3622 | 9128 | 9048 | 6536 | 8824 | 4904 | 2812 | 3112 | 10932 | 12068 | 6.35 | 6.56 | 5.27 | 5.94 | 5.41 | 6.01 | 6.63 | 4.67 | 4.11 | 4.51 | 4.41 | 4.8 | 5.12 | 5.06 | 5.16 | 5.16 | 5.07 | 5.98 | 5.27 | 4.78 | 5.77 | 5.06 | 4.41 | 5.11 | 5.05 | 4.95 | 4.4 | 4.63 | 5.88 | 4.84 | 4.72 | 5.02 | 5.88 | 5.85 | 4.42 | 6.56 | 6.41 | 5.24 | 6.21 | 5.1 | 5.67 | 5.9 | 6.79 | 6.9 | 261.367 | 5.3873 | 6.9 |  | 35250 |  | 62807 |  | 67978 |  | 95332 |  | 35.25 |  | 62.807 |  | 67.978 |  | 95.332 |  | 261.367 | 0 | -2.22e-14% |  | 96 | 559 | 248.27 |  | 70.4
2025-04-11 | 2026 | 2025 | 2025-04-01 | 30 | 8048 | 6866 | 6204 | 6172 | 8244 | 6180 | 4388 | 3544 | 2542 | 3226 | 3752 | 4476 | 4496 | 4530 | 4392 | 5048 | 5862 | 7580 | 5384 | 4687 | 6188 | 6220 | 4844 | 5336 | 5680 | 5264 | 4884 | 482 | 5216 | 820 | 6316 | 4034 | 7780 | 8520 | 4568 | 7112 | 7456 | 6608 | 7756 | 2994 | 3082 | 3576 | 6392 | 7284 | 5.51 | 5.34 | 5.21 | 5.4 | 5.59 | 5.55 | 5.36 | 4.69 | 4.41 | 4.92 | 4.84 | 4.96 | 5.01 | 5.03 | 5.11 | 5.25 | 5.29 | 5.57 | 5.2 | 4.8 | 5.51 | 5.26 | 4.77 | 5.29 | 5.29 | 5.18 | 4.43 | 3.14 | 5.21 | 3.73 | 5.14 | 4.93 | 6.01 | 5.7 | 4.66 | 6 | 6.04 | 5.17 | 5.83 | 4.21 | 4.34 | 4.72 | 5.67 | 5.83 | 234.033 | 5.1159 | 6.04 |  | 43160 |  | 64583 |  | 63690 |  | 62600 |  | 43.16 |  | 64.583 |  | 63.69 |  | 62.6 |  | 234.033 | 0 | 0% |  | 96 | 1616 | 233.77 |  | 70.4
2025-04-12 | 2026 | 2025 | 2025-04-01 | 30 | 9372 | 7640 | 7404 | 7204 | 6904 | 5168 | 7328 | 3656 | 2614 | 3416 | 3996 | 4676 | 4802 | 5186 | 4848 | 6084 | 6810 | 8040 | 6078 | 5279 | 6748 | 7992 | 4904 | 5392 | 6312 | 6128 | 5726 | 3162 | 6636 | 4012 | 7254 | 3960 | 6420 | 8160 | 5812 | 10452 | 10084 | 8388 | 8116 | 3196 | 2426 | 4840 | 9440 | 7704 | 6.03 | 5.74 | 5.79 | 5.84 | 5.39 | 5.26 | 5.84 | 4.79 | 4.39 | 4.92 | 4.78 | 5 | 5.17 | 5.35 | 5.38 | 5.72 | 5.63 | 6.01 | 5.5 | 5.08 | 5.87 | 5.88 | 4.96 | 5.5 | 5.78 | 5.79 | 4.92 | 4.06 | 5.85 | 4.61 | 5.47 | 4.9 | 5.72 | 5.86 | 5.19 | 6.85 | 6.72 | 5.82 | 6.07 | 3.83 | 4.36 | 4.86 | 6.38 | 6.02 | 269.769 | 5.4291 | 6.85 |  | 45896 |  | 75931 |  | 67652 |  | 80290 |  | 45.896 |  | 75.931 |  | 67.652 |  | 80.29 |  | 269.769 | 0 | 0% |  | 96 | 275 | 265.35 |  | 70.4
2025-04-13 | 2026 | 2025 | 2025-04-01 | 30 | 10252 | 8528 | 9040 | 5548 | 5512 | 4576 | 9688 | 1936 | 1346 | 1522 | 1848 | 2180 | 2054 | 2208 | 1996 | 2324 | 2952 | 9008 | 2884 | 2956 | 7852 | 8448 | 3824 | 3912 | 4724 | 3824 | 6906 | 3808 | 5404 | 5510 | 3404 | 2072 | 5196 | 7980 | 3836 | 7772 | 6076 | 6068 | 6396 | 3194 | 5612 | 7896 | 11188 | 8320 | 5.88 | 5.68 | 5.92 | 5.18 | 4.92 | 5.01 | 6.16 | 3.96 | 3.7 | 4 | 3.79 | 4.06 | 4.03 | 4.09 | 4.09 | 4.21 | 4.43 | 5.93 | 4.35 | 4.19 | 5.87 | 5.87 | 4.52 | 4.93 | 5.11 | 4.82 | 5.11 | 4.57 | 5.26 | 5.17 | 4.23 | 3.91 | 5.32 | 5.58 | 4.42 | 6.17 | 5.62 | 5.01 | 5.35 | 3.93 | 4.96 | 5.59 | 6.62 | 5.96 | 227.58 | 4.9427 | 6.62 |  | 27170 |  | 49812 |  | 51648 |  | 98950 |  | 27.17 |  | 49.812 |  | 51.648 |  | 98.95 |  | 227.58 | 0 | -1.11e-14% |  | 96 | 2148 | 222.36 |  | 70.4
2025-04-14 | 2026 | 2025 | 2025-04-01 | 30 | 8752 | 10494 | 11348 | 5314 | 5624 | 5428 | 6458 | 3284 | 2346 | 2432 | 2628 | 2916 | 2880 | 2448 | 2096 | 2540 | 2974 | 7524 | 2560 | 2070 | 5224 | 5896 | 3704 | 3560 | 4268 | 3784 | 10572 | 5176 | 5960 | 6360 | 2934 | 3408 | 5572 | 6320 | 3756 | 7904 | 7272 | 5684 | 6216 | 5606 | 7404 | 8664 | 7740 | 6140 | 5.61 | 6.22 | 6.46 | 5.16 | 4.56 | 5.12 | 5.53 | 4.56 | 4.31 | 4.57 | 4.21 | 4.34 | 4.28 | 4.06 | 4.1 | 4.08 | 4.3 | 5.69 | 4.21 | 3.71 | 5.17 | 5.15 | 4.33 | 4.79 | 4.85 | 4.67 | 6.02 | 4.74 | 5.28 | 5.11 | 3.74 | 4.43 | 5.18 | 5.13 | 4.36 | 5.93 | 5.75 | 4.82 | 5.3 | 4.59 | 5.34 | 5.7 | 5.78 | 5.51 | 231.24 | 4.9261 | 6.46 |  | 31802 |  | 43772 |  | 53428 |  | 102238 |  | 31.802 |  | 43.772 |  | 53.428 |  | 102.238 |  | 231.24 | 0 | 0% |  | 96 | 654 | 220.87 |  | 70.4
2025-04-15 | 2026 | 2025 | 2025-04-01 | 30 | 12860 | 14146 | 15412 | 4154 | 8044 | 6360 | 8280 | 1792 | 862 | 700 | 724 | 812 | 1028 | 1316 | 1186 | 1692 | 2434 | 11076 | 1606 | 1318 | 6200 | 7796 | 2760 | 2600 | 3512 | 2928 | 13956 | 6452 | 4752 | 7662 | 2122 | 3868 | 7772 | 8560 | 2872 | 8824 | 7508 | 7052 | 7100 | 9034 | 8356 | 10844 | 10088 | 6440 | 6.01 | 6.54 | 6.81 | 4.9 | 5.3 | 5.22 | 5.69 | 4.42 | 3.81 | 4 | 3.67 | 3.89 | 3.8 | 3.98 | 3.92 | 4.05 | 4.63 | 5.94 | 4.13 | 3.85 | 6.03 | 6.78 | 4.48 | 4.96 | 5.45 | 5.29 | 6.33 | 5.06 | 5.01 | 5.45 | 4.21 | 4.58 | 5.75 | 5.42 | 4.85 | 6.04 | 5.69 | 5.05 | 5.28 | 5.22 | 5.33 | 5.89 | 5.94 | 5.48 | 254.86 | 5.0939 | 6.81 |  | 17718 |  | 37448 |  | 65088 |  | 134606 |  | 17.718 |  | 37.448 |  | 65.088 |  | 134.606 |  | 254.86 | 0 | -1.11e-14% |  | 52 | 409 | 107.5 |  | 70.4
2025-04-16 | 2026 | 2025 | 2025-04-01 | 30 | 11848 | 9914 | 9336 | 7400 | 10516 | 7636 | 9334 | 3618 | 2236 | 3346 | 3888 | 4528 | 4960 | 4768 | 4528 | 5788 | 7052 | 9612 | 5256 | 4855 | 7872 | 8956 | 5040 | 5504 | 6236 | 5984 | 6604 | 4808 | 7580 | 5616 | 6358 | 4282 | 9732 | 11024 | 5388 | 7504 | 7832 | 7608 | 8672 | 7524 | 6680 | 8652 | 9644 | 6100 | 5.91 | 5.82 | 5.71 | 5.53 | 5.67 | 5.4 | 5.83 | 4.57 | 4.07 | 4.74 | 4.58 | 4.76 | 4.92 | 4.83 | 4.88 | 5.08 | 5.39 | 5.8 | 4.95 | 4.58 | 5.73 | 5.77 | 4.72 | 5.37 | 5.44 | 5.37 | 4.63 | 4.61 | 5.48 | 4.96 | 4.98 | 4.56 | 6.18 | 6.05 | 4.81 | 5.9 | 5.76 | 5.17 | 5.7 | 4.96 | 4.99 | 5.56 | 6.05 | 5.66 | 301.619 | 5.2598 | 6.18 |  | 45340 |  | 75801 |  | 74806 |  | 105672 |  | 45.34 |  | 75.801 |  | 74.806 |  | 105.672 |  | 301.619 | 0 | 0% |  | 54 | 1534 | 142.22 |  | 70.4
2025-04-17 | 2026 | 2025 | 2025-04-01 | 30 | 15284 | 11874 | 11896 | 8462 | 12948 | 13064 | 13038 | 4766 | 3500 | 4270 | 4484 | 4816 | 4888 | 5088 | 4234 | 5196 | 5596 | 13036 | 5816 | 4839 | 9548 | 10992 | 7196 | 7096 | 8764 | 7728 | 9738 | 5820 | 8528 | 8864 | 5484 | 5638 | 13948 | 17140 | 6798 | 14928 | 15268 | 14804 | 15024 | 6020 | 9376 | 12416 | 13312 | 15068 | 7.05 | 6.47 | 6.5 | 6.17 | 7 | 7.22 | 6.94 | 5.27 | 5.03 | 5.58 | 5.23 | 5.25 | 5.46 | 5.51 | 5.38 | 5.6 | 5.45 | 6.95 | 5.57 | 5.14 | 6.47 | 6.65 | 5.68 | 6.06 | 6.52 | 6.28 | 5.72 | 5.2 | 6.18 | 6.07 | 5.28 | 5.62 | 7.63 | 7.65 | 5.6 | 8.07 | 7.7 | 7.02 | 7.41 | 5.01 | 6.14 | 6.75 | 7.58 | 7.54 | 406.593 | 6.2409 | 8.07 |  | 57508 |  | 80581 |  | 122762 |  | 145742 |  | 57.508 |  | 80.581 |  | 122.762 |  | 145.742 |  | 406.593 | 0 | -1.11e-14% |  | 95 | 6832 | 392.95 |  | 70.4
2025-04-18 | 2026 | 2025 | 2025-04-01 | 30 | 15976 | 12770 | 12612 | 10010 | 11112 | 7176 | 14158 | 4776 | 3140 | 3936 | 4360 | 4548 | 4646 | 4580 | 4064 | 5096 | 5804 | 14696 | 5658 | 5017 | 11860 | 12088 | 7464 | 7344 | 8116 | 6556 | 8210 | 4848 | 8776 | 7210 | 6166 | 3616 | 9868 | 11124 | 6944 | 7432 | 9120 | 8864 | 9816 | 6288 | 8292 | 10952 | 15328 | 13316 | 6.84 | 6.52 | 6.52 | 6.15 | 6.17 | 5.58 | 6.93 | 5.05 | 4.6 | 5.11 | 4.86 | 4.88 | 4.96 | 4.94 | 4.94 | 5.09 | 5.2 | 6.94 | 5.16 | 4.81 | 6.54 | 6.51 | 5.42 | 5.84 | 6.02 | 5.61 | 5.44 | 4.81 | 5.96 | 5.52 | 5.02 | 4.55 | 6.4 | 6.15 | 5.25 | 6.46 | 6.17 | 5.57 | 6.12 | 4.91 | 5.65 | 6.16 | 7.18 | 6.85 | 363.733 | 5.7127 | 7.18 |  | 54886 |  | 86063 |  | 78128 |  | 144656 |  | 54.886 |  | 86.063 |  | 78.128 |  | 144.656 |  | 363.733 | 0 | 0% |  | 90 | 1677 | 354.48 |  | 70.4
2025-04-19 | 2026 | 2025 | 2025-04-01 | 30 | 13680 | 13158 | 13488 | 8300 | 10264 | 7384 | 10792 | 3822 | 2828 | 3448 | 3536 | 3702 | 3660 | 3876 | 3660 | 4466 | 4928 | 12576 | 4910 | 4344 | 9272 | 10664 | 5864 | 6008 | 6416 | 5564 | 11814 | 4048 | 7996 | 5792 | 5648 | 4340 | 9520 | 8880 | 5436 | 8876 | 5292 | 8108 | 8848 | 4104 | 6444 | 8614 | 11768 | 10300 | 6.71 | 6.79 | 7.01 | 5.94 | 6.38 | 6.03 | 6.49 | 4.85 | 4.65 | 5.16 | 4.78 | 4.81 | 4.88 | 4.95 | 4.99 | 5.26 | 5.18 | 6.83 | 5.23 | 4.9 | 6.23 | 6.42 | 5.22 | 5.66 | 5.81 | 5.58 | 6.52 | 4.7 | 6 | 5.39 | 5.18 | 5.29 | 6.63 | 5.98 | 4.95 | 6.56 | 6.19 | 5.74 | 6.28 | 4.51 | 5.5 | 5.98 | 6.74 | 6.59 | 316.438 | 5.7152 | 7.01 |  | 44848 |  | 73500 |  | 71512 |  | 126578 |  | 44.848 |  | 73.5 |  | 71.512 |  | 126.578 |  | 316.438 | 0 | 0% |  | 96 | 2198 | 301.5 |  | 70.4
2025-04-20 | 2026 | 2025 | 2025-04-01 | 30 | 14444 | 12916 | 12512 | 6832 | 7132 | 5584 | 12548 | 3418 | 2158 | 2478 | 2616 | 2986 | 2762 | 2916 | 2752 | 3098 | 3614 | 12772 | 3732 | 3553 | 9992 | 11776 | 5596 | 5596 | 6704 | 5404 | 10238 | 5266 | 6368 | 7618 | 4176 | 3340 | 6752 | 7816 | 5444 | 9800 | 7772 | 7272 | 7304 | 6668 | 7058 | 11286 | 13840 | 10576 | 6.32 | 6.31 | 6.23 | 5.04 | 4.93 | 4.91 | 6.3 | 4.52 | 4.13 | 4.42 | 4.13 | 4.3 | 4.2 | 4.16 | 4.19 | 4.17 | 4.49 | 6.27 | 4.4 | 4.18 | 5.93 | 6.19 | 4.84 | 5.3 | 5.5 | 5.16 | 5.58 | 4.71 | 5.07 | 5.41 | 4.21 | 4.28 | 5.42 | 5.2 | 4.76 | 6.22 | 5.65 | 5 | 5.26 | 4.57 | 5.01 | 5.95 | 6.58 | 6.03 | 304.485 | 5.1234 | 6.58 |  | 39718 |  | 64253 |  | 62772 |  | 137742 |  | 39.718 |  | 64.253 |  | 62.772 |  | 137.742 |  | 304.485 | 0 | 0% |  | 96 | 8829.63 | 293.29 |  | 70.4
2025-04-21 | 2026 | 2025 | 2025-04-01 | 30 | 7024 | 7886 | 8292 | 4064 | 3800 | 3248 | 6370 | 2004 | 1064 | 1256 | 1392 | 1772 | 1664 | 1800 | 1636 | 1796 | 1942 | 7492 | 2364 | 2073 | 6348 | 7508 | 3160 | 3128 | 3956 | 3272 | 7778 | 5382 | 3704 | 6804 | 2336 | 2038 | 3604 | 4900 | 4026 | 6560 | 4824 | 4476 | 4364 | 5864 | 5564 | 8416 | 7520 | 6224 | 4.9 | 5.48 | 5.52 | 4.23 | 4.18 | 4.42 | 5.14 | 3.96 | 3.54 | 3.9 | 3.6 | 3.89 | 3.72 | 3.68 | 3.67 | 3.66 | 3.84 | 5.33 | 3.93 | 3.61 | 5.22 | 5.27 | 4.22 | 4.69 | 4.82 | 4.56 | 5.08 | 4.65 | 4.16 | 5.18 | 3.47 | 3.79 | 4.67 | 4.64 | 4.33 | 5.55 | 5.1 | 4.44 | 4.75 | 4.36 | 4.54 | 5.43 | 5.48 | 5.3 | 190.695 | 4.4977 | 5.55 |  | 22668 |  | 39597 |  | 37814 |  | 90616 |  | 22.668 |  | 39.597 |  | 37.814 |  | 90.616 |  | 190.695 | 0 | 0% |  | 96 | 4696.13 | 187.51 |  | 70.4
2025-04-22 | 2026 | 2025 | 2025-04-01 | 30 | 3564 | 3242 | 2616 | 3462 | 2120 | 2144 | 3370 | 2470 | 1926 | 1778 | 3022 | 3280 | 3238 | 2876 | 2724 | 2960 | 3342 | 3552 | 3516 | 3202 | 4032 | 3948 | 3136 | 3496 | 3852 | 3564 | 2130 | 908 | 3192 | 1262 | 3684 | 1490 | 2092 | 1932 | 3240 | 3292 | 2560 | 1884 | 2156 | 1288 | 1178 | 1676 | 3784 | 3280 | 4.56 | 4.74 | 4.26 | 4.2 | 3.84 | 4.33 | 4.72 | 4.03 | 3.9 | 4.36 | 4.26 | 4.44 | 4.36 | 4.16 | 4.23 | 4.16 | 4.35 | 4.58 | 4.41 | 4.06 | 4.76 | 4.5 | 4.14 | 4.81 | 4.75 | 4.62 | 3.55 | 3.18 | 4.11 | 3.69 | 4.06 | 3.73 | 4.4 | 3.95 | 4.14 | 5.27 | 4.92 | 3.85 | 4.27 | 3.2 | 3.35 | 3.93 | 5.27 | 4.89 | 121.46 | 4.2566 | 5.27 |  | 29762 |  | 40178 |  | 19670 |  | 31850 |  | 29.762 |  | 40.178 |  | 19.67 |  | 31.85 |  | 121.46 | 0 | 2.22e-14% |  | 68 | 480 | 80.64 |  | 70.4
2025-04-23 | 2026 | 2025 | 2025-04-01 | 30 | 7452 | 5908 | 5648 | 5262 | 5500 | 4176 | 6712 | 994 | 1904 | 2586 | 3026 | 3416 | 3490 | 3348 | 3192 | 3524 | 3978 | 6956 | 3580 | 3241 | 6220 | 5972 | 1584 | 1536 | 1844 | 1308 | 4084 | 2696 | 4200 | 3742 | 3810 | 2596 | 5180 | 6252 | 4488 | 6128 | 6048 | 1312 | 5680 | 3648 | 3764 | 4762 | 7880 | 6892 | 5.2 | 5.09 | 5.11 | 4.88 | 4.64 | 4.77 | 5.37 | 3.89 | 3.8 | 4.35 | 4.19 | 4.4 | 4.33 | 4.3 | 4.34 | 4.28 | 4.51 | 5.36 | 4.37 | 4.02 | 5.36 | 5.16 | 3.96 | 4.34 | 4.56 | 4.27 | 4.22 | 3.85 | 4.6 | 4.5 | 4.02 | 3.96 | 5.2 | 5.03 | 4.52 | 5.65 | 5.41 | 4.71 | 5.06 | 4.01 | 4.26 | 4.73 | 5.79 | 5.58 | 185.519 | 4.6352 | 5.79 |  | 21688 |  | 50815 |  | 42872 |  | 70144 |  | 21.688 |  | 50.815 |  | 42.872 |  | 70.144 |  | 185.519 | 0 | 0% |  | 96 | 2995.5 | 170 |  | 70.4
2025-04-24 | 2026 | 2025 | 2025-04-01 | 30 | 5176 | 4024 | 3460 | 3884 | 5396 | 4756 | 4432 | 2468 | 720 | 710 | 780 | 852 | 894 | 2644 | 2464 | 2842 | 3594 | 4136 | 3436 | 3144 | 4168 | 3564 | 3216 | 3620 | 4344 | 3904 | 2804 | 1252 | 3132 | 1966 | 3540 | 2584 | 4984 | 6472 | 3216 | 5352 | 5860 | 3344 | 5456 | 1876 | 2046 | 2598 | 5744 | 5948 | 4.77 | 4.63 | 4.45 | 4.82 | 5.19 | 5.26 | 4.92 | 4.33 | 3.87 | 4.17 | 3.84 | 4.04 | 4 | 4.35 | 4.36 | 4.49 | 4.75 | 4.78 | 4.67 | 4.36 | 5.12 | 4.65 | 4.35 | 4.96 | 5.12 | 5 | 3.8 | 3.29 | 4.54 | 3.93 | 4.37 | 4.28 | 5.42 | 5.37 | 4.31 | 5.58 | 5.65 | 5.01 | 5.64 | 3.62 | 3.77 | 4.23 | 5.39 | 5.55 | 150.802 | 4.6136 | 5.65 |  | 21508 |  | 39628 |  | 44204 |  | 45462 |  | 21.508 |  | 39.628 |  | 44.204 |  | 45.462 |  | 150.802 | 0 | 2.22e-14% |  | 54 | 0 | 135 |  | 70.4
2025-04-25 | 2026 | 2025 | 2025-04-01 | 30 | 6648 | 4724 | 4068 | 5136 | 5292 | 3564 | 5910 | 2316 | 1188 | 1320 | 1536 | 1712 | 2030 | 2300 | 2200 | 2684 | 3294 | 6260 | 3364 | 2969 | 5980 | 6040 | 3576 | 3608 | 4272 | 3968 | 3424 | 1296 | 3976 | 2598 | 3710 | 1280 | 4612 | 5452 | 4040 | 5648 | 5228 | 4772 | 6416 | 1788 | 2118 | 3224 | 7256 | 7388 | 4.99 | 4.83 | 4.67 | 4.85 | 4.83 | 4.58 | 5.14 | 4.13 | 3.63 | 3.92 | 3.73 | 3.88 | 3.99 | 4.05 | 4.15 | 4.18 | 4.41 | 5.24 | 4.44 | 4.04 | 5.33 | 5.19 | 4.33 | 4.81 | 5 | 5.03 | 4.12 | 3.25 | 4.58 | 4.16 | 4.11 | 3.53 | 5.06 | 5.33 | 4.5 | 5.56 | 5.37 | 4.87 | 5.37 | 3.28 | 3.63 | 4.34 | 5.66 | 5.76 | 170.185 | 4.542 | 5.76 |  | 25526 |  | 45693 |  | 42264 |  | 56702 |  | 25.526 |  | 45.693 |  | 42.264 |  | 56.702 |  | 170.185 | 0 | 0% |  | 40 | 435.62 | 176.57 |  | 70.4
2025-04-26 | 2026 | 2025 | 2025-04-01 | 30 | 5692 | 4588 | 4000 | 4256 | 4616 | 1684 | 3182 | 2448 | 2012 | 2256 | 2516 | 2744 | 2988 | 824 | 882 | 954 | 900 | 5020 | 1124 | 897 | 4176 | 3892 | 3104 | 3336 | 3776 | 3280 | 4152 | 2010 | 3764 | 3298 | 746 | 2972 | 4552 | 5872 | 3396 | 4964 | 5152 | 4700 | 5328 | 1756 | 2548 | 3328 | 5704 | 5308 | 4.65 | 4.63 | 4.42 | 4.49 | 4.66 | 4.54 | 4.11 | 4.1 | 4.05 | 4.38 | 4.12 | 4.3 | 4.33 | 3.63 | 3.76 | 3.83 | 3.83 | 4.76 | 3.91 | 3.72 | 4.72 | 4.4 | 4.11 | 4.69 | 4.74 | 4.59 | 4.17 | 3.41 | 4.36 | 4.1 | 3.19 | 4.37 | 5.06 | 5.05 | 4.19 | 5.01 | 5.12 | 4.54 | 5.09 | 3.12 | 3.75 | 4.13 | 4.99 | 5.07 | 144.697 | 4.3225 | 5.12 |  | 28460 |  | 25811 |  | 39840 |  | 50586 |  | 28.46 |  | 25.811 |  | 39.84 |  | 50.586 |  | 144.697 | 0 | 0% |  | 96 | 1141.62 | 147.15 |  | 70.4
2025-04-27 | 2026 | 2025 | 2025-04-01 | 30 | 3824 | 2852 | 2860 | 2566 | 4008 | 2728 | 2960 | 1484 | 1076 | 1476 | 1724 | 2000 | 2148 | 1974 | 1918 | 2004 | 2308 | 3400 | 2150 | 2006 | 2892 | 2720 | 2244 | 2456 | 2752 | 2476 | 2416 | 1570 | 2600 | 2098 | 2384 | 1632 | 2252 | 4356 | 2390 | 3424 | 3552 | 3536 | 3944 | 1984 | 2172 | 2656 | 3792 | 3840 | 3.8 | 4.04 | 3.87 | 3.95 | 4.33 | 4.19 | 3.96 | 3.61 | 3.32 | 3.71 | 3.57 | 3.78 | 3.76 | 3.68 | 3.84 | 3.7 | 3.97 | 4.13 | 3.86 | 3.62 | 4.42 | 4.17 | 3.81 | 4.41 | 4.33 | 4.22 | 3.43 | 3.37 | 4.07 | 3.83 | 3.53 | 3.44 | 4.54 | 4.43 | 3.85 | 4.48 | 4.59 | 4.12 | 4.57 | 3.39 | 3.64 | 4.02 | 4.3 | 4.52 | 113.604 | 3.9584 | 4.59 |  | 19836 |  | 27912 |  | 29432 |  | 36424 |  | 19.836 |  | 27.912 |  | 29.432 |  | 36.424 |  | 113.604 | 0 | -1.11e-14% |  | 96 | 12 | 112.74 |  | 70.4
2025-04-28 | 2026 | 2025 | 2025-04-01 | 30 | 5012 | 3940 | 3304 | 3790 | 2020 | 3148 | 4404 | 1704 | 1252 | 1540 | 1584 | 1776 | 1728 | 1878 | 1862 | 2262 | 2504 | 5480 | 2750 | 2280 | 3716 | 3836 | 2540 | 2608 | 2948 | 2620 | 2988 | 1360 | 3320 | 2360 | 2912 | 1594 | 3948 | 5376 | 2382 | 4448 | 4116 | 4132 | 4752 | 1450 | 1628 | 2396 | 4856 | 5208 | 4.48 | 4.51 | 4.21 | 4.39 | 4.28 | 4.38 | 4.66 | 3.74 | 3.56 | 3.85 | 3.6 | 3.76 | 3.66 | 3.75 | 3.85 | 3.97 | 4.12 | 4.8 | 4.14 | 3.83 | 4.65 | 4.45 | 3.88 | 4.42 | 4.3 | 4.19 | 3.74 | 3.13 | 4.31 | 3.9 | 3.87 | 3.54 | 4.76 | 4.7 | 3.73 | 4.93 | 4.87 | 4.39 | 4.82 | 3.12 | 3.41 | 3.93 | 4.96 | 5.13 | 131.712 | 4.1516 | 5.13 |  | 20300 |  | 33492 |  | 33534 |  | 44386 |  | 20.3 |  | 33.492 |  | 33.534 |  | 44.386 |  | 131.712 | 0 | 0% |  | 96 | 88.62 | 131.18 |  | 70.4
2025-04-29 | 2026 | 2025 | 2025-04-01 | 30 | 7672 | 6560 | 5388 | 5362 | 6732 | 5172 | 6084 | 2736 | 2032 | 2700 | 2960 | 3348 | 3376 | 3416 | 3266 | 3874 | 4404 | 8060 | 4280 | 3542 | 5192 | 5880 | 4024 | 4624 | 5232 | 4500 | 3488 | 1818 | 4840 | 2784 | 4220 | 1238 | 6408 | 7940 | 3714 | 6600 | 6332 | 6240 | 7216 | 2018 | 2456 | 3264 | 6996 | 6920 | 5.26 | 5.18 | 4.9 | 5.1 | 5.31 | 5.2 | 5.18 | 4.35 | 4.16 | 4.67 | 4.43 | 4.6 | 4.7 | 4.68 | 4.76 | 4.9 | 4.96 | 5.57 | 4.88 | 4.45 | 5.25 | 5.21 | 4.54 | 5.2 | 5.38 | 5.19 | 3.99 | 3.48 | 5.05 | 4.13 | 4.45 | 3.88 | 5.73 | 5.61 | 4.39 | 5.78 | 5.65 | 5.13 | 5.68 | 3.67 | 3.87 | 4.36 | 5.56 | 5.6 | 204.908 | 4.8641 | 5.78 |  | 35532 |  | 51990 |  | 53878 |  | 63508 |  | 35.532 |  | 51.99 |  | 53.878 |  | 63.508 |  | 204.908 | 0 | 0% |  | 96 | 691.5 | 203.66 |  | 70.4
2025-04-30 | 2026 | 2025 | 2025-04-01 | 30 | 13028 | 10924 | 10548 | 8370 | 10156 | 7608 | 10324 | 3228 | 2502 | 3068 | 3256 | 3080 | 3508 | 3896 | 3744 | 4368 | 4804 | 11728 | 4580 | 3627 | 8504 | 9688 | 5688 | 6040 | 6752 | 5712 | 8652 | 4224 | 7912 | 5660 | 5072 | 3712 | 9692 | 10188 | 5342 | 8264 | 7652 | 8092 | 9060 | 3480 | 6956 | 8868 | 12284 | 10192 | 6.74 | 6.33 | 6.44 | 6.16 | 6.45 | 6.08 | 6.5 | 4.66 | 4.54 | 5.03 | 4.68 | 4.66 | 4.86 | 5 | 5.05 | 5.22 | 5.14 | 6.75 | 5.03 | 4.61 | 6.19 | 6.35 | 5.25 | 5.72 | 6.02 | 5.73 | 5.7 | 4.74 | 6.08 | 5.4 | 4.98 | 5.03 | 6.72 | 6.3 | 5.1 | 6.48 | 6.23 | 5.75 | 6.34 | 4.16 | 5.6 | 6.1 | 7.02 | 6.67 | 304.033 | 5.6725 | 7.02 |  | 42834 |  | 69907 |  | 74424 |  | 116868 |  | 42.834 |  | 69.907 |  | 74.424 |  | 116.868 |  | 304.033 | 0 | 0% |  | 96 | 1791.5 | 298.91 |  | 70.4
2025-05-01 | 2026 | 2025 | 2025-05-01 | 31 | 13832 | 13376 | 14452 | 9372 | 9904 | 7568 | 12124 | 3156 | 1902 | 2176 | 2252 | 2558 | 2572 | 2838 | 2744 | 3324 | 4656 | 12544 | 3830 | 3599 | 11508 | 12828 | 5552 | 5348 | 6376 | 4880 | 12474 | 5426 | 8352 | 7698 | 4700 | 3292 | 9248 | 10860 | 5350 | 11476 | 8976 | 8592 | 8848 | 8212 | 9652 | 12636 | 14936 | 10844 | 6.46 | 6.62 | 7.03 | 5.8 | 6.08 | 5.74 | 6.56 | 4.44 | 4.09 | 4.42 | 4.06 | 4.25 | 4.32 | 4.41 | 4.53 | 4.67 | 5 | 6.63 | 4.77 | 4.56 | 6.37 | 6.59 | 4.89 | 5.36 | 5.52 | 5.15 | 6.49 | 4.89 | 5.66 | 5.57 | 4.8 | 4.55 | 6.38 | 6.38 | 4.87 | 6.88 | 6.25 | 5.8 | 6.01 | 5.23 | 5.84 | 6.46 | 7.19 | 6.48 | 336.843 | 5.5466 | 7.19 |  | 36772 |  | 73101 |  | 78764 |  | 148206 |  | 36.772 |  | 73.101 |  | 78.764 |  | 148.206 |  | 336.843 | 0 | -2.22e-14% |  | 96 | 2155.12 | 326.23 |  | 70.4
2025-05-02 | 2026 | 2025 | 2025-05-01 | 31 | 18020 | 17608 | 19048 | 8728 | 13132 | 14480 | 15656 | 5320 | 3614 | 3892 | 4036 | 4582 | 4672 | 5434 | 5448 | 7740 | 8184 | 15788 | 6674 | 5142 | 10776 | 14108 | 7508 | 7524 | 8936 | 8368 | 18474 | 10368 | 9720 | 13502 | 6864 | 7212 | 14560 | 16928 | 7470 | 18648 | 17304 | 15660 | 15340 | 13326 | 14184 | 17244 | 17032 | 14548 | 7.21 | 7.43 | 7.87 | 5.59 | 6.43 | 7.01 | 7.03 | 5.16 | 4.79 | 5.14 | 4.74 | 4.9 | 4.96 | 5.09 | 5.31 | 5.66 | 5.72 | 7.01 | 5.43 | 4.85 | 6.22 | 6.81 | 5.36 | 5.89 | 6.1 | 5.96 | 7.53 | 5.83 | 5.94 | 6.62 | 5.26 | 5.75 | 7.44 | 7.45 | 5.39 | 8.36 | 7.69 | 6.89 | 7.2 | 6.08 | 6.51 | 7.22 | 7.75 | 7.12 | 492.802 | 6.2659 | 8.36 |  | 58452 |  | 96288 |  | 133264 |  | 204798 |  | 58.452 |  | 96.288 |  | 133.264 |  | 204.798 |  | 492.802 | 0 | 0% |  | 96 | 24622.5 | 475.46 |  | 70.4
2025-05-03 | 2026 | 2025 | 2025-05-01 | 31 | 15716 | 17084 | 17356 | 11444 | 13600 | 13264 | 12008 | 5496 | 4982 | 5174 | 5164 | 5080 | 5140 | 5152 | 4996 | 5632 | 6528 | 16004 | 6904 | 6407 | 11140 | 13568 | 7740 | 7620 | 8616 | 7728 | 16908 | 11180 | 13656 | 13958 | 7934 | 10306 | 14164 | 14648 | 7180 | 18688 | 17564 | 14524 | 14560 | 8952 | 12608 | 13816 | 14776 | 12292 | 6.83 | 7.57 | 7.8 | 7.62 | 6.63 | 6.84 | 6.38 | 5.06 | 5.12 | 5.53 | 5.15 | 5.11 | 5.18 | 5.17 | 5.28 | 5.36 | 5.49 | 7.12 | 5.61 | 5.28 | 7.39 | 7.96 | 5.39 | 5.84 | 6.09 | 5.89 | 7.66 | 6.12 | 7.99 | 6.86 | 5.62 | 6.41 | 7.39 | 7.05 | 6.47 | 8.31 | 7.78 | 6.68 | 7 | 5.13 | 6.33 | 6.66 | 7.03 | 6.62 | 477.257 | 6.4045 | 8.31 |  | 62740 |  | 100541 |  | 131318 |  | 182658 |  | 62.74 |  | 100.541 |  | 131.318 |  | 182.658 |  | 477.257 | 0 | 2.22e-14% |  | 69 | 7746 | 347.9 |  | 70.4
2025-05-04 | 2026 | 2025 | 2025-05-01 | 31 | 14352 | 13288 | 11716 | 14860 | 17652 | 16288 | 12356 | 5124 | 4816 | 5494 | 5934 | 6692 | 5780 | 6400 | 5688 | 6860 | 7276 | 16256 | 7222 | 6157 | 12688 | 15212 | 8520 | 8840 | 9612 | 8216 | 13100 | 10590 | 15708 | 14436 | 8374 | 10680 | 17832 | 17348 | 8648 | 20544 | 19712 | 17128 | 17040 | 4310 | 7964 | 10622 | 15308 | 14852 | 7.01 | 6.95 | 6.79 | 7.52 | 8.02 | 7.98 | 6.93 | 5.4 | 5.47 | 5.9 | 5.65 | 5.74 | 5.69 | 5.83 | 5.75 | 6.07 | 5.92 | 7.69 | 5.93 | 5.45 | 7.08 | 7.49 | 6.08 | 6.52 | 6.85 | 6.51 | 6.95 | 6.53 | 7.69 | 7.46 | 6.04 | 6.92 | 8.58 | 7.81 | 5.94 | 9.13 | 8.64 | 7.62 | 7.93 | 4.58 | 5.77 | 6.53 | 7.55 | 7.59 | 497.495 | 6.7609 | 9.13 |  | 69028 |  | 115093 |  | 154224 |  | 159150 |  | 69.028 |  | 115.093 |  | 154.224 |  | 159.15 |  | 497.495 | 0 | 0% |  | 96 | 3622.38 | 493.44 |  | 70.4
2025-05-05 | 2026 | 2025 | 2025-05-01 | 31 | 17148 | 18204 | 18376 | 13192 | 12208 | 10636 | 11940 | 3746 | 4100 | 4964 | 5506 | 6066 | 5740 | 5586 | 4976 | 5796 | 7168 | 16136 | 6516 | 5584 | 12876 | 15252 | 7888 | 8260 | 9404 | 7964 | 17476 | 9450 | 14124 | 12326 | 7880 | 7194 | 11960 | 13552 | 8452 | 15548 | 14264 | 12328 | 12232 | 6472 | 10642 | 13534 | 15336 | 12316 | 7.25 | 7.68 | 7.82 | 6.87 | 6.48 | 6.49 | 6.58 | 5.05 | 5.11 | 5.51 | 5.27 | 5.34 | 5.35 | 5.28 | 5.29 | 5.41 | 5.63 | 7.35 | 5.48 | 5.11 | 6.86 | 7.24 | 5.62 | 6.1 | 6.49 | 6.2 | 7.41 | 6.09 | 7.01 | 6.77 | 5.58 | 5.74 | 6.98 | 6.78 | 5.7 | 7.96 | 7.4 | 6.45 | 6.7 | 5 | 6.33 | 6.93 | 7.43 | 6.87 | 460.318 | 6.318 | 7.96 |  | 63638 |  | 107402 |  | 109922 |  | 179356 |  | 63.638 |  | 107.402 |  | 109.922 |  | 179.356 |  | 460.318 | 0 | 0% |  | 96 | 16139.25 | 464.18 |  | 70.4
2025-05-06 | 2026 | 2025 | 2025-05-01 | 31 | 12724 | 11808 | 9732 | 10200 | 10908 | 10264 | 8096 | 4692 | 5048 | 6168 | 6272 | 6490 | 6116 | 6118 | 5680 | 6452 | 7052 | 11428 | 6218 | 5318 | 9312 | 10224 | 6756 | 7192 | 7668 | 6868 | 10360 | 7212 | 10568 | 9600 | 7276 | 7360 | 10860 | 11512 | 7456 | 13728 | 13516 | 11944 | 11936 | 4010 | 7984 | 9128 | 12324 | 10140 | 6.43 | 6.44 | 6.13 | 6.2 | 6.3 | 6.5 | 5.75 | 5.04 | 5.45 | 6.01 | 5.68 | 5.63 | 5.64 | 5.62 | 5.65 | 5.74 | 5.69 | 6.41 | 5.48 | 5.08 | 6.1 | 6.18 | 5.34 | 5.93 | 6 | 5.8 | 6.05 | 5.5 | 6.29 | 6.12 | 5.49 | 6.06 | 6.78 | 6.41 | 5.43 | 7.49 | 7.21 | 6.32 | 6.73 | 4.28 | 5.69 | 5.97 | 6.73 | 6.37 | 381.718 | 5.9805 | 7.49 |  | 63270 |  | 91874 |  | 102028 |  | 124546 |  | 63.27 |  | 91.874 |  | 102.028 |  | 124.546 |  | 381.718 | 0 | 0% |  | 96 | 9466.5 | 380.97 |  | 70.4
2025-05-07 | 2026 | 2025 | 2025-05-01 | 31 | 15556 | 11464 | 12536 | 11760 | 16608 | 14096 | 11340 | 7702 | 6558 | 9432 | 10676 | 11802 | 10824 | 9760 | 8576 | 10026 | 9694 | 12484 | 9680 | 7998 | 10784 | 11380 | 9504 | 10364 | 11568 | 10112 | 11248 | 9784 | 11776 | 12156 | 9952 | 10540 | 16516 | 16304 | 8504 | 18732 | 19164 | 16176 | 16784 | 8618 | 12436 | 12840 | 16692 | 14744 | 7.26 | 6.46 | 6.92 | 6.77 | 7.64 | 7.42 | 6.71 | 6.11 | 5.97 | 6.97 | 6.95 | 7 | 6.91 | 6.62 | 6.52 | 6.75 | 6.41 | 6.88 | 6.5 | 5.89 | 6.65 | 6.6 | 6.09 | 6.72 | 7.07 | 6.83 | 6.47 | 6.26 | 6.77 | 6.89 | 6.33 | 6.92 | 8.19 | 7.63 | 5.85 | 8.71 | 8.5 | 7.41 | 7.88 | 5.74 | 6.9 | 6.92 | 7.92 | 7.5 | 525.25 | 6.8957 | 8.71 |  | 98542 |  | 119890 |  | 144920 |  | 161898 |  | 98.542 |  | 119.89 |  | 144.92 |  | 161.898 |  | 525.25 | 0 | 0% |  | 96 | 19096.63 | 522.37 |  | 70.4
2025-05-08 | 2026 | 2025 | 2025-05-01 | 31 | 20072 | 16952 | 13692 | 16204 | 18348 | 19744 | 18256 | 11024 | 6920 | 7492 | 8164 | 12246 | 12604 | 12044 | 9286 | 11726 | 11166 | 14280 | 10852 | 9423 | 15124 | 13020 | 11684 | 7128 | 12112 | 10112 | 11248 | 11560 | 15624 | 13880 | 10212 | 13932 | 18252 | 15400 | 10154 | 23244 | 21828 | 14108 | 19680 | 12836 | 14862 | 16376 | 22900 | 21184 | 8.08 | 7.52 | 7.01 | 7.75 | 7.82 | 8.45 | 8.06 | 6.77 | 5.83 | 6.26 | 6.05 | 7 | 7.07 | 6.9 | 6.66 | 6.9 | 6.46 | 7.14 | 6.76 | 6.07 | 7.55 | 6.87 | 6.31 | 6.33 | 6.97 | 6.46 | 6.24 | 6.7 | 7.74 | 7.36 | 6.12 | 7.52 | 8.44 | 7.22 | 6.19 | 9.55 | 8.93 | 6.79 | 8.34 | 6.91 | 7.45 | 7.66 | 9.09 | 8.67 | 616.955 | 7.2266 | 9.55 |  | 99486 |  | 144835 |  | 164536 |  | 208098 |  | 99.486 |  | 144.835 |  | 164.536 |  | 208.098 |  | 616.955 | 0 | 0% |  | 96 | 39098.5 | 592.7 |  | 70.4
2025-05-09 | 2026 | 2025 | 2025-05-01 | 31 | 8252 | 9048 | 6076 | 7410 | 4716 | 6952 | 7816 | 4492 | 2574 | 1788 | 1888 | 3718 | 3184 | 2534 | 2700 | 3532 | 3372 | 6588 | 5014 | 3393 | 7048 | 6200 | 1912 | 1372 | 2588 | 3776 | 4452 | 3106 | 7176 | 3766 | 3396 | 4548 | 5480 | 3768 | 4938 | 7624 | 6828 | 3472 | 6048 | 3112 | 3604 | 4584 | 8444 | 7596 | 5.73 | 5.97 | 5.23 | 5.83 | 4.8 | 5.8 | 5.92 | 4.98 | 4.36 | 4.25 | 3.94 | 4.69 | 4.57 | 4.49 | 4.54 | 4.83 | 4.47 | 5.38 | 5.16 | 4.42 | 5.88 | 5.36 | 4.31 | 4.59 | 4.83 | 4.73 | 4.32 | 4.28 | 5.89 | 4.69 | 4.14 | 5.24 | 5.4 | 4.61 | 4.87 | 6.73 | 6.38 | 4.47 | 5.84 | 4.2 | 4.49 | 4.97 | 6.13 | 5.9 | 209.885 | 5.0366 | 6.73 |  | 27292 |  | 56713 |  | 49436 |  | 76444 |  | 27.292 |  | 56.713 |  | 49.436 |  | 76.444 |  | 209.885 | 0 | 0% |  | 96 | 7684.87 | 202.61 |  | 70.4
2025-05-10 | 2026 | 2025 | 2025-05-01 | 31 | 5612 | 7000 | 5152 | 5546 | 3928 | 4968 | 5450 | 3156 | 2116 | 1588 | 1944 | 2486 | 2352 | 512 | 2462 | 2840 | 3168 | 5376 | 3910 | 3110 | 5148 | 1232 | 2832 | 3112 | 1792 | 2432 | 4132 | 1742 | 5540 | 1876 | 3020 | 3134 | 3524 | 4048 | 3402 | 5968 | 5200 | 3048 | 4728 | 1762 | 2132 | 2440 | 5904 | 5324 | 5.38 | 6.13 | 5.09 | 5.12 | 4.05 | 4.87 | 5.71 | 4.31 | 3.94 | 3.9 | 3.66 | 4.11 | 3.89 | 3.71 | 4.05 | 4.2 | 4.21 | 5.5 | 4.47 | 4.03 | 5.15 | 4.46 | 3.98 | 4.47 | 3.91 | 3.93 | 4.36 | 3.54 | 5.22 | 3.86 | 3.7 | 4.28 | 4.48 | 4.1 | 4.06 | 5.43 | 5.18 | 3.84 | 4.73 | 3.39 | 3.66 | 4.02 | 5.25 | 5.87 | 156.148 | 4.4364 | 6.13 |  | 23810 |  | 39890 |  | 38546 |  | 53902 |  | 23.81 |  | 39.89 |  | 38.546 |  | 53.902 |  | 156.148 | 0 | 2.22e-14% |  | 73 | 1948.87 | 141.12 |  | 70.4
2025-05-11 | 2026 | 2025 | 2025-05-01 | 31 | 4208 | 4344 | 2472 | 3128 | 2596 | 3528 | 3910 | 1794 | 1010 | 1012 | 1200 | 2002 | 1834 | 1918 | 1688 | 1948 | 1936 | 2804 | 2444 | 1849 | 2900 | 1724 | 1860 | 1836 | 2020 | 1716 | 2058 | 1940 | 3188 | 2542 | 1960 | 2352 | 3020 | 2640 | 1796 | 4616 | 4148 | 2524 | 3596 | 218 | 2428 | 756 | 4552 | 4080 | 4.25 | 4.56 | 3.81 | 4.14 | 3.73 | 4.56 | 4.51 | 3.64 | 3.39 | 3.6 | 3.4 | 3.86 | 3.61 | 3.66 | 3.67 | 3.75 | 3.79 | 4.01 | 3.85 | 3.5 | 4.29 | 3.78 | 3.43 | 3.97 | 3.73 | 3.44 | 3.18 | 3.57 | 4.34 | 3.98 | 3.34 | 4.03 | 4.37 | 3.67 | 3.43 | 4.99 | 4.83 | 3.62 | 4.42 | 3.18 | 3.73 | 3.82 | 4.74 | 4.74 | 108.095 | 3.907 | 4.99 |  | 16284 |  | 26479 |  | 29020 |  | 36312 |  | 16.284 |  | 26.479 |  | 29.02 |  | 36.312 |  | 108.095 | 0 | 0% |  | 92 | 455.87 | 105.19 |  | 70.4
2025-05-12 | 2026 | 2025 | 2025-05-01 | 31 | 4132 | 1424 | 3340 | 2600 | 2352 | 2704 | 3216 | 1290 | 838 | 1152 | 1148 | 1378 | 1378 | 1564 | 1500 | 1840 | 2200 | 3144 | 2080 | 2027 | 2524 | 2276 | 1452 | 1636 | 1836 | 1756 | 2846 | 776 | 2616 | 1516 | 2392 | 1706 | 496 | 2188 | 1738 | 3236 | 2996 | 1940 | 3192 | 984 | 1688 | 724 | 3940 | 4028 | 3.86 | 3.93 | 3.77 | 3.68 | 3.4 | 3.8 | 3.88 | 2.94 | 2.79 | 3.15 | 3.03 | 3.29 | 3.05 | 3.18 | 3.2 | 3.32 | 3.66 | 3.76 | 3.32 | 3.22 | 3.79 | 3.56 | 2.88 | 3.72 | 3.37 | 3.32 | 3.19 | 3.02 | 3.83 | 3.48 | 3.15 | 3.36 | 3.66 | 3.6 | 3.12 | 4.28 | 4.25 | 3.46 | 4.1 | 3.08 | 3.55 | 3.47 | 4.8 | 4.36 | 91.789 | 3.5143 | 4.8 |  | 13864 |  | 25357 |  | 20810 |  | 31758 |  | 13.864 |  | 25.357 |  | 20.81 |  | 31.758 |  | 91.789 | 0 | 0% |  | 96 | 7255.25 | 124.03 |  | 70.4
2025-05-13 | 2026 | 2025 | 2025-05-01 | 31 | 1696 | 1248 | 1436 | 3048 | 1980 | 1336 | 1092 | 1828 | 1360 | 2200 | 2632 | 2924 | 2690 | 2362 | 2092 | 2460 | 2708 | 1504 | 2418 | 2173 | 2976 | 2896 | 2448 | 2668 | 2724 | 2400 | 1260 | 880 | 2880 | 1062 | 2592 | 824 | 0 | 1752 | 554 | 1908 | 1648 | 1812 | 1864 | 1086 | 1324 | 1120 | 1728 | 1512 | 2.88 | 3.35 | 3.1 | 3.67 | 3.64 | 3.47 | 3.05 | 3.14 | 3.1 | 3.65 | 3.55 | 3.81 | 3.64 | 3.52 | 3.61 | 3.65 | 3.85 | 3.23 | 3.62 | 3.57 | 3.85 | 3.67 | 3.24 | 4.01 | 3.66 | 3.48 | 2.75 | 2.75 | 3.8 | 3.03 | 3.52 | 2.89 | 3.71 | 3.31 | 3.18 | 3.38 | 3.61 | 3.21 | 3.6 | 2.88 | 3.05 | 3.21 | 3.19 | 3.43 | 83.105 | 3.398 | 4.01 |  | 23874 |  | 29159 |  | 13124 |  | 16948 |  | 23.874 |  | 29.159 |  | 13.124 |  | 16.948 |  | 83.105 | 0 | -2.22e-14% |  | 69 | 0 | 35.5 |  | 70.4
2025-05-14 | 2026 | 2025 | 2025-05-01 | 31 | 3744 | 3488 | 3020 | 516 | 568 | 1648 | 2312 | 1476 | 1120 | 1276 | 1234 | 1440 | 1528 | 1532 | 1456 | 1696 | 1836 | 3576 | 2028 | 1838 | 3020 | 3168 | 2188 | 2112 | 2484 | 2260 | 3036 | 1606 | 3032 | 2858 | 1672 | 924 | 1140 | 3368 | 1106 | 3668 | 2912 | 2804 | 3104 | 1214 | 2032 | 2948 | 4096 | 3764 | 4.06 | 4.12 | 3.95 | 3.34 | 3.29 | 3.83 | 3.8 | 3.3 | 3.29 | 3.64 | 3.38 | 3.59 | 3.52 | 3.51 | 3.51 | 3.58 | 3.66 | 3.97 | 3.51 | 3.32 | 3.93 | 3.87 | 3.46 | 4.04 | 3.92 | 3.88 | 3.59 | 3.04 | 3.73 | 3.8 | 3.19 | 3.3 | 3.88 | 4.02 | 3.35 | 4.69 | 4.36 | 3.77 | 4.26 | 2.74 | 3.32 | 3.96 | 4.45 | 4.44 | 97.848 | 3.7082 | 4.69 |  | 17118 |  | 22900 |  | 20136 |  | 37694 |  | 17.118 |  | 22.9 |  | 20.136 |  | 37.694 |  | 97.848 | 0 | 0% |  | 96 | 0 | 107.19 |  | 70.4
2025-05-15 | 2026 | 2025 | 2025-05-01 | 31 | 3496 | 3012 | 2848 | 1124 | 1732 | 2348 | 2580 | 1212 | 680 | 754 | 910 | 1074 | 1058 | 1086 | 932 | 1198 | 1516 | 3500 | 1588 | 1499 | 3488 | 3676 | 2028 | 2132 | 2320 | 1868 | 2526 | 1338 | 3696 | 2508 | 1812 | 1216 | 2496 | 3928 | 2352 | 3500 | 3112 | 3064 | 3572 | 1104 | 1826 | 2620 | 3908 | 3816 | 4.51 | 4.67 | 4.45 | 3.83 | 4.19 | 4.6 | 4.37 | 3.24 | 2.95 | 3.22 | 3.04 | 3.23 | 2.99 | 3.04 | 3.12 | 3.16 | 3.51 | 5.1 | 3.35 | 3.24 | 4.39 | 4.33 | 3.5 | 4.08 | 3.94 | 3.72 | 4.11 | 3.64 | 4.36 | 4.58 | 3.19 | 3.6 | 4.86 | 4.93 | 3.65 | 5.3 | 5.19 | 4.43 | 5.07 | 3.18 | 3.99 | 4.43 | 5.26 | 5.43 | 98.053 | 4.022 | 5.43 |  | 14036 |  | 23967 |  | 24968 |  | 35082 |  | 14.036 |  | 23.967 |  | 24.968 |  | 35.082 |  | 98.053 | 0 | 0% |  | 71 | 2 | 91.28 |  | 70.4
2025-05-16 | 2026 | 2025 | 2025-05-01 | 31 | 2396 | 1696 | 1528 | 2138 | 2536 | 1856 | 1612 | 1172 | 716 | 974 | 1332 | 1582 | 1656 | 1336 | 1392 | 1594 | 1840 | 1844 | 1634 | 1279 | 2000 | 1872 | 1312 | 1412 | 1580 | 1472 | 1090 | 888 | 2020 | 1348 | 1728 | 1116 | 2228 | 2540 | 1224 | 2404 | 2436 | 2160 | 2588 | 1184 | 1522 | 1548 | 2596 | 2116 | 3.58 | 3.64 | 3.35 | 3.76 | 3.94 | 3.81 | 3.53 | 3.11 | 2.93 | 3.3 | 3.44 | 3.6 | 3.5 | 3.49 | 3.61 | 3.74 | 3.86 | 3.55 | 3.56 | 3.43 | 3.84 | 3.68 | 3.1 | 3.86 | 3.56 | 3.5 | 2.77 | 2.85 | 3.91 | 3.23 | 3.4 | 3.2 | 4.28 | 3.8 | 3.15 | 3.92 | 4.08 | 3.56 | 4.04 | 3.1 | 3.31 | 3.54 | 3.85 | 3.87 | 74.497 | 3.5484 | 4.28 |  | 13208 |  | 20057 |  | 19864 |  | 21368 |  | 13.208 |  | 20.057 |  | 19.864 |  | 21.368 |  | 74.497 | 0 | 0% |  | 44 | 0 | 5.64 |  | 70.4
2025-05-17 | 2026 | 2025 | 2025-05-01 | 31 | 6200 | 4356 | 3944 | 4634 | 5800 | 4880 | 4512 | 2636 | 1916 | 2364 | 2470 | 2664 | 2298 | 2564 | 1618 | 2870 | 3096 | 5188 | 3296 | 2663 | 4400 | 4152 | 3576 | 3580 | 3856 | 3200 | 4002 | 2168 | 4416 | 3526 | 3656 | 3488 | 5680 | 6552 | 2790 | 6528 | 6436 | 5672 | 6332 | 2316 | 3208 | 3712 | 6596 | 5796 | 5.2 | 4.71 | 4.57 | 5.15 | 5.31 | 5.35 | 5 | 4.38 | 4.28 | 4.73 | 4.31 | 4.4 | 4.28 | 4.46 | 4.37 | 4.65 | 4.6 | 5.17 | 4.56 | 4.2 | 5.21 | 4.9 | 4.53 | 4.93 | 4.97 | 4.75 | 4.38 | 4 | 5.22 | 4.73 | 4.51 | 4.83 | 5.69 | 5.44 | 4.11 | 6.14 | 5.92 | 5.16 | 5.67 | 3.82 | 4.33 | 4.74 | 5.77 | 5.61 | 175.607 | 4.8418 | 6.14 |  | 28560 |  | 40155 |  | 51368 |  | 55524 |  | 28.56 |  | 40.155 |  | 51.368 |  | 55.524 |  | 175.607 | 0 | 0% |  | 95 | 0 | 38.29 |  | 70.4
2025-05-18 | 2026 | 2025 | 2025-05-01 | 31 | 4628 | 4100 | 3848 | 3528 | 4424 | 4044 | 4378 | 1664 | 1364 | 1426 | 1436 | 1504 | 1530 | 1630 | 1608 | 1746 | 1932 | 4764 | 1880 | 1739 | 3204 | 3128 | 2504 | 2432 | 2616 | 2212 | 4434 | 3360 | 2084 | 3230 | 2146 | 2868 | 3360 | 4252 | 3612 | 4836 | 4672 | 4584 | 5108 | 2580 | 3268 | 2936 | 5068 | 5080 | 6.93 | 6.84 | 5.77 | 5.95 | 6.95 | 6.85 | 6.97 | 3.96 | 3.95 | 3.9 | 3.96 | 3.93 | 3.8 | 3.82 | 3.98 | 3.73 | 3.95 | 6.98 | 3.69 | 3.86 | 5.73 | 5.9 | 4.95 | 5.98 | 5.93 | 5.95 | 6.78 | 5.82 | 5.44 | 6.71 | 5.98 | 5.61 | 5.52 | 6.9 | 5.62 | 6.3 | 6.67 | 6.61 | 6.67 | 4.53 | 5.98 | 4.23 | 6.53 | 6.7 | 136.747 | 5.5184 | 6.98 |  | 18688 |  | 28237 |  | 38148 |  | 51674 |  | 18.688 |  | 28.237 |  | 38.148 |  | 51.674 |  | 136.747 | 0 | 0% |  | 86 | 0 | 65.28 |  | 70.4
2025-05-19 | 2026 | 2025 | 2025-05-01 | 31 | 3895 | 3718 | 3584 | 3310 | 3341 | 3703 | 2536 | 2236 | 2936 | 2282 | 2193 | 2824 | 2246 | 2112 | 2219 | 2025 | 2115 | 2258 | 2295 | 2355 | 2118 | 2123 | 2245 | 2456 | 2856 | 2456 | 2984 | 2569 | 3516 | 3025 | 2734 | 2854 | 2236 | 3136 | 2854 | 3456 | 2984 | 3135 | 3892 | 3168 | 3146 | 2980 | 3350 | 3416 | 5.56 | 5.74 | 5.26 | 5.2 | 4.84 | 4.83 | 4.72 | 4.83 | 4.9 | 4.86 | 4.76 | 5.44 | 4.86 | 4.96 | 4.73 | 4.66 | 4.85 | 4.98 | 4.91 | 4.66 | 4.76 | 4.9 | 4.84 | 5.31 | 5.75 | 5.62 | 4.55 | 4.18 | 5.11 | 4.69 | 4.06 | 4.73 | 4.9 | 4.95 | 4.14 | 5.27 | 4.92 | 4.85 | 5.27 | 5.2 | 4.35 | 4.33 | 5.27 | 5.89 | 123.872 | 4.9407 | 5.89 |  | 24730 |  | 29776 |  | 28737 |  | 40629 |  | 24.73 |  | 29.776 |  | 28.737 |  | 40.629 |  | 123.872 | 0 | -1.11e-14% |  | 96 | 0 | 77.28 |  | 70.4
2025-05-20 | 2026 | 2025 | 2025-05-01 | 31 | 3028 | 2600 | 2828 | 1354 | 3848 | 3504 | 2444 | 2270 | 1920 | 2288 | 2286 | 2420 | 2502 | 2560 | 2596 | 2996 | 2586 | 2420 | 3068 | 2951 | 1680 | 1324 | 2648 | 2896 | 2904 | 2920 | 2628 | 1052 | 944 | 1938 | 300 | 3148 | 3892 | 3820 | 2086 | 4392 | 3968 | 3260 | 3852 | 1852 | 1610 | 2356 | 3384 | 2648 | 4.45 | 4.38 | 4.04 | 4.29 | 4.51 | 4.3 | 4.55 | 4.15 | 4.15 | 4.84 | 4.57 | 4.81 | 4.5 | 4.8 | 4.71 | 4.67 | 4.6 | 4.07 | 4.94 | 4.85 | 4.51 | 4.34 | 4.46 | 5.06 | 5.1 | 5.35 | 3.81 | 3.32 | 3.68 | 3.99 | 4.12 | 4.13 | 4.82 | 4.3 | 4.57 | 5.38 | 4.91 | 4.26 | 4.57 | 3.62 | 3.65 | 4.32 | 4.83 | 4.56 | 113.971 | 4.4509 | 5.38 |  | 25054 |  | 24445 |  | 33684 |  | 30788 |  | 25.054 |  | 24.445 |  | 33.684 |  | 30.788 |  | 113.971 | 0 | -1.11e-14% |  | 69 | 0 | 79.88 |  | 70.4
2025-05-21 | 2026 | 2025 | 2025-05-01 | 31 | 4044 | 4228 | 4080 | 3650 | 4176 | 4856 | 3752 | 3302 | 1968 | 1974 | 2006 | 2636 | 2950 | 3196 | 2604 | 2596 | 3136 | 3060 | 4696 | 3501 | 3480 | 3360 | 4308 | 3540 | 3304 | 3260 | 3362 | 2004 | 3320 | 3466 | 3278 | 2888 | 4460 | 3184 | 3394 | 7604 | 6000 | 3668 | 3336 | 2592 | 3394 | 3912 | 5432 | 4024 | 4.35 | 4.72 | 4.62 | 4.52 | 4.69 | 5.13 | 4.64 | 4.49 | 4.49 | 4.03 | 4.3 | 3.88 | 4.06 | 3.86 | 4.47 | 4.38 | 4.29 | 4.39 | 4.32 | 4.84 | 4.5 | 4.57 | 4.42 | 4.52 | 4.69 | 4.48 | 4.51 | 4 | 3.64 | 4.43 | 4.36 | 4.18 | 4.31 | 5.15 | 4.29 | 4.21 | 6.25 | 5.54 | 4.46 | 4.63 | 3.88 | 4.25 | 4.62 | 5.16 | 156.981 | 4.4891 | 6.25 |  | 29248 |  | 40211 |  | 40172 |  | 47350 |  | 29.248 |  | 40.211 |  | 40.172 |  | 47.35 |  | 156.981 | 0 | 0% |  | 96 | 0 | 155.18 |  | 70.4
2025-05-22 | 2026 | 2025 | 2025-05-01 | 31 | 6036 | 5160 | 4416 | 3308 | 1224 | 3620 | 4346 | 5252 | 4544 | 3826 | 4124 | 3664 | 3658 | 3398 | 2648 | 2892 | 2992 | 4024 | 3546 | 2418 | 3804 | 3100 | 4864 | 4088 | 4736 | 5192 | 3130 | 1464 | 3088 | 2278 | 1890 | 3380 | 1900 | 4372 | 3124 | 8232 | 4428 | 4836 | 4556 | 1924 | 2400 | 2370 | 6704 | 3492 | 5.15 | 4.97 | 4.81 | 4.52 | 3.29 | 4.59 | 4.61 | 5.29 | 5.29 | 5.02 | 5.03 | 4.73 | 4.63 | 4.64 | 4.55 | 4.42 | 4.46 | 4.32 | 4.56 | 4.42 | 3.99 | 4.81 | 4.43 | 4.73 | 4.78 | 5.15 | 5.32 | 4.04 | 3.52 | 4.46 | 4 | 3.44 | 4.41 | 4.02 | 4.64 | 4.3 | 6.51 | 5 | 4.87 | 4.95 | 3.58 | 3.92 | 4.07 | 5.6 | 164.448 | 4.5873 | 6.51 |  | 43948 |  | 36208 |  | 36548 |  | 47744 |  | 43.948 |  | 36.208 |  | 36.548 |  | 47.744 |  | 164.448 | 0 | 0% |  | 71 | 0 | 170.89 |  | 70.4
2025-05-23 | 2026 | 2025 | 2025-05-01 | 31 | 2208 | 1744 | 1540 | 2852 | 2856 | 3280 | 1554 | 3876 | 2940 | 3632 | 4028 | 3908 | 4026 | 4702 | 3964 | 3550 | 2840 | 1328 | 3950 | 3067 | 3596 | 3796 | 5104 | 5524 | 5112 | 5628 | 1152 | 1792 | 2612 | 3340 | 3252 | 2658 | 3012 | 3236 | 4452 | 6012 | 4232 | 3300 | 3548 | 2894 | 2322 | 3682 | 2712 | 1828 | 4.26 | 4.08 | 4.01 | 4.22 | 4.14 | 4.63 | 4.08 | 4.37 | 4.37 | 4.16 | 4.66 | 4.59 | 4.71 | 4.79 | 5.01 | 4.75 | 4.68 | 4.16 | 3.8 | 4.46 | 4.3 | 4.39 | 4.38 | 4.45 | 4.98 | 5.08 | 5.48 | 3.4 | 3.52 | 4.11 | 4.51 | 4.15 | 4.18 | 4.55 | 4.39 | 4.7 | 6.17 | 4.94 | 4.4 | 4.6 | 4.17 | 3.83 | 4.82 | 4.45 | 146.641 | 4.4518 | 6.17 |  | 43778 |  | 42633 |  | 32134 |  | 28096 |  | 43.778 |  | 42.633 |  | 32.134 |  | 28.096 |  | 146.641 | 0 | 0% |  | 44 | 0 | 170.25 |  | 70.4
2025-05-24 | 2026 | 2025 | 2025-05-01 | 31 | 2332 | 1888 | 1648 | 1210 | 948 | 852 | 1692 | 1176 | 440 | 366 | 648 | 688 | 338 | 446 | 388 | 574 | 504 | 1408 | 544 | 609 | 2008 | 1996 | 1120 | 940 | 1176 | 1268 | 1212 | 476 | 1352 | 1636 | 588 | 642 | 820 | 1060 | 1336 | 2188 | 1588 | 828 | 1228 | 1112 | 828 | 1886 | 1780 | 1544 | 3.36 | 3.47 | 3.19 | 2.76 | 2.61 | 2.96 | 3.33 | 2.97 | 2.97 | 2.56 | 2.76 | 2.87 | 3.07 | 1.12 | 2.79 | 2.75 | 2.81 | 2.9 | 3.03 | 2.4 | 2.64 | 3.26 | 3.2 | 2.67 | 3.29 | 3.07 | 3.27 | 2.65 | 2.23 | 2.87 | 3.02 | 2.3 | 2.67 | 3.15 | 2.74 | 2.87 | 3.79 | 3.39 | 2.61 | 3.1 | 2.6 | 2.38 | 3.2 | 3.29 | 49.311 | 2.885 | 3.79 |  | 8160 |  | 11555 |  | 10154 |  | 19442 |  | 8.16 |  | 11.555 |  | 10.154 |  | 19.442 |  | 49.311 | 0 | 0% |  | 95 | 0 | 48.3 |  | 70.4
2025-05-25 | 2026 | 2025 | 2025-05-01 | 31 | 14740 | 17408 | 19836 | 9294 | 17940 | 16424 | 11696 | 6624 | 7212 | 7986 | 7742 | 7620 | 2584 | 7032 | 6596 | 7432 | 8484 | 16384 | 7716 | 7434 | 8976 | 9748 | 9088 | 8888 | 9160 | 8984 | 22106 | 6448 | 8784 | 8652 | 10076 | 12004 | 17844 | 17640 | 7280 | 18272 | 18772 | 16632 | 17720 | 5888 | 9124 | 9830 | 13356 | 13212 | 6.82 | 7.49 | 7.99 | 6.18 | 7.43 | 7.47 | 6.53 | 5.47 | 5.47 | 5.41 | 6.13 | 5.78 | 5.7 | 1.55 | 5.64 | 5.76 | 5.91 | 5.83 | 7.44 | 5.68 | 5.53 | 5.91 | 6.07 | 5.68 | 5.99 | 6.23 | 6.19 | 8.34 | 5.31 | 5.99 | 5.92 | 6.11 | 6.79 | 8.15 | 7.39 | 5.28 | 8.55 | 7.86 | 7.27 | 7.57 | 5.07 | 5.99 | 6.09 | 7.13 | 496.668 | 6.3202 | 8.55 |  | 75888 |  | 98852 |  | 153248 |  | 168680 |  | 75.888 |  | 98.852 |  | 153.248 |  | 168.68 |  | 496.668 | 0 | 0% |  | 86 | 0 | 500.2 |  | 70.4
2025-05-26 | 2026 | 2025 | 2025-05-01 | 31 | 13828 | 19344 | 19252 | 12348 | 19104 | 18768 | 12984 | 9124 | 8068 | 9656 | 10874 | 11520 | 10948 | 10310 | 8936 | 9758 | 10472 | 15864 | 10316 | 9153 | 12100 | 11320 | 11160 | 12288 | 12508 | 11848 | 17338 | 7484 | 12808 | 10426 | 11310 | 12680 | 18980 | 20196 | 9350 | 22004 | 21956 | 18428 | 21096 | 7600 | 12084 | 10804 | 16628 | 13756 | 7.71 | 8.23 | 8.51 | 7.19 | 7.85 | 8.17 | 7.28 | 6.32 | 6.32 | 6.22 | 6.83 | 6.74 | 6.71 | 6.67 | 6.53 | 6.53 | 6.57 | 6.53 | 7.76 | 6.43 | 6.08 | 6.76 | 6.57 | 6.36 | 6.87 | 7.27 | 7.02 | 8.35 | 5.91 | 7.02 | 6.65 | 6.56 | 7.22 | 8.55 | 8.13 | 5.95 | 9.75 | 8.71 | 7.82 | 8.46 | 5.76 | 7 | 7.01 | 8.24 | 586.779 | 7.1618 | 9.75 |  | 107994 |  | 128181 |  | 173212 |  | 177392 |  | 107.994 |  | 128.181 |  | 173.212 |  | 177.392 |  | 586.779 | 0 | 0% |  | 56 | 0 | 588 |  | 70.4
2025-05-27 | 2026 | 2025 | 2025-05-01 | 31 | 16900 | 17912 | 18488 | 11020 | 14748 | 13396 | 11540 | 7496 | 6914 | 8000 | 8776 | 8456 | 8212 | 7512 | 6778 | 7306 | 8000 | 15916 | 7900 | 6997 | 10364 | 10524 | 8744 | 9312 | 9760 | 9016 | 18168 | 8328 | 11540 | 10496 | 9080 | 9594 | 14792 | 16412 | 8822 | 16672 | 16672 | 15304 | 15900 | 8274 | 12684 | 12772 | 15240 | 13872 | 7.15 | 7.57 | 7.83 | 6.5 | 6.94 | 6.95 | 6.38 | 5.64 | 5.64 | 5.59 | 6.13 | 5.97 | 5.85 | 5.86 | 5.71 | 5.76 | 5.85 | 5.69 | 7.23 | 5.69 | 5.42 | 6.2 | 6.24 | 5.55 | 6.08 | 6.26 | 6.14 | 7.58 | 5.5 | 6.52 | 6.1 | 5.84 | 6.18 | 7.58 | 7.23 | 5.57 | 8.17 | 7.63 | 6.95 | 7.36 | 5.28 | 6.47 | 6.51 | 7.24 | 504.609 | 6.3984 | 8.17 |  | 84686 |  | 105843 |  | 133490 |  | 180590 |  | 84.686 |  | 105.843 |  | 133.49 |  | 180.59 |  | 504.609 | 0 | 2.22e-14% |  | 88 | 0 | 503 |  | 70.4
2025-05-28 | 2026 | 2025 | 2025-05-01 | 31 | 19200 | 19484 | 19456 | 14060 | 15200 | 13220 | 13824 | 8484 | 7742 | 9694 | 11008 | 11588 | 10704 | 10564 | 9540 | 10616 | 11026 | 17236 | 10306 | 8477 | 13516 | 14076 | 11832 | 12528 | 13080 | 12064 | 19470 | 10060 | 13880 | 13188 | 11066 | 8894 | 15392 | 15060 | 9840 | 15844 | 16320 | 14492 | 13560 | 9362 | 14840 | 15144 | 18092 | 15704 | 7.75 | 8.01 | 8.21 | 7.19 | 7.96 | 7.85 | 7.09 | 6.14 | 6.14 | 6.19 | 6.87 | 6.86 | 6.82 | 6.71 | 6.67 | 6.69 | 6.83 | 6.55 | 7.7 | 6.46 | 5.92 | 7 | 7.09 | 6.52 | 7.01 | 7.33 | 7.07 | 8.03 | 6.23 | 7.09 | 6.96 | 6.48 | 6.96 | 8.7 | 7.85 | 6.01 | 8.91 | 8.49 | 7.7 | 8.01 | 5.79 | 7.22 | 7.23 | 8.12 | 578.733 | 7.1457 | 8.91 |  | 108724 |  | 136967 |  | 127982 |  | 205060 |  | 108.724 |  | 136.967 |  | 127.982 |  | 205.06 |  | 578.733 | 0 | 0% |  | 88 | 0 | 579 |  | 70.4
2025-05-29 | 2026 | 2025 | 2025-05-01 | 31 | 21808 | 19588 | 20624 | 18064 | 22256 | 19816 | 17842 | 10276 | 9120 | 11372 | 13450 | 14380 | 13056 | 12428 | 11298 | 12500 | 12952 | 20192 | 11030 | 9101 | 15780 | 15296 | 13752 | 14488 | 12076 | 12468 | 21122 | 13012 | 18220 | 16318 | 13168 | 12604 | 21976 | 20844 | 10024 | 22780 | 22720 | 20724 | 22144 | 12936 | 17664 | 18176 | 21792 | 20296 | 8.23 | 7.99 | 8.35 | 8.06 | 8.54 | 8.46 | 7.85 | 6.5 | 6.5 | 6.49 | 7.29 | 7.51 | 7.48 | 7.32 | 7.14 | 7.11 | 7.24 | 7 | 8.24 | 6.67 | 6.07 | 7.46 | 7.27 | 6.87 | 7.44 | 7.46 | 7.12 | 8.27 | 6.93 | 7.95 | 7.62 | 6.99 | 7.35 | 9.27 | 8.18 | 6.03 | 9.62 | 8.96 | 8.19 | 8.74 | 6.76 | 7.84 | 7.84 | 8.83 | 711.533 | 7.6143 | 9.62 |  | 124438 |  | 159861 |  | 185864 |  | 241370 |  | 124.438 |  | 159.861 |  | 185.864 |  | 241.37 |  | 711.533 | 0 | 0% |  | 92 | 4874.5 | 715.1 |  | 70.4
2025-05-30 | 2026 | 2025 | 2025-05-01 | 31 | 35656 | 33632 | 34808 | 30400 | 34572 | 30552 | 32058 | 22420 | 17820 | 23602 | 28722 | 30596 | 23396 | 26542 | 24544 | 27144 | 28978 | 33564 | 24588 | 22509 | 28684 | 25508 | 23260 | 26384 | 28480 | 25668 | 32940 | 25160 | 31148 | 27908 | 27600 | 23250 | 33328 | 34156 | 22716 | 33712 | 33464 | 33800 | 34824 | 32008 | 33084 | 31156 | 35296 | 34148 | 11.32 | 11.49 | 11.73 | 10.36 | 11.1 | 10.45 | 10.52 | 8.91 | 8.91 | 8.16 | 9.48 | 10.74 | 10.78 | 9.91 | 9.58 | 9.66 | 9.8 | 10.14 | 11.08 | 9.21 | 8.47 | 9.69 | 9.19 | 8.35 | 9.74 | 10.12 | 9.46 | 10.92 | 9.14 | 10.36 | 9.64 | 9.61 | 9.25 | 12.39 | 11.27 | 8.55 | 12.36 | 11.79 | 11.06 | 11.63 | 10.76 | 11.06 | 10.28 | 11.96 | 1283.785 | 10.2359 | 12.39 |  | 250348 |  | 320361 |  | 291658 |  | 421418 |  | 250.348 |  | 320.361 |  | 291.658 |  | 421.418 |  | 1283.785 | 0 | 0% |  | 91 | 0 | 1280.2 |  | 70.4
2025-05-31 | 2026 | 2025 | 2025-05-01 | 31 | 27252 | 23100 | 18748 | 24224 | 27128 | 24928 | 24682 | 15502 | 11552 | 15596 | 20700 | 23420 | 24876 | 20098 | 18744 | 20982 | 23722 | 20412 | 20252 | 19493 | 23100 | 18644 | 16244 | 20308 | 22788 | 21964 | 16556 | 20740 | 23984 | 23962 | 23324 | 19384 | 25304 | 25788 | 19556 | 29928 | 29680 | 26152 | 29028 | 22492 | 26400 | 26198 | 30312 | 28176 | 9.3 | 8.77 | 8.01 | 9.17 | 9.45 | 9.52 | 9.21 | 7.53 | 6.89 | 7.99 | 8.85 | 9.18 | 9.36 | 8.37 | 8.51 | 8.66 | 8.99 | 8.29 | 8.36 | 7.9 | 8.82 | 7.74 | 7.07 | 8.56 | 8.94 | 8.78 | 7.18 | 8.44 | 9.08 | 8.94 | 8.66 | 8.64 | 10.16 | 9.38 | 7.85 | 11.18 | 10.63 | 9.21 | 10.25 | 8.67 | 9.61 | 9.37 | 10.56 | 9.95 | 995.423 | 8.8632 | 11.18 |  | 192950 |  | 256123 |  | 237320 |  | 309030 |  | 192.95 |  | 256.123 |  | 237.32 |  | 309.03 |  | 995.423 | 0 | 0% |  | 93 | 0 | 994 |  | 70.4
2025-06-01 | 2026 | 2025 | 2025-06-01 | 30 | 15156 | 13980 | 10136 | 12256 | 13160 | 15836 | 13966 | 8754 | 5878 | 5468 | 6048 | 10344 | 10024 | 10616 | 7802 | 9646 | 6878 | 10300 | 11804 | 6197 | 12060 | 11380 | 10016 | 9132 | 9412 | 7900 | 7812 | 8246 | 12156 | 11204 | 6796 | 10442 | 13916 | 7764 | 9062 | 19420 | 17524 | 8748 | 13164 | 9054 | 10492 | 12534 | 18468 | 16108 | 7.14 | 7.03 | 6.34 | 7.04 | 6.7 | 7.67 | 7.25 | 6.15 | 5.5 | 5.7 | 5.42 | 6.52 | 6.43 | 6.52 | 6.09 | 6.42 | 5.44 | 6.34 | 6.77 | 5.25 | 6.94 | 6.7 | 6.09 | 6.24 | 6.3 | 5.9 | 5.52 | 5.94 | 6.98 | 6.64 | 5.27 | 6.73 | 7.39 | 5.39 | 5.98 | 8.93 | 8.05 | 5.69 | 6.97 | 6.1 | 6.54 | 6.94 | 8.23 | 7.75 | 477.059 | 6.5211 | 8.93 |  | 82976 |  | 116653 |  | 119974 |  | 157456 |  | 82.976 |  | 116.653 |  | 119.974 |  | 157.456 |  | 477.059 | 0 | -1.11e-14% |  | 96 | 0 | 372 |  | 70.4
2025-06-02 | 2026 | 2025 | 2025-06-01 | 30 | 15232 | 14788 | 9096 | 13316 | 13948 | 15708 | 13944 | 8964 | 5886 | 5864 | 7046 | 11272 | 11496 | 10868 | 6060 | 10160 | 8212 | 9924 | 11298 | 8100 | 11764 | 9980 | 9548 | 9868 | 10312 | 8360 | 5360 | 8284 | 12992 | 11288 | 7428 | 11228 | 13424 | 9524 | 8172 | 19152 | 16712 | 9196 | 16224 | 10642 | 11620 | 13060 | 18144 | 16968 | 7.11 | 7.12 | 5.94 | 7.25 | 6.91 | 7.68 | 7.24 | 6.27 | 5.57 | 5.9 | 5.79 | 6.87 | 6.98 | 6.77 | 6.5 | 6.65 | 5.81 | 6.16 | 6.72 | 5.77 | 6.87 | 6.3 | 5.97 | 6.51 | 6.64 | 6.17 | 5.04 | 5.98 | 7.16 | 6.68 | 5.43 | 6.97 | 7.31 | 5.86 | 5.77 | 8.89 | 8.11 | 5.69 | 7.67 | 6.43 | 6.75 | 7.06 | 8.21 | 7.9 | 490.432 | 6.645 | 8.89 |  | 88616 |  | 118350 |  | 125116 |  | 158350 |  | 88.616 |  | 118.35 |  | 125.116 |  | 158.35 |  | 490.432 | 0 | 0% |  | 89 | 0 | 148.3 |  | 70.4
2025-06-03 | 2026 | 2025 | 2025-06-01 | 30 | 16708 | 14980 | 10180 | 12560 | 15444 | 16480 | 14758 | 9230 | 5654 | 6684 | 9466 | 13520 | 12872 | 11326 | 9026 | 9852 | 8440 | 10712 | 10548 | 6905 | 12236 | 10444 | 9924 | 10172 | 11360 | 7424 | 8328 | 9582 | 12824 | 12454 | 7860 | 11044 | 14872 | 12236 | 9042 | 19868 | 19060 | 11260 | 16940 | 10058 | 11864 | 14108 | 19088 | 17468 | 7.36 | 7.13 | 6.23 | 6.98 | 7.14 | 7.76 | 7.37 | 6.19 | 5.51 | 6.07 | 6.3 | 7.19 | 7.04 | 6.65 | 6.4 | 6.49 | 5.86 | 6.38 | 6.49 | 5.49 | 6.87 | 6.32 | 5.94 | 6.5 | 6.69 | 6.14 | 5.51 | 6.23 | 7.05 | 6.85 | 5.59 | 6.88 | 7.61 | 6.43 | 5.91 | 8.99 | 8.28 | 6.19 | 7.69 | 6.28 | 6.73 | 7.17 | 8.36 | 7.95 | 524.861 | 6.7316 | 8.99 |  | 96306 |  | 121063 |  | 137204 |  | 170288 |  | 96.306 |  | 121.063 |  | 137.204 |  | 170.288 |  | 524.861 | 0 | 0% |  | 54 | 5590.37 | 321.96 |  | 70.4
2025-06-04 | 2026 | 2025 | 2025-06-01 | 30 | 16388 | 15436 | 15280 | 12198 | 14272 | 15156 | 13570 | 9960 | 8726 | 7804 | 8440 | 9296 | 7972 | 8146 | 7360 | 8430 | 9472 | 11804 | 10834 | 7663 | 12604 | 11372 | 12616 | 9924 | 10664 | 5016 | 13916 | 9112 | 12120 | 10892 | 9556 | 10472 | 14152 | 11764 | 9968 | 19944 | 17600 | 13024 | 12444 | 9888 | 11808 | 11980 | 18100 | 13268 | 7.29 | 7.27 | 7.45 | 6.92 | 6.87 | 7.5 | 7.09 | 6.31 | 6.17 | 6.07 | 6.1 | 6.28 | 5.93 | 5.9 | 5.99 | 6.05 | 6.05 | 6.54 | 6.55 | 5.62 | 6.98 | 6.55 | 6.58 | 6.57 | 6.44 | 5.35 | 6.97 | 5.97 | 6.91 | 6.37 | 6.12 | 6.68 | 7.37 | 6.39 | 6.11 | 9.1 | 8 | 6.61 | 6.64 | 6.1 | 6.58 | 6.51 | 8.16 | 6.95 | 510.411 | 6.6355 | 9.1 |  | 90418 |  | 119723 |  | 128828 |  | 171442 |  | 90.418 |  | 119.723 |  | 128.828 |  | 171.442 |  | 510.411 | 0 | 2.22e-14% |  | 90 | 57457.88 | 439.93 |  | 70.4
2025-06-05 | 2026 | 2025 | 2025-06-01 | 30 | 11576 | 12092 | 12092 | 9480 | 12004 | 11220 | 8064 | 5290 | 6012 | 7048 | 6664 | 6660 | 5764 | 6416 | 5448 | 6106 | 6024 | 11316 | 5292 | 4342 | 8760 | 9120 | 8624 | 8096 | 7820 | 4616 | 14364 | 5776 | 9400 | 8040 | 6040 | 7230 | 12628 | 12280 | 5924 | 12760 | 12544 | 11340 | 12212 | 4854 | 8132 | 8996 | 10612 | 9476 | 6.34 | 6.59 | 6.78 | 6.37 | 6.82 | 7.11 | 5.93 | 5.14 | 5.81 | 6.35 | 5.9 | 5.79 | 5.7 | 5.74 | 5.65 | 5.8 | 5.5 | 6.69 | 5.29 | 4.91 | 6.14 | 6.16 | 5.85 | 6.14 | 6.14 | 5.38 | 7.11 | 5.3 | 6.34 | 5.97 | 5.38 | 6.24 | 7.43 | 6.77 | 5.11 | 7.6 | 7.22 | 6.47 | 7.04 | 4.71 | 5.86 | 6.09 | 6.58 | 6.41 | 378.554 | 6.1284 | 7.6 |  | 66594 |  | 82352 |  | 104218 |  | 125390 |  | 66.594 |  | 82.352 |  | 104.218 |  | 125.39 |  | 378.554 | 0 | 0% |  | 89 | 2043.25 | 320.79 |  | 70.4
2025-06-06 | 2026 | 2025 | 2025-06-01 | 30 | 11248 | 11184 | 9516 | 6566 | 6032 | 5708 | 6442 | 2692 | 1850 | 1872 | 1868 | 1828 | 1180 | 1980 | 1854 | 2162 | 2802 | 11256 | 2948 | 2595 | 6976 | 7904 | 4120 | 4084 | 4644 | 4064 | 8438 | 4328 | 7016 | 6764 | 3364 | 3776 | 6128 | 6332 | 5320 | 8832 | 7656 | 7068 | 7852 | 1816 | 6110 | 8092 | 9868 | 9204 | 6.36 | 6.58 | 6.38 | 5.61 | 5.53 | 5.76 | 5.47 | 4.38 | 4.27 | 4.51 | 4.11 | 4.14 | 4.08 | 4.21 | 4.29 | 4.44 | 4.54 | 6.79 | 4.49 | 4.3 | 5.75 | 5.98 | 4.75 | 5.13 | 5.35 | 5.2 | 6.03 | 4.89 | 5.85 | 5.73 | 4.51 | 5.09 | 5.78 | 5.97 | 5.07 | 6.84 | 6.27 | 5.58 | 6.13 | 3.48 | 5.34 | 5.91 | 6.54 | 6.54 | 243.339 | 5.317 | 6.84 |  | 28202 |  | 51487 |  | 59384 |  | 104266 |  | 28.202 |  | 51.487 |  | 59.384 |  | 104.266 |  | 243.339 | 0 | 0% |  | 89 | 1151.12 | 208.73 |  | 70.4
2025-06-07 | 2026 | 2025 | 2025-06-01 | 30 | 11992 | 11256 | 9040 | 9092 | 8084 | 7968 | 6868 | 3700 | 3134 | 3348 | 3264 | 3100 | 2816 | 3232 | 3002 | 3340 | 3930 | 12464 | 3848 | 3157 | 8748 | 9288 | 6160 | 5800 | 6288 | 5524 | 8826 | 3974 | 8060 | 6676 | 4476 | 5310 | 8368 | 11440 | 6666 | 10712 | 9800 | 9500 | 9852 | 1592 | 5158 | 7086 | 11176 | 10344 | 6.46 | 6.52 | 6.2 | 6.26 | 6.11 | 6.39 | 5.59 | 4.74 | 4.9 | 5.21 | 4.79 | 4.7 | 4.74 | 4.85 | 4.88 | 5.04 | 4.99 | 7.03 | 4.89 | 4.57 | 6.16 | 6.27 | 5.34 | 5.56 | 5.85 | 5.67 | 6 | 4.75 | 6.19 | 5.7 | 4.99 | 5.67 | 6.41 | 6.63 | 5.43 | 7.26 | 6.75 | 6.19 | 6.62 | 3.53 | 5.08 | 5.7 | 6.82 | 6.77 | 297.459 | 5.6864 | 7.26 |  | 43134 |  | 66839 |  | 81034 |  | 106452 |  | 43.134 |  | 66.839 |  | 81.034 |  | 106.452 |  | 297.459 | 0 | 0% |  | 88 | 58.37 | 255.38 |  | 70.4
2025-06-08 | 2026 | 2025 | 2025-06-01 | 30 | 16272 | 16412 | 14480 | 14668 | 15760 | 15420 | 10990 | 6340 | 6332 | 7096 | 7096 | 6940 | 6236 | 6836 | 6140 | 7030 | 7224 | 18304 | 7150 | 6097 | 13552 | 14848 | 10376 | 10516 | 10756 | 9288 | 15096 | 7022 | 14028 | 10336 | 8348 | 10592 | 16544 | 19176 | 10218 | 16776 | 16276 | 15704 | 16868 | 4310 | 8712 | 10746 | 14836 | 14176 | 7.33 | 7.57 | 7.34 | 7.5 | 7.61 | 7.93 | 6.6 | 5.64 | 5.97 | 6.42 | 6.09 | 5.9 | 5.93 | 6.03 | 6.04 | 6.2 | 5.91 | 8.08 | 5.96 | 5.5 | 7.16 | 7.41 | 6.4 | 6.81 | 7.01 | 6.66 | 7.36 | 5.66 | 7.4 | 6.61 | 6.11 | 7.07 | 8.24 | 8.07 | 6.31 | 8.57 | 7.97 | 7.4 | 8.06 | 4.48 | 6.02 | 6.56 | 7.62 | 7.47 | 501.923 | 6.8177 | 8.57 |  | 80976 |  | 116139 |  | 143116 |  | 161692 |  | 80.976 |  | 116.139 |  | 143.116 |  | 161.692 |  | 501.923 | 0 | 0% |  | 88 | 1277.87 | 448.22 |  | 70.4
2025-06-09 | 2026 | 2025 | 2025-06-01 | 30 | 16940 | 18236 | 16776 | 16532 | 20504 | 20520 | 12128 | 8652 | 9538 | 10458 | 10170 | 9840 | 8880 | 9484 | 8716 | 9292 | 9242 | 20004 | 9754 | 9209 | 16132 | 16792 | 13236 | 13472 | 14468 | 13176 | 17692 | 9324 | 15816 | 12992 | 11256 | 13448 | 21704 | 23956 | 13724 | 22036 | 21456 | 20508 | 22340 | 4666 | 10828 | 12460 | 17356 | 17380 | 7.42 | 7.85 | 7.75 | 7.83 | 8.39 | 8.74 | 6.75 | 6.18 | 6.82 | 7.26 | 6.91 | 6.63 | 6.62 | 6.63 | 6.69 | 6.71 | 6.37 | 8.34 | 6.56 | 6.26 | 7.57 | 7.73 | 6.94 | 7.39 | 7.69 | 7.48 | 7.79 | 6.16 | 7.7 | 7.01 | 6.71 | 7.61 | 9.24 | 8.83 | 6.97 | 9.48 | 8.76 | 8.17 | 8.88 | 4.63 | 6.48 | 6.82 | 8.04 | 7.99 | 631.093 | 7.3814 | 9.48 |  | 111890 |  | 145949 |  | 186472 |  | 186782 |  | 111.89 |  | 145.949 |  | 186.472 |  | 186.782 |  | 631.093 | 0 | 2.22e-14% |  | 88 | 7317.37 | 553.03 |  | 70.4
2025-06-10 | 2026 | 2025 | 2025-06-01 | 30 | 24196 | 25240 | 24932 | 19492 | 22920 | 21536 | 17028 | 9980 | 10090 | 10840 | 10442 | 9888 | 8660 | 9344 | 8536 | 8916 | 8990 | 25260 | 9608 | 8518 | 19384 | 20144 | 15308 | 13504 | 15072 | 13060 | 23764 | 14612 | 18956 | 18500 | 10694 | 14312 | 23096 | 26168 | 14422 | 24492 | 22780 | 22304 | 24300 | 8910 | 18918 | 20834 | 23140 | 21940 | 8.76 | 9.44 | 9.38 | 8.55 | 8.8 | 8.95 | 7.57 | 6.86 | 7.03 | 7.44 | 7.08 | 6.76 | 6.66 | 6.67 | 6.75 | 6.7 | 6.46 | 9.32 | 6.7 | 6.25 | 8.37 | 8.73 | 7.58 | 7.93 | 8.12 | 7.71 | 9.03 | 7.14 | 8.56 | 7.99 | 6.77 | 7.73 | 9.6 | 9.44 | 7.39 | 10.03 | 9.1 | 8.53 | 9.31 | 5.53 | 8 | 8.35 | 9.09 | 8.8 | 743.03 | 7.9764 | 10.03 |  | 116844 |  | 157004 |  | 201908 |  | 267274 |  | 116.844 |  | 157.004 |  | 201.908 |  | 267.274 |  | 743.03 | 0 | 0% |  | 46 | 30691.5 | 333 |  | 70.4
2025-06-11 | 2026 | 2025 | 2025-06-01 | 30 | 26848 | 29624 | 29888 | 22960 | 22984 | 22604 | 19756 | 13976 | 12856 | 13350 | 13108 | 12576 | 12416 | 12842 | 12008 | 12492 | 11744 | 27292 | 13188 | 12000 | 22824 | 25256 | 17560 | 18140 | 19120 | 18040 | 29972 | 17014 | 18836 | 21024 | 14360 | 16360 | 23972 | 27140 | 20686 | 25664 | 24512 | 23912 | 25080 | 10968 | 23360 | 24166 | 23932 | 23244 | 9.26 | 10.48 | 10.56 | 8.91 | 8.75 | 9.1 | 8.04 | 7.36 | 7.46 | 7.78 | 7.49 | 7.17 | 7.28 | 7.31 | 7.43 | 7.42 | 6.87 | 9.8 | 7.27 | 6.85 | 8.59 | 9.24 | 7.58 | 8.27 | 8.49 | 8.35 | 10.32 | 7.67 | 8.75 | 8.49 | 7.35 | 8.21 | 9.68 | 9.45 | 8.21 | 10.19 | 9.3 | 8.76 | 9.38 | 6.03 | 8.92 | 9 | 9.26 | 9.1 | 869.654 | 8.4359 | 10.56 |  | 151142 |  | 199196 |  | 212228 |  | 307088 |  | 151.142 |  | 199.196 |  | 212.228 |  | 307.088 |  | 869.654 | 0 | 0% |  | 46 | 13380.75 | 305.49 |  | 70.4
2025-06-12 | 2026 | 2025 | 2025-06-01 | 30 | 22828 | 27164 | 27808 | 14710 | 15188 | 15524 | 15484 | 10594 | 9624 | 9644 | 8592 | 7896 | 7740 | 8038 | 7424 | 7284 | 8218 | 22240 | 8612 | 7553 | 15504 | 18048 | 12244 | 12116 | 12872 | 12256 | 27744 | 10994 | 16284 | 14372 | 9026 | 10860 | 15924 | 20804 | 13654 | 20720 | 19632 | 17676 | 18500 | 8602 | 18210 | 19786 | 19344 | 18436 | 8.37 | 9.71 | 9.94 | 7.23 | 7.31 | 7.82 | 7.4 | 6.56 | 6.55 | 6.84 | 6.26 | 6.04 | 6.12 | 6.17 | 6.26 | 6.12 | 6.06 | 8.69 | 6.2 | 5.84 | 7.29 | 7.87 | 6.55 | 6.96 | 7.22 | 7.12 | 9.72 | 6.48 | 7.57 | 7.27 | 6.18 | 7.07 | 7.98 | 8.21 | 6.91 | 9.34 | 8.5 | 7.67 | 8.15 | 5.45 | 7.92 | 8.15 | 8.35 | 8.18 | 645.773 | 7.3545 | 9.94 |  | 103578 |  | 134355 |  | 154828 |  | 253012 |  | 103.578 |  | 134.355 |  | 154.828 |  | 253.012 |  | 645.773 | 0 | -2.22e-14% |  | 93 | 28400.5 | 611.16 |  | 70.4
Formulas:
Month Year = [Date]-DAY([Date])+1
Days = DAY(EOMONTH(Input_Raw[[#This Row],[Date]],0))
Date = [Date, row above]+1

## WTG_BD
Sr. No. | Date | Finacial Year | Calendor Year | Month | Operating Year | Affected WTG | SPV | Consumaer | Plant Equivalent Weightage | Error Code | Error Text | Breakdown Description | Fault Start TimeStamp | Work Start TimeStamp | Fault Clearance time | Response Time | Resolution Time | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Paired WTG for Enegy based MA | Energy Production during breakdwon of paired WTG | Fault Category
1 | 2025-03-29 | 2025 | 2025 | 2025-03-01 | Year_2 | P-51 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity | 0.41111 | 0.41111 | 0.73958 | 0 | 7.8833 | 7.8833 | 12th Annual Maintenance Activity completed | Close | 0.17917 | P-52 | 750 | WTG Scheduled Maintenance
2 | 2025-03-29 | 2025 | 2025 | 2025-03-01 | Year_2 | P-56 | PWEPL | MSEDCL | 2.273% | 86 | Secondary brake pads worn | Secondary brake pads worn | 0.69028 | 0.69028 | 0.80069 | 0 | 2.65 | 2.65 | Hydraulic Brake Pad Replaced & wtg restored | Close | 0.060227 | P-56 | 388 | WTG Breakdown Maintenance
3 | 2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_2 | P-52 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity | 0.40556 | 0.40556 | 0.75486 | 0 | 8.3833 | 8.3833 | 12th Annual Maintenance Activity completed | Close | 0.19053 | P-51 | 357 | WTG Scheduled Maintenance
4 | 2025-04-01 | 2026 | 2026 | 2025-04-01 | Year_3 | P-09 | PWEPL | MSEDCL | 2.273% | 77 | Gearbox oil overtemperature | Radiator Motor Failure | 0.97569 | 0.97569 | 0.99931 | 0 | 0.56667 | 0.56667 | Rediator Motor replaced | Close | 0.012879 | P-8 | 397 | WTG Breakdown Maintenance
5 | 2025-04-01 | 2026 | 2026 | 2025-04-01 | Year_3 | P-27 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault | 0.84236 | 0.84236 | 0.92569 | 0 | 2 | 2 | Hard Rebooted Turbine from down tower assembly | Close | 0.045455 | P-28 | 3065 | WTG Breakdown Maintenance
6 | 2025-04-01 | 2026 | 2026 | 2025-04-01 | Year_3 | P-32 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | DTA Maintenance | 0.65486 | 0.65486 | 0.69306 | 0 | 0.91667 | 0.91667 | DTA Maintenance activity completed | Close | 0.020833 | P-37 | 66 | WTG Scheduled Maintenance
7 | 2025-04-01 | 2026 | 2026 | 2025-04-01 | Year_3 | P-37 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | DTA Maintenance | 0.60417 | 0.60417 | 0.64792 | 0 | 1.05 | 1.05 | DTA Maintenance activity completed | Close | 0.023864 | P-32 | 54 | WTG Scheduled Maintenance
8 | 2025-04-01 | 2026 | 2026 | 2025-04-01 | Year_3 | P-51 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | DTA Maintenance | 0.58333 | 0.58333 | 0.62222 | 0 | 0.93333 | 0.93333 | DTA Maintenance activity completed | Close | 0.021212 | P-52 | 0 | WTG Scheduled Maintenance
9 | 2025-04-01 | 2026 | 2026 | 2025-04-01 | Year_3 | P-52 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | DTA Maintenance | 0.54167 | 0.54167 | 0.57361 | 0 | 0.76667 | 0.76667 | DTA Maintenance activity completed | Close | 0.017424 | P-50 | 0 | WTG Scheduled Maintenance
10 | 2025-04-02 | 2026 | 2026 | 2025-04-01 | Year_3 | P-09 | PWEPL | MSEDCL | 2.273% | 77 | Gearbox oil overtemperature | Radiator Motor Failure | 0.046528 | 0.046528 | 0.25972 | 0 | 5.1167 | 5.1167 | Radiator motor replaced | Close | 0.11629 | P-08 | 932 | WTG Breakdown Maintenance
11 | 2025-04-02 | 2026 | 2026 | 2025-04-01 | Year_3 | P-46 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault | 0.090972 | 0.090972 | 0.15069 | 0 | 1.4333 | 1.4333 | Rebooted the PLC & reset at scada | Close | 0.032576 | P-47 | 163 | WTG Breakdown Maintenance
12 | 2025-04-02 | 2026 | 2026 | 2025-04-01 | Year_3 | P-46 | PWEPL | MSEDCL | 2.273% | 352 | Communication fault wind measurement device | FT Sensor failure | 0.17153 | 0.17153 | 0.33819 | 0 | 4 | 4 | FT sensor replaced. | Close | 0.090909 | P-47 | 1720 | WTG Breakdown Maintenance
13 | 2025-04-03 | 2026 | 2026 | 2025-04-01 | Year_3 | P-31 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity | 0.4625 | 0.4625 | 0.72986 | 0 | 6.4167 | 6.4167 | 12th Annual Maintenance Day 1 Activity completed | Close | 0.14583 | P-03 | 1202 | WTG Scheduled Maintenance
14 | 2025-04-03 | 2026 | 2026 | 2025-04-01 | Year_3 | P-51 | PWEPL | MSEDCL | 2.273% | 60 | Yaw limit switch activated | Yaw limit switch activated | 0.89514 | 0.89514 | 0.96667 | 0 | 1.7167 | 1.7167 | Cable Twist Release & Turbine Restored | Close | 0.039015 | P-52 | 44 | WTG Breakdown Maintenance
15 | 2025-04-04 | 2026 | 2026 | 2025-04-01 | Year_3 | P-05 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Gearbox Oil & Main Bering Grease Sample Collection work | 0.45694 | 0.45694 | 0.48472 | 0 | 0.66667 | 0.66667 | OIL & Grease sample collection work completed | Close | 0.015152 | P-41 | 2 | WTG Scheduled Maintenance
16 | 2025-04-04 | 2026 | 2026 | 2025-04-01 | Year_3 | P-06 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Gearbox Oil & Main Bering Grease Sample Collection work | 0.53611 | 0.53611 | 0.56806 | 0 | 0.76667 | 0.76667 | OIL & Grease sample collection work completed | Close | 0.017424 | P-41 | 0 | WTG Scheduled Maintenance
17 | 2025-04-04 | 2026 | 2026 | 2025-04-01 | Year_3 | P-40 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Gearbox Oil & Main Bering Grease Sample Collection work | 0.47014 | 0.47014 | 0.5125 | 0 | 1.0167 | 1.0167 | OIL & Grease sample collection work completed | Close | 0.023106 | P-46 | 0 | WTG Scheduled Maintenance
18 | 2025-04-04 | 2026 | 2026 | 2025-04-01 | Year_3 | P-41 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Gearbox Oil & Main Bering Grease Sample Collection work | 0.52986 | 0.52986 | 0.55694 | 0 | 0.65 | 0.65 | OIL & Grease sample collection work completed | Close | 0.014773 | P-05 | 0 | WTG Scheduled Maintenance
19 | 2025-04-04 | 2026 | 2026 | 2025-04-01 | Year_3 | P-42 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Gearbox Oil & Main Bering Grease Sample Collection work | 0.64514 | 0.64514 | 0.68542 | 0 | 0.96667 | 0.96667 | OIL & Grease sample collection work completed | Close | 0.02197 | P-12 | 12 | WTG Scheduled Maintenance
20 | 2025-04-04 | 2026 | 2026 | 2025-04-01 | Year_3 | P-48 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Gearbox Oil & Main Bering Grease Sample Collection work | 0.63542 | 0.63542 | 0.6625 | 0 | 0.65 | 0.65 | OIL & Grease sample collection work completed | Close | 0.014773 | P-47 | 14 | WTG Scheduled Maintenance
21 | 2025-04-05 | 2026 | 2026 | 2025-04-01 | Year_3 | P-31 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity | 0.4125 | 0.4125 | 0.72083 | 0 | 7.4 | 7.4 | 12th Annual Maintenance Day 2 Activity completed | Close | 0.16818 | P-3 | 5340 | WTG Scheduled Maintenance
22 | 2025-04-05 | 2026 | 2026 | 2025-04-01 | Year_3 | P-56 | PWEPL | MSEDCL | 2.273% | 134 | Battery charging voltage not OK | Battery Voltage Not OK | 0.87083 | 0.87083 | 0.96667 | 0 | 2.3 | 2.3 | Axis Box 5 Amp Fuse Replaced & wtg restored | Close | 0.052273 | P-55 | 904 | WTG Breakdown Maintenance
23 | 2025-04-05 | 2026 | 2026 | 2025-04-01 | Year_3 | P-27 | PWEPL | MSEDCL | 2.273% | 201 | IO Card 28V power supply failed | WETB card failure | 0.85139 | 0.85139 | 0.99931 | 0 | 3.55 | 3.55 | Replaced WETB card. | Close | 0.080682 | P-28 | 476 | WTG Breakdown Maintenance
24 | 2025-04-06 | 2026 | 2026 | 2025-04-01 | Year_3 | P-26 | PWEPL | MSEDCL | 2.273% | 60 | Yaw limit switch activated | Yaw limit switch activated | 0.63403 | 0.63403 | 0.68403 | 0 | 1.2 | 1.2 | Cable Twist Release & Turbine Restored | Close | 0.027273 | P-25 | 58 | WTG Breakdown Maintenance
25 | 2025-04-06 | 2026 | 2026 | 2025-04-01 | Year_3 | P-47 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Gearbox Oil & Main Bering Grease Sample Collection work | 0.89028 | 0.89028 | 0.92431 | 0 | 0.81667 | 0.81667 | OIL & Grease sample collection work completed | Close | 0.018561 | P-48 | 72 | WTG Breakdown Maintenance
26 | 2025-04-07 | 2026 | 2026 | 2025-04-01 | Year_3 | P-03 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity | 0.39722 | 0.39722 | 0.71528 | 0 | 7.6333 | 7.6333 | 12th Annual Maintenance Activity completed | Close | 0.17348 | P-02 | 905 | WTG Scheduled Maintenance
27 | 2025-04-07 | 2026 | 2026 | 2025-04-01 | Year_3 | P-07 | PWEPL | MSEDCL | 2.273% | 81 | Shaft Bearing Over Tempreture | Shaft Bearing Over Tempreture | 0.6375 | 0.6375 | 0.76736 | 0 | 3.1167 | 3.1167 | Tempreture sensor cable connection tight proparly & turbine restored | Close | 0.070833 | P-18 | 474 | WTG Breakdown Maintenance
28 | 2025-04-08 | 2026 | 2026 | 2025-04-01 | Year_3 | P-02 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity | 0.38472 | 0.38472 | 0.7125 | 0 | 7.8667 | 7.8667 | 12th Annual Maintenance Activity completed | Close | 0.17879 | P-18 | 668 | WTG Scheduled Maintenance
29 | 2025-04-08 | 2026 | 2026 | 2025-04-01 | Year_3 | P-02 | PWEPL | MSEDCL | 2.273% | 86 | Braking pad of secondary brake worn out | Braking pad of secondary brake worn out | 0.85625 | 0.85625 | 0.99931 | 0 | 3.4333 | 3.4333 | Hydralic Brake pad & Sensor replaced | Close | 0.07803 | P-18 | 1305 | WTG Breakdown Maintenance
30 | 2025-04-08 | 2026 | 2026 | 2025-04-01 | Year_3 | P-06 | PWEPL | MSEDCL | 2.273% | 430 | Yaw tooth sensor 1 timeout | Yaw tooth sensor 1 timeout | 0.83958 | 0.83958 | 0.88889 | 0 | 1.1833 | 1.1833 | Rebooted the PLC & reset at scada | Close | 0.026894 | P-41 | 53 | WTG Breakdown Maintenance
31 | 2025-04-09 | 2026 | 2026 | 2025-04-01 | Year_3 | P-06 | PWEPL | MSEDCL | 2.273% | 86 | Braking pad of secondary brake worn out | Braking pad of secondary brake worn out | 0.0041667 | 0.0041667 | 0.052778 | 0 | 1.1667 | 1.1667 | Hydralic Brake pad & Sensor replaced | Close | 0.026515 | P-18 | 490 | WTG Breakdown Maintenance
32 | 2025-04-09 | 2026 | 2026 | 2025-04-01 | Year_3 | P-02 | PWEPL | MSEDCL | 2.273% | 430 | Yaw tooth sensor 1 timeout | Yaw tooth sensor 1 timeout | 0 | 0 | 0.11528 | 0 | 2.7667 | 2.7667 | Grease cleaned from yaw sensor, Yaw teeth, Pinion. | Close | 0.062879 | P-41 | 117 | WTG Breakdown Maintenance
33 | 2025-04-09 | 2026 | 2026 | 2025-04-01 | Year_3 | P-18 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity | 0.40486 | 0.40486 | 0.71667 | 0 | 7.4833 | 7.4833 | 12th Annual Maintenance Activity completed | Close | 0.17008 | P-07 | 824 | WTG Scheduled Maintenance
34 | 2025-04-09 | 2026 | 2026 | 2025-04-01 | Year_3 | P-11 | PWEPL | MSEDCL | 2.273% | 275 | Pitch thyristor 2 fault | Pitch thyristor 2 fault | 0.11667 | 0.11667 | 0.16528 | 0 | 1.1667 | 1.1667 | Hard Rebooted Turbine from down tower assembly | Close | 0.026515 | P-10 | 21 | WTG Breakdown Maintenance
35 | 2025-04-09 | 2026 | 2026 | 2025-04-01 | Year_3 | P-13 | PWEPL | MSEDCL | 2.273% | 142 | Line CCU collective faults | Line CCU Collective faults | 0.11667 | 0.11667 | 0.22361 | 0 | 2.5667 | 2.5667 | Replaced WEMA card. | Close | 0.058333 | P-12 | 32 | WTG Breakdown Maintenance
36 | 2025-04-09 | 2026 | 2026 | 2025-04-01 | Year_3 | P-46 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Gearbox Oil & Main Bering Grease Sample Collection work | 0.80903 | 0.80903 | 0.83333 | 0 | 0.58333 | 0.58333 | OIL & Grease sample collection work completed | Close | 0.013258 | P-45 | 193 | WTG Scheduled Maintenance
37 | 2025-04-10 | 2026 | 2026 | 2025-04-01 | Year_3 | P-01 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity | 0.375 | 0.375 | 0.70903 | 0 | 8.0167 | 8.0167 | 12th Annual Maintenance Activity completed | Close | 0.1822 | P-07 | 1327 | WTG Scheduled Maintenance
38 | 2025-04-11 | 2026 | 2026 | 2025-04-01 | Year_3 | P-07 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity | 0.40625 | 0.40625 | 0.77778 | 0 | 8.9167 | 8.9167 | 12th Annual Maintenance Activity completed | Close | 0.20265 | P-18 | 2709 | WTG Scheduled Maintenance
39 | 2025-04-11 | 2026 | 2026 | 2025-04-01 | Year_3 | P-11 | PWEPL | MSEDCL | 2.273% | 60 | Yaw limit switch activated | Yaw limit switch activated | 0.66042 | 0.66042 | 0.68403 | 0 | 0.56667 | 0.56667 | Cable Twist Release & Turbine Restored | Close | 0.012879 | P-10 | 245 | WTG Breakdown Maintenance
40 | 2025-04-12 | 2026 | 2026 | 2025-04-01 | Year_3 | P-01 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity | 0.75347 | 0.75347 | 0.76875 | 0 | 0.36667 | 0.36667 | DTA Maintenance activity completed | Close | 0.0083333 | P-07 | 240 | WTG Scheduled Maintenance
41 | 2025-04-12 | 2026 | 2026 | 2025-04-01 | Year_3 | P-02 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity | 0.53611 | 0.53611 | 0.60069 | 0 | 1.55 | 1.55 | DTA Maintenance activity completed | Close | 0.035227 | P-18 | 393 | WTG Scheduled Maintenance
42 | 2025-04-12 | 2026 | 2026 | 2025-04-01 | Year_3 | P-03 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity | 0.72292 | 0.72292 | 0.74514 | 0 | 0.53333 | 0.53333 | DTA Maintenance activity completed | Close | 0.012121 | P-02 | 261 | WTG Scheduled Maintenance
43 | 2025-04-12 | 2026 | 2026 | 2025-04-01 | Year_3 | P-18 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity | 0.63403 | 0.63403 | 0.66875 | 0 | 0.83333 | 0.83333 | DTA Maintenance activity completed | Close | 0.018939 | P-07 | 377 | WTG Scheduled Maintenance
44 | 2025-04-12 | 2026 | 2026 | 2025-04-01 | Year_3 | P-51 | PWEPL | MSEDCL | 2.273% | 60 | Yaw limit switch activated | Yaw limit switch activated | 0.69444 | 0.69444 | 0.82639 | 0 | 3.1667 | 3.1667 | Cable Twist Release & Turbine Restored | Close | 0.07197 | P-52 | 1092 | WTG Breakdown Maintenance
45 | 2025-04-14 | 2026 | 2026 | 2025-04-01 | Year_3 | P-55 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Gearbox Oil & Main Bering Grease Sample Collection work | 0.43889 | 0.43889 | 0.50556 | 0 | 1.6 | 1.6 | OIL & Grease sample collection work completed | Close | 0.036364 | P-56 | 14 | WTG Scheduled Maintenance
46 | 2025-04-14 | 2026 | 2026 | 2025-04-01 | Year_3 | P-45 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Gearbox Oil & Main Bering Grease Sample Collection work | 0.56389 | 0.56389 | 0.60833 | 0 | 1.0667 | 1.0667 | OIL & Grease sample collection work completed | Close | 0.024242 | P-46 | 232 | WTG Scheduled Maintenance
47 | 2025-04-15 | 2026 | 2026 | 2025-04-01 | Year_3 | P-56 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity | 0.42292 | 0.42292 | 0.73611 | 0 | 7.5167 | 7.5167 | 12th Annual Maintenance Day 1 Activity completed | Close | 0.17083 | P-55 | 1493 | WTG Scheduled Maintenance
48 | 2025-04-15 | 2026 | 2026 | 2025-04-01 | Year_3 | P-43 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Hub door open | 0.69375 | 0.69375 | 0.71736 | 0 | 0.56667 | 0.56667 | hub door closing work complited | Close | 0.012879 | P-27 | 137 | WTG Breakdown Maintenance
49 | 2025-04-15 | 2026 | 2026 | 2025-04-01 | Year_3 | P-07 | PWEPL | MSEDCL | 2.273% | 430 | Yaw tooth sensor 1 timeout | Yaw tooth sensor 1 timeout | 0.73819 | 0.73819 | 0.77083 | 0 | 0.78333 | 0.78333 | Grease cleaned from yaw sensor, Yaw teeth, Pinion. | Close | 0.017803 | P-18 | 565 | WTG Breakdown Maintenance
50 | 2025-04-16 | 2026 | 2026 | 2025-04-01 | Year_3 | P-56 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity | 0.4375 | 0.4375 | 0.74375 | 0 | 7.35 | 7.35 | 12th Annual Maintenance Day 2 Activity completed | Close | 0.16705 | P-55 | 2179 | WTG Scheduled Maintenance
51 | 2025-04-16 | 2026 | 2026 | 2025-04-01 | Year_3 | P-38 | PWEPL | MSEDCL | 2.273% | 280 | Prepressure error, active brake | Hydraulic brake test Accumulater pressure error | 0.77778 | 0.77778 | 0.79306 | 0 | 0.36667 | 0.36667 | Accumulater reaplaced & turbine restored | Close | 0.0083333 | P-17 | 338 | WTG Breakdown Maintenance
52 | 2025-04-17 | 2026 | 2026 | 2025-04-01 | Year_3 | P-55 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity | 0.42361 | 0.42361 | 0.81667 | 0 | 9.4333 | 9.4333 | 12th Annual Maintenance Activity completed | Close | 0.21439 | P-56 | 3485 | WTG Scheduled Maintenance
53 | 2025-04-17 | 2026 | 2026 | 2025-04-01 | Year_3 | P-26 | PWEPL | MSEDCL | 2.273% | 123 | Generator carbon brush warn | Generator carbon brush warn | 0.70208 | 0.70208 | 0.73819 | 0 | 0.86667 | 0.86667 | generator carbon brush limit switch connection tight properly | Close | 0.019697 | P-25 | 280 | WTG Breakdown Maintenance
54 | 2025-04-18 | 2026 | 2026 | 2025-04-01 | Year_3 | P-45 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity | 0.42292 | 0.42292 | 0.79583 | 0 | 8.95 | 8.95 | 12th Annual Maintenance Activity completed | Close | 0.20341 | P-46 | 3194 | WTG Scheduled Maintenance
55 | 2025-04-18 | 2026 | 2026 | 2025-04-01 | Year_3 | P-51 | PWEPL | MSEDCL | 2.273% | 60 | Yaw limit switch activated | Yaw limit switch activated | 0.44653 | 0.44653 | 0.55486 | 0 | 2.6 | 2.6 | Cable Twist Release & Turbine Restored | Close | 0.059091 | P-52 | 81 | WTG Breakdown Maintenance
56 | 2025-04-18 | 2026 | 2026 | 2025-04-01 | Year_3 | P-23 | PWEPL | MSEDCL | 2.273% | CE100017 | UPS breakdown | UPS fault | 0.70208 | 0.70208 | 0.70833 | 0 | 0.15 | 0.15 | Replaced UPS Battery Bank | Close | 0.0034091 | P-22 | 164 | WTG Breakdown Maintenance
57 | 2025-04-19 | 2026 | 2026 | 2025-04-01 | Year_3 | P-46 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity | 0.40833 | 0.40833 | 0.76389 | 0 | 8.5333 | 8.5333 | 12th Annual Maintenance Activity completed | Close | 0.19394 | P-45 | 2942 | WTG Scheduled Maintenance
58 | 2025-04-20 | 2026 | 2026 | 2025-04-01 | Year_3 | P-52 | PWEPL | MSEDCL | 2.273% | 201 | PLC fault 24V Supply | IO Card 28V power supply failed | 0.39861 | 0.39861 | 0.41736 | 0 | 0.45 | 0.45 | Rebooted the PLC & reset at scada | Close | 0.010227 | P-51 | 0 | WTG Breakdown Maintenance
59 | 2025-04-21 | 2026 | 2026 | 2025-04-01 | Year_3 | P-10 | PWEPL | MSEDCL | 2.273% | 430 | Yaw tooth sensor 1 timeout | Yaw tooth sensor 1 timeout | 0.52917 | 0.52917 | 0.53264 | 0 | 0.083333 | 0.083333 | Rebooted the PLC & reset at scada | Close | 0.0018939 | P-09 | 7 | WTG Breakdown Maintenance
60 | 2025-04-22 | 2026 | 2026 | 2025-04-01 | Year_3 | P-47 | PWEPL | MSEDCL | 2.273% | 430 | Yaw tooth sensor 1 timeout | Grease on sensor | 0.34236 | 0.34236 | 0.36181 | 0 | 0.46667 | 0.46667 | Grease cleaned from yaw sensor, Yaw teeth, Pinion. | Close | 0.010606 | P-48 | 39 | WTG Breakdown Maintenance
61 | 2025-04-22 | 2026 | 2026 | 2025-04-01 | Year_3 | P-10 | PWEPL | MSEDCL | 2.273% | 430 | Yaw tooth sensor 1 timeout | Grease on sensor | 0.64861 | 0.64861 | 0.68681 | 0 | 0.91667 | 0.91667 | Grease cleaned from yaw sensor, Yaw teeth, Pinion. | Close | 0.020833 | P-09 | 249 | WTG Breakdown Maintenance
62 | 2025-04-22 | 2026 | 2026 | 2025-04-01 | Year_3 | P-26 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault | 0.027778 | 0.027778 | 0.036806 | 0 | 0.21667 | 0.21667 | Rebooted the PLC & reset at scada | Close | 0.0049242 | P-25 | 0 | WTG Breakdown Maintenance
63 | 2025-04-22 | 2026 | 2026 | 2025-04-01 | Year_3 | P-47 | PWEPL | MSEDCL | 2.273% | 430 | Yaw tooth sensor 1 timeout | Yaw tooth sensor 1 timeout | 0.27431 | 0.27431 | 0.29514 | 0 | 0.5 | 0.5 | Rebooted the PLC & reset at scada | Close | 0.011364 | P-48 | 61 | WTG Breakdown Maintenance
64 | 2025-04-22 | 2026 | 2026 | 2025-04-01 | Year_3 | P-10 | PWEPL | MSEDCL | 2.273% | 430 | Yaw tooth sensor 1 timeout | Yaw tooth sensor 1 timeout | 0.32431 | 0.32431 | 0.35903 | 0 | 0.83333 | 0.83333 | Rebooted the PLC & reset at scada | Close | 0.018939 | P-09 | 188 | WTG Breakdown Maintenance
65 | 2025-04-23 | 2026 | 2026 | 2025-04-01 | Year_3 | P-47 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity | 0.42292 | 0.42292 | 0.80556 | 0 | 9.1833 | 9.1833 | 12th Annual Maintenance Activity completed | Close | 0.20871 | P-48 | 2984 | WTG Scheduled Maintenance
66 | 2025-04-24 | 2026 | 2026 | 2025-04-01 | Year_3 | P-48 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity | 0.34514 | 0.34514 | 0.70139 | 0 | 8.55 | 8.55 | 12th Annual Maintenance Activity completed | Close | 0.19432 | P-42 | 1251 | WTG Scheduled Maintenance
67 | 2025-04-25 | 2026 | 2026 | 2025-04-01 | Year_3 | P-07 | PWEPL | MSEDCL | 2.273% | 60 | Yaw limit switch activated | Yaw limit switch activated | 0.39931 | 0.39931 | 0.53125 | 0 | 3.1667 | 3.1667 | Cable Twist Release & Turbine Restored | Close | 0.07197 | P-18 | 52 | WTG Breakdown Maintenance
68 | 2025-04-25 | 2026 | 2026 | 2025-04-01 | Year_3 | P-26 | PWEPL | MSEDCL | 2.273% | 60 | Yaw limit switch activated | Yaw limit switch activated | 0.37639 | 0.37639 | 0.42708 | 0 | 1.2167 | 1.2167 | Cable Twist Release & Turbine Restored | Close | 0.027652 | P-25 | 0 | WTG Breakdown Maintenance
69 | 2025-04-25 | 2026 | 2026 | 2025-04-01 | Year_3 | P-51 | PWEPL | MSEDCL | 2.273% | 60 | Yaw limit switch activated | Yaw limit switch activated | 0.40972 | 0.40972 | 0.42153 | 0 | 0.28333 | 0.28333 | Cable Twist Release & Turbine Restored | Close | 0.0064394 | P-52 | 0 | WTG Breakdown Maintenance
70 | 2025-04-25 | 2026 | 2026 | 2025-04-01 | Year_3 | P-42 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity | 0.41875 | 0.41875 | 0.75486 | 0 | 8.0667 | 8.0667 | 12th Annual Maintenance Activity completed | Close | 0.18333 | P-48 | 1670 | WTG Scheduled Maintenance
71 | 2025-04-25 | 2026 | 2026 | 2025-04-01 | Year_3 | P-47 | PWEPL | MSEDCL | 2.273% | 430 | Yaw tooth sensor 1 timeout | Yaw tooth sensor 1 timeout | 0.59722 | 0.59722 | 0.68958 | 0 | 2.2167 | 2.2167 | Yaw tooth sensor clean & Cable twist release & turbine restored | Close | 0.050379 | P-48 | 769 | WTG Breakdown Maintenance
72 | 2025-04-26 | 2026 | 2026 | 2025-04-01 | Year_3 | P-06 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity | 0.42292 | 0.42292 | 0.79444 | 0 | 8.9167 | 8.9167 | 12th Annual Maintenance Activity completed | Close | 0.20265 | P-41 | 2809 | WTG Scheduled Maintenance
73 | 2025-04-26 | 2026 | 2026 | 2025-04-01 | Year_3 | P-07 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Turbine Ispection | 0.49653 | 0.49653 | 0.54653 | 0 | 1.2 | 1.2 | Turbine Inspection Completed | Close | 0.027273 | P-18 | 167 | WTG Scheduled Maintenance
74 | 2025-04-27 | 2026 | 2026 | 2025-04-01 | Year_3 | P-41 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity | 0.42986 | 0.42986 | 0.71736 | 0 | 6.9 | 6.9 | 12th Annual Maintenance Activity completed | Close | 0.15682 | P-05 | 1170 | WTG Scheduled Maintenance
75 | 2025-04-28 | 2026 | 2026 | 2025-04-01 | Year_3 | P-05 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity | 0.43125 | 0.43125 | 0.78958 | 0 | 8.6 | 8.6 | 12th Annual Maintenance Activity completed | Close | 0.19545 | P-41 | 2101 | WTG Scheduled Maintenance
76 | 2025-04-28 | 2026 | 2026 | 2025-04-01 | Year_3 | P-51 | PWEPL | MSEDCL | 2.273% | 60 | Yaw limit switch activated | Yaw limit switch activated | 0.51389 | 0.51389 | 0.57639 | 0 | 1.5 | 1.5 | Cable Twist Release & Turbine Restored | Close | 0.034091 | P-52 | 96 | WTG Breakdown Maintenance
77 | 2025-04-29 | 2026 | 2026 | 2025-04-01 | Year_3 | P-40 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity | 0.36181 | 0.36181 | 0.69653 | 0 | 8.0333 | 8.0333 | 12th Annual Maintenance Activity completed | Close | 0.18258 | P-05 | 1659 | WTG Scheduled Maintenance
78 | 2025-04-29 | 2026 | 2026 | 2025-04-01 | Year_3 | P-34 | PWEPL | MSEDCL | 2.273% | 201 | IO Card 28V power supply failed | IO Card 28V power supply failed | 0.45903 | 0.45903 | 0.46319 | 0 | 0.1 | 0.1 | Rebooted the PLC & reset at scada | Close | 0.0022727 | P-04 | 0 | WTG Breakdown Maintenance
79 | 2025-04-30 | 2026 | 2026 | 2025-04-01 | Year_3 | P-12 | PWEPL | MSEDCL | 2.273% | 275 | Pitch thyristor 2 fault | Pitch Converter failure | 0.26389 | 0.26389 | 0.50417 | 0 | 5.7667 | 5.7667 | Replaced Pitch converter | Close | 0.13106 | P-11 | 354 | WTG Breakdown Maintenance
80 | 2025-04-30 | 2026 | 2026 | 2025-04-01 | Year_3 | P-07 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | DTA Maintenance | 0.51042 | 0.51042 | 0.54514 | 0 | 0.83333 | 0.83333 | DTA Maintenance activity completed | Close | 0.018939 | P-18 | 282 | WTG Scheduled Maintenance
81 | 2025-04-30 | 2026 | 2026 | 2025-04-01 | Year_3 | P-56 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | DTA Maintenance | 0.55208 | 0.55208 | 0.57778 | 0 | 0.61667 | 0.61667 | DTA Maintenance activity completed | Close | 0.014015 | P-55 | 235 | WTG Scheduled Maintenance
82 | 2025-04-30 | 2026 | 2026 | 2025-04-01 | Year_3 | P-55 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | DTA Maintenance | 0.62569 | 0.62569 | 0.65139 | 0 | 0.61667 | 0.61667 | DTA Maintenance activity completed | Close | 0.014015 | P-56 | 302 | WTG Scheduled Maintenance
83 | 2025-04-30 | 2026 | 2026 | 2025-04-01 | Year_3 | P-45 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | DTA Maintenance | 0.66319 | 0.66319 | 0.69375 | 0 | 0.73333 | 0.73333 | DTA Maintenance activity completed | Close | 0.016667 | P-46 | 470 | WTG Scheduled Maintenance
84 | 2025-04-30 | 2026 | 2026 | 2025-04-01 | Year_3 | P-46 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | DTA Maintenance | 0.69722 | 0.69722 | 0.72292 | 0 | 0.61667 | 0.61667 | DTA Maintenance activity completed | Close | 0.014015 | P-45 | 425 | WTG Scheduled Maintenance
85 | 2025-05-01 | 2026 | 2026 | 2025-05-01 | Year_3 | P-23 | PWEPL | MSEDCL | 2.273% | 157 | Secondary rotor brake does not close | Secondary rotor brake does not close | 0.38611 | 0.38611 | 0.39306 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | P-22 | 0 | WTG Breakdown Maintenance
86 | 2025-05-01 | 2026 | 2026 | 2025-05-01 | Year_3 | P-47 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | DTA Maintenance | 0.44028 | 0.44028 | 0.50833 | 0 | 1.6333 | 1.6333 | DTA Maintenance activity completed | Close | 0.037121 | P-48 | 23 | WTG Scheduled Maintenance
87 | 2025-05-01 | 2026 | 2026 | 2025-05-01 | Year_3 | P-48 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | DTA Maintenance | 0.51944 | 0.51944 | 0.55208 | 0 | 0.78333 | 0.78333 | DTA Maintenance activity completed | Close | 0.017803 | P-47 | 125 | WTG Scheduled Maintenance
88 | 2025-05-01 | 2026 | 2026 | 2025-05-01 | Year_3 | P-42 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | DTA Maintenance | 0.59792 | 0.59792 | 0.65139 | 0 | 1.2833 | 1.2833 | DTA Maintenance activity completed | Close | 0.029167 | P-48 | 291 | WTG Scheduled Maintenance
89 | 2025-05-02 | 2026 | 2026 | 2025-05-01 | Year_3 | P-18 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | A Q A Against PM Audit | 0.48472 | 0.48472 | 0.59167 | 0 | 2.5667 | 2.5667 | Audit work completed | Close | 0.058333 | P-07 | 196 | WTG Unscheduled Maintenance
90 | 2025-05-02 | 2026 | 2026 | 2025-05-01 | Year_3 | P-06 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | DTA Maintenance | 0.50347 | 0.50347 | 0.54792 | 0 | 1.0667 | 1.0667 | DTA Maintenance activity completed | Close | 0.024242 | P-41 | 2025 | WTG Scheduled Maintenance
91 | 2025-05-02 | 2026 | 2026 | 2025-05-01 | Year_3 | P-41 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | DTA Maintenance | 0.55278 | 0.55278 | 0.58958 | 0 | 0.88333 | 0.88333 | DTA Maintenance activity completed | Close | 0.020076 | P-05 | 167 | WTG Scheduled Maintenance
92 | 2025-05-02 | 2026 | 2026 | 2025-05-01 | Year_3 | P-05 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | DTA Maintenance | 0.63194 | 0.63194 | 0.66181 | 0 | 0.71667 | 0.71667 | DTA Maintenance activity completed | Close | 0.016288 | P-41 | 385 | WTG Scheduled Maintenance
93 | 2025-05-02 | 2026 | 2026 | 2025-05-01 | Year_3 | P-34 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | A Q A Against PM Audit | 0.65625 | 0.65625 | 0.73194 | 0 | 1.8167 | 1.8167 | Audit work completed | Close | 0.041288 | P-04 | 792 | WTG Unscheduled Maintenance
94 | 2025-05-02 | 2026 | 2026 | 2025-05-01 | Year_3 | P-40 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | DTA Maintenance | 0.66944 | 0.66944 | 0.69722 | 0 | 0.66667 | 0.66667 | DTA Maintenance activity completed | Close | 0.015152 | P-05 | 377 | WTG Scheduled Maintenance
95 | 2025-05-03 | 2026 | 2026 | 2025-05-01 | Year_3 | P-42 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | A Q A Against PM Audit | 0.475 | 0.475 | 0.58542 | 0 | 2.65 | 2.65 | Audit work completed | Close | 0.060227 | P-48 | 591 | WTG Unscheduled Maintenance
96 | 2025-05-03 | 2026 | 2026 | 2025-05-01 | Year_3 | P-04 | PWEPL | MSEDCL | 2.273% | 142 | Line CCU collective faults | Line CCU Collective faults | 0.7375 | 0.7375 | 0.75 | 0 | 0.3 | 0.3 | Hard Rebooted Turbine from down tower assembly | Close | 0.0068182 | P-22 | 102 | WTG Breakdown Maintenance
97 | 2025-05-05 | 2026 | 2026 | 2025-05-01 | Year_3 | P-20 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Pitch Drive Oil replacement work | 0.475 | 0.475 | 0.58889 | 0 | 2.7333 | 2.7333 | Pitch Motor Oil replacement work done | Close | 0.062121 | P-38 | 566 | WTG Unscheduled Maintenance
98 | 2025-05-05 | 2026 | 2026 | 2025-05-01 | Year_3 | P-51 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | CBM Anomolies | 0.49653 | 0.49653 | 0.57083 | 0 | 1.7833 | 1.7833 | CBM sensor interchange & turbine restored | Close | 0.04053 | P-52 | 404 | WTG Unscheduled Maintenance
99 | 2025-05-05 | 2026 | 2026 | 2025-05-01 | Year_3 | P-08 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Pitch Drive Oil replacement work | 0.625 | 0.625 | 0.73056 | 0 | 2.5333 | 2.5333 | Pitch Motor Oil replacement work done | Close | 0.057576 | P-25 | 1483 | WTG Unscheduled Maintenance
100 | 2025-05-06 | 2026 | 2026 | 2025-05-01 | Year_3 | P-34 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Pitch Drive Oil replacement work | 0.425 | 0.425 | 0.49653 | 0 | 1.7167 | 1.7167 | Pitch Motor Oil replacement work done | Close | 0.039015 | P-04 | 3 | WTG Unscheduled Maintenance
101 | 2025-05-08 | 2026 | 2026 | 2025-05-01 | Year_3 | P-26 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work | 0.35625 | 0.35625 | 0.42639 | 0 | 1.6833 | 1.6833 | Manual stop for Foundation Pressure Grouting work | Close | 0.038258 | P-25 | 983 | WTG Unscheduled Maintenance
102 | 2025-05-08 | 2026 | 2026 | 2025-05-01 | Year_3 | P-37 | PWEPL | MSEDCL | 2.273% | 142 | Line CCU collective faults | Line CCU collective faults | 0.39722 | 0.39722 | 0.44444 | 0 | 1.1333 | 1.1333 | Q1 braker reset | Close | 0.025758 | P-32 | 715 | WTG Breakdown Maintenance
103 | 2025-05-08 | 2026 | 2026 | 2025-05-01 | Year_3 | P-15 | PWEPL | MSEDCL | 2.273% | 338 | Rotor CCU temperature warning | Rotor CCU temperature warning | 0.42847 | 0.42847 | 0.45972 | 0 | 0.75 | 0.75 | Coolent Top up & turbine restored | Close | 0.017045 | P-14 | 1083 | WTG Breakdown Maintenance
104 | 2025-05-08 | 2026 | 2026 | 2025-05-01 | Year_3 | P-26 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work | 0.65972 | 0.65972 | 0.99931 | 0 | 8.15 | 8.15 | Foundation Pressure Grouting work completed,waiting for curing | Close | 0.18523 | P-25 | 4762 | WTG Unscheduled Maintenance
105 | 2025-05-08 | 2026 | 2026 | 2025-05-01 | Year_3 | P-34 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Hub door open | 0.74514 | 0.74514 | 0.76111 | 0 | 0.38333 | 0.38333 | hub door closing work completed | Close | 0.0087121 | P-04 | 603 | WTG Unscheduled Maintenance
106 | 2025-05-09 | 2026 | 2026 | 2025-05-01 | Year_3 | P-26 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work | 0 | 0 | 0.67014 | 0 | 16.0833 | 16.0833 | Foundation Pressure Grouting work completed | Close | 0.36553 | P-27 | 3197 | WTG Unscheduled Maintenance
107 | 2025-05-09 | 2026 | 2026 | 2025-05-01 | Year_3 | P-37 | PWEPL | MSEDCL | 2.273% | 431 | Yaw tooth sensor 2 timeout | Yaw tooth sensor 2 timeout | 0.29306 | 0.29306 | 0.32292 | 0 | 0.71667 | 0.71667 | Yaw tooth sensor clean & turbine restored | Close | 0.016288 | P-32 | 219 | WTG Breakdown Maintenance
108 | 2025-05-09 | 2026 | 2026 | 2025-05-01 | Year_3 | P-25 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work | 0.36319 | 0.36319 | 0.99931 | 0 | 15.2667 | 15.2667 | Foundation Pressure Grouting work completed,waiting for curing | Close | 0.34697 | P-08 | 3034 | WTG Unscheduled Maintenance
109 | 2025-05-09 | 2026 | 2026 | 2025-05-01 | Year_3 | P-27 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work | 0.53264 | 0.53264 | 0.99931 | 0 | 11.2 | 11.2 | Foundation Pressure Grouting work completed,waiting for curing | Close | 0.25455 | P-28 | 2226 | WTG Unscheduled Maintenance
110 | 2025-05-09 | 2026 | 2026 | 2025-05-01 | Year_3 | P-14 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work | 0.73542 | 0.73542 | 0.99931 | 0 | 6.3333 | 6.3333 | Foundation Pressure Grouting work completed,waiting for curing | Close | 0.14394 | P-13 | 1259 | WTG Unscheduled Maintenance
111 | 2025-05-10 | 2026 | 2026 | 2025-05-01 | Year_3 | P-25 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work | 0 | 0 | 0.50972 | 0 | 12.2333 | 12.2333 | Foundation Pressure Grouting work completed | Close | 0.27803 | P-26 | 1809 | WTG Unscheduled Maintenance
112 | 2025-05-10 | 2026 | 2026 | 2025-05-01 | Year_3 | P-27 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work | 0 | 0 | 0.45764 | 0 | 10.9833 | 10.9833 | Foundation Pressure Grouting work completed | Close | 0.24962 | P-26 | 1624 | WTG Unscheduled Maintenance
113 | 2025-05-10 | 2026 | 2026 | 2025-05-01 | Year_3 | P-14 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work | 0 | 0 | 0.74375 | 0 | 17.85 | 17.85 | Foundation Pressure Grouting work completed | Close | 0.40568 | P-13 | 2639 | WTG Unscheduled Maintenance
114 | 2025-05-10 | 2026 | 2026 | 2025-05-01 | Year_3 | P-23 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work | 0.37292 | 0.37292 | 0.99931 | 0 | 15.0333 | 15.0333 | Foundation Pressure Grouting work completed,waiting for curing | Close | 0.34167 | P-22 | 2223 | WTG Unscheduled Maintenance
115 | 2025-05-10 | 2026 | 2026 | 2025-05-01 | Year_3 | P-40 | PWEPL | MSEDCL | 2.273% | 106 | Converter rotor current fault | Converter rotor current fault | 0.56597 | 0.56597 | 0.64514 | 0 | 1.9 | 1.9 | Replaced WEOR card | Close | 0.043182 | P-05 | 70 | WTG Breakdown Maintenance
116 | 2025-05-10 | 2026 | 2026 | 2025-05-01 | Year_3 | P-37 | PWEPL | MSEDCL | 2.273% | 431 | Yaw tooth sensor 2 timeout | Yaw tooth sensor 2 timeout | 0.77708 | 0.77708 | 0.82986 | 0 | 1.2667 | 1.2667 | Yaw tooth sensor clean & Gap set & turbine restored | Close | 0.028788 | P-32 | 82 | WTG Breakdown Maintenance
117 | 2025-05-11 | 2026 | 2026 | 2025-05-01 | Year_3 | P-23 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work | 0 | 0 | 0.52639 | 0 | 12.6333 | 12.6333 | Foundation Pressure Grouting work completed | Close | 0.28712 | P-22 | 1293 | WTG Unscheduled Maintenance
118 | 2025-05-11 | 2026 | 2026 | 2025-05-01 | Year_3 | P-50 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work | 0.38958 | 0.38958 | 0.99931 | 0 | 14.6333 | 14.6333 | Foundation Pressure Grouting work completed,waiting for curing | Close | 0.33258 | P-51 | 1498 | WTG Unscheduled Maintenance
119 | 2025-05-11 | 2026 | 2026 | 2025-05-01 | Year_3 | P-52 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work | 0.57292 | 0.57292 | 0.99931 | 0 | 10.2333 | 10.2333 | Foundation Pressure Grouting work completed,waiting for curing | Close | 0.23258 | P-51 | 1048 | WTG Unscheduled Maintenance
120 | 2025-05-12 | 2026 | 2026 | 2025-05-01 | Year_3 | P-50 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work | 0 | 0 | 0.34444 | 0 | 8.2667 | 8.2667 | Foundation Pressure Grouting work completed | Close | 0.18788 | P-51 | 718 | WTG Unscheduled Maintenance
121 | 2025-05-12 | 2026 | 2026 | 2025-05-01 | Year_3 | P-52 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work | 0 | 0 | 0.34444 | 0 | 8.2667 | 8.2667 | Foundation Pressure Grouting work completed | Close | 0.18788 | P-51 | 719 | WTG Unscheduled Maintenance
122 | 2025-05-12 | 2026 | 2026 | 2025-05-01 | Year_3 | P-52 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work | 0.60694 | 0.60694 | 0.67361 | 0 | 1.6 | 1.6 | Foundation Pressure Grouting work completed | Close | 0.036364 | P-51 | 139 | WTG Unscheduled Maintenance
123 | 2025-05-12 | 2026 | 2026 | 2025-05-01 | Year_3 | P-02 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work | 0.37986 | 0.37986 | 0.99931 | 0 | 14.8667 | 14.8667 | Foundation Pressure Grouting work completed,waiting for curing | Close | 0.33788 | P-18 | 1292 | WTG Unscheduled Maintenance
124 | 2025-05-12 | 2026 | 2026 | 2025-05-01 | Year_3 | P-13 | PWEPL | MSEDCL | 2.273% | 60 | Yaw limit switch activated | Yaw limit switch activated | 0.41111 | 0.41111 | 0.50139 | 0 | 2.1667 | 2.1667 | Cable Twist Release & Turbine Restored | Close | 0.049242 | P-12 | 0 | WTG Breakdown Maintenance
125 | 2025-05-12 | 2026 | 2026 | 2025-05-01 | Year_3 | P-26 | PWEPL | MSEDCL | 2.273% | 60 | Yaw limit switch activated | Yaw limit switch activated | 0.38472 | 0.38472 | 0.41319 | 0 | 0.68333 | 0.68333 | Cable Twist Release & Turbine Restored | Close | 0.01553 | P-25 | 0 | WTG Breakdown Maintenance
126 | 2025-05-12 | 2026 | 2026 | 2025-05-01 | Year_3 | P-41 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work | 0.64097 | 0.64097 | 0.67986 | 0 | 0.93333 | 0.93333 | Foundation Pressure Grouting work completed,waiting for curing | Close | 0.021212 | P-05 | 89 | WTG Unscheduled Maintenance
127 | 2025-05-12 | 2026 | 2026 | 2025-05-01 | Year_3 | P-41 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work | 0.76389 | 0.76389 | 0.99931 | 0 | 5.65 | 5.65 | Foundation Pressure Grouting work completed,waiting for curing | Close | 0.12841 | P-05 | 483 | WTG Unscheduled Maintenance
128 | 2025-05-12 | 2026 | 2026 | 2025-05-01 | Year_3 | P-47 | PWEPL | MSEDCL | 2.273% | 142 | Line CCU collective faults | Line CCU collective faults | 0.65764 | 0.65764 | 0.67986 | 0 | 0.53333 | 0.53333 | Circuit braker tripped so reset breaker | Close | 0.012121 | P-48 | 545 | WTG Breakdown Maintenance
129 | 2025-05-12 | 2026 | 2026 | 2025-05-01 | Year_3 | P-37 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault | 0.60694 | 0.60694 | 0.62639 | 0 | 0.46667 | 0.46667 | Rebooted the PLC & reset at scada | Close | 0.010606 | P-32 | 0 | WTG Breakdown Maintenance
130 | 2025-05-13 | 2026 | 2026 | 2025-05-01 | Year_3 | P-02 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work | 0 | 0 | 0.41667 | 0 | 10 | 10 | Foundation Pressure Grouting work completed,waiting for curing | Close | 0.22727 | P-18 | 787 | WTG Unscheduled Maintenance
131 | 2025-05-13 | 2026 | 2026 | 2025-05-01 | Year_3 | P-02 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work | 0.69167 | 0.69167 | 0.70486 | 0 | 0.31667 | 0.31667 | Foundation Pressure Grouting work completed | Close | 0.007197 | P-18 | 25 | WTG Unscheduled Maintenance
132 | 2025-05-13 | 2026 | 2026 | 2025-05-01 | Year_3 | P-41 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work | 0 | 0 | 0.41667 | 0 | 10 | 10 | Foundation Pressure Grouting work completed,waiting for curing | Close | 0.22727 | P-05 | 787 | WTG Unscheduled Maintenance
133 | 2025-05-13 | 2026 | 2026 | 2025-05-01 | Year_3 | P-41 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work | 0.69167 | 0.69167 | 0.99931 | 0 | 7.3833 | 7.3833 | Foundation Pressure Grouting work completed,waiting for curing | Close | 0.1678 | P-05 | 581 | WTG Unscheduled Maintenance
134 | 2025-05-13 | 2026 | 2026 | 2025-05-01 | Year_3 | P-43 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work | 0.64375 | 0.64375 | 0.99931 | 0 | 8.5333 | 8.5333 | Foundation Pressure Grouting work completed,waiting for curing | Close | 0.19394 | P-27 | 672 | WTG Unscheduled Maintenance
135 | 2025-05-13 | 2026 | 2026 | 2025-05-01 | Year_3 | P-46 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault | 0.69861 | 0.69861 | 0.71528 | 0 | 0.4 | 0.4 | Rebooted the PLC & reset at scada | Close | 0.0090909 | P-45 | 213 | WTG Breakdown Maintenance
136 | 2025-05-14 | 2026 | 2026 | 2025-05-01 | Year_3 | P-41 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work | 0 | 0 | 0.29167 | 0 | 7 | 7 | Foundation Pressure Grouting work completed | Close | 0.15909 | P-05 | 649 | WTG Unscheduled Maintenance
137 | 2025-05-14 | 2026 | 2026 | 2025-05-01 | Year_3 | P-43 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work | 0 | 0 | 0.79653 | 0 | 19.1167 | 19.1167 | Foundation Pressure Grouting work completed | Close | 0.43447 | P-27 | 1771 | WTG Unscheduled Maintenance
138 | 2025-05-14 | 2026 | 2026 | 2025-05-01 | Year_3 | P-05 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work | 0.37569 | 0.37569 | 0.52014 | 0 | 3.4667 | 3.4667 | Foundation Pressure Grouting work completed,waiting for curing | Close | 0.078788 | P-41 | 322 | WTG Unscheduled Maintenance
139 | 2025-05-14 | 2026 | 2026 | 2025-05-01 | Year_3 | P-05 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work | 0.75903 | 0.75903 | 0.99931 | 0 | 5.7667 | 5.7667 | Foundation Pressure Grouting work completed,waiting for curing | Close | 0.13106 | P-41 | 554 | WTG Unscheduled Maintenance
140 | 2025-05-14 | 2026 | 2026 | 2025-05-01 | Year_3 | P-04 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work | 0.64444 | 0.64444 | 0.99931 | 0 | 8.5167 | 8.5167 | Foundation Pressure Grouting work completed,waiting for curing | Close | 0.19356 | P-22 | 789 | WTG Unscheduled Maintenance
141 | 2025-05-14 | 2026 | 2026 | 2025-05-01 | Year_3 | P-52 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault | 0.64722 | 0.64722 | 0.65694 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | P-51 | 0 | WTG Breakdown Maintenance
142 | 2025-05-14 | 2026 | 2026 | 2025-05-01 | Year_3 | P-26 | PWEPL | MSEDCL | 2.273% | 60 | Yaw limit switch activated | Yaw limit switch activated | 0.40833 | 0.40833 | 0.49306 | 0 | 2.0333 | 2.0333 | Cable Twist Release & Turbine Restored | Close | 0.046212 | P-27 | 0 | WTG Breakdown Maintenance
143 | 2025-05-15 | 2026 | 2026 | 2025-05-01 | Year_3 | P-05 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work | 0 | 0 | 0.35278 | 0 | 8.4667 | 8.4667 | Foundation Pressure Grouting work completed | Close | 0.19242 | P-22 | 1504 | WTG Unscheduled Maintenance
144 | 2025-05-15 | 2026 | 2026 | 2025-05-01 | Year_3 | P-04 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work | 0 | 0 | 0.675 | 0 | 16.2 | 16.2 | Foundation Pressure Grouting work completed | Close | 0.36818 | P-41 | 786 | WTG Unscheduled Maintenance
145 | 2025-05-15 | 2026 | 2026 | 2025-05-01 | Year_3 | P-18 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault | 0.65208 | 0.65208 | 0.66111 | 0 | 0.21667 | 0.21667 | Rebooted the PLC & reset at scada | Close | 0.0049242 | P-01 | 17 | WTG Breakdown Maintenance
146 | 2025-05-15 | 2026 | 2026 | 2025-05-01 | Year_3 | P-32 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault | 0.65208 | 0.65208 | 0.65903 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | P-37 | 15 | WTG Breakdown Maintenance
147 | 2025-05-16 | 2026 | 2026 | 2025-05-01 | Year_3 | P-28 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault | 0.66597 | 0.66597 | 0.67569 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | P-27 | 0 | WTG Breakdown Maintenance
148 | 2025-05-16 | 2026 | 2026 | 2025-05-01 | Year_3 | P-40 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault | 0.67361 | 0.67361 | 0.68333 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | P-05 | 33 | WTG Breakdown Maintenance
149 | 2025-05-17 | 2026 | 2026 | 2025-05-01 | Year_3 | P-15 | PWEPL | MSEDCL | 2.273% | 86 | Braking pad of secondary brake worn out | Secondary Brake Pad worn | 0.48958 | 0.48958 | 0.68819 | 0 | 4.7667 | 4.7667 | Brake Pad replaced | Close | 0.10833 | P-16 | 949 | WTG Breakdown Maintenance
150 | 2025-05-19 | 2026 | 2026 | 2025-05-01 | Year_3 | P-27 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Slipring replacement work | 0.61111 | 0.61111 | 0.76458 | 0 | 3.6833 | 3.6833 | Slipring replacement work completed | Close | 0.083712 | P-28 | 274 | WTG Breakdown Maintenance
151 | 2025-05-20 | 2026 | 2026 | 2025-05-01 | Year_3 | P-38 | PWEPL | MSEDCL | 2.273% | 275 | Pitch thyristor 2 fault | Pitch thyristor 2 fault | 0.75347 | 0.75347 | 0.84306 | 0 | 2.15 | 2.15 | Hard Rebooted Turbine from down tower assembly | Close | 0.048864 | P-17 | 2367 | WTG Breakdown Maintenance
152 | 2025-05-23 | 2026 | 2026 | 2025-05-01 | Year_3 | P-48 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | QHSE Turbine Audit | 0.56667 | 0.56667 | 0.65764 | 0 | 2.1833 | 2.1833 | QHSE turbine audit completed | Close | 0.049621 | P-47 | 227 | WTG Unscheduled Maintenance
153 | 2025-05-23 | 2026 | 2026 | 2025-05-01 | Year_3 | P-34 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | QHSE Turbine Audit | 0.50069 | 0.50069 | 0.56806 | 0 | 1.6167 | 1.6167 | QHSE turbine audit completed | Close | 0.036742 | P-04 | 307 | WTG Unscheduled Maintenance
154 | 2025-05-23 | 2026 | 2026 | 2025-05-01 | Year_3 | P-15 | PWEPL | MSEDCL | 2.273% |  | tower vibration sensor failure | tower vibration sensor failure | 0.97778 | 0.97778 | 0.99931 | 0 | 0.51667 | 0.51667 | Hard Rebooted Turbine from down tower assembly | Close | 0.011742 | P-14 | 48 | WTG Breakdown Maintenance
155 | 2025-05-23 | 2026 | 2026 | 2025-05-01 | Year_3 | P-56 | PWEPL | MSEDCL | 2.273% | 275 | Pitch thyristor 2 fault | Pitch thyristor 2 fault | 0.62083 | 0.62083 | 0.62639 | 0 | 0.13333 | 0.13333 | Rebooted the PLC & reset at scada | Close | 0.0030303 | P-55 | 0 | WTG Breakdown Maintenance
156 | 2025-05-24 | 2026 | 2026 | 2025-05-01 | Year_3 | P-14 | PWEPL | MSEDCL | 2.273% | 60 | Yaw limit switch activated | Yaw limit switch activated | 0.52708 | 0.52708 | 0.66111 | 0 | 3.2167 | 3.2167 | Cable Twist Release & Turbine Restored | Close | 0.073106 | P-13 | 0 | WTG Breakdown Maintenance
157 | 2025-05-24 | 2026 | 2026 | 2025-05-01 | Year_3 | P-19 | PWEPL | MSEDCL | 2.273% | 102 | Top box motor protection alarm | Top box motor protection alarm | 0.58056 | 0.58056 | 0.65833 | 0 | 1.8667 | 1.8667 | Replaced WETB card. | Close | 0.042424 | P-20 | 179 | WTG Breakdown Maintenance
158 | 2025-05-25 | 2026 | 2026 | 2025-05-01 | Year_3 | P-13 | PWEPL | MSEDCL | 2.273% | 54 | Anemometer failure | Anemometer failure | 0.42014 | 0.42014 | 0.82986 | 0 | 9.8333 | 9.8333 | Anemometer signal communucating cable replaced | Close | 0.22348 | P-12 | 3776 | WTG Breakdown Maintenance
159 | 2025-05-26 | 2026 | 2026 | 2025-05-01 | Year_3 | P-31 | PWEPL | MSEDCL | 2.273% | 269 | Turbine Communication fault | Weca Card hang | 0.27569 | 0.27569 | 0.38819 | 0 | 2.7 | 2.7 | Hard Rebooted Turbine from down tower assembly | Close | 0.061364 | P-03 | 2018 | WTG Breakdown Maintenance
160 | 2025-05-26 | 2026 | 2026 | 2025-05-01 | Year_3 | P-52 | PWEPL | MSEDCL | 2.273% | 141 | Rotor CCU collective faults | Rotor CCU collective faults | 0.27569 | 0.27569 | 0.36458 | 0 | 2.1333 | 2.1333 | Hard Rebooted Turbine from down tower assembly | Close | 0.048485 | P-51 | 1861 | WTG Breakdown Maintenance
161 | 2025-05-26 | 2026 | 2026 | 2025-05-01 | Year_3 | P-56 | PWEPL | MSEDCL | 2.273% | 142 | Line CCU collective faults | Line CCU collective faults | 0.79861 | 0.79861 | 0.81944 | 0 | 0.5 | 0.5 | Rebooted the PLC & reset at scada | Close | 0.011364 | P-55 | 667 | WTG Breakdown Maintenance
162 | 2025-05-26 | 2026 | 2026 | 2025-05-01 | Year_3 | P-17 | PWEPL | MSEDCL | 2.273% | 269 | Turbine Communication fault | Wema Card failure | 0.90972 | 0.90972 | 0.95417 | 0 | 1.0667 | 1.0667 | Replaced WEMA card. | Close | 0.024242 | P-16 | 290 | WTG Breakdown Maintenance
163 | 2025-05-28 | 2026 | 2026 | 2025-05-01 | Year_3 | P-48 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Gearbox inspection | 0.60833 | 0.60833 | 0.65486 | 0 | 1.1167 | 1.1167 | Thermobypass valve replaced & gearbox inspection done. | Close | 0.025379 | P-47 | 973 | WTG Breakdown Maintenance
164 | 2025-05-28 | 2026 | 2026 | 2025-05-01 | Year_3 | P-09 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Gearbox inspection | 0.70347 | 0.70347 | 0.75139 | 0 | 1.15 | 1.15 | Thermobypass valve replaced & gearbox inspection done. | Close | 0.026136 | P-8 | 544 | WTG Breakdown Maintenance
165 | 2025-05-29 | 2026 | 2026 | 2025-05-01 | Year_3 | P-27 | PWEPL | MSEDCL | 2.273% | 275 | Pitch thyristor 2 fault | Pitch thyristor 2 fault | 0.91736 | 0.91736 | 0.99653 | 0 | 1.9 | 1.9 | Pitch Encoder clean properly & turbine restored | Close | 0.043182 | P-28 | 1947 | WTG Breakdown Maintenance
166 | 2025-05-30 | 2026 | 2026 | 2025-05-01 | Year_3 | P-13 | PWEPL | MSEDCL | 2.273% | 275 | Pitch thyristor 2 fault | Pitch thyristor 2 fault | 0.49861 | 0.49861 | 0.58333 | 0 | 2.0333 | 2.0333 | Pitch Encoder clean properly & turbine restored | Close | 0.046212 | P-12 | 2769 | WTG Breakdown Maintenance
167 | 2025-05-30 | 2026 | 2026 | 2025-05-01 | Year_3 | P-13 | PWEPL | MSEDCL | 2.273% | 142 | Line CCU collective faults | Line CCU collective faults | 0.58333 | 0.58333 | 0.61458 | 0 | 0.75 | 0.75 | Q1 braker reset | Close | 0.017045 | P-12 | 1184 | WTG Breakdown Maintenance
168 | 2025-05-30 | 2026 | 2026 | 2025-05-01 | Year_3 | P-13 | PWEPL | MSEDCL | 2.273% | 142 | Line CCU collective faults | Line CCU collective faults | 0.92014 | 0.92014 | 0.93472 | 0 | 0.35 | 0.35 | Q1 braker reset | Close | 0.0079545 | P-12 | 412 | WTG Breakdown Maintenance
169 | 2025-06-02 | 2026 | 2026 | 2025-06-01 | Year_3 | P-15 | PWEPL | MSEDCL | 2.273% | 120 | Pitch controller communication fault | Pitch controller communication fault | 0.25069 | 0.25069 | 0.57292 | 0 | 7.7333 | 7.7333 | Replaced AEPC card & Top Box to Slipring Lane cable & turbine restored | Close | 0.17576 | P-14 | 3830 | WTG Breakdown Maintenance
170 | 2025-06-02 | 2026 | 2026 | 2025-06-01 | Year_3 | P-14 | PWEPL | MSEDCL | 2.273% | 142 | Line CCU collective faults | Line CCU collective faults | 0.58264 | 0.58264 | 0.59722 | 0 | 0.35 | 0.35 | Rebooted the PLC & reset at scada | Close | 0.0079545 | P-13 | 367 | WTG Breakdown Maintenance
171 | 2025-06-02 | 2026 | 2026 | 2025-06-01 | Year_3 | P-31 | PWEPL | MSEDCL | 2.273% | 52 | Gearbox oil ressure too lo | Gearbox oil pressure too low | 0.66042 | 0.66042 | 0.82778 | 0 | 4.0167 | 4.0167 | Radiator motor replaced | Close | 0.091288 | P-03 | 1908 | WTG Breakdown Maintenance
172 | 2025-06-03 | 2026 | 2026 | 2025-06-01 | Year_3 | P-28 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Yaw puck Pistons replacement | 0.51111 | 0.51111 | 0.75 | 0 | 5.7333 | 5.7333 | Yaw Puck Pistons 6 nos replaced | Close | 0.1303 | P-27 | 2526 | WTG Unscheduled Maintenance
173 | 2025-06-04 | 2026 | 2026 | 2025-06-01 | Year_3 | P-28 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Yaw puck Pistons replacement | 0.40972 | 0.40972 | 0.74931 | 0 | 8.15 | 8.15 | Yaw Puck Pistons 3 nos replaced | Close | 0.18523 | P-27 | 4448 | WTG Unscheduled Maintenance
174 | 2025-06-04 | 2026 | 2026 | 2025-06-01 | Year_3 | P-26 | PWEPL | MSEDCL | 2.273% | 201 | PLC fault 24V Supply | WET B card failure | 0.72778 | 0.72778 | 0.78611 | 0 | 1.4 | 1.4 | Replaced WET B card | Close | 0.031818 | P-25 | 1349 | WTG Breakdown Maintenance
175 | 2025-06-04 | 2026 | 2026 | 2025-06-01 | Year_3 | P-38 | PWEPL | MSEDCL | 2.273% | 134 | Battery charging voltage not OK | Battery charging voltage not OK | 0.50764 | 0.50764 | 0.56944 | 0 | 1.4833 | 1.4833 | Rebooted the PLC & reset at scada | Close | 0.033712 | P-17 | 403 | WTG Breakdown Maintenance
176 | 2025-06-05 | 2026 | 2026 | 2025-06-01 | Year_3 | P-38 | PWEPL | MSEDCL | 2.273% | 134 | Battery charging voltage not OK | Battery charging voltage not OK | 0.3125 | 0.3125 | 0.37083 | 0 | 1.4 | 1.4 | Axis 3 Pitch Battery replaced | Close | 0.031818 | P-17 | 128 | WTG Breakdown Maintenance
177 | 2025-06-05 | 2026 | 2026 | 2025-06-01 | Year_3 | P-28 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Yaw puck Pistons replacement | 0.49097 | 0.49097 | 0.78264 | 0 | 7 | 7 | Yaw Puck Pistons 6 nos replaced | Close | 0.15909 | P-27 | 2265 | WTG Unscheduled Maintenance
178 | 2025-06-06 | 2026 | 2026 | 2025-06-01 | Year_3 | P-13 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Yaw puck Pistons replacement | 0.46111 | 0.46111 | 0.66528 | 0 | 4.9 | 4.9 | Yaw Puck Pistons 12 nos replaced | Close | 0.11136 | P-12 | 832 | WTG Unscheduled Maintenance
179 | 2025-06-06 | 2026 | 2026 | 2025-06-01 | Year_3 | P-42 | PWEPL | MSEDCL | 2.273% | 276 | Pitch thyristor 3 fault | Pitch thyristor 3 fault | 0.65417 | 0.65417 | 0.85972 | 0 | 4.9333 | 4.9333 | Replaced Pitch Encoder & Carbon Brushes | Close | 0.11212 | P-48 | 2441 | WTG Breakdown Maintenance
180 | 2025-06-07 | 2026 | 2026 | 2025-06-01 | Year_3 | P-13 | PWEPL | MSEDCL | 2.273% | 275 | Pitch thyristor 2 fault | Pitch thyristor 2 fault | 0.34167 | 0.34167 | 0.48056 | 0 | 3.3333 | 3.3333 | Pitch Encoder replaced | Close | 0.075758 | P-12 | 147 | WTG Breakdown Maintenance
181 | 2025-06-07 | 2026 | 2026 | 2025-06-01 | Year_3 | P-34 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Audit pending point closing work | 0.59236 | 0.59236 | 0.69931 | 0 | 2.5667 | 2.5667 | Manual stop for Customer Audit pending point closing work | Close | 0.058333 | P-04 | 692 | WTG Unscheduled Maintenance
182 | 2025-06-08 | 2026 | 2026 | 2025-06-01 | Year_3 | P-12 | PWEPL | MSEDCL | 2.273% | 142 | Line CCU collective faults | Line CCU collective faults | 0.44236 | 0.44236 | 0.44583 | 0 | 0.083333 | 0.083333 | Rebooted the PLC & reset at scada | Close | 0.0018939 | P-11 | 45 | WTG Breakdown Maintenance
183 | 2025-06-08 | 2026 | 2026 | 2025-06-01 | Year_3 | P-48 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Audit pending point closing work | 0.57292 | 0.57292 | 0.61528 | 0 | 1.0167 | 1.0167 | Manual stop for Customer Audit pending point closing work | Close | 0.023106 | P-47 | 562 | WTG Unscheduled Maintenance
184 | 2025-06-09 | 2026 | 2026 | 2025-06-01 | Year_3 | P-34 | PWEPL | MSEDCL | 2.273% | 201 | IO Card 28V power supply failed | IO Card 28V power supply failed | 0.89583 | 0.89583 | 0.90347 | 0 | 0.18333 | 0.18333 | Rebooted the PLC & reset at scada | Close | 0.0041667 | P-04 | 172 | WTG Breakdown Maintenance
185 | 2025-06-10 | 2026 | 2026 | 2025-06-01 | Year_3 | P-26 | PWEPL | MSEDCL | 2.273% | 201 | IO Card 28V power supply failed | IO Card 28V power supply failed | 0.57639 | 0.57639 | 0.59028 | 0 | 0.33333 | 0.33333 | Hard Rebooted Turbine from down tower assembly | Close | 0.0075758 | P-25 | 98 | WTG Breakdown Maintenance
186 | 2025-06-10 | 2026 | 2026 | 2025-06-01 | Year_3 | P-26 | PWEPL | MSEDCL | 2.273% | 201 | IO Card 28V power supply failed | WET B card failure | 0.67361 | 0.67361 | 0.72708 | 0 | 1.2833 | 1.2833 | Replaced WET B card | Close | 0.029167 | P-25 | 1117 | WTG Breakdown Maintenance
187 | 2025-06-10 | 2026 | 2026 | 2025-06-01 | Year_3 | P-17 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault | 0.57083 | 0.57083 | 0.57986 | 0 | 0.21667 | 0.21667 | Rebooted the PLC & reset at scada | Close | 0.0049242 | P-16 | 2 | WTG Breakdown Maintenance
188 | 2025-06-10 | 2026 | 2026 | 2025-06-01 | Year_3 | P-19 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault | 0.57083 | 0.57083 | 0.57639 | 0 | 0.13333 | 0.13333 | Rebooted the PLC & reset at scada | Close | 0.0030303 | P-17 | 94 | WTG Breakdown Maintenance
189 | 2025-06-10 | 2026 | 2026 | 2025-06-01 | Year_3 | P-20 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault | 0.57083 | 0.57083 | 0.57708 | 0 | 0.15 | 0.15 | Rebooted the PLC & reset at scada | Close | 0.0034091 | P-19 | 106 | WTG Breakdown Maintenance
190 | 2025-06-10 | 2026 | 2026 | 2025-06-01 | Year_3 | P-38 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault | 0.57083 | 0.57083 | 0.57708 | 0 | 0.15 | 0.15 | Rebooted the PLC & reset at scada | Close | 0.0034091 | P-17 | 106 | WTG Breakdown Maintenance
191 | 2025-06-11 | 2026 | 2026 | 2025-06-01 | Year_3 | P-34 | PWEPL | MSEDCL | 2.273% | 427 | Hydraulic pump enable time too long warning | WET B card failure | 0.375 | 0.375 | 0.48819 | 0 | 2.7167 | 2.7167 | Replaced WET B card & Hydraulic oil top & turbine restored | Close | 0.061742 | P-04 | 3094 | WTG Breakdown Maintenance
Formulas:
Month = [Date]-DAY([Date])+1

## Grid_BD
Sr. No. | Date | Finacial Year | Calendor Year | Month | Operating Year | Affected System | SPV | Concumaer | Plant Equivalent Weightage | Breakdown Description | Fault Start TimeStamp | Work Start TimeStamp | Fault Clearance time | Response Time | Resolution Time | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Paired WTG for Enegy based MA | Energy Production during breakdwon of paired WTG | Fault Category
1 | 2025-04-08 | 2026 | 2025 | 2025-04-01 | Year_3 | Wind_F1 | PWEPL | MSEDCL | 22.73% | S/D for SS V.C.B VDR & IR testing work | 9:54 | 9:54 | 16:57 | 0 | 7.05 | 7.05 | Testing work completed | Close | 1.6023 | Site Average | 6060 | EG Scheduled Maintenance
2 | 2025-04-08 | 2026 | 2025 | 2025-04-01 | Year_3 | Wind_F2 | PWEPL | MSEDCL | 27.27% | S/D for SS V.C.B VDR & IR testing work | 10:58 | 10:58 | 16:58 | 0 | 6 | 6 | Testing work completed | Close | 1.6364 | Site Average | 6204 | EG Scheduled Maintenance
3 | 2025-04-08 | 2026 | 2025 | 2025-04-01 | Year_3 | Wind_F3 | PWEPL | MSEDCL | 20.45% | S/D for SS V.C.B VDR & IR testing work | 17:02 | 17:02 | 20:15 | 0 | 3.2167 | 3.2167 | Testing work completed | Close | 0.65795 | Site Average | 2547 | EG Scheduled Maintenance
4 | 2025-04-08 | 2026 | 2025 | 2025-04-01 | Year_3 | Wind_F4 | PWEPL | MSEDCL | 29.55% | S/D for SS V.C.B VDR & IR testing work | 17:06 | 17:06 | 20:15 | 0 | 3.15 | 3.15 | Testing work completed | Close | 0.93068 | Site Average | 3601 | EG Scheduled Maintenance
5 | 2025-04-15 | 2026 | 2025 | 2025-04-01 | Year_3 | Wind_F1 | PWEPL | MSEDCL | 22.73% | S/D for Nerale S/S bus bar jump replacement work | 8:55 | 8:55 | 18:45 | 0 | 9.8333 | 9.8333 | Jump replacement work completed | Close | 2.2348 | Site Average | 23600 | EG Scheduled Maintenance
6 | 2025-04-15 | 2026 | 2025 | 2025-04-01 | Year_3 | Wind_F2 | PWEPL | MSEDCL | 27.27% | S/D for Nerale S/S bus bar jump replacement work | 8:55 | 8:55 | 18:45 | 0 | 9.8333 | 9.8333 | Jump replacement work completed | Close | 2.6818 | Site Average | 28440 | EG Scheduled Maintenance
7 | 2025-04-22 | 2026 | 2025 | 2025-04-01 | Year_3 | Wind_F3 | PWEPL | MSEDCL | 20.45% | S/D for Nerale S/S bus bar jump replacement work | 10:21 | 10:21 | 18:55 | 0 | 8.5667 | 8.5667 | Jump replacement work completed | Close | 1.7523 | Site Average | 8850 | EG Scheduled Maintenance
8 | 2025-04-22 | 2026 | 2025 | 2025-04-01 | Year_3 | Wind_F4 | PWEPL | MSEDCL | 29.55% | S/D for Nerale S/S bus bar jump replacement work | 10:22 | 10:22 | 18:40 | 0 | 8.3 | 8.3 | Jump replacement work completed | Close | 2.4523 | Site Average | 12270 | EG Scheduled Maintenance
9 | 2025-05-13 | 2026 | 2025 | 2025-05-01 | Year_3 | Wind_F3 | PWEPL | MSEDCL | 20.45% | S/D for Nerale S/S 33kv Side Maintenance & Externel line Maintenance work | 10:00 | 10:00 | 16:40 | 0 | 6.6667 | 6.6667 | Side Maintenance & Externel line Maintenance work done | Close | 1.3636 | Site Average | 4737 | EG Scheduled Maintenance
10 | 2025-05-13 | 2026 | 2025 | 2025-05-01 | Year_3 | Wind_F4 | PWEPL | MSEDCL | 29.55% | S/D for Nerale S/S 33kv Side Maintenance & Externel line Maintenance work | 10:00 | 10:00 | 16:40 | 0 | 6.6667 | 6.6667 | Side Maintenance & Externel line Maintenance work done | Close | 1.9697 | Site Average | 6724 | EG Scheduled Maintenance
11 | 2025-06-10 | 2026 | 2025 | 2025-06-01 | Year_3 | Wind_F1 | PWEPL | MSEDCL | 22.73% | S/D for Nerale S/S 33kv side Maintenance & testing work | 10:58 | 10:58 | 13:41 | 0 | 2.7167 | 2.7167 | Side Maintenance & Testing work completed | Close | 0.61742 | Site Average | 18741 | EG Scheduled Maintenance
12 | 2025-06-10 | 2026 | 2025 | 2025-06-01 | Year_3 | Wind_F2 | PWEPL | MSEDCL | 27.27% | S/D for Nerale S/S 33kv side Maintenance & testing work | 11:15 | 11:15 | 13:42 | 0 | 2.45 | 2.45 | Side Maintenance & Testing work completed | Close | 0.66818 | Site Average | 20430 | EG Scheduled Maintenance
13 | 2025-06-10 | 2026 | 2025 | 2025-06-01 | Year_3 | Wind_F3 | PWEPL | MSEDCL | 20.45% | S/D for Nerale S/S 33kv side Maintenance & testing work | 13:25 | 13:25 | 14:18 | 0 | 0.88333 | 0.88333 | Side Maintenance & Testing work completed | Close | 0.18068 | Site Average | 5386 | EG Scheduled Maintenance
Formulas:
Month = [Date]-DAY([Date])+1

## IGA_BD
Date | Finacial Year | Calendor Year | Month | Operating Year | Affected WTG | SPV | Concumaer | Plant Equivalent Weightage | Breakdown Description | Fault Start TimeStamp | Work Start TimeStamp | Fault Clearance time | Response Time | Resolution Time | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Paired WTG for Enegy based MA | Energy Production during breakdwon of paired WTG | Fault Category
2025-03-29 | 2025 | 2025 | 2025-03-01 | Year_2 | Wind_F2 | PWEPL | MSEDCL | 27.27% | Group VCB-02 Yard YPM activity | 0.49444 | 0.49444 | 0.675 | 0 | 4.3333 | 4.3333 | Group VCB-02 Yard YPM activity complated | Close | 1.1818 | site average | 4001 | IG Scheduled Maintenance
2025-03-29 | 2025 | 2025 | 2025-03-01 | Year_2 | P-14 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.675 | 0.675 | 0.68889 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 27 | IG Scheduled Maintenance
2025-03-29 | 2025 | 2025 | 2025-03-01 | Year_2 | P-15 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.675 | 0.675 | 0.68889 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 27 | IG Scheduled Maintenance
2025-03-29 | 2025 | 2025 | 2025-03-01 | Year_2 | P-16 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.675 | 0.675 | 0.68889 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 27 | IG Scheduled Maintenance
2025-03-29 | 2025 | 2025 | 2025-03-01 | Year_2 | P-17 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.675 | 0.675 | 0.68889 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 27 | IG Scheduled Maintenance
2025-03-29 | 2025 | 2025 | 2025-03-01 | Year_2 | P-19 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.675 | 0.675 | 0.68889 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 27 | IG Scheduled Maintenance
2025-03-29 | 2025 | 2025 | 2025-03-01 | Year_2 | P-20 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.675 | 0.675 | 0.68889 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 27 | IG Scheduled Maintenance
2025-03-29 | 2025 | 2025 | 2025-03-01 | Year_2 | P-38 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.675 | 0.675 | 0.68889 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 27 | IG Scheduled Maintenance
2025-03-29 | 2025 | 2025 | 2025-03-01 | Year_2 | P-04 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.675 | 0.675 | 0.68889 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 27 | IG Scheduled Maintenance
2025-03-29 | 2025 | 2025 | 2025-03-01 | Year_2 | P-22 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.675 | 0.675 | 0.68889 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 27 | IG Scheduled Maintenance
2025-03-29 | 2025 | 2025 | 2025-03-01 | Year_2 | P-23 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.675 | 0.675 | 0.68889 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 27 | IG Scheduled Maintenance
2025-03-29 | 2025 | 2025 | 2025-03-01 | Year_2 | P-34 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.675 | 0.675 | 0.68889 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 27 | IG Scheduled Maintenance
2025-03-29 | 2025 | 2025 | 2025-03-01 | Year_2 | P-43 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.675 | 0.675 | 0.68889 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 27 | IG Scheduled Maintenance
2025-03-30 | 2025 | 2025 | 2025-03-01 | Year_2 | P-08 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for YPM activity | 0.43194 | 0.43194 | 0.57083 | 0 | 3.3333 | 3.3333 | Group VCB-02,CKT-02 Yard YPM activity work | Close | 0.075758 | site average | 175 | IG Scheduled Maintenance
2025-03-30 | 2025 | 2025 | 2025-03-01 | Year_2 | P-08 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.57083 | 0.57083 | 0.58472 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 17 | IG Scheduled Maintenance
2025-03-30 | 2025 | 2025 | 2025-03-01 | Year_2 | P-25 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for YPM activity | 0.43194 | 0.43194 | 0.57083 | 0 | 3.3333 | 3.3333 | Group VCB-02,CKT-02 Yard YPM activity work | Close | 0.075758 | site average | 175 | IG Scheduled Maintenance
2025-03-30 | 2025 | 2025 | 2025-03-01 | Year_2 | P-25 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.57083 | 0.57083 | 0.58472 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 17 | IG Scheduled Maintenance
2025-03-30 | 2025 | 2025 | 2025-03-01 | Year_2 | P-26 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for YPM activity | 0.43194 | 0.43194 | 0.57083 | 0 | 3.3333 | 3.3333 | Group VCB-02,CKT-02 Yard YPM activity work | Close | 0.075758 | site average | 175 | IG Scheduled Maintenance
2025-03-30 | 2025 | 2025 | 2025-03-01 | Year_2 | P-26 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.57083 | 0.57083 | 0.58472 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 17 | IG Scheduled Maintenance
2025-03-30 | 2025 | 2025 | 2025-03-01 | Year_2 | P-27 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for YPM activity | 0.43194 | 0.43194 | 0.57083 | 0 | 3.3333 | 3.3333 | Group VCB-02,CKT-02 Yard YPM activity work | Close | 0.075758 | site average | 175 | IG Scheduled Maintenance
2025-03-30 | 2025 | 2025 | 2025-03-01 | Year_2 | P-27 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.57083 | 0.57083 | 0.58472 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 17 | IG Scheduled Maintenance
2025-03-30 | 2025 | 2025 | 2025-03-01 | Year_2 | P-28 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for YPM activity | 0.43194 | 0.43194 | 0.57083 | 0 | 3.3333 | 3.3333 | Group VCB-02,CKT-02 Yard YPM activity work | Close | 0.075758 | site average | 175 | IG Scheduled Maintenance
2025-03-30 | 2025 | 2025 | 2025-03-01 | Year_2 | P-28 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.57083 | 0.57083 | 0.58472 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 17 | IG Scheduled Maintenance
2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_2 | P-04 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.46528 | 0.46528 | 0.82847 | 0 | 8.7167 | 8.7167 | CT & PT Installation work | Close | 0.19811 | site average | 724 | IG Unscheduled Maintenance
2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_2 | P-04 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.82847 | 0.82847 | 0.84236 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 28 | IG Unscheduled Maintenance
2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_2 | P-22 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.46528 | 0.46528 | 0.82847 | 0 | 8.7167 | 8.7167 | CT & PT Installation work | Close | 0.19811 | site average | 724 | IG Unscheduled Maintenance
2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_2 | P-22 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.82847 | 0.82847 | 0.84236 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 28 | IG Unscheduled Maintenance
2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_2 | P-23 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.46528 | 0.46528 | 0.82847 | 0 | 8.7167 | 8.7167 | CT & PT Installation work | Close | 0.19811 | site average | 724 | IG Unscheduled Maintenance
2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_2 | P-23 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.82847 | 0.82847 | 0.84236 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 28 | IG Unscheduled Maintenance
2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_2 | P-34 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.46528 | 0.46528 | 0.82847 | 0 | 8.7167 | 8.7167 | CT & PT Installation work | Close | 0.19811 | site average | 724 | IG Unscheduled Maintenance
2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_2 | P-34 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.82847 | 0.82847 | 0.84236 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 28 | IG Unscheduled Maintenance
2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_2 | P-43 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.46528 | 0.46528 | 0.82847 | 0 | 8.7167 | 8.7167 | CT & PT Installation work | Close | 0.19811 | site average | 724 | IG Unscheduled Maintenance
2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_2 | P-43 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.82847 | 0.82847 | 0.84236 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 28 | IG Unscheduled Maintenance
2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_2 | P-32 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for Relay Removing work | 0.75 | 0.75 | 0.76111 | 0 | 0.26667 | 0.26667 | Relay Removing work Complated | Close | 0.0060606 | site average | 0 | IG Unscheduled Maintenance
2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_2 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.76111 | 0.76111 | 0.775 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 0 | IG Unscheduled Maintenance
2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_2 | P-37 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for Relay Removing work | 0.67708 | 0.67708 | 0.68403 | 0 | 0.16667 | 0.16667 | Relay Removing work Complated | Close | 0.0037879 | site average | 16 | IG Unscheduled Maintenance
2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_2 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.68403 | 0.68403 | 0.69722 | 0 | 0.31667 | 0.31667 | Rebooted the PLC & reset at scada | Close | 0.007197 | site average | 0 | IG Unscheduled Maintenance
2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_2 | P-42 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for Relay Removing work | 0.65278 | 0.65278 | 0.66111 | 0 | 0.2 | 0.2 | Relay Removing work Complated | Close | 0.0045455 | site average | 42 | IG Unscheduled Maintenance
2025-03-31 | 2025 | 2025 | 2025-03-01 | Year_2 | P-42 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.66111 | 0.66111 | 0.66597 | 0 | 0.11667 | 0.11667 | Rebooted the PLC & reset at scada | Close | 0.0026515 | site average | 39 | IG Unscheduled Maintenance
2025-04-01 | 2026 | 2025 | 2025-04-01 | Year_3 | Wind_F4 | PWEPL | MSEDCL | 29.55% | Feeder tripped by E/F | 0.79583 | 0.79583 | 0.85556 | 0 | 1.4333 | 1.4333 | Test charged taken charged successfully | Close | 0.42348 | site average | 20207 | IG Breakdown Maintenance
2025-04-01 | 2026 | 2025 | 2025-04-01 | Year_3 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.85556 | 0.85556 | 0.86736 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | site average | 388 | IG Breakdown Maintenance
2025-04-01 | 2026 | 2025 | 2025-04-01 | Year_3 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.85556 | 0.85556 | 0.86528 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | site average | 388 | IG Breakdown Maintenance
2025-04-01 | 2026 | 2025 | 2025-04-01 | Year_3 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.85556 | 0.85556 | 0.86806 | 0 | 0.3 | 0.3 | Rebooted the PLC & reset at scada | Close | 0.0068182 | site average | 388 | IG Breakdown Maintenance
2025-04-01 | 2026 | 2025 | 2025-04-01 | Year_3 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.85556 | 0.85556 | 0.86597 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | site average | 388 | IG Breakdown Maintenance
2025-04-01 | 2026 | 2025 | 2025-04-01 | Year_3 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.85556 | 0.85556 | 0.86736 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | site average | 388 | IG Breakdown Maintenance
2025-04-01 | 2026 | 2025 | 2025-04-01 | Year_3 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.85556 | 0.85556 | 0.86736 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | site average | 388 | IG Breakdown Maintenance
2025-04-01 | 2026 | 2025 | 2025-04-01 | Year_3 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.85556 | 0.85556 | 0.86736 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | site average | 388 | IG Breakdown Maintenance
2025-04-01 | 2026 | 2025 | 2025-04-01 | Year_3 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.85556 | 0.85556 | 0.86458 | 0 | 0.21667 | 0.21667 | Rebooted the PLC & reset at scada | Close | 0.0049242 | site average | 388 | IG Breakdown Maintenance
2025-04-01 | 2026 | 2025 | 2025-04-01 | Year_3 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.85556 | 0.85556 | 0.86944 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 388 | IG Breakdown Maintenance
2025-04-01 | 2026 | 2025 | 2025-04-01 | Year_3 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.85556 | 0.85556 | 0.86458 | 0 | 0.21667 | 0.21667 | Rebooted the PLC & reset at scada | Close | 0.0049242 | site average | 388 | IG Breakdown Maintenance
2025-04-01 | 2026 | 2025 | 2025-04-01 | Year_3 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.85556 | 0.85556 | 0.86944 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 388 | IG Breakdown Maintenance
2025-04-01 | 2026 | 2025 | 2025-04-01 | Year_3 | P-07 | PWEPL | MSEDCL | 2.273% | VCB Tripped | 0.85556 | 0.85556 | 0.91944 | 0 | 1.5333 | 1.5333 | VCB reet & Charge | Close | 0.034848 | site average | 450 | IG Breakdown Maintenance
2025-04-01 | 2026 | 2025 | 2025-04-01 | Year_3 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.91944 | 0.91944 | 0.93333 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 388 | IG Breakdown Maintenance
2025-04-01 | 2026 | 2025 | 2025-04-01 | Year_3 | P-56 | PWEPL | MSEDCL | 2.273% | VCB Tripped | 0.85556 | 0.85556 | 0.89861 | 0 | 1.0333 | 1.0333 | VCB reset & Charge | Close | 0.023485 | site average | 234 | IG Breakdown Maintenance
2025-04-01 | 2026 | 2025 | 2025-04-01 | Year_3 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.89861 | 0.89861 | 0.9125 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 388 | IG Breakdown Maintenance
2025-04-01 | 2026 | 2025 | 2025-04-01 | Year_3 | Wind_F3 | PWEPL | MSEDCL | 20.45% | S/D for Group VCB -03 YPM Work | 0.57847 | 0.57847 | 0.66944 | 0 | 2.1833 | 2.1833 | Group VCB-3 YPM Work completed | Close | 0.44659 | site average | 872 | IG Scheduled Maintenance
2025-04-01 | 2026 | 2025 | 2025-04-01 | Year_3 | P-42 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.66944 | 0.66944 | 0.67986 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | site average | 17 | IG Scheduled Maintenance
2025-04-01 | 2026 | 2025 | 2025-04-01 | Year_3 | P-45 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.66944 | 0.66944 | 0.67986 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | site average | 17 | IG Scheduled Maintenance
2025-04-01 | 2026 | 2025 | 2025-04-01 | Year_3 | P-46 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.66944 | 0.66944 | 0.68194 | 0 | 0.3 | 0.3 | Rebooted the PLC & reset at scada | Close | 0.0068182 | site average | 17 | IG Scheduled Maintenance
2025-04-01 | 2026 | 2025 | 2025-04-01 | Year_3 | P-47 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.66944 | 0.66944 | 0.68056 | 0 | 0.26667 | 0.26667 | Rebooted the PLC & reset at scada | Close | 0.0060606 | site average | 17 | IG Scheduled Maintenance
2025-04-01 | 2026 | 2025 | 2025-04-01 | Year_3 | P-48 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.66944 | 0.66944 | 0.68194 | 0 | 0.3 | 0.3 | Rebooted the PLC & reset at scada | Close | 0.0068182 | site average | 17 | IG Scheduled Maintenance
2025-04-01 | 2026 | 2025 | 2025-04-01 | Year_3 | P-05 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.66944 | 0.66944 | 0.68125 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | site average | 17 | IG Scheduled Maintenance
2025-04-01 | 2026 | 2025 | 2025-04-01 | Year_3 | P-06 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.66944 | 0.66944 | 0.68194 | 0 | 0.3 | 0.3 | Rebooted the PLC & reset at scada | Close | 0.0068182 | site average | 17 | IG Scheduled Maintenance
2025-04-01 | 2026 | 2025 | 2025-04-01 | Year_3 | P-40 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.66944 | 0.66944 | 0.68056 | 0 | 0.26667 | 0.26667 | Rebooted the PLC & reset at scada | Close | 0.0060606 | site average | 17 | IG Scheduled Maintenance
2025-04-01 | 2026 | 2025 | 2025-04-01 | Year_3 | P-41 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.66944 | 0.66944 | 0.68264 | 0 | 0.31667 | 0.31667 | Rebooted the PLC & reset at scada | Close | 0.007197 | site average | 17 | IG Scheduled Maintenance
2025-04-01 | 2026 | 2025 | 2025-04-01 | Year_3 | P-09 | PWEPL | MSEDCL | 2.273% | VCB Tripped | 19:05 | 19:05 | 20:05 | 0 | 1 | 1 | VCB reset & Charge | Close | 0.022727 | site average | 1270 | IG Breakdown Maintenance
2025-04-01 | 2026 | 2025 | 2025-04-01 | Year_3 | P-08 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.44861 | 0.44861 | 0.77083 | 0 | 7.7333 | 7.7333 | WTG-27 & 28 Isolator shifting work | Close | 0.17576 | site average | 1790 | IG Unscheduled Maintenance
2025-04-01 | 2026 | 2025 | 2025-04-01 | Year_3 | P-08 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.77083 | 0.77083 | 0.78472 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 77 | IG Unscheduled Maintenance
2025-04-01 | 2026 | 2025 | 2025-04-01 | Year_3 | P-25 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.44861 | 0.44861 | 0.77083 | 0 | 7.7333 | 7.7333 | WTG-27 & 28 Isolator shifting work | Close | 0.17576 | site average | 1790 | IG Unscheduled Maintenance
2025-04-01 | 2026 | 2025 | 2025-04-01 | Year_3 | P-25 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.77083 | 0.77083 | 0.78472 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 77 | IG Unscheduled Maintenance
2025-04-01 | 2026 | 2025 | 2025-04-01 | Year_3 | P-26 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.44861 | 0.44861 | 0.77083 | 0 | 7.7333 | 7.7333 | WTG-27 & 28 Isolator shifting work | Close | 0.17576 | site average | 1790 | IG Unscheduled Maintenance
2025-04-01 | 2026 | 2025 | 2025-04-01 | Year_3 | P-26 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.77083 | 0.77083 | 0.78472 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 77 | IG Unscheduled Maintenance
2025-04-01 | 2026 | 2025 | 2025-04-01 | Year_3 | P-27 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.44861 | 0.44861 | 0.77083 | 0 | 7.7333 | 7.7333 | WTG-27 & 28 Isolator shifting work | Close | 0.17576 | site average | 1790 | IG Unscheduled Maintenance
2025-04-01 | 2026 | 2025 | 2025-04-01 | Year_3 | P-27 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.77083 | 0.77083 | 0.78472 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 77 | IG Unscheduled Maintenance
2025-04-01 | 2026 | 2025 | 2025-04-01 | Year_3 | P-28 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.44861 | 0.44861 | 0.77083 | 0 | 7.7333 | 7.7333 | WTG-27 & 28 Isolator shifting work | Close | 0.17576 | site average | 1790 | IG Unscheduled Maintenance
2025-04-01 | 2026 | 2025 | 2025-04-01 | Year_3 | P-28 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.77083 | 0.77083 | 0.78472 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 77 | IG Unscheduled Maintenance
2025-04-02 | 2026 | 2025 | 2025-04-01 | Year_3 | Wind_F3 | PWEPL | MSEDCL | 20.45% | Feeder tripped by E/F | 0.084722 | 0.084722 | 0.095139 | 0 | 0.25 | 0.25 | Test charged taken charged successfully | Close | 0.051136 | site average | 904 | IG Breakdown Maintenance
2025-04-02 | 2026 | 2025 | 2025-04-01 | Year_3 | P-05 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.095139 | 0.095139 | 0.10486 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | site average | 100 | IG Breakdown Maintenance
2025-04-02 | 2026 | 2025 | 2025-04-01 | Year_3 | P-06 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.095139 | 0.095139 | 0.10486 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | site average | 100 | IG Breakdown Maintenance
2025-04-02 | 2026 | 2025 | 2025-04-01 | Year_3 | P-40 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.095139 | 0.095139 | 0.10625 | 0 | 0.26667 | 0.26667 | Rebooted the PLC & reset at scada | Close | 0.0060606 | site average | 100 | IG Breakdown Maintenance
2025-04-02 | 2026 | 2025 | 2025-04-01 | Year_3 | P-41 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.095139 | 0.095139 | 0.10486 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | site average | 100 | IG Breakdown Maintenance
2025-04-02 | 2026 | 2025 | 2025-04-01 | Year_3 | P-42 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.095139 | 0.095139 | 0.10556 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | site average | 100 | IG Breakdown Maintenance
2025-04-02 | 2026 | 2025 | 2025-04-01 | Year_3 | P-45 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.095139 | 0.095139 | 0.10903 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 100 | IG Breakdown Maintenance
2025-04-02 | 2026 | 2025 | 2025-04-01 | Year_3 | P-46 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.095139 | 0.095139 | 0.10903 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 100 | IG Breakdown Maintenance
2025-04-02 | 2026 | 2025 | 2025-04-01 | Year_3 | P-47 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.095139 | 0.095139 | 0.10694 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | site average | 100 | IG Breakdown Maintenance
2025-04-02 | 2026 | 2025 | 2025-04-01 | Year_3 | P-48 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.095139 | 0.095139 | 0.10556 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | site average | 100 | IG Breakdown Maintenance
2025-04-02 | 2026 | 2025 | 2025-04-01 | Year_3 | P-08 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.64583 | 0.64583 | 0.78819 | 0 | 3.4167 | 3.4167 | WTG- 28 Isolator shifting work | Close | 0.077652 | site average | 1022 | IG Unscheduled Maintenance
2025-04-02 | 2026 | 2025 | 2025-04-01 | Year_3 | P-08 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.78819 | 0.78819 | 0.80208 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 99 | IG Unscheduled Maintenance
2025-04-02 | 2026 | 2025 | 2025-04-01 | Year_3 | P-25 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.64583 | 0.64583 | 0.78819 | 0 | 3.4167 | 3.4167 | WTG- 28 Isolator shifting work | Close | 0.077652 | site average | 1022 | IG Unscheduled Maintenance
2025-04-02 | 2026 | 2025 | 2025-04-01 | Year_3 | P-25 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.78819 | 0.78819 | 0.80208 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 99 | IG Unscheduled Maintenance
2025-04-02 | 2026 | 2025 | 2025-04-01 | Year_3 | P-26 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.64583 | 0.64583 | 0.78819 | 0 | 3.4167 | 3.4167 | WTG- 28 Isolator shifting work | Close | 0.077652 | site average | 1022 | IG Unscheduled Maintenance
2025-04-02 | 2026 | 2025 | 2025-04-01 | Year_3 | P-26 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.78819 | 0.78819 | 0.80208 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 99 | IG Unscheduled Maintenance
2025-04-02 | 2026 | 2025 | 2025-04-01 | Year_3 | P-27 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.64583 | 0.64583 | 0.78819 | 0 | 3.4167 | 3.4167 | WTG- 28 Isolator shifting work | Close | 0.077652 | site average | 1022 | IG Unscheduled Maintenance
2025-04-02 | 2026 | 2025 | 2025-04-01 | Year_3 | P-27 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.78819 | 0.78819 | 0.80208 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 99 | IG Unscheduled Maintenance
2025-04-02 | 2026 | 2025 | 2025-04-01 | Year_3 | P-28 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.64583 | 0.64583 | 0.78819 | 0 | 3.4167 | 3.4167 | WTG- 28 Isolator shifting work | Close | 0.077652 | site average | 1022 | IG Unscheduled Maintenance
2025-04-02 | 2026 | 2025 | 2025-04-01 | Year_3 | P-28 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.78819 | 0.78819 | 0.80208 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 99 | IG Unscheduled Maintenance
2025-04-03 | 2026 | 2025 | 2025-04-01 | Year_3 | P-14 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.45903 | 0.45903 | 0.70833 | 0 | 5.9833 | 5.9833 | WTG- 20 Isolator shifting work | Close | 0.13598 | site average | 437 | IG Unscheduled Maintenance
2025-04-03 | 2026 | 2025 | 2025-04-01 | Year_3 | P-14 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.70833 | 0.70833 | 0.72222 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 24 | IG Unscheduled Maintenance
2025-04-03 | 2026 | 2025 | 2025-04-01 | Year_3 | P-15 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.45903 | 0.45903 | 0.70833 | 0 | 5.9833 | 5.9833 | WTG- 20 Isolator shifting work | Close | 0.13598 | site average | 437 | IG Unscheduled Maintenance
2025-04-03 | 2026 | 2025 | 2025-04-01 | Year_3 | P-15 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.70833 | 0.70833 | 0.72222 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 24 | IG Unscheduled Maintenance
2025-04-03 | 2026 | 2025 | 2025-04-01 | Year_3 | P-16 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.45903 | 0.45903 | 0.70833 | 0 | 5.9833 | 5.9833 | WTG- 20 Isolator shifting work | Close | 0.13598 | site average | 437 | IG Unscheduled Maintenance
2025-04-03 | 2026 | 2025 | 2025-04-01 | Year_3 | P-16 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.70833 | 0.70833 | 0.72222 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 24 | IG Unscheduled Maintenance
2025-04-03 | 2026 | 2025 | 2025-04-01 | Year_3 | P-17 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.45903 | 0.45903 | 0.70833 | 0 | 5.9833 | 5.9833 | WTG- 20 Isolator shifting work | Close | 0.13598 | site average | 437 | IG Unscheduled Maintenance
2025-04-03 | 2026 | 2025 | 2025-04-01 | Year_3 | P-17 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.70833 | 0.70833 | 0.72222 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 24 | IG Unscheduled Maintenance
2025-04-03 | 2026 | 2025 | 2025-04-01 | Year_3 | P-19 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.45903 | 0.45903 | 0.70833 | 0 | 5.9833 | 5.9833 | WTG- 20 Isolator shifting work | Close | 0.13598 | site average | 437 | IG Unscheduled Maintenance
2025-04-03 | 2026 | 2025 | 2025-04-01 | Year_3 | P-19 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.70833 | 0.70833 | 0.72222 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 24 | IG Unscheduled Maintenance
2025-04-03 | 2026 | 2025 | 2025-04-01 | Year_3 | P-20 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.45903 | 0.45903 | 0.70833 | 0 | 5.9833 | 5.9833 | WTG- 20 Isolator shifting work | Close | 0.13598 | site average | 437 | IG Unscheduled Maintenance
2025-04-03 | 2026 | 2025 | 2025-04-01 | Year_3 | P-20 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.70833 | 0.70833 | 0.72222 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 24 | IG Unscheduled Maintenance
2025-04-03 | 2026 | 2025 | 2025-04-01 | Year_3 | P-38 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.45903 | 0.45903 | 0.70833 | 0 | 5.9833 | 5.9833 | WTG- 20 Isolator shifting work | Close | 0.13598 | site average | 437 | IG Unscheduled Maintenance
2025-04-03 | 2026 | 2025 | 2025-04-01 | Year_3 | P-38 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.70833 | 0.70833 | 0.72222 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 24 | IG Unscheduled Maintenance
2025-04-03 | 2026 | 2025 | 2025-04-01 | Year_3 | P-34 | PWEPL | MSEDCL | 2.273% | VCB Tripped | 0.39167 | 0.39167 | 0.43681 | 0 | 1.0833 | 1.0833 | VCB reset & Charge | Close | 0.024621 | site average | 3 | IG Breakdown Maintenance
2025-04-03 | 2026 | 2025 | 2025-04-01 | Year_3 | P-34 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.43681 | 0.43681 | 0.43958 | 0 | 0.066667 | 0.066667 | Rebooted the PLC & reset at scada | Close | 0.0015152 | site average | 0 | IG Breakdown Maintenance
2025-04-04 | 2026 | 2025 | 2025-04-01 | Year_3 | P-14 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.42917 | 0.42917 | 0.80556 | 0 | 9.0333 | 9.0333 | WTG- 19 Isolator shifting work | Close | 0.2053 | site average | 1002 | IG Unscheduled Maintenance
2025-04-04 | 2026 | 2025 | 2025-04-01 | Year_3 | P-14 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.80556 | 0.80556 | 0.81944 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 37 | IG Unscheduled Maintenance
2025-04-04 | 2026 | 2025 | 2025-04-01 | Year_3 | P-15 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.42917 | 0.42917 | 0.80556 | 0 | 9.0333 | 9.0333 | WTG- 19 Isolator shifting work | Close | 0.2053 | site average | 1002 | IG Unscheduled Maintenance
2025-04-04 | 2026 | 2025 | 2025-04-01 | Year_3 | P-15 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.80556 | 0.80556 | 0.81944 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 37 | IG Unscheduled Maintenance
2025-04-04 | 2026 | 2025 | 2025-04-01 | Year_3 | P-16 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.42917 | 0.42917 | 0.80556 | 0 | 9.0333 | 9.0333 | WTG- 19 Isolator shifting work | Close | 0.2053 | site average | 1002 | IG Unscheduled Maintenance
2025-04-04 | 2026 | 2025 | 2025-04-01 | Year_3 | P-16 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.80556 | 0.80556 | 0.81944 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 37 | IG Unscheduled Maintenance
2025-04-04 | 2026 | 2025 | 2025-04-01 | Year_3 | P-17 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.42917 | 0.42917 | 0.80556 | 0 | 9.0333 | 9.0333 | WTG- 19 Isolator shifting work | Close | 0.2053 | site average | 1002 | IG Unscheduled Maintenance
2025-04-04 | 2026 | 2025 | 2025-04-01 | Year_3 | P-17 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.80556 | 0.80556 | 0.81944 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 37 | IG Unscheduled Maintenance
2025-04-04 | 2026 | 2025 | 2025-04-01 | Year_3 | P-19 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.42917 | 0.42917 | 0.80556 | 0 | 9.0333 | 9.0333 | WTG- 19 Isolator shifting work | Close | 0.2053 | site average | 1002 | IG Unscheduled Maintenance
2025-04-04 | 2026 | 2025 | 2025-04-01 | Year_3 | P-19 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.80556 | 0.80556 | 0.81944 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 37 | IG Unscheduled Maintenance
2025-04-04 | 2026 | 2025 | 2025-04-01 | Year_3 | P-20 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.42917 | 0.42917 | 0.80556 | 0 | 9.0333 | 9.0333 | WTG- 19 Isolator shifting work | Close | 0.2053 | site average | 1002 | IG Unscheduled Maintenance
2025-04-04 | 2026 | 2025 | 2025-04-01 | Year_3 | P-20 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.80556 | 0.80556 | 0.81944 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 37 | IG Unscheduled Maintenance
2025-04-04 | 2026 | 2025 | 2025-04-01 | Year_3 | P-38 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.42917 | 0.42917 | 0.80556 | 0 | 9.0333 | 9.0333 | WTG- 19 Isolator shifting work | Close | 0.2053 | site average | 1002 | IG Unscheduled Maintenance
2025-04-04 | 2026 | 2025 | 2025-04-01 | Year_3 | P-38 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.80556 | 0.80556 | 0.81944 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 37 | IG Unscheduled Maintenance
2025-04-04 | 2026 | 2025 | 2025-04-01 | Year_3 | Wind_F4 | PWEPL | MSEDCL | 29.55% | S/D for Group VCB -4 YPM Work | 0.51042 | 0.51042 | 0.66319 | 0 | 3.6667 | 3.6667 | Group VCB-4 YPM Work completed | Close | 1.0833 | site average | 548 | IG Unscheduled Maintenance
2025-04-04 | 2026 | 2025 | 2025-04-01 | Year_3 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.66319 | 0.66319 | 0.67708 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 3.8 | IG Unscheduled Maintenance
2025-04-04 | 2026 | 2025 | 2025-04-01 | Year_3 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.66319 | 0.66319 | 0.67708 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 3.8 | IG Unscheduled Maintenance
2025-04-04 | 2026 | 2025 | 2025-04-01 | Year_3 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.66319 | 0.66319 | 0.67708 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 3.8 | IG Unscheduled Maintenance
2025-04-04 | 2026 | 2025 | 2025-04-01 | Year_3 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.66319 | 0.66319 | 0.67708 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 3.8 | IG Unscheduled Maintenance
2025-04-04 | 2026 | 2025 | 2025-04-01 | Year_3 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.66319 | 0.66319 | 0.67708 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 3.8 | IG Unscheduled Maintenance
2025-04-04 | 2026 | 2025 | 2025-04-01 | Year_3 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.66319 | 0.66319 | 0.67708 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 3.8 | IG Unscheduled Maintenance
2025-04-04 | 2026 | 2025 | 2025-04-01 | Year_3 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.66319 | 0.66319 | 0.67708 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 3.8 | IG Unscheduled Maintenance
2025-04-04 | 2026 | 2025 | 2025-04-01 | Year_3 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.66319 | 0.66319 | 0.67708 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 3.8 | IG Unscheduled Maintenance
2025-04-04 | 2026 | 2025 | 2025-04-01 | Year_3 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.66319 | 0.66319 | 0.67708 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 3.8 | IG Unscheduled Maintenance
2025-04-04 | 2026 | 2025 | 2025-04-01 | Year_3 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.66319 | 0.66319 | 0.67708 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 3.8 | IG Unscheduled Maintenance
2025-04-04 | 2026 | 2025 | 2025-04-01 | Year_3 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.66319 | 0.66319 | 0.67708 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 3.8 | IG Unscheduled Maintenance
2025-04-04 | 2026 | 2025 | 2025-04-01 | Year_3 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.66319 | 0.66319 | 0.67708 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 3.8 | IG Unscheduled Maintenance
2025-04-04 | 2026 | 2025 | 2025-04-01 | Year_3 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.66319 | 0.66319 | 0.67708 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 3.8 | IG Unscheduled Maintenance
2025-04-04 | 2026 | 2025 | 2025-04-01 | Year_3 | P-32 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for MSEB line cross work | 0.70486 | 0.70486 | 0.72569 | 0 | 0.5 | 0.5 | Work Completed | Close | 0.011364 | site average | 55 | IG Unscheduled Maintenance
2025-04-04 | 2026 | 2025 | 2025-04-01 | Year_3 | P-37 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for MSEB line cross work | 0.70486 | 0.70486 | 0.72569 | 0 | 0.5 | 0.5 | Work Completed | Close | 0.011364 | site average | 55 | IG Unscheduled Maintenance
2025-04-04 | 2026 | 2025 | 2025-04-01 | Year_3 | P-50 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for MSEB line cross work | 0.70486 | 0.70486 | 0.72569 | 0 | 0.5 | 0.5 | Work Completed | Close | 0.011364 | site average | 55 | IG Unscheduled Maintenance
2025-04-04 | 2026 | 2025 | 2025-04-01 | Year_3 | P-51 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for MSEB line cross work | 0.70486 | 0.70486 | 0.72569 | 0 | 0.5 | 0.5 | Work Completed | Close | 0.011364 | site average | 55 | IG Unscheduled Maintenance
2025-04-04 | 2026 | 2025 | 2025-04-01 | Year_3 | P-52 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for MSEB line cross work | 0.70486 | 0.70486 | 0.72569 | 0 | 0.5 | 0.5 | Work Completed | Close | 0.011364 | site average | 55 | IG Unscheduled Maintenance
2025-04-04 | 2026 | 2025 | 2025-04-01 | Year_3 | P-55 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for MSEB line cross work | 0.70486 | 0.70486 | 0.72569 | 0 | 0.5 | 0.5 | Work Completed | Close | 0.011364 | site average | 55 | IG Unscheduled Maintenance
2025-04-05 | 2026 | 2025 | 2025-04-01 | Year_3 | P-01 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.36111 | 0.36111 | 0.81597 | 0 | 10.9167 | 10.9167 | WTG- 01 Isolator shifting work | Close | 0.24811 | site average | 1318 | IG Unscheduled Maintenance
2025-04-05 | 2026 | 2025 | 2025-04-01 | Year_3 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.81597 | 0.81597 | 0.82986 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 40 | IG Unscheduled Maintenance
2025-04-05 | 2026 | 2025 | 2025-04-01 | Year_3 | P-02 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.36111 | 0.36111 | 0.37847 | 0 | 0.41667 | 0.41667 | WTG- 01 line jump open work | Close | 0.0094697 | site average | 91 | IG Unscheduled Maintenance
2025-04-05 | 2026 | 2025 | 2025-04-01 | Year_3 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.37847 | 0.37847 | 0.39236 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 40 | IG Unscheduled Maintenance
2025-04-05 | 2026 | 2025 | 2025-04-01 | Year_3 | P-03 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.36111 | 0.36111 | 0.37847 | 0 | 0.41667 | 0.41667 | WTG- 01 line jump open work | Close | 0.0094697 | site average | 91 | IG Unscheduled Maintenance
2025-04-05 | 2026 | 2025 | 2025-04-01 | Year_3 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.37847 | 0.37847 | 0.39236 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 40 | IG Unscheduled Maintenance
2025-04-05 | 2026 | 2025 | 2025-04-01 | Year_3 | P-07 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.36111 | 0.36111 | 0.37847 | 0 | 0.41667 | 0.41667 | WTG- 01 line jump open work | Close | 0.0094697 | site average | 91 | IG Unscheduled Maintenance
2025-04-05 | 2026 | 2025 | 2025-04-01 | Year_3 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.37847 | 0.37847 | 0.39236 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 40 | IG Unscheduled Maintenance
2025-04-05 | 2026 | 2025 | 2025-04-01 | Year_3 | P-18 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.36111 | 0.36111 | 0.37847 | 0 | 0.41667 | 0.41667 | WTG- 01 line jump open work | Close | 0.0094697 | site average | 91 | IG Unscheduled Maintenance
2025-04-05 | 2026 | 2025 | 2025-04-01 | Year_3 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.37847 | 0.37847 | 0.39236 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 40 | IG Unscheduled Maintenance
2025-04-05 | 2026 | 2025 | 2025-04-01 | Year_3 | P-31 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.36111 | 0.36111 | 0.37847 | 0 | 0.41667 | 0.41667 | WTG- 01 line jump open work | Close | 0.0094697 | site average | 91 | IG Unscheduled Maintenance
2025-04-05 | 2026 | 2025 | 2025-04-01 | Year_3 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.37847 | 0.37847 | 0.39236 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 40 | IG Unscheduled Maintenance
2025-04-05 | 2026 | 2025 | 2025-04-01 | Year_3 | P-56 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.36111 | 0.36111 | 0.37847 | 0 | 0.41667 | 0.41667 | WTG- 01 line jump open work | Close | 0.0094697 | site average | 91 | IG Unscheduled Maintenance
2025-04-05 | 2026 | 2025 | 2025-04-01 | Year_3 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.37847 | 0.37847 | 0.39236 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 40 | IG Unscheduled Maintenance
2025-04-05 | 2026 | 2025 | 2025-04-01 | Year_3 | P-02 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.78472 | 0.78472 | 0.81597 | 0 | 0.75 | 0.75 | WTG- 01 line jump connecting work | Close | 0.017045 | site average | 50 | IG Unscheduled Maintenance
2025-04-05 | 2026 | 2025 | 2025-04-01 | Year_3 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.81597 | 0.81597 | 0.82986 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 40 | IG Unscheduled Maintenance
2025-04-05 | 2026 | 2025 | 2025-04-01 | Year_3 | P-03 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.78472 | 0.78472 | 0.81597 | 0 | 0.75 | 0.75 | WTG- 01 line jump connecting work | Close | 0.017045 | site average | 50 | IG Unscheduled Maintenance
2025-04-05 | 2026 | 2025 | 2025-04-01 | Year_3 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.81597 | 0.81597 | 0.82986 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 40 | IG Unscheduled Maintenance
2025-04-05 | 2026 | 2025 | 2025-04-01 | Year_3 | P-07 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.78472 | 0.78472 | 0.81597 | 0 | 0.75 | 0.75 | WTG- 01 line jump connecting work | Close | 0.017045 | site average | 50 | IG Unscheduled Maintenance
2025-04-05 | 2026 | 2025 | 2025-04-01 | Year_3 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.81597 | 0.81597 | 0.82986 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 40 | IG Unscheduled Maintenance
2025-04-05 | 2026 | 2025 | 2025-04-01 | Year_3 | P-18 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.78472 | 0.78472 | 0.81597 | 0 | 0.75 | 0.75 | WTG- 01 line jump connecting work | Close | 0.017045 | site average | 50 | IG Unscheduled Maintenance
2025-04-05 | 2026 | 2025 | 2025-04-01 | Year_3 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.81597 | 0.81597 | 0.82986 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 40 | IG Unscheduled Maintenance
2025-04-05 | 2026 | 2025 | 2025-04-01 | Year_3 | P-31 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.78472 | 0.78472 | 0.81597 | 0 | 0.75 | 0.75 | WTG- 01 line jump connecting work | Close | 0.017045 | site average | 50 | IG Unscheduled Maintenance
2025-04-05 | 2026 | 2025 | 2025-04-01 | Year_3 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.81597 | 0.81597 | 0.82986 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 40 | IG Unscheduled Maintenance
2025-04-05 | 2026 | 2025 | 2025-04-01 | Year_3 | P-56 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.78472 | 0.78472 | 0.81597 | 0 | 0.75 | 0.75 | WTG- 01 line jump connecting work | Close | 0.017045 | site average | 50 | IG Unscheduled Maintenance
2025-04-05 | 2026 | 2025 | 2025-04-01 | Year_3 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.81597 | 0.81597 | 0.82986 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 40 | IG Unscheduled Maintenance
2025-04-06 | 2026 | 2025 | 2025-04-01 | Year_3 | P-01 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.38958 | 0.38958 | 0.41181 | 0 | 0.53333 | 0.53333 | WTG- 31 line jump open work | Close | 0.012121 | site average | 47 | IG Unscheduled Maintenance
2025-04-06 | 2026 | 2025 | 2025-04-01 | Year_3 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.41181 | 0.41181 | 0.42569 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 29 | IG Unscheduled Maintenance
2025-04-06 | 2026 | 2025 | 2025-04-01 | Year_3 | P-02 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.38958 | 0.38958 | 0.41181 | 0 | 0.53333 | 0.53333 | WTG- 31 line jump open work | Close | 0.012121 | site average | 47 | IG Unscheduled Maintenance
2025-04-06 | 2026 | 2025 | 2025-04-01 | Year_3 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.41181 | 0.41181 | 0.42569 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 29 | IG Unscheduled Maintenance
2025-04-06 | 2026 | 2025 | 2025-04-01 | Year_3 | P-03 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.38958 | 0.38958 | 0.41181 | 0 | 0.53333 | 0.53333 | WTG- 31 line jump open work | Close | 0.012121 | site average | 47 | IG Unscheduled Maintenance
2025-04-06 | 2026 | 2025 | 2025-04-01 | Year_3 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.41181 | 0.41181 | 0.42569 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 29 | IG Unscheduled Maintenance
2025-04-06 | 2026 | 2025 | 2025-04-01 | Year_3 | P-07 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.38958 | 0.38958 | 0.41181 | 0 | 0.53333 | 0.53333 | WTG- 31 line jump open work | Close | 0.012121 | site average | 47 | IG Unscheduled Maintenance
2025-04-06 | 2026 | 2025 | 2025-04-01 | Year_3 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.41181 | 0.41181 | 0.42569 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 29 | IG Unscheduled Maintenance
2025-04-06 | 2026 | 2025 | 2025-04-01 | Year_3 | P-18 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.38958 | 0.38958 | 0.41181 | 0 | 0.53333 | 0.53333 | WTG- 31 line jump open work | Close | 0.012121 | site average | 47 | IG Unscheduled Maintenance
2025-04-06 | 2026 | 2025 | 2025-04-01 | Year_3 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.41181 | 0.41181 | 0.42569 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 29 | IG Unscheduled Maintenance
2025-04-06 | 2026 | 2025 | 2025-04-01 | Year_3 | P-31 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.38958 | 0.38958 | 0.80625 | 0 | 10 | 10 | WTG- 31 Isolator shifting work | Close | 0.22727 | site average | 879 | IG Unscheduled Maintenance
2025-04-06 | 2026 | 2025 | 2025-04-01 | Year_3 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.80625 | 0.80625 | 0.82014 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 4 | IG Unscheduled Maintenance
2025-04-06 | 2026 | 2025 | 2025-04-01 | Year_3 | P-56 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.38958 | 0.38958 | 0.41181 | 0 | 0.53333 | 0.53333 | WTG- 31 line jump open work | Close | 0.012121 | site average | 47 | IG Unscheduled Maintenance
2025-04-06 | 2026 | 2025 | 2025-04-01 | Year_3 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.41181 | 0.41181 | 0.42569 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 29 | IG Breakdown Maintenance
2025-04-06 | 2026 | 2025 | 2025-04-01 | Year_3 | Wind_F4 | PWEPL | MSEDCL | 29.55% | Feeder tripped by E/F | 0.54028 | 0.54028 | 0.56597 | 0 | 0.61667 | 0.61667 | Test charged taken charged successfully | Close | 0.1822 | site average | 702 | IG Breakdown Maintenance
2025-04-06 | 2026 | 2025 | 2025-04-01 | Year_3 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.56597 | 0.56597 | 0.57986 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 27 | IG Breakdown Maintenance
2025-04-06 | 2026 | 2025 | 2025-04-01 | Year_3 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.56597 | 0.56597 | 0.57986 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 27 | IG Breakdown Maintenance
2025-04-06 | 2026 | 2025 | 2025-04-01 | Year_3 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.56597 | 0.56597 | 0.57986 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 27 | IG Breakdown Maintenance
2025-04-06 | 2026 | 2025 | 2025-04-01 | Year_3 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.56597 | 0.56597 | 0.57986 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 27 | IG Breakdown Maintenance
2025-04-06 | 2026 | 2025 | 2025-04-01 | Year_3 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.56597 | 0.56597 | 0.57986 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 27 | IG Breakdown Maintenance
2025-04-06 | 2026 | 2025 | 2025-04-01 | Year_3 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.56597 | 0.56597 | 0.57986 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 27 | IG Breakdown Maintenance
2025-04-06 | 2026 | 2025 | 2025-04-01 | Year_3 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.56597 | 0.56597 | 0.57986 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 27 | IG Breakdown Maintenance
2025-04-06 | 2026 | 2025 | 2025-04-01 | Year_3 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.56597 | 0.56597 | 0.57986 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 27 | IG Breakdown Maintenance
2025-04-06 | 2026 | 2025 | 2025-04-01 | Year_3 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.56597 | 0.56597 | 0.57986 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 27 | IG Breakdown Maintenance
2025-04-06 | 2026 | 2025 | 2025-04-01 | Year_3 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.56597 | 0.56597 | 0.57986 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 27 | IG Breakdown Maintenance
2025-04-06 | 2026 | 2025 | 2025-04-01 | Year_3 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.56597 | 0.56597 | 0.57986 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 27 | IG Breakdown Maintenance
2025-04-06 | 2026 | 2025 | 2025-04-01 | Year_3 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.56597 | 0.56597 | 0.57986 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 27 | IG Unscheduled Maintenance
2025-04-06 | 2026 | 2025 | 2025-04-01 | Year_3 | P-01 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.77569 | 0.77569 | 0.80625 | 0 | 0.73333 | 0.73333 | WTG- 31 line jump Connect work | Close | 0.016667 | site average | 65 | IG Unscheduled Maintenance
2025-04-06 | 2026 | 2025 | 2025-04-01 | Year_3 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.80625 | 0.80625 | 0.82014 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 29 | IG Unscheduled Maintenance
2025-04-06 | 2026 | 2025 | 2025-04-01 | Year_3 | P-02 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.77569 | 0.77569 | 0.80625 | 0 | 0.73333 | 0.73333 | WTG- 31 line jump Connect work | Close | 0.016667 | site average | 65 | IG Unscheduled Maintenance
2025-04-06 | 2026 | 2025 | 2025-04-01 | Year_3 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.80625 | 0.80625 | 0.82014 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 29 | IG Unscheduled Maintenance
2025-04-06 | 2026 | 2025 | 2025-04-01 | Year_3 | P-03 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.77569 | 0.77569 | 0.80625 | 0 | 0.73333 | 0.73333 | WTG- 31 line jump Connect work | Close | 0.016667 | site average | 65 | IG Unscheduled Maintenance
2025-04-06 | 2026 | 2025 | 2025-04-01 | Year_3 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.80625 | 0.80625 | 0.82014 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 29 | IG Unscheduled Maintenance
2025-04-06 | 2026 | 2025 | 2025-04-01 | Year_3 | P-07 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.77569 | 0.77569 | 0.80625 | 0 | 0.73333 | 0.73333 | WTG- 31 line jump Connect work | Close | 0.016667 | site average | 65 | IG Unscheduled Maintenance
2025-04-06 | 2026 | 2025 | 2025-04-01 | Year_3 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.80625 | 0.80625 | 0.82014 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 29 | IG Unscheduled Maintenance
2025-04-06 | 2026 | 2025 | 2025-04-01 | Year_3 | P-18 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.77569 | 0.77569 | 0.80625 | 0 | 0.73333 | 0.73333 | WTG- 31 line jump Connect work | Close | 0.016667 | site average | 65 | IG Unscheduled Maintenance
2025-04-06 | 2026 | 2025 | 2025-04-01 | Year_3 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.80625 | 0.80625 | 0.82014 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 29 | IG Unscheduled Maintenance
2025-04-06 | 2026 | 2025 | 2025-04-01 | Year_3 | P-56 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.77569 | 0.77569 | 0.80625 | 0 | 0.73333 | 0.73333 | WTG- 31 line jump Connect work | Close | 0.016667 | site average | 65 | IG Unscheduled Maintenance
2025-04-06 | 2026 | 2025 | 2025-04-01 | Year_3 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.80625 | 0.80625 | 0.82014 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 29 | IG Unscheduled Maintenance
2025-04-07 | 2026 | 2025 | 2025-04-01 | Year_3 | P-05 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.35833 | 0.35833 | 0.39514 | 0 | 0.88333 | 0.88333 | WTG- 40 Isolator shifting work | Close | 0.020076 | site average | 112 | IG Unscheduled Maintenance
2025-04-07 | 2026 | 2025 | 2025-04-01 | Year_3 | P-05 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.39514 | 0.39514 | 0.40208 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | site average | 21 | IG Unscheduled Maintenance
2025-04-07 | 2026 | 2025 | 2025-04-01 | Year_3 | P-06 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.35833 | 0.35833 | 0.39514 | 0 | 0.88333 | 0.88333 | WTG- 40 Isolator shifting work | Close | 0.020076 | site average | 112 | IG Unscheduled Maintenance
2025-04-07 | 2026 | 2025 | 2025-04-01 | Year_3 | P-06 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.39514 | 0.39514 | 0.40903 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 42 | IG Unscheduled Maintenance
2025-04-07 | 2026 | 2025 | 2025-04-01 | Year_3 | P-40 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.35833 | 0.35833 | 0.7875 | 0 | 10.3 | 10.3 | WTG- 40 Isolator shifting work | Close | 0.23409 | site average | 1272 | IG Unscheduled Maintenance
2025-04-07 | 2026 | 2025 | 2025-04-01 | Year_3 | P-40 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.7875 | 0.7875 | 0.79097 | 0 | 0.083333 | 0.083333 | Rebooted the PLC & reset at scada | Close | 0.0018939 | site average | 42 | IG Unscheduled Maintenance
2025-04-07 | 2026 | 2025 | 2025-04-01 | Year_3 | P-41 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.35833 | 0.35833 | 0.39514 | 0 | 0.88333 | 0.88333 | WTG- 40 Isolator shifting work | Close | 0.020076 | site average | 112 | IG Unscheduled Maintenance
2025-04-07 | 2026 | 2025 | 2025-04-01 | Year_3 | P-41 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.39514 | 0.39514 | 0.40903 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 42 | IG Unscheduled Maintenance
2025-04-07 | 2026 | 2025 | 2025-04-01 | Year_3 | P-05 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.74306 | 0.74306 | 0.7875 | 0 | 1.0667 | 1.0667 | WTG- 41 Isolator shifting work | Close | 0.024242 | site average | 135 | IG Unscheduled Maintenance
2025-04-07 | 2026 | 2025 | 2025-04-01 | Year_3 | P-05 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.7875 | 0.7875 | 0.80139 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 42 | IG Unscheduled Maintenance
2025-04-07 | 2026 | 2025 | 2025-04-01 | Year_3 | P-06 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.74306 | 0.74306 | 0.7875 | 0 | 1.0667 | 1.0667 | WTG- 41 Isolator shifting work | Close | 0.024242 | site average | 135 | IG Unscheduled Maintenance
2025-04-07 | 2026 | 2025 | 2025-04-01 | Year_3 | P-06 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.7875 | 0.7875 | 0.80139 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 42 | IG Unscheduled Maintenance
2025-04-07 | 2026 | 2025 | 2025-04-01 | Year_3 | P-41 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.74306 | 0.74306 | 0.7875 | 0 | 1.0667 | 1.0667 | WTG- 41 Isolator shifting work | Close | 0.024242 | site average | 135 | IG Unscheduled Maintenance
2025-04-07 | 2026 | 2025 | 2025-04-01 | Year_3 | P-41 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.7875 | 0.7875 | 0.80139 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 42 | IG Unscheduled Maintenance
2025-04-08 | 2026 | 2025 | 2025-04-01 | Year_3 | P-42 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.3375 | 0.3375 | 0.37292 | 0 | 0.85 | 0.85 | WTG- 47 line jump Connect work | Close | 0.019318 | site average | 74 | IG Unscheduled Maintenance
2025-04-08 | 2026 | 2025 | 2025-04-01 | Year_3 | P-42 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.37292 | 0.37292 | 0.38681 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 20 | IG Unscheduled Maintenance
2025-04-08 | 2026 | 2025 | 2025-04-01 | Year_3 | P-45 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.3375 | 0.3375 | 0.37292 | 0 | 0.85 | 0.85 | WTG- 47 line jump Connect work | Close | 0.019318 | site average | 74 | IG Unscheduled Maintenance
2025-04-08 | 2026 | 2025 | 2025-04-01 | Year_3 | P-45 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.37292 | 0.37292 | 0.38681 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 20 | IG Unscheduled Maintenance
2025-04-08 | 2026 | 2025 | 2025-04-01 | Year_3 | P-46 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.3375 | 0.3375 | 0.37292 | 0 | 0.85 | 0.85 | WTG- 47 line jump Connect work | Close | 0.019318 | site average | 74 | IG Unscheduled Maintenance
2025-04-08 | 2026 | 2025 | 2025-04-01 | Year_3 | P-46 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.37292 | 0.37292 | 0.38681 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 20 | IG Unscheduled Maintenance
2025-04-08 | 2026 | 2025 | 2025-04-01 | Year_3 | P-47 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.3375 | 0.3375 | 0.70972 | 0 | 8.9333 | 8.9333 | WTG- 47 Isolator shifting work | Close | 0.20303 | site average | 785 | IG Unscheduled Maintenance
2025-04-08 | 2026 | 2025 | 2025-04-01 | Year_3 | P-48 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.3375 | 0.3375 | 0.37292 | 0 | 0.85 | 0.85 | WTG- 47 line jump Connect work | Close | 0.019318 | site average | 74 | IG Unscheduled Maintenance
2025-04-08 | 2026 | 2025 | 2025-04-01 | Year_3 | P-48 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.37292 | 0.37292 | 0.38681 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 20 | IG Unscheduled Maintenance
2025-04-09 | 2026 | 2025 | 2025-04-01 | Year_3 | P-42 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.33542 | 0.33542 | 0.36528 | 0 | 0.71667 | 0.71667 | WTG- 48 line jump open work | Close | 0.016288 | site average | 95 | IG Unscheduled Maintenance
2025-04-09 | 2026 | 2025 | 2025-04-01 | Year_3 | P-42 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.36528 | 0.36528 | 0.37917 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 44 | IG Unscheduled Maintenance
2025-04-09 | 2026 | 2025 | 2025-04-01 | Year_3 | P-45 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.33542 | 0.33542 | 0.36528 | 0 | 0.71667 | 0.71667 | WTG- 48 line jump open work | Close | 0.016288 | site average | 95 | IG Unscheduled Maintenance
2025-04-09 | 2026 | 2025 | 2025-04-01 | Year_3 | P-45 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.36528 | 0.36528 | 0.37917 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 44 | IG Unscheduled Maintenance
2025-04-09 | 2026 | 2025 | 2025-04-01 | Year_3 | P-46 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.33542 | 0.33542 | 0.36528 | 0 | 0.71667 | 0.71667 | WTG- 48 line jump open work | Close | 0.016288 | site average | 95 | IG Unscheduled Maintenance
2025-04-09 | 2026 | 2025 | 2025-04-01 | Year_3 | P-46 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.36528 | 0.36528 | 0.36806 | 0 | 0.066667 | 0.066667 | Rebooted the PLC & reset at scada | Close | 0.0015152 | site average | 9 | IG Unscheduled Maintenance
2025-04-09 | 2026 | 2025 | 2025-04-01 | Year_3 | P-47 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.33542 | 0.33542 | 0.36528 | 0 | 0.71667 | 0.71667 | WTG- 48 line jump open work | Close | 0.016288 | site average | 95 | IG Unscheduled Maintenance
2025-04-09 | 2026 | 2025 | 2025-04-01 | Year_3 | P-47 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.36528 | 0.36528 | 0.37917 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 44 | IG Unscheduled Maintenance
2025-04-09 | 2026 | 2025 | 2025-04-01 | Year_3 | P-48 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.33542 | 0.33542 | 0.77847 | 0 | 10.6333 | 10.6333 | WTG- 48 Isolator shifting work | Close | 0.24167 | site average | 1400 | IG Unscheduled Maintenance
2025-04-09 | 2026 | 2025 | 2025-04-01 | Year_3 | P-48 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.77847 | 0.77847 | 0.78889 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | site average | 40 | IG Unscheduled Maintenance
2025-04-09 | 2026 | 2025 | 2025-04-01 | Year_3 | P-42 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.73958 | 0.73958 | 0.77847 | 0 | 0.93333 | 0.93333 | WTG- 47 line jump Connect work | Close | 0.021212 | site average | 123 | IG Unscheduled Maintenance
2025-04-09 | 2026 | 2025 | 2025-04-01 | Year_3 | P-42 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.77847 | 0.77847 | 0.78472 | 0 | 0.15 | 0.15 | Rebooted the PLC & reset at scada | Close | 0.0034091 | site average | 20 | IG Unscheduled Maintenance
2025-04-09 | 2026 | 2025 | 2025-04-01 | Year_3 | P-45 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.73958 | 0.73958 | 0.77847 | 0 | 0.93333 | 0.93333 | WTG- 47 line jump Connect work | Close | 0.021212 | site average | 123 | IG Unscheduled Maintenance
2025-04-09 | 2026 | 2025 | 2025-04-01 | Year_3 | P-45 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.77847 | 0.77847 | 0.78819 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | site average | 30 | IG Unscheduled Maintenance
2025-04-09 | 2026 | 2025 | 2025-04-01 | Year_3 | P-46 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.73958 | 0.73958 | 0.77847 | 0 | 0.93333 | 0.93333 | WTG- 47 line jump Connect work | Close | 0.021212 | site average | 123 | IG Unscheduled Maintenance
2025-04-09 | 2026 | 2025 | 2025-04-01 | Year_3 | P-46 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.77847 | 0.77847 | 0.78472 | 0 | 0.15 | 0.15 | Rebooted the PLC & reset at scada | Close | 0.0034091 | site average | 20 | IG Unscheduled Maintenance
2025-04-09 | 2026 | 2025 | 2025-04-01 | Year_3 | P-47 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.73958 | 0.73958 | 0.77847 | 0 | 0.93333 | 0.93333 | WTG- 47 line jump Connect work | Close | 0.021212 | site average | 123 | IG Unscheduled Maintenance
2025-04-09 | 2026 | 2025 | 2025-04-01 | Year_3 | P-47 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.77847 | 0.77847 | 0.78611 | 0 | 0.18333 | 0.18333 | Rebooted the PLC & reset at scada | Close | 0.0041667 | site average | 24 | IG Unscheduled Maintenance
2025-04-09 | 2026 | 2025 | 2025-04-01 | Year_3 | Wind_F1 | PWEPL | MSEDCL | 22.73% | Feeder tripped by O/C | 0.088194 | 0.088194 | 0.10278 | 0 | 0.35 | 0.35 | Test charged taken charged successfully | Close | 0.079545 | site average | 360 | IG Unscheduled Maintenance
2025-04-09 | 2026 | 2025 | 2025-04-01 | Year_3 | P-08 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.10278 | 0.10278 | 0.11667 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 36 | IG Breakdown Maintenance
2025-04-09 | 2026 | 2025 | 2025-04-01 | Year_3 | P-09 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.10278 | 0.10278 | 0.11458 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | site average | 36 | IG Breakdown Maintenance
2025-04-09 | 2026 | 2025 | 2025-04-01 | Year_3 | P-10 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.10278 | 0.10278 | 0.11667 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 36 | IG Breakdown Maintenance
2025-04-09 | 2026 | 2025 | 2025-04-01 | Year_3 | P-11 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.10278 | 0.10278 | 0.11528 | 0 | 0.3 | 0.3 | Rebooted the PLC & reset at scada | Close | 0.0068182 | site average | 36 | IG Breakdown Maintenance
2025-04-09 | 2026 | 2025 | 2025-04-01 | Year_3 | P-12 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.10278 | 0.10278 | 0.11667 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 36 | IG Breakdown Maintenance
2025-04-09 | 2026 | 2025 | 2025-04-01 | Year_3 | P-13 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.10278 | 0.10278 | 0.11181 | 0 | 0.21667 | 0.21667 | Rebooted the PLC & reset at scada | Close | 0.0049242 | site average | 36 | IG Breakdown Maintenance
2025-04-09 | 2026 | 2025 | 2025-04-01 | Year_3 | P-25 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.10278 | 0.10278 | 0.11667 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 36 | IG Breakdown Maintenance
2025-04-09 | 2026 | 2025 | 2025-04-01 | Year_3 | P-26 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.10278 | 0.10278 | 0.11667 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 36 | IG Breakdown Maintenance
2025-04-09 | 2026 | 2025 | 2025-04-01 | Year_3 | P-27 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.10278 | 0.10278 | 0.11389 | 0 | 0.26667 | 0.26667 | Rebooted the PLC & reset at scada | Close | 0.0060606 | site average | 36 | IG Breakdown Maintenance
2025-04-09 | 2026 | 2025 | 2025-04-01 | Year_3 | P-28 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.10278 | 0.10278 | 0.11667 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 36 | IG Breakdown Maintenance
2025-04-10 | 2026 | 2025 | 2025-04-01 | Year_3 | P-32 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.33194 | 0.33194 | 0.36042 | 0 | 0.68333 | 0.68333 | WTG- 51 & 52 line jump open work | Close | 0.01553 | site average | 169 | IG Unscheduled Maintenance
2025-04-10 | 2026 | 2025 | 2025-04-01 | Year_3 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.36042 | 0.36042 | 0.36736 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | site average | 41 | IG Unscheduled Maintenance
2025-04-10 | 2026 | 2025 | 2025-04-01 | Year_3 | P-37 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.33194 | 0.33194 | 0.36042 | 0 | 0.68333 | 0.68333 | WTG- 51 & 52 line jump open work | Close | 0.01553 | site average | 169 | IG Unscheduled Maintenance
2025-04-10 | 2026 | 2025 | 2025-04-01 | Year_3 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.36042 | 0.36042 | 0.36736 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | site average | 41 | IG Unscheduled Maintenance
2025-04-10 | 2026 | 2025 | 2025-04-01 | Year_3 | P-50 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.33194 | 0.33194 | 0.36042 | 0 | 0.68333 | 0.68333 | WTG- 51 & 52 line jump open work | Close | 0.01553 | site average | 169 | IG Unscheduled Maintenance
2025-04-10 | 2026 | 2025 | 2025-04-01 | Year_3 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.36042 | 0.36042 | 0.36736 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | site average | 41 | IG Unscheduled Maintenance
2025-04-10 | 2026 | 2025 | 2025-04-01 | Year_3 | P-51 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.33194 | 0.33194 | 0.875 | 0 | 13.0333 | 13.0333 | WTG- 51 Isolator shifting work | Close | 0.29621 | site average | 3226 | IG Unscheduled Maintenance
2025-04-10 | 2026 | 2025 | 2025-04-01 | Year_3 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.875 | 0.875 | 0.88194 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | site average | 41 | IG Unscheduled Maintenance
2025-04-10 | 2026 | 2025 | 2025-04-01 | Year_3 | P-52 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.33194 | 0.33194 | 0.875 | 0 | 13.0333 | 13.0333 | WTG- 52 Isolator shifting work | Close | 0.29621 | site average | 3226 | IG Unscheduled Maintenance
2025-04-10 | 2026 | 2025 | 2025-04-01 | Year_3 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.875 | 0.875 | 0.88194 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | site average | 41 | IG Unscheduled Maintenance
2025-04-10 | 2026 | 2025 | 2025-04-01 | Year_3 | P-55 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.33194 | 0.33194 | 0.36042 | 0 | 0.68333 | 0.68333 | WTG- 51 & 52 line jump open work | Close | 0.01553 | site average | 169 | IG Unscheduled Maintenance
2025-04-10 | 2026 | 2025 | 2025-04-01 | Year_3 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.36042 | 0.36042 | 0.36736 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | site average | 41 | IG Unscheduled Maintenance
2025-04-10 | 2026 | 2025 | 2025-04-01 | Year_3 | P-32 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.85278 | 0.85278 | 0.875 | 0 | 0.53333 | 0.53333 | WTG- 51 & 52 line jump Connect work | Close | 0.012121 | site average | 132 | IG Unscheduled Maintenance
2025-04-10 | 2026 | 2025 | 2025-04-01 | Year_3 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.875 | 0.875 | 0.88681 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | site average | 70 | IG Unscheduled Maintenance
2025-04-10 | 2026 | 2025 | 2025-04-01 | Year_3 | P-37 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.85278 | 0.85278 | 0.875 | 0 | 0.53333 | 0.53333 | WTG- 51 & 52 line jump Connect work | Close | 0.012121 | site average | 132 | IG Unscheduled Maintenance
2025-04-10 | 2026 | 2025 | 2025-04-01 | Year_3 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.875 | 0.875 | 0.88194 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | site average | 41 | IG Unscheduled Maintenance
2025-04-10 | 2026 | 2025 | 2025-04-01 | Year_3 | P-50 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.85278 | 0.85278 | 0.875 | 0 | 0.53333 | 0.53333 | WTG- 51 & 52 line jump Connect work | Close | 0.012121 | site average | 132 | IG Unscheduled Maintenance
2025-04-10 | 2026 | 2025 | 2025-04-01 | Year_3 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.875 | 0.875 | 0.88611 | 0 | 0.26667 | 0.26667 | Rebooted the PLC & reset at scada | Close | 0.0060606 | site average | 66 | IG Unscheduled Maintenance
2025-04-10 | 2026 | 2025 | 2025-04-01 | Year_3 | P-55 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.85278 | 0.85278 | 0.875 | 0 | 0.53333 | 0.53333 | WTG- 51 & 52 line jump Connect work | Close | 0.012121 | site average | 132 | IG Unscheduled Maintenance
2025-04-10 | 2026 | 2025 | 2025-04-01 | Year_3 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.875 | 0.875 | 0.88125 | 0 | 0.15 | 0.15 | Rebooted the PLC & reset at scada | Close | 0.0034091 | site average | 37 | IG Unscheduled Maintenance
2025-04-11 | 2026 | 2025 | 2025-04-01 | Year_3 | P-32 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.46875 | 0.46875 | 0.87639 | 0 | 9.7833 | 9.7833 | WTG- 32 Isolator shifting work | Close | 0.22235 | site average | 2168 | IG Unscheduled Maintenance
2025-04-11 | 2026 | 2025 | 2025-04-01 | Year_3 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.87639 | 0.87639 | 0.89028 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 74 | IG Unscheduled Maintenance
2025-04-11 | 2026 | 2025 | 2025-04-01 | Year_3 | P-37 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.46875 | 0.46875 | 0.87639 | 0 | 9.7833 | 9.7833 | WTG- 37 Isolator shifting work | Close | 0.22235 | site average | 2168 | IG Unscheduled Maintenance
2025-04-11 | 2026 | 2025 | 2025-04-01 | Year_3 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.87639 | 0.87639 | 0.89028 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 74 | IG Unscheduled Maintenance
2025-04-11 | 2026 | 2025 | 2025-04-01 | Year_3 | P-50 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.46875 | 0.46875 | 0.51597 | 0 | 1.1333 | 1.1333 | WTG- 32 & 37 line jump open work | Close | 0.025758 | site average | 251 | IG Unscheduled Maintenance
2025-04-11 | 2026 | 2025 | 2025-04-01 | Year_3 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.51597 | 0.51597 | 0.52986 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 74 | IG Unscheduled Maintenance
2025-04-11 | 2026 | 2025 | 2025-04-01 | Year_3 | P-51 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.46875 | 0.46875 | 0.51597 | 0 | 1.1333 | 1.1333 | WTG- 32 & 37 line jump open work | Close | 0.025758 | site average | 251 | IG Unscheduled Maintenance
2025-04-11 | 2026 | 2025 | 2025-04-01 | Year_3 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.51597 | 0.51597 | 0.52986 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 74 | IG Unscheduled Maintenance
2025-04-11 | 2026 | 2025 | 2025-04-01 | Year_3 | P-52 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.46875 | 0.46875 | 0.51597 | 0 | 1.1333 | 1.1333 | WTG- 32 & 37 line jump open work | Close | 0.025758 | site average | 251 | IG Unscheduled Maintenance
2025-04-11 | 2026 | 2025 | 2025-04-01 | Year_3 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.51597 | 0.51597 | 0.52986 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 74 | IG Unscheduled Maintenance
2025-04-11 | 2026 | 2025 | 2025-04-01 | Year_3 | P-55 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.46875 | 0.46875 | 0.51597 | 0 | 1.1333 | 1.1333 | WTG- 32 & 37 line jump open work | Close | 0.025758 | site average | 251 | IG Unscheduled Maintenance
2025-04-11 | 2026 | 2025 | 2025-04-01 | Year_3 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.51597 | 0.51597 | 0.52986 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 74 | IG Unscheduled Maintenance
2025-04-11 | 2026 | 2025 | 2025-04-01 | Year_3 | P-50 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.85208 | 0.85208 | 0.87639 | 0 | 0.58333 | 0.58333 | WTG- 32 & 37 line jump Connect work | Close | 0.013258 | site average | 129 | IG Unscheduled Maintenance
2025-04-11 | 2026 | 2025 | 2025-04-01 | Year_3 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.87639 | 0.87639 | 0.89028 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 74 | IG Unscheduled Maintenance
2025-04-11 | 2026 | 2025 | 2025-04-01 | Year_3 | P-51 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.85208 | 0.85208 | 0.87639 | 0 | 0.58333 | 0.58333 | WTG- 32 & 37 line jump Connect work | Close | 0.013258 | site average | 129 | IG Unscheduled Maintenance
2025-04-11 | 2026 | 2025 | 2025-04-01 | Year_3 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.87639 | 0.87639 | 0.89028 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 74 | IG Unscheduled Maintenance
2025-04-11 | 2026 | 2025 | 2025-04-01 | Year_3 | P-52 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.85208 | 0.85208 | 0.87639 | 0 | 0.58333 | 0.58333 | WTG- 32 & 37 line jump Connect work | Close | 0.013258 | site average | 129 | IG Unscheduled Maintenance
2025-04-11 | 2026 | 2025 | 2025-04-01 | Year_3 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.87639 | 0.87639 | 0.89028 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 74 | IG Unscheduled Maintenance
2025-04-11 | 2026 | 2025 | 2025-04-01 | Year_3 | P-55 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 0.85208 | 0.85208 | 0.87639 | 0 | 0.58333 | 0.58333 | WTG- 32 & 37 line jump Connect work | Close | 0.013258 | site average | 129 | IG Unscheduled Maintenance
2025-04-11 | 2026 | 2025 | 2025-04-01 | Year_3 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.87639 | 0.87639 | 0.89028 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 74 | IG Unscheduled Maintenance
2025-04-12 | 2026 | 2025 | 2025-04-01 | Year_3 | P-34 | PWEPL | MSEDCL | 2.273% | VCB Tripped | 0.16528 | 0.16528 | 0.18403 | 0 | 0.45 | 0.45 | VCB reset & Charge | Close | 0.010227 | site average | 226 | IG Breakdown Maintenance
2025-04-12 | 2026 | 2025 | 2025-04-01 | Year_3 | P-34 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.18403 | 0.18403 | 0.18681 | 0 | 0.066667 | 0.066667 | Rebooted the PLC & reset at scada | Close | 0.0015152 | site average | 182 | IG Breakdown Maintenance
2025-04-17 | 2026 | 2025 | 2025-04-01 | Year_3 | Wind_F2 | PWEPL | MSEDCL | 27.27% | Feeder tripped by O/C | 0.52083 | 0.52083 | 0.53056 | 0 | 0.23333 | 0.23333 | Test charged taken charged successfully | Close | 0.063636 | site average | 991 | IG Breakdown Maintenance
2025-04-17 | 2026 | 2025 | 2025-04-01 | Year_3 | P-14 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.53056 | 0.53056 | 0.53472 | 0 | 0.1 | 0.1 | Rebooted the PLC & reset at scada | Close | 0.0022727 | site average | 34 | IG Breakdown Maintenance
2025-04-17 | 2026 | 2025 | 2025-04-01 | Year_3 | P-15 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.53056 | 0.53056 | 0.53264 | 0 | 0.05 | 0.05 | Rebooted the PLC & reset at scada | Close | 0.0011364 | site average | 17 | IG Breakdown Maintenance
2025-04-17 | 2026 | 2025 | 2025-04-01 | Year_3 | P-16 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.53056 | 0.53056 | 0.53333 | 0 | 0.066667 | 0.066667 | Rebooted the PLC & reset at scada | Close | 0.0015152 | site average | 22 | IG Breakdown Maintenance
2025-04-17 | 2026 | 2025 | 2025-04-01 | Year_3 | P-17 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.53056 | 0.53056 | 0.53264 | 0 | 0.05 | 0.05 | Rebooted the PLC & reset at scada | Close | 0.0011364 | site average | 17 | IG Breakdown Maintenance
2025-04-17 | 2026 | 2025 | 2025-04-01 | Year_3 | P-19 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.53056 | 0.53056 | 0.53819 | 0 | 0.18333 | 0.18333 | Rebooted the PLC & reset at scada | Close | 0.0041667 | site average | 62 | IG Breakdown Maintenance
2025-04-17 | 2026 | 2025 | 2025-04-01 | Year_3 | P-20 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.53056 | 0.53056 | 0.53958 | 0 | 0.21667 | 0.21667 | Rebooted the PLC & reset at scada | Close | 0.0049242 | site average | 73 | IG Breakdown Maintenance
2025-04-17 | 2026 | 2025 | 2025-04-01 | Year_3 | P-38 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.53056 | 0.53056 | 0.53889 | 0 | 0.2 | 0.2 | Rebooted the PLC & reset at scada | Close | 0.0045455 | site average | 67 | IG Breakdown Maintenance
2025-04-17 | 2026 | 2025 | 2025-04-01 | Year_3 | P-04 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.53056 | 0.53056 | 0.53889 | 0 | 0.2 | 0.2 | Rebooted the PLC & reset at scada | Close | 0.0045455 | site average | 67 | IG Breakdown Maintenance
2025-04-17 | 2026 | 2025 | 2025-04-01 | Year_3 | P-22 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.53056 | 0.53056 | 0.53958 | 0 | 0.21667 | 0.21667 | Rebooted the PLC & reset at scada | Close | 0.0049242 | site average | 73 | IG Breakdown Maintenance
2025-04-17 | 2026 | 2025 | 2025-04-01 | Year_3 | P-23 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.53056 | 0.53056 | 0.53958 | 0 | 0.21667 | 0.21667 | Rebooted the PLC & reset at scada | Close | 0.0049242 | site average | 73 | IG Breakdown Maintenance
2025-04-17 | 2026 | 2025 | 2025-04-01 | Year_3 | P-34 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.53056 | 0.53056 | 0.54028 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | site average | 78 | IG Breakdown Maintenance
2025-04-17 | 2026 | 2025 | 2025-04-01 | Year_3 | P-43 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.53056 | 0.53056 | 0.53889 | 0 | 0.2 | 0.2 | Rebooted the PLC & reset at scada | Close | 0.0045455 | site average | 67 | IG Breakdown Maintenance
2025-04-21 | 2026 | 2025 | 2025-04-01 | Year_3 | Wind_F1 | PWEPL | MSEDCL | 22.73% | Feeder tripped by O/C | 22:56 | 22:56 | 23:59 | 0 | 1.05 | 1.05 | work in progress | Close | 0.23864 | site average | 3475 | IG Breakdown Maintenance
2025-04-22 | 2026 | 2025 | 2025-04-01 | Year_3 | Wind_F1 | PWEPL | MSEDCL | 22.73% | Feeder tripped by O/C | 0:00 | 0:00 | 0:20 | 0 | 0.33333 | 0.33333 | Test charged taken charged successfully | Close | 0.075758 | site average | 995 | IG Breakdown Maintenance
2025-04-22 | 2026 | 2025 | 2025-04-01 | Year_3 | P-08 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0:20 | 0:20 | 0:40 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 99.5 | IG Breakdown Maintenance
2025-04-22 | 2026 | 2025 | 2025-04-01 | Year_3 | P-09 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0:20 | 0:20 | 0:40 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 99.5 | IG Breakdown Maintenance
2025-04-22 | 2026 | 2025 | 2025-04-01 | Year_3 | P-10 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0:20 | 0:20 | 0:40 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 99.5 | IG Breakdown Maintenance
2025-04-22 | 2026 | 2025 | 2025-04-01 | Year_3 | P-11 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0:20 | 0:20 | 0:40 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 99.5 | IG Breakdown Maintenance
2025-04-22 | 2026 | 2025 | 2025-04-01 | Year_3 | P-12 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0:20 | 0:20 | 0:40 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 99.5 | IG Breakdown Maintenance
2025-04-22 | 2026 | 2025 | 2025-04-01 | Year_3 | P-13 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0:20 | 0:20 | 0:40 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 99.5 | IG Breakdown Maintenance
2025-04-22 | 2026 | 2025 | 2025-04-01 | Year_3 | P-25 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0:20 | 0:20 | 0:40 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 99.5 | IG Breakdown Maintenance
2025-04-22 | 2026 | 2025 | 2025-04-01 | Year_3 | P-26 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0:20 | 0:20 | 0:40 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 99.5 | IG Breakdown Maintenance
2025-04-22 | 2026 | 2025 | 2025-04-01 | Year_3 | P-27 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0:20 | 0:20 | 0:40 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 99.5 | IG Breakdown Maintenance
2025-04-22 | 2026 | 2025 | 2025-04-01 | Year_3 | P-28 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0:20 | 0:20 | 0:40 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 99.5 | IG Breakdown Maintenance
2025-04-23 | 2026 | 2025 | 2025-04-01 | Year_3 | P-08 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 10:16 | 10:16 | 19:55 | 0 | 9.65 | 9.65 | CT,PT cabling & tray Installation work | Close | 0.21932 | site average | 1694 | IG Unscheduled Maintenance
2025-04-23 | 2026 | 2025 | 2025-04-01 | Year_3 | P-08 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:55 | 19:55 | 20:15 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 60 | IG Unscheduled Maintenance
2025-04-23 | 2026 | 2025 | 2025-04-01 | Year_3 | P-25 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 10:16 | 10:16 | 19:55 | 0 | 9.65 | 9.65 | CT,PT cabling & tray Installation work | Close | 0.21932 | site average | 1694 | IG Unscheduled Maintenance
2025-04-23 | 2026 | 2025 | 2025-04-01 | Year_3 | P-25 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:55 | 19:55 | 20:11 | 0 | 0.26667 | 0.26667 | Rebooted the PLC & reset at scada | Close | 0.0060606 | site average | 48 | IG Unscheduled Maintenance
2025-04-23 | 2026 | 2025 | 2025-04-01 | Year_3 | P-26 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 10:16 | 10:16 | 19:55 | 0 | 9.65 | 9.65 | CT,PT cabling & tray Installation work | Close | 0.21932 | site average | 1694 | IG Unscheduled Maintenance
2025-04-23 | 2026 | 2025 | 2025-04-01 | Year_3 | P-26 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:55 | 19:55 | 20:15 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 60 | IG Unscheduled Maintenance
2025-04-23 | 2026 | 2025 | 2025-04-01 | Year_3 | P-27 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 10:16 | 10:16 | 19:55 | 0 | 9.65 | 9.65 | CT,PT cabling & tray Installation work | Close | 0.21932 | site average | 1694 | IG Unscheduled Maintenance
2025-04-23 | 2026 | 2025 | 2025-04-01 | Year_3 | P-27 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:55 | 19:55 | 20:12 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | site average | 51 | IG Unscheduled Maintenance
2025-04-23 | 2026 | 2025 | 2025-04-01 | Year_3 | P-28 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 10:16 | 10:16 | 19:55 | 0 | 9.65 | 9.65 | CT,PT cabling & tray Installation work | Close | 0.21932 | site average | 1694 | IG Unscheduled Maintenance
2025-04-23 | 2026 | 2025 | 2025-04-01 | Year_3 | P-28 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:55 | 19:55 | 20:15 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 60 | IG Unscheduled Maintenance
2025-04-24 | 2026 | 2025 | 2025-04-01 | Year_3 | P-09 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:55 | 8:55 | 19:15 | 0 | 10.3333 | 10.3333 | CT,PT cabling & tray Installation work | Close | 0.23485 | site average | 1475 | IG Unscheduled Maintenance
2025-04-24 | 2026 | 2025 | 2025-04-01 | Year_3 | P-09 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:15 | 19:15 | 19:32 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | site average | 41 | IG Unscheduled Maintenance
2025-04-24 | 2026 | 2025 | 2025-04-01 | Year_3 | P-10 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:55 | 8:55 | 19:15 | 0 | 10.3333 | 10.3333 | CT,PT cabling & tray Installation work | Close | 0.23485 | site average | 1475 | IG Unscheduled Maintenance
2025-04-24 | 2026 | 2025 | 2025-04-01 | Year_3 | P-10 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:15 | 19:15 | 19:31 | 0 | 0.26667 | 0.26667 | Rebooted the PLC & reset at scada | Close | 0.0060606 | site average | 39 | IG Unscheduled Maintenance
2025-04-24 | 2026 | 2025 | 2025-04-01 | Year_3 | P-11 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:55 | 8:55 | 19:15 | 0 | 10.3333 | 10.3333 | CT,PT cabling & tray Installation work | Close | 0.23485 | site average | 1475 | IG Unscheduled Maintenance
2025-04-24 | 2026 | 2025 | 2025-04-01 | Year_3 | P-11 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:15 | 19:15 | 19:32 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | site average | 41 | IG Unscheduled Maintenance
2025-04-24 | 2026 | 2025 | 2025-04-01 | Year_3 | P-12 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:55 | 8:55 | 19:15 | 0 | 10.3333 | 10.3333 | CT,PT cabling & tray Installation work | Close | 0.23485 | site average | 1475 | IG Unscheduled Maintenance
2025-04-24 | 2026 | 2025 | 2025-04-01 | Year_3 | P-12 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:15 | 19:15 | 19:31 | 0 | 0.26667 | 0.26667 | Rebooted the PLC & reset at scada | Close | 0.0060606 | site average | 39 | IG Unscheduled Maintenance
2025-04-24 | 2026 | 2025 | 2025-04-01 | Year_3 | P-13 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:55 | 8:55 | 19:15 | 0 | 10.3333 | 10.3333 | CT,PT cabling & tray Installation work | Close | 0.23485 | site average | 1474 | IG Unscheduled Maintenance
2025-04-24 | 2026 | 2025 | 2025-04-01 | Year_3 | P-13 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:15 | 19:15 | 19:35 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 49 | IG Unscheduled Maintenance
2025-04-25 | 2026 | 2025 | 2025-04-01 | Year_3 | Wind_F1 | PWEPL | MSEDCL | 22.73% | Feeder tripped by O/C | 3:57 | 3:57 | 4:31 | 0 | 0.56667 | 0.56667 | Test charged taken charged successfully | Close | 0.12879 | site average | 1482 | IG Breakdown Maintenance
2025-04-25 | 2026 | 2025 | 2025-04-01 | Year_3 | P-09 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:31 | 4:31 | 4:51 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 87 | IG Breakdown Maintenance
2025-04-25 | 2026 | 2025 | 2025-04-01 | Year_3 | P-10 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:31 | 4:31 | 4:46 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | site average | 65 | IG Breakdown Maintenance
2025-04-25 | 2026 | 2025 | 2025-04-01 | Year_3 | P-11 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:31 | 4:31 | 4:50 | 0 | 0.31667 | 0.31667 | Rebooted the PLC & reset at scada | Close | 0.007197 | site average | 82 | IG Breakdown Maintenance
2025-04-25 | 2026 | 2025 | 2025-04-01 | Year_3 | P-12 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:31 | 4:31 | 4:51 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 87 | IG Breakdown Maintenance
2025-04-25 | 2026 | 2025 | 2025-04-01 | Year_3 | P-13 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:31 | 4:31 | 4:51 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 87 | IG Breakdown Maintenance
2025-04-25 | 2026 | 2025 | 2025-04-01 | Year_3 | P-08 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:31 | 4:31 | 4:50 | 0 | 0.31667 | 0.31667 | Rebooted the PLC & reset at scada | Close | 0.007197 | site average | 82 | IG Breakdown Maintenance
2025-04-25 | 2026 | 2025 | 2025-04-01 | Year_3 | P-25 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:31 | 4:31 | 4:51 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 87 | IG Breakdown Maintenance
2025-04-25 | 2026 | 2025 | 2025-04-01 | Year_3 | P-26 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:31 | 4:31 | 4:51 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 87 | IG Breakdown Maintenance
2025-04-25 | 2026 | 2025 | 2025-04-01 | Year_3 | P-27 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:31 | 4:31 | 4:49 | 0 | 0.3 | 0.3 | Rebooted the PLC & reset at scada | Close | 0.0068182 | site average | 78 | IG Breakdown Maintenance
2025-04-25 | 2026 | 2025 | 2025-04-01 | Year_3 | P-28 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:31 | 4:31 | 4:51 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 87 | IG Breakdown Maintenance
2025-04-26 | 2026 | 2025 | 2025-04-01 | Year_3 | P-14 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:19 | 7:19 | 18:42 | 0 | 11.3833 | 11.3833 | CT,PT cabling & tray Installation work | Close | 0.25871 | site average | 1559 | IG Unscheduled Maintenance
2025-04-26 | 2026 | 2025 | 2025-04-01 | Year_3 | P-14 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:42 | 18:42 | 18:58 | 0 | 0.26667 | 0.26667 | Rebooted the PLC & reset at scada | Close | 0.0060606 | site average | 37 | IG Unscheduled Maintenance
2025-04-26 | 2026 | 2025 | 2025-04-01 | Year_3 | P-15 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:19 | 7:19 | 18:42 | 0 | 11.3833 | 11.3833 | CT,PT cabling & tray Installation work | Close | 0.25871 | site average | 1560 | IG Unscheduled Maintenance
2025-04-26 | 2026 | 2025 | 2025-04-01 | Year_3 | P-15 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:42 | 18:42 | 18:52 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | site average | 23 | IG Unscheduled Maintenance
2025-04-26 | 2026 | 2025 | 2025-04-01 | Year_3 | P-16 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:19 | 7:19 | 18:42 | 0 | 11.3833 | 11.3833 | CT,PT cabling & tray Installation work | Close | 0.25871 | site average | 1559 | IG Unscheduled Maintenance
2025-04-26 | 2026 | 2025 | 2025-04-01 | Year_3 | P-16 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:42 | 18:42 | 18:58 | 0 | 0.26667 | 0.26667 | Rebooted the PLC & reset at scada | Close | 0.0060606 | site average | 37 | IG Unscheduled Maintenance
2025-04-26 | 2026 | 2025 | 2025-04-01 | Year_3 | P-17 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:19 | 7:19 | 18:42 | 0 | 11.3833 | 11.3833 | CT,PT cabling & tray Installation work | Close | 0.25871 | site average | 1559 | IG Unscheduled Maintenance
2025-04-26 | 2026 | 2025 | 2025-04-01 | Year_3 | P-17 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:42 | 18:42 | 18:57 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | site average | 35 | IG Unscheduled Maintenance
2025-04-26 | 2026 | 2025 | 2025-04-01 | Year_3 | P-19 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:19 | 7:19 | 18:42 | 0 | 11.3833 | 11.3833 | CT,PT cabling & tray Installation work | Close | 0.25871 | site average | 1558 | IG Unscheduled Maintenance
2025-04-26 | 2026 | 2025 | 2025-04-01 | Year_3 | P-19 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:42 | 18:42 | 19:02 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 47 | IG Unscheduled Maintenance
2025-04-26 | 2026 | 2025 | 2025-04-01 | Year_3 | P-20 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:19 | 7:19 | 18:42 | 0 | 11.3833 | 11.3833 | CT,PT cabling & tray Installation work | Close | 0.25871 | site average | 1558 | IG Unscheduled Maintenance
2025-04-26 | 2026 | 2025 | 2025-04-01 | Year_3 | P-20 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:42 | 18:42 | 19:02 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 47 | IG Unscheduled Maintenance
2025-04-26 | 2026 | 2025 | 2025-04-01 | Year_3 | P-38 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:19 | 7:19 | 18:42 | 0 | 11.3833 | 11.3833 | CT,PT cabling & tray Installation work | Close | 0.25871 | site average | 1558 | IG Unscheduled Maintenance
2025-04-26 | 2026 | 2025 | 2025-04-01 | Year_3 | P-38 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:42 | 18:42 | 19:02 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 47 | IG Unscheduled Maintenance
2025-05-03 | 2026 | 2025 | 2025-05-01 | Year_3 | P-04 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:51 | 7:51 | 16:20 | 0 | 8.4833 | 8.4833 | CT,PT cabling & tray Installation work | Close | 0.1928 | site average | 3829 | IG Unscheduled Maintenance
2025-05-03 | 2026 | 2025 | 2025-05-01 | Year_3 | P-04 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:20 | 16:20 | 16:40 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 156 | IG Unscheduled Maintenance
2025-05-03 | 2026 | 2025 | 2025-05-01 | Year_3 | P-22 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:51 | 7:51 | 16:20 | 0 | 8.4833 | 8.4833 | CT,PT cabling & tray Installation work | Close | 0.1928 | site average | 3831 | IG Unscheduled Maintenance
2025-05-03 | 2026 | 2025 | 2025-05-01 | Year_3 | P-22 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:20 | 16:20 | 16:36 | 0 | 0.26667 | 0.26667 | Rebooted the PLC & reset at scada | Close | 0.0060606 | site average | 124 | IG Unscheduled Maintenance
2025-05-03 | 2026 | 2025 | 2025-05-01 | Year_3 | P-23 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:51 | 7:51 | 16:20 | 0 | 8.4833 | 8.4833 | CT,PT cabling & tray Installation work | Close | 0.1928 | site average | 3830 | IG Unscheduled Maintenance
2025-05-03 | 2026 | 2025 | 2025-05-01 | Year_3 | P-23 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:20 | 16:20 | 16:37 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | site average | 132 | IG Unscheduled Maintenance
2025-05-03 | 2026 | 2025 | 2025-05-01 | Year_3 | P-34 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:51 | 7:51 | 16:20 | 0 | 8.4833 | 8.4833 | CT,PT cabling & tray Installation work | Close | 0.1928 | site average | 3831 | IG Unscheduled Maintenance
2025-05-03 | 2026 | 2025 | 2025-05-01 | Year_3 | P-34 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:20 | 16:20 | 16:35 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | site average | 116 | IG Unscheduled Maintenance
2025-05-03 | 2026 | 2025 | 2025-05-01 | Year_3 | P-43 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:51 | 7:51 | 16:20 | 0 | 8.4833 | 8.4833 | CT,PT cabling & tray Installation work | Close | 0.1928 | site average | 3831 | IG Unscheduled Maintenance
2025-05-03 | 2026 | 2025 | 2025-05-01 | Year_3 | P-43 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:20 | 16:20 | 16:35 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | site average | 116 | IG Unscheduled Maintenance
2025-05-08 | 2026 | 2025 | 2025-05-01 | Year_3 | P-19 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 10:19 | 10:19 | 10:55 | 0 | 0.6 | 0.6 | VCB reset & Charge | Close | 0.013636 | site average | 760 | IG Breakdown Maintenance
2025-05-08 | 2026 | 2025 | 2025-05-01 | Year_3 | P-19 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 10:55 | 10:55 | 11:15 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 421 | IG Breakdown Maintenance
2025-05-09 | 2026 | 2025 | 2025-05-01 | Year_3 | P-42 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:03 | 8:03 | 13:28 | 0 | 5.4167 | 5.4167 | CT,PT cabling & tray Installation work | Close | 0.12311 | site average | 1075 | IG Unscheduled Maintenance
2025-05-09 | 2026 | 2025 | 2025-05-01 | Year_3 | P-42 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:28 | 13:28 | 13:42 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | site average | 48 | IG Unscheduled Maintenance
2025-05-09 | 2026 | 2025 | 2025-05-01 | Year_3 | P-45 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:03 | 8:03 | 13:28 | 0 | 5.4167 | 5.4167 | CT,PT cabling & tray Installation work | Close | 0.12311 | site average | 1075 | IG Unscheduled Maintenance
2025-05-09 | 2026 | 2025 | 2025-05-01 | Year_3 | P-45 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:28 | 13:28 | 13:42 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | site average | 48 | IG Unscheduled Maintenance
2025-05-09 | 2026 | 2025 | 2025-05-01 | Year_3 | P-46 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:03 | 8:03 | 13:28 | 0 | 5.4167 | 5.4167 | CT,PT cabling & tray Installation work | Close | 0.12311 | site average | 1075 | IG Unscheduled Maintenance
2025-05-09 | 2026 | 2025 | 2025-05-01 | Year_3 | P-46 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:28 | 13:28 | 13:40 | 0 | 0.2 | 0.2 | Rebooted the PLC & reset at scada | Close | 0.0045455 | site average | 41 | IG Unscheduled Maintenance
2025-05-09 | 2026 | 2025 | 2025-05-01 | Year_3 | P-47 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:03 | 8:03 | 13:28 | 0 | 5.4167 | 5.4167 | CT,PT cabling & tray Installation work | Close | 0.12311 | site average | 1075 | IG Unscheduled Maintenance
2025-05-09 | 2026 | 2025 | 2025-05-01 | Year_3 | P-47 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:28 | 13:28 | 13:40 | 0 | 0.2 | 0.2 | Rebooted the PLC & reset at scada | Close | 0.0045455 | site average | 41 | IG Unscheduled Maintenance
2025-05-09 | 2026 | 2025 | 2025-05-01 | Year_3 | P-48 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:03 | 8:03 | 13:28 | 0 | 5.4167 | 5.4167 | CT,PT cabling & tray Installation work | Close | 0.12311 | site average | 1075 | IG Unscheduled Maintenance
2025-05-09 | 2026 | 2025 | 2025-05-01 | Year_3 | P-48 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:28 | 13:28 | 13:40 | 0 | 0.2 | 0.2 | Rebooted the PLC & reset at scada | Close | 0.0045455 | site average | 41 | IG Unscheduled Maintenance
2025-05-10 | 2026 | 2025 | 2025-05-01 | Year_3 | P-01 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:40 | 7:40 | 13:56 | 0 | 6.2667 | 6.2667 | CT,PT cabling & tray Installation work | Close | 0.14242 | site average | 926 | IG Unscheduled Maintenance
2025-05-10 | 2026 | 2025 | 2025-05-01 | Year_3 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:56 | 13:56 | 14:11 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | site average | 38 | IG Unscheduled Maintenance
2025-05-10 | 2026 | 2025 | 2025-05-01 | Year_3 | P-02 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:40 | 7:40 | 13:56 | 0 | 6.2667 | 6.2667 | CT,PT cabling & tray Installation work | Close | 0.14242 | site average | 927 | IG Unscheduled Maintenance
2025-05-10 | 2026 | 2025 | 2025-05-01 | Year_3 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:56 | 13:56 | 14:01 | 0 | 0.083333 | 0.083333 | Rebooted the PLC & reset at scada | Close | 0.0018939 | site average | 12 | IG Unscheduled Maintenance
2025-05-10 | 2026 | 2025 | 2025-05-01 | Year_3 | P-03 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:40 | 7:40 | 13:56 | 0 | 6.2667 | 6.2667 | CT,PT cabling & tray Installation work | Close | 0.14242 | site average | 924 | IG Unscheduled Maintenance
2025-05-10 | 2026 | 2025 | 2025-05-01 | Year_3 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:56 | 13:56 | 14:15 | 0 | 0.31667 | 0.31667 | Rebooted the PLC & reset at scada | Close | 0.007197 | site average | 49 | IG Unscheduled Maintenance
2025-05-10 | 2026 | 2025 | 2025-05-01 | Year_3 | P-07 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:40 | 7:40 | 13:56 | 0 | 6.2667 | 6.2667 | CT,PT cabling & tray Installation work | Close | 0.14242 | site average | 926 | IG Unscheduled Maintenance
2025-05-10 | 2026 | 2025 | 2025-05-01 | Year_3 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:56 | 13:56 | 14:06 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | site average | 25 | IG Unscheduled Maintenance
2025-05-10 | 2026 | 2025 | 2025-05-01 | Year_3 | P-18 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:40 | 7:40 | 13:56 | 0 | 6.2667 | 6.2667 | CT,PT cabling & tray Installation work | Close | 0.14242 | site average | 926 | IG Unscheduled Maintenance
2025-05-10 | 2026 | 2025 | 2025-05-01 | Year_3 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:56 | 13:56 | 14:07 | 0 | 0.18333 | 0.18333 | Rebooted the PLC & reset at scada | Close | 0.0041667 | site average | 28 | IG Unscheduled Maintenance
2025-05-10 | 2026 | 2025 | 2025-05-01 | Year_3 | P-31 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:40 | 7:40 | 13:56 | 0 | 6.2667 | 6.2667 | CT,PT cabling & tray Installation work | Close | 0.14242 | site average | 936 | IG Unscheduled Maintenance
2025-05-10 | 2026 | 2025 | 2025-05-01 | Year_3 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:56 | 13:56 | 14:05 | 0 | 0.15 | 0.15 | Rebooted the PLC & reset at scada | Close | 0.0034091 | site average | 23 | IG Unscheduled Maintenance
2025-05-10 | 2026 | 2025 | 2025-05-01 | Year_3 | P-56 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:40 | 7:40 | 13:56 | 0 | 6.2667 | 6.2667 | CT,PT cabling & tray Installation work | Close | 0.14242 | site average | 926 | IG Unscheduled Maintenance
2025-05-10 | 2026 | 2025 | 2025-05-01 | Year_3 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:56 | 13:56 | 14:07 | 0 | 0.18333 | 0.18333 | Rebooted the PLC & reset at scada | Close | 0.0041667 | site average | 28 | IG Unscheduled Maintenance
2025-05-12 | 2026 | 2025 | 2025-05-01 | Year_3 | P-32 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:16 | 8:16 | 14:14 | 0 | 5.9667 | 5.9667 | CT,PT cabling & tray Installation work | Close | 0.13561 | site average | 519 | IG Unscheduled Maintenance
2025-05-12 | 2026 | 2025 | 2025-05-01 | Year_3 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 14:14 | 14:14 | 14:25 | 0 | 0.18333 | 0.18333 | Rebooted the PLC & reset at scada | Close | 0.0041667 | site average | 16 | IG Unscheduled Maintenance
2025-05-12 | 2026 | 2025 | 2025-05-01 | Year_3 | P-37 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:16 | 8:16 | 14:14 | 0 | 5.9667 | 5.9667 | CT,PT cabling & tray Installation work | Close | 0.13561 | site average | 518 | IG Unscheduled Maintenance
2025-05-12 | 2026 | 2025 | 2025-05-01 | Year_3 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 14:14 | 14:14 | 14:34 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 30 | IG Unscheduled Maintenance
2025-05-12 | 2026 | 2025 | 2025-05-01 | Year_3 | P-50 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:16 | 8:16 | 14:14 | 0 | 5.9667 | 5.9667 | CT,PT cabling & tray Installation work | Close | 0.13561 | site average | 518 | IG Unscheduled Maintenance
2025-05-12 | 2026 | 2025 | 2025-05-01 | Year_3 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 14:14 | 14:14 | 14:30 | 0 | 0.26667 | 0.26667 | Rebooted the PLC & reset at scada | Close | 0.0060606 | site average | 24 | IG Unscheduled Maintenance
2025-05-12 | 2026 | 2025 | 2025-05-01 | Year_3 | P-51 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:16 | 8:16 | 14:14 | 0 | 5.9667 | 5.9667 | CT,PT cabling & tray Installation work | Close | 0.13561 | site average | 518 | IG Unscheduled Maintenance
2025-05-12 | 2026 | 2025 | 2025-05-01 | Year_3 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 14:14 | 14:14 | 14:27 | 0 | 0.21667 | 0.21667 | Rebooted the PLC & reset at scada | Close | 0.0049242 | site average | 19 | IG Unscheduled Maintenance
2025-05-12 | 2026 | 2025 | 2025-05-01 | Year_3 | P-52 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:16 | 8:16 | 14:14 | 0 | 5.9667 | 5.9667 | CT,PT cabling & tray Installation work | Close | 0.13561 | site average | 518 | IG Unscheduled Maintenance
2025-05-12 | 2026 | 2025 | 2025-05-01 | Year_3 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 14:14 | 14:14 | 14:34 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 30 | IG Unscheduled Maintenance
2025-05-12 | 2026 | 2025 | 2025-05-01 | Year_3 | P-55 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:16 | 8:16 | 14:14 | 0 | 5.9667 | 5.9667 | CT,PT cabling & tray Installation work | Close | 0.13561 | site average | 518 | IG Unscheduled Maintenance
2025-05-12 | 2026 | 2025 | 2025-05-01 | Year_3 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 14:14 | 14:14 | 14:24 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | site average | 15 | IG Unscheduled Maintenance
2025-05-12 | 2026 | 2025 | 2025-05-01 | Year_3 | Wind_F3 | PWEPL | MSEDCL | 20.45% | Feeder tripped by O/C | 16:19 | 16:19 | 18:00 | 0 | 1.6833 | 1.6833 | Test charged taken charged successfully | Close | 0.34432 | site average | 949 | IG Breakdown Maintenance
2025-05-12 | 2026 | 2025 | 2025-05-01 | Year_3 | P-05 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:00 | 18:00 | 18:20 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 47 | IG Breakdown Maintenance
2025-05-12 | 2026 | 2025 | 2025-05-01 | Year_3 | P-06 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:00 | 18:00 | 18:16 | 0 | 0.26667 | 0.26667 | Rebooted the PLC & reset at scada | Close | 0.0060606 | site average | 37 | IG Breakdown Maintenance
2025-05-12 | 2026 | 2025 | 2025-05-01 | Year_3 | P-40 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:00 | 18:00 | 18:20 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 47 | IG Breakdown Maintenance
2025-05-12 | 2026 | 2025 | 2025-05-01 | Year_3 | P-41 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:00 | 18:00 | 18:20 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 47 | IG Breakdown Maintenance
2025-05-12 | 2026 | 2025 | 2025-05-01 | Year_3 | P-42 | PWEPL | MSEDCL | 2.273% | PWEPL-46 R Phase LA failure | 18:00 | 18:00 | 18:33 | 0 | 0.55 | 0.55 | LA replaced | Close | 0.0125 | site average | 723 | IG Breakdown Maintenance
2025-05-12 | 2026 | 2025 | 2025-05-01 | Year_3 | P-42 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:33 | 18:33 | 18:53 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 99 | IG Breakdown Maintenance
2025-05-12 | 2026 | 2025 | 2025-05-01 | Year_3 | P-45 | PWEPL | MSEDCL | 2.273% | PWEPL-46 R Phase LA failure | 18:00 | 18:00 | 18:33 | 0 | 0.55 | 0.55 | LA replaced | Close | 0.0125 | site average | 738 | IG Breakdown Maintenance
2025-05-12 | 2026 | 2025 | 2025-05-01 | Year_3 | P-45 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:33 | 18:33 | 18:50 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | site average | 84 | IG Breakdown Maintenance
2025-05-12 | 2026 | 2025 | 2025-05-01 | Year_3 | P-46 | PWEPL | MSEDCL | 2.273% | PWEPL-46 R Phase LA failure | 18:00 | 18:00 | 18:33 | 0 | 0.55 | 0.55 | LA replaced | Close | 0.0125 | site average | 723 | IG Breakdown Maintenance
2025-05-12 | 2026 | 2025 | 2025-05-01 | Year_3 | P-46 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:33 | 18:33 | 18:53 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 99 | IG Breakdown Maintenance
2025-05-12 | 2026 | 2025 | 2025-05-01 | Year_3 | P-47 | PWEPL | MSEDCL | 2.273% | PWEPL-46 R Phase LA failure | 18:00 | 18:00 | 18:33 | 0 | 0.55 | 0.55 | LA replaced | Close | 0.0125 | site average | 723 | IG Breakdown Maintenance
2025-05-12 | 2026 | 2025 | 2025-05-01 | Year_3 | P-47 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:33 | 18:33 | 18:53 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 99 | IG Breakdown Maintenance
2025-05-12 | 2026 | 2025 | 2025-05-01 | Year_3 | P-48 | PWEPL | MSEDCL | 2.273% | PWEPL-46 R Phase LA failure | 18:00 | 18:00 | 18:33 | 0 | 0.55 | 0.55 | LA replaced | Close | 0.0125 | site average | 723 | IG Breakdown Maintenance
2025-05-12 | 2026 | 2025 | 2025-05-01 | Year_3 | P-48 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:33 | 18:33 | 18:53 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 99 | IG Breakdown Maintenance
2025-05-12 | 2026 | 2025 | 2025-05-01 | Year_3 | P-42 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 18:53 | 18:53 | 19:48 | 0 | 0.91667 | 0.91667 | VCB reset & Charge | Close | 0.020833 | site average | 325 | IG Breakdown Maintenance
2025-05-12 | 2026 | 2025 | 2025-05-01 | Year_3 | P-42 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:48 | 19:48 | 20:05 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | site average | 144 | IG Breakdown Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | P-05 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 12:29 | 12:29 | 13:32 | 0 | 1.05 | 1.05 | CT,PT cabling & tray Installation work | Close | 0.023864 | site average | 97 | IG Unscheduled Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | P-06 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 12:29 | 12:29 | 13:32 | 0 | 1.05 | 1.05 | CT,PT cabling & tray Installation work | Close | 0.023864 | site average | 97 | IG Unscheduled Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | P-40 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 12:29 | 12:29 | 13:32 | 0 | 1.05 | 1.05 | CT,PT cabling & tray Installation work | Close | 0.023864 | site average | 97 | IG Unscheduled Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | P-41 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 12:29 | 12:29 | 13:32 | 0 | 1.05 | 1.05 | CT,PT cabling & tray Installation work | Close | 0.023864 | site average | 97 | IG Unscheduled Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | Wind_F3 | PWEPL | MSEDCL | 20.45% | Feeder tripped by O/C | 13:32 | 13:32 | 14:01 | 0 | 0.48333 | 0.48333 | Test charged taken charged successfully | Close | 0.098864 | site average | 438 | IG Breakdown Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | P-42 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 14:01 | 14:01 | 14:16 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | site average | 25 | IG Breakdown Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | P-45 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 14:01 | 14:01 | 14:16 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | site average | 25 | IG Breakdown Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | P-46 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 14:01 | 14:01 | 14:16 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | site average | 25 | IG Breakdown Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | P-47 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 14:01 | 14:01 | 14:16 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | site average | 25 | IG Breakdown Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | P-48 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 14:01 | 14:01 | 14:16 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | site average | 25 | IG Breakdown Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | P-05 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 14:01 | 14:01 | 14:16 | 0 | 0.25 | 0.25 | CT,PT cabling & tray Installation work | Close | 0.0056818 | site average | 23 | IG Unscheduled Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | P-06 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 14:01 | 14:01 | 14:16 | 0 | 0.25 | 0.25 | CT,PT cabling & tray Installation work | Close | 0.0056818 | site average | 23 | IG Unscheduled Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | P-40 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 14:01 | 14:01 | 14:16 | 0 | 0.25 | 0.25 | CT,PT cabling & tray Installation work | Close | 0.0056818 | site average | 23 | IG Unscheduled Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | P-41 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 14:01 | 14:01 | 14:16 | 0 | 0.25 | 0.25 | CT,PT cabling & tray Installation work | Close | 0.0056818 | site average | 23 | IG Unscheduled Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | Wind_F3 | PWEPL | MSEDCL | 20.45% | Feeder tripped by O/C | 14:16 | 14:16 | 15:13 | 0 | 0.95 | 0.95 | Test charged taken charged successfully | Close | 0.19432 | site average | 952 | IG Breakdown Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | P-42 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 15:13 | 15:13 | 15:31 | 0 | 0.3 | 0.3 | Rebooted the PLC & reset at scada | Close | 0.0068182 | site average | 60 | IG Breakdown Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | P-45 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 15:13 | 15:13 | 15:31 | 0 | 0.3 | 0.3 | Rebooted the PLC & reset at scada | Close | 0.0068182 | site average | 60 | IG Breakdown Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | P-46 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 15:13 | 15:13 | 15:21 | 0 | 0.13333 | 0.13333 | Rebooted the PLC & reset at scada | Close | 0.0030303 | site average | 33 | IG Breakdown Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | P-47 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 15:13 | 15:13 | 15:33 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 66 | IG Breakdown Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | P-48 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 15:13 | 15:13 | 15:31 | 0 | 0.3 | 0.3 | Rebooted the PLC & reset at scada | Close | 0.0068182 | site average | 60 | IG Breakdown Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | P-05 | PWEPL | MSEDCL | 2.273% | CP-49 B-Phase Pin insulator failure | 15:13 | 15:13 | 17:53 | 0 | 2.6667 | 2.6667 | Pin Insulator replaced | Close | 0.060606 | site average | 1443 | IG Breakdown Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | P-05 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 17:53 | 17:53 | 18:13 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 46 | IG Breakdown Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | P-06 | PWEPL | MSEDCL | 2.273% | CP-50 R-Phase Pin insulator failure | 15:13 | 15:13 | 17:53 | 0 | 2.6667 | 2.6667 | Pin Insulator replaced | Close | 0.060606 | site average | 1443 | IG Breakdown Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | P-06 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 17:53 | 17:53 | 18:13 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 46 | IG Breakdown Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | P-40 | PWEPL | MSEDCL | 2.273% | PP-43 R-Phase Pin insulator failure | 15:13 | 15:13 | 17:53 | 0 | 2.6667 | 2.6667 | Pin Insulator replaced | Close | 0.060606 | site average | 1443 | IG Breakdown Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | P-40 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 17:53 | 17:53 | 18:13 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 46 | IG Breakdown Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | P-41 | PWEPL | MSEDCL | 2.273% | PP-56 Y-Phase Pin insulator failure | 15:13 | 15:13 | 17:53 | 0 | 2.6667 | 2.6667 | Pin Insulator replaced | Close | 0.060606 | site average | 1445 | IG Breakdown Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | P-41 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 17:53 | 17:53 | 18:12 | 0 | 0.31667 | 0.31667 | Rebooted the PLC & reset at scada | Close | 0.007197 | site average | 44 | IG Breakdown Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | Wind_F4 | PWEPL | MSEDCL | 29.55% | Feeder tripped by O/C | 14:17 | 14:17 | 15:12 | 0 | 0.91667 | 0.91667 | Test charged taken charged successfully | Close | 0.27083 | site average | 3013 | IG Breakdown Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:12 | 15:12 | 15:30 | 0 | 0.3 | 0.3 | Rebooted the PLC & reset at scada | Close | 0.0068182 | site average | 75 | IG Breakdown Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:12 | 15:12 | 15:27 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | site average | 63 | IG Breakdown Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:12 | 15:12 | 15:30 | 0 | 0.3 | 0.3 | Rebooted the PLC & reset at scada | Close | 0.0068182 | site average | 75 | IG Breakdown Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:12 | 15:12 | 15:30 | 0 | 0.3 | 0.3 | Rebooted the PLC & reset at scada | Close | 0.0068182 | site average | 75 | IG Breakdown Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:12 | 15:12 | 15:30 | 0 | 0.3 | 0.3 | Rebooted the PLC & reset at scada | Close | 0.0068182 | site average | 75 | IG Breakdown Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:12 | 15:12 | 15:29 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | site average | 71 | IG Breakdown Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:12 | 15:12 | 15:24 | 0 | 0.2 | 0.2 | Rebooted the PLC & reset at scada | Close | 0.0045455 | site average | 50 | IG Breakdown Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:12 | 15:12 | 15:27 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | site average | 63 | IG Breakdown Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:12 | 15:12 | 15:26 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | site average | 58 | IG Breakdown Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:12 | 15:12 | 15:24 | 0 | 0.2 | 0.2 | Rebooted the PLC & reset at scada | Close | 0.0045455 | site average | 50 | IG Breakdown Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:12 | 15:12 | 15:26 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | site average | 58 | IG Breakdown Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:12 | 15:12 | 15:32 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 84 | IG Breakdown Maintenance
2025-05-14 | 2026 | 2025 | 2025-05-01 | Year_3 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:12 | 15:12 | 15:31 | 0 | 0.31667 | 0.31667 | Rebooted the PLC & reset at scada | Close | 0.007197 | site average | 80 | IG Breakdown Maintenance
2025-05-15 | 2026 | 2025 | 2025-05-01 | Year_3 | Wind_F3 | PWEPL | MSEDCL | 20.45% | S/D for External line tree trimming work | 8:28 | 8:28 | 15:19 | 0 | 6.85 | 6.85 | Tree trimming work done | Close | 1.4011 | site average | 1376 | IG Unscheduled Maintenance
2025-05-15 | 2026 | 2025 | 2025-05-01 | Year_3 | P-42 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:34 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | site average | 5 | IG Unscheduled Maintenance
2025-05-15 | 2026 | 2025 | 2025-05-01 | Year_3 | P-45 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:34 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | site average | 5 | IG Unscheduled Maintenance
2025-05-15 | 2026 | 2025 | 2025-05-01 | Year_3 | P-46 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:33 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | site average | 5 | IG Unscheduled Maintenance
2025-05-15 | 2026 | 2025 | 2025-05-01 | Year_3 | P-47 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:34 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | site average | 5 | IG Unscheduled Maintenance
2025-05-15 | 2026 | 2025 | 2025-05-01 | Year_3 | P-48 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:33 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | site average | 5 | IG Unscheduled Maintenance
2025-05-15 | 2026 | 2025 | 2025-05-01 | Year_3 | P-05 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:33 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | site average | 5 | IG Unscheduled Maintenance
2025-05-15 | 2026 | 2025 | 2025-05-01 | Year_3 | P-06 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:29 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | site average | 3.7 | IG Unscheduled Maintenance
2025-05-15 | 2026 | 2025 | 2025-05-01 | Year_3 | P-40 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:28 | 0 | 0.15 | 0.15 | Rebooted the PLC & reset at scada | Close | 0.0034091 | site average | 3.3 | IG Unscheduled Maintenance
2025-05-15 | 2026 | 2025 | 2025-05-01 | Year_3 | P-41 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:38 | 0 | 0.31667 | 0.31667 | Rebooted the PLC & reset at scada | Close | 0.007197 | site average | 7 | IG Unscheduled Maintenance
2025-05-15 | 2026 | 2025 | 2025-05-01 | Year_3 | Wind_F4 | PWEPL | MSEDCL | 29.55% | S/D for External line tree trimming work | 8:28 | 8:28 | 15:19 | 0 | 6.85 | 6.85 | Tree trimming work done | Close | 2.0239 | site average | 2249 | IG Unscheduled Maintenance
2025-05-15 | 2026 | 2025 | 2025-05-01 | Year_3 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:33 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | site average | 5.9 | IG Unscheduled Maintenance
2025-05-15 | 2026 | 2025 | 2025-05-01 | Year_3 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:29 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | site average | 4 | IG Unscheduled Maintenance
2025-05-15 | 2026 | 2025 | 2025-05-01 | Year_3 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:33 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | site average | 5.9 | IG Unscheduled Maintenance
2025-05-15 | 2026 | 2025 | 2025-05-01 | Year_3 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:33 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | site average | 5.9 | IG Unscheduled Maintenance
2025-05-15 | 2026 | 2025 | 2025-05-01 | Year_3 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:39 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 8 | IG Unscheduled Maintenance
2025-05-15 | 2026 | 2025 | 2025-05-01 | Year_3 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:28 | 0 | 0.15 | 0.15 | Rebooted the PLC & reset at scada | Close | 0.0034091 | site average | 3.8 | IG Unscheduled Maintenance
2025-05-15 | 2026 | 2025 | 2025-05-01 | Year_3 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:34 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | site average | 6 | IG Unscheduled Maintenance
2025-05-15 | 2026 | 2025 | 2025-05-01 | Year_3 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:39 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 8 | IG Unscheduled Maintenance
2025-05-15 | 2026 | 2025 | 2025-05-01 | Year_3 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:36 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | site average | 7 | IG Unscheduled Maintenance
2025-05-15 | 2026 | 2025 | 2025-05-01 | Year_3 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:32 | 0 | 0.21667 | 0.21667 | Rebooted the PLC & reset at scada | Close | 0.0049242 | site average | 5.4 | IG Unscheduled Maintenance
2025-05-15 | 2026 | 2025 | 2025-05-01 | Year_3 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:32 | 0 | 0.21667 | 0.21667 | Rebooted the PLC & reset at scada | Close | 0.0049242 | site average | 5.4 | IG Unscheduled Maintenance
2025-05-15 | 2026 | 2025 | 2025-05-01 | Year_3 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:39 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 8 | IG Unscheduled Maintenance
2025-05-15 | 2026 | 2025 | 2025-05-01 | Year_3 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:20 | 0 | 0.016667 | 0.016667 | Rebooted the PLC & reset at scada | Close | 0.00037879 | site average | 0.4 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | Wind_F1 | PWEPL | MSEDCL | 22.73% | S/D for FDR 3 & 4 TP-02 R,Y,B Phase Jump & Pam connector replacement work | 9:55 | 9:55 | 15:39 | 0 | 5.7333 | 5.7333 | Jump & Pam connector replacement work done | Close | 1.303 | site average | 102 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-09 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:47 | 0 | 0.13333 | 0.13333 | Rebooted the PLC & reset at scada | Close | 0.0030303 | site average | 0.2 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-10 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:44 | 0 | 0.083333 | 0.083333 | Rebooted the PLC & reset at scada | Close | 0.0018939 | site average | 0.1 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-11 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:47 | 0 | 0.13333 | 0.13333 | Rebooted the PLC & reset at scada | Close | 0.0030303 | site average | 0.2 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-12 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:46 | 0 | 0.11667 | 0.11667 | Rebooted the PLC & reset at scada | Close | 0.0026515 | site average | 0.2 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-13 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:49 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | site average | 0.3 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-08 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:46 | 0 | 0.11667 | 0.11667 | Rebooted the PLC & reset at scada | Close | 0.0026515 | site average | 0.2 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-25 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:59 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 0.6 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-26 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:59 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 0.6 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-27 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:59 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 0.6 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-28 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:59 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 0.6 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | Wind_F2 | PWEPL | MSEDCL | 27.27% | S/D for FDR 3 & 4 TP-02 R,Y,B Phase Jump & Pam connector replacement work | 9:55 | 9:55 | 15:39 | 0 | 5.7333 | 5.7333 | Jump & Pam connector replacement work done | Close | 1.5636 | site average | 133 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-14 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:46 | 0 | 0.11667 | 0.11667 | Rebooted the PLC & reset at scada | Close | 0.0026515 | site average | 0.2 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-15 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:46 | 0 | 0.11667 | 0.11667 | Rebooted the PLC & reset at scada | Close | 0.0026515 | site average | 0.2 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-16 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:46 | 0 | 0.11667 | 0.11667 | Rebooted the PLC & reset at scada | Close | 0.0026515 | site average | 0.2 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-17 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:46 | 0 | 0.11667 | 0.11667 | Rebooted the PLC & reset at scada | Close | 0.0026515 | site average | 0.2 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-19 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:48 | 0 | 0.15 | 0.15 | Rebooted the PLC & reset at scada | Close | 0.0034091 | site average | 0.3 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-20 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:46 | 0 | 0.11667 | 0.11667 | Rebooted the PLC & reset at scada | Close | 0.0026515 | site average | 0.2 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-38 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:46 | 0 | 0.11667 | 0.11667 | Rebooted the PLC & reset at scada | Close | 0.0026515 | site average | 0.2 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-04 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:58 | 0 | 0.31667 | 0.31667 | Rebooted the PLC & reset at scada | Close | 0.007197 | site average | 0.6 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-22 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:58 | 0 | 0.31667 | 0.31667 | Rebooted the PLC & reset at scada | Close | 0.007197 | site average | 0.6 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-23 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:58 | 0 | 0.31667 | 0.31667 | Rebooted the PLC & reset at scada | Close | 0.007197 | site average | 0.6 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-34 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:58 | 0 | 0.31667 | 0.31667 | Rebooted the PLC & reset at scada | Close | 0.007197 | site average | 0.6 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-43 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:58 | 0 | 0.31667 | 0.31667 | Rebooted the PLC & reset at scada | Close | 0.007197 | site average | 0.6 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | Wind_F3 | PWEPL | MSEDCL | 20.45% | S/D for FDR 3 & 4 TP-02 R,Y,B Phase Jump & Pam connector replacement work | 9:50 | 9:50 | 15:50 | 0 | 6 | 6 | Jump & Pam connector replacement work done | Close | 1.2273 | site average | 144 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-42 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:02 | 0 | 0.2 | 0.2 | Rebooted the PLC & reset at scada | Close | 0.0045455 | site average | 0.5 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-45 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:08 | 0 | 0.3 | 0.3 | Rebooted the PLC & reset at scada | Close | 0.0068182 | site average | 0.8 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-46 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:07 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | site average | 0.7 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-47 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:00 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | site average | 0.4 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-48 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:07 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | site average | 0.7 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-05 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:07 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | site average | 0.7 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-06 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:07 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | site average | 0.7 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-40 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 0.9 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-41 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:07 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | site average | 0.7 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | Wind_F4 | PWEPL | MSEDCL | 29.55% | S/D for FDR 3 & 4 TP-02 R,Y,B Phase Jump & Pam connector replacement work | 9:50 | 9:50 | 15:50 | 0 | 6 | 6 | Jump & Pam connector replacement work done | Close | 1.7727 | site average | 151 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:05 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | site average | 0.5 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 15:51 | 0 | 0.016667 | 0.016667 | Rebooted the PLC & reset at scada | Close | 0.00037879 | site average | 0 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:04 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | site average | 0.45 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:04 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | site average | 0.45 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:00 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | site average | 0.3 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:04 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | site average | 0.45 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:01 | 0 | 0.18333 | 0.18333 | Rebooted the PLC & reset at scada | Close | 0.0041667 | site average | 0.35 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:04 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | site average | 0.45 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:00 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | site average | 0.3 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:00 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | site average | 0.3 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:00 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | site average | 0.3 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:03 | 0 | 0.21667 | 0.21667 | Rebooted the PLC & reset at scada | Close | 0.0049242 | site average | 0.4 | IG Unscheduled Maintenance
2025-05-16 | 2026 | 2025 | 2025-05-01 | Year_3 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:00 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | site average | 0.3 | IG Unscheduled Maintenance
2025-05-17 | 2026 | 2025 | 2025-05-01 | Year_3 | P-12 | PWEPL | MSEDCL | 2.273% | S/D for CRP Panel B Phase O/C Relay replacement work | 11:50 | 11:50 | 12:09 | 0 | 0.31667 | 0.31667 | Relay replacement work done | Close | 0.007197 | site average | 48 | IG Unscheduled Maintenance
2025-05-17 | 2026 | 2025 | 2025-05-01 | Year_3 | P-12 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:09 | 12:09 | 12:19 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | site average | 52 | IG Unscheduled Maintenance
2025-05-17 | 2026 | 2025 | 2025-05-01 | Year_3 | P-14 | PWEPL | MSEDCL | 2.273% | S/D for CRP Panel Y & B Phase O/C Relay replacement work | 12:32 | 12:32 | 12:50 | 0 | 0.3 | 0.3 | Relay replacement work done | Close | 0.0068182 | site average | 8.55 | IG Unscheduled Maintenance
2025-05-17 | 2026 | 2025 | 2025-05-01 | Year_3 | P-14 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:50 | 12:50 | 12:54 | 0 | 0.066667 | 0.066667 | Rebooted the PLC & reset at scada | Close | 0.0015152 | site average | 2.44 | IG Unscheduled Maintenance
2025-05-17 | 2026 | 2025 | 2025-05-01 | Year_3 | P-13 | PWEPL | MSEDCL | 2.273% | S/D for CRP Panel Y & B Phase O/C Relay & Ammeter replacement work | 14:19 | 14:19 | 14:46 | 0 | 0.45 | 0.45 | Relay replacement work done | Close | 0.010227 | site average | 173 | IG Unscheduled Maintenance
2025-05-17 | 2026 | 2025 | 2025-05-01 | Year_3 | P-13 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 14:46 | 14:46 | 15:04 | 0 | 0.3 | 0.3 | Rebooted the PLC & reset at scada | Close | 0.0068182 | site average | 87 | IG Unscheduled Maintenance
2025-05-18 | 2026 | 2025 | 2025-05-01 | Year_3 | Wind_F1 | PWEPL | MSEDCL | 22.73% | S/D for External line tree trimming work | 10:00 | 10:00 | 15:50 | 0 | 5.8333 | 5.8333 | Tree trimming work done | Close | 1.3258 | site average | 1816 | IG Unscheduled Maintenance
2025-05-18 | 2026 | 2025 | 2025-05-01 | Year_3 | P-09 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 10 | IG Unscheduled Maintenance
2025-05-18 | 2026 | 2025 | 2025-05-01 | Year_3 | P-10 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 10 | IG Unscheduled Maintenance
2025-05-18 | 2026 | 2025 | 2025-05-01 | Year_3 | P-11 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 10 | IG Unscheduled Maintenance
2025-05-18 | 2026 | 2025 | 2025-05-01 | Year_3 | P-12 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 10 | IG Unscheduled Maintenance
2025-05-18 | 2026 | 2025 | 2025-05-01 | Year_3 | P-13 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 10 | IG Unscheduled Maintenance
2025-05-18 | 2026 | 2025 | 2025-05-01 | Year_3 | P-08 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 10 | IG Unscheduled Maintenance
2025-05-18 | 2026 | 2025 | 2025-05-01 | Year_3 | P-25 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 10 | IG Unscheduled Maintenance
2025-05-18 | 2026 | 2025 | 2025-05-01 | Year_3 | P-26 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 10 | IG Unscheduled Maintenance
2025-05-18 | 2026 | 2025 | 2025-05-01 | Year_3 | P-27 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 10 | IG Unscheduled Maintenance
2025-05-18 | 2026 | 2025 | 2025-05-01 | Year_3 | P-28 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 10 | IG Unscheduled Maintenance
2025-05-18 | 2026 | 2025 | 2025-05-01 | Year_3 | Wind_F2 | PWEPL | MSEDCL | 27.27% | S/D for External line tree trimming work | 10:00 | 10:00 | 15:50 | 0 | 5.8333 | 5.8333 | Tree trimming work done | Close | 1.5909 | site average | 2315 | IG Unscheduled Maintenance
2025-05-18 | 2026 | 2025 | 2025-05-01 | Year_3 | P-14 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 11 | IG Unscheduled Maintenance
2025-05-18 | 2026 | 2025 | 2025-05-01 | Year_3 | P-15 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 11 | IG Unscheduled Maintenance
2025-05-18 | 2026 | 2025 | 2025-05-01 | Year_3 | P-16 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 11 | IG Unscheduled Maintenance
2025-05-18 | 2026 | 2025 | 2025-05-01 | Year_3 | P-17 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 11 | IG Unscheduled Maintenance
2025-05-18 | 2026 | 2025 | 2025-05-01 | Year_3 | P-19 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 11 | IG Unscheduled Maintenance
2025-05-18 | 2026 | 2025 | 2025-05-01 | Year_3 | P-20 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 11 | IG Unscheduled Maintenance
2025-05-18 | 2026 | 2025 | 2025-05-01 | Year_3 | P-38 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 11 | IG Unscheduled Maintenance
2025-05-18 | 2026 | 2025 | 2025-05-01 | Year_3 | P-04 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 11 | IG Unscheduled Maintenance
2025-05-18 | 2026 | 2025 | 2025-05-01 | Year_3 | P-22 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 11 | IG Unscheduled Maintenance
2025-05-18 | 2026 | 2025 | 2025-05-01 | Year_3 | P-23 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 11 | IG Unscheduled Maintenance
2025-05-18 | 2026 | 2025 | 2025-05-01 | Year_3 | P-34 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 11 | IG Unscheduled Maintenance
2025-05-18 | 2026 | 2025 | 2025-05-01 | Year_3 | P-43 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 11 | IG Unscheduled Maintenance
2025-05-19 | 2026 | 2025 | 2025-05-01 | Year_3 | Wind_F3 | PWEPL | MSEDCL | 20.45% | Feeder tripped by E/F | 0.27917 | 0.27917 | 0.33125 | 0 | 1.25 | 1.25 | Test charged taken charged successfully | Close | 0.25568 | site average | 900 | IG Breakdown Maintenance
2025-05-19 | 2026 | 2025 | 2025-05-01 | Year_3 | P-42 | PWEPL | MSEDCL | 2.273% | PWEPL-48 B phase LA failure | 0.33125 | 0.33125 | 0.34028 | 0 | 0.21667 | 0.21667 | LA replaced | Close | 0.0049242 | site average | 15 | IG Breakdown Maintenance
2025-05-19 | 2026 | 2025 | 2025-05-01 | Year_3 | P-42 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.34028 | 0.34028 | 0.35417 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 15 | IG Breakdown Maintenance
2025-05-19 | 2026 | 2025 | 2025-05-01 | Year_3 | P-45 | PWEPL | MSEDCL | 2.273% | PWEPL-48 B phase LA failure | 0.33125 | 0.33125 | 0.34028 | 0 | 0.21667 | 0.21667 | LA replaced | Close | 0.0049242 | site average | 15 | IG Breakdown Maintenance
2025-05-19 | 2026 | 2025 | 2025-05-01 | Year_3 | P-45 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.34028 | 0.34028 | 0.35417 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 15 | IG Breakdown Maintenance
2025-05-19 | 2026 | 2025 | 2025-05-01 | Year_3 | P-46 | PWEPL | MSEDCL | 2.273% | PWEPL-48 B phase LA failure | 0.33125 | 0.33125 | 0.34028 | 0 | 0.21667 | 0.21667 | LA replaced | Close | 0.0049242 | site average | 15 | IG Breakdown Maintenance
2025-05-19 | 2026 | 2025 | 2025-05-01 | Year_3 | P-46 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.34028 | 0.34028 | 0.35417 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 15 | IG Breakdown Maintenance
2025-05-19 | 2026 | 2025 | 2025-05-01 | Year_3 | P-47 | PWEPL | MSEDCL | 2.273% | PWEPL-48 B phase LA failure | 0.33125 | 0.33125 | 0.34028 | 0 | 0.21667 | 0.21667 | LA replaced | Close | 0.0049242 | site average | 15 | IG Breakdown Maintenance
2025-05-19 | 2026 | 2025 | 2025-05-01 | Year_3 | P-47 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.34028 | 0.34028 | 0.35417 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 15 | IG Breakdown Maintenance
2025-05-19 | 2026 | 2025 | 2025-05-01 | Year_3 | P-48 | PWEPL | MSEDCL | 2.273% | PWEPL-48 B phase LA failure | 0.33125 | 0.33125 | 0.34028 | 0 | 0.21667 | 0.21667 | LA replaced | Close | 0.0049242 | site average | 15 | IG Breakdown Maintenance
2025-05-19 | 2026 | 2025 | 2025-05-01 | Year_3 | P-48 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.34028 | 0.34028 | 0.35417 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 15 | IG Breakdown Maintenance
2025-05-19 | 2026 | 2025 | 2025-05-01 | Year_3 | P-05 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.33125 | 0.33125 | 0.34514 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 15 | IG Breakdown Maintenance
2025-05-19 | 2026 | 2025 | 2025-05-01 | Year_3 | P-06 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.33125 | 0.33125 | 0.34514 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 15 | IG Breakdown Maintenance
2025-05-19 | 2026 | 2025 | 2025-05-01 | Year_3 | P-40 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.33125 | 0.33125 | 0.34514 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 15 | IG Breakdown Maintenance
2025-05-19 | 2026 | 2025 | 2025-05-01 | Year_3 | P-41 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.33125 | 0.33125 | 0.34514 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 15 | IG Breakdown Maintenance
2025-05-19 | 2026 | 2025 | 2025-05-01 | Year_3 | Wind_F4 | PWEPL | MSEDCL | 29.55% | Feeder tripped by E/F | 0.35208 | 0.35208 | 0.37986 | 0 | 0.66667 | 0.66667 | Test charged taken charged successfully | Close | 0.19697 | site average | 780 | IG Breakdown Maintenance
2025-05-19 | 2026 | 2025 | 2025-05-01 | Year_3 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.37986 | 0.37986 | 0.39375 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 15 | IG Breakdown Maintenance
2025-05-19 | 2026 | 2025 | 2025-05-01 | Year_3 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.37986 | 0.37986 | 0.39375 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 15 | IG Breakdown Maintenance
2025-05-19 | 2026 | 2025 | 2025-05-01 | Year_3 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.37986 | 0.37986 | 0.39375 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 15 | IG Breakdown Maintenance
2025-05-19 | 2026 | 2025 | 2025-05-01 | Year_3 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.37986 | 0.37986 | 0.39375 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 15 | IG Breakdown Maintenance
2025-05-19 | 2026 | 2025 | 2025-05-01 | Year_3 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.37986 | 0.37986 | 0.39375 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 15 | IG Breakdown Maintenance
2025-05-19 | 2026 | 2025 | 2025-05-01 | Year_3 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.37986 | 0.37986 | 0.39375 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 15 | IG Breakdown Maintenance
2025-05-19 | 2026 | 2025 | 2025-05-01 | Year_3 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.37986 | 0.37986 | 0.39375 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 15 | IG Breakdown Maintenance
2025-05-19 | 2026 | 2025 | 2025-05-01 | Year_3 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.37986 | 0.37986 | 0.39375 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 15 | IG Breakdown Maintenance
2025-05-19 | 2026 | 2025 | 2025-05-01 | Year_3 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.37986 | 0.37986 | 0.39375 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 15 | IG Breakdown Maintenance
2025-05-19 | 2026 | 2025 | 2025-05-01 | Year_3 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.37986 | 0.37986 | 0.39375 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 15 | IG Breakdown Maintenance
2025-05-19 | 2026 | 2025 | 2025-05-01 | Year_3 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.37986 | 0.37986 | 0.39375 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 15 | IG Breakdown Maintenance
2025-05-19 | 2026 | 2025 | 2025-05-01 | Year_3 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.37986 | 0.37986 | 0.39375 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 15 | IG Breakdown Maintenance
2025-05-19 | 2026 | 2025 | 2025-05-01 | Year_3 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.37986 | 0.37986 | 0.39375 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 15 | IG Breakdown Maintenance
2025-05-19 | 2026 | 2025 | 2025-05-01 | Year_3 | P-04 | PWEPL | MSEDCL | 2.273% | S/D for CRP Panel Y Phase O/C Relay replacement work | 0.49653 | 0.49653 | 0.50278 | 0 | 0.15 | 0.15 | Relay replacement work done | Close | 0.0034091 | site average | 0 | IG Unscheduled Maintenance
2025-05-19 | 2026 | 2025 | 2025-05-01 | Year_3 | P-04 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.50278 | 0.50278 | 0.51667 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 0 | IG Unscheduled Maintenance
2025-05-19 | 2026 | 2025 | 2025-05-01 | Year_3 | P-23 | PWEPL | MSEDCL | 2.273% | S/D for CRP Panel R & Y Phase O/C Relay replacement work | 0.51181 | 0.51181 | 0.52153 | 0 | 0.23333 | 0.23333 | Relay replacement work done | Close | 0.005303 | site average | 0 | IG Unscheduled Maintenance
2025-05-19 | 2026 | 2025 | 2025-05-01 | Year_3 | P-23 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.52153 | 0.52153 | 0.53542 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 0 | IG Unscheduled Maintenance
2025-05-19 | 2026 | 2025 | 2025-05-01 | Year_3 | P-43 | PWEPL | MSEDCL | 2.273% | S/D for CRP Panel B Phase O/C Relay replacement work | 0.53611 | 0.53611 | 0.54236 | 0 | 0.15 | 0.15 | Relay replacement work done | Close | 0.0034091 | site average | 0 | IG Unscheduled Maintenance
2025-05-19 | 2026 | 2025 | 2025-05-01 | Year_3 | P-43 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.54236 | 0.54236 | 0.55625 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 0 | IG Unscheduled Maintenance
2025-05-19 | 2026 | 2025 | 2025-05-01 | Year_3 | P-52 | PWEPL | MSEDCL | 2.273% | S/D for CRP Panel R & Y Phase O/C Relay replacement work | 0.56528 | 0.56528 | 0.57569 | 0 | 0.25 | 0.25 | Relay replacement work done | Close | 0.0056818 | site average | 0 | IG Unscheduled Maintenance
2025-05-19 | 2026 | 2025 | 2025-05-01 | Year_3 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.57569 | 0.57569 | 0.58958 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 0 | IG Unscheduled Maintenance
2025-05-19 | 2026 | 2025 | 2025-05-01 | Year_3 | P-02 | PWEPL | MSEDCL | 2.273% | S/D for CRP Panel B Phase O/C Relay replacement work | 0.63472 | 0.63472 | 0.64306 | 0 | 0.2 | 0.2 | Relay replacement work done | Close | 0.0045455 | site average | 0 | IG Unscheduled Maintenance
2025-05-19 | 2026 | 2025 | 2025-05-01 | Year_3 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.64306 | 0.64306 | 0.65694 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 0 | IG Unscheduled Maintenance
2025-05-20 | 2026 | 2025 | 2025-05-01 | Year_3 | Wind_F1 | PWEPL | MSEDCL | 22.73% | S/D for External line tree trimming work | 0.36806 | 0.36806 | 0.71389 | 0 | 8.3 | 8.3 | Tree trimming work done | Close | 1.8864 | site average | 557 | IG Unscheduled Maintenance
2025-05-20 | 2026 | 2025 | 2025-05-01 | Year_3 | P-09 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.71389 | 0.71389 | 0.72778 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 22 | IG Unscheduled Maintenance
2025-05-20 | 2026 | 2025 | 2025-05-01 | Year_3 | P-10 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.71389 | 0.71389 | 0.72778 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 22 | IG Unscheduled Maintenance
2025-05-20 | 2026 | 2025 | 2025-05-01 | Year_3 | P-11 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.71389 | 0.71389 | 0.72778 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 22 | IG Unscheduled Maintenance
2025-05-20 | 2026 | 2025 | 2025-05-01 | Year_3 | P-12 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.71389 | 0.71389 | 0.72778 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 22 | IG Unscheduled Maintenance
2025-05-20 | 2026 | 2025 | 2025-05-01 | Year_3 | P-13 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.71389 | 0.71389 | 0.72778 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 22 | IG Unscheduled Maintenance
2025-05-20 | 2026 | 2025 | 2025-05-01 | Year_3 | P-08 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.71389 | 0.71389 | 0.72778 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 22 | IG Unscheduled Maintenance
2025-05-20 | 2026 | 2025 | 2025-05-01 | Year_3 | P-25 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.71389 | 0.71389 | 0.72778 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 22 | IG Unscheduled Maintenance
2025-05-20 | 2026 | 2025 | 2025-05-01 | Year_3 | P-26 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.71389 | 0.71389 | 0.72778 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 22 | IG Unscheduled Maintenance
2025-05-20 | 2026 | 2025 | 2025-05-01 | Year_3 | P-27 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.71389 | 0.71389 | 0.72778 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 22 | IG Unscheduled Maintenance
2025-05-20 | 2026 | 2025 | 2025-05-01 | Year_3 | P-28 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.71389 | 0.71389 | 0.72778 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 22 | IG Unscheduled Maintenance
2025-05-20 | 2026 | 2025 | 2025-05-01 | Year_3 | Wind_F2 | PWEPL | MSEDCL | 27.27% | S/D for External line tree trimming work | 0.36806 | 0.36806 | 0.72292 | 0 | 8.5167 | 8.5167 | Tree trimming work done | Close | 2.3227 | site average | 7609 | IG Unscheduled Maintenance
2025-05-20 | 2026 | 2025 | 2025-05-01 | Year_3 | P-14 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.72292 | 0.72292 | 0.73681 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 24 | IG Unscheduled Maintenance
2025-05-20 | 2026 | 2025 | 2025-05-01 | Year_3 | P-15 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.72292 | 0.72292 | 0.73681 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 24 | IG Unscheduled Maintenance
2025-05-20 | 2026 | 2025 | 2025-05-01 | Year_3 | P-16 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.72292 | 0.72292 | 0.73681 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 24 | IG Unscheduled Maintenance
2025-05-20 | 2026 | 2025 | 2025-05-01 | Year_3 | P-17 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.72292 | 0.72292 | 0.73681 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 24 | IG Unscheduled Maintenance
2025-05-20 | 2026 | 2025 | 2025-05-01 | Year_3 | P-19 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.72292 | 0.72292 | 0.73681 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 24 | IG Unscheduled Maintenance
2025-05-20 | 2026 | 2025 | 2025-05-01 | Year_3 | P-20 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.72292 | 0.72292 | 0.73681 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 24 | IG Unscheduled Maintenance
2025-05-20 | 2026 | 2025 | 2025-05-01 | Year_3 | P-38 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.72292 | 0.72292 | 0.73681 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 24 | IG Unscheduled Maintenance
2025-05-20 | 2026 | 2025 | 2025-05-01 | Year_3 | P-04 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.72292 | 0.72292 | 0.73681 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 24 | IG Unscheduled Maintenance
2025-05-20 | 2026 | 2025 | 2025-05-01 | Year_3 | P-22 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.72292 | 0.72292 | 0.73681 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 24 | IG Unscheduled Maintenance
2025-05-20 | 2026 | 2025 | 2025-05-01 | Year_3 | P-23 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.72292 | 0.72292 | 0.73681 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 24 | IG Unscheduled Maintenance
2025-05-20 | 2026 | 2025 | 2025-05-01 | Year_3 | P-34 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.72292 | 0.72292 | 0.73681 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 24 | IG Unscheduled Maintenance
2025-05-20 | 2026 | 2025 | 2025-05-01 | Year_3 | P-43 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.72292 | 0.72292 | 0.73681 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 24 | IG Unscheduled Maintenance
2025-05-22 | 2026 | 2025 | 2025-05-01 | Year_3 | P-32 | PWEPL | MSEDCL | 2.273% | S/D for CRP Panel R & B Phase O/C Relay replacement work | 0.49097 | 0.49097 | 0.5 | 0 | 0.21667 | 0.21667 | Relay replacement work done | Close | 0.0049242 | site average | 69 | IG Unscheduled Maintenance
2025-05-22 | 2026 | 2025 | 2025-05-01 | Year_3 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.5 | 0.5 | 0.51389 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 94 | IG Unscheduled Maintenance
2025-05-22 | 2026 | 2025 | 2025-05-01 | Year_3 | P-37 | PWEPL | MSEDCL | 2.273% | S/D for CRP Panel R Phase O/C Relay replacement work | 0.51458 | 0.51458 | 0.52153 | 0 | 0.16667 | 0.16667 | Relay replacement work done | Close | 0.0037879 | site average | 6 | IG Unscheduled Maintenance
2025-05-22 | 2026 | 2025 | 2025-05-01 | Year_3 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.52153 | 0.52153 | 0.53542 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 47 | IG Unscheduled Maintenance
2025-05-22 | 2026 | 2025 | 2025-05-01 | Year_3 | P-25 | PWEPL | MSEDCL | 2.273% | S/D for CRP Panel R & Y Phase O/C Relay replacement work | 0.64306 | 0.64306 | 0.65972 | 0 | 0.4 | 0.4 | Relay replacement work done | Close | 0.0090909 | site average | 152 | IG Unscheduled Maintenance
2025-05-22 | 2026 | 2025 | 2025-05-01 | Year_3 | P-25 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.65972 | 0.65972 | 0.67361 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 21 | IG Unscheduled Maintenance
2025-05-22 | 2026 | 2025 | 2025-05-01 | Year_3 | P-27 | PWEPL | MSEDCL | 2.273% | S/D for CRP Panel R Phase O/C Relay replacement work | 0.58125 | 0.58125 | 0.60208 | 0 | 0.5 | 0.5 | Relay replacement work done | Close | 0.011364 | site average | 369 | IG Unscheduled Maintenance
2025-05-22 | 2026 | 2025 | 2025-05-01 | Year_3 | P-27 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.60208 | 0.60208 | 0.61597 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 60 | IG Unscheduled Maintenance
2025-05-22 | 2026 | 2025 | 2025-05-01 | Year_3 | Wind_F4 | PWEPL | MSEDCL | 29.55% | Feeder tripped by E/F | 0.91042 | 0.91042 | 0.92431 | 0 | 0.33333 | 0.33333 | Test charged taken charged successfully | Close | 0.098485 | site average | 938 | IG Breakdown Maintenance
2025-05-22 | 2026 | 2025 | 2025-05-01 | Year_3 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.92431 | 0.92431 | 0.93819 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 72 | IG Breakdown Maintenance
2025-05-22 | 2026 | 2025 | 2025-05-01 | Year_3 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.92431 | 0.92431 | 0.93819 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 72 | IG Breakdown Maintenance
2025-05-22 | 2026 | 2025 | 2025-05-01 | Year_3 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.92431 | 0.92431 | 0.93819 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 72 | IG Breakdown Maintenance
2025-05-22 | 2026 | 2025 | 2025-05-01 | Year_3 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.92431 | 0.92431 | 0.93819 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 72 | IG Breakdown Maintenance
2025-05-22 | 2026 | 2025 | 2025-05-01 | Year_3 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.92431 | 0.92431 | 0.93819 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 72 | IG Breakdown Maintenance
2025-05-22 | 2026 | 2025 | 2025-05-01 | Year_3 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.92431 | 0.92431 | 0.93819 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 72 | IG Breakdown Maintenance
2025-05-22 | 2026 | 2025 | 2025-05-01 | Year_3 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.92431 | 0.92431 | 0.93819 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 72 | IG Breakdown Maintenance
2025-05-22 | 2026 | 2025 | 2025-05-01 | Year_3 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.92431 | 0.92431 | 0.93819 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 72 | IG Breakdown Maintenance
2025-05-22 | 2026 | 2025 | 2025-05-01 | Year_3 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.92431 | 0.92431 | 0.93819 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 72 | IG Breakdown Maintenance
2025-05-22 | 2026 | 2025 | 2025-05-01 | Year_3 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.92431 | 0.92431 | 0.93819 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 72 | IG Breakdown Maintenance
2025-05-22 | 2026 | 2025 | 2025-05-01 | Year_3 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.92431 | 0.92431 | 0.93819 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 72 | IG Breakdown Maintenance
2025-05-22 | 2026 | 2025 | 2025-05-01 | Year_3 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.92431 | 0.92431 | 0.93819 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 72 | IG Breakdown Maintenance
2025-05-22 | 2026 | 2025 | 2025-05-01 | Year_3 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.92431 | 0.92431 | 0.93819 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 72 | IG Breakdown Maintenance
2025-05-23 | 2026 | 2025 | 2025-05-01 | Year_3 | Wind_F4 | PWEPL | MSEDCL | 29.55% | Feeder tripped by E/F | 0.058333 | 0.058333 | 0.072222 | 0 | 0.33333 | 0.33333 | Test charged taken charged successfully | Close | 0.098485 | site average | 1248 | IG Breakdown Maintenance
2025-05-23 | 2026 | 2025 | 2025-05-01 | Year_3 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.072222 | 0.072222 | 0.077778 | 0 | 0.13333 | 0.13333 | Rebooted the PLC & reset at scada | Close | 0.0030303 | site average | 96 | IG Breakdown Maintenance
2025-05-23 | 2026 | 2025 | 2025-05-01 | Year_3 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.072222 | 0.072222 | 0.077778 | 0 | 0.13333 | 0.13333 | Rebooted the PLC & reset at scada | Close | 0.0030303 | site average | 96 | IG Breakdown Maintenance
2025-05-23 | 2026 | 2025 | 2025-05-01 | Year_3 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.072222 | 0.072222 | 0.077778 | 0 | 0.13333 | 0.13333 | Rebooted the PLC & reset at scada | Close | 0.0030303 | site average | 96 | IG Breakdown Maintenance
2025-05-23 | 2026 | 2025 | 2025-05-01 | Year_3 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.072222 | 0.072222 | 0.077778 | 0 | 0.13333 | 0.13333 | Rebooted the PLC & reset at scada | Close | 0.0030303 | site average | 96 | IG Breakdown Maintenance
2025-05-23 | 2026 | 2025 | 2025-05-01 | Year_3 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.072222 | 0.072222 | 0.077778 | 0 | 0.13333 | 0.13333 | Rebooted the PLC & reset at scada | Close | 0.0030303 | site average | 96 | IG Breakdown Maintenance
2025-05-23 | 2026 | 2025 | 2025-05-01 | Year_3 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.072222 | 0.072222 | 0.077778 | 0 | 0.13333 | 0.13333 | Rebooted the PLC & reset at scada | Close | 0.0030303 | site average | 96 | IG Breakdown Maintenance
2025-05-23 | 2026 | 2025 | 2025-05-01 | Year_3 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.072222 | 0.072222 | 0.077778 | 0 | 0.13333 | 0.13333 | Rebooted the PLC & reset at scada | Close | 0.0030303 | site average | 96 | IG Breakdown Maintenance
2025-05-23 | 2026 | 2025 | 2025-05-01 | Year_3 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.072222 | 0.072222 | 0.077778 | 0 | 0.13333 | 0.13333 | Rebooted the PLC & reset at scada | Close | 0.0030303 | site average | 96 | IG Breakdown Maintenance
2025-05-23 | 2026 | 2025 | 2025-05-01 | Year_3 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.072222 | 0.072222 | 0.077778 | 0 | 0.13333 | 0.13333 | Rebooted the PLC & reset at scada | Close | 0.0030303 | site average | 96 | IG Breakdown Maintenance
2025-05-23 | 2026 | 2025 | 2025-05-01 | Year_3 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.072222 | 0.072222 | 0.077778 | 0 | 0.13333 | 0.13333 | Rebooted the PLC & reset at scada | Close | 0.0030303 | site average | 96 | IG Breakdown Maintenance
2025-05-23 | 2026 | 2025 | 2025-05-01 | Year_3 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.072222 | 0.072222 | 0.077778 | 0 | 0.13333 | 0.13333 | Rebooted the PLC & reset at scada | Close | 0.0030303 | site average | 96 | IG Breakdown Maintenance
2025-05-23 | 2026 | 2025 | 2025-05-01 | Year_3 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.072222 | 0.072222 | 0.077778 | 0 | 0.13333 | 0.13333 | Rebooted the PLC & reset at scada | Close | 0.0030303 | site average | 96 | IG Breakdown Maintenance
2025-05-23 | 2026 | 2025 | 2025-05-01 | Year_3 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.072222 | 0.072222 | 0.077778 | 0 | 0.13333 | 0.13333 | Rebooted the PLC & reset at scada | Close | 0.0030303 | site average | 96 | IG Breakdown Maintenance
2025-05-23 | 2026 | 2025 | 2025-05-01 | Year_3 | Wind_F4 | PWEPL | MSEDCL | 29.55% | Feeder tripped by E/F | 0.077778 | 0.077778 | 0.20486 | 0 | 3.05 | 3.05 | External line cp 186 R phase pin insulator replaced & charge | Close | 0.90114 | site average | 18067 | IG Breakdown Maintenance
2025-05-23 | 2026 | 2025 | 2025-05-01 | Year_3 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.20486 | 0.20486 | 0.21875 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 150 | IG Breakdown Maintenance
2025-05-23 | 2026 | 2025 | 2025-05-01 | Year_3 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.20486 | 0.20486 | 0.21875 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 150 | IG Breakdown Maintenance
2025-05-23 | 2026 | 2025 | 2025-05-01 | Year_3 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.20486 | 0.20486 | 0.21875 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 150 | IG Breakdown Maintenance
2025-05-23 | 2026 | 2025 | 2025-05-01 | Year_3 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.20486 | 0.20486 | 0.21875 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 150 | IG Breakdown Maintenance
2025-05-23 | 2026 | 2025 | 2025-05-01 | Year_3 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.20486 | 0.20486 | 0.21875 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 150 | IG Breakdown Maintenance
2025-05-23 | 2026 | 2025 | 2025-05-01 | Year_3 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.20486 | 0.20486 | 0.21875 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 150 | IG Breakdown Maintenance
2025-05-23 | 2026 | 2025 | 2025-05-01 | Year_3 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.20486 | 0.20486 | 0.21875 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 150 | IG Breakdown Maintenance
2025-05-23 | 2026 | 2025 | 2025-05-01 | Year_3 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.20486 | 0.20486 | 0.21875 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 150 | IG Breakdown Maintenance
2025-05-23 | 2026 | 2025 | 2025-05-01 | Year_3 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.20486 | 0.20486 | 0.21875 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 150 | IG Breakdown Maintenance
2025-05-23 | 2026 | 2025 | 2025-05-01 | Year_3 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.20486 | 0.20486 | 0.21875 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 150 | IG Breakdown Maintenance
2025-05-23 | 2026 | 2025 | 2025-05-01 | Year_3 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.20486 | 0.20486 | 0.21875 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 150 | IG Breakdown Maintenance
2025-05-23 | 2026 | 2025 | 2025-05-01 | Year_3 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.20486 | 0.20486 | 0.21875 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 150 | IG Breakdown Maintenance
2025-05-23 | 2026 | 2025 | 2025-05-01 | Year_3 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.20486 | 0.20486 | 0.21875 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 150 | IG Breakdown Maintenance
2025-05-23 | 2026 | 2025 | 2025-05-01 | Year_3 | P-05 | PWEPL | MSEDCL | 2.273% | S/D for CRP Panel R Phase O/C Relay replacement work | 0.48542 | 0.48542 | 0.49444 | 0 | 0.21667 | 0.21667 | Relay replacement work done | Close | 0.0049242 | site average | 219 | IG Breakdown Maintenance
2025-05-23 | 2026 | 2025 | 2025-05-01 | Year_3 | P-05 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.49444 | 0.49444 | 0.50833 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 34 | IG Unscheduled Maintenance
2025-05-25 | 2026 | 2025 | 2025-05-01 | Year_3 | Wind_F4 | PWEPL | MSEDCL | 29.55% | Feeder tripped by E/F | 0.10903 | 0.10903 | 0.15764 | 0 | 1.1667 | 1.1667 | PWEPL-61 SEM B Phase PT failed | Close | 0.3447 | site average | 899 | IG Breakdown Maintenance
2025-05-25 | 2026 | 2025 | 2025-05-01 | Year_3 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.15764 | 0.15764 | 0.17153 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 20 | IG Breakdown Maintenance
2025-05-25 | 2026 | 2025 | 2025-05-01 | Year_3 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.15764 | 0.15764 | 0.17153 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 20 | IG Breakdown Maintenance
2025-05-25 | 2026 | 2025 | 2025-05-01 | Year_3 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.15764 | 0.15764 | 0.17153 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 20 | IG Breakdown Maintenance
2025-05-25 | 2026 | 2025 | 2025-05-01 | Year_3 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.15764 | 0.15764 | 0.17153 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 20 | IG Breakdown Maintenance
2025-05-25 | 2026 | 2025 | 2025-05-01 | Year_3 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.15764 | 0.15764 | 0.17153 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 20 | IG Breakdown Maintenance
2025-05-25 | 2026 | 2025 | 2025-05-01 | Year_3 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.15764 | 0.15764 | 0.17153 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 20 | IG Breakdown Maintenance
2025-05-25 | 2026 | 2025 | 2025-05-01 | Year_3 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.15764 | 0.15764 | 0.17153 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 20 | IG Breakdown Maintenance
2025-05-25 | 2026 | 2025 | 2025-05-01 | Year_3 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.15764 | 0.15764 | 0.17153 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 20 | IG Breakdown Maintenance
2025-05-25 | 2026 | 2025 | 2025-05-01 | Year_3 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.15764 | 0.15764 | 0.17153 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 20 | IG Breakdown Maintenance
2025-05-25 | 2026 | 2025 | 2025-05-01 | Year_3 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.15764 | 0.15764 | 0.17153 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 20 | IG Breakdown Maintenance
2025-05-25 | 2026 | 2025 | 2025-05-01 | Year_3 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.15764 | 0.15764 | 0.17153 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 20 | IG Breakdown Maintenance
2025-05-25 | 2026 | 2025 | 2025-05-01 | Year_3 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.15764 | 0.15764 | 0.17153 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 20 | IG Breakdown Maintenance
2025-05-25 | 2026 | 2025 | 2025-05-01 | Year_3 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.15764 | 0.15764 | 0.17153 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 20 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | Wind_F4 | PWEPL | MSEDCL | 29.55% | Feeder tripped by O/C | 0.24236 | 0.24236 | 0.26181 | 0 | 0.46667 | 0.46667 | Test charged taken charged successfully | Close | 0.13788 | site average | 3324 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.26181 | 0.26181 | 0.27569 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 183 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.26181 | 0.26181 | 0.27569 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 183 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.26181 | 0.26181 | 0.27569 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 183 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.26181 | 0.26181 | 0.27569 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 183 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.26181 | 0.26181 | 0.27569 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 183 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.26181 | 0.26181 | 0.27569 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 183 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.26181 | 0.26181 | 0.27569 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 183 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.26181 | 0.26181 | 0.27569 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 183 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.26181 | 0.26181 | 0.27569 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 183 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.26181 | 0.26181 | 0.27569 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 183 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.26181 | 0.26181 | 0.27569 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 183 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.26181 | 0.26181 | 0.27569 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 183 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.26181 | 0.26181 | 0.27569 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 183 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | Wind_F4 | PWEPL | MSEDCL | 29.55% | Feeder tripped by O/C | 0.40764 | 0.40764 | 0.42708 | 0 | 0.46667 | 0.46667 | Test charged taken charged successfully | Close | 0.13788 | site average | 8936 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.42708 | 0.42708 | 0.44097 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 491 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.42708 | 0.42708 | 0.44097 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 491 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.42708 | 0.42708 | 0.44097 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 491 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.42708 | 0.42708 | 0.44097 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 491 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.42708 | 0.42708 | 0.44097 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 491 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.42708 | 0.42708 | 0.44097 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 491 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.42708 | 0.42708 | 0.44097 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 491 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.42708 | 0.42708 | 0.44097 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 491 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.42708 | 0.42708 | 0.44097 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 491 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.42708 | 0.42708 | 0.44097 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 491 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.42708 | 0.42708 | 0.44097 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 491 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.42708 | 0.42708 | 0.44097 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 491 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.42708 | 0.42708 | 0.44097 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 491 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | Wind_F4 | PWEPL | MSEDCL | 29.55% | Feeder tripped by O/C | 0.75972 | 0.75972 | 0.76806 | 0 | 0.2 | 0.2 | Test charged taken charged successfully | Close | 0.059091 | site average | 1953 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.76806 | 0.76806 | 0.78194 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 250 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.76806 | 0.76806 | 0.78194 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 250 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.76806 | 0.76806 | 0.78194 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 250 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.76806 | 0.76806 | 0.78194 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 250 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.76806 | 0.76806 | 0.78194 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 250 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.76806 | 0.76806 | 0.78194 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 250 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.76806 | 0.76806 | 0.78194 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 250 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.76806 | 0.76806 | 0.78194 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 250 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.76806 | 0.76806 | 0.78194 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 250 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.76806 | 0.76806 | 0.78194 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 250 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.76806 | 0.76806 | 0.78194 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 250 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.76806 | 0.76806 | 0.78194 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 250 | IG Breakdown Maintenance
2025-05-26 | 2026 | 2025 | 2025-05-01 | Year_3 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.76806 | 0.76806 | 0.78194 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 250 | IG Breakdown Maintenance
2025-05-28 | 2026 | 2025 | 2025-05-01 | Year_3 | Wind_F3 | PWEPL | MSEDCL | 20.45% | Feeder tripped by O/C | 0.72292 | 0.72292 | 0.90278 | 0 | 4.3167 | 4.3167 | CKT-2 ,PP-43 B phase pin insulator replaced | Close | 0.88295 | site average | 16932 | IG Breakdown Maintenance
2025-05-28 | 2026 | 2025 | 2025-05-01 | Year_3 | P-42 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.90278 | 0.90278 | 0.91667 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 156 | IG Breakdown Maintenance
2025-05-28 | 2026 | 2025 | 2025-05-01 | Year_3 | P-45 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.90278 | 0.90278 | 0.91667 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 156 | IG Breakdown Maintenance
2025-05-28 | 2026 | 2025 | 2025-05-01 | Year_3 | P-46 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.90278 | 0.90278 | 0.91667 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 156 | IG Breakdown Maintenance
2025-05-28 | 2026 | 2025 | 2025-05-01 | Year_3 | P-47 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.90278 | 0.90278 | 0.91667 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 156 | IG Breakdown Maintenance
2025-05-28 | 2026 | 2025 | 2025-05-01 | Year_3 | P-48 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.90278 | 0.90278 | 0.91667 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 156 | IG Breakdown Maintenance
2025-05-28 | 2026 | 2025 | 2025-05-01 | Year_3 | P-05 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.90278 | 0.90278 | 0.91667 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 156 | IG Breakdown Maintenance
2025-05-28 | 2026 | 2025 | 2025-05-01 | Year_3 | P-06 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.90278 | 0.90278 | 0.91667 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 156 | IG Breakdown Maintenance
2025-05-28 | 2026 | 2025 | 2025-05-01 | Year_3 | P-40 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.90278 | 0.90278 | 0.91667 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 156 | IG Breakdown Maintenance
2025-05-28 | 2026 | 2025 | 2025-05-01 | Year_3 | P-41 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0.90278 | 0.90278 | 0.91667 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 156 | IG Breakdown Maintenance
2025-05-30 | 2026 | 2025 | 2025-05-01 | Year_3 | P-46 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 17:44 | 17:44 | 18:25 | 0 | 0.68333 | 0.68333 | VCB reset & Charge | Close | 0.01553 | site average | 741 | IG Breakdown Maintenance
2025-05-30 | 2026 | 2025 | 2025-05-01 | Year_3 | P-46 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:25 | 18:25 | 18:45 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 740 | IG Breakdown Maintenance
2025-05-31 | 2026 | 2025 | 2025-05-01 | Year_3 | P-46 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 8:53 | 8:53 | 9:25 | 0 | 0.53333 | 0.53333 | VCB reset & Charge | Close | 0.012121 | site average | 805 | IG Breakdown Maintenance
2025-05-31 | 2026 | 2025 | 2025-05-01 | Year_3 | P-46 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 9:25 | 9:25 | 9:38 | 0 | 0.21667 | 0.21667 | Rebooted the PLC & reset at scada | Close | 0.0049242 | site average | 550 | IG Breakdown Maintenance
2025-06-02 | 2026 | 2025 | 2025-06-01 | Year_3 | Wind_F1 | PWEPL | MSEDCL | 22.73% | Feeder tripped by O/C | 23:14 | 23:14 | 23:24 | 0 | 0.16667 | 0.16667 | Test charged taken charged successfully | Close | 0.037879 | site average | 1200 | IG Breakdown Maintenance
2025-06-02 | 2026 | 2025 | 2025-06-01 | Year_3 | P-09 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 23:24 | 23:24 | 23:28 | 0 | 0.066667 | 0.066667 | Rebooted the PLC & reset at scada | Close | 0.0015152 | site average | 48 | IG Breakdown Maintenance
2025-06-02 | 2026 | 2025 | 2025-06-01 | Year_3 | P-10 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 23:24 | 23:24 | 23:36 | 0 | 0.2 | 0.2 | Rebooted the PLC & reset at scada | Close | 0.0045455 | site average | 144 | IG Breakdown Maintenance
2025-06-02 | 2026 | 2025 | 2025-06-01 | Year_3 | P-11 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 23:24 | 23:24 | 23:35 | 0 | 0.18333 | 0.18333 | Rebooted the PLC & reset at scada | Close | 0.0041667 | site average | 132 | IG Breakdown Maintenance
2025-06-02 | 2026 | 2025 | 2025-06-01 | Year_3 | P-12 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 23:24 | 23:24 | 23:39 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | site average | 180 | IG Breakdown Maintenance
2025-06-02 | 2026 | 2025 | 2025-06-01 | Year_3 | P-13 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 23:24 | 23:24 | 23:35 | 0 | 0.18333 | 0.18333 | Rebooted the PLC & reset at scada | Close | 0.0041667 | site average | 132 | IG Breakdown Maintenance
2025-06-02 | 2026 | 2025 | 2025-06-01 | Year_3 | P-08 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 23:24 | 23:24 | 23:30 | 0 | 0.1 | 0.1 | Rebooted the PLC & reset at scada | Close | 0.0022727 | site average | 72 | IG Breakdown Maintenance
2025-06-02 | 2026 | 2025 | 2025-06-01 | Year_3 | P-25 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 23:24 | 23:24 | 23:29 | 0 | 0.083333 | 0.083333 | Rebooted the PLC & reset at scada | Close | 0.0018939 | site average | 60 | IG Breakdown Maintenance
2025-06-02 | 2026 | 2025 | 2025-06-01 | Year_3 | P-26 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 23:24 | 23:24 | 23:59 | 0 | 0.58333 | 0.58333 | Rebooted the PLC & reset at scada | Close | 0.013258 | site average | 60 | IG Breakdown Maintenance
2025-06-02 | 2026 | 2025 | 2025-06-01 | Year_3 | P-27 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 23:24 | 23:24 | 23:30 | 0 | 0.1 | 0.1 | Rebooted the PLC & reset at scada | Close | 0.0022727 | site average | 72 | IG Breakdown Maintenance
2025-06-02 | 2026 | 2025 | 2025-06-01 | Year_3 | P-28 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 23:24 | 23:24 | 23:44 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 240 | IG Breakdown Maintenance
2025-06-02 | 2026 | 2025 | 2025-06-01 | Year_3 | P-46 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 19:00 | 19:00 | 20:00 | 0 | 1 | 1 | VCB reset & Charge | Close | 0.022727 | site average | 966 | IG Breakdown Maintenance
2025-06-02 | 2026 | 2025 | 2025-06-01 | Year_3 | P-46 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 20:00 | 20:00 | 20:20 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 482 | IG Breakdown Maintenance
2025-06-03 | 2026 | 2025 | 2025-06-01 | Year_3 | P-10 | PWEPL | MSEDCL | 2.273% | S/D for SEM B Phase CT replacement work | 13:39 | 13:39 | 14:30 | 0 | 0.85 | 0.85 | CT replacement work done | Close | 0.019318 | site average | 641 | IG Unscheduled Maintenance
2025-06-03 | 2026 | 2025 | 2025-06-01 | Year_3 | P-10 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 14:30 | 14:30 | 14:50 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | site average | 412 | IG Unscheduled Maintenance
2025-06-03 | 2026 | 2025 | 2025-06-01 | Year_3 | P-09 | PWEPL | MSEDCL | 2.273% | S/D for SEM Y Phase PT replacement work | 14:40 | 14:40 | 15:31 | 0 | 0.85 | 0.85 | PT replacement work done | Close | 0.019318 | site average | 381 | IG Unscheduled Maintenance
2025-06-03 | 2026 | 2025 | 2025-06-01 | Year_3 | P-09 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:31 | 15:31 | 15:47 | 0 | 0.26667 | 0.26667 | Rebooted the PLC & reset at scada | Close | 0.0060606 | site average | 174 | IG Unscheduled Maintenance
2025-06-04 | 2026 | 2025 | 2025-06-01 | Year_3 | P-11 | PWEPL | MSEDCL | 2.273% | S/D for SEM Y Phase CT replacement work | 11:57 | 11:57 | 13:24 | 0 | 1.45 | 1.45 | CT replacement work done | Close | 0.032955 | site average | 172 | IG Unscheduled Maintenance
2025-06-04 | 2026 | 2025 | 2025-06-01 | Year_3 | P-11 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:24 | 13:24 | 13:39 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | site average | 35 | IG Unscheduled Maintenance
2025-06-05 | 2026 | 2025 | 2025-06-01 | Year_3 | P-01 | PWEPL | MSEDCL | 2.273% | S/D for SEM Y Phase PT replacement work | 11:20 | 11:20 | 12:11 | 0 | 0.85 | 0.85 | PT replacement work done | Close | 0.019318 | site average | 83 | IG Unscheduled Maintenance
2025-06-05 | 2026 | 2025 | 2025-06-01 | Year_3 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:11 | 12:11 | 12:18 | 0 | 0.11667 | 0.11667 | Rebooted the PLC & reset at scada | Close | 0.0026515 | site average | 15 | IG Unscheduled Maintenance
2025-06-05 | 2026 | 2025 | 2025-06-01 | Year_3 | P-06 | PWEPL | MSEDCL | 2.273% | S/D for SEM R Phase PT replacement work | 12:33 | 12:33 | 13:09 | 0 | 0.6 | 0.6 | PT replacement work done | Close | 0.013636 | site average | 219 | IG Unscheduled Maintenance
2025-06-05 | 2026 | 2025 | 2025-06-01 | Year_3 | P-06 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:09 | 13:09 | 13:19 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | site average | 83 | IG Unscheduled Maintenance
2025-06-05 | 2026 | 2025 | 2025-06-01 | Year_3 | Wind_F3 | PWEPL | MSEDCL | 20.45% | Feeder tripped by O/C | 16:39 | 16:39 | 16:57 | 0 | 0.3 | 0.3 | Test charged taken charged successfully | Close | 0.061364 | site average | 1647 | IG Breakdown Maintenance
2025-06-05 | 2026 | 2025 | 2025-06-01 | Year_3 | P-42 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:57 | 16:57 | 17:11 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | site average | 142 | IG Breakdown Maintenance
2025-06-05 | 2026 | 2025 | 2025-06-01 | Year_3 | P-45 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:57 | 16:57 | 17:11 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | site average | 142 | IG Breakdown Maintenance
2025-06-05 | 2026 | 2025 | 2025-06-01 | Year_3 | P-46 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:57 | 16:57 | 17:09 | 0 | 0.2 | 0.2 | Rebooted the PLC & reset at scada | Close | 0.0045455 | site average | 122 | IG Breakdown Maintenance
2025-06-05 | 2026 | 2025 | 2025-06-01 | Year_3 | P-47 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:57 | 16:57 | 17:09 | 0 | 0.2 | 0.2 | Rebooted the PLC & reset at scada | Close | 0.0045455 | site average | 122 | IG Breakdown Maintenance
2025-06-05 | 2026 | 2025 | 2025-06-01 | Year_3 | P-48 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:57 | 16:57 | 17:10 | 0 | 0.21667 | 0.21667 | Rebooted the PLC & reset at scada | Close | 0.0049242 | site average | 132 | IG Breakdown Maintenance
2025-06-05 | 2026 | 2025 | 2025-06-01 | Year_3 | P-05 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:57 | 16:57 | 17:09 | 0 | 0.2 | 0.2 | Rebooted the PLC & reset at scada | Close | 0.0045455 | site average | 122 | IG Breakdown Maintenance
2025-06-05 | 2026 | 2025 | 2025-06-01 | Year_3 | P-06 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:57 | 16:57 | 17:13 | 0 | 0.26667 | 0.26667 | Rebooted the PLC & reset at scada | Close | 0.0060606 | site average | 162 | IG Breakdown Maintenance
2025-06-05 | 2026 | 2025 | 2025-06-01 | Year_3 | P-40 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:57 | 16:57 | 17:12 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | site average | 152 | IG Breakdown Maintenance
2025-06-05 | 2026 | 2025 | 2025-06-01 | Year_3 | P-41 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:57 | 16:57 | 17:16 | 0 | 0.31667 | 0.31667 | Rebooted the PLC & reset at scada | Close | 0.007197 | site average | 193 | IG Breakdown Maintenance
Formulas:
Month = [Date]-DAY([Date])+1
Response Time = (IGA_BD[[#This Row],[Work Start TimeStamp]]-IGA_BD[[#This Row],[Fault Start TimeStamp]])*24

## PM
Sr. No. | Location No. | Location Type | FY | CY | Cycle No. | Frequency | PM Title | Day 1 Planned Maintenance Date | Day 2 Planned Maintenance Date | Day 1 Actual Maintenance Date | Day 2 Actual Maintenance Date | Delay Day 1 | Delay Day 2 | Remark
1 | PWEPL-27 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-02 |  | 2023-10-05 |  | 3 |  | 11th Semi Annual Maintenance activity Completed
2 | PWEPL-17 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-03 |  | 2023-10-06 |  | 3 |  | 11th Semi Annual Maintenance activity Completed
3 | PWEPL-38 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-04 |  | 2023-10-07 |  | 3 |  | 11th Semi Annual Maintenance activity Completed
4 | PWEPL-09 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-05 |  | 2023-10-11 |  | 6 |  | 11th Semi Annual Maintenance activity Completed
5 | PWEPL-10 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-06 |  | 2023-10-12 |  | 6 |  | 11th Semi Annual Maintenance activity Completed
6 | PWEPL-11 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-07 |  | 2023-10-13 |  | 6 |  | 11th Semi Annual Maintenance activity Completed
7 | PWEPL-12 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-09 |  | 2023-10-14 |  | 5 |  | 11th Semi Annual Maintenance activity Completed
8 | PWEPL-13 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-10 |  | 2023-10-16 |  | 6 |  | 11th Semi Annual Maintenance activity Completed
9 | PWEPL-14 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-11 |  | 2023-10-17 |  | 6 |  | 11th Semi Annual Maintenance activity Completed
10 | PWEPL-15 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-12 |  | 2023-10-18 |  | 6 |  | 11th Semi Annual Maintenance activity Completed
11 | PWEPL-16 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-13 |  | 2023-10-19 |  | 6 |  | 11th Semi Annual Maintenance activity Completed
12 | PWEPL-19 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-14 |  | 2023-10-20 |  | 6 |  | 11th Semi Annual Maintenance activity Completed
13 | PWEPL-20 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-16 |  | 2023-10-21 |  | 5 |  | 11th Semi Annual Maintenance activity Completed
14 | PWEPL-28 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-17 |  | 2023-10-25 |  | 8 |  | 11th Semi Annual Maintenance activity Completed
15 | PWEPL-26 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-18 |  | 2023-10-26 |  | 8 |  | 11th Semi Annual Maintenance activity Completed
16 | PWEPL-25 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-19 |  | 2023-10-27 |  | 8 |  | 11th Semi Annual Maintenance activity Completed
17 | PWEPL-08 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-20 |  | 2023-10-28 |  | 8 |  | 11th Semi Annual Maintenance activity Completed
18 | PWEPL-43 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-21 |  | 2023-10-30 |  | 9 |  | 11th Semi Annual Maintenance activity Completed
19 | PWEPL-22 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-23 |  | 2023-10-31 |  | 8 |  | 11th Semi Annual Maintenance activity Completed
20 | PWEPL-23 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-24 |  | 2023-11-01 |  | 8 |  | 11th Semi Annual Maintenance activity Completed
21 | PWEPL-04 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-25 |  | 2023-11-02 |  | 8 |  | 11th Semi Annual Maintenance activity Completed
22 | PWEPL-34 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-26 |  | 2023-11-03 |  | 8 |  | 11th Semi Annual Maintenance activity Completed
23 | PWEPL-32 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-27 |  | 2023-11-04 |  | 8 |  | 11th Semi Annual Maintenance activity Completed
24 | PWEPL-37 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-28 |  | 2023-11-06 |  | 9 |  | 11th Semi Annual Maintenance activity Completed
25 | PWEPL-50 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-30 |  | 2023-11-07 |  | 8 |  | 11th Semi Annual Maintenance activity Completed
26 | PWEPL-51 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-31 |  | 2023-11-08 |  | 8 |  | 11th Semi Annual Maintenance activity Completed
27 | PWEPL-52 |  | 2024 | 2023 | 11 |  | SAM | 2023-11-01 |  | 2023-11-09 |  | 8 |  | 11th Semi Annual Maintenance activity Completed
28 | PWEPL-31 |  | 2024 | 2023 | 11 |  | SAM | 2023-11-02 |  | 2023-11-10 |  | 8 |  | 11th Semi Annual Maintenance activity Completed
29 | PWEPL-03 |  | 2024 | 2023 | 11 |  | SAM | 2023-11-03 |  | 2023-11-11 |  | 8 |  | 11th Semi Annual Maintenance activity Completed
30 | PWEPL-02 |  | 2024 | 2023 | 11 |  | SAM | 2023-11-04 |  | 2023-11-16 |  | 12 |  | 11th Semi Annual Maintenance activity Completed
31 | PWEPL-18 |  | 2024 | 2023 | 11 |  | SAM | 2023-11-06 |  | 2023-11-17 |  | 11 |  | 11th Semi Annual Maintenance activity Completed
32 | PWEPL-01 |  | 2024 | 2023 | 11 |  | SAM | 2023-11-07 |  | 2023-11-18 |  | 11 |  | 11th Semi Annual Maintenance activity Completed
33 | PWEPL-07 |  | 2024 | 2023 | 11 |  | SAM | 2023-11-08 |  | 2023-11-20 |  | 12 |  | 11th Semi Annual Maintenance activity Completed
34 | PWEPL-56 |  | 2024 | 2023 | 11 |  | SAM | 2023-11-09 |  | 2023-11-21 |  | 12 |  | 11th Semi Annual Maintenance activity Completed
35 | PWEPL-55 |  | 2024 | 2023 | 11 |  | SAM | 2023-11-10 |  | 2023-11-22 |  | 12 |  | 11th Semi Annual Maintenance activity Completed
36 | PWEPL-45 |  | 2024 | 2023 | 11 |  | SAM | 2023-11-11 |  | 2023-11-23 |  | 12 |  | 11th Semi Annual Maintenance activity Completed
37 | PWEPL-46 |  | 2024 | 2023 | 11 |  | SAM | 2023-11-20 |  | 2023-11-24 |  | 4 |  | 11th Semi Annual Maintenance activity Completed
38 | PWEPL-47 |  | 2024 | 2023 | 11 |  | SAM | 2023-11-21 |  | 2023-11-25 |  | 4 |  | 11th Semi Annual Maintenance activity Completed
39 | PWEPL-48 |  | 2024 | 2023 | 11 |  | SAM | 2023-11-22 |  | 2023-11-27 |  | 5 |  | 11th Semi Annual Maintenance activity Completed
40 | PWEPL-42 |  | 2024 | 2023 | 11 |  | SAM | 2023-11-23 |  | 2023-11-28 |  | 5 |  | 11th Semi Annual Maintenance activity Completed
41 | PWEPL-06 |  | 2024 | 2023 | 11 |  | SAM | 2023-11-24 |  | 2023-11-29 |  | 5 |  | 11th Semi Annual Maintenance activity Completed
42 | PWEPL-41 |  | 2024 | 2023 | 11 |  | SAM | 2023-11-25 |  | 2023-11-30 |  | 5 |  | 11th Semi Annual Maintenance activity Completed
43 | PWEPL-05 |  | 2024 | 2023 | 11 |  | SAM | 2023-11-27 |  | 2023-12-01 |  | 4 |  | 11th Semi Annual Maintenance activity Completed
44 | PWEPL-40 |  | 2024 | 2023 | 11 |  | SAM | 2023-11-28 |  | 2023-12-02 |  | 4 |  | 11th Semi Annual Maintenance activity Completed
1 | PWEPL-09 |  | 2024 | 2024 | 11 |  | AM | 2024-02-12 | 2024-02-13 | 2024-02-13 | 2024-02-19 | 1 | 6 | 11th Annual Maintenance activity Completed
2 | PWEPL-10 |  | 2024 | 2024 | 11 |  | AM | 2024-02-14 | 2024-02-15 | 2024-02-14 | 2024-02-20 | 0 | 5 | 11th Annual Maintenance activity Completed
3 | PWEPL-11 |  | 2024 | 2024 | 11 |  | AM | 2024-02-16 | 2024-02-17 | 2024-02-15 | 2024-02-22 | -1 | 5 | 11th Annual Maintenance activity Completed
4 | PWEPL-12 |  | 2024 | 2024 | 11 |  | AM | 2024-02-19 | 2024-02-20 | 2024-02-16 | 2024-02-23 | -3 | 3 | 11th Annual Maintenance activity Completed
5 | PWEPL-13 |  | 2024 | 2024 | 11 |  | AM | 2024-02-21 | 2024-02-22 | 2024-02-26 | 2024-02-29 | 5 | 7 | 11th Annual Maintenance activity Completed
6 | PWEPL-14 |  | 2024 | 2024 | 11 |  | AM | 2024-02-23 | 2024-02-24 | 2024-02-27 | 2024-03-01 | 4 | 6 | 11th Annual Maintenance activity Completed
7 | PWEPL-15 |  | 2024 | 2024 | 11 |  | AM | 2024-02-26 | 2024-02-27 | 2024-02-28 | 2024-03-08 | 2 | 10 | 11th Annual Maintenance activity Completed
8 | PWEPL-16 |  | 2024 | 2024 | 11 |  | AM | 2024-02-28 | 2024-02-29 | 2024-03-05 | 2024-03-05 | 6 | 5 | 11th Annual Maintenance activity Completed
9 | PWEPL-17 |  | 2024 | 2024 | 11 |  | AM | 2024-03-01 | 2024-03-02 | 2024-03-07 | 2024-03-07 | 6 | 5 | 11th Annual Maintenance activity Completed
10 | PWEPL-19 |  | 2024 | 2024 | 11 |  | AM | 2024-03-04 | 2024-03-05 | 2024-03-12 | 2024-03-12 | 8 | 7 | 11th Annual Maintenance activity Completed
11 | PWEPL-20 |  | 2024 | 2024 | 11 |  | AM | 2024-03-06 | 2024-03-07 | 2024-03-13 | 2024-03-15 | 7 | 8 | 11th Annual Maintenance activity Completed
12 | PWEPL-38 |  | 2024 | 2024 | 11 |  | AM | 2024-03-08 | 2024-03-09 | 2024-03-14 | 2024-03-14 | 6 | 5 | 11th Annual Maintenance activity Completed
13 | PWEPL-28 |  | 2024 | 2024 | 11 |  | AM | 2024-03-11 | 2024-03-12 | 2024-03-06 | 2024-03-06 | -5 | -6 | 11th Annual Maintenance activity Completed
14 | PWEPL-27 |  | 2024 | 2024 | 11 |  | AM | 2024-03-13 | 2024-03-14 | 2024-03-18 | 2024-03-21 | 5 | 7 | 11th Annual Maintenance activity Completed
15 | PWEPL-26 |  | 2024 | 2024 | 11 |  | AM | 2024-03-15 | 2024-03-16 | 2024-03-19 | 2024-03-23 | 4 | 7 | 11th Annual Maintenance activity Completed
16 | PWEPL-25 |  | 2024 | 2024 | 11 |  | AM | 2024-03-18 | 2024-03-19 | 2024-03-20 | 2024-03-26 | 2 | 7 | 11th Annual Maintenance activity Completed
17 | PWEPL-08 |  | 2024 | 2024 | 11 |  | AM | 2024-03-20 | 2024-03-21 | 2024-03-28 | 2024-03-29 | 8 | 8 | 11th Annual Maintenance activity Completed
18 | PWEPL-43 |  | 2024 | 2024 | 11 |  | AM | 2024-03-22 | 2024-03-23 | 2024-03-31 | 2024-04-01 | 9 | 9 | 11th Annual Maintenance activity Completed
19 | PWEPL-22 |  | 2024 | 2024 | 11 |  | AM | 2024-03-26 | 2024-03-27 | 2024-04-02 | 2024-04-03 | 7 | 7 | 11th Annual Maintenance activity Completed
20 | PWEPL-23 |  | 2024 | 2024 | 11 |  | AM | 2024-03-28 | 2024-03-29 | 2024-04-05 | 2024-04-06 | 8 | 8 | 11th Annual Maintenance activity Completed
21 | PWEPL-04 |  | 2024 | 2024 | 11 |  | AM | 2024-03-30 | 2024-04-01 | 2024-04-08 | 2024-04-09 | 9 | 8 | 11th Annual Maintenance activity Completed
22 | PWEPL-34 |  | 2024 | 2024 | 11 |  | AM | 2024-04-02 | 2024-04-03 | 2024-04-10 | 2024-04-11 | 8 | 8 | 11th Annual Maintenance activity Completed
23 | PWEPL-32 |  | 2024 | 2024 | 11 |  | AM | 2024-04-04 | 2024-04-05 | 2024-05-16 | 2024-05-17 | 42 | 42 | 11th Annual Maintenance activity Completed
24 | PWEPL-37 |  | 2024 | 2024 | 11 |  | AM | 2024-04-06 | 2024-04-08 | 2024-05-18 | 2024-05-18 | 42 | 40 | 11th Annual Maintenance activity Completed
25 | PWEPL-50 |  | 2024 | 2024 | 11 |  | AM | 2024-04-10 | 2024-04-11 | 2024-04-15 | 2024-04-15 | 5 | 4 | 11th Annual Maintenance activity Completed
26 | PWEPL-51 |  | 2024 | 2024 | 11 |  | AM | 2024-04-12 | 2024-04-13 | 2024-04-18 | 2024-04-18 | 6 | 5 | 11th Annual Maintenance activity Completed
27 | PWEPL-52 |  | 2024 | 2024 | 11 |  | AM | 2024-04-15 | 2024-04-16 | 2024-04-16 | 2024-04-16 | 1 | 0 | 11th Annual Maintenance activity Completed
28 | PWEPL-31 |  | 2024 | 2024 | 11 |  | AM | 2024-04-17 | 2024-04-18 | 2024-04-24 | 2024-04-24 | 7 | 6 | 11th Annual Maintenance activity Completed
29 | PWEPL-03 |  | 2024 | 2024 | 11 |  | AM | 2024-04-19 | 2024-04-20 | 2024-04-23 | 2024-04-23 | 4 | 3 | 11th Annual Maintenance activity Completed
30 | PWEPL-02 |  | 2024 | 2024 | 11 |  | AM | 2024-04-22 | 2024-04-23 | 2024-04-20 | 2024-04-20 | -2 | -3 | 11th Annual Maintenance activity Completed
31 | PWEPL-18 |  | 2024 | 2024 | 11 |  | AM | 2024-04-24 | 2024-04-25 | 2024-04-25 | 2024-04-25 | 1 | 0 | 11th Annual Maintenance activity Completed
32 | PWEPL-01 |  | 2024 | 2024 | 11 |  | AM | 2024-04-26 | 2024-04-27 | 2024-04-19 | 2024-04-19 | -7 | -8 | 11th Annual Maintenance activity Completed
33 | PWEPL-07 |  | 2024 | 2024 | 11 |  | AM | 2024-04-29 | 2024-04-30 | 2024-04-27 | 2024-04-27 | -2 | -3 | 11th Annual Maintenance activity Completed
34 | PWEPL-56 |  | 2024 | 2024 | 11 |  | AM | 2024-05-02 | 2024-05-03 | 2024-05-01 | 2024-05-01 | -1 | -2 | 11th Annual Maintenance activity Completed
35 | PWEPL-55 |  | 2024 | 2024 | 11 |  | AM | 2024-05-04 | 2024-05-06 | 2024-04-26 | 2024-04-26 | -8 | -10 | 11th Annual Maintenance activity Completed
36 | PWEPL-45 |  | 2024 | 2024 | 11 |  | AM | 2024-05-07 | 2024-05-08 | 2024-05-02 | 2024-05-03 | -5 | -5 | 11th Annual Maintenance activity Completed
37 | PWEPL-46 |  | 2024 | 2024 | 11 |  | AM | 2024-05-09 | 2024-05-10 | 2024-05-04 | 2024-05-04 | -5 | -6 | 11th Annual Maintenance activity Completed
38 | PWEPL-47 |  | 2024 | 2024 | 11 |  | AM | 2024-05-11 | 2024-05-13 | 2024-05-15 | 2024-05-15 | 4 | 2 | 11th Annual Maintenance activity Completed
39 | PWEPL-48 |  | 2024 | 2024 | 11 |  | AM | 2024-05-14 | 2024-05-15 | 2024-05-05 | 2024-05-05 | -9 | -10 | 11th Annual Maintenance activity Completed
40 | PWEPL-42 |  | 2024 | 2024 | 11 |  | AM | 2024-05-16 | 2024-05-17 | 2024-05-06 | 2024-05-06 | -10 | -11 | 11th Annual Maintenance activity Completed
41 | PWEPL-06 |  | 2024 | 2024 | 11 |  | AM | 2024-05-18 | 2024-05-20 | 2024-05-07 | 2024-05-07 | -11 | -13 | 11th Annual Maintenance activity Completed
42 | PWEPL-41 |  | 2024 | 2024 | 11 |  | AM | 2024-05-21 | 2024-05-22 | 2024-05-08 | 2024-05-08 | -13 | -14 | 11th Annual Maintenance activity Completed
43 | PWEPL-05 |  | 2024 | 2024 | 11 |  | AM | 2024-05-23 | 2024-05-24 | 2024-05-09 | 2024-05-09 | -14 | -15 | 11th Annual Maintenance activity Completed
44 | PWEPL-40 |  | 2024 | 2024 | 11 |  | AM | 2024-05-25 | 2024-05-27 | 2024-05-14 | 2024-05-14 | -11 | -13 | 11th Annual Maintenance activity Completed
1 | PWEPL-09 |  | 2024 | 2024 | 12 |  | SAM | 2024-10-03 |  | 2024-10-03 |  | 0 |  | 12th Semi Annual Maintenance activity Completed
2 | PWEPL-10 |  | 2024 | 2024 | 12 |  | SAM | 2024-10-04 |  | 2024-10-04 |  | 0 |  | 12th Semi Annual Maintenance activity Completed
3 | PWEPL-11 |  | 2024 | 2024 | 12 |  | SAM | 2024-10-07 |  | 2024-10-07 |  | 0 |  | 12th Semi Annual Maintenance activity Completed
4 | PWEPL-12 |  | 2024 | 2024 | 12 |  | SAM | 2024-10-08 |  | 2024-10-08 |  | 0 |  | 12th Semi Annual Maintenance activity Completed
5 | PWEPL-13 |  | 2024 | 2024 | 12 |  | SAM | 2024-10-09 |  | 2024-10-09 |  | 0 |  | 12th Semi Annual Maintenance activity Completed
6 | PWEPL-14 |  | 2024 | 2024 | 12 |  | SAM | 2024-10-10 |  | 2024-10-10 |  | 0 |  | 12th Semi Annual Maintenance activity Completed
7 | PWEPL-15 |  | 2024 | 2024 | 12 |  | SAM | 2024-10-11 |  | 2024-10-14 |  | 3 |  | 12th Semi Annual Maintenance activity Completed
8 | PWEPL-16 |  | 2024 | 2024 | 12 |  | SAM | 2024-10-14 |  | 2024-10-15 |  | 1 |  | 12th Semi Annual Maintenance activity Completed
9 | PWEPL-17 |  | 2024 | 2024 | 12 |  | SAM | 2024-10-15 |  | 2024-10-16 |  | 1 |  | 12th Semi Annual Maintenance activity Completed
10 | PWEPL-38 |  | 2024 | 2024 | 12 |  | SAM | 2024-10-16 |  | 2024-10-17 |  | 1 |  | 12th Semi Annual Maintenance activity Completed
11 | PWEPL-20 |  | 2024 | 2024 | 12 |  | SAM | 2024-10-17 |  | 2024-10-18 |  | 1 |  | 12th Semi Annual Maintenance activity Completed
12 | PWEPL-19 |  | 2024 | 2024 | 12 |  | SAM | 2024-10-18 |  | 2024-10-21 |  | 3 |  | 12th Semi Annual Maintenance activity Completed
13 | PWEPL-27 |  | 2024 | 2024 | 12 |  | SAM | 2024-10-21 |  | 2024-10-22 |  | 1 |  | 12th Semi Annual Maintenance activity Completed
14 | PWEPL-28 |  | 2024 | 2024 | 12 |  | SAM | 2024-10-22 |  | 2024-10-23 |  | 1 |  | 12th Semi Annual Maintenance activity Completed
15 | PWEPL-26 |  | 2024 | 2024 | 12 |  | SAM | 2024-10-23 |  | 2024-10-24 |  | 1 |  | 12th Semi Annual Maintenance activity Completed
16 | PWEPL-25 |  | 2024 | 2024 | 12 |  | SAM | 2024-10-24 |  | 2024-10-25 |  | 1 |  | 12th Semi Annual Maintenance activity Completed
17 | PWEPL-08 |  | 2024 | 2024 | 12 |  | SAM | 2024-10-25 |  | 2024-10-26 |  | 1 |  | 12th Semi Annual Maintenance activity Completed
18 | PWEPL-43 |  | 2024 | 2024 | 12 |  | SAM | 2024-11-03 |  | 2024-10-27 |  | -7 |  | 12th Semi Annual Maintenance activity Completed
19 | PWEPL-22 |  | 2024 | 2024 | 12 |  | SAM | 2024-11-04 |  | 2024-10-28 |  | -7 |  | 12th Semi Annual Maintenance activity Completed
20 | PWEPL-23 |  | 2024 | 2024 | 12 |  | SAM | 2024-11-05 |  | 2024-10-29 |  | -7 |  | 12th Semi Annual Maintenance activity Completed
21 | PWEPL-04 |  | 2024 | 2024 | 12 |  | SAM | 2024-11-10 |  | 2024-10-30 |  | -11 |  | 12th Semi Annual Maintenance activity Completed
22 | PWEPL-34 |  | 2024 | 2024 | 12 |  | SAM | 2024-11-06 |  | 2024-11-07 |  | 1 |  | 12th Semi Annual Maintenance activity Completed
23 | PWEPL-32 |  | 2024 | 2024 | 12 |  | SAM | 2024-11-11 |  | 2024-11-08 |  | -3 |  | 12th Semi Annual Maintenance activity Completed
24 | PWEPL-37 |  | 2024 | 2024 | 12 |  | SAM | 2024-11-12 |  | 2024-11-09 |  | -3 |  | 12th Semi Annual Maintenance activity Completed
25 | PWEPL-50 |  | 2024 | 2024 | 12 |  | SAM | 2024-11-13 |  | 2024-11-11 |  | -2 |  | 12th Semi Annual Maintenance activity Completed
26 | PWEPL-51 |  | 2024 | 2024 | 12 |  | SAM | 2024-11-14 |  | 2024-11-12 |  | -2 |  | 12th Semi Annual Maintenance activity Completed
27 | PWEPL-52 |  | 2024 | 2024 | 12 |  | SAM | 2024-11-17 |  | 2024-11-14 |  | -3 |  | 12th Semi Annual Maintenance activity Completed
28 | PWEPL-31 |  | 2024 | 2024 | 12 |  | SAM | 2024-11-18 |  | 2024-11-15 |  | -3 |  | 12th Semi Annual Maintenance activity Completed
29 | PWEPL-03 |  | 2024 | 2024 | 12 |  | SAM | 2024-11-19 |  | 2024-11-18 |  | -1 |  | 12th Semi Annual Maintenance activity Completed
30 | PWEPL-02 |  | 2024 | 2024 | 12 |  | SAM | 2024-11-20 |  | 2024-11-19 |  | -1 |  | 12th Semi Annual Maintenance activity Completed
31 | PWEPL-18 |  | 2024 | 2024 | 12 |  | SAM | 2024-11-21 |  | 2024-11-21 |  | 0 |  | 12th Semi Annual Maintenance activity Completed
32 | PWEPL-01 |  | 2024 | 2024 | 12 |  | SAM | 2024-11-24 |  | 2024-11-22 |  | -2 |  | 12th Semi Annual Maintenance activity Completed
33 | PWEPL-07 |  | 2024 | 2024 | 12 |  | SAM | 2024-11-25 |  | 2024-11-25 |  | 0 |  | 12th Semi Annual Maintenance activity Completed
34 | PWEPL-56 |  | 2024 | 2024 | 12 |  | SAM | 2024-11-26 |  | 2024-11-27 |  | 1 |  | 12th Semi Annual Maintenance activity Completed
35 | PWEPL-55 |  | 2024 | 2024 | 12 |  | SAM | 2024-11-27 |  | 2024-11-28 |  | 1 |  | 12th Semi Annual Maintenance activity Completed
36 | PWEPL-45 |  | 2024 | 2024 | 12 |  | SAM | 2024-11-28 |  | 2024-11-30 |  | 2 |  | 12th Semi Annual Maintenance activity Completed
37 | PWEPL-46 |  | 2024 | 2024 | 12 |  | SAM | 2024-12-01 |  | 2024-12-02 |  | 1 |  | 12th Semi Annual Maintenance activity Completed
38 | PWEPL-47 |  | 2024 | 2024 | 12 |  | SAM | 2024-12-02 |  | 2024-12-04 |  | 2 |  | 12th Semi Annual Maintenance activity Completed
39 | PWEPL-48 |  | 2024 | 2024 | 12 |  | SAM | 2024-12-03 |  | 2024-12-05 |  | 2 |  | 12th Semi Annual Maintenance activity Completed
40 | PWEPL-42 |  | 2024 | 2024 | 12 |  | SAM | 2024-12-04 |  | 2024-12-06 |  | 2 |  | 12th Semi Annual Maintenance activity Completed
41 | PWEPL-06 |  | 2024 | 2024 | 12 |  | SAM | 2024-12-05 |  | 2024-12-07 |  | 2 |  | 12th Semi Annual Maintenance activity Completed
42 | PWEPL-41 |  | 2024 | 2024 | 12 |  | SAM | 2024-12-08 |  | 2024-12-09 |  | 1 |  | 12th Semi Annual Maintenance activity Completed
43 | PWEPL-05 |  | 2024 | 2024 | 12 |  | SAM | 2024-12-09 |  | 2024-12-10 |  | 1 |  | 12th Semi Annual Maintenance activity Completed
44 | PWEPL-40 |  | 2024 | 2024 | 12 |  | SAM | 2024-12-10 |  | 2024-12-11 |  | 1 |  | 12th Semi Annual Maintenance activity Completed
1 | PWEPL-09 |  | 2025 | 2025 | 12 |  | AM | 2025-02-03 | 2025-02-04 | 2025-02-04 | 2025-02-11 | 1 | 7 | 12th Annual Maintenance activity Completed
2 | PWEPL-10 |  | 2025 | 2025 | 12 |  | AM | 2025-02-05 | 2025-02-06 | 2025-02-05 | 2025-02-12 | 0 | 6 | 12th Annual Maintenance activity Completed
3 | PWEPL-11 |  | 2025 | 2025 | 12 |  | AM | 2025-02-07 | 2025-02-08 | 2025-02-06 | 2025-02-13 | -1 | 5 | 12th Annual Maintenance activity Completed
4 | PWEPL-12 |  | 2025 | 2025 | 12 |  | AM | 2025-02-10 | 2025-02-11 | 2025-02-07 | 2025-02-14 | -3 | 3 | 12th Annual Maintenance activity Completed
5 | PWEPL-13 |  | 2025 | 2025 | 12 |  | AM | 2025-02-12 | 2025-02-13 | 2025-02-08 | 2025-02-17 | -4 | 4 | 12th Annual Maintenance activity Completed
6 | PWEPL-14 |  | 2025 | 2025 | 12 |  | AM | 2025-02-14 | 2025-02-15 | 2025-02-10 | 2025-02-18 | -4 | 3 | 12th Annual Maintenance activity Completed
7 | PWEPL-15 |  | 2025 | 2025 | 12 |  | AM | 2025-02-17 | 2025-02-18 | 2025-02-19 | 2025-02-20 | 2 | 2 | 12th Annual Maintenance activity Completed
8 | PWEPL-16 |  | 2025 | 2025 | 12 |  | AM | 2025-02-19 | 2025-02-20 | 2025-02-24 | 2025-02-25 | 5 | 5 | 12th Annual Maintenance activity Completed
9 | PWEPL-17 |  | 2025 | 2025 | 12 |  | AM | 2025-02-21 | 2025-02-22 | 2025-02-26 | 2025-02-27 | 5 | 5 | 12th Annual Maintenance activity Completed
10 | PWEPL-19 |  | 2025 | 2025 | 12 |  | AM | 2025-02-24 | 2025-02-25 | 2025-03-03 | 2025-03-03 | 7 | 6 | 12th Annual Maintenance activity Completed
11 | PWEPL-20 |  | 2025 | 2025 | 12 |  | AM | 2025-02-26 | 2025-02-27 | 2025-03-01 | 2025-03-02 | 3 | 3 | 12th Annual Maintenance activity Completed
12 | PWEPL-38 |  | 2025 | 2025 | 12 |  | AM | 2025-02-28 | 2025-03-01 | 2025-02-28 | 2025-03-02 | 0 | 1 | 12th Annual Maintenance activity Completed
13 | PWEPL-28 |  | 2025 | 2025 | 12 |  | AM | 2025-03-03 | 2025-03-04 | 2025-02-21 | 2025-02-22 | -10 | -10 | 12th Annual Maintenance activity Completed
14 | PWEPL-27 |  | 2025 | 2025 | 12 |  | AM | 2025-03-05 | 2025-03-06 | 2025-03-04 | 2025-03-05 | -1 | -1 | 12th Annual Maintenance activity Completed
15 | PWEPL-26 |  | 2025 | 2025 | 12 |  | AM | 2025-03-07 | 2025-03-08 | 2025-03-06 | 2025-03-07 | -1 | -1 | 12th Annual Maintenance activity Completed
16 | PWEPL-25 |  | 2025 | 2025 | 12 |  | AM | 2025-03-10 | 2025-03-11 | 2025-03-08 | 2025-03-08 | -2 | -3 | 12th Annual Maintenance activity Completed
17 | PWEPL-08 |  | 2025 | 2025 | 12 |  | AM | 2025-03-12 | 2025-03-13 | 2025-03-10 | 2025-03-12 | -2 | -1 | 12th Annual Maintenance activity Completed
18 | PWEPL-43 |  | 2025 | 2025 | 12 |  | AM | 2025-03-14 | 2025-03-15 | 2025-03-17 | 2025-03-18 | 3 | 3 | 12th Annual Maintenance activity Completed
19 | PWEPL-22 |  | 2025 | 2025 | 12 |  | AM | 2025-03-17 | 2025-03-18 | 2025-03-13 | 2025-03-15 | -4 | -3 | 12th Annual Maintenance activity Completed
20 | PWEPL-23 |  | 2025 | 2025 | 12 |  | AM | 2025-03-19 | 2025-03-20 | 2025-03-19 | 2025-03-20 | 0 | 0 | 12th Annual Maintenance activity Completed
21 | PWEPL-04 |  | 2025 | 2025 | 12 |  | AM | 2025-03-21 | 2025-03-22 | 2025-03-21 | 2025-03-22 | 0 | 0 | 12th Annual Maintenance activity Completed
22 | PWEPL-34 |  | 2025 | 2025 | 12 |  | AM | 2025-03-24 | 2025-03-25 | 2025-03-24 | 2025-03-24 | 0 | -1 | 12th Annual Maintenance activity Completed
23 | PWEPL-32 |  | 2025 | 2025 | 12 |  | AM | 2025-03-26 | 2025-03-27 | 2025-03-25 | 2025-03-25 | -1 | -2 | 12th Annual Maintenance activity Completed
24 | PWEPL-37 |  | 2025 | 2025 | 12 |  | AM | 2025-03-28 | 2025-03-29 | 2025-03-26 | 2025-03-26 | -2 | -3 | 12th Annual Maintenance activity Completed
25 | PWEPL-50 |  | 2025 | 2025 | 12 |  | AM | 2025-03-31 | 2025-04-01 | 2025-03-27 | 2025-03-28 | -4 | -4 | 12th Annual Maintenance activity Completed
26 | PWEPL-51 |  | 2025 | 2025 | 12 |  | AM | 2025-04-02 | 2025-04-03 | 2025-03-29 | 2025-03-29 | -4 | -5 | 12th Annual Maintenance activity Completed
27 | PWEPL-52 |  | 2025 | 2025 | 12 |  | AM | 2025-04-04 | 2025-04-05 | 2025-03-31 | 2025-03-31 | -4 | -5 | 12th Annual Maintenance activity Completed
28 | PWEPL-31 |  | 2025 | 2025 | 12 |  | AM | 2025-04-07 | 2025-04-08 | 2025-04-03 | 2025-04-05 | -4 | -3 | 12th Annual Maintenance activity Completed
29 | PWEPL-03 |  | 2025 | 2025 | 12 |  | AM | 2025-04-09 | 2025-04-10 | 2025-04-07 | 2025-04-07 | -2 | -3 | 12th Annual Maintenance activity Completed
30 | PWEPL-02 |  | 2025 | 2025 | 12 |  | AM | 2025-04-11 | 2025-04-12 | 2025-04-08 | 2025-04-12 | -3 | 0 | 12th Annual Maintenance activity Completed
31 | PWEPL-18 |  | 2025 | 2025 | 12 |  | AM | 2025-04-14 | 2025-04-15 | 2025-04-09 | 2025-04-09 | -5 | -6 | 12th Annual Maintenance activity Completed
32 | PWEPL-01 |  | 2025 | 2025 | 12 |  | AM | 2025-04-16 | 2025-04-17 | 2025-04-10 | 2025-04-10 | -6 | -7 | 12th Annual Maintenance activity Completed
33 | PWEPL-07 |  | 2025 | 2025 | 12 |  | AM | 2025-04-18 | 2025-04-19 | 2025-04-11 | 2025-04-30 | -7 | 11 | 12th Annual Maintenance activity Completed
34 | PWEPL-56 |  | 2025 | 2025 | 12 |  | AM | 2025-04-21 | 2025-04-22 | 2025-04-15 | 2025-04-16 | -6 | -6 | 12th Annual Maintenance activity Completed
35 | PWEPL-55 |  | 2025 | 2025 | 12 |  | AM | 2025-04-23 | 2025-04-24 | 2025-04-17 | 2025-04-30 | -6 | 6 | 12th Annual Maintenance activity Completed
36 | PWEPL-45 |  | 2025 | 2025 | 12 |  | AM | 2025-04-25 | 2025-04-26 | 2025-04-18 | 2025-04-30 | -7 | 4 | 12th Annual Maintenance activity Completed
37 | PWEPL-46 |  | 2025 | 2025 | 12 |  | AM | 2025-04-28 | 2025-04-29 | 2025-04-19 | 2025-04-30 | -9 | 1 | 12th Annual Maintenance activity Completed
38 | PWEPL-47 |  | 2025 | 2025 | 12 |  | AM | 2025-04-30 | 2025-05-02 | 2025-04-23 | 2025-05-01 | -7 | -1 | 12th Annual Maintenance activity Completed
39 | PWEPL-48 |  | 2025 | 2025 | 12 |  | AM | 2025-05-03 | 2025-05-05 | 2025-04-24 | 2025-05-01 | -9 | -4 | 12th Annual Maintenance activity Completed
40 | PWEPL-42 |  | 2025 | 2025 | 12 |  | AM | 2025-05-06 | 2025-05-07 | 2025-04-25 | 2025-05-01 | -11 | -6 | 12th Annual Maintenance activity Completed
41 | PWEPL-06 |  | 2025 | 2025 | 12 |  | AM | 2025-05-08 | 2025-05-09 | 2025-04-26 | 2025-05-02 | -12 | -8 | 12th Annual Maintenance activity Completed
42 | PWEPL-41 |  | 2025 | 2025 | 12 |  | AM | 2025-05-12 | 2025-05-13 | 2025-04-27 | 2025-05-02 | -15 | -16 | 12th Annual Maintenance activity Completed
43 | PWEPL-05 |  | 2025 | 2025 | 12 |  | AM | 2025-05-14 | 2025-05-15 | 2025-04-28 | 2025-05-02 | -16 | -17 | 12th Annual Maintenance activity Completed
44 | PWEPL-40 |  | 2025 | 2025 | 12 |  | AM | 2025-05-16 | 2025-05-17 | 2025-04-29 | 2025-05-02 | -17 | -18 | 12th Annual Maintenance activity Completed

## WTG Reactive Power
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49
Date | Financial Year | Calendar Year | Month Year | P-01 | P-02 | P-03 | P-04 | P-05 | P-06 | P-07 | P-08 | P-09 | P-10 | P-11 | P-12 | P-13 | P-14 | P-15 | P-16 | P-17 | P-18 | P-19 | P-20 | P-22 | P-23 | P-25 | P-26 | P-27 | P-28 | P-31 | P-32 | P-34 | P-37 | P-38 | P-40 | P-41 | P-42 | P-43 | P-45 | P-46 | P-47 | P-48 | P-50 | P-51 | P-52 | P-55 | P-56 | Total Reactive Power (kVArH)
2025-03-29 | 2025 | 2025 | 2025-03-01 | [44 empty] | 0
2025-03-30 | 2025 | 2025 | 2025-03-01 | [44 empty] | 0
2025-03-31 | 2025 | 2025 | 2025-04-01 | [44 empty] | 0
2025-04-01 | 2026 | 2025 | 2025-04-01 | 721.7855 | 706.556 | 649.4168 | 1211.4642 | 927.1955 | 923.1035 | 457.2925 | 847.4782 | 717.8808 | 1008.006 | 1258.9807 | 1222.2958 | 1134.9852 | 1084.4103 | 898.1967 | 845.6648 | 759.9462 | 547.7623 | 994.5882 | 832.4698 | 1290.2067 | 1277.826 | 1090.8723 | 1058.623 | 592.3165 | 982.1397 | 599.5368 | 424.3102 | 1014.0687 | 450.91 | 926.223 | 672.3055 | 890.8138 | 769.964 | 1258.6622 | 1286.8588 | 906.5793 | 699.6832 | 802.4002 | 384.6693 | 475.28 | 544.0825 | 639.4147 | 531.5318 | 37.3188
2025-04-02 | 2026 | 2025 | 2025-04-01 | 1279.0202 | 1000.0012 | 826.3672 | 974.136 | 2179.488 | 1830.5527 | 1022.2077 | 940.6755 | 648.2487 | 1004.6227 | 1201.2533 | 1484.9563 | 1740.974 | 1764.889 | 1291.6612 | 1538.5458 | 1692.3157 | 1164.2563 | 2025.9788 | 1739.0328 | 949.6493 | 981.2805 | 1364.3895 | 1696.8098 | 1684.1342 | 1635.549 | 861.6737 | 1131.5123 | 711.7767 | 1502.0345 | 1956.7857 | 1168.4542 | 2110.2432 | 1617.4118 | 1506.7738 | 2441.3997 | 1560.4152 | 1820.044 | 1734.4628 | 1280.416 | 1536.9065 | 1486.0708 | 1869.9907 | 1636.3545 | 63.5937
2025-04-03 | 2026 | 2025 | 2025-04-01 | 554.4818 | 496.6758 | 503.4407 | 503.5803 | 461.6213 | 345.3613 | 403.0327 | 207.971 | 150.5168 | 181.7885 | 187.0547 | 200.022 | 200.4837 | 104.6352 | 108.9352 | 136.3832 | 171.5277 | 501.6038 | 188.559 | 155.3565 | 442.681 | 479.5362 | 261.4628 | 302.9595 | 332.9407 | 295.0062 | 258.4425 | 254.4163 | 508.0893 | 337.8037 | 211.6938 | 294.4058 | 416.0837 | 507.034 | 280.368 | 575.4567 | 529.6665 | 474.1397 | 516.1133 | 208.4443 | 343.6465 | 340.8348 | 540.7648 | 489.9962 | 14.965
2025-04-04 | 2026 | 2025 | 2025-04-01 | 489.2198 | 529.7375 | 586.2853 | 564.4553 | 625.9117 | 482.957 | 493.733 | 420.319 | 304.201 | 337.3478 | 339.1455 | 342.3332 | 405.7633 | 248.7777 | 127.5992 | 165.7818 | 220.4193 | 603.6432 | 226.8388 | 168.4955 | 568.778 | 634.6315 | 525.7253 | 483.5422 | 568.7925 | 523.5513 | 651.1248 | 412.3463 | 520.4463 | 601.5575 | 226.2915 | 285.0857 | 566.729 | 526.5558 | 529.306 | 875.848 | 732.8268 | 601.3043 | 561.9275 | 282.435 | 496.273 | 574.691 | 638.1777 | 607.9772 | 20.6789
2025-04-05 | 2026 | 2025 | 2025-04-01 | 81.5366 | 88.2896 | 97.7142 | 94.0759 | 104.3186 | 80.4928 | 82.2888 | 70.0532 | 50.7002 | 56.2246 | 56.5243 | 57.0555 | 67.6272 | 41.4629 | 21.2665 | 27.6303 | 36.7366 | 100.6072 | 37.8065 | 28.0826 | 94.7963 | 105.7719 | 87.6209 | 80.5904 | 94.7987 | 87.2586 | 108.5208 | 68.7244 | 86.7411 | 100.2596 | 37.7152 | 47.5143 | 94.4548 | 87.7593 | 88.2177 | 145.9747 | 122.1378 | 100.2174 | 93.6546 | 47.0725 | 82.7122 | 95.7818 | 106.3629 | 101.3295 | 3.4465
2025-04-06 | 2026 | 2025 | 2025-04-01 | 13.5894 | 14.7149 | 16.2857 | 15.6793 | 17.3864 | 13.4155 | 13.7148 | 11.6755 | 8.45 | 9.3708 | 9.4207 | 9.5093 | 11.2712 | 6.9105 | 3.5444 | 4.6051 | 6.1228 | 16.7679 | 6.3011 | 4.6804 | 15.7994 | 17.6287 | 14.6035 | 13.4317 | 15.7998 | 14.5431 | 18.0868 | 11.4541 | 14.4568 | 16.7099 | 6.2859 | 7.919 | 15.7425 | 14.6266 | 14.7029 | 24.3291 | 20.3563 | 16.7029 | 15.6091 | 7.8454 | 13.7854 | 15.9636 | 17.7272 | 16.8883 | 0.57441
2025-04-07 | 2026 | 2025 | 2025-04-01 | 766.1405 | 953.848 | 977.1735 | 218.835 | 402.0165 | 71.0122 | 604.976 | 210.8173 | 141.7167 | 174.9242 | 186.0918 | 246.5557 | 260.5342 | 296.4995 | 275.0082 | 312.4618 | 322.5043 | 792.7053 | 383.831 | 333.2443 | 639.3802 | 759.6718 | 376.4815 | 391.3165 | 447.5158 | 418.6393 | 1054.543 | 442.2398 | 651.2677 | 600.4277 | 346.387 | 90.3937 | 89.7267 | 177.1713 | 437.7782 | 159.2613 | 154.8428 | 141.25 | 134.819 | 511.1667 | 768.8697 | 804.645 | 819.6978 | 661.0078 | 19.0094
2025-04-08 | 2026 | 2025 | 2025-04-01 | 322.8392 | 282.5615 | 252.7505 | 166.8033 | 257.2093 | 246.5115 | 265.0405 | 123.1237 | 67.9717 | 70.8108 | 76.4518 | 98.8395 | 112.1115 | 103.0065 | 76.2238 | 78.0282 | 96.8097 | 267.808 | 148.2382 | 104.9922 | 228.0207 | 243.1193 | 164.6447 | 150.2137 | 183.5645 | 187.9168 | 132.58 | 77.8038 | 116.6928 | 184.8913 | 99.639 | 161.6448 | 336.349 | 255.3023 | 147.0575 | 329.405 | 242.273 | 196.0913 | 234.4248 | 79.8872 | 143.5565 | 193.2657 | 393.9905 | 279.1617 | 7.9796
2025-04-09 | 2026 | 2025 | 2025-04-01 | 849.8133 | 757.3283 | 541.2778 | 580.889 | 604.3397 | 594.166 | 774.0387 | 311.0168 | 198.2693 | 243.0448 | 297.5775 | 330.3118 | 350.6927 | 375.0405 | 349.0463 | 423.0813 | 449.911 | 432.8312 | 448.4453 | 405.452 | 557.9507 | 439.6465 | 333.3012 | 417.1175 | 413.441 | 417.847 | 443.9377 | 322.2847 | 606.307 | 417.1 | 453.239 | 418.2953 | 210.5095 | 615.0903 | 383.0875 | 636.4005 | 360.6735 | 419.14 | 374.594 | 411.0922 | 438.6935 | 458.0137 | 801.5085 | 850.621 | 20.5165
2025-04-10 | 2026 | 2025 | 2025-04-01 | 2114.2597 | 2469.9707 | 1278.5827 | 1552.1752 | 1427.267 | 1568.134 | 2346.9182 | 728.8465 | 402.8562 | 420.008 | 566.8998 | 723.704 | 929.5363 | 888.341 | 867.8032 | 904.208 | 996.6408 | 1871.2138 | 1019.6708 | 845.1308 | 1368.2078 | 1056.7385 | 755.3748 | 867.1655 | 879.7385 | 821.7757 | 851.9553 | 271.6058 | 1519.342 | 392.4403 | 960.6945 | 859.5238 | 1392.5213 | 1716.1448 | 730.8452 | 1851.0557 | 1830.6425 | 1329.832 | 1792.784 | 527.9238 | 565.9292 | 627.124 | 2215.041 | 2454.979 | 51.5616
2025-04-11 | 2026 | 2025 | 2025-04-01 | 1608.4338 | 1381.5393 | 1246.4048 | 1233.9242 | 1655.1192 | 1243.6768 | 874.8345 | 713.3523 | 510.9652 | 649.7318 | 750.9972 | 898.927 | 895.5882 | 908.6788 | 877.1323 | 1011.4342 | 1175.6393 | 1520.1668 | 1085.9738 | 949.4033 | 1250.7088 | 1258.6677 | 974.6503 | 1072.6845 | 1146.301 | 1054.384 | 989.6468 | 93.6302 | 1050.2753 | 156.0095 | 1266.753 | 816.2688 | 1571.87 | 1707.7953 | 920.553 | 1421.6427 | 1500.4217 | 1326.6895 | 1558.4938 | 599.0033 | 619.6803 | 712.9038 | 1282.2733 | 1461.9598 | 47.0052
2025-04-12 | 2026 | 2025 | 2025-04-01 | 1891.5332 | 1542.1888 | 1482.765 | 1458.7167 | 1396.8868 | 1039.9977 | 1479.2027 | 735.7097 | 529.0943 | 683.7618 | 809.7427 | 949.3212 | 969.2393 | 1048.0093 | 985.904 | 1226.3092 | 1386.881 | 1621.3808 | 1232.396 | 1066.126 | 1366.1548 | 1616.0542 | 990.9915 | 1091.9385 | 1276.1627 | 1244.5188 | 1147.5052 | 634.194 | 1342.5977 | 807.2152 | 1470.8357 | 797.0488 | 1292.2252 | 1654.4412 | 1175.968 | 2121.3305 | 2039.9872 | 1705.4485 | 1645.064 | 635.0845 | 482.0728 | 971.9917 | 1909.6392 | 1559.7473 | 54.5134
2025-04-13 | 2026 | 2025 | 2025-04-01 | 2080.7448 | 1721.4688 | 1831.614 | 1113.559 | 1107.5483 | 921.0442 | 1962.5255 | 387.7745 | 271.2782 | 304.4303 | 367.9083 | 434.9452 | 410.4843 | 444.565 | 398.7813 | 464.851 | 591.967 | 1817.9848 | 578.6202 | 591.2592 | 1585.4322 | 1704.2888 | 768.7523 | 792.3302 | 952.3043 | 767.52 | 1393.5975 | 763.9332 | 1085.2165 | 1107.2802 | 684.7227 | 408.2552 | 1046.9242 | 1612.7378 | 773.671 | 1569.5888 | 1224.4425 | 1229.485 | 1290.5342 | 641.3092 | 1128.9767 | 1597.8045 | 2266.8295 | 1681.5147 | 45.8808
2025-04-14 | 2026 | 2025 | 2025-04-01 | 1760.998 | 2114.2968 | 2290.731 | 1070.9975 | 1129.1787 | 1090.5463 | 1294.9527 | 658.2933 | 467.1207 | 488.0563 | 525.349 | 581.9282 | 573.2733 | 490.7425 | 416.1177 | 506.4842 | 592.0163 | 1513.3087 | 511.0275 | 412.007 | 1051.1225 | 1189.4933 | 743.9377 | 713.4633 | 856.7233 | 759.0162 | 2129.8542 | 1034.7615 | 1207.254 | 1279.665 | 584.9233 | 675.7923 | 1113.8685 | 1264.3828 | 755.8178 | 1596.1132 | 1459.4208 | 1136.8318 | 1247.9865 | 1124.5065 | 1487.9262 | 1738.2153 | 1553.4983 | 1229.1473 | 46.4211
2025-04-15 | 2026 | 2025 | 2025-04-01 | 1164.4358 | 1117.97 | 1274.8743 | 414.202 | 687.504 | 602.9888 | 883.9807 | 179.564 | 94.9353 | 75.0628 | 74.1143 | 102.2182 | 119.6953 | 143.6773 | 124.1687 | 168.47 | 236.981 | 761.9668 | 125.4875 | 98.1012 | 694.7813 | 868.648 | 264.8942 | 273.4003 | 364.5635 | 321.4822 | 1023.286 | 551.3152 | 377.9115 | 599.6252 | 197.0737 | 264.8218 | 696.5588 | 781.5178 | 281.5758 | 664.6138 | 526.2702 | 555.97 | 537.1208 | 1017.6382 | 891.6502 | 1041.3667 | 957.715 | 627.8675 | 22.8321
2025-04-16 | 2026 | 2025 | 2025-04-01 | 435.7065 | 290.2683 | 253.6542 | 379.8172 | 432.5345 | 295.5975 | 382.8972 | 167.4968 | 118.3662 | 196.0182 | 225.8325 | 266.0245 | 288.2907 | 269.2752 | 245.527 | 269.7627 | 341.9405 | 402.4802 | 284.9163 | 270.4168 | 346.2877 | 317.9907 | 231.19 | 279.3553 | 310.8142 | 313.2643 | 158.141 | 132.7457 | 353.7523 | 162.1092 | 343.414 | 193.4893 | 383.5737 | 448.8047 | 253.7585 | 249.5773 | 323.2482 | 327.5302 | 387.5435 | 191.9708 | 190.2013 | 242.3032 | 377.0317 | 194.2082 | 12.5291
2025-04-17 | 2026 | 2025 | 2025-04-01 | 1972.8162 | 1498.9122 | 1482.4532 | 1133.7433 | 1727.8893 | 1778.6953 | 1717.9773 | 616.2722 | 448.183 | 546.5468 | 563.8882 | 592.9608 | 618.525 | 638.4598 | 537.7372 | 644.345 | 710.5653 | 1677.4428 | 703.9098 | 612.0318 | 1350.4222 | 1502.7798 | 967.427 | 941.8353 | 1152.2888 | 1002.564 | 1215.1803 | 723.436 | 1118.2323 | 1122.337 | 694.6005 | 726.9845 | 1867.0477 | 2293.482 | 880.6715 | 1905.7312 | 2019.7993 | 1997.4907 | 2016.6897 | 733.5103 | 1206.4843 | 1573.9703 | 1848.9403 | 1985.833 | 53.0711
2025-04-18 | 2026 | 2025 | 2025-04-01 | 2078.1465 | 1629.2487 | 1619.6813 | 1382.1412 | 1666.8478 | 1081.0132 | 1837.0563 | 689.8722 | 454.3758 | 599.512 | 674.0715 | 695.7633 | 715.1133 | 714.5557 | 598.4747 | 806.5745 | 860.2965 | 1980.8495 | 866.2475 | 737.7935 | 1541.7563 | 1540.6817 | 1056.4167 | 1043.2535 | 1140.638 | 946.4703 | 1077.4003 | 640.8297 | 1217.0738 | 927.792 | 927.3877 | 550.5767 | 1488.7143 | 1596.0592 | 923.5377 | 962.3747 | 1296.3575 | 1275.275 | 1420.7282 | 847.6945 | 1057.7462 | 1358.1933 | 1976.6917 | 1852.6223 | 50.3539
2025-04-19 | 2026 | 2025 | 2025-04-01 | 2722.8897 | 2608.8077 | 2678.8308 | 1666.5987 | 2052.902 | 1482.2565 | 2153.1465 | 767.5222 | 565.3922 | 692.2865 | 709.7587 | 741.204 | 738.5128 | 779.8368 | 733.6333 | 903.6823 | 994.0512 | 2510.202 | 986.9905 | 870.2955 | 1840.5067 | 2120.023 | 1175.3282 | 1207.3363 | 1289.7187 | 1116.9925 | 2355.6053 | 811.8427 | 1597.0257 | 1152.7723 | 1136.702 | 872.016 | 1918.8392 | 1793.993 | 1082.1028 | 1776.825 | 1055.4002 | 1629.2565 | 1782.7552 | 819.7858 | 1271.6648 | 1712.0558 | 2335.7152 | 2070.3727 | 63.2834
2025-04-20 | 2026 | 2025 | 2025-04-01 | 2862.7638 | 2556.8227 | 2478.6698 | 1370.2927 | 1435.9765 | 1130.4698 | 2483.1532 | 675.6132 | 425.6995 | 494.8247 | 521.8198 | 597.1288 | 553.6932 | 585.2047 | 551.2635 | 620.1447 | 721.071 | 2527.9688 | 747.8802 | 705.8115 | 1992.7833 | 2342.4738 | 1116.6205 | 1117.8915 | 1336.0983 | 1082.8585 | 2025.8425 | 1038.3293 | 1274.1183 | 1506.588 | 837.2748 | 671.938 | 1369.0402 | 1570.0682 | 1084.7992 | 1960.0612 | 1560.1232 | 1458.2888 | 1464.8512 | 1294.6817 | 1400.3492 | 2231.6618 | 2756.8547 | 2109.3882 | 60.6493
2025-04-21 | 2026 | 2025 | 2025-04-01 | 1430.9505 | 1604.0968 | 1691.2038 | 824.112 | 761.8 | 651.977 | 1297.8167 | 405.2408 | 211.8423 | 256.3237 | 281.8137 | 355.1842 | 336.2593 | 360.6883 | 329.808 | 358.3427 | 389.2835 | 1526.446 | 472.1967 | 411.1158 | 1304.596 | 1534.3645 | 637.1972 | 630.8513 | 806.6393 | 662.0367 | 1580.6055 | 1091.2405 | 759.7673 | 1379.9302 | 459.4442 | 409.844 | 725.677 | 991.624 | 810.581 | 1332.1655 | 974.9922 | 901.5143 | 880.1583 | 1193.5423 | 1133.4868 | 1710.4473 | 1529.873 | 1264.9947 | 38.6621
2025-04-22 | 2026 | 2025 | 2025-04-01 | 707.6333 | 636.7458 | 517.6427 | 692.7192 | 414.757 | 420.0403 | 668.9273 | 487.3283 | 377.208 | 354.2953 | 604.3208 | 661.029 | 643.0283 | 572.9013 | 536.8937 | 589.6428 | 668.0233 | 712.3203 | 700.034 | 636.1015 | 839.473 | 819.653 | 622.5835 | 694.6297 | 768.4103 | 713.6578 | 424.6633 | 178.982 | 631.254 | 245.3877 | 730.3728 | 292.2763 | 405.6548 | 381.8617 | 648.7917 | 656.4942 | 506.8318 | 371.7525 | 423.7307 | 253.6452 | 229.415 | 335.7673 | 753.8975 | 649.1158 | 24.1799
2025-04-23 | 2026 | 2025 | 2025-04-01 | 1505.4293 | 1195.8597 | 1135.243 | 395.0345 | 1115.4778 | 840.7738 | 1357.136 | 200.3623 | 383.4843 | 522.4017 | 608.5028 | 685.6587 | 702.2625 | 675.0713 | 646.8023 | 704.6632 | 799.69 | 1409.1922 | 717.6608 | 653.4078 | 579.5885 | 601.2973 | 316.1223 | 305.6963 | 372.5237 | 260.9138 | 823.8888 | 541.9567 | 276.6703 | 753.4847 | 768.4938 | 525.1638 | 1042.3613 | 1263.4588 | 282.9478 | 1234.4692 | 1224.0398 | 266.6348 | 1146.3632 | 736.6848 | 763.243 | 963.03 | 1592.4295 | 1394.7382 | 34.2903
2025-04-24 | 2026 | 2025 | 2025-04-01 | 1505.4293 | 1195.8597 | 1135.243 | 395.0345 | 1115.4778 | 840.7738 | 1357.136 | 200.3623 | 383.4843 | 522.4017 | 608.5028 | 685.6587 | 702.2625 | 675.0713 | 646.8023 | 704.6632 | 799.69 | 1409.1922 | 717.6608 | 653.4078 | 579.5885 | 601.2973 | 316.1223 | 305.6963 | 372.5237 | 260.9138 | 823.8888 | 541.9567 | 276.6703 | 753.4847 | 768.4938 | 525.1638 | 1042.3613 | 1263.4588 | 282.9478 | 1234.4692 | 1224.0398 | 266.6348 | 1146.3632 | 736.6848 | 763.243 | 963.03 | 1592.4295 | 1394.7382 | 34.2903
2025-04-25 | 2026 | 2025 | 2025-04-01 | 1342.3078 | 957.6253 | 820.5778 | 1061.9793 | 1071.0782 | 720.2827 | 1200.8175 | 466.7165 | 239.3713 | 267.4797 | 308.4397 | 342.2948 | 409.8095 | 467.0943 | 448.573 | 546.1183 | 671.1193 | 1271.1873 | 683.2643 | 609.121 | 1207.4765 | 1221.4202 | 722.6425 | 729.218 | 866.5518 | 805.2377 | 687.4973 | 253.8692 | 827.3202 | 520.7445 | 758.538 | 249.7898 | 933.0615 | 1103.5077 | 822.0845 | 1146.6617 | 1060.1327 | 965.4663 | 1297.36 | 361.3475 | 426.3833 | 647.8698 | 1471.076 | 1502.4093 | 34.4929
2025-04-26 | 2026 | 2025 | 2025-04-01 | 1141.5353 | 923.9072 | 802.7843 | 853.1982 | 927.1827 | 336.6265 | 636.4075 | 490.2338 | 402.2518 | 451.1557 | 500.6875 | 550.7045 | 602.25 | 163.0742 | 173.9693 | 190.9832 | 174.1897 | 1011.5827 | 221.1958 | 173.9317 | 836.6625 | 779.0373 | 623.2628 | 675.5605 | 761.0622 | 658.621 | 835.5803 | 402.3182 | 757.1542 | 663.9462 | 144.1933 | 596.5015 | 919.2272 | 1184.9717 | 682.5078 | 1001.618 | 1041.0212 | 947.5315 | 1077.3883 | 349.7342 | 509.1333 | 670.2403 | 1147.9367 | 1068.3587 | 29.0614
2025-04-27 | 2026 | 2025 | 2025-04-01 | 772.6577 | 576.3972 | 575.5663 | 516.271 | 816.8423 | 548.4598 | 596.8792 | 295.245 | 213.2803 | 297.6057 | 345.7778 | 404.554 | 434.3018 | 400.1512 | 387.047 | 403.7878 | 465.8558 | 682.3127 | 435.9282 | 405.1203 | 586.5062 | 549.0692 | 454.36 | 500.6338 | 558.9923 | 501.6048 | 484.2567 | 311.5283 | 523.9998 | 423.981 | 483.6585 | 333.014 | 449.4668 | 881.241 | 482.9005 | 688.5557 | 712.636 | 713.8075 | 796.788 | 396.3142 | 433.373 | 532.5863 | 766.49 | 774.0765 | 22.9139
2025-04-28 | 2026 | 2025 | 2025-04-01 | 772.6577 | 576.3972 | 575.5663 | 516.271 | 816.8423 | 548.4598 | 596.8792 | 295.245 | 213.2803 | 297.6057 | 345.7778 | 404.554 | 434.3018 | 400.1512 | 387.047 | 403.7878 | 465.8558 | 682.3127 | 435.9282 | 405.1203 | 586.5062 | 549.0692 | 454.36 | 500.6338 | 558.9923 | 501.6048 | 484.2567 | 311.5283 | 523.9998 | 423.981 | 483.6585 | 333.014 | 449.4668 | 881.241 | 482.9005 | 688.5557 | 712.636 | 713.8075 | 796.788 | 396.3142 | 433.373 | 532.5863 | 766.49 | 774.0765 | 22.9139
2025-04-29 | 2026 | 2025 | 2025-04-01 | 1560.4042 | 1329.7775 | 1080.5257 | 1083.6692 | 1356.5602 | 1046.659 | 1238.1288 | 553.5475 | 408.4417 | 539.6457 | 596.5655 | 679.3695 | 682.371 | 687.4558 | 658.9067 | 782.9637 | 892.0457 | 1634.1247 | 864.4613 | 711.0245 | 1052.359 | 1190.8057 | 816.2277 | 933.3618 | 1061.0877 | 912.841 | 695.8552 | 359.3957 | 976.1777 | 559.5995 | 859.5272 | 249.2282 | 1290.2077 | 1610.1578 | 748.8715 | 1336.8385 | 1281.2798 | 1266.9823 | 1459.8042 | 403.8873 | 492.5062 | 662.7975 | 1416.8055 | 1400.1438 | 41.4234
2025-04-30 | 2026 | 2025 | 2025-05-01 | 2636.7143 | 2208.6975 | 2127.2432 | 1695.6358 | 2056.9987 | 1534.8863 | 2086.4805 | 654.374 | 504.9968 | 620.1455 | 656.6592 | 619.4683 | 711.4377 | 782.906 | 752.469 | 886.5908 | 970.8263 | 2382.1197 | 922.5835 | 726.2488 | 1725.4717 | 1957.094 | 1152.0232 | 1223.632 | 1362.8792 | 1159.3218 | 1753.5925 | 854.0923 | 1596.4583 | 1144.0068 | 1025.1497 | 750.277 | 1967.0767 | 2065.9718 | 1080.9808 | 1675.2665 | 1551.2895 | 1637.1128 | 1833.6532 | 696.9585 | 1401.3903 | 1799.5333 | 2491.8758 | 2067.6248 | 61.5102
2025-05-01 | 2026 | 2025 | 2025-05-01 | 2769.0955 | 2678.2778 | 2886.2608 | 1881.964 | 1955.3052 | 1484.6278 | 2409.6515 | 632.6983 | 376.2025 | 436.0105 | 451.3138 | 512.7787 | 512.037 | 567.8458 | 544.7223 | 644.2347 | 902.3568 | 2515.4775 | 764.0413 | 711.7403 | 2312.384 | 2569.8947 | 1114.3947 | 1070.2673 | 1283.0125 | 975.684 | 2491.1845 | 1074.3277 | 1669.3173 | 1524.1458 | 927.1267 | 626.6207 | 1792.999 | 2147.1847 | 1070.2182 | 2270.9492 | 1760.621 | 1692.9672 | 1754.4548 | 1639.0407 | 1928.2032 | 2523.9095 | 2965.3643 | 2171.5975 | 66.9925
2025-05-02 | 2026 | 2025 | 2025-05-01 | 3635.8133 | 3561.94 | 3863.5488 | 1761.8272 | 2677.8895 | 2947.3107 | 3172.9808 | 1070.1908 | 725.7755 | 781.9655 | 816.1525 | 921.5865 | 940.5352 | 1097.3277 | 1101.1423 | 1567.5758 | 1664.445 | 3186.4858 | 1351.0998 | 1033.9712 | 2183.2717 | 2856.9695 | 1516.3417 | 1518.6858 | 1795.4558 | 1684.6347 | 3743.7538 | 2080.3363 | 1966.847 | 2738.7663 | 1405.954 | 1457.9387 | 2963.6228 | 3441.1665 | 1510.5095 | 3774.8488 | 3507.2212 | 3175.5748 | 3105.6547 | 2699.206 | 2875.7877 | 3491.4565 | 3452.3818 | 2937.4417 | 99.7634
2025-05-03 | 2026 | 2025 | 2025-05-01 | 3192.2992 | 3465.025 | 3522.5752 | 2322.4707 | 2763.052 | 2686.442 | 2439.9805 | 1117.7605 | 1003.53 | 1043.5332 | 1050.9515 | 1027.5568 | 1037.3063 | 1048.2038 | 1006.4512 | 1139.3343 | 1317.8508 | 3244.2895 | 1396.4378 | 1301.477 | 2247.997 | 2763.2198 | 1567.8518 | 1552.7533 | 1743.8287 | 1562.3963 | 3438.0475 | 2267.6192 | 2776.5668 | 2828.1383 | 1604.7577 | 2091.0747 | 2866.3547 | 2964.5378 | 1452.508 | 3796.257 | 3571.4975 | 2946.9928 | 2942.43 | 1820.0212 | 2563.9478 | 2812.1283 | 2999.8795 | 2493.5985 | 96.8009
2025-05-04 | 2026 | 2025 | 2025-05-01 | 2912.6513 | 2691.9805 | 2363.4183 | 3021.562 | 3578.7297 | 3305.4008 | 2505.4768 | 1039.3208 | 976.2073 | 1108.776 | 1203.0945 | 1349.6293 | 1171.0998 | 1295.2288 | 1154.9283 | 1385.119 | 1469.4135 | 3309.0897 | 1459.947 | 1247.7488 | 2579.8973 | 3084.5385 | 1727.9383 | 1789.0272 | 1947.58 | 1664.8685 | 2652.5443 | 2141.9397 | 3184.0918 | 2928.3898 | 1695.9543 | 2173.721 | 3614.1863 | 3520.468 | 1751.3677 | 4173.4835 | 4010.3185 | 3478.1203 | 3456.3465 | 866.074 | 1609.9667 | 2150.098 | 3089.2285 | 3015.6313 | 100.8546
2025-05-05 | 2026 | 2025 | 2025-05-01 | 3489.8155 | 3695.5155 | 3732.9093 | 2669.0658 | 2470.979 | 2153.7322 | 2417.1913 | 756.6178 | 829.578 | 1008.9793 | 1113.2725 | 1224.799 | 1158.9653 | 1126.7583 | 1010.4368 | 1164.7913 | 1447.1667 | 3277.4523 | 1311.0528 | 1126.8212 | 2603.3745 | 3088.4918 | 1600.3347 | 1673.9815 | 1904.0848 | 1618.6278 | 3548.7738 | 1915.0052 | 2862.9035 | 2504.1575 | 1595.5933 | 1450.7693 | 2422.1705 | 2745.9005 | 1708.8077 | 3144.1272 | 2879.0488 | 2490.1527 | 2472.1532 | 1308.8187 | 2160.5127 | 2748.0033 | 3109.7725 | 2488.9073 | 93.2304
2025-05-06 | 2026 | 2025 | 2025-05-01 | 2575.6895 | 2385.083 | 1967.9995 | 2063.7697 | 2218.2333 | 2078.7282 | 1635.108 | 947.3103 | 1007.0768 | 1242.5617 | 1264.0975 | 1305.9703 | 1227.0705 | 1231.9077 | 1145.8388 | 1307.2853 | 1424.0315 | 2317.5282 | 1253.5958 | 1071.9403 | 1879.0558 | 2062.685 | 1360.1533 | 1451.4268 | 1546.625 | 1390.8668 | 2091.082 | 1468.7155 | 2144.943 | 1934.397 | 1475.229 | 1484.4492 | 2178.5495 | 2327.803 | 1505.8515 | 2777.5787 | 2727.5193 | 2418.8175 | 2413.1078 | 801.968 | 1613.1078 | 1839.0877 | 2501.23 | 2053.9558 | 77.119
2025-05-07 | 2026 | 2025 | 2025-05-01 | 3167.0492 | 2323.4595 | 2539.6637 | 2376.6853 | 3364.5237 | 2855.5405 | 2300.885 | 1565.302 | 1333.5392 | 1919.5543 | 2154.2375 | 2389.3745 | 2182.835 | 1978.9248 | 1749.1697 | 2029.0158 | 1957.288 | 2537.0852 | 1963.639 | 1620.0067 | 2184.2623 | 2305.2673 | 1918.3187 | 2091.9832 | 2348.2115 | 2055.7453 | 2286.2375 | 1985.6512 | 2387.709 | 2453.6388 | 2019.6455 | 2140.363 | 3354.5283 | 3302.5357 | 1732.3578 | 3803.0048 | 3891.3752 | 3284.6317 | 3403.6492 | 1747.0783 | 2520.8648 | 2608.574 | 3390.2357 | 2985.8745 | 106.5095
2025-05-08 | 2026 | 2025 | 2025-05-01 | 4065.4567 | 3435.2857 | 2766.1313 | 3294.3103 | 3728.4225 | 3987.7822 | 3706.0017 | 2228.0403 | 1399.5235 | 1508.1715 | 1651.0942 | 2483.253 | 2551.7488 | 2441.0623 | 1881.8767 | 2447.3368 | 2342.2658 | 2906.3697 | 2215.9842 | 1977.976 | 3058.4283 | 2638.9248 | 2365.4577 | 1451.2468 | 2444.7693 | 2044.4482 | 2278.2347 | 2349.806 | 3179.3162 | 2805.5953 | 2081.0682 | 2820.0562 | 3705.4852 | 3115.2645 | 2056.214 | 4720.8912 | 4424.1213 | 2863.245 | 3996.1732 | 2593.5677 | 3003.584 | 3319.5478 | 4639.7533 | 4285.2592 | 125.2586
2025-05-09 | 2026 | 2025 | 2025-05-01 | 1668.5602 | 1826.4508 | 1226.601 | 1495.9443 | 946.5897 | 1410.7058 | 1571.9698 | 899.883 | 516.23 | 352.2473 | 364.7297 | 742.3433 | 631.4465 | 504.3193 | 540.3407 | 707.6218 | 682.2715 | 1326.4772 | 1015.6377 | 677.1443 | 1418.6137 | 1252.0545 | 389.6217 | 273.0332 | 527.6663 | 759.0737 | 897.7943 | 618.5952 | 1453.6958 | 754.958 | 680.9003 | 918.2488 | 1158.6008 | 761.2333 | 995.8328 | 1546.3997 | 1387.2357 | 705.1733 | 1228.8013 | 621.3433 | 725.4945 | 925.0483 | 1703.0403 | 1534.64 | 42.3446
2025-05-10 | 2026 | 2025 | 2025-05-01 | 1130.5383 | 1420.1587 | 1047.7382 | 1086.2245 | 781.4452 | 983.023 | 1106.5243 | 604.3245 | 396.0218 | 283.8162 | 356.3197 | 437.6957 | 406.9997 | 100.7705 | 440.8383 | 504.0375 | 572.4737 | 1087.6328 | 738.6767 | 580.4585 | 1001.9552 | 252.2467 | 531.9317 | 591.4955 | 328.6938 | 456.975 | 837.0063 | 290.7772 | 1082.4945 | 363.4528 | 558.9007 | 631.9753 | 698.9022 | 791.8805 | 647.4303 | 1148.8772 | 1028.3548 | 588.4667 | 942.9488 | 286.1242 | 375.599 | 443.8322 | 1129.5837 | 1074.884 | 30.1505
2025-05-11 | 2026 | 2025 | 2025-05-01 | 840.2778 | 871.6407 | 495.537 | 631.9733 | 520.7533 | 708.217 | 786.2723 | 353.9152 | 192.2605 | 198.1087 | 230.5065 | 399.4992 | 363.3923 | 380.6563 | 336.4285 | 385.0598 | 384.0487 | 563.7102 | 484.8787 | 370.5232 | 582.279 | 343.4295 | 368.2335 | 364.3385 | 401.11 | 340.1182 | 405.5693 | 385.4957 | 641.1575 | 512.016 | 388.1737 | 472.4452 | 606.4318 | 529.1022 | 357.9082 | 932.9873 | 837.5072 | 507.0555 | 723.8015 | 43.3092 | 491.8343 | 153.1353 | 919.5817 | 825.122 | 21.6298
2025-05-12 | 2026 | 2025 | 2025-05-01 | 948.9998 | 291.0832 | 788.2033 | 521.49 | 325.6413 | 551.639 | 708.6413 | 255.1653 | 496.6462 | 546.469 | 542.5987 | 535.526 | 518.1523 | 579.6903 | 593.1335 | 644.3423 | 703.0897 | 708.9067 | 672.2545 | 664.7398 | 505.9027 | 458.916 | 290.592 | 329.8688 | 371.685 | 353.589 | 713.2185 | 187.8877 | 525.927 | 345.8442 | 740.2117 | 250.4352 | 96.7875 | 464.0558 | 349.6563 | 658.2008 | 543.2735 | 390.722 | 565.4913 | 237.96 | 375.0413 | 174.0245 | 897.7218 | 917.9912 | 22.3414
2025-05-13 | 2026 | 2025 | 2025-05-01 | 344.5638 | 251.1817 | 290.7602 | 611.3807 | 398.9268 | 268.2918 | 221.5855 | 365.8182 | 267.8437 | 318.04 | 449.5347 | 377.8713 | 355.7462 | 315.3737 | 316.9277 | 389.683 | 481.234 | 300.499 | 318.6363 | 338.7037 | 598.9163 | 581.0035 | 492.3575 | 537.7458 | 549.6062 | 483.2733 | 251.5017 | 177.0187 | 579.5997 | 212.8768 | 496.2668 | 165.6563 | 0 | 353.1422 | 111.4742 | 386.7338 | 335.6382 | 358.219 | 377.4817 | 214.9612 | 262.4137 | 223.1878 | 348.5743 | 303.8673 | 15.3841
2025-05-14 | 2026 | 2025 | 2025-05-01 | 754.6305 | 703.5328 | 605.72 | 100.9903 | 114.0243 | 328.9923 | 471.0223 | 293.4108 | 220.1272 | 250.6257 | 241.6107 | 286.5827 | 302.9762 | 300.9918 | 287.123 | 338.5937 | 364.5148 | 716.712 | 408.5385 | 366.9863 | 602.4975 | 637.9402 | 438.2387 | 426.7613 | 499.9062 | 451.6873 | 611.5937 | 318.3042 | 604.3137 | 756.074 | 327.886 | 185.7147 | 227.3288 | 570.0137 | 222.9377 | 631.7672 | 493.9598 | 476.4715 | 516.911 | 243.7993 | 409.055 | 592.9318 | 826.6618 | 761.4187 | 19.2919
2025-05-15 | 2026 | 2025 | 2025-05-01 | 706.1887 | 607.4902 | 576.3323 | 228.4907 | 349.6332 | 472.8933 | 522.612 | 244.2305 | 135.849 | 153.6445 | 181.2108 | 216.674 | 213.3352 | 217.5595 | 186.186 | 242.8332 | 304.8668 | 711.2155 | 322.3245 | 303.1043 | 704.8867 | 744.5152 | 406.0542 | 428.7303 | 465.6235 | 374.1987 | 508.3142 | 262.9677 | 747.267 | 504.5282 | 371.005 | 244.971 | 501.7158 | 795.7513 | 473.4977 | 709.2042 | 630.7482 | 622.2672 | 721.5852 | 218.2207 | 367.4767 | 529.9872 | 792.5142 | 774.1097 | 19.7968
2025-05-16 | 2026 | 2025 | 2025-05-01 | 38.4313 | 26.5782 | 19.4512 | 22.7245 | 38.1415 | 18.7582 | 23.1643 | 0.8105 | 0 | 0 | 0 | 2.6968 | 1.3352 | 1.1443 | 1.8928 | 9.1228 | 17.2753 | 25.3435 | 19.5617 | 22.6925 | 24.2977 | 24.7593 | 4.218 | 8.2223 | 10.1902 | 9.3467 | 5.8357 | 0.89833 | 21.2055 | 3.542 | 18.3343 | 3.325 | 25.9808 | 54.5052 | 14.3535 | 18.482 | 19.192 | 24.2043 | 39.5348 | 12.7888 | 12.1555 | 9.5103 | 25.8252 | 27.9768 | 0.70781
2025-05-17 | 2026 | 2025 | 2025-05-01 | 344.5638 | 251.1817 | 290.7602 | 611.3807 | 398.9268 | 268.2918 | 221.5855 | 365.8182 | 267.8437 | 318.04 | 449.5347 | 377.8713 | 355.7462 | 315.3737 | 316.9277 | 389.683 | 481.234 | 300.499 | 318.6363 | 338.7037 | 598.9163 | 581.0035 | 492.3575 | 537.7458 | 549.6062 | 483.2733 | 251.5017 | 177.0187 | 579.5997 | 212.8768 | 496.2668 | 165.6563 | 0 | 353.1422 | 111.4742 | 386.7338 | 335.6382 | 358.219 | 377.4817 | 214.9612 | 262.4137 | 223.1878 | 348.5743 | 303.8673 | 15.3841
2025-05-18 | 2026 | 2025 | 2025-05-01 | 57.4273 | 41.8636 | 48.46 | 101.8968 | 66.4878 | 44.7153 | 36.9309 | 60.9697 | 44.6406 | 53.0067 | 74.9224 | 62.9786 | 59.291 | 52.5623 | 52.8213 | 64.9472 | 80.2057 | 50.0832 | 53.1061 | 56.4506 | 99.8194 | 96.8339 | 82.0596 | 89.6243 | 91.601 | 80.5456 | 41.9169 | 29.5031 | 96.5999 | 35.4795 | 82.7111 | 27.6094 | 0 | 58.857 | 18.579 | 64.4556 | 55.9397 | 59.7032 | 62.9136 | 35.8269 | 43.7356 | 37.198 | 58.0957 | 50.6446 | 2.564
2025-05-19 | 2026 | 2025 | 2025-05-01 | 70.2792 | 62.2593 | 62.9267 | 56.805 | 38.0287 | 37.0869 | 52.2397 | 18.2814 | 14.5151 | 13.4757 | 8.3177 | 11.9002 | 10.9807 | 7.9328 | 10.5803 | 12.1025 | 15.7468 | 61.3857 | 17.9212 | 13.0607 | 57.0704 | 57.2963 | 30.7453 | 26.5727 | 19.6335 | 25.6727 | 76.7752 | 35.5897 | 45.2383 | 43.8947 | 17.4318 | 21.3094 | 29.4918 | 56.6236 | 39.7455 | 60.0693 | 53.9682 | 48.0629 | 54.8224 | 11.9227 | 44.4108 | 44.2796 | 67.6776 | 54.9113 | 1.619
2025-05-20 | 2026 | 2025 | 2025-05-01 | 10.3543 | 8.557 | 1.1525 | 10.8707 | 2.7775 | 6.484 | 2.6727 | 5.132 | 9.3113 | 7.25 | 12.9285 | 10.4893 | 9.7488 | 8.4478 | 3.8362 | 1.4568 | 1.8588 | 0.314 | 4.4727 | 0 | 20.1777 | 18.4245 | 16.8713 | 18.402 | 15.165 | 16.5087 | 0.29633 | 4.6192 | 3.4642 | 18.387 | 0 | 3.5728 | 4.3073 | 4.5702 | 19.429 | 19.6693 | 2.5833 | 0 | 4.1188 | 3.0355 | 4.3 | 19.7535 | 15.302 | 2.7643 | 0.35384
2025-05-21 | 2026 | 2025 | 2025-05-01 | [44 empty] | 0
2025-05-22 | 2026 | 2025 | 2025-05-01 | 568.1742 | 641.5852 | 539.2913 | 251.5083 | 93.5138 | 346.261 | 485.017 | 521.7978 | 583.8722 | 397.2052 | 510.0913 | 579.9178 | 463.481 | 483.8787 | 268.8848 | 453.7277 | 388.06 | 436.7503 | 399.4282 | 237.336 | 402.3813 | 472.7203 | 466.161 | 454.6742 | 524.5423 | 531.3343 | 453.2938 | 61.6898 | 239.35 | 202.7173 | 152.092 | 261.8975 | 222.1125 | 420.3543 | 277.2652 | 753.5845 | 376.5542 | 518.223 | 593.2063 | 92.5488 | 128.6288 | 192.0787 | 901.4638 | 593.9197 | 17.9426
2025-05-23 | 2026 | 2025 | 2025-05-01 | 784.08 | 1028.976 | 652.872 | 29.136 | 0 | 329.04 | 848.4 | 398.952 | 691.776 | 191.208 | 604.056 | 843.6 | 530.208 | 812.352 | 250.992 | 846.744 | 471.36 | 391.68 | 444.768 | 208.416 | 508.536 | 878.64 | 467.04 | 326.376 | 712.584 | 466.08 | 647.4 | 0 | 210.048 | 258.624 | 43.032 | 55.296 | 189.144 | 523.272 | 74.928 | 1051.896 | 422.928 | 780.528 | 926.952 | 0 | 0 | 171.792 | 2005.512 | 1072.68 | 22.1519
2025-05-24 | 2026 | 2025 | 2025-05-01 | 784.08 | 1028.976 | 652.872 | 29.136 | 0 | 329.04 | 848.4 | 398.952 | 691.776 | 191.208 | 604.056 | 843.6 | 530.208 | 812.352 | 250.992 | 846.744 | 471.36 | 391.68 | 444.768 | 208.416 | 508.536 | 878.64 | 467.04 | 326.376 | 712.584 | 466.08 | 647.4 | 0 | 210.048 | 258.624 | 43.032 | 55.296 | 189.144 | 523.272 | 74.928 | 1051.896 | 422.928 | 780.528 | 926.952 | 0 | 0 | 171.792 | 2005.512 | 1072.68 | 22.1519
2025-05-25 | 2026 | 2025 | 2025-05-01 | 784.08 | 1028.976 | 652.872 | 29.136 | 0 | 329.04 | 848.4 | 398.952 | 691.776 | 191.208 | 604.056 | 843.6 | 530.208 | 812.352 | 250.992 | 846.744 | 471.36 | 391.68 | 444.768 | 208.416 | 508.536 | 878.64 | 467.04 | 326.376 | 712.584 | 466.08 | 647.4 | 0 | 210.048 | 258.624 | 43.032 | 55.296 | 189.144 | 523.272 | 74.928 | 1051.896 | 422.928 | 780.528 | 926.952 | 0 | 0 | 171.792 | 2005.512 | 1072.68 | 22.1519
2025-05-26 | 2026 | 2025 | 2025-05-01 | 784.08 | 1028.976 | 652.872 | 29.136 | 0 | 329.04 | 848.4 | 398.952 | 691.776 | 191.208 | 604.056 | 843.6 | 530.208 | 812.352 | 250.992 | 846.744 | 471.36 | 391.68 | 444.768 | 208.416 | 508.536 | 878.64 | 467.04 | 326.376 | 712.584 | 466.08 | 647.4 | 0 | 210.048 | 258.624 | 43.032 | 55.296 | 189.144 | 523.272 | 74.928 | 1051.896 | 422.928 | 780.528 | 926.952 | 0 | 0 | 171.792 | 2005.512 | 1072.68 | 22.1519
2025-05-27 | 2026 | 2025 | 2025-05-01 | 784.08 | 1028.976 | 652.872 | 29.136 | 0 | 329.04 | 848.4 | 398.952 | 691.776 | 191.208 | 604.056 | 843.6 | 530.208 | 812.352 | 250.992 | 846.744 | 471.36 | 391.68 | 444.768 | 208.416 | 508.536 | 878.64 | 467.04 | 326.376 | 712.584 | 466.08 | 647.4 | 0 | 210.048 | 258.624 | 43.032 | 55.296 | 189.144 | 523.272 | 74.928 | 1051.896 | 422.928 | 780.528 | 926.952 | 0 | 0 | 171.792 | 2005.512 | 1072.68 | 22.1519
2025-05-28 | 2026 | 2025 | 2025-05-01 | 784.08 | 1028.976 | 652.872 | 29.136 | 0 | 329.04 | 848.4 | 398.952 | 691.776 | 191.208 | 604.056 | 843.6 | 530.208 | 812.352 | 250.992 | 846.744 | 471.36 | 391.68 | 444.768 | 208.416 | 508.536 | 878.64 | 467.04 | 326.376 | 712.584 | 466.08 | 647.4 | 0 | 210.048 | 258.624 | 43.032 | 55.296 | 189.144 | 523.272 | 74.928 | 1051.896 | 422.928 | 780.528 | 926.952 | 0 | 0 | 171.792 | 2005.512 | 1072.68 | 22.1519
2025-05-29 | 2026 | 2025 | 2025-05-01 | 784.08 | 1028.976 | 652.872 | 29.136 | 0 | 329.04 | 848.4 | 398.952 | 691.776 | 191.208 | 604.056 | 843.6 | 530.208 | 812.352 | 250.992 | 846.744 | 471.36 | 391.68 | 444.768 | 208.416 | 508.536 | 878.64 | 467.04 | 326.376 | 712.584 | 466.08 | 647.4 | 0 | 210.048 | 258.624 | 43.032 | 55.296 | 189.144 | 523.272 | 74.928 | 1051.896 | 422.928 | 780.528 | 926.952 | 0 | 0 | 171.792 | 2005.512 | 1072.68 | 22.1519
2025-05-30 | 2026 | 2025 | 2025-05-01 | 784.08 | 1028.976 | 652.872 | 29.136 | 0 | 329.04 | 848.4 | 398.952 | 691.776 | 191.208 | 604.056 | 843.6 | 530.208 | 812.352 | 250.992 | 846.744 | 471.36 | 391.68 | 444.768 | 208.416 | 508.536 | 878.64 | 467.04 | 326.376 | 712.584 | 466.08 | 647.4 | 0 | 210.048 | 258.624 | 43.032 | 55.296 | 189.144 | 523.272 | 74.928 | 1051.896 | 422.928 | 780.528 | 926.952 | 0 | 0 | 171.792 | 2005.512 | 1072.68 | 22.1519
2025-05-31 | 2026 | 2025 | 2025-06-01 | 784.08 | 1028.976 | 652.872 | 29.136 | 0 | 329.04 | 848.4 | 398.952 | 691.776 | 191.208 | 604.056 | 843.6 | 530.208 | 812.352 | 250.992 | 846.744 | 471.36 | 391.68 | 444.768 | 208.416 | 508.536 | 878.64 | 467.04 | 326.376 | 712.584 | 466.08 | 647.4 | 0 | 210.048 | 258.624 | 43.032 | 55.296 | 189.144 | 523.272 | 74.928 | 1051.896 | 422.928 | 780.528 | 926.952 | 0 | 0 | 171.792 | 2005.512 | 1072.68 | 22.1519
2025-06-01 | 2026 | 2025 | 2025-06-01 | 784.08 | 1028.976 | 652.872 | 29.136 | 0 | 329.04 | 848.4 | 398.952 | 691.776 | 191.208 | 604.056 | 843.6 | 530.208 | 812.352 | 250.992 | 846.744 | 471.36 | 391.68 | 444.768 | 208.416 | 508.536 | 878.64 | 467.04 | 326.376 | 712.584 | 466.08 | 647.4 | 0 | 210.048 | 258.624 | 43.032 | 55.296 | 189.144 | 523.272 | 74.928 | 1051.896 | 422.928 | 780.528 | 926.952 | 0 | 0 | 171.792 | 2005.512 | 1072.68 | 22.1519
2025-06-02 | 2026 | 2025 | 2025-06-01 | 1183.049 | 1271.1273 | 761.3673 | 883.4788 | 992.8548 | 1179.9508 | 1107.8433 | 555.8388 | 357.8962 | 331.7582 | 352.5453 | 633.5462 | 648.5772 | 718.3917 | 539.264 | 629.558 | 431.1553 | 792.565 | 723.71 | 451.307 | 776.6743 | 724.4562 | 620.7183 | 544.3365 | 608.035 | 490.2773 | 350.782 | 587.2278 | 905.8972 | 798.0212 | 398.9797 | 777.3623 | 956.159 | 678.8772 | 540.2485 | 1402.0772 | 983.7573 | 741.7743 | 1199.3075 | 694.9947 | 800.0698 | 950.6318 | 1337.6397 | 1251.5353 | 33.6656
2025-06-03 | 2026 | 2025 | 2025-06-01 | 3036.79 | 2787.6085 | 2206.3088 | 2234.11 | 2660.4152 | 2844.3665 | 2592.8893 | 1578.1537 | 924.2208 | 1176.408 | 2059.5643 | 2797.876 | 2523.2265 | 2038.8833 | 1798.0878 | 1804.3425 | 1502.597 | 1900.9288 | 1791.0952 | 1151.6105 | 2126.666 | 1706.8418 | 1627.1855 | 1761.3403 | 1972.9295 | 1262.6765 | 1790.1242 | 1747.6392 | 2154.3148 | 2300.338 | 1324.287 | 1972.8075 | 2357.1703 | 2611.1197 | 1492.1467 | 3319.5803 | 3419.6717 | 2207.277 | 3098.3795 | 1813.5995 | 2284.1557 | 2743.8393 | 3434.9162 | 3104.778 | 95.0433
2025-06-04 | 2026 | 2025 | 2025-06-01 | 3124.585 | 2930.4908 | 2925.4907 | 2339.7387 | 2657.7822 | 2863.3913 | 2564.2972 | 1901.2288 | 1678.3185 | 1456.0295 | 1587.185 | 1712.9485 | 1490.3197 | 1509.1542 | 1384.5257 | 1632.4833 | 1801.8912 | 2236.5505 | 1979.0332 | 1410.2003 | 2435.0858 | 2194.4672 | 2407.2573 | 1841.6298 | 1994.901 | 898.2133 | 2672.5243 | 1746.4107 | 2330.1292 | 2079.4133 | 1811.131 | 1987.0713 | 2619.2377 | 2256.196 | 1939.275 | 3802.0742 | 3331.6132 | 2463.8073 | 2307.7432 | 1871.2565 | 2261.2652 | 2267.3287 | 3442.9577 | 2492.7375 | 96.6394
2025-06-05 | 2026 | 2025 | 2025-06-01 | 2031.0357 | 2167.9003 | 2191.7555 | 1690.9687 | 2146.525 | 2073.3272 | 1432.8647 | 918.076 | 1078.4707 | 1287.7355 | 1210.3648 | 1222.4653 | 1038.3502 | 1132.811 | 941.3117 | 1060.7415 | 1035.757 | 2085.0217 | 907.8993 | 751.339 | 1548.2012 | 1620.8472 | 1527.726 | 1439.3545 | 1386.4013 | 773.5038 | 2689.8837 | 1047.336 | 1657.2388 | 1440.57 | 1017.7008 | 1341.715 | 2267.0227 | 2274.5542 | 1076.6833 | 2270.9687 | 2240.657 | 2039.2307 | 2201.6273 | 835.8283 | 1432.0103 | 1587.9913 | 1864.0955 | 1705.373 | 67.6912
2025-06-06 | 2026 | 2025 | 2025-06-01 | 1982.9333 | 1957.4335 | 1623.254 | 1194.5977 | 1122.0002 | 1044.1207 | 1127.3992 | 480.4492 | 330.9067 | 346.9813 | 352.5877 | 347.633 | 214.3 | 376.383 | 344.0793 | 406.9587 | 509.3145 | 1997.252 | 533.3808 | 471.5885 | 1245.3435 | 1391.8548 | 734.5007 | 744.6988 | 844.7862 | 737.6463 | 1489.5537 | 737.4567 | 1251.9993 | 1164.2105 | 619.393 | 680.0763 | 1131.8052 | 1086.916 | 960.1952 | 1565.3762 | 1373.5472 | 1277.2013 | 1419.1235 | 302.55 | 1035.0332 | 1354.2917 | 1741.3113 | 1619.206 | 43.2716
2025-06-07 | 2026 | 2025 | 2025-06-01 | 2079.4483 | 1974.6708 | 1547.3072 | 1640.9432 | 1485.2195 | 1462.4532 | 1217.1478 | 659.632 | 570.569 | 619.2765 | 612.2145 | 592.2402 | 536.2447 | 612.4492 | 566.7508 | 638.7342 | 738.9653 | 2178.6327 | 718.224 | 575.3577 | 1557.0407 | 1661.3697 | 1116.7753 | 1067.1502 | 1146.1477 | 1016.476 | 1596.6358 | 712.6062 | 1448.9178 | 1187.3393 | 829.6437 | 975.63 | 1539.8782 | 2043.8737 | 1196.039 | 1913.3132 | 1766.74 | 1716.0737 | 1765.5408 | 288.392 | 919.0335 | 1228.412 | 1934.6552 | 1788.0708 | 53.4422
2025-06-08 | 2026 | 2025 | 2025-06-01 | 3006.8752 | 3043.5467 | 2686.2795 | 2796.2018 | 2974.229 | 2898.6975 | 2072.699 | 1206.8467 | 1221.1432 | 1367.0017 | 1355.2938 | 1333.3395 | 1167.3105 | 1283.8678 | 1158.4188 | 1329.4583 | 1357.5438 | 3412.8695 | 1352.7622 | 1152.9492 | 2576.2147 | 2821.6212 | 1980.4157 | 2004.096 | 2025.8587 | 1729.4663 | 2806.66 | 1308.6815 | 2668.1475 | 1927.12 | 1581.936 | 2000.1262 | 3107.5847 | 3592.8522 | 1902.8192 | 3176.1012 | 3059.2395 | 2959.7157 | 3153.4512 | 826.7727 | 1579.1333 | 1989.915 | 2760.3985 | 2656.7203 | 94.3724
2025-06-09 | 2026 | 2025 | 2025-06-01 | 3091.1317 | 3316.7352 | 3090.34 | 3054.5342 | 3846.4002 | 3871.6212 | 2247.4247 | 1627.4772 | 1781.272 | 1957.45 | 1925.744 | 1875.1132 | 1692.607 | 1809.0698 | 1676.4513 | 1762.8602 | 1750.7525 | 3670.0607 | 1842.5352 | 1754.5445 | 2998.0393 | 3105.9925 | 2502.9918 | 2559.0925 | 2741.1128 | 2502.3135 | 3255.5683 | 1688.2057 | 2904.9043 | 2421.295 | 2134.8607 | 2536.141 | 4087.3652 | 4460.362 | 2541.8953 | 4121.8112 | 4030.2318 | 3832.6203 | 4197.3928 | 885.6402 | 1982.1977 | 2311.4148 | 3185.327 | 3239.923 | 117.8708
2025-06-10 | 2026 | 2025 | 2025-06-01 | 2482.4427 | 2485.534 | 2291.8115 | 1922.611 | 1825.4868 | 1796.0508 | 1613.3112 | 909.0767 | 707.5853 | 711.1578 | 641.9425 | 568.6457 | 547.4782 | 637.2282 | 600.7473 | 641.318 | 614.9328 | 2458.4622 | 787.2145 | 678.8597 | 2069.0888 | 2122.5815 | 1306.318 | 1236.2758 | 1239.8082 | 1131.2663 | 1838.8235 | 1447.6295 | 2032.4635 | 1935.6473 | 817.6318 | 1115.805 | 1879.8508 | 2490.6555 | 1600.6272 | 2401.0672 | 2068.1697 | 2035.9123 | 2267.9217 | 684.0372 | 1925.4353 | 2214.9025 | 2430.1225 | 2248.3428 | 67.4623
2025-06-11 | 2026 | 2025 | 2025-06-01 | 1790.7097 | 2166.0123 | 2299.6973 | 1543.8738 | 1963.1892 | 1889.0648 | 1268.663 | 973.0462 | 1118.2548 | 1132.2887 | 1126.4022 | 1089.8483 | 1094.278 | 1135.0103 | 1046.0923 | 1140.6743 | 1033.0767 | 1918.0007 | 1108.5932 | 1062.3942 | 1443.9965 | 1619.8077 | 1311.8057 | 1412.9708 | 1456.3167 | 1398.4928 | 2567.8255 | 1093.7773 | 1516.2782 | 1339.617 | 1284.4355 | 1410.7018 | 2080.1928 | 2135.7103 | 1386.0825 | 1904.7392 | 1898.8708 | 1801.1908 | 1966.407 | 743.5148 | 1562.1753 | 1577.8973 | 1519.4418 | 1414.8338 | 65.7463
2025-06-12 | 2026 | 2025 | 2025-06-01 | 4597.7643 | 5485.3198 | 5601.8052 | 2940.9632 | 3084.8662 | 3149.6283 | 3112.287 | 2135.7507 | 1934.8242 | 1938.6197 | 1721.4252 | 1587.9643 | 1565.9048 | 1628.0687 | 1501.1652 | 1478.8243 | 1662.0485 | 4492.1827 | 1744.66 | 1538.6325 | 3086.279 | 3640.4603 | 2461.1788 | 2425.4995 | 2579.0147 | 2471.1448 | 5611.332 | 2213.9443 | 3274.2257 | 2897.989 | 1835.8108 | 2198.8635 | 3222.4398 | 4201.9018 | 2739.6938 | 4187.0807 | 3985.7583 | 3572.6008 | 3742.484 | 1735.6668 | 3650.9502 | 3973.708 | 3897.5102 | 3729.9207 | 130.2382
2025-06-13 | 2026 | 2025 | 2025-06-01 | [44 empty] | 0
2025-06-14 | 2026 | 2025 | 2025-06-01 | [44 empty] | 0
2025-06-15 | 2026 | 2025 | 2025-06-01 | [44 empty] | 0
2025-06-16 | 2026 | 2025 | 2025-06-01 | [44 empty] | 0
2025-06-17 | 2026 | 2025 | 2025-06-01 | [44 empty] | 0
2025-06-18 | 2026 | 2025 | 2025-06-01 | [44 empty] | 0
2025-06-19 | 2026 | 2025 | 2025-06-01 | [44 empty] | 0
2025-06-20 | 2026 | 2025 | 2025-06-01 | [44 empty] | 0
2025-06-21 | 2026 | 2025 | 2025-06-01 | [44 empty] | 0
2025-06-22 | 2026 | 2025 | 2025-06-01 | [44 empty] | 0
2025-06-23 | 2026 | 2025 | 2025-06-01 | [44 empty] | 0
2025-06-24 | 2026 | 2025 | 2025-06-01 | [44 empty] | 0
2025-06-25 | 2026 | 2025 | 2025-06-01 | [44 empty] | 0
2025-06-26 | 2026 | 2025 | 2025-06-01 | [44 empty] | 0
2025-06-27 | 2026 | 2025 | 2025-06-01 | [44 empty] | 0
2025-06-28 | 2026 | 2025 | 2025-06-01 | [44 empty] | 0
2025-06-29 | 2026 | 2025 | 2025-06-01 | [44 empty] | 0
2025-06-30 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-01 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-02 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-03 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-04 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-05 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-06 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-07 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-08 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-09 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-10 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-11 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-12 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-13 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-14 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-15 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-16 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-17 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-18 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-19 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-20 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-21 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-22 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-23 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-24 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-25 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-26 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-27 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-28 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-29 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-30 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-31 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-01 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-02 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-03 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-04 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-05 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-06 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-07 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-08 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-09 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-10 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-11 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-12 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-13 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-14 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-15 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-16 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-17 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-18 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-19 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-20 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-21 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-22 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-23 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-24 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-25 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-26 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-27 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-28 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-29 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-30 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-31 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-01 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-02 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-03 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-04 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-05 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-06 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-07 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-08 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-09 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-10 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-11 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-12 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-13 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-14 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-15 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-16 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-17 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-18 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-19 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-20 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-21 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-22 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-23 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-24 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-25 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-26 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-27 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-28 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-29 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-30 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-01 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-02 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-03 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-04 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-05 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-06 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-07 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-08 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-09 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-10 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-11 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-12 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-13 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-14 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-15 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-16 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-17 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-18 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-19 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-20 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-21 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-22 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-23 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-24 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-25 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-26 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-27 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-28 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-29 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-30 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-31 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-01 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-02 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-03 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-04 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-05 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-06 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-07 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-08 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-09 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-10 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-11 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-12 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-13 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-14 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-15 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-16 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-17 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-18 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-19 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-20 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-21 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-22 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-23 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-24 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-25 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-26 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-27 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-28 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-29 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-30 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-01 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-02 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-03 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-04 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-05 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-06 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-07 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-08 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-09 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-10 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-11 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-12 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-13 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-14 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-15 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-16 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-17 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-18 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-19 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-20 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-21 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-22 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-23 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-24 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-25 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-26 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-27 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-28 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-29 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-30 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-31 | 2026 | 2025 | 2026-01-01 | [44 empty] | 0
2026-01-01 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-02 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-03 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-04 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-05 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-06 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-07 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-08 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-09 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-10 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-11 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-12 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-13 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-14 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-15 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-16 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-17 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-18 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-19 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-20 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-21 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-22 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-23 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-24 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-25 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-26 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-27 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-28 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-29 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-30 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-31 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-01 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-02 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-03 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-04 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-05 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-06 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-07 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-08 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-09 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-10 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-11 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-12 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-13 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-14 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-15 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-16 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-17 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-18 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-19 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-20 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-21 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-22 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-23 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-24 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-25 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-26 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-27 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-28 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-01 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-02 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-03 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-04 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-05 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-06 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-07 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-08 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-09 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-10 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-11 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-12 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-13 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-14 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-15 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-16 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-17 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-18 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-19 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-20 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-21 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-22 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-23 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-24 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-25 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-26 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-27 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-28 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-29 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-30 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-31 | 2026 | 2026 | #VALUE! | [44 empty] | 0
Formulas:
Month Year = Daily_KPI[[#This Row],[Date]]-DAY(Daily_KPI[[#This Row],[Date]])+1

## Basic Data (hidden)
[18 empty] | 1 | Programstart PLC
| Generator | Consumer | Capacity | % Plant Equiva. Weightage | Feeder Number | USS YARD | METERING YARD | OG | Total Capacity | 70.4 | [7 empty] | 2 | No Errors
P-01 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F4 | P-01 |  | OG1 |  |  | Open | PM |  | WTG | IG | EG |  | 3 | Manual Stop
P-02 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F4 | P-02 |  | OG1 |  |  | Close | BM |  | WTG Unscheduled Maintenance | IG Unscheduled Maintenance | EG Unscheduled Maintenance |  | 6 | System OK
P-03 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F4 | P-03 |  | OG1 |  |  |  |  | BM | WTG Breakdown Maintenance | IG Breakdown Maintenance | EG Breakdown Maintenance |  | 7 | Storm shutdown
P-04 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F2 | P-04 |  | OG1 |  |  |  |  | PM | WTG Scheduled Maintenance | IG Scheduled Maintenance | EG Scheduled Maintenance |  | 8 | Overvoltage
P-05 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F3 | P-05 |  | OG1 | [5 empty] | WTG Environmental | IG Force Major | EG Force Major |  | 9 | Undervoltage
P-06 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F3 | P-06 |  | OG1 | [5 empty] | WTG Force Majeure |  |  |  | 10 | Underfrequency
P-07 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F4 | P-07 |  | OG1 | [9 empty] | 11 | Overfrequency
P-08 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F1 | P-08 |  | OG1 | [9 empty] | 12 | Phase angle error
P-09 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F1 | P-09 |  | OG1 | [9 empty] | 13 | Asymmetric generator current
P-10 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F1 | P-10 |  | OG1 | [9 empty] | 14 | Generator overspeed
P-11 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F1 | P-11 |  | OG1 | [9 empty] | 15 | Rotor overspeed
P-12 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F1 | P-12 |  | OG1 | [9 empty] | 16 | RotorSpeedMonitor
P-13 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F1 | P-13 |  | OG1 | [9 empty] | 19 | Maximum motor power
P-14 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F2 | P-14 |  | OG1 | [9 empty] | 20 | Cable twisting right
P-15 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F2 | P-15 |  | OG1 | [9 empty] | 21 | Cable twisting left
P-16 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F2 | P-16 |  | OG1 | [9 empty] | 22 | Yaw drive stop position
P-17 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F2 | P-17 |  | OG1 | [9 empty] | 23 | PowerExceedPeakValue
P-18 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F4 | P-18 |  | OG1 | [9 empty] | 24 | Primary braking time too high
P-19 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F2 | P-19 |  | OG1 | [9 empty] | 25 | No red. of speed when braking with primarybrake
P-20 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F2 | P-20 |  | OG1 | [9 empty] | 27 | Secondary braking time too high
P-22 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F2 | P-22 |  | OG1 | [9 empty] | 28 | No speed reduction with secondary braking
P-23 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F2 | P-23 |  | OG1 | [9 empty] | 31 | Timeout yaw counter
P-25 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F1 | P-25 |  | OG1 | [9 empty] | 34 | Brake not released secondary brake
P-26 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F1 | P-26 |  | OG1 | [9 empty] | 35 | Emergency stop tower base
P-27 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F1 | P-27 |  | OG1 | [9 empty] | 36 | Speed with braked turbine
P-28 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F1 | P-28 |  | OG1 | [9 empty] | 38 | Secondary brake test
P-31 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F4 | P-31 |  | OG1 | [9 empty] | 41 | Vibrations sensor Defect
P-32 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F4 | P-32 |  | OG1 | [9 empty] | 42 | Wrong yaw direction of rotation
P-34 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F2 | P-34 |  | OG1 | [9 empty] | 45 | Hydraulic pump time too high
P-37 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F4 | P-37 |  | OG1 | [9 empty] | 46 | Hydraulic pump time too low
P-38 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F2 | P-38 |  | OG1 | [9 empty] | 47 | Service switch hydraulic top cabinet
P-40 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F3 | P-40 |  | OG1 | [9 empty] | 48 | Hydraulic oil level too low
P-41 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F3 | P-41 |  | OG1 | [9 empty] | 51 | Gearbox oil level too low
P-42 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F3 | P-42 |  | OG1 | [9 empty] | 52 | Gearbox oil ressure too lo
P-43 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F2 | P-43 |  | OG1 | [9 empty] | 53 | Wind vane defect
P-45 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F3 | P-45 |  | OG1 | [9 empty] | 54 | Anemometer defec
P-46 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F3 | P-46 |  | OG1 | [9 empty] | 55 | Rotor impulse sensor defect
P-47 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F3 | P-47 |  | OG1 | [9 empty] | 56 | Generator impulse sensor defect
P-48 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F3 | P-48 |  | OG1 | [9 empty] | 57 | Ratio generator-/rotor speed
P-50 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F4 | P-50 |  | OG1 | [9 empty] | 58 | Demand to stop by an external device
P-51 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F4 | P-51 |  | OG1 | [9 empty] | 59 | Vibration switch
P-52 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F4 | P-52 |  | OG1 | [9 empty] | 60 | Yaw limit switch activated
P-55 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F4 | P-55 |  | OG1 | [9 empty] | 63 | Safety chain
P-56 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F4 | P-56 |  | OG1 | [9 empty] | 65 | Main switch released
Wind_F1 | PWEPL | MSEDCL | 16 | 22.73% |  |  |  | OG1 | [9 empty] | 71 | Dirty gearing oil filter
Wind_F2 | PWEPL | MSEDCL | 19.2 | 27.27% |  |  |  | OG1 | [9 empty] | 72 | Gear oil temperature switching contact
Wind_F3 | PWEPL | MSEDCL | 14.4 | 20.45% |  |  |  | OG1 | [9 empty] | 75 | Generator bearing A overtemperature
Wind_F4 | PWEPL | MSEDCL | 20.8 | 29.55% |  |  |  | OG1 | [9 empty] | 76 | Generator bearing B overtemperature
[18 empty] | 77 | Gearbox oil overtemperature
[18 empty] | 78 | Outside temperature too low
[18 empty] | 81 | Shaft bearing overtemperature
[18 empty] | 82 | Yaw motor overtemperature
[18 empty] | 84 | Gearbox oil temperature too low
[18 empty] | 86 | Braking pad of secondary brake worn out
[18 empty] | 87 | Restart time delay
[18 empty] | 88 | Multiple overtemperature switch off
[18 empty] | 89 | Gearbox oil filter dirty (warning)
[18 empty] | 91 | Gearbox running hot in low stage
[18 empty] | 97 | Generator cooling air overtemperature
[18 empty] | 98 | Gearbox bearing overtemperature
[18 empty] | 99 | Generator overtemperature 1
[18 empty] | 100 | Generator overtemperature 2
[18 empty] | 101 | TopBox DIN21 motor protection aux contact string
[18 empty] | 102 | DTA DIN03 control breaker status
[18 empty] | 105 | Rotor CCU fault voltage
[18 empty] | 106 | Rotor CCU fault current
[18 empty] | 107 | Rotor CCU fault temperature
[18 empty] | 108 | Rotor locking
[18 empty] | 110 | Speed in the tower resonance range
[18 empty] | 112 | Feedback signal from CCU
[18 empty] | 113 | Line CCU fault voltage
[18 empty] | 114 | Line CCU fault current
[18 empty] | 115 | Line CCU fault temperature
[18 empty] | 116 | Line fault voltage
[18 empty] | 117 | Line fault frequency
[18 empty] | 118 | Emergency stop nacelle / hub
[18 empty] | 120 | Communication fault Pitch controller
[18 empty] | 121 | axis 1 fault pitch controller
[18 empty] | 122 | Collective fault pitch controller
[18 empty] | 124 | Pitch Overrun 0deg
[18 empty] | 125 | Pitch Overrun 90deg
[18 empty] | 127 | Generator power switch
[18 empty] | 129 | Generator speed not plausible
[18 empty] | 130 | Braking time rotor blade 1 too high
[18 empty] | 131 | Braking time rotor blade 2 too high
[18 empty] | 132 | Braking time rotor blade 3 too high
[18 empty] | 133 | Battery charging rotor blade drive
[18 empty] | 134 | Battery charging voltage not OK
[18 empty] | 135 | Battery test
[18 empty] | 136 | Limit switch 0deg-rotorblade angle unclear
[18 empty] | 137 | Limit switch 90deg-rotorblade defective
[18 empty] | 138 | Temperature warning pitch motor
[18 empty] | 139 | Overtemperature pitch motor
[18 empty] | 140 | Motor protection pitch motor
[18 empty] | 141 | Rotor CCU collective faults
[18 empty] | 142 | Line CCU collective faults
[18 empty] | 143 | Pulse sensor rotor monitor defect
[18 empty] | 144 | Blade angle asymmetry
[18 empty] | 145 | Pitch control deviation axis 1
[18 empty] | 146 | Turbine stopped due to calm
[18 empty] | 147 | Load shutdown
[18 empty] | 148 | Generator fan service switch
[18 empty] | 149 | axis 2 fault pitch controller
[18 empty] | 150 | axis 3 fault pitch controlle
[18 empty] | 152 | Obstruction light fault / failure
[18 empty] | 153 | Generator brushes worn
[18 empty] | 155 | Maintenance
[18 empty] | 156 | Repair
[18 empty] | 157 | Brake does not close
[18 empty] | 161 | Overvoltage protection triggered
[18 empty] | 163 | Torque deviation
[18 empty] | 164 | Maintenance switch pitch
[18 empty] | 165 | Service switch pitch
[18 empty] | 166 | Normal operation
[18 empty] | 167 | Voltage limiting activated
[18 empty] | 168 | yaw emergency stop
[18 empty] | 169 | Waiting for gearbox oil pressure
[18 empty] | 170 | Increasing speed with falling blade angle
[18 empty] | 171 | Service key brake release
[18 empty] | 173 | Low-noise operation
[18 empty] | 174 | Overtemperature transformer warning
[18 empty] | 175 | Overtemperature transformer disturbance
[18 empty] | 176 | Drive train vibration
[18 empty] | 177 | Tower vibration
[18 empty] | 178 | Fault battery charge switching shut down
[18 empty] | 179 | Successful battery test is needed
[18 empty] | 180 | Wind deviation
[18 empty] | 181 | Spinning position
[18 empty] | 182 | Start-up
[18 empty] | 183 | Load operation
[18 empty] | 184 | Shut down
[18 empty] | 185 | Manual operation pitch
[18 empty] | 186 | Manual operation speed
[18 empty] | 187 | Manual operation torque
[18 empty] | 188 | Manual operation line separation
[18 empty] | 189 | Manual operation yaw
[18 empty] | 190 | Container / nacelle temp.fault (not for CWE turbines)
[18 empty] | 191 | Manual operation generator fan
[18 empty] | 193 | aviation light system common alarm
[18 empty] | 194 | By-pass filter soiling
[18 empty] | 195 | Gearbox pressure loss by-pass filter
[18 empty] | 201 | PLC fault 24V Supply
[18 empty] | 203 | Fault temperature measurement
[18 empty] | 205 | Overtemperature cabinet
[18 empty] | 207 | Ground fault LVMD
[18 empty] | 208 | No communication Cu
[18 empty] | 212 | Battery voltage not OK axis 1
[18 empty] | 213 | Battery voltage not OK axis 2
[18 empty] | 214 | Battery voltage not OK axis 3
[18 empty] | 215 | Direction dependent shut-down
[18 empty] | 218 | Too Frequent cut-ins
[18 empty] | 220 | External stop caused by curtailment
[18 empty] | 221 | External power limitation
[18 empty] | 222 | Yaw runaway
[18 empty] | 223 | Blade angle not plausible axis 1
[18 empty] | 224 | Feedback error circuit breaker
[18 empty] | 235 | Power circuit breaker CCU released
[18 empty] | 237 | Generator overtemperature 3
[18 empty] | 250 | Temp. sensor error (shut down)
[18 empty] | 251 | Temp. sensor error (warning)
[18 empty] | 252 | Temp. not plausible
[18 empty] | 261 | Manual Hydraulic / Brake
[18 empty] | 269 | Reboot PLC
[18 empty] | 271 | Malfunction particle counter
[18 empty] | 272 | Shadow related shut down
[18 empty] | 273 | Too long manual / Service operation
[18 empty] | 274 | Pitch thyristor 1 fault
[18 empty] | 275 | Pitch thyristor 2 fault
[18 empty] | 276 | Pitch thyristor 3 fault
[18 empty] | 277 | Power limitation due to high temperature
[18 empty] | 278 | Shut-down low voltage
[18 empty] | 279 | Low voltage ride through
[18 empty] | 280 | Prepressure error, active brake
[18 empty] | 281 | Prepressure warning, active brake
[18 empty] | 282 | Test prepressure active brake
[18 empty] | 286 | Crow bar triggered CCU
[18 empty] | 287 | Power limitation CCU
[18 empty] | 288 | Response signal interrupt battery driven pitching
[18 empty] | 289 | Test measuring system
[18 empty] | 290 | Idling in speed control
[18 empty] | 291 | Undertemperature Cabinet
[18 empty] | 294 | Warning adv controls sensors
[18 empty] | 295 | Heat up state
[18 empty] | 297 | Turbine heat up error
[18 empty] | 302 | Brake pad worn, warning
[18 empty] | 306 | Manual operation yaw hydraulic
[18 empty] | 308 | Idling command at WTG
[18 empty] | 310 | Fault reset
[18 empty] | 313 | Cabinet overtemperature warning
[18 empty] | 314 | Power limitation freq. dependent
[18 empty] | 317 | Undertemperature slipring
[18 empty] | 319 | Service Switch Rotorlock
[18 empty] | 324 | Activation rotor lock
[18 empty] | 333 | Block restart due to grid frequency
[18 empty] | 334 | Circuit breaker maintenance necessary
[18 empty] | 335 | Generator overspeed 2
[18 empty] | 336 | Rotor overspeed 2
[18 empty] | 337 | Line CCU temperature warning
[18 empty] | 338 | Rotor CCU temperature warning
[18 empty] | 340 | Pitch control deviation Axis 2
[18 empty] | 341 | Pitch control deviation Axis 3
[18 empty] | 342 | Blade Angle not plausible Axis 2
[18 empty] | 343 | Blade Angle not plausible Axis 3
[18 empty] | 344 | Pitch malfunction 2 or 3 blades
[18 empty] | 345 | Battery drive after grid fault
[18 empty] | 346 | Rotor speeds not plausible
[18 empty] | 348 | Service stop
[18 empty] | 349 | Service stop with fault
[18 empty] | 352 | Communication fault wind measurement device
[18 empty] | 353 | Malfunction wind measurement device
[18 empty] | 355 | Power limitation fault adv.Controls sensor
[18 empty] | 357 | Grid voltage drop CU
[18 empty] | 359 | Internal Pitch Mode
[18 empty] | 360 | Internal Pitch Mode Implausible
[18 empty] | 361 | Power limitation adv Power limitation adv control hub offsets
[18 empty] | 362 | Calibrating ALC gains
[18 empty] | 363 | Mapping ALC hub offsets
[18 empty] | 365 | Service switch pitch unplausible
[18 empty] | 366 | Aero balance worsening
[18 empty] | 368 | MSF bending out of threshold
[18 empty] | 371 | Pitch limitation low power avoidance
[18 empty] | 377 | Communication to the frequency converter is not active
[18 empty] | 381 | Communication fault pitch controller Axis 1
[18 empty] | 382 | Communication fault pitch controller Axis 2
[18 empty] | 383 | Communication fault pitch controller Axis 3
[18 empty] | 394 | Yaw Map pending
[18 empty] | 395 | Yaw Mapping
[18 empty] | 396 | Yaw Mapping Error
[17 empty] | New Added | 424 | System re-initialization after grid outage
[18 empty] | 430 | Yaw tooth sensor 1 timeout
[18 empty] | 431 | Yaw tooth sensor 2 timeout
[18 empty] | 907 | Yaw Brake Voltage 230Volt not OK
[18 empty] | 367 | CCU fault at abnormal grid condition
[18 empty] | VCB_OC | Internal Line VCB tripped in over current
[18 empty] | Y_Sens_Err | Yaw sensor error
[18 empty] | CE100001 | Manual Stop
[18 empty] | CE100002 | Major BD - Blade
[18 empty] | CE100003 | Major BD - Transformer
[18 empty] | CE100004 | Major BD - Generator
[18 empty] | CE100005 | Major BD - Gearbox
[18 empty] | CE100006 | Major BD - Main Bearing
[18 empty] | CE100007 | Transmission Line Related work
[18 empty] | CE100008 | General Work Stoppage
[18 empty] | CE100009 | Major BD - Power Cable
[18 empty] | CE100011 | Major BD - DFIG
[18 empty] | CE100012 | Major BD - Foundation
[18 empty] | CE100013 | Theft
[18 empty] | CE100010 | Manual Stop - Preventive Maintenance Activity
[18 empty] | CE100014 | Manual Stop - Audit
[18 empty] | CE100015 | Manual Stop - Safety Related
[18 empty] | CE100016 | Manual Stop - Blade Cleaning
[18 empty] | CE100017 | UPS breakdown

## Modelling New (hidden)
Sr. No. | Month Name | Month Number | Month | CY | FY | No. of Days in Month | GHI | POA | WS | Tamb | Tmod | Egrid (MWh) | Bugt_Capacity | PR | Daily POA | Days Operated | MTD POA | YTD POA | Daily Energy (MWh) | MTD Energy (MWh) | YTD Energy (MWh) | Bugt CUF (%) | Bugt CUF (%) MTD | Bugt CUF (%)YTD | Ave. Cap MTD | Ave. Cap YTD | CC Energy MTD | WS MTD | WS YTD | Bugt PA | Bugt EGA | Bugt TA | Bugt MA | Bugt IGA | Corelation | Bugt Line loss | Bugt Reactive Power | Total Capacity | 70.4
1 | April | 4 | 2022-04-01 | 2022 | FY23 | 30 |  |  | 5.22 |  |  | 6797.3115 | 70.4 |  |  | 0 |  |  | 226.577 | 0 | 0 | 13.41% |  |  | 0 | 70.4 |  | 6.4041 | 6.4041 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
2 | May | 5 | 2022-05-01 | 2022 | FY23 | 31 |  |  | 5.7233 |  |  | 10772.5855 | 70.4 |  |  | 0 |  |  | 347.5028 | 0 | 0 | 20.57% |  |  | 0 | 70.4 |  | 5.9682 | 6.1861 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
3 | June | 6 | 2022-06-01 | 2022 | FY23 | 30 |  |  | 6.81 |  |  | 15494.0713 | 70.4 |  |  | 0 |  |  | 516.469 | 0 | 0 | 30.57% |  |  | 0 | 70.4 |  | 5.6311 | 6.0011 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
4 | July | 7 | 2022-07-01 | 2022 | FY23 | 31 |  |  | 9.8233 |  |  | 27867.6204 | 70.4 |  |  | 0 |  |  | 898.9555 | 0 | 0 | 53.21% |  |  | 0 | 70.4 |  | 7.1311 | 6.2836 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
5 | August | 8 | 2022-08-01 | 2022 | FY23 | 31 |  |  | 9.1 |  |  | 32561.9712 | 70.4 |  |  | 0 |  |  | 1050.3862 | 0 | 0 | 62.17% |  |  | 0 | 70.4 |  | 9.453 | 6.9175 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
6 | September | 9 | 2022-09-01 | 2022 | FY23 | 30 |  |  | 5.56 |  |  | 11125.3402 | 70.4 |  |  | 0 |  |  | 370.8447 | 0 | 0 | 21.95% |  |  | 0 | 70.4 |  | 10.3038 | 7.4819 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
7 | October | 10 | 2022-10-01 | 2022 | FY23 | 31 |  |  | 4.1733 |  |  | 4626.5134 | 70.4 |  |  | 0 |  |  | 149.2424 | 0 | 0 | 8.833% |  |  | 0 | 70.4 |  | 8.5195 | 7.6301 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
8 | November | 11 | 2022-11-01 | 2022 | FY23 | 30 |  |  | 4.4633 |  |  | 7150.0662 | 70.4 |  |  | 0 |  |  | 238.3355 | 0 | 0 | 14.11% |  |  | 0 | 70.4 |  | 7.2367 | 7.5809 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
9 | December | 12 | 2022-12-01 | 2022 | FY23 | 31 |  |  | 4.79 |  |  | 7204.3361 | 70.4 |  |  | 0 |  |  | 232.3979 | 0 | 0 | 13.75% |  |  | 0 | 70.4 |  | 6.0016 | 7.4054 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
10 | January | 1 | 2023-01-01 | 2023 | FY23 | 31 |  |  | 3.75 |  |  | 3283.3321 | 70.4 |  |  | 0 |  |  | 105.9139 | 0 | 0 | 6.269% |  |  | 0 | 70.4 |  | 6.7074 | 7.3356 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
11 | February | 2 | 2023-02-01 | 2023 | FY23 | 28 |  |  | 3.925 |  |  | 3324.0346 | 70.4 |  |  | 0 |  |  | 118.7155 | 0 | 0 | 7.026% |  |  | 0 | 70.4 |  | 7.0533 | 7.31 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
12 | March | 4 | 2023-03-01 | 2023 | FY23 | 31 |  |  | 4.565 |  |  | 5467.6977 | 70.4 |  |  | 0 |  |  | 176.3773 | 0 | 0 | 10.44% |  |  | 0 | 70.4 |  | 7.4111 | 7.3184 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
13 | April | 5 | 2023-04-01 | 2023 | FY24 | 30 |  |  | 5.22 |  |  | 6300 | 70.4 |  |  | 0 |  |  | 210 | 0 | 0 | 12.43% |  |  | 0 | 70.4 |  | 6.4041 | 6.4041 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
14 | May | 6 | 2023-05-01 | 2023 | FY24 | 31 |  |  | 5.7233 |  |  | 10320 | 70.4 |  |  | 0 |  |  | 332.9032 | 0 | 0 | 19.7% |  |  | 0 | 70.4 |  | 5.9682 | 6.1861 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
15 | June | 7 | 2023-06-01 | 2023 | FY24 | 30 |  |  | 6.81 |  |  | 14360 | 70.4 |  |  | 0 |  |  | 478.6667 | 0 | 0 | 28.33% |  |  | 0 | 70.4 |  | 5.6311 | 6.0011 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
16 | July | 8 | 2023-07-01 | 2023 | FY24 | 31 |  |  | 9.8233 |  |  | 26690 | 70.4 |  |  | 0 |  |  | 860.9677 | 0 | 0 | 50.96% |  |  | 0 | 70.4 |  | 7.1311 | 6.2836 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
17 | August | 9 | 2023-08-01 | 2023 | FY24 | 31 |  |  | 9.1 |  |  | 31190 | 70.4 |  |  | 0 |  |  | 1006.129 | 0 | 0 | 59.55% |  |  | 0 | 70.4 |  | 9.453 | 6.9175 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
18 | September | 10 | 2023-09-01 | 2023 | FY24 | 30 |  |  | 5.56 |  |  | 10320 | 70.4 |  |  | 0 |  |  | 344 | 0 | 0 | 20.36% |  |  | 0 | 70.4 |  | 10.3038 | 7.4819 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
19 | October | 11 | 2023-10-01 | 2023 | FY24 | 31 |  |  | 4.1733 |  |  | 4720 | 70.4 |  |  | 0 |  |  | 152.2581 | 0 | 0 | 9.011% |  |  | 0 | 70.4 |  | 8.5195 | 7.6301 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
20 | November | 12 | 2023-11-01 | 2023 | FY24 | 30 |  |  | 4.4633 |  |  | 7060 | 70.4 |  |  | 0 |  |  | 235.3333 | 0 | 0 | 13.93% |  |  | 0 | 70.4 |  | 7.2367 | 7.5809 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
21 | December | 1 | 2023-12-01 | 2023 | FY24 | 31 |  |  | 4.79 |  |  | 7340 | 70.4 |  |  | 0 |  |  | 236.7742 | 0 | 0 | 14.01% |  |  | 0 | 70.4 |  | 6.0016 | 7.4054 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
22 | January | 2 | 2024-01-01 | 2024 | FY24 | 31 |  |  | 3.75 |  |  | 3350 | 70.4 |  |  | 0 |  |  | 108.0645 | 0 | 0 | 6.396% |  |  | 0 | 70.4 |  | 6.7074 | 7.3356 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
23 | February | 4 | 2024-02-01 | 2024 | FY24 | 29 |  |  | 3.925 |  |  | 3170 | 70.4 |  |  | 0 |  |  | 109.3103 | 0 | 0 | 6.47% |  |  | 0 | 70.4 |  | 7.0533 | 7.31 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
24 | March | 5 | 2024-03-01 | 2024 | FY24 | 31 |  |  | 4.565 |  |  | 5570 | 70.4 |  |  | 0 |  |  | 179.6774 | 0 | 0 | 10.63% |  |  | 0 | 70.4 |  | 7.4111 | 7.3184 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
25 | April | 6 | 2024-04-01 | 2024 | FY25 | 30 |  |  | 5.22 |  |  | 6843.4 | 70.4 |  |  | 0 |  |  | 228.1133 | 0 | 532.0645 | 13.5% |  |  | 0 | 70.4 |  | 6.4041 | 6.4041 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
26 | May | 7 | 2024-05-01 | 2024 | FY25 | 31 |  |  | 5.7233 |  |  | 10848.5 | 70.4 |  |  | 0 |  |  | 349.9516 | 0 | 532.0645 | 20.71% |  |  | 0 | 70.4 |  | 5.9682 | 7.3184 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
27 | June | 8 | 2024-06-01 | 2024 | FY25 | 30 |  |  | 6.81 |  |  | 15593.1 | 70.4 |  |  | 0 |  |  | 519.77 | 0 | 0 | 30.76% |  |  | 0 | 70.4 |  | 5.6311 | 6.0011 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
28 | July | 9 | 2024-07-01 | 2024 | FY25 | 31 |  |  | 9.8233 |  |  | 28051.7 | 70.4 |  |  | 0 |  |  | 904.8935 | 0 | 0 | 53.56% |  |  | 0 | 70.4 |  | 7.1311 | 6.2836 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
29 | August | 10 | 2024-08-01 | 2024 | FY25 | 31 |  |  | 9.1 |  |  | 32781.6 | 70.4 |  |  | 0 |  |  | 1057.471 | 0 | 0 | 62.59% |  |  | 0 | 70.4 |  | 9.453 | 6.9175 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
30 | September | 11 | 2024-09-01 | 2024 | FY25 | 30 |  |  | 5.56 |  |  | 11201.7 | 70.4 |  |  | 0 |  |  | 373.39 | 0 | 0 | 22.1% |  |  | 0 | 70.4 |  | 10.3038 | 7.4819 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
31 | October | 12 | 2024-10-01 | 2024 | FY25 | 31 |  |  | 4.1733 |  |  | 4658.2 | 70.4 |  |  | 0 |  |  | 150.2645 | 0 | 0 | 8.893% |  |  | 0 | 70.4 |  | 8.5195 | 7.6301 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
32 | November | 1 | 2024-11-01 | 2024 | FY25 | 30 |  |  | 4.4633 |  |  | 7203.1 | 70.4 |  |  | 0 |  |  | 240.1033 | 0 | 0 | 14.21% |  |  | 0 | 70.4 |  | 7.2367 | 7.5809 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
33 | December | 2 | 2024-12-01 | 2024 | FY25 | 31 |  |  | 4.79 |  |  | 7252 | 70.4 |  |  | 0 |  |  | 233.9355 | 0 | 0 | 13.85% |  |  | 0 | 70.4 |  | 6.0016 | 7.4054 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
34 | January | 4 | 2025-01-01 | 2025 | FY25 | 31 |  |  | 3.75 |  |  | 3308.3 | 70.4 |  |  | 0 |  |  | 106.7194 | 0 | 0 | 6.316% |  |  | 0 | 70.4 |  | 6.7074 | 7.3356 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
35 | February | 5 | 2025-02-01 | 2025 | FY25 | 28 |  |  | 3.925 |  |  | 3320.2 | 70.4 |  |  | 0 |  |  | 118.5786 | 0 | 0 | 7.018% |  |  | 0 | 70.4 |  | 7.0533 | 7.31 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
36 | March | 6 | 2025-03-01 | 2025 | FY25 | 31 |  |  | 4.565 |  |  | 5498 | 70.4 |  |  | 3 |  |  | 177.3548 | 532.0645 | 532.0645 | 10.5% | 10.5% | 10.5% | 6.8129 | 70.4 |  | 7.4111 | 7.3184 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
37 | April | 7 | 2025-04-01 | 2025 | FY26 | 30 |  |  | 5.22 |  |  | 6843.3984 | 70.4 |  |  | 30 |  |  | 228.1133 | 6843.3984 | 6843.3984 | 13.5% | 13.5% | 13.5% | 70.4 | 70.4 |  | 6.4041 | 6.4041 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
38 | May | 8 | 2025-05-01 | 2025 | FY26 | 31 |  |  | 5.7233 |  |  | 10848.466 | 70.4 |  |  | 31 |  |  | 349.9505 | 10848.466 | 17691.8644 | 20.71% | 20.71% | 17.17% | 70.4 | 70.4 |  | 5.9682 | 7.3184 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
39 | June | 9 | 2025-06-01 | 2025 | FY26 | 30 |  |  | 6.81 |  |  | 15593.0879 | 70.4 |  |  | 12 |  |  | 519.7696 | 6237.2352 | 23929.0996 | 30.76% | 30.76% | 19.4% | 28.16 | 70.4 |  | 5.6311 | 6.0011 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
40 | July | 10 | 2025-07-01 | 2025 | FY26 | 31 |  |  | 9.8233 |  |  | 28051.7141 | 70.4 |  |  | 0 |  |  | 904.894 | 0 | 23929.0996 | 53.56% |  | 19.4% | 0 | 70.4 |  | 7.1311 | 6.2836 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
41 | August | 11 | 2025-08-01 | 2025 | FY26 | 31 |  |  | 9.1 |  |  | 32781.5854 | 70.4 |  |  | 0 |  |  | 1057.4705 | 0 | 23929.0996 | 62.59% |  | 19.4% | 0 | 70.4 |  | 9.453 | 6.9175 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
42 | September | 12 | 2025-09-01 | 2025 | FY26 | 30 |  |  | 5.56 |  |  | 11201.6537 | 70.4 |  |  | 0 |  |  | 373.3885 | 0 | 23929.0996 | 22.1% |  | 19.4% | 0 | 70.4 |  | 10.3038 | 7.4819 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
43 | October | 1 | 2025-10-01 | 2025 | FY26 | 31 |  |  | 4.1733 |  |  | 4658.2035 | 70.4 |  |  | 0 |  |  | 150.2646 | 0 | 23929.0996 | 8.894% |  | 19.4% | 0 | 70.4 |  | 8.5195 | 7.6301 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
44 | November | 2 | 2025-11-01 | 2025 | FY26 | 30 |  |  | 4.4633 |  |  | 7203.0753 | 70.4 |  |  | 0 |  |  | 240.1025 | 0 | 23929.0996 | 14.21% |  | 19.4% | 0 | 70.4 |  | 7.2367 | 7.5809 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
45 | December | 4 | 2025-12-01 | 2025 | FY26 | 31 |  |  | 4.79 |  |  | 7252.0328 | 70.4 |  |  | 0 |  |  | 233.9365 | 0 | 23929.0996 | 13.85% |  | 19.4% | 0 | 70.4 |  | 6.0016 | 7.4054 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
46 | January | 5 | 2026-01-01 | 2026 | FY26 | 31 |  |  | 3.75 |  |  | 3308.3229 | 70.4 |  |  | 0 |  |  | 106.7201 | 0 | 23929.0996 | 6.316% |  | 19.4% | 0 | 70.4 |  | 6.7074 | 7.3356 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
47 | February | 6 | 2026-02-01 | 2026 | FY26 | 28 |  |  | 3.925 |  |  | 3320.2002 | 70.4 |  |  | 0 |  |  | 118.5786 | 0 | 23929.0996 | 7.018% |  | 19.4% | 0 | 70.4 |  | 7.0533 | 7.3184 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
48 | March | 7 | 2026-03-01 | 2026 | FY26 | 31 |  |  | 4.565 |  |  | 5498.0142 | 70.4 |  |  | 0 |  |  | 177.3553 | 0 | 23929.0996 | 10.5% |  | 19.4% | 0 | 70.4 |  | 7.4111 | 7.3184 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
Formulas:
No. of Days in Month = DAY(EOMONTH([Month],0))